TO BE DELIVERED AND E-FILED: Boardsec@oeb.gov.on.ca

April 26, 2010

Ontario Energy Board

2300 Yonge Street

27th Floor

Toronto, ON M4P 1E4

Attn: Ms. Kirsten Walli, Board Secretary

Re: Hydro One Networks Inc. Toronto Midtown Transmission Reinforcement Project – Your File EB-2009-0425

Evidence of The North Rosedale Ratepayers Association

The North Rosedale Ratepayers Association (“NRRA”) hereby submits the following evidence to the Ontario Energy Board in respect of this Application by Hydro One Networks Inc. (“Hydro One”). This evidence is limited to the portion of the Project located between Birch Junction and Bayview Junction.

Our detailed review and consideration of the route and construction methods proposed by Hydro One indicate that the associated costs would be excessive when compared with a construction hybrid consisting of soft ground tunneling in the vicinity of Yonge Street and trenching elsewhere along a route deviating slightly from that proposed by Hydro One, as described below (the “Hybrid Solution”). The Hybrid Solution would result in substantially lower costs and a much shorter construction schedule, while at the same time avoiding most of the difficulties inherent in co-ordinating schedules and making the necessary arrangements with the CPR. Furthermore, the impact on the community would be greatly reduced because the work will be undertaken in sections and “move along” with the trench.

THE HYBRID SOLUTION

Our review of the material filed by Hydro One, as well as our site inspections, indicates that the optimal routing and construction technique would be as follows:

I - Birch Junction to East Side of Summerhill Subway Station on Shaftesbury Avenue

This section of the route will involve relatively shallow, soft ground tunneling, rather that hard rock tunneling at great depth. We recognize the serious issues associated with running the proposed circuits across the Yonge Street strip, with its extensive utility infrastructure and the proximity of the Yonge Street Subway and Summerhill Station. However, this tunnel does not need to be 3 metres in diameter or 50 – 60 metres deep, since it will be accessed and serviced from either end and its length will be relatively short.

II - Balance of Shaftesbury Avenue

Trenching, located so as to minimize interference with the existing utility infrastructure, will be used on Shaftesbury Avenue. We note that we have asked for, but have not yet received, details of the existing below-ground infrastructure in Shaftesbury Avenue and Yonge Street. Trenching will be within the street pavement where-ever possible. The road allowance south of the curb/sidewalk on the south side of Shaftesbury Avenue will be used only the extent absolutely necessary. If required, the existing trees which have been planted in front of the relatively new (approximately 10-12 years old) residential development on the south side of Shaftesbury Avenue could be temporarily removed and/or replaced as appropriate. Further east on Shaftesbury Avenue, the absence of buildings on the south side of the street should reduce interference with existing utilities, but partial re-landscaping of this strip is quite viable. We appreciate the concerns of the residents of Shaftesbury Avenue in this respect, concerns that are equally shared by the residents of the North Rosedale, Moore Park and Bennington Heights communities. However, the Shaftesbury residents appear not to appreciate the enormous additional costs associated with tunneling.

III - David Balfour Park from Shaftesbury Avenue to Mount Pleasant Road

The existing Hydro One circuits have been trenched through David Balfour Park. There is no reason why the proposed new circuits cannot also be trenched, following a route adjacent to the existing underground circuits.

IV - Mount Pleasant Road to East End of Hydro One Lands Immediately North of CPR

This stretch, along Carstowe Road, across MacLennan Avenue and through the Hydro One lands located immediately north of the CPR right-of-way, comprises about one-third of the entire route. This section of the route is ideal for trenching since, with the exception of the street crossings over Mount Pleasant Road, MacLennan Avenue and possibly the southerly extension of Sighthill Avenue, there appears to be little or no existing below-ground infrastructure.

V - East End of Hydro One Lands to Moore Park Ravine

This section of the route involves the acquisition, by agreement or expropriation, of a relatively narrow easement across the rear portions of 17 large residential properties fronting onto Rosedale Heights Drive. The lands over which the easement will be required are immediately adjacent to the CPR right-of-way, partially covered with decaying forest and, for the most part, not visible from the residences which are situate on lots having depths of between 225 and 400 feet. In addition, approximately 300 feet of this stretch is over a public, but un-opened, lane owned by the City of Toronto. There does not appear to be any existing below-ground infrastructure to interfere with or limit trenching through this section of the route.

VI – Moore Park Ravine

The existing Hydro One circuits have been trenched through the Moore Park Ravine. There is no reason why the proposed new circuits cannot also be trenched, following a route adjacent to the existing underground circuits.

VII – Moore Park Ravine to Bayview Junction

This section of the route also requires the acquisition of a narrow easement, having a total length of about 100 metres, across the rear portions of 4 residential properties fronting onto Moorehill Drive. The balance of this section of the route is across an un-opened portion of the original road allowance for Bayview Avenue. Of the 4 residential properties, 3 are shallower in depth than those located on Rosedale Heights Drive and drop off steeply towards the CPR right-of-way. There does not appear to be any existing below-ground infrastructure to interfere with or limit trenching through this section of the route. However, the steepness of the site may suggest boring through this short easement, rather than trenching, or trenching though a portion of the CPR right-of-way.

THE ADVANTAGES OF THE HYBRID SOLUTION

A – Tunneling is new Technology for Hydro One

Hydro One has very limited project experience with tunneling. Given the fact that substantial contingencies have been built into the budget for this Project, tunneling is very clearly viewed by Hydro One as much more risky than trenching.

B - Tunneling Makes a Relatively Simple Installation into an Enormous Project

Tunneling requires the construction of a large staging area and main shaft with a depth of between 50 & 60 metres and a width of between 7 & 10 metres. This is necessary in order to lower the boring equipment to the level of the hard rock tunnel, to install elevating equipment to provide access to the underground work site for workers, supplies and equipment and to remove and store the spoil from the shaft and tunnel. The proposed tunneling project would create huge amounts of rock tailings that will need to be transported to dump sites. On the other hand, a substantial portion of the material excavated in the trenching process will go right back into the trench to cover the new cable duct.

C - The Cost and Time Efficiencies from Trenching are Very Significant

Trenching does not utilize the sophisticated tunneling equipment required for deep rock tunneling. We believe there to be a very limited supply of tunneling equipment and for that reason it is subject to highly variable costs. These costs have not yet been determined by Hydro One. In addition, a catastrophic failure of the equipment could lead to lengthy constructions delays and associated cost escalations. Conversely, trenching uses basic excavation equipment and workers are well experienced using this approach. Furthermore, construction time can be reduced by installing prefabricated cable ducts and using other modified trenching techniques.

D – This Route is Ideal for Trenching

The route described in the Hybrid Solution is ideal for trenching. The adjacent CPR right-of-way has been effectively used for earlier trenching installations by both Hydro One and the CPR. With the exception of the Yonge Street / Subway strip and a portion of Shaftesbury Avenue, there is relatively little below-ground infrastructure to interfere with or limit trenching, with substantial associated cost benefits.

E – Co-ordination with CPR

Scheduling and coordinating work and easement issues with the CPR has been cited by Hydro One as a major challenge. Using the route described in the Hybrid Solution will mean that most, if not all, of the trenching will occur well away from the CPR tracks.

The NRRA also has a number of concerns regarding the environmental and community impact of this Project, irrespective of the means of construction and the route chosen. These have already been raised with Hydro One in the context of the current Environmental Assessment and, to the extent necessary, they will also be addressed with the Ministry of the Environment.

The NRRA expressly reserves the right to submit additional evidence upon receipt and review of the further responses to the NRRA Interrogatories to be provided by Hydro One pursuant to the letter dated April 23, 2010 from Hydro One to the Board.

c.c. Hydro One Networks Inc. BY DELIVERY & E-MAIL TO regulatory@hydroone.com

c.c. Hydro One Networks Inc. BY DELIVERY & E-MAIL TO mengelberg@hydroone.com