## App.2-P_Loss Factors
Appendix 2-P
Loss Factors
|  | Historical Years |  |  |  |  | 5-Year Average
|  | 2007 | 2008 | 2009 | 2010 | 2011
Losses Within Distributor's System
A(1) | "Wholesale" kWh delivered to distributor (higher value) | 8249691981 | 8096551762 | 7742344266 | 7949145632 | 7880490220 | 7983644772.2
A(2) | "Wholesale" kWh delivered to distributor (lower value) | 8212734674.9627 | 8060280499.7511 | 7707659796.9139 | 7913534725.7342 | 7845186879.0443 | 7947879315.2812
B | Portion of "Wholesale" kWh delivered to distributor for its Large Use Customer(s) | 1027043917.3714 | 1066438921.2 | 1019358131.9143 | 1064815719.9 | 1062207205.8857 | 1047972779.2543
C | Net "Wholesale" kWh delivered to distributor = A(2) - B | 7185690757.5912 | 6993841578.5511 | 6688301664.9996 | 6848719005.8342 | 6782979673.1586 | 6899906536.0269
D | "Retail" kWh delivered by distributor | 7935279546.8911 | 7821062567.7343 | 7498987528.8681 | 7708674747.9391 | 7626204362.8963 | 7718041750.8658
E | Portion of "Retail" kWh delivered by distributor to its Large Use Customer(s) | 1016875165.7143 | 1055880120 | 1009265477.1429 | 1054272990 | 1051690302.8571 | 1037596811.1429
F | Net "Retail" kWh delivered by distributor = D - E | 6918404381.1768 | 6765182447.7343 | 6489722051.7253 | 6654401757.9391 | 6574514060.0392 | 6680444939.7229
G | Loss Factor in Distributor's system = C / F | 1.0386 | 1.0338 | 1.0306 | 1.0292 | 1.0317 | 1.0329
Losses Upstream of Distributor's System
H | Supply Facilities Loss Factor | 1.0045 | 1.0045 | 1.0045 | 1.0045 | 1.0045 | 1.0045
Total Losses
I | Total Loss Factor = G x H | 1.0433 | 1.0385 | 1.0352 | 1.0338 | 1.0364 | 1.0375
Notes
A(1) | If directly connected to the IESO-controlled grid, kWh pertains to the virtual meter on the primary or high voltage side of the transformer at the interface with the transmission grid. This corresponds to the "With Losses" kWh value provided by the IESO's MV-WEB. It is the higher of the two values provided by MV-WEB.
If fully embedded within a host distributor, kWh pertains to the virtual meter on the primary or high voltage side of the transformer, at the interface between the host distributor and the transmission grid. For example, if the host distributor is Hydro One Networks Inc., kWh from the Hydro One Networks' invoice corresponding to "Total kWh w Losses" should be reported. This corresponds to the higher of the two kWh values provided in Hydro One Networks' invoice.
If partially embedded, kWh pertains to the sum of the above.
A(2) | If directly connected to the IESO-controlled grid, kWh pertains to a metering installation on the secondary or low voltage side of the transformer at the interface with the transmission grid. This corresponds to the "Without Losses" kWh value provided by the IESO's MV-WEB. It is the lower of the two kWh values provided by MV-WEB.
If fully embedded with the host distributor, kWh pertains to an actual or virtual meter at the interface between the embedded distributor and the host distributor. For example, if the host distributor is Hydro One Networks Inc., kWh from the Hydro One Networks' invoice corresponding to "Total kWh" should be reported. This corresponds to the lower of the two kWh values provided in Hydro One Networks' invoice.
If partially embedded, kWh pertains to the sum of the above.
Additionally, kWh pertaining to distributed generation directly connected to the distributor's own distribution network should be included in A(2).
B | If a Large Use Customer is metered on the secondary or low voltage side of the transformer, the default loss is 1% (i.e., B = 1.01 X E).
D | kWh corresponding to D should equal "total billed energy sales in kWhs for each rate class" in item 1 of Section 2.1.3 of the "Electricity Reporting and Record-keeping Requirements" dated May 1, 2010 or in any successor document.
G and I | These loss factors pertain to secondary-metered customers with demand less than 5,000 kW.
H | If directly connected to the IESO-controlled grid, SFLF = 1.0045.
If fully embedded within a host distributor, SFLF = loss factor re losses in transformer at grid interface X loss factor re losses in host distributor's system. If the host distributor is Hydro One Networks Inc., SFLF = 1.0060 X 1.0278 = 1.0340. If partially embedded, SFLF should be calculated as the weighted average of above.
Distributors that wish to propose a different SFLF should provide appropriate justification for any such proposal including supporting
calculations and any other relevant material.