## Appendix 2BB Service Life Comp
[11 empty] | File Number: |  | EB-2013-0123
Exhibit:
Tab:
Schedule:
Page:
Date:
Appendix 2-BB
Service Life Comparison
Table F-1 from Kinetrics Report1
|  | Asset Details |  |  | Useful Life |  |  | USoA Account Number | USoA Account Description | Current |  | Proposed
Parent* | # | Category¦ Component ¦ Type |  |  | MIN UL | TUL | MAX UL |  |  | Years | Rate | Years | Rate
OH | 1 | Fully Dressed Wood Poles | Overall |  | 35 | 45 | 75 | 1830 | Overhead poles, towers, and fixtures | 25 | 4% | 45 | 2.222%
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 2 | Fully Dressed Concrete Poles | Overall |  | 50 | 60 | 80
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 3 | Fully Dressed Steel Poles | Overall |  | 60 | 60 | 80
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 4 | OH Line Switch |  |  | 30 | 45 | 55 | 1835 | Overhead line switches, conductors & devices | 25 | 4% | 60 | 1.667%
| 5 | OH Line Switch Motor |  |  | 15 | 25 | 25
| 6 | OH Line Switch RTU |  |  | 15 | 20 | 20
| 7 | OH Integral Switches |  |  | 35 | 45 | 60
| 8 | OH Conductors |  |  | 50 | 60 | 75
| 9 | OH Transformers & Voltage Regulators |  |  | 30 | 40 | 60 | 1850 | Line Transformers- Overhead & Underground Transformers | 25 | 4% | 40 | 2.5%
| 10 | OH Shunt Capacitor Banks |  |  | 25 | 30 | 40
| 11 | Reclosers |  |  | 25 | 40 | 55
TS & MS | 12 | Power Transformers | Overall |  | 30 | 45 | 60
|  |  | Bushing |  | 10 | 20 | 30
|  |  | Tap Changer |  | 20 | 30 | 60
| 13 | Station Service Transformer |  |  | 30 | 45 | 55
| 14 | Station Grounding Transformer |  |  | 30 | 40 | 40
| 15 | Station DC System | Overall |  | 10 | 20 | 30 | 1820 | Station Equipment | 30 | 3.333% | 30 | 3.333%
|  |  | Battery Bank |  | 10 | 15 | 15
|  |  | Charger |  | 20 | 20 | 30
| 16 | Station Metal Clad Switchgear | Overall |  | 30 | 40 | 60
|  |  | Removable Breaker |  | 25 | 40 | 60
| 17 | Station Independent Breakers |  |  | 35 | 45 | 65
| 18 | Station Switch |  |  | 30 | 50 | 60
| 19 | Electromechanical Relays |  |  | 25 | 35 | 50
| 20 | Solid State Relays |  |  | 10 | 30 | 45
| 21 | Digital & Numeric Relays |  |  | 15 | 20 | 20
| 22 | Rigid Busbars |  |  | 30 | 55 | 60
| 23 | Steel Structure |  |  | 35 | 50 | 90
UG | 24 | Primary Paper Insulated Lead Covered (PILC) Cables |  |  | 60 | 65 | 75
| 25 | Primary Ethylene-Propylene Rubber (EPR) Cables |  |  | 20 | 25 | 25
| 26 | Primary Non-Tree Retardant (TR) Cross Linked Polyethylene (XLPE) Cables Direct Buried |  |  | 20 | 25 | 30
| 27 | Primary Non-TR XLPE Cables in Duct |  |  | 20 | 25 | 30
| 28 | Primary TR XLPE Cables Direct Buried |  |  | 25 | 30 | 35
| 29 | Primary TR XLPE Cables in Duct |  |  | 35 | 40 | 55 | 1846 | Undergound conductors & devices- primary cables | 25 | 4% | 40 | 2.5%
| 30 | Secondary PILC Cables |  |  | 70 | 75 | 80
| 31 | Secondary Cables Direct Buried |  |  | 25 | 35 | 40
| 32 | Secondary Cables in Duct |  |  | 35 | 40 | 60 | 1847 | Underground conductors & devices - secondary cables | 25 | 4% | 35 | 2.857%
| 33 | Network Tranformers | Overall |  | 20 | 35 | 50
|  |  | Protector |  | 20 | 35 | 40
| 34 | Pad-Mounted Transformers |  |  | 25 | 40 | 45
| 35 | Submersible/Vault Transformers |  |  | 25 | 35 | 45 | 1845 | Undergound Conductors & devices | 25 | 4% | 0
| 36 | UG Foundation |  |  | 35 | 55 | 70 | 1852 | Line Transformers- Underground Foundations & Underground Vaults | 25 | 4% | 60 | 1.667%
| 37 | UG Vaults | Overall |  | 40 | 60 | 80
|  |  | Roof |  | 20 | 30 | 45
| 38 | UG Vault Switches |  |  | 20 | 35 | 50
| 39 | Pad-Mounted Switchgear |  |  | 20 | 30 | 45 | 1851 | Line Transformers-Pad Mounted Switchgear | 25 | 4% | 20 | 5%
| 40 | Ducts |  |  | 30 | 50 | 85
| 41 | Concrete Encased Duct Banks |  |  | 35 | 55 | 80 | 1840 | Undergound conduit- ducts & encased duct banks | 25 | 4% | 50 | 2%
| 42 | Cable Chambers |  |  | 50 | 60 | 80
S | 43 | Remote SCADA |  |  | 15 | 20 | 30
Table F-2 from Kinetrics Report1
|  | Asset Details |  |  | Useful Life Range |  |  | USoA Account Number | USoA Account Description | Current |  | Proposed
| # | Category¦ Component ¦ Type | [7 empty] | Years | Rate | Years | Rate
| 1 | Office Equipment |  |  | 5-15 |  |  | 1915 | Office Furniture & Equipment | 10 | 10% | 10 | 10%
| 2 | Vehicles | Trucks & Buckets |  | 5-15 |  |  | 1930 | Transportation Equipment - Heavy Vehicles | 8 | 12.5% | 15 | 6.667%
|  |  | Trailers |  | 5-20 |  |  | 1931 | Transportation Equipment- Light Vehicles | 8 | 12.5% | 8 | 12.5%
[8 empty] | 1932 | Transportation Equipment- Underground/Dump Trucks | 8 |  | 10
|  |  | Vans |  | 5-10 |  |  | 1930 | Transportation Equipment | 8 | 12.5% | 0
| 3 | Administrative Buildings |  |  | 50-75 |  |  | 1908 | Buildings & Fixtures | 50 | 2% | 50 | 2%
| 4 | Leasehold Improvements |  |  | Lease dependent
| 5 | Station Buildings | Station Buildings |  | 50-75
|  |  | Parking |  | 25-30
|  |  | Fence |  | 25-60
|  |  | Roof |  | 20-30
| 6 | Computer Equipment | Hardware |  | 3-5 |  |  | 1920 | Computer equipment - hardware | 5 | 20% | 5 | 20%
|  |  | Software |  | 2-5 |  |  | 1925 | Computer equipment - software | 5 | 20% | 5 | 20%
| 7 | Equipment | Power Operated |  | 5-10
|  |  | Stores |  | 5-10
|  |  | Tools, Shop, Garage Equipment |  | 5-10 |  |  | 1940 | Tool, shop & garage equipment | 10 | 10% | 10 | 10%
|  |  | Measurement & Testing Equipment |  | 5-10
| 8 | Communication | Towers |  | 60-70
|  |  | Wireless |  | 2-10 |  |  | 1955 | Communication equipment | 10 | 10% | 10 | 10%
| 9 | Residential Energy Meters |  |  | 25-35 |  |  | 1860 | Meters | 25 | 4% | 0
| 10 | Industrial/Commercial Energy Meters |  |  | 25-35 |  |  | 1862 | Meters- Industrial/ Commercial | 25 | 4% | 15 | 6.667%
| 11 | Wholesale Energy Meters |  |  | 15-30 |  |  | 1863 | Meters- Wholesale | 25 | 4% | 15 | 6.667%
| 12 | Current & Potential Transformer (CT & PT) |  |  | 35-50 |  |  | 1864 | Meters- CT's & PT's | 25 | 4% | 40 | 2.5%
| 13 | Smart Meters |  |  | 5-15 |  |  | 1861 | Residential SM (including repeaters & data collectors) | 25 | 4% | 10 | 10%
| 14 | Repeaters - Smart Metering |  |  | 10-15
| 15 | Data Collectors - Smart Metering |  |  | 15-20
* TS & MS = Transformer and Municipal Stations UG = Underground Systems S = Monitoring and Control Systems
Note 1: | Tables F-1 and F-2 above are to be used as a reference in order to complete columns J, K, L and N.
See pages 17-19 of Kinetrics Report