## Sheet1
North Bay Hydro
Asset Condition Assessment Summary
2-SEC-28
Asset | Population * if two numbers shown, first number represents overall Health Index by station for that asset type, number in brackets represents total number of units with that Health Index | Condition * if two numbers shown, first number represents overall Health Index by station for that asset type, number in brackets represents total number of units with that Health Index | [5 empty] | Number of Units Replaced | [5 empty] | Number of Units Planned for Replacement
|  | Very Good | Good | Fair | Poor | Very Poor | N/A | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 Forecast | 2016 | 2017 | 2018 | 2019 | 2020
Substation Transformers | 20 | 4 | 8 | 5 | 3 | 0 |  | 0 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | 0
Substation Circuit Breakers and Reclosers | 16 (54) | 6 (18) | 7 (26) | 2 (7) | 1 (3) | 0 |  | 0 | 3 | 1 | 6 | 0 | 4 | 0 | 4 | 1 | 1
Substation Protection and Control Relays | 16 (54) | 6 (18) | 7 (26) | 2 (7) | 0 | 0 | 1 | 0 | 3 | 0 | 6 | 0 | 4 | 0 | 4 | 1 | 1
Substation Ground Grids | 16 | 5 | 3 | 0 | 8 | 0 |  | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 1
Wood Poles (Entire Population) | 7176 | 2570 | 2206 | 1603 | 420 | 377 |  | 252 | 112 | 135 | 196 | 203 | 200 | 200 | 200 | 200 | 200
Overhead Primary Conductor* | 398861 | 69099 | 98043 | 108011 | 61854 | 61854
Overhead Primary Conductor - 4.16kV 1-ph | 10413 | 3471 | 3468 | 1258 | 1108 | 1108
Overhead Primary Conductor - 4.16kV 3-ph | 30922 | 9702 | 9931 | 5149 | 3070 | 3070
Overhead Primary Conductor - 12.47kV 1-ph | 151541 | 21432 | 34376 | 42789 | 26472 | 26472
Overhead Primary Conductor - 12.47kV 3-ph | 205985 | 34494 | 50268 | 58815 | 31204 | 31204
Underground Primary Conductor* | 110382 | 6347 | 7299 | 73901 | 9141 | 13694 | [7 empty] | 3844 | 4228 | 4228 | 3995
Underground Primary Conductor - 4.16kV 1-ph | 2648 | 0 | 0 | 0 | 2648 | 0
Underground Primary Conductor - 4.16kV 3-ph | 5376 | 0 | 0 | 247 | 4882 | 247
Underground Primary Conductor - 12.47kV 1-ph | 88371 | 6153 | 6030 | 64604 | 826 | 10758
Underground Primary Conductor - 12.47kV 3-ph | 13987 | 194 | 1269 | 9050 | 785 | 2689
Underground Low Voltage Cables | N/A | N/A | N/A | N/A | N/A | N/A | [7 empty] | 2438 | 1560
3-Phase Pole Mounted Switches* | 605 | 360 | 95 | 13 | 127 | 10
Mid-Span Opener | 10 | 6 | 0 | 0 | 4 | 0
Load Break Switches | 91 | 55 | 18 | 0 | 17 | 1
Blade | 90 | 43 | 16 | 0 | 30 | 1
Fused | 414 | 256 | 61 | 13 | 76 | 8
Distribution Transformers* | 3147 | 405 | 1788 | 689 | 152 | 113
* Further breakdown as per Exhibit 2 Appendix B 2013 Asset Condition Assessment - Expand Table as required
NBHDL Notes:
1) Replacements in all overhead conductor categories and 3 phase pole mounted switch categories have not been tracked, nor planned and therefore data is not available. These assets are renewed at the pace of the wood pole replacements, as it is much more efficient to handle construction in this manner. Outside of the pace of wood pole replacements these items are replaced when failed, or when they present imminent danger.
2) Replacements in the underground primary conductor are not available historically, however there has been very minimal replacement to date. For the forecast year and forward, replacement amounts are only available in total. They have not been broken down by subgroup.
3) Underground low voltage cables are not tracked or planned, but a section on them was included in the ACA due to specific knowledge of a problem area in the NBHDL service territory that requires attention. The numbers provided are based on the proposed projects to rectify the problem and will be complete in 2016
4) Distribution Transformers are run to failure and therefore replacements are not tracked or planned
5) All conductor quantities are in metres (m)