## TRC - System
System Measures
Facility Size Category | Measure | Measure Life (Years) | Individual Measure % Savings | Baseline Energy Consumption (GJ) | Baseline Gas Consumption (m3) | Baseline Technology Capital Cost | Measure Capital Cost (Full) | Installation / Engineering Cost (Full) | Incremental Annual O&M Cost | Now/ EOL | Annual Gas Savings (GJ) | Annual Gas Savings (m3) | Net Measure TRC | Simple Payback Period (Yrs) | B/C Ratio
Medium | Integrated control system | 10 | 8% | 1500000 | 39798355.0013 | N/A | 165000 | 13200 | N/A | Now | 120000 | 3183868.4001 | 7786043.2212 | 0.13626 | 44.6927
| Sub-metering | 15 | 5% | 1500000 | 39798355.0013 | N/A | 330000 | 33000 | 3300 | Now | 75000 | 1989917.7501 | 5939892.4567 | 0.44995 | 16.3051

## TRC - Boiler
Boiler, Steam & Hot Water Systems
System / Technology Size Category | Measure | Measure Life (Years) | Individual Measure % Savings | Baseline Energy Consumption (GJ) | Baseline Gas Consumption (m3) | Baseline Technology Capital Cost | Measure Capital Cost (Full) | Installation / Engineering Cost (Full) | Incremental Annual O&M Cost | Now/ EOL | Annual Gas Savings (GJ) | Annual Gas Savings (m3) | Net Measure TRC | Simple Payback Period (Yrs) | B/C Ratio
Small (200 BHP) | Economizer | 20 | 4% | 30987.0439 | 822155.5824 | N/A | 27000 | 3000 | 1000 | Now | 1239.4818 | 32886.2233 | 81164.6002 | 2.4783 | 3.1074
| Blowdown heat recovery | 20 | 2% | 30987.0439 | 822155.5824 | N/A | 23000 | 2000 | 1000 | Now | 619.7409 | 16443.1116 | 26325.5183 | 4.5184 | 1.7855
| Boiler combustion air preheat | 15 | 5% | 30987.0439 | 822155.5824 | N/A | 50000 | 10000 | 2000 | Now | 1549.3522 | 41107.7791 | 55511.6957 | 4.1651 | 1.7381
| Process heat recovery to preheat makeup water | 20 | 6% | 30987.0439 | 822155.5824 | N/A | 70000 | 8000 | 1500 | Now | 1859.2226 | 49329.3349 | 88746.9004 | 4.2371 | 1.9777
| Condensing boiler | 20 | 10% | 30987.0439 | 822155.5824 | 80000 | 120000 | 20000 | 1000 | EOL | 3098.7044 | 82215.5582 | 250681.8462 | 1.8614 | 6.1673
| Direct contact hot water heaters | 20 | 10% | 30987.0439 | 822155.5824 | 80000 | 75000 | 13000 | -3000 | EOL | 3098.7044 | 82215.5582 | 329736.1011 | 0.13598 | N/A
| Boiler right sizing and load management | 20 | 10% | 30987.0439 | 822155.5824 | 80000 | 70000 | 13000 | -3000 | EOL | 3098.7044 | 82215.5582 | 334736.1011 | 0 | N/A
| High efficiency burners | 20 | 5% | 30987.0439 | 822155.5824 | N/A | 48000 | 6000 | 0 | Now | 1549.3522 | 41107.7791 | 95597.705 | 3.198 | 2.7703
| Insulation | 15 | 5% | 30987.0439 | 822155.5824 | N/A | 20000 | 1500 | 150 | Now | 1549.3522 | 41107.7791 | 108082.9427 | 1.2937 | 5.7738
| Advanced boiler controls | 15 | 3% | 30987.0439 | 822155.5824 | N/A | 40000 | 1200 | 150 | Now | 929.6113 | 24664.6675 | 36093.4009 | 4.1427 | 1.8524
| Blowdown control | 20 | 1% | 30987.0439 | 822155.5824 | N/A | 35000 | 3500 | 600 | Now | 309.8704 | 8221.5558 | -13688.5972 | 14.0794 | 0.6861
| Boiler water treatment | 10 | 1% | 30987.0439 | 822155.5824 | N/A | 10000 | 2000 | 500 | Now | 309.8704 | 8221.5558 | 5493.4126 | 4.3446 | 1.3645
| Boiler maintenance | 5 | 5% | 30987.0439 | 822155.5824 | N/A | 0 | 0 | 8000 | Now | 1549.3522 | 41107.7791 | 31488.878 | 0.90034 | 2.0383
| Minimize deaerator vent losses | 20 | 2% | 30987.0439 | 822155.5824 | N/A | 35000 | 3500 | 600 | Now | 619.7409 | 16443.1116 | 16230.9438 | 6.3534 | 1.3722
| Condensate return | 20 | 2% | 30987.0439 | 822155.5824 | N/A | 40000 | 8000 | 700 | Now | 619.7409 | 16443.1116 | 5879.5874 | 8.044 | 1.109
| Steam trap survey and repair | 3 | 4% | 30987.0439 | 822155.5824 | N/A | 20000 | 1000 | 0 | Now | 1239.4818 | 32886.2233 | 11627.8742 | 1.5546 | 1.5537
| Instantaneous Steam Generation | 15 | 15% | 30987.0439 | 822155.5824 | 80000 | 120000 | 20000 | 1000 | EOL | 4648.0566 | 123323.3374 | 344565.4845 | 1.2284 | 8.2378
Medium (450 BHP) | Economizer | 20 | 4% | 78435.9549 | 2081081.3181 | N/A | 55000 | 4400 | 1000 | Now | 3137.4382 | 83243.2527 | 235021.7888 | 1.8196 | 4.4606
| Blowdown heat recovery | 20 | 2% | 78435.9549 | 2081081.3181 | N/A | 50000 | 4000 | 1000 | Now | 1568.7191 | 41621.6264 | 88954.1126 | 3.4169 | 2.423
| Boiler combustion air preheat | 15 | 5% | 78435.9549 | 2081081.3181 | N/A | 140000 | 21000 | 5000 | Now | 3921.7977 | 104054.0659 | 131864.3596 | 4.3983 | 1.6625
| Process heat recovery to preheat makeup water | 20 | 6% | 78435.9549 | 2081081.3181 | N/A | 130000 | 15000 | 1800 | Now | 4706.1573 | 124864.8791 | 294078.6141 | 2.9663 | 2.8343
| Condensing boiler | 20 | 10% | 78435.9549 | 2081081.3181 | 135000 | 180000 | 15000 | 2800 | EOL | 7843.5955 | 208108.1318 | 688500.403 | 0.75953 | 11.0018
| Direct contact hot water heaters | 20 | 10% | 78435.9549 | 2081081.3181 | 135000 | 130000 | 20000 | -5000 | EOL | 7843.5955 | 208108.1318 | 804906.2 | 0.11052 | N/A
| Boiler right sizing and load management | 20 | 10% | 78435.9549 | 2081081.3181 | 135000 | 125000 | 20000 | -5000 | EOL | 7843.5955 | 208108.1318 | 809906.2 | 0.055259 | N/A
| High efficiency burners | 20 | 5% | 78435.9549 | 2081081.3181 | N/A | 90000 | 10000 | 0 | Now | 3921.7977 | 104054.0659 | 278669.1907 | 2.3396 | 3.7867
| Insulation | 15 | 5% | 78435.9549 | 2081081.3181 | N/A | 35000 | 2800 | 1000 | Now | 3921.7977 | 104054.0659 | 285488.6776 | 0.92953 | 7.2875
| Advanced boiler controls | 15 | 3% | 78435.9549 | 2081081.3181 | N/A | 75000 | 6500 | 800 | Now | 2353.0786 | 62432.4395 | 110951.9907 | 3.3125 | 2.2668
| Blowdown control | 20 | 1% | 78435.9549 | 2081081.3181 | N/A | 60000 | 6000 | 1000 | Now | 784.3595 | 20810.8132 | 1220.2744 | 8.8762 | 1.0164
| Boiler water treatment | 10 | 1% | 78435.9549 | 2081081.3181 | N/A | 20000 | 3500 | 1000 | Now | 784.3595 | 20810.8132 | 22412.3514 | 3.2458 | 1.756
| Boiler maintenance | 5 | 5% | 78435.9549 | 2081081.3181 | N/A | 0 | 0 | 13000 | Now | 3921.7977 | 104054.0659 | 107189.4266 | 0.4371 | 3.1751
| Minimize deaerator vent losses | 20 | 2% | 78435.9549 | 2081081.3181 | N/A | 60000 | 6000 | 1000 | Now | 1568.7191 | 41621.6264 | 76954.1126 | 4.1624 | 2.0328
| Condensate return | 20 | 2% | 78435.9549 | 2081081.3181 | N/A | 80000 | 15000 | 1200 | Now | 1568.7191 | 41621.6264 | 46251.3998 | 6.0516 | 1.4396
| Steam trap survey and repair | 3 | 4% | 78435.9549 | 2081081.3181 | N/A | 35000 | 1500 | 0 | Now | 3137.4382 | 83243.2527 | 46089.3066 | 1.0675 | 2.2627
| Instantaneous Steam Generation | 15 | 15% | 78435.9549 | 2081081.3181 | 135000 | 180000 | 28000 | 1500 | EOL | 11765.3932 | 312162.1977 | 936275.1521 | 0.58789 | 17.5979
Large (3,000 BHP) | Economizer | 20 | 4% | 813409.9024 | 21581584.0392 | N/A | 350000 | 40000 | 2000 | Now | 32536.3961 | 863263.3616 | 2734524.6768 | 1.1118 | 7.7183
| Blowdown heat recovery | 20 | 2% | 813409.9024 | 21581584.0392 | N/A | 200000 | 25000 | 5000 | Now | 16268.198 | 431631.6808 | 1303208.0835 | 1.3349 | 5.8706
| Boiler combustion air preheat | 15 | 5% | 813409.9024 | 21581584.0392 | N/A | 500000 | 60000 | 7000 | Now | 40670.4951 | 1079079.202 | 2818258.6285 | 1.2997 | 5.5957
| Process heat recovery to preheat makeup water | 20 | 6% | 813409.9024 | 21581584.0392 | N/A | 400000 | 50000 | 5000 | Now | 48804.5941 | 1294895.0424 | 4219759.8877 | 0.86355 | 9.5669
| Boiler right sizing and load management | 20 | 10% | 813409.9024 | 21581584.0392 | 2800000 | 2700000 | 150000 | -10000 | EOL | 81340.9902 | 2158158.4039 | 8039015.1477 | 0.044618 | N/A
| High efficiency burners | 20 | 5% | 813409.9024 | 21581584.0392 | N/A | 400000 | 60000 | 0 | Now | 40670.4951 | 1079079.202 | 3466939.7552 | 1.0378 | 8.5368
| Insulation | 15 | 5% | 813409.9024 | 21581584.0392 | N/A | 150000 | 30000 | 1500 | Now | 40670.4951 | 1079079.202 | 3240092.0658 | 0.41087 | 17.9276
| Advanced boiler controls | 15 | 3% | 813409.9024 | 21581584.0392 | N/A | 200000 | 40000 | 3000 | Now | 24402.2971 | 647447.5212 | 1796082.4725 | 0.92414 | 7.8339
| Blowdown control | 20 | 1% | 813409.9024 | 21581584.0392 | N/A | 120000 | 12000 | 2000 | Now | 8134.099 | 215815.8404 | 636360.8236 | 1.5465 | 5.2701
| Boiler water treatment | 10 | 1% | 813409.9024 | 21581584.0392 | N/A | 50000 | 8000 | 3000 | Now | 8134.099 | 215815.8404 | 463415.8238 | 0.71221 | 7.063
| Boiler maintenance | 5 | 5% | 813409.9024 | 21581584.0392 | N/A | 0 | 0 | 30000 | Now | 40670.4951 | 1079079.202 | 1508924.6672 | 0.072596 | 14.2684
| Minimize deaerator vent losses | 20 | 2% | 813409.9024 | 21581584.0392 | N/A | 150000 | 15000 | 2000 | Now | 16268.198 | 431631.6808 | 1388748.7747 | 0.95266 | 8.6294
| Condensate return | 20 | 2% | 813409.9024 | 21581584.0392 | N/A | 350000 | 80000 | 10000 | Now | 16268.198 | 431631.6808 | 1055640.2649 | 2.63 | 3.0492
| Steam trap survey and repair | 3 | 4% | 813409.9024 | 21581584.0392 | N/A | 200000 | 30000 | 0 | Now | 32536.3961 | 863263.3616 | 626481.698 | 0.64862 | 3.7238

## TRC - Process Direct Heat
Process Direct Heat (Furnaces / Kilns / Ovens / Dryers)
System / Technology Size Category | Measure | Measure Life (Years) | Individual Measure % Savings | Baseline Energy Consumption (GJ) | Baseline Gas Consumption (m3) | Baseline Technology Capital Cost | Measure Capital Cost (Full) | Installation / Engineering Cost (Full) | Incremental Annual O&M Cost | Now/ EOL | Annual Gas Savings (GJ) | Annual Gas Savings (m3) | Net Measure TRC | Simple Payback Period (Yrs) | B/C Ratio
Small (2 MMBTU) | Exhaust gas heat recovery | 15 | 15% | 9472.464 | 251325.6567 | N/A | 30000 | 5000 | 1000 | Now | 1420.8696 | 37698.8485 | 77277.2832 | 2.4853 | 2.8138
| High efficiency burners and burner controls | 20 | 10% | 9472.464 | 251325.6567 | N/A | 15000 | 2000 | 0 | Now | 947.2464 | 25132.5657 | 74461.3785 | 1.6467 | 5.3801
| Insulation | 15 | 5% | 9472.464 | 251325.6567 | N/A | 8000 | 500 | 300 | Now | 473.6232 | 12566.2828 | 29179.297 | 1.81 | 3.7063
| High efficiency ovens | 20 | 12% | 9472.464 | 251325.6567 | N/A | 18000 | 2000 | 0 | Now | 1136.6957 | 30159.0788 | 89753.6541 | 1.6144 | 5.4877
| High efficiency dryers | 20 | 12% | 9472.464 | 251325.6567 | N/A | 18000 | 2000 | 0 | Now | 1136.6957 | 30159.0788 | 89753.6541 | 1.6144 | 5.4877
| Air curtains | 20 | 15% | 9472.464 | 251325.6567 | N/A | 15000 | 2000 | 1000 | Now | 1420.8696 | 37698.8485 | 111678.504 | 1.2426 | 5.3772
Medium (20 MMBTU) | Exhaust gas heat recovery | 15 | 15% | 106565.22 | 2827413.6376 | N/A | 120000 | 35000 | 3000 | Now | 15984.783 | 424112.0456 | 1170869.5914 | 0.92285 | 7.5846
| High efficiency burners and burner controls | 20 | 10% | 106565.22 | 2827413.6376 | N/A | 60000 | 4000 | 0 | Now | 10656.522 | 282741.3638 | 964940.5076 | 0.55106 | 16.0772
| Insulation | 15 | 5% | 106565.22 | 2827413.6376 | N/A | 40000 | 3000 | 1000 | Now | 5328.261 | 141370.6819 | 398956.5305 | 0.77099 | 8.8836
| Advanced heating and process controls | 15 | 10% | 106565.22 | 2827413.6376 | N/A | 100000 | 25000 | 3000 | Now | 10656.522 | 282741.3638 | 751306.9814 | 1.1313 | 6.0826
| High efficiency ovens | 20 | 12% | 106565.22 | 2827413.6376 | N/A | 100000 | 15000 | 0 | Now | 12787.8264 | 339289.6365 | 1119728.6091 | 0.82516 | 10.7368
| High efficiency dryers | 20 | 12% | 106565.22 | 2827413.6376 | N/A | 100000 | 15000 | 0 | Now | 12787.8264 | 339289.6365 | 1119728.6091 | 0.82516 | 10.7368
| High Efficiency kilns | 20 | 14% | 106565.22 | 2827413.6376 | N/A | 100000 | 15000 | 0 | Now | 14919.1308 | 395837.9093 | 1325516.7106 | 0.70728 | 12.5262
| High Efficiency Furnaces | 20 | 14% | 106565.22 | 2827413.6376 | N/A | 100000 | 15000 | 0 | Now | 14919.1308 | 395837.9093 | 1325516.7106 | 0.70728 | 12.5262
| Air curtains | 20 | 15% | 106565.22 | 2827413.6376 | N/A | 80000 | 18000 | 1000 | Now | 15984.783 | 424112.0456 | 1436897.1977 | 0.57156 | 14.4903
Large (100 MMBTU) | Exhaust gas heat recovery | 15 | 15% | 828840.6 | 21990994.9589 | N/A | 900000 | 180000 | 10000 | Now | 124326.09 | 3298649.2438 | 9333733.4375 | 0.81043 | 9.0737
| High efficiency burners and burner controls | 20 | 10% | 828840.6 | 21990994.9589 | N/A | 500000 | 80000 | 5000 | Now | 82884.06 | 2199099.4959 | 7380302.7959 | 0.65122 | 12.8546
| Insulation | 15 | 5% | 828840.6 | 21990994.9589 | N/A | 250000 | 30000 | 2000 | Now | 41442.03 | 1099549.7479 | 3201385.9185 | 0.62715 | 11.8444
| Advanced heating and process controls | 15 | 10% | 828840.6 | 21990994.9589 | N/A | 500000 | 6500 | 8000 | Now | 82884.06 | 2199099.4959 | 6425847.519 | 0.57466 | 12.3261
| High efficiency ovens | 20 | 12% | 828840.6 | 21990994.9589 | N/A | 1000000 | 100000 | 0 | Now | 99460.872 | 2638919.3951 | 8503444.7374 | 1.0148 | 8.7304
| High efficiency dryers | 20 | 12% | 828840.6 | 21990994.9589 | N/A | 1000000 | 100000 | 0 | Now | 99460.872 | 2638919.3951 | 8503444.7374 | 1.0148 | 8.7304
| High Efficiency kilns | 20 | 14% | 828840.6 | 21990994.9589 | N/A | 1000000 | 100000 | 0 | Now | 116037.684 | 3078739.2942 | 10104018.8603 | 0.86982 | 10.1855
| High Efficiency Furnaces | 20 | 14% | 828840.6 | 21990994.9589 | N/A | 1000000 | 100000 | 0 | Now | 116037.684 | 3078739.2942 | 10104018.8603 | 0.86982 | 10.1855

## TRC - Other Process
Other Process
System / Technology Size Category | Measure | Measure Life (Years) | Individual Measure % Savings | Baseline Energy Consumption (GJ) | Baseline Gas Consumption (m3) | Baseline Technology Capital Cost | Measure Capital Cost (Full) | Installation / Engineering Cost (Full) | Incremental Annual O&M Cost | Now/ EOL | Annual Gas Savings (GJ) | Annual Gas Savings (m3) | Net Measure TRC | Simple Payback Period (Yrs) | B/C Ratio
Medium (20 MMTBU) | Pollution control measures | 20 | 10% | 106565.22 | 2827413.6376 | N/A | 80000 | 6400 | 20000 | Now | 10656.522 | 282741.3638 | 772269.2332 | 1.1067 | 4.0088
| Hydrogen Atmospheres for Steel Batch Coil Annealing | 15 | 30% | 106565.22 | 2827413.6376 | N/A | 250000 | 60000 | 3000 | Now | 31969.566 | 848224.0913 | 2364557.4213 | 0.90615 | 8.1047
| Process Heat Recovery | 15 | 15% | 106565.22 | 2827413.6376 | N/A | 300000 | 60000 | 10000 | Now | 15984.783 | 424112.0456 | 912627.0348 | 2.2532 | 3.0929
Large (100 MMBTU) | Pollution control measures | 20 | 10% | 828840.6 | 21990994.9589 | N/A | 1000000 | 80000 | 125000 | Now | 82884.06 | 2199099.4959 | 5858675.1496 | 1.5482 | 3.7323
| Hydrogen Atmospheres for Steel Batch Coil Annealing | 15 | 30% | 828840.6 | 21990994.9589 | N/A | 2000000 | 160000 | 10000 | Now | 248652.18 | 6597298.4877 | 18743527.6701 | 0.80373 | 9.3824
| Process Heat Recovery | 15 | 15% | 828840.6 | 21990994.9589 | N/A | 1000000 | 150000 | 25000 | Now | 124326.09 | 3298649.2438 | 9149642.2449 | 0.88348 | 7.8273

## TRC - HVAC
Heating, Ventilation & Air Conditioning (HVAC)
System / Technology Size Category | Measure | Measure Life (Years) | Individual Measure % Savings | Baseline Energy Consumption (GJ) | Baseline Gas Consumption (m3) | Baseline Technology Capital Cost | Measure Capital Cost (Full) | Installation / Engineering Cost (Full) | Incremental Annual O&M Cost | Now/ EOL | Annual Gas Savings (GJ) | Annual Gas Savings (m3) | Net Measure TRC | Simple Payback Period (Yrs) | B/C Ratio
Small (0.8 MMBTU) | Radiant heaters | 20 | 25% | 3250.3553 | 86239.1959 | N/A | 30000 | 4000 | 1000 | Now | 812.5888 | 21559.799 | 35945.9521 | 4.4552 | 1.8455
| Automated temperature control | 20 | 15% | 3250.3553 | 86239.1959 | N/A | 12000 | 960 | 500 | Now | 487.5533 | 12935.8794 | 29858.9276 | 2.7963 | 2.7343
| Solar Walls | 20 | 15% | 3250.3553 | 86239.1959 | N/A | 100000 | 8000 | 0 | Now | 487.5533 | 12935.8794 | -60924.2905 | 20.3253 | 0.43589
| Ventilation & Heat Recovery Optimization | 20 | 17% | 3250.3553 | 86239.1959 | N/A | 25000 | 1600 | 200 | Now | 552.5604 | 14660.6633 | 25049.758 | 4.6032 | 1.8851
| Warehouse loading dock seals | 10 | 5% | 3250.3553 | 86239.1959 | N/A | 10000 | 5000 | 500 | Now | 162.5178 | 4311.9598 | -7286.1918 | 12.1933 | 0.59683
| Air curtains | 15 | 5% | 3250.3553 | 86239.1959 | N/A | 13000 | 2000 | 500 | Now | 162.5178 | 4311.9598 | -5090.8904 | 12.1933 | 0.72925
| Air compressor heat recovery | 20 | 15% | 3250.3553 | 86239.1959 | N/A | 18000 | 2500 | 500 | Now | 487.5533 | 12935.8794 | 22318.9276 | 4.3627 | 1.9015
| Destratification fans | 20 | 8% | 3250.3553 | 86239.1959 | N/A | 10000 | 800 | 0 | Now | 260.0284 | 6899.1357 | 14307.0451 | 3.811 | 2.3247
Medium (2 MMBTU) | Radiant heaters | 20 | 25% | 8125.8882 | 215597.9898 | N/A | 70000 | 10000 | 1000 | Now | 2031.4721 | 53899.4974 | 107635.2259 | 3.8316 | 2.216
| Automated temperature control | 20 | 15% | 8125.8882 | 215597.9898 | N/A | 29000 | 2320 | 500 | Now | 1218.8832 | 32339.6985 | 82112.4919 | 2.4891 | 3.308
| Solar Walls | 20 | 15% | 8125.8882 | 215597.9898 | N/A | 175000 | 14000 | 0 | Now | 1218.8832 | 32339.6985 | -71310.7263 | 14.2277 | 0.62269
| Ventilation & Heat Recovery Optimization | 20 | 17% | 8125.8882 | 215597.9898 | N/A | 70000 | 12000 | 1000 | Now | 1381.401 | 36651.6583 | 42867.6132 | 5.9053 | 1.4736
| Warehouse loading dock seals | 10 | 5% | 8125.8882 | 215597.9898 | N/A | 20000 | 4000 | 500 | Now | 406.2944 | 10779.8995 | -107.0543 | 6.2373 | 0.99605
| Air curtains | 15 | 5% | 8125.8882 | 215597.9898 | N/A | 18000 | 1440 | 500 | Now | 406.2944 | 10779.8995 | 11037.3336 | 5.0764 | 1.4749
| Air compressor heat recovery | 20 | 15% | 8125.8882 | 215597.9898 | N/A | 45000 | 3500 | 1000 | Now | 1218.8832 | 32339.6985 | 60675.71 | 4.0296 | 2.0642
| Destratification fans | 20 | 8% | 8125.8882 | 215597.9898 | N/A | 25000 | 2000 | 500 | Now | 650.0711 | 17247.8392 | 31510.8308 | 4.1763 | 2.0081
Large (5 MMBTU) | Radiant heaters | 20 | 25% | 20314.7206 | 538994.9745 | N/A | 200000 | 20000 | 5000 | Now | 5078.6801 | 134748.7436 | 227804.1553 | 4.4687 | 1.8676
| Automated temperature control | 20 | 15% | 20314.7206 | 538994.9745 | N/A | 70000 | 5600 | 1000 | Now | 3047.2081 | 80849.2462 | 210109.6206 | 2.3782 | 3.4979
| Solar Walls | 20 | 15% | 20314.7206 | 538994.9745 | N/A | 250000 | 20000 | 0 | Now | 3047.2081 | 80849.2462 | 24223.1844 | 8.1301 | 1.0897
| Ventilation & Heat Recovery Optimization | 20 | 17% | 20314.7206 | 538994.9745 | N/A | 150000 | 15000 | 1000 | Now | 3453.5025 | 91629.1457 | 159939.3786 | 4.5308 | 1.9218
| Warehouse loading dock seals | 10 | 5% | 20314.7206 | 538994.9745 | N/A | 40000 | 8000 | 1000 | Now | 1015.736 | 26949.7487 | 13268.5061 | 4.866 | 1.2451
| Air curtains | 15 | 5% | 20314.7206 | 538994.9745 | N/A | 40000 | 7000 | 1000 | Now | 1015.736 | 26949.7487 | 31094.8538 | 4.7667 | 1.5694
| Air compressor heat recovery | 20 | 15% | 20314.7206 | 538994.9745 | N/A | 100000 | 10000 | 2000 | Now | 3047.2081 | 80849.2462 | 167196.0569 | 3.5886 | 2.3162
| Destratification fans | 20 | 8% | 20314.7206 | 538994.9745 | N/A | 60000 | 4800 | 2000 | Now | 1625.1776 | 43119.598 | 75091.9042 | 4.2515 | 1.9177