## Energy Costs & GHG Adder
Customer Energy Prices
| Residential |  |  | Commercial |  |  | Industrial
| Nat. Gas ($/m3) | Electricity ($/kWh) | Water ($/1000L) | Nat. Gas ($/m3) | Electricity ($/kWh) | Water ($/1000L) | Nat. Gas ($/m3) | Electricity ($/kWh) | Water ($/1000L)
Northern Service Region | 0.4 | 0.1 | 1.75 | 0.466 | 0.10323 | 2.25 | 0.4 | 0.1 | 1.75
Southern Service Region | 0.466 | 0.10323 | 2.25 | 0.441 | 0.11124 | 3.05 | 0.4 | 0.1 | 1.75
Natural gas prices are estimates based on Union rates (as of July, 2008) in each service region and average NG consumption levels. Rate excludes monthly charge (see http://www.uniongas.com/business/rates/summary/index.asp)
Customer electricity prices are based on those charged by London Hydro (Southern Region) and North Bay Hydro (Northern Region) according to their websites as of July 2008. Delivery charge is estimated based on a monthly average peak demand of 250 kW, and monthly consumption of 35,000 kWh. (See http://www.londonhydro.com/lh_website/commercial/erates.jsp and http://www.northbayhydro.on.ca/billing.asp)
Water prices are based in resource rates in the cities of London and North Bay. (See www.londonhydro.com/lh_website/commercial/rates.jsp and www.city.north-bay.on.ca/common/pdf/waterrates2008.pdf)
GHG Adder
| Residential |  |  | Commercial |  |  | Industrial
| Nat. Gas (m3) | Electricity (kWh) | Water (1000L) | Nat. Gas (m3) | Electricity (kWh) | Water (1000L) | Nat. Gas (m3) | Electricity (kWh) | Water (1000L)
GHG Cost, 2008-2012 ($/tonne CO2e) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
GHG Cost, 2013+ ($/tonne CO2e) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Emissions Coefficient (tonnes CO2e/unit) | 0.001925 | 0.000278 |  | 0.001925 | 0.000278 |  | 0.001925 | 0.000278
GHG Adder, 2008-12 ($/unit) | 0.028875 | 0.00417 | 0 | 0.028875 | 0.00417 | 0 | 0.028875 | 0.00417 | 0
GHG Adder, 2013+ ($/unit) | 0.0385 | 0.00556 | 0 | 0.0385 | 0.00556 | 0 | 0.0385 | 0.00556 | 0
- Based on emission factors and Global Warming Potentials (GWPs) presented in Environment Canada; National Inventory Report (1990-2005): Greenhouse Gas Sources and Sinks in Canada, pgs. 23 and 583, April 2007.
- Electricity emissions coefficient based on Ontario emission factors presented in Environment Canada; National Inventory Report (1990-2005): Greenhouse Gas Sources and Sinks in Canada, pg. 521, April 2007.
Other Economic Parameters
Discount Rate | 10%
TRC Cutoff | 0
London elec | 0.11124
North Bay elec | 0.10323

## Avoided Costs (hidden)
2008 AVOIDED COSTS
|  | INFLATION FACTOR |  | 1.9%
|  | DISCOUNT RATE |  | 10%
| NATURAL GAS ENERGY SAVINGS RATES | [6 empty] | WATER AND ELECTRICITY SAVINGS RATES
|  | Residential/Commercial |  |  |  | Industrial |  |  | Residential/Commercial/Industrial
|  | Baseload |  | Weather Sensitive |  | Baseload |  |  | Water Rates |  | Electricity Rates
| Year | Rates | NPV | Rates | NPV | Rates | NPV | Year | Rates | NPV | Rates | NPV
| 1 | 0.3701 | 0.3701 | 0.37255 | 0.37255 | 0.34728 | 0.34728 | 1 | 1.685 | 1.685 | 0.07615 | 0.07615
| 2 | 0.35301 | 0.69102 | 0.35935 | 0.69923 | 0.3312 | 0.64837 | 2 | 1.7171 | 3.246 | 0.077597 | 0.14669
| 3 | 0.33622 | 0.96889 | 0.33343 | 0.97479 | 0.31816 | 0.91131 | 3 | 1.7497 | 4.692 | 0.079071 | 0.21204
| 4 | 0.34261 | 1.2263 | 0.33977 | 1.2301 | 0.32421 | 1.1549 | 4 | 1.7829 | 6.0315 | 0.080573 | 0.27258
| 5 | 0.34912 | 1.4647 | 0.34622 | 1.4665 | 0.33036 | 1.3805 | 5 | 1.8168 | 7.2724 | 0.082104 | 0.32865
| 6 | 0.35575 | 1.6856 | 0.3528 | 1.6856 | 0.33664 | 1.5896 | 6 | 1.8513 | 8.4219 | 0.083664 | 0.3806
| 7 | 0.36251 | 1.8903 | 0.3595 | 1.8885 | 0.34304 | 1.7832 | 7 | 1.8865 | 9.4868 | 0.085254 | 0.42873
| 8 | 0.3694 | 2.0798 | 0.36633 | 2.0765 | 0.34956 | 1.9626 | 8 | 1.9223 | 10.4733 | 0.086874 | 0.47331
| 9 | 0.37642 | 2.2554 | 0.37329 | 2.2507 | 0.3562 | 2.1287 | 9 | 1.9589 | 11.3871 | 0.088524 | 0.5146
| 10 | 0.38357 | 2.4181 | 0.38039 | 2.412 | 0.36297 | 2.2827 | 10 | 1.9961 | 12.2336 | 0.090206 | 0.55286
| 11 | 0.39086 | 2.5688 | 0.38761 | 2.5614 | 0.36986 | 2.4253 | 11 | 2.034 | 13.0178 | 0.09192 | 0.5883
| 12 | 0.39828 | 2.7084 | 0.39498 | 2.6999 | 0.37689 | 2.5574 | 12 | 2.0726 | 13.7443 | 0.093667 | 0.62113
| 13 | 0.40585 | 2.8377 | 0.40248 | 2.8281 | 0.38405 | 2.6797 | 13 | 2.112 | 14.4172 | 0.095446 | 0.65154
| 14 | 0.41356 | 2.9575 | 0.41013 | 2.9469 | 0.39135 | 2.7931 | 14 | 2.1522 | 15.0406 | 0.09726 | 0.67971
| 15 | 0.42142 | 3.0685 | 0.41792 | 3.057 | 0.39878 | 2.8981 | 15 | 2.193 | 15.6181 | 0.099108 | 0.70581
| 16 | 0.42943 | 3.1713 | 0.42586 | 3.1589 | 0.40636 | 2.9954 | 16 | 2.2347 | 16.1531 | 0.10099 | 0.72999
| 17 | 0.43758 | 3.2665 | 0.43395 | 3.2533 | 0.41408 | 3.0855 | 17 | 2.2772 | 16.6487 | 0.10291 | 0.75239
| 18 | 0.4459 | 3.3547 | 0.4422 | 3.3408 | 0.42195 | 3.169 | 18 | 2.3204 | 17.1078 | 0.10486 | 0.77313
| 19 | 0.45437 | 3.4364 | 0.4506 | 3.4219 | 0.42996 | 3.2463 | 19 | 2.3645 | 17.5331 | 0.10686 | 0.79235
| 20 | 0.463 | 3.5121 | 0.45916 | 3.4969 | 0.43813 | 3.318 | 20 | 2.4095 | 17.927 | 0.10889 | 0.81016
| 21 | 0.4718 | 3.5823 | 0.46789 | 3.5665 | 0.44646 | 3.3843 | 21 | 2.4552 | 18.292 | 0.11096 | 0.82665
| 22 | 0.48077 | 3.6472 | 0.47678 | 3.6309 | 0.45494 | 3.4458 | 22 | 2.5019 | 18.6301 | 0.11306 | 0.84193
| 23 | 0.4899 | 3.7074 | 0.48583 | 3.6906 | 0.46358 | 3.5028 | 23 | 2.5494 | 18.9432 | 0.11521 | 0.85608
| 24 | 0.49921 | 3.7632 | 0.49507 | 3.7459 | 0.47239 | 3.5555 | 24 | 2.5979 | 19.2334 | 0.1174 | 0.86919
| 25 | 0.50869 | 3.8148 | 0.50447 | 3.7971 | 0.48137 | 3.6044 | 25 | 2.6472 | 19.5021 | 0.11963 | 0.88134
| 26 | 0.51836 | 3.8627 | 0.51406 | 3.8446 | 0.49051 | 3.6497 | 26 | 2.6975 | 19.7511 | 0.12191 | 0.89259
| 27 | 0.52821 | 3.907 | 0.52382 | 3.8885 | 0.49983 | 3.6916 | 27 | 2.7488 | 19.9817 | 0.12422 | 0.90301
| 28 | 0.53824 | 3.948 | 0.53378 | 3.9292 | 0.50933 | 3.7304 | 28 | 2.801 | 20.1954 | 0.12658 | 0.91267
| 29 | 0.54847 | 3.9861 | 0.54392 | 3.9669 | 0.51901 | 3.7664 | 29 | 2.8542 | 20.3933 | 0.12899 | 0.92161
| 30 | 0.55889 | 4.0213 | 0.55425 | 4.0019 | 0.52887 | 3.7998 | 30 | 2.9084 | 20.5766 | 0.13144 | 0.9299

## Avoided Costs (GHG Adder)
2008 AVOIDED COSTS (WITH GHG ADDER)
|  | INFLATION FACTOR |  | 1.9%
|  | DISCOUNT RATE |  | 10%
| NATURAL GAS ENERGY SAVINGS RATES | [6 empty] | WATER AND ELECTRICITY SAVINGS RATES
|  | Residential/Commercial |  |  |  | Industrial |  |  | Residential/Commercial/Industrial
|  | Baseload |  | Weather Sensitive |  | Baseload |  |  | Water Rates |  | Electricity Rates
| Year | Rates | NPV | Rates | NPV | Rates | NPV | Year | Rates | NPV | Rates | NPV
| 1 | 0.39898 | 0.39898 | 0.40142 | 0.40142 | 0.37616 | 0.37616 | 1 | 1.685 | 1.685 | 0.08032 | 0.08032
| 2 | 0.38188 | 0.74614 | 0.38822 | 0.75436 | 0.36007 | 0.7035 | 2 | 1.7171 | 3.246 | 0.081767 | 0.15465
| 3 | 0.3651 | 1.0479 | 0.3623 | 1.0538 | 0.34703 | 0.9903 | 3 | 1.7497 | 4.692 | 0.083241 | 0.22345
| 4 | 0.37148 | 1.327 | 0.36864 | 1.3307 | 0.35308 | 1.2556 | 4 | 1.7829 | 6.0315 | 0.084743 | 0.28712
| 5 | 0.37799 | 1.5851 | 0.3751 | 1.5869 | 0.35924 | 1.5009 | 5 | 1.8168 | 7.2724 | 0.086274 | 0.34604
| 6 | 0.39425 | 1.8299 | 0.3913 | 1.8299 | 0.37514 | 1.7339 | 6 | 1.8513 | 8.4219 | 0.089224 | 0.40144
| 7 | 0.40101 | 2.0563 | 0.398 | 2.0546 | 0.38154 | 1.9492 | 7 | 1.8865 | 9.4868 | 0.090814 | 0.45271
| 8 | 0.4079 | 2.2656 | 0.40483 | 2.2623 | 0.38806 | 2.1484 | 8 | 1.9223 | 10.4733 | 0.092434 | 0.50014
| 9 | 0.41492 | 2.4592 | 0.41179 | 2.4544 | 0.3947 | 2.3325 | 9 | 1.9589 | 11.3871 | 0.094084 | 0.54403
| 10 | 0.42207 | 2.6382 | 0.41889 | 2.6321 | 0.40147 | 2.5028 | 10 | 1.9961 | 12.2336 | 0.095766 | 0.58464
| 11 | 0.42936 | 2.8037 | 0.42611 | 2.7964 | 0.40836 | 2.6602 | 11 | 2.034 | 13.0178 | 0.09748 | 0.62223
| 12 | 0.43678 | 2.9568 | 0.43348 | 2.9483 | 0.41539 | 2.8058 | 12 | 2.0726 | 13.7443 | 0.099227 | 0.65701
| 13 | 0.44435 | 3.0984 | 0.44098 | 3.0888 | 0.42255 | 2.9404 | 13 | 2.112 | 14.4172 | 0.10101 | 0.68919
| 14 | 0.45206 | 3.2293 | 0.44863 | 3.2187 | 0.42985 | 3.0649 | 14 | 2.1522 | 15.0406 | 0.10282 | 0.71897
| 15 | 0.45992 | 3.3504 | 0.45642 | 3.3389 | 0.43728 | 3.1801 | 15 | 2.193 | 15.6181 | 0.10467 | 0.74654
| 16 | 0.46793 | 3.4625 | 0.46436 | 3.4501 | 0.44486 | 3.2866 | 16 | 2.2347 | 16.1531 | 0.10655 | 0.77204
| 17 | 0.47608 | 3.5661 | 0.47245 | 3.5529 | 0.45258 | 3.3851 | 17 | 2.2772 | 16.6487 | 0.10847 | 0.79565
| 18 | 0.4844 | 3.6619 | 0.4807 | 3.648 | 0.46045 | 3.4762 | 18 | 2.3204 | 17.1078 | 0.11042 | 0.8175
| 19 | 0.49287 | 3.7506 | 0.4891 | 3.736 | 0.46846 | 3.5604 | 19 | 2.3645 | 17.5331 | 0.11242 | 0.83772
| 20 | 0.5015 | 3.8326 | 0.49766 | 3.8174 | 0.47663 | 3.6384 | 20 | 2.4095 | 17.927 | 0.11445 | 0.85643
| 21 | 0.5103 | 3.9084 | 0.50639 | 3.8926 | 0.48496 | 3.7105 | 21 | 2.4552 | 18.292 | 0.11652 | 0.87375
| 22 | 0.51927 | 3.9786 | 0.51528 | 3.9623 | 0.49344 | 3.7771 | 22 | 2.5019 | 18.6301 | 0.11862 | 0.88978
| 23 | 0.5284 | 4.0435 | 0.52433 | 4.0267 | 0.50208 | 3.8388 | 23 | 2.5494 | 18.9432 | 0.12077 | 0.90461
| 24 | 0.53771 | 4.1035 | 0.53357 | 4.0863 | 0.51089 | 3.8959 | 24 | 2.5979 | 19.2334 | 0.12296 | 0.91835
| 25 | 0.54719 | 4.1591 | 0.54297 | 4.1414 | 0.51987 | 3.9487 | 25 | 2.6472 | 19.5021 | 0.12519 | 0.93106
| 26 | 0.55686 | 4.2105 | 0.55256 | 4.1924 | 0.52901 | 3.9975 | 26 | 2.6975 | 19.7511 | 0.12747 | 0.94282
| 27 | 0.56671 | 4.258 | 0.56232 | 4.2396 | 0.53833 | 4.0427 | 27 | 2.7488 | 19.9817 | 0.12978 | 0.95371
| 28 | 0.57674 | 4.302 | 0.57228 | 4.2832 | 0.54783 | 4.0844 | 28 | 2.801 | 20.1954 | 0.13214 | 0.96379
| 29 | 0.58697 | 4.3427 | 0.58242 | 4.3236 | 0.55751 | 4.1231 | 29 | 2.8542 | 20.3933 | 0.13455 | 0.97312
| 30 | 0.59739 | 4.3804 | 0.59275 | 4.361 | 0.56737 | 4.1589 | 30 | 2.9084 | 20.5766 | 0.137 | 0.98176

## HP Glazings
High-Performance Glazings
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.361 | 0.441
Electricity ($/kWh) |  | 0.98176 | 0.11124
Water ($/1000L) |  | 20.5766 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio | Savings | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | High Performance Glazings (0.32 Btu/hr.ft2.F) - baseline building with a U value of 0.46 Btu/hr.ft2.F and a space heating EUI of 17.4 m3/m2/yr. | 17.4 | 0 | 0 | 15.66 |  |  | I | 4.3809 | 0 | 30 | 1.74 | 0 | 0 | 0.76734 | 5.7091 | 0 | 7.5881 | 0 | 0 | 3.2072 | 1.7321 | 10% | 1.8432
2 | [9 empty] | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.361 | 0.466
Electricity ($/kWh) |  | 0.98176 | 0.10323
Water ($/1000L) |  | 20.5766 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | High Performance Glazings (0.32 Btu/hr.ft2.F) - baseline building with a U value of 0.46 Btu/hr.ft2.F and a space heating EUI of 21.9 m3/m2/yr. | 21.9 | 0 | 0 | 19.71 |  |  | I | 4.3809 | 0 | 30 | 2.19 | 0 | 0 | 0.96579 | 4.536 | 0 | 9.5505 | 0 | 0 | 5.1697 | 2.1801 | 10%
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Costs based on $5 per square foot of window area based on ACEEE and translated to floor area based on WWR of 0.28
2. Savings are 10% of space heating energy based on CEEAM simulations.
3. The service life of glazing is 30 years (BC Hydro QA Standard)
4. The analysis is based on 1 m2 of floor area
Note on J15: Richard Patterson: $5/ft2 incremental. Baseline school = 28000ft2; 8142 ft2 wall area; 0.28 WWR; and 2280 ft2 of window
Note on J49: Richard Patterson: $5/ft2 incremental. Baseline school = 28000ft2; 8142 ft2 wall area; 0.28 WWR; and 2280 ft2 of window

## Super HP Glazings
Super High-Performance Glazings
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.361 | 0.441
Electricity ($/kWh) |  | 0.98176 | 0.11124
Water ($/1000L) |  | 20.5766 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Super High-Performance Glazings (.2 Btu/hr.ft2.F) - baseline office with a window U value of 0.46 Btu/hr.ft2.F and a space heating EUI of 14 m3/m2/yr. | 14 | 0 | 0 | 11.9 |  |  | I | 15.6937 | 0 | 30 | 2.1 | 0 | 0 | 0.9261 | 16.9461 | 0 | 9.158 | 0 | 0 | -6.5357 | 0.58355 | 15% | -3.1122
2 | [9 empty] | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.361 | 0.466
Electricity ($/kWh) |  | 0.98176 | 0.10323
Water ($/1000L) |  | 20.5766 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Super High-Performance Glazings (.2 Btu/hr.ft2.F) - baseline office with a window U value of 0.46 Btu/hr.ft2.F and a space heating EUI of 17 m3/m2/yr. | 17 | 0 | 0 | 14.45 |  |  | I | 15.6937 | 0 | 30 | 2.55 | 0 | 0 | 1.1245 | 13.9556 | 0 | 11.1205 | 0 | 0 | -4.5733 | 0.70859 | 15%
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Costs based on $10-15 per square foot of glazing based on Marbek database translated to floor area based on WWR of 0.35
2. Savings are 15% of space heating energy based on CEEAM simulations
3. The service life of glazing is 30 years (BC Hydro QA Standard)
4. The analysis is based on 1 m2 of floor area
Note on J15: Richard Patterson: $12.5/ft2 incremental. Baseline officel = 21520ft2; 7176 ft2 wall area; 0.35 WWR; and 2511 ft2 of window
Note on J49: Richard Patterson: $12.5/ft2 incremental. Baseline officel = 21520ft2; 7176 ft2 wall area; 0.35 WWR; and 2511 ft2 of window

## Wall Insulation
Wall Insulation
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8174 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Wall Insulation (R-24) - baseline wall R-12 and a space heating EUI of 12.9 m3/m2/yr. | 12.9 | 0 | 0 | 11.8 |  |  | I | 14.8488 | 0 | 20 | 1.1 | 0 | 0 | 0.4851 | 30.6098 | 0 | 4.1991 | 0 | 0 | -10.6497 | 0.28279 | 8.527% | -9.6815
2 | [9 empty] | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8174 | 0.466
Electricity ($/kWh) |  | 0.85643 | 0.10323
Water ($/1000L) |  | 17.927 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Wall Insulation (R-24) - baseline wall R-12 and a space heating EUI of 15.9 m3/m2/yr. | 15.9 | 0 | 0 | 14.5 |  |  | I | 14.8488 | 0 | 20 | 1.4 | 0 | 0 | 0.6174 | 24.0505 | 0 | 5.3443 | 0 | 0 | -9.5045 | 0.35992
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Costs based on $1.38 per square foot of floor area based on Marbek database
2. Savings are 9% of space heating energy based on CEEAM simulations
3. The service life of insulation is 20 years (BC Hydro QA Standard)
4. The analysis is based on 1 m2 of floor area

## Roof Insulation
Roof Insulation
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8174 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Roof Insulation (R-22) - baseline roof R-12 and a space heating EUI of 15.3 m3/m2/yr. | 15.3 | 0 | 0 | 12.1 |  |  | I | 10.76 | 0 | 20 | 3.2 | 0 | 0 | 1.4112 | 7.6247 | 0 | 12.2156 | 0 | 0 | 1.4556 | 1.1353 | 20.92% | 0.45486
2 | [9 empty] | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Roof Insulation (R-22) - baseline roof R-12 and a space heating EUI of 18.9 m3/m2/yr. | 18.9 | 0 | 0 | 15.12 |  |  | I | 10.76 | 0 | 25 | 3.78 | 0 | 0 | 1.667 | 6.4548 | 0 | 14.4296 | 0 | 0 | 3.6696 | 1.341
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1.. Costs based on $1 per square foot of roof area based on Marbek database
2. Savings are 20% of space heating energy based on CEEAM simulations (single story building)
3. The service life of insulation is 20 years (BC Hydro QA Standard)
4. The analysis is based on 1 m2 of floor area

## Air Sealing
Air Sealing
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 1.8299 | 0.441
Electricity ($/kWh) |  | 0.40144 | 0.11124
Water ($/1000L) |  | 8.4219 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Air Sealing - highrise office with a poor envelope and a space heating EUI of 12.9 m3/m2/yr. | 12.9 | 0 | 0 | 12.255 |  |  | F | 1.076 | 0 | 6 | 0.645 | 0 | 0 | 0.28445 | 3.7828 | 0 | 1.1803 | 0 | 0 | 0.10429 | 1.0969 | 5% | 0.16169
2 | [9 empty] | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | F |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Costs based on $0.10 per square foot of floor area based on Marbek database
2. Savings are 5% of space heating energy based on CEEAM simulations
3. The service life of air sealing is 6 years (BC Hydro QA Standard)
4. The analysis is based on 1 m2 of floor area

## Air Curtains
Air Curtains | [25 empty] | Calculator on | 0
Service Region: |  | Southern | [23 empty] | Aside: calculating air flow rate through an entrance
Measure Type: |  | Weather | [28 empty] | Volume flow rate equation
Assumed Discount Rate: |  | 10% | [23 empty] | Due to Buoyancy (temp difference) | 0.66286 | m3/s | Entrance width (m) | 1.8 |  | Buoancy portion | (Cd*A/3)*(g*h*deltaT/T(out))^0.5
Adjustment Factor: |  | 100% | [23 empty] | Due to wind | 0.108 | m3/s | Entrance height (m) | 2.4 |  | Wind portion | 0.025A*V
Free Rider Rate: |  | 0% | [23 empty] | Total | 0.6716 | m3/s | Flow Coefficient (Cd) | 0.6 |  | Total | (bouyancy^2 + wind^2)^0.5
Resource Costs: | [28 empty] | Coeff of gravity (g) | 9.81
|  | Avoided Cost (NPV) | Customer Cost | [17 empty] | 0 | [9 empty] | Energy Loss Equation |  | E(loss) = Vol rate (air)*rho(air)*Cp(air)*deltaT*t
Natural Gas ($/m3) |  | 3.3389 | 0.441 | [22 empty] | Hours open per day (assumed) | 4 |  | delta rho (density of air, kg/m3) | 0.06
Electricity ($/kWh) |  | 0.74654 | 0.11124 | [25 empty] | rho (average) | 1.24
Water ($/1000L) |  | 15.6181 | 3.05 | [25 empty] | Annual mean wind velocity at, m/s | 4
[26 empty] | Infiltration when air curtain is in use | 15% |  | Wind direction frequency factor | 0.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3 |  |  |  |  | Indoor temp (oC) | 22
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water | [8 empty] | Avg outdoor temp, London (oC) | 7
1 | Air curtain with rated effectiveness of 85% installed on double door - baseline: A "double door" entranceway open 4 hours per day. | 6440 | 0 | 0 | 1932 | -1023 |  | F | 2500 | 0 | 15 | 4508 | 1023 | 0 | 2101.8236 | 1.1894 | 0 | 15051.9183 | 763.7055 | 0 | 13315.6238 | 6.3262 | 70% | 2.9538 |  |  |  |  | Avg outdoor temp, Ottawa (oC) | 6
2 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | [6 empty] | Cp(AIR) | 1.006
3 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! |  | 62400
4 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! |  | 75000
5 |  |  | 0 | 0 |  |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.4
Electricity ($/kWh) |  | 0.74654 | 0.1
Water ($/1000L) |  | 15.6181 | 1.75
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. This upgrade consists of installing an air curtain (Enershield MCS-72) on the main double doors of a retail building.
2. It is assumed that the door is open for 4 hours per day and that the air curtain has an effectiveness of 85%
3. Installed cost is $2,500 as per Enbridge input assumptions
4. The service life is estimated to be 15 years (Enbridge Gas input assumptions) .
www.enershield.ca
Note on B19: Chris Pulfer: Average of above four measures (Weighted by average yearly use)
Note on G15: Chris Pulfer: 3 * 0.5 hp motors, running 4 hours/day (Subject to revision, as manufacturer suggests that barriers are generally driven by door sensor, usually + 15s delay) Average overall savings due to reduced cooling and auxillary equipment (fans/blowers) = 2142 kWh/yr.
Note on J15: Chris Pulfer: $1650 equipment cost, $300 installation (for electrical service, brackets, commissioning etc)
Note on AD1: Chris Pulfer: 1 for on, 0 for off
Note on AH6: Chris Pulfer: From Allocca for sharp-edged opening
Note on AH11: Chris Pulfer: Approx for London & Toronto (from EC, 14.6 and 14.7 km/hr respectively) (Ottawa 12.9 km/hr)
Note on AH14: Chris Pulfer: From EC. London & Toronto = 7.5, Ottawa = 6.0
Note on AL4: Chris Pulfer: H is defined as the height between the incoming and outgoing airflow paths. (Assume 1/2 heaight of opening) T(out) expressed in Kelvins
Note on AL8: Chris Pulfer: t = time door is open per year (s)

## Vinyl Strip Curtains
Vinyl Strip Curtains
Service Region: |  | Southern | [23 empty] | Aside: calculating air flow rate through an entrance
Measure Type: |  | Weather | [28 empty] | Volume flow rate equation
Assumed Discount Rate: |  | 10% | [23 empty] | Due to Buoyancy (temp difference) | 0.9196 | m3/s | Entrance width (m) | 2.4384 |  | Buoancy portion | (Cd*A/3)*(g*h*deltaT/T(out))^0.5
Adjustment Factor: |  | 100% | [23 empty] | Due to wind | 0.14864 | m3/s | Entrance height (m) | 2.4384 |  | Wind portion | 0.025A*V
Free Rider Rate: |  | 0% | [23 empty] | Total | 0.93153 | m3/s | Flow Coefficient (Cd) | 0.6 |  | Total | (bouyancy^2 + wind^2)^0.5
Resource Costs: | [28 empty] | Coeff of gravity (g) | 9.81
|  | Avoided Cost (NPV) | Customer Cost | [17 empty] | 0 | [9 empty] | Energy Loss Equation |  | E(loss) = Vol rate (air)*rho(air)*Cp(air)*deltaT*t
Natural Gas ($/m3) |  | 1.5869 | 0.441 | [22 empty] | Hours open per day (assumed) | 1 |  | delta rho (density of air, kg/m3) | 0.06
Electricity ($/kWh) |  | 0.34604 | 0.11124 | [25 empty] | rho (average) | 1.24
Water ($/1000L) |  | 7.2724 | 3.05 | [25 empty] | Annual mean wind velocity at, m/s | 4
[26 empty] | infiltration when of strip door is in place (adjusted for traffic) | 40% |  | Wind direction frequency factor | 0.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3 |  |  |  |  | Indoor temp (oC) | 21
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water | [8 empty] | Avg outdoor temp, Toronto (oC) | 7
1 | Baseline: Loading dock entranceway open 1 hour/day. Upgrade: Vinyl strip curtain installed on loading dock door. | 581.0465 | 0 | 0 | 232.4186 |  |  | F | 420 | 0 | 5 | 348.6279 | 0 | 0 | 153.7449 | 2.7318 | 0 | 553.2525 | 0 | 0 | 133.2525 | 1.3173 | 60% | 0.38222 |  |  |  |  | Avg outdoor temp, Ottawa (oC) | 6
2 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | [6 empty] | Cp(AIR) | 1.006
3 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! |  | 62400
4 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! |  | 75000
5 |  |  | 0 | 0 |  |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.4
Electricity ($/kWh) |  | 0.74654 | 0.1
Water ($/1000L) |  | 15.6181 | 1.75
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
This upgrade consists of installing a vinyl strip door with 100% overlap on a 12' X 12' loading dock door.
It is assumed that the door is open for one hour per day and that the strip door prevents 60% of air infiltration.
Installed cost is $420 as per supplier information and RS Means
The service life is estimated to be 5 years.
www.envirobarrier.com
Note on B19: Chris Pulfer: Average of above four measures (Weighted by average yearly use)
Note on J15: Chris Pulfer: $600 equipment cost, $150 installation (2.5 hr @$60/hr)
Note on AH4: Chris Pulfer: 8 feet
Note on AH6: Chris Pulfer: From Allocca for sharp-edged opening
Note on AH11: Chris Pulfer: Approx for Toronto (from EC, 14.7 km/hr) (Ottawa 12.9 km/hr)
Note on AH14: Chris Pulfer: From EC. Toronto = 7.5, Ottawa = 6.0
Note on AL4: Chris Pulfer: H is defined as the height between the incoming and outgoing airflow paths. (Assume 1/2 heaight of opening) T(out) expressed in Kelvins
Note on AL8: Chris Pulfer: t = time door is open per year (s)

## Fast Moving Doors
Fast Moving Doors
Service Region: |  | Southern | [23 empty] | Aside: calculating air flow rate through an entrance
Measure Type: |  | Weather | [28 empty] | Volume flow rate equation
Assumed Discount Rate: |  | 10% | [23 empty] | Due to Buoyancy (temp difference) | 5.5368 | m3/s | Entrance width (m) | 5 |  | Buoancy portion | (Cd*A/3)*(g*h*deltaT/T(out))^0.5
Adjustment Factor: |  | 100% | [23 empty] | Due to wind | 0.625 | m3/s | Entrance height (m) | 5 |  | Wind portion | 0.025A*V
Free Rider Rate: |  | 0% | [23 empty] | Total | 5.572 | m3/s | Flow Coefficient (Cd) | 0.6 |  | Total | (bouyancy^2 + wind^2)^0.5
Resource Costs: | [28 empty] | Coeff of gravity (g) | 9.81
|  | Avoided Cost (NPV) | Customer Cost | [17 empty] | 0 | [9 empty] | Energy Loss Equation |  | E(loss) = Vol rate (air)*rho(air)*Cp(air)*deltaT*t
Natural Gas ($/m3) |  | 2.6321 | 0.441 | [22 empty] | base door speed | 0.2 | m/s
Electricity ($/kWh) |  | 0.58464 | 0.11124 | [22 empty] | upgrade speed | 1.5 | m/s | rho (air density, average) | 1.24
Water ($/1000L) |  | 12.2336 | 3.05 | [22 empty] | cycles/day | 20 |  | Annual mean wind velocity at, m/s | 4
[26 empty] | door treatment efficiency | 1 |  | Wind direction frequency factor | 0.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3 |  | Open/close time (s,standard) | 500 |  | Indoor temp (oC) | 22
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water | [5 empty] | Open/close time (s,fast-moving) | 66.6667 |  | Avg outdoor temp, London (oC) | 7
1 | Baseline: A standard speed (0.2 m/s) 5m x 5m overhead door. Upgrade: High Speed (1.5m/s) 5m x 5m overhead door. | 517.1934 | 0 | 0 | 68.9591 | 0 |  | I | 10500 | 0 | 10 | 448.2343 | 0 | 0 | 197.6713 | 53.1185 | 0 | 1179.7823 | 0 | 0 | -9320.2177 | 0.11236 | 86.67% | -20.7932 |  |  |  |  | Avg outdoor temp, Ottawa (oC) | 6
2 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  |  |  | 0.86667 |  |  | Cp(AIR) | 1.006
3 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! |  | 62400
4 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! |  | 75000
5 |  |  | 0 | 0 |  |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.4
Electricity ($/kWh) |  | 0.74654 | 0.1
Water ($/1000L) |  | 15.6181 | 1.75
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
This upgrade consists of installing JetRoll high speed fabric door on a 16' x 16' loading dock
The baseline is a rolling steel door with a standard electric operator
It is assumed that the door is open for 20 times per day, and that the fast moving door opens and closes at 1.5 m/s, while the baseline overhead steel door opens and closes at 0.2 m/s.
Installed cost is $26,500 as per supplier information.
The service life is estimated to be 10 years.
Costing information from personal communication
bcrombeen@edwardsdoors.com
Note on B19: Chris Pulfer: Average of above four measures (Weighted by average yearly use)
Note on J15: Chris Pulfer: Personal Communication: Brian Crombeen, V.P. Edwards Door Systems Limited. bcrombeen@edwardsdoors.com
Note on AD13: Chris Pulfer: *2 for open and close in each cycle *0.5 for "half open" (as the average condition during a cycle, i.e. door doesn't go from fully open directly to fully closed instantaneaously )
Note on AH6: Chris Pulfer: From Allocca for sharp-edged opening
Note on AH11: Chris Pulfer: Approx for London & Toronto (from EC, 14.6 and 14.7 km/hr respectively) (Ottawa 12.9 km/hr)
Note on AH14: Chris Pulfer: From EC. London & Toronto = 7.5, Ottawa = 6.0
Note on AL4: Chris Pulfer: H is defined as the height between the incoming and outgoing airflow paths. (Assume 1/2 heaight of opening) T(out) expressed in Kelvins
Note on AL8: Chris Pulfer: t = time door is open per year (s)

## L Shaped Vestibules
L-Shaped Vestibule
Service Region: |  | Southern | [23 empty] | Aside: calculating air flow rate through an entrance
Measure Type: |  | Weather | [28 empty] | Volume flow rate equation
Assumed Discount Rate: |  | 10% | [23 empty] | Due to Buoyancy (temp difference) | 0.56451 | m3/s | Entrance width (m) | 1.8288 |  | Buoancy portion | (Cd*A/3)*(g*h*deltaT/T(out))^0.5
Adjustment Factor: |  | 100% | [23 empty] | Due to wind | 0.097548 | m3/s | Entrance height (m) | 2.1336 |  | Wind portion | 0.025A*V
Free Rider Rate: |  | 0% | [23 empty] | Total | 0.57287 | m3/s | Flow Coefficient (Cd) | 0.6 |  | Total | (bouyancy^2 + wind^2)^0.5
Resource Costs: | [28 empty] | Coeff of gravity (g) | 9.81
|  | Avoided Cost (NPV) | Customer Cost | [17 empty] | 0 | [9 empty] | Energy Loss Equation |  | E(loss) = Vol rate (air)*rho(air)*Cp(air)*deltaT*t
Natural Gas ($/m3) |  | 4.1414 | 0.441 | [22 empty] | Hours open per day (assumed) | 3 |  | delta rho (density of air, kg/m3) | 0.06
Electricity ($/kWh) |  | 0.93106 | 0.11124 | [25 empty] | rho (average) | 1.24
Water ($/1000L) |  | 19.5021 | 3.05 | [25 empty] | Annual mean wind velocity at, m/s | 4
[26 empty] | Infiltration doors are both open in L-shaped vestibule (baseline, double door) | 20% |  | Wind direction frequency factor | 0.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3 |  |  |  |  | Indoor temp (oC) | 22
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water | [8 empty] | Avg outdoor temp, London (oC) | 7
1 | Baseline: A double-door entranceway with both doors open for four hour per day (in a building occupied 10 hours/day). Upgrade: L-Shaped vestibule. | 1148.5693 | 0 | 0 | 229.7139 |  |  | F | 7040 | 0 | 25 | 918.8554 | 0 | 0 | 405.2152 | 17.3735 | 0 | 3805.3382 | 0 | 0 | -3234.6618 | 0.54053 | 80% | -3.5203 |  |  |  |  | Avg outdoor temp, Ottawa (oC) | 6
2 | Baseline: A "straight" double-door vestibule entranceway with both doors open simultaneaously for 1 hour per day (in a building occupied 10 hours/day). Upgrade: L-Shaped vestibule. | 306.2851 | 0 | 0 | 229.7139 |  |  | I | 0 | 0 | 25 | 76.5713 | 0 | 0 | 33.7679 | 0 | 0 | 317.1115 | 0 | 0 | 317.1115 | N/A | 25% | 4.1414 |  |  |  |  | Cp(AIR) | 1.006
3 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! |  | 62400
4 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! |  | 75000
5 |  |  | 0 | 0 |  |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.4
Electricity ($/kWh) |  | 0.74654 | 0.1
Water ($/1000L) |  | 15.6181 | 1.75
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
This upgrade consists of installing a 10' x10' L-shaped vestibule with two entrance doors.
The measure is evaluated at full cost against a standard double door, and incrementally against a standard "straight vestibule"
It is assumed that the door is open for three hours per day, with both "straight" vestibule doors are open simultaneously for 1 hour per day.
Full Installed cost is $7,040 (RS Means), There is no incremental cost, as the incremental upgrade is a matter of alternate door placement.
The service life is estimated to be 25 years (BC Hydro QA standard).
Note on B1: Chris Pulfer: Update / confirm
Note on B19: Chris Pulfer: Average of above four measures (Weighted by average yearly use)
Note on C16: Chris Pulfer: Assume losses when both doors are open are 80% of a simple double-door entrance when open
Note on J15: Chris Pulfer: Estimated two additional doors, 120 ft2 of additional glazing, 50ft2 of additional roofing
Note on AH4: Chris Pulfer: 6 feet x 7 feet
Note on AH6: Chris Pulfer: From Allocca for sharp-edged opening
Note on AH11: Chris Pulfer: Approx for London & Toronto (from EC, 14.6 and 14.7 km/hr respectively) (Ottawa 12.9 km/hr)
Note on AH14: Chris Pulfer: From EC. London & Toronto = 7.5, Ottawa = 6.0
Note on AL4: Chris Pulfer: H is defined as the height between the incoming and outgoing airflow paths. (Assume 1/2 heaight of opening) T(out) expressed in Kelvins
Note on AL8: Chris Pulfer: t = time door is open per year (s)

## Turnstile Doors
Turnstile Doors
Service Region: |  | Southern | [23 empty] | Aside: calculating air flow rate through an entrance
Measure Type: |  | Weather | [28 empty] | Volume flow rate equation
Assumed Discount Rate: |  | 10% | [23 empty] | Due to Buoyancy (temp difference) | 0.56451 | m3/s | Entrance width (m) | 1.8288 |  | Buoancy portion | (Cd*A/3)*(g*h*deltaT/T(out))^0.5
Adjustment Factor: |  | 100% | [23 empty] | Due to wind | 0.097548 | m3/s | Entrance height (m) | 2.1336 |  | Wind portion | 0.025A*V
Free Rider Rate: |  | 0% | [23 empty] | Total | 0.57287 | m3/s | Flow Coefficient (Cd) | 0.6 |  | Total | (bouyancy^2 + wind^2)^0.5
Resource Costs: | [28 empty] | Coeff of gravity (g) | 9.81
|  | Avoided Cost (NPV) | Customer Cost | [17 empty] | 0 | [9 empty] | Energy Loss Equation |  | E(loss) = Vol rate (air)*rho(air)*Cp(air)*deltaT*t
Natural Gas ($/m3) |  | 4.1414 | 0.441 | [22 empty] | Hours open per day (assumed) | 3 |  | delta rho (density of air, kg/m3) | 0.06
Electricity ($/kWh) |  | 0.93106 | 0.11124 | [25 empty] | rho (average) | 1.24
Water ($/1000L) |  | 19.5021 | 3.05 | [25 empty] | Annual mean wind velocity at, m/s | 4
[26 empty] | Infiltration when revolving door is in use | 11.11% |  | Wind direction frequency factor | 0.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3 |  |  |  |  | Indoor temp (oC) | 22
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water | [8 empty] | Avg outdoor temp, London (oC) | 7
1 | Baseline: A "double door" entranceway open 3 hours per day (in a building occupied 10 hours/day). Upgrade: Turnstile door with identical frontage dimensions. | 1148.5693 | 0 | 0 | 127.6188 |  |  | F | 19675 | 0 | 25 | 1020.9505 | 0 | 0 | 450.2392 | 43.699 | 0 | 4228.1536 | 0 | 0 | -15446.8464 | 0.2149 | 88.89% | -15.1299 |  |  |  |  | Avg outdoor temp, Ottawa (oC) | 6
2 | Baseline: A "double door" entranceway open 3 hours per day (in a building occupied 10 hours/day). Upgrade: Turnstile door with identical frontage dimensions. | 1148.5693 | 0 | 0 | 127.6188 |  |  | I | 6725 | 0 | 25 | 1020.9505 | 0 | 0 | 450.2392 | 14.9365 | 0 | 4228.1536 | 0 | 0 | -2496.8464 | 0.62872 | 88.89% | -2.4456 |  |  |  |  | Cp(AIR) | 1.006
3 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! |  | 62400
4 |  |  | 0 | 0 | 0 |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! |  | 75000
5 |  |  | 0 | 0 |  |  |  | I |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.4
Electricity ($/kWh) |  | 0.74654 | 0.1
Water ($/1000L) |  | 15.6181 | 1.75
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
This upgrade consists of installing a revolving door in place of s standard double door.
It is assumed that the door is open for three hours per day and reduces energy loss due to air infiltration to by 7/8 compared with standard balanced swinging door (Sustainability @ MIT, sustainability.mit.edu/Revolving_Door)
Incremental Installed cost is $6,725 (RS Means)
The service life is estimated to be 25 years (BC Hydro).
Note on B19: Chris Pulfer: Average of above four measures (Weighted by average yearly use)
Note on J15: Chris Pulfer: Installed cost, RS Means ($16,900 equipment, $2,775 installation)
Note on AH4: Chris Pulfer: 6 feet x 7 feet
Note on AH6: Chris Pulfer: From Allocca for sharp-edged opening
Note on AH11: Chris Pulfer: Approx for London & Toronto (from EC, 14.6 and 14.7 km/hr respectively) (Ottawa 12.9 km/hr)
Note on AH14: Chris Pulfer: From EC. London & Toronto = 7.5, Ottawa = 6.0
Note on AL4: Chris Pulfer: H is defined as the height between the incoming and outgoing airflow paths. (Assume 1/2 heaight of opening) T(out) expressed in Kelvins
Note on AL8: Chris Pulfer: t = time door is open per year (s)

## Condensing Boiler
Condensing Boiler
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.441
Electricity ($/kWh) |  | 0.93106 | 0.11124
Water ($/1000L) |  | 19.5021 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Condensing Boiler - 1,000 MBH, 94% Et (88% seasonal) - baseline standard efficiency 80% Et (76% seasonal) - 1,000 FLE hours | 37295.62 | 0 | 0 | 32209.8536 |  |  | I | 17777.7778 | 0 | 25 | 5085.7664 | 0 | 0 | 2242.823 | 7.9265 | 0 | 21062.1396 | 0 | 0 | 3284.3618 | 1.1847 | 13.64% | 0.64579
2 | Condensing Boiler - 1,000 MBH, 94% Et (88% seasonal) - baseline standard efficiency 80% Et (76% seasonal) - 1,500 FLE hours | 55943.43 | 0 | 0 | 48314.7805 |  |  | I | 17777.7778 | 0 | 25 | 7628.6495 | 0 | 0 | 3364.2344 | 5.2843 | 0 | 31593.2094 | 0 | 0 | 13815.4316 | 1.7771 | 13.64% | 1.811
3 | Condensing Boiler - 1,000 MBH, 94% Et (88% seasonal) - baseline standard efficiency 80% Et (76% seasonal) - 2,000 FLE hours | 74591.24 | 0 | 0 | 64419.7073 |  |  | I | 17777.7778 | 0 | 25 | 10171.5327 | 0 | 0 | 4485.6459 | 3.9633 | 0 | 42124.2792 | 0 | 0 | 24346.5014 | 2.3695 | 13.64% | 2.3936
4 | Condensing Boiler - 1,000 MBH, 94% Et (88% seasonal) - baseline near-condensing 85% Et (81% seasonal) - 1,000 FLE hours | 34993.4212 | 0 | 0 | 32209.8536 |  |  | I | 14836.6013 | 0 | 25 | 2783.5676 | 0 | 0 | 1227.5533 | 12.0863 | 0 | 11527.8377 | 0 | 0 | -3308.7636 | 0.77699 | 7.955% | -1.1887
5 | Condensing Boiler - 1,000 MBH, 94% Et (88% seasonal) - baseline near-condensing 85% Et (81% seasonal) - 1,500 FLE hours | 52490.1319 | 0 | 0 | 48314.7805 |  |  | I | 14836.6013 | 0 | 25 | 4175.3514 | 0 | 0 | 1841.33 | 8.0575 | 0 | 17291.7566 | 0 | 0 | 2455.1553 | 1.1655 | 7.955% | 0.58801
6 | Condensing Boiler - 1,000 MBH, 94% Et (88% seasonal) - baseline near-condensing 85% Et (81% seasonal) - 2,000 FLE hours | 69986.8425 | 0 | 0 | 64419.7073 |  |  | I | 14836.6013 | 0 | 25 | 5567.1352 | 0 | 0 | 2455.1066 | 6.0432 | 0 | 23055.6755 | 0 | 0 | 8219.0741 | 1.554 | 7.955% | 1.4764
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Boilers evaluated at 1,000, 1,500, and 2,000 full-load equivalent hours to reflect the range of operation commonly found in commercial buildings in both the Southern and Northern service regions.
2. The seasonal efficiency of the standard efficiency boiler is 76%; near-condensing, 81%; and condensing, 88% (Union Gas 2007-2009 DSM Plan, Appendix A and Terasen Gas)
3. The input capacity of the condensing boiler is approximately 12% less than the standard efficiency boiler and 6% less than the near-condensing boiler.
4. The boiler costs are based on Marbek's in-house database as follows:
- Standard efficiency boiler at $8/MBH
- Near-condensing at $11/MBH
- Condensing at $25/MBH
5. The service life of a boiler is 25 years (ASHRAE Applications Handbook - 2003, Chapter 36, Table 3).

## Near-Condensing Boiler
Near Condensing Boiler
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.441
Electricity ($/kWh) |  | 0.93106 | 0.11124
Water ($/1000L) |  | 19.5021 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Near-Condensing Boiler - 1,000 MBH, 85% Et (81% seasonal) - baseline standard efficiency 80% Et (76% seasonal) - 1,000 FLE hours | 37295.62 | 0 | 0 | 34993.4212 |  |  | I | 2941.1765 | 0 | 25 | 2302.1988 | 0 | 0 | 1015.2697 | 2.8969 | 0 | 9534.3019 | 0 | 0 | 6593.1254 | 3.2417 | 6.173% | 2.8638
2 | Near-Condensing Boiler - 1,000 MBH, 85% Et (81% seasonal) - baseline standard efficiency 80% Et (76% seasonal) - 1,500 FLE hours | 55943.43 | 0 | 0 | 52490.1319 |  |  | I | 2941.1765 | 0 | 25 | 3453.2981 | 0 | 0 | 1522.9045 | 1.9313 | 0 | 14301.4528 | 0 | 0 | 11360.2763 | 4.8625 | 6.173% | 3.2897
3 | Near-Condensing Boiler - 1,000 MBH, 85% Et (81% seasonal) - baseline standard efficiency 80% Et (76% seasonal) - 2,000 FLE hours | 74591.24 | 0 | 0 | 69986.8425 |  |  | I | 2941.1765 | 0 | 25 | 4604.3975 | 0 | 0 | 2030.5393 | 1.4485 | 0 | 19068.6038 | 0 | 0 | 16127.4273 | 6.4833 | 6.173% | 3.5026
4 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Boilers evaluated at 1,000, 1,500, and 2,000 full-load equivalent hours to reflect the range of operation commonly found in commercial buildings in both the Southern and Northern service regions.
2. The seasonal efficiency of the standard efficiency boiler is 76%; near-condensing, 81% (Union Gas 2007-2009 DSM Plan, Appendix A and Terasen Gas)
3. The input capacity of the near-condensing boiler is approximately 6% less than the standard efficiency boiler.
4. The boiler costs are based on Marbek's in-house database as follows:
- Standard efficiency boiler at $8/MBH
- Near-condensing at $11/MBH
5. The service life of a boiler is 25 years (ASHRAE Applications Handbook - 2003, Chapter 36, Table 3).

## Condensing UH
Condensing Unit Heater
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8174 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Condensing UH - 160 MBH, 91% Et (89% seasonal) - baseline standard efficiency 80% Et (79% seasonal) - 1,000 FLE hours | 5740.6929 | 0 | 0 | 5095.6712 |  |  | I | 1044.4444 | 0 | 20 | 645.0217 | 0 | 0 | 284.4546 | 3.6717 | 0 | 2462.2822 | 0 | 0 | 1417.8377 | 2.3575 | 11.24% | 2.1981
2 | Condensing UH - 160 MBH, 91% Et (89% seasonal) - baseline standard efficiency 80% Et (79% seasonal) - 1,500 FLE hours | 8611.0394 | 0 | 0 | 7643.5068 |  |  | I | 1044.4444 | 0 | 20 | 967.5325 | 0 | 0 | 426.6818 | 2.4478 | 0 | 3693.4233 | 0 | 0 | 2648.9788 | 3.5363 | 11.24% | 2.7379
3 | Condensing UH - 160 MBH, 91% Et (89% seasonal) - baseline standard efficiency 80% Et (79% seasonal) - 2,000 FLE hours | 11481.3858 | 0 | 0 | 10191.3425 |  |  | I | 1044.4444 | 0 | 20 | 1290.0433 | 0 | 0 | 568.9091 | 1.8359 | 0 | 4924.5644 | 0 | 0 | 3880.1199 | 4.715 | 11.24% | 3.0077
4 | [7 empty] | I |  | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | #DIV/0!
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.648 | 0.466
Electricity ($/kWh) |  | 0.8175 | 0.10323
Water ($/1000L) |  | 17.1078 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Unit heaters evaluated at 1,000, 1,500, and 2,000 full-load equivalent hours to reflect the range of operation commonly found in commercial buildings in both the Southern and Northern service regions.
2. The standard unit heater has a thermal efficiency of 80% and a seasonal efficiency of 79% (NRCan's proposed amendment to Canada's Energy Efficiency Regulation Aug 8, 2008)
3. The condensing unit heater has a thermal efficiency of 91% (Reznor Model UEAS 180) and a seasonal efficiency of 89% (Marbek estimate).
4. The input capacity of the condensing unit heater is approximately 12% less than the standard efficiency unit heater.
5. The unit heater costs are based on RS Means Mechanical Cost Data 2007 and personal communication with with Reznor as follows:
- Standard efficiency UH with power vent - $8/MBH
- Condensing UH - $16/MBH
6. The service life of a unit heater is 20 years (Union Gas 2007-2009 DSM Plan, Appendix A - Input Assumptions).

## HE Rooftop
High-Efficiency Rooftop Unit
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8174 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | High Efficiency Rooftop Unit - 375 MBH, 83% Et (80% seasonal) - baseline standard efficiency 80% Et (73% seasonal) - 1,000 FLE hours | 14560.6188 | 0 | 0 | 13286.5646 |  |  | I | 1875 | 0 | 20 | 1274.0541 | 0 | 0 | 561.8579 | 3.3371 | 0 | 4863.5278 | 0 | 0 | 2988.5278 | 2.5939 | 8.75% | 2.3457
2 | High Efficiency Rooftop Unit - 375 MBH, 83% Et (80% seasonal) - baseline standard efficiency 80% Et (73% seasonal) - 1,500 FLE hours | 21840.9282 | 0 | 0 | 19929.8469 |  |  | I | 1875 | 0 | 20 | 1911.0812 | 0 | 0 | 842.7868 | 2.2248 | 0 | 7295.2917 | 0 | 0 | 5420.2917 | 3.8908 | 8.75% | 2.8362
3 | High Efficiency Rooftop Unit - 375 MBH, 83% Et (80% seasonal) - baseline standard efficiency 80% Et (73% seasonal) - 2,000 FLE hours | 29121.2375 | 0 | 0 | 26573.1293 |  |  | I | 1875 | 0 | 20 | 2548.1083 | 0 | 0 | 1123.7158 | 1.6686 | 0 | 9727.0555 | 0 | 0 | 7852.0555 | 5.1878 | 8.75% | 3.0815
4 | [7 empty] | I |  | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | #DIV/0!
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.466
Electricity ($/kWh) |  | 0.74654 | 0.10323
Water ($/1000L) |  | 15.6181 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Rooftops were evaluated at 1,000, 1,500, and 2,000 full-load equivalent hours to reflect the range of operation commonly found in commercial buildings in both the Southern and Northern service regions.
2. The standard rooftop unit has a thermal efficiency of 80% and a seasonal efficiency of 73%.
3. The high efficiency rooftop unit has a thermal efficiency of 83% and a seasonal efficiency of 80%.
4. The incremental cost of a modulating burner is $5/MBH (RS Means Mechanical Cost Data 2007 and personal communication with Engineered Air)
5. The service life of a rooftop unit is 20 years (Union Gas 2007-2009 DSM Plan, Appendix A - Input Assumptions).
Note on J15: Richard Patterson: RS Means - Mech 2007 page 374 for 5,000 cfm MUA c/w 375 MBH burner

## Condensing Rooftop
Condensing Rooftop Unit
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8174 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Condensing Rooftop Unit - 375 MBH, 92% seasonal - baseline standard efficiency 80% Et (73% seasonal) - 1000 FLE hours | 14560.6188 | 0 | 0 | 11810.2797 |  |  | I | 9375 | 0 | 20 | 2750.3391 | 0 | 0 | 1212.8995 | 7.7294 | 0 | 10499.0441 | 0 | 0 | 1124.0441 | 1.1199 | 18.89% | 0.40869
2 | Condensing Rooftop Unit - 375 MBH, 83% Et (80% seasonal) - baseline standard efficiency 80% Et (73% seasonal) - 1,500 FLE hours | 21840.9282 | 0 | 0 | 17715.4195 |  |  | I | 9375 | 0 | 20 | 4125.5087 | 0 | 0 | 1819.3493 | 5.1529 | 0 | 15748.5661 | 0 | 0 | 6373.5661 | 1.6798 | 18.89% | 1.5449
3 | Condensing Rooftop Unit - 375 MBH, 83% Et (80% seasonal) - baseline standard efficiency 80% Et (73% seasonal) - 2,000 FLE hours | 29121.2375 | 0 | 0 | 23620.5593 |  |  | I | 9375 | 0 | 20 | 5500.6782 | 0 | 0 | 2425.7991 | 3.8647 | 0 | 20998.0881 | 0 | 0 | 11623.0881 | 2.2398 | 18.89% | 2.113
4 | [7 empty] | I |  | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | #DIV/0!
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.466
Electricity ($/kWh) |  | 0.74654 | 0.10323
Water ($/1000L) |  | 15.6181 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Rooftops were evaluated at 1,000, 1,500, and 2,000 full-load equivalent hours to reflect the range of operation commonly found in commercial buildings in both the Southern and Northern service regions.
2. The standard rooftop unit has a thermal efficiency of 80% and a seasonal efficiency of 73%.
3. The condensing boiler has a seasonal efficiency of 92%.
4. The incremental cost of a condensing rooftop unit is $25/MBH based on a 100% premium over a standard unit and RS Means Mechanical Cost Data 2007
5. The service life of a rooftop unit is 20 years (Union Gas 2007-2009 DSM Plan, Appendix A - Input Assumptions).
Note on J15: Richard Patterson: RS Means - Mech 2007 page 374 for 5,000 cfm MUA c/w 375 MBH burner
Note on J16: Richard Patterson: RS Means - Mech 2007 page 374 for 5,000 cfm MUA c/w 375 MBH burner
Note on J17: Richard Patterson: RS Means - Mech 2007 page 374 for 5,000 cfm MUA c/w 375 MBH burner

## Absorption Heat Pump
Absorption Heat Pump
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.441
Electricity ($/kWh) |  | 0.74654 | 0.11124
Water ($/1000L) |  | 15.6181 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Gas Absorption Heat Pump - 124 MBH at 105% seasonal - baseline standard efficiency boiler, 76% seasonal - 1,000 FLE hours | 4624.6569 |  | 0 | 3514.7392 |  |  | I | 2108 | 0 | 15 | 1109.9177 | 0 | 0 | 489.4737 | 4.3067 | 0 | 3705.9427 | 0 | 0 | 1597.9427 | 1.758 | 24% | 1.4397
2 | Gas Absorption Heat Pump - 124 MBH at 105% seasonal - baseline standard efficiency boiler, 76% seasonal - 1,500 FLE hours | 6936.9853 | 0 | 0 | 5272.1088 |  |  | I | 2108 | 0 | 15 | 1664.8765 | 0 | 0 | 734.2105 | 2.8711 | 0 | 5558.9141 | 0 | 0 | 3450.9141 | 2.6371 | 24% | 2.0728
3 | Gas Absorption Heat Pump - 124 MBH at 105% seasonal - baseline standard efficiency boiler, 76% seasonal - 2,000 FLE hours | 9249.3138 | 0 | 0 | 7029.4785 |  |  | I | 2108 | 0 | 15 | 2219.8353 | 0 | 0 | 978.9474 | 2.1533 | 0 | 7411.8854 | 0 | 0 | 5303.8854 | 3.5161 | 24% | 2.3893
4 | [7 empty] | I |  | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | #DIV/0!
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0! | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.466
Electricity ($/kWh) |  | 0.74654 | 0.10323
Water ($/1000L) |  | 15.6181 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Heat pumps were evaluated at 1,000, 1,500, and 2,000 full-load equivalent hours to reflect the range of operation commonly found in commercial buildings in both the Southern and Northern service regions.
2. The standard boiler has a thermal efficiency of 80% and a seasonal efficiency of 76%.
3. The heat pump is based on a Robur gas-fired absorption heat pump GAHP-A (heating only) with a a seasonal efficiency of 105%. (GazMetro InformaTECH Vol 22, Number 2, June 2008)
4. The incremental cost of a GAHP is $17/MBH over a standard efficiency boiler (Marbek estimate and personal communication with D-B Cooling Systems Inc)
5. The service life of a heat pump is 15 years (BC Hydro QA Standard).

## Steam Plant Measures
Steam Plant Efficiency Measures
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 2.6321 | 0.441
Electricity ($/kWh) |  | 0.58464 | 0.11124
Water ($/1000L) |  | 12.2336 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Steam Plant Efficiency Measures | 100 |  | 0 | 86.3 |  |  | F | 7.25 | 0 | 10 | 13.7 | 0 | 0 | 6.0417 | 1.2 | 0 | 36.0593 | 0 | 0 | 28.8093 | 4.9737 | 13.7% | 2.1029
2 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
4 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.466
Electricity ($/kWh) |  | 0.74654 | 0.10323
Water ($/1000L) |  | 15.6181 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Cost and savings based on results of Enbridge's Steam Plant Performance Test and Audit Program up to the end of 2005.
2. Analysis based on 100 m3 of gas and 13.7 % savings at a 1.2 year payback.
3. Measure life estimated to be an average of 10 years.
4. Analysis does not include electricity or water savings.

## Destratification Fans
HVLS De-stratification Fans
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.441
Electricity ($/kWh) |  | 0.74654 | 0.11124
Water ($/1000L) |  | 15.6181 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | HVLS De-stratification Fans - baseline is a 58,000 ft2 warehouse with 30' ceilings and 20' heater height - London | 90250 |  | 0 | 72712 | 1568.6275 |  | F | 21264 |  | 15 | 17538 | -1568.6275 | 0 | 7559.7684 | 2.8128 | 0 | 58558.2394 | -1171.0356 | 0 | 36123.2037 | 2.6101 | 19.43% | 2.0597
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.466
Electricity ($/kWh) |  | 0.74654 | 0.10323
Water ($/1000L) |  | 15.6181 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | HVLS De-stratification Fans - baseline is a 58,000 ft2 warehouse with 30' ceilings and 20' heater height - North Bay | 108845 |  | 0 | 91731 | 1568.6275 |  | F | 21264 |  | 15 | 17114 | -1568.6275 | 0 | 7372.7844 | 2.8841 | 0 | 57142.531 | -1171.0356 | 0 | 34707.4954 | 2.547 | 15.72% | 17.58%
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Analysis and assumptions are based on Energy Savings Associated with De-stratification in Buildings With High Ceilings (Draft), Caneta Research Inc., October 2007.
2. Cost based on 24' three diameter fans and information provided by suppliers.
3. Savings based on 15% of space heating load
4. Service life is 15 years (Enbridge DSM input assumptions)
5. The analysis does not account for any cooling savings in the summer.
Note on G15: Richard Patterson: 3*60W*8760
Note on Z49: Richard Patterson: avg

## Heat Reflector Panels
Heat Reflector Panels
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.648 | 0.441
Electricity ($/kWh) |  | 0.8175 | 0.11124
Water ($/1000L) |  | 17.1078 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Heat Reflector Panels - baseline is an apartment building with radiators and a space heating heating EUI of 16.2 m3/m2/yr. | 16.2 | 0 | 0 | 15.714 |  |  | F | 0.73973 | 0 | 18 | 0.486 | 0 | 0 | 0.21433 | 3.4514 | 0 | 1.7729 | 0 | 0 | 1.0332 | 2.3968 | 3% | 2.126
2 | [9 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 1.5869 | 0.466
Electricity ($/kWh) |  | 0.34604 | 0.10323
Water ($/1000L) |  | 7.2724 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Installed cost of approx $25/unit estimated using manufacturer retail costs (see www.novitherm.com)
2. Savings are 3% of space heating energy based on manufacturer case studies, Discussions with Union Gas personnel, and
Natural Gas Technologies Centre, 2004. Measurement and Verification of Heating Energy Savings Resulting from the Installation of Heat Reflector Panels, Site 2 report: Habitations L’Equerre, Sherbrook,
3. The service life is estimated to be 18 years (Enbridge input assumptions).
4. The analysis is based on one m2 of floor area.
Note on J15: Chris Pulfer: Assume a 6 floor, 78,000 sq. ft (7,300 sq m) apartment building with 72 suites of approximately 850 sq ft. Each suite with three radiators, and three reflector panels @ $25 installed.

## Heat Recovery
Heat Recovery
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.441
Electricity ($/kWh) |  | 0.74654 | 0.11124
Water ($/1000L) |  | 15.6181 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Air-To-Air Heat Recovery - 50% effectiveness, 8 hours/day | 1.4304 | 0 | 0 | 0.71522 |  |  | I | 2.1688 | 0 | 15 | 0.71522 | 0 | 0 | 0.31541 | 6.8759 | 0 | 2.3881 | 0 | 0 | 0.21934 | 1.1011 | 50% | 0.30667
2 | Air-To-Air Heat Recovery - 50% effectiveness, 16 hours/day | 2.8609 | 0 | 0 | 1.4304 |  |  | I | 2.1688 | 0 | 15 | 1.4304 | 0 | 0 | 0.63083 | 3.4379 | 0 | 4.7762 | 0 | 0 | 2.6074 | 2.2023 | 50% | 1.8228
3 | Air-To-Air Heat Recovery - 50% effectiveness, 24 hours/day | 4.2913 | 0 | 0 | 2.1457 |  |  | I | 2.1688 | 0 | 15 | 2.1457 | 0 | 0 | 0.94624 | 2.292 | 0 | 7.1643 | 0 | 0 | 4.9955 | 3.3034 | 50% | 2.3282
[8 empty] | I |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.466
Electricity ($/kWh) |  | 0.74654 | 0.10323
Water ($/1000L) |  | 15.6181 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Air-To-Air Heat Recovery - 50% effectiveness, 8 hours/day | 1.9383 | 0 | 0 | 0.96913 |  |  | I | 2.1688 | 0 | 15 | 0.96913 | 0 | 0 | 0.42739 | 5.0744 | 0 | 3.2359 | 0 | 0 | 1.0671 | 1.492
2 | Air-To-Air Heat Recovery - 50% effectiveness, 16 hours/day | 3.8765 | 0 | 0 | 1.9383 |  |  | I | 2.1688 | 0 | 15 | 1.9383 | 0 | 0 | 0.85478 | 2.5372 | 0 | 6.4718 | 0 | 0 | 4.303 | 2.9841
3 | Air-To-Air Heat Recovery - 50% effectiveness, 24 hours/day | 5.8148 | 0 | 0 | 2.9074 |  |  | I | 2.1688 | 0 | 15 | 2.9074 | 0 | 0 | 1.2822 | 1.6915 | 0 | 9.7076 | 0 | 0 | 7.5389 | 4.4761
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. The measure is evaluated at 8,16, and 24 hours to reflect range of operation found in building stock.
2. Baseline is 1 cfm of exhaust with no heat recovery
3. Upgrade is a heat wheel with an average sensible heat recovery effectiveness of 50% over the heating season.
4. Service life is 15 years based on BC Hydro QA Standard for packaged equipment and Union Gas input assumptions.
5. Costs ($2.17 / cfm average for 1,000 to 8,000 cfm heat wheels) based on RS Means Mechanical Cost Data 2007 page 371.
6. Analysis based on 1 cfm and sensible heat recovery only - no cooling savings considered.
Note on C15: Richard Patterson: 1 cfm, 3245 deg C HDD (< 15 deg C base), 8 hours per day operation
Note on J15: Richard Patterson: RS Means Mech 2007 page 371 - average of 1000 to 8000 cfm enthalpy recovery wheel
Note on J49: Richard Patterson: RS Means Mech 2007 page 371 - average of 1000 to 8000 cfm enthalpy recovery wheel

## Programmable Tstats
Programmable Thermostats
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.441
Electricity ($/kWh) |  | 0.74654 | 0.11124
Water ($/1000L) |  | 15.6181 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Programmable Thermostats - baseline is a small commercial building with packaged rooftop equipment, standard thermostats, and a space heating EUI of 12.9 m3/m2/yr. | 12.9 | 0 | 0 | 11.61 |  |  | F | 1.375 | 0 | 15 | 1.29 | 0 | 0 | 0.56889 | 2.417 | 0 | 4.3072 | 0 | 0 | 2.9322 | 3.1325 | 10% | 2.273
2 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | F |  | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Baseline building: 10,000 ft2, 400 ft2/ton, 5 RTUs, standard t'stats
2. Upgrade: programmable thermostats and sheduling of RTUs
3. Savings 10% of space heating (CEEAM)
4. Service life is 15 years (Pers comm, Union Gas / Enbridge input assumptions)
5. Costs based on $250-$300 provided by Union Gas
6. The analysis is based on 1 m2 of floor area
Note on F15: Richard Patterson: based on NFLD study analysis

## DCV
Demand Controlled Ventilation
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3389 | 0.441
Electricity ($/kWh) |  | 0.74654 | 0.11124
Water ($/1000L) |  | 15.6181 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Demand Controlled Ventilation - baseline is a large office with standard mixed air control and a space heating EUI of 13/m3/m2/yr. | 13 | 0 | 0 | 11.7 |  |  | F | 0.85714 | 0.057143 | 15 | 1.3 | 0 | 0 | 0.51616 | 1.6606 | 0.43463 | 4.3406 | 0 | 0 | 3.0488 | 3.3602 | 10% | 2.3453
2 | [9 empty] | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | F |  | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Baseline building: 150,000 ft2, 8 RTUs, standard mixed air control
2. Savings 10% of space heating (CEEAM)
3. Service life of DCV is 15 years (same a building automation system)
4. Costs based on supplier information and RS Means.
5. The analysis is based on 1 m2 of floor area and includes an increase in O&M for maintenance and calibration of CO2 sensors.
Note on F15: Richard Patterson: based on Terasen

## DCKV
Demand Control Kitchen Ventilation
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8174 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Demand Control Kitchen Ventilation - baseline 0-4999 cfm constant volume | [6 empty] | F | 5000 | 0 | 20 | 3660 | 7319 | 0 | 2428.2046 | 2.0591 | 0 | 13971.5504 | 6268.1975 | 0 | 15239.7479 | 4.0479 |  | 4.1639
2 | Demand Control Kitchen Ventilation - baseline 5000-9999 cfm constant volume | [6 empty] | F | 10000 | 0 | 20 | 9535 | 23180 | 0 | 6783.412 | 1.4742 | 0 | 36398.5609 | 19852.0041 | 0 | 46250.565 | 5.6251 |  | 4.8506
3 | Demand Control Kitchen Ventilation - baseline 10000-15000 cfm constant volume | [6 empty] | F | 15000 | 0 | 20 | 17455 | 40929 | 0 | 12250.48 | 1.2244 | 0 | 66632.0798 | 35052.7471 | 0 | 86684.8268 | 6.779 |  | 4.9662
[10 empty] | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Costs and savings based on Union Gas 2007-2009 DSM Plan page 48
2. Gas savings are assumed to be equivalent to ~ 30% required to heat make-up air.
3. Service life is estimated to be 20 years as per Union Gas Updated input assumptions (July 2008)
4. Costs range from approximately $1 to $2 per cfm.
Note on J15: Richard Patterson: Union Gas 2007-2009 DSM Plan
Note on M15: Richard Patterson: Union Gas 2007-2009 DSM Plan page 48 based on MELINK Calcs

## Furnace Boiler Tune ups
Furnace Boiler Tune Ups
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 0.75436 | 0.441
Electricity ($/kWh) |  | 0.15465 | 0.11124
Water ($/1000L) |  | 3.246 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Furnace Boiler Tune Ups - baseline is a 400 m2 retail building with two gas-fired rooftop units and a space heating EUI of 13m3/m2/yr. | 13 | 0 | 0 | 12.35 |  |  | F | 0.5 | 0 | 2 | 0.65 | 0 | 0 | 0.28665 | 1.7443 | 0 | 0.49033 | 0 | 0 | -0.0096681 | 0.98066 | 5% | -0.014874
2 | [9 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | F |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Baseline is a 400 m2 retail building with two gas-fired rooftop units and a space heating EUI of 13 m3/m2/yr.
2. Savings 5% of space heating
3. Service life of tune-up is estimated to be 2 years
4. The analysis is based on 1 m2 of floor area
5. Cost is $500/unit (personal communication, Union Gas)

## Condensing Furnace
Condensing Furnace
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.648 | 0.441
Electricity ($/kWh) |  | 0.8175 | 0.11124
Water ($/1000L) |  | 17.1078 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Condensing Furnace - 100 MBH, 94% AFUE - baseline standard 80% AFUE - 1,000 FLE hours | 3543.0839 | 0 | 0 | 3015.3906 |  |  | I | 600 | 0 | 18 | 527.6933 | 0 | 0 | 232.7128 | 2.5783 | 0 | 1925.0374 | 0 | 0 | 1325.0374 | 3.2084 | 14.89% | 2.511
2 | Condensing Furnace - 100 MBH, 94% AFUE - baseline standard 80% AFUE - 1,500 FLE hours | 5314.6259 | 0 | 0 | 4523.0858 |  |  | I | 600 | 0 | 18 | 791.54 | 0 | 0 | 349.0691 | 1.7189 | 0 | 2887.556 | 0 | 0 | 2287.556 | 4.8126 | 14.89% | 2.89
3 | Condensing Furnace - 100 MBH, 94% AFUE - baseline standard 80% AFUE - 2,000 FLE hours | 7086.1678 | 0 | 0 | 6030.7811 |  |  | I | 600 | 0 | 18 | 1055.3867 | 0 | 0 | 465.4255 | 1.2891 | 0 | 3850.0747 | 0 | 0 | 3250.0747 | 6.4168 | 14.89% | 3.0795
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
5 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Furnaces evaluated at 1,000, 1,500, and 2,000 full-load equivalent hours to reflect the range of operation commonly found in commercial buildings in both the Southern and Northern service regions.
2. Costs based on scan of supplier information and RS Means.
3. Service life of 18 years based on ASHRAE/Union Gas Updated input assumptions (July 2008)

## Infrared Heaters
Infrared Heaters
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8174 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Infrared Heaters - 100 MBH, 80% Et - baseline standard unit heater 80% Et - 1,000 FLE hours | 3587.9331 | 0 | 0 | 3157.3811 |  |  | I | 375 | 0 | 20 | 430.552 | 0 | 0 | 189.8734 | 1.975 | 0 | 1643.5734 | 0 | 0 | 1268.5734 | 4.3829 | 12% | 2.9464
2 | Infrared Heaters - 100 MBH, 80% Et - baseline standard unit heater 80% Et - 1,500 FLE hours | 5381.8996 | 0 | 0 | 4736.0716 |  |  | I | 375 | 0 | 20 | 645.828 | 0 | 0 | 284.8101 | 1.3167 | 0 | 2465.36 | 0 | 0 | 2090.36 | 6.5743 | 12% | 3.2367
3 | Infrared Heaters - 100 MBH, 80% Et - baseline standard unit heater 80% Et - 2,000 FLE hours | 7175.8661 | 0 | 0 | 6314.7622 |  |  | I | 375 | 0 | 20 | 861.1039 | 0 | 0 | 379.7468 | 0.9875 | 0 | 3287.1467 | 0 | 0 | 2912.1467 | 8.7657 | 12% | 3.3819
4 | [7 empty] | I |  | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.648 | 0.466
Electricity ($/kWh) |  | 0.8175 | 0.10323
Water ($/1000L) |  | 17.1078 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Infrared heaters evaluated at 1,000, 1,500, and 2,000 full-load equivalent hours to reflect the range of operation commonly found in commercial buildings in both the Southern and Northern service regions.
2. The standard unit heater has a thermal efficiency of 80% and a seasonal efficiency of 79% (NRCan's amendment to Canada's Energy Efficiency Regulation Aug 8, 2008)
3. The infrared heater is tube-style with an efficiency of 80% (Union Gas).
4. Costs based on RS Means Mechanical Cost Data 2007
5. The service life is estimated to be 20 years (Union Gas Updated input assumptions (July 2008))

## Solar Preheat
Solar Preheated Make-up Air
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8174 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Solar Preheated Make-up Air - baseline 1500 cfm make-up air unit at 80% efficiency and 24 hour operation | 11348 | 0 | 0 | 9282 |  |  | F | 11200 | 0 | 20 | 2066 | 0 | 0 | 911.106 | 12.2928 | 0 | 7886.673 | 0 | 0 | -3313.327 | 0.70417 | 18.21% | -1.6037
2 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8174 | 0.466
Electricity ($/kWh) |  | 0.85643 | 0.10323
Water ($/1000L) |  | 17.927 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [10 empty] | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [10 empty] | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [10 empty] | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Measure analysis based on a RETSceen analysis for a warehouse application; 1500 cfm and 280 ft2 of cladding.
2. Costs are 40/ft2 of cladding (installed) based on Marbek review of REDI applications.
3. Service life based on 20 years (Marbek estimate)
4. Savings based on RETScreen simulations

## Condensing Water Heater
Condensing Water Heater
Service Region: |  | Southern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1035 | 0.441
Electricity ($/kWh) |  | 0.91835 | 0.11124
Water ($/1000L) |  | 19.2334 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Condensing Water Heater - 150 MBH, (90% seasonal) - baseline standard efficiency 80% Et (70% seasonal) - 500 FLE hours | 3036.9291 | 0 | 0 | 2362.0559 |  |  | I | 2447.3684 | 0 | 24 | 674.8731 | 0 | 0 | 297.619 | 8.2232 | 0 | 2769.3713 | 0 | 0 | 322.0028 | 1.1316 | 22.22% | 0.47713
2 | Condensing Water Heater - 150 MBH, (90% seasonal) - baseline standard efficiency 80% Et (70% seasonal) - 1,000 FLE hours | 6073.8581 | 0 | 0 | 4724.1119 |  |  | I | 2447.3684 | 0 | 24 | 1349.7462 | 0 | 0 | 595.2381 | 4.1116 | 0 | 5538.7425 | 0 | 0 | 3091.3741 | 2.2631 | 22.22% | 2.2903
3 | Condensing Water Heater - 150 MBH, (90% seasonal) - baseline standard efficiency 80% Et (70% seasonal) - 1,500 FLE hours | 9110.7872 | 0 | 0 | 7086.1678 |  |  | I | 2447.3684 | 0 | 24 | 2024.6194 | 0 | 0 | 892.8571 | 2.7411 | 0 | 8308.1138 | 0 | 0 | 5860.7454 | 3.3947 | 22.22% | 2.8947
4 | [7 empty] | I |  | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1591 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Heaters were evaluated at 500, 1,000, and 1,500 equivalent full-load hours to reflect the range of operation and loads commonly found in commercial buildings.
2. The seasonal efficiency of the standard efficiency heater is 75%; and condensing heater 90% (Marbek estimate)
3. The input capacity of the condensing heater is less than the standard efficiency heater.
4. The boiler costs are based on Marbek's in-house database as follows:
- Standard efficiency heater at $8/MBH
- Condensing heater $25/MBH
5. The service life of a DHW boiler is 24 years. (BC Hydro QA Standard)

## Condensing Tank Water Heater
Condensing Tank-Type Water Heater
Service Region: |  | Southern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3504 | 0.441
Electricity ($/kWh) |  | 0.74654 | 0.11124
Water ($/1000L) |  | 15.6181 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Condensing Tank-Type Water Heater - 150 MBH, (90% seasonal) - baseline standard efficiency 80% Et (70% seasonal) - 500 FLE hours | 3036.9291 | 0 | 0 | 2362.0559 |  |  | I | 2000 | 0 | 15 | 674.8731 | 0 | 0 | 297.619 | 6.72 | 0 | 2261.1284 | 0 | 0 | 261.1284 | 1.1306 | 22.22% | 0.38693
2 | Condensing Storage Water Heater - 150 MBH, (90% seasonal) - baseline standard efficiency 80% Et (70% seasonal) - 1,000 FLE hours | 6073.8581 | 0 | 0 | 4724.1119 |  |  | I | 2000 | 0 | 15 | 1349.7462 | 0 | 0 | 595.2381 | 3.36 | 0 | 4522.2568 | 0 | 0 | 2522.2568 | 2.2611 | 22.22% | 1.8687
3 | Condensing Storage Water Heater - 150 MBH, (90% seasonal) - baseline standard efficiency 80% Et (70% seasonal) - 1,500 FLE hours | 9110.7872 | 0 | 0 | 7086.1678 |  |  | I | 2000 | 0 | 15 | 2024.6194 | 0 | 0 | 892.8571 | 2.24 | 0 | 6783.3852 | 0 | 0 | 4783.3852 | 3.3917 | 22.22% | 2.3626
4 | [7 empty] | I |  | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1591 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Heaters were evaluated at 500, 1,000, and 1,500 equivalent full-load hours to reflect the range of operation and loads commonly found in commercial buildings.
2. The seasonal efficiency of the standard efficiency heater is 75%; and condensing heater 90% (Marbek estimate)
3. The input capacity of the condensing heater is less than the standard efficiency heater.
4. The heater costs are based on Marbek's in-house database and RS Means
5. The service life of a DHW heater is 15 years. (Union Gas DSM 2006 Evaluation Report, June 2007)
Note on J15: Richard Patterson: based on BC Hydro 2006 CPR

## Tankless Water Heater
Tankless Water Heater
Service Region: |  | Southern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8326 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Tankless Water Heater - 150 MBH, (81% seasonal) - baseline standard efficiency 80% Et (70% seasonal) - 500 FLE hours | 3036.9291 | 0 | 0 | 2624.5066 |  |  | I | 2196.0688 | 0 | 20 | 412.4225 | 0 | 0 | 181.8783 | 12.0744 | 0 | 1580.6338 | 0 | 0 | -615.435 | 0.71976 | 13.58% | -1.4922
2 | Tankless Water Heater - 150 MBH, (81% seasonal) - baseline standard efficiency 80% Et (70% seasonal) - 1,000 FLE hours | 6073.8581 | 0 | 0 | 5249.0132 |  |  | I | 2196.0688 | 0 | 20 | 824.8449 | 0 | 0 | 363.7566 | 6.0372 | 0 | 3161.2676 | 0 | 0 | 965.1989 | 1.4395 | 13.58% | 1.1702
3 | Tankless Water Heater - 150 MBH, (81% seasonal) - baseline standard efficiency 80% Et (70% seasonal) - 1,500 FLE hours | 9110.7872 | 0 | 0 | 7873.5198 |  |  | I | 2196.0688 | 0 | 20 | 1237.2674 | 0 | 0 | 545.6349 | 4.0248 | 0 | 4741.9015 | 0 | 0 | 2545.8327 | 2.1593 | 13.58% | 2.0576
4 | [7 empty] | I |  | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1591 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Heaters were evaluated at 500, 1,000, and 1,500 equivalent full-load hours to reflect the range of operation and loads commonly found in commercial buildings.
2. The seasonal efficiency of the standard efficiency heater is 70%; and tankless heater 81% (Marbek estimate)
3. The service life of a Tankless DHW heater is 20 years, tank-type 15 years. (Union Gas DSM 2006 Evaluation Report, June 2007)
4. Incremental cost of $15/MBH are based on Marbek's in-house database as follows:
- Tank-type Heater @ approx $39/MBH (RS Means)
| - Annualized cost over lifetime (@ 10% discount rate): |  |  |  |  | -5.1713 | /MBH
| - Present value of annualized cost over 20 years (life of tankless heater): |  |  |  |  | 44.0262 | /MBH
- Tankless Heater @ approx $59/MBH (Supplier Information, Takagi)
| - Incremental cost = Tankless/MBH-Tank/MBH |  |  |  |  | 14.6405 | /MBH
Note on J15: Richard Patterson: based on BC Hydro 2006 FS CPR - replace one 100 G (150 MBH) tank heater at $5,900 installed with 2 Takagi TM1 at $4,400 each installed.

## Drainwater Heat Recovery
Drainwater Heat Recovery
Service Region: |  | Southern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8326 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Drainwater Heat Recovery - 10 minute shower, 1.5 times per day | 215.5376 | 0 | 0 | 112.0796 |  |  | I | 900 | 0 | 20 | 103.458 | 0 | 0 | 45.625 | 19.726 | 0 | 396.5092 | 0 | 0 | -503.4908 | 0.44057 | 48% | -4.8666
2 | Drainwater Heat Recovery - 10 minute shower, 3 times per day | 431.0752 | 0 | 0 | 224.1591 |  |  | I | 900 | 0 | 20 | 206.9161 | 0 | 0 | 91.25 | 9.863 | 0 | 793.0184 | 0 | 0 | -106.9816 | 0.88113 | 48% | -0.51703
3 | Drainwater Heat Recovery - 10 minute shower, 4.5 times per day | 646.6128 | 0 | 0 | 336.2387 |  |  | I | 900 | 0 | 20 | 310.3741 | 0 | 0 | 136.875 | 6.5753 | 0 | 1189.5275 | 0 | 0 | 289.5275 | 1.3217 | 48% | 0.93283
4 | [7 empty] | I |  | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1591 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Heat recovery was evaluated 1.5, 3 and 4.5 showers per day.
2. The heat recovery efficiency of the drain water system is 48% (NRCan)
3. The cost of the drain water system is $600 to $1,200 (RenewABILITY Energy Inc)
5. The service life is estimated to be 20 years.
Note on C15: Richard Patterson: The Hilton Garden Inn, currently under construction in Edison, New Jersey, is the first hotel in the U.S. to install drainwater heat recovery using the GFX device. Hotels are a prime candidate for GFX, because they use a large amount of hot water for showers. In this project, two adjacent rooms share a single GFX unit installed in the 4-inch drain stack in the floor below. A branch of the cold water supply to showers passes through the GFX on its way to the showers, preheating the water and reducing the amount of hot water needed. Savings for the 132-room hotel are estimated at 42,417 kWh per year. This estimate assumes an average cold water temperature of 55 degrees F, 2.5 gpm shower heads, 10-minute shower duration, 1.5 showers per unit per day and occupancy of 60 percent. GFX is also well suited to commercial dish washing and laundry applications. GFX units have been in use at a hotel in Wellington, New Zealand for several years.
Note on C16: Richard Patterson: The Hilton Garden Inn, currently under construction in Edison, New Jersey, is the first hotel in the U.S. to install drainwater heat recovery using the GFX device. Hotels are a prime candidate for GFX, because they use a large amount of hot water for showers. In this project, two adjacent rooms share a single GFX unit installed in the 4-inch drain stack in the floor below. A branch of the cold water supply to showers passes through the GFX on its way to the showers, preheating the water and reducing the amount of hot water needed. Savings for the 132-room hotel are estimated at 42,417 kWh per year. This estimate assumes an average cold water temperature of 55 degrees F, 2.5 gpm shower heads, 10-minute shower duration, 1.5 showers per unit per day and occupancy of 60 percent. GFX is also well suited to commercial dish washing and laundry applications. GFX units have been in use at a hotel in Wellington, New Zealand for several years.
Note on C17: Richard Patterson: The Hilton Garden Inn, currently under construction in Edison, New Jersey, is the first hotel in the U.S. to install drainwater heat recovery using the GFX device. Hotels are a prime candidate for GFX, because they use a large amount of hot water for showers. In this project, two adjacent rooms share a single GFX unit installed in the 4-inch drain stack in the floor below. A branch of the cold water supply to showers passes through the GFX on its way to the showers, preheating the water and reducing the amount of hot water needed. Savings for the 132-room hotel are estimated at 42,417 kWh per year. This estimate assumes an average cold water temperature of 55 degrees F, 2.5 gpm shower heads, 10-minute shower duration, 1.5 showers per unit per day and occupancy of 60 percent. GFX is also well suited to commercial dish washing and laundry applications. GFX units have been in use at a hotel in Wellington, New Zealand for several years.

## Faucets & Showerheads
Low-Flow Faucets Aerators and Showerheads
Service Region: |  | Southern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 2.6382 | 0.441
Electricity ($/kWh) |  | 0.58464 | 0.11124
Water ($/1000L) |  | 12.2336 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Low Flow Faucets (1.0 gpm) - baseline faucet 2.0 gpm for 1 min/day. | 11.4953 | 0 | 2763.05 | 5.7477 |  | 2072.2875 | F | 5 | 0 | 10 | 5.7477 | 0 | 690.7625 | 4.6415 | 1.0772 | 0 | 15.1634 | 0 | 8.4505 | 18.6139 | 4.7228 | 50% | 3.2385
2 | Low Flow Faucets (1.0 gpm) - baseline faucet 2.0 gpm for 3 min/day. | 34.486 | 0 | 8289.15 | 17.243 |  | 6216.8625 | F | 5 | 0 | 10 | 17.243 | 0 | 2072.2875 | 13.9246 | 0.35908 | 0 | 45.4902 | 0 | 25.3516 | 65.8418 | 14.1684 | 50% | 3.8185
3 | Low Flow Faucets (1.0 gpm) - baseline faucet 2.0 gpm for 5 min/day. | 57.4767 | 0 | 13815.25 | 28.7383 |  | 10361.4375 | F | 5 | 0 | 10 | 28.7383 | 0 | 3453.8125 | 23.2077 | 0.21545 | 0 | 75.8171 | 0 | 42.2527 | 113.0697 | 23.6139 | 50% | 3.9345
4 | Low Flow Showerheads (1.25 gpm) - baseline showerhead 2.5 gpm for 5 min/day. | 71.8459 | 0 | 17269.0625 | 35.9229 |  | 8634.5312 | F | 20 | 0 | 10 | 35.9229 | 0 | 8634.5312 | 42.1773 | 0.47419 | 0 | 94.7713 | 0 | 105.6317 | 180.403 | 10.0202 | 50% | 5.0219
5 | Low Flow Showerheads (1.25 gpm) - baseline showerhead 2.5 gpm for 10 min/day. | 143.6917 | 0 | 34538.125 | 71.8459 |  | 17269.0625 | F | 20 | 0 | 10 | 71.8459 | 0 | 17269.0625 | 84.3547 | 0.23709 | 0 | 189.5426 | 0 | 211.2634 | 380.806 | 20.0403 | 50% | 5.3003
6 | Low Flow Showerheads (1.25 gpm) - baseline showerhead 2.5 gpm for 15 min/day. | 215.5376 | 0 | 51807.1875 | 107.7688 |  | 25903.5938 | F | 20 | 0 | 10 | 107.7688 | 0 | 25903.5938 | 126.532 | 0.15806 | 0 | 284.3139 | 0 | 316.8951 | 581.209 | 30.0605 | 50% | 5.3931
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1591 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Savings evaluated at 1,3, and 5 minutes/day for faucets and 5,10, and 15 minutes/day to reflect the range of diversity found in the commercial building stock.
2. Savings based on installing 1.0 gpm (50% savings) faucet aerators and 1.25 gpm (50% savings) shower heads.
3. Costs based on $5 per aerator and $20 per head as per personal communication with Water Conservation Company.
4. The service life is estimated to be 10 years. (BC Hydro QA Standard, Union Gas DSM input assumptions)
Note on H15: Chris Pulfer: Assume 50% is for "consumptive" type uses (i.e. not hand washing), where aerators give no savings

## Spray Valve
Pre-Rinse Spray Valve
Service Region: |  | Southern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 1.5851 | 0.441
Electricity ($/kWh) |  | 0.34604 | 0.11124
Water ($/1000L) |  | 7.2724 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Consumption |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Pre-Rinse Spray Valve (1.2 gpm) - baseline 3.0 gpm for 20 minutes per day | 344.8602 | 0 | 82891.5 | 137.9441 |  | 33156.6 | F | 100 | 0 | 5 | 206.9161 | 0 | 49734.9 | 242.9414 | 0.41162 | 0 | 327.993 | 0 | 361.6936 | 589.6865 | 6.8969 | 60% | 2.8499
2 | Pre-Rinse Spray Valve (1.2 gpm) - baseline 3.0 gpm for 40 minutes per day | 689.7203 | 0 | 165783 | 275.8881 |  | 66313.2 | F | 100 | 0 | 5 | 413.8322 | 0 | 99469.8 | 485.8829 | 0.20581 | 0 | 655.9859 | 0 | 723.3872 | 1279.3731 | 13.7937 | 60% | 3.0915
3 | Pre-Rinse Spray Valve (1.2 gpm) - baseline 3.0 gpm for 60 minutes per day | 1034.5805 |  | 248674.5 | 413.8322 |  | 99469.8 | F | 100 | 0 | 5 | 620.7483 | 0 | 149204.7 | 728.8243 | 0.13721 | 0 | 983.9789 | 0 | 1085.0807 | 1969.0596 | 20.6906 | 60% | 3.1721
4 | Pre-Rinse Spray Valve (1.2 gpm) - baseline 3.0 gpm for 225 minutes per day | 3879.6769 | 0 | 927419.625 | 2392.2194 |  | 383333.445 | F | 100 | 0 | 5 | 1487.4575 | 0 | 544086.18 | 2315.4316 | 0.043188 | 0 | 2357.8425 | 0 | 3956.8286 | 6214.6712 | 63.1467
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1591 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Measure evaluated at 20,40, and 60 minutes/day to reflect range of operation commonly found in food service operations. (see Veritec Consulting. "Region of Waterloo Pre-Rinse Spray Valve Pilot Study")
2. Measure evaluated at 225 minutes/day to reflect Union Gas input assumptions (presently under review)
3. Cost, savings, and service life assumptions based on information provided in study conducted by Veritec Consulting for the Region of Waterloo.
4. Baseline spray valve flow rate from Union Gas input assumptions

## Solar Water Heating
Solar Water Heating
Service Region: |  | Southern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.3504 | 0.441
Electricity ($/kWh) |  | 0.74654 | 0.11124
Water ($/1000L) |  | 15.6181 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Solar Weater Heating System - baseline standard efficiency 80% Et (70% seasonal) - 500 FLE hours | 3036.9291 | 0 | 0 | 2429.5432 |  |  | F | 9000 | 100 | 15 | 607.3858 | 0 | 0 | 167.8571 | 53.617 | 760.608 | 2035.0156 | 0 | 0 | -7725.5924 | 0.20849 | 20% | -12.7194
2 | Solar Weater Heating System - baseline standard efficiency 80% Et (70% seasonal) - 1,000 FLE hours | 6073.8581 | 0 | 0 | 4859.0865 |  |  | F | 9000 | 100 | 15 | 1214.7716 | 0 | 0 | 435.7143 | 20.6557 | 760.608 | 4070.0311 | 0 | 0 | -5690.5768 | 0.41699 | 20% | -4.6845
3 | Solar Weater Heating System - baseline standard efficiency 80% Et (70% seasonal) - 1,500 FLE hours | 9110.7872 | 0 | 0 | 7288.6297 |  |  | F | 9000 | 100 | 15 | 1822.1574 | 0 | 0 | 703.5714 | 12.7919 | 760.608 | 6105.0467 | 0 | 0 | -3655.5613 | 0.62548 | 20% | -2.0062
4 | [7 empty] | F |  | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1591 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Heating systems were evaluated at 500, 1,000, and 1,500 equivalent full-load hours to reflect the range of operation and loads commonly found in commercial buildings.
2. The seasonal efficiency of the standard efficiency heater is 75%;
3. The cost of the closed loop solar add on based on RS Means Mechanical Cost Data 2007 for a 100 gallon storage tank heater
4. The service life of a solar heating system is estimated to be the same as a storage tank heater - 15 years. (BC Hydro QA Standard)
Note on J15: Richard Patterson: RS Means 2007, page 471 - $8,000 to $11,000 for ~ 120 USG storage tank
Note on J16: Richard Patterson: RS Means 2007, page 471 - $8,000 to $11,000 for ~ 120 USG storage tank
Note on J17: Richard Patterson: RS Means 2007, page 471 - $8,000 to $11,000 for ~ 120 USG storage tank

## Booster
Booster Water Heater
Service Region: |  | Southern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.8326 | 0.441
Electricity ($/kWh) |  | 0.85643 | 0.11124
Water ($/1000L) |  | 17.927 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Tankless Booster Water Heater - 75 MBH, (83% seasonal) - baseline standard efficiency 80% Et (70% seasonal) - 800 FLE hours | 2274.1917 | 0 | 0 | 1917.993 |  |  | I | 1200 | 0 | 20 | 356.1987 | 0 | 0 | 157.0836 | 7.6392 | 0 | 1365.1529 | 0 | 0 | 165.1529 | 1.1376 | 15.66% | 0.46365
2
3 | [23 empty] | #DIV/0!
4
5 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1591 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Heaters were evaluated at 500 equivalent full-load hours to reflect the typical operation and load of a commercial dishwasher.
2. The seasonal efficiency of the standard efficiency heater is 70%; and tankless heater 83% (Marbek estimate)
3. The burner size of the tankless heater is approximately 3x larger than the standard efficiency heater.
4. The baseline cost based on RS Means, tankless costs are based on supplier information:
(http://www.tanklesswaterheaters.ca/takmobtm1.html)
5. The service life of a tankless water booster water heater is assumed to be 20 years (BC Hydro QA Standard)
Note on J15: Richard Patterson: Partially based on BC Hydro 2006 FS CPR - replace one 50 G (75 MBH) booster tank heater at $3,200 installed with a Takagi TM1 at $4,400 installed. Works out to 1200/75 = $16/MBH

## Commercial Cooking
Commercial Cooking
Service Region: |  | Southern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost | [17 empty] | 0
Natural Gas ($/m3) |  | 2.6382 | 0.441
Electricity ($/kWh) |  | 0.58464 | 0.11124
Water ($/1000L) |  | 12.2336 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water |  |  |  |  | avg use
1 | Commercial Griddle (86,100 kBtu/year) Baseline griddle: 32% efficient - High efficiency product: 40% | 2414.5534 | 0 | 0 | 1931.6427 |  |  | I | 1150 | 0 | 10 | 482.9107 | 0 | 0 | 212.9636 | 5.4 | 0 | 1274.0073 | 0 | 0 | 124.0073 | 1.1078 | 20% | 0.25679 | 86100
2 | Commercial Broiler (115,000 - 210,000 kBtu/year) Baseline broiler: 0.808 therms/hr - High efficiency product: 0.658 therms/hr at standard duty cycles. | 4557.084 | 0 | 0 | 3711.0907 |  |  | I | 200 | 0 | 10 | 845.9933 | 0 | 0 | 373.0831 | 0.53607 | 0 | 2231.8861 | 0 | 0 | 2031.8861 | 11.1594 | 18.56% | 2.4018 | 162500
3 | Commercial Oven (62,400 kBtu/year) Baseline oven: Baseline griddle: 30% efficient - High efficiency product: 40% | 1749.9203 | 0 | 0 | 1312.4402 |  |  | I | 1600 | 0 | 10 | 437.4801 | 0 | 0 | 192.9287 | 8.2932 | 0 | 1154.153 | 0 | 0 | -445.847 | 0.72135 | 25% | -1.0191 | 62400
4 | Commercial Gas Fryers (75,000 kBtu/year) Baseline gas range: 35% efficient - High efficiency product: 50% | 2103.2695 | 0 | 0 | 1472.2887 |  |  | I | 1100 | 0 | 10 | 630.9809 | 0 | 0 | 278.2626 | 3.9531 | 0 | 1664.6437 | 0 | 0 | 564.6437 | 1.5133 | 30% | 0.89487 | 75000
5 | Efficient Gas Kitchen Appliances Measure | 10824.8272 | 0 | 0 | 8864.9424 |  |  | I | 2450 | 0 | 10 | 1959.8849 | 0 | 0 | 864.3092 | 2.8346 | 0 | 5170.5372 | 0 | 0 | 2720.5372 | 2.1104 | 18.11% | 1.3881
6 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -900 | 0
Service Region: |  | Northern
Measure Type: |  | Baseload
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 3.6619 | 0.4
Electricity ($/kWh) |  | 0.8175 | 0.1
Water ($/1000L) |  | 17.1078 | 1.75
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
Griddle | 1. Griddles evaluated at 12 hours per day, 6 days per week and a duty cycle of 34% (Food Service Technology Center, 2002).
Gives baseline use is 86,100 kBtu/yr (Food Service Technology Centre, 2002)
2. The upgrade has a cooking efficiency of 40% (US ENERGYSTAR)
3. The baseline griddle unit has a cooking efficiency of 32% (US ENERGYSTAR), assumed improvements in same proportion to idling energy use.
4. The griddle costs are based on US ENERGY STAR calculator assumptions
- Standard efficiency unit $2000
- High efficiency unit: $3150
5. The service life of a griddle is 10 years.
Broiler | 1. Broilers evaluated at 8 hours per day, 6 days per week and a duty cycle of 70-80% (Food Service Technology Center, 2002).
Gives baseline use is 115,000 - 210,000 kBtu/yr dependingon eqiupment type (Food Service Technology Centre, 2002)
2. The upgrade has an average energy use of 0.658 Therms/h (US ENERGYSTAR)
3. The baseline broiler has an average energy use of 0.808 Therms/h (US ENERGYSTAR)
4. The broiler costs are based on US ENERGY STAR calculator assumptions
- Standard efficiency unit $2300
- High efficiency unit: $2500
5. The service life of a broiler is 10 years (US ENERGY STAR).
Oven | 1. Ovens evaluated at 8 hours per day, 6 days per week and a duty cycle of 35% (Food Service Technology Center, 2002).
Gives baseline use is 62,400 kBtu/yr for standard size ovens (standard/convection and combination) (Food Service Technology Centre, 2002)
2. The upgrade has a cooking efficiency of 40% (ENERGYSTAR)
3. The baseline oven has a cooking efficiency of 30% (ENERGYSTAR), assumed improvements in same proportion to idling energy use.
4. The oven costs are based on US ENERGY STAR calculator assumptions
- Standard efficiency unit $2800
- High efficiency unit: $4400
5. The service life of an oven is 10 years.
Fryer | 1. Fryers evaluated at 12 hours per day, 6 days per week and a duty cycle of 20% (Food Service Technology Center, 2002).
Gives baseline use is 75,000 kBtu/yr for standard size fryer ("open" deep fat type) (Food Service Technology Centre, 2002)
2. The upgrade has a cooking efficiency of 50% (ENERGYSTAR)
3. The baseline oven has a cooking efficiency of 35% (ENERGYSTAR), assumed improvements in same proportion to idling energy use.
4. The oven costs are based on US ENERGY STAR calculator assumptions
- Standard efficiency unit $2200
- High efficiency unit: $3300
5. The service life of a fryer is 10 years (US ENERGY STAR).
Note on B19: Chris Pulfer: Average of above four measures (Weighted by average yearly use)

## Recommissioning
Building Recommissioning
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 1.5869 | 0.441
Electricity ($/kWh) |  | 0.34604 | 0.11124
Water ($/1000L) |  | 7.2724 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Recommisioning - baseline is a large office buiding with a gas EUI of 16 m3/m2.yr and an electric EUI of 190 kWh/m2.yr | 16 | 190 | 0 | 13.6 | 161.5 |  | F | 3.766 | 0 | 5 | 2.4 | 28.5 | 0 | 4.2287 | 0.89059 | 0 | 3.8087 | 9.8622 | 0 | 9.9049 | 3.6301 | 15% | 4.127
2 | [9 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | F |  | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. Savings based on 15% of total building energy use.
2. Costs are $0.35 per square foot based on 2004 LBNL study of retrocommissioning
3. The service life is estimated to be 5 years based on recommended cycle for recommissioning
4. The analysis is based on one m2 of floor area.

## Advanced BAS
Advanced Building Automation Systems
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 2.6321 | 0.441
Electricity ($/kWh) |  | 0.58464 | 0.11124
Water ($/1000L) |  | 12.2336 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | Advanced BAS - baseline is a large office buiding with a gas EUI of 16 m3/m2.yr and an electric EUI of 190 kWh/m2.yr | 16 | 190 | 0 | 14.4 | 171 |  | F | 9.684 | 0 | 10 | 1.6 | 19 | 0 | 2.8191 | 3.4351 | 0 | 4.2113 | 11.1083 | 0 | 5.6356 | 1.5819 | 10% | 3.5222
2 | [9 empty] | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
3 | [9 empty] | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | F |  | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
Installation of an advanced BAS or upgrade with new front-end, automated diagnosis and
new control strategies. In this analysis savings of 10% of the whole building EUI are estimated through
re-institution of equipment scheduling, expanded control (lighting) and improved self-tuning control
strategies.
The costs of an advanced BAS is based on $900 per control point and the and the additional of 1 point per 1,000 ft2 to provide DDC room controls (terminal devices), lighting control
and augmented control of central plants and air handling systems.
The service life is estimated to be 10 years.
The analysis is based on one m2 of floor area.

## HP New Construction
High Performance New Construction
Service Region: |  | Southern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.441
Electricity ($/kWh) |  | 0.93106 | 0.11124
Water ($/1000L) |  | 19.5021 | 3.05
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy & Water Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV O&M Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio |  | TRC/m3
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | High Performane New Construction (25% more efficient) - baseline is a new office buiding with a gas EUI of 12 m3/m2.yr and an electric EUI of 160 kWh/m2.yr | 12 | 160 | 0 | 9 | 120 |  | I | 26.9 | 0 | 25 | 3 | 40 | 0 | 5.7725 | 4.66 | 0 | 12.4242 | 37.2423 | 0 | 22.7664 | 1.8463 | 25% | 7.5888
2 | High Performane New Construction (40% more efficient) - baseline is a newe office buiding with a gas EUI of 12 m3/m2.yr and an electric EUI of 160 kWh/m2.yr | 12 | 160 | 0 | 7.2 | 88 |  | I | 48.42 | 0 | 25 | 4.8 | 72 | 0 | 10.1259 | 4.7818 | 0 | 19.8787 | 67.0361 | 0 | 38.4947 | 1.795 | 40% | 8.0197
3 | [9 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[10 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
[8 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | #DIV/0!
7 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
8 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
9 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
10 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
11 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
12 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
13 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
14 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
15 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
16 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
17 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
18 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
19 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
20 | [7 empty] | I |  | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
Service Region: |  | Northern
Measure Type: |  | Weather
Assumed Discount Rate: |  | 10%
Adjustment Factor: |  | 100%
Free Rider Rate: |  | 0%
Resource Costs:
|  | Avoided Cost (NPV) | Customer Cost
Natural Gas ($/m3) |  | 4.1414 | 0.466
Electricity ($/kWh) |  | 0.93106 | 0.10323
Water ($/1000L) |  | 19.5021 | 2.25
Measure Description |  | Baseline Consumption |  |  | Upgrade Energy Use |  |  | Installed Cost F=full; I=Incr. |  | Incr. O&M ($/yr) | Measure Life (yrs) | Annual Energy Savings |  |  | Annual Savings ($) | Simple Payback (Yrs) | NPV Maintenance Cost ($) | Total Benefits, Not Adjusted for Free Ridership or Adjustment Factor |  |  | Adjusted Measure TRC ($) | Adjusted Benefit/Cost Ratio
|  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  |  | Nat. Gas (m3/yr) | Elec. (kWh/yr) | Water (L/yr) |  |  |  | Nat. Gas | Elec. | Water
1 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
2 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
3 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
4 | [9 empty] | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A
5 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
6 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
7 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
8 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
9 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
10 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
11 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
12 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
13 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
14 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
15 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
16 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
17 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
18 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
19 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
20 | [7 empty] | I | 900 | 0 | 25 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | -900 | 0
Notes:
1. New commercial construction with a performance of 25% better than current practice has incremental cost of $2.50/sqft based on 1.7% premium and $150/sqft for office buildings.
2. New commercial construction with a performance of 40% better than current practice has an incremental cost of $4.50/sqft based on 3% premium and $150/sqft for office buidings.
3. The service life is estimated to be 25 years.
4. The analysis is based on one m2 of floor area.
5. Ref: The Costs and Financial Benefits of Green Buildings: A Report of California's Sustainable Building Task Force, October 2003.

## Example Report Exhibit
Exhbit 4.x Summary of Measures TRC Screening Results - Southern Region
Measure Name | Target Market |  |  |  | Simple Payback (Yrs) | Measure TRC | B/C Ratio
| Service Region | Sub Sector(s) | Vintage | Full/Incr
Air Sealing | S | SD/Dupl | Existing | Full | 6.8931 | 48.6938 | 1.0541
|  | Row | Existing | Full | 12.6257 | -379.5648 | 0.57826
|  | SD/Dupl | New | Incr. | 7.094 | 28.8686 | 1.0412
|  | Row | New | Incr. | 9.5046 | -162.7528 | 0.7675
Attic Insulation | LM | SD/Dupl | Existing | Full | 15.3181 | -989.8161 | 0.010184
|  | Row | Existing | Full | 28.057 | -993.2107 | 0.0067893
Wall Insulation | LM | SD/Dupl | Existing | Full | 17.6747 | -2477.9349 | 0.008826
|  | Row | Existing | Full | 32.3735 | -2485.2899 | 0.005884
Foundation Insulation | LM | SD/Dupl | Existing | Full | 20.8883 | -2481.3296 | 0.0074682
|  | Row | Existing | Full | 38.2596 | -2487.553 | 0.0049788
Crawl-space Upgrade | LM | SD/Dupl | Existing | Full | 112.3324 | -1098.4724 | 0.0013887
|  | Row | Existing | Full | 205.7517 | -1098.9816 | 0.00092581
Vacuum Panel Insulation | LM | SD/Dupl | Existing | Full | 34.1899 | -7215.6102 | 0.22413
|  | Row | Existing | Full | 62.6233 | -8156.5438 | 0.12295
|  | SD/Dupl | New | Incr. | 45.2396 | -7698.5915 | 0.17219
|  | Row | New | Incr. | 60.6123 | -8119.6058 | 0.12692
High Performance Windows | S | SD/Dupl | Existing | Incr. | 36.7633 | -1899.7464 | 0.20844
|  | Row | Existing | Incr. | 67.3369 | -2125.5705 | 0.11435
|  | SD/Dupl | New | Incr. | 6.0806 | 309.2395 | 1.2811
|  | Row | New | Incr. | 8.1468 | -61.2531 | 0.94432
High Performance Windows |  | SD/Dupl | Existing | Incr. | 45.9542 | -4166.2441 | 0.16675
|  | Row | Existing | Incr. | 84.1711 | -4542.6175 | 0.091476
|  | SD/Dupl | New | Incr. | 20.2687 | -3078.3098 | 0.38434
|  | Row | New | Incr. | 27.156 | -3583.527 | 0.28329
R2000 Construction |  | SD/Dupl | New | Incr. | 26.3493 | -6432.1075 | 0.010445
|  | Row | New | Incr. | 35.3029 | -6466.0537 | 0.0052225
Energuide 80 Construction |  | SD/Dupl | New | Incr. | 15.4042 | -3732.1075 | 0.017866
|  | Row | New | Incr. | 20.6386 | -3766.0537 | 0.0089332
Furnace Efficiency Upgrade | S | SD/Dupl | Existing | Incr. | 3.7522 | 379.3544 | 1.6323
|  | Row | Existing | Incr. | 6.9259 | -69.4256 | 0.88429
|  | SD/Dupl | New | Incr. | 5.1714 | 110.5883 | 1.1843
|  | Row | New | Incr. | 6.7873 | -58.5873 | 0.90235
Boiler Efficiency Upgrade |  | SD/Dupl | Existing | Incr. | 24.3002 | -2392.3978 | 0.25238
|  | Row | Existing | Incr. | 44.8341 | -2762.1426 | 0.13683
|  | SD/Dupl | New | Incr. | 32.9803 | -2604.3052 | 0.18615
|  | Row | New | Incr. | 43.3382 | -2747.0538 | 0.14155
High Efficiency Heat Recovery Ventilator |  | SD/Dupl | Existing | Incr. | 9.5108 | -267.7109 | 0.58814
|  | Row | Existing | Incr. | 17.5553 | -442.8913 | 0.31863
|  | SD/Dupl | New | Incr. | 12.9285 | -368.7708 | 0.43266
|  | Row | New | Incr. | 16.9682 | -435.7254 | 0.32965
Integrated Heating and DHW | S | SD/Dupl | Existing | Incr. | 3.0358 | 568.9674 | 2.1379
|  | Row | Existing | Incr. | 5.112 | 138.1707 | 1.2763
|  | SD/Dupl | New | Incr. | 3.7366 | 392.5206 | 1.785
|  | Row | New | Incr. | 5.0147 | 149.9573 | 1.2999
Gas-fired Heat Pump |  | SD/Dupl | Existing | Incr. | 14.4102 | -2874.9351 | 0.42501
|  | Row | Existing | Incr. | 26.599 | -3848.7263 | 0.23025
|  | SD/Dupl | New | Incr. | 19.5886 | -3436.7057 | 0.31266
|  | Row | New | Incr. | 25.7094 | -3808.8921 | 0.23822
Low-Flow Showerheads and Faucets | S | SD/Dupl | Existing | Full | 0.97246 | 81.9415 | 4.2777
|  | Row | Existing | Full | 1.2234 | 60.0064 | 3.4003
DHW Heat Trap | S | SD/Dupl | Existing | Full | 2.6548 | 48.6608 | 1.7486
|  | Row | Existing | Full | 3.3399 | 25.3475 | 1.39
|  | SD/Dupl | New | Full | 2.709 | 46.3876 | 1.7137
|  | Row | New | Full | 3.408 | 23.5405 | 1.3622
Condensing Water Heater |  | SD/Dupl | Existing | Incr. | 17.0181 | -977.9427 | 0.21765
|  | Row | Existing | Incr. | 21.4095 | -1033.7452 | 0.173
|  | SD/Dupl | New | Incr. | 17.3654 | -983.3838 | 0.21329
|  | Row | New | Incr. | 21.8464 | -1038.0703 | 0.16954
DHW Pipe Insulation | S | SD/Dupl | Existing | Full | 0.54458 | 14.7433 | 4.6858
|  | Row | Existing | Full | 0.6851 | 10.8988 | 3.7247
|  | SD/Dupl | New | Full | 0.55569 | 14.3684 | 4.5921
|  | Row | New | Full | 0.69909 | 10.6008 | 3.6502
Instantaneous (in-line) Water Heater |  | SD/Dupl | Existing | Incr. | 10.2109 | -332.9605 | 0.52434
|  | Row | Existing | Incr. | 12.8457 | -408.2451 | 0.41679
|  | SD/Dupl | New | Incr. | 10.4193 | -340.3013 | 0.51386
|  | Row | New | Incr. | 13.1079 | -414.0802 | 0.40846
Waste Water Heat Recovery |  | SD/Dupl | Existing | Full | 16.2077 | -428.9932 | 0.31361
|  | Row | Existing | Full | 20.39 | -469.1968 | 0.24929
|  | SD/Dupl | New | Full | 16.5385 | -432.9134 | 0.30734
|  | Row | New | Full | 20.8061 | -472.3129 | 0.2443
Solar Orphans Program |  | SD/Dupl | Existing | Full | 5.1054 | -137.2569 | 0.72549
|  | Row | Existing | Full | 6.4228 | -211.6603 | 0.57668
Energy Star Dishwasher | S | SD/Dupl | Existing | Incr. | 0 | 67.3084 | N/A
|  | Row | Existing | Incr. | 0 | 53.2944 | N/A
|  | SD/Dupl | New | Incr. | 0 | 64.5812 | N/A
|  | Row | New | Incr. | 0 | 51.1606 | N/A
Best Available Dishwasher |  | SD/Dupl | Existing | Incr. | 23.7446 | -482.2104 | 0.19632
|  | Row | Existing | Incr. | 29.9404 | -506.7348 | 0.15544
|  | SD/Dupl | New | Incr. | 24.5322 | -486.983 | 0.18836
|  | Row | New | Incr. | 30.9238 | -510.4689 | 0.14922
Energy Star Clothes Washer | S | SD/Dupl | Existing | Incr. | 2.5953 | 84.7188 | 1.8472
|  | Row | Existing | Incr. | 3.3009 | 44.9218 | 1.4492
|  | SD/Dupl | New | Incr. | 2.6642 | 78.9194 | 1.7892
|  | Row | New | Incr. | 3.3874 | 40.4472 | 1.4045
Horizontal Axis Clothes Washer |  | SD/Dupl | Existing | Incr. | 9.5041 | -251.2149 | 0.49757
|  | Row | Existing | Incr. | 12.0525 | -304.1527 | 0.39169
|  | SD/Dupl | New | Incr. | 9.7406 | -258.2956 | 0.48341
|  | Row | New | Incr. | 12.3494 | -309.6458 | 0.38071
Insulating Pool Cover | S | SD/Dupl | Existing | Full | 1.5895 | 465.581 | 2.3302
|  | SD/Dupl | New | Full | 1.5895 | 465.581 | 2.3302
High Efficiency Pool Heater |  | SD/Dupl | Existing | Incr. | 38.4976 | -2550.2978 | 0.12059
|  | SD/Dupl | New | Incr. | 38.4976 | -2550.2978 | 0.12059
Solar Pool Heater |  | SD/Dupl | Existing | Incr. | 12.7161 | -2480.5238 | 0.29128
|  | SD/Dupl | New | Incr. | 12.7161 | -2480.5238 | 0.29128
Energy Efficient Fireplace | S | SD/Dupl | Existing | Incr. | 2.9258 | 88.0034 | 1.5867
|  | Row | Existing | Incr. | 2.9258 | 88.0034 | 1.5867
|  | SD/Dupl | New | Incr. | 2.9258 | 88.0034 | 1.5867
|  | Row | New | Incr. | 2.9258 | 88.0034 | 1.5867

## Drop-Down Menus (hidden)
Type of Measure
Baseload
Weather

## Tech Profile Summary
Measure Information |  |  | Applicability |  |  |  | Life | Cost | Measure TRC ($/m3) | Economic Screen | Basis | Savings by End Use | [19 empty] | Reference and Max Penetration | [6 empty] | Economic Penetration | [5 empty] | Default Participation Rates
Measure # | Technology | Climate Zone | Building Type(s) | Exist | Reno | New | [5 empty] | Food Services | Space Heating | Space Cooling | Domestic Hot Water | Other | Enduses | Enduses | Enduses | Enduses | Enduses | Enduses | Enduses | Enduses | Enduses | Enduses | Enduses | Enduses | Enduses | Enduses | Enduses | Starting in 2007 | 2012 | 2017 | 2022 | 2027 | 2032 | Maximum Technical | Starting in 2007 | 2012 | 2017 | 2022 | 2027 | 2032 | Maximum Technical | Starting in 2007 | 2012 | 2017 | 2022 | 2027 | Notes
1 | Efficient Food Service Equipment | 1 | All Buildings | y | y |  | 10 | 2450 | 1.3881 | Pass | Incr | 18.11% |  |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 40% | 80% |  |  |  | 0% | 10% | 20% |  |  |  | This measure aggregates all individual cooking measures analysed which passedd the measure TRC test. | Independent envelope savings |  | Windows | Roof | % windows | % roof | base
2 | Space Heating - Envelope measures (Conductive) | 2 | Large Office | y | y |  | 28.2486 |  | 1.6001 | Pass | Incr |  | 15.88% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 50% | 0% | 8.85% | 17.7% |  |  |  | 0% | 10% | 20% | [6 empty] | 182.1 | 239.6 | 82.49% | 17.51% | 255.1
3 | Space Heating - Envelope measures (Conductive) | 1 | Small Office | y | y |  | 27.9105 |  | 1.5531 | Pass | Incr |  | 28.65% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 16.12% | 32.25% |  |  |  | 0% | 10% | 20% | [6 empty] | 446.7 | 545.6 | 79.11% | 20.89% | 581.1
4 | Space Heating - Envelope measures (Conductive) | 2 | Retail | y | y |  | 24.5626 |  | 1.0883 | Pass | Incr |  | 25.44% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 18.32% | 36.64% |  |  |  | 0% | 10% | 20% | [6 empty] | 310.9 | 298.4 | 45.63% | 54.37% | 376.1
5 | Space Heating - Envelope measures (Conductive) | 1 | Large Hotel | y | y |  | 28.5691 |  | 1.6446 | Pass | Incr |  | 15.69% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 14% | 28% |  |  |  | 0% | 10% | 20% | [6 empty] | 97.3 | 140.7 | 85.69% | 14.31% | 149.4
6 | Space Heating - Envelope measures (Conductive) | 2 | Small Hotel/Motel | y | y |  | 25.9724 |  | 1.2841 | Pass | Incr |  | 25.22% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 17.33% | 34.65% |  |  |  | 0% | 10% | 20% | [6 empty] | 285.3 | 306.4 | 59.72% | 40.28% | 350.1
7 | Space Heating - Envelope measures (Conductive) | 1 | Contract Hospital | y | y |  | 28.456 |  | 1.6289 | Pass | Incr |  | 3.672% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 15.81% | 31.63% |  |  |  | 0% | 10% | 20% | [6 empty] | 128.3 | 166.8 | 84.56% | 15.44% | 175.4
8 | Space Heating - Envelope measures (Conductive) | 2 | Hospital | y | y |  | 28.5538 |  | 1.6425 | Pass | Incr |  | 5.431% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 15.76% | 31.52% |  |  |  | 0% | 10% | 20% | [6 empty] | 186.6 | 244.1 | 85.54% | 14.46% | 255.8
9 | Space Heating - Envelope measures (Conductive) | 1 | Nursing Home | y | y |  | 27.6541 |  | 1.5175 | Pass | Incr |  | 9.134% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 16.27% | 32.54% |  |  |  | 0% | 10% | 20% | [6 empty] | 175.7 | 206.7 | 76.54% | 23.46% | 220.4
10 | Space Heating - Envelope measures (Conductive) | 2 | School | y | y |  | 28.2848 |  | 1.6051 | Pass | Incr |  | 9.274% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 15.91% | 31.82% |  |  |  | 0% | 10% | 20% | [6 empty] | 203.9 | 246.8 | 82.85% | 17.15% | 258
11 | Space Heating - Envelope measures (Conductive) | 1 | Contract University/College | y | y |  | 27.7019 |  | 1.5242 | Pass | Incr |  | 8.753% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 16.24% | 32.49% |  |  |  | 0% | 10% | 20% | [6 empty] | 195.1 | 221.2 | 77.02% | 22.98% | 232.3
12 | Space Heating - Envelope measures (Conductive) | 2 | University/College | y | y |  | 27.8544 |  | 1.5454 | Pass | Incr |  | 8.768% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 16.16% | 32.31% |  |  |  | 0% | 10% | 20% | [6 empty] | 192.6 | 222.4 | 78.54% | 21.46% | 233.6
13 | Space Heating - Envelope measures (Conductive) | 1 | Restaurant/Food Service | y | y |  | 28.0382 |  | 1.5709 | Pass | Incr |  | 14.71% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 16.05% | 32.1% |  |  |  | 0% | 10% | 20% | [6 empty] | 454.7 | 559.7 | 80.38% | 19.62% | 593.6
14 | Space Heating - Envelope measures (Conductive) | 2 | Warehouse | y | y |  | 21.6667 |  | 0.68626 | Pass | Incr |  | 5.637% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 20.77% | 41.54% |  |  |  | 0% | 10% | 20% | [6 empty] | 420.7 | 395.9 | 16.67% | 83.33% | 426.9
15 | Space Heating - Envelope measures (Conductive) | 1 | Contract Apartment | y | y |  | 28.9364 |  | 1.6956 | Pass | Incr |  | 13.66% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 15.55% | 31.1% |  |  |  | 0% | 10% | 20% | [6 empty] | 217 | 277.7 | 89.36% | 10.64% | 285.9
16 | Space Heating - Envelope measures (Conductive) | 2 | Highrise Apartment | y | y |  | 28.9364 |  | 1.6956 | Pass | Incr |  | 13.66% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 15.55% | 31.1% |  |  |  | 0% | 10% | 20% | [6 empty] | 217 | 277.7 | 89.36% | 10.64% | 285.9
17 | Space Heating - Envelope measures (Conductive) | 1 | Midrise Apartment | y | y |  | 29.1651 |  | 1.7273 | Pass | Incr |  | 27.02% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 90% | 0% | 15.43% | 30.86% |  |  |  | 0% | 10% | 20% | [6 empty] | 438.1 | 574.8 | 91.65% | 8.349% | 588.5
18
19
20
21
22
23
24 | Space Heating - Envelope measures - Air Sealing | 2 | Large Office | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 4% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
25 | Space Heating - Envelope measures - Air Sealing | 1 | Small Office | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 2% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20% | [5 empty] | weighted |  |  | 1006531.3342 | 440512.3304
26 | Space Heating - Envelope measures - Air Curtains | 2 | Retail | y | y |  | 15 |  | 0.8623 | Pass | Full |  | 4% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20% | [5 empty] | weighted % savings |  |  | 0.69558 | 0.30442
27 | Space Heating - Envelope measures - Air Sealing | 1 | Large Hotel | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 3% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
28 | Space Heating - Envelope measures - Air Sealing | 2 | Small Hotel/Motel | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 2% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
29 | Space Heating - Envelope measures - Air Sealing | 1 | Contract Hospital | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 1% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
30 | Space Heating - Envelope measures - Air Sealing | 2 | Hospital | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 1% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
31 | Space Heating - Envelope measures - Air Sealing | 1 | Nursing Home | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 2% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
32 | Space Heating - Envelope measures - Air Sealing | 2 | School | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 2% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
33 | Space Heating - Envelope measures - Air Sealing | 1 | Contract University/College | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 2% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
34 | Space Heating - Envelope measures - Air Sealing | 2 | University/College | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 2% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
35 | Space Heating - Envelope measures - Air Sealing | 1 | Restaurant/Food Service | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 0.5% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
36 | Space Heating - Envelope measures - Air Curtains | 2 | Warehouse | y | y |  | 15 |  | 0.8623 | Pass | Full |  | 5% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
37 | Space Heating - Envelope measures - Air Sealing | 1 | Contract Apartment | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 3% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
38 | Space Heating - Envelope measures - Air Sealing | 2 | Highrise Apartment | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 3% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
39 | Space Heating - Envelope measures - Air Sealing | 1 | Midrise Apartment | y | y |  | 6 |  | 0.16169 | Pass | Full |  | 2% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 80% | 0% | 80% | 80% |  |  |  | 0% | 10% | 20%
40 |  | 2 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
41 |  | 1 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
42 |  | 2 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
43 |  | 1 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
44 |  | 2 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
45 |  | 1 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
46 | Space Heating - Ventilation Measures - DCV | 2 | Large Office | y | y |  | 15 |  | 2.3453 | Pass | Full |  | 12% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 65% | 0% | 65% | 65% |  |  |  | 0% | 10% | 20%
47 | Space Heating - Ventilation Measures - DCV | 1 | Small Office | y | y |  | 15 |  | 2.3453 | Pass | Full |  | 12% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 50% | 0% | 50% | 50% |  |  |  | 0% | 10% | 20%
48 | Space Heating - Ventilation Measures - Heat Recovery | 2 | Retail | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 5% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 60% | 0% | 20% | 40% |  |  |  | 0% | 10% | 20%
49 | Space Heating - Ventilation Measures - Heat Recovery | 1 | Large Hotel | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 25% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 60% | 0% | 20% | 40% |  |  |  | 0% | 10% | 20%
50 | Space Heating - Ventilation Measures - Heat Recovery | 2 | Small Hotel/Motel | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 5% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 60% | 0% | 20% | 40% |  |  |  | 0% | 10% | 20%
51 | Space Heating - Ventilation Measures - Heat Recovery | 1 | Contract Hospital | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 32% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 40% | 0% | 13.33% | 26.67% |  |  |  | 0% | 10% | 20%
52 | Space Heating - Ventilation Measures - Heat Recovery | 2 | Hospital | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 32% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 50% | 0% | 16.67% | 33.33% |  |  |  | 0% | 10% | 20%
53 | Space Heating - Ventilation Measures - Heat Recovery | 1 | Nursing Home | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 30% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 50% | 0% | 16.67% | 33.33% |  |  |  | 0% | 10% | 20%
54 | Space Heating - Ventilation Measures - DCV | 2 | School | y | y |  | 15 |  | 2.3453 | Pass | Full |  | 15% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 50% | 0% | 50% | 50% |  |  |  | 0% | 10% | 20%
55 | Space Heating - Ventilation Measures - Heat Recovery | 1 | Contract University/College | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 25% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 65% | 0% | 21.67% | 43.33% |  |  |  | 0% | 10% | 20%
56 | Space Heating - Ventilation Measures - Heat Recovery | 2 | University/College | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 25% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 65% | 0% | 21.67% | 43.33% |  |  |  | 0% | 10% | 20%
57 | Space Heating - Ventilation Measures - DCKV | 1 | Restaurant/Food Service | y | y |  | 20 |  | 4.8506 | Pass | Full |  | 21% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 65% | 0% | 65% | 65% |  |  |  | 0% | 10% | 20%
58 | Space Heating - Ventilation Measures - Heat Recovery | 2 | Warehouse | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 15% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 65% | 0% | 21.67% | 43.33% |  |  |  | 0% | 10% | 20%
59 | Space Heating - Ventilation Measures - Heat Recovery | 1 | Contract Apartment | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 20% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 65% | 0% | 21.67% | 43.33% |  |  |  | 0% | 10% | 20%
60 | Space Heating - Ventilation Measures - Heat Recovery | 2 | Highrise Apartment | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 20% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 65% | 0% | 21.67% | 43.33% |  |  |  | 0% | 10% | 20%
61 | Space Heating - Ventilation Measures - Heat Recovery | 1 | Midrise Apartment | y | y |  | 15 |  | 1.8228 | Pass | Incr |  | 10% |  |  |  | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 50% | 0% | 16.67% | 33.33% |  |  |  | 0% | 10% | 20%
62 |  | 2 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
63 |  | 1 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
64 |  | 2 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
65 |  | 1 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
66 |  | 2 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
67 |  | 1 | [14 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
68 | Space Heating / Other - Recommissioning | 2 | Large Office | y | y |  | 5 |  | 4.127 | Pass | Full |  | 15% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
69 | Space Heating / Other - Recommissioning | 1 | Small Office | y | y |  | 5 |  | 4.127 | Pass | Full |  | 15% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
70 | Space Heating / Other - Recommissioning | 2 | Retail | y | y |  | 5 |  | 4.127 | Pass | Full |  | 15% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
71 | Space Heating / Other - Recommissioning | 0 | Large Hotel | y | y |  | 5 |  | 4.127 | Pass | Full |  | 15% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
72 | Space Heating / Other - Recommissioning | 0 | Small Hotel/Motel | y | y |  | 5 |  | 4.127 | Pass | Full |  | 15% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
73 | Space Heating / Other - Recommissioning & Steam system measures | 0 | Contract Hospital | y | y |  | 5 |  | 4.127 | Pass | Full |  | 20% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
74 | Space Heating / Other - Recommissioning & Steam system measures | 0 | Hospital | y | y |  | 5 |  | 4.127 | Pass | Full |  | 20% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
75 | Space Heating / Other - Recommissioning | 0 | Nursing Home | y | y |  | 5 |  | 4.127 | Pass | Full |  | 15% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
76 | Space Heating / Other - Recommissioning | 0 | School | y | y |  | 5 |  | 4.127 | Pass | Full |  | 15% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
77 | Space Heating / Other - Recommissioning & Steam system measures | 0 | Contract University/College | y | y |  | 5 |  | 4.127 | Pass | Full |  | 20% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
78 | Space Heating / Other - Recommissioning & Steam system measures | 0 | University/College | y | y |  | 5 |  | 4.127 | Pass | Full |  | 20% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
79 | Space Heating / Other - Recommissioning | 0 | Restaurant/Food Service | y | y |  | 5 |  | 4.127 | Pass | Full |  | 15% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
80 | Space Heating / Other - Recommissioning & De-strat fans | 0 | Warehouse | y | y |  | 5 |  | 4.127 | Pass | Full |  | 19% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
81 | Space Heating / Other - Recommissioning & Reflector Panels | 0 | Contract Apartment | y | y |  | 5 |  | 4.127 | Pass | Full |  | 17% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
82 | Space Heating / Other - Recommissioning & Reflector Panels | 0 | Highrise Apartment | y | y |  | 5 |  | 4.127 | Pass | Full |  | 17% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
83 | Space Heating / Other - Recommissioning & Reflector Panels | 0 | Midrise Apartment | y | y |  | 5 |  | 4.127 | Pass | Full |  | 17% | 15% |  | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 95% | 95% |  |  |  | 0% | 10% | 20%
84 |  | 0 | [35 empty] | 95%
85 |  | 0 | [35 empty] | 95%
86 |  | 0 | [35 empty] | 95%
87 |  | 0 | [35 empty] | 95%
88 |  | 0 | [35 empty] | 95%
89 |  | 0 | [35 empty] | 95%
90 | Space Heating - Equipment | 0 | Large Office | y | y |  | 20 |  | 3 | Pass | Incr |  | 13.58% |  |  | 13.58% | 0% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
91 | Space Heating - Equipment | 0 | Small Office | y | y |  | 20 |  | 3 | Pass | Incr |  | 13.73% |  |  | 13.73% | 0% | 0% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
92 | Space Heating - Equipment | 0 | Retail | y | y |  | 20 |  | 3 | Pass | Incr |  | 14.08% |  |  | 14.08% | 0% | 0% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
93 | Space Heating - Equipment | 0 | Large Hotel | y | y |  | 20 |  | 3 | Pass | Incr |  | 14.21% |  |  | 14.21% | 0% | 0% | 0% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
94 | Space Heating - Equipment | 0 | Small Hotel/Motel | y | y |  | 20 |  | 3 | Pass | Incr |  | 14.35% |  |  | 14.35% | 0% | 0% | 0% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
95 | Space Heating - Equipment | 0 | Contract Hospital | y | y |  | 20 |  | 3 | Pass | Incr |  | 2.696% |  |  | 2.696% | 0% | 0% | 0% | 0% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
96 | Space Heating - Equipment | 0 | Hospital | y | y |  | 20 |  | 3 | Pass | Incr |  | 2.696% |  |  | 2.696% | 0% | 0% | 0% | 0% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
97 | Space Heating - Equipment |  | Nursing Home | y | y |  | 20 |  | 3 | Pass | Incr |  | 12.93% |  |  | 12.93% | [15 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
98 | Space Heating - Equipment |  | School | y | y |  | 20 |  | 3 | Pass | Incr |  | 10.36% |  |  | 10.36% | [15 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
99 | Space Heating - Equipment |  | Contract University/College | y | y |  | 20 |  | 3 | Pass | Incr |  | 5.985% |  |  | 5.985% | [15 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
100 | Space Heating - Equipment |  | University/College | y | y |  | 20 |  | 3 | Pass | Incr |  | 5.985% |  |  | 5.985% | [15 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
101 | Space Heating - Equipment |  | Restaurant/Food Service | y | y |  | 20 |  | 3 | Pass | Incr |  | 14.08% |  |  | 14.08% | [15 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
102 | Space Heating - Equipment |  | Warehouse | y | y |  | 20 |  | 3 | Pass | Incr |  | 15.34% |  |  | 15.34% | [15 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
103 | Space Heating - Equipment |  | Contract Apartment | y | y |  | 20 |  | 3 | Pass | Incr |  | 13.77% |  |  | 13.77% | [15 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
104 | Space Heating - Equipment |  | Highrise Apartment | y | y |  | 20 |  | 3 | Pass | Incr |  | 13.77% |  |  | 13.77% | [15 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
105 | Space Heating - Equipment |  | Midrise Apartment | y | y |  | 20 |  | 3 | Pass | Incr |  | 13.13% |  |  | 13.13% | [15 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 23.75% | 47.5% |  |  |  | 0% | 10% | 20%
106
107
108
109
110
111
112 | DHW - Conservation Measures |  | Large Office | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
113 | DHW - Conservation Measures |  | Small Office | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 50% | 0% | 50% | 50% |  |  |  | 0% | 10% | 20%
114 | DHW - Conservation Measures |  | Retail | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
115 | DHW - Conservation Measures |  | Large Hotel | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
116 | DHW - Conservation Measures |  | Small Hotel/Motel | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 50% | 0% | 50% | 50% |  |  |  | 0% | 10% | 20%
117 | DHW - Conservation Measures |  | Contract Hospital | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
118 | DHW - Conservation Measures |  | Hospital | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
119 | DHW - Conservation Measures |  | Nursing Home | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
120 | DHW - Conservation Measures |  | School | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
121 | DHW - Conservation Measures |  | Contract University/College | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
122 | DHW - Conservation Measures |  | University/College | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
123 | DHW - Conservation Measures |  | Restaurant/Food Service | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
124 | DHW - Conservation Measures |  | Warehouse | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 50% | 0% | 50% | 50% |  |  |  | 0% | 10% | 20%
125 | DHW - Conservation Measures |  | Contract Apartment | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
126 | DHW - Conservation Measures |  | Highrise Apartment | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
127 | DHW - Conservation Measures |  | Midrise Apartment | y | y |  | 10 |  | 5.0135 | Pass | Full |  |  |  | 40% | [16 empty] | 0% | 0% | 0% |  |  |  | 75% | 0% | 75% | 75% |  |  |  | 0% | 10% | 20%
128 | [14 empty] | #DIV/0!
129 | [14 empty] | #DIV/0!
130 | [14 empty] | #DIV/0!
131 | [14 empty] | #DIV/0!
132 | [14 empty] | #DIV/0!
133 | [14 empty] | #DIV/0!
134 | DHW - Equipment Measures |  | Large Office | y | y |  | 16.1096 |  | 1.9207 | Pass | Incr |  |  |  | 25.03% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 29.49% | 58.97% |  |  |  | 0% | 10% | 20%
135 | DHW - Equipment Measures |  | Small Office | y | y |  | 15.2082 |  | 1.8784 | Pass | Incr |  |  |  | 26.68% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 31.23% | 62.47% |  |  |  | 0% | 10% | 20%
136 | DHW - Equipment Measures |  | Retail | y | y |  | 15.1656 |  | 1.8764 | Pass | Incr |  |  |  | 29.38% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 31.32% | 62.64% |  |  |  | 0% | 10% | 20%
137 | DHW - Equipment Measures |  | Large Hotel | y | y |  | 22 |  | 2.1966 | Pass | Incr |  |  |  | 17.05% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 21.59% | 43.18% |  |  |  | 0% | 10% | 20%
138 | DHW - Equipment Measures |  | Small Hotel/Motel | y | y |  | 20.7857 |  | 2.1397 | Pass | Incr |  |  |  | 18.3% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 22.85% | 45.7% |  |  |  | 0% | 10% | 20%
139 | DHW - Equipment Measures |  | Contract Hospital | y | y |  | 22.2692 |  | 2.2093 | Pass | Incr |  |  |  | 17.62% | [16 empty] | 0% | 0% | 0% |  |  |  | 50% | 0% | 11.23% | 22.45% |  |  |  | 0% | 10% | 20%
140 | DHW - Equipment Measures |  | Hospital | y | y |  | 22.2692 |  | 2.2093 | Pass | Incr |  |  |  | 17.62% | [16 empty] | 0% | 0% | 0% |  |  |  | 50% | 0% | 11.23% | 22.45% |  |  |  | 0% | 10% | 20%
141 | DHW - Equipment Measures |  | Nursing Home | y | y |  | 20.9492 |  | 2.1474 | Pass | Incr |  |  |  | 18.21% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 22.67% | 45.35% |  |  |  | 0% | 10% | 20%
142 | DHW - Equipment Measures |  | School | y | y |  | 17.6129 |  | 1.9911 | Pass | Incr |  |  |  | 22.37% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 26.97% | 53.94% |  |  |  | 0% | 10% | 20%
143 | DHW - Equipment Measures |  | Contract University/College | y | y |  | 21.0395 |  | 2.1516 | Pass | Incr |  |  |  | 18.56% | [16 empty] | 0% | 0% | 0% |  |  |  | 50% | 0% | 11.88% | 23.76% |  |  |  | 0% | 10% | 20%
144 | DHW - Equipment Measures |  | University/College | y | y |  | 21.0395 |  | 2.1516 | Pass | Incr |  |  |  | 18.56% | [16 empty] | 0% | 0% | 0% |  |  |  | 50% | 0% | 11.88% | 23.76% |  |  |  | 0% | 10% | 20%
145 | DHW - Equipment Measures |  | Restaurant/Food Service | y | y |  | 15.7606 |  | 1.9043 | Pass | Incr |  |  |  | 24.05% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 30.14% | 60.28% |  |  |  | 0% | 10% | 20%
146 | DHW - Equipment Measures |  | Warehouse | y | y |  | 15.45 |  | 1.8898 | Pass | Incr |  |  |  | 26.04% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 30.74% | 61.49% |  |  |  | 0% | 10% | 20%
147 | DHW - Equipment Measures |  | Contract Apartment | y | y |  | 16.8319 |  | 1.9545 | Pass | Incr |  |  |  | 23.84% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 28.22% | 56.44% |  |  |  | 0% | 10% | 20%
148 | DHW - Equipment Measures |  | Highrise Apartment | y | y |  | 16.8319 |  | 1.9545 | Pass | Incr |  |  |  | 23.84% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 28.22% | 56.44% |  |  |  | 0% | 10% | 20%
149 | DHW - Equipment Measures |  | Midrise Apartment | y | y |  | 16.1591 |  | 1.923 | Pass | Incr |  |  |  | 25% | [16 empty] | 0% | 0% | 0% |  |  |  | 95% | 0% | 29.4% | 58.79% |  |  |  | 0% | 10% | 20%
150 |  |  |  |  | y
151 |  |  |  |  | y
152 |  |  |  |  | y
153 |  |  |  |  | y
154 |  |  |  |  | y
155 |  |  |  |  | y
156 | New construction - 40% Better |  | Large Office | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 50% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
157 | New construction - 40% Better |  | Small Office | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 50% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
158 | New construction - 40% Better |  | Retail | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 50% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
159 | New construction - 40% Better |  | Large Hotel | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 50% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
160 | New construction - 40% Better |  | Small Hotel/Motel | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 50% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
161 | New construction - 40% Better |  | Contract Hospital | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 40% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
162 | New construction - 40% Better |  | Hospital | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 40% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
163 | New construction - 40% Better |  | Nursing Home | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 40% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
164 | New construction - 40% Better |  | School | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 50% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
165 | New construction - 40% Better |  | Contract University/College | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 40% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
166 | New construction - 40% Better |  | University/College | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 40% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
167 | New construction - 40% Better |  | Restaurant/Food Service | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 40% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
168 | New construction - 40% Better |  | Warehouse | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 50% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
169 | New construction - 40% Better |  | Contract Apartment | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 40% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
170 | New construction - 40% Better |  | Highrise Apartment | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 40% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
171 | New construction - 40% Better |  | Midrise Apartment | y | y |  | 25 |  | 8.0197 | Pass | Full |  | 40% | 40% | 40% | 40% | [15 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 100% | 100% |  |  |  | 0% | 10% | 20%
172 |  |  |  | y | y | [26 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 0% | 0% |  |  |  | 0% | 10% | 20%
173 |  |  |  | y | y | [26 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 0% | 0% |  |  |  | 0% | 10% | 20%
174 |  |  |  | y | y | [26 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 0% | 0% |  |  |  | 0% | 10% | 20%
175 |  |  |  | y | y | [26 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 0% | 0% |  |  |  | 0% | 10% | 20%
176 |  |  |  | y | y | [26 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 0% | 0% |  |  |  | 0% | 10% | 20%
177 |  |  |  | y | y | [26 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | 0% | 0% |  |  |  | 0% | 10% | 20%
178 |  |  | Large Office | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
179 |  |  | Small Office | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
180 |  |  | Retail | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
181 |  |  | Large Hotel | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
182 |  |  | Small Hotel/Motel | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
183 |  |  | Contract Hospital | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
184 |  |  | Hospital | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
185 |  |  | Nursing Home | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
186 |  |  | School | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
187 |  |  | Contract University/College | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
188 |  |  | University/College | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
189 |  |  | Restaurant/Food Service | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
190 |  |  | Warehouse | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
191 |  |  | Contract Apartment | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
192 |  |  | Highrise Apartment | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
193 |  |  | Midrise Apartment | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
194 |  |  |  | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
195 |  |  |  | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
196 |  |  |  | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
197 |  |  |  | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
198 |  |  |  | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
199 |  |  |  | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
200 |  |  | Large Office | y | y |  |  |  |  | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
201 |  |  | Small Office | [6 empty] | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
202 |  |  | Retail | [6 empty] | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
203 |  |  | Large Hotel | [6 empty] | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
204 |  |  | Small Hotel/Motel | [6 empty] | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
205 |  |  | Contract Hospital | [6 empty] | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
206 |  |  | Hospital | [6 empty] | Pass | [21 empty] | 0% | 0% | 0% |  |  |  | 100% | 0% | #DIV/0! | #DIV/0! |  |  |  | 0% | 10% | 20%
|  |  | Nursing Home | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | School | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Contract University/College | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | University/College | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Restaurant/Food Service | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Warehouse | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Contract Apartment | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Highrise Apartment | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Midrise Apartment | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
[39 empty] | 0% | [5 empty] | 0% | 10% | 20%
[39 empty] | 0% | [5 empty] | 0% | 10% | 20%
[39 empty] | 0% | [5 empty] | 0% | 10% | 20%
[39 empty] | 0% | [5 empty] | 0% | 10% | 20%
[39 empty] | 0% | [5 empty] | 0% | 10% | 20%
[39 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Large Office | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Small Office | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Retail | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Large Hotel | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Small Hotel/Motel | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Contract Hospital | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Hospital | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Nursing Home | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | School | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | Contract University/College | [35 empty] | 0% | [5 empty] | 0% | 10% | 20%
|  |  | University/College | [41 empty] | 0% | 10% | 20%
|  |  | Restaurant/Food Service | [41 empty] | 0% | 10% | 20%
|  |  | Warehouse | [41 empty] | 0% | 10% | 20%
|  |  | Contract Apartment | [41 empty] | 0% | 10% | 20%
|  |  | Highrise Apartment | [41 empty] | 0% | 10% | 20%
|  |  | Midrise Apartment | [41 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%
|  |  | Large Office | [41 empty] | 0% | 10% | 20%
|  |  | Small Office | [41 empty] | 0% | 10% | 20%
|  |  | Retail | [41 empty] | 0% | 10% | 20%
|  |  | Large Hotel | [41 empty] | 0% | 10% | 20%
|  |  | Small Hotel/Motel | [41 empty] | 0% | 10% | 20%
|  |  | Contract Hospital | [41 empty] | 0% | 10% | 20%
|  |  | Hospital | [41 empty] | 0% | 10% | 20%
|  |  | Nursing Home | [41 empty] | 0% | 10% | 20%
|  |  | School | [41 empty] | 0% | 10% | 20%
|  |  | Contract University/College | [41 empty] | 0% | 10% | 20%
|  |  | University/College | [41 empty] | 0% | 10% | 20%
|  |  | Restaurant/Food Service | [41 empty] | 0% | 10% | 20%
|  |  | Warehouse | [41 empty] | 0% | 10% | 20%
|  |  | Contract Apartment | [41 empty] | 0% | 10% | 20%
|  |  | Highrise Apartment | [41 empty] | 0% | 10% | 20%
|  |  | Midrise Apartment | [41 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%
[45 empty] | 0% | 10% | 20%