## Line Losses
Savings due to Line Loss
2005 line loss | 5%
2014 line loss | 3.39%
Reduction in line loss (savings) | 1.61%
2014 cost of power (million) | 155
2014 savings (million) | 2.4955

## DS Decommissioning
Cost per Station
MS / DS Regular Station Inspection and Maintenance (Per Station) | Frequency | People | Hours | Freq | Total Hours | Rate | Sub-Total | Other Costs | Small Vehicel | Large Vehicle | Total Cost | Anuallized Cost
preventative maintenance & testing | 4 years | 4 | 40 | 1 | 160 | 62.4412 | 9990.5898 |  | 600 | 3520 | 14110.5898 | 3527.6474
lawn & grounds mtce | bi weekly in season | 2 | 1.5 | 16 | 48 | 45.2382 | 2171.4316 |  | 600 |  | 2771.4316 | 2771.4316
station inspections, | monthly | 1 | 1 | 12 | 12 | 62.4412 | 749.2942 |  |  | 528 | 1277.2942 | 1277.2942
replacement of silica gel | bi-annual | 1 | 1 | 2 | 2 | 62.4412 | 124.8824 | 200 |  | 176 | 500.8824 | 500.8824
infrared scanning | annual | 2 | 0.5 | 1 | 1 | 62.4412 | 62.4412 | 200 |  | 22 | 284.4412 | 284.4412
transformer oil sampling and testing, | annual | 1 | 1 | 1 | 1 | 62.4412 | 62.4412 | 200 |  | 44 | 306.4412 | 306.4412
battery testing | annual | 1 | 8 | 1 | 8 | 62.4412 | 499.5295 |  |  | 352 | 851.5295 | 851.5295
vegetation control | annual | 1 | 2 | 1 | 2 | 62.4412 | 124.8824 | 600 | 30 |  | 754.8824 | 754.8824
property Taxes (PILS) | annual | 0 | 40 | 2 | 0 | 62.4412 | 0 | 3860 |  |  | 3860 | 3860
insurance | annual | 0 | 40 | 2 | 0 | 62.4412 | 0 | 500 |  |  | 500 | 500
yard cleanup, and minor repairs. | as required | 1 | 2 | 2 | 4 | 62.4412 | 249.7647 |  |  | 176 | 425.7647 | 425.7647
snow Removal ( sidewalk and driveway) | as required | 1 | 1 | 10 | 10 | 62.4412 | 624.4119 | 1000 | 240 |  | 1864.4119 | 1864.4119
[10 empty] | Total | 27507.6688 | 16924.7265
Assumptions part b)
Number of Stations | 6
Total annual savings after these stations retired | 101548.3588
Rates are fully burdened
Based on 2015 labour rates

## Distribution Automation
Avoided costs due to remote switching via Distributed automation | Reclosers in Service | People | Hours | Freq | Total Hours | Rate | Sub-Total | Other Costs | Small Vehicel | Large Vehicle | Total | Anuallized
Avoided Costs by end of 2016 | 40 | 2 | 1 | 80 | 160 | 59.4925 | 9518.8051 |  |  | 3520 | 13038.8051 | 13038.8051
Avoided Costs by end of 2020 | 100 | 2 | 1 | 200 | 400 | 59.4925 | 23797.0128 |  |  | 17600 | 41397.0128 | 41397.0128
Assumptions part b)
Savings will be greater if avoided callout for switching is perform after hours on overtime.
Based on 2015 labour rates
Rates are fully burdened

## Asset Management Software
Asset Management Software | People | Hours | Freq | Total Hours | Rate | Sub-Total | Other Costs | Small Vehicel | Large Vehicle | Total | Anuallized
Staff #1 | 1 | 280 | 1 | 280 | 128.6954 | 36034.726 |  |  |  | 36034.726 | 36034.726
Staff #2 | 1 | 320 | 1 | 320 | 85.2641 | 27284.4986 |  |  |  | 27284.4986 | 27284.4986
Staff #3 | 3 | 80 | 1 | 240 | 68.5829 | 16459.9061 |  |  |  | 16459.9061 | 16459.9061
Staff #4 | 1 | 120 | 1 | 120 | 70.2941 | 8435.2894 |  |  |  | 8435.2894 | 8435.2894
Staff #5 | 1 | 40 | 1 | 40 | 70.2941 | 2811.7631 |  |  |  | 2811.7631 | 2811.7631
|  | 840 | [7 empty] | 91026.1831 | 91026.1831
Assumptions part b)
Based on 2015 labour rates
Rates are fully burdened

## Reduction in 4.16 kV Inventory
The uprating to higher operating voltages that comes with SR investments in overhead and underground lines reduces the requirement for 4.16 kV and 8.32 kV inventory materials. It is expected that total inventory can be reduced by a value of $112,000.

## Savings by Year
| O&M Savings | 2016 | 2017 | 2018 | 2019 | 2020
1) | Station Retirement (5) | 12693.75 | 42312.5 | 71931.25 | 93087.5 | 101550
2) | Distribution Automation | 8000 | 12000 | 20000 | 30000 | 40000
3) | Asset Management Software | $ - | 90000 | 90000 | 90000 | 90000
4) | Reactive based maintenance
| Total O&M Savings | 20693.75 | 144312.5 | 181931.25 | 213087.5 | 231550
4) | WNH has not been able to quantify expected savings from reactive based maintenace.
Total estimated savings in inventory costs of $112,000 are expected as the 4.16 kV distribution system is retired by 2018.”
The intent was to state that there would be a reduction in inventory of $112,000 due to retirement of the 4.16kV distribution.