## 2011 By Feeder
MM/DD/YYYY | Feeder | Code | Customers | Duration Hours | Total Customer Hours of Interruptions | Primary | Secondary | Comments
2011-01-12 | Colb. F2 | 5 | 10 | 0.5 | 5 |  | X | Lead burnt off
2011-01-14 | F28-1 | 5 | 1000 | 0.5 | 500 | X |  | Breaker tripped
2011-01-14 | F28-1 | 5 | 10 | 1 | 10 | X |  | Blown Tx
2011-01-18 | F28-4 | 5 | 10 | 0.25 | 2.5 |  | X | Tx Connections
2011-01-18 | F28-4 | 5 | 10 | 0.5 | 5 | X |  | Sparking Arrestor
2011-01-27 | F4-14 | 5 | 1 | 1 | 1 |  | X | Connections
2011-02-06 | Colb. F1 | 5 | 20 | 2 | 40 | X |  | Broken Insulator
2011-02-18 | F28-1 | 5 | 1 | 1 | 1 | X |  | Dirty Arrestor
2011-02-19 | F28-1 | 6 | 10 | 1 | 10 |  | X | Neutral
2011-03-18 | Colb. F1 | 5 | 1 | 1 | 1 |  | X | Connections
2011-03-23 | F28-1 | 5 | 8 | 1 | 8 | X |  | Broken Switch
2011-04-04 | F28-6 | 5 | 1 | 0.5 | 0.5 |  | X | Connection
2011-04-09 | F4-14 | 6 | 1 | 1 | 1 |  | X | Neutral
2011-04-10 | F28-2 | 5 | 1 | 1 | 1 |  | X | Connection
2011-04-11 | F28-2 | 4 | 16 | 3.5 | 56 | X |  | Tx
2011-04-11 | F28-4 | 9 | 500 | 1 | 500 | X |  | Racoon
2011-04-11 | F28-4 | 9 | 1 | 3.5 | 3.5 | X |  | Racoon
2011-04-15 | Colb. F5 | 5 | 1 | 2.5 | 2.5 |  | X | U/G Fault
2011-04-16 | F4-20 | 6 | 20 | 2.5 | 50 | X |  | Primary wire down
2011-04-16 | F4-20 | 6 | 1 | 1 | 1 | X |  | Tx Lead
2011-04-16 | F4-20 | 6 | 40 | 0.25 | 10 | X |  | Trees
2011-04-20 | F28-2 | 5 | 1 | 0.75 | 0.75 |  | X | Connection
2011-04-28 | F4-13 | 6 | 200 | 2 | 400 | X |  | Wind
2011-04-28 | F4-14 | 6 | 200 | 2 | 400 | X |  | Wind
2011-04-28 | F4-15 | 6 | 100 | 2 | 200 | X |  | Wind
2011-05-15 | Colb. F5 | 6 | 30 | 1 | 30 | X |  | Wind
2011-05-26 | F28-1 | 6 | 1000 | 1.5 | 1500 | X |  | Lightning
2011-05-30 | F28-6 | 0 | 1000 | 1 | 1000 | X |  | Breaker trip
2011-06-02 | F28-1 | 5 | 1000 | 1 | 1000 | X |  | Blown Tx
2011-06-02 | F28-1 | 5 | 200 | 3 | 600 | X |  | Blown Tx
2011-06-08 | F28-6 | 3 | 1000 | 0.5 | 500 | X |  | Limb on line
2011-06-11 | F4-15 | 0 | 30 | 3 | 90 | X |  | Fuse
2011-06-12 | F28-4 | 9 | 500 | 1.5 | 750 | X |  | Crowe
2011-06-17 | F28-4 | 9 | 500 | 1 | 500 | X |  | Crowe
2011-07-05 | F28-1 | 9 | 1000 | 1 | 1000 | X |  | Squirrel
2011-07-08 | F28-2 | 9 | 500 | 1 | 500 | X |  | Squirrel
2011-07-17 | F28-1 | 9 | 1000 | 0.5 | 500 | X |  | Crowe
2011-08-15 | F28-6 | 9 | 1 | 1 | 1 | X |  | Crowe
2011-08-19 | Colb. F5 | 5 | 30 | 1.25 | 37.5 | X |  | Faulty switch
2011-08-25 | F28-2 | 4 | 12 | 3 | 36 | X |  | Lightning
2011-08-25 | F28-2 | 6 | 1 | 3 | 3 | X |  | Lightning
2011-08-25 | F28-4 | 6 | 5 | 1 | 5 | X |  | Lightning
2011-08-25 | F28-4 | 6 | 4 | 0.5 | 2 | X |  | Lightning
2011-08-28 | F28-6 | 6 | 1000 | 2.5 | 2500 | X |  | Tree
2011-09-09 | Colb. F2 | 3 | 1 | 1.75 | 1.75 |  | X | Tree branch
2011-09-10 | F28-4 | 0 | 1 | 1.5 | 1.5 | X |  | Fuse
2011-09-13 | F28-6 | 0 | 45 | 0.5 | 22.5 | X |  | Fuse
2011-09-13 | F28-6 | 3 | 1 | 1.5 | 1.5 |  | X | Tree
2011-10-01 | F28-2 | 3 | 1 | 1 | 1 |  | X | Triplex
2011-10-07 | F28-1 | 0 | 5 | 2.5 | 12.5 | X |  | Fuse
2011-10-15 | F4-14 | 6 | 500 | 3 | 1500 | X |  | Winds & Trees
2011-10-15 | F28-2 | 6 | 1 | 1 | 1 |  | X | Tree - Winds
2011-10-15 | F28-6 | 6 | 96 | 2 | 192 | X |  | Tree - Winds
2011-10-16 | Colb. F1 | 3 | 1 | 1 | 1 |  | X | Tree on triplex
2011-10-28 | F28-1 | 5 | 1000 | 1.5 | 1500 | X |  | Blown Tx
2011-10-31 | F28-6 | 3 | 100 | 0.5 | 50 | X |  | Tree
2011-11-06 | F28-2 | 5 | 1 | 1.75 | 1.75 | X |  | Switch
2011-11-09 | F28-1 | 0 | 1000 | 1 | 1000 | X |  | Fuse Sutherland
2011-11-16 | F-20 | 5 | 1 | 2 | 2 |  | X | Connection
2011-11-28 | F4-15 | 5 | 100 | 2.25 | 225 | X |  | Wire down 1st St.
2011-12-06 | F28-1 | 0 | 1 | 0.75 | 0.75 | X |  | dip Fuse
2011-12-07 | F4-20 | 9 | 10 | 2.5 | 25 |  | X | Truck caught wires
2011-12-11 | F4-20 | 5 | 1 | 1 | 1 |  | X | Connection
2011-12-18 | Colb. F3 | 5 | 30 | 2.5 | 75 | X |  | HLC burnt off
2011-12-24 | Colb. F5 | 5 | 60 | 2.75 | 165 | X |  | Faulty switch
2011-12-25 | F28-1 | 0 | 25 | 1 | 25 | X |  | Dip Fuse
2011-12-25 | F28-1 | 5 | 25 | 2.25 | 56.25 | X |  | Blown Tx
2011-12-26 | F28-4 | 5 | 1 | 1 | 1 |  | X | U/G fault

## 2012 By Feeder
MM/DD/YYYY | Feeder | Code | Customers | Duration Hours | Total Customer Hours of Interruptions | Primary | Secondary | Comments
2012-01-13 | F28-1 | 5 | 1 | 4.5 | 4.5 | X |  | PMH-9 flash over
2012-01-16 | F28-6 | 0 | 10 | 0.5 | 5 | X |  | Tx Fuse
2012-01-28 | Colb. F5 | 25 | 8 | 1 | 8 | X |  | Car hit pole
2012-02-11 | F4-14 | 5 | 10 | 1.5 | 15 | X |  | Tx Bushing
2012-02-24 | F28-2 | 6 | 832 | 1.25 | 1040 | X |  | Wires hitting together
2012-02-24 | F28-4 | 6 | 724 | 1.5 | 1086 | X |  | ?
2012-02-24 | F28-4 | 6 | 724 | 0.75 | 543 | X |  | ?
2012-02-25 | F4-14 | 5 | 1 | 1 | 1 |  | X | neutral
2012-03-03 | F4-13 | 6 | 214 | 3 | 642 | X |  | Winds
2012-03-03 | F4-14 | 6 | 631 | 3 | 1893 | X |  | Winds
2012-03-03 | F4-15 | 6 | 106 | 3 | 318 | X |  | Winds
2012-03-03 | F28-2 | 6 | 6 | 1.5 | 9 | X |  | Wind
2012-03-03 | F28-4 | 6 | 26 | 0.5 | 13 | X |  | Winds
2012-03-03 | F28-4 | 6 | 724 | 1 | 724 | X |  | Winds
2012-03-03 | Colb. F2 | 6 | 10 | 1.5 | 15 | X |  | Tx Fuse
2012-03-03 | Colb. F5 | 1 | 4 | 0 | 0 |  | X | Tree
2012-03-11 | Colb. F2 | 5 | 10 | 2.5 | 25 | X |  | Switch
2012-03-24 | Colb. F3 | 5 | 3 | 0.5 | 1.5 | X |  | Bad Lead
2012-04-16 | Colb. F3 | 5 | 285 | 1.75 | 498.75 | X |  | Broken Insulator
2012-04-18 | F28-1 | 8 | 1934 | 0.25 | 483.5 | X |  | Breaker
2012-04-18 | F28-2 | 8 | 832 | 0.25 | 208 | X |  | Breaker
2012-04-21 | F28-2 | 5 | 10 | 2.5 | 25 | X |  | Blown Tx
2012-04-29 | F4-20 | 5 | 15 | 1.5 | 22.5 |  | X | Tx connection
2012-06-12 | F28-1 | 6 | 4 | 1 | 4 | X |  | Lightning
2012-06-17 | F28-1 | 9 | 1 | 2 | 2 | X |  | Crow
2012-06-21 | Colb. F2 | 5 | 8 | 1.5 | 12 | X |  | HLC
2012-06-21 | Colb. F5 | 5 | 6 | 2 | 12 | X |  | Tx Fuse
2012-06-24 | F28-1 | 9 | 1934 | 1.25 | 2417.5 | X |  | Squirrel
2012-07-02 | F28-2 | 9 | 10 | 1.25 | 12.5 | X |  | Squirrel in Tx
2012-07-14 | F28-1 | 9 | 1 | 1 | 1 | X |  | Crowe
2012-07-21 | F28-1 | 9 | 1 | 0.5 | 0.5 | X |  | Squirrel
2012-08-01 | F28-1 | 9 | 1 | 0.75 | 0.75 | X |  | Crowe
2012-08-02 | F28-1 | 0 | 1 | 1 | 1 | X |  | Unknown
2012-08-05 | F28-2 | 9 | 335 | 2 | 670 | X |  | Squirrel in Tx
2012-08-05 | Colb. F4 | 9 | 1 | 2.5 | 2.5 |  | X | Truck hit triplex
2012-08-11 | F28-1 | 9 | 63 | 1.75 | 110.25 | X |  | Squirrel
2012-08-15 | F28-1 | 0 | 1034 | 0.5 | 517 | X |  | Unknown
2012-08-16 | F28-2 | 9 | 1 | 0.5 | 0.5 | X |  | Squirrel in Tx
2012-09-08 | F28-6 | 6 | 824 | 1.25 | 1030 | X |  | Wind
2012-09-08 | Colb. F2 | 6 | 65 | 4 | 260 | X |  | Winds & Tree
2012-09-08 | Colb. F3 | 6 | 10 | 3.5 | 35 | X |  | Winds
2012-09-20 | Colb. F1 | 3 | 126 | 2 | 252 | X |  | Tree
2012-09-20 | Colb. F1 | 3 | 2 | 1.75 | 3.5 | X |  | Tree
2012-09-28 | F28-4 | 5 | 1 | 1 | 1 |  | X | Connections
2012-09-29 | F4-15 | 5 | 2 | 0.75 | 1.5 |  | X | Connections
2012-10-07 | F4-20 | 5 | 1 | 1.5 | 1.5 |  | X | Connections
2012-10-15 | F28-6 | 5 | 1 | 2.5 | 2.5 |  | X | Connections
2012-10-16 | Colb. F2 | 0 | 6 | 1 | 6 | X |  | Line Fuse
2012-10-29 | F28-2 | 6 | 189 | 5.5 | 1039.5 | X |  | Wind
2012-10-29 | F28-6 | 6 | 1 | 12 | 12 | X |  | Wind
2012-10-29 | F28-6 | 6 | 90 | 9.5 | 855 | X |  | Tree Broken Pole
2012-10-29 | F28-6 | 6 | 824 | 2.75 | 2266 | X |  | Wind
2012-10-30 | F28-6 | 0 | 1 | 1 | 1 | X |  | Fuse
2012-11-08 | F28-2 | 8&9 | 832 | 0.75 | 624 | X |  | Truck in Wires
2012-11-09 | F28-4 | 8&9 | 724 | 0.25 | 181 | X |  | Grador hit guy wire
2012-11-14 | F28-2 | 0 | 250 | 0.5 | 125 | X |  | Unknown
2012-11-16 | F4-14 | 5 | 1527 | 2 | 3054 | X |  | Tap burnt off
2012-11-16 | F4-14 | 5 | 12 | 6.5 | 78 | X |  | Load
2012-11-19 | F28-1 | 5 | 1034 | 0.5 | 517 | X |  | Tx Blown
2012-11-21 | Colb. F4 | 5 | 10 | 3.5 | 35 | X |  | Blown Tx
2012-12-20 | F28-4 | 6 | 724 | 2.5 | 1810 | X |  | Winds
2012-12-21 | F28-2 | 5 | 1 | 2 | 2 |  | X | UG Fault
2012-12-31 | F28-2 | 3 | 1 | 1 | 1 |  | X | Tree

## 2013 By Feeder
MM/DD/YYYY | Feeder | Code | Customers | Duration Hours | Total Customer Hours of Interruptions | Primary | Secondary | Comments
2013-01-08 | Colb. F5 | 0 | 20 | 2.5 | 50 | X |  | Switch
2013-01-09 | F28-1 | 9 | 5 | 10 | 50 |  | X | Contractor dug in
2013-01-10 | F28-4 | 4 | 1 | 2.5 | 2.5 | X |  | Blown Tx
2013-01-25 | Colb. F4 | 0&5 | 10 | 1.5 | 15 | X |  | Switch Burnt
2013-02-03 | F28-4 | 9 | 270 | 1 | 270 | X |  | Birds
2013-02-09 | F28-6 | 3 | 1 | 0.5 | 0.5 |  | X | Triplex in tree
2013-02-10 | F4-14 | 5 | 12 | 1 | 12 | X |  | Broken switch
2013-02-10 | F28-6 | 5 | 1 | 0.5 | 0.5 |  | X | Insulinks
2013-02-10 | F28-6 | 8 | 36 | 3 | 108 | X |  | Truck broke pole
2013-02-10 | F28-6 | 8 | 175 | 1 | 175 | X |  | Truck broke pole
2013-02-27 | F4-15 | 6 | 106 | 4.5 | 477 | X |  | Weather/Snow/Wind
2013-02-27 | F28-2 | 6 | 832 | 1.5 | 1248 | X |  | Weather/Snow/Wind
2013-02-27 | F28-4 | 6 | 50 | 0.75 | 37.5 | X |  | Weather/Snow/Wind
2013-03-17 | F4-20 | 5 | 12 | 3 | 36 | X |  | Blown Tx
2013-03-22 | Colb. F5 | 5 | 12 | 1 | 12 | X |  | HLC
2013-04-12 | F28-4 | 6 | 20 | 1 | 20 | X |  | Wind
2013-04-12 | F28-4 | 5 | 14 | 2.5 | 35 | X |  | Blown Tx
2013-04-12 | Colb. F3 | 6 | 20 | 4.5 | 90 | X |  | Ice Storm
2013-04-12 | Colb. F4 | 6 | 15 | 8 | 120 | X |  | Tree and Ice
2013-04-13 | F28-1 | 5 | 3 | 1 | 3 |  | X | Connection
2013-04-13 | Colb. F3 | 6 | 2 | 2 | 4 | X |  | Switch Burnt
2013-04-27 | F4-9 | 8 | 400 | 0.25 | 100 | X |  | Phase to Phase
2013-05-11 | F28-4 | 9 | 5 | 2 | 10 | X |  | Squirrel
2013-05-15 | F4-20 | 5 | 20 | 2 | 40 | X |  | Broken Switch
2013-05-25 | Colb. F1 | 5 | 1 | 1 | 1 |  | X | Bad Connection
2013-06-23 | Colb. F2 | 3 | 213 | 0.5 | 106.5 | X |  | Tree dropped on line
2013-06-26 | F28-1 | 5 | 1 | 3 | 3 |  | X | UG Fault
2013-07-07 | F28-1 | 5 | 1 | 1 | 1 |  | X | Connection
2013-07-14 | F28-6 | 5 | 10 | 3.5 | 35 | X |  | Blown Tx
2013-07-17 | F28-4 | 5 | 10 | 2 | 20 | X |  | Blown Tx
2013-07-21 | Colb. F2 | 0 | 10 | 2 | 20 | X |  | Primary burnt down
2013-07-23 | F28-6 | 3 | 1 | 1.5 | 1.5 |  | X | Triplex in tree
2013-08-05 | Colb. F4 | 5 | 1 | 2 | 2 |  | X | Connections
2013-08-08 | F28-6 | 9 | 2 | 1 | 2 | X |  | Squirrel
2013-08-12 | F28-6 | 9 | 1 | 0.5 | 0.5 | X |  | Squirrel
2013-09-03 | F28-2 | 4 | 1 | 3 | 3 | X |  | Blown Tx.
2013-09-09 | Colb. F2 | 9 | 3 | 2.5 | 7.5 |  | X | Truck caught wires
2013-09-24 | F28-4 | 9 | 12 | 1.25 | 15 |  | X | Truck caught wire.
2013-10-17 | F28-1 | 9 | 1 | 1.5 | 1.5 |  | X | Car hit stop light pole
2013-10-22 | F28-2 | 9 | 1 | 1.5 | 1.5 | X |  | Squirrel
2013-11-01 | F28-1 | 9 | 1 | 8 | 8 | X |  | Broken Pole
2013-11-01 | Colb. F3 | 6 | 40 | 1 | 40 | X |  | Fuse blown
2013-11-02 | F4-20 | 5 | 80 | 3.5 | 280 | X |  | Burnt private pole
2013-11-03 | Colb. F1 | 5 | 1 | 0.5 | 0.5 |  | X | Bad Connection
2013-11-03 | Colb. F5 | 5 | 1 | 0.5 | 0.5 |  | X | Bad connection
2013-11-07 | F28-4 | 5 | 1 | 0.5 | 0.5 |  | X | Connection
2013-11-07 | F4-14 | 3 | 1 | 0.5 | 0.5 |  | X | Broken hot leg
2013-11-14 | Colb. F3 | 5 | 10 | 2 | 20 | X |  | Blown Tx
2013-12-01 | Colb. F3 | 5 | 40 | 1.5 | 60 |  |  | Switch Burnt
2013-12-09 | F28-4 | 5 | 14 | 0.75 | 10.5 | X |  | Broken Wire

## 2014 by Feeder
MM/DD/YYYY | Feeder | Code | Customers | Duration Hours | Total Customer Hours of Interruptions | Primary | Secondary | Comments
2014-01-05 | F4-20 | 5 | 3 | 0.5 | 1.5 |  | X | Connections
2014-01-19 | F28-4 | 5 | 12 | 1.25 | 15 | X |  | Broken Switch
2014-01-24 | Colb. F3 | 6 | 285 | 2.5 | 712.5 | X |  | Tree
2014-01-25 | F28-2 | 5 | 1 | 1 | 1 |  | X | Connection
2014-02-03 | Colb. F1 | 5 | 1 | 1.5 | 1.5 |  | X | Connection
2014-02-03 | Colb. F4 | 5 | 10 | 1 | 10 |  | X | Tx Connection
2014-02-14 | F4-9 | 0 | 2 | 0.5 | 1 |  | X | Unknown
2014-02-26 | F4-14 | 5 | 1 | 0.5 | 0.5 |  | X | Connection
2014-03-12 | F28-4 | 6 | 10 | 0.5 | 5 | X |  | Wind
2014-04-05 | F28-4 | 5 | 2 | 1 | 2 | X |  | Broken Switch
2014-05-15 | F28-4 | 5 | 724 | 3.5 | 2534 | X |  | Station Tx Blown
2014-05-15 | F28-6 | 5 | 824 | 3.5 | 2884 | X |  | Station Tx Blown
2014-05-16 | Colb. F2 | 5 | 213 | 2.5 | 532.5 | X |  | HLC
2014-05-19 | F28-2 | 9 | 10 | 2 | 20 | X |  | Squirrel
2014-06-03 | F28-2 | 3 | 10 | 0.75 | 7.5 | X |  | Tree Limb
2014-06-23 | F28-1 | 0 | 1034 | 2.5 | 2585 | X |  | Tx Fuse
2014-08-21 | F28-2 | 9 | 10 | 0.5 | 5 | X |  | Squirrel
2014-09-21 | Colb. F2 | 6 | 213 | 4.5 | 958.5 | X |  | Wind
2014-10-15 | F28-2 | 9 | 10 | 1 | 10 | X |  | Squirrel
2014-11-16 | F4-19 | 9 | 1 | 10 | 10 |  | X
2014-11-18 | F4-14 | 5 | 1 | 0.75 | 0.75 | X |  | XFRM Lead
2014-11-25 | F28-4 | 5 | 8 | 2.5 | 20 | X
2014-11-29 | F28-1 | 9 | 1 | 1 | 1 |  | X | Tx Fuse
2014-12-13 | Colb. F3 | 0 | 6 | 0.75 | 4.5 | X |  | Tx Fuse
2014-12-19 | F28-6 | 0 | 1 | 1.5 | 1.5 |  | X | Meter Base
2014-12-26 | F28-6 | 5 | 1 | 0.5 | 0.5 |  | X | Burn Off

## 2015 By Feeder
MM/DD/YYYY | Feeder | Code | Customers | Duration Hours | Total Customer Hours of Interruptions | Primary/ Secondary | Comments
2015-01-01 | F-20 | 3 | 1 | 1 | 1 | Secondary | tree rubbing, repaired service | np | no power (primary)
2015-02-08 | F-9 | 3 | 1 | 1 | 1 | Secondary | broke neutral + hot leg, sleeved + repaired | pp | part power (secondary)
2015-02-16 | F-4 | 5 | 1 | 1 | 1 | Secondary | terminator burnt @ riser, replaced | conn | connnection
2015-03-06 | M2 | 5 | 507 | 0.17 | 86.19 | Primary | np, arrestor blown, customer to change | TX | transformer
2015-03-31 | F-1 | 5 | 7 | 2 | 14 | Secondary | faulty secondary service, changed TX | HLC | hot leg clamp
2015-03-26 | F4&F6 | 5 | 1548 | 0.75 | 1161 | Primary | main breaker open, broken switch replaced
2015-03-18 | Colb. F5 | 5 | 1 | 7.25 | 7.25 | Secondary | UG burn off, located, dug, repaired
2015-03-10 | Colb. F4 | 5 | 1 | 2.25 | 2.25 | Secondary | terminator burnt @ riser, replaced
2015-04-01 | F-1 | 5 | 7 | 3.75 | 26.25 | Secondary | customer secondary burnt off, contractor to repair conductors (1/2)
2015-04-01 | F-1 | 5 | 7 | 0.5 | 3.5 | Secondary | re-energized TX (2/2)
2015-05-07 | F-4 | 5 | 1 | 1.25 | 1.25 | Secondary | Loose secondary conn, replaced the leg on overhead
2015-05-08 | F-2 | 9 | 832 | 1.5 | 1248 | Primary | crow into switch, refuse/closed F2
2015-05-14 | F-9 | 0 | 1 | 1 | 1 | Secondary | bad voltage, open neutral, new conn @ neutral
2015-05-19 | Colb. F2 | 3 | 6 | 0.75 | 4.5 | Primary | trimmed tree, refused/closed
2015-06-01 | F-4 | 5 | 1 | 0.83 | 0.83 | Secondary | wire broke of at conn spun buss, replaced conn
2015-06-08 | F-5 | 3 | 1 | 1 | 1 | Secondary | tree rubbing, trimmed, replace wire
2015-06-15 | F-6 | 5 | 1 | 0.67 | 0.67 | Secondary | 1 leg burnt, made new conn
2015-06-18 | F-6 | 5 | 10 | 2.67 | 26.7 | Primary | faulty TX, replaced
2015-06-19 | F-1 | 9 | 1 | 0.92 | 0.92 | Secondary | Cut out open on 3 Phase, crow, refused,closed
2015-06-23 | M2 | 2 | 3970 | 0.5 | 1985 | Primary | Hydro One side, reported locations
2015-06-23 | F-3 | 3 | 285 | 1.5 | 427.5 | Primary | tree on wire, cleared and closed feeder
2015-06-27 | F-15 | 7 | 106 | 1.25 | 132.5 | Primary | Patrolled F15, closed breaker
2015-07-31 | F-6 | 6 | 30 | 1 | 30 | Primary | Blown fuse
2015-07-27 | F-4 | 0 | 1 | 1 | 1 | Secondary | Blown fuse
2015-07-06 | F-19 | 3 | 2 | 0.75 | 1.5 | Secondary | Tree, trimmed and repaired wire
2015-08-20 | F-4 | 0 | 7 | 1.33 | 9.31 | Primary | S-112 open, Closed
2015-08-02 | F-2 | 6 | 1 | 2 | 2 | Secondary | Wind, repaired neutral & fixed service
2015-08-21 | F-1 | 5 | 6 | 1 | 6 | Primary | Broken TX switch, replaced
2015-08-14 | F-4 | 4 | 8 | 6.25 | 50 | Primary | 2 blown TXs, replaced both
2015-08-14 | F-4 | 4 | 10 | 2.75 | 27.5 | Primary | blown TX, replaced it
2015-08-14 | F-1 | 4 | 4 | 2 | 8 | Primary | blown TX, replaced it
2015-09-01 | F-1 | 9 | 126 | 1.25 | 157.5 | Primary | Homeowner cut tree on wire, refused.
2015-10-15 | F-1 | 4 | 126 | 1.17 | 147.42 | Primary | Re-energized F1
2015-10-25 | F-2 | 9 | 10 | 0.5 | 5 | Primary | Squirrel, installed new switch
2015-10-25 | F-2 | 0 | 2 | 4.42 | 8.84 | Secondary | No voltage coming in, refused & closed
2015-10-28 | F-2 | 5 | 1 | 0.75 | 0.75 | Secondary | burnt live leg, replaced leg
2015-10-29 | F-6 | 3 | 824 | 0.75 | 618 | Primary | tree, re-closed F6
2015-10-29 | F-2 | 0 | 213 | 3.5 | 745.5 | Primary | no problem, closed F2
2015-10-29 | F-14 | 5 | 1 | 0.5 | 0.5 | Secondary | lead broke of switch, replaced lead
2015-10-31 | F-2 | 9 | 10 | 0.75 | 7.5 | Primary | Squirrel, replaced arrestor
2015-10-03 | F-2 | 5 | 1 | 1.25 | 1.25 | Secondary | Loose conn
2015-11-03 | F-3 | 5 | 2 | 1.5 | 3 | Secondary | bad conn @ house, tighten conn @ TX
2015-11-16 | F-6 | 9 | 2 | 1.42 | 2.84 | Primary | Homeowner dropped limb on service, repaired transformer conn.
2015-11-13 | F-4 | 5 | 1 | 0.58 | 0.58 | Secondary | Broken customer switch
2015-12-27 | F-1 | 5 | 3 | 1.33 | 3.99 | Primary | Faulty hot line clamp
2015-12-16 | F-14 | 5 | 1 | 0.5 | 0.5 | Secondary | Faulty Insulinks @ Stack