## Sheet1
Exhibit I, Tab 3, Schedule 30, Attachment 1
Hydro One Networks Inc. Transmission Rate Application
EB-2016-0160
Ref: B1 Tab 2 Schedule 6
Current Asset Condition | [14 empty] | Column P, Q, R are proxy dollar values consistent with SEC #20. Except that transformer forecast budget excludes unknown demand failures.
TRANSMISSION ASSETS | Population | Unit | Expected Service Life | # Within ESL | # Beyond ESL | # very high condition risks | # high condition risks | # fair condition risks | # low condition risks | # very low condition risks | # Needs Assessment | Forecast # Replaced 2016 | Forecast # Replaced 2017 | Forecast # Replaced 2018 | Forecast Budget $ 2016 | Forecast Budget $ 2017 | Forecast Budget $ 2018 | Forecast # replaced in 2019-2021 | Budget $ 2019-2021 | Forecast # Replaced 2010 to 2015 | Actual # replaced 2010 to 2015 | Actual $ Spent 2010 to 2015
Transformer | [19 empty] | 97 | 98 | 656.6
Autotransformer - 500 kV | 40 |  | 40 | 27 | 13 | 0 | 2 | 3 | 13 | 22 |  | 1 | 0 | 0 | 5.5 | 0 | 0 | N/A | N/A
Autotransformer - 345 kV | 4 |  | 50 | 2 | 2 | 0 | 0 | 0 | 0 | 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
Autotransformer - 230 kV | 87 |  | 50 | 66 | 21 | 0 | 5 | 10 | 35 | 37 |  | 2 | 2 | 1 | 11 | 11 | 5.5 | N/A | N/A
230 kV Phase Shifter/230 kV Regulator/500 kV Reactor | 9 |  | 40 | 4 | 5 | 0 | 0 | 0 | 0 | 9 |  | 2 | 0 | 0 | 11 | 0 | 0 | N/A | N/A
Step Down Transformer - 500 kV | 1 |  | 50 | 1 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
Step Down Transformer - 230 kV | 292 |  | 40-50 | 245 | 47 | 1 | 33 | 22 | 104 | 132 |  | 1 | 4 | 2 | 5.5 | 22 | 11 | N/A | N/A
Step Down Transformer - 115 kV | 288 |  | 50-60 | 173 | 115 | 13 | 57 | 28 | 71 | 119 |  | 12 | 17 | 15 | 66 | 93.5 | 82.5 | N/A | N/A
Circuit Breakers | [19 empty] | 585 | 407 | 270.2
Oil | 1717 |  | 55 | 1606 | 111 | 20 | 191 | 307 | 563 | 636 |  | 21 | 49 | 56 | 14.7 | 34.3 | 39.2 | N/A | N/A
SF 6 | 1649 |  | 40 | 1648 | 1 | 10 | 172 | 222 | 175 | 1070 |  | 7 | 7 | 7 | 4.9 | 4.9 | 4.9 | N/A | N/A
Air Blast | 191 |  | 40 | 35 | 156 | 1 | 9 | 46 | 77 | 58 |  | 15 | 2 | 17 | 10.5 | 1.4 | 11.9 | N/A | N/A
GIS | 162 |  | 40 | 162 | 0 | 2 | 7 | 28 | 40 | 85 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
Metaclad | 796 |  | 40 | 666 | 130 | 5 | 50 | 68 | 232 | 441 |  | 0 | 7 | 52 | 0 | 4.9 | 36.4 | N/A | N/A
Vacuum | 28 |  | 40 | 27 | 1 | 0 | 2 | 0 | 24 | 2 |  | 0 | 1 | 0 | 0 | 0.7 | 0 | N/A | N/A
Protection Systems | [19 empty] | 1735 | 2238 | 277.4
Electromechanical | 4318 |  | 45 | 3417 | 901 | 70 | 1161 | 391 | 2304 | 392 |  | Unable to provide further breakdown due to time constraint | [5 empty] | N/A | N/A
Solid State | 2409 |  | 25 | 719 | 1690 | 1230 | 787 | 81 | 274 | 37 |  | Numbers are total protections per year | [5 empty] | N/A | N/A
Microprocessor | 5376 |  | 20 | 5366 | 10 | 2 | 15 | 32 | 1430 | 3897 |  | 367 | 449 | 528 | 45.9 | 56.1 | 66 | N/A | N/A
Conductors | 30000 | cct-km | 70 | 24300 | 5700 | N/A | 2700 | 6000 | 12000 | N/A | 9300 | 183 | 192 | 440 | 76.9 M | 67.1 M | 143.1 M | N/A | N/A | 378.3 | 458 | 166.4
Poles
Wood | 42000 | number of poles | 50 | 30660 | 11340 | N/A | 1260 | 8400 | 29820 | N/A | 2520 | 850 | 850 | 850 | 38.3 M | 35.3 M | 35.3 M | N/A | N/A | 5085 | 4727 | 209.6
Steel Structures | 52000 | number of structures | 80 | 41000 | 11000 | N/A | 2080 | 7280 | 42640 | N/A | N/A | 462 | 1250 | 1600 | 8.8 M | 42.5 M | 54.4 M | N/A | N/A | 1505 | 1179 | 20.5
Insulators
Glass | 38100 | circuit structures | 80 | 38100 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Poreclain | 76200 | circuit structures | 80 | 59800 | 16400 | N/A | 34000 | N/A | N/A | N/A | N/A | 2100 | 3970 | 3880 | 26.1 M | 62.3 M | 61.4 M | N/A | N/A | N/A | N/A | N/A
Polymer | 12700 | circuit structures | 30 | 12700 | 0 | N/A | 60 | N/A | N/A | N/A | N/A | N/A | 60 | N/A | N/A | 1.6 M | N/A | N/A | N/A | N/A | N/A | N/A
circuit structures | 127000 | circuit structures | N/A | 110600 | 16400 | N/A | 34060 | N/A | N/A | N/A | N/A | 2100 | 4030 | 3880 | 26.1 M | 63.9 M | 61.4 M | N/A | N/A | N/A | 1365 | 21.9
Underground Cable | 270 | cct-km | 50 | 219 | 51 | N/A | 11 | 59 | 197 | N/A | 3 | 0 | 0 | 4.8 | 1.4 M | 2.3 M | 22.5 M | N/A | N/A | 29.8 | 8.1 | 60.1