## Sheet1
SAA Cost Comp. - Sellick Equipment (2131 Roseborough Dr.) - Hydro One's Offer to Connect dated August 3, 2016
Based on Sellick's Loading Profile Change (July 25, 2016) for 2000Amp service, 347/600V Secondary (1200kW Maximum Load)
| HONI |  | E.L.K. Energy
| Explanation | HONI Cost | Explanation | E.L.K
Design Costs | Prepare Offer to Connect and Design based on customer's connection requirements | 0 | Customer provided the design | 0
Non-Contestable Costs (Line Expansion) | No Non-Constestable Line Expansion Costs | NA | Supply & install 750KVA 600/347 Volt padmounted transformer, transformer vault, high voltage duct structure, high voltage cable and ancillary equipment. Includes civil work. | 48217.68
Contestable Costs (Line Expansion) | No Line Expansion Contestable Costs | NA | There is no contestable work | 0
Non-Contestable Costs (other than line expansion) - Secondary | No Non-Constestable Secondary Line Expansion Costs | NA | Install 2 new 45’ poles into existing overhead line at the intersection of Roseborough and Clark to facilitate new connection. | 20619.35
Non-Contestable Costs (other than line expansion) - Primary | Supply and install 55' class 2 Bell tangent pole. Supply and install 22m of O/H primary and neutral conductor, anchor, guys, switches, terminations, meters, PTs and CTs. Supply and install 45' class 3 road crossing wood pole and dead-end wires. | 18494.38 | Place new distribution assets into service | 14958.77
Contestable Costs (other than line expansion) - Secondary | No Contestable Secondary Costs | NA | There is no contestable work | 0
Contestable Costs (other than line expansion) - Primary | No Contestable Primary Costs | NA | There is no contestable work | 0
Customer Accountabilities | All customer work to be completed in accordance with ESA standards and requirements. - customer dig trench and supply and install 3 phase primary 2/0 28kV U/G from Hydro One 45' class 3 pole to customer's transformer - customer will install transformer pad complete with grounding to ESA specs and provide a 1500kVA 16/27.6kV (primary), 347/600V (secondary) transformer complete with all secondary and primary connections at the transformer - customer will supply all pipe, duct, straps and metal guards to run the 3 phase primary up the pole (Hydro One will terminate the cables at the pole) - customer to supply and install 1200A secondary service and complete all connections at the transformer - customer to install a Hydro One supplied meter enclosure (3'x3' meter cabinet) on the building, and install 1.25" duct between the enclosure and the cabinet.
Civil Work | Customer is Accountable | NA | Included in costs above (ln 2) | 0
TOTAL COSTS=> (Excludes HST) |  | 18494.38 | Excludes HST | 83795.8
Security Deposit Required |  | 0 | Excludes HST | 125316.05
Total Present Value(PV) of OM+A Over 10yrs |  |  |  | 43272
Capital Contributions required |  | 0 | Per OTC | 0
Total Cost of Connection |  | 18494.38 |  | 0

## Sheet2
2.8
0.8
12.8
0.3
0.08
0.24
0.6
2
2.2
1
0.12
0.4
0.3
0.3
2
1.6
0.2
3
0.3
0.6
4.1
0.55
0.9
2.1
0.45
4
0.8
1.38
1.45
5.7
0.3
53.37