## Sheet1
EB-2017-0024
Enersource Rate Zone
ERZ-AMPCO-10 Appendix C
| Asset | Population | % | % | % | % | % | Number of Units Replaced |  | Forecast Number of Units to be Replaced | [6 empty] | TOTAL | % Assets Replaced in 2018 in very poor & poor condition
|  |  | Very Good | Good | Fair | Poor | Very Poor | 2015 | 2016 | 2017 | 2018 Projects Excluding ICM | 2018 ICM Projects | 2019 | 2020 | 2021 | 2022
1 | Substation Transformers |  | 47.22% | 36.11% | 14% | 2% | < 1%
2 | Substation Transformer Spares |  | 66.67% | 8.333% | 17% | 0% | 8%
3 | Circuit Breakers |  | 92.55% | 3.922% | 2% | < 1% | 2%
4 | Pole Mounted Transformers |  | 80.45% | 11.34% | 6% | < 1% | 2%
5 | Pad Mounted Transformers 1 Phase |  | 59.33% | 28.72% | 7% | 4% | < 1%
6 | Pad Mounted Transformers 3 Phase |  | 84.24% | 9.445% | 4% | 2% | < 1%
7 | Vault Transformers |  | 70.58% | 13.05% | 7% | 7% | 2%
8 | Pad Mounted Switchgear |  | 65.31% | 19.37% | 7% | 3% | 6%
9 | Overhead Switches 44 kV Load Break |  | 88.46% | 5.917% | < 1% | 5% | 0%
10 | Overhead Switches 27.6 kV Load Break |  | 93.43% | 2.347% | 3% | 1% | 0%
11 | Overhead Switches Inline |  | 85.66% | 5.495% | 4% | 3% | 1%
12 | Overhead Switches Motorized |  | 77.88% | 5.769% | 2% | 7% | 8%
13 | UG Cables Main Feeder |  | 72.9% | 6.639% | 0% | 9% | 12%
14 | UG Cables Distribution |  | 59.71% | 6.127% | 0% | 13% | 21%
15 | Poles Wood |  | 59.67% | 15.06% | 7% | 9% | 9%
16 | Poles Concrete |  | 95.08% | 3.848% | 1% | < 1% | 0%
17 | TOTAL

## Sheet2
Asset | Population | Condition - Quantities |  |  |  |  | % | % | % | % | % | Number of Units Planned for Replacement |  | Number of Units Replaced
|  | Very Good | Good | Fair | Poor | Very Poor | Very Good | Good | Fair | Poor | Very Poor | 2015 | 2016 | 2010 | 2011 | 2012 | 2013 | 2014
Substation Transformers | 108 | 51 | 39 | 15 | 2 | 1 | 47.22% | 36.11% | 14% | 2% | < 1% | 2 | 4 | 4 | 1 | 3 | 4 | 0
Substation Transformer Spares | 12 | 8 | 1 | 2 | 0 | 1 | 66.67% | 8.333% | 17% | 0% | 8% | N/A | N/A | 0 | 0 | 0 | 0 | 0
Circuit Breakers | 510 | 472 | 20 | 8 | 1 | 9 | 92.55% | 3.922% | 2% | < 1% | 2% | 33 | 17 | 28 | 17 | 16 | 15 | 13
Pole Mounted Transformers | 5346 | 4301 | 606 | 329 | 26 | 84 | 80.45% | 11.34% | 6% | < 1% | 2% | 200 | 200 | 162 | 109 | 98 | 154 | 205
Pad Mounted Transformers 1 Phase | 14242 | 8450 | 4091 | 987 | 621 | 93 | 59.33% | 28.72% | 7% | 4% | < 1% | 350 | 350 | 200 | 213 | 170 | 322 | 315
Pad Mounted Transformers 3 Phase | 1821 | 1534 | 172 | 68 | 38 | 9 | 84.24% | 9.445% | 4% | 2% | < 1% | 70 | 70 | 37 | 55 | 48 | 68 | 65
Vault Transformers | 3861 | 2725 | 504 | 285 | 280 | 67 | 70.58% | 13.05% | 7% | 7% | 2% | 250 | 200 | 18 | 44 | 34 | 40 | 166
Pad Mounted Switchgear | 862 | 563 | 167 | 59 | 25 | 48 | 65.31% | 19.37% | 7% | 3% | 6% | 40 | 40 | 17 | 25 | 23 | 35 | 34
Overhead Switches 44 kV Load Break | 338 | 299 | 20 | 3 | 16 | 0 | 88.46% | 5.917% | < 1% | 5% | 0% | 10 | 10 | 6 | 10 | 6 | 2 | 7
Overhead Switches 27.6 kV Load Break | 213 | 199 | 5 | 6 | 3 | 0 | 93.43% | 2.347% | 3% | 1% | 0% | 5 | 5 | 12 | 2 | 4 | 4 | 3
Overhead Switches Inline | 2002 | 1715 | 110 | 83 | 67 | 27 | 85.66% | 5.495% | 4% | 3% | 1% | 75 | 75 | 101 | 108 | 90 | 63 | 73
Overhead Switches Motorized | 104 | 81 | 6 | 2 | 7 | 8 | 77.88% | 5.769% | 2% | 7% | 8% | 5 | 5 | 3 | 2 | 4 | 4 | 5
UG Cables Main Feeder | 2233 | 1627.911 | 148.253 | 0 | 199.574 | 257.505 | 72.9% | 6.639% | 0% | 9% | 12% | 40 | 50 | 26 | 13 | 33 | 36 | 22
UG Cables Distribution | 4038 | 2411.032 | 247.42 | 0 | 519.023 | 860.637 | 59.71% | 6.127% | 0% | 13% | 21% | 60 | 70 | 39 | 59 | 35 | 52 | 56
Poles Wood | 12917 | 7707 | 1945 | 935 | 1153 | 1177 | 59.67% | 15.06% | 7% | 9% | 9% | 500 | 500 | 403 | 306 | 254 | 214 | 282
Poles Concrete | 8966 | 8525 | 345 | 91 | 5 | 0 | 95.08% | 3.848% | 1% | < 1% | 0% | 100 | 100 | 101 | 77 | 63 | 53 | 70