## Sheet1
EB-2017-0024
Enersource Rate Zone
ERZ-AMPCO-17 Appendix D
| Asset | Population | Failure Rate 2011 | Failure Rate 2012 | Failure Rate 2013 | Failure Rate 2014 | Failure Rate 2015 | Failure Rate 2016 | Failure Rate 2017 | Replacement Rate 2011 | Replacement Rate 2012 | Replacement Rate 2013 | Replacement Rate 2014 | Replacement Rate 2015 | Replacement Rate 2016 | Replacement Rate 2017 | Replacement Rate 2018
1 | Substation Transformers | 120 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 0 | 2 | 3 | 2
3 | Circuit Breakers | 432 | 0 | 3 | 2 | 2 | 0 | 0 | 0 | 26 | 12 | 18 | 8 | 30 | 17 | 15
4 | Pole Mounted Transformers | 5353 | 38 | 67 | 89 | 64 | 65 | 59 | 39 |  | 42 | 172 | 221 | 472 | 451 | 159
5 | Pad Mounted Transformers | 16121 | [8 empty] | 90 | 311 | 308 | 572 | 530 | 298
7 | Vault Transformers | 3854 | [8 empty] | 12 | 45 | 200 | 138 | 253 | 112
8 | Pad Mounted Switchgear | 834 | 13 | 5 | 10 | 23 | 30 | 7 | 1 |  | 17 | 48 | 40 | 49 | 60 | 47
9 | Overhead Switches | 2653 | 7 | 9 | 8 | 7 | 8 | 5 | 7 |  | 7 | 9 | 14 | 19 | 34 | 23
13 | UG Cables Main Feeder in Conductor-Km | 2238 | 193 | 139 | 133 | 112 | 176 | 223 | 131 |  | 26.27 | 44.58 | 30.94 | 14.29 | 23.35 | 16.86
14 | UG Cables Distribution in Conductor-Km | 4076 | [8 empty] | 27.58 | 37.02 | 39.09 | 40.63 | 40.53 | 20.18
15 | Poles Wood | 12436 | 14 | 19 | 12 | 11 | 22 | 6 | 5 |  | 11 | 304 | 212 | 330 | 444 | 528
16 | Poles Concrete | 9488 | [8 empty] | 6 | 109 | 39 | 151 | 135 | 76
Note: Failure data based on asset failures resulting in customer outages
Transformer failure events not differentiated by type
cable faults
NOTE:
Population counts (column C) are based on Figure 18 of the DSP
Replacement information is coming from our GIS system, based on available "removed date" information. The accuracy of this field has been increasing as we've have been utilizing improved tools and workflows to more accurately and quickly update information
Main Feeder is defined as any primary cable with cable size other than: #1, #2, #4, #6, 1/0, 2/0, 3/0, 4/0
Distribution is defined as any primary cable with cable size indicated as: #1, #2, #4, #6, 1/0, 2/0, 3/0, 4/0
We do not have good tracking of failure rates for these assets. The information could be derived from our OMS system, but would require a labour intensive effort of reading through various comment fields.