## PART A & B
PART A | [6 empty] | PART B
Table 1 - SAIDI & SAIFI Corporate Results | [6 empty] | Table 7 - Relative Change in Fleet Condition, Poles
Year | SAIDI | SAIFI |  |  |  |  | OPTION | Wood Poles in Need of Replacement (,000s) | Relative Change in Fleet Condition by Option*
2013 | 6.9 | 2.5 |  |  |  |  | Current | 106 | 0%
2014 | 7.4 | 2.7 |  |  |  |  | Plan A | 93 | 12.26%
2015 | 7.6 | 2.6 |  |  |  |  | Plan B | 96 | 9.434%
2016 | 7.8 | 2.5 |  |  |  |  | Plan C | 126 | -18.87%
2013-2016 Avg. | 7.425 | 2.575 |  |  |  |  | Plan B-Modified | 99 | 6.604%
Excluding Loss of Supply (LoS) and Force Majeure (FM) | [6 empty] | *From I-29-Staff-164, b), i., the net change in fleet level condition is then assumed to reflect a potential improvement or deterioration in reliability.
Table 8 - Relative Change in Fleet Condition, Stations
Table 2 - Interruption Statistics, Poles | [6 empty] | OPTION | Stations in Poor Condition | Relative Change in Fleet Condition by Option | JT 3.10 - % of Station-caused Outages at Poor-Condition Stations | Relative Change in Reliability Impact
YEAR | SADI | SAIFI |  |  |  |  | Current | 70 | 0 | 0 | 0
2013 | 0.26748 | 0.073257 |  |  |  |  | Plan A | 0 | 100% | 9% | 9%
2014 | 0.37286 | 0.080243 |  |  |  |  | Plan B | 40 | 42.86% | 9% | 4%
2015 | 0.80273 | 0.1472 |  |  |  |  | Plan C | 90 | -28.57% | 9% | -3%
2016 | 0.37642 | 0.082841 |  |  |  |  | Plan B-Modified | 70 | 0% | 9% | 0%
2013-2016 Avg. | 0.45487 | 0.095885
Table 3 - Interruption Statistics, Stations |  |  | Table 6 - Contribution to Table 1 by Component (Tables 2-5) |  |  |  | Table 9 - Relative Change in Fleet Condition, Other Line Components
YEAR | SAIDI | SAIFI | COMPONENT | 2013-2016 SAIDI CONTRIBUTION | 2013-2016 SAIFI CONTRIBUTION |  | OPTION | Other Line Components Defects (,000s) | Relative Change in Fleet Condition by Option | JT 3.10 - Reliability Impact*
2013 | 0.1613 | 0.042262 | Poles | 6.126% | 3.724% | To Part C, Tables 11 & 12 (color-coded) | Current | 300 | 0% | 0
2014 | 0.17236 | 0.064991 | Stations | 2.181% | 2.255% |  | Plan A | 275 | 8.333% | 10%
2015 | 0.16722 | 0.075376 | Other Line Components | 21.78% | 20.63% |  | Plan B | 300 | 0% | 0%
2016 | 0.14673 | 0.04963 | Vegetation | 30.94% | 19.68% |  | Plan C | 334 | -11.33% | -10%
2013-2016 Avg. | 0.1619 | 0.058065 |  |  |  |  | Plan B-Modified | 305 | -1.667% | -5%
*As Shown in Tables 52 and 53
Table 4 - Interruption Statistics, Other Line Components | [6 empty] | Table 10 - Relative Change in Condition, Vegetation Management
YEAR | SAIDI | SAIFI |  |  |  |  | OPTION | RoW Maintenance, Low/Med. Priority (km) | Relative Change in RoW Maintenance Low/Med by Option* | Reduction in Low/Med. Priority RoW (km) | Improvement in High Priority RoW | Impact to Reliability** | Combined Relative Change in Reliability Impact
2013 | 1.4404 | 0.50181 |  |  |  |  | Current | 104000 | 0% | 0 | 0 | 0 | 0
2014 | 2.0119 | 0.59746 |  |  |  |  | Plan A | 103000 | -0.9615% | -1000 | 1000 | 9% | 8.038%
2015 | 1.6178 | 0.54978 |  |  |  |  | Plan B | 103000 | -0.9615% | -1000 | 1000 | 9% | 8.038%
2016 | 1.3973 | 0.47536 |  |  |  |  | Plan C | 99000 | -4.808% | -2000 | 5000 | 9% | 4.192%
2013-2016 Avg. | 1.6169 | 0.5311 |  |  |  |  | Plan B-Modified | 103000 | -0.9615% | -1000 | 1000 | 9% | 8.038%
*The net change is then assumed to reflect a potential improvement or deterioration in reliability.
Table 5 - Interruptions Statistics, Vegetation
YEAR | SAIDI | SAIFI |  |  |  |  | **Based on vegetation management feeder model impact on reliability
2013 | 1.9338 | 0.44246
2014 | 2.0282 | 0.48405
2015 | 2.2472 | 0.50293
2016 | 2.9803 | 0.59793
2013-2016 Avg. | 2.2974 | 0.50684

## PART C
PART C
Table 11 - SAIDI
SAIDI1: | Avg. 2013-16: 7.43 hours/year | Average Number of Hours a Customer is Interrupted
| Assumptions |  |  | Forecasted Impact on SAIDI by 20222
| Failure Rate/Impact | Contribution to SAIDI | SAIDI Contribution (based on 2013-16) | Plan A | Plan B | Plan C | Plan B-Modified
Poles | ● 0.3k outages/year ● 0.4k customers/outage ● 5 hours/outage | 6.126% | 0.45487 | 12.26% | 9.434% | -18.87% | 6.604%
Stations | ● 0.1k outages/year ● 0.9k customers/outage ● 3 hours/outage | 2.181% | 0.1619 | 9% | 4% | -3% | 0% | From Part B, Tables 7, 8, 9, 10 (color-coded)
Other Line Components | ● 7k outages/year ● 0.1k customers/outage ● 3 hours/outage | 21.78% | 1.6169 | 10% | 0% | -10% | -5%
Vegetation | ● 7k outages/year | 30.94% | 2.2974 | 8.038% | 8.038% | 4.192% | 8.038%
Estimated Impact to SAIDI |  |  |  | 5.612% | 3.152% | -2.102% | 1.803%
Forecasted SAIDI (hours) |  |  |  | 7.0083 | 7.1909 | 7.5811 | 7.2911
1-Excludes force majure and loss of supply event
2-These columns reflect the forecasted impact on SAIDI by the end of 2022. Estimated performance improvement is expressed as a positive value;
performance deterioration is expressed as a negative value
These forecasted impact do not include changes based on the new vegetation management strategy as the data set is incompatible.
Table 12 - SAIFI
SAIFI1: | Avg. 2013-16: 2.58 outages/year | Average Number of Times a Customer is Interrupted
| Assumptions |  |  | Forecasted Impact on SAIFI by 20222
| Failure Rate/Impact | Contribution to SAIFI | SAIFI Contribution (based on 2013-16) | Plan A | Plan B | Plan C | Plan B-Modified3
Poles | ● 0.3k outages/year ● 0.4k customers/outage ● 5 hours/outage | 3.724% | 0.095885 | 12.26% | 9.434% | -18.87% | 6.604%
Stations | ● 0.1k outages/year ● 0.9k customers/outage ● 3 hours/outage | 2.255% | 0.058065 | 9% | 4% | -3% | 0% | From Part B, Tables 7, 8, 9, 10 (color-coded)
Other Line Components | ● 7k outages/year ● 0.1k customers/outage ● 3 hours/outage | 20.63% | 0.5311 | 10% | 0% | -10% | -5%
Vegetation | ● 7k outages/year | 19.68% | 0.50684 | 8.038% | 8.038% | 4.192% | 8.038%
Estimated Impact to SAIFI |  |  |  | 4.304% | 2.024% | -2.008% | 0.7969%
Forecasted SAIDI (instances) |  |  |  | 2.4642 | 2.5229 | 2.6267 | 2.5545
1-Excludes force majure and loss of supply event
2-These columns reflect the forecasted impact on SAIDI by the end of 2022. Estimated performance improvement is expressed as a positive value;
performance deterioration is expressed as a negative value
These forecasted impact do not include changes based on the new vegetation management strategy as the data set is incompatible.