## Pole replacement
| Feeder | # of poles (approx.) | m of line | km of line |  |  |  |  | Historical |  |  |  |  | Forecast
| F2 | 80 | 1153 | 1.153 |  |  |  |  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
| F8 | 311 | 1382 | 1.382 |  |  |  | Net Capital Expenses after Contribution | 18923 | 45854 | 35284 | 4389 | 34352 | 80666.6667 | 80666.6667 | 80666.6667 | 80666.6667 | 80666.6667
| F9 | 166 | 4050 | 4.05 |  |  |  | System O&M | 744673 | 730565 | 744037 | 716586 | 797830 | 813787 | 805808.5 | 809797.75 | 807803.125 | 808800.4375
| (Approx.) Total | 557 | 6585 | 6.585
| Total Poles in system | 730
| F5 | 173
Scenario # | Scenario Description | # of poles /year |  |  |  |  | # of poles/year |  | Historical 2017: Total poles replaced; Historical 2018: Additional years required @ current replacement rate; Forecast 2021: Completion Year; Forecast 2022: To complete pole replacement under 10 years | To complete pole replacement under 5 years
|  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
1 | No Poles past age 55 years old | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 140 | 29.7857 | years required |  | 2057.7857 | 41.7 | poles/year 2029-2038 | 83.4 | poles/year 2029-2033
2 | No Poles past age 65 years old | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 70 | 69.5714 | years required |  | 2097.5714 | 48.7 | poles/year 2029-2038 | 97.4 | poles/year 2029-2034
3 | Replace all 4kV poles with 25kV capable poles | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 210 | 16.5238 | years required |  | 2044.5238 | 34.7 | poles/year 2029-2038 | 69.4 | poles/year 2029-2035
4 | Custom (define # of additional years required to complete pole replacement) | 27.85 | 27.85 | 27.85 | 27.85 | 27.85 | 27.85 | 27.85 | 27.85 | 27.85 | 27.85 | 278.5 | 10 | years required |  | 2038
| Assumptions | # of poles/year 2025: 4; # of poles/year 2026: # of poles to be replaced by contractor; # of poles/year 2027: 14000; # of poles/year 2028: Contractor cost for pole |  | ** 14 poles with 6 new tx:
| Scenario 2 utilizes historical replacement rate of 6 for base | # of poles/year 2027: $/pole; # of poles/year 2028: $/km cable | $/tx | 2.3333 | poles/tx
| Scenario 3 caps pole replacement program to 20 years | # of poles/year 2027: 2000; # of poles/year 2028: 50000 | 2000 | 6 | pole/tx (approx) |  | *every 3 poles a transformer is replaced, every 6th pole transformer is relocated
| All scenarios assume constant replacement |  |  |  | Year | Targetted Poles Replaced to Date | Targetted poles | # of Poles | km of cable | Pole ($) | Cable ($) | Tx ($) | Station ($) | Total ($) | Average | Notes
| All scenarios smooth out replacements | # of poles /year 2022: 2015; # of poles/year 2024: 0; # of poles/year 2025: 6; # of poles/year 2027: 12000; # of poles/year 2028: 0 | 2000 |  | 14000
| Year 2026 is 8-year mark after transformer is refurbished | # of poles /year 2022: 2016; # of poles/year 2024: 0; # of poles/year 2025: 6; # of poles/year 2027: 12000; # of poles/year 2028: 0 | 2000 |  | 14000
| 11 poles inspected in 2018 requiring replacement | # of poles /year 2022: 2017; # of poles/year 2024: 0; # of poles/year 2025: 6; # of poles/year 2027: 12000; # of poles/year 2028: 0 | 2000 |  | 14000
|  | # of poles /year 2022: 2018; # of poles/year 2024: 0; # of poles/year 2025: 6; # of poles/year 2027: 12000; # of poles/year 2028: 0 | 2000 |  | 14000
[5 empty] | 2019 | 8 | 8 | 14 |  | 76000 | 0 | 4666.6667 |  | 80666.6667 | 218679.1667 | > Flat line it at 14 poles, push to $70k
[5 empty] | 2020 | 16 | 8 | 14 |  | 76000 | 0 | 4666.6667 |  | 80666.6667 | 218679.1667 | > Push difference to next rate filing
[5 empty] | 2021 | 24 | 8 | 14 |  | 76000 | 0 | 4666.6667 |  | 80666.6667 | 218679.1667
[5 empty] | 2022 | 32 | 8 | 14 |  | 76000 | 0 | 4666.6667 |  | 80666.6667 | 218679.1667
[5 empty] | 2023 | 40 | 8 | 14 |  | 76000 | 0 | 4666.6667 |  | 80666.6667 | 218679.1667
|  |  |  | 20 | 2024 | 68 | 28 | 34 |  | 116000 | 0 | 11333.3333 |  | 127333.3333 | 218679.1667
| Feeder | # of poles | km of line | 20 | 2025 | 96 | 28 | 34 |  | 116000 | 0 | 11333.3333 |  | 127333.3333 | 218679.1667
| F2 | 80 | 1.153 | 20 | 2026 | 124 | 28 | 34 | 0.2306 | 116000 | 11530 | 11333.3333 | 750000 | 888863.3333 | 218679.1667 | > 20% of F2 cables
| F8 | 311 | 1.382 | 20 | 2027 | 152 | 28 | 34 | 0.9224 | 116000 | 46120 | 11333.3333 |  | 173453.3333 | 218679.1667 | > 80% of F2 cables
| F9 | 166 | 4.05 | 20 | 2028 | 180 | 28 | 34 |  | 116000 | 0 | 11333.3333 |  | 127333.3333 | 218679.1667
| (Approx.) Total | 557 | 6.585 | 25 | 2029 | 213 | 33 | 39 |  | 126000 | 0 | 13000 |  | 139000 | 218679.1667
| F2+F9 | 246 | 5.203 | 25 | 2030 | 246 | 33 | 39 |  | 126000 | 0 | 13000 |  | 139000 | 218679.1667
|  |  |  | 25 | 2031 | 279 | 33 | 39 | 0.81 | 126000 | 40500 | 13000 | 750000 | 929500 | 218679.1667 | > 20% of F9 cables
|  |  |  | 25 | 2032 | 312 | 33 | 39 | 3.24 | 126000 | 162000 | 13000 |  | 301000 | 218679.1667 | > 80% of F9 cables
|  |  |  | 25 | 2033 | 345 | 33 | 39 |  | 126000 | 0 | 13000 |  | 139000 | 218679.1667
|  |  |  | 30 | 2034 | 383 | 38 | 44 |  | 136000 | 0 | 14666.6667 |  | 150666.6667 | 218679.1667
|  |  |  | 30 | 2035 | 421 | 38 | 44 | 0.691 | 136000 | 34550 | 14666.6667 |  | 185216.6667 | 218679.1667 | > 50% of F8 cables
|  |  |  | 30 | 2036 | 459 | 38 | 44 | 0.691 | 136000 | 34550 | 14666.6667 |  | 185216.6667 | 218679.1667 | > 50% of F8 cables
|  |  |  | 30 | 2037 | 497 | 38 | 44 |  | 136000 | 0 | 14666.6667 |  | 150666.6667 | 218679.1667
|  |  |  | 30 | 2038 | 535 | 38 | 44 |  | 136000 | 0 | 14666.6667 |  | 150666.6667 | 218679.1667
|  | # of poles /year 2023: 535; # of poles/year 2025: 655 |  |  | 4373583.3333 | 218679.1667 | per year on average
|  | # of poles /year 2022: Contractors are needed to help replace poles | [7 empty] | DSP Period End |  | Targetted Poles Replaced | Poles Remaining on Feeders to be Replaced for Conversion
|  | # of poles /year 2022: Contractors are experienced and have tools to deal with pole replacements without having a planned outage | [10 empty] | F2 | F9 | F8
|  | # of poles /year 2022: Contractors are higher cost but maintain the reliaiblity indices with no outages or very little | [7 empty] | 2023 |  | 40 | 40 | 166 | 311
[19 empty] | 2028 |  | 140 | 0 | 66 | 311
[19 empty] | 2033 |  | 165 | - | 0 | 212
[19 empty] | 2038 |  | 190 | - | - | 22
2nd Transformer Replaced
1st Transformer Replaced
Feeder/Station Conversion 20-year Plan
All poles originally installed for 4kV feeders will need to replaced to suport 25kV feeders. The estimated number of poles and cables is based on CPUC's line diagram and counting the approximate amount of poles on the 4kV feeders.
In Years 1-5 (2019-2023), poles that are "failed" are replaced with the historical replacement rate of 6 poles and the remaining poles for replacement are targetted mostly on feeder F2. This sums up to 14 poles per year.
In Years 6-10 (2024-2028), continue with pole replacement program and increase the count of poles replaced by 2028 to complete all pole replacements on F2 and to begin pole replacements on F9. Ideeally, the pole replacements on F9 would begin late 2026. In 2026, the station that feeds into F2 is rebuilt and presents the option to move the load off Hydro One's 25kV feeder. Near the end of this term and beginning of the next five year block, the F9 feeder can be converted to a hybrid 25kV/4kV system with the use of conversion transformers. Targetting feeder F9 over feeder F8 is advantagoues and beneficial for CUCP because it would improve the losses experienced on the system faster, since majority of losses are experienced on F9.
In Years 11-15 (2029-2033), pole replacement continues for F9 and will begin for F8 mid period. The underlying assumption still runs that 6 poles/year are "failed" and require replacement, with the remaining poles in the replacement plan are targetted for feeder F9 primarily, and once completed followed by poles on feeder F8. By 2032, majority if not all poles on F9 should be replaced allowing for the conversion of the second transformer.
In Years 16-20 (2034-2038), pole replacement is steady with the remaining poles on feeder F8 decreasing. By the end of the 20 year plan, feeder F8 will converted to the 25kV system with very few poles remaining. Pole replacement will return to replacing "fail" poles based on condition assessment and service requests in the next DSP period.