## OEB
[11 empty] | File Number: |  | 0
Exhibit:
Tab:
Schedule:
Page:
Date:
OEB Appendix 2-BB
Service Life Comparison
Table F-1 from Kinetrics Report1
|  | Asset Details |  |  | Useful Life |  |  | USoA Account Number | USoA Account Description | Current |  | Proposed |  | Outside Range of Min, Max TUL?
Parent* | # | Category¦ Component ¦ Type |  |  | MIN UL | TUL | MAX UL |  |  | Years | Rate | Years | Rate | Below Min TUL | Above Max TUL
OH | 1 | Fully Dressed Wood Poles | Overall |  | 35 | 45 | 75 | 1830 | Poles, Towers and Fixtures | 40 | 2.5% | 40 | 2.5% | No | No
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 2 | Fully Dressed Concrete Poles | Overall |  | 50 | 60 | 80 | 1830 | Poles, Towers and Fixtures (Streetlighting Assembly) | 40 | 2.5% | 40 | 2.5% | Yes | No
[8 empty] | 1830 | Poles, Towers and Fixtures | 50 | 2% | 50 | 2% | No | No
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95 | 1830 | Poles, Towers and Fixtures | 50 | 2% | 50 | 2% | No | No
| 3 | Fully Dressed Steel Poles | Overall |  | 60 | 60 | 80
|  |  | Cross Arm | Wood | 20 | 40 | 55
|  |  |  | Steel | 30 | 70 | 95
| 4 | OH Line Switch |  |  | 30 | 45 | 55 | 1835 | Overhead Conductors and Devices | 30 | 3.333% | 30 | 3.333% | No | No
| 5 | OH Line Switch Motor |  |  | 15 | 25 | 25
| 6 | OH Line Switch RTU |  |  | 15 | 20 | 20
| 7 | OH Integral Switches |  |  | 35 | 45 | 60 | 1835 | Overhead Conductors and Devices | 45 | 2.222% | 45 | 2.222% | No | No
| 8 | OH Conductors |  |  | 50 | 60 | 75 | 1835 | Overhead Conductors and Devices (Streetlighting Assembly) | 40 | 2.5% | 40 | 2.5% | Yes | No
[8 empty] | 1835 | Overhead Conductors and Devices | 50 | 2% | 50 | 2% | No | No
[8 empty] | 1855 | Services (Overhead & Underground) | 50 | 2% | 50 | 2% | No | No
| 9 | OH Transformers & Voltage Regulators |  |  | 30 | 40 | 60 | 1850 | Line Transformers | 30 | 3.333% | 30 | 3.333% | No | No
| 10 | OH Shunt Capacitor Banks |  |  | 25 | 30 | 40
| 11 | Reclosers |  |  | 25 | 40 | 55
TS & MS | 12 | Power Transformers | Overall |  | 30 | 45 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV | 32 | 3.125% | 32 | 3.125% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 32 | 3.125% | 32 | 3.125% | No | No
|  |  | Bushing |  | 10 | 20 | 30
|  |  | Tap Changer |  | 20 | 30 | 60
| 13 | Station Service Transformer |  |  | 30 | 45 | 55 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV | 32 | 3.125% | 32 | 3.125% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 32 | 3.125% | 32 | 3.125% | No | No
| 14 | Station Grounding Transformer |  |  | 30 | 40 | 40 | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 25 | 4% | 25 | 4% | Yes | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 30 | 3.333% | 30 | 3.333% | No | No
| 15 | Station DC System | Overall |  | 10 | 20 | 30
|  |  | Battery Bank |  | 10 | 15 | 15 | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 10 | 10% | 10 | 10% | No | No
|  |  | Charger |  | 20 | 20 | 30 | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 20 | 5% | 20 | 5% | No | No
| 16 | Station Metal Clad Switchgear | Overall |  | 30 | 40 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV | 50 | 2% | 50 | 2% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 40 | 2.5% | 40 | 2.5% | No | No
|  |  | Removable Breaker |  | 25 | 40 | 60
| 17 | Station Independent Breakers |  |  | 35 | 45 | 65 | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 30 | 3.333% | 30 | 3.333% | Yes | No
| 18 | Station Switch |  |  | 30 | 50 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV | 30 | 3.333% | 30 | 3.333% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 30 | 3.333% | 30 | 3.333% | No | No
| 19 | Electromechanical Relays |  |  | 25 | 35 | 50
| 20 | Solid State Relays |  |  | 10 | 30 | 45 | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 10 | 10% | 10 | 10% | No | No
| 21 | Digital & Numeric Relays |  |  | 15 | 20 | 20
| 22 | Rigid Busbars |  |  | 30 | 55 | 60 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV | 35 | 2.857% | 35 | 2.857% | No | No
| 23 | Steel Structure |  |  | 35 | 50 | 90 | 1815 | Transformer Station Equipment - Normally Primary Above 50 kV | 35 | 2.857% | 35 | 2.857% | No | No
[8 empty] | 1820 | Distribution Station Equipment - Normally Primary Below 50 kV | 35 | 2.857% | 35 | 2.857% | No | No
UG | 24 | Primary Paper Insulated Lead Covered (PILC) Cables |  |  | 60 | 65 | 75 | 1845 | Underground Conductors and Devices | 60 | 1.667% | 60 | 1.667% | No | No
| 25 | Primary Ethylene-Propylene Rubber (EPR) Cables |  |  | 20 | 25 | 25
| 26 | Primary Non-Tree Retardant (TR) Cross Linked Polyethylene (XLPE) Cables Direct Buried |  |  | 20 | 25 | 30
| 27 | Primary Non-TR XLPE Cables in Duct |  |  | 20 | 25 | 30
| 28 | Primary TR XLPE Cables Direct Buried |  |  | 25 | 30 | 35 | 1845 | Underground Conductors and Devices | 20 | 5% | 20 | 5% | Yes | No
| 29 | Primary TR XLPE Cables in Duct |  |  | 35 | 40 | 55 | 1845 | Underground Conductors and Devices | 40 | 2.5% | 40 | 2.5% | No | No
| 30 | Secondary PILC Cables |  |  | 70 | 75 | 80
| 31 | Secondary Cables Direct Buried |  |  | 25 | 35 | 40 | 1845 | Underground Conductors and Devices | 20 | 5% | 20 | 5% | Yes | No
[8 empty] | 1855 | Services (Overhead & Underground) | 20 | 5% | 20 | 5% | Yes | No
| 32 | Secondary Cables in Duct |  |  | 35 | 40 | 60 | 1845 | Underground Conductors and Devices | 40 | 2.5% | 40 | 2.5% | No | No
[8 empty] | 1855 | Services (Overhead & Underground) | 40 | 2.5% | 40 | 2.5% | No | No
| 33 | Network Tranformers | Overall |  | 20 | 35 | 50 | 1850 | Line Transformers | 20 | 5% | 20 | 5% | No | No
|  |  | Protector |  | 20 | 35 | 40 | 1850 | Line Transformers | 20 | 5% | 20 | 5% | No | No
| 34 | Pad-Mounted Transformers |  |  | 25 | 40 | 45 | 1850 | Line Transformers | 30 | 3.333% | 30 | 3.333% | No | No
| 35 | Submersible/Vault Transformers |  |  | 25 | 35 | 45 | 1850 | Line Transformers | 30 | 3.333% | 30 | 3.333% | No | No
| 36 | UG Foundation |  |  | 35 | 55 | 70 | 1840 | Underground Conduit | 50 | 2% | 50 | 2% | No | No
| 37 | UG Vaults | Overall |  | 40 | 60 | 80 | 1840 | Underground Conduit | 40 | 2.5% | 40 | 2.5% | No | No
|  |  | Roof |  | 20 | 30 | 45 | 1840 | Underground Conduit | 20 | 5% | 20 | 5% | No | No
| 38 | UG Vault Switches |  |  | 20 | 35 | 50 | 1845 | Underground Conductors and Devices | 30 | 3.333% | 30 | 3.333% | No | No
| 39 | Pad-Mounted Switchgear |  |  | 20 | 30 | 45 | 1845 | Underground Conductors and Devices | 20 | 5% | 20 | 5% | No | No
| 40 | Ducts |  |  | 30 | 50 | 85 | 1840 | Underground Conduit | 30 | 3.333% | 30 | 3.333% | No | No
| 41 | Concrete Encased Duct Banks |  |  | 35 | 55 | 80
| 42 | Cable Chambers |  |  | 50 | 60 | 80 | 1840 | Underground Conduit | 50 | 2% | 50 | 2% | No | No
[8 empty] | 1840 | Underground Conduit (Cable Chamber Roof) | 20 | 5% | 20 | 5% | Yes | No
S | 43 | Remote SCADA |  |  | 15 | 20 | 30 | 1835 | Overhead Conductors & Devices | 30 | 3.333% | 30 | 3.333% | No | No
[8 empty] | 1980 | System Supervisory Equipment | 15 | 6.667% | 15 | 6.667% | No | No
[8 empty] | 1980 | System Supervisory Equipment | 30 | 3.333% | 30 | 3.333% | No | No
Table F-2 from Kinetrics Report1
|  | Asset Details |  |  | Useful Life Range |  |  | USoA Account Number | USoA Account Description | Current |  | Proposed |  | Outside Range of Min, Max TUL?
| # | Category¦ Component ¦ Type | [7 empty] | Years | Rate | Years | Rate | Below Min Range | Above Max Range
| 1 | Office Equipment |  |  | 5 | 15 |  | 1915 | Office Furniture and Equipment | 10 | 10% | 10 | 10% | No | No
| 2 | Vehicles | Trucks & Buckets |  | 5 | 15 |  | 1930 | Transportation Equipment | 8 | 12.5% | 8 | 12.5% | No | No
|  |  | Trailers |  | 5 | 20 |  | 1930 | Transportation Equipment | 5 | 20% | 5 | 20% | No | No
|  |  | Vans |  | 5 | 10
| 3 | Administrative Buildings |  |  | 50 | 75 |  | 1908 | Buildings and Fixtures | 20 | 5% | 20 | 5% | Yes | No
[8 empty] | 1908 | Buildings and Fixtures | 30 | 3.333% | 30 | 3.333% | Yes | No
[8 empty] | 1908 | Buildings and Fixtures | 50 | 2% | 50 | 2% | No | No
[8 empty] | 1908 | Buildings and Fixtures | 75 | 1.333% | 75 | 1.333% | No | No
| 4 | Leasehold Improvements |  |  | Lease dependent |  |  | 1910 | Leasehold Improvements | 5 | 20% | 5 | 20% | Yes | Yes
| 5 | Station Buildings | Station Buildings |  | 50 | 75 |  | 1808 | Buildings and Fixtures | 20 | 5% | 20 | 5% | Yes | No
[8 empty] | 1808 | Buildings and Fixtures | 30 | 3.333% | 30 | 3.333% | Yes | No
[8 empty] | 1808 | Buildings and Fixtures | 36 | 2.778% | 36 | 2.778% | Yes | No
[8 empty] | 1808 | Buildings and Fixtures | 75 | 1.333% | 75 | 1.333% | No | No
|  |  | Parking |  | 25 | 30 |  | 1808 | Buildings and Fixtures | 30 | 3.333% | 30 | 3.333% | No | No
|  |  | Fence |  | 25 | 60 |  | 1808 | Buildings and Fixtures | 30 | 3.333% | 30 | 3.333% | No | No
|  |  | Roof |  | 20 | 30 |  | 1808 | Buildings and Fixtures | 20 | 5% | 20 | 5% | No | No
| 6 | Computer Equipment | Hardware |  | 3 | 5 |  | 1920 | Computer Equipment - Hardware | 4 | 25% | 4 | 25% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware | 5 | 20% | 5 | 20% | No | No
[8 empty] | 1920 | Computer Equipment - Hardware | 6 | 16.67% | 6 | 16.67% | No | Yes
|  |  | Software |  | 2 | 5 |  | 1611 | Computer Software | 4 | 25% | 4 | 25% | No | No
[8 empty] | 1611 | Computer Software | 5 | 20% | 5 | 20% | No | No
[8 empty] | 1611 | Computer Software | 10 | 10% | 10 | 10% | No | Yes
| 7 | Equipment | Power Operated |  | 5 | 10
|  |  | Stores |  | 5 | 10 |  | 1935 | Stores Equipment | 10 | 10% | 10 | 10% | No | No
|  |  | Tools, Shop, Garage Equipment |  | 5 | 10 |  | 1940 | Tools, Shop and Garage Equipment | 6 | 16.67% | 6 | 16.67% | No | No
[8 empty] | 1940 | Tools, Shop and Garage Equipment | 10 | 10% | 10 | 10% | No | No
[8 empty] | 1950 | Service Equipment | 8 | 12.5% | 8 | 12.5% | No | No
[8 empty] | 1960 | Miscellaneous Equipment | 10 | 10% | 10 | 10% | No | No
[8 empty] | 1930 | Transportation Equipment | 8 | 12.5% | 8 | 12.5% | No | No
|  |  | Measurement & Testing Equipment |  | 5 | 10 |  | 1945 | Measurement and Testing Equipment | 10 | 10% | 10 | 10% | No | No
[8 empty] | 1970 | Load Management Controls - Customer Premises | 10 | 10% | 10 | 10% | No | No
[8 empty] | 1975 | Load Management Controls - Utility Premises | 10 | 10% | 10 | 10% | No | No
| 8 | Communication | Towers |  | 60 | 70
|  |  | Wireless |  | 2 | 10 |  | 1955 | Communication Equipment | 5 | 20% | 5 | 20% | No | No
[8 empty] | 1955 | Communication Equipment | 10 | 10% | 10 | 10% | No | No
| 9 | Residential Energy Meters |  |  | 25 | 35 |  | 1860 | Meters | 25 | 4% | 25 | 4% | No | No
| 10 | Industrial/Commercial Energy Meters |  |  | 25 | 35 |  | 1860 | Meters | 25 | 4% | 25 | 4% | No | No
| 11 | Wholesale Energy Meters |  |  | 15 | 30 |  | 1860 | Meters | 25 | 4% | 25 | 4% | No | No
| 12 | Current & Potential Transformer (CT & PT) |  |  | 35 | 50 |  | 1860 | Meters | 40 | 2.5% | 40 | 2.5% | No | No
| 13 | Smart Meters |  |  | 5 | 15 |  | 1860 | Meters (Smart Meters) | 15 | 6.667% | 15 | 6.667% | No | No
| 14 | Repeaters - Smart Metering |  |  | 10 | 15
| 15 | Data Collectors - Smart Metering |  |  | 15 | 20
Additional Notes
The useful life of Toronto Hydro handwells is twenty years. The streetlighting handwells is fourty years
The useful life of the IT related data centre is ten years.
* TS & MS = Transformer and Municipal Stations UG = Underground Systems S = Monitoring and Control Systems
Note 1: | Tables F-1 and F-2 above are to be used as a reference in order to complete columns J, K, L and N.
| See pages 17-19 of Kinetrics Report | [6 empty] | `