## Streetlight Conversion Summary
ENTEGRUS
PHASE I - June - October 2016
Existing System (HPS) | [5 empty] | LED
Existing Rated Wattage (W) | Estimated Input Wattage | Measured Input Wattage (W) | Quantities | Total Estimated Connected Load | Total HPS Load (kW) | Actual Input Wattage (W) | LED Load (W) | LOAD/DEMAND REDUCTION (kW)
70 | 95 | 86 | 1 | #REF! | 0.086 | 41 | 0.041 | 0.045
100 | 130 | 112 | 3198 | #REF! | 358.176 | 41 | 131.118 | 227.058
150 | 190 | 152 | 1840 | #REF! | 279.68 | 53 | 97.52 | 182.16
200 | 250 | 215 | 5 | #REF! | 1.075 | 67 | 0.335 | 0.74
250 | 300 | 286 | 943 | #REF! | 269.698 | 67 | 63.181 | 206.517
400 | 465 | 389 | 35 | #REF! | 13.615 | 108 | 3.78 | 9.835
|  |  | 6022 |  | 922.33 |  |  | 626.355
ENTEGRUS
PHASE II - November 2016 - April 2017
Existing System (HPS) | [5 empty] | LED
Existing Rated Wattage (W) | Estimated Input Wattage | Measured Input Wattage (W) | Quantities | Total Estimated Connected Load | Total HPS Load (kW) | Actual Input Wattage (W) | LED Load (W) | LOAD REDUCTION (kW)
70 | 95 | 86 | 995 | #REF! | 85.57 | 41 | 40.795 | 44.775
100 | 130 | 112 | 1202 | #REF! | 134.624 | 41 | 49.282 | 85.342
150 | 190 | 152 | 495 | #REF! | 75.24 | 53 | 26.235 | 49.005
200 | 250 | 215 | 0 | #REF! | 0 | 67 | 0 | 0
250 | 300 | 286 | 450 | #REF! | 128.7 | 67 | 30.15 | 98.55
400 | 465 | 389 | 30 | #REF! | 11.67 | 108 | 3.24 | 8.43
|  |  | 3172 |  | 435.804 |  |  | 286.102
[7 empty] | TOTAL: | 912.457

## Payback Chatham-Kent (HydroOne) (hidden)
Hydro One Chatham-Kent
LED Streetlighting Conversion Project
Simple Payback Calculation (January 2016)
Energy Cost per Kwh: |  |  | #REF!
Annual Operating Hours: |  |  | 4380
|  | Cost per kW (Demand): | #REF!
Cobra Head Evaluation (HPS to LED)
Existing System (HPS) | [6 empty] | LED Option
Existing Rated Wattage | Actual Input Wattage | Estimated Quantity | Total Connected Load | Annual Energy Cost | Annual Maintenance Cost | Total Annual Operating Costs | LED System Parameters | Actual Input Wattage | Estimated Quantity | Total Connected Load | Annual Energy Cost | Annual Maintenance Cost | Total Annual Operating Costs | Unit Cost | Photocell | Installation Costs | Contingency | Unit Installed Cost | saveONenergy Incentive | Incentive | Total Capital Cost
70 | 95 | 2 | 0.19 | #REF! | 34 | #REF! | 12 LED 1250mA | 50 | 2 | 0.1 | #REF! | 4.8 | #REF! | 253.17 | 22.85 | 100 | 15% | 432.423 | 88 | 176 | 688.846
100 | 130 | 337 | 43.81 | #REF! | 5729 | #REF! | 12 LED 1250mA | 50 | 337 | 16.85 | #REF! | 808.8 | #REF! | 253.17 | 22.85 | 100 | 15% | 432.423 | 88 | 29656 | 116070.551
150 | 190 | 175 | 33.25 | #REF! | 2975 | #REF! | 36 LED 525 mA | 60 | 175 | 10.5 | #REF! | 420 | #REF! | 334.9 | 22.85 | 100 | 15% | 526.4125 | 88 | 15400 | 76722.1875
200 | 250 | 2 | 0.5 | #REF! | 44 | #REF! | 60 LED 600mA | 60 | 2 | 0.12 | #REF! | 4.8 | #REF! | 426.92 | 22.85 | 100 | 15% | 632.2355 | 126 | 252 | 1012.471
250 | 300 | 53 | 15.9 | #REF! | 1166 | #REF! | 60 LED 600mA | 113 | 53 | 5.989 | #REF! | 127.2 | #REF! | 426.92 | 22.85 | 100 | 15% | 632.2355 | 126 | 6678 | 26830.4815
400 | 465 | 0 | 0 | #REF! | 0 | #REF! | 72 LED 700mA | 158 | 0 | 0 | #REF! | 0 | #REF! | 450.03 | 22.85 | 100 | 15% | 658.812 | 183 | 0 | 0
Totals: |  | 569 | 93.65 | #REF! | 9948 | #REF! |  |  | 569 | 33.559 | #REF! | 1365.6 | #REF! | [6 empty] | 52162 | 221324.537
(Decorative - 49)
| Initial Capital Cost: |  | 221324.537 |  |  |  | Annual Energy Savings (GWh): | #REF!
15% Project Management: |  |  | 33198.6805 |  | Annual Energy Cost Savings: |  |  | #REF!
|  | TOTAL PROJECT COST: | 254523.2175 |  | Annual Reduction in Maintenance Costs: |  |  | 8582.4
[5 empty] | #REF! |  |  | #REF!
[5 empty] | Reduction in Connected Load: |  |  | 60.091 | kW
[5 empty] | Simple Payback: |  |  | #REF! | Years
[7 empty] | #REF! | #REF!
[7 empty] | IRR: | #REF!
Notes: | Maintenance Costs estimate for LED:
Driver replacement; 2% over 20 Years @ $800 each including labour; → $8.00 per luminaire → $0.40 per luminaire annually
Photocontrol replacement will be similar to that for the LED luminaires
Washing every 5 years at $10 per luminaire → $2.00 annually
Maintenance Costs estimate for HPS Luminaires;
Lamp cost; 70 - 150W = $10, 200 - 400W = $15
Individual lamp replacement labour @10% of luminaires per year @$75 per change
Ballast and luminaire replacements not included
Installation Replacement Cost per LED luminaire; $75

## Configurations (hidden)
Table 1; Energus Reference Streetlight Configurations
Cobra Head Style
Energus Reference | Road Classification | Pedestrian Conflict | IESNA RP-8-05 Recommendations |  |  |  | Number of Lanes | Lane width | Median | Parking Bay |  | Bike Lanes |  | Luminaire Mounting Height | Pole Setback | Arm Length | Spacing | Arrangement | HPS Lamp Watts | LED Replacement
|  |  | Luminance | Uniformity |  | Lv
|  |  | cd/m² | Avg/Min | Max/Min | Max/Avg |  |  |  | No. | Width | No. | Width
LL-1 | Local | Low | 0.3 | 6 | 10 | 0.4 | 2 | 3.6 | [5 empty] | 7.3 | 1.2 | 2.4 | 55 | One Side | 100 | 50
LL-2 | Local | Low | 0.3 | 6 | 10 | 0.4 | 2 | 3.6 | [5 empty] | 7.3 | 1.2 | 2.4 | 91 | Staggered | 100 | 50
LL-3 | Local | Low | 0.3 | 6 | 10 | 0.4 | 2 | 3.6 | [5 empty] | 7.3 | 1 | 1.8 | 60 | One Side | 150
LM-1 | Local | Medium
LM-2 | Local | Medium
CL-1 | Collector | Low | 0.4 | 4 | 8 | 0.4 | 2 | 3.6 | [5 empty] | 7.3 | 1.5 | 1.8 | 62 | One Side | 100 | 50
CL-2 | Collector | Low | 0.4 | 4 | 8 | 0.4 | 2 | 3.6 |  |  |  | 1 | 1.5 | 7.3 | 1.8 | 2.4 | 38 | One Side | 150 | 95
CL-3 | Collector | Low | 0.4 | 4 | 8 | 0.4 | 3 | 3.6 | [5 empty] | 7.3 | 1.8 | 2.4 | 64 | One Side | 150 | 95
CL-4 | Collector | Low | 0.4 | 4 | 8 | 0.4 | 4 | 4.2 | [5 empty] | 7.6 | 1 | 2.4 | 61 | One Side | 150
CM-1 | Collector | Medium | 0.6 | 3.5 | 6 | 0.4 | 3 | 3.6 | [5 empty] | 7.3 | 1.8 | 2.4 | 45 | One Side | 250 | 190
CM-2 | Collector | Medium | 0.6 | 3.5 | 6 | 0.4 | 3 | 3.6 | [5 empty] | 7.3 | 1.8 | 2.4 | 45 | Staggered | 150 | 95
ML-1 | Major | Low | 0.6 | 3.5 | 6 | 0.3 | 2 | 4.2 |  | 2 | 4.2 |  |  | 7.6 | 0.5 | 1.2 | 41 | Staggered | 150 | 95
ML-2 | Major | Low | 0.6 | 3.5 | 6 | 0.3 | 2 | 3.6 |  | 1 | 2.4 |  |  | 7.3 | 0.5 | 2.4 | 36 | One Side | 150 | 95
ML-3 | Major | Low | 0.6 | 3.5 | 6 | 0.3 | 2 | 4.2 | 3.6 |  |  |  |  | 7.6 | 0.5 | 2.4 | 62 | One Side | 200
ML-4 | Major | Low | 0.6 | 3.5 | 6 | 0.3 | 4 | 4.2 | [5 empty] | 7.6 | 1 | 2.4 | 61 | One Side | 250
ML-5 | Major | Low | 0.6 | 3.5 | 6 | 0.3 | 4 | 3.6 | 2.5 |  |  |  |  | 7.3 | 1.2 | 2.4 | 35 | One Side | 250 | 190
ML-6 | Major | Low | 0.6 | 3.5 | 6 | 0.3 | 4 | 3.6 | [5 empty] | 7.6 | 1.8 | 1.8 | 70 | Staggered | 250 | 190
MM-1 | Major | Medium | 0.9 | 3 | 5 | 0.3 | 4 | 3.6 | 2.5 |  |  |  |  | 7.3 | 1.2 | 2.4 | 40 | Opposite | 250 | 190
Energus Reference | Road Classification | Pedestrian Conflict | LED Suppliers
|  |  | AEL | Cooper Lighting | Philips Lumec | LRL | Cree | GE
Input Watts
LL-1 | Local | Low | 49 |  |  | 60
LL-2 | Local | Low | 49 |  |  | 60
LL-3 | Local | Low | 49 |  |  | 60
LM-1 | Local | Medium
LM-2 | Local | Medium
CL-1 | Collector | Low |  |  |  | 80
CL-2 | Collector | Low | [5 empty] | 98
CL-3 | Collector | Low | 94 |  |  |  |  | 98
CL-4 | Collector | Low
CM-1 | Collector | Medium | 94 | 101 |  | 80 |  | 98
CM-2 | Collector | Medium
ML-1 | Major | Low
ML-2 | Major | Low
ML-3 | Major | Low
ML-4 | Major | Low
ML-5 | Major | Low | 187
ML-6 | Major | Low | 187
MM-1 | Major | Medium | 187 | 154 |  | 175