## Plots
|  | OEB | Median | THESL | OEB | Median 1 | THESL | OEB | Median 2 | THESL
Wood Pole Replacement | Each | 5604 | 7371.7619 | 7434 | 5604 | 7437.9356 | 7434 | 5604 | 7664.8401 | 7434
UG Cable Replacement-XLPE | per Meter | 56 | 95.619 | 96 | 56 | 96.0254 | 96 | 56 | 98.3419 | 96
OH Switches Replacement | Each | 30882 | 21589.5238 | 21062 | 30882 | 22268.7089 | 21062 | 30882 | 23451.1048 | 21062
Pole Top Transformer Replacement | Each | 0 | 8651.9048 | 11761 | 0 | 9300.9947 | 11761 | 0 | 10514.3946 | 11761
Padmount / UG Transformer Replacement | Each | 16817 | 21491.2857 | 21454 | 16817 | 21645.0554 | 21454 | 16817 | 23478.9932 | 21454
Network Transformer / Protector Replacement | Each | 68105 | 89253.881 | 88943 | 68105 | 87990.5356 | 88943 | 68105 | 95369.2707 | 88943
Breaker Replacement | Each | 167542 | 85228.1429 | 85242 | 167542 | 85127.7378 | 85242 | 167542 | 92937.5642 | 85242
Switchgear Replacement |  | 1713484 |  | 1529625 | 1713484 |  | 1529625 | 1713484 |  | 1529625
Vegetation Management | per KM |  | 5358.0952 | 2111 |  | 5037 | 2111 |  | 5235 | 2111
Pole Test and Treat | Each | 18 | 45.7143 | 18 | 18 | 52 | 18 | 18 | 54 | 18
Overhead Line Patrol | Meter | 44 | 49.5238 | 44 | 44 | 115 | 44 | 44 | 118 | 44
Vault Inspection | Each |  | 255.2381 | 253 |  | 275 | 253 |  | 278 | 253
|  | OEB | Median | THESL | OEB | Median 1 | THESL | OEB | Median 2 | THESL
Vegetation Management | per KM | 0 | 3739.1667 | 2111 | 0 | 3792.2042 | 2111 | 0 | 3965.3229 | 2111
Pole Test and Treat | Each | 18 | 17.1429 | 18 | 18 | 18.898 | 18 | 18 | 18.898 | 18
Overhead Line Patrol | Meter | 44 | 43.8095 | 44 | 44 | 47.2151 | 44 | 44 | 47.2151 | 44
Vault Inspection | Each | 0 | 253 | 253 | 0 | 261.0022 | 253 | 0 | 272.3501 | 253
Inferred Unit Costs4
| THESL1 | OEB2
Asset Categories
Wood Pole Replacement | 7434 | 5604
UG Cable Replacement-XLPE | 96 | 56
OH Switches Replacement | 21062 | 30882
Pole Top Transformer Replacement | 11761 | Note 3
Padmount / UG Transformer Replacement | 21454 | 16817
Network Transformer / Protector Replacement | 88943 | 68105
Breaker Replacement | 85242 | 167542
Switchgear Replacement | 1529625 | 1713484
Maintenance Practices
Vegetation Management | 2111 | Note 3
Pole Test and Treat | 18 | 18
Overhead Line Patrol | 44 | 44
Vault Inspection | 253 | Note 3
| Units | THESL1 | Median | Median 1 | Median 2
Asset Categories
Wood Pole Replacement | Each | 7434 | 7371.7619 | 7437.9356 | 7664.8401
UG Cable Replacement-XLPE | per Meter | 96 | 95.619 | 96.0254 | 98.3419
OH Switches Replacement | Each | 21062 | 21589.5238 | 22268.7089 | 23451.1048
Pole Top Transformer Replacement | Each | 11761 | 8651.9048 | 9300.9947 | 10514.3946
Padmount / UG Transformer Replacement | Each | 21454 | 21491.2857 | 21645.0554 | 23478.9932
Network Transformer / Protector Replacement | Each | 88943 | 89253.881 | 87990.5356 | 95369.2707
Breaker Replacement | Each | 85242 | 85228.1429 | 85127.7378 | 92937.5642
Switchgear Replacement | Each | 1529625 | Note 2 | Note 2 | Note 2
Maintenance Practices
Vegetation Management | per Line KM | 2111 | 3739.1667 | 3792.2042 | 3965.3229
Pole Test and Treat | Each | 18 | 17.1429 | 18.898 | 18.898
Overhead Line Patrol | per Line KM | 44 | 43.8095 | 47.2151 | 47.2151
Vault Inspection | Each | 253 | 253 | 261.0022 | 272.3501

## Working Data
[21 empty] | Median | Average |  |  |  |  | FE-CEI | IPL | DPL | Ameren | DTE | Dominion | ENMAX | LBWL | PGE | PECO | SMUD | Sask | SCL | SCE | Xcel | BG&E | PG&E
Asset Category / Maintenance Practice | % Labor | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q |  |  |  |  | Cost Impact Category | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q
Wood Pole Replacement |  | Each | 7434 | 6499 | 5830 | 6255 | 5490 | 5041 | 7945 | 7533 | 5433 | 7825 | 7595 | 7650 | 7964 | 8240 | 7830 | 8150 | 7675 | 7925 | 7622.5 | 7128.5556 |  |  | Excessive Travel Time | X |  | X | X | X | X | X | X |  |  | X | X | X | X | X | X | X | X
UG Cable Replacement (XLPE) |  | Meter | 96 | 76 | 83 | 88 | 81 | 104 | 97 | 96 | 100 | 106 | 98 | 94 | 99 | 101 | 103 | 102 | 92 | 105 | 97.5 | 95.6111 |  |  | Road restrictions which limit working hours | X | X | X | X | X | X | X | X |  | X | X | X |  | X | X | X | X | X
OH Switches Replacement |  | Each | 21062 | 28829 | 22140 | 20050 | 19196 | 22653 | 22875 | 23278 | 22685 | 17654 | 18650 | 21793 | 23795 | 27625 | 23415 | 23555 | 19875 | 25362 | 22669 | 22471.7778 |  |  | High water table | X | X |  |  |  |  | X | X |  | X |  | X |  | X | X
Pole Top Transformer Replacement |  | Each | 11761 | 7356 | 8495 | 7783 | 8498 | 8565 | 9765 | 12576 | 7866 | 10674 | 12645 | 7649 | 12435 | 14367 | 8953 | 8742 | 10876 | 9216 | 9084.5 | 9901.2222 |  |  | Working next to energized lines (requiring dedicated observer, gloves, etc.) | X | X | X | X | X | X | X | X | X | X | X | X |  | X | X | X | X | X
Padmount / UG Transformer Replacement |  | Each | 21454 | 20668 | 19151 | 19885 | 19543 | 20449 | 20274 | 22375 | 19623 | 22776 | 22948 | 22825 | 23025 | 25840 | 22753 | 18325 | 22605 | 23005 | 21914.5 | 21529.1111 |  |  | Requirements to perform work off hours (i.e., night/weekend) | X |  | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X
Network Transformer / Protector Replacement |  | Each | 88943 | 85902 | 84104 | 83754 | 75734 | 85965 | 76675 | 92465 | 76550 | 95994 | 90336 | 94043 | 90700 | 98755 | 99552 | 96645 | 95582 | 94996 | 90518 | 89260.8333 |  |  | Changed standards requiring rebuilds rather than like-for-like (i.e., clearances) | X | X | X | X |  | X |  | X | X |  |  | X | X | X
Breaker Replacement |  | Each | 85242 | 78092 | 82511 | 77760 | 74775 | 85649 | 83762 | 89565 | 82500 | 92744 | 89475 | 90674 | 87765 | 92652 | 92732 | 86949 | 92546 | 91448 | 87357 | 86491.1667 |  |  | Excessive switching requirements (i.e., to isolate on dual radial construction) | X | X | X | X |  |  |  | X | X | X |  |  | X |  | X
Switchgear Replacement |  | Each | 1529625 | 588000 | [16 empty] | 1058812.5 |  |  |  | Shoring requirements for UG work | X | [10 empty] | X |  | X |  | X | X | X
[25 empty] | Limitations on tree trimming (e.g.; unusually tight clearances) | X | X |  |  |  | X | X |  |  | X | X | X |  | X | X | X | X | X
Vegetation Management |  | Line KM | 2111 | 4275 | 2523 | 2832 | 3975 | 3899 | 3867 | 3436 | 4587 | 3478 | 4477 | 4231 | 3765 | 3780 | 4341 | 4792 | 3271 | 4761 | 3883 | 3800.0556 |  |  | Prior use of lead cables | X | X | [6 empty] | X |  |  |  | X |  |  |  | X
Pole Test and Treat |  | Each | 18 | 16 | 17 | 18 |  | 18 |  | 19 |  |  | 16 |  |  |  | 16 |  | 19 |  | 18 | 19.625 |  |  | High fault currents (impacting equipment sourcing) | X | X | [7 empty] | X | X | X | X | X | X | X | X | X
Overhead Line Patrol |  | Line KM | 44 | 42 | 46 | 47 |  | 48 |  | 46 |  |  | 43 |  |  |  | 46 |  | 44 |  | 46 | 50.75 |  |  | Paid duty for police presence on public roads | X | X | X | X | X | X | X |  |  | X |  | X | X | X | X | X | X | X
Vault Inspection |  | Each | 253 | 225 | 232 | 226 |  | 240 |  | 275 |  |  | 270 |  |  |  | 297 |  | 269 |  | 253 | 285.875 |  |  | Extensive use of submersible transformers | X | X | [5 empty] | X | [9 empty] | X
[25 empty] | Environmental regulations | X | X |  |  |  | X | X | X |  | X |  | X |  | X | X | X |  | X
[25 empty] | Insufficient IT Enablement | [8 empty] | X | [7 empty] | X
[25 empty] | Union Work Rules | [9 empty] | X |  | X |  | X
[25 empty] | City consent requirements (i.e., customer notification, restoration, progressive clean-up, etc.) | X | X | X | X | X | X | X |  | X | X | X | X | X | X | X | X | X | X
3-Year Average Converted to $CAD (3-Year Average Conversion Factor of 0.84) | [24 empty] | Level of Difficulty | High | High | Medium | Medium | Low | Medium | Medium | Medium | Low | High | Medium | High | Medium | High | High | High | High | High
Median
Asset Category / Maintenance Practice | %THESL Labor | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | [23 empty] | Asset Category / Maintenance Practice | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | Median | Asset Category / Maintenance Practice | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | Median | Asset Category / Maintenance Practice | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | Median
Wood Pole Replacement |  | Each | 7434 | 6189.5238 | 5552.381 | 5957.1429 | 5228.5714 | 4800.9524 | 7566.6667 | 7533 | 5174.2857 | 7452.381 | 7233.3333 | 7285.7143 | 7964 | 7847.619 | 7457.1429 | 7761.9048 | 7309.5238 | 7547.619 | 7371.7619 | 7434 | [21 empty] | Wood Pole Replacement | Each | [19 empty] | Wood Pole Replacement | Each | [19 empty] | Wood Pole Replacement | Each
UG Cable Replacement (XLPE) |  | Meter | 96 | 72.381 | 79.0476 | 83.8095 | 77.1429 | 99.0476 | 92.381 | 96 | 95.2381 | 100.9524 | 93.3333 | 89.5238 | 99 | 96.1905 | 98.0952 | 97.1429 | 87.619 | 100 | 95.619 | 96 | [21 empty] | UG Cable Replacement (XLPE) | Meter | [19 empty] | UG Cable Replacement (XLPE) | Meter | [19 empty] | UG Cable Replacement (XLPE) | Meter
OH Switches Replacement |  | Each | 21062 | 27456.1905 | 21085.7143 | 19095.2381 | 18281.9048 | 21574.2857 | 21785.7143 | 23278 | 21604.7619 | 16813.3333 | 17761.9048 | 20755.2381 | 23795 | 26309.5238 | 22300 | 22433.3333 | 18928.5714 | 24154.2857 | 21589.5238 | 21062 | [21 empty] | OH Switches Replacement | Each | [19 empty] | OH Switches Replacement | Each | [19 empty] | OH Switches Replacement | Each
Pole Top Transformer Replacement |  | Each | 11761 | 7005.7143 | 8090.4762 | 7412.381 | 8093.3333 | 8157.1429 | 9300 | 12576 | 7491.4286 | 10165.7143 | 12042.8571 | 7284.7619 | 12435 | 13682.8571 | 8526.6667 | 8325.7143 | 10358.0952 | 8777.1429 | 8651.9048 | 11761 | [21 empty] | Pole Top Transformer Replacement | Each | [19 empty] | Pole Top Transformer Replacement | Each | [19 empty] | Pole Top Transformer Replacement | Each
Padmount / UG Transformer Replacement |  | Each | 21454 | 19683.8095 | 18239.0476 | 18938.0952 | 18612.381 | 19475.2381 | 19308.5714 | 22375 | 18688.5714 | 21691.4286 | 21855.2381 | 21738.0952 | 23025 | 24609.5238 | 21669.5238 | 17452.381 | 21528.5714 | 21909.5238 | 21491.2857 | 21454 | [21 empty] | Padmount / UG Transformer Replacement | Each | [19 empty] | Padmount / UG Transformer Replacement | Each | [19 empty] | Padmount / UG Transformer Replacement | Each
Network Transformer / Protector Replacement |  | Each | 88943 | 81811.4286 | 80099.0476 | 79765.7143 | 72127.619 | 81871.4286 | 73023.8095 | 92465 | 72904.7619 | 91422.8571 | 86034.2857 | 89564.7619 | 90700 | 94052.381 | 94811.4286 | 92042.8571 | 91030.4762 | 90472.381 | 89253.881 | 88943 | [21 empty] | Network Transformer / Protector Replacement | Each | [19 empty] | Network Transformer / Protector Replacement | Each | [19 empty] | Network Transformer / Protector Replacement | Each
Breaker Replacement |  | Each | 85242 | 74373.3333 | 78581.9048 | 74057.1429 | 71214.2857 | 81570.4762 | 79773.3333 | 89565 | 78571.4286 | 88327.619 | 85214.2857 | 86356.1905 | 87765 | 88240 | 88316.1905 | 82808.5714 | 88139.0476 | 87093.3333 | 85228.1429 | 85242 | [21 empty] | Breaker Replacement | Each | [19 empty] | Breaker Replacement | Each | [19 empty] | Breaker Replacement | Each
0
Vegetation Management |  | Line KM | 2111 | 4071.4286 | 2402.8571 | 2697.1429 | 3785.7143 | 3713.3333 | 3682.8571 | 3436 | 4368.5714 | 3312.381 | 4263.8095 | 4029.5238 | 3765 | 3600 | 4134.2857 | 4563.8095 | 3115.2381 | 4534.2857 | 3739.1667 | [22 empty] | Vegetation Management | Line KM | [19 empty] | Vegetation Management | Line KM | [19 empty] | Vegetation Management | Line KM
Pole Test and Treat |  | Each | 18 | 15.2381 | 16.1905 | 17.1429 |  | 17.1429 |  | 19 |  |  | 15.2381 |  |  |  | 15.2381 |  | 18.0952 |  | 17.1429 | [22 empty] | Pole Test and Treat | Each | [19 empty] | Pole Test and Treat | Each | [19 empty] | Pole Test and Treat | Each
Overhead Line Patrol |  | Line KM | 44 | 40 | 43.8095 | 44.7619 |  | 45.7143 |  | 46 |  |  | 40.9524 |  |  |  | 43.8095 |  | 41.9048 |  | 43.8095 | [22 empty] | Overhead Line Patrol | Line KM | [19 empty] | Overhead Line Patrol | Line KM | [19 empty] | Overhead Line Patrol | Line KM
Vault Inspection |  | Each | 253 | 214.2857 | 220.9524 | 215.2381 |  | 228.5714 |  | 275 |  |  | 257.1429 |  |  |  | 282.8571 |  | 256.1905 |  | 253 | [22 empty] | Vault Inspection | Each | [19 empty] | Vault Inspection | Each | [19 empty] | Vault Inspection | Each
Cost Category | % THESL Lavor | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q
Design and Permitting costs
Project Management and Supervisory costs
Other project-related costs (e.g.; Fleet and Warehouse)
Other labor-related costs (e.g.; training, conferences, and meetings) | bar: THESL to K; M to P
Employee-related costs (e.g.; vacation, sick time, insurances and pension)
Administrative and General costs | bar: B to C; G to I; K; N to O; Q
AFUDC / CWIP | bar: THESL; B to D; G to I; L to O; Q
Adjustment Factor |  |  | 1 | 1.02 | 0.95 | 0.95 | 1 | 1.02 | 1.02 | 0.95 | 0.95 | 0.95 | 1.02 | 1 | 1.01 | 1 | 0.95 | 0.95 | 1.02 | 1
Cost Impact Categories |  |  | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q
Excessive Travel Time | bar: THESL; B to G; J to Q
Road restrictions which limit working hours | bar: THESL to G; I to K; M to Q
High Water Table | bar: THESL to A; F to G; I; K; M to N
Working next to energized lines (requiring dedicated observer, gloves, etc.) | bar: THESL to K; M to Q
Requirements to perform work off hours (i.e., night/weekend) | bar: THESL; B to G; I to Q
Changed standards requiring rebuilds rather than like-for-like (i.e., clearances) | bar: THESL to C; E; G to H; K to M
Excessive switching requirements (i.e., to isolate on dual radial construction) | bar: THESL to C; G to I; L; N
Shoring requirements for UG work | bar: THESL; K; M; O to Q
Limitations on tree trimming (e.g.; unusually tight clearances) | bar: THESL to A; E to F; I to K; M to Q
Prior use of lead cables | bar: THESL to A; H; L; P
High fault currents (impacting equipment sourcing) | bar: THESL to A; I to Q
Paid duty for police presence on public roads | bar: THESL to F; I; K to Q
Extensive use of submersible transformers | bar: THESL to A; G; Q
Excessive Environmental Regulations | bar: THESL to A; E to G; I; K; M to O; Q
City consent requirements (i.e., customer notification, restoration, progressive clean-up, etc.) | bar: THESL to F; H to Q
Insufficient IT Enablement | bar: H; P
Union Work Rules | bar: I; K; M
Level of Difficulty |  |  | High | High | Medium | Medium | Low | Medium | Medium | Medium | Low | High | Medium | High | Medium | High | High | High | High | High
3-Year Average $CAD with Adjustment for Regional Costs
Asset Category / Maintenance Practice | %Labor | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | Median
Wood Pole Replacement | 0.6 | Each | 7434 | 7334.7357 | 6710.9153 | 7155.3021 | 6196.8347 | 5451.404 | 8862.6635 | 6401.8596 | 6191.4512 | 8212.1784 | 8005.8543 | 7960.2251 | 7368.1894 | 7834.9016 | 6403.2388 | 8449.2615 | 7965.0677 | 6772.781 | 7351.4626 | 7434
UG Cable Replacement (XLPE) | 0.5 | Meter | 96 | 83.5411 | 92.7924 | 97.8567 | 89.0477 | 110.2304 | 105.5666 | 83.9874 | 110.8397 | 109.5294 | 101.64 | 96.4306 | 92.8279 | 96.0606 | 86.5422 | 104.3116 | 94.1674 | 91.445 | 96.0303 | 96
OH Switches Replacement | 0.4 | Each | 21062 | 30842.8976 | 24018.8132 | 21655.653 | 20538.9518 | 23522.9309 | 24273.3105 | 20947.7476 | 24436.1502 | 17956.1206 | 19026.554 | 22036.2503 | 22608.2167 | 26281.0999 | 20198.9219 | 23757.7249 | 20060.2921 | 22501.1674 | 22268.7089 | 21062
Pole Top Transformer Replacement | 0.5 | Each | 11761 | 8085.9034 | 9497.2442 | 8654.7568 | 9342.3166 | 9078.1106 | 10627.3977 | 11002.3438 | 8718.6547 | 11029.4074 | 13114.6728 | 7846.7808 | 11659.7505 | 13664.379 | 7522.4518 | 8940.1184 | 11132.2207 | 8026.2588 | 9419.7804 | 11761
Padmount / UG Transformer Replacement | 0.5 | Each | 21454 | 22718.7944 | 21410.4442 | 22112.2755 | 21484.6896 | 21674.0553 | 22064.5018 | 19575.1784 | 21750.0841 | 23534.3623 | 23800.3568 | 23415.1879 | 21589.5259 | 24576.2897 | 19117.4295 | 18740.2963 | 23137.5366 | 20035.1652 | 21712.0697 | 21454
Network Transformer / Protector Replacement | 0.4 | Each | 88943 | 91902.8266 | 91241.114 | 90461.2251 | 81032.3491 | 89266.2673 | 81362.0147 | 83208.7585 | 82459.2152 | 97636.7869 | 92159.9347 | 95092.6944 | 86176.3082 | 93950.7701 | 85878.4143 | 97476.7704 | 96473.099 | 84280.4551 | 89863.7462 | 88943
Breaker Replacement | 0.4 | Each | 85242 | 83547.2461 | 89512.9311 | 83987.2109 | 80006.2575 | 88938.1321 | 88882.2312 | 80599.064 | 88868.5206 | 94331.1683 | 91281.5507 | 91686.0901 | 83387.6923 | 88144.6686 | 79995.1494 | 87697.3223 | 93408.7948 | 81132.6694 | 87920.9954 | 85242
Vegetation Management | 0.7 | Line KM | 2111 | 4950.2937 | 2987.7878 | 3330.0315 | 4603.6234 | 4300.2796 | 4418.7778 | 2834.0665 | 5370.4785 | 3706.3752 | 4795.0809 | 4464.7523 | 3436.384 | 3593.1937 | 3452.6131 | 5035.3166 | 3441.1879 | 3991.2147 | 3848.7949
Pole Test and Treat | 0.7 | Each | THESL: 18; A: 18.5274; B: 20.1317; C: 21.1655; E: 19.8525; G: 15.6715; J: 17.1368; N: 12.7256; P: 19.9886 | 18.5274
Overhead Line Patrol | 0.7 | Line KM | THESL: 44; A: 48.6345; B: 54.4741; C: 55.2654; E: 52.9401; G: 37.9415; J: 46.0551; N: 36.5861; P: 46.2893 | 46.2893
Vault Inspection | 0.7 | Each | THESL: 253; A: 260.5418; B: 274.7391; C: 265.744; E: 264.7005; G: 226.8243; J: 289.1829; N: 236.2189; P: 282.9959 | 264.7005
3-Year Average $CAD with Adjustment for Regional Costs and Cost Components
Asset Category / Maintenance Practice | %Labor | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | Median 1
Wood Pole Replacement |  | Each | 7434 | 7481.4304 | 6375.3695 | 6797.537 | 6196.8347 | 5560.4321 | 9039.9168 | 6081.7666 | 5881.8786 | 7801.5695 | 8165.9714 | 7960.2251 | 7441.8713 | 7834.9016 | 6083.0769 | 8026.7984 | 8124.369 | 6772.781 | 7437.9356 | 7434 | 8181.7292 | 6694.1421
UG Cable Replacement (XLPE) |  | Meter | 96 | 85.212 | 88.1528 | 92.9639 | 89.0477 | 112.435 | 107.6779 | 79.788 | 105.2978 | 104.053 | 103.6728 | 96.4306 | 93.7562 | 96.0606 | 82.2151 | 99.096 | 96.0507 | 91.445 | 96.0254 | 96 | 105.6279 | 86.4228
OH Switches Replacement |  | Each | 21062 | 31459.7555 | 22817.8725 | 20572.8704 | 20538.9518 | 23993.3895 | 24758.7768 | 19900.3602 | 23214.3427 | 17058.3145 | 19407.0851 | 22036.2503 | 22834.2989 | 26281.0999 | 19188.9758 | 22569.8387 | 20461.498 | 22501.1674 | 22268.7089 | 21062 | 24495.5798 | 20041.838
Pole Top Transformer Replacement |  | Each | 11761 | 8247.6215 | 9022.382 | 8222.019 | 9342.3166 | 9259.6728 | 10839.9456 | 10452.2266 | 8282.722 | 10477.937 | 13376.9663 | 7846.7808 | 11776.348 | 13664.379 | 7146.3292 | 8493.1125 | 11354.8651 | 8026.2588 | 9300.9947 | 11761 | 10231.0942 | 8370.8952
Padmount / UG Transformer Replacement |  | Each | 21454 | 23173.1702 | 20339.922 | 21006.6617 | 21484.6896 | 22107.5364 | 22505.7919 | 18596.4195 | 20662.5799 | 22357.6442 | 24276.3639 | 23415.1879 | 21805.4211 | 24576.2897 | 18161.558 | 17803.2815 | 23600.2874 | 20035.1652 | 21645.0554 | 21454 | 23809.5609 | 19480.5498
Network Transformer / Protector Replacement |  | Each | 88943 | 93740.8831 | 86679.0583 | 85938.1638 | 81032.3491 | 91051.5926 | 82989.255 | 79048.3205 | 78336.2545 | 92754.9476 | 94003.1334 | 95092.6944 | 87038.0713 | 93950.7701 | 81584.4936 | 92602.9319 | 98402.561 | 84280.4551 | 87990.5356 | 88943 | 96789.5892 | 79191.4821
Breaker Replacement |  | Each | 85242 | 85218.191 | 85037.2845 | 79787.8504 | 80006.2575 | 90716.8947 | 90659.8758 | 76569.1108 | 84425.0946 | 89614.6098 | 93107.1817 | 91686.0901 | 84221.5692 | 88144.6686 | 75995.3919 | 83312.4562 | 95276.9707 | 81132.6694 | 85127.7378 | 85242 | 93640.5115 | 76614.964
Vegetation Management |  | Line KM | 2111 | 5049.2996 | 2838.3984 | 3163.5299 | 4603.6234 | 4386.2852 | 4507.1534 | 2692.3632 | 5101.9546 | 3521.0564 | 4890.9825 | 4464.7523 | 3470.7478 | 3593.1937 | 3279.9824 | 4783.5507 | 3510.0117 | 3991.2147 | 3792.2042 | 2111 | 4171.4246 | 3412.9838
Pole Test and Treat |  | Each | THESL: 18; A: 18.898; B: 19.1252; C: 20.1072; E: 20.2496; G: 14.8879; J: 17.4795; N: 12.0893; P: 20.3883 | 18.898 | 18 | 20.7878 | 17.0082
Overhead Line Patrol |  | Line KM | THESL: 44; A: 49.6072; B: 51.7504; C: 52.5021; E: 53.9989; G: 36.0444; J: 46.9762; N: 34.7568; P: 47.2151 | 47.2151 | 44 | 51.9366 | 42.4936
Vault Inspection |  | Each | THESL: 253; A: 265.7526; B: 261.0022; C: 252.4568; E: 269.9945; G: 215.4831; J: 294.9666; N: 224.4079; P: 288.6558 | 261.0022 | 253 | 287.1024 | 234.9019
3-Year Average $CAD with Adjustment for Regional Costs, Cost Components and Difficulty Factors
Asset Category / Maintenance Practice | %Labor | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | Median 2
Wood Pole Replacement |  | Each | 7434 | 7481.4304 | 6954.9486 | 7724.4739 | 7605.2062 | 6065.9259 | 9861.7274 | 6358.2105 | 6683.953 | 8156.1863 | 8165.9714 | 8322.0536 | 8456.6719 | 7834.9016 | 6636.0839 | 8026.7984 | 8124.369 | 7080.6346 | 7664.8401 | 7434 | 6898.3561 | 8431.3241
UG Cable Replacement (XLPE) |  | Meter | 96 | 85.212 | 91.9855 | 105.0896 | 108.4059 | 122.212 | 126.4045 | 83.257 | 119.0323 | 108.577 | 108.1803 | 100.6232 | 105.9853 | 96.0606 | 85.7897 | 94.7875 | 96.0507 | 95.4209 | 98.3419 | 96 | 88.5077 | 108.1761
OH Switches Replacement |  | Each | 21062 | 31459.7555 | 24892.2246 | 23378.2618 | 25206.8954 | 26174.6067 | 27009.5746 | 20804.922 | 26379.9349 | 17833.6925 | 19407.0851 | 23037.8981 | 25948.0669 | 26281.0999 | 20933.4281 | 22569.8387 | 20461.498 | 23523.9478 | 23451.1048 | 21062 | 21105.9943 | 25796.2153
Pole Top Transformer Replacement |  | Each | 11761 | 8247.6215 | 9842.5985 | 9343.2034 | 11465.5703 | 10101.4612 | 11825.3952 | 10927.3279 | 9412.1841 | 10954.2069 | 13376.9663 | 8203.4527 | 13382.2136 | 13664.379 | 7795.9955 | 8493.1125 | 11354.8651 | 8391.0887 | 10514.3946 | 11761 | 9462.9551 | 11565.834
Padmount / UG Transformer Replacement |  | Each | 21454 | 23173.1702 | 21224.2665 | 23746.661 | 26155.2743 | 24029.9309 | 26419.8426 | 19404.9594 | 23357.699 | 23329.7157 | 25331.858 | 24433.2395 | 24649.6065 | 24576.2897 | 18951.191 | 17029.2257 | 23600.2874 | 20906.2594 | 23478.9932 | 21454 | 21131.0939 | 25826.8925
Network Transformer / Protector Replacement |  | Each | 88943 | 93740.8831 | 90447.713 | 97147.4896 | 98648.0772 | 98969.1224 | 97422.1689 | 82485.204 | 88554.0268 | 96787.7714 | 98090.2262 | 99227.1593 | 98390.8632 | 93950.7701 | 85131.6455 | 88576.7175 | 98402.561 | 87944.8227 | 95369.2707 | 88943 | 85832.3436 | 104906.1978
Breaker Replacement |  | Each | 85242 | 85218.191 | 92767.9468 | 90668.0118 | 98189.4978 | 98963.8852 | 98901.6827 | 80049.5249 | 95937.6075 | 93688.0012 | 93107.1817 | 95853.6396 | 95706.3286 | 88144.6686 | 82904.0639 | 83312.4562 | 95276.9707 | 84820.518 | 92937.5642 | 85242 | 83643.8078 | 102231.3206
Vegetation Management |  | Line KM | 2111 | 5049.2996 | 3193.1982 | 3558.9711 | 5466.8028 | 4934.5708 | 4788.8505 | 2860.6359 | 6058.571 | 3521.0564 | 4890.9825 | 4743.7993 | 3687.6695 | 3593.1937 | 3689.9802 | 4783.5507 | 3510.0117 | 4240.6656 | 3965.3229 | 2111 | 3568.7906 | 4361.8552
Pole Test and Treat |  | Each | THESL: 18; A: 18.898; B: 20.8638; C: 22.8491; E: 22.0905; G: 15.5646; J: 17.4795; N: 13.1883; P: 20.3883 | 18.898 | 18 | 17.0082 | 20.7878
Overhead Line Patrol |  | Line KM | THESL: 44; A: 49.6072; B: 56.455; C: 59.6615; E: 58.9079; G: 37.6828; J: 46.9762; N: 37.9165; P: 47.2151 | 47.2151 | 44 | 42.4936 | 51.9366
Vault Inspection |  | Each | THESL: 253; A: 265.7526; B: 272.3501; C: 285.386; E: 293.4723; G: 224.8519; J: 307.7912; N: 234.1648; P: 288.6558 | 272.3501 | 253 | 245.1151 | 299.5851

## Tables C-8 to C-10
TABLE C-8
Asset Category | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | Median
Wood Pole Replacement | Each | 7434 | 6189.5238 | 5552.381 | 5957.1429 | 5228.5714 | 4800.9524 | 7566.6667 | 7533 | 5174.2857 | 7452.381 | 7233.3333 | 7285.7143 | 7964 | 7847.619 | 7457.1429 | 7761.9048 | 7309.5238 | 7547.619 | 7371.7619
UG Cable Replacement (XLPE) | Meter | 96 | 72.381 | 79.0476 | 83.8095 | 77.1429 | 99.0476 | 92.381 | 96 | 95.2381 | 100.9524 | 93.3333 | 89.5238 | 99 | 96.1905 | 98.0952 | 97.1429 | 87.619 | 100 | 95.619
OH Switches Replacement | Each | 21062 | 27456.1905 | 21085.7143 | 19095.2381 | 18281.9048 | 21574.2857 | 21785.7143 | 23278 | 21604.7619 | 16813.3333 | 17761.9048 | 20755.2381 | 23795 | 26309.5238 | 22300 | 22433.3333 | 18928.5714 | 24154.2857 | 21589.5238
Pole Top Transformer Replacement | Each | 11761 | 7005.7143 | 8090.4762 | 7412.381 | 8093.3333 | 8157.1429 | 9300 | 12576 | 7491.4286 | 10165.7143 | 12042.8571 | 7284.7619 | 12435 | 13682.8571 | 8526.6667 | 8325.7143 | 10358.0952 | 8777.1429 | 8651.9048
Padmount / UG Transformer Replacement | Each | 21454 | 19683.8095 | 18239.0476 | 18938.0952 | 18612.381 | 19475.2381 | 19308.5714 | 22375 | 18688.5714 | 21691.4286 | 21855.2381 | 21738.0952 | 23025 | 24609.5238 | 21669.5238 | 17452.381 | 21528.5714 | 21909.5238 | 21491.2857
Network Transformer / Protector Replacement | Each | 88943 | 81811.4286 | 80099.0476 | 79765.7143 | 72127.619 | 81871.4286 | 73023.8095 | 92465 | 72904.7619 | 91422.8571 | 86034.2857 | 89564.7619 | 90700 | 94052.381 | 94811.4286 | 92042.8571 | 91030.4762 | 90472.381 | 89253.881
Breaker Replacement | Each | 85242 | 74373.3333 | 78581.9048 | 74057.1429 | 71214.2857 | 81570.4762 | 79773.3333 | 89565 | 78571.4286 | 88327.619 | 85214.2857 | 86356.1905 | 87765 | 88240 | 88316.1905 | 82808.5714 | 88139.0476 | 87093.3333 | 85228.1429
Maintenance Practice
Vegetation Management | Line KM | 2111 | 4071.4286 | 2402.8571 | 2697.1429 | 3785.7143 | 3713.3333 | 3682.8571 | 3436 | 4368.5714 | 3312.381 | 4263.8095 | 4029.5238 | 3765 | 3600 | 4134.2857 | 4563.8095 | 3115.2381 | 4534.2857 | 3739.1667
Pole Test and Treat | Each | 18 | 15.2381 | 16.1905 | 17.1429 |  | 17.1429 |  | 19 |  |  | 15.2381 |  |  |  | 15.2381 |  | 18.0952 |  | 17.1429
Overhead Line Patrol | Line KM | 44 | 40 | 43.8095 | 44.7619 |  | 45.7143 |  | 46 |  |  | 40.9524 |  |  |  | 43.8095 |  | 41.9048 |  | 43.8095
Vault Inspection | Each | 253 | 214.2857 | 220.9524 | 215.2381 |  | 228.5714 |  | 275 |  |  | 257.1429 |  |  |  | 282.8571 |  | 256.1905 |  | 253
TABLE C-9
Asset Category | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | Median 1
Wood Pole Replacement | Each | 7434 | 7481.4304 | 6375.3695 | 6797.537 | 6196.8347 | 5560.4321 | 9039.9168 | 6081.7666 | 5881.8786 | 7801.5695 | 8165.9714 | 7960.2251 | 7441.8713 | 7834.9016 | 6083.0769 | 8026.7984 | 8124.369 | 6772.781 | 7437.9356
UG Cable Replacement (XLPE) | Meter | 96 | 85.212 | 88.1528 | 92.9639 | 89.0477 | 112.435 | 107.6779 | 79.788 | 105.2978 | 104.053 | 103.6728 | 96.4306 | 93.7562 | 96.0606 | 82.2151 | 99.096 | 96.0507 | 91.445 | 96.0254
OH Switches Replacement | Each | 21062 | 31459.7555 | 22817.8725 | 20572.8704 | 20538.9518 | 23993.3895 | 24758.7768 | 19900.3602 | 23214.3427 | 17058.3145 | 19407.0851 | 22036.2503 | 22834.2989 | 26281.0999 | 19188.9758 | 22569.8387 | 20461.498 | 22501.1674 | 22268.7089
Pole Top Transformer Replacement | Each | 11761 | 8247.6215 | 9022.382 | 8222.019 | 9342.3166 | 9259.6728 | 10839.9456 | 10452.2266 | 8282.722 | 10477.937 | 13376.9663 | 7846.7808 | 11776.348 | 13664.379 | 7146.3292 | 8493.1125 | 11354.8651 | 8026.2588 | 9300.9947
Padmount / UG Transformer Replacement | Each | 21454 | 23173.1702 | 20339.922 | 21006.6617 | 21484.6896 | 22107.5364 | 22505.7919 | 18596.4195 | 20662.5799 | 22357.6442 | 24276.3639 | 23415.1879 | 21805.4211 | 24576.2897 | 18161.558 | 17803.2815 | 23600.2874 | 20035.1652 | 21645.0554
Network Transformer / Protector Replacement | Each | 88943 | 93740.8831 | 86679.0583 | 85938.1638 | 81032.3491 | 91051.5926 | 82989.255 | 79048.3205 | 78336.2545 | 92754.9476 | 94003.1334 | 95092.6944 | 87038.0713 | 93950.7701 | 81584.4936 | 92602.9319 | 98402.561 | 84280.4551 | 87990.5356
Breaker Replacement | Each | 85242 | 85218.191 | 85037.2845 | 79787.8504 | 80006.2575 | 90716.8947 | 90659.8758 | 76569.1108 | 84425.0946 | 89614.6098 | 93107.1817 | 91686.0901 | 84221.5692 | 88144.6686 | 75995.3919 | 83312.4562 | 95276.9707 | 81132.6694 | 85127.7378
Maintenance Practice
Vegetation Management | Line KM | 2111 | 5049.2996 | 2838.3984 | 3163.5299 | 4603.6234 | 4386.2852 | 4507.1534 | 2692.3632 | 5101.9546 | 3521.0564 | 4890.9825 | 4464.7523 | 3470.7478 | 3593.1937 | 3279.9824 | 4783.5507 | 3510.0117 | 3991.2147 | 3792.2042
Pole Test and Treat | Each | 18 | 18.898 | 19.1252 | 20.1072 |  | 20.2496 |  | 14.8879 |  |  | 17.4795 |  |  |  | 12.0893 |  | 20.3883 |  | 18.898
Overhead Line Patrol | Line KM | 44 | 49.6072 | 51.7504 | 52.5021 |  | 53.9989 |  | 36.0444 |  |  | 46.9762 |  |  |  | 34.7568 |  | 47.2151 |  | 47.2151
Vault Inspection | Each | 253 | 265.7526 | 261.0022 | 252.4568 |  | 269.9945 |  | 215.4831 |  |  | 294.9666 |  |  |  | 224.4079 |  | 288.6558 |  | 261.0022
TABLE C-10
Asset Category | Unit | THESL | A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | Median 2
Wood Pole Replacement | Each | 7434 | 7481.4304 | 6954.9486 | 7724.4739 | 7605.2062 | 6065.9259 | 9861.7274 | 6358.2105 | 6683.953 | 8156.1863 | 8165.9714 | 8322.0536 | 8456.6719 | 7834.9016 | 6636.0839 | 8026.7984 | 8124.369 | 7080.6346 | 7664.8401
UG Cable Replacement (XLPE) | Meter | 96 | 85.212 | 91.9855 | 105.0896 | 108.4059 | 122.212 | 126.4045 | 83.257 | 119.0323 | 108.577 | 108.1803 | 100.6232 | 105.9853 | 96.0606 | 85.7897 | 94.7875 | 96.0507 | 95.4209 | 98.3419
OH Switches Replacement | Each | 21062 | 31459.7555 | 24892.2246 | 23378.2618 | 25206.8954 | 26174.6067 | 27009.5746 | 20804.922 | 26379.9349 | 17833.6925 | 19407.0851 | 23037.8981 | 25948.0669 | 26281.0999 | 20933.4281 | 22569.8387 | 20461.498 | 23523.9478 | 23451.1048
Pole Top Transformer Replacement | Each | 11761 | 8247.6215 | 9842.5985 | 9343.2034 | 11465.5703 | 10101.4612 | 11825.3952 | 10927.3279 | 9412.1841 | 10954.2069 | 13376.9663 | 8203.4527 | 13382.2136 | 13664.379 | 7795.9955 | 8493.1125 | 11354.8651 | 8391.0887 | 10514.3946
Padmount / UG Transformer Replacement | Each | 21454 | 23173.1702 | 21224.2665 | 23746.661 | 26155.2743 | 24029.9309 | 26419.8426 | 19404.9594 | 23357.699 | 23329.7157 | 25331.858 | 24433.2395 | 24649.6065 | 24576.2897 | 18951.191 | 17029.2257 | 23600.2874 | 20906.2594 | 23478.9932
Network Transformer / Protector Replacement | Each | 88943 | 93740.8831 | 90447.713 | 97147.4896 | 98648.0772 | 98969.1224 | 97422.1689 | 82485.204 | 88554.0268 | 96787.7714 | 98090.2262 | 99227.1593 | 98390.8632 | 93950.7701 | 85131.6455 | 88576.7175 | 98402.561 | 87944.8227 | 95369.2707
Breaker Replacement | Each | 85242 | 85218.191 | 92767.9468 | 90668.0118 | 98189.4978 | 98963.8852 | 98901.6827 | 80049.5249 | 95937.6075 | 93688.0012 | 93107.1817 | 95853.6396 | 95706.3286 | 88144.6686 | 82904.0639 | 83312.4562 | 95276.9707 | 84820.518 | 92937.5642
Maintenance Practice
Vegetation Management | Line KM | 2111 | 5049.2996 | 3193.1982 | 3558.9711 | 5466.8028 | 4934.5708 | 4788.8505 | 2860.6359 | 6058.571 | 3521.0564 | 4890.9825 | 4743.7993 | 3687.6695 | 3593.1937 | 3689.9802 | 4783.5507 | 3510.0117 | 4240.6656 | 3965.3229
Pole Test and Treat | Each | 18 | 18.898 | 20.8638 | 22.8491 |  | 22.0905 |  | 15.5646 |  |  | 17.4795 |  |  |  | 13.1883 |  | 20.3883 |  | 18.898
Overhead Line Patrol | Line KM | 44 | 49.6072 | 56.455 | 59.6615 |  | 58.9079 |  | 37.6828 |  |  | 46.9762 |  |  |  | 37.9165 |  | 47.2151 |  | 47.2151
Vault Inspection | Each | 253 | 265.7526 | 272.3501 | 285.386 |  | 293.4723 |  | 224.8519 |  |  | 307.7912 |  |  |  | 234.1648 |  | 288.6558 |  | 272.3501
|  | E | G | N | H | B | Q | THESL | A | D | C | M | O | P | I | J | K | L | F
Wood Pole Replacement |  | 6065.9259 | 6358.2105 | 6636.0839 | 6683.953 | 6954.9486 | 7080.6346 | 7434 | 7481.4304 | 7605.2062 | 7724.4739 | 7834.9016 | 8026.7984 | 8124.369 | 8156.1863 | 8165.9714 | 8322.0536 | 8456.6719 | 9861.7274
Median |  | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401 | 7664.8401
|  | G | A | N | B | O | Q | THESL | P | M | K | C | L | J | D | I | H | E | F
UG Cable Replacement (XLPE) |  | 83.257 | 85.212 | 85.7897 | 91.9855 | 94.7875 | 95.4209 | 96 | 96.0507 | 96.0606 | 100.6232 | 105.0896 | 105.9853 | 108.1803 | 108.4059 | 108.577 | 119.0323 | 122.212 | 126.4045
Median |  | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419 | 98.3419
|  | I | J | P | G | N | THESL | O | K | C | Q | B | D | L | E | M | H | F | A
OH Switches Replacement |  | 17833.6925 | 19407.0851 | 20461.498 | 20804.922 | 20933.4281 | 21062 | 22569.8387 | 23037.8981 | 23378.2618 | 23523.9478 | 24892.2246 | 25206.8954 | 25948.0669 | 26174.6067 | 26281.0999 | 26379.9349 | 27009.5746 | 31459.7555
Median |  | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048 | 23451.1048
|  | N | K | A | Q | O | C | H | B | E | G | I | P | D | THESL | F | J | L | M
Pole Top Transformer Replacement |  | 7795.9955 | 8203.4527 | 8247.6215 | 8391.0887 | 8493.1125 | 9343.2034 | 9412.1841 | 9842.5985 | 10101.4612 | 10927.3279 | 10954.2069 | 11354.8651 | 11465.5703 | 11761 | 11825.3952 | 13376.9663 | 13382.2136 | 13664.379
Median |  | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946 | 10514.3946
|  | O | N | G | Q | B | THESL | A | I | H | P | C | E | K | M | L | J | D | F
Padmount / UG Transformer Replacement |  | 17029.2257 | 18951.191 | 19404.9594 | 20906.2594 | 21224.2665 | 21454 | 23173.1702 | 23329.7157 | 23357.699 | 23600.2874 | 23746.661 | 24029.9309 | 24433.2395 | 24576.2897 | 24649.6065 | 25331.858 | 26155.2743 | 26419.8426
Median |  | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932 | 23478.9932
|  | G | N | Q | H | O | THESL | B | A | M | I | C | F | J | L | P | D | E | K
Network Transformer / Protector Replacement |  | 82485.204 | 85131.6455 | 87944.8227 | 88554.0268 | 88576.7175 | 88943 | 90447.713 | 93740.8831 | 93950.7701 | 96787.7714 | 97147.4896 | 97422.1689 | 98090.2262 | 98390.8632 | 98402.561 | 98648.0772 | 98969.1224 | 99227.1593
Median |  | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707 | 95369.2707
|  | G | N | O | Q | A | THESL | M | C | B | J | I | P | L | K | H | D | F | E
Breaker Replacement |  | 80049.5249 | 82904.0639 | 83312.4562 | 84820.518 | 85218.191 | 85242 | 88144.6686 | 90668.0118 | 92767.9468 | 93107.1817 | 93688.0012 | 95276.9707 | 95706.3286 | 95853.6396 | 95937.6075 | 98189.4978 | 98901.6827 | 98963.8852
Median |  | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642 | 92937.5642
|  | THESL | B | C | P | I | G | M | F | E | L | D | K | A | N | J | H | Q | O
Vegetation Management |  | 2111 | 2402.8571 | 2697.1429 | 3115.2381 | 3312.381 | 3436 | 3600 | 3682.8571 | 3713.3333 | 3765 | 3785.7143 | 4029.5238 | 4071.4286 | 4134.2857 | 4263.8095 | 4368.5714 | 4534.2857 | 4563.8095
Median |  | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229 | 3965.3229
|  | N | G | J | THESL | A | P | B | E | C
Pole Test and Treat |  | 13.1883 | 15.5646 | 17.4795 | 18 | 18.898 | 20.3883 | 20.8638 | 22.0905 | 22.8491
Median |  | 18.898 | 18.898 | 18.898 | 18.898 | 18.898 | 18.898 | 18.898 | 18.898 | 18.898
|  | G | N | THESL | J | P | A | B | E | C
Overhead Line Patrol |  | 37.6828 | 37.9165 | 44 | 46.9762 | 47.2151 | 49.6072 | 56.455 | 58.9079 | 59.6615
Median |  | 47.2151 | 47.2151 | 47.2151 | 47.2151 | 47.2151 | 47.2151 | 47.2151 | 47.2151 | 47.2151
|  | G | N | THESL | A | B | C | P | E | J
Vault Inspection |  | 224.8519 | 234.1648 | 253 | 265.7526 | 272.3501 | 285.386 | 288.6558 | 293.4723 | 307.7912
Median |  | 272.3501 | 272.3501 | 272.3501 | 272.3501 | 272.3501 | 272.3501 | 272.3501 | 272.3501 | 272.3501

## Difficulty Factors
Peer Group Panel | Population Density | UG Utility Congestion | External Factors | Weather / Climate | Vegetation | OH Adjustment |  | UG Adjustment |  | VM Adjustment
[6 empty] | Score | Factor | Score | Factor | Score | Factor
| 6 | 6 | 5 | 5 | 4 | 20 | 1.0909 | 22 | 1.0435 | 14 | 1.125
| 5 | 5 | 5 | 5 | 4 | 19 | 1.1364 | 20 | 1.1304 | 14 | 1.125
| 4 | 5 | 4 | 5 | 4 | 17 | 1.2273 | 18 | 1.2174 | 13 | 1.1875
| 6 | 6 | 6 | 5 | 5 | 22 | 1 | 23 | 1 | 16 | 1
| 6 | 5 | 5 | 5 | 4 | 20 | 1.0909 | 21 | 1.087 | 14 | 1.125
| 5 | 5 | 5 | 4 | 6 | 20 | 1.0909 | 19 | 1.1739 | 15 | 1.0625
| 6 | 5 | 5 | 6 | 4 | 21 | 1.0455 | 22 | 1.0435 | 15 | 1.0625
| 6 | 6 | 6 | 5 | 5 | 22 | 1 | 23 | 1 | 16 | 1
| 6 | 5 | 4 | 5 | 4 | 19 | 1.1364 | 20 | 1.1304 | 13 | 1.1875
| 6 | 6 | 6 | 4 | 5 | 21 | 1.0455 | 22 | 1.0435 | 15 | 1.0625
| 5 | 6 | 6 | 5 | 5 | 21 | 1.0455 | 22 | 1.0435 | 16 | 1
| 6 | 6 | 5 | 5 | 6 | 22 | 1 | 22 | 1.0435 | 16 | 1
| 6 | 6 | 6 | 4 | 5 | 21 | 1.0455 | 22 | 1.0435 | 15 | 1.0625
| 4 | 5 | 5 | 6 | 4 | 19 | 1.1364 | 20 | 1.1304 | 15 | 1.0625
| 6 | 6 | 6 | 5 | 5 | 22 | 1 | 23 | 1 | 16 | 1
| 6 | 6 | 6 | 4 | 4 | 20 | 1.0909 | 22 | 1.0435 | 14 | 1.125
Toronto Hydro | 6 | 6 | 6 | 5 | 5 | 22 | 1 | 23 | 1 | 16 | 1
| 6 | 6 | 6 | 6 | 4 | 22 | 1 | 24 | 0.95652 | 16 | 1
Average Adjustment | [6 empty] | 1.0695 |  | 1.0665 |  | 1.0699

## Wage Adjustors
[6 empty] | Peer Group Panel | Number of Customers | Service Territory (Sq. KM) | Population Density
Peer Group Panel | Average Wage | Factor | Adjustment
[7 empty] | 480000 | 1367.52 | 351.0004
| 58081.6 | 0.74197 | 1.3478 | 1.3478 | 1.258 |  | 520000 | 6000 | 86.6667
| 58627.2 | 0.74894 | 1.3352 |  |  |  | 1200000 | 113183 | 10.6023
| 59817.6 | 0.76415 | 1.3086 |  |  |  | 1250000 | 5957 | 209.8372
| 68100.8 | 0.86996 | 1.1495 |  |  |  | 2200000 | 20000 | 110
| 63860 | 0.81579 | 1.2258 |  |  |  | 2600000 | 77700 | 33.462
| 60896.4 | 0.77793 | 1.2855 |  |  |  | 850000 | 1087 | 781.9687
| 104410 | 1.3338 | 0.74974 |  |  |  | 700000 | 4403 | 158.9825
| 59830 | 0.76431 | 1.3084 |  |  |  | 100000 | 130 | 769.2308
| 58962 | 0.75322 | 1.3276 |  |  |  | 16000000 | 181300 | 88.2515
| 94438.4 | 1.2064 | 0.8289 |  |  |  | 862000 | 10360 | 83.2046
| 66910.4 | 0.85476 | 1.1699 |  |  |  | 1600000 | 5439 | 294.1717
| 66451.6 | 0.8489 | 1.178 |  |  |  | 625000 | 1431 | 436.7575
| 67816 | 0.86633 | 1.1543 |  |  |  | 522000 | 651000 | 0.80184
| 89431 | 1.1425 | 0.87531 |  |  |  | 425000 | 341.88 | 1243.1262
| 78492 | 1.0027 | 0.9973 |  |  |  | 15000000 | 130000 | 115.3846
| 102400 | 1.3081 | 0.76445 |  |  | Toronto Hydro | 761000 | 630 | 1207.9365
Toronto Hydro | 78280 | 1 | 1 |  |  |  | 2500000 | 17066 | 146.4901
| 68212.4 | 0.87139 | 1.1476
Average Adjustment |  |  | 1.1267
Avg. Wage
| 94438.4 | 16000000 | 181300 | 88.2515
| 67381.6 | 3800000 | 29554.49 | 128.5761
| 68212.4 | 2500000 | 17066 | 146.4901
| 78516.8 | 3400000 | 3496.5 | 972.401
| 60896.4 | 2600000 | 77700 | 33.462
| 63860 | 2200000 | 20000 | 110
| 74263.6 | 2200000 | 3755.5 | 585.8075
| 66451.6 | 1600000 | 5439 | 294.1717
| 68100.8 | 1250000 | 5957 | 209.8372
| 59817.6 | 1200000 | 113183 | 10.6023
| 66910.4 | 862000 | 10360 | 83.2046
| 104410 | 850000 | 1087 | 781.9687
Toronto Hydro | 78280 | 761000 | 630 | 1207.9365
| 59830 | 700000 | 4403 | 158.9825
| 67815.6 | 625000 | 1431 | 436.7575
| 97940 | 522000 | 651000 | 0.80184
| 58627.2 | 520000 | 6000 | 86.6667
| 58081.6 | 480000 | 1367.52 | 351.0004
| 78492 | 425000 | 341.88 | 1243.1262
| 58962 | 100000 | 130 | 769.2308