## Sheet1
Asset Failures by Asset Type
Ref: 2B Section D2
| 2013 | 2014 | 2015 | 2016 | 2017 | 2018
Overhead
Pole Transformer | 185 | 198 | 231 | 113 | 117 | 54
Wood Poles | 131 | 195 | 236 | 135 | 159 | 104
Auxilliary Equipment | Information not available.
Overhead Switches | 235 | 290 | 267 | 242 | 214 | 262
Underground
U/G Cable | 177 | 144 | 134 | 163 | 102 | 118
Submersible Transformers | 113 | 132 | 140 | 361 | 213 | 89
Pad Mounted Transformers | 42 | 49 | 62 | 39 | 80 | 36
U/G Switches | 77 | 62 | 123 | 92 | 119 | 100
Cable Chambers | 15 | 26 | 28 | 21 | 28 | 27
U/G Primary Cable | Please see U/G Cable above. Breakdown by primary and secondary not available.
U/G Secondary Cable
Network Transformer | 28 | 43 | 58 | 45 | 62 | 40
Network Protector | 16 | 77 | 93 | 100 | 123 | 165
Power Transformer | 0 | 1 | 0 | 2 | 14 | 17
KSO Circuit Breaker* | 17 | 25 | 29 | 18 | 39 | 60
DC Battery System | 4 | 4 |  | 24 | 14 | 2
Energy Meter | 3114 | 5939 | 4362 | 5326 | 5234 | 6708
Instrument Transformer | 28 | 49 | 17 | 20 | 23 | 42
*Asset failures reported for all breakers. Information to segregate out failures for only KSO not available for the period requested.

## Sheet2
2B-AMPCO-35
Ref: 2B Section D3 P9
1 | Allocation of Work Requests
|  | 2015 | 2016 | 2017 | 2018
Overhead Assets
| P1 | 673 | 333 | 422 | 347
| P2 | 421 | 452 | 316 | 434
| P3 | 52 | 218 | 107 | 105
Underground Assets
| P1 | 1079 | 948 | 1175 | 897
| P2 | 1099 | 726 | 1117 | 1033
| P3 | 1354 | 2485 | 3096 | 1943
Network Assets
| P1 | 198 | 130 | 270 | 241
| P2 | 272 | 120 | 323 | 544
| P3 | 507 | 885 | 688 | 693
Station Assets
| P1 | 334 | 293 | 260 | 228
| P2 | 255 | 220 | 320 | 451
| P3 | 105 | 256 | 98 | 165
Other
| P1 | All Work Requests included in above.
P2
P3
2 | Allocation of Work Requests to System Renewal Investments
|  | 2015 | 2016 | 2017 | 2018
E6.2 | Underground - Horseshoe
| P1 | Work Requests are not issued and addressed by these programs. Work Requests are issued and addressed through the Reactive & Corrective Capital program (Exhibit 2B, Section E6.7) or the Corrective Maintenance program (Exhibit 4A, Tab 2, Schedule 4).
P2
P3
E6.3 | Underground - Downtown
P1
P2
P3
E6.4 | Network System
P1
P2
P3

## Sheet3
# Outages (Customer Interruptions) Caused by Asset Failure
Ref: 2B Section E6.3
| 2013 | 2014 | 2015 | 2016 | 2017
Underground - Horseshoe
Cables | 177361 | 144783 | 175653 | 152228 | 136110
Transformers | 11971 | 14171 | 18313 | 29120 | 41280
Switches | 10455 | 40308 | 31136 | 27549 | 11718
# Outage Minutes (Customer Interruption Minutes) Caused by Asset Failure
| 2013 | 2014 | 2015 | 2016 | 2017
Underground - Horseshoe
Cables | 7839052 | 6991906 | 8115982 | 8301388 | 6237826
Transformers | 1231785 | 1091128 | 1201478 | 1186042 | 1659620
Switches | 344049 | 1744208 | 1490970 | 1213101 | 1412014
# Outages (Customer Interruptions) Caused by Asset Failure
Ref: 2B Section E6.3
| 2013 | 2014 | 2015 | 2016 | 2017
Underground - Horseshoe
Cables | Please see table above.
Transformers
Switches
# Outage Minutes (Customer Interruption Minutes) Caused by Asset Failure
| 2013 | 2014 | 2015 | 2016 | 2017
Underground - Horseshoe
Cables | Please see table above.
Transformers
Switches