## Sheet1
4A-AMPCO-76
Ref: 4A-T2-S1
1 | Overhead Inspections & Maintenance
|  |  |  | # Inspections from Prev. & Pred. Maintenance Programs (1) | [5 empty] | # Forecats Asset Inspections
| Equipment Type | Population | Inspection Cycle | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
[10 empty] | N/A | N/A | N/A | N/A | N/A | N/A
| Circuit km Primary (4) | 4100 | See 2B-AMPCO-32, Table 1 | 1593 | 1181 | 1326 | 1593 | 1181 | 1326 | N/A | N/A | N/A | N/A | N/A | N/A
| Circuit km Secondary | 11500 |  | 4280 | 2603 | 4616 | 4280 | 2603 | 4616 | N/A | N/A | N/A | N/A | N/A | N/A
| Pole Mounted Transformers | 30100 |  | 11711 | 6531 | 11857 | 11711 | 6531 | 11857 | N/A | N/A | N/A | N/A | N/A | N/A
| Overhead Switches | 20500 |  | 7833 | 5202 | 7465 | 7833 | 5202 | 7465 | N/A | N/A | N/A | N/A | N/A | N/A
| Lightning Arrestors | Not available | 3 Years | # Inspections from Prev. & Pred. Maintenance Programs (1) 2013: Breakdown not available. All equipment and wire associated with Circuit km noted above was inspected. | N/A | N/A | N/A | N/A | N/A | N/A
| Auxiliary Equipment |  | 3 Years | [6 empty] | N/A | N/A | N/A | N/A | N/A | N/A
| Conductor Wire | See Circuit km Primary | See 2B-AMPCO-32, Table 1 | [6 empty] | N/A | N/A | N/A | N/A | N/A | N/A
| Wood Pole (3) | 107000 |  | 73752 | 50091 | 84067 | 80398 | 54413 | 83154 | N/A | N/A | N/A | N/A | N/A | N/A
| Concrete Pole | 61000 | [7 empty] | N/A | N/A | N/A | N/A | N/A | N/A
| Steel Pole | 10000 | [7 empty] | N/A | N/A | N/A | N/A | N/A | N/A
| Line Insulators | See Poles | 3 Years | # Inspections from Prev. & Pred. Maintenance Programs (1) 2013: See Poles. Insulators are inspected by pole location. | N/A | N/A | N/A | N/A | N/A | N/A
| Overhead SCADA Switches | 1100 | See 2B-AMPCO-32, Table 1 | 374 | 283 | 247 | 35 | 133 | 201 | N/A | N/A | N/A | N/A | N/A | N/A
| 3 Phase Gang Operated Switches | 970 |  | 361 | 322 | 394 | 317 | 211 | 93 | N/A | N/A | N/A | N/A | N/A | N/A
| Insulators (Washing) (2) | 31000 | 6 months | 2916 | 6143 | 11422 | 8015 | 8217 | 6618 | N/A | N/A | N/A | N/A | N/A | N/A
Note 1: Line patrols are managed on a route kilometre basis. Figures in the table above have been populated using observations from line patrols.
Note 2: Insulator Washing is managed on a per pole location basis. All figures are pole locations.
| Note 3: Includes both line patrol and pole inspection. | [8 empty] | *Please refer to Exhibit 4A, Tab 2, Schedule 1 for information on Toronto's 2020-2024 plans
Note 4: Includes line patrol only. Incremental infra-red patrols performed annually not captured in above data set.
2 | Overhead Deficiencies
# Deficiencies from Prev. & Pred. Maintenance Programs (1)
| Equipment Type |  |  | 2013 (2) | 2014 | 2015 | 2016 | 2017 | 2018
| Pole Mounted Transformers (1) |  |  | (2) | 3 | 30 | 38 | 9 | 9
| Overhead Switches |  |  | # Inspections from Prev. & Pred. Maintenance Programs (1) 2013: See Overhead SCADA Switches and 3 Phase Gang Switches Below
| Lightning Arrestors (1) |  |  | (2) | 10 | 4 | 14 | 4 | 9
| Auxiliary Equipment (1) |  |  | # Inspections from Prev. & Pred. Maintenance Programs (1) 2013: Not available
| Conductor Wire (1) |  |  | (2) | 1 | 7 | 10 | 1 | 4
| Wood Pole |  |  | N/A | 158 | 256 | 417 | 215 | 93
Concrete Pole
Steel Pole
| Line Insulators (1) |  |  | (2) | 5 | 3 | 7 | 2 | 3
| Overhead SCADA Switches |  |  | 47 | 51 | 60 | 8 | 34 | 15
| 3 Phase Gang Operated Switches |  |  | 152 | 200 | 225 | 136 | 52 | 20
| Insulators |  |  | # Inspections from Prev. & Pred. Maintenance Programs (1) 2013: See Line Insulator
Note 1: Deficiencies that may be mapped directly to these equipment types have been included from line patrols only. Line patrols typically identify between 1,000 and 2,000 deficiencies annually, the vast majority of which have not been mapped to the types in the table above. In addition, infra-red patrols identify an additional 20 to 100 deficiencies a year, typically on connection points.
Note 2: Toronto Hydro transitioned from a paper-based data capture system to a digital one in 2013. Not all data available.
3 | Overhead Asset Failures
# Failures (1)
| Equipment Type |  |  | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
| Pole Mounted Transformers |  |  | 185 | 198 | 231 | 113 | 117 | 54
| Overhead Switches |  |  | 235 | 290 | 267 | 242 | 214 | 262
| Auxiliary Equipment |  |  | # Failures (1) 2013: Not Available
Lightning Arrestors
| Conductor Wire |  |  | 4 | 2 | 0 | 2 | 2 | 8
| Wood Pole |  |  | 131 | 195 | 236 | 135 | 159 | 104
| Concrete Pole |  |  | 64 | 113 | 84 | 46 | 57 | 20
| Steel Pole |  |  | 8 | 20 | 5 | 1 | 3 | 1
| Line Insulators |  |  | 0 | 1 | 0 | 5 | 1 | 2
| Overhead SCADA Switches |  |  | 13 | 10 | 9 | 5 | 4 | 8
| 3 Phase Gang Operated Switches |  |  | 6 | 11 | 12 | 10 | 25 | 2
| Insulators |  |  | # Failures (1) 2013: See Line Insulator
Note 1: Captured from Toronto Hydro's Reactive Capital Work Requests and Defective Equipment Tracking System
4 | Overhead Maintenance
# Assets Maintained
| Equipment Type | Population | Maintenance Cycle | 2013 | 2014 | 2015 | 2016 | 2017 | 2018
| Overhead SCADA Switches | Please see figures in Table 1 above.
3 Phase Gang Operated Switches
Insulators (Washing)