## Appendix 2-R
Loss Factors
|  | Historical Years | [5 empty] | 6-Year Average
|  | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Losses Within Distributor's System
A(1) | "Wholesale" kWh delivered to distributor (higher value) | 28011153 | 29749924 | 29940176 | 27625506 | 26137724 | 26216509 | 27946832 | IESO and Hydro One with losses
A(2) | "Wholesale" kWh delivered to distributor (lower value) | 27416251.6 | 29149338.1 | 29316784.5 | 27033615.2 | 25569974.5 | 25649082.6 | 27355841.0833 | IESO and Hydro without losses
B | Portion of "Wholesale" kWh delivered to distributor for its Large Use Customer(s) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Load Transfer | -1127517.2 | -1150832.9 | -1118984.9 | -1102929.8 | -1087662.2 | -938246.2 | -1087695.5333 | delivered from IESO Without losses
C | Net "Wholesale" kWh delivered to distributor = A(2) - B | 26288734.4 | 27998505.2 | 28197799.6 | 25930685.4 | 24482312.3 | 24710836.4 | 26268145.55 | A(2) minus the load transfer
D | "Retail" kWh delivered by distributor | 25022490.8 | 26728813.1 | 26821085.1 | 24700434.2 | 23487176.8 | 23634961.8 | 25065826.9667 | What I delivered to my customers without losses and less load transfer
E | Portion of "Retail" kWh delivered by distributor to its Large Use Customer(s) |  | 0 |  | 0 | 0 | 0 | 0 | C is what was suplied to me and D is what I supplied to my customer all without losses and without load transfers
F | Net "Retail" kWh delivered by distributor = D - E | 25022490.8 | 26728813.1 | 26821085.1 | 24700434.2 | 23487176.8 | 23634961.8 | 25065826.9667
G | Loss Factor in Distributor's system = C / F | 1.0506 | 1.0475 | 1.0513 | 1.0498 | 1.0424 | 1.0455 | 1.0479
Losses Upstream of Distributor's System
H | Supply Facilities Loss Factor | 1.0217 | 1.0206 | 1.0213 | 1.0219 | 1.0222 | 1.0221 | 1.0216
Total Losses
I | Total Loss Factor = G x H | 1.0734 | 1.0691 | 1.0737 | 1.0728 | 1.0655 | 1.0687 | 1.0705
Notes
A(1) | If directly connected to the IESO-controlled grid, kWh pertains to the virtual meter on the primary or high voltage side of the transformer at the interface with the transmission grid. This corresponds to the "With Losses" kWh value provided by the IESO's MV-WEB. It is the higher of the two values provided by MV-WEB.
If fully embedded within a host distributor, kWh pertains to the virtual meter on the primary or high voltage side of the transformer, at the interface between the host distributor and the transmission grid. For example, if the host distributor is Hydro One Networks Inc., kWh from the Hydro One Networks' invoice corresponding to "Total kWh w Losses" should be reported. This corresponds to the higher of the two kWh values provided in Hydro One Networks' invoice.
If partially embedded, kWh pertains to the sum of the above.
A(2) | If directly connected to the IESO-controlled grid, kWh pertains to a metering installation on the secondary or low voltage side of the transformer at the interface with the transmission grid. This corresponds to the "Without Losses" kWh value provided by the IESO's MV-WEB. It is the lower of the two kWh values provided by MV-WEB.
If fully embedded with the host distributor, kWh pertains to a metering installation on the secondary or low voltage side of the transformer at the interface between the embedded distributor and the host distributor. For example, if the host distributor is Hydro One Networks Inc., kWh from the Hydro One Networks' invoice corresponding to "Total kWh" should be reported. This corresponds to the lower of the two kWh values provided in Hydro One Networks' invoice.
If partially embedded, kWh pertains to the sum of the above.
Additionally, kWh pertaining to distributed generation directly connected to the distributor's own distribution network should be included in A(2).
B | If a Large Use Customer is metered on the secondary or low voltage side of the transformer, the default loss is 1% (i.e., B = 1.01 X E).
D | kWh corresponding to D should equal metered or estimated kWh at the customer’s delivery point.
G and I | These loss factors pertain to secondary-metered customers with demand less than 5,000 kW.
H | If directly connected to the IESO-controlled grid, SFLF = 1.0045.
If fully embedded within a host distributor, SFLF = loss factor re losses in transformer at grid interface X loss factor re losses in host distributor's system. If the host distributor is Hydro One Networks Inc., SFLF = 1.0060 X 1.0278 = 1.0340. If partially embedded, SFLF should be calculated as the weighted average of above.
Distributors that wish to propose a different SFLF should provide appropriate justification for any such proposal including supporting
calculations and any other relevant material.