## Sheet1
Table 1 Health Index Results Summary
Asset Category |  | Population | Sample Size | Average Health Index | Health Index Distribution |  |  |  |  | Average Age | Age Availability | Average DAI
[5 empty] | Very Poor (<25%) | Poor (25-<50%) | Fair (50-70%) | Good (70-<85%) | Very Good (>=85%)
Power Transformers | Combined | 10 | 10 | 71% | 2 | 0 | 0 | 2 | 6 | 19 | 100% | 98%
| Main tank | 10 | 10 | 83% | 0 | 0 | 0 | 7 | 3 | 19 | 100% | 98%
| LTC | 10 | 10 | 75% | 2 | 0 | 0 | 2 | 6 | 19 | 100% | 40%
Station Service Tranformers |  | 10 | 10 | 89% | 0 | 0 | 0 | 2 | 8 | 19 | 100% | 0%
Grounding Tranformers |  | 8 | 8 | 88% | 0 | 0 | 0 | 2 | 6 | 20 | 100% | 0%
Instrument Transformers |  | 50 | 44 | 95% | 0 | 0 | 0 | 0 | 44 | 20 | 88% | 0%
Station Breakers | Stand Alone | 9 | 9 | 73% | 0 | 0 | 0 | 8 | 1 | 28 | 100% | 89%
| Switchgear | 24 | 23 | 83% | 3 | 0 | 0 | 0 | 20 | 16 | 96% | 58%
Station Switches |  | 34 | 22 | 97% | 0 | 0 | 0 | 0 | 22 | 19 | 65% | 0%
Relays |  | 102 | 102 | 92% | 0 | 0 | 23 | 0 | 79 | 6 | 100% | 0%
PLC System |  | 47 | 47 | 70% | 18 | 0 | 0 | 0 | 29 | 8 | 100% | 0%
Station Batteries |  | 4 | 4 | 100% | 0 | 0 | 0 | 0 | 4 | 1 | 100% | 0%
Reclosers |  | 68 | 68 | 92% | 0 | 0 | 3 | 1 | 64 | 9 | 100% | 22%
Overhead Switches | Manual | 163 | 125 | 73% | 0 | 16 | 38 | 24 | 47 | 21 | 77% | 0%
| Remote | 52 | 34 | 97% | 0 | 0 | 0 | 4 | 30 | 3 | 54% | 27%
Poles | Wood | 20933 | 20051 | 86% | 1608 | 644 | 314 | 831 | 16654 | 24 | 96% | 85%
| Concrete | 4572 | 4351 | 87% | 2 | 16 | 683 | 514 | 3136 | 23 | 95% | 54%
Distribution Transformers | Pole 1-Ph | 2978 | 2969 | 72% | 141 | 215 | 328 | 1658 | 627 | 14 | 98% | 97%
| Pole 3-Ph | 2324 | 2316 | 73% | 86 | 122 | 251 | 1409 | 448 | 15 | 98% | 97%
| Pad 1-Ph | 1584 | 1342 | 97% | 0 | 1 | 1 | 159 | 1181 | 17 | 85% | 63%
| Pad 3-Ph | 482 | 482 | 78% | 0 | 22 | 113 | 169 | 178 | 19 | 99% | 43%
| Submersible | 556 | 556 | 58% | 85 | 131 | 121 | 132 | 87 | 24 | 98% | 28%
Pad Mounted Switchgear |  | 170 | 146 | 76% | 7 | 12 | 15 | 48 | 64 | 17 | 81% | 70%
Primary Underground Cables (km) |  | 29.8 | 29.8 | 87% | 0.6 | 0 | 4.9 | 4 | 20.3 | 14 | 100% | 0%
Manholes |  | 461 | 386 | 88% | 1 | 3 | 11 | 189 | 182 | 49 | 37% | 35%