## Sheet1
2.0-AMPCO-28
Hydro One Networks Inc. Transmission Rate Application
EB-2019-0082
Ex B TSP Section 2
Replacement History by ESL & Condition
TRANSMISSION ASSETS | Population | Expected Service Life | 2015 # replaced beyond ESL | 2016 # replaced beyond ESL | 2017 # replaced beyond ESL | 2018 # replaced beyond ESL | 2015 # replaced in very high & high risk | 2016 # replaced in very high & high risk | 2017 # replaced in very high & high risk | 2018 # replaced in very high & high risk | 2015 # replaced beyond ESL & in very high & high risk | 2016 # replaced beyond ESL & in very high & high risk | 2017 # replaced beyond ESL & in very high & high risk | 2018 # replaced beyond ESL & in very high & high risk
Transformer
115kV | 273 | 40-60 | 10 | 16 | 10 | 13 | 8 | 8 | 8 | 5 | 6 | 7 | 7 | 5
230 kV | 397 | 40-50 | 7 | 4 | 5 | 15 | 4 | 3 | 3 | 6 | 4 | 2 | 3 | 6
500 kV | 46 | 40 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 0
Circuit Breakers
Oil | 1600 | 55 | 20 | 13 | 23 | 58 | 23 | 13 | 58 | 63 | 20 | 13 | 23 | 58
SF 6 | 1857 | 40 | 3 | 6 | 1 | 1 | 20 | 15 | 9 | 3 | 3 | 6 | 1 | 1
Air Blast | 157 | 40 | 10 | 19 | 13 | 17 | 10 | 19 | 13 | 17 | 10 | 19 | 13 | 17
GIS | 364 | 40 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Metaclad | 767 | 40 | 0 | 4 | 3 | 0 | 1 | 10 | 14 | 1 | 0 | 4 | 3 | 0
Vacuum | 29 | 40 | 1 | 3 | 0 | 7 | 3 | 3 | 0 | 7 | 1 | 3 | 0 | 7
Protection Systems
Electromechanical | 3484 | 45 | 66 | 77 | 54 | 55 | 66 | 77 | 54 | 55 | 66 | 77 | 54 | 55
Solid State | 1970 | 25 | 126 | 235 | 104 | 103 | 126 | 235 | 104 | 103 | 126 | 235 | 104 | 103
Microprocessor | 7268 | 20 | 1 | 7 | 1 | 5 | 1 | 7 | 1 | 5 | 1 | 7 | 1 | 5
Conductors (circuit-km) | 29107 | 70 (These replacements were planned before the ESL for ACSR conductors was changed from 70 to 90 years - Therefore they are based on an ESL of 70 years) See: Exhibit B-1-1, TSP Section 1.4, Attachment 4 | 201 | 183 | 119 | 51 | 201 | 183 | 119 | 51 | 201 | 183 | 119 | 51
Poles1
Wood |  | 50 years | 0 | 0 | 0 | 0 | 845 | 761 | 966 | 735 | 0 | 0 | 0 | 0
Steel Structures2
Steel Towers in Light Corrosion Zones |  | 80 years | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Steel Towers in Heavy Corrosion Zones |  | 80 years | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Steel Poles |  | 80 years | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Insulators
Glass | N/A | 70 years (as per for life of the line) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Poreclain | N/A | 70 years (as per for life of the line) | 0 | 0 | 0 | 0 | 155 | 2100 | 3422 | 3900 | 0 | 0 | 0 | 0
Polymer | N/A | 30 years | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 58 | 0 | 0 | 0 | 0
Underground Cable
LPLF | 60 km | 70 years | 0 | 0 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0
HPLF | 173 km | 70 years | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XLPE | 31 km | 50 years | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Notes:
1. Wood Poles are only replaced at end of life (high risk) per Hydro One asset management phylosophy. Records of the structures replacements which had passed ESL are not readily available.
2. Steel Structures are not scheduled to be replaced under a yearly program. They are coated in order to extend their life and delay high capital costs in the future.

## Sheet2
2.0-AMPCO-
Hydro One Networks Inc. Transmission Rate Application
EB-2019-0082
Ex B TSP Section 2
Failure Rates
TRANSMISSION ASSETS
Transformer
115kV
230 kV
500 kV
Circuit Breakers
Oil
SF 6
Air Blast
GIS
Metaclad
Vacuum
Protection Systems
Electromechanical
Solid State
Microprocessor
Conductors
Poles
Wood
Steel Structures
Insulators
Glass
Poreclain
Polymer
circuit structures
Underground Cable