## Sheet1
2.0-AMPCO-30
Hydro One Networks Inc. Transmission Rate Application
EB-2019-0082
Ex B TSP Section 2
5 Year Asset Failure History
TRANSMISSION ASSETS | Current Population | # Failures 2014 | # Failures 2015 | # Failures 2016 | # Failures 2017 | # Failures 2018
Transformer
115kV | 273 | 3 | 1 | 2 | 1 | 5
230 kV | 397 | 1 | 2 | 2 | 1 | 3
500 kV | 46 | 1 | 1 | 2 | 1 | 1
Circuit Breakers
Oil | 1600 | 2 | 4 | 6 | 3 | 1
SF 6 | 1857 | 0 | 0 | 1 | 1 | 0
Air Blast | 157 | 0 | 2 | 1 | 0 | 0
GIS | 364 | 0 | 0 | 0 | 0 | 0
Metaclad | 767 | 0 | 0 | 2 | 0 | 0
Vacuum | 29 | 0 | 0 | 0 | 0 | 0
Protection Systems
Electromechanical | 3484 | 23 | 28 | 22 | 42 | 38
Solid State | 1970 | 21 | 17 | 25 | 25 | 17
Microprocessor | 7268 | 54 | 78 | 88 | 99 | 98
Conductors | 29107 | 4 | 3 | 6 | 1 | 5
Poles
Wood | 42000 | 10 | 6 | 19 | 22 | 26
Steel Structures
Steel Towers in Light Corrosion Zones | 37300 | 1 | 1 | 1 | 2 | 8
Steel Towers in Heavy Corrosion Zones | 13000
Steel Poles | 1950 | 0 | 0 | 0 | 0 | 0
Insulators
Glass | 30% | 0 | 0 | 0 | 0 | 0
Poreclain | 60% | 4 | 9 | 4 | 6 | 6
Polymer | 10% | 1 | 2 | 3 | 2 | 1
Underground Cable
LPLF | 60 km | 0 | 1 | 2 | 2 | 2
HPLF | 173 km | 0 | 1 | 2 | 2 | 2
XLPE | 31 km | 0 | 0 | 0 | 0 | 0
Note on G23: TURKBEN Deniz: forced outage frequency

## Sheet2
2.0-AMPCO-
Hydro One Networks Inc. Transmission Rate Application
EB-2019-0082
Ex B TSP Section 2
Failure Rates
TRANSMISSION ASSETS
Transformer
115kV
230 kV
500 kV
Circuit Breakers
Oil
SF 6
Air Blast
GIS
Metaclad
Vacuum
Protection Systems
Electromechanical
Solid State
Microprocessor
Conductors
Poles
Wood
Steel Structures
Insulators
Glass
Poreclain
Polymer
circuit structures
Underground Cable