## Sheet1
AMPCO_SUB_THESL_20190828_Appendix A
EB-2018-0165
Original AMPCO ACA Table - Panel 1 - Uncorrected
| 2B-AMPCO-42 (a) ACA from EB-2014-0116 | [18 empty] | 2B-AMPCO-48 2016 ACA from EB-2018-0165
| 2014 ACA Results - Kinectrics Methodology | [18 empty] | 2016 ACA Results - Kinectrics Methodology
| Asset | Population | Sample Size % | % very poor | % poor | % fair | % good | % very good | % very poor & poor | % very poor, poor & fair | # very poor | # poor | # fair | # good | # very good | Total | # very poor & poor | # very poor, poor & fair |  | Asset | Population | Sample Size % | % very poor | % poor | % fair | % good | % very good | % very poor & poor | % very poor, poor & fair | # very poor | # poor | # fair | # good | # very good | Total | # very poor & poor | # very poor, poor & fair
1 | Station Power Transformer | 268 | 90.3 | 1.24% | 13.64% | 49.59% | 23.14% | 12.4% | 14.88% | 64.47% | 3.3232 | 36.5552 | 132.9012 | 62.0152 | 33.232 | 268.0268 | 39.8784 | 172.7796 | 1 | Station Power Transformer | 292 | 89.7 | 0% | 0.4% | 26.7% | 49.6% | 23.3% | 0.4% | 27.1% | 0 | 1.168 | 77.964 | 144.832 | 68.036 | 292 | 1.168 | 79.132
2 | Station Switchgear | 279 | 88.89 | 4.84% | 36.69% | 33.47% | 9.27% | 15.73% | 41.53% | 75% | 13.5036 | 102.3651 | 93.3813 | 25.8633 | 43.8867 | 279 | 115.8687 | 209.25 | 2 | Station Switchgear
3 | Air Blast Circuit Breakers | 290 | 62.07 | 0% | 3.89% | 87.78% | 2.78% | 5.56% | 3.89% | 91.67% | 0 | 11.281 | 254.562 | 8.062 | 16.124 | 290.029 | 11.281 | 265.843 | 3 | Air Blast Circuit Breakers | 241 | 75.9 | 0% | 4.4% | 88% | 7.1% | 0.6% | 4.4% | 92.4% | 0 | 10.604 | 212.08 | 17.111 | 1.446 | 241.241 | 10.604 | 222.684
4 | Air Magnetic Circuit Breakers | 627 | 74.32 | 0.21% | 4.72% | 74.25% | 18.88% | 1.93% | 4.93% | 79.18% | 1.3167 | 29.5944 | 465.5475 | 118.3776 | 12.1011 | 626.9373 | 30.9111 | 496.4586 | 4 | Air Magnetic Circuit Breakers | 562 | 89.7 | 0.2% | 6.2% | 74.4% | 16.9% | 2.4% | 6.4% | 80.8% | 1.124 | 34.844 | 418.128 | 94.978 | 13.488 | 562.562 | 35.968 | 454.096
5 | Oil Circuit Breakers | 332 | 47.29 | 0.64% | 10.19% | 82.8% | 6.37% | 0% | 10.83% | 93.63% | 2.1248 | 33.8308 | 274.896 | 21.1484 | 0 | 332 | 35.9556 | 310.8516 | 5 | Oil Circuit Breakers | 198 | 74.2 | 0% | 12.9% | 79.6% | 7.5% | 0% | 12.9% | 92.5% | 0 | 25.542 | 157.608 | 14.85 | 0 | 198 | 25.542 | 183.15
6 | Oil KSO Breakers | 59 | 37.29 | 0% | 4.55% | 81.82% | 13.64% | 0% | 4.55% | 86.37% | 0 | 2.6845 | 48.2738 | 8.0476 | 0 | 59.0059 | 2.6845 | 50.9583 | 6 | Oil KSO Breakers | 46 | 84.8 | 0% | 7.7% | 74.4% | 18% | 0% | 7.7% | 82.1% | 0 | 3.542 | 34.224 | 8.28 | 0 | 46.046 | 3.542 | 37.766
7 | SF6 Circuit Breaker | 201 | 32.34 | 0% | 0% | 7.69% | 46.15% | 46.15% | 0% | 7.69% | 0 | 0 | 15.4569 | 92.7615 | 92.7615 | 200.9799 | 0 | 15.4569 | 7 | SF6 Circuit Breaker | 174 | 70.7 | 0% | 0% | 19.5% | 65% | 15.5% | 0% | 19.5% | 0 | 0 | 33.93 | 113.1 | 26.97 | 174 | 0 | 33.93
8 | Vacuum Circuit Breakers | 675 | 70.81 | 0% | 0.21% | 3.14% | 10.25% | 86.4% | 0.21% | 3.35% | 0 | 1.4175 | 21.195 | 69.1875 | 583.2 | 675 | 1.4175 | 22.6125 | 8 | Vacuum Circuit Breakers | 661 | 81.4 | 0% | 0.2% | 4.8% | 42.2% | 52.8% | 0.2% | 5% | 0 | 1.322 | 31.728 | 278.942 | 349.008 | 661 | 1.322 | 33.05
9 | Submersible Transformers | 9554 | 95.2 | 0% | 0.02% | 6.68% | 34.93% | 58.36% | 0.02% | 6.7% | 0 | 1.9108 | 638.2072 | 3337.2122 | 5575.7144 | 9553.0446 | 1.9108 | 640.118 | 9 | Submersible Transformers | 9244 | 97.9 | 0% | 0.5% | 8.6% | 33.1% | 57.9% | 0.5% | 9.1% | 0 | 46.22 | 794.984 | 3059.764 | 5352.276 | 9253.244 | 46.22 | 841.204
10 | Vault Transformers | 13034 | 88.24 | 0% | 0.23% | 23.48% | 39.8% | 36.5% | 0.23% | 23.71% | 0 | 29.9782 | 3060.3832 | 5187.532 | 4757.41 | 13035.3034 | 29.9782 | 3090.3614 | 10 | Vault Transformers | 13283 | 91.5 | 0% | 1% | 28.4% | 42% | 28.7% | 1% | 29.4% | 0 | 132.83 | 3772.372 | 5578.86 | 3812.221 | 13296.283 | 132.83 | 3905.202
11 | Padmounted Transformers | 7160 | 84.55 | 0% | 0.02% | 10.09% | 43.51% | 46.38% | 0.02% | 10.11% | 0 | 1.432 | 722.444 | 3115.316 | 3320.808 | 7160 | 1.432 | 723.876 | 11 | Padmounted Transformers | 7496 | 88.6 | 0% | 0% | 6.8% | 79.3% | 13.9% | 0% | 6.8% | 0 | 0 | 509.728 | 5944.328 | 1041.944 | 7496 | 0 | 509.728
12 | Padmounted Switches | 802 | 97.01 | 0% | 0.39% | 7.2% | 36.12% | 56.3% | 0.39% | 7.59% | 0 | 3.1278 | 57.744 | 289.6824 | 451.526 | 802.0802 | 3.1278 | 60.8718 | 12 | Padmounted Switches | 643 | 94.9 | 0% | 0% | 4.3% | 55.6% | 40.2% | 0% | 4.3% | 0 | 0 | 27.649 | 357.508 | 258.486 | 643.643 | 0 | 27.649
13 | 3 Phase O/H Gang Manual Switches | 1108 | 32.94 | 0% | 0.39% | 3.01% | 63.84% | 33.15% | 0.39% | 3.4% | 0 | 4.3212 | 33.3508 | 707.3472 | 367.302 | 1112.3212 | 4.3212 | 37.672 | 13 | 3 Phase O/H Gang Manual Switches | 1071 | 54 | 0% | 0.2% | 1% | 70.4% | 28.4% | 0.2% | 1.2% | 0 | 2.142 | 10.71 | 753.984 | 304.164 | 1071 | 2.142 | 12.852
14 | 3 Phase O/H Gang Remote Switches | 15 | 86.67 | 0% | 0% | 15.38% | 76.92% | 7.69% | 0% | 15.38% | 0 | 0 | 2.307 | 11.538 | 1.1535 | 14.9985 | 0 | 2.307 | 14 | 3 Phase O/H Gang Remote Switches
15 | SCADAMATE Switches | 926 | 85.31 | 0.13% | 0% | 1.14% | 57.34% | 41.39% | 0.13% | 1.27% | 1.2038 | 0 | 10.5564 | 530.9684 | 383.2714 | 926 | 1.2038 | 11.7602 | 15 | SCADAMATE Switches | 1114 | 93.7 | 0% | 0% | 0.9% | 41.8% | 57.4% | 0% | 0.9% | 0 | 0 | 10.026 | 465.652 | 639.436 | 1115.114 | 0 | 10.026
16 | Wood Poles | 123280 | 37.66 | 2.34% | 7.64% | 44.13% | 7.28% | 38.61% | 9.98% | 54.11% | 2884.752 | 9418.592 | 54403.464 | 8974.784 | 47598.408 | 123280 | 12303.344 | 66706.808 | 16 | Wood Poles | 125899 | 67.3 | 1.5% | 1.4% | 15.6% | 19.6% | 61.9% | 2.9% | 18.5% | 1888.485 | 1762.586 | 19640.244 | 24676.204 | 77931.481 | 125899 | 3651.071 | 23291.315
17 | Automatic Transfer Switches | 58 | 91.38 | 0% | 16.98% | 32.08% | 30.19% | 20.75% | 16.98% | 49.06% | 0 | 9.8484 | 18.6064 | 17.5102 | 12.035 | 58 | 9.8484 | 28.4548 | 17 | Automatic Transfer Switches | 39 | 66.7 | 0% | 0% | 15.4% | 76.9% | 7.7% | 0% | 15.4% | 0 | 0 | 6.006 | 29.991 | 3.003 | 39 | 0 | 6.006
18 | Network Transformers | 1892 | 99.58 | 0% | 0% | 16.4% | 41.45% | 42.14% | 0% | 16.4% | 0 | 0 | 310.288 | 784.234 | 797.2888 | 1891.8108 | 0 | 310.288 | 18 | Network Transformers | 1821 | 98.2 | 0% | 0.1% | 7.1% | 42.2% | 50.6% | 0.1% | 7.2% | 0 | 1.821 | 129.291 | 768.462 | 921.426 | 1821 | 1.821 | 131.112
19 | Network Protectors | 1615 | 97.52 | 0% | 0% | 3.75% | 32.25% | 64% | 0% | 3.75% | 0 | 0 | 60.5625 | 520.8375 | 1033.6 | 1615 | 0 | 60.5625 | 19 | Network Protectors | 1683 | 98.2 | 0% | 0.1% | 27.5% | 12.5% | 59.8% | 0.1% | 27.6% | 0 | 1.683 | 462.825 | 210.375 | 1006.434 | 1681.317 | 1.683 | 464.508
20 | Network Vaults | 1062 | 99.53 | 1.7% | 8.8% | 72.37% | 16.08% | 1.04% | 10.5% | 82.87% | 18.054 | 93.456 | 768.5694 | 170.7696 | 11.0448 | 1061.8938 | 111.51 | 880.0794 | 20 | Network Vaults | 1055 | 99.6 | 0% | 0.9% | 32.5% | 66.6% | 0% | 0.9% | 33.4% | 0 | 9.495 | 342.875 | 702.63 | 0 | 1055 | 9.495 | 352.37
21 | Cable Cambers | 10902 | 35.01 | 0.26% | 1.6% | 10.77% | 50.17% | 37.2% | 1.86% | 12.63% | 28.3452 | 174.432 | 1174.1454 | 5469.5334 | 4055.544 | 10902 | 202.7772 | 1376.9226 | 21 | Cable Cambers | 11132 | 62.4 | 0.2% | 2.7% | 10.1% | 62.4% | 24.6% | 2.9% | 13% | 22.264 | 300.564 | 1124.332 | 6946.368 | 2738.472 | 11132 | 322.828 | 1447.16
22 | TOTAL | 174139 | [14 empty] | 12907.4502 | 75474.2922 |  | TOTAL | 176654 | [14 empty] | 4246.236 | 32042.94
[17 empty] | 7.412% | [18 empty] | 2.404%