## Sheet1
AMPCO_SUB_THESL_20190828_Appendix B
EB-2018-0165
AMPCO ACA Table - Panel 1 - Corrected
| 2B-AMPCO-42 (a) ACA from EB-2014-0116 | [19 empty] | 2B-AMPCO-48 ACA from EB-2018-0165
| 2014 ACA - Kinectrics Methodology | [19 empty] | 2016 ACA - Kinectrics Methodology
| Asset | Population | Sample Size % | Adjusted Population for Sample Size | % very poor | % poor | % fair | % good | % very good | % very poor & poor | % very poor, poor & fair | # very poor | # poor | # fair | # good | # very good | Total | # very poor & poor | # very poor, poor & fair |  | Asset | Population | Sample Size % | Adjusted Population for Sample Size | % very poor | % poor | % fair | % good | % very good | % very poor & poor | % very poor, poor & fair | # very poor | # poor | # fair | # good | # very good | Total | # very poor & poor | # very poor, poor & fair
1 | Station Power Transformer | 268 | 90.3 | 242.004 | 1.24% | 13.64% | 49.59% | 23.14% | 12.4% | 14.88% | 64.47% | 3.0008 | 33.0093 | 120.0098 | 55.9997 | 30.0085 | 242.0282 | 36.0102 | 156.02 | 1 | Station Power Transformer | 292 | 89.7 | 261.924 | 0% | 0.4% | 26.7% | 49.6% | 23.3% | 0.4% | 27.1% | 0 | 1.0477 | 69.9337 | 129.9143 | 61.0283 | 261.924 | 1.0477 | 70.9814
2 | Station Switchgear | 279 | 88.89 | 248.0031 | 4.84% | 36.69% | 33.47% | 9.27% | 15.73% | 41.53% | 75% | 12.0034 | 90.9923 | 83.0066 | 22.9899 | 39.0109 | 248.0031 | 102.9957 | 186.0023 | 2 | Station Switchgear
3 | Air Blast Circuit Breakers | 290 | 62.07 | 180.003 | 0% | 3.89% | 87.78% | 2.78% | 5.56% | 3.89% | 91.67% | 0 | 7.0021 | 158.0066 | 5.0041 | 10.0082 | 180.021 | 7.0021 | 165.0088 | 3 | Air Blast Circuit Breakers | 241 | 75.9 | 182.919 | 0% | 4.4% | 88% | 7.1% | 0.6% | 4.4% | 92.4% | 0 | 8.0484 | 160.9687 | 12.9872 | 1.0975 | 183.1019 | 8.0484 | 169.0172
4 | Air Magnetic Circuit Breakers | 627 | 74.32 | 465.9864 | 0.21% | 4.72% | 74.25% | 18.88% | 1.93% | 4.93% | 79.18% | 0.97857 | 21.9946 | 345.9949 | 87.9782 | 8.9935 | 465.9398 | 22.9731 | 368.968 | 4 | Air Magnetic Circuit Breakers | 562 | 89.7 | 504.114 | 0.2% | 6.2% | 74.4% | 16.9% | 2.4% | 6.4% | 80.8% | 1.0082 | 31.2551 | 375.0608 | 85.1953 | 12.0987 | 504.6181 | 32.2633 | 407.3241
5 | Oil Circuit Breakers | 332 | 47.29 | 157.0028 | 0.64% | 10.19% | 82.8% | 6.37% | 0% | 10.83% | 93.63% | 1.0048 | 15.9986 | 129.9983 | 10.0011 | 0 | 157.0028 | 17.0034 | 147.0017 | 5 | Oil Circuit Breakers | 198 | 74.2 | 146.916 | 0% | 12.9% | 79.6% | 7.5% | 0% | 12.9% | 92.5% | 0 | 18.9522 | 116.9451 | 11.0187 | 0 | 146.916 | 18.9522 | 135.8973
6 | Oil KSO Breakers | 59 | 37.29 | 22.0011 | 0% | 4.55% | 81.82% | 13.64% | 0% | 4.55% | 86.37% | 0 | 1.0011 | 18.0013 | 3.001 | 0 | 22.0033 | 1.0011 | 19.0024 | 6 | Oil KSO Breakers | 46 | 84.8 | 39.008 | 0% | 7.7% | 74.4% | 18% | 0% | 7.7% | 82.1% | 0 | 3.0036 | 29.022 | 7.0214 | 0 | 39.047 | 3.0036 | 32.0256
7 | SF6 Circuit Breaker | 201 | 32.34 | 65.0034 | 0% | 0% | 7.69% | 46.15% | 46.15% | 0% | 7.69% | 0 | 0 | 4.9988 | 29.9991 | 29.9991 | 64.9969 | 0 | 4.9988 | 7 | SF6 Circuit Breaker | 174 | 70.7 | 123.018 | 0% | 0% | 19.5% | 65% | 15.5% | 0% | 19.5% | 0 | 0 | 23.9885 | 79.9617 | 19.0678 | 123.018 | 0 | 23.9885
8 | Vacuum Circuit Breakers | 675 | 70.81 | 477.9675 | 0% | 0.21% | 3.14% | 10.25% | 86.4% | 0.21% | 3.35% | 0 | 1.0037 | 15.0082 | 48.9917 | 412.9639 | 477.9675 | 1.0037 | 16.0119 | 8 | Vacuum Circuit Breakers | 661 | 81.4 | 538.054 | 0% | 0.2% | 4.8% | 42.2% | 52.8% | 0.2% | 5% | 0 | 1.0761 | 25.8266 | 227.0588 | 284.0925 | 538.054 | 1.0761 | 26.9027
9 | Submersible Transformers | 9554 | 95.2 | 9095.408 | 0% | 0.02% | 6.68% | 34.93% | 58.36% | 0.02% | 6.7% | 0 | 1.8191 | 607.5733 | 3177.026 | 5308.0801 | 9094.4985 | 1.8191 | 609.3923 | 9 | Submersible Transformers | 9244 | 97.9 | 9049.876 | 0% | 0.5% | 8.6% | 33.1% | 57.9% | 0.5% | 9.1% | 0 | 45.2494 | 778.2893 | 2995.509 | 5239.8782 | 9058.9259 | 45.2494 | 823.5387
10 | Vault Transformers | 13034 | 88.24 | 11501.2016 | 0% | 0.23% | 23.48% | 39.8% | 36.5% | 0.23% | 23.71% | 0 | 26.4528 | 2700.4821 | 4577.4782 | 4197.9386 | 11502.3517 | 26.4528 | 2726.9349 | 10 | Vault Transformers | 13283 | 91.5 | 12153.945 | 0% | 1% | 28.4% | 42% | 28.7% | 1% | 29.4% | 0 | 121.5395 | 3451.7204 | 5104.6569 | 3488.1822 | 12166.0989 | 121.5395 | 3573.2598
11 | Padmounted Transformers | 7160 | 84.55 | 6053.78 | 0% | 0.02% | 10.09% | 43.51% | 46.38% | 0.02% | 10.11% | 0 | 1.2108 | 610.8264 | 2633.9997 | 2807.7432 | 6053.78 | 1.2108 | 612.0372 | 11 | Padmounted Transformers | 7496 | 88.6 | 6641.456 | 0% | 0% | 6.8% | 79.3% | 13.9% | 0% | 6.8% | 0 | 0 | 451.619 | 5266.6746 | 923.1624 | 6641.456 | 0 | 451.619
12 | Padmounted Switches | 802 | 97.01 | 778.0202 | 0% | 0.39% | 7.2% | 36.12% | 56.3% | 0.39% | 7.59% | 0 | 3.0343 | 56.0175 | 281.0209 | 438.0254 | 778.098 | 3.0343 | 59.0517 | 12 | Padmounted Switches | 643 | 94.9 | 610.207 | 0% | 0% | 4.3% | 55.6% | 40.2% | 0% | 4.3% | 0 | 0 | 26.2389 | 339.2751 | 245.3032 | 610.8172 | 0 | 26.2389
13 | 3 Phase O/H Gang Manual Switches | 1108 | 32.94 | 364.9752 | 0% | 0.39% | 3.01% | 63.84% | 33.15% | 0.39% | 3.4% | 0 | 1.4234 | 10.9858 | 233.0002 | 120.9893 | 366.3986 | 1.4234 | 12.4092 | 13 | 3 Phase O/H Gang Manual Switches | 1071 | 54 | 578.34 | 0% | 0.2% | 1% | 70.4% | 28.4% | 0.2% | 1.2% | 0 | 1.1567 | 5.7834 | 407.1514 | 164.2486 | 578.34 | 1.1567 | 6.9401
14 | 3 Phase O/H Gang Remote Switches | 15 | 86.67 | 13.0005 | 0% | 0% | 15.38% | 76.92% | 7.69% | 0% | 15.38% | 0 | 0 | 1.9995 | 10 | 0.99974 | 12.9992 | 0 | 1.9995 | 14 | 3 Phase O/H Gang Remote Switches
15 | SCADAMATE Switches | 926 | 85.31 | 789.9706 | 0.13% | 0% | 1.14% | 57.34% | 41.39% | 0.13% | 1.27% | 1.027 | 0 | 9.0057 | 452.9691 | 326.9688 | 789.9706 | 1.027 | 10.0326 | 15 | SCADAMATE Switches | 1114 | 93.7 | 1043.818 | 0% | 0% | 0.9% | 41.8% | 57.4% | 0% | 0.9% | 0 | 0 | 9.3944 | 436.3159 | 599.1515 | 1044.8618 | 0 | 9.3944
16 | Wood Poles | 123280 | 37.66 | 46427.248 | 2.34% | 7.64% | 44.13% | 7.28% | 38.61% | 9.98% | 54.11% | 1086.3976 | 3547.0417 | 20488.3445 | 3379.9037 | 17925.5605 | 46427.248 | 4633.4394 | 25121.7839 | 16 | Wood Poles | 125899 | 67.3 | 84730.027 | 1.5% | 1.4% | 15.6% | 19.6% | 61.9% | 2.9% | 18.5% | 1270.9504 | 1186.2204 | 13217.8842 | 16607.0853 | 52447.8867 | 84730.027 | 2457.1708 | 15675.055
17 | Automatic Transfer Switches | 58 | 91.38 | 53.0004 | 0% | 16.98% | 32.08% | 30.19% | 20.75% | 16.98% | 49.06% | 0 | 8.9995 | 17.0025 | 16.0008 | 10.9976 | 53.0004 | 8.9995 | 26.002 | 17 | Automatic Transfer Switches | 39 | 66.7 | 26.013 | 0% | 0% | 15.4% | 76.9% | 7.7% | 0% | 15.4% | 0 | 0 | 4.006 | 20.004 | 2.003 | 26.013 | 0 | 4.006
18 | Network Transformers | 1892 | 99.58 | 1884.0536 | 0% | 0% | 16.4% | 41.45% | 42.14% | 0% | 16.4% | 0 | 0 | 308.9848 | 780.9402 | 793.9402 | 1883.8652 | 0 | 308.9848 | 18 | Network Transformers | 1821 | 98.2 | 1788.222 | 0% | 0.1% | 7.1% | 42.2% | 50.6% | 0.1% | 7.2% | 0 | 1.7882 | 126.9638 | 754.6297 | 904.8403 | 1788.222 | 1.7882 | 128.752
19 | Network Protectors | 1615 | 97.52 | 1574.948 | 0% | 0% | 3.75% | 32.25% | 64% | 0% | 3.75% | 0 | 0 | 59.0605 | 507.9207 | 1007.9667 | 1574.948 | 0 | 59.0605 | 19 | Network Protectors | 1683 | 98.2 | 1652.706 | 0% | 0.1% | 27.5% | 12.5% | 59.8% | 0.1% | 27.6% | 0 | 1.6527 | 454.4942 | 206.5883 | 988.3182 | 1651.0533 | 1.6527 | 456.1469
20 | Network Vaults | 1062 | 99.53 | 1057.0086 | 1.7% | 8.8% | 72.37% | 16.08% | 1.04% | 10.5% | 82.87% | 17.9691 | 93.0168 | 764.9571 | 169.967 | 10.9929 | 1056.9029 | 110.9859 | 875.943 | 20 | Network Vaults | 1055 | 99.6 | 1050.78 | 0% | 0.9% | 32.5% | 66.6% | 0% | 0.9% | 33.4% | 0 | 9.457 | 341.5035 | 699.8195 | 0 | 1050.78 | 9.457 | 350.9605
21 | Cable Cambers | 10902 | 35.01 | 3816.7902 | 0.26% | 1.6% | 10.77% | 50.17% | 37.2% | 1.86% | 12.63% | 9.9237 | 61.0686 | 411.0683 | 1914.8836 | 1419.846 | 3816.7902 | 70.9923 | 482.0606 | 21 | Cable Cambers | 11132 | 62.4 | 6946.368 | 0.2% | 2.7% | 10.1% | 62.4% | 24.6% | 2.9% | 13% | 13.8927 | 187.5519 | 701.5832 | 4334.5336 | 1708.8065 | 6946.368 | 201.4447 | 903.0278
| TOTAL | 174139 |  | 85267.3762 | [7 empty] | 1132.305 | 3915.0686 |  |  |  | 85268.8139 | 5047.3736 | 31968.7061 |  | TOTAL | 176654 |  | 128067.711 | [7 empty] | 1285.8514 | 1617.9989 |  |  |  | 128089.6422 | 2903.8502 | 23275.0758
[18 empty] | 5.919% | [19 empty] | 2.267%