## 2020 - FULL
Dry Core Transformer Losses Proposed for 2020
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.3448 | 0.0869 |  | 4.5731
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.85888 | 7.8976 | 8.7565 | 0.73487 | 9.4914
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1452 | 10.5302 | 11.6754 | 0.97983 | 12.6552
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4601 | 13.2473 | 14.7074 | 1.2493 | 15.9567
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9468 | 18.2587 | 20.2055 | 1.6657 | 21.8713
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3476 | 21.2295 | 23.5771 | 2.0086 | 25.5857
150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1063 | 27.9377 | 31.0439 | 2.6578 | 33.7017
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.8649 | 34.6459 | 38.5108 | 3.3069 | 41.8177
200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.1352 | 37.0881 | 41.2233 | 3.5381 | 44.7614
225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4438 | 39.8581 | 44.3019 | 3.8022 | 48.1041
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7524 | 42.628 | 47.3805 | 4.0663 | 51.4468
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68712 | 6.4968 | 7.1839 | 0.58791 | 7.7718
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7178 | 15.7953 | 17.513 | 1.4697 | 18.9828
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2904 | 21.0604 | 23.3507 | 1.9597 | 25.3104
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.3783 | 31.4214 | 34.7997 | 2.8905 | 37.6903
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.094 | 37.1093 | 41.2033 | 3.5029 | 44.7062
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1247 | 47.3013 | 52.426 | 4.3848 | 56.8107
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2126 | 57.6623 | 63.875 | 5.3156 | 69.1906
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7959 | 120.6126 | 132.4085 | 10.0927 | 142.5012
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4604 | 152.8796 | 168.34 | 13.2281 | 181.5681
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3501 | 172.7562 | 190.1063 | 14.845 | 204.9512
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1906 | 229.3193 | 252.51 | 19.8422 | 272.3522
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.657 | 274.6759 | 302.3329 | 23.6637 | 325.9966
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2113 | 330.3935 | 363.6049 | 28.4161 | 392.021
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1665 | 390.8689 | 430.0355 | 33.5114 | 463.5469
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.0993 | 481.582 | 529.6813 | 41.1545 | 570.8358
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.2571 | 556.3308 | 611.5879 | 47.2788 | 658.8666