## Master
Project List for Oral Hearing Undertakings
Project Number | Funding | Project Name | 2020 ($MM) | 2021 ($MM) | 2022 ($MM) | 2023 ($MM) | 2024 ($MM) | Total DSP 2020-2024 ($MM) | Project Score | Investment Category | Investment Grouping | Rate Zone | Comment
150404 | Base | Kenilworth TS Power Factor Correction | 0.10114 | 0.86947 | 0.62073 | 0 | 0 | 1.5913 | 184356.97 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of capacitor bank installation at Kenilworth TS to improve PF and to comply with IESO market rules.
150725 | Base | Lines Central-North - Reactive Renewal | 1.1952 | 1.2209 | 1.2471 | 1.2739 | 1.3013 | 6.2385 | 181453.58 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have failured and requires replacement in order to restore power to customers
150690 | Base | Lines Central-South - Reactive Renewal | 3.0631 | 3.1289 | 3.1962 | 3.2649 | 3.3351 | 15.9883 | 171817.68 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have failured and requires replacement in order to restore power to customers
150682 | Base | Remote Fault Indicator Deployment | 0.43832 | 0.4434 | 0.44855 | 0.45375 | 0.10035 | 1.8844 | 164220.93 | System Service | System Control, Comm'ns & Performance | Multiple | This project consists of remote fault indictor deployment which will result improved outage response, operational efficiency, and reliability
150217 | Base | Build double 27.6kV ccts on Teston Rd and Pine Valley Dr to supply Block 40/47 | 1.4455 | 0 | 0 | 0 | 0 | 1.4455 | 151265.43 | System Service | Capacity (Lines) | Powerstream | This project is to rebuild existing 8.32 kV poleline on teston road (Pine Valley drive to Weston road) as it does not have sufficent capacity for new developments.
150587 | Base | Kenilworth TS Upgrade | 0.55677 | 0 | 0 | 0 | 0 | 0.55677 | 134983.87 | System Access | Transmitter Related Upgrades | Horizon | HONI will be replacing transformers at Kenilworth TS which is at physical end-of-life, as well as switchgear. Alectra Utilities role in the project will be to coordinate planned outages and disconnect and reconnect feeder egress connections
150259 | Base | Barrie TS Upgrade Feeders and Metering | 0 | 2.2052 | 0 | 0 | 0 | 2.2052 | 127868.42 | System Access | Transmitter Related Upgrades | Powerstream | Hydro One will be rebuilding and reconfiguring its Barrie TS. As part of this upgrade, Hydro One plans to increase the capacity from 55/92 MVA to 75/125MVA and upgrade the E/4B transmission line from 115KV to 230KV. The feeder egress relocation and additional feeder will require integration reconfiguration for the six Alectra Utilities feeders (13M3 to 13M8) emanating from the station
102247 | Base | Interest Capitalization | 1.1166 | 1.1518 | 1.1887 | 1.2263 | 1.2646 | 5.948 | 104303.71 | General Plant | Other General Plant | Powerstream
150596 | Base | Meter Renewal - all types but Suite - PowerStream RZ | 0.082053 | 0.083143 | 0.085105 | 0.087106 | 0.089146 | 0.42655 | 94470.24 | System Access | Metering | Powerstream | Multi-year project to renew existing residential (except suite) metering equipment.
101871 | Base | Services (New and Upgrades) - Layouts – East North - Commercial Services | 0.013391 | 0.014239 | 0.015105 | 0.016031 | 0.017017 | 0.075783 | 94398.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151180 | Base | Central-North - Capitalization of Locates | 0 | 0 | 0.023974 | 0.024489 | 0.025016 | 0.073479 | 94387.49 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150600 | Base | Firmware Upgrades for Smart Meters - East | 0.034024 | 0.035002 | 0.023999 | 0.024675 | 0.025364 | 0.14306 | 94363.34 | System Access | Metering | Powerstream | Multi-year project to renew residential Smart meter firmware to improve communication performance.
151169 | Base | Central-South - Capitalization of Locates | 0.028719 | 0.029336 | 0.029967 | 0.030611 | 0.031269 | 0.1499 | 94344.62 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
151174 | Base | West Lines - Capitalization locates | 0.034463 | 0.035204 | 0.035961 | 0.036734 | 0.031269 | 0.17363 | 94319.23 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150631 | Base | Transformer Station Metering - Central North | 0.069175 | 0.051453 | 0.051958 | 0.052471 | 0.052993 | 0.27805 | 94245.75 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew wholesale metering equipment.
101696 | Base | Subdivision - North Underground Residential Distribution System Final Close out and Inspection. | 0.045289 | 0.046619 | 0.047975 | 0.049355 | 0.05076 | 0.24 | 94197.28 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
103381 | Base | East Lines - Capitalization locates | 0.059681 | 0.060361 | 0.061048 | 0.061743 | 0.062446 | 0.30528 | 94144.61 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101870 | Base | Services (New and Upgrades) - Layouts – East South - Commercial Services | 0.065617 | 0.069772 | 0.074015 | 0.078548 | 0.083384 | 0.37134 | 94022.15 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101869 | Base | Services (New and Upgrades) - Layouts – East North - New Residential | 0.06959 | 0.073996 | 0.078495 | 0.083304 | 0.088432 | 0.39382 | 93989.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150650 | Base | Replace PCB Risk PT's - Enersource RZ | 0.10064 | 0.10179 | 0.10295 | 0.10412 | 0.10531 | 0.51481 | 93977.25 | System Access | Metering | Enersource | Multi-year project to replace metering transformers identified with unacceptable levels of PCB's, to prevent hazardous spills.
101919 | Base | New Services (new and upgrades) - Commercial, Industrial and Institutional (ICI) Projects - NORTH | 0.074034 | 0.078559 | 0.083592 | 0.088729 | 0.093972 | 0.41889 | 93955.31 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150647 | Base | Transformer Station Metering - Enersource RZ | 0.06542 | 0.28611 | 0.14441 | 0.14692 | 0.052993 | 0.69585 | 93884.28 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew wholesale metering equipment.
151049 | Base | Commercial, Industrial, Institutional, Apartment Connections | 0.1236 | 0.12879 | 0.13419 | 0.13981 | 0.14568 | 0.67207 | 93829.96 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
101685 | Base | Subdivision - South Underground Residential Distribution System Final Close out and Inspection. | 0.10915 | 0.11238 | 0.11568 | 0.11903 | 0.12244 | 0.57869 | 93778.29 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150457 | Base | Services (New and Upgrades) - Layouts – St Catharines | 0.18711 | 0.19128 | 0.1945 | 0.20089 | 0.20424 | 0.97802 | 93519.09 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151162 | Base | Non Recoverable replacement of Distribution Equipment due to accident/vandalism | 0.24378 | 0.24902 | 0.25438 | 0.25985 | 0.26543 | 1.2725 | 93457.13 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101924 | Base | Mulit Unit Metering for New Buildings NORTH - PowerStream RZ | 0.14799 | 0.15716 | 0.1669 | 0.17724 | 0.18822 | 0.8375 | 93421.21 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in northern area of territory.
150588 | Base | New Residential Subdivision Development - Alectra West | 0.2579 | 0.26084 | 0.21105 | 0.23124 | 0.23387 | 1.1949 | 93265.82 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
101791 | Base | New Services - new and upgrades - COMMERCIAL, INDUSTRIAL, INSTITUTIONAL (ICI) SERVICES - SOUTH | 0.22252 | 0.2353 | 0.24859 | 0.26192 | 0.2859 | 1.2542 | 92878.02 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101812 | Base | Reactive Capital, Alectra East - LIS | 0.30621 | 0.29665 | 0.28737 | 0.27838 | 0.26966 | 1.4383 | 92710.01 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150754 | Base | Lines Central-North - Non-Recoverable Replacements | 0.34355 | 0.35094 | 0.35849 | 0.36619 | 0.37407 | 1.7932 | 92705.38 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150726 | Base | Lines Central-South - Non-Recoverable Replacements | 0.34355 | 0.35094 | 0.35849 | 0.36619 | 0.37407 | 1.7932 | 92705.38 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101820 | Base | Reactive Capital, Alectra East - Non-Recoverable Replacement | 0.28674 | 0.29595 | 0.30541 | 0.31512 | 0.32508 | 1.5283 | 92582.71 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150389 | Base | Services (New and Upgrades) - Layouts – Central North | 0.35059 | 0.37232 | 0.39537 | 0.41988 | 0.4459 | 1.9841 | 92563.35 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150651 | Base | C & I Metering - Renewal- Brampton RZ | 0.59145 | 0.090669 | 0.066045 | 0.64177 | 0.76749 | 2.1574 | 92560.77 | System Access | Metering | Brampton | Multi-year project to renew existing ICI metering equipment.
150386 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central North | 0.37582 | 0.39911 | 0.42384 | 0.4501 | 0.47799 | 2.1269 | 92424.37 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150453 | Base | CIS CC&B Modifications(Regulatory Enhancements) | 0.91073 | 0.87857 | 0.94882 | 0.9498 | 1.84 | 5.5279 | 92260.88 | General Plant | Information Technology | Multiple | Enhancements to the CIS (CC&B) application needed to meet any regulatory requirements Such requirements in the past have been Ontario Energy Savings Program (OESP) as well as the Monthly Billing projects.
150649 | Base | Suite Metering - Enersource RZ | 0.45016 | 0.45552 | 0.56469 | 0.57141 | 0.578 | 2.6198 | 91838.22 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew suite metering equipment.
150654 | Base | C & I Metering - New Services - Brampton RZ | 0.61006 | 0.53644 | 0.58376 | 0.58993 | 0.5967 | 2.9169 | 91552.85 | System Access | Metering | Brampton | Multi-year project to purchase and install ICI metering equipment on new services.
150595 | Base | C & I and Wholesale Metering - PowerStream RZ | 0.52637 | 0.53831 | 0.55172 | 0.56542 | 0.57816 | 2.76 | 91530.35 | System Access | Metering | Powerstream | Multi-year project to purchase, install, and renew ICI and wholesale metering equipment.
101868 | Base | Services (New and Upgrades) - Layouts – East South - New Residential | 0.41513 | 0.44142 | 0.46825 | 0.49694 | 0.52753 | 2.3493 | 91488.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101795 | Base | Multi Unit Metering for New Buildings SOUTH - PowerStream RZ | 0.44256 | 0.46998 | 0.4991 | 0.53002 | 0.56286 | 2.5045 | 91273.08 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in southern area of territory.
101873 | Base | Services (New and Upgrades) - Layouts – East North - Residential Upgrades | 0.48811 | 0.51902 | 0.55057 | 0.5843 | 0.62027 | 2.7623 | 91023.49 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151051 | Base | System Relocations Road Authorities | 1.0169 | 0.67475 | 0.68926 | 0.70408 | 0.71922 | 3.8042 | 91002.2 | System Access | Road Authority | Guelph | Mandatory - System Access Related Project
150652 | Base | New Residential Subdivision Development - Alectra Central South | 0.64729 | 0.98199 | 1.0759 | 0.50224 | 0.46563 | 3.6731 | 90948.17 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150388 | Base | Services (New and Upgrades) - Layouts – Central South | 0.67547 | 0.71733 | 0.76177 | 0.80897 | 0.85908 | 3.8226 | 90774.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150692 | Base | New Feeder in Residential Subdivision Development - Alectra Central North | 0.85968 | 0.76718 | 0.74488 | 0.74289 | 0.75664 | 3.8713 | 90609.19 | System Service | Capacity (Lines) | Brampton | This expenditure is required to meet the needs of the development community that construct municipal approved residential subdivisions in Alectra Utilities' Central North service territory
150599 | Base | Suite Meter - Reverification - PowerStream RZ | 0.87682 | 0.13206 | 0.12717 | 0.95673 | 0.52324 | 2.616 | 90368.15 | System Access | Metering | Powerstream | Multi-year project to renew Measurement Canada seal dates on existing suite metering equipment.
150455 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - St Catharines | 0.86575 | 0.86128 | 0.87937 | 0.8988 | 0.92173 | 4.4269 | 90201.14 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150659 | Base | Residential Meters - by Metering - Brampton RZ | 0.96979 | 0.87367 | 0.85775 | 0.88514 | 0.9131 | 4.4995 | 90095.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Metering.
150456 | Base | Services (New and Upgrades) - Layouts – Hamilton | 0.87181 | 0.88992 | 0.90833 | 0.926 | 0.94501 | 4.5411 | 89961.61 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150630 | Base | New Residential Subdivision Development - Alectra Central North | 0.687 | 0.713 | 1.099 | 1.25 | 1.187 | 4.936 | 89952.48 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101828 | Base | Reactive Capital, Alectra East - Recoverable Replacement | 0.69797 | 0.72254 | 0.74789 | 0.77405 | 0.80105 | 3.7435 | 89765.65 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover some costs for (i.e. pole hit, vehicle at scene of accicent, Alectra Utilities obtains most of costs (near $0 impact too budget))
101896 | Base | New Institutional/Commercial/Industrial Subdivision Development - Alectra East | 0.9099 | 0.92026 | 0.93074 | 0.94134 | 0.95206 | 4.6543 | 89347.36 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101872 | Base | Services (New and Upgrades) - Layouts – East South - Residential Upgrades | 0.72312 | 0.76892 | 0.81566 | 0.86564 | 0.91892 | 4.0923 | 89344.81 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101800 | Base | Reactive Capital, Alectra East - Storm Damage | 1.1509 | 1.1955 | 1.2418 | 1.2899 | 1.3398 | 6.218 | 86549 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151047 | Base | Subdivisions | 0.66674 | 0.73863 | 0.3556 | 0.45393 | 0.47565 | 2.6905 | 85393.33 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
150620 | Base | Metering Renewal - all types - Horizon RZ | 1.8909 | 1.9701 | 2.0522 | 2.139 | 2.2274 | 10.2796 | 84064.36 | System Access | Metering | Horizon | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment.
101808 | Base | Reactive Capital, Alectra East - Switchgears | 1.8047 | 1.7866 | 1.7686 | 1.7507 | 1.7331 | 8.8437 | 83304.08 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150648 | Base | Metering Renewal - all types but Suite - Enersource RZ | 2.2626 | 2.2887 | 2.3142 | 2.3405 | 2.3671 | 11.5731 | 82569.47 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew residential (except suite) and ICI metering equipment.
101892 | Base | New Subdivision Development - Secondary Service Lateral - Alectra East | 2.5667 | 2.6856 | 2.8058 | 2.9306 | 3.0613 | 14.0501 | 80775.74 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151125 | M-Factor | Connection Cost Recovery Agreement (CCRA) – Midhurst TS – 15th Anniversary True-up | 3.175 | 0 | 0 | 0 | 0 | 3.175 | 78171.93 | General Plant | Connection and Cost Recovery Agreements | Powerstream | In accordance with the Connection Cost Recovery Agreement, a 15-year true-up is required for Midhurst TS.
150384 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central South | 3.0125 | 3.1991 | 3.3973 | 3.6078 | 3.8313 | 17.0479 | 77903.71 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
151124 | M-Factor | Goreway TS Expansion (CCRA) - 10 Yr True-Up Payment, Brampton | 5.5626 | 0 | 0 | 0 | 0 | 5.5626 | 76025.7 | General Plant | Connection and Cost Recovery Agreements | Brampton | In accordance with the Connection Cost Recovery Agreement, a 10-year true-up is required for Goreway TS.
150449 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - Hamilton | 4.9871 | 5.0143 | 5.1748 | 5.3342 | 5.5039 | 26.0143 | 69328.05 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151095 | Base | Reactive Restoration | 1.0029 | 1.0239 | 1.0452 | 1.0671 | 1.0894 | 5.2285 | 63546.92 | System Renewal | Reactive Capital | Guelph | Replacement of assets which have failured and requires replacement in order to restore power to customers
151301 | Base | Cable Replacement Project - (HAM) - Rymal - Mud - Upper Centennial - Upper Red Hill Valley | 0 | 0 | 0 | 0 | 3.3122 | 3.3122 | 61747.15 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 8 failures, or 14 failures per 100km. This area includes the 331X & 341X feeders which were identified as a Worst Performing Feeder in 2018. The average cable installation year is 1968 in this project scope.
150465 | Base | LPSS Upgrade - IT Infrastructure | 0.50569 | 0 | 0 | 0 | 0 | 0.50569 | 59939.65 | General Plant | Information Technology | Multiple | Enhancement to LPSS Alectra market settlement system LPSS is the Alectra settlement system. This is one of the core applications of the organization, operational enhancements come in from a number of venues and thereby feedback into the other downstream systems. These enhancements are considered for the overall customer and organizational benefits.
101824 | Base | Reactive Capital, Alectra East - Distribution Equipment | 5.1994 | 5.3112 | 5.4254 | 5.542 | 5.6612 | 27.1393 | 58189.58 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151161 | Base | Joint Use Pole Removal | 0.11273 | 0.11515 | 0.11763 | 0.12016 | 0.12274 | 0.58841 | 57199.8 | System Renewal | Overhead Asset Renewal | Horizon | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
150463 | Base | Customer Self Service Portal Enhancements | 0.85968 | 0.25573 | 0 | 0 | 0 | 1.1154 | 56341.32 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) self service portal application to support process improvement requirements.The self service portal is the means by which Alecra customers can obtain their customer related information, interact with a CSR, post questions. The enhancements will allow Alectra customers a better experience when interacting with Alectra through the web portal channel.
151050 | Base | Metering - all types - Guelph RZ | 0.63655 | 0.40508 | 0.41379 | 0.42268 | 0.43177 | 2.3099 | 55986.2 | System Access | Metering | Guelph | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment in Guelph RZ.
150469 | Base | ERP JD Edwards Enhancements | 2.0301 | 1.0945 | 1.8321 | 1.8359 | 1.3588 | 8.1514 | 55714.6 | General Plant | Information Technology | Multiple | Allocation of capital funds to provide 3rd party assistance on capital work, along with creating system enhancements to the JD Edwards ERP and supporting Systems.
150325 | Base | CIS CC&B Enhancements | 1.2642 | 0.77863 | 0 | 1.3079 | 1.5874 | 4.9381 | 55520.48 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) application to support process improvement requirements.As the CIS (CC&B) system is one of the core applications of the organization, operational enhancements come in from a number of venues and thereby feedback into the other downstream systems. These enhancements are considered for the overall customer and organizational benefits.
103637 | Base | GS>50 MIST Meter Multi-year initiative Implementation | 0.58131 | 0 | 0 | 0 | 0 | 0.58131 | 55000.21 | System Access | Metering | Powerstream | Multi-year project to install MIST meters on GS>50 accounts, as required by the Distribution System Code.
101832 | Base | Joint Use Pole Removal | 0.55536 | 0.57187 | 0.58872 | 0.60592 | 0.62348 | 2.9453 | 54024.42 | System Renewal | Overhead Asset Renewal | Powerstream | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
100159 | M-Factor | Hydro One Asset Purchase - Alliston | 0 | 0 | 0.49814 | 0 | 0 | 0.49814 | 52600.71 | System Service | Capacity (Lines) | Powerstream | Purchase the 44 kV pole line along Industrial Parkway (approx 4.5 km's). The pole line is required for the new Alliston 10MVA substation 13.8kV integration (101571).
101570 | Base | New Alliston 10MVA Substation - 44 kV Supply | 0 | 0 | 0 | 0.01765 | 0.33896 | 0.35661 | 50412.78 | System Service | Capacity (Stations) | Powerstream | This project is the 44KV feeder extension to supply Alliston MS (101569)
101571 | Base | New Alliston 10MVA Substation - 13.8 kV Feeder Integration | 0 | 0 | 0 | 0.0353 | 0.63717 | 0.67247 | 50183.69 | System Service | Capacity (Stations) | Powerstream | This project is the 13.8KV feeder integration for Alliston MS (101569)
150344 | Base | HaLRT_New Lake Feeder for TPSS#8 area capacity | 0.57199 | 0 | 0 | 0 | 0 | 0.57199 | 48091.05 | System Service | Capacity (Lines) | Horizon | The TPSS#8 location has supply constraints on the 13.8kV system. This project is to bring a new feeder out of Lake TS to the area to reinforce the supply and allow for switching to free up capacity to accommodate the new load request.
151236 | Base | Edinburgh Rd (Paisley to Willow) Extension | 0.65969 | 0 | 0 | 0 | 0 | 0.65969 | 48010.63 | System Service | Capacity (Lines) | Guelph | Replace existing pole line to accommodate two 13.8kV circuits in order to provide capacity and contingency for the new developments on Edinburgh Road North and also act as an inter-tie between Campbell TS and Cedar TS
101887 | Base | New Residential Subdivision Development - Alectra East | 8.9703 | 9.4493 | 10.1819 | 10.9856 | 11.3994 | 50.9865 | 44863.95 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101569 | M-Factor | New Alliston 10MVA Substation - Industrial Parkway | 0 | 0 | 0 | 0.84023 | 1.0623 | 1.9025 | 44829.96 | System Service | Capacity (Stations) | Powerstream | The project entails the purchase of a station site in the vicinity of Dufferin St and Industrial Pkwy in Alliston, and constructing a new 10MVA, 44/13.8 kV, dual-stage fan, 4-feeder municipal substation
100859 | Base | Switchgear Renewal - East | 2.5779 | 2.692 | 2.8111 | 2.9356 | 3.0655 | 14.082 | 43704.68 | System Renewal | Underground Asset Renewal | Powerstream | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151117 | M-Factor | Vansickle TS True-up Payment (CCRA), St.Catharines | 0 | 1.5808 | 0 | 0 | 0 | 1.5808 | 43572.72 | General Plant | Connection and Cost Recovery Agreements | Horizon | In accordance with the Connection Cost Recovery Agreement, a 10 year true-up is required for Vansickle TS.
151089 | Base | Overhead Rebuilds | 1.1898 | 1.2154 | 1.2415 | 1.2682 | 1.2955 | 6.2104 | 39246.49 | System Renewal | Overhead Asset Renewal | Guelph | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
150471 | Base | ERP JD Edwards Hardware Upgrades | 0 | 0 | 0.55348 | 0 | 0 | 0.55348 | 38645.83 | General Plant | Information Technology | Multiple | Hardware upgrade to support ERP refresh cycle.
151241 | M-Factor | Arlen MTS - New Feeder | 0 | 0 | 0 | 0.45 | 0 | 0.45 | 37816.52 | System Service | Capacity (Lines) | Guelph | New Distribution feeder from Arlen MTS to support the load growth in the south Guelph and to meet continengency requirement.
150369 | M-Factor | New build - 44kV Feeder Extension York/Meadowpine, Mississauga | 0 | 1.776 | 0 | 0 | 0 | 1.776 | 37794.94 | System Service | Capacity (Lines) | Enersource | There is no 44KV circuit on Meadowpine Blvd. and it is expected that the large customers will be connecting to the 44KV circuit. In addition 16MVA of connected load is on radial supply. This project will address the capacity constraints as well as eliminatethe current radial supply configuration for 16MVA of load.
151118 | M-Factor | Nebo TS 27.6kV True-up Payment (CCRA) | 0 | 0 | 0 | 0.54985 | 0 | 0.54985 | 37750.31 | General Plant | Connection and Cost Recovery Agreements | Horizon | In accordance with the Connection Cost Recovery Agreement, a 10 year true-up is required for Nebo TS.
101508 | Base | Transformer Renewal - East | 2.1632 | 2.5337 | 2.9346 | 3.0752 | 3.2223 | 13.929 | 37474.31 | System Renewal | Transformer Renewal | Powerstream | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
101003 | M-Factor | Richmond Hill TS#2 Upgrade Bus, Line & Transformer Protections | 0.14822 | 0 | 0 | 0 | 0 | 0.14822 | 36019.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project entails upgrade of Bus, Line and Transformer Protection relays at Richmond Hill TS#2 (Lazenby TS#2) with new relays having fault recording capabilities. This project will also address the communications protocol at this station whihch is obsolete and is incompatible with that of the rest of the system.
150673 | Base | Road Authority Central (Mississauga) | 3.7168 | 3.9471 | 4.1917 | 4.4514 | 4.7271 | 21.0342 | 35000.51 | System Access | Road Authority | Enersource | Mandatory - System Access Related Project
150134 | Base | Cable Injection Project - (V37) - Langstaff and Weston, Vaughan | 1.5389 | 1.6043 | 1.671 | 0 | 0 | 4.8143 | 34877.34 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 20 failures.
151240 | M-Factor | Southgate Dr to Maltby Rd O/H Extension | 0 | 0 | 0 | 0 | 0.55781 | 0.55781 | 34668.47 | System Service | Capacity (Lines) | Guelph | The road extension from COG and potential developments on Southgate requires two 13.8kV circuit expanded in order to provide capacity and contingency supply.
102387 | M-Factor | Install 44kV & 13.8kV Bryne Drive | 0 | 1.0617 | 0 | 0 | 0 | 1.0617 | 34653.9 | System Service | Capacity (Lines) | Powerstream | The City of Barrie has identified 64 acres north of Harvie Road along Bryne Drive for development of industrial/commercial/residential. Another 34 acres south of Harvie Road along Bryne Drive has been identified for industrial/commercial development. The developable areas will result in 4MVA of new load north of Harvie Road and 2.2MVA of load south of Harvie Road. There is currently no existing 44kV or 13.8kV supply along Bryne Drive between P6231 and SC13487.
151238 | Base | New Feeder Maltby Rd W (Crawley to Gordon) | 0 | 0 | 0 | 0 | 0.89685 | 0.89685 | 34423.41 | System Service | Capacity (Lines) | Guelph | Build new pole line on Maltby Rd between Crawley Rd and Gordon St to back-up radially fed loads on Gordon St south of Clair Rd/Gordon St intersection with 556ASC OH Conductor to replace 3/0ACSR to act a feeder inter-tie.
150073 | M-Factor | Vaughan TS#1 Bus Differential & Overcurrent Protections Upgrades | 0 | 0 | 0.29034 | 0.15265 | 0 | 0.44299 | 34014.15 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Vaughan TS#1 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
150405 | Base | 25M9 Jim Yarrow TS Extensions | 0.32599 | 0.32091 | 0 | 0 | 0 | 0.6469 | 33741.34 | System Service | Capacity (Lines) | Brampton | Jim Yarrow TS extension with new underground line extending 25M9 from Winston Churchill Blvd utility corridor to Steeles Ave in order to back up 25M8 & 25M10 to accomodate future load growth in Churchill Business Community Park and residential developments between Steeles Ave & Embleton Rd
150645 | Base | Road Authority Central (Brampton) | 4.4046 | 4.6775 | 4.9673 | 5.275 | 5.6018 | 24.9262 | 31813.54 | System Access | Road Authority | Brampton | Mandatory - System Access Related Project
150828 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-West | 0.905 | 0.915 | 0.925 | 0.935 | 0.95 | 4.63 | 31592.28 | System Renewal | Overhead Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151452 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-West | 0.895 | 0.915 | 0.925 | 0.945 | 0.955 | 4.635 | 31590.16 | System Renewal | Underground Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
101762 | Base | Road Authority Expenditure PS South | 4.0206 | 4.091 | 4.1233 | 4.1217 | 4.2653 | 20.6219 | 31544.34 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
101355 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-East | 0.935 | 0.945 | 0.955 | 0.965 | 0.975 | 4.775 | 31424.67 | System Renewal | Overhead Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151450 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-East | 0.935 | 0.945 | 0.955 | 0.965 | 0.975 | 4.775 | 31424.67 | System Renewal | Underground Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
103633 | M-Factor | Install Two 27.6kV Ccts on 16th Ave from Hwy 404 to Woodbine Ave | 0 | 5.5273 | 0 | 0 | 0 | 5.5273 | 30531 | System Service | Capacity (Lines) | Powerstream | This project is to reroute two 27.6kV feeders along 16th Ave from Woodbine Ave in Markham to Leslie St Richmond Hill to supply new load in Richmond Hill. The customers on Leslie St north of 16th Ave in Richmond Hill are supplied by feeder 12M5, 12M7, and 12M12. There is only 290A or 14 MVA capacity left on these feeders for future development.
150074 | M-Factor | Vaughan TS#2 Bus Differential and Overcurrent Protections Upgrade | 0 | 0 | 0 | 0 | 0.31236 | 0.31236 | 28627.81 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Vaughan TS#2 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
100340 | M-Factor | Vaughan TS#4 Feeder Integration - Part 3 | 0 | 0 | 0 | 5.2023 | 3.5854 | 8.7877 | 28489.24 | System Service | Capacity (Lines) | Powerstream | This project is the third part of a multi-part project to construct and integrate new feeders from VTS#4. This project is to integrate four 27.6kV feeders (25M5/25M6/25M7/25M8) from VTS4 to the distribution system.
151363 | Base | Cable Injection Project - (M25) - 14th - McCowan - Steeles - Old Kennedy, Markham | 0 | 0.819 | 0.819 | 0.819 | 1.6214 | 4.0784 | 27518.58 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 14 failures.
150072 | M-Factor | Markham TS#3 Bus Differential & Overcurrent Protections Upgrades | 0.2336 | 0.11369 | 0 | 0 | 0 | 0.34729 | 27028.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Markham TS#3 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
150364 | M-Factor | New build - Port Credit Village East (Marina) 27.6kV Feeders, Mississauga | 0 | 0 | 4.4396 | 0 | 0 | 4.4396 | 25989.14 | System Service | Capacity (Lines) | Enersource | The Port Credit East development requires a 27.6kV circuit expansion in order to provide capacity and contingency for the Mid-rise mixed residential/commercial development.
100867 | Base | Pole Renewal - East | 4.3557 | 5.0405 | 5.2696 | 5.5081 | 5.7564 | 25.9302 | 25595.06 | System Renewal | Overhead Asset Renewal | Powerstream | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
151074 | Base | Reactive renewal | 3.2047 | 3.2736 | 3.3439 | 3.4158 | 3.4893 | 16.7273 | 25136.12 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have failured and requires replacement in order to restore power to customers
150571 | Base | Cable Injection Project - (J3-K3-N2-O2), Brampton | 2.2957 | 0 | 0 | 0 | 0 | 2.2957 | 24483.9 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 32 outages due to cable failures from 2007 to 2018 with average duration of 104 minutes.
151362 | Base | Cable Injection Project - (M39) - 16th - Warden - Hwy 7 - Woodbine, Markham | 0 | 0.74784 | 1.2602 | 1.26 | 0.92758 | 4.1957 | 23713.55 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 8 failures.
151360 | Base | Cable Injection Project - (M31) - 14th - Old Kennedy - Steeles - Warden, Markham | 0 | 0.84754 | 0.84754 | 0.84754 | 0.84754 | 3.3902 | 23640.66 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 38 failures.
150070 | M-Factor | Markham TS#1 Bus Differential & Overcurrent Protections Upgrades | 0 | 0.24074 | 0.11644 | 0 | 0 | 0.35719 | 22499.7 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Markham TS#1 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
150375 | Base | New Build - 136M10 Goreway TS Extensions, Brampton | 1.5725 | 0 | 0 | 0 | 0 | 1.5725 | 22413.42 | System Service | Capacity (Lines) | Brampton | The 136M10 feeder egress project will install a new feeder from the Goreway TS to provide relief to the 136M44 circuit which is over the planning limit
100015 | Base | Transformer Temperature Monitoring - Aurora MS, King & Concord | 0.14953 | 0 | 0 | 0 | 0 | 0.14953 | 22039.57 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consist of transformer temperature monitoring and telemetry at Aurora MS - King and Concord which will improve system reliability and enables controlled emergency loading beyond the nameplate rating.
151043 | Base | Transformer Renewal - Central South | 1.8571 | 1.897 | 1.9378 | 1.9795 | 2.022 | 9.6934 | 21869.73 | System Renewal | Transformer Renewal | Enersource | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
102545 | Base | Install a New 27.6kV Pole Line on 19th Ave from Leslie St to Woodbine Ave | 1.3732 | 0 | 0 | 0 | 0 | 1.3732 | 21589.69 | System Service | Capacity (Lines) | Powerstream | This is to remediate radial supply on Leslie St north of Elgin Mills Rd (supplying Leslie North development in Richmond Hill) and radial supply on Woodbine Ave north of Elgin Mills Rd (supplying future urban area in Markham).
150467 | M-Factor | CIS CC&B upgrade | 0 | 6.5458 | 6.7766 | 0 | 0 | 13.3224 | 21391.8 | General Plant | Information Technology | Multiple | Aligns with Alectra customer experience plan requirements and enhanced services and emerging channels. Comprised of third party integration support, hardware, resources, testing to support existing Alectra platform as the current version 2.5 support ends in 2022. Project ensures enhanced functionality, compatibility with ancillary systems, security upgrades, automation and rate billing engine to support future utility DER integration.
150071 | M-Factor | Markham TS#2 Bus Differential & Overcurrent Protections Upgrades | 0 | 0 | 0 | 0.25925 | 0.082435 | 0.34169 | 21087.3 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Markham TS#2 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
101480 | M-Factor | Build double ccts 27.6kV pole line on 19th Ave between Leslie St and Bayview Ave | 0 | 0 | 1.2926 | 0 | 0 | 1.2926 | 20986.73 | System Service | Capacity (Lines) | Powerstream | This project is to build 2 ccts pole line on 19th Ave from Leslie St to Bayview Ave to supply the new subdivision in Leslie North that is bounded by Elgin Mills Rd., Leslie St., 19th Avenue and Bayview Avenue. There will be new houses along 19th Ave between Bayview Ave and Leslie St as the subdivision secondary plan, however, there is no pole line now.
150688 | Base | Station Sustainment & Protection & Control CASCADE Expansion | 0.054109 | 0.04378 | 0 | 0 | 0 | 0.097889 | 20717.32 | General Plant | Information Technology | Multiple | Expand the use of the CASCADE system to be used by the Protection and Control asset in addition to the Station assets
101593 | Base | Station Ground Grid Refurbishments | 0.11569 | 0 | 0 | 0 | 0 | 0.11569 | 20602.33 | System Service | Safety & Security | Powerstream | This project consists of refurbishment of station ground grid in East. The project would be to design and implement ground grid improvements to meet step and touch potential requirements.
150371 | M-Factor | New build - 27.6kV Feeder Extension Traders, Mississauga | 0 | 2.7518 | 2.7822 | 0 | 0 | 5.5339 | 19791.79 | System Service | Capacity (Lines) | Enersource | Install new feeders in the Traders area between Hurontario St and Kennedy Rd from Matheson Blvd to Britannia Rd required to meet demand due to intensification and to ensure the reliability of current customers.
151303 | Base | Cable Replacement Project - (HAM) - Stone Church - Garth - Lincoln M. Alexander | 0 | 0 | 2.4283 | 3.2043 | 0.94333 | 6.5759 | 19664.79 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 5 failures, or 18 failures per 100km. The average cable installation year is 1976 in this project scope.
150664 | Base | Residential Meters - by Lines - Brampton RZ | 0.68567 | 0.65495 | 0.64049 | 0.63608 | 1.3894 | 4.0066 | 18166.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Lines.
151109 | Base | Switch Replacement | 0.17128 | 0.17496 | 0.17872 | 0.18257 | 0.18649 | 0.89403 | 18145.07 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
102455 | Base | Melbourne MS322 Land Purchase & TX Upgrade - Bradford | 0 | 0 | 0 | 0.43692 | 0.91603 | 1.353 | 17823.71 | System Service | Capacity (Stations) | Powerstream | This project consists of transformer upgrade to increase the capacity at Melbourne MS to meet the load growth the contingency condition for Bradford area.
151367 | Base | Cable Injection Project - (M21) - Hwy 7 - Markham - 16th - McCowan, Markham | 0 | 0 | 0 | 1.0575 | 1.7718 | 2.8293 | 17674.76 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 6 failures.
150319 | M-Factor | New MS - Duke MS 20 MVA Substation, Mississauga | 0 | 0 | 0 | 1.9528 | 4.2 | 6.1528 | 17540.57 | System Service | Capacity (Stations) | Enersource | The Downtown21 plan forecasts a total population of 56,565 residents and 34,247 jobs in the Mississauga downtown core. The current capacity available for the downtown core is approximately 140 MVA ONAN rating. Based on growth projected and the land parcels available, Alectra Utilities estimates that, upon completion of Downtown21 the combined transformation load requirement will increase approximately by 300 MVA. This station will provide 20MVA ONAN capacity.
150458 | Base | MAS upgrade - IT Infrastructure | 0.080911 | 0.051145 | 0.10345 | 0 | 0 | 0.23551 | 17425.57 | General Plant | Information Technology | Multiple | Metering Automation System for smart grid Upgrade to be implemented in a phased approach over the next 4 years as smart grid continues to evolve work in conjunction with the metering team to analyze and implement leverage new technologies to provide better more accurate meter readings be responsive to the issues first not reactive when a customer calls
151104 | Base | Distribution Automation - Central North | 0.44566 | 0.46513 | 0.48499 | 0.50504 | 0.52588 | 2.4267 | 17389.16 | System Service | SCADA and Automation | Brampton | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151366 | Base | Cable Injection Project - (M19) - Markham - Steeles - McCowan - 14th, Markham | 0 | 0 | 0 | 1.3532 | 1.3532 | 2.7065 | 17258.97 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 7 failures.
102352 | Base | Vaughan TS#4 Feeder Integration - Part 2 | 3.9784 | 0 | 0 | 0 | 0 | 3.9784 | 16373.29 | System Service | Capacity (Lines) | Powerstream | This project is the second part of VTS4 feeder integration plan. The purposes is to integrate two new 27.6kV feeders (25M9 to 25M10) from VTS4 into Alectra's distribution system to increase distribution capacity by 40 MVA, off load existing feeders and stations with the new feeders and increase supply capacity to Vaughan West.
151318 | Base | Cable Injection Project - (I3) -Bovaird - Dixie - Queen - Hwy 410, Brampton | 0.51681 | 0.42438 | 0.26269 | 0.57763 | 0.467 | 2.2485 | 16118.68 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2014 to 2015 with average duration of 71 minutes.
151046 | Base | Addiscott Court Security Fence Improvement | 0.303 | 0 | 0 | 0 | 0 | 0.303 | 16096.97 | General Plant | Facilities Management | Powerstream | To improve the fencing to secure the capital inventory within the operational yard in Markham
151216 | Base | Purchase & Installation of Station DC System Monitoring - South West | 0 | 0.02 | 0 | 0 | 0 | 0.02 | 15958.11 | System Renewal | Substation Renewal | Guelph | This project involves the installation of real-time monitoring at Arlen TS in the South West Operating Area (Guelph) that eliminates required on-site maintenance activities such as routine manual battery testing. By the addition of DC System monitoring, it will ensure that any potential problems will be immediately reported via SCADA/PI System Notification and help to avoid a station outage due to DC system failure as occurred at Vaughan TS#3. It will also reduce the human interaction with the dangerous DC Equipment and dramatically reduce the hazard/risk to the worker by eliminating the need to perform battery testing.
150639 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-CENTRAL | 0.037721 | 0.038252 | 0.038785 | 0.039321 | 0.03986 | 0.19394 | 15735.56 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of DC charging system for Central South Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150638 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-East | 0.037721 | 0.038252 | 0.038785 | 0.039321 | 0.03986 | 0.19394 | 15735.56 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of DC charging system for Central North Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150636 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-North & TS | 0.037721 | 0.038252 | 0.038785 | 0.039321 | 0.03986 | 0.19394 | 15735.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of DC charging system for East Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150640 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-WEST | 0.037721 | 0.038252 | 0.038785 | 0.039321 | 0.03986 | 0.19394 | 15735.56 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of DC charging system for West Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
151460 | M-Factor | Cable Injection Project - (V17) - Langstaff - Keele - Rutherford - Dufferin, Vaughan | 0 | 0 | 0.62198 | 0.56259 | 1.663 | 2.8476 | 15316.59 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 3 failures. From 2015-2019 YTD customers in this area experienced 4 failures.
150749 | M-Factor | New WiMAX Communication Network - Central South | 0.41446 | 0 | 0 | 0 | 0 | 0.41446 | 15089.12 | System Service | System Control, Comm'ns & Performance | Enersource | This project is required to implement the WiMax Network for Central South for secure data transfer of monitoring sensors.
100337 | M-Factor | Markham TS #4 Feeder Egress Part 3 | 0 | 0 | 0 | 4.9176 | 0 | 4.9176 | 14794.76 | System Service | Capacity (Lines) | Powerstream | This project is to install four 27.6kV feeders from MTS4 along Rodick Rd to 14th Ave. These feeders will be connected to existing feeders on 14th Ave and Miller Ave. It is MTS4 Feeder Integration Plan Part 3. This project will increase supply capacity by 80 MVA to support growth and development in Markham
150285 | Base | Transformer Renewal - Central North | 0.581 | 0.79864 | 1.0293 | 1.2737 | 1.4595 | 5.1421 | 14492.05 | System Renewal | Transformer Renewal | Brampton | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150025 | Base | Cable Injection Project - (V18) - Major Mackenzie and Keele, Vaughan | 1.1127 | 0 | 0 | 0 | 0 | 1.1127 | 14485.46 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2017 customers in this area experienced 2 failures.
150559 | Base | Rathburn Rd Duct Extension (LRT Betterment) | 0.35399 | 0 | 0 | 0 | 0 | 0.35399 | 14447.96 | System Service | Capacity (Lines) | Enersource | A duct installation to connect existing ducts west and east on Rathburn Rd. A 5 year moratorium is proposed due to streetscaping and this project should be completed with other work.
101027 | Base | Switch Renewal - East | 0.63034 | 0.6543 | 0.68016 | 0.70579 | 0.73228 | 3.4029 | 14308.5 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
150505 | Base | Purchase and Install 11 Self Recharging Transformer Air Breathers - TS and MS - Multi-year initiative - EAST | 0.025232 | 0 | 0 | 0 | 0 | 0.025232 | 14276.73 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of transformer air breather at TS and MS stations in West. Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
100913 | M-Factor | Pole Line Installation Double Cct on Major Mack - Huntington Rd to Hwy 50 | 0 | 0 | 0 | 0 | 1.4394 | 1.4394 | 14222.63 | System Service | Capacity (Lines) | Powerstream | This project is to build two ccts on Major Mack Dr between Huntington Rd and Hwy 50 in conjunction with the road widening project to supply new customers on both side of Major Mack, as well as customers along Hwy 50.
102062 | Base | Purchase & Installation of 10 Self Recharging Transformer Air Breathers on TS transformers-Multi-year initiative-North & TS | 0.109 | 0 | 0 | 0 | 0 | 0.109 | 14210.75 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of transformer air breather at TS and MS stations in East. Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
150506 | Base | Purchase and Installation of 15 Self Recharging Transformer Air Breathers on MS Transformers - Multi-year initiative-CENTRAL | 0.13872 | 0 | 0 | 0 | 0 | 0.13872 | 14154.95 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of transformer air breather at TS and MS stations in Central South. Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
150504 | Base | Purchase and Installation of 10 Self Recharging Transformer Air Breathers on TS and MS Transformers - Multi-year initiative-WEST | 0.096386 | 0.097603 | 0.05495 | 0 | 0 | 0.24894 | 14105.38 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of transformer air breather at TS and MS stations in East .Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
151066 | Base | Cable Replacement Project - Hamilton Mountain URD | 3.8379 | 0 | 0 | 0 | 0 | 3.8379 | 14039.84 | System Renewal | Underground Asset Renewal | Horizon | Recent underground cable failures in this area are unknown at this time. The average cable installation year is 1971 in this project scope. The cables are 23 years over the TUL.
102098 | Base | Client - IT Infrastructure | 1.0742 | 1.2101 | 1.2313 | 1.3485 | 0.56951 | 5.4336 | 13761.18 | General Plant | Information Technology | Multiple | To upgrade desktop/laptop/mobile devices that are 5 years or older (Approximately 20% of our equipment). Net new equipment for mobile computing as well as upgrades and replacements for damaged devices. Request made by various business units. This budget also includes RSA tokens\Licenses, monitors, mice, keyboards, docking stations, tablets and small non-MFP printers. Out of Scope: Large MFP Printers
150014 | Base | Cable Injection Project - (V01) - Yonge - Steeles - Bathurst - Center, Vaughan | 0.84264 | 0 | 0 | 0 | 0 | 0.84264 | 13574.23 | System Renewal | Underground Asset Renewal | Powerstream | From 2014-2016 customers in this area experienced 13 failures.
151214 | Base | Purchase & Install Self Re-Charging Transformer Air Breathers | 0 | 0.04 | 0 | 0 | 0 | 0.04 | 13524.34 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of installation of transformer air breather at TS and MS stations in Guelph. Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
151247 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.575 | 0.585 | 0.595 | 0.605 | 0.685 | 3.045 | 13413.53 | System Renewal | Overhead Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102232 | Base | Capital Funds for Emergency P&C Purchases - East | 0.032466 | 0.032835 | 0.033209 | 0.033587 | 0.033969 | 0.16607 | 13270.97 | System Renewal | Substation Renewal | Powerstream | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the East Operating Area (former PowerStream). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150683 | Base | Capital Funds for Emergency P&C Purchases - Central North | 0.032466 | 0.032835 | 0.033209 | 0.033587 | 0.033969 | 0.16607 | 13184.55 | System Renewal | Substation Renewal | Brampton | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central North Operating Area (Brampton). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150685 | Base | Capital Funds for Emergency P&C Purchases - West | 0.032466 | 0.032835 | 0.033209 | 0.033587 | 0.033969 | 0.16607 | 13184.55 | System Renewal | Substation Renewal | Horizon | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the West Operating Area (former Horizon). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150684 | Base | Capital Funds for Emergency P&C Purchases - Central South | 0.032466 | 0.032835 | 0.033209 | 0.033587 | 0.033969 | 0.16607 | 13184.55 | System Renewal | Substation Renewal | Enersource | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central South Operating Area (former Mississauga). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150360 | M-Factor | New build - Extend 44kV feeder Centre View Dr, Mississauga | 0 | 0 | 0 | 0.88546 | 5.5933 | 6.4788 | 13005.45 | System Service | Capacity (Lines) | Enersource | A new 44 kV overhead/underground feeder extension is needed to provide supply to downtown Mississauga area on Centre View Drive as well as provide primary supply for Duke Municipal Station (MS).
150784 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.675 | 0.685 | 0.695 | 0.705 | 0.755 | 3.515 | 12968.3 | System Renewal | Overhead Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151453 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.61628 | 0.63824 | 0.74382 | 0.755 | 0.78605 | 3.5394 | 12922.02 | System Renewal | Underground Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
150823 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.725 | 0.735 | 0.745 | 0.785 | 0.85 | 3.84 | 12654.97 | System Renewal | Overhead Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102099 | Base | Printer & Copier Fleet Replacement | 0.040455 | 0.040916 | 0.033209 | 0.083706 | 0.049451 | 0.24774 | 12636.08 | General Plant | Information Technology | Multiple | Replacement of existing fleet of printers/copiers that are 5 or more years old. This will include non-MFP printers. Replacement to be determined by an evaluation of evolving needs and corporate requirements as well as age of equipment.
151449 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.795 | 0.855 | 0.885 | 0.905 | 0.915 | 4.355 | 12175.67 | System Renewal | Underground Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
103211 | Base | Misc Software Upgrades (FormScape, AutoCAD, etc.) - IT/OT Infrastructure | 0.12297 | 0.016711 | 0.076823 | 0.020151 | 0.02038 | 0.25703 | 12020.93 | General Plant | Information Technology | Multiple | Upgrade/ acquire software as required / requested by business.
151451 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.825 | 0.885 | 0.905 | 0.935 | 0.95 | 4.5 | 11935.99 | System Renewal | Underground Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151233 | M-Factor | New Construction - Campbell TS 36M63 Feeder PHASE 1 & 2, Guelph | 0 | 1.1528 | 1.1869 | 0 | 0 | 2.3397 | 11851.33 | System Service | Capacity (Lines) | Guelph | This project identifies a new 13.8kV feeder required from Campbell TS to bring additional load support to NW section of the city as the existing 13.8kV feeders in the area are unable to accommodate the additional load growth
150007 | Base | Extend 153M10 to Transfer MS322 | 1.6897 | 0 | 0 | 0 | 0 | 1.6897 | 11505.19 | System Service | Capacity (Lines) | Powerstream | This project consists of extenstion of 153M10 to transfer MS322. Back-up capability lines project extending the 153M10 circuit along Holland Street from Bridge Street , south along Morris Road, west along Centre Street to Thomas Street, north on Drury Street, west along Holland Street to Miller Park Avenue (approximately 2 km's)
150579 | Base | New build - Extend Bunting M81 Feeder, St.Catharines | 1.5146 | 1.5461 | 0 | 0 | 0 | 3.0606 | 11461.01 | System Service | Capacity (Lines) | Horizon | This project is to extend M81 feeder to supply new development and meet contigency condition in St. Catharines. This project will deal with ongoing capacity constraints in the North end of St.Catharines by bringing available supply from Bunting and Carlton TS's
103180 | Base | Citrix Xen Virtualization Expansion - IT Infrastructure | 0.050569 | 0.051145 | 0.051727 | 0.3139 | 0.21165 | 0.67899 | 11298.77 | General Plant | Information Technology | Multiple | Client computing virtualization (Citrix) is currently the standard delivery method for applications and desktops at Alectra. This system has had a tremendous uptake in the organization and requires an upgrade in back-end infrastructure to support the additional demand from the business.
150693 | M-Factor | Blockchain | 0.34691 | 0.35392 | 0.57314 | 0.57967 | 0.58627 | 2.4399 | 11191.63 | System Service | Distributed Energy Resources (DER) | Multiple | The project will prepare Alectra Utilities to engage with customers in a real-time and transparent process to record the flow of electricity to and from DERs, enabling the efficient procurement of distribution benefits, such as demand response and frequency regulation. The project will provide a robust settlement mechanism between Alectra and customers, backed by timely and efficient financial transactions, to enable overall trust and customer value delivery and leading to increased customer satisfaction.
151302 | Base | Cable Injection Project - (HAM) - Rymal - Mud - Upper Centennial - Upper Red Hill Valley | 0.64706 | 0.8583 | 0.54449 | 0 | 0 | 2.0498 | 11132.21 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 8 failures, or 14 failures per 100km. This area includes the 331X & 341X feeders which were identified as a Worst Performing Feeder in 2018. The average cable installation year is 1989 in this project scope.
151314 | Base | Cable Injection Project - (G2) -Wanless - Kennedy - Bovaird - Main, Brampton | 0 | 0.3125 | 0.21875 | 0.3125 | 0.68887 | 1.5326 | 11045.83 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2013 to 2017 with average duration of 125 minutes.
151409 | Base | Cable Replacement Project- Central Parkway & Bloor (29), Mississauga | 0 | 0 | 10.8851 | 0 | 0 | 10.8851 | 10937.44 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there are 9 outages, the length is 12,462 m, and the average cable age is 48 years old. There are 35 backlot transformers that we are also replacing.
150740 | Base | Facilities_Nebo_ Roof Replacement | 0 | 0 | 0.009 | 0 | 0 | 0.009 | 10932.65 | General Plant | Facilities Management | Horizon | 2019 Project and to be completed by Dec 2019. Not sure why we have $9K in 2022.
150342 | M-Factor | HaLRT_New Stirton Feeder for TPSS#4 and 8852X load shedding, Hamilton | 4.8476 | 0 | 0 | 0 | 0 | 4.8476 | 10906.89 | System Service | Capacity (Lines) | Horizon | The 8852X is the only 13.8kV feeder in the vicinity of the HaLRT TPSS#4 location and is at its utilization limit. To accommodate the new TPSS a new feeder from Stirton is to be built, and part of the 8852X load will also be transferred to this new feeder
150665 | Base | Emerging Customer Initiated Work (West) | 1.4515 | 1.5414 | 1.6369 | 1.7383 | 1.846 | 8.2142 | 10905.1 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151465 | M-Factor | Cable Replacement - Mississauga Left Behind Cable | 0 | 0.37682 | 0 | 0.55777 | 1.7918 | 2.7264 | 10856.69 | System Renewal | Underground Asset Renewal | Enersource | This project is to address cables which were part of a cable injection project but were ultimately not injectable at the time of project execution. These 'left behind' segments must be addressed, if they are left in the system they could cause a failure. Customers would not only experience an outage, but question the utilities work practices as we would have addressed only a portion of the cables instead of all the cables which could cause an outage.
101562 | Base | Arc Flash Mitigation Projects | 0.041677 | 0.042995 | 0.044349 | 0.045741 | 0.047172 | 0.22193 | 10618.95 | System Service | Safety & Security | Powerstream | This project is to mitigate arc flash risk at East stations.
151307 | Base | Cable Injection Project - (HAM) - Upper Sherman - Stone Church - Nebo - Rymal | 0 | 0 | 0 | 0.28409 | 0.74786 | 1.032 | 10594.98 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 2 failures, or 5 failures per 100km. The average cable installation year is 1989 in this project scope.
151429 | Base | Cable Injection- 003- AREA36 -Matheson & Kennedy, Mississauga | 0 | 0 | 0 | 0 | 1.2528 | 1.2528 | 10394.6 | System Renewal | Underground Asset Renewal | Enersource | There are 2 outages, we are injecting a total of 14,907 m of cable for this project, and the average age of the cable is 31 years.
151299 | Base | Cable Replacement Project - (HAM) - Millen - Barton - Fruitland | 0 | 1.0793 | 1.6195 | 1.3457 | 0 | 4.0444 | 10341.62 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 16 failures, or 44 failures per 100km. The average cable installation year is 1970 in this project scope.
150653 | Base | Road Authority West (St. Catharines) | 0.77414 | 0.86125 | 0.95816 | 1.066 | 1.1859 | 4.8455 | 10216.94 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
150615 | Base | Metering Tools & Equipment - Central North | 0.037876 | 0.038308 | 0.038744 | 0.039185 | 0.039631 | 0.19374 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150616 | Base | Metering Tools & Equipment - Central South | 0.037876 | 0.038308 | 0.038744 | 0.039185 | 0.039631 | 0.19374 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150613 | Base | Metering Tools & Equipment - East | 0.037876 | 0.038308 | 0.038744 | 0.039185 | 0.039631 | 0.19374 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150614 | Base | Metering Tools & Equipment - West | 0.037876 | 0.038308 | 0.038744 | 0.039185 | 0.039631 | 0.19374 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
151402 | Base | Cable Replacement Project- Montevideo & Treviso (19a), Mississauga | 0 | 5.1828 | 0 | 0 | 0 | 5.1828 | 9918.05 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 10 outages, the length is 14,151 m, and the average cable age is 34 years old.
102263 | M-Factor | Work Force Management / Mobile Dispatch | 0 | 0 | 2.35 | 2.35 | 0 | 4.7 | 9761.78 | General Plant | Information Technology | Multiple | Enterprise wide field crew management system that will enable more efficient use of crews and improve visibility to job progress enabling better communication of expectations to customers
151315 | Base | Cable Injection Project - (G5) - Steeles - Kennedy - Hwy 407 - Main, Brampton | 0 | 0 | 0 | 0 | 1.5577 | 1.5577 | 9694.62 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 7 outages due to cable failures from 2010 to 2019 with average duration of 109 minutes.
151439 | Base | 2020 GUELPH - Remotely Controlled Switches | 0.36711 | 0 | 0 | 0 | 0 | 0.36711 | 9307.37 | System Service | SCADA and Automation | Guelph | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151456 | M-Factor | Cable Injection Project - (V50) - Hwy 7 - Kipling - Steeles - Hwy 27, Vaughan | 0 | 0.93454 | 0.37819 | 0.18416 | 0 | 1.4969 | 9187.5 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 3 failures in 2018.
150261 | Base | Cable Injection Project - (V38) - Rutherford and Weston, Vaughan | 1.4139 | 0 | 0 | 0 | 0 | 1.4139 | 9110.1 | System Renewal | Underground Asset Renewal | Powerstream | From 2015-2018 customers in this area experienced 5 failures.
151063 | Base | Pole Renewal - Central South | 3.7094 | 3.8699 | 3.5139 | 3.1407 | 2.7499 | 16.9839 | 9065.1 | System Renewal | Overhead Asset Renewal | Enersource | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
100886 | Base | Distribution Automation - East | 1.2173 | 1.2878 | 1.3615 | 1.4385 | 2.0387 | 7.3437 | 9041.12 | System Service | SCADA and Automation | Powerstream | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151275 | Base | Cable Injection Project - (SCH) - QEW - Highway 406 - Martindale Road | 0 | 0.5544 | 0.78127 | 0.79689 | 0 | 2.1326 | 8905.36 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 3 failures, or 11 failures per 100km. The average cable installation year is 1988 in this project scope.
151298 | Base | Cable Injection Project - (HAM) - Govenors - Old Ancaster | 0 | 0 | 0.44177 | 0.9099 | 0.58388 | 1.9356 | 8842.48 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 3 failures, or 10 failures per 100km. The average cable installation year is 1989 in this project scope.
150808 | Base | Implementation of Doble - Enoserv PowerBase and Enoserv RTS applications for Protection and Control Department | 0.032465 | 0.02189 | 0 | 0 | 0 | 0.054355 | 8798.22 | General Plant | Information Technology | Multiple | PowerBase is the premier application to manage and report on protection assets maintenance and engineering records. It manages workflow and connect with maintenance management systems such as Cascade. RTS is a vendor neutral software which allows connection to a variety of test sets. It offers an extensive relay test plan library.
151300 | Base | Cable Injection Project - (HAM) - Millen - Barton - Fruitland | 0.9103 | 0.71914 | 0 | 0 | 0 | 1.6294 | 8690.38 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 16 failures, or 44 failures per 100km. The average cable installation year is 1987 in this project scope.
151389 | Base | 2021 GUELPH - Remotely Controlled Switches | 0 | 0.42587 | 0 | 0 | 0 | 0.42587 | 8627.99 | System Service | SCADA and Automation | Guelph | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
150097 | M-Factor | Line Protections and HMI Upgrade - KDU-10 Replacement - Markham TS#2 | 0.48367 | 0 | 0 | 0 | 0 | 0.48367 | 8506.15 | System Renewal | Substation Renewal | Powerstream | KDU-10 protection relay malfunction can cause an outage on the 230 kV supply of the station, resulting in a major power interruption. Replacement of this obsolete equipment is expected to provide improved reliability and will provide fault and event record information which will enable accurate diagnosis of system events and outage duration reductions.
150418 | Base | 42M62 Extension Bovaird Dr, Mississauga Rd to Heritage Rd | 0 | 0.39514 | 0 | 0 | 0 | 0.39514 | 8351.21 | System Service | Capacity (Lines) | Brampton | This project consists of 42M62 extension on Bovaird drive from Mississauga Road to Heritage Road. The 42M62 circuit extension will supply industrial on Heritage Road, as well as new residential developments
101804 | Base | Purchase of Major Tools | 0.34612 | 0.35356 | 0.36116 | 0.36893 | 0.37686 | 1.8066 | 8158.3 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
151424 | Base | Cable Replacement Project-Miss. Valley & Bloor (15) Mississauga | 0 | 0 | 0 | 0 | 9.8721 | 9.8721 | 8140.7 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 10,780 m, and the average cable age is 34 years old. There are 32 backlot transformers that we are also replacing.
101488 | Base | Markham TS #5 | 0 | 0 | 0 | 0.2722 | 0.44685 | 0.71905 | 8116.61 | System Service | Capacity (Stations) | Powerstream | This project is to perform Class EA and purchase land for Markham TS#5 which has been recommended as per the York Region IRRP
151390 | Base | 2022 GUELPH - Remotely Controlled Switches | 0 | 0 | 0.4099 | 0 | 0 | 0.4099 | 8051.64 | System Service | SCADA and Automation | Guelph | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151213 | Base | Installation of Transformer Bushing Monitoring | 0 | 0 | 0.09 | 0 | 0 | 0.09 | 8001.2 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of installation of Transformer bushing monitoring system in Guelph. bushing monitoring unit provides real time condition monitoring of the transformer bushings.
150773 | M-Factor | New WiMAX Communications System - Central North | 0.27498 | 0 | 0 | 0 | 0 | 0.27498 | 7999.76 | System Service | System Control, Comm'ns & Performance | Brampton | This project is to provide WiMax for Central North for secure data transfer of monitoring devices.
150509 | Base | Installation of Transformer Bushing Monitoring Yarrow TS and MS txmrs-Multi Year -EAST | 0.12154 | 0.089936 | 0 | 0 | 0 | 0.21148 | 7885.3 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Transformer bushing monitoring system in Central North. Bushing monitoring unit provides real time condition monitoring of the transformer bushings.
150709 | Base | Spare Station Transformer Bushing Conversion from PILC to XLPE - West | 0.11015 | 0.11155 | 0 | 0 | 0 | 0.2217 | 7847.53 | System Renewal | Substation Renewal | Horizon | This project involves converting the spare station transformer primary and secondary bushings/compartments from PILC to XLPE in the West Operating Area (former Horizon). The spare transformers are used when a failure occurs on a station transformer. The PILC cable will be replaced with XLPE at the station in order to improve station reliability and worker and equipment safety. The conversion of bushings is critical as primary bushing compartments have ruptured on multiple occasions in 2017 in the West Operating Area - causing oil spills larger than 200 liters.
151313 | Base | Cable Injection Project - (F5) - Steeles - Main - Hwy 407 - McLaughlin, Brampton | 0 | 0.3125 | 0.21875 | 0.3125 | 0.098938 | 0.94269 | 7751.39 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 5 outages due to cable failures from 2007 to 2016 with average duration of 80 minutes.
102038 | Base | Installation of Transformer Bushing Monitoring on TS and MS txmrs-Multi Year | 0.12367 | 0.12564 | 0 | 0 | 0 | 0.24931 | 7734.98 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of Transformer bushing monitoring system in East. bushing monitoring unit provides real time condition monitoring of the transformer bushings.
150785 | M-Factor | New WiMAX Communications System - West | 0.48704 | 0 | 0 | 0 | 0 | 0.48704 | 7655.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project is to provide WiMax for West for secure data transfer of monitoring device.
151349 | Base | Cable Injection Project - (V16) - Langstaff - Dufferin - Steeles - Jane, Vaughan | 0 | 0.90311 | 0 | 0 | 0 | 0.90311 | 7572.02 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 23 failures.
151352 | Base | Cable Injection Project - (M38) - Hwy 7 - Warden - 14th - Woodbine, Markham | 0 | 0 | 0.96869 | 0 | 0 | 0.96869 | 7548.01 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 18 failures.
150282 | Base | Switchgear Renewal - Central North | 0.46462 | 0.47937 | 0.49461 | 0.51036 | 0.52663 | 2.4756 | 7521.14 | System Renewal | Underground Asset Renewal | Brampton | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150508 | Base | Installation of Transformer Bushing Monitoring on MS txmrs-Multi Year -CENTRAL | 0.16526 | 0.16732 | 0.16939 | 0.17148 | 0 | 0.67345 | 7508.89 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Transformer bushing monitoring system in Central South. bushing monitoring unit provides real time condition monitoring of the transformer bushings.
151062 | Base | Cable Replacement - (279) - 201 Silvercreek Pky N Subdivision, Guelph | 0.69856 | 0 | 0 | 0 | 0 | 0.69856 | 7505.11 | System Renewal | Underground Asset Renewal | Guelph
151391 | Base | 2023 GUELPH - Remotely Controlled Switches | 0 | 0 | 0 | 0.42012 | 0 | 0.42012 | 7487.72 | System Service | SCADA and Automation | Guelph | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151361 | Base | Cable Injection Project - (V26) - Teston - Keele - Major Mackenzie - Jane, Vaughan | 0 | 0 | 0 | 0 | 1.194 | 1.194 | 7472.7 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 8 failures.
151407 | Base | Cable Replacement Project- Glen Erin & Burnhamthorpe (12), Mississauga | 0 | 0 | 7.3358 | 0 | 0 | 7.3358 | 7413.63 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 10 outages, the length is 22,109 m, and the average cable age is 34 years old.
151325 | Base | Cable Replacement Project - (M31) - 14th - Old Kennedy - Steeles - Warden, Markham | 0 | 3.5 | 3.5 | 3.5 | 1.1785 | 11.6785 | 7411.62 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 38 failures.
151457 | M-Factor | Cable Injection Project - (V25) - Major Mackenzie - Keele - Rutherford - Jane, Vaughan | 0 | 0 | 0.8749 | 0.40538 | 0 | 1.2803 | 7409.58 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 2 failures. From 2015-2019 YTD customers in this area experienced 3 failures.
151339 | Base | Cable Replacement Project - (BA19) - Letitia - Anne - Edgehill - Ferndale, Barrie | 0 | 0 | 7.3499 | 4.4258 | 0 | 11.7758 | 7397.06 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 2 failures in 2018.
150370 | M-Factor | New build - 27.6kV New Feeders Lakeview Development, Mississauga | 0 | 0 | 0 | 1.8901 | 0 | 1.8901 | 7391.03 | System Service | Capacity (Lines) | Enersource | Two 27.6kV feeders are to be extended in order to provide for additional capacity in the Lakeview area for the brownfield development and intesificiation
151316 | Base | Cable Injection Project - (H2) - Wanless - Heart Lake - Bovaird - Kennedy, Brampton | 0 | 0.3125 | 0.21875 | 0.40906 | 0 | 0.94031 | 7371.2 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2009 to 2017 with average duration of 107 minutes.
151121 | Base | Cable Injection Project - (V43) - Hwy 7 and Pine Valley Dr, Vaughan | 1.0195 | 0 | 0 | 0 | 0 | 1.0195 | 7356.55 | System Renewal | Underground Asset Renewal | Powerstream | From 2015-2016 customers in this area experienced 3 failures.
150284 | Base | Pole Renewal - Central North | 0.9285 | 2.0544 | 2.793 | 2.898 | 3.0054 | 11.6793 | 7304.65 | System Renewal | Overhead Asset Renewal | Brampton | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
150484 | Base | 25M8 27.6kV Feeder Extension Heritage Rd, South of Embleton Rd | 0.44307 | 0 | 0 | 0 | 0 | 0.44307 | 7282.14 | System Service | Capacity (Lines) | Brampton | This project consists of 25M8 feeder extension to Hertitage road to supply new developments
102017 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-North & TS | 0.32275 | 0.32654 | 0.33036 | 0.33423 | 0.33814 | 1.652 | 7275.34 | System Service | Safety & Security | Powerstream | This project consists of Sorbweb Oil containment system in East. Protects the environment in the event of a transformer tank rupture
100924 | M-Factor | Install two additional 27.6 kV ccts on Hwy 7 from Jane St to Weston Rd | 0 | 0 | 0 | 2.6201 | 0 | 2.6201 | 7255.59 | System Service | Capacity (Lines) | Powerstream | This project is to reroute two 27.6kV feeders (21M3 & 21M4) to supply new load in Vaughan Metro Center (VMC). Vaughan Metro Center (VMC) is supplied by two feeders 21M5 and 21M11 from VTS2. There is limited capacity on VTS2 left before it reaches the 10 day Limited Time Rating (LTR) of 153 MW. VTS4 was completed in 2017 and is in service and will off load VTS2 so that will have extra capacity to supply new loads in the VMC development (approx. 80MW).
151351 | Base | Cable Injection Project - (M32) - Hwy 7 - Main - 14th - Warden, Markham | 0 | 0 | 0.89983 | 0 | 0 | 0.89983 | 6971.35 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 17 failures.
151392 | Base | 2024 GUELPH - Remotely Controlled Switches | 0 | 0 | 0 | 0 | 0.43065 | 0.43065 | 6956.6 | System Service | SCADA and Automation | Guelph | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
150026 | Base | Cable Injection Project - (M43) - John and Woodbine, Markham | 1.0296 | 0 | 0 | 0 | 0 | 1.0296 | 6955.31 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 38 years old and will be 39 when project starts (2020).
150343 | M-Factor | Bathurst Street Widening | 3.4061 | 0 | 0 | 0 | 0 | 3.4061 | 6905.3 | System Access | Road Authority | Powerstream | 2020 portion of scope of the Bathurst Street road widening as per requirements of PSWHA.
150021 | Base | Cable Injection Project - (V36) - Steeles and Pine Valley, Vaughan | 0.6044 | 0 | 0 | 0 | 0 | 0.6044 | 6821.94 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2017 customers in this area experienced 9 failures.
150714 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - Central | 0.073902 | 0.074795 | 0.075697 | 0.076608 | 0.077526 | 0.37853 | 6819.25 | System Renewal | Substation Renewal | Enersource | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central South Operating Area (former Enersource). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150713 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.073902 | 0.074795 | 0.075697 | 0.076608 | 0.077526 | 0.37853 | 6819.25 | System Renewal | Substation Renewal | Brampton | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central North Operating Area (Brampton). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150715 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - West | 0.073902 | 0.074795 | 0.075697 | 0.076608 | 0.077526 | 0.37853 | 6819.25 | System Renewal | Substation Renewal | Horizon | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the West Operating Area (former Horizon). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150644 | Base | Road Authority West (Hamilton) | 1.3896 | 1.5459 | 1.7199 | 1.9134 | 2.1287 | 8.6975 | 6689.48 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
151355 | Base | Cable Injection Project - (M26) - Hwy 7 -McCowan - 14th - Old Kennedy, Markham | 0 | 0 | 0 | 0.92043 | 0 | 0.92043 | 6565.53 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 14 failures.
150507 | Base | 230kV TS Transformer Primary Bushing Monitoring Enablement-BPD Elimination - 4 TS Transformers-Multi-year initiative-TS | 0.24481 | 0.48553 | 0.50099 | 0.49794 | 0 | 1.7293 | 6521.07 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to install primary bushing monitoring at TS in EAST
151459 | M-Factor | Cable Injection Project - (V24) - Langstaff - Jane - Rutherford - Keele, Vaughan | 0 | 0 | 0 | 0.53203 | 0.73081 | 1.2628 | 6509.15 | System Renewal | Underground Asset Renewal | Powerstream | From 2015-2019 YTD customers in this area experienced 0 failures. From 2013-2019 YTD customers in this area experienced 2 failures.
150352 | Base | Voltage Conversion - Central MS, Hamilton | 1.7173 | 1.4628 | 1.8425 | 0 | 0 | 5.0227 | 6498.05 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 23 outages and had 1,060,300 customer minutes of interruption (75 mins per customer per year). The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail. Specifically Central MS is the only station remaining in service with oil breakers which are functionally obsolete with no spare parts readily available.
150468 | Base | Meter to Cash auxiliary systems ongoing upgrades - IT/OT Infrastructure | 0 | 0 | 0 | 0.17264 | 0.17461 | 0.34725 | 6494.96 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) Meter to Cash ancillary systems to support process improvement requirements. Ancillary systems but not limited to upgrading FW, MV90, LPSS. These enhancements are considered for the overall customer and organizational benefits.
151418 | Base | Cable Replacement Project- Innovator & Courtney Park E (4), Mississauga | 0 | 0 | 0 | 2.8903 | 0 | 2.8903 | 6467.04 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 7 outages, the length is 7,263 m, and the average cable age is 22 years old. This is a commerical/industrial (3-phase) area.
151310 | Base | Cable Injection Project - (E4) - Queen - McLaughlin - Steeles - Chinguacousy, Brampton | 0 | 0.3125 | 0.21875 | 0.24013 | 0 | 0.77138 | 6421.34 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2008 to 2016 with average duration of 104 minutes.
150357 | Base | New build - 25M9 Extension to Derry Rd, Mississauga | 0.45622 | 1.6706 | 0 | 0 | 0 | 2.1268 | 6400.82 | System Service | Capacity (Lines) | Enersource | This project consists of 25M9 extension into Mississauga to provide additional 27.6KV capacity. It will offload Erindale TS in Mississauga and avoid building Mini-Britannia MS and also provides capacity back to Brampton using a link along Derry Rd.
151044 | Base | Switch Renewal - Central South | 0.26412 | 0.2698 | 0.2756 | 0.28152 | 0.28758 | 1.3786 | 6318.96 | System Renewal | Overhead Asset Renewal | Enersource | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
150065 | Base | Basement Flood Risk Mitigation - Richmond Hill TS#2 | 0.15967 | 0 | 0 | 0 | 0 | 0.15967 | 6280.45 | System Renewal | Substation Renewal | Powerstream | This project involves mitigating the flood risk at the Richmond Hill TS#2 where there is equipment installed in the basement by relocating or repositioning this equipment. This critical equipment includes DC system, AC and DC panels, feeder switches, UPS, ATS located in the basement of this station. Damage to this equipment due to flooding would cause extensive power interruptions to many customers.
103659 | Base | Storm Hardening - Four-Circuit Poles | 1.7828 | 1.8732 | 1.968 | 2.0675 | 2.1719 | 9.8635 | 6254.52 | System Renewal | Overhead Asset Renewal | Powerstream
100459 | Base | New Barrie 20MVA Substation - Harvie - 44 kV Supply | 0 | 0 | 0 | 0 | 0.0041218 | 0.0041218 | 6215.37 | System Service | Capacity (Stations) | Powerstream | This project consists of 44KV feeder extension to supply for Harvie MS project (101452)
150514 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear Initiative-WEST | 0.33357 | 0.33748 | 0.34254 | 0.34696 | 0.35101 | 1.7116 | 6213.41 | System Service | Safety & Security | Horizon | This project consists of Sorbweb Oil containment system in West. Protects the environment in the event of a transformer tank rupture
151336 | Base | Cable Replacement Project - (BA22) - Sunnidale and Anne, Barrie | 1.0002 | 1.9157 | 1.4826 | 1.5309 | 3.8566 | 9.786 | 6208.17 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 2 failures in 2019.
151305 | Base | Cable Injection Project - (HAM) - Stone Church - Upper Sherman - Rymal - Upper Wellington | 0 | 0 | 0 | 0 | 0.71046 | 0.71046 | 6019.14 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 1 failure, or 3 failures per 100km. The average cable installation year is 1989 in this project scope.
151086 | Base | Insulator Replacements | 0.08172 | 0.083477 | 0.085272 | 0.087105 | 0.088978 | 0.42655 | 5948.6 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
102128 | M-Factor | Aurora MS6 Expansion | 0 | 0.8326 | 1.1231 | 0 | 0 | 1.9557 | 5909.69 | System Service | Capacity (Lines) | Powerstream | 2C land is currently supplied by a 13.8kV feeder 5F2. It had a peak of 269A in 2018 and does not have sufficient capacity to supply future growth in the 2C lands. New feeder capacity is required to supply the additional load.
150066 | Base | Basement Flood Risk Mitigation - Vaughan TS#2 | 0.12303 | 0.12625 | 0 | 0 | 0 | 0.24928 | 5867.18 | System Renewal | Substation Renewal | Powerstream | This project involves mitigating the flood risk at the Vaughan TS#2 where there is equipment installed in the basement by relocating or repositioning this equipment. This critical equipment includes DC system, AC and DC panels, feeder switches, UPS, ATS located in the basement of this station. Damage to this equipment due to flooding would cause extensive power interruptions to many customers.
100461 | Base | New Barrie 20MVA Substation - Harvie - 13.8kV Feeder Integration | 0 | 0 | 0 | 0 | 0.028851 | 0.028851 | 5856.18 | System Service | Capacity (Stations) | Powerstream | This project consist of 13.8KV feeder integration for Harvie MS project (101542)
151176 | Base | Cable Replacement Project - MS Argentia distribution feeder(s) upgrade | 1.5666 | 0 | 0 | 0 | 0 | 1.5666 | 5705.35 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 11 outages, the length is 1,587 m, and the average cable age is 30 years old.
150351 | M-Factor | Voltage Conversion - Aberdeen MS, Hamilton | 0 | 2.08 | 1.269 | 0 | 0 | 3.349 | 5674.67 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 16 outages and had 500,475 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151404 | Base | Cable Replacement Project- Central Pk E & Miss. Valley (28) | 0 | 8.4404 | 0 | 0 | 0 | 8.4404 | 5611.16 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 11 outages, the length is 7,100 m, and the average cable age is 42 years old. There are 27 backlot transformers that we are also replacing.
151463 | M-Factor | Cable Injection Project - (F4-G4) - Main - Steeles - Chinguacousy - Queen, Brampton | 0 | 0 | 0 | 0.34735 | 0.72699 | 1.0743 | 5559.84 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 86 failures. Exact number of failures in recent years is unknown at this moment.
150637 | Base | Station Switchgear Replacement - MS10 | 2.5738 | 0 | 0 | 0 | 0 | 2.5738 | 5499.15 | System Renewal | Substation Renewal | Brampton | The existing switchgear at MS10 in Brampton is no longer suitable for service. The main project driver for replacement is the condition of the metal-clad switchgear housing the feeder breakers and bus-tie breakers. The manufacturer no longer supports this type of equipment and the design of the switchgear does not meet Alectra Utilities' current safety standards and presents a potential risk to its employees. An increasing failure risk will have a negative impact on Alectra Utilities' customers, and safety. Additionally, failure of the existing switchgear would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions.
150337 | Base | Switch Renewal - West | 0.4261 | 0.43526 | 0.44462 | 0.45418 | 0.46394 | 2.2241 | 5475.59 | System Renewal | Overhead Asset Renewal | Horizon | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
151055 | Base | Major Tools | 0.073792 | 0.075379 | 0.077 | 0.078655 | 0.080346 | 0.38517 | 5431.72 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
150067 | Base | Basement Flood Risk Mitigation - Markham TS#4 | 0 | 0.12831 | 0.13095 | 0 | 0 | 0.25926 | 5409.71 | System Renewal | Substation Renewal | Powerstream | This project involves mitigating the flood risk at the Markham TS#4 where there is equipment installed in the basement by relocating or repositioning this equipment. This critical equipment includes DC system, AC and DC panels, feeder switches, UPS, ATS located in the basement of this station. Damage to this equipment due to flooding would cause extensive power interruptions to many customers.
150598 | Base | Suite Metering - Renewals & Retrofits - PowerStream RZ | 0.35225 | 0.35626 | 0.36032 | 0.36442 | 0.36857 | 1.8018 | 5394.14 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering equipment in existing buildings upgraded from bulk metering.
150515 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-CENTRAL | 0.33465 | 0.33858 | 0.34254 | 0.34696 | 0.35101 | 1.7137 | 5352.14 | System Service | Safety & Security | Enersource | This project consists of Sorbweb Oil containment system in Central South. Protects the environment in the event of a transformer tank rupture
150516 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-EAST | 0.33465 | 0.33858 | 0.34254 | 0.34696 | 0.35101 | 1.7137 | 5352.14 | System Service | Safety & Security | Brampton | This project consists of Sorbweb Oil containment system in Central North. Protects the environment in the event of a transformer tank rupture
150744 | Base | John Street underground parking renewal | 0.30951 | 0 | 0 | 0 | 0 | 0.30951 | 5343.15 | General Plant | Facilities Management | Horizon | Repairs to the undergrown parking level that is in poor condition impacting builsing system below that support the building operations and craeting saftey risks. The building was built in 1950 and many of the building infrastructure is still original.
150336 | Base | Transformer Renewal - West | 0.56332 | 0.66396 | 0.67823 | 0.69281 | 0.70771 | 3.306 | 5293.52 | System Renewal | Transformer Renewal | Horizon | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
151306 | Base | Cable Injection Project - (HAM) - Upper Wentworth - Lincoln M. Alexander - Upper Ottawa - Stone Church | 0 | 0 | 0 | 0.46107 | 0.52639 | 0.98746 | 5236.89 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 2 failures, or 8 failures per 100km. The average cable installation year is 1988 in this project scope.
150750 | Base | Lines Central-North - Major Tools | 0.091257 | 0.093219 | 0.095223 | 0.09727 | 0.099361 | 0.47633 | 5234.11 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
151432 | Base | Cable Injection- 007- AREA 43 & 51- Hurontario & Derry Rd W, Mississauga | 0 | 0 | 0 | 0 | 1.3799 | 1.3799 | 5149.22 | System Renewal | Underground Asset Renewal | Enersource | There are 3 outages, we are injecting a total of 16,419 m of cable for this project, and the average age of the cable is 28 years.
150009 | Base | Insulator Renewal - East | 0.20501 | 0.22509 | 0.23334 | 0.24187 | 0.2507 | 1.156 | 5107.82 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
100909 | M-Factor | Rebuild 27.6 kV pole line for 4 Ccts on Warden Ave from Major Mack to Elgin Mills | 0 | 0 | 2.1805 | 0 | 0 | 2.1805 | 4927.44 | System Service | Capacity (Lines) | Powerstream | This project is the third part of a multiple year project of rerouting two feeders 12M10/12M11 to Markham Future Urban Area. This project provide 40 MVA capacity.
151203 | Base | Capital Corrective Equipment Replacement - Stations South West | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.3 | 4921.2 | System Renewal | Substation Renewal | Guelph | This project is intended to provide capital for all unplanned station equipment replacements in the South West Operating Area (Guelph) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
102042 | Base | Purchase and Installation of Animal Guards at Various Stations-Annual Multi-year initiative-North & TS | 0.015834 | 0.016055 | 0.016279 | 0.016503 | 0.016728 | 0.0814 | 4893.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of animal guard installation in East
150716 | M-Factor | New build - 42M69 Feeder Extension Williams Pkwy - Main St to Kennedy Rd, Brampton | 0 | 0 | 1.1277 | 0 | 0 | 1.1277 | 4865.64 | System Service | Capacity (Lines) | Brampton | 27.6kV UG Feeder Extension along Williams Pkwy from Main St to Kennedy Rd OH to meet contingency conditions
150605 | M-Factor | Residential "ICON F" Meter Replacement - PowerStream RZ | 3.0236 | 4.2354 | 0 | 0 | 0 | 7.259 | 4853.17 | System Access | Metering | Powerstream | Multi-year project to replace Icon-F smart meters with secure encryption, last gasp and tamper detection capabilities.
151403 | Base | Cable Replacement Project- Montevideo & Battleford (19b), Mississauga | 0 | 1.6698 | 0 | 0 | 0 | 1.6698 | 4849.24 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 12 outages, the length is 5,013 m, and the average cable age is 39 years old.
151359 | Base | Cable Injection Project - (M16) - Major Mackenzie - 9th - 16th - Hwy 48, Markham | 0 | 0 | 0 | 0.66553 | 0 | 0.66553 | 4782.06 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 7 failures.
151464 | M-Factor | Cable Injection Project - (F3-G3-H3) - Phase 2, Brampton | 0 | 0 | 0.37968 | 0.45851 | 0 | 0.83819 | 4696.76 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 103 failures. Exact number of failures in recent years is unknown at this moment.
151328 | Base | Cable Replacement Project- (21a) Darcel & Brandon Gate, Mississauga | 0 | 1.4364 | 0 | 0 | 0 | 1.4364 | 4688.73 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 4,087 m, and the average cable age is 46 years old.
151083 | Base | Switchgear Renewal - West | 0.41269 | 0.42156 | 0.43062 | 0.43988 | 0.44934 | 2.1541 | 4683.89 | System Renewal | Underground Asset Renewal | Horizon | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151010 | Base | Switch Renewal - Central North | 0.63119 | 0.6454 | 0.65985 | 0.67455 | 0.68949 | 3.3005 | 4603.75 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
150720 | Base | Lines Central-South - Major Tools | 0.21472 | 0.21934 | 0.22405 | 0.22887 | 0.23379 | 1.1208 | 4591.27 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
151461 | M-Factor | Cable Injection Project - (V51) - Langstaff - Kipling - Hwy 7 - Hwy 27, Vaughan | 0 | 0 | 0 | 0 | 0.67168 | 0.67168 | 4537.27 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 1 failure. From 2015-2019 YTD customers in this area experienced 5 failures.
151022 | M-Factor | New Three Sector WiMAX Node - MS305 | 0.1287 | 0 | 0 | 0 | 0 | 0.1287 | 4525.35 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to install three sector WiMax node at MS305. The node would provide last mile broadband connectivity to field devices such as intelligent overhead reclosers and padmounted switchgears, FIT monitoring data concentrators and Ethernet enabled revenue meters. The node would provide Transfer Trip capability to FIT generators.
151420 | Base | Cable Replacement Project-Eglinton & Credit Valley (5), Mississauga | 0 | 0 | 0 | 10.2106 | 0 | 10.2106 | 4485.73 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 27,821 m, and the average cable age is 35 years old.
150411 | M-Factor | 42M64 Feeder Extension Mississauga Rd, Williams Pkwy to Queen / Embleton | 0.11948 | 0 | 0 | 0 | 0 | 0.11948 | 4471.12 | System Service | Capacity (Lines) | Brampton | 42M64 Feeder Extension from Mississauga Rd from Queen St. to Embleton Rd to supply new developments on Embleton and provide relief to the existing feeder 25M8
151433 | Base | Cable Injection- 008- AREA46 - Glen Erin & Aquitane, Mississauga | 0.60219 | 0.61424 | 0 | 0 | 0 | 1.2164 | 4470.89 | System Renewal | Underground Asset Renewal | Enersource | There are 6 outages, we are injecting a total of 19,827 m of cable for this project, and the average age of the cable is 33 years.
150677 | Base | Station Switchgear Replacement - Aquitaine MS59 LV1 | 1.7021 | 0 | 0 | 0 | 0 | 1.7021 | 4470.11 | System Renewal | Substation Renewal | Enersource | The existing LV1 switchgear at Aquitaine MS59 station houses gas circuit breakers that utilize vintage technology to provide short circuit protection against faults. These circuit breakers are technically obsolete and are prone to failure. Also the switchgear is non-arc-resistant and poses a potential safety hazard to Alectra personnel and even to the general public who happen to be in the vicinity of the station during a failure event. Failure of the existing switchgear and breakers would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions. Therefore, proactive replacement of the existing switchgear and associated equipment is a prudent strategy as the restoration of the system could take 8-10 months due to long equipment lead times in the event of a failure.
151364 | Base | Cable Injection Project - (V23) - Hwy 7 - Keele - Langstaff - Jane, Vaughan | 0 | 0 | 0 | 0 | 0.6615 | 0.6615 | 4381.14 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 2 failures.
151401 | Base | Cable Replacement Project- (21b) Sigsbee & Morning Star, Mississauga | 0 | 1.0406 | 0 | 0 | 0 | 1.0406 | 4296.47 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 7 outages, the length is 2,956 m, and the average cable age is 46 years old.
151021 | Base | Insulator Renewal - Central North | 0.33484 | 0.35316 | 0.3755 | 0.38723 | 0.39792 | 1.8486 | 4235.99 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of non-polymer insulators (Areas are prioritiezed by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
150536 | Base | Implement database security - IT Infrastructure | 0 | 0.12755 | 0 | 0 | 0 | 0.12755 | 4195.13 | General Plant | Information Technology | Multiple | This project will address security risks related to data-at-rest.
150674 | Base | Emerging Customer Initiated Work Central (Brampton) | 0.14337 | 0.15225 | 0.16168 | 0.1717 | 0.18233 | 0.81133 | 4183.83 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101763 | Base | Unforeseen Projects Initiated by the customer PS North | 0.1124 | 0.11937 | 0.12676 | 0.13462 | 0.14296 | 0.63611 | 4161.34 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150125 | M-Factor | Aurora MS6 (AMS6) Transformer and Bus Protection Upgrade | 0.13286 | 0 | 0 | 0 | 0 | 0.13286 | 4156.05 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade transformer and bus protection at Aurora MS6 station from the current electromechnical KBCH relay.
150745 | Base | John Street VAV Updating - Facilities | 0.51586 | 0 | 0 | 0 | 0 | 0.51586 | 4034.02 | General Plant | Facilities Management | Horizon | Update main building ventilation systems that have surpass end of life and replacement apsrt ca no longer be obatined that support the main Alectra control room, customer services group and communications systesm.
150520 | Base | Security Additions & Enhancements | 0.23898 | 0 | 0 | 0 | 0 | 0.23898 | 4023.87 | General Plant | Information Technology | Multiple | As per Alectra Security roadmap to key IT systems.
150541 | Base | Business Support | 0.16784 | 0 | 0 | 0 | 0 | 0.16784 | 4021.57 | General Plant | Information Technology | Multiple | The project will encompass a variety of sub projects for the purpose of investigating new and emerging technologies. Building a culture of innovation Alectra will need a continued effort in remaining ahead of the trends and implementing new and more efficient ways of doing business. The projects that are slated for this years budget are room Artificial Intelligence and Wearable Technology
150679 | M-Factor | Alectra Drive for the Workplace | 0.15373 | 0.15753 | 0.16346 | 0.16532 | 0.1672 | 0.80724 | 3997.47 | System Service | Capacity (Lines) | Multiple | Alectra Drive for the Workplace will demonstrate the value of integrating smart electric vehicle (EV) charging system at workplaces into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. The planned investment will help manage the flow of electricity needed to serve the building and EV charging stations, so that electricity costs are minimized for commercial customers while EV drivers have an easy and accessible charging solution.
150320 | M-Factor | Voltage Conversion - Dewitt MS , Hamilton | 2.6467 | 0.96641 | 0.49349 | 0 | 0 | 4.1066 | 3972.49 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 12 outages and had 888,434 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151348 | Base | Cable Injection Project - (M20) - Hwy 7 - Markham - 14th - McCowan, Markham | 0 | 0.43073 | 0 | 0 | 0 | 0.43073 | 3971.28 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 14 failures.
150358 | M-Factor | New build - QEW Dixie West New OH Circuits, Mississauga | 0 | 0 | 1.0659 | 0 | 0 | 1.0659 | 3906.72 | System Service | Capacity (Lines) | Enersource | This project is an to added betterment coordinated with the MTO's QEW Expansion along Dixie West OH.
150466 | Base | Atomic Scheduler Upgrade - IT Infrastructure | 0 | 0 | 0.31347 | 0 | 0 | 0.31347 | 3883.01 | General Plant | Information Technology | Multiple | Enhancement to Atomic application scheduler to support process improvement requirements. Atomic is the application scheduler in use at Alectra. This application will be used to support application and report scheduling for both CC&B and JDE. These enhancements are considered for the overall customer and organizational benefits.
150540 | Base | Implement application security - IT Infrastructure | 0 | 0 | 0.12953 | 0 | 0 | 0.12953 | 3860.92 | General Plant | Information Technology | Multiple | Ongoing application security enhancements and additions to meet vendor requirements .
150408 | Base | 42M71 Feeder Egress Salvation Rd, West, Creditview, Wanless | 0 | 0.38649 | 0 | 0 | 0 | 0.38649 | 3769.35 | System Service | Capacity (Lines) | Brampton | This project consists of 42M71 feeder egress and ties to 42M61 and 42M43 will provide contingency to circuits nearing planning limits.
151430 | Base | Cable Injection- 005- AREA 38- Bristol & Creditview, Mississauga | 0 | 0.88643 | 0 | 0 | 0 | 0.88643 | 3745.79 | System Renewal | Underground Asset Renewal | Enersource | There is 1 outage, we are injecting a total of 11,193 m of cable for this project, and the average age of the cable is 32 years.
151413 | Base | Cable Replacement Project- Rathburn Rd W & Elora Dr (9), Mississauga | 0 | 0 | 0 | 1.5737 | 0 | 1.5737 | 3743.76 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 8 outages, the length is 3,270 m, and the average cable age is 27 years old.
150367 | M-Factor | Mini-Orlando MS 27.6kV Land Purchase, Mississauga | 0 | 0 | 0 | 0 | 2.1561 | 2.1561 | 3726.8 | System Service | Capacity (Stations) | Enersource | Mini-Orlando MS is situated on leased land in the area of Mavis Road, south of Highway 401, provides capacity for the commercial and industrial customers in the Heartland area
150043 | M-Factor | Rear Lot Renewal Project - East of Queen St. to Eastern Ave./North of Greenway St. | 2.5524 | 0 | 0 | 0 | 0 | 2.5524 | 3714.07 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 1.7 outages lasting 9.7hrs per year based on a 3 year average.
102075 | Base | Major repairs, refurbishment, or modifications to switches/switchgear | 0.10114 | 0.10229 | 0.10346 | 0.10463 | 0.10582 | 0.51734 | 3702.48 | System Renewal | Underground Asset Renewal | Powerstream | Switchgear and Switches in stores that repair/refurbishment of the units can allow them to be returned to service
150521 | Base | Security Additions & Enhancements | 0 | 0.24247 | 0 | 0 | 0 | 0.24247 | 3699.67 | General Plant | Information Technology | Multiple | As per Alectra Security roadmap to key IT systems.
150376 | Base | New build - Hamilton South Mountain feeders capacity relief, Hamilton | 0 | 1.1222 | 1.0573 | 0 | 0 | 2.1795 | 3693.91 | System Service | Capacity (Lines) | Horizon | This project is build new feeder to alleviate capacity in South Hamilton and to alleviate on the four feeders which are over the planning limit
151411 | Base | Cable Replacement Project- Queensway & Mavis (31), Mississauga | 0 | 0 | 0 | 3.5553 | 0 | 3.5553 | 3693.6 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 8 outages, the length is 8,488 m, and the average cable age is 42 years old.
151319 | Base | Cable Injection Project - (I4) -Queen - Dixie - Steeles - Hwy 410, Brampton | 0 | 0 | 0.42787 | 0 | 0 | 0.42787 | 3650.43 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 outage due to cable failures to date. Cables are 31 years old and will be at the injection eligibility threshold by the time of project execution in 2022.
150415 | Base | 42M65 Feeder Egress Pleasant TS to SG20-1438 | 0 | 0.5387 | 0 | 0 | 0 | 0.5387 | 3640.88 | System Service | Capacity (Lines) | Brampton | This project consists of 42M65 feeder egress out of Pleasant TS and will supply the redvelopments in downtown.
150535 | Base | Network Segmentation - IT Infrastructure | 0.32788 | 0 | 0 | 0 | 0 | 0.32788 | 3636.03 | General Plant | Information Technology | Multiple | As per Alectra Security roadmap to key IT systems with focus on network segmentation for corporate environments.
151428 | Base | Cable Injection- 002- AREA 30- Eglinton Ave W & Miss Rd, Mississauga | 0 | 0.58737 | 0.57547 | 0 | 0 | 1.1628 | 3632.2 | System Renewal | Underground Asset Renewal | Enersource | There are 2 outages, we are injecting a total of 14,541 m of cable for this project, and the average age of the cable is 31 years.
150329 | M-Factor | Rear Lot Renewal Project - Main Street / Unionville / Carlton | 0 | 0 | 0 | 0 | 2.486 | 2.486 | 3599.28 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 1 outages lasting an 1hr 40 minutes per year based on a 3 year average.
151276 | Base | Cable Injection Project - (SCH) - Vansickle | 0 | 0.36816 | 0.73247 | 0.36054 | 0 | 1.4612 | 3555.68 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 11 failures per 100km. The average cable installation year is 1990 in this project scope.
151200 | M-Factor | Alectra Single Platform Website ongoing | 0.10822 | 0.10945 | 0.1107 | 0 | 0 | 0.32837 | 3548.17 | General Plant | Information Technology | Multiple | Ongoing enhancements to the Alectra platform to improve functionality for customers
150498 | Base | Capital Corrective Equipment Replacement - Stations Central South | 0.26932 | 0.2729 | 0.27652 | 0.28015 | 0.28382 | 1.3827 | 3534.76 | System Renewal | Substation Renewal | Enersource | This project is intended to provide capital for all unplanned station equipment replacements in the Central South Operating Area (former Enersource) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150499 | Base | Capital Corrective Equipment Replacement - Stations Central North | 0.26932 | 0.2729 | 0.27652 | 0.28015 | 0.28382 | 1.3827 | 3534.76 | System Renewal | Substation Renewal | Brampton | This project is intended to provide capital for all unplanned station equipment replacements in the Central North Operating Area (Brampton) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150497 | Base | Capital Corrective Equipment Replacement - Stations West | 0.26932 | 0.2729 | 0.27652 | 0.28015 | 0.28382 | 1.3827 | 3534.76 | System Renewal | Substation Renewal | Horizon | This project is intended to provide capital for all unplanned station equipment replacements in the West Operating Area (former Horizon) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
151304 | Base | Cable Injection Project - (HAM) - Stone Church - Garth - Lincoln M. Alexander | 0.56877 | 0 | 0 | 0 | 0 | 0.56877 | 3492.29 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 5 failures, or 18 failures per 100km. The average cable installation year is 1986 in this project scope.
150047 | M-Factor | Rear Lot Renewal Project - Royal Orchard - North | 1.8433 | 1.035 | 1.1307 | 0 | 0 | 4.0091 | 3478.27 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 3 failures per year lasting 4 hours per year based on 3 year average.
101542 | M-Factor | New Barrie 20MVA Substation - Harvie | 0 | 0 | 0 | 0.81585 | 1.3694 | 2.1852 | 3447.05 | System Service | Capacity (Stations) | Powerstream | The project entails the purchase of a station site in the vicinity of Harvie Road and Veterans Drive in Barrie and constructing a new 44/13.8kV, 20MVA, 4-feeder municipal substation.
151462 | M-Factor | Cable Injection Project - (G1) - Hwy 410 - Kennedy - Wanless - Main, Brampton | 0 | 0.31046 | 0.24276 | 0 | 0 | 0.55322 | 3437.98 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 2 failures. Exact number of failures in recent years is unknown at this moment.
150774 | Base | Lines Central-North - Site Restorations | 0.10317 | 0.10539 | 0.10766 | 0.10997 | 0 | 0.42619 | 3434.48 | System Renewal | Overhead Asset Renewal | Brampton
150721 | Base | Lines Central-South - Site Restorations | 0.10317 | 0.10539 | 0.10766 | 0.10997 | 0 | 0.42619 | 3434.48 | System Renewal | Underground Asset Renewal | Enersource
151344 | Base | Cable Injection Project - (R16) - Major Mackenzie - Bayview - 16th - Yonge, Richmond Hill | 0 | 0.3007 | 0 | 0 | 0 | 0.3007 | 3396.52 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 16 failures.
150523 | Base | Security Additions & Enhancements | 0 | 0 | 0.24602 | 0 | 0 | 0.24602 | 3395.44 | General Plant | Information Technology | Multiple | As per Alectra Security roadmap to key IT systems.
150353 | M-Factor | Truscott Plaza - Additional capacity, Mississauga | 0 | 0 | 0 | 0 | 1.0396 | 1.0396 | 3353.44 | System Service | Capacity (Lines) | Enersource | This project is to provide 27.6 KV capacity to supply developments in Truscott areas as the existing 4.16kV does not provide service size
150672 | Base | Burden Allocation - System Service | 0.10214 | 0.10598 | 0.10998 | 0.11412 | 0.11842 | 0.55064 | 3353.13 | System Service | Capacity (Lines) | Horizon
150537 | Base | Cyber Security - Upgrade access management controls | 0 | 0.33157 | 0 | 0 | 0 | 0.33157 | 3321.24 | General Plant | Information Technology | Multiple | As per Alectra Security roadmap to key IT systems with focus on end user access management controls.
150662 | Base | Station Sustainment PI System Expansion for CASCADE CARE | 0.062766 | 0 | 0 | 0 | 0 | 0.062766 | 3302.05 | General Plant | Information Technology | Multiple | Expanding the use of the PI System to enable more efficient interfaces with other enterprise systems such as OMS and SCADA; Cascade is used to drive maintenance and generate work orders for maintenance of grid equipment
151458 | M-Factor | Cable Injection Project - (V31) - Langstaff - Weston - Rutherford - Jane, Vaughan | 0 | 0 | 0 | 0.61248 | 0 | 0.61248 | 3280.12 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 1 failure in 2017.
150390 | M-Factor | New build - Waterdown 3rd Feeder, Hamilton | 0 | 1.7134 | 0 | 0 | 0 | 1.7134 | 3248.15 | System Service | Capacity (Lines) | Horizon | This project is to alleviate capacity issues in the Waterdown area of Hamilton, primarily served by two Dundas 27.6kV feeders
150263 | Base | Cable Replacement Project - East Left Behind Cable | 1.3044 | 2.7032 | 1.5672 | 3.3747 | 1.575 | 10.5246 | 3237.07 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in these areas have experienced 11 failures.
150345 | Base | Overhead Conductor Replacement - #6 Copper - Feeder WT10 | 0.43655 | 0 | 0 | 0 | 0 | 0.43655 | 3209.69 | System Service | Safety & Security | Horizon | This project consists of overhead conductor replacement to mitigate safety risk and provide additional capacity.
151416 | Base | Cable Replacement Project- Woodchester & Thorn Lodge (34), Mississauga | 0 | 0 | 0 | 2.3956 | 0 | 2.3956 | 3183.8 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 7 outages, the length is 6,669 m, and the average cable age is 49 years old.
151356 | Base | Cable Injection Project - (V44) - Langstaff - Pine Valley - Hwy 7 - Kipling, Vaughan | 0 | 0 | 0 | 0.41378 | 0 | 0.41378 | 3176.08 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 6 failures.
150601 | Base | Advanced Metering Infrastructure (AMI) Security Audit - East | 0.064598 | 0 | 0 | 0.06706 | 0 | 0.13166 | 3170.74 | System Access | Metering | Powerstream | Multi-year project to renew meter data security to address emerging cyber threats.
151440 | Base | 2020 GUELPH - Transite Underground Duct Replacement | 0.26559 | 0 | 0 | 0 | 0 | 0.26559 | 3168.07 | System Renewal | Underground Asset Renewal | Guelph | Replacement of Duct Structure which contains asbestoes a known carcinogen and impacts worker safety.
102065 | Base | Capital Corrective Equipment Replacement - East | 0.33425 | 0.33857 | 0.34293 | 0.34733 | 0.35176 | 1.7148 | 3161.46 | System Renewal | Substation Renewal | Powerstream | This project is intended to provide capital for all unplanned station equipment replacements in the East Operating Area (former PowerStream area) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
151297 | Base | Cable Replacement Project - (HAM) - Govenors - Old Ancaster | 0 | 0 | 0 | 0 | 0.99443 | 0.99443 | 3147.62 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 3 failures, or 10 failures per 100km. The average cable installation year is 1957 in this project scope.
150611 | Base | Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.16496 | 0.16692 | 0.16889 | 0.17089 | 0.17291 | 0.84457 | 3116.96 | System Renewal | Substation Renewal | Powerstream | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the East Operating Area (former PowerStream). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150524 | Base | Security Additions & Enhancements | 0 | 0 | 0 | 0.24961 | 0 | 0.24961 | 3109.96 | General Plant | Information Technology | Multiple | details refer to PWC doc
150623 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-WEST | 0.0057529 | 0.0058386 | 0.0059255 | 0.0054528 | 0.0055333 | 0.028503 | 3095.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of animal guard installation in West
150622 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-CENTRAL | 0.0068351 | 0.0058391 | 0.0059255 | 0.0054528 | 0.0055333 | 0.029586 | 3093.04 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Animal guard at Central South Stations
150621 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-EAST | 0.0086292 | 0.0082112 | 0.0083347 | 0.0073394 | 0.0074507 | 0.039965 | 3081.51 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Animal guard at East Stations
151317 | Base | Cable Injection Project - (H4) - Queen - Hwy 410 - Steeles - Kennedy, Brampton | 0 | 0 | 0 | 0.36525 | 0 | 0.36525 | 3033.4 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 2 outages due to cable failures in 2007 and 2012 with average duration of 72 minutes.
151426 | Base | Cable Replacement Project-Southdown & Lakeshore (35), Mississauga | 0 | 0 | 0 | 0 | 6.8498 | 6.8498 | 3019.59 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 3 outages, the length is 8,126 m, and the average cable age is 48 years old. There are 62 backlot transformers that we are also replacing.
150348 | Base | Overhead Conductor Replacement - #6 Copper - Feeder OT2 | 0.44008 | 0 | 0 | 0 | 0 | 0.44008 | 3017.86 | System Service | Safety & Security | Horizon | This project consists of overhead conductor replacement to mitigate safety risk and provide additional capacity
151417 | Base | Cable Replacement Project- Rathburn & Cawthra (27), Mississauga | 0 | 0 | 0 | 0.63662 | 0 | 0.63662 | 2967.95 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 8 outages, the length is 1,103 m, and the average cable age is 38 years old.
150089 | M-Factor | Markham TS#3 T1/T2 "B" Differential Protections Upgrade | 0.084239 | 0.11 | 0 | 0 | 0 | 0.19424 | 2935.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to replace the T1/T2 GEC solid state Transformer "B" Differential Protection relays at Markham TS#3 with new relays having fault recording capabilities
100632 | M-Factor | 27.6 kV Pole Line on 14th Ave from Hwy 48 to 9th Line | 0 | 0 | 0 | 2.039 | 0 | 2.039 | 2933.45 | System Service | Capacity (Lines) | Powerstream | This project consists of building new 27.6 KV pole line on 14th Avenue from HWY 48 to 9th Line. Feeders in this area are over the planning limit and existing load over planning limit and this project will redirected to alternate supply as well as supply new development.
101036 | M-Factor | Install a new 4 ccts CNR yard overhead crossing on the south side of Hwy 7 | 0 | 0 | 1.3574 | 0 | 0 | 1.3574 | 2919.48 | System Service | Capacity (Lines) | Powerstream | This project is to increase supply capacity to Vaughan Metro Center and Vaughan Mills. It will also reduce outage impact in case of pole failure on the north side of Hwy 7 crossing CN yard.
151393 | Base | 2021 GUELPH - Transite Underground Duct Replacement | 0 | 0.2713 | 0 | 0 | 0 | 0.2713 | 2917.98 | System Renewal | Underground Asset Renewal | Guelph | Replacement of Duct Structure which contains asbestoes a known carcinogen and impacts worker safety.
151208 | Base | Station Equipment Temperature Monitoring - South West | 0 | 0 | 0 | 0.015 | 0 | 0.015 | 2910.58 | System Renewal | Substation Renewal | Guelph | MULTI ANSWER
150699 | Base | Station Switchgear Replacement - Shawson MS43 LV1 | 1.056 | 0 | 0 | 0 | 0 | 1.056 | 2878.45 | System Renewal | Substation Renewal | Enersource | The existing LV1 switchgear at Shawson MS43 station houses gas circuit breakers that utilize vintage technology to provide short circuit protection against faults. These circuit breakers are technically obsolete and are prone to failure. Also the switchgear is non-arc-resistant and poses a potential safety hazard to Alectra personnel and even to the general public who happen to be in the vicinity of the station during a failure event. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions. Therefore, proactive replacement of the existing switchgear and associated equipment is a prudent strategy as the restoration of the system could take 8-10 months due to long equipment lead times in the event of a failure.
151286 | Base | Cable Replacement Project - (H2) - Wanless - Heart Lake - Bovaird - Kennedy, Brampton | 0 | 0.40495 | 1.6632 | 1.323 | 0.35875 | 3.7499 | 2867.55 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2011 to 2017 with an average duration of 126 minutes
101625 | Base | Cyber Security Audit & Upgrades | 0.065433 | 0.068676 | 0.07145 | 0.074335 | 0.075326 | 0.35522 | 2865.1 | General Plant | Information Technology | Multiple | This project would fund various activities and countermeasures to improve the cyber security posture of the Operations' Network. This will be a mandate for compliance to Ontario Cyber Security framework. The counter measures include: - an annual audit of the cyber security countermeasures in place; - implementation of new technologies to seal identified compromises; - replacement of deployed cyber security equipment deemed end of life or not able to deliver an expected level of service.
150783 | Base | Fleet_Central South Vehicle Replacement-Pick ups | 0.537 | 0.147 | 0 | 0 | 0 | 0.684 | 2848.48 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150525 | Base | Security Additions & Enhancements | 0 | 0 | 0 | 0 | 0.25325 | 0.25325 | 2842.12 | General Plant | Information Technology | Multiple | details refer to PWC doc
150671 | Base | Burden Allocation - System Renewal | 1.6642 | 1.7269 | 1.792 | 1.8595 | 1.9296 | 8.9722 | 2831.23 | System Renewal | Other System Renewal | Horizon
151107 | Base | Cable Replacement Project - 7143 Main Feeder | 0.8557 | 0 | 0 | 0 | 0 | 0.8557 | 2821.57 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 4 outages, the length is 1,325 m, and the average cable age is 39 years old.
150401 | M-Factor | 136M6 Goreway TS Extensions | 0 | 0 | 0.9804 | 0 | 0 | 0.9804 | 2821 | System Service | Capacity (Lines) | Brampton | This feeder will supply all future residential & small commercial loads around the Gore Rd., Ebenezer Rd. & Castlemore Rd. 136M6 will off load 136M4 on the south section of the area mentioned. 136M6 will off load and provide contingency for 136M4 on the south section of this area.
150632 | Base | AMI Gatekeeper Expansion - Brampton RZ | 0.029777 | 0.029884 | 0.029996 | 0.030113 | 0.030233 | 0.15 | 2820.22 | System Access | Metering | Brampton | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
151422 | Base | Cable Replacement Project-Queen St W & Paisley (30), Mississauga | 0 | 0 | 0 | 0 | 1.5333 | 1.5333 | 2819.61 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 3,992 m, and the average cable age is 36 years old.
150141 | Base | Cable Replacement Project – (M49) - Steeles and Fairway Heights, Markham | 2.9255 | 0 | 0 | 0 | 0 | 2.9255 | 2807.08 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 37 years old and will be 38 when project starts (2020).
150572 | Base | Cable Replacement Project - (J4) - Queen - Clark - Bramalea - Kensington - Knightsbridge, Brampton | 1.0937 | 0 | 0 | 0 | 0 | 1.0937 | 2794.02 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 9 outages due to cable failures from 2007 to 2017 with average duration of 127 minutes.
151311 | Base | Cable Injection Project - (E5) - Steeles - Mclaughlin - Hwy 407 - Chinguacousy, Brampton | 0 | 0 | 0.2935 | 0 | 0 | 0.2935 | 2784.8 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 2 outages due to cable failures in 2007 and 2012 with average duration of 70 minutes.
151365 | Base | Cable Injection Project - (V02) - Atkinson and Worth, Vaughan | 0 | 0 | 0 | 0 | 0.37283 | 0.37283 | 2765.48 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 1 failure.
151394 | Base | 2022 GUELPH - Transite Underground Duct Replacement | 0 | 0 | 0.27713 | 0 | 0 | 0.27713 | 2682.53 | System Renewal | Underground Asset Renewal | Guelph | Replacement of Duct Structure which contains asbestoes a known carcinogen and impacts worker safety.
151144 | Base | Cable Replacement Project and Transformers Replacement - Rathburn Rd. W, Mississauga | 1.1758 | 0 | 0 | 0 | 0 | 1.1758 | 2657.53 | System Renewal | Underground Asset Renewal | Enersource | Tis project is split into 3 phases. 2 phases are being completed in 2019, the duct structure for third phase is expected to be completed in 2019 and the final phase is will be done in 2020.
151346 | Base | Cable Injection Project - (M45) - Hwy 7 and Woodbine, Markham | 0 | 0.25087 | 0 | 0 | 0 | 0.25087 | 2649.75 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 9 failures.
150666 | M-Factor | Facilities_John_Roof Deck – Rooftop Renovation | 0.41624 | 0 | 0 | 0 | 0 | 0.41624 | 2610.29 | General Plant | Facilities Management | Horizon | Removal of cooling tower, chillers and lines that contain R-22 refrigerant (hazardous substance), replace emergency fire exit pathway on the roof from the Hughson St to the John St buildings to ensure employee safety and meet with City Bylaws. Repair roof as a result of the equipment removals.
150079 | M-Factor | Markham TS#1 T1/T2 "B" Overcurrent Protections and HMI Upgrade | 0 | 0.16325 | 0.15919 | 0 | 0 | 0.32244 | 2596.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade Markham TS#1 T1/T2 "B" Overcurrent Protections with fault recording ability and HMI Upgrade
151340 | Base | Cable Replacement Project - (V29) - Hwy 7 - Jane - Steeles - Weston, Vaughan | 0 | 0 | 0 | 0 | 4.2773 | 4.2773 | 2593.62 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 5 failures.
150374 | M-Factor | New build - 13.8kV Feeder Extension 9th Line, Derry to Argentia, Mississauga | 0 | 0 | 0 | 1.2051 | 0 | 1.2051 | 2570.63 | System Service | Capacity (Lines) | Enersource | 13.8kV OH feeder extension 9th Line from Derry Rd W to Argentia Rd in Mississauga.This will provide additional capacity for growth along 9th Line.
151427 | Base | Cable Injection- 001- AREA 11- Truscott & Southdown, Mississauga | 0 | 0.41387 | 1.3207 | 0 | 0 | 1.7346 | 2550.48 | System Renewal | Underground Asset Renewal | Enersource | There are 2 outages, we are injecting a total of 21,576 m of cable for this project, and the average age of the cable is 32 years.
150332 | M-Factor | Non-Wires Alternative Pilot | 0.77068 | 0.78661 | 0.81936 | 0.82869 | 0.83813 | 4.0435 | 2536.94 | System Service | Capacity (Stations) | Powerstream | The project will provide customers with increased flexibility to make decisions about their electricity consumption, generation, and costs; it leads to more efficient integration of DERs which yields greater benefits to customer, system reliability, and power quality. This project will also provide the opportunity to increase operational efficiency and improved asset management to enhance service to customer and defer and/or reduce infrastructure investment needs in York Region.
151042 | Base | Markham TS1 Firewall Upgrade | 0.20427 | 0 | 0 | 0 | 0 | 0.20427 | 2531.42 | System Service | System Control, Comm'ns & Performance | Powerstream | Markham TS1 Firewall Upgrade
150681 | Base | Data Analytics - IT/OT Infrastructure | 0.34691 | 0.35392 | 0 | 0 | 0 | 0.70083 | 2527.57 | General Plant | Information Technology | Multiple | This project will develop a data analytics platform to provide enhanced customer value by implementing preventative measures to improve overall outage detection and prediction with use-cases focusing on Distributed Energy Resource (DER) monitoring, integration and optimization.
151421 | Base | Cable Replacement Project-Rathkeale Rd & Edenrose St (6), Mississauga | 0 | 0 | 0 | 0 | 2.81 | 2.81 | 2502.05 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 8,577 m, and the average cable age is 31 years old.
150580 | Base | West Region Tools and Test Equipment | 0.20228 | 0.20458 | 0.20691 | 0.20927 | 0.21165 | 1.0347 | 2494.28 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
150627 | Base | Station Equipment Temperature Monitoring-EAST | 0.075261 | 0.076305 | 0.077354 | 0.07841 | 0.079471 | 0.3868 | 2479.48 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of Station Temperature Monitoring system in Central North and it enables controlled emergency loading beyond the nameplate rating.
150629 | Base | Station Equipment Temperature Monitoring-WEST | 0.075261 | 0.076305 | 0.077354 | 0.07841 | 0.079471 | 0.3868 | 2479.48 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of Station Temperature Monitoring system in West and it enables controlled emergency loading beyond the nameplate rating.
150095 | M-Factor | Vaughan TS#1 T1/T2 "B" Differential Protections Upgrade | 0 | 0 | 0.089941 | 0.11583 | 0 | 0.20577 | 2477.83 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the current T1/T2 ASEA solid state Transformer "B" Differential Protection relays at Vaughan TS#1 with new relays having fault recording capabilities
151202 | Base | Purchase of Major Station Tools - Multi-year | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.05 | 2472.82 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
151342 | Base | Cable Injection Project - (M40) - Major Mackenzie - Warden - 16th - Woodbine, Markham | 0 | 0.21433 | 0 | 0 | 0 | 0.21433 | 2470.32 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 16 failures.
151419 | Base | Cable Replacement Project- Thomas St & Hillside (24), Mississauga | 0 | 0 | 0 | 1.8379 | 0 | 1.8379 | 2467.12 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 4,089 m, and the average cable age is 30 years old.
151395 | Base | 2023 GUELPH - Transite Underground Duct Replacement | 0 | 0 | 0 | 0.28309 | 0 | 0.28309 | 2460.85 | System Renewal | Underground Asset Renewal | Guelph | Replacement of Duct Structure which contains asbestoes a known carcinogen and impacts worker safety.
150625 | Base | Purchase of Major Tools - Muliti Year-CENTRAL | 0.021644 | 0.02189 | 0.022139 | 0.022391 | 0.022646 | 0.11071 | 2395 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150624 | Base | Purchase of Major Tools - Muliti Year-EAST | 0.021644 | 0.02189 | 0.022139 | 0.022391 | 0.022646 | 0.11071 | 2395 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150626 | Base | Purchase of Major Tools - Muliti Year-WEST | 0.021644 | 0.02189 | 0.022139 | 0.022391 | 0.022646 | 0.11071 | 2395 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
151221 | Base | Metering - AMI Hardware Upgrade | 0 | 0.35 | 0.35 | 0 | 0 | 0.7 | 2384.22 | System Access | Metering | Guelph | Multi-year project to expand and upgrade AMI field communication equipment to service new connections, in Guelph RZ.
150707 | Base | Alectra Station Access Harmonization - Abloy CLIQ system expansion-CENTRAL | 0.014626 | 0 | 0 | 0 | 0 | 0.014626 | 2376.26 | System Service | Safety & Security | Enersource | This project consists of upgrade to station access in Central South. Provides added security and risk mitigation for keys that are lost or stolen and provides a system that tracks key and lock cylinder usage as well provides the ability to activate and deactivate keys from an application
150705 | Base | Alectra Station Access Harmonization - Abloy CLIQ system expansion-EAST | 0.014626 | 0 | 0 | 0 | 0 | 0.014626 | 2371.05 | System Service | Safety & Security | Brampton | This project consists of upgrade to station access in Central North. Provides added security and risk mitigation for keys that are lost or stolen and provides a system that tracks key and lock cylinder usage as well provides the ability to activate and deactivate keys from an application
101761 | Base | Unforeseen Projects Initiated by the customer PS South | 0.36099 | 0.38335 | 0.4071 | 0.43233 | 0.45911 | 2.0429 | 2365.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151061 | Base | Markham TS2 Firewall Upgrade | 0.033266 | 0.21776 | 0 | 0 | 0 | 0.25103 | 2334.71 | System Service | System Control, Comm'ns & Performance | Powerstream | Markham TS2 Firewall Upgrade
151435 | Base | Cable Injection- 010 - Area 56- Derry Rd W & Ninth Line, Mississauga | 0 | 0 | 1.193 | 1.2798 | 1.3054 | 3.7782 | 2307.05 | System Renewal | Underground Asset Renewal | Enersource | There are 3 outages, we are injecting a total of 45,837 m of cable for this project, and the average age of the cable is 30 years.
151098 | Base | Station Switchgear Replacement - Battleford MS54 LV1 | 1.2679 | 0 | 0 | 0 | 0 | 1.2679 | 2296.96 | System Renewal | Substation Renewal | Enersource | The existing LV1 switchgear at Battleford MS54 station houses gas circuit breakers that utilize vintage technology to provide short circuit protection against faults. These circuit breakers are technically obsolete and are prone to failure. Also the switchgear is non-arc-resistant and poses a potential safety hazard to Alectra personnel and even to the general public who happen to be in the vicinity of the station during a failure event. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions. Therefore, proactive replacement of the existing switchgear and associated equipment is a prudent strategy as the restoration of the system could take 8-10 months due to long equipment lead times in the event of a failure.
151425 | Base | Cable Replacement Project-Rathburn Rd E & Tomken (10), Mississauga | 0 | 0 | 0 | 0 | 1.3631 | 1.3631 | 2294.54 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 10 outages, the length is 3,180 m, and the average cable age is 38 years old.
151290 | Base | Cable Replacement Project - (I3) - Bovaird - Dixie - Queen - Hwy 410, Brampton | 0 | 0.7259 | 0.7259 | 0.7259 | 0.72555 | 2.9033 | 2280.06 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 8 outages due to cable failures from 2007 to 2018 with average duration of 133 minutes.
151347 | Base | Cable Injection Project - (V40) - Teston - Weston - Major Mackenzie - Pine Valley, Vaughan | 0 | 0.19751 | 0 | 0 | 0 | 0.19751 | 2273.85 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 7 failures.
150084 | M-Factor | Markham TS#2 T1/T2 "B" Differential Protections Upgrade | 0 | 0 | 0 | 0.093418 | 0.11765 | 0.21107 | 2269.53 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the T1/T2 GEC solid state Transformer "B" Differential Protection relays at Markham TS#3 with new relays having fault recording capabilities
151396 | Base | 2024 GUELPH - Transite Underground Duct Replacement | 0 | 0 | 0 | 0 | 0.28918 | 0.28918 | 2252.14 | System Renewal | Underground Asset Renewal | Guelph | Replacement of Duct Structure which contains asbestoes a known carcinogen and impacts worker safety.
151244 | Base | Fault Indicators | 0.01 | 0.02 | 0.015 | 0.018 | 0.018 | 0.081 | 2243.02 | System Service | System Control, Comm'ns & Performance | Guelph | The scope of this project is to install Fault Indicators in Guelph. The project would include the fault indicators communicating to the existing SCADA and will improve the fault locating and improve SAIDI
150708 | Base | Alectra Station Access Harmonization - Abloy CLIQ system expansion-North&TS | 0.093238 | 0 | 0 | 0 | 0 | 0.093238 | 2235.48 | System Service | Safety & Security | Powerstream | This project consists of upgrade to station access in East. Provides added security and risk mitigation for keys that are lost or stolen and provides a system that tracks key and lock cylinder usage as well provides the ability to activate and deactivate keys from an application
151281 | Base | Cable Replacement Project - (SCH) - Lake - Linwell - Geneva - Scott | 0 | 0.99129 | 0 | 0 | 0 | 0.99129 | 2227.25 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 6 failures, or 189 failures per 100km. The average cable installation year is 1976 in this project scope.
150542 | Base | Meeting Room Transformation - IT/OT Infrastructure | 0.31036 | 0 | 0 | 0 | 0 | 0.31036 | 2222.94 | General Plant | Information Technology | Multiple | The meeting room transformation project aim to leverage and deliver automation technology for better use of the meeting space; centralized control; consistent experiences across the enterprise; and standard design of the physical space. Efficiencies will be met when meeting rooms can start on time due to the ease of use and collaboration efforts will reduce travel and health and safety concerns. With Alectra being so geographically diverse, it imperative to keep the employees off the road as much as possible to reduce the risk of injury.
151181 | Base | Cable Replacement Project - Left Behind Cable, Brampton | 0.38278 | 0.525 | 0.525 | 0.525 | 0.525 | 2.4828 | 2163.34 | System Renewal | Underground Asset Renewal | Brampton | This project is to address cables which were part of a cable injection project but were ultimately not injectable at the time of project execution. These 'left behind' segments must be addressed, if they are left in the system they could cause a failure. Customers would not only experience an outage, but question the utilities work practices as we would have addressed only a portion of the cables instead of all the cables which could cause an outage.
151070 | Base | Markham TS3 Firewall Upgrade | 0 | 0.033687 | 0.23263 | 0 | 0 | 0.26632 | 2148.93 | System Service | System Control, Comm'ns & Performance | Powerstream | Markham TS3 Firewall Upgrade
150321 | M-Factor | Voltage Conversion - Galbraith MS, Hamilton | 0 | 1.0036 | 2.289 | 0 | 0 | 3.2926 | 2139.96 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 4 outages and had 77,467 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151423 | Base | Cable Replacement Project-Old Carriage Road (33), Mississauga | 0 | 0 | 0 | 0 | 1.3717 | 1.3717 | 2103.57 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 5 outages, the length is 2,229 m, and the average cable age is 45 years old.
151192 | Base | Asset Register | 0.4815 | 0 | 0 | 0 | 0 | 0.4815 | 2082.28 | General Plant | Information Technology | Multiple | Develop an enterprise asset register application to support Asset Management requirements to manage and track movement of assets, asset demographics, equipment failures, and support asset condition assessments and business case modelling.
151341 | Base | Cable Injection Project - (M15) - 16th - Markham - 9th - Hwy 7, Markham | 0 | 0.18176 | 0 | 0 | 0 | 0.18176 | 2076.47 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 30 failures.
150096 | M-Factor | Vaughan TS#2 T1/T2 "B" Differential Protections Upgrade | 0 | 0 | 0 | 0 | 0.095821 | 0.095821 | 2074.26 | System Service | System Control, Comm'ns & Performance | Powerstream | Vaughan TS#2 T1/T2 "B" Differential Protections Upgrade
151345 | Base | Cable Injection Project - (M51) - 14th - Bayview - Steeles - Yonge, Markham | 0 | 0.18856 | 0 | 0 | 0 | 0.18856 | 2070.59 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 9 failures.
151343 | Base | Cable Injection Project - (M14) - Hwy 7 - Markham - 9th - 14th, Markham | 0 | 0.18875 | 0 | 0 | 0 | 0.18875 | 2070.43 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 10 failures.
151338 | Base | Cable Replacement Project- (BA15) - Burton - Huronia - Little - Bayview, Barrie | 0 | 0 | 0 | 0 | 3.1787 | 3.1787 | 2062.55 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 41 years old and will be 46 when project starts (2024).
150661 | Base | SS2019-Purchase and Installation of Online Transformer tap Changer Filtration Systems - CENTRAL | 0.021615 | 0 | 0 | 0 | 0 | 0.021615 | 2055.7 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of transformer tap changer filtration system in Central South
150663 | Base | Technology Changes in Control Room | 0.3279 | 0 | 0 | 0 | 0 | 0.3279 | 2052.17 | General Plant | Facilities Management | Multiple | Replace aging equipment within the Control room to ensure optimal performance in managing the distribution assets
102728 | Base | Station Switchgear Replacement - Big Bay Point MS304 | 0.23668 | 0.81486 | 0 | 0 | 0 | 1.0515 | 2051.19 | System Renewal | Substation Renewal | Powerstream | This substation project consists of replacing the existing switchgear and associated equipment, as well as the primary circuit switcher at Big Bay Point MS304. The current line-up is technically obsolete, in poor condition, and is prone to failure. A failure could affect a large number of customers and potentially result in complete loss of supply from the station, requiring load transfer to another station. Proactive replacement of the existing equipment is a prudent strategy as system reliability would be greatly affected in the event of a failure. Additionally, the restoration of the system to normal conditions could take 8-10 months due to long equipment lead times.
150675 | Base | Emerging Customer Inititated Work Central (Mississauga) | 0.15929 | 0.16916 | 0.17965 | 0.19078 | 0.2026 | 0.90147 | 2049.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150558 | Base | OT Hardware Refresh | 0 | 0.66386 | 0 | 0 | 0 | 0.66386 | 2049.01 | General Plant | Information Technology | Multiple | Current routers in PS backbone are limited to 100Mbps ports. Backbone with new hardware is operating at 1gbps. New routers need to operate at that capacity. Equipment in Barrie office is at end of life and hasn't been upgraded since before BHDI merger with PS in 2008. Equipment in Sandalwood is consumer grade unmanaged switches Mavis brocade switches will be nearing end of life. Replace unmanaged Linksys switches in LegHZ datacentres
151329 | Base | Cable Replacement Project - (V51) - Langstaff - Kipling - Hwy 7 - Hwy 27, Vaughan | 0 | 2.1672 | 0 | 0 | 0 | 2.1672 | 2048.89 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 5 failures.
101764 | Base | Road Authority Expenditure PS North | 0.96617 | 1.5272 | 1.5827 | 1.6405 | 1.7004 | 7.417 | 2038.3 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
150604 | Base | Smart Meter Network Expansion - PowerStream RZ | 0.26645 | 0.2091 | 0.21148 | 0.27577 | 0.2968 | 1.2596 | 2035.93 | System Access | Metering | Powerstream | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
151092 | Base | Distribution Automation - Central South | 0.522 | 0.538 | 0.554 | 0.57 | 0.78634 | 2.9703 | 2013.5 | System Service | SCADA and Automation | Enersource | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151030 | Base | Addition of Sensors to SCADA Controllable 44kV LISs in Brampton | 0.2591 | 0.26272 | 0.26635 | 0.27001 | 0.27368 | 1.3319 | 2012.97 | System Service | System Control, Comm'ns & Performance | Brampton | This project is to add sensors to the 44KV switches in Central North
151068 | Base | Return to Service of Smart Fault Indicators - East | 0.16648 | 0 | 0 | 0 | 0 | 0.16648 | 1998.06 | System Renewal | Substation Renewal | Powerstream | This project involves making necessary modifications to 50 previously installed SMART Fault Indicators in the East Operating Area (former PowerStream) so as to return them to service. These devices will greatly improve monitoring capability and facilitate prompt decision making during emergency situations, thus reducing outage durations.
150694 | M-Factor | Cityview microgrid enhancements | 0.045798 | 0.014869 | 0.01579 | 0.015721 | 0.015652 | 0.10783 | 1985.17 | System Service | Capacity (Lines) | Powerstream | The project is to understand how microgrids can be integrated into the distribution grid in a safe and reliable manner. The microgrid is used to evaluate integration and connection to the distribution grid, while reducing the building's load, greenhouse gas emissions, and increasing its resiliency to grid outages.
150538 | Base | Cyber Security Devices Upgrades | 0 | 0 | 0 | 0.56351 | 0 | 0.56351 | 1984.93 | General Plant | Information Technology | Multiple | This project upgrades security tools to maintain compliance with OEB Cyber Security Framework
151335 | Base | Cable Replacement Project - (BA14) - Tifffin and Hwy 400, Barrie | 0 | 0 | 0 | 2.6821 | 0 | 2.6821 | 1975.76 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 43 years old and will be 47 when project starts (2023).
102547 | M-Factor | Two Ccts on Birchmount Rd from ROW to 14th Ave | 0 | 0 | 1.5746 | 0 | 0 | 1.5746 | 1969.46 | System Service | Capacity (Lines) | Powerstream | This project is to build 2 ccts pole line on Birchmount Rd from the Right of Way (ROW) to 14th Ave. This will extend 2 feeders 26M17 and 26M18 to 14th Ave to tie with feeder 22M7/22M8 for reliability
151324 | Base | Cable Injection Project - (M3) - Castlemore - Goreway - Queen - Airport, Brampton | 0 | 0 | 0.16294 | 0 | 0 | 0.16294 | 1916.04 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 1 outage due to cable failure in 2008 with average duration of 61 minutes. The cables are 31 years old and will be at the injection eligibility threshold by the time of project execution in 2022.
151350 | Base | Cable Injection Project - (M22) - Major Machenzie - Hwy 48 - 16th - McCowan, Markham | 0 | 0 | 0.16481 | 0 | 0 | 0.16481 | 1914.52 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 4 failures.
151330 | Base | Cable Replacement Project - (A01) - Henderson - Yonge - Bloomington - Bathurst, Aurora | 0 | 1.8456 | 0 | 0 | 0 | 1.8456 | 1904.82 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 3 failures.
151321 | Base | Cable Injection Project - (J5) - Steeles - Bramalea - Hwy 407 - Dixie, Brampton | 0 | 0.13856 | 0 | 0 | 0 | 0.13856 | 1902.8 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 outage due to cable failures to date. Cables are 31 to 33 years old and will be at the injection eligibility threshold by the time of project execution in 2021.
100268 | Base | Low Voltage Transformer Bushing Replacement - Markham TS#3 - T1/T2 | 0.27397 | 0 | 0 | 0 | 0 | 0.27397 | 1882.55 | System Renewal | Substation Renewal | Powerstream | This project involves replacing end-of-life low-voltage bushings on Markham TS#3 power transformers. Bushing failure would result in environmental risk due to spilled oil and in transformer failure causing an extended power interruption.
100904 | M-Factor | Install Double Cct Pole Line on Major Mackenzie - Hwy 27 to Huntington Rd | 0 | 0 | 0 | 3.6506 | 0 | 3.6506 | 1874.19 | System Service | Capacity (Lines) | Powerstream | This project is to build two 27.6kV ccts on Major Mackenzie - Hwy 27 to Huntington Rd to supply new customers on Major Major Dr and existing customers. There is one 4.8kV single phase cct on the west half of the section and there is one 27.6kV cct (1/0 AL) on the east half the section. They don’t have sufficient capacity for future developments in the area.
101013 | Base | Planned Circuit Breaker Replacement Markham TS#3 - E & Z Buses | 0.50357 | 0.48351 | 0 | 0 | 0 | 0.98708 | 1832.29 | System Renewal | Substation Renewal | Powerstream | The existing 27.6 kV circuit breakers at Markham TS#3 have been identified in the Asset Condition Assessment (ACA) Model as requiring replacement due to obsolescence and historical failures. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions.
151224 | Base | Cable Replacement - (920) - Scottsdale Drive Subdivision, Guelph | 0.56697 | 0 | 0 | 0 | 0 | 0.56697 | 1807.87 | System Renewal | Underground Asset Renewal | Guelph
150801 | Base | Fleet_West_Vehicle Replacement_Bucket Truck 1-286 | 0.4 | 0 | 0 | 0 | 0 | 0.4 | 1804.37 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150670 | Base | SCADA FDIR | 0.11803 | 0.12046 | 0.1231 | 0.1256 | 0.12603 | 0.61322 | 1798.98 | System Service | SCADA and Automation | Multiple | Fault Detection, Isolation, and Restoration implementation, next generation of distribution automation technology. This utilizes devices which are already automated and integrates them into the OMS system such that devices perform self healing after a fault. in some cases reducing the outage time to less then 1 minute.
150539 | Base | Cyber Security Devices Upgrades | 0 | 0 | 0 | 0 | 0.57072 | 0.57072 | 1788.51 | General Plant | Information Technology | Multiple | This project upgrades security tools to maintain compliance with OEB Cyber Security Framework
150764 | Base | Fleet_West_Vehicle Replacement_Bucket Truck 1-285 | 0 | 0.4 | 0 | 0 | 0 | 0.4 | 1780.18 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151323 | Base | Cable Injection Project - (L4) - Queen - Airport - Steeles - Torbram, Brampton | 0 | 0 | 0 | 0.16725 | 0 | 0.16725 | 1746.01 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 outage due to cable failures to date. Cables are 31 years old and will be at the injection eligibility threshold by the time of project execution in 2023.
151283 | Base | Cable Replacement Project - (HAM) - Mohawk | 0 | 0.78654 | 0.80227 | 0 | 0 | 1.5888 | 1740.19 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 1 failure, or 20 failures per 100km. This area includes the 2D2X feeder which was identified as a Worst Performing Feeder in 2018. The average cable installation year is 1953 in this project scope.
150680 | M-Factor | Alectra Drive at Home | 0.4622 | 0.47974 | 0.58969 | 0.59641 | 0.6032 | 2.7312 | 1731.44 | System Service | Capacity (Lines) | Multiple | Alectra Drive at Home will demonstrate the value of integrating smart electric vehicle (EV) charging system in multi rise buildings as well as residential homes into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. It will also provide insight into the characteristics of EV Charging, how EVs can be aggregated and controlled to provide the benefit at the local, regional and provincial system levels, and customer response to these control and optimization strategies.
151201 | Base | Purchase of New Critical Spare Parts - Guelph | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.05 | 1727.97 | System Renewal | Substation Renewal | Guelph | This project involves procurement of critical spare parts for stations in the South West Operating Area (Guelph) so as to facilitate prompt repair of failed assets during emergency situations.
151333 | Base | Cable Replacement Project - (BA9) - Little - Fairview - Harvie - Ferndale, Barrie | 0 | 0 | 1.8438 | 0 | 0 | 1.8438 | 1717.62 | System Renewal | Underground Asset Renewal | Powerstream | From 2014-2018 customers in this area experienced 6 failures.
150378 | M-Factor | Rear Lot Renewal Project - East of Queen Street/North of Mill Street | 0 | 0 | 0 | 1.7925 | 0 | 1.7925 | 1698.83 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 1 outage lasting 8.6hrs per year based on 3 a year average.
150108 | Base | Low Voltage Transformer Bushing Replacement - Vaughan TS#3 - T1/T2 | 0.31615 | 0 | 0 | 0 | 0 | 0.31615 | 1677.09 | System Renewal | Substation Renewal | Powerstream | This project involves replacing end-of-life low-voltage bushings on Vaughan TS#3 power transformers. Bushing failure would result in environmental risk due to spilled oil and in transformer failure causing an extended power interruption.
150912 | Base | Unit # 362 Palfinger crane truck | 0 | 0.515 | 0 | 0 | 0 | 0.515 | 1659.67 | General Plant | Fleet Renewal | Powerstream
150619 | Base | Purchase of Critical Spare Parts - West | 0.02186 | 0.022109 | 0.022361 | 0.022616 | 0.022873 | 0.11182 | 1648.51 | System Renewal | Substation Renewal | Horizon | This project involves procurement of critical spare parts for stations in the West Operating Area (former Horizon) so as to facilitate prompt repair of failed assets during emergency situations.
150839 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-346 | 0 | 0.56 | 0 | 0 | 0 | 0.56 | 1641.93 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150844 | Base | Fleet_West_Vehicle Replacement_Bucket Truck 1-270 | 0 | 0 | 0.42 | 0 | 0 | 0.42 | 1636.32 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151295 | Base | Cable Replacement Project - (SCH) - Welland - Bunting - Carlton - Cushman | 0 | 0.22473 | 0 | 0 | 0 | 0.22473 | 1635.38 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 48 failures per 100km. The average cable installation year is 1975 in this project scope.
151385 | Base | Cable Replacement - (892) - 30-250 Janefield Ave Subdivision, Guelph | 0 | 0.65774 | 0 | 0 | 0 | 0.65774 | 1629.86 | System Renewal | Underground Asset Renewal | Guelph
151136 | Base | C55 Alectra: Optimization of Business Practices | 0.54111 | 0.59953 | 0.1605 | 0.1605 | 0.107 | 1.5686 | 1624.9 | General Plant | Information Technology | Multiple | Optimizing the current software to communicate with other systems such as the ERP will allow for more efficient and effective budgeting processes and consolidation of information allowing for consistent reporting of the information from one system.
150885 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-361 | 0 | 0 | 0.435 | 0 | 0 | 0.435 | 1624.1 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150893 | Base | Fleet_West_Vehicle Replacement_ Digger Derrick 1-342 | 0 | 0 | 0.445 | 0 | 0 | 0.445 | 1615.96 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151137 | Base | Cable Replacement Project - Main Fedeer(s) upgrade - 68F2, 68F4, 68F7, 83F5, 83F3 | 0.82593 | 0 | 0 | 0 | 0 | 0.82593 | 1614.34 | System Renewal | Underground Asset Renewal | Enersource | Only 2 outages on all of the feeders combined. If we can replace it with feeders with 4-5 failures, we can show better reliability analysis. The combined length of these feeders is 3,885 m.
151436 | Base | Cable Injection-011 - Area 58 & 59- Winston Churchill & The Collegeway, Mississauga | 1.7463 | 1.8731 | 1.9105 | 0 | 0 | 5.53 | 1614.06 | System Renewal | Underground Asset Renewal | Enersource | There are 14 outages, we are injecting a total of 69,795 m of cable for this project, and the average age of the cable is 30 years.
150333 | Base | Overhead Conductor Replacement - #6 Copper - Feeder OT8 | 0.67255 | 0 | 0 | 0 | 0 | 0.67255 | 1610.61 | System Service | Safety & Security | Horizon | This project consists of overhead conductor replacement to mitigate safety risk and provide additional capacity.
151331 | Base | Cable Replacement Project - (V41) - Stephanie Blvd, Vaughan | 0 | 1.4609 | 0 | 0 | 0 | 1.4609 | 1604.2 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 2 failures.
151139 | M-Factor | Voltage Conversion - MS-12 Hansen Rd, Brampton | 0 | 0 | 3.0541 | 2.4212 | 0 | 5.4753 | 1599.32 | System Renewal | Overhead Asset Renewal | Brampton | From 2015-2017 customers in this area experienced 29 outages and had 94,267 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151386 | Base | Cable Replacement - (278) - 31 Greengate Rd Subdivision, Guelph | 0 | 0 | 0.58954 | 0 | 0 | 0.58954 | 1596.1 | System Renewal | Underground Asset Renewal | Guelph
150902 | Base | Unit # 396 Backhoe replacement | 0.16 | 0 | 0 | 0 | 0 | 0.16 | 1591.88 | General Plant | Fleet Renewal | Powerstream
150842 | Base | Fleet_West_Vehicle Replacement_Bucket Truck 1-365 | 0 | 0.373 | 0 | 0 | 0 | 0.373 | 1584.73 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150642 | Base | Proactive Replacement of Remote Terminal Units - Central North | 0.1584 | 0.16024 | 0.16209 | 0.16397 | 0.16586 | 0.81056 | 1582.3 | System Renewal | Substation Renewal | Brampton | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the Central-North Operating Area (Brampton). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
150617 | Base | Purchase of Critical Spare Parts - Central North | 0.029219 | 0.029552 | 0.029888 | 0.030228 | 0.030573 | 0.14946 | 1568.76 | System Renewal | Substation Renewal | Brampton | This project involves procurement of critical spare parts for municipal stations in the Central North Operating Area (Brampton) so as to facilitate prompt repair of failed assets during emergency situations.
151292 | Base | Cable Replacement Project- (K4) - Queen - Torbram - Steeles - Bramalea | 0 | 1.2583 | 0 | 0 | 0 | 1.2583 | 1568.3 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 cable failure to date. Cables are 41 to 50 years old and beyond EUL.
151353 | Base | Cable Injection Project - (V41) - Kirby - Weston - Teston - Pine Valley, Vaughan | 0 | 0 | 0.11365 | 0 | 0 | 0.11365 | 1566.16 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 2 failures.
151332 | Base | Cable Replacement Project - (BA20) - Bayfield and Simcoe, Barrie | 0 | 0 | 0 | 0 | 2.0338 | 2.0338 | 1564.86 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 43 years old and will be 48 when project starts (2024).
151309 | Base | Cable Injection Project - (E3) - Bovaird - McLaughlin - Queen - Chinguacousy, Brampton | 0 | 0 | 0.12087 | 0 | 0 | 0.12087 | 1560.28 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 1 outage due to cable failure in 2015 with duration of 86 minutes.
151087 | Base | Switchgear Replacement | 0.23636 | 0.24145 | 0.24664 | 0.25194 | 0.25736 | 1.2337 | 1559.43 | System Renewal | Underground Asset Renewal | Guelph | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150618 | Base | Purchase of Critical Spare Parts - Central South | 0.03463 | 0.035024 | 0.035423 | 0.035826 | 0.036234 | 0.17714 | 1556.59 | System Renewal | Substation Renewal | Enersource | This project involves procurement of critical spare parts for stations in the Central South Operating Area (former Enersource) so as to facilitate prompt repair of failed assets during emergency situations.
151354 | Base | Cable Injection Project - (V52) - Rutherford - Kipling - Langstaff - Hwy 27, Vaughan | 0 | 0 | 0.13022 | 0 | 0 | 0.13022 | 1552.67 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 2 failures.
102077 | Base | Major repair, refurbishment, or conversions of distribution transformers | 0.030341 | 0.030687 | 0.031036 | 0.031389 | 0.031747 | 0.1552 | 1540.55 | System Renewal | Transformer Renewal | Powerstream | Transformers returned or in stores where repair/refurbishment of the unit can return it to service at a lower cost then purchase of a new unit
150883 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-374 | 0 | 0 | 0.42 | 0 | 0 | 0.42 | 1540.38 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150398 | M-Factor | Rear Lot Renewal Project - Strathcona Dr | 0 | 0 | 0 | 0 | 0.94487 | 0.94487 | 1536.61 | System Renewal | Rear Lot Conversion | Horizon | This area has had an average of 44 outages lasting 0.35hrs per year based on 3 year average.
150964 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-337 | 0 | 0 | 0 | 0.4 | 0 | 0.4 | 1530.72 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150989 | Base | Fleet_West_Vehicle Replacement_ Underground Reel Tensioner Truck 1-351 | 0 | 0 | 0 | 0.415 | 0 | 0.415 | 1519.21 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150887 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-379 | 0 | 0 | 0 | 0.438 | 0 | 0.438 | 1501.57 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151372 | Base | Cable Replacement - (451) - Country Club Dr Subdivision, Guelph | 0 | 0 | 0.381 | 0 | 0 | 0.381 | 1481.82 | System Renewal | Underground Asset Renewal | Guelph
150368 | M-Factor | New build - North Central feeders capacity (Carlton TS to Linwell Rd/Lake St) relief, St.Catharines | 0 | 0.98956 | 1.0077 | 0 | 0 | 1.9973 | 1480.62 | System Service | Capacity (Lines) | Horizon | This project is to alleviate capacity issues in the North and Central section of St.Catharines, primarily served by Carlton BY bus feeders which are over the planning limit.
151222 | Base | Concrete Structures | 0.19086 | 0.19468 | 0.19857 | 0.20254 | 0.20659 | 0.99324 | 1469.44 | System Renewal | Underground Asset Renewal | Guelph | Replacement of lids on civil structures to avoid public risk
150763 | Base | Facilities_Reno_Addiscott - Service Centre Upgrades | 0 | 0 | 0.11092 | 0 | 0 | 0.11092 | 1461.63 | General Plant | Facilities Management | Powerstream | Repairs to building envelop/walls to prevent further damage to the build infrastructure and systems that are supporting critical operational systems such as control rooms, server rooms, customer services groups, etc.
150410 | M-Factor | 42M66 OH Feeder Egress Mississauga Rd, Bovaird to CNR | 0.13232 | 0 | 0 | 0 | 0 | 0.13232 | 1457.65 | System Service | Capacity (Lines) | Brampton | 42M66 OH Feeder extension from Mississauga Rd from Bovaird Dr. to CNR Tracks to feed new developments in the area of Bovaird drive and Mississauga road.
151408 | Base | Cable Replacement Project- Burnhamthorpe & Miss. Road (13), Mississauga | 0 | 0 | 2.4484 | 0 | 0 | 2.4484 | 1429.36 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 11 outages, the length is 7,311 m, and the average cable age is 30 years old.
151320 | Base | Cable Injection Project - (I5) - Steeles - Dixie - Hwy 407 - Hwy 410, Brampton | 0 | 0 | 0 | 0.11569 | 0 | 0.11569 | 1425.74 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 outage due to cable failures to date. Cables are 31 years old and will be at injection eligibility threshold by the time of project execution in 2023.
150858 | Base | Fleet_West_Vehicle Replacement_SUVs | 0.28 | 0 | 0 | 0 | 0 | 0.28 | 1425.59 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150334 | Base | Distribution Automation - West | 0.72 | 0.72 | 0.72 | 0.72 | 0.78634 | 3.6663 | 1424.45 | System Service | SCADA and Automation | Horizon | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151371 | Base | Cable Replacement - (87) - Marksam Rd/ Rhonda Rd Subdivision, Guelph | 0 | 0.635 | 0.35 | 0 | 0 | 0.985 | 1423.41 | System Renewal | Underground Asset Renewal | Guelph
150889 | Base | Fleet_West_Vehicle Replacement_ Digger Derrick 1-333 | 0 | 0 | 0.435 | 0 | 0 | 0.435 | 1415.07 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150019 | Base | Cable Injection Project - (M41) - Woodbine and Elgin Mills, Markham | 0.11368 | 0 | 0 | 0 | 0 | 0.11368 | 1413.89 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 40 years old and will be 41 when project starts (2020).
151052 | Base | Emerging Customer Initiated Work - Relocations | 0.0919 | 0.093876 | 0.095894 | 0.097956 | 0.10006 | 0.47969 | 1412.11 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
150941 | Base | Unit # 300 Dump truck replacement | 0 | 0 | 0.13905 | 0 | 0 | 0.13905 | 1399.77 | General Plant | Fleet Renewal | Powerstream
151410 | Base | Cable Replacement Project-Roselle & Priority Cres (2), Mississauga | 0 | 0 | 1.0307 | 0 | 0 | 1.0307 | 1390.9 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 7 outages, the length is 3,006 m, and the average cable age is 43 years old.
151308 | Base | Cable Injection Project - (HAM) - Hollybush - Parkside - Dundas - Spring Creek | 0 | 0 | 0 | 0 | 0.11531 | 0.11531 | 1389.43 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 1 failure, or 5 failures per 100km. The average cable installation year is 1988 in this project scope.
151207 | Base | On-line Dissolved Gas Monitoring | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 1386.01 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of installation of Online DGA monitoring system at MS in Guelph. Online DGA has proven to be invaluable in diagnosing a potential transformer failure as well as assessing the health of a transformer
150751 | Base | Facilities_East_Capital Replacement Investment Support | 0.099527 | 1.1888 | 0.52232 | 0.090175 | 0.069647 | 1.9705 | 1374.32 | General Plant | Facilities Management | Powerstream | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150641 | Base | Replace 230kV Primary Switches - Jim Yarrow TS | 0.17015 | 0 | 0 | 0 | 0 | 0.17015 | 1372.72 | System Renewal | Substation Renewal | Brampton | The primary switches at Jim Yarrow TS are non-standard, have a history of problems, particularly with alignment issues, and have no spare parts on hand. Failure of one of these switches could result in loss of supply to a 125 MVA power transformer.
150965 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-256 | 0 | 0 | 0 | 0 | 0.46 | 0.46 | 1370.9 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150982 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-299 | 0 | 0 | 0 | 0 | 0.46 | 0.46 | 1370.9 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151134 | Base | Cable Replacement Project - Winston Churchill consolidation - 49F6 and 49F4 | 0.31889 | 0 | 0 | 0 | 0 | 0.31889 | 1358.05 | System Renewal | Underground Asset Renewal | Enersource | This project is already with design. We are not doing this like-for-like. Miron has completed D10-111-001 for removal of the bad feeders.
151288 | Base | Cable Replacement Project - (H4) - Queen - Hwy 410 - Steeles - Kennedy, Brampton | 0 | 0.5859 | 0.5859 | 0.58625 | 0 | 1.7581 | 1353.9 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2009 to 2018 with average duration of 189 minutes.
150349 | Base | Overhead Conductor Replacement - #6 Copper - Feeder WL1 | 0.70615 | 0 | 0 | 0 | 0 | 0.70615 | 1347.16 | System Service | Safety & Security | Horizon | This project consists of overhead conductor replacement to mitigate safety risk and provide additional capacity
150830 | Base | Fleet_West_Vehicle Replacement_Dump Truck_1-330 | 0.07 | 0 | 0 | 0 | 0 | 0.07 | 1345.36 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151296 | Base | Cable Injection Project - (SCH) - Welland - Bunting - Carlton - Cushman | 0.26447 | 0 | 0 | 0 | 0 | 0.26447 | 1345.07 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 48 failures per 100km. The average cable installation year is 1989 in this project scope.
151357 | Base | Cable Injection Project - (V34) - Kirby - Jane - Teston - Weston, Vaughan | 0 | 0 | 0 | 0.072513 | 0 | 0.072513 | 1342.87 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 1 failure.
150335 | Base | Pole Renewal - West | 2.1503 | 2.4306 | 2.7171 | 3.0097 | 3.1763 | 13.484 | 1338.4 | System Renewal | Overhead Asset Renewal | Horizon | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
150795 | Base | Fleet_Central South Vehicle Replacement- 244-08 S Bucket | 0 | 0.49 | 0 | 0 | 0 | 0.49 | 1329.29 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150362 | M-Factor | Voltage Conversion - Dufferin St S, between MS431 and Albert St S, Alliston | 0.38517 | 0 | 0 | 0 | 0 | 0.38517 | 1328.26 | System Renewal | Overhead Asset Renewal | Powerstream | Customers in this area experienced 11 outages and had 15,031,879 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151374 | Base | Cable Replacement - (893) - Janefield Ave Subdivision, Guelph | 0 | 0 | 0 | 0 | 0.61733 | 0.61733 | 1324.84 | System Renewal | Underground Asset Renewal | Guelph
151387 | Base | Cable Replacement - (833) - 295 Water St Subdivision, Guelph | 0 | 0 | 0 | 0.59393 | 0 | 0.59393 | 1319.63 | System Renewal | Underground Asset Renewal | Guelph
151337 | Base | Cable Replacement Project - (BA18) - Ferndale and Benson, Barrie | 0 | 0 | 0 | 1.023 | 0 | 1.023 | 1318.19 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 41 years old and will be 45 when project starts (2023).
151326 | Base | Cable Replacement Project - (V44) - Hayhoe - Islington - Hwy 7, Vaughan | 0 | 0.82285 | 0 | 0 | 0 | 0.82285 | 1311.54 | System Renewal | Underground Asset Renewal | Powerstream | From 2016-2019YTD customers in this area experienced 6 failures.
102102 | Base | Enterprise File Synchronization and Sharing Platform | 0.012509 | 0.025319 | 0.025608 | 0 | 0 | 0.063436 | 1307.59 | General Plant | Information Technology | Multiple | Alectra is looking for a secure Enterprise File Synchronization and Sharing solution that will increase productivity of internal and external teams by facilitating seamless collaboration of corporate data anywhere , anytime, and on any device without the restrictions of having to connect to the Alectra network. The overarching goal of this implementation will be to provide a balance between delivering business productivity and securing enterprise information.
151388 | Base | Cable Replacement - (724) - 30 Hadati Rd, Guelph | 0 | 0 | 0 | 0 | 0.7606 | 0.7606 | 1302.79 | System Renewal | Underground Asset Renewal | Guelph
151291 | Base | Cable Replacement Project - (I4) - Queen - Dixie - Steeles - Hwy 410, Brampton | 0 | 0 | 0 | 0 | 1.4805 | 1.4805 | 1302.23 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 cable failure to date. Cables are 41 to 42 years old and beyond EUL.
150963 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-224 | 0 | 0 | 0 | 0 | 0.56 | 0.56 | 1298.62 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150502 | Base | On-Line Dissolved Gas Oil Monitoring of 10 MS Transformers - EAST | 0.10319 | 0.10459 | 0 | 0 | 0 | 0.20778 | 1292.71 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Online DGA monitoring system at MS in East. Online DGA has proven to be invaluable in diagnosing a potential transformer failure as well as assessing the health of a transformer
150738 | Base | Facilities_West_Capital Replacement Investment Support | 0.77379 | 0.26347 | 0.2651 | 1.7576 | 0.50803 | 3.568 | 1289.1 | General Plant | Facilities Management | Horizon | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150330 | M-Factor | Rear Lot Renewal Project - Marsdale, St.Catharines | 0 | 0 | 0 | 1.0693 | 2.0204 | 3.0897 | 1284.11 | System Renewal | Rear Lot Conversion | Horizon | This area has had an average of 19 outages lasting 1hr per year based on 3 year average.
150355 | M-Factor | Voltage Conversion - Elmwood MS, Hamilton | 0 | 0 | 0 | 0 | 2.8196 | 2.8196 | 1274.55 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 23 outages and had 251,178 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
150573 | Base | Oracle ULA Extension | 1.5 | 1.5 | 0 | 0 | 0 | 3 | 1265.44 | General Plant | Information Technology | Multiple | MULTI ANSWER
151358 | Base | Cable Injection Project - (V62) - Kirby - Hwy 27 - Nashville - Huntington, Vaughan | 0 | 0 | 0 | 0.090468 | 0 | 0.090468 | 1265.18 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 1 failure.
150790 | Base | Fleet_Central South Vehicle Replacement-Puller/Tensioner | 0 | 0.2 | 0.2 | 0.2 | 0 | 0.6 | 1264.62 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150350 | Base | Overhead Conductor Replacement - #6 Copper - Feeder WL4 | 0.80059 | 0 | 0 | 0 | 0 | 0.80059 | 1260.56 | System Service | Safety & Security | Horizon | This project consists of overhead conductor replacement to mitigate safety risk and provide additional capacity
151138 | M-Factor | Voltage Conversion - MS-2 Church St, Brampton | 3 | 1.42 | 0 | 0 | 0 | 4.42 | 1255.22 | System Renewal | Overhead Asset Renewal | Brampton | From 2015-2017 customers in this area experienced 11 outages and had 20,372 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
102241 | Base | Proactive Replacement of Remote Terminal Units - East | 0.099693 | 0.10121 | 0.10274 | 0.1043 | 0.10588 | 0.51381 | 1239.66 | System Renewal | Substation Renewal | Powerstream | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the East Operating Area (former PowerStream). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
151183 | Base | OH Rebuild Project - Church Street | 0.80925 | 0 | 0 | 0 | 0 | 0.80925 | 1238.59 | System Renewal | Overhead Asset Renewal | Enersource | This project involves the replacment of 55 poles, 35 which are in very poor and poor condition. Due to the significantly high population of poor poles this area is a candidate for multi-pole line faliure under high winds.
150422 | M-Factor | 136M9 Feeder Extension Castlemore Rd, Goreway Dr to McVean Dr | 0 | 0 | 0.13341 | 0 | 0 | 0.13341 | 1232.89 | System Service | Capacity (Lines) | Brampton | This project provides 136M9 capacity along Castlemore Dr from Goreway Dr to McVean Dr., and McVean will bring greenfield capacity up to Mayfield Rd to service north east Brampton. 136M9 in future will connect to and provide offloading and contingency for 136M8 and 136M42 which are at approching planning limit.
151146 | Base | Cable Replacement and Transformers Replacement - Project - Folkway, Mississauga | 3.981 | 0 | 0 | 0 | 0 | 3.981 | 1228.76 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 34 outages, the length is 10,432 m
150323 | M-Factor | Station Switchgear Replacement - Bloor MS38 LV1 | 0 | 0 | 0 | 0 | 0.69081 | 0.69081 | 1228.09 | System Renewal | Substation Renewal | Enersource | Bloor MS is centrally located, supplying a large number of customers, and reliability is very important. This switchgear is non-arc-resistant and poses a potential safety hazard to Alectra personnel and even to the general public who happen to be in the vicinity of the station during a failure event. The circuit breakers that are housed in the switchgear prone to failure and are considered obsolete (no longer supported by the manufacturer and parts are difficult to come by). Obsolescence translates into more frequent and more lengthy maintenance requirements and longer outage duration in the event of a failure. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted reactive capital expenditure.
150877 | Base | Fleet_ Central North Vehicle Replacement S/Bucket 7109 | 0 | 0 | 0.47 | 0 | 0 | 0.47 | 1222.49 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151282 | Base | Cable Replacement Project - (SCH) - Weiden | 0 | 0.19476 | 0 | 0 | 0 | 0.19476 | 1218.42 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 6 failures, or 962 failures per 100km. The average cable installation year is 1978 in this project scope.
150529 | Base | OT GIS & OMS Software Upgrade | 0 | 0 | 0 | 0.28826 | 0 | 0.28826 | 1210.24 | General Plant | Information Technology | Multiple | Requried upgrades to our customer facing GIS and OMS systems to ensure product support and security patches.
150814 | Base | Fleet_West_Vehicle Replacement_Step Vans 1-279 & 1-281 | 0.4 | 0 | 0 | 0 | 0 | 0.4 | 1179.47 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151064 | Base | Secondary Pedestals -St. Catharines | 0.19496 | 0.19915 | 0.20343 | 0.20781 | 0.21227 | 1.0176 | 1153.93 | System Service | Safety & Security | Horizon | This project involves the replacment of above grade steel secondary pedestals which pose a safety risk to the general public
150044 | M-Factor | Rear Lot Renewal Project - Blake/Kempenfelt | 0.30779 | 0 | 0 | 0 | 0 | 0.30779 | 1144.48 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 0.66 outages lasting 2.2hrs per year based on a 3 year average.
151312 | Base | Cable Injection Project - (F2) - Wanless - Main - Bovaird - McLaughlin, Brampton | 0 | 0 | 0.044625 | 0 | 0 | 0.044625 | 1139.85 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 cable failure to date. Cables will be at the injection eligibility threshold by the time of project execution in 2022.
150254 | M-Factor | Cable Replacement Project - (A02) - Steeplechase Ave, Aurora | 2.892 | 0 | 0 | 0 | 0 | 2.892 | 1133.22 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 outages to date. Cable is 45 years old and beyond EUL
150862 | Base | Fleet_Central North Vehicle Replacement-RBD 57 | 0 | 0.55 | 0 | 0 | 0 | 0.55 | 1125.31 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151322 | Base | Cable Injection Project - (K4) - Queen - Torbram - Steeles - Bramalea, Brampton | 0 | 0.062063 | 0 | 0 | 0 | 0.062063 | 1124.92 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 1 outage due to cable failure in 2007.
101125 | Base | Lines Mobile Equipment - IT/OT Infrastructure | 0.078888 | 0.079786 | 0.080695 | 0.083706 | 0.076963 | 0.40004 | 1119.08 | General Plant | Information Technology | Multiple | This budget covers the deployment of mobile technology - laptops/field tablets and accessories - within the Lines Department to gain efficiencies in field operations. By deploying this technology, the Lines area can move away from a paper-based to a more electronic environment. In future, it is envisioned that, for example, mobile applications will facilitate the electonic transmission of work orders and electronic record keeping (asset tracking, tailboards, switching orders, timesheets). This will allow for streamlined operational processes and record-keeping, thereby supporting corporate technological initiatives such as the GIS, Outage Management System, and future Workforce Management system. At present, all Lines Management personnel and Subforemen have laptops, facilitating activities such as viewing of the GIS, electronic Asset Tracking Forms, and use of OMS Responder Mobile. Expenditures in this area will allow for more deployment of field devices among Lines crews and for the implementation of more computerized processes.
150500 | Base | On-Line Dissolved Gas Oil Monitoring of 10 MS Transformers - WEST | 0.10319 | 0.20859 | 0.106 | 0 | 0 | 0.41777 | 1116.55 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of Transformer bushing monitoring system in West
150856 | Base | Fleet_West_Vehicle Replacement_Dump/Cargo Truck | 0.14 | 0 | 0 | 0 | 0 | 0.14 | 1114.55 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150908 | Base | Fleet East Unit # 103 Bucket truck replacement | 0.25 | 0 | 0 | 0 | 0 | 0.25 | 1107.23 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151405 | Base | Cable Replacement Project- Erin Mills & N.Sheridan (16), Mississauga | 0 | 1.2009 | 0 | 0 | 0 | 1.2009 | 1104.63 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 8 outages, the length is 3,326 m, and the average cable age is 45 years old.
150139 | Base | Cable Replacement Project – (B19) - Donald St and Simcoe Terrace, Barrie | 0.5793 | 0 | 0 | 0 | 0 | 0.5793 | 1101.95 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 44 years old and will be 45 when project starts (2020).
150570 | Base | Alectra West Substation Ground Grid Installations | 0.28056 | 0.28943 | 0.29858 | 0.30802 | 0 | 1.1766 | 1091.19 | System Service | Safety & Security | Horizon | This project is to install ground grid at East Stations
151204 | Base | Upgrade to Station Facilities (Buildings/Civil work) Multi-year | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.05 | 1089.29 | General Plant | Facilities Management | Guelph | This project involves work involving structural components of stations, including windows, brickwork, roofs, foundations, drainage, doors, etc. at stations in the SouthWest Operational Area. Not keeping up with this work would result in advanced deterioration resulting in even greater maintenance costs, potential safety concerns and potential failure of the electrical equipment in the building causing power interruptions.
150879 | Base | Fleet East Vehicle replacement - Pickup 2500 | 0.21218 | 0 | 0 | 0 | 0 | 0.21218 | 1086.88 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
103198 | Base | BizTalk Upgrade - IT Infrastructure | 0 | 0 | 0.27416 | 0.26158 | 0 | 0.53574 | 1085.47 | General Plant | Information Technology | Multiple | Upgrade existing BizTalk to latest version. We currently have a development, test, and Production environment.
151434 | Base | Cable Injection- 009- AREA 54- Highway 401 & Argentia, Mississauga | 0 | 0 | 0 | 2.5247 | 0 | 2.5247 | 1085.23 | System Renewal | Underground Asset Renewal | Enersource | There are 0 outages, we are injecting a total of 30,642 m of cable for this project, and the average age of the cable is 30 years.
151284 | Base | Cable Replacement Project - (E3) - Bovaird - McLaughlin - Queen - Chinguacousy, Brampton | 0 | 0 | 0 | 0.68985 | 0 | 0.68985 | 1081.89 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 cable failure to date. Cables will be at the injection eligibility threshold by the time of project execution in 2023.
151293 | Base | Cable Replacement Project - (SCH) - Lakeshore - Stanley - Parnell - Chancery | 0 | 0.87706 | 0 | 0 | 0 | 0.87706 | 1080.5 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 55 failures per 100km. The average cable installation year is 1978 in this project scope.
151327 | Base | Cable Replacement Project - (BR6) - 8th and Dissette, Bradford | 0 | 0.3612 | 0 | 0 | 0 | 0.3612 | 1077.44 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 6 failures.
150752 | Base | Cityview back up generator replacement | 0.41269 | 0 | 0 | 0 | 0 | 0.41269 | 1071.5 | General Plant | Facilities Management | Powerstream
150794 | Base | Fleet_Central South Vehicle Replacement- 229-09 S/Bucket | 0 | 0 | 0.49 | 0 | 0 | 0.49 | 1070.69 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150806 | Base | Fleet_Central South Vehicle Replacement-207-09 S/bucket | 0 | 0 | 0 | 0.49 | 0 | 0.49 | 1068.7 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151041 | Base | Protection Logic Upgrades - East MSs (North) | 0.080038 | 0.082351 | 0.084705 | 0.087103 | 0 | 0.3342 | 1061.11 | System Service | System Control, Comm'ns & Performance | Powerstream
151373 | Base | Cable Replacement - (923) - Scottsdale Drive Subdivision, Guelph | 0 | 0 | 0 | 0.755 | 0 | 0.755 | 1060.3 | System Renewal | Underground Asset Renewal | Guelph
150758 | M-Factor | Facilities_Reno_Staff Relocation from Jane St | 0 | 0 | 0.55459 | 0 | 0 | 0.55459 | 1060.04 | General Plant | Facilities Management | Brampton | Required renovations to the Cityview building to accommodate employees from various Alectra groups currently at Jane St, reducing the need to continue the office space lease at Jane St. The Jane St office lease expires in 2021 and would not be renewed, reducing operating expenditures.
150859 | Base | Fleet_West_Vehicle Replacement_Cargo Vans | 0 | 0.16 | 0 | 0 | 0 | 0.16 | 1059.81 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150865 | Base | Fleet_West_Vehicle Replacement_Pickups | 0 | 0.165 | 0 | 0 | 0 | 0.165 | 1055.49 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151406 | Base | Cable Replacement Project- Rathburn Rd W & Queenbridge (8), Mississauga | 0 | 0.27904 | 0 | 0 | 0 | 0.27904 | 1052.58 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 4 outages, the length is 857 m, and the average cable age is 40 years old.
151003 | Base | Fleet_West_Vehicle Replacement_Pickups | 0 | 0 | 0 | 0 | 0.057 | 0.057 | 1041.55 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150762 | Base | Facilities_Reno_Patterson - Service Centre Upgrades | 0 | 0.10858 | 0 | 0 | 0 | 0.10858 | 1035.79 | General Plant | Facilities Management | Powerstream | Repairs to building envelop/walls to prevent further damage to the build infrastructure and systems that are supporting critical operational systems such as control rooms, server rooms, customer services groups, etc.
100919 | M-Factor | Install 2nd 27.6 kV Cct on Woodbine Ave from Elgin Mills Rd to 19th Ave | 0 | 0.64108 | 0 | 0 | 0 | 0.64108 | 1027.78 | System Service | Capacity (Lines) | Powerstream | This project is to add one additional 27.6kV cct on the existing pole line from Elgin Mills Rd to 19th Ave that has provision for 2nd cct to increase capacity in the 19th and woodbine area as well as the Future Urban area
151157 | Base | Fleet_West_Vehicle Replacement_Dump/Cargo Truck | 0 | 0.2 | 0 | 0 | 0 | 0.2 | 1025.25 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150354 | M-Factor | Voltage Conversion - Eastmount MS, Hamilton | 0 | 0 | 0 | 0 | 3.752 | 3.752 | 1021.7 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 43 outages and had 2,261,630 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
150578 | Base | Alectra - Microsoft Software | 0.1 | 0.10229 | 0.10345 | 0 | 0 | 0.30575 | 1020.9 | General Plant | Information Technology | Multiple | Compliance for Alectra employees for Microsoft application suite of products to perform daily operation .
151334 | Base | Cable Replacement Project - (BA13) - Dunlop and Miller, Barrie | 0 | 0.4011 | 0 | 0 | 0 | 0.4011 | 1009.91 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 41 years old and will be 43 when project starts (2021).
150776 | Base | Fleet_Central South Equipment Replacement-forklift | 0.045 | 0 | 0 | 0 | 0 | 0.045 | 1006.1 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150257 | M-Factor | Cable Replacement Project - (V15) - Jardin Dr, Vaughan | 2.9337 | 0 | 0 | 0 | 0 | 2.9337 | 1004.3 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 5 outages.
150937 | Base | Fleet_West_Vehicle Replacement_Cargo/Passenger Vans. | 0 | 0 | 0.039 | 0.04 | 0 | 0.079 | 995.47 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150392 | Base | Storage Upgrade | 0.703 | 0.30687 | 1.2885 | 0 | 0 | 2.2984 | 994.99 | General Plant | Information Technology | Multiple | Upgrade on premise Enterprise Storage platform in addition to increased capacity requirements as a result of employee and customer demand for data retention. Off Premise storage costs (SharePoint Online, One Drive, Development, test and production environments)
150916 | Base | Fleet East Vehicle replacement - Extended Vans | 0.10687 | 0 | 0 | 0 | 0 | 0.10687 | 987.32 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151091 | Base | Switchgear Renewal - Central South | 3.611 | 3.6886 | 3.7679 | 3.849 | 3.9317 | 18.8483 | 982.44 | System Renewal | Underground Asset Renewal | Enersource | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150983 | Base | Fleet East Vehicle replacement - Pickup truck 1500 | 0 | 0 | 0 | 0.32459 | 0 | 0.32459 | 982.4 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150882 | Base | Fleet East Vehicle replacement - Pickup 3500 | 0.20229 | 0 | 0 | 0 | 0 | 0.20229 | 973.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150380 | M-Factor | Rear Lot Renewal Project - Gunn/Oakley Park/St.Vincent | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 966.87 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 1 outage lasting 13hrs per year based on a 3 year average.
150890 | Base | Fleet East Vehicle replacement - Work van | 0.0618 | 0 | 0 | 0 | 0 | 0.0618 | 966.83 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151159 | Base | Fault Indicator Installation and Replacement - Hamilton and St. Catharines | 0.26813 | 0.2739 | 0.27979 | 0.2858 | 0.29195 | 1.3996 | 966.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of fault indicator installation in West
150628 | Base | Station Equipment Temperature Monitoring-CENTRAL | 0 | 0.077185 | 0.078244 | 0.07931 | 0.080381 | 0.31512 | 965.25 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of Station Temperature Monitoring system in Central South and this enables controlled emergency loading beyond the nameplate rating.
150815 | Base | Fleet_Central South Vehicle Replacement-Trailers | 0 | 0 | 0 | 0.087 | 0 | 0.087 | 960.75 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150929 | Base | Fleet East Vehicle replacement - Pickup truck 3500 | 0 | 0.5245 | 0 | 0 | 0 | 0.5245 | 957.25 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151294 | Base | Cable Injection Project - (SCH) - Lakeshore - Stanley - Parnell - Chancery | 0.062817 | 0 | 0 | 0 | 0 | 0.062817 | 953.78 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 55 failures per 100km. The average cable installation year is 1985 in this project scope.
151287 | Base | Cable Replacement Project - (SCH) - Bolger - Elma - Dorothy - The Meadows | 0 | 0.44633 | 0 | 0 | 0 | 0.44633 | 952.98 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 10 failures, or 322 failures per 100km. The average cable installation year is 1976 in this project scope.
150947 | Base | Fleet_West_Vehicle Replacement_ Pickups | 0 | 0 | 0 | 0 | 0.057 | 0.057 | 952.45 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151065 | Base | Manhole Lid Replacement | 0.25592 | 0.34856 | 0.35606 | 0.36371 | 0.37153 | 1.6958 | 925.3 | System Renewal | Underground Asset Renewal | Horizon | Replacement of lids on civil structures to avoid public risk
150911 | Base | Fleet East Unit # 81 Single bucket truck replacement | 0.46062 | 0 | 0 | 0 | 0 | 0.46062 | 923.32 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150900 | Base | Fleet_West_Vehicle Replacement_ Step Vans | 0 | 0 | 0 | 0.36 | 0 | 0.36 | 917.53 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150981 | Base | Fleet East Vehicle replacement - Pickup truck 2500 | 0 | 0 | 0 | 0.52167 | 0 | 0.52167 | 913.9 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151156 | Base | Fleet_West_Vehicle Replacement_Step Vans | 0 | 0 | 0.38 | 0 | 0 | 0.38 | 913.53 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151280 | Base | Cable Injection Project - (SCH) - Millward - Jeanette Drive - Trevor | 0.046588 | 0 | 0 | 0 | 0 | 0.046588 | 909.23 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 333 failures per 100km. The average cable installation year is 1992 in this project scope.
150361 | M-Factor | Airport 88M5 & 88M7 HONI Purchase | 0 | 0 | 0 | 0.53902 | 0 | 0.53902 | 905.21 | System Service | Capacity (Lines) | Enersource | Hydro One owns the OH Feeders from Richview TS to the CN rails approximately 6100m away. 88M5 and 88M7 would transfer ownership from HONI to Alectra to reliably supply to airport.
150932 | Base | Fleet East Vehicle replacement - SUV | 0 | 0 | 0.19133 | 0 | 0 | 0.19133 | 905.06 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151017 | Base | Fleet_West_Vehicle_Replacement_Tensioner Trailers | 0 | 0 | 0 | 0.391 | 0 | 0.391 | 893.75 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150781 | Base | Fleet_Central South Replacement-Tractor 301-08 | 0 | 0 | 0.2 | 0 | 0 | 0.2 | 893.48 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150819 | Base | Fleet_West_Vehicle Replacement_Cargo Vans 1-347, 1-350, 1-368, 1-349, 1-110, 1-111, 1-114 | 0.35 | 0 | 0 | 0 | 0 | 0.35 | 890.03 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150969 | Base | Fleet East Vehicle replacement - SUV/Van | 0 | 0 | 0 | 0.23649 | 0 | 0.23649 | 884.61 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150892 | Base | Fleet East Vehicle replacement - Van pool vans | 0.0824 | 0 | 0 | 0 | 0 | 0.0824 | 875.45 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150317 | M-Factor | Voltage Conversion - Deerhurst MS, Hamilton | 2.9645 | 2.5985 | 2.249 | 0 | 0 | 7.8121 | 869.07 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 6 outages and had 121,838 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151279 | Base | Cable Injection Project - (SCH) - Jacobson - Chestnut - Woodcrest | 0 | 0 | 0 | 0 | 0.12859 | 0.12859 | 866.07 | System Renewal | Underground Asset Renewal | Horizon | Customers in this area have experienced 0 underground XLPE cable outages to date. The average cable installation year is 1991. Since this project is in 2024, the cable will now be 8 years over the TUL while simultaneously pushing the boundary of Area 2 as a candidate for injection (see Figure A10 - 8: XLPE Cable by Type in Exhibit 04, Tab 01, Schedule 01, Appendix A10, Page 14)
150974 | Base | Fleet East Vehicle replacement - Forklift | 0 | 0 | 0.16 | 0 | 0 | 0.16 | 862.99 | General Plant | Fleet Renewal | Powerstream | Asset replacement due to poor conditions and age and lack of parts replacement. Equipment not as available to support capital system renewal projects and respond to emergencies with material handling. .
150923 | Base | Fleet_Central North Vehicle Replacement-DBL.Bucket 49 | 0.56 | 0 | 0 | 0 | 0 | 0.56 | 854.86 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150943 | Base | Fleet East Vehicle replacement - Extended Van | 0 | 0 | 0.25921 | 0 | 0 | 0.25921 | 849.79 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150904 | Base | Fleet East Yearly Light and Misc equipment | 0.017219 | 0.03655 | 0.055658 | 0.023516 | 0.02 | 0.15294 | 846.86 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150935 | Base | Fleet East Vehicle replacement - Pickup truck 1500 | 0 | 0 | 0.15756 | 0 | 0 | 0.15756 | 846.65 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150780 | Base | Fleet_Central South Replacement-DBL>Bucket 234-05 | 0.58 | 0 | 0 | 0 | 0 | 0.58 | 844.63 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150698 | Base | Station Switchgear Replacement - City Centre South MS61 LV1 | 0 | 0 | 0 | 0 | 0.42073 | 0.42073 | 843.66 | System Renewal | Substation Renewal | Enersource | City Centre South MS is located centrally adjacent to Square One shopping mall, and feeds a large number of customers. Therefore, reliability is very important. This project involves replacing the existing LV1 13.8 kV switchgear with new arc-rated switchgear and new circuit breakers. It also includes upgrading the transformer protection and replacing end-of-life feeder egress cables. The existing equipment line-up is technically obsolete, poses safety and environmental risks, and is prone to failure. Proactive replacement of the existing equipment is a prudent strategy as system reliability would be greatly affected in the event of a failure. Additionally, the restoration of the system to normal conditions could take 8-10 months due to long equipment lead times.
150914 | Base | Fleet East Vehicle replacement - Pickup truck 1500 | 0 | 0.038244 | 0 | 0 | 0 | 0.038244 | 841.88 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151285 | Base | Cable Replacement Project - (G2) - Wanless - Kennedy - Bovaird - Main, Brampton | 0 | 0 | 0 | 0 | 0.7602 | 0.7602 | 841.27 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 1 outage due to cable failure in 2007 with duration of 82 minutes. The cables are 41 to 43 years old and beyond EUL.
150907 | Base | Fleet East Unit # 361 digger truck | 0.55167 | 0 | 0 | 0 | 0 | 0.55167 | 839.82 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150910 | Base | Fleet East Unit # 91 Single bucket truck replacement | 0 | 0.48131 | 0 | 0 | 0 | 0.48131 | 838.95 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150262 | M-Factor | Cable Replacement Project - (M33) - 16th Avenue and Village Parkway, Markham | 0 | 0 | 2.0987 | 0 | 0 | 2.0987 | 834.98 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 1 failure. From 2015-2019 YTD customers in this area experienced 3 failures. Cable is 42 years old.
150909 | Base | Fleet East Unit # 115 Single bucket truck replacement | 0 | 0 | 0.4 | 0 | 0 | 0.4 | 834.56 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150817 | Base | Fleet_Central South Vehicle Replacement-230-11 S/bucket | 0 | 0 | 0 | 0.53 | 0 | 0.53 | 830.28 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150834 | Base | Fleet East Vehicle replacement - Unit # 500 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150835 | Base | Fleet East Vehicle replacement -Unit # 507 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150836 | Base | Fleet East Vehicle replacement -Unit # 515 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150837 | Base | Fleet East Vehicle replacement -Unit # 522 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150838 | Base | Fleet East Vehicle replacement -Unit # 534 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150867 | Base | Fleet East Vehicle replacement -Unit # 535 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150840 | Base | Fleet East Vehicle replacement -Unit # 536 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150841 | Base | Fleet East Vehicle replacement -Unit # 537 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150845 | Base | Fleet East Vehicle replacement -Unit # 549 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150829 | Base | Fleet East Vehicle replacement -Unit # 553 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151149 | Base | Fleet East Vehicle replacement - Unit 523 SUV | 0.03607 | 0 | 0 | 0 | 0 | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150915 | Base | Fleet East Vehicle replacement - Pickup truck 1500 | 0.037131 | 0 | 0 | 0 | 0 | 0.037131 | 824.23 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150917 | Base | Fleet East Vehicle replacement - Passenger Van | 0.0412 | 0 | 0 | 0 | 0 | 0.0412 | 820.5 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151163 | Base | Fleet_West_Vehicle Replacement_ Passenger Van_1-370 | 0 | 0 | 0.039 | 0 | 0 | 0.039 | 807.37 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150746 | Base | Facilities_Central_Capital Replacement Investment Support | 0 | 0 | 0.38361 | 1.5044 | 0.46001 | 2.348 | 807.27 | General Plant | Facilities Management | Multiple | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150913 | Base | Fleet East Vehicle replacement - Cube Vans | 0 | 0 | 0.78286 | 0 | 0 | 0.78286 | 806.41 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151469 | M-Factor | Cable Replacement Project - (F4-G4) - Main - Steeles - Chinguacousy - Queen, Brampton | 0 | 0 | 0 | 0 | 0.9804 | 0.9804 | 804.25 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 86 failures. Exact number of failures in recent years is unknown at this moment.
151466 | M-Factor | Cable Replacement Project - (V24) - Langstaff - Jane - Rutherford - Keele, Vaughan | 0 | 0 | 0 | 0 | 0.98581 | 0.98581 | 800.33 | System Renewal | Underground Asset Renewal | Powerstream | From 2015-2019 YTD customers in this area experienced 0 failures. From 2013-2019 YTD customers in this area experienced 2 failures.
151468 | M-Factor | Cable Replacement Project - (V51) - Langstaff - Kipling - Hwy 7 - Hwy 27, Vaughan | 0 | 0 | 0 | 0 | 0.98784 | 0.98784 | 798.87 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 1 failure. From 2015-2019 YTD customers in this area experienced 5 failures.
150866 | Base | Fleet_ Central North Vehicle Replacement -Forklift 178 | 0 | 0.075 | 0 | 0 | 0 | 0.075 | 791.81 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151431 | Base | Cable Injection- 006- AREA 39- Erin Mills Pkway & Thomas St, Mississauga | 0 | 0 | 0 | 1.8205 | 1.3744 | 3.1948 | 786.04 | System Renewal | Underground Asset Renewal | Enersource | There are 0 outages, we are injecting a total of 38,448 m of cable for this project, and the average age of the cable is 30 years.
150946 | Base | Fleet East Vehicle replacement - Van pool vans | 0 | 0 | 0.13113 | 0 | 0 | 0.13113 | 782.26 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150805 | Base | Fleet_Central South Vehicle Replacement-206-09 S/bucket | 0 | 0 | 0.49 | 0 | 0 | 0.49 | 781.51 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150939 | Base | Fleet East Unit # 105 Bucket truck replacement | 0 | 0 | 0.21115 | 0 | 0 | 0.21115 | 781.04 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150788 | Base | Fleet_Central South Vehicle Replacement-Arrowboard | 0.012 | 0 | 0 | 0 | 0 | 0.012 | 765.85 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
101622 | Base | DACS Inverters and RTU's removal - East | 0.026229 | 0.026659 | 0.054178 | 0.05504 | 0.027952 | 0.19006 | 765.32 | System Renewal | Substation Renewal | Powerstream | This project involves removal of obsolete and out-of-service DACs inverters, RTUs and associated wiring at stations in the East Operating Area (former PowerStream) so as to remove clutter, thus simplifying future work and freeing up space for future station upgrades.
150779 | Base | Fleet_Central South Replacement-DBL.Bucket 228-05 | 0 | 0.58 | 0 | 0 | 0 | 0.58 | 763.21 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150864 | Base | Fleet_Central North Vehicle Replacement_Loader 175 | 0 | 0.09 | 0 | 0 | 0 | 0.09 | 762.45 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150824 | Base | Fleet_West_Vehicle Replacement_Pickups. | 0.22 | 0 | 0 | 0 | 0 | 0.22 | 758.91 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150881 | Base | Fleet_ Central North Vehicle Replacement DBL.Bucket 7808 | 0 | 0 | 0 | 0.6 | 0 | 0.6 | 749.12 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150765 | Base | Facilities_Reno_Vansickle - Service Centre Upgrades | 0 | 0 | 0 | 0.1133 | 0 | 0.1133 | 745.86 | General Plant | Facilities Management | Horizon | Repairs to building envelop/walls to prevent further damage to the build infrastructure and systems that are supporting critical operational systems such as control rooms, server rooms, customer services groups, etc.
150971 | Base | Fleet East Vehicle replacement - Pickup truck 2500 | 0 | 0 | 0.18055 | 0 | 0 | 0.18055 | 742.02 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
101632 | Base | Obsolete Revenue Metering Removal from TSs | 0.026466 | 0.027144 | 0.055667 | 0.057071 | 0.02925 | 0.1956 | 739.84 | System Service | Safety & Security | Powerstream | Evolution of the distribution system to permit more efficient integration of DERs to yield 18
150979 | M-Factor | Fleet East Vehicle replacement - Extended Vans | 0 | 0 | 0 | 0 | 0.23805 | 0.23805 | 737.95 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150996 | Base | Fleet East Vehicle replacement - Pickup truck 1500 | 0 | 0 | 0 | 0 | 0.16716 | 0.16716 | 729.23 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151072 | M-Factor | Station Service Transfer Upgrade - Vaughan TS#3 | 0.1185 | 0 | 0 | 0 | 0 | 0.1185 | 725.89 | System Renewal | Substation Renewal | Powerstream | This project involves replacing the manual station service transfer switch with an automatic transfer switch. This work will mitigate the risk of loss of the entire station due to DC system failure as occurred in March 2016, thus avoiding another major lengthy power interruption.
150921 | Base | Fleet East Unit # 123 83' Double Bucket | 0 | 0.6111 | 0 | 0 | 0 | 0.6111 | 717.92 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150799 | Base | Fleet_Central South Vehicle Replacement- Reel Carrier | 0 | 0 | 0.29 | 0 | 0 | 0.29 | 716.12 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151178 | M-Factor | Cable Replacement Project - Mason Heights | 0.71457 | 0 | 0 | 0 | 0 | 0.71457 | 715.85 | System Renewal | Underground Asset Renewal | Enersource | From 2015-2017 customers in this area experienced 5 outages. 1 cable with 4 failures. 2 cables with 2 failures.
150970 | Base | Fleet East Vehicle replacement - Van pool vans | 0 | 0 | 0 | 0.13506 | 0 | 0.13506 | 714.37 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150922 | Base | Fleet East Unit # 59 digger truck | 0 | 0.56822 | 0 | 0 | 0 | 0.56822 | 714.31 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151467 | M-Factor | Cable Replacement Project - (V17) - Langstaff - Keele - Rutherford - Dufferin, Vaughan | 0 | 0 | 0 | 0 | 2.4213 | 2.4213 | 702.73 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 3 failures. From 2015-2019 YTD customers in this area experienced 4 failures.
150925 | Base | Fleet East Vehicle replacement - Cube Vans | 0 | 0.2387 | 0 | 0 | 0 | 0.2387 | 701.21 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150827 | Base | Fleet_West_Equipment Replacement_Backhoe | 0.09 | 0 | 0 | 0 | 0 | 0.09 | 699.29 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150869 | Base | Fleet_ Central North Vehicle Replacement-Puller/tensioner 194 | 0.25 | 0 | 0 | 0 | 0 | 0.25 | 692.98 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151082 | Base | SCADA Infrastructure | 0.14814 | 0.10358 | 0.14914 | 0.14082 | 0.14662 | 0.6883 | 688.19 | System Service | System Control, Comm'ns & Performance | Guelph
150706 | Base | Alectra Station Access Harmonization - Abloy CLIQ system expansion-WEST | 0.014595 | 0 | 0 | 0 | 0 | 0.014595 | 685.59 | System Service | Safety & Security | Horizon | This project consists of upgrade to station access in West
151191 | Base | Facilities_Reno_Nebo - Service Centre Upgrades | 0 | 0 | 0 | 0 | 0.11574 | 0.11574 | 685.17 | General Plant | Facilities Management | Horizon | Repairs to building envelop/walls to prevent further damage to the build infrastructure and systems that are supporting critical operational systems such as control rooms, server rooms, customer services groups, etc.
151058 | Base | Distribution Transformer Replacements & Upgrades | 0.34158 | 0.34892 | 0.35642 | 0.36409 | 0.37191 | 1.7829 | 682.68 | System Renewal | Transformer Renewal | Guelph | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150719 | Base | Upgrade of JMUX Optical Interfaces - Alectra East SONET Ring | 0.25695 | 0.25995 | 0 | 0 | 0 | 0.5169 | 676.42 | System Service | System Control, Comm'ns & Performance | Powerstream
151005 | Base | Fleet_West_Vehicle Replacement_Cargo Van | 0 | 0 | 0 | 0 | 0.057 | 0.057 | 674.03 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150669 | Base | Burden Allocation - System Access | 0.60623 | 0.62907 | 0.65278 | 0.67738 | 0.7029 | 3.2684 | 669.62 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150377 | M-Factor | Voltage Conversion and Rear Lot - Montgomery Dr, Hamilton | 0 | 0 | 1.8248 | 0 | 0 | 1.8248 | 661.01 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 71 outages and had 7,403,242 minutes of interruption. This project also addresses rear lot assets which are extrememly difficult to replace if they fail due to complexities of access issues and restricitions for equipment to rebuild the assets.
150894 | Base | Fleet_ Central North Vehicle Replacement S/Bucket 3110 | 0 | 0 | 0 | 0.51 | 0 | 0.51 | 655.77 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151048 | Base | Station Switchgear Replacement - City Centre North MS47 HV1 | 0.32554 | 0 | 0 | 0 | 0 | 0.32554 | 655.68 | System Renewal | Substation Renewal | Enersource | City Centre North MS is located centrally adjacent to Square One shopping mall, and feeds a large number of customers. It also provides back up to City Centre South MS – hence, reliability is very important. This substation project consists of replacing the HV1 44 kV switchgear and associated breaker and protection in City Centre North MS47. The current transformer protection device consists of a vintage 1973 Markham Electric oil with spring actuator type 44 kV circuit breaker. Station subject matter experts have identified this breaker as problematic. Parts are no longer available and this equipment is prone to failure. Proactive replacement of the LV switchgear, circuit breakers and protective equipment is a prudent strategy as system reliability would be greatly affected in the event of a failure. Additionally, the restoration of the system to normal conditions could take 8-10 months due to long equipment lead times.
150792 | Base | Fleet_Central South Vehicle Replacement- RBD 109-07 | 0 | 0 | 0 | 0.57 | 0 | 0.57 | 652.63 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150966 | Base | Fleet East Unit # 124 83' Double Bucket | 0 | 0 | 0.63555 | 0 | 0 | 0.63555 | 651.33 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150962 | M-Factor | Fleet East Unit # 61 Digger truck replacement | 0 | 0 | 0 | 0 | 0.44558 | 0.44558 | 643.77 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
102166 | Base | SQL Expansion - IT Infrastructure | 0.094522 | 0.46031 | 0.062073 | 0.06278 | 0.1978 | 0.87748 | 635.85 | General Plant | Information Technology | Multiple | Expand existing SQL infrastructure to meet project demands and natural growth of database. Add system capacity, improve performance, and reduce the risk of downtime due resource constraints.
150818 | M-Factor | Fleet_Central South Vehicle Replacement-236-10 S/bucket | 0 | 0 | 0 | 0 | 0.51 | 0.51 | 635.35 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150980 | M-Factor | Fleet East Vehicle replacement - Work Van | 0 | 0 | 0 | 0 | 0.067528 | 0.067528 | 622.46 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150942 | M-Factor | Fleet_ Central North Vehicle Replacement_S/Bucket | 0 | 0 | 0 | 0 | 0.53 | 0.53 | 620.9 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150807 | M-Factor | Fleet_Central South Vehicle Replacement-209-09 S/bucket | 0 | 0 | 0 | 0 | 0.53 | 0.53 | 620.9 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150863 | Base | Fleet_Central North Vehicle Replacement-S/Bucket 70 | 0 | 0.49 | 0 | 0 | 0 | 0.49 | 620.35 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150933 | Base | Fleet_ Central North Vehicle Replacement Stake Trucks | 0 | 0 | 0.27 | 0 | 0 | 0.27 | 615.92 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150203 | Base | Station Equipment Temperature Monitoring-NORTH & TS | 0.063979 | 0.065041 | 0.064777 | 0.065617 | 0.066463 | 0.32588 | 614.42 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of Station Temperature Monitoring system in East and it enables controlled emergency loading beyond the nameplate rating.
150945 | M-Factor | Fleet_ Central North Vehicle Replacement_Reel Carriers | 0 | 0 | 0 | 0 | 0.67 | 0.67 | 613.76 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150803 | M-Factor | Fleet_Central South Vehicle Replacement- Material Handler | 0 | 0 | 0 | 0 | 0.55 | 0.55 | 606.44 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150976 | Base | Fleet East Unit # 365 digger truck | 0 | 0 | 0 | 0.61903 | 0 | 0.61903 | 604.13 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150977 | Base | Fleet East Unit # 366 digger truck | 0 | 0 | 0 | 0.61903 | 0 | 0.61903 | 604.13 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150896 | M-Factor | Fleet_ Central North Vehicle Replacement S/Bucket 8910 | 0 | 0 | 0 | 0 | 0.53 | 0.53 | 595.61 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150871 | M-Factor | Fleet_Central North Vehicle Replacement-Step Van 8108 | 0.22 | 0 | 0 | 0 | 0 | 0.22 | 594.61 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150880 | Base | Fleet_ Central North Vehicle Replacement Tractor 7708 | 0 | 0 | 0.2 | 0 | 0 | 0.2 | 592.75 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150496 | Base | iPass Project Management – Planned Capital - West | 0.69089 | 0.69705 | 0.70328 | 0.70959 | 0.71596 | 3.5168 | 589.28 | System Renewal | Underground Asset Renewal | Horizon | Help in optimizing DER performance and efficiency to improve addressing overall energy needs.
150846 | M-Factor | Fleet_West_Vehicle Replacement_Step Vans | 0.36 | 0 | 0 | 0 | 0 | 0.36 | 589.19 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150732 | Base | Vault Cover Rehabilitation | 0.10916 | 0 | 0 | 0 | 0 | 0.10916 | 582.22 | System Renewal | Underground Asset Renewal | Powerstream | Replacement of lids on civil structures to avoid public risk
150967 | M-Factor | Fleet East Unit # 125, 83' Double Bucket | 0 | 0 | 0 | 0.66097 | 0 | 0.66097 | 580.18 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150978 | M-Factor | Fleet East Vehicle replacement - Cube Vans | 0 | 0 | 0 | 0 | 0.7483 | 0.7483 | 579.7 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150876 | M-Factor | Fleet_Central North Vehicle Replacement_ Step Vans 6310 | 0 | 0.25 | 0 | 0 | 0 | 0.25 | 567.71 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150953 | M-Factor | Fleet_ Central North Vehicle Replacement_Trailer 11510 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 566.09 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102046 | Base | Purchase of Major Tools - Muliti Year-North & TS | 0.045452 | 0.045969 | 0.046493 | 0.046601 | 0.047132 | 0.23165 | 565.1 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150793 | M-Factor | Fleet_Central South Vehicle Replacement-210-09 S/bucket | 0 | 0.49 | 0 | 0 | 0 | 0.49 | 560.3 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151209 | M-Factor | Station LED Lighting Upgrades - South West | 0 | 0 | 0 | 0 | 0.002 | 0.002 | 555.75 | System Renewal | Substation Renewal | Guelph | Replacement of inefficient lighting fixtures and lamps at Guelph stations will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
151128 | M-Factor | MS Transformer & HV Switchgear Replacement - Western MS36 T1 & HV1 | 0 | 0 | 0 | 0.2037 | 0.58825 | 0.79196 | 553.77 | System Renewal | Substation Renewal | Enersource | Recent testing has indicated possible mechanical damage to the transformer windings and the HV switchgear has suffered damage due to a prior failure. The station is in a residential area and a transformer failure could result in a fire, posing a risk to the community and collateral damage to other assets in the station, as well as resulting in an extensive power interruption. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted reactive capital expenditure.
151150 | M-Factor | Fleet East Vehicle replacement - SUV | 0 | 0 | 0 | 0 | 0.040596 | 0.040596 | 550.35 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150968 | M-Factor | Fleet East Vehicle replacement Pickup truck 2500 | 0 | 0 | 0 | 0 | 0.059701 | 0.059701 | 548.54 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151206 | Base | Installation of SWI Video Security System | 0 | 0.025 | 0.01 | 0 | 0 | 0.035 | 544.35 | System Service | Safety & Security | Guelph | This project consists of installation of SWI Video security system in SouthWest. The implementation of video monitoring will ensure that station security and safety related issues can be easily identified and addressed immediately
150905 | Base | Fleet East Multi Year Shop tools | 0.0107 | 0.011035 | 0.011366 | 0.011706 | 0.012057 | 0.056864 | 544.12 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of tools and shop equipment required to repair and maintain vehicles to ensure vehicle availability to support capital systems projects.
101816 | Base | Alectra East (South), Fault Indicator Installation and Replacement Multi-year initiative | 0.23904 | 0.24416 | 0.24937 | 0.25467 | 0.26006 | 1.2473 | 542.12 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - North Region which will result improved outage response, operational efficiency, and reliability
150938 | M-Factor | Fleet_ Central North Vehicle Replacement_Stake Trucks | 0 | 0 | 0 | 0.28 | 0 | 0.28 | 539.37 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151085 | M-Factor | Rear Lot Conversions | 0.1135 | 0.11594 | 0.11843 | 0.12098 | 0.12358 | 0.59243 | 530.82 | System Renewal | Rear Lot Conversion | Guelph
101134 | Base | Alectra East (North), Fault Indicator Installation and Replacement Multi-year initiative | 0.24128 | 0.24643 | 0.25167 | 0.25699 | 0.2624 | 1.2588 | 527.43 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - South Region which will result improved outage response, operational efficiency, and reliability
150437 | Base | OT GIS & OMS Enhancements | 0.32543 | 0.35097 | 0.33467 | 0.26694 | 0.41822 | 1.6962 | 519.79 | General Plant | Information Technology | Multiple | Ongoing productivity enhancements to core GIS and OMS platforms to meet internal and customer demand for functionality.
150975 | M-Factor | Fleet East Unit # 75 83' Double Bucket | 0 | 0 | 0 | 0 | 0.68741 | 0.68741 | 513.15 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151179 | M-Factor | Cable Replacement Project - Area of Erin Mills Parkway and South Millway | 0.53426 | 0 | 0 | 0 | 0 | 0.53426 | 482.04 | System Renewal | Underground Asset Renewal | Enersource | From 2015-2017 customers in this area experienced 4 outages. 1 cable with 4 failures.
150602 | Base | Smart Meter Test Facility - PowerStream RZ | 0.019794 | 0.020075 | 0.020357 | 0.020641 | 0.041851 | 0.12272 | 471.4 | System Access | Metering | Powerstream | Multi-year project to expand the capability of the Meter Test Facility to test increasing types of meters and AMI systems before they are placed into production.
150810 | M-Factor | Fleet_Central South Vehicle Replacement-Step Vans | 0 | 0 | 0 | 0.235 | 0 | 0.235 | 461.7 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150955 | Base | Fleet_ Central North Vehicle Replacement_Arrowboards | 0 | 0 | 0 | 0 | 0.052 | 0.052 | 458.92 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150798 | M-Factor | Fleet_Central South Vehicle Replacement- Arrowboard | 0 | 0 | 0 | 0.012 | 0 | 0.012 | 450.06 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150848 | Base | Fleet_Central South Vehicle Replacement-Compressors | 0 | 0 | 0 | 0.084 | 0 | 0.084 | 449.03 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150782 | M-Factor | Fleet_Central South Vehicle Replacement-Step Van | 0.22 | 0 | 0 | 0 | 0 | 0.22 | 438.9 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150811 | M-Factor | Fleet_Central South Vehicle Replacement-Pick ups | 0 | 0 | 0.156 | 0 | 0 | 0.156 | 433.74 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151141 | M-Factor | Cable Replacement and Transformers replacement - Project - Windjammer, Mississauga | 2.7095 | 0 | 0 | 0 | 0 | 2.7095 | 432.38 | System Renewal | Underground Asset Renewal | Enersource | From 2005-2019 YTD customers in this area experienced 32 failures. This area has had an average of 2.3 outages per year.
102027 | Base | Purchase of Critical Spare Parts - Multiyear - East | 0.070612 | 0.071417 | 0.072229 | 0.073053 | 0.073884 | 0.3612 | 427.82 | System Renewal | Substation Renewal | Powerstream | This project involves procurement of critical spare parts for transformer and municipal stations in the East Operating Area (former PowerStream) so as to facilitate prompt repair of failed assets during emergency situations.
150576 | M-Factor | Split the 1/0 loop on Cityview Blvd into two loops | 0 | 0 | 0.4529 | 0 | 0 | 0.4529 | 422.68 | System Service | Capacity (Lines) | Powerstream | This project is to split the 1/0 loop on Cityview Blvd into two loops. As of 2019, there is 18.5MVA connected kVA on the loop: 12MVA on the residential side and 6.5 MVA on the commercial side with 1865 residential and 93 commerical customers.
101781 | Base | iPass Project Management – Planned Capital - East | 0.38201 | 0.39019 | 0.39851 | 0.40696 | 0.41556 | 1.9932 | 408.86 | System Renewal | Overhead Asset Renewal | Powerstream | Estimating the effects of DER contribution at the feeder and region levels to further optimize the energy flows between the Utility and its consumers,
150494 | Base | iPass Project Management – Planned Capital - Central-North | 0.37996 | 0.38599 | 0.39204 | 0.39812 | 0.40422 | 1.9603 | 408.86 | System Renewal | Overhead Asset Renewal | Brampton | Predicting the influence of weather conditions and DER contribution simultaneously on the power grid, for proactively mitigating local outages,
150495 | Base | iPass Project Management – Planned Capital - Central-South | 0.37996 | 0.38599 | 0.39204 | 0.39812 | 0.40422 | 1.9603 | 408.86 | System Renewal | Overhead Asset Renewal | Enersource | Enable better visibility towards preventive equipment maintenance needs arising due to DER penetration which will further help mitigate outage risks,
150607 | M-Factor | Station LED Lighting Upgrades - Central | 0.026572 | 0.026953 | 0.027335 | 0.027719 | 0.028104 | 0.13668 | 407.91 | System Renewal | Substation Renewal | Enersource | Replacement of inefficient lighting fixtures and lamps at stations in the Central Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150606 | M-Factor | Station LED Lighting Upgrades - EAST | 0.026572 | 0.026953 | 0.027335 | 0.027719 | 0.028104 | 0.13668 | 407.91 | System Renewal | Substation Renewal | Brampton | Replacement of inefficient lighting fixtures and lamps at stations in this Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
151013 | M-Factor | Fleet_West_Vehicle_Replacement_Bucket Truck_1-354 | 0 | 0 | 0 | 0.4 | 0 | 0.4 | 407.29 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151158 | M-Factor | Fleet_Central South_Vehicle Replacement -Vans | 0.081 | 0 | 0 | 0 | 0 | 0.081 | 407.26 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151132 | M-Factor | MS Transformer & HV Switchgear Replacement - Munden MS35 T1 & HV1 | 0 | 0 | 0 | 0.20424 | 0.6564 | 0.86064 | 405.83 | System Renewal | Substation Renewal | Enersource | Recent testing has indicated that the transformer insulation has deteriorated and lacks a proper foundation and is beginning to lean. The station is in a residential area and a transformer failure could result in a fire, posing a risk to the community and collateral damage to other assets in the station, as well as resulting in an extensive power interruption. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted reactive capital expenditure.
150786 | M-Factor | Fleet_Central South Vehicle Replacement-SUV | 0.035 | 0 | 0 | 0 | 0 | 0.035 | 403.38 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150868 | M-Factor | Fleet_Central North Vehicle Replacement-180 Loader | 0.29 | 0 | 0 | 0 | 0 | 0.29 | 399.89 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150518 | Base | Upgrade to Station Facilities (Building / Civil work) Multi-year - Central | 0 | 0 | 0 | 0 | 0.12161 | 0.12161 | 399.38 | System Renewal | Substation Renewal | Enersource | MULTI ANSWER
150517 | Base | Upgrade to Station Facilities (Building / Civil work) Multi-year - West | 0 | 0 | 0 | 0 | 0.12161 | 0.12161 | 399.38 | System Renewal | Substation Renewal | Horizon | MULTI ANSWER
151168 | M-Factor | Fleet_Central South Vehicle Replacement-Step Vans | 0 | 0 | 0 | 0 | 0.735 | 0.735 | 395.07 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150399 | M-Factor | Rear Lot Renewal Project - Richlieu Dr and Trelawne Dr, St.Catharines | 0 | 0 | 0 | 1.2633 | 1.1574 | 2.4207 | 392.54 | System Renewal | Rear Lot Conversion | Horizon | This area has had an average of 40 outages lasting 1.5hrs per year based on 3 year average.
151212 | M-Factor | Driveway Paving Multi-year initiative - South West | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 391 | System Renewal | Substation Renewal | Guelph | These driveways at Guelph stations that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150138 | M-Factor | Cable Replacement Project – (BA23-BA24) - Cook St and Steel St, Barrie | 0 | 0 | 0 | 1.707 | 0 | 1.707 | 389.44 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 43 years old. Project is in 2023 so it will be over EUL by 6 years.
150920 | M-Factor | Fleet East Vehicle addition - Van pool van | 0.0412 | 0 | 0 | 0 | 0 | 0.0412 | 386.61 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150831 | M-Factor | Fleet_West_Vehicle Replacement_SUVs_1-268,1-226,1-227 | 0.12 | 0 | 0 | 0 | 0 | 0.12 | 376.22 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150513 | Base | Installation of SWI Video security system at 4 MS stations per year - Annual Multi-year initiative-EAST | 0.15244 | 0.11992 | 0 | 0 | 0 | 0.27236 | 372.49 | System Service | Safety & Security | Brampton | This project consists of installation of SWI Video security system in CentralNorth
151007 | M-Factor | Fleet_West_Vehicle_Replacement_Trailers | 0 | 0 | 0 | 0 | 0.06 | 0.06 | 366.82 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150608 | M-Factor | Station LED Lighting Upgrades - West | 0 | 0 | 0 | 0.02813 | 0.02852 | 0.05665 | 359.12 | System Renewal | Substation Renewal | Horizon | Replacement of inefficient lighting fixtures and lamps at stations in the West Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150356 | M-Factor | Voltage Conversion - Clarkson Area, Mississauga | 0 | 0 | 0 | 0 | 2.7147 | 2.7147 | 358.78 | System Renewal | Overhead Asset Renewal | Enersource | From 2015-2017 customers in this area experienced 35 outages and had 91,638 minutes of interruption.
150951 | M-Factor | Fleet East Vehicle addition - Van pool van | 0 | 0.042436 | 0 | 0 | 0 | 0.042436 | 344.51 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102034 | Base | Upgrade to Station Facilities (Building / Civil work) Multi-year - East | 0.1326 | 0.13419 | 0.1358 | 0.13741 | 0.13905 | 0.67906 | 339.91 | System Renewal | Substation Renewal | Powerstream | MULTI ANSWER
150854 | M-Factor | Fleet_Central South Vehicle Replacement-Trailers | 0 | 0 | 0 | 0 | 0.175 | 0.175 | 330.19 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150813 | M-Factor | Fleet_Central South Vehicle Replacement-SUV | 0 | 0 | 0 | 0 | 0.1065 | 0.1065 | 330.13 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150797 | M-Factor | Fleet_Central South Vehicle Replacement- SUV | 0 | 0 | 0.102 | 0 | 0 | 0.102 | 325.75 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150550 | Base | ServiceNow Expansion - IT Infrastructure | 0 | 0.058664 | 0 | 0 | 0 | 0.058664 | 325.33 | General Plant | Information Technology | Multiple | Building and adding features within ServiceNow we will eliminate outdated processes by automating more tasks and decisions allowing us to be more efficient and productive. Enhancements include the automation of the flow of data between other systems and across programs used by various departments and ServiceNow. Servicebots will be used as ServiceNow learns from past patterns, in order to predict future outcomes, including determining risks, assigning owners, and categorizing work. Learned models set the category of the IT request and assign the task to the right team, as well as calculate associated risk of action or inaction. This capability will improve the speed and efficiency of IT service delivery.
150549 | Base | ServiceNow Expansion - IT Infrastructure | 0.057851 | 0 | 0 | 0 | 0 | 0.057851 | 322.89 | General Plant | Information Technology | Multiple | Building and adding features within ServiceNow we will eliminate outdated processes by automating more tasks and decisions allowing us to be more efficient and productive. Enhancements include the automation of the flow of data between other systems and across programs used by various departments and ServiceNow. Servicebots will be used as ServiceNow learns from past patterns, in order to predict future outcomes, including determining risks, assigning owners, and categorizing work. Learned models set the category of the IT request and assign the task to the right team, as well as calculate associated risk of action or inaction. This capability will improve the speed and efficiency of IT service delivery.
150575 | Base | OT Scada map Cleanup | 0 | 0.46031 | 0 | 0 | 0 | 0.46031 | 315.81 | General Plant | Information Technology | Multiple | SCADA Map clean up program to ensure accuracy and safety in the SCADA environment.
150501 | Base | On-Line Dissolved Gas Oil Monitoring of 20 MS Transformers - CENTRAL | 0 | 0 | 0 | 0 | 0.22262 | 0.22262 | 313.42 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Transformer bushing monitoring system in Central South
150712 | Base | New JMUX Node at AMS4 | 0.10085 | 0 | 0 | 0 | 0 | 0.10085 | 311.33 | System Service | System Control, Comm'ns & Performance | Powerstream | New JMUX Node at AMS4
150873 | M-Factor | Fleet_Central North Vehicle Replacement_Vans | 0 | 0.108 | 0 | 0 | 0 | 0.108 | 308.34 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150741 | Base | Facilities_Replacement_Patterson Road Roof | 0 | 0 | 0 | 0 | 1.2188 | 1.2188 | 307.59 | General Plant | Facilities Management | Powerstream | Building roofs have exceeded the project useful life. Various decaying roof conditions identified need to be addressed to prevent further damage to the building envelope, structure and assets.
150884 | M-Factor | Fleet_Central North Vehicle Replacement Pick up 9514 | 0 | 0.052 | 0 | 0 | 0 | 0.052 | 299.15 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102537 | Base | Insulator Replacement - 44kV Multi year project | 0.1524 | 0 | 0 | 0 | 0 | 0.1524 | 294.58 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of non-polymer insulators (Areas are prioritiezed by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
150100 | Base | Convert Three MS's in Bradford to WiMax Communications | 0.022747 | 0 | 0 | 0 | 0 | 0.022747 | 294.32 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of conversion of three Bradford MS to Wimax communication
150531 | Base | OT GIS Hardware Refresh | 0 | 0 | 0 | 0.37668 | 0 | 0.37668 | 294.15 | General Plant | Information Technology | Multiple | Hardware platform refresh to support GIS infrastructure.
150101 | Base | Convert Three MS's in Alliston to WiMax Communications | 0.023069 | 0 | 0 | 0 | 0 | 0.023069 | 294.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of conversion of three Alliston MS to Wimax communication
150610 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - Central | 0.020881 | 0.021144 | 0.02141 | 0.021678 | 0.021948 | 0.10706 | 289.6 | System Renewal | Substation Renewal | Enersource | Existing driveways at stations in the Central Operational Area that are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150609 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - East | 0.020881 | 0.021144 | 0.02141 | 0.021678 | 0.021948 | 0.10706 | 289.6 | System Renewal | Substation Renewal | Brampton | Existing driveways in this Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150612 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - West | 0.020881 | 0.021144 | 0.02141 | 0.021678 | 0.021948 | 0.10706 | 289.6 | System Renewal | Substation Renewal | Horizon | Existing driveways in the West Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150870 | M-Factor | Fleet_Central North Vehicle Replacement-Van 5910 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 288.94 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150800 | M-Factor | Fleet_Central South Vehicle Replacement- trailer | 0 | 0.04 | 0 | 0 | 0 | 0.04 | 288.32 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150796 | M-Factor | Fleet_Central South Vehicle Replacement- Vans | 0 | 0 | 0.216 | 0 | 0 | 0.216 | 285.52 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150551 | Base | ServiceNow Expansion - IT Infrastructure | 0 | 0 | 0.059486 | 0 | 0 | 0.059486 | 279.25 | General Plant | Information Technology | Multiple | Building and adding features within ServiceNow we will eliminate outdated processes by automating more tasks and decisions allowing us to be more efficient and productive. Enhancements include the automation of the flow of data between other systems and across programs used by various departments and ServiceNow. Servicebots will be used as ServiceNow learns from past patterns, in order to predict future outcomes, including determining risks, assigning owners, and categorizing work. Learned models set the category of the IT request and assign the task to the right team, as well as calculate associated risk of action or inaction. This capability will improve the speed and efficiency of IT service delivery.
150552 | Base | ServiceNow Expansion - IT Infrastructure | 0 | 0 | 0 | 0.060844 | 0 | 0.060844 | 258.47 | General Plant | Information Technology | Multiple | Building and adding features within ServiceNow we will eliminate outdated processes by automating more tasks and decisions allowing us to be more efficient and productive. Enhancements include the automation of the flow of data between other systems and across programs used by various departments and ServiceNow. Servicebots will be used as ServiceNow learns from past patterns, in order to predict future outcomes, including determining risks, assigning owners, and categorizing work. Learned models set the category of the IT request and assign the task to the right team, as well as calculate associated risk of action or inaction. This capability will improve the speed and efficiency of IT service delivery.
151166 | M-Factor | Fleet_ Central North Vehicle Replacement pick ups | 0 | 0 | 0 | 0.054 | 0 | 0.054 | 244.57 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150812 | M-Factor | Fleet_Central South Vehicle Replacement-Vans | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 240.44 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102050 | Base | Various Stations-Station Lighting Upgrade/Retrofit-Energy Efficiency Lighting-initiative Multi-year - East | 0.054219 | 0.055316 | 0.056432 | 0.057565 | 0.058717 | 0.28225 | 239.8 | System Renewal | Substation Renewal | Powerstream | Replacement of inefficient indoor and outdoor lighting fixtures and lamps at stations in the East Operating Area (former PowerStream) will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
103028 | Base | Installation of a New JMUX Node at VTS1-T1T2 | 0.072623 | 0 | 0 | 0 | 0 | 0.072623 | 238.33 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of JMUX node at Vaughan TS1
151167 | M-Factor | Fleet_Central South Vehicle Replacement-Pick ups | 0 | 0 | 0 | 0 | 0.162 | 0.162 | 236.9 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150391 | Base | Wireless LAN Upgrade | 0.49548 | 0 | 0 | 0.080052 | 0 | 0.57553 | 235.12 | General Plant | Information Technology | Multiple | Corporate Wireless LAN upgrade to replace end of life wireless infrastructure in corporate and operation center locations.
150897 | M-Factor | Fleet_ Central North Vehicle Replacement pick ups | 0 | 0 | 0.054 | 0 | 0 | 0.054 | 234.38 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151075 | Base | Fuel Pump Replacement Nebo Rd. | 0.043287 | 0 | 0 | 0 | 0 | 0.043287 | 233.69 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of systems that have surpass end of life, are consistently down for repairs and parts are difficult to obtain, impacting fuel of vehicles to support capital systems projects and customer emergencies responses.
150421 | M-Factor | 2D7X Pimlico Dr - Voltage Conversion and Rear Lot | 0 | 0 | 0 | 0 | 0.57628 | 0.57628 | 233.54 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 28 outages and had 805,077 minutes of interruption. This project also addresses rear lot assets which are extrememly difficult to replace if they fail due to complexities of access issues and restricitions for equipment to rebuild the assets.
150853 | M-Factor | Fleet_Central South Vehicle Replacement-Vans | 0 | 0 | 0 | 0 | 0.228 | 0.228 | 227.74 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151155 | M-Factor | Fleet_Central South Vehicle Replacement-Pick ups | 0.065 | 0 | 0 | 0 | 0 | 0.065 | 226.53 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151164 | Base | Fleet_Central South _key box replacement | 0.03 | 0 | 0 | 0 | 0.004 | 0.034 | 223.47 | General Plant | Fleet Renewal | Enersource | Adopted the current vehicles key management system at all sites to ensure access to vehicles when required. This ensure access to vehicles after hours and tracking of vehceil keys.
151038 | Base | Fleet_West_Equipment_Key Boxes | 0.03 | 0 | 0 | 0 | 0.004 | 0.034 | 223.47 | General Plant | Fleet Renewal | Horizon | Adopted the current vehicles key management system at all sites to ensure access to vehicles when required. This ensure access to vehicles after hours and tracking of vehceil keys.
150843 | M-Factor | Fleet_Central South Vehicle Replacement-Bocat | 0 | 0 | 0 | 0.026 | 0 | 0.026 | 223.44 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150888 | M-Factor | Fleet_ Central North Vehicle Replacement SUVs | 0 | 0 | 0.0355 | 0 | 0 | 0.0355 | 223.15 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150961 | Base | Fleet_West_Vehicle Replacement_Forklift | 0 | 0.24 | 0 | 0 | 0 | 0.24 | 219.79 | General Plant | Fleet Renewal | Horizon | Asset replacement due to poor conditions and age and lack of parts replacement. Equipment not as available to support capital system renewal projects and respond to emergencies with material handling. .
100319 | M-Factor | Radial Supply Remediation/Conversion - 13.8 kV to 27.6 kV on Miller Ave | 0 | 0 | 0 | 1.5371 | 0 | 1.5371 | 207.69 | System Renewal | Overhead Asset Renewal | Powerstream | From 2015-2017 customers in this area experienced 15 outages and had 45,942 minutes of interruption. Customers in this area ona radial supply with no backup, this is atypical of Alectra Utilities customers and needs to be rectified to ensure customers here are receiving service similar to other Alectra Utiliites customers.
150891 | M-Factor | Fleet_ Central North Vehicle Replacement Car | 0 | 0 | 0.0355 | 0 | 0 | 0.0355 | 207.64 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151059 | Base | Station Switchgear Replacement - City Centre North MS47 HV2 | 0.32554 | 0 | 0 | 0 | 0 | 0.32554 | 199.27 | System Renewal | Substation Renewal | Enersource | City Centre North MS is located centrally adjacent to Square One shopping mall, and feeds a large number of customers. It also provides back up to City Centre South MS – hence, reliability is very important. The current transformer protection device consists of a vintage 1973 Markham Electric oil with spring actuator type 44 kV circuit breaker. Station subject matter experts have identified this breaker as problematic. Additionally, due to obsolescence, it is no longer supported by the manufacturer and parts are difficult to come by.
151145 | M-Factor | Cable Replacement Project - Bough Beeches Blvd. | 0.69436 | 0 | 0 | 0 | 0 | 0.69436 | 196.82 | System Renewal | Underground Asset Renewal | Enersource | From 2015-2017 customers in this area experienced 5 outages. 3 cables with 3 failures each.
150936 | Base | Fleet_ Central North Vehicle Replacement Tower Lights | 0 | 0 | 0 | 0.015 | 0 | 0.015 | 192.17 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150394 | M-Factor | King St. Voltage Conversion & Loop (LRT Betterment) | 0 | 0 | 0 | 0 | 0.32442 | 0.32442 | 191.85 | System Renewal | Overhead Asset Renewal | Enersource | From 2015-2017 customers in this area experienced 5 outages and had 61,455 minutes of interruption.
150686 | Base | Rockwood MS - Station RTU and Protection Relays Upgrade | 0.094848 | 0 | 0 | 0 | 0 | 0.094848 | 191.32 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of bus, line and transformer protection at Richmond Hill TS
150802 | Base | Fleet_Central South Vehicle Replacement- Scissor lift | 0 | 0 | 0 | 0.03 | 0 | 0.03 | 184.85 | General Plant | Fleet Renewal | Enersource | Asset replacement due to poor conditions and age and lack of parts replacement. Equipment not as available to support capital system renewal projects and respond to emergencies with material handling. .
150787 | M-Factor | Fleet_Central South Vehicle Replacement- Van | 0 | 0.05 | 0 | 0 | 0 | 0.05 | 182.88 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150944 | M-Factor | Fleet_ Central North Vehicle Replacement_Trailer | 0 | 0 | 0 | 0.12 | 0 | 0.12 | 182.44 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150822 | Base | Fleet_Central South Vehicle Replacement-Arrowboard | 0 | 0 | 0 | 0 | 0.013 | 0.013 | 178.68 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150326 | Base | Software Asset Management as a Service | 0 | 0 | 0 | 0 | 0.06223 | 0.06223 | 173.23 | General Plant | Information Technology | Multiple | The Software Asset Management module of ServiceNow will enable the creation of an accurate, up to date, single system of record for IT infrastructure, both on premises and in public clouds. It will identify IP‑enabled configuration items (CIs), map their interdependencies, and populate and maintain them in the ServiceNow Configuration Management Database (CMDB). Software spend across the year will be more predictable, and access to software agreements will be more efficient. Auditing of agreements will be more manageable. The implementation will all better control over the complexity of our software assets, allowing us to optimize the use of these assets.
150153 | Base | Bradford MS324-F2 Reconductor - Holland Street | 0 | 0 | 0 | 0 | 0.035154 | 0.035154 | 169.19 | System Service | Capacity (Lines) | Powerstream | This project is to reconductor MS324f2 feeder to increase capacity and meet contingency requirements. Increase the ampacity of the existing section of 13.8kV feeder along Holland Street by reconductoring the existing 3/0 Al with 336 Al from Langford Drive to Professor Day
150825 | Base | Line & Transformer Protection Migration to DNP - Jim Yarrow TS | 0 | 0 | 0.10439 | 0.10407 | 0 | 0.20846 | 164.32 | System Renewal | Substation Renewal | Brampton | This is part of a multi-phase project to upgrade aging and failure-prone protection systems at Jim Yarrow TS to the current protection standards. Proper protection to transmission lines will provide protection to the assets in the case of faults.
150512 | M-Factor | Installation of SWI Video security system at 4 MS stations per year - Annual Multi-year initiative-CENTRAL | 0 | 0 | 0 | 0 | 0.16523 | 0.16523 | 163.78 | System Service | Safety & Security | Enersource | This project consists of installation of SWI Video security system in Central South. The implementation of video monitoring will ensure that station security and safety related issues can be easily identified and addressed immediately
150511 | M-Factor | Installation of SWI Video security system at 4 MS stations per year - Annual Multi-year initiative-WEST | 0 | 0 | 0 | 0 | 0.16522 | 0.16522 | 163.78 | System Service | Safety & Security | Horizon | This project consists of installation of SWI Video security system in West. The implementation of video monitoring will ensure that station security and safety related issues can be easily identified and addressed immediately
150519 | M-Factor | Upgrade to Station Facilities (Building / Civil work) MultiYear - East | 0 | 0 | 0 | 0 | 0.12387 | 0.12387 | 156.08 | System Renewal | Substation Renewal | Brampton | This project involves work involving structural components of stations, including windows, brickwork, roofs, foundations, drainage, doors, etc. at stations in the East Operational Area. Not keeping up with this work would result in advanced deterioration resulting in even greater maintenance costs, potential safety concerns and potential failure of the electrical equipment in the building causing power interruptions.
151382 | Base | 2022 GUELPH - Fleet | 0 | 0 | 0.6 | 0 | 0 | 0.6 | 151.48 | General Plant | Fleet Renewal | Guelph | Replacement of end of life asset due to poor conditions, high mileage and engine hours and age. Vehicle experiencing more down time at the shop for repairs and maintenance impacting vehicle availability.
150510 | Base | Upgrade/Retrofit SWI Video Security System at Jim Yarrow TS station | 0.055464 | 0 | 0 | 0 | 0 | 0.055464 | 148.08 | System Service | Safety & Security | Brampton | This project consists of installation of SWI Video security system at Jim Yarrow TS
103030 | Base | Technology Upgrades Improving the System Control Room Environment | 0.054949 | 0.055714 | 0.056483 | 0.057256 | 0.058033 | 0.28243 | 147.52 | General Plant | Information Technology | Multiple | This project will continue to build on the original capital project whose scope was focused on the replacement of computers used as Operator WorkStations. The scope of this program has been expanded to account for all technology purchases required for the Control Room theater.
151438 | Base | 2020 GUELPH - Fleet | 0.7 | 0 | 0 | 0 | 0 | 0.7 | 146.11 | General Plant | Fleet Renewal | Guelph | Replacement of end of life asset due to poor conditions, high mileage and engine hours and age. Vehicle experiencing more down time at the shop for repairs and maintenance impacting vehicle availability.
151108 | Base | Office Equipment | 0.07102 | 0.072546 | 0.074107 | 0.075699 | 0.077327 | 0.3707 | 143.52 | General Plant | Facilities Management | Guelph | Replace aging equipment within the Guelph operational centre to ensure optimal performance in managing the distribution assets
150687 | Base | Woodlands MS - Station RTU & Protection Relays Replacement | 0.1495 | 0 | 0 | 0 | 0 | 0.1495 | 141.21 | System Service | System Control, Comm'ns & Performance | Enersource | Woodlands MS - Station RTU & Protection Relays Replacement
151381 | Base | 2021 GUELPH - Fleet | 0 | 0.68 | 0 | 0 | 0 | 0.68 | 138.35 | General Plant | Fleet Renewal | Guelph | Replacement of end of life asset due to poor conditions, high mileage and engine hours and age. Vehicle experiencing more down time at the shop for repairs and maintenance impacting vehicle availability.
151384 | Base | 2024 GUELPH - Fleet | 0 | 0 | 0 | 0 | 0.63 | 0.63 | 137.66 | General Plant | Fleet Renewal | Guelph | Replacement of end of life asset due to poor conditions, high mileage and engine hours and age. Vehicle experiencing more down time at the shop for repairs and maintenance impacting vehicle availability.
150586 | Base | OT SCADA map cleanup | 0 | 0 | 0.25864 | 0 | 0 | 0.25864 | 136.57 | General Plant | Information Technology | Multiple | SCADA Map clean up program to ensure accuracy and safety in the SCADA environment.
151245 | M-Factor | Capacitor Bank Installations | 0.02 | 0.01 | 0.030841 | 0.041841 | 0.041841 | 0.14452 | 134.68 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of capacitor bank installation to increase power factor, capacity and reduce losses.
150235 | M-Factor | Greenwood Expansion Station Service Supply Backup | 0 | 0 | 0 | 0 | 0.04402 | 0.04402 | 130.13 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of providing back up to the station service transformer at Greenwood TS. In the current configurationt the two station transformers are supplied from VTS#1 and a failure on VTS#1 result in removal of both VTS#1 and VTS#1.
150582 | M-Factor | Back-end Automation (Orchestration Tool\Setup) | 0 | 0 | 0 | 0 | 0.22006 | 0.22006 | 128.21 | General Plant | Information Technology | Multiple | Automated integration of enterprise system platforms with HR functionality. Increase in productivity related to human resources
102931 | Base | Paving of 3 MS & TS Station Driveways per year - Annual Multi-year initiative - East | 0.047824 | 0.048447 | 0.049079 | 0.049718 | 0.050365 | 0.24543 | 125.42 | System Renewal | Substation Renewal | Powerstream | Existing driveways at stations in the East Operating Area (former PowerStream) are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
151039 | Base | Fleet_West_Equipment_Key Box | 0 | 0.015 | 0 | 0 | 0 | 0.015 | 124.35 | General Plant | Fleet Renewal | Horizon | Adopted the current vehicles key management system at all sites to ensure access to vehicles when required. This ensure access to vehicles after hours and tracking of vehceil keys.
150655 | Base | Maingate MS - Station RTU and Protection Relays Upgrade | 0 | 0.15255 | 0 | 0 | 0 | 0.15255 | 123.91 | System Service | System Control, Comm'ns & Performance | Enersource | This project consist of RTU and protection relay upgrade at Maingate MS
150689 | Base | Rogers MS - Station RTU and Protection Relays Upgrade | 0 | 0.15255 | 0 | 0 | 0 | 0.15255 | 123.91 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of bus, line and transformer protection at Richmond Hill TS
151076 | Base | Fuel Pump Replacement Vansickle Rd. | 0 | 0.027363 | 0 | 0 | 0 | 0.027363 | 122.83 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of systems that have surpass end of life, are consistently down for repairs and parts are difficult to obtain, impacting fuel of vehicles to support capital systems projects and customer emergencies responses.
150597 | Base | Lock Box Installs - East | 0.0097775 | 0.0098551 | 0.0099352 | 0.010017 | 0.0101 | 0.049685 | 115.84 | System Access | Metering | Powerstream | Multi-year project to install lock boxes at ICI properties with restricted access to eliminate need for a customer appointment for access.
151143 | M-Factor | Cable Replacement and Transformers Replacement -Project - Shelter Bay Rd. Mississauga | 1.0755 | 0 | 0 | 0 | 0 | 1.0755 | 111.66 | System Renewal | Underground Asset Renewal | Enersource | From 2017-2019 YTD customers in this area experienced 6 failures.
150821 | M-Factor | Fleet_Central South Vehicle Replacement-Van | 0 | 0 | 0 | 0 | 0.055 | 0.055 | 111.07 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
101487 | M-Factor | Add one Additional 27.6 kV Cct on Major Mack Dr and 9th Line | 0 | 0 | 0 | 1.325 | 0 | 1.325 | 107.71 | System Service | Capacity (Lines) | Powerstream | There are two ccts 12M1/12M3 on Major Mack Dr east of Hwy 48, but only one cct 12M3 goes all the way to 9th Line. The second cct stops half way and is a radial supply. This project is to establish another tie between two ccts on Major Mack and 9th Line. The purpose is to form a supply loop and a new tie between Buttonville TS and MTS2.
150255 | M-Factor | Cable Replacement Project - (B23) - Cundles Rd and Janine St, Barrie | 0 | 0 | 0 | 1.0562 | 0 | 1.0562 | 99.3 | System Renewal | Underground Asset Renewal | Powerstream
151383 | Base | 2023 GUELPH - Fleet | 0 | 0 | 0 | 0.595 | 0 | 0.595 | 98.28 | General Plant | Fleet Renewal | Guelph | Replacement of end of life asset due to poor conditions, high mileage and engine hours and age. Vehicle experiencing more down time at the shop for repairs and maintenance impacting vehicle availability.
150462 | Base | MV90 Upgrade | 0.15171 | 0 | 0 | 0 | 0 | 0.15171 | 97.77 | General Plant | Information Technology | Multiple | Enhancement to MV90 systems application to support process improvement requirements. As the MV90 system is one of the core applications of the organization, operational enhancements come in from a number of venues and thereby feedback into the other downstream systems. These enhancements are considered for the overall customer and organizational benefits.
150569 | Base | Server OS Upgrades - IT Infrastructure | 0.074123 | 0.075094 | 0.081246 | 0.19265 | 0 | 0.42311 | 95.22 | General Plant | Information Technology | Multiple | Operating system upgrades to support IT infrastructure.
150737 | Base | Facilities_East Region_Reactive Capital | 0.25793 | 0.26347 | 0.26914 | 0.27493 | 0.28084 | 1.3463 | 91.88 | General Plant | Facilities Management | Powerstream | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150736 | Base | Facilities_West Region_Reactive Capital | 0.25793 | 0.26347 | 0.26914 | 0.27493 | 0.28084 | 1.3463 | 91.88 | General Plant | Facilities Management | Horizon | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150734 | Base | Facilities_Central Region_Reactive Capital | 0.25937 | 0.26347 | 0.26928 | 0.27493 | 0.28084 | 1.3479 | 91.85 | General Plant | Facilities Management | Multiple | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150464 | M-Factor | Fieldworker Upgrade - IT/OT Infrastructure | 0.30342 | 0 | 0 | 0 | 0 | 0.30342 | 91.28 | General Plant | Information Technology | Multiple | Upgrade to increase functionality for the metering field staff to improve response times for customers
151079 | Base | Fleet West Major Equipment & Tools | 0 | 0.05 | 0 | 0 | 0 | 0.05 | 90.95 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of tools and shop equipment required to repair and maintain vehicles to ensure vehicle availability to support capital systems projects.
150958 | M-Factor | Fleet_West_Vehicle Replacement_Forklift | 0 | 0 | 0 | 0 | 0.099 | 0.099 | 90.74 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
101393 | M-Factor | Redundant Fibre Path to Aurora MS#4 Sub-Station | 0 | 0 | 0 | 0.49431 | 0 | 0.49431 | 89.62 | System Service | System Control, Comm'ns & Performance | Powerstream | AMS4 is a major node on the Operations Network, but the fiber optic routes into the AMS4 are not diverse. This major hub is therefore exposed to a single point of failure, and loss of communications to this hub would be very impact. This project is to provide redundant fibre path to Aurora MS to offer increased security and reliability.
150676 | Base | Mobile Devices - IT Infrastructure | 0.010114 | 0.010229 | 0.010345 | 0.010463 | 0 | 0.041152 | 88.32 | General Plant | Information Technology | Multiple
151078 | Base | Fleet West Major Equipment & Tools | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 81.47 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of tools and shop equipment required to repair and maintain vehicles to ensure vehicle availability to support capital systems projects.
103171 | Base | Implementation of a new Alectra Network Operations Voice Radio System | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 0.125 | 79 | General Plant | Information Technology | Multiple
150564 | Base | OT SCADA hardware upgrade cycle 4 | 0 | 0 | 0.20691 | 0 | 0 | 0.20691 | 75.49 | General Plant | Information Technology | Multiple | Planned hardware updrades for monitors and workstations on enterprise SCADA platform.
151069 | Base | PI Upgrades & Enhancements - IT/OT Infrastructure | 0.12056 | 0 | 0 | 0 | 0 | 0.12056 | 62.9 | General Plant | Information Technology | Multiple | Partner with OSIsoft (creator of PI) implement next level predictive analytics using AI (artificial intelligence) and ML (machine learning).
151016 | M-Factor | Fleet_West_Vehicle_Replacement_Pickups | 0 | 0 | 0.11 | 0 | 0 | 0.11 | 55.85 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151018 | M-Factor | Fleet_West_Vehicle_Replacement_Trailer | 0 | 0 | 0 | 0.11 | 0 | 0.11 | 49.52 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102922 | Base | Installation/Retrofit of SWI Video Security System at 3 TS stations | 0.031138 | 0 | 0 | 0 | 0 | 0.031138 | 48.21 | System Service | Safety & Security | Powerstream | This project consists of installation of SWI Video security system at 3 Transformer Station in West
150563 | Base | OT SCADA upgrade cycle 3 | 0 | 0.20617 | 0 | 0 | 0 | 0.20617 | 46.3 | General Plant | Information Technology | Multiple | Planned hardware updrades for monitors and workstations on enterprise SCADA platform.
150906 | Base | Vehicle key box system | 0.03 | 0 | 0 | 0 | 0.004 | 0.034 | 43.15 | General Plant | Fleet Renewal | Powerstream
150747 | M-Factor | Net Zero Energy Emissions | 0.30847 | 0.31505 | 0.32795 | 0.33169 | 0.33546 | 1.6186 | 34.58 | System Service | Distributed Energy Resources (DER) | Powerstream | The project will help Alectra Utilities to ensure that growing DER challenges are met through building expertise and capability in real time monitoring, integrating and optimizing of DERs in line with customer preferences. This will lead to a system that can safely integrate and optimize value from DERs for the benefit of customers.
151053 | Base | Building Sustainment | 0.17911 | 0.18296 | 0.18689 | 0.19091 | 0.19501 | 0.93488 | 31.98 | General Plant | Facilities Management | Guelph | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150584 | Base | OT Control room hardware upgrade cycle | 0 | 0 | 0.32588 | 0 | 0 | 0.32588 | 26.59 | General Plant | Information Technology | Multiple | Planned hardware updrades for monitors and workstations on enterprise control room platforms. .
103065 | Base | Upgrade Advanced Distribution Management System (ADMS) to latest version release. | 0 | 0 | 0 | 0.098265 | 0 | 0.098265 | 24.76 | General Plant | Information Technology | Powerstream
151084 | Base | Shop equipment refurbishment and replacement | 0 | 0 | 0.025 | 0 | 0 | 0.025 | 22.69 | General Plant | Fleet Renewal | Brampton
150878 | M-Factor | Bus & Main Breaker Protections Replacement - Jim Yarrow TS | 0 | 0 | 0 | 0 | 0.11398 | 0.11398 | 21.53 | System Renewal | Substation Renewal | Brampton | This is part of a multi-phase project to upgrade aging and failure-prone protection systems to the current protection standards. Proper protection to the main bus and transformers will provide protection to the assets in the case of faults when they occur.
150562 | Base | OT Firewall Upgrade | 0 | 0.24509 | 0 | 0 | 0 | 0.24509 | 19.71 | General Plant | Information Technology | Multiple | Hardware upgrade cycle for OT platform.
150704 | Base | Feeder Protection Migration to DNP - Jim Yarrow TS | 0.32841 | 0.17153 | 0 | 0 | 0 | 0.49995 | 15.9 | System Renewal | Substation Renewal | Brampton | This is part of a multi-phase project to upgrade aging and failure-prone protection systems at Jim Yarrow TS to the current protection standards. Proper protection to distribution feeders will provide protection to the assets in the case of faults.
151160 | M-Factor | Fleet_West_Vehicle Replacement_ Pole Trailer_1-405 | 0 | 0 | 0 | 0.079 | 0 | 0.079 | 15.12 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150581 | Base | Analytics\Monitoring Tool IT infrastrucutre rescources | 0 | 0 | 0 | 0.32664 | 0 | 0.32664 | 13.59 | General Plant | Information Technology | Multiple | Gather requirements, determine available products that meet those requirements and RFP. SOW will include POC of chosen products as well as Professional Services to assist with design, build and implementation.
150583 | Base | OT Server Hardware upgrade OMS/SCADA | 0 | 0 | 0 | 0.33234 | 0 | 0.33234 | 13.49 | General Plant | Information Technology | Multiple | Hardware refresh for customer facing OMS platform and SCADA architecture .
151031 | Base | Fleet Shop equipment refurbishment and replacement | 0.077 | 0.054 | 0.058 | 0.06 | 0.062 | 0.311 | 12.85 | General Plant | Fleet Renewal | Enersource | For the refurbishment of trailers, shop compressors and hoists to extend the life of the assets instead of replacement to reduce the need fro capital expenditures.
150678 | Base | P&C Specific Tools & Testing Equipment - West | 0.016233 | 0.016418 | 0.016604 | 0.016793 | 0.016985 | 0.083033 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
102999 | Base | P&C Specific Tools and Testing Equipment | 0.016233 | 0.016418 | 0.016604 | 0.016793 | 0.016985 | 0.083033 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
102157 | Base | Server Refresh - IT Infrastructure | 0.95638 | 0.41131 | 1.2465 | 0.36224 | 0.3956 | 3.372 | 10.1 | General Plant | Information Technology | Multiple | Ongoing server refresh to support applications.
150396 | Base | Network Refresh - IT Infrastructure | 0.35942 | 0.3638 | 0.36823 | 0 | 0 | 1.0915 | 9.81 | General Plant | Information Technology | Multiple | Replacement of existing network infrastructure that is unsupported (or soon to be) including further rationalization and design modifications to support the delivery of services throughout the Alectra Environment.
150547 | M-Factor | Business Support | 0 | 0 | 0 | 0 | 0.17621 | 0.17621 | 7.83 | General Plant | Information Technology | Multiple | The project will encompass a variety of sub projects for the purpose of investigating new and emerging technologies. Building a culture of innovation Alectra will need a continued effort in remaining ahead of the trends and implementing new and more efficient ways of doing business.
151029 | M-Factor | Fleet_West_Vehicle_Replacement_Pickups | 0 | 0 | 0 | 0 | 0.169 | 0.169 | 0.9 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.

## 2020 Ranking
Project List for Oral Hearing Undertakings
Project Number | Funding | Project Name | 2020 ($MM) | Project Score | Investment Category | Investment Grouping | Rate Zone | Comment
150404 | Base | Kenilworth TS Power Factor Correction | 0.10114 | 184356.97 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of capacitor bank installation at Kenilworth TS to improve PF and to comply with IESO market rules.
150725 | Base | Lines Central-North - Reactive Renewal | 1.1952 | 181453.58 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have failured and requires replacement in order to restore power to customers
150690 | Base | Lines Central-South - Reactive Renewal | 3.0631 | 171817.68 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have failured and requires replacement in order to restore power to customers
150682 | Base | Remote Fault Indicator Deployment | 0.43832 | 164220.93 | System Service | System Control, Comm'ns & Performance | Multiple | This project consists of remote fault indictor deployment which will result improved outage response, operational efficiency, and reliability
150217 | Base | Build double 27.6kV ccts on Teston Rd and Pine Valley Dr to supply Block 40/47 | 1.4455 | 151265.43 | System Service | Capacity (Lines) | Powerstream | This project is to rebuild existing 8.32 kV poleline on teston road (Pine Valley drive to Weston road) as it does not have sufficent capacity for new developments.
150587 | Base | Kenilworth TS Upgrade | 0.55677 | 134983.87 | System Access | Transmitter Related Upgrades | Horizon | HONI will be replacing transformers at Kenilworth TS which is at physical end-of-life, as well as switchgear. Alectra Utilities role in the project will be to coordinate planned outages and disconnect and reconnect feeder egress connections
102247 | Base | Interest Capitalization | 1.1166 | 104303.71 | General Plant | Other General Plant | Powerstream
150596 | Base | Meter Renewal - all types but Suite - PowerStream RZ | 0.082053 | 94470.24 | System Access | Metering | Powerstream | Multi-year project to renew existing residential (except suite) metering equipment.
101871 | Base | Services (New and Upgrades) - Layouts – East North - Commercial Services | 0.013391 | 94398.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150600 | Base | Firmware Upgrades for Smart Meters - East | 0.034024 | 94363.34 | System Access | Metering | Powerstream | Multi-year project to renew residential Smart meter firmware to improve communication performance.
151169 | Base | Central-South - Capitalization of Locates | 0.028719 | 94344.62 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
151174 | Base | West Lines - Capitalization locates | 0.034463 | 94319.23 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150631 | Base | Transformer Station Metering - Central North | 0.069175 | 94245.75 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew wholesale metering equipment.
101696 | Base | Subdivision - North Underground Residential Distribution System Final Close out and Inspection. | 0.045289 | 94197.28 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
103381 | Base | East Lines - Capitalization locates | 0.059681 | 94144.61 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101870 | Base | Services (New and Upgrades) - Layouts – East South - Commercial Services | 0.065617 | 94022.15 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101869 | Base | Services (New and Upgrades) - Layouts – East North - New Residential | 0.06959 | 93989.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150650 | Base | Replace PCB Risk PT's - Enersource RZ | 0.10064 | 93977.25 | System Access | Metering | Enersource | Multi-year project to replace metering transformers identified with unacceptable levels of PCB's, to prevent hazardous spills.
101919 | Base | New Services (new and upgrades) - Commercial, Industrial and Institutional (ICI) Projects - NORTH | 0.074034 | 93955.31 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150647 | Base | Transformer Station Metering - Enersource RZ | 0.06542 | 93884.28 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew wholesale metering equipment.
151049 | Base | Commercial, Industrial, Institutional, Apartment Connections | 0.1236 | 93829.96 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
101685 | Base | Subdivision - South Underground Residential Distribution System Final Close out and Inspection. | 0.10915 | 93778.29 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150457 | Base | Services (New and Upgrades) - Layouts – St Catharines | 0.18711 | 93519.09 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151162 | Base | Non Recoverable replacement of Distribution Equipment due to accident/vandalism | 0.24378 | 93457.13 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101924 | Base | Mulit Unit Metering for New Buildings NORTH - PowerStream RZ | 0.14799 | 93421.21 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in northern area of territory.
150588 | Base | New Residential Subdivision Development - Alectra West | 0.2579 | 93265.82 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
101791 | Base | New Services - new and upgrades - COMMERCIAL, INDUSTRIAL, INSTITUTIONAL (ICI) SERVICES - SOUTH | 0.22252 | 92878.02 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101812 | Base | Reactive Capital, Alectra East - LIS | 0.30621 | 92710.01 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150754 | Base | Lines Central-North - Non-Recoverable Replacements | 0.34355 | 92705.38 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150726 | Base | Lines Central-South - Non-Recoverable Replacements | 0.34355 | 92705.38 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101820 | Base | Reactive Capital, Alectra East - Non-Recoverable Replacement | 0.28674 | 92582.71 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150389 | Base | Services (New and Upgrades) - Layouts – Central North | 0.35059 | 92563.35 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150651 | Base | C & I Metering - Renewal- Brampton RZ | 0.59145 | 92560.77 | System Access | Metering | Brampton | Multi-year project to renew existing ICI metering equipment.
150386 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central North | 0.37582 | 92424.37 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150453 | Base | CIS CC&B Modifications(Regulatory Enhancements) | 0.91073 | 92260.88 | General Plant | Information Technology | Multiple | Enhancements to the CIS (CC&B) application needed to meet any regulatory requirements Such requirements in the past have been Ontario Energy Savings Program (OESP) as well as the Monthly Billing projects.
150649 | Base | Suite Metering - Enersource RZ | 0.45016 | 91838.22 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew suite metering equipment.
150654 | Base | C & I Metering - New Services - Brampton RZ | 0.61006 | 91552.85 | System Access | Metering | Brampton | Multi-year project to purchase and install ICI metering equipment on new services.
150595 | Base | C & I and Wholesale Metering - PowerStream RZ | 0.52637 | 91530.35 | System Access | Metering | Powerstream | Multi-year project to purchase, install, and renew ICI and wholesale metering equipment.
101868 | Base | Services (New and Upgrades) - Layouts – East South - New Residential | 0.41513 | 91488.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101795 | Base | Multi Unit Metering for New Buildings SOUTH - PowerStream RZ | 0.44256 | 91273.08 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in southern area of territory.
101873 | Base | Services (New and Upgrades) - Layouts – East North - Residential Upgrades | 0.48811 | 91023.49 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151051 | Base | System Relocations Road Authorities | 1.0169 | 91002.2 | System Access | Road Authority | Guelph | Mandatory - System Access Related Project
150652 | Base | New Residential Subdivision Development - Alectra Central South | 0.64729 | 90948.17 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150388 | Base | Services (New and Upgrades) - Layouts – Central South | 0.67547 | 90774.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150692 | Base | New Feeder in Residential Subdivision Development - Alectra Central North | 0.85968 | 90609.19 | System Service | Capacity (Lines) | Brampton | This expenditure is required to meet the needs of the development community that construct municipal approved residential subdivisions in Alectra Utilities' Central North service territory
150599 | Base | Suite Meter - Reverification - PowerStream RZ | 0.87682 | 90368.15 | System Access | Metering | Powerstream | Multi-year project to renew Measurement Canada seal dates on existing suite metering equipment.
150455 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - St Catharines | 0.86575 | 90201.14 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150659 | Base | Residential Meters - by Metering - Brampton RZ | 0.96979 | 90095.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Metering.
150456 | Base | Services (New and Upgrades) - Layouts – Hamilton | 0.87181 | 89961.61 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150630 | Base | New Residential Subdivision Development - Alectra Central North | 0.687 | 89952.48 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101828 | Base | Reactive Capital, Alectra East - Recoverable Replacement | 0.69797 | 89765.65 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover some costs for (i.e. pole hit, vehicle at scene of accicent, Alectra Utilities obtains most of costs (near $0 impact too budget))
101896 | Base | New Institutional/Commercial/Industrial Subdivision Development - Alectra East | 0.9099 | 89347.36 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101872 | Base | Services (New and Upgrades) - Layouts – East South - Residential Upgrades | 0.72312 | 89344.81 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101800 | Base | Reactive Capital, Alectra East - Storm Damage | 1.1509 | 86549 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151047 | Base | Subdivisions | 0.66674 | 85393.33 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
150620 | Base | Metering Renewal - all types - Horizon RZ | 1.8909 | 84064.36 | System Access | Metering | Horizon | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment.
101808 | Base | Reactive Capital, Alectra East - Switchgears | 1.8047 | 83304.08 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150648 | Base | Metering Renewal - all types but Suite - Enersource RZ | 2.2626 | 82569.47 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew residential (except suite) and ICI metering equipment.
101892 | Base | New Subdivision Development - Secondary Service Lateral - Alectra East | 2.5667 | 80775.74 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151125 | M-Factor | Connection Cost Recovery Agreement (CCRA) – Midhurst TS – 15th Anniversary True-up | 3.175 | 78171.93 | General Plant | Connection and Cost Recovery Agreements | Powerstream | In accordance with the Connection Cost Recovery Agreement, a 15-year true-up is required for Midhurst TS.
150384 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central South | 3.0125 | 77903.71 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
151124 | M-Factor | Goreway TS Expansion (CCRA) - 10 Yr True-Up Payment, Brampton | 5.5626 | 76025.7 | General Plant | Connection and Cost Recovery Agreements | Brampton | In accordance with the Connection Cost Recovery Agreement, a 10-year true-up is required for Goreway TS.
150449 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - Hamilton | 4.9871 | 69328.05 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151095 | Base | Reactive Restoration | 1.0029 | 63546.92 | System Renewal | Reactive Capital | Guelph | Replacement of assets which have failured and requires replacement in order to restore power to customers
150465 | Base | LPSS Upgrade - IT Infrastructure | 0.50569 | 59939.65 | General Plant | Information Technology | Multiple | Enhancement to LPSS Alectra market settlement system LPSS is the Alectra settlement system. This is one of the core applications of the organization, operational enhancements come in from a number of venues and thereby feedback into the other downstream systems. These enhancements are considered for the overall customer and organizational benefits.
101824 | Base | Reactive Capital, Alectra East - Distribution Equipment | 5.1994 | 58189.58 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151161 | Base | Joint Use Pole Removal | 0.11273 | 57199.8 | System Renewal | Overhead Asset Renewal | Horizon | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
150463 | Base | Customer Self Service Portal Enhancements | 0.85968 | 56341.32 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) self service portal application to support process improvement requirements.The self service portal is the means by which Alecra customers can obtain their customer related information, interact with a CSR, post questions. The enhancements will allow Alectra customers a better experience when interacting with Alectra through the web portal channel.
151050 | Base | Metering - all types - Guelph RZ | 0.63655 | 55986.2 | System Access | Metering | Guelph | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment in Guelph RZ.
150469 | Base | ERP JD Edwards Enhancements | 2.0301 | 55714.6 | General Plant | Information Technology | Multiple | Allocation of capital funds to provide 3rd party assistance on capital work, along with creating system enhancements to the JD Edwards ERP and supporting Systems.
150325 | Base | CIS CC&B Enhancements | 1.2642 | 55520.48 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) application to support process improvement requirements.As the CIS (CC&B) system is one of the core applications of the organization, operational enhancements come in from a number of venues and thereby feedback into the other downstream systems. These enhancements are considered for the overall customer and organizational benefits.
103637 | Base | GS>50 MIST Meter Multi-year initiative Implementation | 0.58131 | 55000.21 | System Access | Metering | Powerstream | Multi-year project to install MIST meters on GS>50 accounts, as required by the Distribution System Code.
101832 | Base | Joint Use Pole Removal | 0.55536 | 54024.42 | System Renewal | Overhead Asset Renewal | Powerstream | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
150344 | Base | HaLRT_New Lake Feeder for TPSS#8 area capacity | 0.57199 | 48091.05 | System Service | Capacity (Lines) | Horizon | The TPSS#8 location has supply constraints on the 13.8kV system. This project is to bring a new feeder out of Lake TS to the area to reinforce the supply and allow for switching to free up capacity to accommodate the new load request.
151236 | Base | Edinburgh Rd (Paisley to Willow) Extension | 0.65969 | 48010.63 | System Service | Capacity (Lines) | Guelph | Replace existing pole line to accommodate two 13.8kV circuits in order to provide capacity and contingency for the new developments on Edinburgh Road North and also act as an inter-tie between Campbell TS and Cedar TS
101887 | Base | New Residential Subdivision Development - Alectra East | 8.9703 | 44863.95 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
100859 | Base | Switchgear Renewal - East | 2.5779 | 43704.68 | System Renewal | Underground Asset Renewal | Powerstream | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151089 | Base | Overhead Rebuilds | 1.1898 | 39246.49 | System Renewal | Overhead Asset Renewal | Guelph | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
101508 | Base | Transformer Renewal - East | 2.1632 | 37474.31 | System Renewal | Transformer Renewal | Powerstream | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
101003 | M-Factor | Richmond Hill TS#2 Upgrade Bus, Line & Transformer Protections | 0.14822 | 36019.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project entails upgrade of Bus, Line and Transformer Protection relays at Richmond Hill TS#2 (Lazenby TS#2) with new relays having fault recording capabilities. This project will also address the communications protocol at this station whihch is obsolete and is incompatible with that of the rest of the system.
150673 | Base | Road Authority Central (Mississauga) | 3.7168 | 35000.51 | System Access | Road Authority | Enersource | Mandatory - System Access Related Project
150134 | Base | Cable Injection Project - (V37) - Langstaff and Weston, Vaughan | 1.5389 | 34877.34 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 20 failures.
150405 | Base | 25M9 Jim Yarrow TS Extensions | 0.32599 | 33741.34 | System Service | Capacity (Lines) | Brampton | Jim Yarrow TS extension with new underground line extending 25M9 from Winston Churchill Blvd utility corridor to Steeles Ave in order to back up 25M8 & 25M10 to accomodate future load growth in Churchill Business Community Park and residential developments between Steeles Ave & Embleton Rd
150645 | Base | Road Authority Central (Brampton) | 4.4046 | 31813.54 | System Access | Road Authority | Brampton | Mandatory - System Access Related Project
150828 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-West | 0.905 | 31592.28 | System Renewal | Overhead Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151452 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-West | 0.895 | 31590.16 | System Renewal | Underground Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
101762 | Base | Road Authority Expenditure PS South | 4.0206 | 31544.34 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
101355 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-East | 0.935 | 31424.67 | System Renewal | Overhead Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151450 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-East | 0.935 | 31424.67 | System Renewal | Underground Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
150072 | M-Factor | Markham TS#3 Bus Differential & Overcurrent Protections Upgrades | 0.2336 | 27028.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Markham TS#3 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
100867 | Base | Pole Renewal - East | 4.3557 | 25595.06 | System Renewal | Overhead Asset Renewal | Powerstream | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
151074 | Base | Reactive renewal | 3.2047 | 25136.12 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have failured and requires replacement in order to restore power to customers
150571 | Base | Cable Injection Project - (J3-K3-N2-O2), Brampton | 2.2957 | 24483.9 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 32 outages due to cable failures from 2007 to 2018 with average duration of 104 minutes.
150375 | Base | New Build - 136M10 Goreway TS Extensions, Brampton | 1.5725 | 22413.42 | System Service | Capacity (Lines) | Brampton | The 136M10 feeder egress project will install a new feeder from the Goreway TS to provide relief to the 136M44 circuit which is over the planning limit
100015 | Base | Transformer Temperature Monitoring - Aurora MS, King & Concord | 0.14953 | 22039.57 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consist of transformer temperature monitoring and telemetry at Aurora MS - King and Concord which will improve system reliability and enables controlled emergency loading beyond the nameplate rating.
151043 | Base | Transformer Renewal - Central South | 1.8571 | 21869.73 | System Renewal | Transformer Renewal | Enersource | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
102545 | Base | Install a New 27.6kV Pole Line on 19th Ave from Leslie St to Woodbine Ave | 1.3732 | 21589.69 | System Service | Capacity (Lines) | Powerstream | This is to remediate radial supply on Leslie St north of Elgin Mills Rd (supplying Leslie North development in Richmond Hill) and radial supply on Woodbine Ave north of Elgin Mills Rd (supplying future urban area in Markham).
150688 | Base | Station Sustainment & Protection & Control CASCADE Expansion | 0.054109 | 20717.32 | General Plant | Information Technology | Multiple | Expand the use of the CASCADE system to be used by the Protection and Control asset in addition to the Station assets
101593 | Base | Station Ground Grid Refurbishments | 0.11569 | 20602.33 | System Service | Safety & Security | Powerstream | This project consists of refurbishment of station ground grid in East. The project would be to design and implement ground grid improvements to meet step and touch potential requirements.
150664 | Base | Residential Meters - by Lines - Brampton RZ | 0.68567 | 18166.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Lines.
151109 | Base | Switch Replacement | 0.17128 | 18145.07 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
150458 | Base | MAS upgrade - IT Infrastructure | 0.080911 | 17425.57 | General Plant | Information Technology | Multiple | Metering Automation System for smart grid Upgrade to be implemented in a phased approach over the next 4 years as smart grid continues to evolve work in conjunction with the metering team to analyze and implement leverage new technologies to provide better more accurate meter readings be responsive to the issues first not reactive when a customer calls
151104 | Base | Distribution Automation - Central North | 0.44566 | 17389.16 | System Service | SCADA and Automation | Brampton | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
102352 | Base | Vaughan TS#4 Feeder Integration - Part 2 | 3.9784 | 16373.29 | System Service | Capacity (Lines) | Powerstream | This project is the second part of VTS4 feeder integration plan. The purposes is to integrate two new 27.6kV feeders (25M9 to 25M10) from VTS4 into Alectra's distribution system to increase distribution capacity by 40 MVA, off load existing feeders and stations with the new feeders and increase supply capacity to Vaughan West.
151318 | Base | Cable Injection Project - (I3) -Bovaird - Dixie - Queen - Hwy 410, Brampton | 0.51681 | 16118.68 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2014 to 2015 with average duration of 71 minutes.
151046 | Base | Addiscott Court Security Fence Improvement | 0.303 | 16096.97 | General Plant | Facilities Management | Powerstream | To improve the fencing to secure the capital inventory within the operational yard in Markham
150639 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-CENTRAL | 0.037721 | 15735.56 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of DC charging system for Central South Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150638 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-East | 0.037721 | 15735.56 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of DC charging system for Central North Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150636 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-North & TS | 0.037721 | 15735.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of DC charging system for East Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150640 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-WEST | 0.037721 | 15735.56 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of DC charging system for West Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150749 | M-Factor | New WiMAX Communication Network - Central South | 0.41446 | 15089.12 | System Service | System Control, Comm'ns & Performance | Enersource | This project is required to implement the WiMax Network for Central South for secure data transfer of monitoring sensors.
150285 | Base | Transformer Renewal - Central North | 0.581 | 14492.05 | System Renewal | Transformer Renewal | Brampton | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150025 | Base | Cable Injection Project - (V18) - Major Mackenzie and Keele, Vaughan | 1.1127 | 14485.46 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2017 customers in this area experienced 2 failures.
150559 | Base | Rathburn Rd Duct Extension (LRT Betterment) | 0.35399 | 14447.96 | System Service | Capacity (Lines) | Enersource | A duct installation to connect existing ducts west and east on Rathburn Rd. A 5 year moratorium is proposed due to streetscaping and this project should be completed with other work.
101027 | Base | Switch Renewal - East | 0.63034 | 14308.5 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
150505 | Base | Purchase and Install 11 Self Recharging Transformer Air Breathers - TS and MS - Multi-year initiative - EAST | 0.025232 | 14276.73 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of transformer air breather at TS and MS stations in West. Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
102062 | Base | Purchase & Installation of 10 Self Recharging Transformer Air Breathers on TS transformers-Multi-year initiative-North & TS | 0.109 | 14210.75 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of transformer air breather at TS and MS stations in East. Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
150506 | Base | Purchase and Installation of 15 Self Recharging Transformer Air Breathers on MS Transformers - Multi-year initiative-CENTRAL | 0.13872 | 14154.95 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of transformer air breather at TS and MS stations in Central South. Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
150504 | Base | Purchase and Installation of 10 Self Recharging Transformer Air Breathers on TS and MS Transformers - Multi-year initiative-WEST | 0.096386 | 14105.38 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of transformer air breather at TS and MS stations in East .Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
151066 | Base | Cable Replacement Project - Hamilton Mountain URD | 3.8379 | 14039.84 | System Renewal | Underground Asset Renewal | Horizon | Recent underground cable failures in this area are unknown at this time. The average cable installation year is 1971 in this project scope. The cables are 23 years over the TUL.
102098 | Base | Client - IT Infrastructure | 1.0742 | 13761.18 | General Plant | Information Technology | Multiple | To upgrade desktop/laptop/mobile devices that are 5 years or older (Approximately 20% of our equipment). Net new equipment for mobile computing as well as upgrades and replacements for damaged devices. Request made by various business units. This budget also includes RSA tokens\Licenses, monitors, mice, keyboards, docking stations, tablets and small non-MFP printers. Out of Scope: Large MFP Printers
150014 | Base | Cable Injection Project - (V01) - Yonge - Steeles - Bathurst - Center, Vaughan | 0.84264 | 13574.23 | System Renewal | Underground Asset Renewal | Powerstream | From 2014-2016 customers in this area experienced 13 failures.
151247 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.575 | 13413.53 | System Renewal | Overhead Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102232 | Base | Capital Funds for Emergency P&C Purchases - East | 0.032466 | 13270.97 | System Renewal | Substation Renewal | Powerstream | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the East Operating Area (former PowerStream). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150683 | Base | Capital Funds for Emergency P&C Purchases - Central North | 0.032466 | 13184.55 | System Renewal | Substation Renewal | Brampton | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central North Operating Area (Brampton). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150685 | Base | Capital Funds for Emergency P&C Purchases - West | 0.032466 | 13184.55 | System Renewal | Substation Renewal | Horizon | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the West Operating Area (former Horizon). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150684 | Base | Capital Funds for Emergency P&C Purchases - Central South | 0.032466 | 13184.55 | System Renewal | Substation Renewal | Enersource | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central South Operating Area (former Mississauga). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150784 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.675 | 12968.3 | System Renewal | Overhead Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151453 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.61628 | 12922.02 | System Renewal | Underground Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
150823 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.725 | 12654.97 | System Renewal | Overhead Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102099 | Base | Printer & Copier Fleet Replacement | 0.040455 | 12636.08 | General Plant | Information Technology | Multiple | Replacement of existing fleet of printers/copiers that are 5 or more years old. This will include non-MFP printers. Replacement to be determined by an evaluation of evolving needs and corporate requirements as well as age of equipment.
151449 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.795 | 12175.67 | System Renewal | Underground Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
103211 | Base | Misc Software Upgrades (FormScape, AutoCAD, etc.) - IT/OT Infrastructure | 0.12297 | 12020.93 | General Plant | Information Technology | Multiple | Upgrade/ acquire software as required / requested by business.
151451 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.825 | 11935.99 | System Renewal | Underground Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
150007 | Base | Extend 153M10 to Transfer MS322 | 1.6897 | 11505.19 | System Service | Capacity (Lines) | Powerstream | This project consists of extenstion of 153M10 to transfer MS322. Back-up capability lines project extending the 153M10 circuit along Holland Street from Bridge Street , south along Morris Road, west along Centre Street to Thomas Street, north on Drury Street, west along Holland Street to Miller Park Avenue (approximately 2 km's)
150579 | Base | New build - Extend Bunting M81 Feeder, St.Catharines | 1.5146 | 11461.01 | System Service | Capacity (Lines) | Horizon | This project is to extend M81 feeder to supply new development and meet contigency condition in St. Catharines. This project will deal with ongoing capacity constraints in the North end of St.Catharines by bringing available supply from Bunting and Carlton TS's
103180 | Base | Citrix Xen Virtualization Expansion - IT Infrastructure | 0.050569 | 11298.77 | General Plant | Information Technology | Multiple | Client computing virtualization (Citrix) is currently the standard delivery method for applications and desktops at Alectra. This system has had a tremendous uptake in the organization and requires an upgrade in back-end infrastructure to support the additional demand from the business.
150693 | M-Factor | Blockchain | 0.34691 | 11191.63 | System Service | Distributed Energy Resources (DER) | Multiple | The project will prepare Alectra Utilities to engage with customers in a real-time and transparent process to record the flow of electricity to and from DERs, enabling the efficient procurement of distribution benefits, such as demand response and frequency regulation. The project will provide a robust settlement mechanism between Alectra and customers, backed by timely and efficient financial transactions, to enable overall trust and customer value delivery and leading to increased customer satisfaction.
151302 | Base | Cable Injection Project - (HAM) - Rymal - Mud - Upper Centennial - Upper Red Hill Valley | 0.64706 | 11132.21 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 8 failures, or 14 failures per 100km. This area includes the 331X & 341X feeders which were identified as a Worst Performing Feeder in 2018. The average cable installation year is 1989 in this project scope.
150342 | M-Factor | HaLRT_New Stirton Feeder for TPSS#4 and 8852X load shedding, Hamilton | 4.8476 | 10906.89 | System Service | Capacity (Lines) | Horizon | The 8852X is the only 13.8kV feeder in the vicinity of the HaLRT TPSS#4 location and is at its utilization limit. To accommodate the new TPSS a new feeder from Stirton is to be built, and part of the 8852X load will also be transferred to this new feeder
150665 | Base | Emerging Customer Initiated Work (West) | 1.4515 | 10905.1 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
101562 | Base | Arc Flash Mitigation Projects | 0.041677 | 10618.95 | System Service | Safety & Security | Powerstream | This project is to mitigate arc flash risk at East stations.
150653 | Base | Road Authority West (St. Catharines) | 0.77414 | 10216.94 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
150615 | Base | Metering Tools & Equipment - Central North | 0.037876 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150616 | Base | Metering Tools & Equipment - Central South | 0.037876 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150613 | Base | Metering Tools & Equipment - East | 0.037876 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150614 | Base | Metering Tools & Equipment - West | 0.037876 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
151439 | Base | 2020 GUELPH - Remotely Controlled Switches | 0.36711 | 9307.37 | System Service | SCADA and Automation | Guelph | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
150261 | Base | Cable Injection Project - (V38) - Rutherford and Weston, Vaughan | 1.4139 | 9110.1 | System Renewal | Underground Asset Renewal | Powerstream | From 2015-2018 customers in this area experienced 5 failures.
151063 | Base | Pole Renewal - Central South | 3.7094 | 9065.1 | System Renewal | Overhead Asset Renewal | Enersource | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
100886 | Base | Distribution Automation - East | 1.2173 | 9041.12 | System Service | SCADA and Automation | Powerstream | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
150808 | Base | Implementation of Doble - Enoserv PowerBase and Enoserv RTS applications for Protection and Control Department | 0.032465 | 8798.22 | General Plant | Information Technology | Multiple | PowerBase is the premier application to manage and report on protection assets maintenance and engineering records. It manages workflow and connect with maintenance management systems such as Cascade. RTS is a vendor neutral software which allows connection to a variety of test sets. It offers an extensive relay test plan library.
151300 | Base | Cable Injection Project - (HAM) - Millen - Barton - Fruitland | 0.9103 | 8690.38 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 16 failures, or 44 failures per 100km. The average cable installation year is 1987 in this project scope.
150097 | M-Factor | Line Protections and HMI Upgrade - KDU-10 Replacement - Markham TS#2 | 0.48367 | 8506.15 | System Renewal | Substation Renewal | Powerstream | KDU-10 protection relay malfunction can cause an outage on the 230 kV supply of the station, resulting in a major power interruption. Replacement of this obsolete equipment is expected to provide improved reliability and will provide fault and event record information which will enable accurate diagnosis of system events and outage duration reductions.
101804 | Base | Purchase of Major Tools | 0.34612 | 8158.3 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150773 | M-Factor | New WiMAX Communications System - Central North | 0.27498 | 7999.76 | System Service | System Control, Comm'ns & Performance | Brampton | This project is to provide WiMax for Central North for secure data transfer of monitoring devices.
150509 | Base | Installation of Transformer Bushing Monitoring Yarrow TS and MS txmrs-Multi Year -EAST | 0.12154 | 7885.3 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Transformer bushing monitoring system in Central North. Bushing monitoring unit provides real time condition monitoring of the transformer bushings.
150709 | Base | Spare Station Transformer Bushing Conversion from PILC to XLPE - West | 0.11015 | 7847.53 | System Renewal | Substation Renewal | Horizon | This project involves converting the spare station transformer primary and secondary bushings/compartments from PILC to XLPE in the West Operating Area (former Horizon). The spare transformers are used when a failure occurs on a station transformer. The PILC cable will be replaced with XLPE at the station in order to improve station reliability and worker and equipment safety. The conversion of bushings is critical as primary bushing compartments have ruptured on multiple occasions in 2017 in the West Operating Area - causing oil spills larger than 200 liters.
102038 | Base | Installation of Transformer Bushing Monitoring on TS and MS txmrs-Multi Year | 0.12367 | 7734.98 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of Transformer bushing monitoring system in East. bushing monitoring unit provides real time condition monitoring of the transformer bushings.
150785 | M-Factor | New WiMAX Communications System - West | 0.48704 | 7655.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project is to provide WiMax for West for secure data transfer of monitoring device.
150282 | Base | Switchgear Renewal - Central North | 0.46462 | 7521.14 | System Renewal | Underground Asset Renewal | Brampton | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150508 | Base | Installation of Transformer Bushing Monitoring on MS txmrs-Multi Year -CENTRAL | 0.16526 | 7508.89 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Transformer bushing monitoring system in Central South. bushing monitoring unit provides real time condition monitoring of the transformer bushings.
151062 | Base | Cable Replacement - (279) - 201 Silvercreek Pky N Subdivision, Guelph | 0.69856 | 7505.11 | System Renewal | Underground Asset Renewal | Guelph
151121 | Base | Cable Injection Project - (V43) - Hwy 7 and Pine Valley Dr, Vaughan | 1.0195 | 7356.55 | System Renewal | Underground Asset Renewal | Powerstream | From 2015-2016 customers in this area experienced 3 failures.
150284 | Base | Pole Renewal - Central North | 0.9285 | 7304.65 | System Renewal | Overhead Asset Renewal | Brampton | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
150484 | Base | 25M8 27.6kV Feeder Extension Heritage Rd, South of Embleton Rd | 0.44307 | 7282.14 | System Service | Capacity (Lines) | Brampton | This project consists of 25M8 feeder extension to Hertitage road to supply new developments
102017 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-North & TS | 0.32275 | 7275.34 | System Service | Safety & Security | Powerstream | This project consists of Sorbweb Oil containment system in East. Protects the environment in the event of a transformer tank rupture
150026 | Base | Cable Injection Project - (M43) - John and Woodbine, Markham | 1.0296 | 6955.31 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 38 years old and will be 39 when project starts (2020).
150343 | M-Factor | Bathurst Street Widening | 3.4061 | 6905.3 | System Access | Road Authority | Powerstream | 2020 portion of scope of the Bathurst Street road widening as per requirements of PSWHA.
150021 | Base | Cable Injection Project - (V36) - Steeles and Pine Valley, Vaughan | 0.6044 | 6821.94 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2017 customers in this area experienced 9 failures.
150714 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - Central | 0.073902 | 6819.25 | System Renewal | Substation Renewal | Enersource | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central South Operating Area (former Enersource). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150713 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.073902 | 6819.25 | System Renewal | Substation Renewal | Brampton | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central North Operating Area (Brampton). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150715 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - West | 0.073902 | 6819.25 | System Renewal | Substation Renewal | Horizon | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the West Operating Area (former Horizon). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150644 | Base | Road Authority West (Hamilton) | 1.3896 | 6689.48 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
150507 | Base | 230kV TS Transformer Primary Bushing Monitoring Enablement-BPD Elimination - 4 TS Transformers-Multi-year initiative-TS | 0.24481 | 6521.07 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to install primary bushing monitoring at TS in EAST
150352 | Base | Voltage Conversion - Central MS, Hamilton | 1.7173 | 6498.05 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 23 outages and had 1,060,300 customer minutes of interruption (75 mins per customer per year). The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail. Specifically Central MS is the only station remaining in service with oil breakers which are functionally obsolete with no spare parts readily available.
150357 | Base | New build - 25M9 Extension to Derry Rd, Mississauga | 0.45622 | 6400.82 | System Service | Capacity (Lines) | Enersource | This project consists of 25M9 extension into Mississauga to provide additional 27.6KV capacity. It will offload Erindale TS in Mississauga and avoid building Mini-Britannia MS and also provides capacity back to Brampton using a link along Derry Rd.
151044 | Base | Switch Renewal - Central South | 0.26412 | 6318.96 | System Renewal | Overhead Asset Renewal | Enersource | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
150065 | Base | Basement Flood Risk Mitigation - Richmond Hill TS#2 | 0.15967 | 6280.45 | System Renewal | Substation Renewal | Powerstream | This project involves mitigating the flood risk at the Richmond Hill TS#2 where there is equipment installed in the basement by relocating or repositioning this equipment. This critical equipment includes DC system, AC and DC panels, feeder switches, UPS, ATS located in the basement of this station. Damage to this equipment due to flooding would cause extensive power interruptions to many customers.
103659 | Base | Storm Hardening - Four-Circuit Poles | 1.7828 | 6254.52 | System Renewal | Overhead Asset Renewal | Powerstream
150514 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear Initiative-WEST | 0.33357 | 6213.41 | System Service | Safety & Security | Horizon | This project consists of Sorbweb Oil containment system in West. Protects the environment in the event of a transformer tank rupture
151336 | Base | Cable Replacement Project - (BA22) - Sunnidale and Anne, Barrie | 1.0002 | 6208.17 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 2 failures in 2019.
151086 | Base | Insulator Replacements | 0.08172 | 5948.6 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
150066 | Base | Basement Flood Risk Mitigation - Vaughan TS#2 | 0.12303 | 5867.18 | System Renewal | Substation Renewal | Powerstream | This project involves mitigating the flood risk at the Vaughan TS#2 where there is equipment installed in the basement by relocating or repositioning this equipment. This critical equipment includes DC system, AC and DC panels, feeder switches, UPS, ATS located in the basement of this station. Damage to this equipment due to flooding would cause extensive power interruptions to many customers.
151176 | Base | Cable Replacement Project - MS Argentia distribution feeder(s) upgrade | 1.5666 | 5705.35 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 11 outages, the length is 1,587 m, and the average cable age is 30 years old.
150637 | Base | Station Switchgear Replacement - MS10 | 2.5738 | 5499.15 | System Renewal | Substation Renewal | Brampton | The existing switchgear at MS10 in Brampton is no longer suitable for service. The main project driver for replacement is the condition of the metal-clad switchgear housing the feeder breakers and bus-tie breakers. The manufacturer no longer supports this type of equipment and the design of the switchgear does not meet Alectra Utilities' current safety standards and presents a potential risk to its employees. An increasing failure risk will have a negative impact on Alectra Utilities' customers, and safety. Additionally, failure of the existing switchgear would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions.
150337 | Base | Switch Renewal - West | 0.4261 | 5475.59 | System Renewal | Overhead Asset Renewal | Horizon | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
151055 | Base | Major Tools | 0.073792 | 5431.72 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
150598 | Base | Suite Metering - Renewals & Retrofits - PowerStream RZ | 0.35225 | 5394.14 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering equipment in existing buildings upgraded from bulk metering.
150515 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-CENTRAL | 0.33465 | 5352.14 | System Service | Safety & Security | Enersource | This project consists of Sorbweb Oil containment system in Central South. Protects the environment in the event of a transformer tank rupture
150516 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-EAST | 0.33465 | 5352.14 | System Service | Safety & Security | Brampton | This project consists of Sorbweb Oil containment system in Central North. Protects the environment in the event of a transformer tank rupture
150744 | Base | John Street underground parking renewal | 0.30951 | 5343.15 | General Plant | Facilities Management | Horizon | Repairs to the undergrown parking level that is in poor condition impacting builsing system below that support the building operations and craeting saftey risks. The building was built in 1950 and many of the building infrastructure is still original.
150336 | Base | Transformer Renewal - West | 0.56332 | 5293.52 | System Renewal | Transformer Renewal | Horizon | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150750 | Base | Lines Central-North - Major Tools | 0.091257 | 5234.11 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150009 | Base | Insulator Renewal - East | 0.20501 | 5107.82 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
151203 | Base | Capital Corrective Equipment Replacement - Stations South West | 0.06 | 4921.2 | System Renewal | Substation Renewal | Guelph | This project is intended to provide capital for all unplanned station equipment replacements in the South West Operating Area (Guelph) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
102042 | Base | Purchase and Installation of Animal Guards at Various Stations-Annual Multi-year initiative-North & TS | 0.015834 | 4893.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of animal guard installation in East
150605 | M-Factor | Residential "ICON F" Meter Replacement - PowerStream RZ | 3.0236 | 4853.17 | System Access | Metering | Powerstream | Multi-year project to replace Icon-F smart meters with secure encryption, last gasp and tamper detection capabilities.
151083 | Base | Switchgear Renewal - West | 0.41269 | 4683.89 | System Renewal | Underground Asset Renewal | Horizon | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151010 | Base | Switch Renewal - Central North | 0.63119 | 4603.75 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
150720 | Base | Lines Central-South - Major Tools | 0.21472 | 4591.27 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
151022 | M-Factor | New Three Sector WiMAX Node - MS305 | 0.1287 | 4525.35 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to install three sector WiMax node at MS305. The node would provide last mile broadband connectivity to field devices such as intelligent overhead reclosers and padmounted switchgears, FIT monitoring data concentrators and Ethernet enabled revenue meters. The node would provide Transfer Trip capability to FIT generators.
150411 | M-Factor | 42M64 Feeder Extension Mississauga Rd, Williams Pkwy to Queen / Embleton | 0.11948 | 4471.12 | System Service | Capacity (Lines) | Brampton | 42M64 Feeder Extension from Mississauga Rd from Queen St. to Embleton Rd to supply new developments on Embleton and provide relief to the existing feeder 25M8
151433 | Base | Cable Injection- 008- AREA46 - Glen Erin & Aquitane, Mississauga | 0.60219 | 4470.89 | System Renewal | Underground Asset Renewal | Enersource | There are 6 outages, we are injecting a total of 19,827 m of cable for this project, and the average age of the cable is 33 years.
150677 | Base | Station Switchgear Replacement - Aquitaine MS59 LV1 | 1.7021 | 4470.11 | System Renewal | Substation Renewal | Enersource | The existing LV1 switchgear at Aquitaine MS59 station houses gas circuit breakers that utilize vintage technology to provide short circuit protection against faults. These circuit breakers are technically obsolete and are prone to failure. Also the switchgear is non-arc-resistant and poses a potential safety hazard to Alectra personnel and even to the general public who happen to be in the vicinity of the station during a failure event. Failure of the existing switchgear and breakers would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions. Therefore, proactive replacement of the existing switchgear and associated equipment is a prudent strategy as the restoration of the system could take 8-10 months due to long equipment lead times in the event of a failure.
151021 | Base | Insulator Renewal - Central North | 0.33484 | 4235.99 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of non-polymer insulators (Areas are prioritiezed by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
150674 | Base | Emerging Customer Initiated Work Central (Brampton) | 0.14337 | 4183.83 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101763 | Base | Unforeseen Projects Initiated by the customer PS North | 0.1124 | 4161.34 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150125 | M-Factor | Aurora MS6 (AMS6) Transformer and Bus Protection Upgrade | 0.13286 | 4156.05 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade transformer and bus protection at Aurora MS6 station from the current electromechnical KBCH relay.
150745 | Base | John Street VAV Updating - Facilities | 0.51586 | 4034.02 | General Plant | Facilities Management | Horizon | Update main building ventilation systems that have surpass end of life and replacement apsrt ca no longer be obatined that support the main Alectra control room, customer services group and communications systesm.
150520 | Base | Security Additions & Enhancements | 0.23898 | 4023.87 | General Plant | Information Technology | Multiple | As per Alectra Security roadmap to key IT systems.
150541 | Base | Business Support | 0.16784 | 4021.57 | General Plant | Information Technology | Multiple | The project will encompass a variety of sub projects for the purpose of investigating new and emerging technologies. Building a culture of innovation Alectra will need a continued effort in remaining ahead of the trends and implementing new and more efficient ways of doing business. The projects that are slated for this years budget are room Artificial Intelligence and Wearable Technology
150679 | M-Factor | Alectra Drive for the Workplace | 0.15373 | 3997.47 | System Service | Capacity (Lines) | Multiple | Alectra Drive for the Workplace will demonstrate the value of integrating smart electric vehicle (EV) charging system at workplaces into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. The planned investment will help manage the flow of electricity needed to serve the building and EV charging stations, so that electricity costs are minimized for commercial customers while EV drivers have an easy and accessible charging solution.
150320 | M-Factor | Voltage Conversion - Dewitt MS , Hamilton | 2.6467 | 3972.49 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 12 outages and had 888,434 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
150043 | M-Factor | Rear Lot Renewal Project - East of Queen St. to Eastern Ave./North of Greenway St. | 2.5524 | 3714.07 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 1.7 outages lasting 9.7hrs per year based on a 3 year average.
102075 | Base | Major repairs, refurbishment, or modifications to switches/switchgear | 0.10114 | 3702.48 | System Renewal | Underground Asset Renewal | Powerstream | Switchgear and Switches in stores that repair/refurbishment of the units can allow them to be returned to service
150535 | Base | Network Segmentation - IT Infrastructure | 0.32788 | 3636.03 | General Plant | Information Technology | Multiple | As per Alectra Security roadmap to key IT systems with focus on network segmentation for corporate environments.
151200 | M-Factor | Alectra Single Platform Website ongoing | 0.10822 | 3548.17 | General Plant | Information Technology | Multiple | Ongoing enhancements to the Alectra platform to improve functionality for customers
150498 | Base | Capital Corrective Equipment Replacement - Stations Central South | 0.26932 | 3534.76 | System Renewal | Substation Renewal | Enersource | This project is intended to provide capital for all unplanned station equipment replacements in the Central South Operating Area (former Enersource) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150499 | Base | Capital Corrective Equipment Replacement - Stations Central North | 0.26932 | 3534.76 | System Renewal | Substation Renewal | Brampton | This project is intended to provide capital for all unplanned station equipment replacements in the Central North Operating Area (Brampton) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150497 | Base | Capital Corrective Equipment Replacement - Stations West | 0.26932 | 3534.76 | System Renewal | Substation Renewal | Horizon | This project is intended to provide capital for all unplanned station equipment replacements in the West Operating Area (former Horizon) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
151304 | Base | Cable Injection Project - (HAM) - Stone Church - Garth - Lincoln M. Alexander | 0.56877 | 3492.29 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 5 failures, or 18 failures per 100km. The average cable installation year is 1986 in this project scope.
150047 | M-Factor | Rear Lot Renewal Project - Royal Orchard - North | 1.8433 | 3478.27 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 3 failures per year lasting 4 hours per year based on 3 year average.
150774 | Base | Lines Central-North - Site Restorations | 0.10317 | 3434.48 | System Renewal | Overhead Asset Renewal | Brampton
150721 | Base | Lines Central-South - Site Restorations | 0.10317 | 3434.48 | System Renewal | Underground Asset Renewal | Enersource
150672 | Base | Burden Allocation - System Service | 0.10214 | 3353.13 | System Service | Capacity (Lines) | Horizon
150662 | Base | Station Sustainment PI System Expansion for CASCADE CARE | 0.062766 | 3302.05 | General Plant | Information Technology | Multiple | Expanding the use of the PI System to enable more efficient interfaces with other enterprise systems such as OMS and SCADA; Cascade is used to drive maintenance and generate work orders for maintenance of grid equipment
150263 | Base | Cable Replacement Project - East Left Behind Cable | 1.3044 | 3237.07 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in these areas have experienced 11 failures.
150345 | Base | Overhead Conductor Replacement - #6 Copper - Feeder WT10 | 0.43655 | 3209.69 | System Service | Safety & Security | Horizon | This project consists of overhead conductor replacement to mitigate safety risk and provide additional capacity.
150601 | Base | Advanced Metering Infrastructure (AMI) Security Audit - East | 0.064598 | 3170.74 | System Access | Metering | Powerstream | Multi-year project to renew meter data security to address emerging cyber threats.
151440 | Base | 2020 GUELPH - Transite Underground Duct Replacement | 0.26559 | 3168.07 | System Renewal | Underground Asset Renewal | Guelph | Replacement of Duct Structure which contains asbestoes a known carcinogen and impacts worker safety.
102065 | Base | Capital Corrective Equipment Replacement - East | 0.33425 | 3161.46 | System Renewal | Substation Renewal | Powerstream | This project is intended to provide capital for all unplanned station equipment replacements in the East Operating Area (former PowerStream area) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150611 | Base | Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.16496 | 3116.96 | System Renewal | Substation Renewal | Powerstream | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the East Operating Area (former PowerStream). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150623 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-WEST | 0.0057529 | 3095.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of animal guard installation in West
150622 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-CENTRAL | 0.0068351 | 3093.04 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Animal guard at Central South Stations
150621 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-EAST | 0.0086292 | 3081.51 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Animal guard at East Stations
150348 | Base | Overhead Conductor Replacement - #6 Copper - Feeder OT2 | 0.44008 | 3017.86 | System Service | Safety & Security | Horizon | This project consists of overhead conductor replacement to mitigate safety risk and provide additional capacity
150089 | M-Factor | Markham TS#3 T1/T2 "B" Differential Protections Upgrade | 0.084239 | 2935.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to replace the T1/T2 GEC solid state Transformer "B" Differential Protection relays at Markham TS#3 with new relays having fault recording capabilities
150699 | Base | Station Switchgear Replacement - Shawson MS43 LV1 | 1.056 | 2878.45 | System Renewal | Substation Renewal | Enersource | The existing LV1 switchgear at Shawson MS43 station houses gas circuit breakers that utilize vintage technology to provide short circuit protection against faults. These circuit breakers are technically obsolete and are prone to failure. Also the switchgear is non-arc-resistant and poses a potential safety hazard to Alectra personnel and even to the general public who happen to be in the vicinity of the station during a failure event. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions. Therefore, proactive replacement of the existing switchgear and associated equipment is a prudent strategy as the restoration of the system could take 8-10 months due to long equipment lead times in the event of a failure.
101625 | Base | Cyber Security Audit & Upgrades | 0.065433 | 2865.1 | General Plant | Information Technology | Multiple | This project would fund various activities and countermeasures to improve the cyber security posture of the Operations' Network. This will be a mandate for compliance to Ontario Cyber Security framework. The counter measures include: - an annual audit of the cyber security countermeasures in place; - implementation of new technologies to seal identified compromises; - replacement of deployed cyber security equipment deemed end of life or not able to deliver an expected level of service.
150783 | Base | Fleet_Central South Vehicle Replacement-Pick ups | 0.537 | 2848.48 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150671 | Base | Burden Allocation - System Renewal | 1.6642 | 2831.23 | System Renewal | Other System Renewal | Horizon
151107 | Base | Cable Replacement Project - 7143 Main Feeder | 0.8557 | 2821.57 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 4 outages, the length is 1,325 m, and the average cable age is 39 years old.
150632 | Base | AMI Gatekeeper Expansion - Brampton RZ | 0.029777 | 2820.22 | System Access | Metering | Brampton | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
150141 | Base | Cable Replacement Project – (M49) - Steeles and Fairway Heights, Markham | 2.9255 | 2807.08 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 37 years old and will be 38 when project starts (2020).
150572 | Base | Cable Replacement Project - (J4) - Queen - Clark - Bramalea - Kensington - Knightsbridge, Brampton | 1.0937 | 2794.02 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 9 outages due to cable failures from 2007 to 2017 with average duration of 127 minutes.
151144 | Base | Cable Replacement Project and Transformers Replacement - Rathburn Rd. W, Mississauga | 1.1758 | 2657.53 | System Renewal | Underground Asset Renewal | Enersource | Tis project is split into 3 phases. 2 phases are being completed in 2019, the duct structure for third phase is expected to be completed in 2019 and the final phase is will be done in 2020.
150666 | M-Factor | Facilities_John_Roof Deck – Rooftop Renovation | 0.41624 | 2610.29 | General Plant | Facilities Management | Horizon | Removal of cooling tower, chillers and lines that contain R-22 refrigerant (hazardous substance), replace emergency fire exit pathway on the roof from the Hughson St to the John St buildings to ensure employee safety and meet with City Bylaws. Repair roof as a result of the equipment removals.
150332 | M-Factor | Non-Wires Alternative Pilot | 0.77068 | 2536.94 | System Service | Capacity (Stations) | Powerstream | The project will provide customers with increased flexibility to make decisions about their electricity consumption, generation, and costs; it leads to more efficient integration of DERs which yields greater benefits to customer, system reliability, and power quality. This project will also provide the opportunity to increase operational efficiency and improved asset management to enhance service to customer and defer and/or reduce infrastructure investment needs in York Region.
151042 | Base | Markham TS1 Firewall Upgrade | 0.20427 | 2531.42 | System Service | System Control, Comm'ns & Performance | Powerstream | Markham TS1 Firewall Upgrade
150681 | Base | Data Analytics - IT/OT Infrastructure | 0.34691 | 2527.57 | General Plant | Information Technology | Multiple | This project will develop a data analytics platform to provide enhanced customer value by implementing preventative measures to improve overall outage detection and prediction with use-cases focusing on Distributed Energy Resource (DER) monitoring, integration and optimization.
150580 | Base | West Region Tools and Test Equipment | 0.20228 | 2494.28 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
150627 | Base | Station Equipment Temperature Monitoring-EAST | 0.075261 | 2479.48 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of Station Temperature Monitoring system in Central North and it enables controlled emergency loading beyond the nameplate rating.
150629 | Base | Station Equipment Temperature Monitoring-WEST | 0.075261 | 2479.48 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of Station Temperature Monitoring system in West and it enables controlled emergency loading beyond the nameplate rating.
151202 | Base | Purchase of Major Station Tools - Multi-year | 0.01 | 2472.82 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
150625 | Base | Purchase of Major Tools - Muliti Year-CENTRAL | 0.021644 | 2395 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150624 | Base | Purchase of Major Tools - Muliti Year-EAST | 0.021644 | 2395 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150626 | Base | Purchase of Major Tools - Muliti Year-WEST | 0.021644 | 2395 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
150707 | Base | Alectra Station Access Harmonization - Abloy CLIQ system expansion-CENTRAL | 0.014626 | 2376.26 | System Service | Safety & Security | Enersource | This project consists of upgrade to station access in Central South. Provides added security and risk mitigation for keys that are lost or stolen and provides a system that tracks key and lock cylinder usage as well provides the ability to activate and deactivate keys from an application
150705 | Base | Alectra Station Access Harmonization - Abloy CLIQ system expansion-EAST | 0.014626 | 2371.05 | System Service | Safety & Security | Brampton | This project consists of upgrade to station access in Central North. Provides added security and risk mitigation for keys that are lost or stolen and provides a system that tracks key and lock cylinder usage as well provides the ability to activate and deactivate keys from an application
101761 | Base | Unforeseen Projects Initiated by the customer PS South | 0.36099 | 2365.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151061 | Base | Markham TS2 Firewall Upgrade | 0.033266 | 2334.71 | System Service | System Control, Comm'ns & Performance | Powerstream | Markham TS2 Firewall Upgrade
151098 | Base | Station Switchgear Replacement - Battleford MS54 LV1 | 1.2679 | 2296.96 | System Renewal | Substation Renewal | Enersource | The existing LV1 switchgear at Battleford MS54 station houses gas circuit breakers that utilize vintage technology to provide short circuit protection against faults. These circuit breakers are technically obsolete and are prone to failure. Also the switchgear is non-arc-resistant and poses a potential safety hazard to Alectra personnel and even to the general public who happen to be in the vicinity of the station during a failure event. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions. Therefore, proactive replacement of the existing switchgear and associated equipment is a prudent strategy as the restoration of the system could take 8-10 months due to long equipment lead times in the event of a failure.
151244 | Base | Fault Indicators | 0.01 | 2243.02 | System Service | System Control, Comm'ns & Performance | Guelph | The scope of this project is to install Fault Indicators in Guelph. The project would include the fault indicators communicating to the existing SCADA and will improve the fault locating and improve SAIDI
150708 | Base | Alectra Station Access Harmonization - Abloy CLIQ system expansion-North&TS | 0.093238 | 2235.48 | System Service | Safety & Security | Powerstream | This project consists of upgrade to station access in East. Provides added security and risk mitigation for keys that are lost or stolen and provides a system that tracks key and lock cylinder usage as well provides the ability to activate and deactivate keys from an application
150542 | Base | Meeting Room Transformation - IT/OT Infrastructure | 0.31036 | 2222.94 | General Plant | Information Technology | Multiple | The meeting room transformation project aim to leverage and deliver automation technology for better use of the meeting space; centralized control; consistent experiences across the enterprise; and standard design of the physical space. Efficiencies will be met when meeting rooms can start on time due to the ease of use and collaboration efforts will reduce travel and health and safety concerns. With Alectra being so geographically diverse, it imperative to keep the employees off the road as much as possible to reduce the risk of injury.
151181 | Base | Cable Replacement Project - Left Behind Cable, Brampton | 0.38278 | 2163.34 | System Renewal | Underground Asset Renewal | Brampton | This project is to address cables which were part of a cable injection project but were ultimately not injectable at the time of project execution. These 'left behind' segments must be addressed, if they are left in the system they could cause a failure. Customers would not only experience an outage, but question the utilities work practices as we would have addressed only a portion of the cables instead of all the cables which could cause an outage.
151192 | Base | Asset Register | 0.4815 | 2082.28 | General Plant | Information Technology | Multiple | Develop an enterprise asset register application to support Asset Management requirements to manage and track movement of assets, asset demographics, equipment failures, and support asset condition assessments and business case modelling.
150661 | Base | SS2019-Purchase and Installation of Online Transformer tap Changer Filtration Systems - CENTRAL | 0.021615 | 2055.7 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of transformer tap changer filtration system in Central South
150663 | Base | Technology Changes in Control Room | 0.3279 | 2052.17 | General Plant | Facilities Management | Multiple | Replace aging equipment within the Control room to ensure optimal performance in managing the distribution assets
102728 | Base | Station Switchgear Replacement - Big Bay Point MS304 | 0.23668 | 2051.19 | System Renewal | Substation Renewal | Powerstream | This substation project consists of replacing the existing switchgear and associated equipment, as well as the primary circuit switcher at Big Bay Point MS304. The current line-up is technically obsolete, in poor condition, and is prone to failure. A failure could affect a large number of customers and potentially result in complete loss of supply from the station, requiring load transfer to another station. Proactive replacement of the existing equipment is a prudent strategy as system reliability would be greatly affected in the event of a failure. Additionally, the restoration of the system to normal conditions could take 8-10 months due to long equipment lead times.
150675 | Base | Emerging Customer Inititated Work Central (Mississauga) | 0.15929 | 2049.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
101764 | Base | Road Authority Expenditure PS North | 0.96617 | 2038.3 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
150604 | Base | Smart Meter Network Expansion - PowerStream RZ | 0.26645 | 2035.93 | System Access | Metering | Powerstream | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
151092 | Base | Distribution Automation - Central South | 0.522 | 2013.5 | System Service | SCADA and Automation | Enersource | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151030 | Base | Addition of Sensors to SCADA Controllable 44kV LISs in Brampton | 0.2591 | 2012.97 | System Service | System Control, Comm'ns & Performance | Brampton | This project is to add sensors to the 44KV switches in Central North
151068 | Base | Return to Service of Smart Fault Indicators - East | 0.16648 | 1998.06 | System Renewal | Substation Renewal | Powerstream | This project involves making necessary modifications to 50 previously installed SMART Fault Indicators in the East Operating Area (former PowerStream) so as to return them to service. These devices will greatly improve monitoring capability and facilitate prompt decision making during emergency situations, thus reducing outage durations.
150694 | M-Factor | Cityview microgrid enhancements | 0.045798 | 1985.17 | System Service | Capacity (Lines) | Powerstream | The project is to understand how microgrids can be integrated into the distribution grid in a safe and reliable manner. The microgrid is used to evaluate integration and connection to the distribution grid, while reducing the building's load, greenhouse gas emissions, and increasing its resiliency to grid outages.
100268 | Base | Low Voltage Transformer Bushing Replacement - Markham TS#3 - T1/T2 | 0.27397 | 1882.55 | System Renewal | Substation Renewal | Powerstream | This project involves replacing end-of-life low-voltage bushings on Markham TS#3 power transformers. Bushing failure would result in environmental risk due to spilled oil and in transformer failure causing an extended power interruption.
101013 | Base | Planned Circuit Breaker Replacement Markham TS#3 - E & Z Buses | 0.50357 | 1832.29 | System Renewal | Substation Renewal | Powerstream | The existing 27.6 kV circuit breakers at Markham TS#3 have been identified in the Asset Condition Assessment (ACA) Model as requiring replacement due to obsolescence and historical failures. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions.
151224 | Base | Cable Replacement - (920) - Scottsdale Drive Subdivision, Guelph | 0.56697 | 1807.87 | System Renewal | Underground Asset Renewal | Guelph
150801 | Base | Fleet_West_Vehicle Replacement_Bucket Truck 1-286 | 0.4 | 1804.37 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150670 | Base | SCADA FDIR | 0.11803 | 1798.98 | System Service | SCADA and Automation | Multiple | Fault Detection, Isolation, and Restoration implementation, next generation of distribution automation technology. This utilizes devices which are already automated and integrates them into the OMS system such that devices perform self healing after a fault. in some cases reducing the outage time to less then 1 minute.
150680 | M-Factor | Alectra Drive at Home | 0.4622 | 1731.44 | System Service | Capacity (Lines) | Multiple | Alectra Drive at Home will demonstrate the value of integrating smart electric vehicle (EV) charging system in multi rise buildings as well as residential homes into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. It will also provide insight into the characteristics of EV Charging, how EVs can be aggregated and controlled to provide the benefit at the local, regional and provincial system levels, and customer response to these control and optimization strategies.
151201 | Base | Purchase of New Critical Spare Parts - Guelph | 0.01 | 1727.97 | System Renewal | Substation Renewal | Guelph | This project involves procurement of critical spare parts for stations in the South West Operating Area (Guelph) so as to facilitate prompt repair of failed assets during emergency situations.
150108 | Base | Low Voltage Transformer Bushing Replacement - Vaughan TS#3 - T1/T2 | 0.31615 | 1677.09 | System Renewal | Substation Renewal | Powerstream | This project involves replacing end-of-life low-voltage bushings on Vaughan TS#3 power transformers. Bushing failure would result in environmental risk due to spilled oil and in transformer failure causing an extended power interruption.
150619 | Base | Purchase of Critical Spare Parts - West | 0.02186 | 1648.51 | System Renewal | Substation Renewal | Horizon | This project involves procurement of critical spare parts for stations in the West Operating Area (former Horizon) so as to facilitate prompt repair of failed assets during emergency situations.
151136 | Base | C55 Alectra: Optimization of Business Practices | 0.54111 | 1624.9 | General Plant | Information Technology | Multiple | Optimizing the current software to communicate with other systems such as the ERP will allow for more efficient and effective budgeting processes and consolidation of information allowing for consistent reporting of the information from one system.
151137 | Base | Cable Replacement Project - Main Fedeer(s) upgrade - 68F2, 68F4, 68F7, 83F5, 83F3 | 0.82593 | 1614.34 | System Renewal | Underground Asset Renewal | Enersource | Only 2 outages on all of the feeders combined. If we can replace it with feeders with 4-5 failures, we can show better reliability analysis. The combined length of these feeders is 3,885 m.
151436 | Base | Cable Injection-011 - Area 58 & 59- Winston Churchill & The Collegeway, Mississauga | 1.7463 | 1614.06 | System Renewal | Underground Asset Renewal | Enersource | There are 14 outages, we are injecting a total of 69,795 m of cable for this project, and the average age of the cable is 30 years.
150333 | Base | Overhead Conductor Replacement - #6 Copper - Feeder OT8 | 0.67255 | 1610.61 | System Service | Safety & Security | Horizon | This project consists of overhead conductor replacement to mitigate safety risk and provide additional capacity.
150902 | Base | Unit # 396 Backhoe replacement | 0.16 | 1591.88 | General Plant | Fleet Renewal | Powerstream
150642 | Base | Proactive Replacement of Remote Terminal Units - Central North | 0.1584 | 1582.3 | System Renewal | Substation Renewal | Brampton | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the Central-North Operating Area (Brampton). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
150617 | Base | Purchase of Critical Spare Parts - Central North | 0.029219 | 1568.76 | System Renewal | Substation Renewal | Brampton | This project involves procurement of critical spare parts for municipal stations in the Central North Operating Area (Brampton) so as to facilitate prompt repair of failed assets during emergency situations.
151087 | Base | Switchgear Replacement | 0.23636 | 1559.43 | System Renewal | Underground Asset Renewal | Guelph | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150618 | Base | Purchase of Critical Spare Parts - Central South | 0.03463 | 1556.59 | System Renewal | Substation Renewal | Enersource | This project involves procurement of critical spare parts for stations in the Central South Operating Area (former Enersource) so as to facilitate prompt repair of failed assets during emergency situations.
102077 | Base | Major repair, refurbishment, or conversions of distribution transformers | 0.030341 | 1540.55 | System Renewal | Transformer Renewal | Powerstream | Transformers returned or in stores where repair/refurbishment of the unit can return it to service at a lower cost then purchase of a new unit
151222 | Base | Concrete Structures | 0.19086 | 1469.44 | System Renewal | Underground Asset Renewal | Guelph | Replacement of lids on civil structures to avoid public risk
150410 | M-Factor | 42M66 OH Feeder Egress Mississauga Rd, Bovaird to CNR | 0.13232 | 1457.65 | System Service | Capacity (Lines) | Brampton | 42M66 OH Feeder extension from Mississauga Rd from Bovaird Dr. to CNR Tracks to feed new developments in the area of Bovaird drive and Mississauga road.
150858 | Base | Fleet_West_Vehicle Replacement_SUVs | 0.28 | 1425.59 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150334 | Base | Distribution Automation - West | 0.72 | 1424.45 | System Service | SCADA and Automation | Horizon | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
150019 | Base | Cable Injection Project - (M41) - Woodbine and Elgin Mills, Markham | 0.11368 | 1413.89 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 40 years old and will be 41 when project starts (2020).
151052 | Base | Emerging Customer Initiated Work - Relocations | 0.0919 | 1412.11 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
151207 | Base | On-line Dissolved Gas Monitoring | 0.1 | 1386.01 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of installation of Online DGA monitoring system at MS in Guelph. Online DGA has proven to be invaluable in diagnosing a potential transformer failure as well as assessing the health of a transformer
150751 | Base | Facilities_East_Capital Replacement Investment Support | 0.099527 | 1374.32 | General Plant | Facilities Management | Powerstream | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150641 | Base | Replace 230kV Primary Switches - Jim Yarrow TS | 0.17015 | 1372.72 | System Renewal | Substation Renewal | Brampton | The primary switches at Jim Yarrow TS are non-standard, have a history of problems, particularly with alignment issues, and have no spare parts on hand. Failure of one of these switches could result in loss of supply to a 125 MVA power transformer.
151134 | Base | Cable Replacement Project - Winston Churchill consolidation - 49F6 and 49F4 | 0.31889 | 1358.05 | System Renewal | Underground Asset Renewal | Enersource | This project is already with design. We are not doing this like-for-like. Miron has completed D10-111-001 for removal of the bad feeders.
150349 | Base | Overhead Conductor Replacement - #6 Copper - Feeder WL1 | 0.70615 | 1347.16 | System Service | Safety & Security | Horizon | This project consists of overhead conductor replacement to mitigate safety risk and provide additional capacity
150830 | Base | Fleet_West_Vehicle Replacement_Dump Truck_1-330 | 0.07 | 1345.36 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151296 | Base | Cable Injection Project - (SCH) - Welland - Bunting - Carlton - Cushman | 0.26447 | 1345.07 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 48 failures per 100km. The average cable installation year is 1989 in this project scope.
150335 | Base | Pole Renewal - West | 2.1503 | 1338.4 | System Renewal | Overhead Asset Renewal | Horizon | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
150362 | M-Factor | Voltage Conversion - Dufferin St S, between MS431 and Albert St S, Alliston | 0.38517 | 1328.26 | System Renewal | Overhead Asset Renewal | Powerstream | Customers in this area experienced 11 outages and had 15,031,879 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
102102 | Base | Enterprise File Synchronization and Sharing Platform | 0.012509 | 1307.59 | General Plant | Information Technology | Multiple | Alectra is looking for a secure Enterprise File Synchronization and Sharing solution that will increase productivity of internal and external teams by facilitating seamless collaboration of corporate data anywhere , anytime, and on any device without the restrictions of having to connect to the Alectra network. The overarching goal of this implementation will be to provide a balance between delivering business productivity and securing enterprise information.
150502 | Base | On-Line Dissolved Gas Oil Monitoring of 10 MS Transformers - EAST | 0.10319 | 1292.71 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Online DGA monitoring system at MS in East. Online DGA has proven to be invaluable in diagnosing a potential transformer failure as well as assessing the health of a transformer
150738 | Base | Facilities_West_Capital Replacement Investment Support | 0.77379 | 1289.1 | General Plant | Facilities Management | Horizon | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150573 | Base | Oracle ULA Extension | 1.5 | 1265.44 | General Plant | Information Technology | Multiple | MULTI ANSWER
150350 | Base | Overhead Conductor Replacement - #6 Copper - Feeder WL4 | 0.80059 | 1260.56 | System Service | Safety & Security | Horizon | This project consists of overhead conductor replacement to mitigate safety risk and provide additional capacity
151138 | M-Factor | Voltage Conversion - MS-2 Church St, Brampton | 3 | 1255.22 | System Renewal | Overhead Asset Renewal | Brampton | From 2015-2017 customers in this area experienced 11 outages and had 20,372 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
102241 | Base | Proactive Replacement of Remote Terminal Units - East | 0.099693 | 1239.66 | System Renewal | Substation Renewal | Powerstream | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the East Operating Area (former PowerStream). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
151183 | Base | OH Rebuild Project - Church Street | 0.80925 | 1238.59 | System Renewal | Overhead Asset Renewal | Enersource | This project involves the replacment of 55 poles, 35 which are in very poor and poor condition. Due to the significantly high population of poor poles this area is a candidate for multi-pole line faliure under high winds.
151146 | Base | Cable Replacement and Transformers Replacement - Project - Folkway, Mississauga | 3.981 | 1228.76 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 34 outages, the length is 10,432 m
150814 | Base | Fleet_West_Vehicle Replacement_Step Vans 1-279 & 1-281 | 0.4 | 1179.47 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151064 | Base | Secondary Pedestals -St. Catharines | 0.19496 | 1153.93 | System Service | Safety & Security | Horizon | This project involves the replacment of above grade steel secondary pedestals which pose a safety risk to the general public
150044 | M-Factor | Rear Lot Renewal Project - Blake/Kempenfelt | 0.30779 | 1144.48 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 0.66 outages lasting 2.2hrs per year based on a 3 year average.
150254 | M-Factor | Cable Replacement Project - (A02) - Steeplechase Ave, Aurora | 2.892 | 1133.22 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 outages to date. Cable is 45 years old and beyond EUL
101125 | Base | Lines Mobile Equipment - IT/OT Infrastructure | 0.078888 | 1119.08 | General Plant | Information Technology | Multiple | This budget covers the deployment of mobile technology - laptops/field tablets and accessories - within the Lines Department to gain efficiencies in field operations. By deploying this technology, the Lines area can move away from a paper-based to a more electronic environment. In future, it is envisioned that, for example, mobile applications will facilitate the electonic transmission of work orders and electronic record keeping (asset tracking, tailboards, switching orders, timesheets). This will allow for streamlined operational processes and record-keeping, thereby supporting corporate technological initiatives such as the GIS, Outage Management System, and future Workforce Management system. At present, all Lines Management personnel and Subforemen have laptops, facilitating activities such as viewing of the GIS, electronic Asset Tracking Forms, and use of OMS Responder Mobile. Expenditures in this area will allow for more deployment of field devices among Lines crews and for the implementation of more computerized processes.
150500 | Base | On-Line Dissolved Gas Oil Monitoring of 10 MS Transformers - WEST | 0.10319 | 1116.55 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of Transformer bushing monitoring system in West
150856 | Base | Fleet_West_Vehicle Replacement_Dump/Cargo Truck | 0.14 | 1114.55 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150908 | Base | Fleet East Unit # 103 Bucket truck replacement | 0.25 | 1107.23 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150139 | Base | Cable Replacement Project – (B19) - Donald St and Simcoe Terrace, Barrie | 0.5793 | 1101.95 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 44 years old and will be 45 when project starts (2020).
150570 | Base | Alectra West Substation Ground Grid Installations | 0.28056 | 1091.19 | System Service | Safety & Security | Horizon | This project is to install ground grid at East Stations
151204 | Base | Upgrade to Station Facilities (Buildings/Civil work) Multi-year | 0.01 | 1089.29 | General Plant | Facilities Management | Guelph | This project involves work involving structural components of stations, including windows, brickwork, roofs, foundations, drainage, doors, etc. at stations in the SouthWest Operational Area. Not keeping up with this work would result in advanced deterioration resulting in even greater maintenance costs, potential safety concerns and potential failure of the electrical equipment in the building causing power interruptions.
150879 | Base | Fleet East Vehicle replacement - Pickup 2500 | 0.21218 | 1086.88 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150752 | Base | Cityview back up generator replacement | 0.41269 | 1071.5 | General Plant | Facilities Management | Powerstream
151041 | Base | Protection Logic Upgrades - East MSs (North) | 0.080038 | 1061.11 | System Service | System Control, Comm'ns & Performance | Powerstream
150578 | Base | Alectra - Microsoft Software | 0.1 | 1020.9 | General Plant | Information Technology | Multiple | Compliance for Alectra employees for Microsoft application suite of products to perform daily operation .
150776 | Base | Fleet_Central South Equipment Replacement-forklift | 0.045 | 1006.1 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150257 | M-Factor | Cable Replacement Project - (V15) - Jardin Dr, Vaughan | 2.9337 | 1004.3 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 5 outages.
150392 | Base | Storage Upgrade | 0.703 | 994.99 | General Plant | Information Technology | Multiple | Upgrade on premise Enterprise Storage platform in addition to increased capacity requirements as a result of employee and customer demand for data retention. Off Premise storage costs (SharePoint Online, One Drive, Development, test and production environments)
150916 | Base | Fleet East Vehicle replacement - Extended Vans | 0.10687 | 987.32 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151091 | Base | Switchgear Renewal - Central South | 3.611 | 982.44 | System Renewal | Underground Asset Renewal | Enersource | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150882 | Base | Fleet East Vehicle replacement - Pickup 3500 | 0.20229 | 973.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150890 | Base | Fleet East Vehicle replacement - Work van | 0.0618 | 966.83 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151159 | Base | Fault Indicator Installation and Replacement - Hamilton and St. Catharines | 0.26813 | 966.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of fault indicator installation in West
151294 | Base | Cable Injection Project - (SCH) - Lakeshore - Stanley - Parnell - Chancery | 0.062817 | 953.78 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 55 failures per 100km. The average cable installation year is 1985 in this project scope.
151065 | Base | Manhole Lid Replacement | 0.25592 | 925.3 | System Renewal | Underground Asset Renewal | Horizon | Replacement of lids on civil structures to avoid public risk
150911 | Base | Fleet East Unit # 81 Single bucket truck replacement | 0.46062 | 923.32 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151280 | Base | Cable Injection Project - (SCH) - Millward - Jeanette Drive - Trevor | 0.046588 | 909.23 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 333 failures per 100km. The average cable installation year is 1992 in this project scope.
150819 | Base | Fleet_West_Vehicle Replacement_Cargo Vans 1-347, 1-350, 1-368, 1-349, 1-110, 1-111, 1-114 | 0.35 | 890.03 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150892 | Base | Fleet East Vehicle replacement - Van pool vans | 0.0824 | 875.45 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150317 | M-Factor | Voltage Conversion - Deerhurst MS, Hamilton | 2.9645 | 869.07 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 6 outages and had 121,838 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
150923 | Base | Fleet_Central North Vehicle Replacement-DBL.Bucket 49 | 0.56 | 854.86 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150904 | Base | Fleet East Yearly Light and Misc equipment | 0.017219 | 846.86 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150780 | Base | Fleet_Central South Replacement-DBL>Bucket 234-05 | 0.58 | 844.63 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150907 | Base | Fleet East Unit # 361 digger truck | 0.55167 | 839.82 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150834 | Base | Fleet East Vehicle replacement - Unit # 500 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150835 | Base | Fleet East Vehicle replacement -Unit # 507 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150836 | Base | Fleet East Vehicle replacement -Unit # 515 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150837 | Base | Fleet East Vehicle replacement -Unit # 522 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150838 | Base | Fleet East Vehicle replacement -Unit # 534 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150867 | Base | Fleet East Vehicle replacement -Unit # 535 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150840 | Base | Fleet East Vehicle replacement -Unit # 536 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150841 | Base | Fleet East Vehicle replacement -Unit # 537 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150845 | Base | Fleet East Vehicle replacement -Unit # 549 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150829 | Base | Fleet East Vehicle replacement -Unit # 553 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151149 | Base | Fleet East Vehicle replacement - Unit 523 SUV | 0.03607 | 825.2 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150915 | Base | Fleet East Vehicle replacement - Pickup truck 1500 | 0.037131 | 824.23 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150917 | Base | Fleet East Vehicle replacement - Passenger Van | 0.0412 | 820.5 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150788 | Base | Fleet_Central South Vehicle Replacement-Arrowboard | 0.012 | 765.85 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
101622 | Base | DACS Inverters and RTU's removal - East | 0.026229 | 765.32 | System Renewal | Substation Renewal | Powerstream | This project involves removal of obsolete and out-of-service DACs inverters, RTUs and associated wiring at stations in the East Operating Area (former PowerStream) so as to remove clutter, thus simplifying future work and freeing up space for future station upgrades.
150824 | Base | Fleet_West_Vehicle Replacement_Pickups. | 0.22 | 758.91 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
101632 | Base | Obsolete Revenue Metering Removal from TSs | 0.026466 | 739.84 | System Service | Safety & Security | Powerstream | Evolution of the distribution system to permit more efficient integration of DERs to yield 18
151072 | M-Factor | Station Service Transfer Upgrade - Vaughan TS#3 | 0.1185 | 725.89 | System Renewal | Substation Renewal | Powerstream | This project involves replacing the manual station service transfer switch with an automatic transfer switch. This work will mitigate the risk of loss of the entire station due to DC system failure as occurred in March 2016, thus avoiding another major lengthy power interruption.
151178 | M-Factor | Cable Replacement Project - Mason Heights | 0.71457 | 715.85 | System Renewal | Underground Asset Renewal | Enersource | From 2015-2017 customers in this area experienced 5 outages. 1 cable with 4 failures. 2 cables with 2 failures.
150827 | Base | Fleet_West_Equipment Replacement_Backhoe | 0.09 | 699.29 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150869 | Base | Fleet_ Central North Vehicle Replacement-Puller/tensioner 194 | 0.25 | 692.98 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151082 | Base | SCADA Infrastructure | 0.14814 | 688.19 | System Service | System Control, Comm'ns & Performance | Guelph
150706 | Base | Alectra Station Access Harmonization - Abloy CLIQ system expansion-WEST | 0.014595 | 685.59 | System Service | Safety & Security | Horizon | This project consists of upgrade to station access in West
151058 | Base | Distribution Transformer Replacements & Upgrades | 0.34158 | 682.68 | System Renewal | Transformer Renewal | Guelph | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150719 | Base | Upgrade of JMUX Optical Interfaces - Alectra East SONET Ring | 0.25695 | 676.42 | System Service | System Control, Comm'ns & Performance | Powerstream
150669 | Base | Burden Allocation - System Access | 0.60623 | 669.62 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151048 | Base | Station Switchgear Replacement - City Centre North MS47 HV1 | 0.32554 | 655.68 | System Renewal | Substation Renewal | Enersource | City Centre North MS is located centrally adjacent to Square One shopping mall, and feeds a large number of customers. It also provides back up to City Centre South MS – hence, reliability is very important. This substation project consists of replacing the HV1 44 kV switchgear and associated breaker and protection in City Centre North MS47. The current transformer protection device consists of a vintage 1973 Markham Electric oil with spring actuator type 44 kV circuit breaker. Station subject matter experts have identified this breaker as problematic. Parts are no longer available and this equipment is prone to failure. Proactive replacement of the LV switchgear, circuit breakers and protective equipment is a prudent strategy as system reliability would be greatly affected in the event of a failure. Additionally, the restoration of the system to normal conditions could take 8-10 months due to long equipment lead times.
102166 | Base | SQL Expansion - IT Infrastructure | 0.094522 | 635.85 | General Plant | Information Technology | Multiple | Expand existing SQL infrastructure to meet project demands and natural growth of database. Add system capacity, improve performance, and reduce the risk of downtime due resource constraints.
150203 | Base | Station Equipment Temperature Monitoring-NORTH & TS | 0.063979 | 614.42 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of Station Temperature Monitoring system in East and it enables controlled emergency loading beyond the nameplate rating.
150871 | M-Factor | Fleet_Central North Vehicle Replacement-Step Van 8108 | 0.22 | 594.61 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150496 | Base | iPass Project Management – Planned Capital - West | 0.69089 | 589.28 | System Renewal | Underground Asset Renewal | Horizon | Help in optimizing DER performance and efficiency to improve addressing overall energy needs.
150846 | M-Factor | Fleet_West_Vehicle Replacement_Step Vans | 0.36 | 589.19 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150732 | Base | Vault Cover Rehabilitation | 0.10916 | 582.22 | System Renewal | Underground Asset Renewal | Powerstream | Replacement of lids on civil structures to avoid public risk
102046 | Base | Purchase of Major Tools - Muliti Year-North & TS | 0.045452 | 565.1 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150905 | Base | Fleet East Multi Year Shop tools | 0.0107 | 544.12 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of tools and shop equipment required to repair and maintain vehicles to ensure vehicle availability to support capital systems projects.
101816 | Base | Alectra East (South), Fault Indicator Installation and Replacement Multi-year initiative | 0.23904 | 542.12 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - North Region which will result improved outage response, operational efficiency, and reliability
151085 | M-Factor | Rear Lot Conversions | 0.1135 | 530.82 | System Renewal | Rear Lot Conversion | Guelph
101134 | Base | Alectra East (North), Fault Indicator Installation and Replacement Multi-year initiative | 0.24128 | 527.43 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - South Region which will result improved outage response, operational efficiency, and reliability
150437 | Base | OT GIS & OMS Enhancements | 0.32543 | 519.79 | General Plant | Information Technology | Multiple | Ongoing productivity enhancements to core GIS and OMS platforms to meet internal and customer demand for functionality.
151179 | M-Factor | Cable Replacement Project - Area of Erin Mills Parkway and South Millway | 0.53426 | 482.04 | System Renewal | Underground Asset Renewal | Enersource | From 2015-2017 customers in this area experienced 4 outages. 1 cable with 4 failures.
150602 | Base | Smart Meter Test Facility - PowerStream RZ | 0.019794 | 471.4 | System Access | Metering | Powerstream | Multi-year project to expand the capability of the Meter Test Facility to test increasing types of meters and AMI systems before they are placed into production.
150782 | M-Factor | Fleet_Central South Vehicle Replacement-Step Van | 0.22 | 438.9 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151141 | M-Factor | Cable Replacement and Transformers replacement - Project - Windjammer, Mississauga | 2.7095 | 432.38 | System Renewal | Underground Asset Renewal | Enersource | From 2005-2019 YTD customers in this area experienced 32 failures. This area has had an average of 2.3 outages per year.
102027 | Base | Purchase of Critical Spare Parts - Multiyear - East | 0.070612 | 427.82 | System Renewal | Substation Renewal | Powerstream | This project involves procurement of critical spare parts for transformer and municipal stations in the East Operating Area (former PowerStream) so as to facilitate prompt repair of failed assets during emergency situations.
101781 | Base | iPass Project Management – Planned Capital - East | 0.38201 | 408.86 | System Renewal | Overhead Asset Renewal | Powerstream | Estimating the effects of DER contribution at the feeder and region levels to further optimize the energy flows between the Utility and its consumers,
150494 | Base | iPass Project Management – Planned Capital - Central-North | 0.37996 | 408.86 | System Renewal | Overhead Asset Renewal | Brampton | Predicting the influence of weather conditions and DER contribution simultaneously on the power grid, for proactively mitigating local outages,
150495 | Base | iPass Project Management – Planned Capital - Central-South | 0.37996 | 408.86 | System Renewal | Overhead Asset Renewal | Enersource | Enable better visibility towards preventive equipment maintenance needs arising due to DER penetration which will further help mitigate outage risks,
150607 | M-Factor | Station LED Lighting Upgrades - Central | 0.026572 | 407.91 | System Renewal | Substation Renewal | Enersource | Replacement of inefficient lighting fixtures and lamps at stations in the Central Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150606 | M-Factor | Station LED Lighting Upgrades - EAST | 0.026572 | 407.91 | System Renewal | Substation Renewal | Brampton | Replacement of inefficient lighting fixtures and lamps at stations in this Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
151158 | M-Factor | Fleet_Central South_Vehicle Replacement -Vans | 0.081 | 407.26 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150786 | M-Factor | Fleet_Central South Vehicle Replacement-SUV | 0.035 | 403.38 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150868 | M-Factor | Fleet_Central North Vehicle Replacement-180 Loader | 0.29 | 399.89 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150920 | M-Factor | Fleet East Vehicle addition - Van pool van | 0.0412 | 386.61 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150831 | M-Factor | Fleet_West_Vehicle Replacement_SUVs_1-268,1-226,1-227 | 0.12 | 376.22 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150513 | Base | Installation of SWI Video security system at 4 MS stations per year - Annual Multi-year initiative-EAST | 0.15244 | 372.49 | System Service | Safety & Security | Brampton | This project consists of installation of SWI Video security system in CentralNorth
102034 | Base | Upgrade to Station Facilities (Building / Civil work) Multi-year - East | 0.1326 | 339.91 | System Renewal | Substation Renewal | Powerstream | MULTI ANSWER
150549 | Base | ServiceNow Expansion - IT Infrastructure | 0.057851 | 322.89 | General Plant | Information Technology | Multiple | Building and adding features within ServiceNow we will eliminate outdated processes by automating more tasks and decisions allowing us to be more efficient and productive. Enhancements include the automation of the flow of data between other systems and across programs used by various departments and ServiceNow. Servicebots will be used as ServiceNow learns from past patterns, in order to predict future outcomes, including determining risks, assigning owners, and categorizing work. Learned models set the category of the IT request and assign the task to the right team, as well as calculate associated risk of action or inaction. This capability will improve the speed and efficiency of IT service delivery.
150712 | Base | New JMUX Node at AMS4 | 0.10085 | 311.33 | System Service | System Control, Comm'ns & Performance | Powerstream | New JMUX Node at AMS4
102537 | Base | Insulator Replacement - 44kV Multi year project | 0.1524 | 294.58 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of non-polymer insulators (Areas are prioritiezed by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
150100 | Base | Convert Three MS's in Bradford to WiMax Communications | 0.022747 | 294.32 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of conversion of three Bradford MS to Wimax communication
150101 | Base | Convert Three MS's in Alliston to WiMax Communications | 0.023069 | 294.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of conversion of three Alliston MS to Wimax communication
150610 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - Central | 0.020881 | 289.6 | System Renewal | Substation Renewal | Enersource | Existing driveways at stations in the Central Operational Area that are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150609 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - East | 0.020881 | 289.6 | System Renewal | Substation Renewal | Brampton | Existing driveways in this Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150612 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - West | 0.020881 | 289.6 | System Renewal | Substation Renewal | Horizon | Existing driveways in the West Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150870 | M-Factor | Fleet_Central North Vehicle Replacement-Van 5910 | 0.05 | 288.94 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102050 | Base | Various Stations-Station Lighting Upgrade/Retrofit-Energy Efficiency Lighting-initiative Multi-year - East | 0.054219 | 239.8 | System Renewal | Substation Renewal | Powerstream | Replacement of inefficient indoor and outdoor lighting fixtures and lamps at stations in the East Operating Area (former PowerStream) will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
103028 | Base | Installation of a New JMUX Node at VTS1-T1T2 | 0.072623 | 238.33 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of JMUX node at Vaughan TS1
150391 | Base | Wireless LAN Upgrade | 0.49548 | 235.12 | General Plant | Information Technology | Multiple | Corporate Wireless LAN upgrade to replace end of life wireless infrastructure in corporate and operation center locations.
151075 | Base | Fuel Pump Replacement Nebo Rd. | 0.043287 | 233.69 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of systems that have surpass end of life, are consistently down for repairs and parts are difficult to obtain, impacting fuel of vehicles to support capital systems projects and customer emergencies responses.
151155 | M-Factor | Fleet_Central South Vehicle Replacement-Pick ups | 0.065 | 226.53 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151164 | Base | Fleet_Central South _key box replacement | 0.03 | 223.47 | General Plant | Fleet Renewal | Enersource | Adopted the current vehicles key management system at all sites to ensure access to vehicles when required. This ensure access to vehicles after hours and tracking of vehceil keys.
151038 | Base | Fleet_West_Equipment_Key Boxes | 0.03 | 223.47 | General Plant | Fleet Renewal | Horizon | Adopted the current vehicles key management system at all sites to ensure access to vehicles when required. This ensure access to vehicles after hours and tracking of vehceil keys.
151059 | Base | Station Switchgear Replacement - City Centre North MS47 HV2 | 0.32554 | 199.27 | System Renewal | Substation Renewal | Enersource | City Centre North MS is located centrally adjacent to Square One shopping mall, and feeds a large number of customers. It also provides back up to City Centre South MS – hence, reliability is very important. The current transformer protection device consists of a vintage 1973 Markham Electric oil with spring actuator type 44 kV circuit breaker. Station subject matter experts have identified this breaker as problematic. Additionally, due to obsolescence, it is no longer supported by the manufacturer and parts are difficult to come by.
151145 | M-Factor | Cable Replacement Project - Bough Beeches Blvd. | 0.69436 | 196.82 | System Renewal | Underground Asset Renewal | Enersource | From 2015-2017 customers in this area experienced 5 outages. 3 cables with 3 failures each.
150686 | Base | Rockwood MS - Station RTU and Protection Relays Upgrade | 0.094848 | 191.32 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of bus, line and transformer protection at Richmond Hill TS
150510 | Base | Upgrade/Retrofit SWI Video Security System at Jim Yarrow TS station | 0.055464 | 148.08 | System Service | Safety & Security | Brampton | This project consists of installation of SWI Video security system at Jim Yarrow TS
103030 | Base | Technology Upgrades Improving the System Control Room Environment | 0.054949 | 147.52 | General Plant | Information Technology | Multiple | This project will continue to build on the original capital project whose scope was focused on the replacement of computers used as Operator WorkStations. The scope of this program has been expanded to account for all technology purchases required for the Control Room theater.
151438 | Base | 2020 GUELPH - Fleet | 0.7 | 146.11 | General Plant | Fleet Renewal | Guelph | Replacement of end of life asset due to poor conditions, high mileage and engine hours and age. Vehicle experiencing more down time at the shop for repairs and maintenance impacting vehicle availability.
151108 | Base | Office Equipment | 0.07102 | 143.52 | General Plant | Facilities Management | Guelph | Replace aging equipment within the Guelph operational centre to ensure optimal performance in managing the distribution assets
150687 | Base | Woodlands MS - Station RTU & Protection Relays Replacement | 0.1495 | 141.21 | System Service | System Control, Comm'ns & Performance | Enersource | Woodlands MS - Station RTU & Protection Relays Replacement
151245 | M-Factor | Capacitor Bank Installations | 0.02 | 134.68 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of capacitor bank installation to increase power factor, capacity and reduce losses.
102931 | Base | Paving of 3 MS & TS Station Driveways per year - Annual Multi-year initiative - East | 0.047824 | 125.42 | System Renewal | Substation Renewal | Powerstream | Existing driveways at stations in the East Operating Area (former PowerStream) are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150597 | Base | Lock Box Installs - East | 0.0097775 | 115.84 | System Access | Metering | Powerstream | Multi-year project to install lock boxes at ICI properties with restricted access to eliminate need for a customer appointment for access.
151143 | M-Factor | Cable Replacement and Transformers Replacement -Project - Shelter Bay Rd. Mississauga | 1.0755 | 111.66 | System Renewal | Underground Asset Renewal | Enersource | From 2017-2019 YTD customers in this area experienced 6 failures.
150462 | Base | MV90 Upgrade | 0.15171 | 97.77 | General Plant | Information Technology | Multiple | Enhancement to MV90 systems application to support process improvement requirements. As the MV90 system is one of the core applications of the organization, operational enhancements come in from a number of venues and thereby feedback into the other downstream systems. These enhancements are considered for the overall customer and organizational benefits.
150569 | Base | Server OS Upgrades - IT Infrastructure | 0.074123 | 95.22 | General Plant | Information Technology | Multiple | Operating system upgrades to support IT infrastructure.
150737 | Base | Facilities_East Region_Reactive Capital | 0.25793 | 91.88 | General Plant | Facilities Management | Powerstream | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150736 | Base | Facilities_West Region_Reactive Capital | 0.25793 | 91.88 | General Plant | Facilities Management | Horizon | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150734 | Base | Facilities_Central Region_Reactive Capital | 0.25937 | 91.85 | General Plant | Facilities Management | Multiple | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150464 | M-Factor | Fieldworker Upgrade - IT/OT Infrastructure | 0.30342 | 91.28 | General Plant | Information Technology | Multiple | Upgrade to increase functionality for the metering field staff to improve response times for customers
150676 | Base | Mobile Devices - IT Infrastructure | 0.010114 | 88.32 | General Plant | Information Technology | Multiple
151078 | Base | Fleet West Major Equipment & Tools | 0.05 | 81.47 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of tools and shop equipment required to repair and maintain vehicles to ensure vehicle availability to support capital systems projects.
103171 | Base | Implementation of a new Alectra Network Operations Voice Radio System | 0.025 | 79 | General Plant | Information Technology | Multiple
151069 | Base | PI Upgrades & Enhancements - IT/OT Infrastructure | 0.12056 | 62.9 | General Plant | Information Technology | Multiple | Partner with OSIsoft (creator of PI) implement next level predictive analytics using AI (artificial intelligence) and ML (machine learning).
102922 | Base | Installation/Retrofit of SWI Video Security System at 3 TS stations | 0.031138 | 48.21 | System Service | Safety & Security | Powerstream | This project consists of installation of SWI Video security system at 3 Transformer Station in West
150906 | Base | Vehicle key box system | 0.03 | 43.15 | General Plant | Fleet Renewal | Powerstream
150747 | M-Factor | Net Zero Energy Emissions | 0.30847 | 34.58 | System Service | Distributed Energy Resources (DER) | Powerstream | The project will help Alectra Utilities to ensure that growing DER challenges are met through building expertise and capability in real time monitoring, integrating and optimizing of DERs in line with customer preferences. This will lead to a system that can safely integrate and optimize value from DERs for the benefit of customers.
151053 | Base | Building Sustainment | 0.17911 | 31.98 | General Plant | Facilities Management | Guelph | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150704 | Base | Feeder Protection Migration to DNP - Jim Yarrow TS | 0.32841 | 15.9 | System Renewal | Substation Renewal | Brampton | This is part of a multi-phase project to upgrade aging and failure-prone protection systems at Jim Yarrow TS to the current protection standards. Proper protection to distribution feeders will provide protection to the assets in the case of faults.
151031 | Base | Fleet Shop equipment refurbishment and replacement | 0.077 | 12.85 | General Plant | Fleet Renewal | Enersource | For the refurbishment of trailers, shop compressors and hoists to extend the life of the assets instead of replacement to reduce the need fro capital expenditures.
150678 | Base | P&C Specific Tools & Testing Equipment - West | 0.016233 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
102999 | Base | P&C Specific Tools and Testing Equipment | 0.016233 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
102157 | Base | Server Refresh - IT Infrastructure | 0.95638 | 10.1 | General Plant | Information Technology | Multiple | Ongoing server refresh to support applications.
150396 | Base | Network Refresh - IT Infrastructure | 0.35942 | 9.81 | General Plant | Information Technology | Multiple | Replacement of existing network infrastructure that is unsupported (or soon to be) including further rationalization and design modifications to support the delivery of services throughout the Alectra Environment.

## 2021 Ranking
Project List for Oral Hearing Undertakings
Project Number | Funding | Project Name | 2021 ($MM) | Project Score | Investment Category | Investment Grouping | Rate Zone | Comment
150404 | Base | Kenilworth TS Power Factor Correction | 0.86947 | 184356.97 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of capacitor bank installation at Kenilworth TS to improve PF and to comply with IESO market rules.
150725 | Base | Lines Central-North - Reactive Renewal | 1.2209 | 181453.58 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have failured and requires replacement in order to restore power to customers
150690 | Base | Lines Central-South - Reactive Renewal | 3.1289 | 171817.68 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have failured and requires replacement in order to restore power to customers
150682 | Base | Remote Fault Indicator Deployment | 0.4434 | 164220.93 | System Service | System Control, Comm'ns & Performance | Multiple | This project consists of remote fault indictor deployment which will result improved outage response, operational efficiency, and reliability
150259 | Base | Barrie TS Upgrade Feeders and Metering | 2.2052 | 127868.42 | System Access | Transmitter Related Upgrades | Powerstream | Hydro One will be rebuilding and reconfiguring its Barrie TS. As part of this upgrade, Hydro One plans to increase the capacity from 55/92 MVA to 75/125MVA and upgrade the E/4B transmission line from 115KV to 230KV. The feeder egress relocation and additional feeder will require integration reconfiguration for the six Alectra Utilities feeders (13M3 to 13M8) emanating from the station
102247 | Base | Interest Capitalization | 1.1518 | 104303.71 | General Plant | Other General Plant | Powerstream
150596 | Base | Meter Renewal - all types but Suite - PowerStream RZ | 0.083143 | 94470.24 | System Access | Metering | Powerstream | Multi-year project to renew existing residential (except suite) metering equipment.
101871 | Base | Services (New and Upgrades) - Layouts – East North - Commercial Services | 0.014239 | 94398.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150600 | Base | Firmware Upgrades for Smart Meters - East | 0.035002 | 94363.34 | System Access | Metering | Powerstream | Multi-year project to renew residential Smart meter firmware to improve communication performance.
151169 | Base | Central-South - Capitalization of Locates | 0.029336 | 94344.62 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
151174 | Base | West Lines - Capitalization locates | 0.035204 | 94319.23 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150631 | Base | Transformer Station Metering - Central North | 0.051453 | 94245.75 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew wholesale metering equipment.
101696 | Base | Subdivision - North Underground Residential Distribution System Final Close out and Inspection. | 0.046619 | 94197.28 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
103381 | Base | East Lines - Capitalization locates | 0.060361 | 94144.61 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101870 | Base | Services (New and Upgrades) - Layouts – East South - Commercial Services | 0.069772 | 94022.15 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101869 | Base | Services (New and Upgrades) - Layouts – East North - New Residential | 0.073996 | 93989.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150650 | Base | Replace PCB Risk PT's - Enersource RZ | 0.10179 | 93977.25 | System Access | Metering | Enersource | Multi-year project to replace metering transformers identified with unacceptable levels of PCB's, to prevent hazardous spills.
101919 | Base | New Services (new and upgrades) - Commercial, Industrial and Institutional (ICI) Projects - NORTH | 0.078559 | 93955.31 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150647 | Base | Transformer Station Metering - Enersource RZ | 0.28611 | 93884.28 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew wholesale metering equipment.
151049 | Base | Commercial, Industrial, Institutional, Apartment Connections | 0.12879 | 93829.96 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
101685 | Base | Subdivision - South Underground Residential Distribution System Final Close out and Inspection. | 0.11238 | 93778.29 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150457 | Base | Services (New and Upgrades) - Layouts – St Catharines | 0.19128 | 93519.09 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151162 | Base | Non Recoverable replacement of Distribution Equipment due to accident/vandalism | 0.24902 | 93457.13 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101924 | Base | Mulit Unit Metering for New Buildings NORTH - PowerStream RZ | 0.15716 | 93421.21 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in northern area of territory.
150588 | Base | New Residential Subdivision Development - Alectra West | 0.26084 | 93265.82 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
101791 | Base | New Services - new and upgrades - COMMERCIAL, INDUSTRIAL, INSTITUTIONAL (ICI) SERVICES - SOUTH | 0.2353 | 92878.02 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101812 | Base | Reactive Capital, Alectra East - LIS | 0.29665 | 92710.01 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150754 | Base | Lines Central-North - Non-Recoverable Replacements | 0.35094 | 92705.38 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150726 | Base | Lines Central-South - Non-Recoverable Replacements | 0.35094 | 92705.38 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101820 | Base | Reactive Capital, Alectra East - Non-Recoverable Replacement | 0.29595 | 92582.71 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150389 | Base | Services (New and Upgrades) - Layouts – Central North | 0.37232 | 92563.35 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150651 | Base | C & I Metering - Renewal- Brampton RZ | 0.090669 | 92560.77 | System Access | Metering | Brampton | Multi-year project to renew existing ICI metering equipment.
150386 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central North | 0.39911 | 92424.37 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150453 | Base | CIS CC&B Modifications(Regulatory Enhancements) | 0.87857 | 92260.88 | General Plant | Information Technology | Multiple | Enhancements to the CIS (CC&B) application needed to meet any regulatory requirements Such requirements in the past have been Ontario Energy Savings Program (OESP) as well as the Monthly Billing projects.
150649 | Base | Suite Metering - Enersource RZ | 0.45552 | 91838.22 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew suite metering equipment.
150654 | Base | C & I Metering - New Services - Brampton RZ | 0.53644 | 91552.85 | System Access | Metering | Brampton | Multi-year project to purchase and install ICI metering equipment on new services.
150595 | Base | C & I and Wholesale Metering - PowerStream RZ | 0.53831 | 91530.35 | System Access | Metering | Powerstream | Multi-year project to purchase, install, and renew ICI and wholesale metering equipment.
101868 | Base | Services (New and Upgrades) - Layouts – East South - New Residential | 0.44142 | 91488.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101795 | Base | Multi Unit Metering for New Buildings SOUTH - PowerStream RZ | 0.46998 | 91273.08 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in southern area of territory.
101873 | Base | Services (New and Upgrades) - Layouts – East North - Residential Upgrades | 0.51902 | 91023.49 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151051 | Base | System Relocations Road Authorities | 0.67475 | 91002.2 | System Access | Road Authority | Guelph | Mandatory - System Access Related Project
150652 | Base | New Residential Subdivision Development - Alectra Central South | 0.98199 | 90948.17 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150388 | Base | Services (New and Upgrades) - Layouts – Central South | 0.71733 | 90774.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150692 | Base | New Feeder in Residential Subdivision Development - Alectra Central North | 0.76718 | 90609.19 | System Service | Capacity (Lines) | Brampton | This expenditure is required to meet the needs of the development community that construct municipal approved residential subdivisions in Alectra Utilities' Central North service territory
150599 | Base | Suite Meter - Reverification - PowerStream RZ | 0.13206 | 90368.15 | System Access | Metering | Powerstream | Multi-year project to renew Measurement Canada seal dates on existing suite metering equipment.
150455 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - St Catharines | 0.86128 | 90201.14 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150659 | Base | Residential Meters - by Metering - Brampton RZ | 0.87367 | 90095.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Metering.
150456 | Base | Services (New and Upgrades) - Layouts – Hamilton | 0.88992 | 89961.61 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150630 | Base | New Residential Subdivision Development - Alectra Central North | 0.713 | 89952.48 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101828 | Base | Reactive Capital, Alectra East - Recoverable Replacement | 0.72254 | 89765.65 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover some costs for (i.e. pole hit, vehicle at scene of accicent, Alectra Utilities obtains most of costs (near $0 impact too budget))
101896 | Base | New Institutional/Commercial/Industrial Subdivision Development - Alectra East | 0.92026 | 89347.36 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101872 | Base | Services (New and Upgrades) - Layouts – East South - Residential Upgrades | 0.76892 | 89344.81 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101800 | Base | Reactive Capital, Alectra East - Storm Damage | 1.1955 | 86549 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151047 | Base | Subdivisions | 0.73863 | 85393.33 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
150620 | Base | Metering Renewal - all types - Horizon RZ | 1.9701 | 84064.36 | System Access | Metering | Horizon | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment.
101808 | Base | Reactive Capital, Alectra East - Switchgears | 1.7866 | 83304.08 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150648 | Base | Metering Renewal - all types but Suite - Enersource RZ | 2.2887 | 82569.47 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew residential (except suite) and ICI metering equipment.
101892 | Base | New Subdivision Development - Secondary Service Lateral - Alectra East | 2.6856 | 80775.74 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150384 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central South | 3.1991 | 77903.71 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150449 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - Hamilton | 5.0143 | 69328.05 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151095 | Base | Reactive Restoration | 1.0239 | 63546.92 | System Renewal | Reactive Capital | Guelph | Replacement of assets which have failured and requires replacement in order to restore power to customers
101824 | Base | Reactive Capital, Alectra East - Distribution Equipment | 5.3112 | 58189.58 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151161 | Base | Joint Use Pole Removal | 0.11515 | 57199.8 | System Renewal | Overhead Asset Renewal | Horizon | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
150463 | Base | Customer Self Service Portal Enhancements | 0.25573 | 56341.32 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) self service portal application to support process improvement requirements.The self service portal is the means by which Alecra customers can obtain their customer related information, interact with a CSR, post questions. The enhancements will allow Alectra customers a better experience when interacting with Alectra through the web portal channel.
151050 | Base | Metering - all types - Guelph RZ | 0.40508 | 55986.2 | System Access | Metering | Guelph | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment in Guelph RZ.
150469 | Base | ERP JD Edwards Enhancements | 1.0945 | 55714.6 | General Plant | Information Technology | Multiple | Allocation of capital funds to provide 3rd party assistance on capital work, along with creating system enhancements to the JD Edwards ERP and supporting Systems.
150325 | Base | CIS CC&B Enhancements | 0.77863 | 55520.48 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) application to support process improvement requirements.As the CIS (CC&B) system is one of the core applications of the organization, operational enhancements come in from a number of venues and thereby feedback into the other downstream systems. These enhancements are considered for the overall customer and organizational benefits.
101832 | Base | Joint Use Pole Removal | 0.57187 | 54024.42 | System Renewal | Overhead Asset Renewal | Powerstream | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
101887 | Base | New Residential Subdivision Development - Alectra East | 9.4493 | 44863.95 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
100859 | Base | Switchgear Renewal - East | 2.692 | 43704.68 | System Renewal | Underground Asset Renewal | Powerstream | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151117 | M-Factor | Vansickle TS True-up Payment (CCRA), St.Catharines | 1.5808 | 43572.72 | General Plant | Connection and Cost Recovery Agreements | Horizon | In accordance with the Connection Cost Recovery Agreement, a 10 year true-up is required for Vansickle TS.
151089 | Base | Overhead Rebuilds | 1.2154 | 39246.49 | System Renewal | Overhead Asset Renewal | Guelph | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
150369 | M-Factor | New build - 44kV Feeder Extension York/Meadowpine, Mississauga | 1.776 | 37794.94 | System Service | Capacity (Lines) | Enersource | There is no 44KV circuit on Meadowpine Blvd. and it is expected that the large customers will be connecting to the 44KV circuit. In addition 16MVA of connected load is on radial supply. This project will address the capacity constraints as well as eliminatethe current radial supply configuration for 16MVA of load.
101508 | Base | Transformer Renewal - East | 2.5337 | 37474.31 | System Renewal | Transformer Renewal | Powerstream | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150673 | Base | Road Authority Central (Mississauga) | 3.9471 | 35000.51 | System Access | Road Authority | Enersource | Mandatory - System Access Related Project
150134 | Base | Cable Injection Project - (V37) - Langstaff and Weston, Vaughan | 1.6043 | 34877.34 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 20 failures.
102387 | M-Factor | Install 44kV & 13.8kV Bryne Drive | 1.0617 | 34653.9 | System Service | Capacity (Lines) | Powerstream | The City of Barrie has identified 64 acres north of Harvie Road along Bryne Drive for development of industrial/commercial/residential. Another 34 acres south of Harvie Road along Bryne Drive has been identified for industrial/commercial development. The developable areas will result in 4MVA of new load north of Harvie Road and 2.2MVA of load south of Harvie Road. There is currently no existing 44kV or 13.8kV supply along Bryne Drive between P6231 and SC13487.
150405 | Base | 25M9 Jim Yarrow TS Extensions | 0.32091 | 33741.34 | System Service | Capacity (Lines) | Brampton | Jim Yarrow TS extension with new underground line extending 25M9 from Winston Churchill Blvd utility corridor to Steeles Ave in order to back up 25M8 & 25M10 to accomodate future load growth in Churchill Business Community Park and residential developments between Steeles Ave & Embleton Rd
150645 | Base | Road Authority Central (Brampton) | 4.6775 | 31813.54 | System Access | Road Authority | Brampton | Mandatory - System Access Related Project
150828 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-West | 0.915 | 31592.28 | System Renewal | Overhead Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151452 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-West | 0.915 | 31590.16 | System Renewal | Underground Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
101762 | Base | Road Authority Expenditure PS South | 4.091 | 31544.34 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
101355 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-East | 0.945 | 31424.67 | System Renewal | Overhead Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151450 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-East | 0.945 | 31424.67 | System Renewal | Underground Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
103633 | M-Factor | Install Two 27.6kV Ccts on 16th Ave from Hwy 404 to Woodbine Ave | 5.5273 | 30531 | System Service | Capacity (Lines) | Powerstream | This project is to reroute two 27.6kV feeders along 16th Ave from Woodbine Ave in Markham to Leslie St Richmond Hill to supply new load in Richmond Hill. The customers on Leslie St north of 16th Ave in Richmond Hill are supplied by feeder 12M5, 12M7, and 12M12. There is only 290A or 14 MVA capacity left on these feeders for future development.
151363 | Base | Cable Injection Project - (M25) - 14th - McCowan - Steeles - Old Kennedy, Markham | 0.819 | 27518.58 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 14 failures.
150072 | M-Factor | Markham TS#3 Bus Differential & Overcurrent Protections Upgrades | 0.11369 | 27028.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Markham TS#3 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
100867 | Base | Pole Renewal - East | 5.0405 | 25595.06 | System Renewal | Overhead Asset Renewal | Powerstream | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
151074 | Base | Reactive renewal | 3.2736 | 25136.12 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have failured and requires replacement in order to restore power to customers
151362 | Base | Cable Injection Project - (M39) - 16th - Warden - Hwy 7 - Woodbine, Markham | 0.74784 | 23713.55 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 8 failures.
151360 | Base | Cable Injection Project - (M31) - 14th - Old Kennedy - Steeles - Warden, Markham | 0.84754 | 23640.66 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 38 failures.
150070 | M-Factor | Markham TS#1 Bus Differential & Overcurrent Protections Upgrades | 0.24074 | 22499.7 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Markham TS#1 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
151043 | Base | Transformer Renewal - Central South | 1.897 | 21869.73 | System Renewal | Transformer Renewal | Enersource | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150467 | M-Factor | CIS CC&B upgrade | 6.5458 | 21391.8 | General Plant | Information Technology | Multiple | Aligns with Alectra customer experience plan requirements and enhanced services and emerging channels. Comprised of third party integration support, hardware, resources, testing to support existing Alectra platform as the current version 2.5 support ends in 2022. Project ensures enhanced functionality, compatibility with ancillary systems, security upgrades, automation and rate billing engine to support future utility DER integration.
150688 | Base | Station Sustainment & Protection & Control CASCADE Expansion | 0.04378 | 20717.32 | General Plant | Information Technology | Multiple | Expand the use of the CASCADE system to be used by the Protection and Control asset in addition to the Station assets
150371 | M-Factor | New build - 27.6kV Feeder Extension Traders, Mississauga | 2.7518 | 19791.79 | System Service | Capacity (Lines) | Enersource | Install new feeders in the Traders area between Hurontario St and Kennedy Rd from Matheson Blvd to Britannia Rd required to meet demand due to intensification and to ensure the reliability of current customers.
150664 | Base | Residential Meters - by Lines - Brampton RZ | 0.65495 | 18166.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Lines.
151109 | Base | Switch Replacement | 0.17496 | 18145.07 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
150458 | Base | MAS upgrade - IT Infrastructure | 0.051145 | 17425.57 | General Plant | Information Technology | Multiple | Metering Automation System for smart grid Upgrade to be implemented in a phased approach over the next 4 years as smart grid continues to evolve work in conjunction with the metering team to analyze and implement leverage new technologies to provide better more accurate meter readings be responsive to the issues first not reactive when a customer calls
151104 | Base | Distribution Automation - Central North | 0.46513 | 17389.16 | System Service | SCADA and Automation | Brampton | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151318 | Base | Cable Injection Project - (I3) -Bovaird - Dixie - Queen - Hwy 410, Brampton | 0.42438 | 16118.68 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2014 to 2015 with average duration of 71 minutes.
151216 | Base | Purchase & Installation of Station DC System Monitoring - South West | 0.02 | 15958.11 | System Renewal | Substation Renewal | Guelph | This project involves the installation of real-time monitoring at Arlen TS in the South West Operating Area (Guelph) that eliminates required on-site maintenance activities such as routine manual battery testing. By the addition of DC System monitoring, it will ensure that any potential problems will be immediately reported via SCADA/PI System Notification and help to avoid a station outage due to DC system failure as occurred at Vaughan TS#3. It will also reduce the human interaction with the dangerous DC Equipment and dramatically reduce the hazard/risk to the worker by eliminating the need to perform battery testing.
150639 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-CENTRAL | 0.038252 | 15735.56 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of DC charging system for Central South Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150638 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-East | 0.038252 | 15735.56 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of DC charging system for Central North Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150636 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-North & TS | 0.038252 | 15735.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of DC charging system for East Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150640 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-WEST | 0.038252 | 15735.56 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of DC charging system for West Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150285 | Base | Transformer Renewal - Central North | 0.79864 | 14492.05 | System Renewal | Transformer Renewal | Brampton | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
101027 | Base | Switch Renewal - East | 0.6543 | 14308.5 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
150504 | Base | Purchase and Installation of 10 Self Recharging Transformer Air Breathers on TS and MS Transformers - Multi-year initiative-WEST | 0.097603 | 14105.38 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of transformer air breather at TS and MS stations in East .Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
102098 | Base | Client - IT Infrastructure | 1.2101 | 13761.18 | General Plant | Information Technology | Multiple | To upgrade desktop/laptop/mobile devices that are 5 years or older (Approximately 20% of our equipment). Net new equipment for mobile computing as well as upgrades and replacements for damaged devices. Request made by various business units. This budget also includes RSA tokens\Licenses, monitors, mice, keyboards, docking stations, tablets and small non-MFP printers. Out of Scope: Large MFP Printers
151214 | Base | Purchase & Install Self Re-Charging Transformer Air Breathers | 0.04 | 13524.34 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of installation of transformer air breather at TS and MS stations in Guelph. Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
151247 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.585 | 13413.53 | System Renewal | Overhead Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102232 | Base | Capital Funds for Emergency P&C Purchases - East | 0.032835 | 13270.97 | System Renewal | Substation Renewal | Powerstream | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the East Operating Area (former PowerStream). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150683 | Base | Capital Funds for Emergency P&C Purchases - Central North | 0.032835 | 13184.55 | System Renewal | Substation Renewal | Brampton | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central North Operating Area (Brampton). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150685 | Base | Capital Funds for Emergency P&C Purchases - West | 0.032835 | 13184.55 | System Renewal | Substation Renewal | Horizon | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the West Operating Area (former Horizon). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150684 | Base | Capital Funds for Emergency P&C Purchases - Central South | 0.032835 | 13184.55 | System Renewal | Substation Renewal | Enersource | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central South Operating Area (former Mississauga). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150784 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.685 | 12968.3 | System Renewal | Overhead Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151453 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.63824 | 12922.02 | System Renewal | Underground Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
150823 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.735 | 12654.97 | System Renewal | Overhead Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102099 | Base | Printer & Copier Fleet Replacement | 0.040916 | 12636.08 | General Plant | Information Technology | Multiple | Replacement of existing fleet of printers/copiers that are 5 or more years old. This will include non-MFP printers. Replacement to be determined by an evaluation of evolving needs and corporate requirements as well as age of equipment.
151449 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.855 | 12175.67 | System Renewal | Underground Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
103211 | Base | Misc Software Upgrades (FormScape, AutoCAD, etc.) - IT/OT Infrastructure | 0.016711 | 12020.93 | General Plant | Information Technology | Multiple | Upgrade/ acquire software as required / requested by business.
151451 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.885 | 11935.99 | System Renewal | Underground Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151233 | M-Factor | New Construction - Campbell TS 36M63 Feeder PHASE 1 & 2, Guelph | 1.1528 | 11851.33 | System Service | Capacity (Lines) | Guelph | This project identifies a new 13.8kV feeder required from Campbell TS to bring additional load support to NW section of the city as the existing 13.8kV feeders in the area are unable to accommodate the additional load growth
150579 | Base | New build - Extend Bunting M81 Feeder, St.Catharines | 1.5461 | 11461.01 | System Service | Capacity (Lines) | Horizon | This project is to extend M81 feeder to supply new development and meet contigency condition in St. Catharines. This project will deal with ongoing capacity constraints in the North end of St.Catharines by bringing available supply from Bunting and Carlton TS's
103180 | Base | Citrix Xen Virtualization Expansion - IT Infrastructure | 0.051145 | 11298.77 | General Plant | Information Technology | Multiple | Client computing virtualization (Citrix) is currently the standard delivery method for applications and desktops at Alectra. This system has had a tremendous uptake in the organization and requires an upgrade in back-end infrastructure to support the additional demand from the business.
150693 | M-Factor | Blockchain | 0.35392 | 11191.63 | System Service | Distributed Energy Resources (DER) | Multiple | The project will prepare Alectra Utilities to engage with customers in a real-time and transparent process to record the flow of electricity to and from DERs, enabling the efficient procurement of distribution benefits, such as demand response and frequency regulation. The project will provide a robust settlement mechanism between Alectra and customers, backed by timely and efficient financial transactions, to enable overall trust and customer value delivery and leading to increased customer satisfaction.
151302 | Base | Cable Injection Project - (HAM) - Rymal - Mud - Upper Centennial - Upper Red Hill Valley | 0.8583 | 11132.21 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 8 failures, or 14 failures per 100km. This area includes the 331X & 341X feeders which were identified as a Worst Performing Feeder in 2018. The average cable installation year is 1989 in this project scope.
151314 | Base | Cable Injection Project - (G2) -Wanless - Kennedy - Bovaird - Main, Brampton | 0.3125 | 11045.83 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2013 to 2017 with average duration of 125 minutes.
150665 | Base | Emerging Customer Initiated Work (West) | 1.5414 | 10905.1 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151465 | M-Factor | Cable Replacement - Mississauga Left Behind Cable | 0.37682 | 10856.69 | System Renewal | Underground Asset Renewal | Enersource | This project is to address cables which were part of a cable injection project but were ultimately not injectable at the time of project execution. These 'left behind' segments must be addressed, if they are left in the system they could cause a failure. Customers would not only experience an outage, but question the utilities work practices as we would have addressed only a portion of the cables instead of all the cables which could cause an outage.
101562 | Base | Arc Flash Mitigation Projects | 0.042995 | 10618.95 | System Service | Safety & Security | Powerstream | This project is to mitigate arc flash risk at East stations.
151299 | Base | Cable Replacement Project - (HAM) - Millen - Barton - Fruitland | 1.0793 | 10341.62 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 16 failures, or 44 failures per 100km. The average cable installation year is 1970 in this project scope.
150653 | Base | Road Authority West (St. Catharines) | 0.86125 | 10216.94 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
150615 | Base | Metering Tools & Equipment - Central North | 0.038308 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150616 | Base | Metering Tools & Equipment - Central South | 0.038308 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150613 | Base | Metering Tools & Equipment - East | 0.038308 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150614 | Base | Metering Tools & Equipment - West | 0.038308 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
151402 | Base | Cable Replacement Project- Montevideo & Treviso (19a), Mississauga | 5.1828 | 9918.05 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 10 outages, the length is 14,151 m, and the average cable age is 34 years old.
151456 | M-Factor | Cable Injection Project - (V50) - Hwy 7 - Kipling - Steeles - Hwy 27, Vaughan | 0.93454 | 9187.5 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 3 failures in 2018.
151063 | Base | Pole Renewal - Central South | 3.8699 | 9065.1 | System Renewal | Overhead Asset Renewal | Enersource | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
100886 | Base | Distribution Automation - East | 1.2878 | 9041.12 | System Service | SCADA and Automation | Powerstream | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151275 | Base | Cable Injection Project - (SCH) - QEW - Highway 406 - Martindale Road | 0.5544 | 8905.36 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 3 failures, or 11 failures per 100km. The average cable installation year is 1988 in this project scope.
150808 | Base | Implementation of Doble - Enoserv PowerBase and Enoserv RTS applications for Protection and Control Department | 0.02189 | 8798.22 | General Plant | Information Technology | Multiple | PowerBase is the premier application to manage and report on protection assets maintenance and engineering records. It manages workflow and connect with maintenance management systems such as Cascade. RTS is a vendor neutral software which allows connection to a variety of test sets. It offers an extensive relay test plan library.
151300 | Base | Cable Injection Project - (HAM) - Millen - Barton - Fruitland | 0.71914 | 8690.38 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 16 failures, or 44 failures per 100km. The average cable installation year is 1987 in this project scope.
151389 | Base | 2021 GUELPH - Remotely Controlled Switches | 0.42587 | 8627.99 | System Service | SCADA and Automation | Guelph | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
150418 | Base | 42M62 Extension Bovaird Dr, Mississauga Rd to Heritage Rd | 0.39514 | 8351.21 | System Service | Capacity (Lines) | Brampton | This project consists of 42M62 extension on Bovaird drive from Mississauga Road to Heritage Road. The 42M62 circuit extension will supply industrial on Heritage Road, as well as new residential developments
101804 | Base | Purchase of Major Tools | 0.35356 | 8158.3 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150509 | Base | Installation of Transformer Bushing Monitoring Yarrow TS and MS txmrs-Multi Year -EAST | 0.089936 | 7885.3 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Transformer bushing monitoring system in Central North. Bushing monitoring unit provides real time condition monitoring of the transformer bushings.
150709 | Base | Spare Station Transformer Bushing Conversion from PILC to XLPE - West | 0.11155 | 7847.53 | System Renewal | Substation Renewal | Horizon | This project involves converting the spare station transformer primary and secondary bushings/compartments from PILC to XLPE in the West Operating Area (former Horizon). The spare transformers are used when a failure occurs on a station transformer. The PILC cable will be replaced with XLPE at the station in order to improve station reliability and worker and equipment safety. The conversion of bushings is critical as primary bushing compartments have ruptured on multiple occasions in 2017 in the West Operating Area - causing oil spills larger than 200 liters.
151313 | Base | Cable Injection Project - (F5) - Steeles - Main - Hwy 407 - McLaughlin, Brampton | 0.3125 | 7751.39 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 5 outages due to cable failures from 2007 to 2016 with average duration of 80 minutes.
102038 | Base | Installation of Transformer Bushing Monitoring on TS and MS txmrs-Multi Year | 0.12564 | 7734.98 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of Transformer bushing monitoring system in East. bushing monitoring unit provides real time condition monitoring of the transformer bushings.
151349 | Base | Cable Injection Project - (V16) - Langstaff - Dufferin - Steeles - Jane, Vaughan | 0.90311 | 7572.02 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 23 failures.
150282 | Base | Switchgear Renewal - Central North | 0.47937 | 7521.14 | System Renewal | Underground Asset Renewal | Brampton | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150508 | Base | Installation of Transformer Bushing Monitoring on MS txmrs-Multi Year -CENTRAL | 0.16732 | 7508.89 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Transformer bushing monitoring system in Central South. bushing monitoring unit provides real time condition monitoring of the transformer bushings.
151325 | Base | Cable Replacement Project - (M31) - 14th - Old Kennedy - Steeles - Warden, Markham | 3.5 | 7411.62 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 38 failures.
151316 | Base | Cable Injection Project - (H2) - Wanless - Heart Lake - Bovaird - Kennedy, Brampton | 0.3125 | 7371.2 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2009 to 2017 with average duration of 107 minutes.
150284 | Base | Pole Renewal - Central North | 2.0544 | 7304.65 | System Renewal | Overhead Asset Renewal | Brampton | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
102017 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-North & TS | 0.32654 | 7275.34 | System Service | Safety & Security | Powerstream | This project consists of Sorbweb Oil containment system in East. Protects the environment in the event of a transformer tank rupture
150714 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - Central | 0.074795 | 6819.25 | System Renewal | Substation Renewal | Enersource | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central South Operating Area (former Enersource). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150713 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.074795 | 6819.25 | System Renewal | Substation Renewal | Brampton | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central North Operating Area (Brampton). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150715 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - West | 0.074795 | 6819.25 | System Renewal | Substation Renewal | Horizon | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the West Operating Area (former Horizon). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150644 | Base | Road Authority West (Hamilton) | 1.5459 | 6689.48 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
150507 | Base | 230kV TS Transformer Primary Bushing Monitoring Enablement-BPD Elimination - 4 TS Transformers-Multi-year initiative-TS | 0.48553 | 6521.07 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to install primary bushing monitoring at TS in EAST
150352 | Base | Voltage Conversion - Central MS, Hamilton | 1.4628 | 6498.05 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 23 outages and had 1,060,300 customer minutes of interruption (75 mins per customer per year). The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail. Specifically Central MS is the only station remaining in service with oil breakers which are functionally obsolete with no spare parts readily available.
151310 | Base | Cable Injection Project - (E4) - Queen - McLaughlin - Steeles - Chinguacousy, Brampton | 0.3125 | 6421.34 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2008 to 2016 with average duration of 104 minutes.
150357 | Base | New build - 25M9 Extension to Derry Rd, Mississauga | 1.6706 | 6400.82 | System Service | Capacity (Lines) | Enersource | This project consists of 25M9 extension into Mississauga to provide additional 27.6KV capacity. It will offload Erindale TS in Mississauga and avoid building Mini-Britannia MS and also provides capacity back to Brampton using a link along Derry Rd.
151044 | Base | Switch Renewal - Central South | 0.2698 | 6318.96 | System Renewal | Overhead Asset Renewal | Enersource | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
103659 | Base | Storm Hardening - Four-Circuit Poles | 1.8732 | 6254.52 | System Renewal | Overhead Asset Renewal | Powerstream
150514 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear Initiative-WEST | 0.33748 | 6213.41 | System Service | Safety & Security | Horizon | This project consists of Sorbweb Oil containment system in West. Protects the environment in the event of a transformer tank rupture
151336 | Base | Cable Replacement Project - (BA22) - Sunnidale and Anne, Barrie | 1.9157 | 6208.17 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 2 failures in 2019.
151086 | Base | Insulator Replacements | 0.083477 | 5948.6 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
102128 | M-Factor | Aurora MS6 Expansion | 0.8326 | 5909.69 | System Service | Capacity (Lines) | Powerstream | 2C land is currently supplied by a 13.8kV feeder 5F2. It had a peak of 269A in 2018 and does not have sufficient capacity to supply future growth in the 2C lands. New feeder capacity is required to supply the additional load.
150066 | Base | Basement Flood Risk Mitigation - Vaughan TS#2 | 0.12625 | 5867.18 | System Renewal | Substation Renewal | Powerstream | This project involves mitigating the flood risk at the Vaughan TS#2 where there is equipment installed in the basement by relocating or repositioning this equipment. This critical equipment includes DC system, AC and DC panels, feeder switches, UPS, ATS located in the basement of this station. Damage to this equipment due to flooding would cause extensive power interruptions to many customers.
150351 | M-Factor | Voltage Conversion - Aberdeen MS, Hamilton | 2.08 | 5674.67 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 16 outages and had 500,475 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151404 | Base | Cable Replacement Project- Central Pk E & Miss. Valley (28) | 8.4404 | 5611.16 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 11 outages, the length is 7,100 m, and the average cable age is 42 years old. There are 27 backlot transformers that we are also replacing.
150337 | Base | Switch Renewal - West | 0.43526 | 5475.59 | System Renewal | Overhead Asset Renewal | Horizon | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
151055 | Base | Major Tools | 0.075379 | 5431.72 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
150067 | Base | Basement Flood Risk Mitigation - Markham TS#4 | 0.12831 | 5409.71 | System Renewal | Substation Renewal | Powerstream | This project involves mitigating the flood risk at the Markham TS#4 where there is equipment installed in the basement by relocating or repositioning this equipment. This critical equipment includes DC system, AC and DC panels, feeder switches, UPS, ATS located in the basement of this station. Damage to this equipment due to flooding would cause extensive power interruptions to many customers.
150598 | Base | Suite Metering - Renewals & Retrofits - PowerStream RZ | 0.35626 | 5394.14 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering equipment in existing buildings upgraded from bulk metering.
150515 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-CENTRAL | 0.33858 | 5352.14 | System Service | Safety & Security | Enersource | This project consists of Sorbweb Oil containment system in Central South. Protects the environment in the event of a transformer tank rupture
150516 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-EAST | 0.33858 | 5352.14 | System Service | Safety & Security | Brampton | This project consists of Sorbweb Oil containment system in Central North. Protects the environment in the event of a transformer tank rupture
150336 | Base | Transformer Renewal - West | 0.66396 | 5293.52 | System Renewal | Transformer Renewal | Horizon | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150750 | Base | Lines Central-North - Major Tools | 0.093219 | 5234.11 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150009 | Base | Insulator Renewal - East | 0.22509 | 5107.82 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
151203 | Base | Capital Corrective Equipment Replacement - Stations South West | 0.06 | 4921.2 | System Renewal | Substation Renewal | Guelph | This project is intended to provide capital for all unplanned station equipment replacements in the South West Operating Area (Guelph) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
102042 | Base | Purchase and Installation of Animal Guards at Various Stations-Annual Multi-year initiative-North & TS | 0.016055 | 4893.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of animal guard installation in East
150605 | M-Factor | Residential "ICON F" Meter Replacement - PowerStream RZ | 4.2354 | 4853.17 | System Access | Metering | Powerstream | Multi-year project to replace Icon-F smart meters with secure encryption, last gasp and tamper detection capabilities.
151403 | Base | Cable Replacement Project- Montevideo & Battleford (19b), Mississauga | 1.6698 | 4849.24 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 12 outages, the length is 5,013 m, and the average cable age is 39 years old.
151328 | Base | Cable Replacement Project- (21a) Darcel & Brandon Gate, Mississauga | 1.4364 | 4688.73 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 4,087 m, and the average cable age is 46 years old.
151083 | Base | Switchgear Renewal - West | 0.42156 | 4683.89 | System Renewal | Underground Asset Renewal | Horizon | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151010 | Base | Switch Renewal - Central North | 0.6454 | 4603.75 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
150720 | Base | Lines Central-South - Major Tools | 0.21934 | 4591.27 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
151433 | Base | Cable Injection- 008- AREA46 - Glen Erin & Aquitane, Mississauga | 0.61424 | 4470.89 | System Renewal | Underground Asset Renewal | Enersource | There are 6 outages, we are injecting a total of 19,827 m of cable for this project, and the average age of the cable is 33 years.
151401 | Base | Cable Replacement Project- (21b) Sigsbee & Morning Star, Mississauga | 1.0406 | 4296.47 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 7 outages, the length is 2,956 m, and the average cable age is 46 years old.
151021 | Base | Insulator Renewal - Central North | 0.35316 | 4235.99 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of non-polymer insulators (Areas are prioritiezed by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
150536 | Base | Implement database security - IT Infrastructure | 0.12755 | 4195.13 | General Plant | Information Technology | Multiple | This project will address security risks related to data-at-rest.
150674 | Base | Emerging Customer Initiated Work Central (Brampton) | 0.15225 | 4183.83 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101763 | Base | Unforeseen Projects Initiated by the customer PS North | 0.11937 | 4161.34 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150679 | M-Factor | Alectra Drive for the Workplace | 0.15753 | 3997.47 | System Service | Capacity (Lines) | Multiple | Alectra Drive for the Workplace will demonstrate the value of integrating smart electric vehicle (EV) charging system at workplaces into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. The planned investment will help manage the flow of electricity needed to serve the building and EV charging stations, so that electricity costs are minimized for commercial customers while EV drivers have an easy and accessible charging solution.
150320 | M-Factor | Voltage Conversion - Dewitt MS , Hamilton | 0.96641 | 3972.49 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 12 outages and had 888,434 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151348 | Base | Cable Injection Project - (M20) - Hwy 7 - Markham - 14th - McCowan, Markham | 0.43073 | 3971.28 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 14 failures.
150408 | Base | 42M71 Feeder Egress Salvation Rd, West, Creditview, Wanless | 0.38649 | 3769.35 | System Service | Capacity (Lines) | Brampton | This project consists of 42M71 feeder egress and ties to 42M61 and 42M43 will provide contingency to circuits nearing planning limits.
151430 | Base | Cable Injection- 005- AREA 38- Bristol & Creditview, Mississauga | 0.88643 | 3745.79 | System Renewal | Underground Asset Renewal | Enersource | There is 1 outage, we are injecting a total of 11,193 m of cable for this project, and the average age of the cable is 32 years.
102075 | Base | Major repairs, refurbishment, or modifications to switches/switchgear | 0.10229 | 3702.48 | System Renewal | Underground Asset Renewal | Powerstream | Switchgear and Switches in stores that repair/refurbishment of the units can allow them to be returned to service
150521 | Base | Security Additions & Enhancements | 0.24247 | 3699.67 | General Plant | Information Technology | Multiple | As per Alectra Security roadmap to key IT systems.
150376 | Base | New build - Hamilton South Mountain feeders capacity relief, Hamilton | 1.1222 | 3693.91 | System Service | Capacity (Lines) | Horizon | This project is build new feeder to alleviate capacity in South Hamilton and to alleviate on the four feeders which are over the planning limit
150415 | Base | 42M65 Feeder Egress Pleasant TS to SG20-1438 | 0.5387 | 3640.88 | System Service | Capacity (Lines) | Brampton | This project consists of 42M65 feeder egress out of Pleasant TS and will supply the redvelopments in downtown.
151428 | Base | Cable Injection- 002- AREA 30- Eglinton Ave W & Miss Rd, Mississauga | 0.58737 | 3632.2 | System Renewal | Underground Asset Renewal | Enersource | There are 2 outages, we are injecting a total of 14,541 m of cable for this project, and the average age of the cable is 31 years.
151276 | Base | Cable Injection Project - (SCH) - Vansickle | 0.36816 | 3555.68 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 11 failures per 100km. The average cable installation year is 1990 in this project scope.
151200 | M-Factor | Alectra Single Platform Website ongoing | 0.10945 | 3548.17 | General Plant | Information Technology | Multiple | Ongoing enhancements to the Alectra platform to improve functionality for customers
150498 | Base | Capital Corrective Equipment Replacement - Stations Central South | 0.2729 | 3534.76 | System Renewal | Substation Renewal | Enersource | This project is intended to provide capital for all unplanned station equipment replacements in the Central South Operating Area (former Enersource) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150499 | Base | Capital Corrective Equipment Replacement - Stations Central North | 0.2729 | 3534.76 | System Renewal | Substation Renewal | Brampton | This project is intended to provide capital for all unplanned station equipment replacements in the Central North Operating Area (Brampton) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150497 | Base | Capital Corrective Equipment Replacement - Stations West | 0.2729 | 3534.76 | System Renewal | Substation Renewal | Horizon | This project is intended to provide capital for all unplanned station equipment replacements in the West Operating Area (former Horizon) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150047 | M-Factor | Rear Lot Renewal Project - Royal Orchard - North | 1.035 | 3478.27 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 3 failures per year lasting 4 hours per year based on 3 year average.
151462 | M-Factor | Cable Injection Project - (G1) - Hwy 410 - Kennedy - Wanless - Main, Brampton | 0.31046 | 3437.98 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 2 failures. Exact number of failures in recent years is unknown at this moment.
150774 | Base | Lines Central-North - Site Restorations | 0.10539 | 3434.48 | System Renewal | Overhead Asset Renewal | Brampton
150721 | Base | Lines Central-South - Site Restorations | 0.10539 | 3434.48 | System Renewal | Underground Asset Renewal | Enersource
151344 | Base | Cable Injection Project - (R16) - Major Mackenzie - Bayview - 16th - Yonge, Richmond Hill | 0.3007 | 3396.52 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 16 failures.
150672 | Base | Burden Allocation - System Service | 0.10598 | 3353.13 | System Service | Capacity (Lines) | Horizon
150537 | Base | Cyber Security - Upgrade access management controls | 0.33157 | 3321.24 | General Plant | Information Technology | Multiple | As per Alectra Security roadmap to key IT systems with focus on end user access management controls.
150390 | M-Factor | New build - Waterdown 3rd Feeder, Hamilton | 1.7134 | 3248.15 | System Service | Capacity (Lines) | Horizon | This project is to alleviate capacity issues in the Waterdown area of Hamilton, primarily served by two Dundas 27.6kV feeders
150263 | Base | Cable Replacement Project - East Left Behind Cable | 2.7032 | 3237.07 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in these areas have experienced 11 failures.
102065 | Base | Capital Corrective Equipment Replacement - East | 0.33857 | 3161.46 | System Renewal | Substation Renewal | Powerstream | This project is intended to provide capital for all unplanned station equipment replacements in the East Operating Area (former PowerStream area) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150611 | Base | Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.16692 | 3116.96 | System Renewal | Substation Renewal | Powerstream | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the East Operating Area (former PowerStream). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150623 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-WEST | 0.0058386 | 3095.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of animal guard installation in West
150622 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-CENTRAL | 0.0058391 | 3093.04 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Animal guard at Central South Stations
150621 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-EAST | 0.0082112 | 3081.51 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Animal guard at East Stations
150089 | M-Factor | Markham TS#3 T1/T2 "B" Differential Protections Upgrade | 0.11 | 2935.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to replace the T1/T2 GEC solid state Transformer "B" Differential Protection relays at Markham TS#3 with new relays having fault recording capabilities
151393 | Base | 2021 GUELPH - Transite Underground Duct Replacement | 0.2713 | 2917.98 | System Renewal | Underground Asset Renewal | Guelph | Replacement of Duct Structure which contains asbestoes a known carcinogen and impacts worker safety.
151286 | Base | Cable Replacement Project - (H2) - Wanless - Heart Lake - Bovaird - Kennedy, Brampton | 0.40495 | 2867.55 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2011 to 2017 with an average duration of 126 minutes
101625 | Base | Cyber Security Audit & Upgrades | 0.068676 | 2865.1 | General Plant | Information Technology | Multiple | This project would fund various activities and countermeasures to improve the cyber security posture of the Operations' Network. This will be a mandate for compliance to Ontario Cyber Security framework. The counter measures include: - an annual audit of the cyber security countermeasures in place; - implementation of new technologies to seal identified compromises; - replacement of deployed cyber security equipment deemed end of life or not able to deliver an expected level of service.
150783 | Base | Fleet_Central South Vehicle Replacement-Pick ups | 0.147 | 2848.48 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150671 | Base | Burden Allocation - System Renewal | 1.7269 | 2831.23 | System Renewal | Other System Renewal | Horizon
150632 | Base | AMI Gatekeeper Expansion - Brampton RZ | 0.029884 | 2820.22 | System Access | Metering | Brampton | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
151346 | Base | Cable Injection Project - (M45) - Hwy 7 and Woodbine, Markham | 0.25087 | 2649.75 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 9 failures.
150079 | M-Factor | Markham TS#1 T1/T2 "B" Overcurrent Protections and HMI Upgrade | 0.16325 | 2596.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade Markham TS#1 T1/T2 "B" Overcurrent Protections with fault recording ability and HMI Upgrade
151427 | Base | Cable Injection- 001- AREA 11- Truscott & Southdown, Mississauga | 0.41387 | 2550.48 | System Renewal | Underground Asset Renewal | Enersource | There are 2 outages, we are injecting a total of 21,576 m of cable for this project, and the average age of the cable is 32 years.
150332 | M-Factor | Non-Wires Alternative Pilot | 0.78661 | 2536.94 | System Service | Capacity (Stations) | Powerstream | The project will provide customers with increased flexibility to make decisions about their electricity consumption, generation, and costs; it leads to more efficient integration of DERs which yields greater benefits to customer, system reliability, and power quality. This project will also provide the opportunity to increase operational efficiency and improved asset management to enhance service to customer and defer and/or reduce infrastructure investment needs in York Region.
150681 | Base | Data Analytics - IT/OT Infrastructure | 0.35392 | 2527.57 | General Plant | Information Technology | Multiple | This project will develop a data analytics platform to provide enhanced customer value by implementing preventative measures to improve overall outage detection and prediction with use-cases focusing on Distributed Energy Resource (DER) monitoring, integration and optimization.
150580 | Base | West Region Tools and Test Equipment | 0.20458 | 2494.28 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
150627 | Base | Station Equipment Temperature Monitoring-EAST | 0.076305 | 2479.48 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of Station Temperature Monitoring system in Central North and it enables controlled emergency loading beyond the nameplate rating.
150629 | Base | Station Equipment Temperature Monitoring-WEST | 0.076305 | 2479.48 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of Station Temperature Monitoring system in West and it enables controlled emergency loading beyond the nameplate rating.
151202 | Base | Purchase of Major Station Tools - Multi-year | 0.01 | 2472.82 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
151342 | Base | Cable Injection Project - (M40) - Major Mackenzie - Warden - 16th - Woodbine, Markham | 0.21433 | 2470.32 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 16 failures.
150625 | Base | Purchase of Major Tools - Muliti Year-CENTRAL | 0.02189 | 2395 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150624 | Base | Purchase of Major Tools - Muliti Year-EAST | 0.02189 | 2395 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150626 | Base | Purchase of Major Tools - Muliti Year-WEST | 0.02189 | 2395 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
151221 | Base | Metering - AMI Hardware Upgrade | 0.35 | 2384.22 | System Access | Metering | Guelph | Multi-year project to expand and upgrade AMI field communication equipment to service new connections, in Guelph RZ.
101761 | Base | Unforeseen Projects Initiated by the customer PS South | 0.38335 | 2365.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151061 | Base | Markham TS2 Firewall Upgrade | 0.21776 | 2334.71 | System Service | System Control, Comm'ns & Performance | Powerstream | Markham TS2 Firewall Upgrade
151290 | Base | Cable Replacement Project - (I3) - Bovaird - Dixie - Queen - Hwy 410, Brampton | 0.7259 | 2280.06 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 8 outages due to cable failures from 2007 to 2018 with average duration of 133 minutes.
151347 | Base | Cable Injection Project - (V40) - Teston - Weston - Major Mackenzie - Pine Valley, Vaughan | 0.19751 | 2273.85 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 7 failures.
151244 | Base | Fault Indicators | 0.02 | 2243.02 | System Service | System Control, Comm'ns & Performance | Guelph | The scope of this project is to install Fault Indicators in Guelph. The project would include the fault indicators communicating to the existing SCADA and will improve the fault locating and improve SAIDI
151281 | Base | Cable Replacement Project - (SCH) - Lake - Linwell - Geneva - Scott | 0.99129 | 2227.25 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 6 failures, or 189 failures per 100km. The average cable installation year is 1976 in this project scope.
151181 | Base | Cable Replacement Project - Left Behind Cable, Brampton | 0.525 | 2163.34 | System Renewal | Underground Asset Renewal | Brampton | This project is to address cables which were part of a cable injection project but were ultimately not injectable at the time of project execution. These 'left behind' segments must be addressed, if they are left in the system they could cause a failure. Customers would not only experience an outage, but question the utilities work practices as we would have addressed only a portion of the cables instead of all the cables which could cause an outage.
151070 | Base | Markham TS3 Firewall Upgrade | 0.033687 | 2148.93 | System Service | System Control, Comm'ns & Performance | Powerstream | Markham TS3 Firewall Upgrade
150321 | M-Factor | Voltage Conversion - Galbraith MS, Hamilton | 1.0036 | 2139.96 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 4 outages and had 77,467 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151341 | Base | Cable Injection Project - (M15) - 16th - Markham - 9th - Hwy 7, Markham | 0.18176 | 2076.47 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 30 failures.
151345 | Base | Cable Injection Project - (M51) - 14th - Bayview - Steeles - Yonge, Markham | 0.18856 | 2070.59 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 9 failures.
151343 | Base | Cable Injection Project - (M14) - Hwy 7 - Markham - 9th - 14th, Markham | 0.18875 | 2070.43 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 10 failures.
102728 | Base | Station Switchgear Replacement - Big Bay Point MS304 | 0.81486 | 2051.19 | System Renewal | Substation Renewal | Powerstream | This substation project consists of replacing the existing switchgear and associated equipment, as well as the primary circuit switcher at Big Bay Point MS304. The current line-up is technically obsolete, in poor condition, and is prone to failure. A failure could affect a large number of customers and potentially result in complete loss of supply from the station, requiring load transfer to another station. Proactive replacement of the existing equipment is a prudent strategy as system reliability would be greatly affected in the event of a failure. Additionally, the restoration of the system to normal conditions could take 8-10 months due to long equipment lead times.
150675 | Base | Emerging Customer Inititated Work Central (Mississauga) | 0.16916 | 2049.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150558 | Base | OT Hardware Refresh | 0.66386 | 2049.01 | General Plant | Information Technology | Multiple | Current routers in PS backbone are limited to 100Mbps ports. Backbone with new hardware is operating at 1gbps. New routers need to operate at that capacity. Equipment in Barrie office is at end of life and hasn't been upgraded since before BHDI merger with PS in 2008. Equipment in Sandalwood is consumer grade unmanaged switches Mavis brocade switches will be nearing end of life. Replace unmanaged Linksys switches in LegHZ datacentres
151329 | Base | Cable Replacement Project - (V51) - Langstaff - Kipling - Hwy 7 - Hwy 27, Vaughan | 2.1672 | 2048.89 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 5 failures.
101764 | Base | Road Authority Expenditure PS North | 1.5272 | 2038.3 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
150604 | Base | Smart Meter Network Expansion - PowerStream RZ | 0.2091 | 2035.93 | System Access | Metering | Powerstream | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
151092 | Base | Distribution Automation - Central South | 0.538 | 2013.5 | System Service | SCADA and Automation | Enersource | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151030 | Base | Addition of Sensors to SCADA Controllable 44kV LISs in Brampton | 0.26272 | 2012.97 | System Service | System Control, Comm'ns & Performance | Brampton | This project is to add sensors to the 44KV switches in Central North
150694 | M-Factor | Cityview microgrid enhancements | 0.014869 | 1985.17 | System Service | Capacity (Lines) | Powerstream | The project is to understand how microgrids can be integrated into the distribution grid in a safe and reliable manner. The microgrid is used to evaluate integration and connection to the distribution grid, while reducing the building's load, greenhouse gas emissions, and increasing its resiliency to grid outages.
151330 | Base | Cable Replacement Project - (A01) - Henderson - Yonge - Bloomington - Bathurst, Aurora | 1.8456 | 1904.82 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 3 failures.
151321 | Base | Cable Injection Project - (J5) - Steeles - Bramalea - Hwy 407 - Dixie, Brampton | 0.13856 | 1902.8 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 outage due to cable failures to date. Cables are 31 to 33 years old and will be at the injection eligibility threshold by the time of project execution in 2021.
101013 | Base | Planned Circuit Breaker Replacement Markham TS#3 - E & Z Buses | 0.48351 | 1832.29 | System Renewal | Substation Renewal | Powerstream | The existing 27.6 kV circuit breakers at Markham TS#3 have been identified in the Asset Condition Assessment (ACA) Model as requiring replacement due to obsolescence and historical failures. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted funding requirements and could result in lengthy customer interruptions.
150670 | Base | SCADA FDIR | 0.12046 | 1798.98 | System Service | SCADA and Automation | Multiple | Fault Detection, Isolation, and Restoration implementation, next generation of distribution automation technology. This utilizes devices which are already automated and integrates them into the OMS system such that devices perform self healing after a fault. in some cases reducing the outage time to less then 1 minute.
150764 | Base | Fleet_West_Vehicle Replacement_Bucket Truck 1-285 | 0.4 | 1780.18 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151283 | Base | Cable Replacement Project - (HAM) - Mohawk | 0.78654 | 1740.19 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 1 failure, or 20 failures per 100km. This area includes the 2D2X feeder which was identified as a Worst Performing Feeder in 2018. The average cable installation year is 1953 in this project scope.
150680 | M-Factor | Alectra Drive at Home | 0.47974 | 1731.44 | System Service | Capacity (Lines) | Multiple | Alectra Drive at Home will demonstrate the value of integrating smart electric vehicle (EV) charging system in multi rise buildings as well as residential homes into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. It will also provide insight into the characteristics of EV Charging, how EVs can be aggregated and controlled to provide the benefit at the local, regional and provincial system levels, and customer response to these control and optimization strategies.
151201 | Base | Purchase of New Critical Spare Parts - Guelph | 0.01 | 1727.97 | System Renewal | Substation Renewal | Guelph | This project involves procurement of critical spare parts for stations in the South West Operating Area (Guelph) so as to facilitate prompt repair of failed assets during emergency situations.
150912 | Base | Unit # 362 Palfinger crane truck | 0.515 | 1659.67 | General Plant | Fleet Renewal | Powerstream
150619 | Base | Purchase of Critical Spare Parts - West | 0.022109 | 1648.51 | System Renewal | Substation Renewal | Horizon | This project involves procurement of critical spare parts for stations in the West Operating Area (former Horizon) so as to facilitate prompt repair of failed assets during emergency situations.
150839 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-346 | 0.56 | 1641.93 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151295 | Base | Cable Replacement Project - (SCH) - Welland - Bunting - Carlton - Cushman | 0.22473 | 1635.38 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 48 failures per 100km. The average cable installation year is 1975 in this project scope.
151385 | Base | Cable Replacement - (892) - 30-250 Janefield Ave Subdivision, Guelph | 0.65774 | 1629.86 | System Renewal | Underground Asset Renewal | Guelph
151136 | Base | C55 Alectra: Optimization of Business Practices | 0.59953 | 1624.9 | General Plant | Information Technology | Multiple | Optimizing the current software to communicate with other systems such as the ERP will allow for more efficient and effective budgeting processes and consolidation of information allowing for consistent reporting of the information from one system.
151436 | Base | Cable Injection-011 - Area 58 & 59- Winston Churchill & The Collegeway, Mississauga | 1.8731 | 1614.06 | System Renewal | Underground Asset Renewal | Enersource | There are 14 outages, we are injecting a total of 69,795 m of cable for this project, and the average age of the cable is 30 years.
151331 | Base | Cable Replacement Project - (V41) - Stephanie Blvd, Vaughan | 1.4609 | 1604.2 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 2 failures.
150842 | Base | Fleet_West_Vehicle Replacement_Bucket Truck 1-365 | 0.373 | 1584.73 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150642 | Base | Proactive Replacement of Remote Terminal Units - Central North | 0.16024 | 1582.3 | System Renewal | Substation Renewal | Brampton | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the Central-North Operating Area (Brampton). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
150617 | Base | Purchase of Critical Spare Parts - Central North | 0.029552 | 1568.76 | System Renewal | Substation Renewal | Brampton | This project involves procurement of critical spare parts for municipal stations in the Central North Operating Area (Brampton) so as to facilitate prompt repair of failed assets during emergency situations.
151292 | Base | Cable Replacement Project- (K4) - Queen - Torbram - Steeles - Bramalea | 1.2583 | 1568.3 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 cable failure to date. Cables are 41 to 50 years old and beyond EUL.
151087 | Base | Switchgear Replacement | 0.24145 | 1559.43 | System Renewal | Underground Asset Renewal | Guelph | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150618 | Base | Purchase of Critical Spare Parts - Central South | 0.035024 | 1556.59 | System Renewal | Substation Renewal | Enersource | This project involves procurement of critical spare parts for stations in the Central South Operating Area (former Enersource) so as to facilitate prompt repair of failed assets during emergency situations.
102077 | Base | Major repair, refurbishment, or conversions of distribution transformers | 0.030687 | 1540.55 | System Renewal | Transformer Renewal | Powerstream | Transformers returned or in stores where repair/refurbishment of the unit can return it to service at a lower cost then purchase of a new unit
150368 | M-Factor | New build - North Central feeders capacity (Carlton TS to Linwell Rd/Lake St) relief, St.Catharines | 0.98956 | 1480.62 | System Service | Capacity (Lines) | Horizon | This project is to alleviate capacity issues in the North and Central section of St.Catharines, primarily served by Carlton BY bus feeders which are over the planning limit.
151222 | Base | Concrete Structures | 0.19468 | 1469.44 | System Renewal | Underground Asset Renewal | Guelph | Replacement of lids on civil structures to avoid public risk
150334 | Base | Distribution Automation - West | 0.72 | 1424.45 | System Service | SCADA and Automation | Horizon | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151371 | Base | Cable Replacement - (87) - Marksam Rd/ Rhonda Rd Subdivision, Guelph | 0.635 | 1423.41 | System Renewal | Underground Asset Renewal | Guelph
151052 | Base | Emerging Customer Initiated Work - Relocations | 0.093876 | 1412.11 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
150751 | Base | Facilities_East_Capital Replacement Investment Support | 1.1888 | 1374.32 | General Plant | Facilities Management | Powerstream | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
151288 | Base | Cable Replacement Project - (H4) - Queen - Hwy 410 - Steeles - Kennedy, Brampton | 0.5859 | 1353.9 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2009 to 2018 with average duration of 189 minutes.
150335 | Base | Pole Renewal - West | 2.4306 | 1338.4 | System Renewal | Overhead Asset Renewal | Horizon | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
150795 | Base | Fleet_Central South Vehicle Replacement- 244-08 S Bucket | 0.49 | 1329.29 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151326 | Base | Cable Replacement Project - (V44) - Hayhoe - Islington - Hwy 7, Vaughan | 0.82285 | 1311.54 | System Renewal | Underground Asset Renewal | Powerstream | From 2016-2019YTD customers in this area experienced 6 failures.
102102 | Base | Enterprise File Synchronization and Sharing Platform | 0.025319 | 1307.59 | General Plant | Information Technology | Multiple | Alectra is looking for a secure Enterprise File Synchronization and Sharing solution that will increase productivity of internal and external teams by facilitating seamless collaboration of corporate data anywhere , anytime, and on any device without the restrictions of having to connect to the Alectra network. The overarching goal of this implementation will be to provide a balance between delivering business productivity and securing enterprise information.
150502 | Base | On-Line Dissolved Gas Oil Monitoring of 10 MS Transformers - EAST | 0.10459 | 1292.71 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Online DGA monitoring system at MS in East. Online DGA has proven to be invaluable in diagnosing a potential transformer failure as well as assessing the health of a transformer
150738 | Base | Facilities_West_Capital Replacement Investment Support | 0.26347 | 1289.1 | General Plant | Facilities Management | Horizon | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150573 | Base | Oracle ULA Extension | 1.5 | 1265.44 | General Plant | Information Technology | Multiple | MULTI ANSWER
150790 | Base | Fleet_Central South Vehicle Replacement-Puller/Tensioner | 0.2 | 1264.62 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151138 | M-Factor | Voltage Conversion - MS-2 Church St, Brampton | 1.42 | 1255.22 | System Renewal | Overhead Asset Renewal | Brampton | From 2015-2017 customers in this area experienced 11 outages and had 20,372 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
102241 | Base | Proactive Replacement of Remote Terminal Units - East | 0.10121 | 1239.66 | System Renewal | Substation Renewal | Powerstream | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the East Operating Area (former PowerStream). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
151282 | Base | Cable Replacement Project - (SCH) - Weiden | 0.19476 | 1218.42 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 6 failures, or 962 failures per 100km. The average cable installation year is 1978 in this project scope.
151064 | Base | Secondary Pedestals -St. Catharines | 0.19915 | 1153.93 | System Service | Safety & Security | Horizon | This project involves the replacment of above grade steel secondary pedestals which pose a safety risk to the general public
150862 | Base | Fleet_Central North Vehicle Replacement-RBD 57 | 0.55 | 1125.31 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151322 | Base | Cable Injection Project - (K4) - Queen - Torbram - Steeles - Bramalea, Brampton | 0.062063 | 1124.92 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 1 outage due to cable failure in 2007.
101125 | Base | Lines Mobile Equipment - IT/OT Infrastructure | 0.079786 | 1119.08 | General Plant | Information Technology | Multiple | This budget covers the deployment of mobile technology - laptops/field tablets and accessories - within the Lines Department to gain efficiencies in field operations. By deploying this technology, the Lines area can move away from a paper-based to a more electronic environment. In future, it is envisioned that, for example, mobile applications will facilitate the electonic transmission of work orders and electronic record keeping (asset tracking, tailboards, switching orders, timesheets). This will allow for streamlined operational processes and record-keeping, thereby supporting corporate technological initiatives such as the GIS, Outage Management System, and future Workforce Management system. At present, all Lines Management personnel and Subforemen have laptops, facilitating activities such as viewing of the GIS, electronic Asset Tracking Forms, and use of OMS Responder Mobile. Expenditures in this area will allow for more deployment of field devices among Lines crews and for the implementation of more computerized processes.
150500 | Base | On-Line Dissolved Gas Oil Monitoring of 10 MS Transformers - WEST | 0.20859 | 1116.55 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of Transformer bushing monitoring system in West
151405 | Base | Cable Replacement Project- Erin Mills & N.Sheridan (16), Mississauga | 1.2009 | 1104.63 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 8 outages, the length is 3,326 m, and the average cable age is 45 years old.
150570 | Base | Alectra West Substation Ground Grid Installations | 0.28943 | 1091.19 | System Service | Safety & Security | Horizon | This project is to install ground grid at East Stations
151204 | Base | Upgrade to Station Facilities (Buildings/Civil work) Multi-year | 0.01 | 1089.29 | General Plant | Facilities Management | Guelph | This project involves work involving structural components of stations, including windows, brickwork, roofs, foundations, drainage, doors, etc. at stations in the SouthWest Operational Area. Not keeping up with this work would result in advanced deterioration resulting in even greater maintenance costs, potential safety concerns and potential failure of the electrical equipment in the building causing power interruptions.
151293 | Base | Cable Replacement Project - (SCH) - Lakeshore - Stanley - Parnell - Chancery | 0.87706 | 1080.5 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 55 failures per 100km. The average cable installation year is 1978 in this project scope.
151327 | Base | Cable Replacement Project - (BR6) - 8th and Dissette, Bradford | 0.3612 | 1077.44 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 6 failures.
151041 | Base | Protection Logic Upgrades - East MSs (North) | 0.082351 | 1061.11 | System Service | System Control, Comm'ns & Performance | Powerstream
150859 | Base | Fleet_West_Vehicle Replacement_Cargo Vans | 0.16 | 1059.81 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150865 | Base | Fleet_West_Vehicle Replacement_Pickups | 0.165 | 1055.49 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151406 | Base | Cable Replacement Project- Rathburn Rd W & Queenbridge (8), Mississauga | 0.27904 | 1052.58 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 4 outages, the length is 857 m, and the average cable age is 40 years old.
150762 | Base | Facilities_Reno_Patterson - Service Centre Upgrades | 0.10858 | 1035.79 | General Plant | Facilities Management | Powerstream | Repairs to building envelop/walls to prevent further damage to the build infrastructure and systems that are supporting critical operational systems such as control rooms, server rooms, customer services groups, etc.
100919 | M-Factor | Install 2nd 27.6 kV Cct on Woodbine Ave from Elgin Mills Rd to 19th Ave | 0.64108 | 1027.78 | System Service | Capacity (Lines) | Powerstream | This project is to add one additional 27.6kV cct on the existing pole line from Elgin Mills Rd to 19th Ave that has provision for 2nd cct to increase capacity in the 19th and woodbine area as well as the Future Urban area
151157 | Base | Fleet_West_Vehicle Replacement_Dump/Cargo Truck | 0.2 | 1025.25 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150578 | Base | Alectra - Microsoft Software | 0.10229 | 1020.9 | General Plant | Information Technology | Multiple | Compliance for Alectra employees for Microsoft application suite of products to perform daily operation .
151334 | Base | Cable Replacement Project - (BA13) - Dunlop and Miller, Barrie | 0.4011 | 1009.91 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 41 years old and will be 43 when project starts (2021).
150392 | Base | Storage Upgrade | 0.30687 | 994.99 | General Plant | Information Technology | Multiple | Upgrade on premise Enterprise Storage platform in addition to increased capacity requirements as a result of employee and customer demand for data retention. Off Premise storage costs (SharePoint Online, One Drive, Development, test and production environments)
151091 | Base | Switchgear Renewal - Central South | 3.6886 | 982.44 | System Renewal | Underground Asset Renewal | Enersource | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151159 | Base | Fault Indicator Installation and Replacement - Hamilton and St. Catharines | 0.2739 | 966.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of fault indicator installation in West
150628 | Base | Station Equipment Temperature Monitoring-CENTRAL | 0.077185 | 965.25 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of Station Temperature Monitoring system in Central South and this enables controlled emergency loading beyond the nameplate rating.
150929 | Base | Fleet East Vehicle replacement - Pickup truck 3500 | 0.5245 | 957.25 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151287 | Base | Cable Replacement Project - (SCH) - Bolger - Elma - Dorothy - The Meadows | 0.44633 | 952.98 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 10 failures, or 322 failures per 100km. The average cable installation year is 1976 in this project scope.
151065 | Base | Manhole Lid Replacement | 0.34856 | 925.3 | System Renewal | Underground Asset Renewal | Horizon | Replacement of lids on civil structures to avoid public risk
150317 | M-Factor | Voltage Conversion - Deerhurst MS, Hamilton | 2.5985 | 869.07 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 6 outages and had 121,838 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
150904 | Base | Fleet East Yearly Light and Misc equipment | 0.03655 | 846.86 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150914 | Base | Fleet East Vehicle replacement - Pickup truck 1500 | 0.038244 | 841.88 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150910 | Base | Fleet East Unit # 91 Single bucket truck replacement | 0.48131 | 838.95 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150866 | Base | Fleet_ Central North Vehicle Replacement -Forklift 178 | 0.075 | 791.81 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
101622 | Base | DACS Inverters and RTU's removal - East | 0.026659 | 765.32 | System Renewal | Substation Renewal | Powerstream | This project involves removal of obsolete and out-of-service DACs inverters, RTUs and associated wiring at stations in the East Operating Area (former PowerStream) so as to remove clutter, thus simplifying future work and freeing up space for future station upgrades.
150779 | Base | Fleet_Central South Replacement-DBL.Bucket 228-05 | 0.58 | 763.21 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150864 | Base | Fleet_Central North Vehicle Replacement_Loader 175 | 0.09 | 762.45 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
101632 | Base | Obsolete Revenue Metering Removal from TSs | 0.027144 | 739.84 | System Service | Safety & Security | Powerstream | Evolution of the distribution system to permit more efficient integration of DERs to yield 18
150921 | Base | Fleet East Unit # 123 83' Double Bucket | 0.6111 | 717.92 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150922 | Base | Fleet East Unit # 59 digger truck | 0.56822 | 714.31 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150925 | Base | Fleet East Vehicle replacement - Cube Vans | 0.2387 | 701.21 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151082 | Base | SCADA Infrastructure | 0.10358 | 688.19 | System Service | System Control, Comm'ns & Performance | Guelph
151058 | Base | Distribution Transformer Replacements & Upgrades | 0.34892 | 682.68 | System Renewal | Transformer Renewal | Guelph | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150719 | Base | Upgrade of JMUX Optical Interfaces - Alectra East SONET Ring | 0.25995 | 676.42 | System Service | System Control, Comm'ns & Performance | Powerstream
150669 | Base | Burden Allocation - System Access | 0.62907 | 669.62 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
102166 | Base | SQL Expansion - IT Infrastructure | 0.46031 | 635.85 | General Plant | Information Technology | Multiple | Expand existing SQL infrastructure to meet project demands and natural growth of database. Add system capacity, improve performance, and reduce the risk of downtime due resource constraints.
150863 | Base | Fleet_Central North Vehicle Replacement-S/Bucket 70 | 0.49 | 620.35 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150203 | Base | Station Equipment Temperature Monitoring-NORTH & TS | 0.065041 | 614.42 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of Station Temperature Monitoring system in East and it enables controlled emergency loading beyond the nameplate rating.
150496 | Base | iPass Project Management – Planned Capital - West | 0.69705 | 589.28 | System Renewal | Underground Asset Renewal | Horizon | Help in optimizing DER performance and efficiency to improve addressing overall energy needs.
150876 | M-Factor | Fleet_Central North Vehicle Replacement_ Step Vans 6310 | 0.25 | 567.71 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102046 | Base | Purchase of Major Tools - Muliti Year-North & TS | 0.045969 | 565.1 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150793 | M-Factor | Fleet_Central South Vehicle Replacement-210-09 S/bucket | 0.49 | 560.3 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151206 | Base | Installation of SWI Video Security System | 0.025 | 544.35 | System Service | Safety & Security | Guelph | This project consists of installation of SWI Video security system in SouthWest. The implementation of video monitoring will ensure that station security and safety related issues can be easily identified and addressed immediately
150905 | Base | Fleet East Multi Year Shop tools | 0.011035 | 544.12 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of tools and shop equipment required to repair and maintain vehicles to ensure vehicle availability to support capital systems projects.
101816 | Base | Alectra East (South), Fault Indicator Installation and Replacement Multi-year initiative | 0.24416 | 542.12 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - North Region which will result improved outage response, operational efficiency, and reliability
151085 | M-Factor | Rear Lot Conversions | 0.11594 | 530.82 | System Renewal | Rear Lot Conversion | Guelph
101134 | Base | Alectra East (North), Fault Indicator Installation and Replacement Multi-year initiative | 0.24643 | 527.43 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - South Region which will result improved outage response, operational efficiency, and reliability
150437 | Base | OT GIS & OMS Enhancements | 0.35097 | 519.79 | General Plant | Information Technology | Multiple | Ongoing productivity enhancements to core GIS and OMS platforms to meet internal and customer demand for functionality.
150602 | Base | Smart Meter Test Facility - PowerStream RZ | 0.020075 | 471.4 | System Access | Metering | Powerstream | Multi-year project to expand the capability of the Meter Test Facility to test increasing types of meters and AMI systems before they are placed into production.
102027 | Base | Purchase of Critical Spare Parts - Multiyear - East | 0.071417 | 427.82 | System Renewal | Substation Renewal | Powerstream | This project involves procurement of critical spare parts for transformer and municipal stations in the East Operating Area (former PowerStream) so as to facilitate prompt repair of failed assets during emergency situations.
150494 | Base | iPass Project Management – Planned Capital - Central-North | 0.38599 | 408.86 | System Renewal | Overhead Asset Renewal | Brampton | Predicting the influence of weather conditions and DER contribution simultaneously on the power grid, for proactively mitigating local outages,
150495 | Base | iPass Project Management – Planned Capital - Central-South | 0.38599 | 408.86 | System Renewal | Overhead Asset Renewal | Enersource | Enable better visibility towards preventive equipment maintenance needs arising due to DER penetration which will further help mitigate outage risks,
101781 | Base | iPass Project Management – Planned Capital - East | 0.39019 | 408.86 | System Renewal | Overhead Asset Renewal | Powerstream | Estimating the effects of DER contribution at the feeder and region levels to further optimize the energy flows between the Utility and its consumers,
150607 | M-Factor | Station LED Lighting Upgrades - Central | 0.026953 | 407.91 | System Renewal | Substation Renewal | Enersource | Replacement of inefficient lighting fixtures and lamps at stations in the Central Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150606 | M-Factor | Station LED Lighting Upgrades - EAST | 0.026953 | 407.91 | System Renewal | Substation Renewal | Brampton | Replacement of inefficient lighting fixtures and lamps at stations in this Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150513 | Base | Installation of SWI Video security system at 4 MS stations per year - Annual Multi-year initiative-EAST | 0.11992 | 372.49 | System Service | Safety & Security | Brampton | This project consists of installation of SWI Video security system in CentralNorth
150951 | M-Factor | Fleet East Vehicle addition - Van pool van | 0.042436 | 344.51 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102034 | Base | Upgrade to Station Facilities (Building / Civil work) Multi-year - East | 0.13419 | 339.91 | System Renewal | Substation Renewal | Powerstream | MULTI ANSWER
150550 | Base | ServiceNow Expansion - IT Infrastructure | 0.058664 | 325.33 | General Plant | Information Technology | Multiple | Building and adding features within ServiceNow we will eliminate outdated processes by automating more tasks and decisions allowing us to be more efficient and productive. Enhancements include the automation of the flow of data between other systems and across programs used by various departments and ServiceNow. Servicebots will be used as ServiceNow learns from past patterns, in order to predict future outcomes, including determining risks, assigning owners, and categorizing work. Learned models set the category of the IT request and assign the task to the right team, as well as calculate associated risk of action or inaction. This capability will improve the speed and efficiency of IT service delivery.
150575 | Base | OT Scada map Cleanup | 0.46031 | 315.81 | General Plant | Information Technology | Multiple | SCADA Map clean up program to ensure accuracy and safety in the SCADA environment.
150873 | M-Factor | Fleet_Central North Vehicle Replacement_Vans | 0.108 | 308.34 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150884 | M-Factor | Fleet_Central North Vehicle Replacement Pick up 9514 | 0.052 | 299.15 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150610 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - Central | 0.021144 | 289.6 | System Renewal | Substation Renewal | Enersource | Existing driveways at stations in the Central Operational Area that are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150609 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - East | 0.021144 | 289.6 | System Renewal | Substation Renewal | Brampton | Existing driveways in this Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150612 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - West | 0.021144 | 289.6 | System Renewal | Substation Renewal | Horizon | Existing driveways in the West Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150800 | M-Factor | Fleet_Central South Vehicle Replacement- trailer | 0.04 | 288.32 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102050 | Base | Various Stations-Station Lighting Upgrade/Retrofit-Energy Efficiency Lighting-initiative Multi-year - East | 0.055316 | 239.8 | System Renewal | Substation Renewal | Powerstream | Replacement of inefficient indoor and outdoor lighting fixtures and lamps at stations in the East Operating Area (former PowerStream) will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150961 | Base | Fleet_West_Vehicle Replacement_Forklift | 0.24 | 219.79 | General Plant | Fleet Renewal | Horizon | Asset replacement due to poor conditions and age and lack of parts replacement. Equipment not as available to support capital system renewal projects and respond to emergencies with material handling. .
150787 | M-Factor | Fleet_Central South Vehicle Replacement- Van | 0.05 | 182.88 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
103030 | Base | Technology Upgrades Improving the System Control Room Environment | 0.055714 | 147.52 | General Plant | Information Technology | Multiple | This project will continue to build on the original capital project whose scope was focused on the replacement of computers used as Operator WorkStations. The scope of this program has been expanded to account for all technology purchases required for the Control Room theater.
151108 | Base | Office Equipment | 0.072546 | 143.52 | General Plant | Facilities Management | Guelph | Replace aging equipment within the Guelph operational centre to ensure optimal performance in managing the distribution assets
151381 | Base | 2021 GUELPH - Fleet | 0.68 | 138.35 | General Plant | Fleet Renewal | Guelph | Replacement of end of life asset due to poor conditions, high mileage and engine hours and age. Vehicle experiencing more down time at the shop for repairs and maintenance impacting vehicle availability.
151245 | M-Factor | Capacitor Bank Installations | 0.01 | 134.68 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of capacitor bank installation to increase power factor, capacity and reduce losses.
102931 | Base | Paving of 3 MS & TS Station Driveways per year - Annual Multi-year initiative - East | 0.048447 | 125.42 | System Renewal | Substation Renewal | Powerstream | Existing driveways at stations in the East Operating Area (former PowerStream) are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
151039 | Base | Fleet_West_Equipment_Key Box | 0.015 | 124.35 | General Plant | Fleet Renewal | Horizon | Adopted the current vehicles key management system at all sites to ensure access to vehicles when required. This ensure access to vehicles after hours and tracking of vehceil keys.
150655 | Base | Maingate MS - Station RTU and Protection Relays Upgrade | 0.15255 | 123.91 | System Service | System Control, Comm'ns & Performance | Enersource | This project consist of RTU and protection relay upgrade at Maingate MS
150689 | Base | Rogers MS - Station RTU and Protection Relays Upgrade | 0.15255 | 123.91 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of bus, line and transformer protection at Richmond Hill TS
151076 | Base | Fuel Pump Replacement Vansickle Rd. | 0.027363 | 122.83 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of systems that have surpass end of life, are consistently down for repairs and parts are difficult to obtain, impacting fuel of vehicles to support capital systems projects and customer emergencies responses.
150597 | Base | Lock Box Installs - East | 0.0098551 | 115.84 | System Access | Metering | Powerstream | Multi-year project to install lock boxes at ICI properties with restricted access to eliminate need for a customer appointment for access.
150569 | Base | Server OS Upgrades - IT Infrastructure | 0.075094 | 95.22 | General Plant | Information Technology | Multiple | Operating system upgrades to support IT infrastructure.
150737 | Base | Facilities_East Region_Reactive Capital | 0.26347 | 91.88 | General Plant | Facilities Management | Powerstream | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150736 | Base | Facilities_West Region_Reactive Capital | 0.26347 | 91.88 | General Plant | Facilities Management | Horizon | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150734 | Base | Facilities_Central Region_Reactive Capital | 0.26347 | 91.85 | General Plant | Facilities Management | Multiple | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
151079 | Base | Fleet West Major Equipment & Tools | 0.05 | 90.95 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of tools and shop equipment required to repair and maintain vehicles to ensure vehicle availability to support capital systems projects.
150676 | Base | Mobile Devices - IT Infrastructure | 0.010229 | 88.32 | General Plant | Information Technology | Multiple
103171 | Base | Implementation of a new Alectra Network Operations Voice Radio System | 0.025 | 79 | General Plant | Information Technology | Multiple
150563 | Base | OT SCADA upgrade cycle 3 | 0.20617 | 46.3 | General Plant | Information Technology | Multiple | Planned hardware updrades for monitors and workstations on enterprise SCADA platform.
150747 | M-Factor | Net Zero Energy Emissions | 0.31505 | 34.58 | System Service | Distributed Energy Resources (DER) | Powerstream | The project will help Alectra Utilities to ensure that growing DER challenges are met through building expertise and capability in real time monitoring, integrating and optimizing of DERs in line with customer preferences. This will lead to a system that can safely integrate and optimize value from DERs for the benefit of customers.
151053 | Base | Building Sustainment | 0.18296 | 31.98 | General Plant | Facilities Management | Guelph | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150562 | Base | OT Firewall Upgrade | 0.24509 | 19.71 | General Plant | Information Technology | Multiple | Hardware upgrade cycle for OT platform.
150704 | Base | Feeder Protection Migration to DNP - Jim Yarrow TS | 0.17153 | 15.9 | System Renewal | Substation Renewal | Brampton | This is part of a multi-phase project to upgrade aging and failure-prone protection systems at Jim Yarrow TS to the current protection standards. Proper protection to distribution feeders will provide protection to the assets in the case of faults.
151031 | Base | Fleet Shop equipment refurbishment and replacement | 0.054 | 12.85 | General Plant | Fleet Renewal | Enersource | For the refurbishment of trailers, shop compressors and hoists to extend the life of the assets instead of replacement to reduce the need fro capital expenditures.
150678 | Base | P&C Specific Tools & Testing Equipment - West | 0.016418 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
102999 | Base | P&C Specific Tools and Testing Equipment | 0.016418 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
102157 | Base | Server Refresh - IT Infrastructure | 0.41131 | 10.1 | General Plant | Information Technology | Multiple | Ongoing server refresh to support applications.
150396 | Base | Network Refresh - IT Infrastructure | 0.3638 | 9.81 | General Plant | Information Technology | Multiple | Replacement of existing network infrastructure that is unsupported (or soon to be) including further rationalization and design modifications to support the delivery of services throughout the Alectra Environment.

## 2022 Ranking
Project List for Oral Hearing Undertakings
Project Number | Funding | Project Name | 2022 ($MM) | Project Score | Investment Category | Investment Grouping | Rate Zone | Comment
150404 | Base | Kenilworth TS Power Factor Correction | 0.62073 | 184356.97 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of capacitor bank installation at Kenilworth TS to improve PF and to comply with IESO market rules.
150725 | Base | Lines Central-North - Reactive Renewal | 1.2471 | 181453.58 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have failured and requires replacement in order to restore power to customers
150690 | Base | Lines Central-South - Reactive Renewal | 3.1962 | 171817.68 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have failured and requires replacement in order to restore power to customers
150682 | Base | Remote Fault Indicator Deployment | 0.44855 | 164220.93 | System Service | System Control, Comm'ns & Performance | Multiple | This project consists of remote fault indictor deployment which will result improved outage response, operational efficiency, and reliability
102247 | Base | Interest Capitalization | 1.1887 | 104303.71 | General Plant | Other General Plant | Powerstream
150596 | Base | Meter Renewal - all types but Suite - PowerStream RZ | 0.085105 | 94470.24 | System Access | Metering | Powerstream | Multi-year project to renew existing residential (except suite) metering equipment.
101871 | Base | Services (New and Upgrades) - Layouts – East North - Commercial Services | 0.015105 | 94398.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151180 | Base | Central-North - Capitalization of Locates | 0.023974 | 94387.49 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150600 | Base | Firmware Upgrades for Smart Meters - East | 0.023999 | 94363.34 | System Access | Metering | Powerstream | Multi-year project to renew residential Smart meter firmware to improve communication performance.
151169 | Base | Central-South - Capitalization of Locates | 0.029967 | 94344.62 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
151174 | Base | West Lines - Capitalization locates | 0.035961 | 94319.23 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150631 | Base | Transformer Station Metering - Central North | 0.051958 | 94245.75 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew wholesale metering equipment.
101696 | Base | Subdivision - North Underground Residential Distribution System Final Close out and Inspection. | 0.047975 | 94197.28 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
103381 | Base | East Lines - Capitalization locates | 0.061048 | 94144.61 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101870 | Base | Services (New and Upgrades) - Layouts – East South - Commercial Services | 0.074015 | 94022.15 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101869 | Base | Services (New and Upgrades) - Layouts – East North - New Residential | 0.078495 | 93989.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150650 | Base | Replace PCB Risk PT's - Enersource RZ | 0.10295 | 93977.25 | System Access | Metering | Enersource | Multi-year project to replace metering transformers identified with unacceptable levels of PCB's, to prevent hazardous spills.
101919 | Base | New Services (new and upgrades) - Commercial, Industrial and Institutional (ICI) Projects - NORTH | 0.083592 | 93955.31 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150647 | Base | Transformer Station Metering - Enersource RZ | 0.14441 | 93884.28 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew wholesale metering equipment.
151049 | Base | Commercial, Industrial, Institutional, Apartment Connections | 0.13419 | 93829.96 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
101685 | Base | Subdivision - South Underground Residential Distribution System Final Close out and Inspection. | 0.11568 | 93778.29 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150457 | Base | Services (New and Upgrades) - Layouts – St Catharines | 0.1945 | 93519.09 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151162 | Base | Non Recoverable replacement of Distribution Equipment due to accident/vandalism | 0.25438 | 93457.13 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101924 | Base | Mulit Unit Metering for New Buildings NORTH - PowerStream RZ | 0.1669 | 93421.21 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in northern area of territory.
150588 | Base | New Residential Subdivision Development - Alectra West | 0.21105 | 93265.82 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
101791 | Base | New Services - new and upgrades - COMMERCIAL, INDUSTRIAL, INSTITUTIONAL (ICI) SERVICES - SOUTH | 0.24859 | 92878.02 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101812 | Base | Reactive Capital, Alectra East - LIS | 0.28737 | 92710.01 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150754 | Base | Lines Central-North - Non-Recoverable Replacements | 0.35849 | 92705.38 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150726 | Base | Lines Central-South - Non-Recoverable Replacements | 0.35849 | 92705.38 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101820 | Base | Reactive Capital, Alectra East - Non-Recoverable Replacement | 0.30541 | 92582.71 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150389 | Base | Services (New and Upgrades) - Layouts – Central North | 0.39537 | 92563.35 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150651 | Base | C & I Metering - Renewal- Brampton RZ | 0.066045 | 92560.77 | System Access | Metering | Brampton | Multi-year project to renew existing ICI metering equipment.
150386 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central North | 0.42384 | 92424.37 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150453 | Base | CIS CC&B Modifications(Regulatory Enhancements) | 0.94882 | 92260.88 | General Plant | Information Technology | Multiple | Enhancements to the CIS (CC&B) application needed to meet any regulatory requirements Such requirements in the past have been Ontario Energy Savings Program (OESP) as well as the Monthly Billing projects.
150649 | Base | Suite Metering - Enersource RZ | 0.56469 | 91838.22 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew suite metering equipment.
150654 | Base | C & I Metering - New Services - Brampton RZ | 0.58376 | 91552.85 | System Access | Metering | Brampton | Multi-year project to purchase and install ICI metering equipment on new services.
150595 | Base | C & I and Wholesale Metering - PowerStream RZ | 0.55172 | 91530.35 | System Access | Metering | Powerstream | Multi-year project to purchase, install, and renew ICI and wholesale metering equipment.
101868 | Base | Services (New and Upgrades) - Layouts – East South - New Residential | 0.46825 | 91488.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101795 | Base | Multi Unit Metering for New Buildings SOUTH - PowerStream RZ | 0.4991 | 91273.08 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in southern area of territory.
101873 | Base | Services (New and Upgrades) - Layouts – East North - Residential Upgrades | 0.55057 | 91023.49 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151051 | Base | System Relocations Road Authorities | 0.68926 | 91002.2 | System Access | Road Authority | Guelph | Mandatory - System Access Related Project
150652 | Base | New Residential Subdivision Development - Alectra Central South | 1.0759 | 90948.17 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150388 | Base | Services (New and Upgrades) - Layouts – Central South | 0.76177 | 90774.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150692 | Base | New Feeder in Residential Subdivision Development - Alectra Central North | 0.74488 | 90609.19 | System Service | Capacity (Lines) | Brampton | This expenditure is required to meet the needs of the development community that construct municipal approved residential subdivisions in Alectra Utilities' Central North service territory
150599 | Base | Suite Meter - Reverification - PowerStream RZ | 0.12717 | 90368.15 | System Access | Metering | Powerstream | Multi-year project to renew Measurement Canada seal dates on existing suite metering equipment.
150455 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - St Catharines | 0.87937 | 90201.14 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150659 | Base | Residential Meters - by Metering - Brampton RZ | 0.85775 | 90095.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Metering.
150456 | Base | Services (New and Upgrades) - Layouts – Hamilton | 0.90833 | 89961.61 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150630 | Base | New Residential Subdivision Development - Alectra Central North | 1.099 | 89952.48 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101828 | Base | Reactive Capital, Alectra East - Recoverable Replacement | 0.74789 | 89765.65 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover some costs for (i.e. pole hit, vehicle at scene of accicent, Alectra Utilities obtains most of costs (near $0 impact too budget))
101896 | Base | New Institutional/Commercial/Industrial Subdivision Development - Alectra East | 0.93074 | 89347.36 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101872 | Base | Services (New and Upgrades) - Layouts – East South - Residential Upgrades | 0.81566 | 89344.81 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101800 | Base | Reactive Capital, Alectra East - Storm Damage | 1.2418 | 86549 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151047 | Base | Subdivisions | 0.3556 | 85393.33 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
150620 | Base | Metering Renewal - all types - Horizon RZ | 2.0522 | 84064.36 | System Access | Metering | Horizon | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment.
101808 | Base | Reactive Capital, Alectra East - Switchgears | 1.7686 | 83304.08 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150648 | Base | Metering Renewal - all types but Suite - Enersource RZ | 2.3142 | 82569.47 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew residential (except suite) and ICI metering equipment.
101892 | Base | New Subdivision Development - Secondary Service Lateral - Alectra East | 2.8058 | 80775.74 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150384 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central South | 3.3973 | 77903.71 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150449 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - Hamilton | 5.1748 | 69328.05 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151095 | Base | Reactive Restoration | 1.0452 | 63546.92 | System Renewal | Reactive Capital | Guelph | Replacement of assets which have failured and requires replacement in order to restore power to customers
101824 | Base | Reactive Capital, Alectra East - Distribution Equipment | 5.4254 | 58189.58 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151161 | Base | Joint Use Pole Removal | 0.11763 | 57199.8 | System Renewal | Overhead Asset Renewal | Horizon | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
151050 | Base | Metering - all types - Guelph RZ | 0.41379 | 55986.2 | System Access | Metering | Guelph | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment in Guelph RZ.
150469 | Base | ERP JD Edwards Enhancements | 1.8321 | 55714.6 | General Plant | Information Technology | Multiple | Allocation of capital funds to provide 3rd party assistance on capital work, along with creating system enhancements to the JD Edwards ERP and supporting Systems.
101832 | Base | Joint Use Pole Removal | 0.58872 | 54024.42 | System Renewal | Overhead Asset Renewal | Powerstream | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
100159 | M-Factor | Hydro One Asset Purchase - Alliston | 0.49814 | 52600.71 | System Service | Capacity (Lines) | Powerstream | Purchase the 44 kV pole line along Industrial Parkway (approx 4.5 km's). The pole line is required for the new Alliston 10MVA substation 13.8kV integration (101571).
101887 | Base | New Residential Subdivision Development - Alectra East | 10.1819 | 44863.95 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
100859 | Base | Switchgear Renewal - East | 2.8111 | 43704.68 | System Renewal | Underground Asset Renewal | Powerstream | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151089 | Base | Overhead Rebuilds | 1.2415 | 39246.49 | System Renewal | Overhead Asset Renewal | Guelph | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
150471 | Base | ERP JD Edwards Hardware Upgrades | 0.55348 | 38645.83 | General Plant | Information Technology | Multiple | Hardware upgrade to support ERP refresh cycle.
101508 | Base | Transformer Renewal - East | 2.9346 | 37474.31 | System Renewal | Transformer Renewal | Powerstream | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150673 | Base | Road Authority Central (Mississauga) | 4.1917 | 35000.51 | System Access | Road Authority | Enersource | Mandatory - System Access Related Project
150134 | Base | Cable Injection Project - (V37) - Langstaff and Weston, Vaughan | 1.671 | 34877.34 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 20 failures.
150073 | M-Factor | Vaughan TS#1 Bus Differential & Overcurrent Protections Upgrades | 0.29034 | 34014.15 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Vaughan TS#1 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
150645 | Base | Road Authority Central (Brampton) | 4.9673 | 31813.54 | System Access | Road Authority | Brampton | Mandatory - System Access Related Project
150828 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-West | 0.925 | 31592.28 | System Renewal | Overhead Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151452 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-West | 0.925 | 31590.16 | System Renewal | Underground Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
101762 | Base | Road Authority Expenditure PS South | 4.1233 | 31544.34 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
101355 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-East | 0.955 | 31424.67 | System Renewal | Overhead Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151450 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-East | 0.955 | 31424.67 | System Renewal | Underground Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151363 | Base | Cable Injection Project - (M25) - 14th - McCowan - Steeles - Old Kennedy, Markham | 0.819 | 27518.58 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 14 failures.
150364 | M-Factor | New build - Port Credit Village East (Marina) 27.6kV Feeders, Mississauga | 4.4396 | 25989.14 | System Service | Capacity (Lines) | Enersource | The Port Credit East development requires a 27.6kV circuit expansion in order to provide capacity and contingency for the Mid-rise mixed residential/commercial development.
100867 | Base | Pole Renewal - East | 5.2696 | 25595.06 | System Renewal | Overhead Asset Renewal | Powerstream | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
151074 | Base | Reactive renewal | 3.3439 | 25136.12 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have failured and requires replacement in order to restore power to customers
151362 | Base | Cable Injection Project - (M39) - 16th - Warden - Hwy 7 - Woodbine, Markham | 1.2602 | 23713.55 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 8 failures.
151360 | Base | Cable Injection Project - (M31) - 14th - Old Kennedy - Steeles - Warden, Markham | 0.84754 | 23640.66 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 38 failures.
150070 | M-Factor | Markham TS#1 Bus Differential & Overcurrent Protections Upgrades | 0.11644 | 22499.7 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Markham TS#1 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
151043 | Base | Transformer Renewal - Central South | 1.9378 | 21869.73 | System Renewal | Transformer Renewal | Enersource | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150467 | M-Factor | CIS CC&B upgrade | 6.7766 | 21391.8 | General Plant | Information Technology | Multiple | Aligns with Alectra customer experience plan requirements and enhanced services and emerging channels. Comprised of third party integration support, hardware, resources, testing to support existing Alectra platform as the current version 2.5 support ends in 2022. Project ensures enhanced functionality, compatibility with ancillary systems, security upgrades, automation and rate billing engine to support future utility DER integration.
101480 | M-Factor | Build double ccts 27.6kV pole line on 19th Ave between Leslie St and Bayview Ave | 1.2926 | 20986.73 | System Service | Capacity (Lines) | Powerstream | This project is to build 2 ccts pole line on 19th Ave from Leslie St to Bayview Ave to supply the new subdivision in Leslie North that is bounded by Elgin Mills Rd., Leslie St., 19th Avenue and Bayview Avenue. There will be new houses along 19th Ave between Bayview Ave and Leslie St as the subdivision secondary plan, however, there is no pole line now.
150371 | M-Factor | New build - 27.6kV Feeder Extension Traders, Mississauga | 2.7822 | 19791.79 | System Service | Capacity (Lines) | Enersource | Install new feeders in the Traders area between Hurontario St and Kennedy Rd from Matheson Blvd to Britannia Rd required to meet demand due to intensification and to ensure the reliability of current customers.
151303 | Base | Cable Replacement Project - (HAM) - Stone Church - Garth - Lincoln M. Alexander | 2.4283 | 19664.79 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 5 failures, or 18 failures per 100km. The average cable installation year is 1976 in this project scope.
150664 | Base | Residential Meters - by Lines - Brampton RZ | 0.64049 | 18166.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Lines.
151109 | Base | Switch Replacement | 0.17872 | 18145.07 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
150458 | Base | MAS upgrade - IT Infrastructure | 0.10345 | 17425.57 | General Plant | Information Technology | Multiple | Metering Automation System for smart grid Upgrade to be implemented in a phased approach over the next 4 years as smart grid continues to evolve work in conjunction with the metering team to analyze and implement leverage new technologies to provide better more accurate meter readings be responsive to the issues first not reactive when a customer calls
151104 | Base | Distribution Automation - Central North | 0.48499 | 17389.16 | System Service | SCADA and Automation | Brampton | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151318 | Base | Cable Injection Project - (I3) -Bovaird - Dixie - Queen - Hwy 410, Brampton | 0.26269 | 16118.68 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2014 to 2015 with average duration of 71 minutes.
150639 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-CENTRAL | 0.038785 | 15735.56 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of DC charging system for Central South Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150638 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-East | 0.038785 | 15735.56 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of DC charging system for Central North Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150636 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-North & TS | 0.038785 | 15735.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of DC charging system for East Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150640 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-WEST | 0.038785 | 15735.56 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of DC charging system for West Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
151460 | M-Factor | Cable Injection Project - (V17) - Langstaff - Keele - Rutherford - Dufferin, Vaughan | 0.62198 | 15316.59 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 3 failures. From 2015-2019 YTD customers in this area experienced 4 failures.
150285 | Base | Transformer Renewal - Central North | 1.0293 | 14492.05 | System Renewal | Transformer Renewal | Brampton | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
101027 | Base | Switch Renewal - East | 0.68016 | 14308.5 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
150504 | Base | Purchase and Installation of 10 Self Recharging Transformer Air Breathers on TS and MS Transformers - Multi-year initiative-WEST | 0.05495 | 14105.38 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of transformer air breather at TS and MS stations in East .Moisture in transformer oil is a major cause of acceleration of transformer ageing and internal failure of transformers. By elimination of moisture ingress through the transformer breather, and having the breather perform this task automatically without human intervention ensures that the transformer oil moisture is minimal.
102098 | Base | Client - IT Infrastructure | 1.2313 | 13761.18 | General Plant | Information Technology | Multiple | To upgrade desktop/laptop/mobile devices that are 5 years or older (Approximately 20% of our equipment). Net new equipment for mobile computing as well as upgrades and replacements for damaged devices. Request made by various business units. This budget also includes RSA tokens\Licenses, monitors, mice, keyboards, docking stations, tablets and small non-MFP printers. Out of Scope: Large MFP Printers
151247 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.595 | 13413.53 | System Renewal | Overhead Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102232 | Base | Capital Funds for Emergency P&C Purchases - East | 0.033209 | 13270.97 | System Renewal | Substation Renewal | Powerstream | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the East Operating Area (former PowerStream). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150683 | Base | Capital Funds for Emergency P&C Purchases - Central North | 0.033209 | 13184.55 | System Renewal | Substation Renewal | Brampton | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central North Operating Area (Brampton). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150685 | Base | Capital Funds for Emergency P&C Purchases - West | 0.033209 | 13184.55 | System Renewal | Substation Renewal | Horizon | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the West Operating Area (former Horizon). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150684 | Base | Capital Funds for Emergency P&C Purchases - Central South | 0.033209 | 13184.55 | System Renewal | Substation Renewal | Enersource | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central South Operating Area (former Mississauga). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150784 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.695 | 12968.3 | System Renewal | Overhead Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151453 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.74382 | 12922.02 | System Renewal | Underground Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
150823 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.745 | 12654.97 | System Renewal | Overhead Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102099 | Base | Printer & Copier Fleet Replacement | 0.033209 | 12636.08 | General Plant | Information Technology | Multiple | Replacement of existing fleet of printers/copiers that are 5 or more years old. This will include non-MFP printers. Replacement to be determined by an evaluation of evolving needs and corporate requirements as well as age of equipment.
151449 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.885 | 12175.67 | System Renewal | Underground Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
103211 | Base | Misc Software Upgrades (FormScape, AutoCAD, etc.) - IT/OT Infrastructure | 0.076823 | 12020.93 | General Plant | Information Technology | Multiple | Upgrade/ acquire software as required / requested by business.
151451 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.905 | 11935.99 | System Renewal | Underground Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151233 | M-Factor | New Construction - Campbell TS 36M63 Feeder PHASE 1 & 2, Guelph | 1.1869 | 11851.33 | System Service | Capacity (Lines) | Guelph | This project identifies a new 13.8kV feeder required from Campbell TS to bring additional load support to NW section of the city as the existing 13.8kV feeders in the area are unable to accommodate the additional load growth
103180 | Base | Citrix Xen Virtualization Expansion - IT Infrastructure | 0.051727 | 11298.77 | General Plant | Information Technology | Multiple | Client computing virtualization (Citrix) is currently the standard delivery method for applications and desktops at Alectra. This system has had a tremendous uptake in the organization and requires an upgrade in back-end infrastructure to support the additional demand from the business.
150693 | M-Factor | Blockchain | 0.57314 | 11191.63 | System Service | Distributed Energy Resources (DER) | Multiple | The project will prepare Alectra Utilities to engage with customers in a real-time and transparent process to record the flow of electricity to and from DERs, enabling the efficient procurement of distribution benefits, such as demand response and frequency regulation. The project will provide a robust settlement mechanism between Alectra and customers, backed by timely and efficient financial transactions, to enable overall trust and customer value delivery and leading to increased customer satisfaction.
151302 | Base | Cable Injection Project - (HAM) - Rymal - Mud - Upper Centennial - Upper Red Hill Valley | 0.54449 | 11132.21 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 8 failures, or 14 failures per 100km. This area includes the 331X & 341X feeders which were identified as a Worst Performing Feeder in 2018. The average cable installation year is 1989 in this project scope.
151314 | Base | Cable Injection Project - (G2) -Wanless - Kennedy - Bovaird - Main, Brampton | 0.21875 | 11045.83 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2013 to 2017 with average duration of 125 minutes.
151409 | Base | Cable Replacement Project- Central Parkway & Bloor (29), Mississauga | 10.8851 | 10937.44 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there are 9 outages, the length is 12,462 m, and the average cable age is 48 years old. There are 35 backlot transformers that we are also replacing.
150740 | Base | Facilities_Nebo_ Roof Replacement | 0.009 | 10932.65 | General Plant | Facilities Management | Horizon | 2019 Project and to be completed by Dec 2019. Not sure why we have $9K in 2022.
150665 | Base | Emerging Customer Initiated Work (West) | 1.6369 | 10905.1 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
101562 | Base | Arc Flash Mitigation Projects | 0.044349 | 10618.95 | System Service | Safety & Security | Powerstream | This project is to mitigate arc flash risk at East stations.
151299 | Base | Cable Replacement Project - (HAM) - Millen - Barton - Fruitland | 1.6195 | 10341.62 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 16 failures, or 44 failures per 100km. The average cable installation year is 1970 in this project scope.
150653 | Base | Road Authority West (St. Catharines) | 0.95816 | 10216.94 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
150615 | Base | Metering Tools & Equipment - Central North | 0.038744 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150616 | Base | Metering Tools & Equipment - Central South | 0.038744 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150613 | Base | Metering Tools & Equipment - East | 0.038744 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150614 | Base | Metering Tools & Equipment - West | 0.038744 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
102263 | M-Factor | Work Force Management / Mobile Dispatch | 2.35 | 9761.78 | General Plant | Information Technology | Multiple | Enterprise wide field crew management system that will enable more efficient use of crews and improve visibility to job progress enabling better communication of expectations to customers
151456 | M-Factor | Cable Injection Project - (V50) - Hwy 7 - Kipling - Steeles - Hwy 27, Vaughan | 0.37819 | 9187.5 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 3 failures in 2018.
151063 | Base | Pole Renewal - Central South | 3.5139 | 9065.1 | System Renewal | Overhead Asset Renewal | Enersource | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
100886 | Base | Distribution Automation - East | 1.3615 | 9041.12 | System Service | SCADA and Automation | Powerstream | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151275 | Base | Cable Injection Project - (SCH) - QEW - Highway 406 - Martindale Road | 0.78127 | 8905.36 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 3 failures, or 11 failures per 100km. The average cable installation year is 1988 in this project scope.
151298 | Base | Cable Injection Project - (HAM) - Govenors - Old Ancaster | 0.44177 | 8842.48 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 3 failures, or 10 failures per 100km. The average cable installation year is 1989 in this project scope.
101804 | Base | Purchase of Major Tools | 0.36116 | 8158.3 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
151390 | Base | 2022 GUELPH - Remotely Controlled Switches | 0.4099 | 8051.64 | System Service | SCADA and Automation | Guelph | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151213 | Base | Installation of Transformer Bushing Monitoring | 0.09 | 8001.2 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of installation of Transformer bushing monitoring system in Guelph. bushing monitoring unit provides real time condition monitoring of the transformer bushings.
151313 | Base | Cable Injection Project - (F5) - Steeles - Main - Hwy 407 - McLaughlin, Brampton | 0.21875 | 7751.39 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 5 outages due to cable failures from 2007 to 2016 with average duration of 80 minutes.
151352 | Base | Cable Injection Project - (M38) - Hwy 7 - Warden - 14th - Woodbine, Markham | 0.96869 | 7548.01 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 18 failures.
150282 | Base | Switchgear Renewal - Central North | 0.49461 | 7521.14 | System Renewal | Underground Asset Renewal | Brampton | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150508 | Base | Installation of Transformer Bushing Monitoring on MS txmrs-Multi Year -CENTRAL | 0.16939 | 7508.89 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Transformer bushing monitoring system in Central South. bushing monitoring unit provides real time condition monitoring of the transformer bushings.
151407 | Base | Cable Replacement Project- Glen Erin & Burnhamthorpe (12), Mississauga | 7.3358 | 7413.63 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 10 outages, the length is 22,109 m, and the average cable age is 34 years old.
151325 | Base | Cable Replacement Project - (M31) - 14th - Old Kennedy - Steeles - Warden, Markham | 3.5 | 7411.62 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 38 failures.
151457 | M-Factor | Cable Injection Project - (V25) - Major Mackenzie - Keele - Rutherford - Jane, Vaughan | 0.8749 | 7409.58 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 2 failures. From 2015-2019 YTD customers in this area experienced 3 failures.
151339 | Base | Cable Replacement Project - (BA19) - Letitia - Anne - Edgehill - Ferndale, Barrie | 7.3499 | 7397.06 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 2 failures in 2018.
151316 | Base | Cable Injection Project - (H2) - Wanless - Heart Lake - Bovaird - Kennedy, Brampton | 0.21875 | 7371.2 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2009 to 2017 with average duration of 107 minutes.
150284 | Base | Pole Renewal - Central North | 2.793 | 7304.65 | System Renewal | Overhead Asset Renewal | Brampton | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
102017 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-North & TS | 0.33036 | 7275.34 | System Service | Safety & Security | Powerstream | This project consists of Sorbweb Oil containment system in East. Protects the environment in the event of a transformer tank rupture
151351 | Base | Cable Injection Project - (M32) - Hwy 7 - Main - 14th - Warden, Markham | 0.89983 | 6971.35 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 17 failures.
150714 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - Central | 0.075697 | 6819.25 | System Renewal | Substation Renewal | Enersource | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central South Operating Area (former Enersource). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150713 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.075697 | 6819.25 | System Renewal | Substation Renewal | Brampton | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central North Operating Area (Brampton). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150715 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - West | 0.075697 | 6819.25 | System Renewal | Substation Renewal | Horizon | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the West Operating Area (former Horizon). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150644 | Base | Road Authority West (Hamilton) | 1.7199 | 6689.48 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
150507 | Base | 230kV TS Transformer Primary Bushing Monitoring Enablement-BPD Elimination - 4 TS Transformers-Multi-year initiative-TS | 0.50099 | 6521.07 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to install primary bushing monitoring at TS in EAST
150352 | Base | Voltage Conversion - Central MS, Hamilton | 1.8425 | 6498.05 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 23 outages and had 1,060,300 customer minutes of interruption (75 mins per customer per year). The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail. Specifically Central MS is the only station remaining in service with oil breakers which are functionally obsolete with no spare parts readily available.
151310 | Base | Cable Injection Project - (E4) - Queen - McLaughlin - Steeles - Chinguacousy, Brampton | 0.21875 | 6421.34 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2008 to 2016 with average duration of 104 minutes.
151044 | Base | Switch Renewal - Central South | 0.2756 | 6318.96 | System Renewal | Overhead Asset Renewal | Enersource | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
103659 | Base | Storm Hardening - Four-Circuit Poles | 1.968 | 6254.52 | System Renewal | Overhead Asset Renewal | Powerstream
150514 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear Initiative-WEST | 0.34254 | 6213.41 | System Service | Safety & Security | Horizon | This project consists of Sorbweb Oil containment system in West. Protects the environment in the event of a transformer tank rupture
151336 | Base | Cable Replacement Project - (BA22) - Sunnidale and Anne, Barrie | 1.4826 | 6208.17 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 2 failures in 2019.
151086 | Base | Insulator Replacements | 0.085272 | 5948.6 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
102128 | M-Factor | Aurora MS6 Expansion | 1.1231 | 5909.69 | System Service | Capacity (Lines) | Powerstream | 2C land is currently supplied by a 13.8kV feeder 5F2. It had a peak of 269A in 2018 and does not have sufficient capacity to supply future growth in the 2C lands. New feeder capacity is required to supply the additional load.
150351 | M-Factor | Voltage Conversion - Aberdeen MS, Hamilton | 1.269 | 5674.67 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 16 outages and had 500,475 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
150337 | Base | Switch Renewal - West | 0.44462 | 5475.59 | System Renewal | Overhead Asset Renewal | Horizon | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
151055 | Base | Major Tools | 0.077 | 5431.72 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
150067 | Base | Basement Flood Risk Mitigation - Markham TS#4 | 0.13095 | 5409.71 | System Renewal | Substation Renewal | Powerstream | This project involves mitigating the flood risk at the Markham TS#4 where there is equipment installed in the basement by relocating or repositioning this equipment. This critical equipment includes DC system, AC and DC panels, feeder switches, UPS, ATS located in the basement of this station. Damage to this equipment due to flooding would cause extensive power interruptions to many customers.
150598 | Base | Suite Metering - Renewals & Retrofits - PowerStream RZ | 0.36032 | 5394.14 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering equipment in existing buildings upgraded from bulk metering.
150515 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-CENTRAL | 0.34254 | 5352.14 | System Service | Safety & Security | Enersource | This project consists of Sorbweb Oil containment system in Central South. Protects the environment in the event of a transformer tank rupture
150516 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-EAST | 0.34254 | 5352.14 | System Service | Safety & Security | Brampton | This project consists of Sorbweb Oil containment system in Central North. Protects the environment in the event of a transformer tank rupture
150336 | Base | Transformer Renewal - West | 0.67823 | 5293.52 | System Renewal | Transformer Renewal | Horizon | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150750 | Base | Lines Central-North - Major Tools | 0.095223 | 5234.11 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150009 | Base | Insulator Renewal - East | 0.23334 | 5107.82 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
100909 | M-Factor | Rebuild 27.6 kV pole line for 4 Ccts on Warden Ave from Major Mack to Elgin Mills | 2.1805 | 4927.44 | System Service | Capacity (Lines) | Powerstream | This project is the third part of a multiple year project of rerouting two feeders 12M10/12M11 to Markham Future Urban Area. This project provide 40 MVA capacity.
151203 | Base | Capital Corrective Equipment Replacement - Stations South West | 0.06 | 4921.2 | System Renewal | Substation Renewal | Guelph | This project is intended to provide capital for all unplanned station equipment replacements in the South West Operating Area (Guelph) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
102042 | Base | Purchase and Installation of Animal Guards at Various Stations-Annual Multi-year initiative-North & TS | 0.016279 | 4893.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of animal guard installation in East
150716 | M-Factor | New build - 42M69 Feeder Extension Williams Pkwy - Main St to Kennedy Rd, Brampton | 1.1277 | 4865.64 | System Service | Capacity (Lines) | Brampton | 27.6kV UG Feeder Extension along Williams Pkwy from Main St to Kennedy Rd OH to meet contingency conditions
151464 | M-Factor | Cable Injection Project - (F3-G3-H3) - Phase 2, Brampton | 0.37968 | 4696.76 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 103 failures. Exact number of failures in recent years is unknown at this moment.
151083 | Base | Switchgear Renewal - West | 0.43062 | 4683.89 | System Renewal | Underground Asset Renewal | Horizon | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151010 | Base | Switch Renewal - Central North | 0.65985 | 4603.75 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
150720 | Base | Lines Central-South - Major Tools | 0.22405 | 4591.27 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
151021 | Base | Insulator Renewal - Central North | 0.3755 | 4235.99 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of non-polymer insulators (Areas are prioritiezed by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
150674 | Base | Emerging Customer Initiated Work Central (Brampton) | 0.16168 | 4183.83 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101763 | Base | Unforeseen Projects Initiated by the customer PS North | 0.12676 | 4161.34 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150679 | M-Factor | Alectra Drive for the Workplace | 0.16346 | 3997.47 | System Service | Capacity (Lines) | Multiple | Alectra Drive for the Workplace will demonstrate the value of integrating smart electric vehicle (EV) charging system at workplaces into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. The planned investment will help manage the flow of electricity needed to serve the building and EV charging stations, so that electricity costs are minimized for commercial customers while EV drivers have an easy and accessible charging solution.
150320 | M-Factor | Voltage Conversion - Dewitt MS , Hamilton | 0.49349 | 3972.49 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 12 outages and had 888,434 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
150358 | M-Factor | New build - QEW Dixie West New OH Circuits, Mississauga | 1.0659 | 3906.72 | System Service | Capacity (Lines) | Enersource | This project is an to added betterment coordinated with the MTO's QEW Expansion along Dixie West OH.
150466 | Base | Atomic Scheduler Upgrade - IT Infrastructure | 0.31347 | 3883.01 | General Plant | Information Technology | Multiple | Enhancement to Atomic application scheduler to support process improvement requirements. Atomic is the application scheduler in use at Alectra. This application will be used to support application and report scheduling for both CC&B and JDE. These enhancements are considered for the overall customer and organizational benefits.
150540 | Base | Implement application security - IT Infrastructure | 0.12953 | 3860.92 | General Plant | Information Technology | Multiple | Ongoing application security enhancements and additions to meet vendor requirements .
102075 | Base | Major repairs, refurbishment, or modifications to switches/switchgear | 0.10346 | 3702.48 | System Renewal | Underground Asset Renewal | Powerstream | Switchgear and Switches in stores that repair/refurbishment of the units can allow them to be returned to service
150376 | Base | New build - Hamilton South Mountain feeders capacity relief, Hamilton | 1.0573 | 3693.91 | System Service | Capacity (Lines) | Horizon | This project is build new feeder to alleviate capacity in South Hamilton and to alleviate on the four feeders which are over the planning limit
151319 | Base | Cable Injection Project - (I4) -Queen - Dixie - Steeles - Hwy 410, Brampton | 0.42787 | 3650.43 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 outage due to cable failures to date. Cables are 31 years old and will be at the injection eligibility threshold by the time of project execution in 2022.
151428 | Base | Cable Injection- 002- AREA 30- Eglinton Ave W & Miss Rd, Mississauga | 0.57547 | 3632.2 | System Renewal | Underground Asset Renewal | Enersource | There are 2 outages, we are injecting a total of 14,541 m of cable for this project, and the average age of the cable is 31 years.
151276 | Base | Cable Injection Project - (SCH) - Vansickle | 0.73247 | 3555.68 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 11 failures per 100km. The average cable installation year is 1990 in this project scope.
151200 | M-Factor | Alectra Single Platform Website ongoing | 0.1107 | 3548.17 | General Plant | Information Technology | Multiple | Ongoing enhancements to the Alectra platform to improve functionality for customers
150498 | Base | Capital Corrective Equipment Replacement - Stations Central South | 0.27652 | 3534.76 | System Renewal | Substation Renewal | Enersource | This project is intended to provide capital for all unplanned station equipment replacements in the Central South Operating Area (former Enersource) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150499 | Base | Capital Corrective Equipment Replacement - Stations Central North | 0.27652 | 3534.76 | System Renewal | Substation Renewal | Brampton | This project is intended to provide capital for all unplanned station equipment replacements in the Central North Operating Area (Brampton) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150497 | Base | Capital Corrective Equipment Replacement - Stations West | 0.27652 | 3534.76 | System Renewal | Substation Renewal | Horizon | This project is intended to provide capital for all unplanned station equipment replacements in the West Operating Area (former Horizon) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150047 | M-Factor | Rear Lot Renewal Project - Royal Orchard - North | 1.1307 | 3478.27 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 3 failures per year lasting 4 hours per year based on 3 year average.
151462 | M-Factor | Cable Injection Project - (G1) - Hwy 410 - Kennedy - Wanless - Main, Brampton | 0.24276 | 3437.98 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 2 failures. Exact number of failures in recent years is unknown at this moment.
150774 | Base | Lines Central-North - Site Restorations | 0.10766 | 3434.48 | System Renewal | Overhead Asset Renewal | Brampton
150721 | Base | Lines Central-South - Site Restorations | 0.10766 | 3434.48 | System Renewal | Underground Asset Renewal | Enersource
150523 | Base | Security Additions & Enhancements | 0.24602 | 3395.44 | General Plant | Information Technology | Multiple | As per Alectra Security roadmap to key IT systems.
150672 | Base | Burden Allocation - System Service | 0.10998 | 3353.13 | System Service | Capacity (Lines) | Horizon
150263 | Base | Cable Replacement Project - East Left Behind Cable | 1.5672 | 3237.07 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in these areas have experienced 11 failures.
102065 | Base | Capital Corrective Equipment Replacement - East | 0.34293 | 3161.46 | System Renewal | Substation Renewal | Powerstream | This project is intended to provide capital for all unplanned station equipment replacements in the East Operating Area (former PowerStream area) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150611 | Base | Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.16889 | 3116.96 | System Renewal | Substation Renewal | Powerstream | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the East Operating Area (former PowerStream). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150623 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-WEST | 0.0059255 | 3095.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of animal guard installation in West
150622 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-CENTRAL | 0.0059255 | 3093.04 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Animal guard at Central South Stations
150621 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-EAST | 0.0083347 | 3081.51 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Animal guard at East Stations
101036 | M-Factor | Install a new 4 ccts CNR yard overhead crossing on the south side of Hwy 7 | 1.3574 | 2919.48 | System Service | Capacity (Lines) | Powerstream | This project is to increase supply capacity to Vaughan Metro Center and Vaughan Mills. It will also reduce outage impact in case of pole failure on the north side of Hwy 7 crossing CN yard.
151286 | Base | Cable Replacement Project - (H2) - Wanless - Heart Lake - Bovaird - Kennedy, Brampton | 1.6632 | 2867.55 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2011 to 2017 with an average duration of 126 minutes
101625 | Base | Cyber Security Audit & Upgrades | 0.07145 | 2865.1 | General Plant | Information Technology | Multiple | This project would fund various activities and countermeasures to improve the cyber security posture of the Operations' Network. This will be a mandate for compliance to Ontario Cyber Security framework. The counter measures include: - an annual audit of the cyber security countermeasures in place; - implementation of new technologies to seal identified compromises; - replacement of deployed cyber security equipment deemed end of life or not able to deliver an expected level of service.
150671 | Base | Burden Allocation - System Renewal | 1.792 | 2831.23 | System Renewal | Other System Renewal | Horizon
150401 | M-Factor | 136M6 Goreway TS Extensions | 0.9804 | 2821 | System Service | Capacity (Lines) | Brampton | This feeder will supply all future residential & small commercial loads around the Gore Rd., Ebenezer Rd. & Castlemore Rd. 136M6 will off load 136M4 on the south section of the area mentioned. 136M6 will off load and provide contingency for 136M4 on the south section of this area.
150632 | Base | AMI Gatekeeper Expansion - Brampton RZ | 0.029996 | 2820.22 | System Access | Metering | Brampton | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
151311 | Base | Cable Injection Project - (E5) - Steeles - Mclaughlin - Hwy 407 - Chinguacousy, Brampton | 0.2935 | 2784.8 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 2 outages due to cable failures in 2007 and 2012 with average duration of 70 minutes.
151394 | Base | 2022 GUELPH - Transite Underground Duct Replacement | 0.27713 | 2682.53 | System Renewal | Underground Asset Renewal | Guelph | Replacement of Duct Structure which contains asbestoes a known carcinogen and impacts worker safety.
150079 | M-Factor | Markham TS#1 T1/T2 "B" Overcurrent Protections and HMI Upgrade | 0.15919 | 2596.02 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade Markham TS#1 T1/T2 "B" Overcurrent Protections with fault recording ability and HMI Upgrade
151427 | Base | Cable Injection- 001- AREA 11- Truscott & Southdown, Mississauga | 1.3207 | 2550.48 | System Renewal | Underground Asset Renewal | Enersource | There are 2 outages, we are injecting a total of 21,576 m of cable for this project, and the average age of the cable is 32 years.
150332 | M-Factor | Non-Wires Alternative Pilot | 0.81936 | 2536.94 | System Service | Capacity (Stations) | Powerstream | The project will provide customers with increased flexibility to make decisions about their electricity consumption, generation, and costs; it leads to more efficient integration of DERs which yields greater benefits to customer, system reliability, and power quality. This project will also provide the opportunity to increase operational efficiency and improved asset management to enhance service to customer and defer and/or reduce infrastructure investment needs in York Region.
150580 | Base | West Region Tools and Test Equipment | 0.20691 | 2494.28 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
150627 | Base | Station Equipment Temperature Monitoring-EAST | 0.077354 | 2479.48 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of Station Temperature Monitoring system in Central North and it enables controlled emergency loading beyond the nameplate rating.
150629 | Base | Station Equipment Temperature Monitoring-WEST | 0.077354 | 2479.48 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of Station Temperature Monitoring system in West and it enables controlled emergency loading beyond the nameplate rating.
150095 | M-Factor | Vaughan TS#1 T1/T2 "B" Differential Protections Upgrade | 0.089941 | 2477.83 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the current T1/T2 ASEA solid state Transformer "B" Differential Protection relays at Vaughan TS#1 with new relays having fault recording capabilities
151202 | Base | Purchase of Major Station Tools - Multi-year | 0.01 | 2472.82 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
150625 | Base | Purchase of Major Tools - Muliti Year-CENTRAL | 0.022139 | 2395 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150624 | Base | Purchase of Major Tools - Muliti Year-EAST | 0.022139 | 2395 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150626 | Base | Purchase of Major Tools - Muliti Year-WEST | 0.022139 | 2395 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
151221 | Base | Metering - AMI Hardware Upgrade | 0.35 | 2384.22 | System Access | Metering | Guelph | Multi-year project to expand and upgrade AMI field communication equipment to service new connections, in Guelph RZ.
101761 | Base | Unforeseen Projects Initiated by the customer PS South | 0.4071 | 2365.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151435 | Base | Cable Injection- 010 - Area 56- Derry Rd W & Ninth Line, Mississauga | 1.193 | 2307.05 | System Renewal | Underground Asset Renewal | Enersource | There are 3 outages, we are injecting a total of 45,837 m of cable for this project, and the average age of the cable is 30 years.
151290 | Base | Cable Replacement Project - (I3) - Bovaird - Dixie - Queen - Hwy 410, Brampton | 0.7259 | 2280.06 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 8 outages due to cable failures from 2007 to 2018 with average duration of 133 minutes.
151244 | Base | Fault Indicators | 0.015 | 2243.02 | System Service | System Control, Comm'ns & Performance | Guelph | The scope of this project is to install Fault Indicators in Guelph. The project would include the fault indicators communicating to the existing SCADA and will improve the fault locating and improve SAIDI
151181 | Base | Cable Replacement Project - Left Behind Cable, Brampton | 0.525 | 2163.34 | System Renewal | Underground Asset Renewal | Brampton | This project is to address cables which were part of a cable injection project but were ultimately not injectable at the time of project execution. These 'left behind' segments must be addressed, if they are left in the system they could cause a failure. Customers would not only experience an outage, but question the utilities work practices as we would have addressed only a portion of the cables instead of all the cables which could cause an outage.
151070 | Base | Markham TS3 Firewall Upgrade | 0.23263 | 2148.93 | System Service | System Control, Comm'ns & Performance | Powerstream | Markham TS3 Firewall Upgrade
150321 | M-Factor | Voltage Conversion - Galbraith MS, Hamilton | 2.289 | 2139.96 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 4 outages and had 77,467 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
150675 | Base | Emerging Customer Inititated Work Central (Mississauga) | 0.17965 | 2049.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
101764 | Base | Road Authority Expenditure PS North | 1.5827 | 2038.3 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
150604 | Base | Smart Meter Network Expansion - PowerStream RZ | 0.21148 | 2035.93 | System Access | Metering | Powerstream | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
151092 | Base | Distribution Automation - Central South | 0.554 | 2013.5 | System Service | SCADA and Automation | Enersource | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151030 | Base | Addition of Sensors to SCADA Controllable 44kV LISs in Brampton | 0.26635 | 2012.97 | System Service | System Control, Comm'ns & Performance | Brampton | This project is to add sensors to the 44KV switches in Central North
150694 | M-Factor | Cityview microgrid enhancements | 0.01579 | 1985.17 | System Service | Capacity (Lines) | Powerstream | The project is to understand how microgrids can be integrated into the distribution grid in a safe and reliable manner. The microgrid is used to evaluate integration and connection to the distribution grid, while reducing the building's load, greenhouse gas emissions, and increasing its resiliency to grid outages.
102547 | M-Factor | Two Ccts on Birchmount Rd from ROW to 14th Ave | 1.5746 | 1969.46 | System Service | Capacity (Lines) | Powerstream | This project is to build 2 ccts pole line on Birchmount Rd from the Right of Way (ROW) to 14th Ave. This will extend 2 feeders 26M17 and 26M18 to 14th Ave to tie with feeder 22M7/22M8 for reliability
151324 | Base | Cable Injection Project - (M3) - Castlemore - Goreway - Queen - Airport, Brampton | 0.16294 | 1916.04 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 1 outage due to cable failure in 2008 with average duration of 61 minutes. The cables are 31 years old and will be at the injection eligibility threshold by the time of project execution in 2022.
151350 | Base | Cable Injection Project - (M22) - Major Machenzie - Hwy 48 - 16th - McCowan, Markham | 0.16481 | 1914.52 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 4 failures.
150670 | Base | SCADA FDIR | 0.1231 | 1798.98 | System Service | SCADA and Automation | Multiple | Fault Detection, Isolation, and Restoration implementation, next generation of distribution automation technology. This utilizes devices which are already automated and integrates them into the OMS system such that devices perform self healing after a fault. in some cases reducing the outage time to less then 1 minute.
151283 | Base | Cable Replacement Project - (HAM) - Mohawk | 0.80227 | 1740.19 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 1 failure, or 20 failures per 100km. This area includes the 2D2X feeder which was identified as a Worst Performing Feeder in 2018. The average cable installation year is 1953 in this project scope.
150680 | M-Factor | Alectra Drive at Home | 0.58969 | 1731.44 | System Service | Capacity (Lines) | Multiple | Alectra Drive at Home will demonstrate the value of integrating smart electric vehicle (EV) charging system in multi rise buildings as well as residential homes into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. It will also provide insight into the characteristics of EV Charging, how EVs can be aggregated and controlled to provide the benefit at the local, regional and provincial system levels, and customer response to these control and optimization strategies.
151201 | Base | Purchase of New Critical Spare Parts - Guelph | 0.01 | 1727.97 | System Renewal | Substation Renewal | Guelph | This project involves procurement of critical spare parts for stations in the South West Operating Area (Guelph) so as to facilitate prompt repair of failed assets during emergency situations.
151333 | Base | Cable Replacement Project - (BA9) - Little - Fairview - Harvie - Ferndale, Barrie | 1.8438 | 1717.62 | System Renewal | Underground Asset Renewal | Powerstream | From 2014-2018 customers in this area experienced 6 failures.
150619 | Base | Purchase of Critical Spare Parts - West | 0.022361 | 1648.51 | System Renewal | Substation Renewal | Horizon | This project involves procurement of critical spare parts for stations in the West Operating Area (former Horizon) so as to facilitate prompt repair of failed assets during emergency situations.
150844 | Base | Fleet_West_Vehicle Replacement_Bucket Truck 1-270 | 0.42 | 1636.32 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151136 | Base | C55 Alectra: Optimization of Business Practices | 0.1605 | 1624.9 | General Plant | Information Technology | Multiple | Optimizing the current software to communicate with other systems such as the ERP will allow for more efficient and effective budgeting processes and consolidation of information allowing for consistent reporting of the information from one system.
150885 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-361 | 0.435 | 1624.1 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150893 | Base | Fleet_West_Vehicle Replacement_ Digger Derrick 1-342 | 0.445 | 1615.96 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151436 | Base | Cable Injection-011 - Area 58 & 59- Winston Churchill & The Collegeway, Mississauga | 1.9105 | 1614.06 | System Renewal | Underground Asset Renewal | Enersource | There are 14 outages, we are injecting a total of 69,795 m of cable for this project, and the average age of the cable is 30 years.
151139 | M-Factor | Voltage Conversion - MS-12 Hansen Rd, Brampton | 3.0541 | 1599.32 | System Renewal | Overhead Asset Renewal | Brampton | From 2015-2017 customers in this area experienced 29 outages and had 94,267 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151386 | Base | Cable Replacement - (278) - 31 Greengate Rd Subdivision, Guelph | 0.58954 | 1596.1 | System Renewal | Underground Asset Renewal | Guelph
150642 | Base | Proactive Replacement of Remote Terminal Units - Central North | 0.16209 | 1582.3 | System Renewal | Substation Renewal | Brampton | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the Central-North Operating Area (Brampton). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
150617 | Base | Purchase of Critical Spare Parts - Central North | 0.029888 | 1568.76 | System Renewal | Substation Renewal | Brampton | This project involves procurement of critical spare parts for municipal stations in the Central North Operating Area (Brampton) so as to facilitate prompt repair of failed assets during emergency situations.
151353 | Base | Cable Injection Project - (V41) - Kirby - Weston - Teston - Pine Valley, Vaughan | 0.11365 | 1566.16 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 2 failures.
151309 | Base | Cable Injection Project - (E3) - Bovaird - McLaughlin - Queen - Chinguacousy, Brampton | 0.12087 | 1560.28 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 1 outage due to cable failure in 2015 with duration of 86 minutes.
151087 | Base | Switchgear Replacement | 0.24664 | 1559.43 | System Renewal | Underground Asset Renewal | Guelph | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150618 | Base | Purchase of Critical Spare Parts - Central South | 0.035423 | 1556.59 | System Renewal | Substation Renewal | Enersource | This project involves procurement of critical spare parts for stations in the Central South Operating Area (former Enersource) so as to facilitate prompt repair of failed assets during emergency situations.
151354 | Base | Cable Injection Project - (V52) - Rutherford - Kipling - Langstaff - Hwy 27, Vaughan | 0.13022 | 1552.67 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 2 failures.
102077 | Base | Major repair, refurbishment, or conversions of distribution transformers | 0.031036 | 1540.55 | System Renewal | Transformer Renewal | Powerstream | Transformers returned or in stores where repair/refurbishment of the unit can return it to service at a lower cost then purchase of a new unit
150883 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-374 | 0.42 | 1540.38 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151372 | Base | Cable Replacement - (451) - Country Club Dr Subdivision, Guelph | 0.381 | 1481.82 | System Renewal | Underground Asset Renewal | Guelph
150368 | M-Factor | New build - North Central feeders capacity (Carlton TS to Linwell Rd/Lake St) relief, St.Catharines | 1.0077 | 1480.62 | System Service | Capacity (Lines) | Horizon | This project is to alleviate capacity issues in the North and Central section of St.Catharines, primarily served by Carlton BY bus feeders which are over the planning limit.
151222 | Base | Concrete Structures | 0.19857 | 1469.44 | System Renewal | Underground Asset Renewal | Guelph | Replacement of lids on civil structures to avoid public risk
150763 | Base | Facilities_Reno_Addiscott - Service Centre Upgrades | 0.11092 | 1461.63 | General Plant | Facilities Management | Powerstream | Repairs to building envelop/walls to prevent further damage to the build infrastructure and systems that are supporting critical operational systems such as control rooms, server rooms, customer services groups, etc.
151408 | Base | Cable Replacement Project- Burnhamthorpe & Miss. Road (13), Mississauga | 2.4484 | 1429.36 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 11 outages, the length is 7,311 m, and the average cable age is 30 years old.
150334 | Base | Distribution Automation - West | 0.72 | 1424.45 | System Service | SCADA and Automation | Horizon | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151371 | Base | Cable Replacement - (87) - Marksam Rd/ Rhonda Rd Subdivision, Guelph | 0.35 | 1423.41 | System Renewal | Underground Asset Renewal | Guelph
150889 | Base | Fleet_West_Vehicle Replacement_ Digger Derrick 1-333 | 0.435 | 1415.07 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151052 | Base | Emerging Customer Initiated Work - Relocations | 0.095894 | 1412.11 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
150941 | Base | Unit # 300 Dump truck replacement | 0.13905 | 1399.77 | General Plant | Fleet Renewal | Powerstream
151410 | Base | Cable Replacement Project-Roselle & Priority Cres (2), Mississauga | 1.0307 | 1390.9 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 7 outages, the length is 3,006 m, and the average cable age is 43 years old.
150751 | Base | Facilities_East_Capital Replacement Investment Support | 0.52232 | 1374.32 | General Plant | Facilities Management | Powerstream | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
151288 | Base | Cable Replacement Project - (H4) - Queen - Hwy 410 - Steeles - Kennedy, Brampton | 0.5859 | 1353.9 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2009 to 2018 with average duration of 189 minutes.
150335 | Base | Pole Renewal - West | 2.7171 | 1338.4 | System Renewal | Overhead Asset Renewal | Horizon | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
102102 | Base | Enterprise File Synchronization and Sharing Platform | 0.025608 | 1307.59 | General Plant | Information Technology | Multiple | Alectra is looking for a secure Enterprise File Synchronization and Sharing solution that will increase productivity of internal and external teams by facilitating seamless collaboration of corporate data anywhere , anytime, and on any device without the restrictions of having to connect to the Alectra network. The overarching goal of this implementation will be to provide a balance between delivering business productivity and securing enterprise information.
150738 | Base | Facilities_West_Capital Replacement Investment Support | 0.2651 | 1289.1 | General Plant | Facilities Management | Horizon | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150790 | Base | Fleet_Central South Vehicle Replacement-Puller/Tensioner | 0.2 | 1264.62 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
102241 | Base | Proactive Replacement of Remote Terminal Units - East | 0.10274 | 1239.66 | System Renewal | Substation Renewal | Powerstream | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the East Operating Area (former PowerStream). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
150422 | M-Factor | 136M9 Feeder Extension Castlemore Rd, Goreway Dr to McVean Dr | 0.13341 | 1232.89 | System Service | Capacity (Lines) | Brampton | This project provides 136M9 capacity along Castlemore Dr from Goreway Dr to McVean Dr., and McVean will bring greenfield capacity up to Mayfield Rd to service north east Brampton. 136M9 in future will connect to and provide offloading and contingency for 136M8 and 136M42 which are at approching planning limit.
150877 | Base | Fleet_ Central North Vehicle Replacement S/Bucket 7109 | 0.47 | 1222.49 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151064 | Base | Secondary Pedestals -St. Catharines | 0.20343 | 1153.93 | System Service | Safety & Security | Horizon | This project involves the replacment of above grade steel secondary pedestals which pose a safety risk to the general public
151312 | Base | Cable Injection Project - (F2) - Wanless - Main - Bovaird - McLaughlin, Brampton | 0.044625 | 1139.85 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 cable failure to date. Cables will be at the injection eligibility threshold by the time of project execution in 2022.
101125 | Base | Lines Mobile Equipment - IT/OT Infrastructure | 0.080695 | 1119.08 | General Plant | Information Technology | Multiple | This budget covers the deployment of mobile technology - laptops/field tablets and accessories - within the Lines Department to gain efficiencies in field operations. By deploying this technology, the Lines area can move away from a paper-based to a more electronic environment. In future, it is envisioned that, for example, mobile applications will facilitate the electonic transmission of work orders and electronic record keeping (asset tracking, tailboards, switching orders, timesheets). This will allow for streamlined operational processes and record-keeping, thereby supporting corporate technological initiatives such as the GIS, Outage Management System, and future Workforce Management system. At present, all Lines Management personnel and Subforemen have laptops, facilitating activities such as viewing of the GIS, electronic Asset Tracking Forms, and use of OMS Responder Mobile. Expenditures in this area will allow for more deployment of field devices among Lines crews and for the implementation of more computerized processes.
150500 | Base | On-Line Dissolved Gas Oil Monitoring of 10 MS Transformers - WEST | 0.106 | 1116.55 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of Transformer bushing monitoring system in West
150570 | Base | Alectra West Substation Ground Grid Installations | 0.29858 | 1091.19 | System Service | Safety & Security | Horizon | This project is to install ground grid at East Stations
151204 | Base | Upgrade to Station Facilities (Buildings/Civil work) Multi-year | 0.01 | 1089.29 | General Plant | Facilities Management | Guelph | This project involves work involving structural components of stations, including windows, brickwork, roofs, foundations, drainage, doors, etc. at stations in the SouthWest Operational Area. Not keeping up with this work would result in advanced deterioration resulting in even greater maintenance costs, potential safety concerns and potential failure of the electrical equipment in the building causing power interruptions.
103198 | Base | BizTalk Upgrade - IT Infrastructure | 0.27416 | 1085.47 | General Plant | Information Technology | Multiple | Upgrade existing BizTalk to latest version. We currently have a development, test, and Production environment.
150794 | Base | Fleet_Central South Vehicle Replacement- 229-09 S/Bucket | 0.49 | 1070.69 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151041 | Base | Protection Logic Upgrades - East MSs (North) | 0.084705 | 1061.11 | System Service | System Control, Comm'ns & Performance | Powerstream
150758 | M-Factor | Facilities_Reno_Staff Relocation from Jane St | 0.55459 | 1060.04 | General Plant | Facilities Management | Brampton | Required renovations to the Cityview building to accommodate employees from various Alectra groups currently at Jane St, reducing the need to continue the office space lease at Jane St. The Jane St office lease expires in 2021 and would not be renewed, reducing operating expenditures.
150578 | Base | Alectra - Microsoft Software | 0.10345 | 1020.9 | General Plant | Information Technology | Multiple | Compliance for Alectra employees for Microsoft application suite of products to perform daily operation .
150937 | Base | Fleet_West_Vehicle Replacement_Cargo/Passenger Vans. | 0.039 | 995.47 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150392 | Base | Storage Upgrade | 1.2885 | 994.99 | General Plant | Information Technology | Multiple | Upgrade on premise Enterprise Storage platform in addition to increased capacity requirements as a result of employee and customer demand for data retention. Off Premise storage costs (SharePoint Online, One Drive, Development, test and production environments)
151091 | Base | Switchgear Renewal - Central South | 3.7679 | 982.44 | System Renewal | Underground Asset Renewal | Enersource | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151159 | Base | Fault Indicator Installation and Replacement - Hamilton and St. Catharines | 0.27979 | 966.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of fault indicator installation in West
150628 | Base | Station Equipment Temperature Monitoring-CENTRAL | 0.078244 | 965.25 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of Station Temperature Monitoring system in Central South and this enables controlled emergency loading beyond the nameplate rating.
151065 | Base | Manhole Lid Replacement | 0.35606 | 925.3 | System Renewal | Underground Asset Renewal | Horizon | Replacement of lids on civil structures to avoid public risk
151156 | Base | Fleet_West_Vehicle Replacement_Step Vans | 0.38 | 913.53 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150932 | Base | Fleet East Vehicle replacement - SUV | 0.19133 | 905.06 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150781 | Base | Fleet_Central South Replacement-Tractor 301-08 | 0.2 | 893.48 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150317 | M-Factor | Voltage Conversion - Deerhurst MS, Hamilton | 2.249 | 869.07 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 6 outages and had 121,838 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
150974 | Base | Fleet East Vehicle replacement - Forklift | 0.16 | 862.99 | General Plant | Fleet Renewal | Powerstream | Asset replacement due to poor conditions and age and lack of parts replacement. Equipment not as available to support capital system renewal projects and respond to emergencies with material handling. .
150943 | Base | Fleet East Vehicle replacement - Extended Van | 0.25921 | 849.79 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150904 | Base | Fleet East Yearly Light and Misc equipment | 0.055658 | 846.86 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150935 | Base | Fleet East Vehicle replacement - Pickup truck 1500 | 0.15756 | 846.65 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150262 | M-Factor | Cable Replacement Project - (M33) - 16th Avenue and Village Parkway, Markham | 2.0987 | 834.98 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 1 failure. From 2015-2019 YTD customers in this area experienced 3 failures. Cable is 42 years old.
150909 | Base | Fleet East Unit # 115 Single bucket truck replacement | 0.4 | 834.56 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151163 | Base | Fleet_West_Vehicle Replacement_ Passenger Van_1-370 | 0.039 | 807.37 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150746 | Base | Facilities_Central_Capital Replacement Investment Support | 0.38361 | 807.27 | General Plant | Facilities Management | Multiple | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150913 | Base | Fleet East Vehicle replacement - Cube Vans | 0.78286 | 806.41 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150946 | Base | Fleet East Vehicle replacement - Van pool vans | 0.13113 | 782.26 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150805 | Base | Fleet_Central South Vehicle Replacement-206-09 S/bucket | 0.49 | 781.51 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150939 | Base | Fleet East Unit # 105 Bucket truck replacement | 0.21115 | 781.04 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
101622 | Base | DACS Inverters and RTU's removal - East | 0.054178 | 765.32 | System Renewal | Substation Renewal | Powerstream | This project involves removal of obsolete and out-of-service DACs inverters, RTUs and associated wiring at stations in the East Operating Area (former PowerStream) so as to remove clutter, thus simplifying future work and freeing up space for future station upgrades.
150971 | Base | Fleet East Vehicle replacement - Pickup truck 2500 | 0.18055 | 742.02 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
101632 | Base | Obsolete Revenue Metering Removal from TSs | 0.055667 | 739.84 | System Service | Safety & Security | Powerstream | Evolution of the distribution system to permit more efficient integration of DERs to yield 18
150799 | Base | Fleet_Central South Vehicle Replacement- Reel Carrier | 0.29 | 716.12 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151082 | Base | SCADA Infrastructure | 0.14914 | 688.19 | System Service | System Control, Comm'ns & Performance | Guelph
151058 | Base | Distribution Transformer Replacements & Upgrades | 0.35642 | 682.68 | System Renewal | Transformer Renewal | Guelph | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150669 | Base | Burden Allocation - System Access | 0.65278 | 669.62 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150377 | M-Factor | Voltage Conversion and Rear Lot - Montgomery Dr, Hamilton | 1.8248 | 661.01 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 71 outages and had 7,403,242 minutes of interruption. This project also addresses rear lot assets which are extrememly difficult to replace if they fail due to complexities of access issues and restricitions for equipment to rebuild the assets.
150966 | Base | Fleet East Unit # 124 83' Double Bucket | 0.63555 | 651.33 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
102166 | Base | SQL Expansion - IT Infrastructure | 0.062073 | 635.85 | General Plant | Information Technology | Multiple | Expand existing SQL infrastructure to meet project demands and natural growth of database. Add system capacity, improve performance, and reduce the risk of downtime due resource constraints.
150933 | Base | Fleet_ Central North Vehicle Replacement Stake Trucks | 0.27 | 615.92 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150203 | Base | Station Equipment Temperature Monitoring-NORTH & TS | 0.064777 | 614.42 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of Station Temperature Monitoring system in East and it enables controlled emergency loading beyond the nameplate rating.
150880 | Base | Fleet_ Central North Vehicle Replacement Tractor 7708 | 0.2 | 592.75 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150496 | Base | iPass Project Management – Planned Capital - West | 0.70328 | 589.28 | System Renewal | Underground Asset Renewal | Horizon | Help in optimizing DER performance and efficiency to improve addressing overall energy needs.
102046 | Base | Purchase of Major Tools - Muliti Year-North & TS | 0.046493 | 565.1 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
151206 | Base | Installation of SWI Video Security System | 0.01 | 544.35 | System Service | Safety & Security | Guelph | This project consists of installation of SWI Video security system in SouthWest. The implementation of video monitoring will ensure that station security and safety related issues can be easily identified and addressed immediately
150905 | Base | Fleet East Multi Year Shop tools | 0.011366 | 544.12 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of tools and shop equipment required to repair and maintain vehicles to ensure vehicle availability to support capital systems projects.
101816 | Base | Alectra East (South), Fault Indicator Installation and Replacement Multi-year initiative | 0.24937 | 542.12 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - North Region which will result improved outage response, operational efficiency, and reliability
151085 | M-Factor | Rear Lot Conversions | 0.11843 | 530.82 | System Renewal | Rear Lot Conversion | Guelph
101134 | Base | Alectra East (North), Fault Indicator Installation and Replacement Multi-year initiative | 0.25167 | 527.43 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - South Region which will result improved outage response, operational efficiency, and reliability
150437 | Base | OT GIS & OMS Enhancements | 0.33467 | 519.79 | General Plant | Information Technology | Multiple | Ongoing productivity enhancements to core GIS and OMS platforms to meet internal and customer demand for functionality.
150602 | Base | Smart Meter Test Facility - PowerStream RZ | 0.020357 | 471.4 | System Access | Metering | Powerstream | Multi-year project to expand the capability of the Meter Test Facility to test increasing types of meters and AMI systems before they are placed into production.
150811 | M-Factor | Fleet_Central South Vehicle Replacement-Pick ups | 0.156 | 433.74 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
102027 | Base | Purchase of Critical Spare Parts - Multiyear - East | 0.072229 | 427.82 | System Renewal | Substation Renewal | Powerstream | This project involves procurement of critical spare parts for transformer and municipal stations in the East Operating Area (former PowerStream) so as to facilitate prompt repair of failed assets during emergency situations.
150576 | M-Factor | Split the 1/0 loop on Cityview Blvd into two loops | 0.4529 | 422.68 | System Service | Capacity (Lines) | Powerstream | This project is to split the 1/0 loop on Cityview Blvd into two loops. As of 2019, there is 18.5MVA connected kVA on the loop: 12MVA on the residential side and 6.5 MVA on the commercial side with 1865 residential and 93 commerical customers.
150494 | Base | iPass Project Management – Planned Capital - Central-North | 0.39204 | 408.86 | System Renewal | Overhead Asset Renewal | Brampton | Predicting the influence of weather conditions and DER contribution simultaneously on the power grid, for proactively mitigating local outages,
150495 | Base | iPass Project Management – Planned Capital - Central-South | 0.39204 | 408.86 | System Renewal | Overhead Asset Renewal | Enersource | Enable better visibility towards preventive equipment maintenance needs arising due to DER penetration which will further help mitigate outage risks,
101781 | Base | iPass Project Management – Planned Capital - East | 0.39851 | 408.86 | System Renewal | Overhead Asset Renewal | Powerstream | Estimating the effects of DER contribution at the feeder and region levels to further optimize the energy flows between the Utility and its consumers,
150607 | M-Factor | Station LED Lighting Upgrades - Central | 0.027335 | 407.91 | System Renewal | Substation Renewal | Enersource | Replacement of inefficient lighting fixtures and lamps at stations in the Central Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150606 | M-Factor | Station LED Lighting Upgrades - EAST | 0.027335 | 407.91 | System Renewal | Substation Renewal | Brampton | Replacement of inefficient lighting fixtures and lamps at stations in this Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
102034 | Base | Upgrade to Station Facilities (Building / Civil work) Multi-year - East | 0.1358 | 339.91 | System Renewal | Substation Renewal | Powerstream | MULTI ANSWER
150797 | M-Factor | Fleet_Central South Vehicle Replacement- SUV | 0.102 | 325.75 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150610 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - Central | 0.02141 | 289.6 | System Renewal | Substation Renewal | Enersource | Existing driveways at stations in the Central Operational Area that are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150609 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - East | 0.02141 | 289.6 | System Renewal | Substation Renewal | Brampton | Existing driveways in this Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150612 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - West | 0.02141 | 289.6 | System Renewal | Substation Renewal | Horizon | Existing driveways in the West Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150796 | M-Factor | Fleet_Central South Vehicle Replacement- Vans | 0.216 | 285.52 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150551 | Base | ServiceNow Expansion - IT Infrastructure | 0.059486 | 279.25 | General Plant | Information Technology | Multiple | Building and adding features within ServiceNow we will eliminate outdated processes by automating more tasks and decisions allowing us to be more efficient and productive. Enhancements include the automation of the flow of data between other systems and across programs used by various departments and ServiceNow. Servicebots will be used as ServiceNow learns from past patterns, in order to predict future outcomes, including determining risks, assigning owners, and categorizing work. Learned models set the category of the IT request and assign the task to the right team, as well as calculate associated risk of action or inaction. This capability will improve the speed and efficiency of IT service delivery.
102050 | Base | Various Stations-Station Lighting Upgrade/Retrofit-Energy Efficiency Lighting-initiative Multi-year - East | 0.056432 | 239.8 | System Renewal | Substation Renewal | Powerstream | Replacement of inefficient indoor and outdoor lighting fixtures and lamps at stations in the East Operating Area (former PowerStream) will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150897 | M-Factor | Fleet_ Central North Vehicle Replacement pick ups | 0.054 | 234.38 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150888 | M-Factor | Fleet_ Central North Vehicle Replacement SUVs | 0.0355 | 223.15 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150891 | M-Factor | Fleet_ Central North Vehicle Replacement Car | 0.0355 | 207.64 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150825 | Base | Line & Transformer Protection Migration to DNP - Jim Yarrow TS | 0.10439 | 164.32 | System Renewal | Substation Renewal | Brampton | This is part of a multi-phase project to upgrade aging and failure-prone protection systems at Jim Yarrow TS to the current protection standards. Proper protection to transmission lines will provide protection to the assets in the case of faults.
151382 | Base | 2022 GUELPH - Fleet | 0.6 | 151.48 | General Plant | Fleet Renewal | Guelph | Replacement of end of life asset due to poor conditions, high mileage and engine hours and age. Vehicle experiencing more down time at the shop for repairs and maintenance impacting vehicle availability.
103030 | Base | Technology Upgrades Improving the System Control Room Environment | 0.056483 | 147.52 | General Plant | Information Technology | Multiple | This project will continue to build on the original capital project whose scope was focused on the replacement of computers used as Operator WorkStations. The scope of this program has been expanded to account for all technology purchases required for the Control Room theater.
151108 | Base | Office Equipment | 0.074107 | 143.52 | General Plant | Facilities Management | Guelph | Replace aging equipment within the Guelph operational centre to ensure optimal performance in managing the distribution assets
150586 | Base | OT SCADA map cleanup | 0.25864 | 136.57 | General Plant | Information Technology | Multiple | SCADA Map clean up program to ensure accuracy and safety in the SCADA environment.
151245 | M-Factor | Capacitor Bank Installations | 0.030841 | 134.68 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of capacitor bank installation to increase power factor, capacity and reduce losses.
102931 | Base | Paving of 3 MS & TS Station Driveways per year - Annual Multi-year initiative - East | 0.049079 | 125.42 | System Renewal | Substation Renewal | Powerstream | Existing driveways at stations in the East Operating Area (former PowerStream) are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150597 | Base | Lock Box Installs - East | 0.0099352 | 115.84 | System Access | Metering | Powerstream | Multi-year project to install lock boxes at ICI properties with restricted access to eliminate need for a customer appointment for access.
150569 | Base | Server OS Upgrades - IT Infrastructure | 0.081246 | 95.22 | General Plant | Information Technology | Multiple | Operating system upgrades to support IT infrastructure.
150737 | Base | Facilities_East Region_Reactive Capital | 0.26914 | 91.88 | General Plant | Facilities Management | Powerstream | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150736 | Base | Facilities_West Region_Reactive Capital | 0.26914 | 91.88 | General Plant | Facilities Management | Horizon | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150734 | Base | Facilities_Central Region_Reactive Capital | 0.26928 | 91.85 | General Plant | Facilities Management | Multiple | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150676 | Base | Mobile Devices - IT Infrastructure | 0.010345 | 88.32 | General Plant | Information Technology | Multiple
103171 | Base | Implementation of a new Alectra Network Operations Voice Radio System | 0.025 | 79 | General Plant | Information Technology | Multiple
150564 | Base | OT SCADA hardware upgrade cycle 4 | 0.20691 | 75.49 | General Plant | Information Technology | Multiple | Planned hardware updrades for monitors and workstations on enterprise SCADA platform.
151016 | M-Factor | Fleet_West_Vehicle_Replacement_Pickups | 0.11 | 55.85 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150747 | M-Factor | Net Zero Energy Emissions | 0.32795 | 34.58 | System Service | Distributed Energy Resources (DER) | Powerstream | The project will help Alectra Utilities to ensure that growing DER challenges are met through building expertise and capability in real time monitoring, integrating and optimizing of DERs in line with customer preferences. This will lead to a system that can safely integrate and optimize value from DERs for the benefit of customers.
151053 | Base | Building Sustainment | 0.18689 | 31.98 | General Plant | Facilities Management | Guelph | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150584 | Base | OT Control room hardware upgrade cycle | 0.32588 | 26.59 | General Plant | Information Technology | Multiple | Planned hardware updrades for monitors and workstations on enterprise control room platforms. .
151084 | Base | Shop equipment refurbishment and replacement | 0.025 | 22.69 | General Plant | Fleet Renewal | Brampton
151031 | Base | Fleet Shop equipment refurbishment and replacement | 0.058 | 12.85 | General Plant | Fleet Renewal | Enersource | For the refurbishment of trailers, shop compressors and hoists to extend the life of the assets instead of replacement to reduce the need fro capital expenditures.
150678 | Base | P&C Specific Tools & Testing Equipment - West | 0.016604 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
102999 | Base | P&C Specific Tools and Testing Equipment | 0.016604 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
102157 | Base | Server Refresh - IT Infrastructure | 1.2465 | 10.1 | General Plant | Information Technology | Multiple | Ongoing server refresh to support applications.
150396 | Base | Network Refresh - IT Infrastructure | 0.36823 | 9.81 | General Plant | Information Technology | Multiple | Replacement of existing network infrastructure that is unsupported (or soon to be) including further rationalization and design modifications to support the delivery of services throughout the Alectra Environment.

## 2023 Ranking
Project List for Oral Hearing Undertakings
Project Number | Funding | Project Name | 2023 ($MM) | Project Score | Investment Category | Investment Grouping | Rate Zone | Comment
150725 | Base | Lines Central-North - Reactive Renewal | 1.2739 | 181453.58 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have failured and requires replacement in order to restore power to customers
150690 | Base | Lines Central-South - Reactive Renewal | 3.2649 | 171817.68 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have failured and requires replacement in order to restore power to customers
150682 | Base | Remote Fault Indicator Deployment | 0.45375 | 164220.93 | System Service | System Control, Comm'ns & Performance | Multiple | This project consists of remote fault indictor deployment which will result improved outage response, operational efficiency, and reliability
102247 | Base | Interest Capitalization | 1.2263 | 104303.71 | General Plant | Other General Plant | Powerstream
150596 | Base | Meter Renewal - all types but Suite - PowerStream RZ | 0.087106 | 94470.24 | System Access | Metering | Powerstream | Multi-year project to renew existing residential (except suite) metering equipment.
101871 | Base | Services (New and Upgrades) - Layouts – East North - Commercial Services | 0.016031 | 94398.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151180 | Base | Central-North - Capitalization of Locates | 0.024489 | 94387.49 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150600 | Base | Firmware Upgrades for Smart Meters - East | 0.024675 | 94363.34 | System Access | Metering | Powerstream | Multi-year project to renew residential Smart meter firmware to improve communication performance.
151169 | Base | Central-South - Capitalization of Locates | 0.030611 | 94344.62 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
151174 | Base | West Lines - Capitalization locates | 0.036734 | 94319.23 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150631 | Base | Transformer Station Metering - Central North | 0.052471 | 94245.75 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew wholesale metering equipment.
101696 | Base | Subdivision - North Underground Residential Distribution System Final Close out and Inspection. | 0.049355 | 94197.28 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
103381 | Base | East Lines - Capitalization locates | 0.061743 | 94144.61 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101870 | Base | Services (New and Upgrades) - Layouts – East South - Commercial Services | 0.078548 | 94022.15 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101869 | Base | Services (New and Upgrades) - Layouts – East North - New Residential | 0.083304 | 93989.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150650 | Base | Replace PCB Risk PT's - Enersource RZ | 0.10412 | 93977.25 | System Access | Metering | Enersource | Multi-year project to replace metering transformers identified with unacceptable levels of PCB's, to prevent hazardous spills.
101919 | Base | New Services (new and upgrades) - Commercial, Industrial and Institutional (ICI) Projects - NORTH | 0.088729 | 93955.31 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150647 | Base | Transformer Station Metering - Enersource RZ | 0.14692 | 93884.28 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew wholesale metering equipment.
151049 | Base | Commercial, Industrial, Institutional, Apartment Connections | 0.13981 | 93829.96 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
101685 | Base | Subdivision - South Underground Residential Distribution System Final Close out and Inspection. | 0.11903 | 93778.29 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150457 | Base | Services (New and Upgrades) - Layouts – St Catharines | 0.20089 | 93519.09 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151162 | Base | Non Recoverable replacement of Distribution Equipment due to accident/vandalism | 0.25985 | 93457.13 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101924 | Base | Mulit Unit Metering for New Buildings NORTH - PowerStream RZ | 0.17724 | 93421.21 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in northern area of territory.
150588 | Base | New Residential Subdivision Development - Alectra West | 0.23124 | 93265.82 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
101791 | Base | New Services - new and upgrades - COMMERCIAL, INDUSTRIAL, INSTITUTIONAL (ICI) SERVICES - SOUTH | 0.26192 | 92878.02 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101812 | Base | Reactive Capital, Alectra East - LIS | 0.27838 | 92710.01 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150754 | Base | Lines Central-North - Non-Recoverable Replacements | 0.36619 | 92705.38 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150726 | Base | Lines Central-South - Non-Recoverable Replacements | 0.36619 | 92705.38 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101820 | Base | Reactive Capital, Alectra East - Non-Recoverable Replacement | 0.31512 | 92582.71 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150389 | Base | Services (New and Upgrades) - Layouts – Central North | 0.41988 | 92563.35 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150651 | Base | C & I Metering - Renewal- Brampton RZ | 0.64177 | 92560.77 | System Access | Metering | Brampton | Multi-year project to renew existing ICI metering equipment.
150386 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central North | 0.4501 | 92424.37 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150453 | Base | CIS CC&B Modifications(Regulatory Enhancements) | 0.9498 | 92260.88 | General Plant | Information Technology | Multiple | Enhancements to the CIS (CC&B) application needed to meet any regulatory requirements Such requirements in the past have been Ontario Energy Savings Program (OESP) as well as the Monthly Billing projects.
150649 | Base | Suite Metering - Enersource RZ | 0.57141 | 91838.22 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew suite metering equipment.
150654 | Base | C & I Metering - New Services - Brampton RZ | 0.58993 | 91552.85 | System Access | Metering | Brampton | Multi-year project to purchase and install ICI metering equipment on new services.
150595 | Base | C & I and Wholesale Metering - PowerStream RZ | 0.56542 | 91530.35 | System Access | Metering | Powerstream | Multi-year project to purchase, install, and renew ICI and wholesale metering equipment.
101868 | Base | Services (New and Upgrades) - Layouts – East South - New Residential | 0.49694 | 91488.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101795 | Base | Multi Unit Metering for New Buildings SOUTH - PowerStream RZ | 0.53002 | 91273.08 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in southern area of territory.
101873 | Base | Services (New and Upgrades) - Layouts – East North - Residential Upgrades | 0.5843 | 91023.49 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151051 | Base | System Relocations Road Authorities | 0.70408 | 91002.2 | System Access | Road Authority | Guelph | Mandatory - System Access Related Project
150652 | Base | New Residential Subdivision Development - Alectra Central South | 0.50224 | 90948.17 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150388 | Base | Services (New and Upgrades) - Layouts – Central South | 0.80897 | 90774.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150692 | Base | New Feeder in Residential Subdivision Development - Alectra Central North | 0.74289 | 90609.19 | System Service | Capacity (Lines) | Brampton | This expenditure is required to meet the needs of the development community that construct municipal approved residential subdivisions in Alectra Utilities' Central North service territory
150599 | Base | Suite Meter - Reverification - PowerStream RZ | 0.95673 | 90368.15 | System Access | Metering | Powerstream | Multi-year project to renew Measurement Canada seal dates on existing suite metering equipment.
150455 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - St Catharines | 0.8988 | 90201.14 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150659 | Base | Residential Meters - by Metering - Brampton RZ | 0.88514 | 90095.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Metering.
150456 | Base | Services (New and Upgrades) - Layouts – Hamilton | 0.926 | 89961.61 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150630 | Base | New Residential Subdivision Development - Alectra Central North | 1.25 | 89952.48 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101828 | Base | Reactive Capital, Alectra East - Recoverable Replacement | 0.77405 | 89765.65 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover some costs for (i.e. pole hit, vehicle at scene of accicent, Alectra Utilities obtains most of costs (near $0 impact too budget))
101896 | Base | New Institutional/Commercial/Industrial Subdivision Development - Alectra East | 0.94134 | 89347.36 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101872 | Base | Services (New and Upgrades) - Layouts – East South - Residential Upgrades | 0.86564 | 89344.81 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101800 | Base | Reactive Capital, Alectra East - Storm Damage | 1.2899 | 86549 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151047 | Base | Subdivisions | 0.45393 | 85393.33 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
150620 | Base | Metering Renewal - all types - Horizon RZ | 2.139 | 84064.36 | System Access | Metering | Horizon | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment.
101808 | Base | Reactive Capital, Alectra East - Switchgears | 1.7507 | 83304.08 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150648 | Base | Metering Renewal - all types but Suite - Enersource RZ | 2.3405 | 82569.47 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew residential (except suite) and ICI metering equipment.
101892 | Base | New Subdivision Development - Secondary Service Lateral - Alectra East | 2.9306 | 80775.74 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150384 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central South | 3.6078 | 77903.71 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150449 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - Hamilton | 5.3342 | 69328.05 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151095 | Base | Reactive Restoration | 1.0671 | 63546.92 | System Renewal | Reactive Capital | Guelph | Replacement of assets which have failured and requires replacement in order to restore power to customers
101824 | Base | Reactive Capital, Alectra East - Distribution Equipment | 5.542 | 58189.58 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151161 | Base | Joint Use Pole Removal | 0.12016 | 57199.8 | System Renewal | Overhead Asset Renewal | Horizon | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
151050 | Base | Metering - all types - Guelph RZ | 0.42268 | 55986.2 | System Access | Metering | Guelph | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment in Guelph RZ.
150469 | Base | ERP JD Edwards Enhancements | 1.8359 | 55714.6 | General Plant | Information Technology | Multiple | Allocation of capital funds to provide 3rd party assistance on capital work, along with creating system enhancements to the JD Edwards ERP and supporting Systems.
150325 | Base | CIS CC&B Enhancements | 1.3079 | 55520.48 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) application to support process improvement requirements.As the CIS (CC&B) system is one of the core applications of the organization, operational enhancements come in from a number of venues and thereby feedback into the other downstream systems. These enhancements are considered for the overall customer and organizational benefits.
101832 | Base | Joint Use Pole Removal | 0.60592 | 54024.42 | System Renewal | Overhead Asset Renewal | Powerstream | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
101570 | Base | New Alliston 10MVA Substation - 44 kV Supply | 0.01765 | 50412.78 | System Service | Capacity (Stations) | Powerstream | This project is the 44KV feeder extension to supply Alliston MS (101569)
101571 | Base | New Alliston 10MVA Substation - 13.8 kV Feeder Integration | 0.0353 | 50183.69 | System Service | Capacity (Stations) | Powerstream | This project is the 13.8KV feeder integration for Alliston MS (101569)
101887 | Base | New Residential Subdivision Development - Alectra East | 10.9856 | 44863.95 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101569 | M-Factor | New Alliston 10MVA Substation - Industrial Parkway | 0.84023 | 44829.96 | System Service | Capacity (Stations) | Powerstream | The project entails the purchase of a station site in the vicinity of Dufferin St and Industrial Pkwy in Alliston, and constructing a new 10MVA, 44/13.8 kV, dual-stage fan, 4-feeder municipal substation
100859 | Base | Switchgear Renewal - East | 2.9356 | 43704.68 | System Renewal | Underground Asset Renewal | Powerstream | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151089 | Base | Overhead Rebuilds | 1.2682 | 39246.49 | System Renewal | Overhead Asset Renewal | Guelph | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
151241 | M-Factor | Arlen MTS - New Feeder | 0.45 | 37816.52 | System Service | Capacity (Lines) | Guelph | New Distribution feeder from Arlen MTS to support the load growth in the south Guelph and to meet continengency requirement.
151118 | M-Factor | Nebo TS 27.6kV True-up Payment (CCRA) | 0.54985 | 37750.31 | General Plant | Connection and Cost Recovery Agreements | Horizon | In accordance with the Connection Cost Recovery Agreement, a 10 year true-up is required for Nebo TS.
101508 | Base | Transformer Renewal - East | 3.0752 | 37474.31 | System Renewal | Transformer Renewal | Powerstream | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150673 | Base | Road Authority Central (Mississauga) | 4.4514 | 35000.51 | System Access | Road Authority | Enersource | Mandatory - System Access Related Project
150073 | M-Factor | Vaughan TS#1 Bus Differential & Overcurrent Protections Upgrades | 0.15265 | 34014.15 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Vaughan TS#1 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
150645 | Base | Road Authority Central (Brampton) | 5.275 | 31813.54 | System Access | Road Authority | Brampton | Mandatory - System Access Related Project
150828 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-West | 0.935 | 31592.28 | System Renewal | Overhead Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151452 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-West | 0.945 | 31590.16 | System Renewal | Underground Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
101762 | Base | Road Authority Expenditure PS South | 4.1217 | 31544.34 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
101355 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-East | 0.965 | 31424.67 | System Renewal | Overhead Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151450 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-East | 0.965 | 31424.67 | System Renewal | Underground Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
100340 | M-Factor | Vaughan TS#4 Feeder Integration - Part 3 | 5.2023 | 28489.24 | System Service | Capacity (Lines) | Powerstream | This project is the third part of a multi-part project to construct and integrate new feeders from VTS#4. This project is to integrate four 27.6kV feeders (25M5/25M6/25M7/25M8) from VTS4 to the distribution system.
151363 | Base | Cable Injection Project - (M25) - 14th - McCowan - Steeles - Old Kennedy, Markham | 0.819 | 27518.58 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 14 failures.
100867 | Base | Pole Renewal - East | 5.5081 | 25595.06 | System Renewal | Overhead Asset Renewal | Powerstream | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
151074 | Base | Reactive renewal | 3.4158 | 25136.12 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have failured and requires replacement in order to restore power to customers
151362 | Base | Cable Injection Project - (M39) - 16th - Warden - Hwy 7 - Woodbine, Markham | 1.26 | 23713.55 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 8 failures.
151360 | Base | Cable Injection Project - (M31) - 14th - Old Kennedy - Steeles - Warden, Markham | 0.84754 | 23640.66 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 38 failures.
151043 | Base | Transformer Renewal - Central South | 1.9795 | 21869.73 | System Renewal | Transformer Renewal | Enersource | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150071 | M-Factor | Markham TS#2 Bus Differential & Overcurrent Protections Upgrades | 0.25925 | 21087.3 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Markham TS#2 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
151303 | Base | Cable Replacement Project - (HAM) - Stone Church - Garth - Lincoln M. Alexander | 3.2043 | 19664.79 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 5 failures, or 18 failures per 100km. The average cable installation year is 1976 in this project scope.
150664 | Base | Residential Meters - by Lines - Brampton RZ | 0.63608 | 18166.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Lines.
151109 | Base | Switch Replacement | 0.18257 | 18145.07 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
102455 | Base | Melbourne MS322 Land Purchase & TX Upgrade - Bradford | 0.43692 | 17823.71 | System Service | Capacity (Stations) | Powerstream | This project consists of transformer upgrade to increase the capacity at Melbourne MS to meet the load growth the contingency condition for Bradford area.
151367 | Base | Cable Injection Project - (M21) - Hwy 7 - Markham - 16th - McCowan, Markham | 1.0575 | 17674.76 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 6 failures.
150319 | M-Factor | New MS - Duke MS 20 MVA Substation, Mississauga | 1.9528 | 17540.57 | System Service | Capacity (Stations) | Enersource | The Downtown21 plan forecasts a total population of 56,565 residents and 34,247 jobs in the Mississauga downtown core. The current capacity available for the downtown core is approximately 140 MVA ONAN rating. Based on growth projected and the land parcels available, Alectra Utilities estimates that, upon completion of Downtown21 the combined transformation load requirement will increase approximately by 300 MVA. This station will provide 20MVA ONAN capacity.
151104 | Base | Distribution Automation - Central North | 0.50504 | 17389.16 | System Service | SCADA and Automation | Brampton | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151366 | Base | Cable Injection Project - (M19) - Markham - Steeles - McCowan - 14th, Markham | 1.3532 | 17258.97 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 7 failures.
151318 | Base | Cable Injection Project - (I3) -Bovaird - Dixie - Queen - Hwy 410, Brampton | 0.57763 | 16118.68 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2014 to 2015 with average duration of 71 minutes.
150639 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-CENTRAL | 0.039321 | 15735.56 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of DC charging system for Central South Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150638 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-East | 0.039321 | 15735.56 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of DC charging system for Central North Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150636 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-North & TS | 0.039321 | 15735.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of DC charging system for East Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150640 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-WEST | 0.039321 | 15735.56 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of DC charging system for West Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
151460 | M-Factor | Cable Injection Project - (V17) - Langstaff - Keele - Rutherford - Dufferin, Vaughan | 0.56259 | 15316.59 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 3 failures. From 2015-2019 YTD customers in this area experienced 4 failures.
100337 | M-Factor | Markham TS #4 Feeder Egress Part 3 | 4.9176 | 14794.76 | System Service | Capacity (Lines) | Powerstream | This project is to install four 27.6kV feeders from MTS4 along Rodick Rd to 14th Ave. These feeders will be connected to existing feeders on 14th Ave and Miller Ave. It is MTS4 Feeder Integration Plan Part 3. This project will increase supply capacity by 80 MVA to support growth and development in Markham
150285 | Base | Transformer Renewal - Central North | 1.2737 | 14492.05 | System Renewal | Transformer Renewal | Brampton | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
101027 | Base | Switch Renewal - East | 0.70579 | 14308.5 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
102098 | Base | Client - IT Infrastructure | 1.3485 | 13761.18 | General Plant | Information Technology | Multiple | To upgrade desktop/laptop/mobile devices that are 5 years or older (Approximately 20% of our equipment). Net new equipment for mobile computing as well as upgrades and replacements for damaged devices. Request made by various business units. This budget also includes RSA tokens\Licenses, monitors, mice, keyboards, docking stations, tablets and small non-MFP printers. Out of Scope: Large MFP Printers
151247 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.605 | 13413.53 | System Renewal | Overhead Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102232 | Base | Capital Funds for Emergency P&C Purchases - East | 0.033587 | 13270.97 | System Renewal | Substation Renewal | Powerstream | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the East Operating Area (former PowerStream). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150683 | Base | Capital Funds for Emergency P&C Purchases - Central North | 0.033587 | 13184.55 | System Renewal | Substation Renewal | Brampton | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central North Operating Area (Brampton). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150685 | Base | Capital Funds for Emergency P&C Purchases - West | 0.033587 | 13184.55 | System Renewal | Substation Renewal | Horizon | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the West Operating Area (former Horizon). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150684 | Base | Capital Funds for Emergency P&C Purchases - Central South | 0.033587 | 13184.55 | System Renewal | Substation Renewal | Enersource | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central South Operating Area (former Mississauga). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150360 | M-Factor | New build - Extend 44kV feeder Centre View Dr, Mississauga | 0.88546 | 13005.45 | System Service | Capacity (Lines) | Enersource | A new 44 kV overhead/underground feeder extension is needed to provide supply to downtown Mississauga area on Centre View Drive as well as provide primary supply for Duke Municipal Station (MS).
150784 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.705 | 12968.3 | System Renewal | Overhead Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151453 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.755 | 12922.02 | System Renewal | Underground Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
150823 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.785 | 12654.97 | System Renewal | Overhead Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102099 | Base | Printer & Copier Fleet Replacement | 0.083706 | 12636.08 | General Plant | Information Technology | Multiple | Replacement of existing fleet of printers/copiers that are 5 or more years old. This will include non-MFP printers. Replacement to be determined by an evaluation of evolving needs and corporate requirements as well as age of equipment.
151449 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.905 | 12175.67 | System Renewal | Underground Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
103211 | Base | Misc Software Upgrades (FormScape, AutoCAD, etc.) - IT/OT Infrastructure | 0.020151 | 12020.93 | General Plant | Information Technology | Multiple | Upgrade/ acquire software as required / requested by business.
151451 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.935 | 11935.99 | System Renewal | Underground Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
103180 | Base | Citrix Xen Virtualization Expansion - IT Infrastructure | 0.3139 | 11298.77 | General Plant | Information Technology | Multiple | Client computing virtualization (Citrix) is currently the standard delivery method for applications and desktops at Alectra. This system has had a tremendous uptake in the organization and requires an upgrade in back-end infrastructure to support the additional demand from the business.
150693 | M-Factor | Blockchain | 0.57967 | 11191.63 | System Service | Distributed Energy Resources (DER) | Multiple | The project will prepare Alectra Utilities to engage with customers in a real-time and transparent process to record the flow of electricity to and from DERs, enabling the efficient procurement of distribution benefits, such as demand response and frequency regulation. The project will provide a robust settlement mechanism between Alectra and customers, backed by timely and efficient financial transactions, to enable overall trust and customer value delivery and leading to increased customer satisfaction.
151314 | Base | Cable Injection Project - (G2) -Wanless - Kennedy - Bovaird - Main, Brampton | 0.3125 | 11045.83 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2013 to 2017 with average duration of 125 minutes.
150665 | Base | Emerging Customer Initiated Work (West) | 1.7383 | 10905.1 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151465 | M-Factor | Cable Replacement - Mississauga Left Behind Cable | 0.55777 | 10856.69 | System Renewal | Underground Asset Renewal | Enersource | This project is to address cables which were part of a cable injection project but were ultimately not injectable at the time of project execution. These 'left behind' segments must be addressed, if they are left in the system they could cause a failure. Customers would not only experience an outage, but question the utilities work practices as we would have addressed only a portion of the cables instead of all the cables which could cause an outage.
101562 | Base | Arc Flash Mitigation Projects | 0.045741 | 10618.95 | System Service | Safety & Security | Powerstream | This project is to mitigate arc flash risk at East stations.
151307 | Base | Cable Injection Project - (HAM) - Upper Sherman - Stone Church - Nebo - Rymal | 0.28409 | 10594.98 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 2 failures, or 5 failures per 100km. The average cable installation year is 1989 in this project scope.
151299 | Base | Cable Replacement Project - (HAM) - Millen - Barton - Fruitland | 1.3457 | 10341.62 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 16 failures, or 44 failures per 100km. The average cable installation year is 1970 in this project scope.
150653 | Base | Road Authority West (St. Catharines) | 1.066 | 10216.94 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
150615 | Base | Metering Tools & Equipment - Central North | 0.039185 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150616 | Base | Metering Tools & Equipment - Central South | 0.039185 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150613 | Base | Metering Tools & Equipment - East | 0.039185 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150614 | Base | Metering Tools & Equipment - West | 0.039185 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
102263 | M-Factor | Work Force Management / Mobile Dispatch | 2.35 | 9761.78 | General Plant | Information Technology | Multiple | Enterprise wide field crew management system that will enable more efficient use of crews and improve visibility to job progress enabling better communication of expectations to customers
151456 | M-Factor | Cable Injection Project - (V50) - Hwy 7 - Kipling - Steeles - Hwy 27, Vaughan | 0.18416 | 9187.5 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 3 failures in 2018.
151063 | Base | Pole Renewal - Central South | 3.1407 | 9065.1 | System Renewal | Overhead Asset Renewal | Enersource | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
100886 | Base | Distribution Automation - East | 1.4385 | 9041.12 | System Service | SCADA and Automation | Powerstream | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151275 | Base | Cable Injection Project - (SCH) - QEW - Highway 406 - Martindale Road | 0.79689 | 8905.36 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 3 failures, or 11 failures per 100km. The average cable installation year is 1988 in this project scope.
151298 | Base | Cable Injection Project - (HAM) - Govenors - Old Ancaster | 0.9099 | 8842.48 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 3 failures, or 10 failures per 100km. The average cable installation year is 1989 in this project scope.
101804 | Base | Purchase of Major Tools | 0.36893 | 8158.3 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
101488 | Base | Markham TS #5 | 0.2722 | 8116.61 | System Service | Capacity (Stations) | Powerstream | This project is to perform Class EA and purchase land for Markham TS#5 which has been recommended as per the York Region IRRP
151313 | Base | Cable Injection Project - (F5) - Steeles - Main - Hwy 407 - McLaughlin, Brampton | 0.3125 | 7751.39 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 5 outages due to cable failures from 2007 to 2016 with average duration of 80 minutes.
150282 | Base | Switchgear Renewal - Central North | 0.51036 | 7521.14 | System Renewal | Underground Asset Renewal | Brampton | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150508 | Base | Installation of Transformer Bushing Monitoring on MS txmrs-Multi Year -CENTRAL | 0.17148 | 7508.89 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Transformer bushing monitoring system in Central South. bushing monitoring unit provides real time condition monitoring of the transformer bushings.
151391 | Base | 2023 GUELPH - Remotely Controlled Switches | 0.42012 | 7487.72 | System Service | SCADA and Automation | Guelph | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151325 | Base | Cable Replacement Project - (M31) - 14th - Old Kennedy - Steeles - Warden, Markham | 3.5 | 7411.62 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 38 failures.
151457 | M-Factor | Cable Injection Project - (V25) - Major Mackenzie - Keele - Rutherford - Jane, Vaughan | 0.40538 | 7409.58 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 2 failures. From 2015-2019 YTD customers in this area experienced 3 failures.
151339 | Base | Cable Replacement Project - (BA19) - Letitia - Anne - Edgehill - Ferndale, Barrie | 4.4258 | 7397.06 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 2 failures in 2018.
150370 | M-Factor | New build - 27.6kV New Feeders Lakeview Development, Mississauga | 1.8901 | 7391.03 | System Service | Capacity (Lines) | Enersource | Two 27.6kV feeders are to be extended in order to provide for additional capacity in the Lakeview area for the brownfield development and intesificiation
151316 | Base | Cable Injection Project - (H2) - Wanless - Heart Lake - Bovaird - Kennedy, Brampton | 0.40906 | 7371.2 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2009 to 2017 with average duration of 107 minutes.
150284 | Base | Pole Renewal - Central North | 2.898 | 7304.65 | System Renewal | Overhead Asset Renewal | Brampton | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
102017 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-North & TS | 0.33423 | 7275.34 | System Service | Safety & Security | Powerstream | This project consists of Sorbweb Oil containment system in East. Protects the environment in the event of a transformer tank rupture
100924 | M-Factor | Install two additional 27.6 kV ccts on Hwy 7 from Jane St to Weston Rd | 2.6201 | 7255.59 | System Service | Capacity (Lines) | Powerstream | This project is to reroute two 27.6kV feeders (21M3 & 21M4) to supply new load in Vaughan Metro Center (VMC). Vaughan Metro Center (VMC) is supplied by two feeders 21M5 and 21M11 from VTS2. There is limited capacity on VTS2 left before it reaches the 10 day Limited Time Rating (LTR) of 153 MW. VTS4 was completed in 2017 and is in service and will off load VTS2 so that will have extra capacity to supply new loads in the VMC development (approx. 80MW).
150714 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - Central | 0.076608 | 6819.25 | System Renewal | Substation Renewal | Enersource | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central South Operating Area (former Enersource). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150713 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.076608 | 6819.25 | System Renewal | Substation Renewal | Brampton | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central North Operating Area (Brampton). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150715 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - West | 0.076608 | 6819.25 | System Renewal | Substation Renewal | Horizon | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the West Operating Area (former Horizon). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150644 | Base | Road Authority West (Hamilton) | 1.9134 | 6689.48 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
151355 | Base | Cable Injection Project - (M26) - Hwy 7 -McCowan - 14th - Old Kennedy, Markham | 0.92043 | 6565.53 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 14 failures.
150507 | Base | 230kV TS Transformer Primary Bushing Monitoring Enablement-BPD Elimination - 4 TS Transformers-Multi-year initiative-TS | 0.49794 | 6521.07 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to install primary bushing monitoring at TS in EAST
151459 | M-Factor | Cable Injection Project - (V24) - Langstaff - Jane - Rutherford - Keele, Vaughan | 0.53203 | 6509.15 | System Renewal | Underground Asset Renewal | Powerstream | From 2015-2019 YTD customers in this area experienced 0 failures. From 2013-2019 YTD customers in this area experienced 2 failures.
150468 | Base | Meter to Cash auxiliary systems ongoing upgrades - IT/OT Infrastructure | 0.17264 | 6494.96 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) Meter to Cash ancillary systems to support process improvement requirements. Ancillary systems but not limited to upgrading FW, MV90, LPSS. These enhancements are considered for the overall customer and organizational benefits.
151418 | Base | Cable Replacement Project- Innovator & Courtney Park E (4), Mississauga | 2.8903 | 6467.04 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 7 outages, the length is 7,263 m, and the average cable age is 22 years old. This is a commerical/industrial (3-phase) area.
151310 | Base | Cable Injection Project - (E4) - Queen - McLaughlin - Steeles - Chinguacousy, Brampton | 0.24013 | 6421.34 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2008 to 2016 with average duration of 104 minutes.
151044 | Base | Switch Renewal - Central South | 0.28152 | 6318.96 | System Renewal | Overhead Asset Renewal | Enersource | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
103659 | Base | Storm Hardening - Four-Circuit Poles | 2.0675 | 6254.52 | System Renewal | Overhead Asset Renewal | Powerstream
150514 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear Initiative-WEST | 0.34696 | 6213.41 | System Service | Safety & Security | Horizon | This project consists of Sorbweb Oil containment system in West. Protects the environment in the event of a transformer tank rupture
151336 | Base | Cable Replacement Project - (BA22) - Sunnidale and Anne, Barrie | 1.5309 | 6208.17 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 2 failures in 2019.
151086 | Base | Insulator Replacements | 0.087105 | 5948.6 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
151463 | M-Factor | Cable Injection Project - (F4-G4) - Main - Steeles - Chinguacousy - Queen, Brampton | 0.34735 | 5559.84 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 86 failures. Exact number of failures in recent years is unknown at this moment.
150337 | Base | Switch Renewal - West | 0.45418 | 5475.59 | System Renewal | Overhead Asset Renewal | Horizon | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
151055 | Base | Major Tools | 0.078655 | 5431.72 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
150598 | Base | Suite Metering - Renewals & Retrofits - PowerStream RZ | 0.36442 | 5394.14 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering equipment in existing buildings upgraded from bulk metering.
150515 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-CENTRAL | 0.34696 | 5352.14 | System Service | Safety & Security | Enersource | This project consists of Sorbweb Oil containment system in Central South. Protects the environment in the event of a transformer tank rupture
150516 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-EAST | 0.34696 | 5352.14 | System Service | Safety & Security | Brampton | This project consists of Sorbweb Oil containment system in Central North. Protects the environment in the event of a transformer tank rupture
150336 | Base | Transformer Renewal - West | 0.69281 | 5293.52 | System Renewal | Transformer Renewal | Horizon | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
151306 | Base | Cable Injection Project - (HAM) - Upper Wentworth - Lincoln M. Alexander - Upper Ottawa - Stone Church | 0.46107 | 5236.89 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 2 failures, or 8 failures per 100km. The average cable installation year is 1988 in this project scope.
150750 | Base | Lines Central-North - Major Tools | 0.09727 | 5234.11 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150009 | Base | Insulator Renewal - East | 0.24187 | 5107.82 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
151203 | Base | Capital Corrective Equipment Replacement - Stations South West | 0.06 | 4921.2 | System Renewal | Substation Renewal | Guelph | This project is intended to provide capital for all unplanned station equipment replacements in the South West Operating Area (Guelph) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
102042 | Base | Purchase and Installation of Animal Guards at Various Stations-Annual Multi-year initiative-North & TS | 0.016503 | 4893.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of animal guard installation in East
151359 | Base | Cable Injection Project - (M16) - Major Mackenzie - 9th - 16th - Hwy 48, Markham | 0.66553 | 4782.06 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 7 failures.
151464 | M-Factor | Cable Injection Project - (F3-G3-H3) - Phase 2, Brampton | 0.45851 | 4696.76 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 103 failures. Exact number of failures in recent years is unknown at this moment.
151083 | Base | Switchgear Renewal - West | 0.43988 | 4683.89 | System Renewal | Underground Asset Renewal | Horizon | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151010 | Base | Switch Renewal - Central North | 0.67455 | 4603.75 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
150720 | Base | Lines Central-South - Major Tools | 0.22887 | 4591.27 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
151420 | Base | Cable Replacement Project-Eglinton & Credit Valley (5), Mississauga | 10.2106 | 4485.73 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 27,821 m, and the average cable age is 35 years old.
151021 | Base | Insulator Renewal - Central North | 0.38723 | 4235.99 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of non-polymer insulators (Areas are prioritiezed by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
150674 | Base | Emerging Customer Initiated Work Central (Brampton) | 0.1717 | 4183.83 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101763 | Base | Unforeseen Projects Initiated by the customer PS North | 0.13462 | 4161.34 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150679 | M-Factor | Alectra Drive for the Workplace | 0.16532 | 3997.47 | System Service | Capacity (Lines) | Multiple | Alectra Drive for the Workplace will demonstrate the value of integrating smart electric vehicle (EV) charging system at workplaces into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. The planned investment will help manage the flow of electricity needed to serve the building and EV charging stations, so that electricity costs are minimized for commercial customers while EV drivers have an easy and accessible charging solution.
151413 | Base | Cable Replacement Project- Rathburn Rd W & Elora Dr (9), Mississauga | 1.5737 | 3743.76 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 8 outages, the length is 3,270 m, and the average cable age is 27 years old.
102075 | Base | Major repairs, refurbishment, or modifications to switches/switchgear | 0.10463 | 3702.48 | System Renewal | Underground Asset Renewal | Powerstream | Switchgear and Switches in stores that repair/refurbishment of the units can allow them to be returned to service
151411 | Base | Cable Replacement Project- Queensway & Mavis (31), Mississauga | 3.5553 | 3693.6 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 8 outages, the length is 8,488 m, and the average cable age is 42 years old.
151276 | Base | Cable Injection Project - (SCH) - Vansickle | 0.36054 | 3555.68 | System Renewal | Underground Asset Renewal | Horizon | From 2015-2018 YTD customers in this area experienced 2 failures, or 11 failures per 100km. The average cable installation year is 1990 in this project scope.
150498 | Base | Capital Corrective Equipment Replacement - Stations Central South | 0.28015 | 3534.76 | System Renewal | Substation Renewal | Enersource | This project is intended to provide capital for all unplanned station equipment replacements in the Central South Operating Area (former Enersource) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150499 | Base | Capital Corrective Equipment Replacement - Stations Central North | 0.28015 | 3534.76 | System Renewal | Substation Renewal | Brampton | This project is intended to provide capital for all unplanned station equipment replacements in the Central North Operating Area (Brampton) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150497 | Base | Capital Corrective Equipment Replacement - Stations West | 0.28015 | 3534.76 | System Renewal | Substation Renewal | Horizon | This project is intended to provide capital for all unplanned station equipment replacements in the West Operating Area (former Horizon) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
101542 | M-Factor | New Barrie 20MVA Substation - Harvie | 0.81585 | 3447.05 | System Service | Capacity (Stations) | Powerstream | The project entails the purchase of a station site in the vicinity of Harvie Road and Veterans Drive in Barrie and constructing a new 44/13.8kV, 20MVA, 4-feeder municipal substation.
150774 | Base | Lines Central-North - Site Restorations | 0.10997 | 3434.48 | System Renewal | Overhead Asset Renewal | Brampton
150721 | Base | Lines Central-South - Site Restorations | 0.10997 | 3434.48 | System Renewal | Underground Asset Renewal | Enersource
150672 | Base | Burden Allocation - System Service | 0.11412 | 3353.13 | System Service | Capacity (Lines) | Horizon
151458 | M-Factor | Cable Injection Project - (V31) - Langstaff - Weston - Rutherford - Jane, Vaughan | 0.61248 | 3280.12 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 1 failure in 2017.
150263 | Base | Cable Replacement Project - East Left Behind Cable | 3.3747 | 3237.07 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in these areas have experienced 11 failures.
151416 | Base | Cable Replacement Project- Woodchester & Thorn Lodge (34), Mississauga | 2.3956 | 3183.8 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 7 outages, the length is 6,669 m, and the average cable age is 49 years old.
151356 | Base | Cable Injection Project - (V44) - Langstaff - Pine Valley - Hwy 7 - Kipling, Vaughan | 0.41378 | 3176.08 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 6 failures.
150601 | Base | Advanced Metering Infrastructure (AMI) Security Audit - East | 0.06706 | 3170.74 | System Access | Metering | Powerstream | Multi-year project to renew meter data security to address emerging cyber threats.
102065 | Base | Capital Corrective Equipment Replacement - East | 0.34733 | 3161.46 | System Renewal | Substation Renewal | Powerstream | This project is intended to provide capital for all unplanned station equipment replacements in the East Operating Area (former PowerStream area) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150611 | Base | Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.17089 | 3116.96 | System Renewal | Substation Renewal | Powerstream | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the East Operating Area (former PowerStream). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150524 | Base | Security Additions & Enhancements | 0.24961 | 3109.96 | General Plant | Information Technology | Multiple | details refer to PWC doc
150623 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-WEST | 0.0054528 | 3095.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of animal guard installation in West
150622 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-CENTRAL | 0.0054528 | 3093.04 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Animal guard at Central South Stations
150621 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-EAST | 0.0073394 | 3081.51 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Animal guard at East Stations
151317 | Base | Cable Injection Project - (H4) - Queen - Hwy 410 - Steeles - Kennedy, Brampton | 0.36525 | 3033.4 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 2 outages due to cable failures in 2007 and 2012 with average duration of 72 minutes.
151417 | Base | Cable Replacement Project- Rathburn & Cawthra (27), Mississauga | 0.63662 | 2967.95 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 8 outages, the length is 1,103 m, and the average cable age is 38 years old.
100632 | M-Factor | 27.6 kV Pole Line on 14th Ave from Hwy 48 to 9th Line | 2.039 | 2933.45 | System Service | Capacity (Lines) | Powerstream | This project consists of building new 27.6 KV pole line on 14th Avenue from HWY 48 to 9th Line. Feeders in this area are over the planning limit and existing load over planning limit and this project will redirected to alternate supply as well as supply new development.
151208 | Base | Station Equipment Temperature Monitoring - South West | 0.015 | 2910.58 | System Renewal | Substation Renewal | Guelph | MULTI ANSWER
151286 | Base | Cable Replacement Project - (H2) - Wanless - Heart Lake - Bovaird - Kennedy, Brampton | 1.323 | 2867.55 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2011 to 2017 with an average duration of 126 minutes
101625 | Base | Cyber Security Audit & Upgrades | 0.074335 | 2865.1 | General Plant | Information Technology | Multiple | This project would fund various activities and countermeasures to improve the cyber security posture of the Operations' Network. This will be a mandate for compliance to Ontario Cyber Security framework. The counter measures include: - an annual audit of the cyber security countermeasures in place; - implementation of new technologies to seal identified compromises; - replacement of deployed cyber security equipment deemed end of life or not able to deliver an expected level of service.
150671 | Base | Burden Allocation - System Renewal | 1.8595 | 2831.23 | System Renewal | Other System Renewal | Horizon
150632 | Base | AMI Gatekeeper Expansion - Brampton RZ | 0.030113 | 2820.22 | System Access | Metering | Brampton | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
150374 | M-Factor | New build - 13.8kV Feeder Extension 9th Line, Derry to Argentia, Mississauga | 1.2051 | 2570.63 | System Service | Capacity (Lines) | Enersource | 13.8kV OH feeder extension 9th Line from Derry Rd W to Argentia Rd in Mississauga.This will provide additional capacity for growth along 9th Line.
150332 | M-Factor | Non-Wires Alternative Pilot | 0.82869 | 2536.94 | System Service | Capacity (Stations) | Powerstream | The project will provide customers with increased flexibility to make decisions about their electricity consumption, generation, and costs; it leads to more efficient integration of DERs which yields greater benefits to customer, system reliability, and power quality. This project will also provide the opportunity to increase operational efficiency and improved asset management to enhance service to customer and defer and/or reduce infrastructure investment needs in York Region.
150580 | Base | West Region Tools and Test Equipment | 0.20927 | 2494.28 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
150627 | Base | Station Equipment Temperature Monitoring-EAST | 0.07841 | 2479.48 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of Station Temperature Monitoring system in Central North and it enables controlled emergency loading beyond the nameplate rating.
150629 | Base | Station Equipment Temperature Monitoring-WEST | 0.07841 | 2479.48 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of Station Temperature Monitoring system in West and it enables controlled emergency loading beyond the nameplate rating.
150095 | M-Factor | Vaughan TS#1 T1/T2 "B" Differential Protections Upgrade | 0.11583 | 2477.83 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the current T1/T2 ASEA solid state Transformer "B" Differential Protection relays at Vaughan TS#1 with new relays having fault recording capabilities
151202 | Base | Purchase of Major Station Tools - Multi-year | 0.01 | 2472.82 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
151419 | Base | Cable Replacement Project- Thomas St & Hillside (24), Mississauga | 1.8379 | 2467.12 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 4,089 m, and the average cable age is 30 years old.
151395 | Base | 2023 GUELPH - Transite Underground Duct Replacement | 0.28309 | 2460.85 | System Renewal | Underground Asset Renewal | Guelph | Replacement of Duct Structure which contains asbestoes a known carcinogen and impacts worker safety.
150625 | Base | Purchase of Major Tools - Muliti Year-CENTRAL | 0.022391 | 2395 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150624 | Base | Purchase of Major Tools - Muliti Year-EAST | 0.022391 | 2395 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150626 | Base | Purchase of Major Tools - Muliti Year-WEST | 0.022391 | 2395 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
101761 | Base | Unforeseen Projects Initiated by the customer PS South | 0.43233 | 2365.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151435 | Base | Cable Injection- 010 - Area 56- Derry Rd W & Ninth Line, Mississauga | 1.2798 | 2307.05 | System Renewal | Underground Asset Renewal | Enersource | There are 3 outages, we are injecting a total of 45,837 m of cable for this project, and the average age of the cable is 30 years.
151290 | Base | Cable Replacement Project - (I3) - Bovaird - Dixie - Queen - Hwy 410, Brampton | 0.7259 | 2280.06 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 8 outages due to cable failures from 2007 to 2018 with average duration of 133 minutes.
150084 | M-Factor | Markham TS#2 T1/T2 "B" Differential Protections Upgrade | 0.093418 | 2269.53 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the T1/T2 GEC solid state Transformer "B" Differential Protection relays at Markham TS#3 with new relays having fault recording capabilities
151244 | Base | Fault Indicators | 0.018 | 2243.02 | System Service | System Control, Comm'ns & Performance | Guelph | The scope of this project is to install Fault Indicators in Guelph. The project would include the fault indicators communicating to the existing SCADA and will improve the fault locating and improve SAIDI
151181 | Base | Cable Replacement Project - Left Behind Cable, Brampton | 0.525 | 2163.34 | System Renewal | Underground Asset Renewal | Brampton | This project is to address cables which were part of a cable injection project but were ultimately not injectable at the time of project execution. These 'left behind' segments must be addressed, if they are left in the system they could cause a failure. Customers would not only experience an outage, but question the utilities work practices as we would have addressed only a portion of the cables instead of all the cables which could cause an outage.
150675 | Base | Emerging Customer Inititated Work Central (Mississauga) | 0.19078 | 2049.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
101764 | Base | Road Authority Expenditure PS North | 1.6405 | 2038.3 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
150604 | Base | Smart Meter Network Expansion - PowerStream RZ | 0.27577 | 2035.93 | System Access | Metering | Powerstream | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
151092 | Base | Distribution Automation - Central South | 0.57 | 2013.5 | System Service | SCADA and Automation | Enersource | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151030 | Base | Addition of Sensors to SCADA Controllable 44kV LISs in Brampton | 0.27001 | 2012.97 | System Service | System Control, Comm'ns & Performance | Brampton | This project is to add sensors to the 44KV switches in Central North
150694 | M-Factor | Cityview microgrid enhancements | 0.015721 | 1985.17 | System Service | Capacity (Lines) | Powerstream | The project is to understand how microgrids can be integrated into the distribution grid in a safe and reliable manner. The microgrid is used to evaluate integration and connection to the distribution grid, while reducing the building's load, greenhouse gas emissions, and increasing its resiliency to grid outages.
150538 | Base | Cyber Security Devices Upgrades | 0.56351 | 1984.93 | General Plant | Information Technology | Multiple | This project upgrades security tools to maintain compliance with OEB Cyber Security Framework
151335 | Base | Cable Replacement Project - (BA14) - Tifffin and Hwy 400, Barrie | 2.6821 | 1975.76 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 43 years old and will be 47 when project starts (2023).
100904 | M-Factor | Install Double Cct Pole Line on Major Mackenzie - Hwy 27 to Huntington Rd | 3.6506 | 1874.19 | System Service | Capacity (Lines) | Powerstream | This project is to build two 27.6kV ccts on Major Mackenzie - Hwy 27 to Huntington Rd to supply new customers on Major Major Dr and existing customers. There is one 4.8kV single phase cct on the west half of the section and there is one 27.6kV cct (1/0 AL) on the east half the section. They don’t have sufficient capacity for future developments in the area.
150670 | Base | SCADA FDIR | 0.1256 | 1798.98 | System Service | SCADA and Automation | Multiple | Fault Detection, Isolation, and Restoration implementation, next generation of distribution automation technology. This utilizes devices which are already automated and integrates them into the OMS system such that devices perform self healing after a fault. in some cases reducing the outage time to less then 1 minute.
151323 | Base | Cable Injection Project - (L4) - Queen - Airport - Steeles - Torbram, Brampton | 0.16725 | 1746.01 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 outage due to cable failures to date. Cables are 31 years old and will be at the injection eligibility threshold by the time of project execution in 2023.
150680 | M-Factor | Alectra Drive at Home | 0.59641 | 1731.44 | System Service | Capacity (Lines) | Multiple | Alectra Drive at Home will demonstrate the value of integrating smart electric vehicle (EV) charging system in multi rise buildings as well as residential homes into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. It will also provide insight into the characteristics of EV Charging, how EVs can be aggregated and controlled to provide the benefit at the local, regional and provincial system levels, and customer response to these control and optimization strategies.
151201 | Base | Purchase of New Critical Spare Parts - Guelph | 0.01 | 1727.97 | System Renewal | Substation Renewal | Guelph | This project involves procurement of critical spare parts for stations in the South West Operating Area (Guelph) so as to facilitate prompt repair of failed assets during emergency situations.
150378 | M-Factor | Rear Lot Renewal Project - East of Queen Street/North of Mill Street | 1.7925 | 1698.83 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 1 outage lasting 8.6hrs per year based on 3 a year average.
150619 | Base | Purchase of Critical Spare Parts - West | 0.022616 | 1648.51 | System Renewal | Substation Renewal | Horizon | This project involves procurement of critical spare parts for stations in the West Operating Area (former Horizon) so as to facilitate prompt repair of failed assets during emergency situations.
151136 | Base | C55 Alectra: Optimization of Business Practices | 0.1605 | 1624.9 | General Plant | Information Technology | Multiple | Optimizing the current software to communicate with other systems such as the ERP will allow for more efficient and effective budgeting processes and consolidation of information allowing for consistent reporting of the information from one system.
151139 | M-Factor | Voltage Conversion - MS-12 Hansen Rd, Brampton | 2.4212 | 1599.32 | System Renewal | Overhead Asset Renewal | Brampton | From 2015-2017 customers in this area experienced 29 outages and had 94,267 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
150642 | Base | Proactive Replacement of Remote Terminal Units - Central North | 0.16397 | 1582.3 | System Renewal | Substation Renewal | Brampton | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the Central-North Operating Area (Brampton). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
150617 | Base | Purchase of Critical Spare Parts - Central North | 0.030228 | 1568.76 | System Renewal | Substation Renewal | Brampton | This project involves procurement of critical spare parts for municipal stations in the Central North Operating Area (Brampton) so as to facilitate prompt repair of failed assets during emergency situations.
151087 | Base | Switchgear Replacement | 0.25194 | 1559.43 | System Renewal | Underground Asset Renewal | Guelph | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150618 | Base | Purchase of Critical Spare Parts - Central South | 0.035826 | 1556.59 | System Renewal | Substation Renewal | Enersource | This project involves procurement of critical spare parts for stations in the Central South Operating Area (former Enersource) so as to facilitate prompt repair of failed assets during emergency situations.
102077 | Base | Major repair, refurbishment, or conversions of distribution transformers | 0.031389 | 1540.55 | System Renewal | Transformer Renewal | Powerstream | Transformers returned or in stores where repair/refurbishment of the unit can return it to service at a lower cost then purchase of a new unit
150964 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-337 | 0.4 | 1530.72 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150989 | Base | Fleet_West_Vehicle Replacement_ Underground Reel Tensioner Truck 1-351 | 0.415 | 1519.21 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150887 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-379 | 0.438 | 1501.57 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151222 | Base | Concrete Structures | 0.20254 | 1469.44 | System Renewal | Underground Asset Renewal | Guelph | Replacement of lids on civil structures to avoid public risk
151320 | Base | Cable Injection Project - (I5) - Steeles - Dixie - Hwy 407 - Hwy 410, Brampton | 0.11569 | 1425.74 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 outage due to cable failures to date. Cables are 31 years old and will be at injection eligibility threshold by the time of project execution in 2023.
150334 | Base | Distribution Automation - West | 0.72 | 1424.45 | System Service | SCADA and Automation | Horizon | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151052 | Base | Emerging Customer Initiated Work - Relocations | 0.097956 | 1412.11 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
150751 | Base | Facilities_East_Capital Replacement Investment Support | 0.090175 | 1374.32 | General Plant | Facilities Management | Powerstream | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
151288 | Base | Cable Replacement Project - (H4) - Queen - Hwy 410 - Steeles - Kennedy, Brampton | 0.58625 | 1353.9 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2009 to 2018 with average duration of 189 minutes.
151357 | Base | Cable Injection Project - (V34) - Kirby - Jane - Teston - Weston, Vaughan | 0.072513 | 1342.87 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 1 failure.
150335 | Base | Pole Renewal - West | 3.0097 | 1338.4 | System Renewal | Overhead Asset Renewal | Horizon | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
151387 | Base | Cable Replacement - (833) - 295 Water St Subdivision, Guelph | 0.59393 | 1319.63 | System Renewal | Underground Asset Renewal | Guelph
151337 | Base | Cable Replacement Project - (BA18) - Ferndale and Benson, Barrie | 1.023 | 1318.19 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 41 years old and will be 45 when project starts (2023).
150738 | Base | Facilities_West_Capital Replacement Investment Support | 1.7576 | 1289.1 | General Plant | Facilities Management | Horizon | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150330 | M-Factor | Rear Lot Renewal Project - Marsdale, St.Catharines | 1.0693 | 1284.11 | System Renewal | Rear Lot Conversion | Horizon | This area has had an average of 19 outages lasting 1hr per year based on 3 year average.
151358 | Base | Cable Injection Project - (V62) - Kirby - Hwy 27 - Nashville - Huntington, Vaughan | 0.090468 | 1265.18 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 1 failure.
150790 | Base | Fleet_Central South Vehicle Replacement-Puller/Tensioner | 0.2 | 1264.62 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
102241 | Base | Proactive Replacement of Remote Terminal Units - East | 0.1043 | 1239.66 | System Renewal | Substation Renewal | Powerstream | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the East Operating Area (former PowerStream). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
150529 | Base | OT GIS & OMS Software Upgrade | 0.28826 | 1210.24 | General Plant | Information Technology | Multiple | Requried upgrades to our customer facing GIS and OMS systems to ensure product support and security patches.
151064 | Base | Secondary Pedestals -St. Catharines | 0.20781 | 1153.93 | System Service | Safety & Security | Horizon | This project involves the replacment of above grade steel secondary pedestals which pose a safety risk to the general public
101125 | Base | Lines Mobile Equipment - IT/OT Infrastructure | 0.083706 | 1119.08 | General Plant | Information Technology | Multiple | This budget covers the deployment of mobile technology - laptops/field tablets and accessories - within the Lines Department to gain efficiencies in field operations. By deploying this technology, the Lines area can move away from a paper-based to a more electronic environment. In future, it is envisioned that, for example, mobile applications will facilitate the electonic transmission of work orders and electronic record keeping (asset tracking, tailboards, switching orders, timesheets). This will allow for streamlined operational processes and record-keeping, thereby supporting corporate technological initiatives such as the GIS, Outage Management System, and future Workforce Management system. At present, all Lines Management personnel and Subforemen have laptops, facilitating activities such as viewing of the GIS, electronic Asset Tracking Forms, and use of OMS Responder Mobile. Expenditures in this area will allow for more deployment of field devices among Lines crews and for the implementation of more computerized processes.
150570 | Base | Alectra West Substation Ground Grid Installations | 0.30802 | 1091.19 | System Service | Safety & Security | Horizon | This project is to install ground grid at East Stations
151204 | Base | Upgrade to Station Facilities (Buildings/Civil work) Multi-year | 0.01 | 1089.29 | General Plant | Facilities Management | Guelph | This project involves work involving structural components of stations, including windows, brickwork, roofs, foundations, drainage, doors, etc. at stations in the SouthWest Operational Area. Not keeping up with this work would result in advanced deterioration resulting in even greater maintenance costs, potential safety concerns and potential failure of the electrical equipment in the building causing power interruptions.
103198 | Base | BizTalk Upgrade - IT Infrastructure | 0.26158 | 1085.47 | General Plant | Information Technology | Multiple | Upgrade existing BizTalk to latest version. We currently have a development, test, and Production environment.
151434 | Base | Cable Injection- 009- AREA 54- Highway 401 & Argentia, Mississauga | 2.5247 | 1085.23 | System Renewal | Underground Asset Renewal | Enersource | There are 0 outages, we are injecting a total of 30,642 m of cable for this project, and the average age of the cable is 30 years.
151284 | Base | Cable Replacement Project - (E3) - Bovaird - McLaughlin - Queen - Chinguacousy, Brampton | 0.68985 | 1081.89 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 cable failure to date. Cables will be at the injection eligibility threshold by the time of project execution in 2023.
150806 | Base | Fleet_Central South Vehicle Replacement-207-09 S/bucket | 0.49 | 1068.7 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151041 | Base | Protection Logic Upgrades - East MSs (North) | 0.087103 | 1061.11 | System Service | System Control, Comm'ns & Performance | Powerstream
151373 | Base | Cable Replacement - (923) - Scottsdale Drive Subdivision, Guelph | 0.755 | 1060.3 | System Renewal | Underground Asset Renewal | Guelph
150937 | Base | Fleet_West_Vehicle Replacement_Cargo/Passenger Vans. | 0.04 | 995.47 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151091 | Base | Switchgear Renewal - Central South | 3.849 | 982.44 | System Renewal | Underground Asset Renewal | Enersource | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150983 | Base | Fleet East Vehicle replacement - Pickup truck 1500 | 0.32459 | 982.4 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151159 | Base | Fault Indicator Installation and Replacement - Hamilton and St. Catharines | 0.2858 | 966.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of fault indicator installation in West
150628 | Base | Station Equipment Temperature Monitoring-CENTRAL | 0.07931 | 965.25 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of Station Temperature Monitoring system in Central South and this enables controlled emergency loading beyond the nameplate rating.
150815 | Base | Fleet_Central South Vehicle Replacement-Trailers | 0.087 | 960.75 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151065 | Base | Manhole Lid Replacement | 0.36371 | 925.3 | System Renewal | Underground Asset Renewal | Horizon | Replacement of lids on civil structures to avoid public risk
150900 | Base | Fleet_West_Vehicle Replacement_ Step Vans | 0.36 | 917.53 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150981 | Base | Fleet East Vehicle replacement - Pickup truck 2500 | 0.52167 | 913.9 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150361 | M-Factor | Airport 88M5 & 88M7 HONI Purchase | 0.53902 | 905.21 | System Service | Capacity (Lines) | Enersource | Hydro One owns the OH Feeders from Richview TS to the CN rails approximately 6100m away. 88M5 and 88M7 would transfer ownership from HONI to Alectra to reliably supply to airport.
151017 | Base | Fleet_West_Vehicle_Replacement_Tensioner Trailers | 0.391 | 893.75 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150969 | Base | Fleet East Vehicle replacement - SUV/Van | 0.23649 | 884.61 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150904 | Base | Fleet East Yearly Light and Misc equipment | 0.023516 | 846.86 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150817 | Base | Fleet_Central South Vehicle Replacement-230-11 S/bucket | 0.53 | 830.28 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150746 | Base | Facilities_Central_Capital Replacement Investment Support | 1.5044 | 807.27 | General Plant | Facilities Management | Multiple | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
151431 | Base | Cable Injection- 006- AREA 39- Erin Mills Pkway & Thomas St, Mississauga | 1.8205 | 786.04 | System Renewal | Underground Asset Renewal | Enersource | There are 0 outages, we are injecting a total of 38,448 m of cable for this project, and the average age of the cable is 30 years.
101622 | Base | DACS Inverters and RTU's removal - East | 0.05504 | 765.32 | System Renewal | Substation Renewal | Powerstream | This project involves removal of obsolete and out-of-service DACs inverters, RTUs and associated wiring at stations in the East Operating Area (former PowerStream) so as to remove clutter, thus simplifying future work and freeing up space for future station upgrades.
150881 | Base | Fleet_ Central North Vehicle Replacement DBL.Bucket 7808 | 0.6 | 749.12 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150765 | Base | Facilities_Reno_Vansickle - Service Centre Upgrades | 0.1133 | 745.86 | General Plant | Facilities Management | Horizon | Repairs to building envelop/walls to prevent further damage to the build infrastructure and systems that are supporting critical operational systems such as control rooms, server rooms, customer services groups, etc.
101632 | Base | Obsolete Revenue Metering Removal from TSs | 0.057071 | 739.84 | System Service | Safety & Security | Powerstream | Evolution of the distribution system to permit more efficient integration of DERs to yield 18
150970 | Base | Fleet East Vehicle replacement - Van pool vans | 0.13506 | 714.37 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151082 | Base | SCADA Infrastructure | 0.14082 | 688.19 | System Service | System Control, Comm'ns & Performance | Guelph
151058 | Base | Distribution Transformer Replacements & Upgrades | 0.36409 | 682.68 | System Renewal | Transformer Renewal | Guelph | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150669 | Base | Burden Allocation - System Access | 0.67738 | 669.62 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150894 | Base | Fleet_ Central North Vehicle Replacement S/Bucket 3110 | 0.51 | 655.77 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150792 | Base | Fleet_Central South Vehicle Replacement- RBD 109-07 | 0.57 | 652.63 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
102166 | Base | SQL Expansion - IT Infrastructure | 0.06278 | 635.85 | General Plant | Information Technology | Multiple | Expand existing SQL infrastructure to meet project demands and natural growth of database. Add system capacity, improve performance, and reduce the risk of downtime due resource constraints.
150203 | Base | Station Equipment Temperature Monitoring-NORTH & TS | 0.065617 | 614.42 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of Station Temperature Monitoring system in East and it enables controlled emergency loading beyond the nameplate rating.
150976 | Base | Fleet East Unit # 365 digger truck | 0.61903 | 604.13 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150977 | Base | Fleet East Unit # 366 digger truck | 0.61903 | 604.13 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150496 | Base | iPass Project Management – Planned Capital - West | 0.70959 | 589.28 | System Renewal | Underground Asset Renewal | Horizon | Help in optimizing DER performance and efficiency to improve addressing overall energy needs.
150967 | M-Factor | Fleet East Unit # 125, 83' Double Bucket | 0.66097 | 580.18 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
102046 | Base | Purchase of Major Tools - Muliti Year-North & TS | 0.046601 | 565.1 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
151128 | M-Factor | MS Transformer & HV Switchgear Replacement - Western MS36 T1 & HV1 | 0.2037 | 553.77 | System Renewal | Substation Renewal | Enersource | Recent testing has indicated possible mechanical damage to the transformer windings and the HV switchgear has suffered damage due to a prior failure. The station is in a residential area and a transformer failure could result in a fire, posing a risk to the community and collateral damage to other assets in the station, as well as resulting in an extensive power interruption. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted reactive capital expenditure.
150905 | Base | Fleet East Multi Year Shop tools | 0.011706 | 544.12 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of tools and shop equipment required to repair and maintain vehicles to ensure vehicle availability to support capital systems projects.
101816 | Base | Alectra East (South), Fault Indicator Installation and Replacement Multi-year initiative | 0.25467 | 542.12 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - North Region which will result improved outage response, operational efficiency, and reliability
150938 | M-Factor | Fleet_ Central North Vehicle Replacement_Stake Trucks | 0.28 | 539.37 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151085 | M-Factor | Rear Lot Conversions | 0.12098 | 530.82 | System Renewal | Rear Lot Conversion | Guelph
101134 | Base | Alectra East (North), Fault Indicator Installation and Replacement Multi-year initiative | 0.25699 | 527.43 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - South Region which will result improved outage response, operational efficiency, and reliability
150437 | Base | OT GIS & OMS Enhancements | 0.26694 | 519.79 | General Plant | Information Technology | Multiple | Ongoing productivity enhancements to core GIS and OMS platforms to meet internal and customer demand for functionality.
150602 | Base | Smart Meter Test Facility - PowerStream RZ | 0.020641 | 471.4 | System Access | Metering | Powerstream | Multi-year project to expand the capability of the Meter Test Facility to test increasing types of meters and AMI systems before they are placed into production.
150810 | M-Factor | Fleet_Central South Vehicle Replacement-Step Vans | 0.235 | 461.7 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150798 | M-Factor | Fleet_Central South Vehicle Replacement- Arrowboard | 0.012 | 450.06 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150848 | Base | Fleet_Central South Vehicle Replacement-Compressors | 0.084 | 449.03 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102027 | Base | Purchase of Critical Spare Parts - Multiyear - East | 0.073053 | 427.82 | System Renewal | Substation Renewal | Powerstream | This project involves procurement of critical spare parts for transformer and municipal stations in the East Operating Area (former PowerStream) so as to facilitate prompt repair of failed assets during emergency situations.
150494 | Base | iPass Project Management – Planned Capital - Central-North | 0.39812 | 408.86 | System Renewal | Overhead Asset Renewal | Brampton | Predicting the influence of weather conditions and DER contribution simultaneously on the power grid, for proactively mitigating local outages,
150495 | Base | iPass Project Management – Planned Capital - Central-South | 0.39812 | 408.86 | System Renewal | Overhead Asset Renewal | Enersource | Enable better visibility towards preventive equipment maintenance needs arising due to DER penetration which will further help mitigate outage risks,
101781 | Base | iPass Project Management – Planned Capital - East | 0.40696 | 408.86 | System Renewal | Overhead Asset Renewal | Powerstream | Estimating the effects of DER contribution at the feeder and region levels to further optimize the energy flows between the Utility and its consumers,
150607 | M-Factor | Station LED Lighting Upgrades - Central | 0.027719 | 407.91 | System Renewal | Substation Renewal | Enersource | Replacement of inefficient lighting fixtures and lamps at stations in the Central Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150606 | M-Factor | Station LED Lighting Upgrades - EAST | 0.027719 | 407.91 | System Renewal | Substation Renewal | Brampton | Replacement of inefficient lighting fixtures and lamps at stations in this Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
151013 | M-Factor | Fleet_West_Vehicle_Replacement_Bucket Truck_1-354 | 0.4 | 407.29 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
151132 | M-Factor | MS Transformer & HV Switchgear Replacement - Munden MS35 T1 & HV1 | 0.20424 | 405.83 | System Renewal | Substation Renewal | Enersource | Recent testing has indicated that the transformer insulation has deteriorated and lacks a proper foundation and is beginning to lean. The station is in a residential area and a transformer failure could result in a fire, posing a risk to the community and collateral damage to other assets in the station, as well as resulting in an extensive power interruption. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted reactive capital expenditure.
150399 | M-Factor | Rear Lot Renewal Project - Richlieu Dr and Trelawne Dr, St.Catharines | 1.2633 | 392.54 | System Renewal | Rear Lot Conversion | Horizon | This area has had an average of 40 outages lasting 1.5hrs per year based on 3 year average.
150138 | M-Factor | Cable Replacement Project – (BA23-BA24) - Cook St and Steel St, Barrie | 1.707 | 389.44 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 43 years old. Project is in 2023 so it will be over EUL by 6 years.
150608 | M-Factor | Station LED Lighting Upgrades - West | 0.02813 | 359.12 | System Renewal | Substation Renewal | Horizon | Replacement of inefficient lighting fixtures and lamps at stations in the West Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
102034 | Base | Upgrade to Station Facilities (Building / Civil work) Multi-year - East | 0.13741 | 339.91 | System Renewal | Substation Renewal | Powerstream | MULTI ANSWER
150531 | Base | OT GIS Hardware Refresh | 0.37668 | 294.15 | General Plant | Information Technology | Multiple | Hardware platform refresh to support GIS infrastructure.
150610 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - Central | 0.021678 | 289.6 | System Renewal | Substation Renewal | Enersource | Existing driveways at stations in the Central Operational Area that are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150609 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - East | 0.021678 | 289.6 | System Renewal | Substation Renewal | Brampton | Existing driveways in this Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150612 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - West | 0.021678 | 289.6 | System Renewal | Substation Renewal | Horizon | Existing driveways in the West Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150552 | Base | ServiceNow Expansion - IT Infrastructure | 0.060844 | 258.47 | General Plant | Information Technology | Multiple | Building and adding features within ServiceNow we will eliminate outdated processes by automating more tasks and decisions allowing us to be more efficient and productive. Enhancements include the automation of the flow of data between other systems and across programs used by various departments and ServiceNow. Servicebots will be used as ServiceNow learns from past patterns, in order to predict future outcomes, including determining risks, assigning owners, and categorizing work. Learned models set the category of the IT request and assign the task to the right team, as well as calculate associated risk of action or inaction. This capability will improve the speed and efficiency of IT service delivery.
151166 | M-Factor | Fleet_ Central North Vehicle Replacement pick ups | 0.054 | 244.57 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102050 | Base | Various Stations-Station Lighting Upgrade/Retrofit-Energy Efficiency Lighting-initiative Multi-year - East | 0.057565 | 239.8 | System Renewal | Substation Renewal | Powerstream | Replacement of inefficient indoor and outdoor lighting fixtures and lamps at stations in the East Operating Area (former PowerStream) will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150391 | Base | Wireless LAN Upgrade | 0.080052 | 235.12 | General Plant | Information Technology | Multiple | Corporate Wireless LAN upgrade to replace end of life wireless infrastructure in corporate and operation center locations.
150843 | M-Factor | Fleet_Central South Vehicle Replacement-Bocat | 0.026 | 223.44 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
100319 | M-Factor | Radial Supply Remediation/Conversion - 13.8 kV to 27.6 kV on Miller Ave | 1.5371 | 207.69 | System Renewal | Overhead Asset Renewal | Powerstream | From 2015-2017 customers in this area experienced 15 outages and had 45,942 minutes of interruption. Customers in this area ona radial supply with no backup, this is atypical of Alectra Utilities customers and needs to be rectified to ensure customers here are receiving service similar to other Alectra Utiliites customers.
150936 | Base | Fleet_ Central North Vehicle Replacement Tower Lights | 0.015 | 192.17 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150802 | Base | Fleet_Central South Vehicle Replacement- Scissor lift | 0.03 | 184.85 | General Plant | Fleet Renewal | Enersource | Asset replacement due to poor conditions and age and lack of parts replacement. Equipment not as available to support capital system renewal projects and respond to emergencies with material handling. .
150944 | M-Factor | Fleet_ Central North Vehicle Replacement_Trailer | 0.12 | 182.44 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150825 | Base | Line & Transformer Protection Migration to DNP - Jim Yarrow TS | 0.10407 | 164.32 | System Renewal | Substation Renewal | Brampton | This is part of a multi-phase project to upgrade aging and failure-prone protection systems at Jim Yarrow TS to the current protection standards. Proper protection to transmission lines will provide protection to the assets in the case of faults.
103030 | Base | Technology Upgrades Improving the System Control Room Environment | 0.057256 | 147.52 | General Plant | Information Technology | Multiple | This project will continue to build on the original capital project whose scope was focused on the replacement of computers used as Operator WorkStations. The scope of this program has been expanded to account for all technology purchases required for the Control Room theater.
151108 | Base | Office Equipment | 0.075699 | 143.52 | General Plant | Facilities Management | Guelph | Replace aging equipment within the Guelph operational centre to ensure optimal performance in managing the distribution assets
151245 | M-Factor | Capacitor Bank Installations | 0.041841 | 134.68 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of capacitor bank installation to increase power factor, capacity and reduce losses.
102931 | Base | Paving of 3 MS & TS Station Driveways per year - Annual Multi-year initiative - East | 0.049718 | 125.42 | System Renewal | Substation Renewal | Powerstream | Existing driveways at stations in the East Operating Area (former PowerStream) are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150597 | Base | Lock Box Installs - East | 0.010017 | 115.84 | System Access | Metering | Powerstream | Multi-year project to install lock boxes at ICI properties with restricted access to eliminate need for a customer appointment for access.
101487 | M-Factor | Add one Additional 27.6 kV Cct on Major Mack Dr and 9th Line | 1.325 | 107.71 | System Service | Capacity (Lines) | Powerstream | There are two ccts 12M1/12M3 on Major Mack Dr east of Hwy 48, but only one cct 12M3 goes all the way to 9th Line. The second cct stops half way and is a radial supply. This project is to establish another tie between two ccts on Major Mack and 9th Line. The purpose is to form a supply loop and a new tie between Buttonville TS and MTS2.
150255 | M-Factor | Cable Replacement Project - (B23) - Cundles Rd and Janine St, Barrie | 1.0562 | 99.3 | System Renewal | Underground Asset Renewal | Powerstream
151383 | Base | 2023 GUELPH - Fleet | 0.595 | 98.28 | General Plant | Fleet Renewal | Guelph | Replacement of end of life asset due to poor conditions, high mileage and engine hours and age. Vehicle experiencing more down time at the shop for repairs and maintenance impacting vehicle availability.
150569 | Base | Server OS Upgrades - IT Infrastructure | 0.19265 | 95.22 | General Plant | Information Technology | Multiple | Operating system upgrades to support IT infrastructure.
150737 | Base | Facilities_East Region_Reactive Capital | 0.27493 | 91.88 | General Plant | Facilities Management | Powerstream | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150736 | Base | Facilities_West Region_Reactive Capital | 0.27493 | 91.88 | General Plant | Facilities Management | Horizon | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150734 | Base | Facilities_Central Region_Reactive Capital | 0.27493 | 91.85 | General Plant | Facilities Management | Multiple | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
101393 | M-Factor | Redundant Fibre Path to Aurora MS#4 Sub-Station | 0.49431 | 89.62 | System Service | System Control, Comm'ns & Performance | Powerstream | AMS4 is a major node on the Operations Network, but the fiber optic routes into the AMS4 are not diverse. This major hub is therefore exposed to a single point of failure, and loss of communications to this hub would be very impact. This project is to provide redundant fibre path to Aurora MS to offer increased security and reliability.
150676 | Base | Mobile Devices - IT Infrastructure | 0.010463 | 88.32 | General Plant | Information Technology | Multiple
103171 | Base | Implementation of a new Alectra Network Operations Voice Radio System | 0.025 | 79 | General Plant | Information Technology | Multiple
151018 | M-Factor | Fleet_West_Vehicle_Replacement_Trailer | 0.11 | 49.52 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150747 | M-Factor | Net Zero Energy Emissions | 0.33169 | 34.58 | System Service | Distributed Energy Resources (DER) | Powerstream | The project will help Alectra Utilities to ensure that growing DER challenges are met through building expertise and capability in real time monitoring, integrating and optimizing of DERs in line with customer preferences. This will lead to a system that can safely integrate and optimize value from DERs for the benefit of customers.
151053 | Base | Building Sustainment | 0.19091 | 31.98 | General Plant | Facilities Management | Guelph | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
103065 | Base | Upgrade Advanced Distribution Management System (ADMS) to latest version release. | 0.098265 | 24.76 | General Plant | Information Technology | Powerstream
151160 | M-Factor | Fleet_West_Vehicle Replacement_ Pole Trailer_1-405 | 0.079 | 15.12 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150581 | Base | Analytics\Monitoring Tool IT infrastrucutre rescources | 0.32664 | 13.59 | General Plant | Information Technology | Multiple | Gather requirements, determine available products that meet those requirements and RFP. SOW will include POC of chosen products as well as Professional Services to assist with design, build and implementation.
150583 | Base | OT Server Hardware upgrade OMS/SCADA | 0.33234 | 13.49 | General Plant | Information Technology | Multiple | Hardware refresh for customer facing OMS platform and SCADA architecture .
151031 | Base | Fleet Shop equipment refurbishment and replacement | 0.06 | 12.85 | General Plant | Fleet Renewal | Enersource | For the refurbishment of trailers, shop compressors and hoists to extend the life of the assets instead of replacement to reduce the need fro capital expenditures.
150678 | Base | P&C Specific Tools & Testing Equipment - West | 0.016793 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
102999 | Base | P&C Specific Tools and Testing Equipment | 0.016793 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
102157 | Base | Server Refresh - IT Infrastructure | 0.36224 | 10.1 | General Plant | Information Technology | Multiple | Ongoing server refresh to support applications.

## 2024 Ranking
Project List for Oral Hearing Undertakings
Project Number | Funding | Project Name | 2024 ($MM) | Project Score | Investment Category | Investment Grouping | Rate Zone | Comment
150725 | Base | Lines Central-North - Reactive Renewal | 1.3013 | 181453.58 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have failured and requires replacement in order to restore power to customers
150690 | Base | Lines Central-South - Reactive Renewal | 3.3351 | 171817.68 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have failured and requires replacement in order to restore power to customers
150682 | Base | Remote Fault Indicator Deployment | 0.10035 | 164220.93 | System Service | System Control, Comm'ns & Performance | Multiple | This project consists of remote fault indictor deployment which will result improved outage response, operational efficiency, and reliability
102247 | Base | Interest Capitalization | 1.2646 | 104303.71 | General Plant | Other General Plant | Powerstream
150596 | Base | Meter Renewal - all types but Suite - PowerStream RZ | 0.089146 | 94470.24 | System Access | Metering | Powerstream | Multi-year project to renew existing residential (except suite) metering equipment.
101871 | Base | Services (New and Upgrades) - Layouts – East North - Commercial Services | 0.017017 | 94398.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151180 | Base | Central-North - Capitalization of Locates | 0.025016 | 94387.49 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150600 | Base | Firmware Upgrades for Smart Meters - East | 0.025364 | 94363.34 | System Access | Metering | Powerstream | Multi-year project to renew residential Smart meter firmware to improve communication performance.
151169 | Base | Central-South - Capitalization of Locates | 0.031269 | 94344.62 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
151174 | Base | West Lines - Capitalization locates | 0.031269 | 94319.23 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150631 | Base | Transformer Station Metering - Central North | 0.052993 | 94245.75 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew wholesale metering equipment.
101696 | Base | Subdivision - North Underground Residential Distribution System Final Close out and Inspection. | 0.05076 | 94197.28 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
103381 | Base | East Lines - Capitalization locates | 0.062446 | 94144.61 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101870 | Base | Services (New and Upgrades) - Layouts – East South - Commercial Services | 0.083384 | 94022.15 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101869 | Base | Services (New and Upgrades) - Layouts – East North - New Residential | 0.088432 | 93989.16 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150650 | Base | Replace PCB Risk PT's - Enersource RZ | 0.10531 | 93977.25 | System Access | Metering | Enersource | Multi-year project to replace metering transformers identified with unacceptable levels of PCB's, to prevent hazardous spills.
101919 | Base | New Services (new and upgrades) - Commercial, Industrial and Institutional (ICI) Projects - NORTH | 0.093972 | 93955.31 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150647 | Base | Transformer Station Metering - Enersource RZ | 0.052993 | 93884.28 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew wholesale metering equipment.
151049 | Base | Commercial, Industrial, Institutional, Apartment Connections | 0.14568 | 93829.96 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
101685 | Base | Subdivision - South Underground Residential Distribution System Final Close out and Inspection. | 0.12244 | 93778.29 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150457 | Base | Services (New and Upgrades) - Layouts – St Catharines | 0.20424 | 93519.09 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151162 | Base | Non Recoverable replacement of Distribution Equipment due to accident/vandalism | 0.26543 | 93457.13 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101924 | Base | Mulit Unit Metering for New Buildings NORTH - PowerStream RZ | 0.18822 | 93421.21 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in northern area of territory.
150588 | Base | New Residential Subdivision Development - Alectra West | 0.23387 | 93265.82 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
101791 | Base | New Services - new and upgrades - COMMERCIAL, INDUSTRIAL, INSTITUTIONAL (ICI) SERVICES - SOUTH | 0.2859 | 92878.02 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101812 | Base | Reactive Capital, Alectra East - LIS | 0.26966 | 92710.01 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150754 | Base | Lines Central-North - Non-Recoverable Replacements | 0.37407 | 92705.38 | System Renewal | Reactive Capital | Brampton | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150726 | Base | Lines Central-South - Non-Recoverable Replacements | 0.37407 | 92705.38 | System Renewal | Reactive Capital | Enersource | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
101820 | Base | Reactive Capital, Alectra East - Non-Recoverable Replacement | 0.32508 | 92582.71 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover costs for (i.e. pole hit no vehicle at scene of accicent)
150389 | Base | Services (New and Upgrades) - Layouts – Central North | 0.4459 | 92563.35 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150651 | Base | C & I Metering - Renewal- Brampton RZ | 0.76749 | 92560.77 | System Access | Metering | Brampton | Multi-year project to renew existing ICI metering equipment.
150386 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central North | 0.47799 | 92424.37 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
150453 | Base | CIS CC&B Modifications(Regulatory Enhancements) | 1.84 | 92260.88 | General Plant | Information Technology | Multiple | Enhancements to the CIS (CC&B) application needed to meet any regulatory requirements Such requirements in the past have been Ontario Energy Savings Program (OESP) as well as the Monthly Billing projects.
150649 | Base | Suite Metering - Enersource RZ | 0.578 | 91838.22 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew suite metering equipment.
150654 | Base | C & I Metering - New Services - Brampton RZ | 0.5967 | 91552.85 | System Access | Metering | Brampton | Multi-year project to purchase and install ICI metering equipment on new services.
150595 | Base | C & I and Wholesale Metering - PowerStream RZ | 0.57816 | 91530.35 | System Access | Metering | Powerstream | Multi-year project to purchase, install, and renew ICI and wholesale metering equipment.
101868 | Base | Services (New and Upgrades) - Layouts – East South - New Residential | 0.52753 | 91488.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101795 | Base | Multi Unit Metering for New Buildings SOUTH - PowerStream RZ | 0.56286 | 91273.08 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering in new buildings in southern area of territory.
101873 | Base | Services (New and Upgrades) - Layouts – East North - Residential Upgrades | 0.62027 | 91023.49 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151051 | Base | System Relocations Road Authorities | 0.71922 | 91002.2 | System Access | Road Authority | Guelph | Mandatory - System Access Related Project
150652 | Base | New Residential Subdivision Development - Alectra Central South | 0.46563 | 90948.17 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150388 | Base | Services (New and Upgrades) - Layouts – Central South | 0.85908 | 90774.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150692 | Base | New Feeder in Residential Subdivision Development - Alectra Central North | 0.75664 | 90609.19 | System Service | Capacity (Lines) | Brampton | This expenditure is required to meet the needs of the development community that construct municipal approved residential subdivisions in Alectra Utilities' Central North service territory
150599 | Base | Suite Meter - Reverification - PowerStream RZ | 0.52324 | 90368.15 | System Access | Metering | Powerstream | Multi-year project to renew Measurement Canada seal dates on existing suite metering equipment.
150455 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - St Catharines | 0.92173 | 90201.14 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150659 | Base | Residential Meters - by Metering - Brampton RZ | 0.9131 | 90095.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Metering.
150456 | Base | Services (New and Upgrades) - Layouts – Hamilton | 0.94501 | 89961.61 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150630 | Base | New Residential Subdivision Development - Alectra Central North | 1.187 | 89952.48 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101828 | Base | Reactive Capital, Alectra East - Recoverable Replacement | 0.80105 | 89765.65 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have been damaged causing catastrophic failure by third parties which Alectra Utilities is not able to recover some costs for (i.e. pole hit, vehicle at scene of accicent, Alectra Utilities obtains most of costs (near $0 impact too budget))
101896 | Base | New Institutional/Commercial/Industrial Subdivision Development - Alectra East | 0.95206 | 89347.36 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101872 | Base | Services (New and Upgrades) - Layouts – East South - Residential Upgrades | 0.91892 | 89344.81 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101800 | Base | Reactive Capital, Alectra East - Storm Damage | 1.3398 | 86549 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151047 | Base | Subdivisions | 0.47565 | 85393.33 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
150620 | Base | Metering Renewal - all types - Horizon RZ | 2.2274 | 84064.36 | System Access | Metering | Horizon | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment.
101808 | Base | Reactive Capital, Alectra East - Switchgears | 1.7331 | 83304.08 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
150648 | Base | Metering Renewal - all types but Suite - Enersource RZ | 2.3671 | 82569.47 | System Access | Metering | Enersource | Multi-year project to purchase, install and renew residential (except suite) and ICI metering equipment.
101892 | Base | New Subdivision Development - Secondary Service Lateral - Alectra East | 3.0613 | 80775.74 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150384 | Base | New Service (new and upgrades) - Commercial and Institutional (ICI) Projects - Central South | 3.8313 | 77903.71 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
150449 | Base | Services (New and Upgrades) - Commercial, Industrial and Institutional (ICI) Projects - Hamilton | 5.5039 | 69328.05 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151095 | Base | Reactive Restoration | 1.0894 | 63546.92 | System Renewal | Reactive Capital | Guelph | Replacement of assets which have failured and requires replacement in order to restore power to customers
151301 | Base | Cable Replacement Project - (HAM) - Rymal - Mud - Upper Centennial - Upper Red Hill Valley | 3.3122 | 61747.15 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 8 failures, or 14 failures per 100km. This area includes the 331X & 341X feeders which were identified as a Worst Performing Feeder in 2018. The average cable installation year is 1968 in this project scope.
101824 | Base | Reactive Capital, Alectra East - Distribution Equipment | 5.6612 | 58189.58 | System Renewal | Reactive Capital | Powerstream | Replacement of assets which have failured and requires replacement in order to restore power to customers
151161 | Base | Joint Use Pole Removal | 0.12274 | 57199.8 | System Renewal | Overhead Asset Renewal | Horizon | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
151050 | Base | Metering - all types - Guelph RZ | 0.43177 | 55986.2 | System Access | Metering | Guelph | Multi-year project to purchase, install, and renew residential, ICI and wholesale metering equipment in Guelph RZ.
150469 | Base | ERP JD Edwards Enhancements | 1.3588 | 55714.6 | General Plant | Information Technology | Multiple | Allocation of capital funds to provide 3rd party assistance on capital work, along with creating system enhancements to the JD Edwards ERP and supporting Systems.
150325 | Base | CIS CC&B Enhancements | 1.5874 | 55520.48 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) application to support process improvement requirements.As the CIS (CC&B) system is one of the core applications of the organization, operational enhancements come in from a number of venues and thereby feedback into the other downstream systems. These enhancements are considered for the overall customer and organizational benefits.
101832 | Base | Joint Use Pole Removal | 0.62348 | 54024.42 | System Renewal | Overhead Asset Renewal | Powerstream | This project is for the removal of poles in the field after third party (joint use) attachements have been removed or transferred for projects already closed by Alectra Utilities.
101570 | Base | New Alliston 10MVA Substation - 44 kV Supply | 0.33896 | 50412.78 | System Service | Capacity (Stations) | Powerstream | This project is the 44KV feeder extension to supply Alliston MS (101569)
101571 | Base | New Alliston 10MVA Substation - 13.8 kV Feeder Integration | 0.63717 | 50183.69 | System Service | Capacity (Stations) | Powerstream | This project is the 13.8KV feeder integration for Alliston MS (101569)
101887 | Base | New Residential Subdivision Development - Alectra East | 11.3994 | 44863.95 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
101569 | M-Factor | New Alliston 10MVA Substation - Industrial Parkway | 1.0623 | 44829.96 | System Service | Capacity (Stations) | Powerstream | The project entails the purchase of a station site in the vicinity of Dufferin St and Industrial Pkwy in Alliston, and constructing a new 10MVA, 44/13.8 kV, dual-stage fan, 4-feeder municipal substation
100859 | Base | Switchgear Renewal - East | 3.0655 | 43704.68 | System Renewal | Underground Asset Renewal | Powerstream | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151089 | Base | Overhead Rebuilds | 1.2955 | 39246.49 | System Renewal | Overhead Asset Renewal | Guelph | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
101508 | Base | Transformer Renewal - East | 3.2223 | 37474.31 | System Renewal | Transformer Renewal | Powerstream | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150673 | Base | Road Authority Central (Mississauga) | 4.7271 | 35000.51 | System Access | Road Authority | Enersource | Mandatory - System Access Related Project
151240 | M-Factor | Southgate Dr to Maltby Rd O/H Extension | 0.55781 | 34668.47 | System Service | Capacity (Lines) | Guelph | The road extension from COG and potential developments on Southgate requires two 13.8kV circuit expanded in order to provide capacity and contingency supply.
151238 | Base | New Feeder Maltby Rd W (Crawley to Gordon) | 0.89685 | 34423.41 | System Service | Capacity (Lines) | Guelph | Build new pole line on Maltby Rd between Crawley Rd and Gordon St to back-up radially fed loads on Gordon St south of Clair Rd/Gordon St intersection with 556ASC OH Conductor to replace 3/0ACSR to act a feeder inter-tie.
150645 | Base | Road Authority Central (Brampton) | 5.6018 | 31813.54 | System Access | Road Authority | Brampton | Mandatory - System Access Related Project
150828 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-West | 0.95 | 31592.28 | System Renewal | Overhead Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151452 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-West | 0.955 | 31590.16 | System Renewal | Underground Asset Renewal | Horizon | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
101762 | Base | Road Authority Expenditure PS South | 4.2653 | 31544.34 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
101355 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-East | 0.975 | 31424.67 | System Renewal | Overhead Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151450 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-East | 0.975 | 31424.67 | System Renewal | Underground Asset Renewal | Powerstream | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
150074 | M-Factor | Vaughan TS#2 Bus Differential and Overcurrent Protections Upgrade | 0.31236 | 28627.81 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Vaughan TS#2 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
100340 | M-Factor | Vaughan TS#4 Feeder Integration - Part 3 | 3.5854 | 28489.24 | System Service | Capacity (Lines) | Powerstream | This project is the third part of a multi-part project to construct and integrate new feeders from VTS#4. This project is to integrate four 27.6kV feeders (25M5/25M6/25M7/25M8) from VTS4 to the distribution system.
151363 | Base | Cable Injection Project - (M25) - 14th - McCowan - Steeles - Old Kennedy, Markham | 1.6214 | 27518.58 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 14 failures.
100867 | Base | Pole Renewal - East | 5.7564 | 25595.06 | System Renewal | Overhead Asset Renewal | Powerstream | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
151074 | Base | Reactive renewal | 3.4893 | 25136.12 | System Renewal | Reactive Capital | Horizon | Replacement of assets which have failured and requires replacement in order to restore power to customers
151362 | Base | Cable Injection Project - (M39) - 16th - Warden - Hwy 7 - Woodbine, Markham | 0.92758 | 23713.55 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 8 failures.
151360 | Base | Cable Injection Project - (M31) - 14th - Old Kennedy - Steeles - Warden, Markham | 0.84754 | 23640.66 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 38 failures.
151043 | Base | Transformer Renewal - Central South | 2.022 | 21869.73 | System Renewal | Transformer Renewal | Enersource | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
150071 | M-Factor | Markham TS#2 Bus Differential & Overcurrent Protections Upgrades | 0.082435 | 21087.3 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the Markham TS#2 Bus Differential & Overcurrent Protections Upgrades with new relays having fault recording capabilities.
151303 | Base | Cable Replacement Project - (HAM) - Stone Church - Garth - Lincoln M. Alexander | 0.94333 | 19664.79 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 5 failures, or 18 failures per 100km. The average cable installation year is 1976 in this project scope.
150664 | Base | Residential Meters - by Lines - Brampton RZ | 1.3894 | 18166.54 | System Access | Metering | Brampton | Multi-year project to purchase, install and renew residential metering equipment. Work carried out by Lines.
151109 | Base | Switch Replacement | 0.18649 | 18145.07 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
102455 | Base | Melbourne MS322 Land Purchase & TX Upgrade - Bradford | 0.91603 | 17823.71 | System Service | Capacity (Stations) | Powerstream | This project consists of transformer upgrade to increase the capacity at Melbourne MS to meet the load growth the contingency condition for Bradford area.
151367 | Base | Cable Injection Project - (M21) - Hwy 7 - Markham - 16th - McCowan, Markham | 1.7718 | 17674.76 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 6 failures.
150319 | M-Factor | New MS - Duke MS 20 MVA Substation, Mississauga | 4.2 | 17540.57 | System Service | Capacity (Stations) | Enersource | The Downtown21 plan forecasts a total population of 56,565 residents and 34,247 jobs in the Mississauga downtown core. The current capacity available for the downtown core is approximately 140 MVA ONAN rating. Based on growth projected and the land parcels available, Alectra Utilities estimates that, upon completion of Downtown21 the combined transformation load requirement will increase approximately by 300 MVA. This station will provide 20MVA ONAN capacity.
151104 | Base | Distribution Automation - Central North | 0.52588 | 17389.16 | System Service | SCADA and Automation | Brampton | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151366 | Base | Cable Injection Project - (M19) - Markham - Steeles - McCowan - 14th, Markham | 1.3532 | 17258.97 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 7 failures.
151318 | Base | Cable Injection Project - (I3) -Bovaird - Dixie - Queen - Hwy 410, Brampton | 0.467 | 16118.68 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2014 to 2015 with average duration of 71 minutes.
150639 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-CENTRAL | 0.03986 | 15735.56 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of DC charging system for Central South Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150638 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-East | 0.03986 | 15735.56 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of DC charging system for Central North Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150636 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-North & TS | 0.03986 | 15735.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of installation of DC charging system for East Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
150640 | Base | Purchase and Installation of 4 Station DC System Monitoring-Multi-year initiative-WEST | 0.03986 | 15735.56 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of installation of DC charging system for West Sations. A better real-time assessment of Station batteries will lower the risk of battery failure/fire/explosion
151460 | M-Factor | Cable Injection Project - (V17) - Langstaff - Keele - Rutherford - Dufferin, Vaughan | 1.663 | 15316.59 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 3 failures. From 2015-2019 YTD customers in this area experienced 4 failures.
150285 | Base | Transformer Renewal - Central North | 1.4595 | 14492.05 | System Renewal | Transformer Renewal | Brampton | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
101027 | Base | Switch Renewal - East | 0.73228 | 14308.5 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacment units
100913 | M-Factor | Pole Line Installation Double Cct on Major Mack - Huntington Rd to Hwy 50 | 1.4394 | 14222.63 | System Service | Capacity (Lines) | Powerstream | This project is to build two ccts on Major Mack Dr between Huntington Rd and Hwy 50 in conjunction with the road widening project to supply new customers on both side of Major Mack, as well as customers along Hwy 50.
102098 | Base | Client - IT Infrastructure | 0.56951 | 13761.18 | General Plant | Information Technology | Multiple | To upgrade desktop/laptop/mobile devices that are 5 years or older (Approximately 20% of our equipment). Net new equipment for mobile computing as well as upgrades and replacements for damaged devices. Request made by various business units. This budget also includes RSA tokens\Licenses, monitors, mice, keyboards, docking stations, tablets and small non-MFP printers. Out of Scope: Large MFP Printers
151247 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.685 | 13413.53 | System Renewal | Overhead Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102232 | Base | Capital Funds for Emergency P&C Purchases - East | 0.033969 | 13270.97 | System Renewal | Substation Renewal | Powerstream | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the East Operating Area (former PowerStream). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150683 | Base | Capital Funds for Emergency P&C Purchases - Central North | 0.033969 | 13184.55 | System Renewal | Substation Renewal | Brampton | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central North Operating Area (Brampton). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150685 | Base | Capital Funds for Emergency P&C Purchases - West | 0.033969 | 13184.55 | System Renewal | Substation Renewal | Horizon | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the West Operating Area (former Horizon). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150684 | Base | Capital Funds for Emergency P&C Purchases - Central South | 0.033969 | 13184.55 | System Renewal | Substation Renewal | Enersource | This project provides funds for the emergency procurement of Intelligent Electronic Devices (IED), communications equipment, protective relays, and other critical spare parts for the municipal/transformer substations in the Central South Operating Area (former Mississauga). These parts are critical to maintaining the viability of key operations’ systems and the conformance to the ESA Regulation 22/04. Failure or underperformance of this equipment could cause a catastrophic failure of a key component of the distribution grid.
150360 | M-Factor | New build - Extend 44kV feeder Centre View Dr, Mississauga | 5.5933 | 13005.45 | System Service | Capacity (Lines) | Enersource | A new 44 kV overhead/underground feeder extension is needed to provide supply to downtown Mississauga area on Centre View Drive as well as provide primary supply for Duke Municipal Station (MS).
150784 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.755 | 12968.3 | System Renewal | Overhead Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
151453 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Guelph | 0.78605 | 12922.02 | System Renewal | Underground Asset Renewal | Guelph | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
150823 | Base | Overhead Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.85 | 12654.97 | System Renewal | Overhead Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
102099 | Base | Printer & Copier Fleet Replacement | 0.049451 | 12636.08 | General Plant | Information Technology | Multiple | Replacement of existing fleet of printers/copiers that are 5 or more years old. This will include non-MFP printers. Replacement to be determined by an evaluation of evolving needs and corporate requirements as well as age of equipment.
151449 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central North | 0.915 | 12175.67 | System Renewal | Underground Asset Renewal | Brampton | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
103211 | Base | Misc Software Upgrades (FormScape, AutoCAD, etc.) - IT/OT Infrastructure | 0.02038 | 12020.93 | General Plant | Information Technology | Multiple | Upgrade/ acquire software as required / requested by business.
151451 | Base | Underground Asset Renewal-Alectra Field Distribution System Projects-Central South | 0.95 | 11935.99 | System Renewal | Underground Asset Renewal | Enersource | These are projects which during the course of the year evolve due to customer issues around reliability which cannot wait for execution in the following year due to the impact on customers in terms of either frequency or outages, duration or both.
103180 | Base | Citrix Xen Virtualization Expansion - IT Infrastructure | 0.21165 | 11298.77 | General Plant | Information Technology | Multiple | Client computing virtualization (Citrix) is currently the standard delivery method for applications and desktops at Alectra. This system has had a tremendous uptake in the organization and requires an upgrade in back-end infrastructure to support the additional demand from the business.
150693 | M-Factor | Blockchain | 0.58627 | 11191.63 | System Service | Distributed Energy Resources (DER) | Multiple | The project will prepare Alectra Utilities to engage with customers in a real-time and transparent process to record the flow of electricity to and from DERs, enabling the efficient procurement of distribution benefits, such as demand response and frequency regulation. The project will provide a robust settlement mechanism between Alectra and customers, backed by timely and efficient financial transactions, to enable overall trust and customer value delivery and leading to increased customer satisfaction.
151314 | Base | Cable Injection Project - (G2) -Wanless - Kennedy - Bovaird - Main, Brampton | 0.68887 | 11045.83 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 4 outages due to cable failures from 2013 to 2017 with average duration of 125 minutes.
150665 | Base | Emerging Customer Initiated Work (West) | 1.846 | 10905.1 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
151465 | M-Factor | Cable Replacement - Mississauga Left Behind Cable | 1.7918 | 10856.69 | System Renewal | Underground Asset Renewal | Enersource | This project is to address cables which were part of a cable injection project but were ultimately not injectable at the time of project execution. These 'left behind' segments must be addressed, if they are left in the system they could cause a failure. Customers would not only experience an outage, but question the utilities work practices as we would have addressed only a portion of the cables instead of all the cables which could cause an outage.
101562 | Base | Arc Flash Mitigation Projects | 0.047172 | 10618.95 | System Service | Safety & Security | Powerstream | This project is to mitigate arc flash risk at East stations.
151307 | Base | Cable Injection Project - (HAM) - Upper Sherman - Stone Church - Nebo - Rymal | 0.74786 | 10594.98 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 2 failures, or 5 failures per 100km. The average cable installation year is 1989 in this project scope.
151429 | Base | Cable Injection- 003- AREA36 -Matheson & Kennedy, Mississauga | 1.2528 | 10394.6 | System Renewal | Underground Asset Renewal | Enersource | There are 2 outages, we are injecting a total of 14,907 m of cable for this project, and the average age of the cable is 31 years.
150653 | Base | Road Authority West (St. Catharines) | 1.1859 | 10216.94 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
150615 | Base | Metering Tools & Equipment - Central North | 0.039631 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150616 | Base | Metering Tools & Equipment - Central South | 0.039631 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150613 | Base | Metering Tools & Equipment - East | 0.039631 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
150614 | Base | Metering Tools & Equipment - West | 0.039631 | 9947.21 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
151315 | Base | Cable Injection Project - (G5) - Steeles - Kennedy - Hwy 407 - Main, Brampton | 1.5577 | 9694.62 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 7 outages due to cable failures from 2010 to 2019 with average duration of 109 minutes.
151063 | Base | Pole Renewal - Central South | 2.7499 | 9065.1 | System Renewal | Overhead Asset Renewal | Enersource | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
100886 | Base | Distribution Automation - East | 2.0387 | 9041.12 | System Service | SCADA and Automation | Powerstream | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151298 | Base | Cable Injection Project - (HAM) - Govenors - Old Ancaster | 0.58388 | 8842.48 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 3 failures, or 10 failures per 100km. The average cable installation year is 1989 in this project scope.
101804 | Base | Purchase of Major Tools | 0.37686 | 8158.3 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
151424 | Base | Cable Replacement Project-Miss. Valley & Bloor (15) Mississauga | 9.8721 | 8140.7 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 10,780 m, and the average cable age is 34 years old. There are 32 backlot transformers that we are also replacing.
101488 | Base | Markham TS #5 | 0.44685 | 8116.61 | System Service | Capacity (Stations) | Powerstream | This project is to perform Class EA and purchase land for Markham TS#5 which has been recommended as per the York Region IRRP
151313 | Base | Cable Injection Project - (F5) - Steeles - Main - Hwy 407 - McLaughlin, Brampton | 0.098938 | 7751.39 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 5 outages due to cable failures from 2007 to 2016 with average duration of 80 minutes.
150282 | Base | Switchgear Renewal - Central North | 0.52663 | 7521.14 | System Renewal | Underground Asset Renewal | Brampton | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151361 | Base | Cable Injection Project - (V26) - Teston - Keele - Major Mackenzie - Jane, Vaughan | 1.194 | 7472.7 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 8 failures.
151325 | Base | Cable Replacement Project - (M31) - 14th - Old Kennedy - Steeles - Warden, Markham | 1.1785 | 7411.62 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 38 failures.
150284 | Base | Pole Renewal - Central North | 3.0054 | 7304.65 | System Renewal | Overhead Asset Renewal | Brampton | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
102017 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-North & TS | 0.33814 | 7275.34 | System Service | Safety & Security | Powerstream | This project consists of Sorbweb Oil containment system in East. Protects the environment in the event of a transformer tank rupture
151392 | Base | 2024 GUELPH - Remotely Controlled Switches | 0.43065 | 6956.6 | System Service | SCADA and Automation | Guelph | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
150714 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - Central | 0.077526 | 6819.25 | System Renewal | Substation Renewal | Enersource | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central South Operating Area (former Enersource). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150713 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.077526 | 6819.25 | System Renewal | Substation Renewal | Brampton | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the Central North Operating Area (Brampton). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150715 | Base | MS Transformer Tank and Radiator Reconditioning- Multi-year initiative - West | 0.077526 | 6819.25 | System Renewal | Substation Renewal | Horizon | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the West Operating Area (former Horizon). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150644 | Base | Road Authority West (Hamilton) | 2.1287 | 6689.48 | System Access | Road Authority | Horizon | Mandatory - System Access Related Project
151459 | M-Factor | Cable Injection Project - (V24) - Langstaff - Jane - Rutherford - Keele, Vaughan | 0.73081 | 6509.15 | System Renewal | Underground Asset Renewal | Powerstream | From 2015-2019 YTD customers in this area experienced 0 failures. From 2013-2019 YTD customers in this area experienced 2 failures.
150468 | Base | Meter to Cash auxiliary systems ongoing upgrades - IT/OT Infrastructure | 0.17461 | 6494.96 | General Plant | Information Technology | Multiple | Enhancement to CIS (CC&B) Meter to Cash ancillary systems to support process improvement requirements. Ancillary systems but not limited to upgrading FW, MV90, LPSS. These enhancements are considered for the overall customer and organizational benefits.
151044 | Base | Switch Renewal - Central South | 0.28758 | 6318.96 | System Renewal | Overhead Asset Renewal | Enersource | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
103659 | Base | Storm Hardening - Four-Circuit Poles | 2.1719 | 6254.52 | System Renewal | Overhead Asset Renewal | Powerstream
100459 | Base | New Barrie 20MVA Substation - Harvie - 44 kV Supply | 0.0041218 | 6215.37 | System Service | Capacity (Stations) | Powerstream | This project consists of 44KV feeder extension to supply for Harvie MS project (101452)
150514 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear Initiative-WEST | 0.35101 | 6213.41 | System Service | Safety & Security | Horizon | This project consists of Sorbweb Oil containment system in West. Protects the environment in the event of a transformer tank rupture
151336 | Base | Cable Replacement Project - (BA22) - Sunnidale and Anne, Barrie | 3.8566 | 6208.17 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 2 failures in 2019.
151305 | Base | Cable Injection Project - (HAM) - Stone Church - Upper Sherman - Rymal - Upper Wellington | 0.71046 | 6019.14 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 1 failure, or 3 failures per 100km. The average cable installation year is 1989 in this project scope.
151086 | Base | Insulator Replacements | 0.088978 | 5948.6 | System Renewal | Overhead Asset Renewal | Guelph | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
100461 | Base | New Barrie 20MVA Substation - Harvie - 13.8kV Feeder Integration | 0.028851 | 5856.18 | System Service | Capacity (Stations) | Powerstream | This project consist of 13.8KV feeder integration for Harvie MS project (101542)
151463 | M-Factor | Cable Injection Project - (F4-G4) - Main - Steeles - Chinguacousy - Queen, Brampton | 0.72699 | 5559.84 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 86 failures. Exact number of failures in recent years is unknown at this moment.
150337 | Base | Switch Renewal - West | 0.46394 | 5475.59 | System Renewal | Overhead Asset Renewal | Horizon | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
151055 | Base | Major Tools | 0.080346 | 5431.72 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
150598 | Base | Suite Metering - Renewals & Retrofits - PowerStream RZ | 0.36857 | 5394.14 | System Access | Metering | Powerstream | Multi-year project to purchase and install suite metering equipment in existing buildings upgraded from bulk metering.
150515 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-CENTRAL | 0.35101 | 5352.14 | System Service | Safety & Security | Enersource | This project consists of Sorbweb Oil containment system in Central South. Protects the environment in the event of a transformer tank rupture
150516 | Base | Sorbweb Oil Containment Systems - 4 Transformers -Multiyear initiative-EAST | 0.35101 | 5352.14 | System Service | Safety & Security | Brampton | This project consists of Sorbweb Oil containment system in Central North. Protects the environment in the event of a transformer tank rupture
150336 | Base | Transformer Renewal - West | 0.70771 | 5293.52 | System Renewal | Transformer Renewal | Horizon | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
151306 | Base | Cable Injection Project - (HAM) - Upper Wentworth - Lincoln M. Alexander - Upper Ottawa - Stone Church | 0.52639 | 5236.89 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 2 failures, or 8 failures per 100km. The average cable installation year is 1988 in this project scope.
150750 | Base | Lines Central-North - Major Tools | 0.099361 | 5234.11 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
151432 | Base | Cable Injection- 007- AREA 43 & 51- Hurontario & Derry Rd W, Mississauga | 1.3799 | 5149.22 | System Renewal | Underground Asset Renewal | Enersource | There are 3 outages, we are injecting a total of 16,419 m of cable for this project, and the average age of the cable is 28 years.
150009 | Base | Insulator Renewal - East | 0.2507 | 5107.82 | System Renewal | Overhead Asset Renewal | Powerstream | Replacement of non-polymer insulators (Areas are prioritized by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
151203 | Base | Capital Corrective Equipment Replacement - Stations South West | 0.06 | 4921.2 | System Renewal | Substation Renewal | Guelph | This project is intended to provide capital for all unplanned station equipment replacements in the South West Operating Area (Guelph) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
102042 | Base | Purchase and Installation of Animal Guards at Various Stations-Annual Multi-year initiative-North & TS | 0.016728 | 4893.56 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of animal guard installation in East
151083 | Base | Switchgear Renewal - West | 0.44934 | 4683.89 | System Renewal | Underground Asset Renewal | Horizon | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
151010 | Base | Switch Renewal - Central North | 0.68949 | 4603.75 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of gang-operated (3 phase) load break switches that can no longer be maintained and are no longer operable with new manual replacement units
150720 | Base | Lines Central-South - Major Tools | 0.23379 | 4591.27 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
151461 | M-Factor | Cable Injection Project - (V51) - Langstaff - Kipling - Hwy 7 - Hwy 27, Vaughan | 0.67168 | 4537.27 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 1 failure. From 2015-2019 YTD customers in this area experienced 5 failures.
151364 | Base | Cable Injection Project - (V23) - Hwy 7 - Keele - Langstaff - Jane, Vaughan | 0.6615 | 4381.14 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 2 failures.
151021 | Base | Insulator Renewal - Central North | 0.39792 | 4235.99 | System Renewal | Overhead Asset Renewal | Brampton | Replacement of non-polymer insulators (Areas are prioritiezed by insulators showing signs of defects), with modern polymer style insulators, we reduce pole fires and insulator flashovers. this will also drive efficiencies as insulator washing will no longer be required once all non-polymer insulators are replaced.
150674 | Base | Emerging Customer Initiated Work Central (Brampton) | 0.18233 | 4183.83 | System Access | Customer Connections | Brampton | Mandatory - System Access Related Project
101763 | Base | Unforeseen Projects Initiated by the customer PS North | 0.14296 | 4161.34 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
150679 | M-Factor | Alectra Drive for the Workplace | 0.1672 | 3997.47 | System Service | Capacity (Lines) | Multiple | Alectra Drive for the Workplace will demonstrate the value of integrating smart electric vehicle (EV) charging system at workplaces into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. The planned investment will help manage the flow of electricity needed to serve the building and EV charging stations, so that electricity costs are minimized for commercial customers while EV drivers have an easy and accessible charging solution.
150367 | M-Factor | Mini-Orlando MS 27.6kV Land Purchase, Mississauga | 2.1561 | 3726.8 | System Service | Capacity (Stations) | Enersource | Mini-Orlando MS is situated on leased land in the area of Mavis Road, south of Highway 401, provides capacity for the commercial and industrial customers in the Heartland area
102075 | Base | Major repairs, refurbishment, or modifications to switches/switchgear | 0.10582 | 3702.48 | System Renewal | Underground Asset Renewal | Powerstream | Switchgear and Switches in stores that repair/refurbishment of the units can allow them to be returned to service
150329 | M-Factor | Rear Lot Renewal Project - Main Street / Unionville / Carlton | 2.486 | 3599.28 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 1 outages lasting an 1hr 40 minutes per year based on a 3 year average.
150498 | Base | Capital Corrective Equipment Replacement - Stations Central South | 0.28382 | 3534.76 | System Renewal | Substation Renewal | Enersource | This project is intended to provide capital for all unplanned station equipment replacements in the Central South Operating Area (former Enersource) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150499 | Base | Capital Corrective Equipment Replacement - Stations Central North | 0.28382 | 3534.76 | System Renewal | Substation Renewal | Brampton | This project is intended to provide capital for all unplanned station equipment replacements in the Central North Operating Area (Brampton) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
150497 | Base | Capital Corrective Equipment Replacement - Stations West | 0.28382 | 3534.76 | System Renewal | Substation Renewal | Horizon | This project is intended to provide capital for all unplanned station equipment replacements in the West Operating Area (former Horizon) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
101542 | M-Factor | New Barrie 20MVA Substation - Harvie | 1.3694 | 3447.05 | System Service | Capacity (Stations) | Powerstream | The project entails the purchase of a station site in the vicinity of Harvie Road and Veterans Drive in Barrie and constructing a new 44/13.8kV, 20MVA, 4-feeder municipal substation.
150353 | M-Factor | Truscott Plaza - Additional capacity, Mississauga | 1.0396 | 3353.44 | System Service | Capacity (Lines) | Enersource | This project is to provide 27.6 KV capacity to supply developments in Truscott areas as the existing 4.16kV does not provide service size
150672 | Base | Burden Allocation - System Service | 0.11842 | 3353.13 | System Service | Capacity (Lines) | Horizon
150263 | Base | Cable Replacement Project - East Left Behind Cable | 1.575 | 3237.07 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in these areas have experienced 11 failures.
102065 | Base | Capital Corrective Equipment Replacement - East | 0.35176 | 3161.46 | System Renewal | Substation Renewal | Powerstream | This project is intended to provide capital for all unplanned station equipment replacements in the East Operating Area (former PowerStream area) that occur due to unexpected or run to failure equipment failures. This project improves response time as well as administration work as the work order and funds are pre-approved. The risk increases significantly when a piece of failed equipment is not available for service. These assets need to have spares readily available in order to quickly replace the failed asset and mitigate the impact of failure on customer reliability.
151297 | Base | Cable Replacement Project - (HAM) - Govenors - Old Ancaster | 0.99443 | 3147.62 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 3 failures, or 10 failures per 100km. The average cable installation year is 1957 in this project scope.
150611 | Base | Transformer Tank and Radiator Reconditioning- Multi-year initiative - East | 0.17291 | 3116.96 | System Renewal | Substation Renewal | Powerstream | This project is intended for corrosion mitigation of station power transformer main tanks and cooling radiators in the East Operating Area (former PowerStream). It also prevents oil from leaking out of failed tanks and radiators due to corrosion. Preventing the main tank and radiators from corrosion extends the useful life of the unit and improves the reliability to customers.
150623 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-WEST | 0.0055333 | 3095.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of animal guard installation in West
150622 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-CENTRAL | 0.0055333 | 3093.04 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Animal guard at Central South Stations
150621 | Base | Purchase and Installation of Animal Guarding-Annual Multi-year initiative-EAST | 0.0074507 | 3081.51 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of installation of Animal guard at East Stations
151426 | Base | Cable Replacement Project-Southdown & Lakeshore (35), Mississauga | 6.8498 | 3019.59 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 3 outages, the length is 8,126 m, and the average cable age is 48 years old. There are 62 backlot transformers that we are also replacing.
151286 | Base | Cable Replacement Project - (H2) - Wanless - Heart Lake - Bovaird - Kennedy, Brampton | 0.35875 | 2867.55 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 6 outages due to cable failures from 2011 to 2017 with an average duration of 126 minutes
101625 | Base | Cyber Security Audit & Upgrades | 0.075326 | 2865.1 | General Plant | Information Technology | Multiple | This project would fund various activities and countermeasures to improve the cyber security posture of the Operations' Network. This will be a mandate for compliance to Ontario Cyber Security framework. The counter measures include: - an annual audit of the cyber security countermeasures in place; - implementation of new technologies to seal identified compromises; - replacement of deployed cyber security equipment deemed end of life or not able to deliver an expected level of service.
150525 | Base | Security Additions & Enhancements | 0.25325 | 2842.12 | General Plant | Information Technology | Multiple | details refer to PWC doc
150671 | Base | Burden Allocation - System Renewal | 1.9296 | 2831.23 | System Renewal | Other System Renewal | Horizon
150632 | Base | AMI Gatekeeper Expansion - Brampton RZ | 0.030233 | 2820.22 | System Access | Metering | Brampton | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
151422 | Base | Cable Replacement Project-Queen St W & Paisley (30), Mississauga | 1.5333 | 2819.61 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 3,992 m, and the average cable age is 36 years old.
151365 | Base | Cable Injection Project - (V02) - Atkinson and Worth, Vaughan | 0.37283 | 2765.48 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 1 failure.
151340 | Base | Cable Replacement Project - (V29) - Hwy 7 - Jane - Steeles - Weston, Vaughan | 4.2773 | 2593.62 | System Renewal | Underground Asset Renewal | Powerstream | From 2013-2018 customers in this area experienced 5 failures.
150332 | M-Factor | Non-Wires Alternative Pilot | 0.83813 | 2536.94 | System Service | Capacity (Stations) | Powerstream | The project will provide customers with increased flexibility to make decisions about their electricity consumption, generation, and costs; it leads to more efficient integration of DERs which yields greater benefits to customer, system reliability, and power quality. This project will also provide the opportunity to increase operational efficiency and improved asset management to enhance service to customer and defer and/or reduce infrastructure investment needs in York Region.
151421 | Base | Cable Replacement Project-Rathkeale Rd & Edenrose St (6), Mississauga | 2.81 | 2502.05 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 6 outages, the length is 8,577 m, and the average cable age is 31 years old.
150580 | Base | West Region Tools and Test Equipment | 0.21165 | 2494.28 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
150627 | Base | Station Equipment Temperature Monitoring-EAST | 0.079471 | 2479.48 | System Service | System Control, Comm'ns & Performance | Brampton | This project consists of Station Temperature Monitoring system in Central North and it enables controlled emergency loading beyond the nameplate rating.
150629 | Base | Station Equipment Temperature Monitoring-WEST | 0.079471 | 2479.48 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of Station Temperature Monitoring system in West and it enables controlled emergency loading beyond the nameplate rating.
151202 | Base | Purchase of Major Station Tools - Multi-year | 0.01 | 2472.82 | General Plant | Tools, Shop and Garage Equipment | Guelph | Replacement of Capital tools required to perform work
150625 | Base | Purchase of Major Tools - Muliti Year-CENTRAL | 0.022646 | 2395 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
150624 | Base | Purchase of Major Tools - Muliti Year-EAST | 0.022646 | 2395 | General Plant | Tools, Shop and Garage Equipment | Brampton | Replacement of Capital tools required to perform work
150626 | Base | Purchase of Major Tools - Muliti Year-WEST | 0.022646 | 2395 | General Plant | Tools, Shop and Garage Equipment | Horizon | Replacement of Capital tools required to perform work
101761 | Base | Unforeseen Projects Initiated by the customer PS South | 0.45911 | 2365.48 | System Access | Customer Connections | Powerstream | Mandatory - System Access Related Project
151435 | Base | Cable Injection- 010 - Area 56- Derry Rd W & Ninth Line, Mississauga | 1.3054 | 2307.05 | System Renewal | Underground Asset Renewal | Enersource | There are 3 outages, we are injecting a total of 45,837 m of cable for this project, and the average age of the cable is 30 years.
151425 | Base | Cable Replacement Project-Rathburn Rd E & Tomken (10), Mississauga | 1.3631 | 2294.54 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 10 outages, the length is 3,180 m, and the average cable age is 38 years old.
151290 | Base | Cable Replacement Project - (I3) - Bovaird - Dixie - Queen - Hwy 410, Brampton | 0.72555 | 2280.06 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 8 outages due to cable failures from 2007 to 2018 with average duration of 133 minutes.
150084 | M-Factor | Markham TS#2 T1/T2 "B" Differential Protections Upgrade | 0.11765 | 2269.53 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is to upgrade the T1/T2 GEC solid state Transformer "B" Differential Protection relays at Markham TS#3 with new relays having fault recording capabilities
151396 | Base | 2024 GUELPH - Transite Underground Duct Replacement | 0.28918 | 2252.14 | System Renewal | Underground Asset Renewal | Guelph | Replacement of Duct Structure which contains asbestoes a known carcinogen and impacts worker safety.
151244 | Base | Fault Indicators | 0.018 | 2243.02 | System Service | System Control, Comm'ns & Performance | Guelph | The scope of this project is to install Fault Indicators in Guelph. The project would include the fault indicators communicating to the existing SCADA and will improve the fault locating and improve SAIDI
151181 | Base | Cable Replacement Project - Left Behind Cable, Brampton | 0.525 | 2163.34 | System Renewal | Underground Asset Renewal | Brampton | This project is to address cables which were part of a cable injection project but were ultimately not injectable at the time of project execution. These 'left behind' segments must be addressed, if they are left in the system they could cause a failure. Customers would not only experience an outage, but question the utilities work practices as we would have addressed only a portion of the cables instead of all the cables which could cause an outage.
151423 | Base | Cable Replacement Project-Old Carriage Road (33), Mississauga | 1.3717 | 2103.57 | System Renewal | Underground Asset Renewal | Enersource | Since 2005, there have been 5 outages, the length is 2,229 m, and the average cable age is 45 years old.
150096 | M-Factor | Vaughan TS#2 T1/T2 "B" Differential Protections Upgrade | 0.095821 | 2074.26 | System Service | System Control, Comm'ns & Performance | Powerstream | Vaughan TS#2 T1/T2 "B" Differential Protections Upgrade
151338 | Base | Cable Replacement Project- (BA15) - Burton - Huronia - Little - Bayview, Barrie | 3.1787 | 2062.55 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 41 years old and will be 46 when project starts (2024).
150675 | Base | Emerging Customer Inititated Work Central (Mississauga) | 0.2026 | 2049.12 | System Access | Customer Connections | Enersource | Mandatory - System Access Related Project
101764 | Base | Road Authority Expenditure PS North | 1.7004 | 2038.3 | System Access | Road Authority | Powerstream | Mandatory - System Access Related Project
150604 | Base | Smart Meter Network Expansion - PowerStream RZ | 0.2968 | 2035.93 | System Access | Metering | Powerstream | Multi-year project to expand and upgrade AMI field communication equipment to service new connections.
151092 | Base | Distribution Automation - Central South | 0.78634 | 2013.5 | System Service | SCADA and Automation | Enersource | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151030 | Base | Addition of Sensors to SCADA Controllable 44kV LISs in Brampton | 0.27368 | 2012.97 | System Service | System Control, Comm'ns & Performance | Brampton | This project is to add sensors to the 44KV switches in Central North
150694 | M-Factor | Cityview microgrid enhancements | 0.015652 | 1985.17 | System Service | Capacity (Lines) | Powerstream | The project is to understand how microgrids can be integrated into the distribution grid in a safe and reliable manner. The microgrid is used to evaluate integration and connection to the distribution grid, while reducing the building's load, greenhouse gas emissions, and increasing its resiliency to grid outages.
150670 | Base | SCADA FDIR | 0.12603 | 1798.98 | System Service | SCADA and Automation | Multiple | Fault Detection, Isolation, and Restoration implementation, next generation of distribution automation technology. This utilizes devices which are already automated and integrates them into the OMS system such that devices perform self healing after a fault. in some cases reducing the outage time to less then 1 minute.
150539 | Base | Cyber Security Devices Upgrades | 0.57072 | 1788.51 | General Plant | Information Technology | Multiple | This project upgrades security tools to maintain compliance with OEB Cyber Security Framework
150680 | M-Factor | Alectra Drive at Home | 0.6032 | 1731.44 | System Service | Capacity (Lines) | Multiple | Alectra Drive at Home will demonstrate the value of integrating smart electric vehicle (EV) charging system in multi rise buildings as well as residential homes into the distribution grid such that mass uptake of electric vehicles can be managed in a safe and reliable manner. It will also provide insight into the characteristics of EV Charging, how EVs can be aggregated and controlled to provide the benefit at the local, regional and provincial system levels, and customer response to these control and optimization strategies.
151201 | Base | Purchase of New Critical Spare Parts - Guelph | 0.01 | 1727.97 | System Renewal | Substation Renewal | Guelph | This project involves procurement of critical spare parts for stations in the South West Operating Area (Guelph) so as to facilitate prompt repair of failed assets during emergency situations.
150619 | Base | Purchase of Critical Spare Parts - West | 0.022873 | 1648.51 | System Renewal | Substation Renewal | Horizon | This project involves procurement of critical spare parts for stations in the West Operating Area (former Horizon) so as to facilitate prompt repair of failed assets during emergency situations.
151136 | Base | C55 Alectra: Optimization of Business Practices | 0.107 | 1624.9 | General Plant | Information Technology | Multiple | Optimizing the current software to communicate with other systems such as the ERP will allow for more efficient and effective budgeting processes and consolidation of information allowing for consistent reporting of the information from one system.
150642 | Base | Proactive Replacement of Remote Terminal Units - Central North | 0.16586 | 1582.3 | System Renewal | Substation Renewal | Brampton | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the Central-North Operating Area (Brampton). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
150617 | Base | Purchase of Critical Spare Parts - Central North | 0.030573 | 1568.76 | System Renewal | Substation Renewal | Brampton | This project involves procurement of critical spare parts for municipal stations in the Central North Operating Area (Brampton) so as to facilitate prompt repair of failed assets during emergency situations.
151332 | Base | Cable Replacement Project - (BA20) - Bayfield and Simcoe, Barrie | 2.0338 | 1564.86 | System Renewal | Underground Asset Renewal | Powerstream | Customers in this area have experienced 0 failures to date. Cable is 43 years old and will be 48 when project starts (2024).
151087 | Base | Switchgear Replacement | 0.25736 | 1559.43 | System Renewal | Underground Asset Renewal | Guelph | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150618 | Base | Purchase of Critical Spare Parts - Central South | 0.036234 | 1556.59 | System Renewal | Substation Renewal | Enersource | This project involves procurement of critical spare parts for stations in the Central South Operating Area (former Enersource) so as to facilitate prompt repair of failed assets during emergency situations.
102077 | Base | Major repair, refurbishment, or conversions of distribution transformers | 0.031747 | 1540.55 | System Renewal | Transformer Renewal | Powerstream | Transformers returned or in stores where repair/refurbishment of the unit can return it to service at a lower cost then purchase of a new unit
150398 | M-Factor | Rear Lot Renewal Project - Strathcona Dr | 0.94487 | 1536.61 | System Renewal | Rear Lot Conversion | Horizon | This area has had an average of 44 outages lasting 0.35hrs per year based on 3 year average.
151222 | Base | Concrete Structures | 0.20659 | 1469.44 | System Renewal | Underground Asset Renewal | Guelph | Replacement of lids on civil structures to avoid public risk
150334 | Base | Distribution Automation - West | 0.78634 | 1424.45 | System Service | SCADA and Automation | Horizon | Installation of remote operable switches and switchgear, overlaping as much as possible switches that are end of life. These devices will directly impact the duration of outages as they allow for faster outage detection and fault finding. Furthermore, as many devices deployed as possible will have additional protection enabled to limit the number of customers effected by the outage in the first place
151052 | Base | Emerging Customer Initiated Work - Relocations | 0.10006 | 1412.11 | System Access | Customer Connections | Guelph | Mandatory - System Access Related Project
151308 | Base | Cable Injection Project - (HAM) - Hollybush - Parkside - Dundas - Spring Creek | 0.11531 | 1389.43 | System Renewal | Underground Asset Renewal | Horizon | From 2010-2018 YTD customers in this area experienced 1 failure, or 5 failures per 100km. The average cable installation year is 1988 in this project scope.
150751 | Base | Facilities_East_Capital Replacement Investment Support | 0.069647 | 1374.32 | General Plant | Facilities Management | Powerstream | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150965 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-256 | 0.46 | 1370.9 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150982 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-299 | 0.46 | 1370.9 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150335 | Base | Pole Renewal - West | 3.1763 | 1338.4 | System Renewal | Overhead Asset Renewal | Horizon | This project involves the replacement of poles that either by testing or visual inspection in accordance with the ACA are in very poor or poor condition and must be replaced
151374 | Base | Cable Replacement - (893) - Janefield Ave Subdivision, Guelph | 0.61733 | 1324.84 | System Renewal | Underground Asset Renewal | Guelph
151388 | Base | Cable Replacement - (724) - 30 Hadati Rd, Guelph | 0.7606 | 1302.79 | System Renewal | Underground Asset Renewal | Guelph
151291 | Base | Cable Replacement Project - (I4) - Queen - Dixie - Steeles - Hwy 410, Brampton | 1.4805 | 1302.23 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 0 cable failure to date. Cables are 41 to 42 years old and beyond EUL.
150963 | Base | Fleet_West_Vehicle Replacement_ Bucket Truck 1-224 | 0.56 | 1298.62 | General Plant | Fleet Renewal | Horizon | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150738 | Base | Facilities_West_Capital Replacement Investment Support | 0.50803 | 1289.1 | General Plant | Facilities Management | Horizon | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150330 | M-Factor | Rear Lot Renewal Project - Marsdale, St.Catharines | 2.0204 | 1284.11 | System Renewal | Rear Lot Conversion | Horizon | This area has had an average of 19 outages lasting 1hr per year based on 3 year average.
150355 | M-Factor | Voltage Conversion - Elmwood MS, Hamilton | 2.8196 | 1274.55 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 23 outages and had 251,178 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
102241 | Base | Proactive Replacement of Remote Terminal Units - East | 0.10588 | 1239.66 | System Renewal | Substation Renewal | Powerstream | This project involves replacement of end-of-life remote terminal units and communications equipment at stations in the East Operating Area (former PowerStream). Replacement equipment can be leveraged to allow for Smart Grid initiatives such as quicker fault detection and automatic isolation and restoration. If existing equipment were to fail, the ability to remotely monitor and control switching devices would be lost, thus risking longer interruptions.
150323 | M-Factor | Station Switchgear Replacement - Bloor MS38 LV1 | 0.69081 | 1228.09 | System Renewal | Substation Renewal | Enersource | Bloor MS is centrally located, supplying a large number of customers, and reliability is very important. This switchgear is non-arc-resistant and poses a potential safety hazard to Alectra personnel and even to the general public who happen to be in the vicinity of the station during a failure event. The circuit breakers that are housed in the switchgear prone to failure and are considered obsolete (no longer supported by the manufacturer and parts are difficult to come by). Obsolescence translates into more frequent and more lengthy maintenance requirements and longer outage duration in the event of a failure. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted reactive capital expenditure.
151064 | Base | Secondary Pedestals -St. Catharines | 0.21227 | 1153.93 | System Service | Safety & Security | Horizon | This project involves the replacment of above grade steel secondary pedestals which pose a safety risk to the general public
101125 | Base | Lines Mobile Equipment - IT/OT Infrastructure | 0.076963 | 1119.08 | General Plant | Information Technology | Multiple | This budget covers the deployment of mobile technology - laptops/field tablets and accessories - within the Lines Department to gain efficiencies in field operations. By deploying this technology, the Lines area can move away from a paper-based to a more electronic environment. In future, it is envisioned that, for example, mobile applications will facilitate the electonic transmission of work orders and electronic record keeping (asset tracking, tailboards, switching orders, timesheets). This will allow for streamlined operational processes and record-keeping, thereby supporting corporate technological initiatives such as the GIS, Outage Management System, and future Workforce Management system. At present, all Lines Management personnel and Subforemen have laptops, facilitating activities such as viewing of the GIS, electronic Asset Tracking Forms, and use of OMS Responder Mobile. Expenditures in this area will allow for more deployment of field devices among Lines crews and for the implementation of more computerized processes.
151204 | Base | Upgrade to Station Facilities (Buildings/Civil work) Multi-year | 0.01 | 1089.29 | General Plant | Facilities Management | Guelph | This project involves work involving structural components of stations, including windows, brickwork, roofs, foundations, drainage, doors, etc. at stations in the SouthWest Operational Area. Not keeping up with this work would result in advanced deterioration resulting in even greater maintenance costs, potential safety concerns and potential failure of the electrical equipment in the building causing power interruptions.
151003 | Base | Fleet_West_Vehicle Replacement_Pickups | 0.057 | 1041.55 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150354 | M-Factor | Voltage Conversion - Eastmount MS, Hamilton | 3.752 | 1021.7 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 43 outages and had 2,261,630 minutes of interruption. The station assets are in very poor and poor condition and if this project does not proceed station renewal costs will be incurred to ensure the station does not fail.
151091 | Base | Switchgear Renewal - Central South | 3.9317 | 982.44 | System Renewal | Underground Asset Renewal | Enersource | Replacement of switchgear that is tracking, has some level of device failure (non-operable)
150380 | M-Factor | Rear Lot Renewal Project - Gunn/Oakley Park/St.Vincent | 1.8 | 966.87 | System Renewal | Rear Lot Conversion | Powerstream | This area has had an average of 1 outage lasting 13hrs per year based on a 3 year average.
151159 | Base | Fault Indicator Installation and Replacement - Hamilton and St. Catharines | 0.29195 | 966.07 | System Service | System Control, Comm'ns & Performance | Horizon | This project consists of fault indicator installation in West
150628 | Base | Station Equipment Temperature Monitoring-CENTRAL | 0.080381 | 965.25 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of Station Temperature Monitoring system in Central South and this enables controlled emergency loading beyond the nameplate rating.
150947 | Base | Fleet_West_Vehicle Replacement_ Pickups | 0.057 | 952.45 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151065 | Base | Manhole Lid Replacement | 0.37153 | 925.3 | System Renewal | Underground Asset Renewal | Horizon | Replacement of lids on civil structures to avoid public risk
151279 | Base | Cable Injection Project - (SCH) - Jacobson - Chestnut - Woodcrest | 0.12859 | 866.07 | System Renewal | Underground Asset Renewal | Horizon | Customers in this area have experienced 0 underground XLPE cable outages to date. The average cable installation year is 1991. Since this project is in 2024, the cable will now be 8 years over the TUL while simultaneously pushing the boundary of Area 2 as a candidate for injection (see Figure A10 - 8: XLPE Cable by Type in Exhibit 04, Tab 01, Schedule 01, Appendix A10, Page 14)
150904 | Base | Fleet East Yearly Light and Misc equipment | 0.02 | 846.86 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150698 | Base | Station Switchgear Replacement - City Centre South MS61 LV1 | 0.42073 | 843.66 | System Renewal | Substation Renewal | Enersource | City Centre South MS is located centrally adjacent to Square One shopping mall, and feeds a large number of customers. Therefore, reliability is very important. This project involves replacing the existing LV1 13.8 kV switchgear with new arc-rated switchgear and new circuit breakers. It also includes upgrading the transformer protection and replacing end-of-life feeder egress cables. The existing equipment line-up is technically obsolete, poses safety and environmental risks, and is prone to failure. Proactive replacement of the existing equipment is a prudent strategy as system reliability would be greatly affected in the event of a failure. Additionally, the restoration of the system to normal conditions could take 8-10 months due to long equipment lead times.
151285 | Base | Cable Replacement Project - (G2) - Wanless - Kennedy - Bovaird - Main, Brampton | 0.7602 | 841.27 | System Renewal | Underground Asset Renewal | Brampton | Customers in this area experienced 1 outage due to cable failure in 2007 with duration of 82 minutes. The cables are 41 to 43 years old and beyond EUL.
150746 | Base | Facilities_Central_Capital Replacement Investment Support | 0.46001 | 807.27 | General Plant | Facilities Management | Multiple | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
151469 | M-Factor | Cable Replacement Project - (F4-G4) - Main - Steeles - Chinguacousy - Queen, Brampton | 0.9804 | 804.25 | System Renewal | Underground Asset Renewal | Brampton | From 2000-2018 customers in this area experienced 86 failures. Exact number of failures in recent years is unknown at this moment.
151466 | M-Factor | Cable Replacement Project - (V24) - Langstaff - Jane - Rutherford - Keele, Vaughan | 0.98581 | 800.33 | System Renewal | Underground Asset Renewal | Powerstream | From 2015-2019 YTD customers in this area experienced 0 failures. From 2013-2019 YTD customers in this area experienced 2 failures.
151468 | M-Factor | Cable Replacement Project - (V51) - Langstaff - Kipling - Hwy 7 - Hwy 27, Vaughan | 0.98784 | 798.87 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 1 failure. From 2015-2019 YTD customers in this area experienced 5 failures.
151431 | Base | Cable Injection- 006- AREA 39- Erin Mills Pkway & Thomas St, Mississauga | 1.3744 | 786.04 | System Renewal | Underground Asset Renewal | Enersource | There are 0 outages, we are injecting a total of 38,448 m of cable for this project, and the average age of the cable is 30 years.
101622 | Base | DACS Inverters and RTU's removal - East | 0.027952 | 765.32 | System Renewal | Substation Renewal | Powerstream | This project involves removal of obsolete and out-of-service DACs inverters, RTUs and associated wiring at stations in the East Operating Area (former PowerStream) so as to remove clutter, thus simplifying future work and freeing up space for future station upgrades.
101632 | Base | Obsolete Revenue Metering Removal from TSs | 0.02925 | 739.84 | System Service | Safety & Security | Powerstream | Evolution of the distribution system to permit more efficient integration of DERs to yield 18
150979 | M-Factor | Fleet East Vehicle replacement - Extended Vans | 0.23805 | 737.95 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150996 | Base | Fleet East Vehicle replacement - Pickup truck 1500 | 0.16716 | 729.23 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151467 | M-Factor | Cable Replacement Project - (V17) - Langstaff - Keele - Rutherford - Dufferin, Vaughan | 2.4213 | 702.73 | System Renewal | Underground Asset Renewal | Powerstream | From 2017-2019 YTD customers in this area experienced 3 failures. From 2015-2019 YTD customers in this area experienced 4 failures.
151082 | Base | SCADA Infrastructure | 0.14662 | 688.19 | System Service | System Control, Comm'ns & Performance | Guelph
151191 | Base | Facilities_Reno_Nebo - Service Centre Upgrades | 0.11574 | 685.17 | General Plant | Facilities Management | Horizon | Repairs to building envelop/walls to prevent further damage to the build infrastructure and systems that are supporting critical operational systems such as control rooms, server rooms, customer services groups, etc.
151058 | Base | Distribution Transformer Replacements & Upgrades | 0.37191 | 682.68 | System Renewal | Transformer Renewal | Guelph | Alectra Utilities will replace transformers proactively when they are found to be in a condition that introduces an unacceptable safety risk to the public, or to the environmental, (e.g., corroded or damaged enclosure that may expose the public to energized components), or risk of environmental contamination, (e.g., leaking oil), are of obsolete vintage construction, are consistently overloaded, or are configured in a way that increases the likelihood of a lengthy outage due to difficult replacement.
151005 | Base | Fleet_West_Vehicle Replacement_Cargo Van | 0.057 | 674.03 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150669 | Base | Burden Allocation - System Access | 0.7029 | 669.62 | System Access | Customer Connections | Horizon | Mandatory - System Access Related Project
150962 | M-Factor | Fleet East Unit # 61 Digger truck replacement | 0.44558 | 643.77 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
102166 | Base | SQL Expansion - IT Infrastructure | 0.1978 | 635.85 | General Plant | Information Technology | Multiple | Expand existing SQL infrastructure to meet project demands and natural growth of database. Add system capacity, improve performance, and reduce the risk of downtime due resource constraints.
150818 | M-Factor | Fleet_Central South Vehicle Replacement-236-10 S/bucket | 0.51 | 635.35 | General Plant | Fleet Renewal | Enersource | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150980 | M-Factor | Fleet East Vehicle replacement - Work Van | 0.067528 | 622.46 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150942 | M-Factor | Fleet_ Central North Vehicle Replacement_S/Bucket | 0.53 | 620.9 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150807 | M-Factor | Fleet_Central South Vehicle Replacement-209-09 S/bucket | 0.53 | 620.9 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150203 | Base | Station Equipment Temperature Monitoring-NORTH & TS | 0.066463 | 614.42 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of Station Temperature Monitoring system in East and it enables controlled emergency loading beyond the nameplate rating.
150945 | M-Factor | Fleet_ Central North Vehicle Replacement_Reel Carriers | 0.67 | 613.76 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150803 | M-Factor | Fleet_Central South Vehicle Replacement- Material Handler | 0.55 | 606.44 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150896 | M-Factor | Fleet_ Central North Vehicle Replacement S/Bucket 8910 | 0.53 | 595.61 | General Plant | Fleet Renewal | Brampton | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150496 | Base | iPass Project Management – Planned Capital - West | 0.71596 | 589.28 | System Renewal | Underground Asset Renewal | Horizon | Help in optimizing DER performance and efficiency to improve addressing overall energy needs.
150978 | M-Factor | Fleet East Vehicle replacement - Cube Vans | 0.7483 | 579.7 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150953 | M-Factor | Fleet_ Central North Vehicle Replacement_Trailer 11510 | 0.04 | 566.09 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102046 | Base | Purchase of Major Tools - Muliti Year-North & TS | 0.047132 | 565.1 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
151209 | M-Factor | Station LED Lighting Upgrades - South West | 0.002 | 555.75 | System Renewal | Substation Renewal | Guelph | Replacement of inefficient lighting fixtures and lamps at Guelph stations will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
151128 | M-Factor | MS Transformer & HV Switchgear Replacement - Western MS36 T1 & HV1 | 0.58825 | 553.77 | System Renewal | Substation Renewal | Enersource | Recent testing has indicated possible mechanical damage to the transformer windings and the HV switchgear has suffered damage due to a prior failure. The station is in a residential area and a transformer failure could result in a fire, posing a risk to the community and collateral damage to other assets in the station, as well as resulting in an extensive power interruption. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted reactive capital expenditure.
151150 | M-Factor | Fleet East Vehicle replacement - SUV | 0.040596 | 550.35 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150968 | M-Factor | Fleet East Vehicle replacement Pickup truck 2500 | 0.059701 | 548.54 | General Plant | Fleet Renewal | Powerstream | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150905 | Base | Fleet East Multi Year Shop tools | 0.012057 | 544.12 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of tools and shop equipment required to repair and maintain vehicles to ensure vehicle availability to support capital systems projects.
101816 | Base | Alectra East (South), Fault Indicator Installation and Replacement Multi-year initiative | 0.26006 | 542.12 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - North Region which will result improved outage response, operational efficiency, and reliability
151085 | M-Factor | Rear Lot Conversions | 0.12358 | 530.82 | System Renewal | Rear Lot Conversion | Guelph
101134 | Base | Alectra East (North), Fault Indicator Installation and Replacement Multi-year initiative | 0.2624 | 527.43 | System Service | System Control, Comm'ns & Performance | Powerstream | This project is installtion of fault indictor in East - South Region which will result improved outage response, operational efficiency, and reliability
150437 | Base | OT GIS & OMS Enhancements | 0.41822 | 519.79 | General Plant | Information Technology | Multiple | Ongoing productivity enhancements to core GIS and OMS platforms to meet internal and customer demand for functionality.
150975 | M-Factor | Fleet East Unit # 75 83' Double Bucket | 0.68741 | 513.15 | General Plant | Fleet Renewal | Powerstream | Vehicle replacement due to poor conditions, high mileage, engine hours and age. Due to increasing repairs & parts availability, vehicle not as available to support capital system renewal projects and respond to emergencies.
150602 | Base | Smart Meter Test Facility - PowerStream RZ | 0.041851 | 471.4 | System Access | Metering | Powerstream | Multi-year project to expand the capability of the Meter Test Facility to test increasing types of meters and AMI systems before they are placed into production.
150955 | Base | Fleet_ Central North Vehicle Replacement_Arrowboards | 0.052 | 458.92 | General Plant | Fleet Renewal | Brampton | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102027 | Base | Purchase of Critical Spare Parts - Multiyear - East | 0.073884 | 427.82 | System Renewal | Substation Renewal | Powerstream | This project involves procurement of critical spare parts for transformer and municipal stations in the East Operating Area (former PowerStream) so as to facilitate prompt repair of failed assets during emergency situations.
150494 | Base | iPass Project Management – Planned Capital - Central-North | 0.40422 | 408.86 | System Renewal | Overhead Asset Renewal | Brampton | Predicting the influence of weather conditions and DER contribution simultaneously on the power grid, for proactively mitigating local outages,
150495 | Base | iPass Project Management – Planned Capital - Central-South | 0.40422 | 408.86 | System Renewal | Overhead Asset Renewal | Enersource | Enable better visibility towards preventive equipment maintenance needs arising due to DER penetration which will further help mitigate outage risks,
101781 | Base | iPass Project Management – Planned Capital - East | 0.41556 | 408.86 | System Renewal | Overhead Asset Renewal | Powerstream | Estimating the effects of DER contribution at the feeder and region levels to further optimize the energy flows between the Utility and its consumers,
150607 | M-Factor | Station LED Lighting Upgrades - Central | 0.028104 | 407.91 | System Renewal | Substation Renewal | Enersource | Replacement of inefficient lighting fixtures and lamps at stations in the Central Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150606 | M-Factor | Station LED Lighting Upgrades - EAST | 0.028104 | 407.91 | System Renewal | Substation Renewal | Brampton | Replacement of inefficient lighting fixtures and lamps at stations in this Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
151132 | M-Factor | MS Transformer & HV Switchgear Replacement - Munden MS35 T1 & HV1 | 0.6564 | 405.83 | System Renewal | Substation Renewal | Enersource | Recent testing has indicated that the transformer insulation has deteriorated and lacks a proper foundation and is beginning to lean. The station is in a residential area and a transformer failure could result in a fire, posing a risk to the community and collateral damage to other assets in the station, as well as resulting in an extensive power interruption. Failure of the existing equipment would warrant emergency replacement resulting in non-budgeted reactive capital expenditure.
150517 | Base | Upgrade to Station Facilities (Building / Civil work) Multi-year - West | 0.12161 | 399.38 | System Renewal | Substation Renewal | Horizon | MULTI ANSWER
150518 | Base | Upgrade to Station Facilities (Building / Civil work) Multi-year - Central | 0.12161 | 399.38 | System Renewal | Substation Renewal | Enersource | MULTI ANSWER
151168 | M-Factor | Fleet_Central South Vehicle Replacement-Step Vans | 0.735 | 395.07 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150399 | M-Factor | Rear Lot Renewal Project - Richlieu Dr and Trelawne Dr, St.Catharines | 1.1574 | 392.54 | System Renewal | Rear Lot Conversion | Horizon | This area has had an average of 40 outages lasting 1.5hrs per year based on 3 year average.
151212 | M-Factor | Driveway Paving Multi-year initiative - South West | 0.02 | 391 | System Renewal | Substation Renewal | Guelph | These driveways at Guelph stations that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
151007 | M-Factor | Fleet_West_Vehicle_Replacement_Trailers | 0.06 | 366.82 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150608 | M-Factor | Station LED Lighting Upgrades - West | 0.02852 | 359.12 | System Renewal | Substation Renewal | Horizon | Replacement of inefficient lighting fixtures and lamps at stations in the West Operational Area will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
150356 | M-Factor | Voltage Conversion - Clarkson Area, Mississauga | 2.7147 | 358.78 | System Renewal | Overhead Asset Renewal | Enersource | From 2015-2017 customers in this area experienced 35 outages and had 91,638 minutes of interruption.
102034 | Base | Upgrade to Station Facilities (Building / Civil work) Multi-year - East | 0.13905 | 339.91 | System Renewal | Substation Renewal | Powerstream | MULTI ANSWER
150854 | M-Factor | Fleet_Central South Vehicle Replacement-Trailers | 0.175 | 330.19 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150813 | M-Factor | Fleet_Central South Vehicle Replacement-SUV | 0.1065 | 330.13 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150501 | Base | On-Line Dissolved Gas Oil Monitoring of 20 MS Transformers - CENTRAL | 0.22262 | 313.42 | System Service | System Control, Comm'ns & Performance | Enersource | This project consists of installation of Transformer bushing monitoring system in Central South
150741 | Base | Facilities_Replacement_Patterson Road Roof | 1.2188 | 307.59 | General Plant | Facilities Management | Powerstream | Building roofs have exceeded the project useful life. Various decaying roof conditions identified need to be addressed to prevent further damage to the building envelope, structure and assets.
150610 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - Central | 0.021948 | 289.6 | System Renewal | Substation Renewal | Enersource | Existing driveways at stations in the Central Operational Area that are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150609 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - East | 0.021948 | 289.6 | System Renewal | Substation Renewal | Brampton | Existing driveways in this Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150612 | M-Factor | Driveway Paving - Various Stations - Multi-year initiative - West | 0.021948 | 289.6 | System Renewal | Substation Renewal | Horizon | Existing driveways in the West Operational Area that are covered in gravel require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150812 | M-Factor | Fleet_Central South Vehicle Replacement-Vans | 0.11 | 240.44 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
102050 | Base | Various Stations-Station Lighting Upgrade/Retrofit-Energy Efficiency Lighting-initiative Multi-year - East | 0.058717 | 239.8 | System Renewal | Substation Renewal | Powerstream | Replacement of inefficient indoor and outdoor lighting fixtures and lamps at stations in the East Operating Area (former PowerStream) will result in longer lasting lighting. Lighting at stations in important for safety and security. LED lighting provides lower power consumption, longer life which results in less likelihood of outages between inspections cycles, less maintenance and enable standardization of replacement stock.
151167 | M-Factor | Fleet_Central South Vehicle Replacement-Pick ups | 0.162 | 236.9 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150421 | M-Factor | 2D7X Pimlico Dr - Voltage Conversion and Rear Lot | 0.57628 | 233.54 | System Renewal | Overhead Asset Renewal | Horizon | From 2015-2017 customers in this area experienced 28 outages and had 805,077 minutes of interruption. This project also addresses rear lot assets which are extrememly difficult to replace if they fail due to complexities of access issues and restricitions for equipment to rebuild the assets.
150853 | M-Factor | Fleet_Central South Vehicle Replacement-Vans | 0.228 | 227.74 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
151164 | Base | Fleet_Central South _key box replacement | 0.004 | 223.47 | General Plant | Fleet Renewal | Enersource | Adopted the current vehicles key management system at all sites to ensure access to vehicles when required. This ensure access to vehicles after hours and tracking of vehceil keys.
151038 | Base | Fleet_West_Equipment_Key Boxes | 0.004 | 223.47 | General Plant | Fleet Renewal | Horizon | Adopted the current vehicles key management system at all sites to ensure access to vehicles when required. This ensure access to vehicles after hours and tracking of vehceil keys.
150394 | M-Factor | King St. Voltage Conversion & Loop (LRT Betterment) | 0.32442 | 191.85 | System Renewal | Overhead Asset Renewal | Enersource | From 2015-2017 customers in this area experienced 5 outages and had 61,455 minutes of interruption.
150822 | Base | Fleet_Central South Vehicle Replacement-Arrowboard | 0.013 | 178.68 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150326 | Base | Software Asset Management as a Service | 0.06223 | 173.23 | General Plant | Information Technology | Multiple | The Software Asset Management module of ServiceNow will enable the creation of an accurate, up to date, single system of record for IT infrastructure, both on premises and in public clouds. It will identify IP‑enabled configuration items (CIs), map their interdependencies, and populate and maintain them in the ServiceNow Configuration Management Database (CMDB). Software spend across the year will be more predictable, and access to software agreements will be more efficient. Auditing of agreements will be more manageable. The implementation will all better control over the complexity of our software assets, allowing us to optimize the use of these assets.
150153 | Base | Bradford MS324-F2 Reconductor - Holland Street | 0.035154 | 169.19 | System Service | Capacity (Lines) | Powerstream | This project is to reconductor MS324f2 feeder to increase capacity and meet contingency requirements. Increase the ampacity of the existing section of 13.8kV feeder along Holland Street by reconductoring the existing 3/0 Al with 336 Al from Langford Drive to Professor Day
150511 | M-Factor | Installation of SWI Video security system at 4 MS stations per year - Annual Multi-year initiative-WEST | 0.16522 | 163.78 | System Service | Safety & Security | Horizon | This project consists of installation of SWI Video security system in West. The implementation of video monitoring will ensure that station security and safety related issues can be easily identified and addressed immediately
150512 | M-Factor | Installation of SWI Video security system at 4 MS stations per year - Annual Multi-year initiative-CENTRAL | 0.16523 | 163.78 | System Service | Safety & Security | Enersource | This project consists of installation of SWI Video security system in Central South. The implementation of video monitoring will ensure that station security and safety related issues can be easily identified and addressed immediately
150519 | M-Factor | Upgrade to Station Facilities (Building / Civil work) MultiYear - East | 0.12387 | 156.08 | System Renewal | Substation Renewal | Brampton | This project involves work involving structural components of stations, including windows, brickwork, roofs, foundations, drainage, doors, etc. at stations in the East Operational Area. Not keeping up with this work would result in advanced deterioration resulting in even greater maintenance costs, potential safety concerns and potential failure of the electrical equipment in the building causing power interruptions.
103030 | Base | Technology Upgrades Improving the System Control Room Environment | 0.058033 | 147.52 | General Plant | Information Technology | Multiple | This project will continue to build on the original capital project whose scope was focused on the replacement of computers used as Operator WorkStations. The scope of this program has been expanded to account for all technology purchases required for the Control Room theater.
151108 | Base | Office Equipment | 0.077327 | 143.52 | General Plant | Facilities Management | Guelph | Replace aging equipment within the Guelph operational centre to ensure optimal performance in managing the distribution assets
151384 | Base | 2024 GUELPH - Fleet | 0.63 | 137.66 | General Plant | Fleet Renewal | Guelph | Replacement of end of life asset due to poor conditions, high mileage and engine hours and age. Vehicle experiencing more down time at the shop for repairs and maintenance impacting vehicle availability.
151245 | M-Factor | Capacitor Bank Installations | 0.041841 | 134.68 | System Service | System Control, Comm'ns & Performance | Guelph | This project consists of capacitor bank installation to increase power factor, capacity and reduce losses.
150235 | M-Factor | Greenwood Expansion Station Service Supply Backup | 0.04402 | 130.13 | System Service | System Control, Comm'ns & Performance | Powerstream | This project consists of providing back up to the station service transformer at Greenwood TS. In the current configurationt the two station transformers are supplied from VTS#1 and a failure on VTS#1 result in removal of both VTS#1 and VTS#1.
150582 | M-Factor | Back-end Automation (Orchestration Tool\Setup) | 0.22006 | 128.21 | General Plant | Information Technology | Multiple | Automated integration of enterprise system platforms with HR functionality. Increase in productivity related to human resources
102931 | Base | Paving of 3 MS & TS Station Driveways per year - Annual Multi-year initiative - East | 0.050365 | 125.42 | System Renewal | Substation Renewal | Powerstream | Existing driveways at stations in the East Operating Area (former PowerStream) are covered in gravel and require ongoing maintenance for smoothing and filling depressions as well as gaps that may allow for crawl space under fencing, which presents a safety and security risk. Paving will facilitate snow plowing and will enable ready access to the station for maintenance and emergency repair activities year-round. Impeded access due to poor driveway conditions could result in longer outage durations. Paving the driveway also improves safety by eliminating tripping hazards and allowing for improved snow removal.
150597 | Base | Lock Box Installs - East | 0.0101 | 115.84 | System Access | Metering | Powerstream | Multi-year project to install lock boxes at ICI properties with restricted access to eliminate need for a customer appointment for access.
150821 | M-Factor | Fleet_Central South Vehicle Replacement-Van | 0.055 | 111.07 | General Plant | Fleet Renewal | Enersource | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
150737 | Base | Facilities_East Region_Reactive Capital | 0.28084 | 91.88 | General Plant | Facilities Management | Powerstream | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150736 | Base | Facilities_West Region_Reactive Capital | 0.28084 | 91.88 | General Plant | Facilities Management | Horizon | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150734 | Base | Facilities_Central Region_Reactive Capital | 0.28084 | 91.85 | General Plant | Facilities Management | Multiple | Approved capital funds available to address any unforeseen and unbudgeted asset replacements/demands. Having these funds available for immediate use is critical for Facilities building operations to restore equipment/assets back to normal operations a.s.a.p.
150958 | M-Factor | Fleet_West_Vehicle Replacement_Forklift | 0.099 | 90.74 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.
103171 | Base | Implementation of a new Alectra Network Operations Voice Radio System | 0.025 | 79 | General Plant | Information Technology | Multiple
150906 | Base | Vehicle key box system | 0.004 | 43.15 | General Plant | Fleet Renewal | Powerstream
150747 | M-Factor | Net Zero Energy Emissions | 0.33546 | 34.58 | System Service | Distributed Energy Resources (DER) | Powerstream | The project will help Alectra Utilities to ensure that growing DER challenges are met through building expertise and capability in real time monitoring, integrating and optimizing of DERs in line with customer preferences. This will lead to a system that can safely integrate and optimize value from DERs for the benefit of customers.
151053 | Base | Building Sustainment | 0.19501 | 31.98 | General Plant | Facilities Management | Guelph | Projects planned to maintain the buildings, assets and systems in a condition that contributes to maintaining efficiencies, business operations and to alleviate pressure on the operating expenditures. Planned expenditures are based on the condition and/or lifecycle of a given building or component/asset and is scheduled for replacement (e.g. condenser, furnace, windows, roofing).
150878 | M-Factor | Bus & Main Breaker Protections Replacement - Jim Yarrow TS | 0.11398 | 21.53 | System Renewal | Substation Renewal | Brampton | This is part of a multi-phase project to upgrade aging and failure-prone protection systems to the current protection standards. Proper protection to the main bus and transformers will provide protection to the assets in the case of faults when they occur.
151031 | Base | Fleet Shop equipment refurbishment and replacement | 0.062 | 12.85 | General Plant | Fleet Renewal | Enersource | For the refurbishment of trailers, shop compressors and hoists to extend the life of the assets instead of replacement to reduce the need fro capital expenditures.
150678 | Base | P&C Specific Tools & Testing Equipment - West | 0.016985 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Enersource | Replacement of Capital tools required to perform work
102999 | Base | P&C Specific Tools and Testing Equipment | 0.016985 | 12.43 | General Plant | Tools, Shop and Garage Equipment | Powerstream | Replacement of Capital tools required to perform work
102157 | Base | Server Refresh - IT Infrastructure | 0.3956 | 10.1 | General Plant | Information Technology | Multiple | Ongoing server refresh to support applications.
150547 | M-Factor | Business Support | 0.17621 | 7.83 | General Plant | Information Technology | Multiple | The project will encompass a variety of sub projects for the purpose of investigating new and emerging technologies. Building a culture of innovation Alectra will need a continued effort in remaining ahead of the trends and implementing new and more efficient ways of doing business.
151029 | M-Factor | Fleet_West_Vehicle_Replacement_Pickups | 0.169 | 0.9 | General Plant | Fleet Renewal | Horizon | Replacement due to poor conditions, high mileage, engine hours and age. These vehicles are critical to support capital system renewal projects, support assets maintenance programs and respond to emergencies.