## 2021-FULL
Dry Core Transformer Losses Proposed for 2021
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.3446 | 0.1329 |  | 5.2723
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.85885 | 12.0782 | 12.9371 | 0.84723 | 13.7843
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1451 | 16.1043 | 17.2494 | 1.1296 | 18.3791
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.46 | 20.2596 | 21.7197 | 1.4403 | 23.16
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9467 | 27.9239 | 29.8706 | 1.9204 | 31.791
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3475 | 32.4672 | 34.8147 | 2.3158 | 37.1304
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6321 | 36.3215 | 38.9536 | 2.5965 | 41.55
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1062 | 42.7263 | 45.8325 | 3.0641 | 48.8966 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.8648 | 52.9854 | 56.8502 | 3.8125 | 60.6627 | GS 50 to 1,499 kW | 0.02434 | 2.9017 | 2.0474 | 5.4567
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 3.9524 | 54.201 | 58.1534 | 3.8989 | 62.0523 | GS 1,500 to 4,999 kW | 0.02601 | 3.0128 | 2.1882 | 5.0861
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.135 | 56.7204 | 60.8555 | 4.0791 | 64.9346 | Large Use | 0.02929 | 3.3399 | 2.4642 | 5.2741
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4437 | 60.9567 | 65.4004 | 4.3835 | 69.7839
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7523 | 65.1929 | 69.9452 | 4.688 | 74.6332
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 5.8974 | 81.2972 | 87.1946 | 5.8176 | 93.0122 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.44718 | 6.5565 | 7.0037 | 0.44113 | 7.4449
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68709 | 9.9359 | 10.6229 | 0.67779 | 11.3007 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.3742 | 19.8717 | 21.2459 | 1.3556 | 22.6015 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7177 | 24.1564 | 25.8741 | 1.6945 | 27.5686 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2903 | 32.2085 | 34.4988 | 2.2593 | 36.7581
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.3782 | 48.0542 | 51.4324 | 3.3325 | 54.7648
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.0938 | 56.7529 | 60.8467 | 4.0384 | 64.8852
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.4348 | 61.9005 | 66.3353 | 4.3748 | 70.7101
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.7795 | 67.1195 | 71.8991 | 4.7148 | 76.6139
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1245 | 72.3399 | 77.4644 | 5.0552 | 82.5196
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2124 | 88.1856 | 94.3979 | 6.1283 | 100.5263
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.3997 | 160.39 | 170.7897 | 10.259 | 181.0487
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7955 | 184.4582 | 196.2536 | 11.6359 | 207.8895
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4598 | 233.8055 | 249.2653 | 15.2507 | 264.5159
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3494 | 264.2037 | 281.5531 | 17.1147 | 298.6677
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1897 | 350.7082 | 373.8979 | 22.876 | 396.7739
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.656 | 420.074 | 447.7299 | 27.2818 | 475.0117
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2101 | 505.2854 | 538.4955 | 32.7608 | 571.2562
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1651 | 597.7731 | 636.9381 | 38.6352 | 675.5733
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.0975 | 736.5046 | 784.6021 | 47.4467 | 832.0489
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.255 | 850.8212 | 906.0762 | 54.5074 | 960.5836
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2022-FULL
Dry Core Transformer Losses Proposed for 2022
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.345 | 0.1329 |  | 5.753
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.85891 | 12.0782 | 12.9371 | 0.92448 | 13.8616
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1452 | 16.1043 | 17.2495 | 1.2326 | 18.4821
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4601 | 20.2596 | 21.7198 | 1.5716 | 23.2914
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9469 | 27.9239 | 29.8707 | 2.0955 | 31.9662
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3477 | 32.4672 | 34.8148 | 2.5269 | 37.3417
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6322 | 36.3215 | 38.9537 | 2.8332 | 41.7869
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1064 | 42.7263 | 45.8326 | 3.3435 | 49.1761 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.865 | 52.9854 | 56.8505 | 4.1601 | 61.0106 | GS 50 to 1,499 kW | 0.02465 | 2.9017 | 2.0474 | 5.9173
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 3.9527 | 54.201 | 58.1537 | 4.2544 | 62.4081 | GS 1,500 to 4,999 kW | 0.02635 | 3.0128 | 2.1882 | 5.568
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.1353 | 56.7204 | 60.8558 | 4.451 | 65.3068 | Large Use | 0.02967 | 3.3399 | 2.4642 | 5.7737
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4439 | 60.9567 | 65.4006 | 4.7832 | 70.1838
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7526 | 65.1929 | 69.9455 | 5.1154 | 75.0609
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 5.8978 | 81.2972 | 87.195 | 6.348 | 93.543 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.44721 | 6.5565 | 7.0038 | 0.48135 | 7.4851
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68713 | 9.9359 | 10.623 | 0.73959 | 11.3626 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.3743 | 19.8717 | 21.246 | 1.4792 | 22.7252 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7178 | 24.1564 | 25.8742 | 1.849 | 27.7232 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2904 | 32.2085 | 34.499 | 2.4653 | 36.9642
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.3784 | 48.0542 | 51.4326 | 3.6363 | 55.0689
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.0941 | 56.7529 | 60.847 | 4.4067 | 65.2536
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.4351 | 61.9005 | 66.3356 | 4.7737 | 71.1093
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.7798 | 67.1195 | 71.8994 | 5.1447 | 77.0441
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1248 | 72.3399 | 77.4647 | 5.5161 | 82.9808
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2128 | 88.1856 | 94.3983 | 6.6871 | 101.0854
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.4004 | 160.39 | 170.7904 | 11.1943 | 181.9847
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7962 | 184.4582 | 196.2544 | 12.6968 | 208.9511
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4608 | 233.8055 | 249.2663 | 16.6411 | 265.9074
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3505 | 264.2037 | 281.5542 | 18.6751 | 300.2293
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1912 | 350.7082 | 373.8994 | 24.9617 | 398.8611
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.6577 | 420.074 | 447.7317 | 29.7692 | 477.5009
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2122 | 505.2854 | 538.4976 | 35.7477 | 574.2453
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1676 | 597.7731 | 636.9407 | 42.1577 | 679.0984
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.1006 | 736.5046 | 784.6052 | 51.7727 | 836.3779
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.2586 | 850.8212 | 906.0797 | 59.4771 | 965.5568
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2023-FULL
Dry Core Transformer Losses Proposed for 2023
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.3453 | 0.1329 |  | 6.1039
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.85896 | 12.0782 | 12.9372 | 0.98087 | 13.918
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1453 | 16.1043 | 17.2495 | 1.3078 | 18.5574
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4602 | 20.2596 | 21.7199 | 1.6675 | 23.3873
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.947 | 27.9239 | 29.8708 | 2.2233 | 32.0942
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3478 | 32.4672 | 34.815 | 2.681 | 37.496
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6324 | 36.3215 | 38.9539 | 3.006 | 41.9599
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1065 | 42.7263 | 45.8328 | 3.5474 | 49.3803 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.8653 | 52.9854 | 56.8507 | 4.4139 | 61.2646 | GS 50 to 1,499 kW | 0.02494 | 2.9017 | 2.0474 | 6.2408
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 3.9529 | 54.201 | 58.1539 | 4.5139 | 62.6678 | GS 1,500 to 4,999 kW | 0.02666 | 3.0128 | 2.1882 | 5.9253
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.1356 | 56.7204 | 60.856 | 4.7225 | 65.5785 | Large Use | 0.03002 | 3.3399 | 2.4642 | 6.1456
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4442 | 60.9567 | 65.4009 | 5.075 | 70.4759
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7529 | 65.1929 | 69.9458 | 5.4274 | 75.3732
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 5.8981 | 81.2972 | 87.1953 | 6.7352 | 93.9306 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.44724 | 6.5565 | 7.0038 | 0.51071 | 7.5145
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68717 | 9.9359 | 10.623 | 0.7847 | 11.4077 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.3743 | 19.8717 | 21.2461 | 1.5694 | 22.8155 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7179 | 24.1564 | 25.8743 | 1.9617 | 27.8361 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2906 | 32.2085 | 34.4991 | 2.6156 | 37.1147
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.3786 | 48.0542 | 51.4328 | 3.8581 | 55.2909
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.0943 | 56.7529 | 60.8472 | 4.6754 | 65.5227
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.4354 | 61.9005 | 66.3358 | 5.0649 | 71.4007
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.7801 | 67.1195 | 71.8996 | 5.4585 | 77.3582
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1251 | 72.3399 | 77.465 | 5.8525 | 83.3175
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2132 | 88.1856 | 94.3987 | 7.095 | 101.4937
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.401 | 160.39 | 170.791 | 11.8771 | 182.6681
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7969 | 184.4582 | 196.2551 | 13.4712 | 209.7263
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4617 | 233.8055 | 249.2672 | 17.6561 | 266.9233
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3516 | 264.2037 | 281.5552 | 19.8142 | 301.3694
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1926 | 350.7082 | 373.9008 | 26.4842 | 400.385
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.6594 | 420.074 | 447.7333 | 31.5849 | 479.3183
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2142 | 505.2854 | 538.4996 | 37.9281 | 576.4277
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1699 | 597.7731 | 636.943 | 44.7291 | 681.6721
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.1035 | 736.5046 | 784.6081 | 54.9305 | 839.5386
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.2618 | 850.8212 | 906.083 | 63.1049 | 969.1879
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2024-FULL
Dry Core Transformer Losses Proposed for 2024
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.3455 | 0.1329 |  | 6.3777
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.859 | 12.0782 | 12.9372 | 1.0249 | 13.9621
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1453 | 16.1043 | 17.2496 | 1.3665 | 18.6161
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4603 | 20.2596 | 21.7199 | 1.7423 | 23.4622
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9471 | 27.9239 | 29.8709 | 2.3231 | 32.194
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3479 | 32.4672 | 34.8151 | 2.8013 | 37.6164
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6325 | 36.3215 | 38.954 | 3.1409 | 42.0949
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1067 | 42.7263 | 45.833 | 3.7066 | 49.5396 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.8655 | 52.9854 | 56.8509 | 4.6119 | 61.4628 | GS 50 to 1,499 kW | 0.02518 | 2.9017 | 2.0474 | 6.4843
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 3.9531 | 54.201 | 58.1541 | 4.7164 | 62.8705 | GS 1,500 to 4,999 kW | 0.02691 | 3.0128 | 2.1882 | 6.21
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.1358 | 56.7204 | 60.8562 | 4.9344 | 65.7906 | Large Use | 0.0303 | 3.3399 | 2.4642 | 6.4389
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4444 | 60.9567 | 65.4011 | 5.3026 | 70.7037
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7531 | 65.1929 | 69.946 | 5.6709 | 75.6169
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 5.8984 | 81.2972 | 87.1956 | 7.0374 | 94.233 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.44726 | 6.5565 | 7.0038 | 0.53362 | 7.5374
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68721 | 9.9359 | 10.6231 | 0.81991 | 11.443 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.3744 | 19.8717 | 21.2461 | 1.6398 | 22.8859 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.718 | 24.1564 | 25.8744 | 2.0497 | 27.9241 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2907 | 32.2085 | 34.4992 | 2.733 | 37.2322
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.3787 | 48.0542 | 51.4329 | 4.0312 | 55.4641
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.0945 | 56.7529 | 60.8474 | 4.8852 | 65.7326
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.4356 | 61.9005 | 66.3361 | 5.2921 | 71.6281
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.7803 | 67.1195 | 71.8999 | 5.7034 | 77.6033
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1254 | 72.3399 | 77.4653 | 6.1151 | 83.5803
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2135 | 88.1856 | 94.399 | 7.4133 | 101.8123
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.4015 | 160.39 | 170.7915 | 12.41 | 183.2014
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7975 | 184.4582 | 196.2556 | 14.0755 | 210.3312
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4625 | 233.8055 | 249.2679 | 18.4482 | 267.7162
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3524 | 264.2037 | 281.556 | 20.7031 | 302.2591
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1937 | 350.7082 | 373.9019 | 27.6723 | 401.5742
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.6607 | 420.074 | 447.7347 | 33.0019 | 480.7366
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2158 | 505.2854 | 538.5012 | 39.6296 | 578.1308
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1718 | 597.7731 | 636.9449 | 46.7357 | 683.6806
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.1058 | 736.5046 | 784.6104 | 57.3948 | 842.0052
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.2645 | 850.8212 | 906.0857 | 65.9359 | 972.0215
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2025-FULL
Dry Core Transformer Losses Proposed for 2025
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.3459 | 0.1329 |  | 6.5648
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.85906 | 12.0782 | 12.9373 | 1.0549 | 13.9922
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1454 | 16.1043 | 17.2497 | 1.4066 | 18.6563
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4604 | 20.2596 | 21.72 | 1.7934 | 23.5134
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9472 | 27.9239 | 29.8711 | 2.3912 | 32.2623
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3481 | 32.4672 | 34.8152 | 2.8835 | 37.6987
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6327 | 36.3215 | 38.9542 | 3.233 | 42.1872
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1069 | 42.7263 | 45.8332 | 3.8153 | 49.6485 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.8657 | 52.9854 | 56.8512 | 4.7471 | 61.5983 | GS 50 to 1,499 kW | 0.02552 | 2.9017 | 2.0474 | 6.6728
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 3.9534 | 54.201 | 58.1544 | 4.8547 | 63.0091 | GS 1,500 to 4,999 kW | 0.02728 | 3.0128 | 2.1882 | 6.3938
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.136 | 56.7204 | 60.8565 | 5.0791 | 65.9356 | Large Use | 0.03072 | 3.3399 | 2.4642 | 6.6278
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4447 | 60.9567 | 65.4014 | 5.4582 | 70.8596
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7534 | 65.1929 | 69.9464 | 5.8372 | 75.7836
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 5.8988 | 81.2972 | 87.196 | 7.2438 | 94.4398 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.44729 | 6.5565 | 7.0038 | 0.54928 | 7.5531
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68726 | 9.9359 | 10.6231 | 0.84395 | 11.4671 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.3745 | 19.8717 | 21.2462 | 1.6879 | 22.9341 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7181 | 24.1564 | 25.8745 | 2.1099 | 27.9844 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2908 | 32.2085 | 34.4994 | 2.8131 | 37.3125
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.379 | 48.0542 | 51.4332 | 4.1494 | 55.5826
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.0948 | 56.7529 | 60.8477 | 5.0285 | 65.8762
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.4359 | 61.9005 | 66.3364 | 5.4473 | 71.7837
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.7807 | 67.1195 | 71.9002 | 5.8707 | 77.7709
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1257 | 72.3399 | 77.4656 | 6.2944 | 83.7601
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2139 | 88.1856 | 94.3995 | 7.6307 | 102.0301
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.4022 | 160.39 | 170.7922 | 12.774 | 183.5662
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7983 | 184.4582 | 196.2565 | 14.4884 | 210.7449
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4636 | 233.8055 | 249.269 | 18.9893 | 268.2584
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3536 | 264.2037 | 281.5573 | 21.3103 | 302.8676
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1954 | 350.7082 | 373.9035 | 28.484 | 402.3875
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.6627 | 420.074 | 447.7366 | 33.9699 | 481.7065
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2181 | 505.2854 | 538.5035 | 40.792 | 579.2955
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1745 | 597.7731 | 636.9476 | 48.1065 | 685.0541
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.1092 | 736.5046 | 784.6138 | 59.0783 | 843.6921
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.2684 | 850.8212 | 906.0896 | 67.8699 | 973.9594
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1
New Transformers added 2021

## 2021 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2021
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.3446 | 0.1329 |  | 5.2723
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.85885 | 12.0782 | 12.9371 | 0.84723 | 13.7843
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1451 | 16.1043 | 17.2494 | 1.1296 | 18.3791
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.46 | 20.2596 | 21.7197 | 1.4403 | 23.16
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9467 | 27.9239 | 29.8706 | 1.9204 | 31.791
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.3475 | 32.4672 | 34.8147 | 2.3158 | 37.1304
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6321 | 36.3215 | 38.9536 | 2.5965 | 41.55
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1062 | 42.7263 | 45.8325 | 3.0641 | 48.8966
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.8648 | 52.9854 | 56.8502 | 3.8125 | 60.6627
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 3.9524 | 54.201 | 58.1534 | 3.8989 | 62.0523
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.135 | 56.7204 | 60.8555 | 4.0791 | 64.9346
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.4437 | 60.9567 | 65.4004 | 4.3835 | 69.7839
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.7523 | 65.1929 | 69.9452 | 4.688 | 74.6332
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 5.8974 | 81.2972 | 87.1946 | 5.8176 | 93.0122
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.44718 | 6.5565 | 7.0037 | 0.44113 | 7.4449
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.68709 | 9.9359 | 10.6229 | 0.67779 | 11.3007
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.3742 | 19.8717 | 21.2459 | 1.3556 | 22.6015
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7177 | 24.1564 | 25.8741 | 1.6945 | 27.5686
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.2903 | 32.2085 | 34.4988 | 2.2593 | 36.7581
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.3782 | 48.0542 | 51.4324 | 3.3325 | 54.7648
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.0938 | 56.7529 | 60.8467 | 4.0384 | 64.8852
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.4348 | 61.9005 | 66.3353 | 4.3748 | 70.7101
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.7795 | 67.1195 | 71.8991 | 4.7148 | 76.6139
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.1245 | 72.3399 | 77.4644 | 5.0552 | 82.5196
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.2124 | 88.1856 | 94.3979 | 6.1283 | 100.5263
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.3997 | 160.39 | 170.7897 | 10.259 | 181.0487
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 11.7955 | 184.4582 | 196.2536 | 11.6359 | 207.8895
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.4598 | 233.8055 | 249.2653 | 15.2507 | 264.5159
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.3494 | 264.2037 | 281.5531 | 17.1147 | 298.6677
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.1897 | 350.7082 | 373.8979 | 22.876 | 396.7739
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 27.656 | 420.074 | 447.7299 | 27.2818 | 475.0117
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.2101 | 505.2854 | 538.4955 | 32.7608 | 571.2562
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 39.1651 | 597.7731 | 636.9381 | 38.6352 | 675.5733
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 48.0975 | 736.5046 | 784.6021 | 47.4467 | 832.0489
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 55.255 | 850.8212 | 906.0762 | 54.5074 | 960.5836
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2022 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2022
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.345 | 0.1329 |  | 5.753
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.85891 | 12.0782 | 12.9371 | 0.92448 | 13.8616
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1452 | 16.1043 | 17.2495 | 1.2326 | 18.4821
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4601 | 20.2596 | 21.7198 | 1.5716 | 23.2914
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9469 | 27.9239 | 29.8707 | 2.0955 | 31.9662
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.3477 | 32.4672 | 34.8148 | 2.5269 | 37.3417
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6322 | 36.3215 | 38.9537 | 2.8332 | 41.7869
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1064 | 42.7263 | 45.8326 | 3.3435 | 49.1761
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.865 | 52.9854 | 56.8505 | 4.1601 | 61.0106
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 3.9527 | 54.201 | 58.1537 | 4.2544 | 62.4081
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.1353 | 56.7204 | 60.8558 | 4.451 | 65.3068
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.4439 | 60.9567 | 65.4006 | 4.7832 | 70.1838
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.7526 | 65.1929 | 69.9455 | 5.1154 | 75.0609
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 5.8978 | 81.2972 | 87.195 | 6.348 | 93.543
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.44721 | 6.5565 | 7.0038 | 0.48135 | 7.4851
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.68713 | 9.9359 | 10.623 | 0.73959 | 11.3626
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.3743 | 19.8717 | 21.246 | 1.4792 | 22.7252
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7178 | 24.1564 | 25.8742 | 1.849 | 27.7232
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.2904 | 32.2085 | 34.499 | 2.4653 | 36.9642
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.3784 | 48.0542 | 51.4326 | 3.6363 | 55.0689
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.0941 | 56.7529 | 60.847 | 4.4067 | 65.2536
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.4351 | 61.9005 | 66.3356 | 4.7737 | 71.1093
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.7798 | 67.1195 | 71.8994 | 5.1447 | 77.0441
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.1248 | 72.3399 | 77.4647 | 5.5161 | 82.9808
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.2128 | 88.1856 | 94.3983 | 6.6871 | 101.0854
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.4004 | 160.39 | 170.7904 | 11.1943 | 181.9847
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 11.7962 | 184.4582 | 196.2544 | 12.6968 | 208.9511
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.4608 | 233.8055 | 249.2663 | 16.6411 | 265.9074
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.3505 | 264.2037 | 281.5542 | 18.6751 | 300.2293
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.1912 | 350.7082 | 373.8994 | 24.9617 | 398.8611
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 27.6577 | 420.074 | 447.7317 | 29.7692 | 477.5009
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.2122 | 505.2854 | 538.4976 | 35.7477 | 574.2453
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 39.1676 | 597.7731 | 636.9407 | 42.1577 | 679.0984
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 48.1006 | 736.5046 | 784.6052 | 51.7727 | 836.3779
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 55.2586 | 850.8212 | 906.0797 | 59.4771 | 965.5568
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2023 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2023
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.3453 | 0.1329 |  | 6.1039
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.85896 | 12.0782 | 12.9372 | 0.98087 | 13.918
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1453 | 16.1043 | 17.2495 | 1.3078 | 18.5574
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4602 | 20.2596 | 21.7199 | 1.6675 | 23.3873
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.947 | 27.9239 | 29.8708 | 2.2233 | 32.0942
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.3478 | 32.4672 | 34.815 | 2.681 | 37.496
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6324 | 36.3215 | 38.9539 | 3.006 | 41.9599
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1065 | 42.7263 | 45.8328 | 3.5474 | 49.3803
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.8653 | 52.9854 | 56.8507 | 4.4139 | 61.2646
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 3.9529 | 54.201 | 58.1539 | 4.5139 | 62.6678
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.1356 | 56.7204 | 60.856 | 4.7225 | 65.5785
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.4442 | 60.9567 | 65.4009 | 5.075 | 70.4759
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.7529 | 65.1929 | 69.9458 | 5.4274 | 75.3732
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 5.8981 | 81.2972 | 87.1953 | 6.7352 | 93.9306
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.44724 | 6.5565 | 7.0038 | 0.51071 | 7.5145
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.68717 | 9.9359 | 10.623 | 0.7847 | 11.4077
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.3743 | 19.8717 | 21.2461 | 1.5694 | 22.8155
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7179 | 24.1564 | 25.8743 | 1.9617 | 27.8361
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.2906 | 32.2085 | 34.4991 | 2.6156 | 37.1147
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.3786 | 48.0542 | 51.4328 | 3.8581 | 55.2909
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.0943 | 56.7529 | 60.8472 | 4.6754 | 65.5227
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.4354 | 61.9005 | 66.3358 | 5.0649 | 71.4007
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.7801 | 67.1195 | 71.8996 | 5.4585 | 77.3582
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.1251 | 72.3399 | 77.465 | 5.8525 | 83.3175
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.2132 | 88.1856 | 94.3987 | 7.095 | 101.4937
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.401 | 160.39 | 170.791 | 11.8771 | 182.6681
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 11.7969 | 184.4582 | 196.2551 | 13.4712 | 209.7263
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.4617 | 233.8055 | 249.2672 | 17.6561 | 266.9233
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.3516 | 264.2037 | 281.5552 | 19.8142 | 301.3694
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.1926 | 350.7082 | 373.9008 | 26.4842 | 400.385
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 27.6594 | 420.074 | 447.7333 | 31.5849 | 479.3183
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.2142 | 505.2854 | 538.4996 | 37.9281 | 576.4277
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 39.1699 | 597.7731 | 636.943 | 44.7291 | 681.6721
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 48.1035 | 736.5046 | 784.6081 | 54.9305 | 839.5386
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 55.2618 | 850.8212 | 906.083 | 63.1049 | 969.1879
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2024 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2024
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.3455 | 0.1329 |  | 6.3777
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.859 | 12.0782 | 12.9372 | 1.0249 | 13.9621
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1453 | 16.1043 | 17.2496 | 1.3665 | 18.6161
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4603 | 20.2596 | 21.7199 | 1.7423 | 23.4622
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9471 | 27.9239 | 29.8709 | 2.3231 | 32.194
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.3479 | 32.4672 | 34.8151 | 2.8013 | 37.6164
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6325 | 36.3215 | 38.954 | 3.1409 | 42.0949
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1067 | 42.7263 | 45.833 | 3.7066 | 49.5396
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.8655 | 52.9854 | 56.8509 | 4.6119 | 61.4628
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 3.9531 | 54.201 | 58.1541 | 4.7164 | 62.8705
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.1358 | 56.7204 | 60.8562 | 4.9344 | 65.7906
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.4444 | 60.9567 | 65.4011 | 5.3026 | 70.7037
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.7531 | 65.1929 | 69.946 | 5.6709 | 75.6169
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 5.8984 | 81.2972 | 87.1956 | 7.0374 | 94.233
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.44726 | 6.5565 | 7.0038 | 0.53362 | 7.5374
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.68721 | 9.9359 | 10.6231 | 0.81991 | 11.443
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.3744 | 19.8717 | 21.2461 | 1.6398 | 22.8859
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.718 | 24.1564 | 25.8744 | 2.0497 | 27.9241
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.2907 | 32.2085 | 34.4992 | 2.733 | 37.2322
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.3787 | 48.0542 | 51.4329 | 4.0312 | 55.4641
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.0945 | 56.7529 | 60.8474 | 4.8852 | 65.7326
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.4356 | 61.9005 | 66.3361 | 5.2921 | 71.6281
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.7803 | 67.1195 | 71.8999 | 5.7034 | 77.6033
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.1254 | 72.3399 | 77.4653 | 6.1151 | 83.5803
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.2135 | 88.1856 | 94.399 | 7.4133 | 101.8123
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.4015 | 160.39 | 170.7915 | 12.41 | 183.2014
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 11.7975 | 184.4582 | 196.2556 | 14.0755 | 210.3312
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.4625 | 233.8055 | 249.2679 | 18.4482 | 267.7162
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.3524 | 264.2037 | 281.556 | 20.7031 | 302.2591
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.1937 | 350.7082 | 373.9019 | 27.6723 | 401.5742
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 27.6607 | 420.074 | 447.7347 | 33.0019 | 480.7366
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.2158 | 505.2854 | 538.5012 | 39.6296 | 578.1308
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 39.1718 | 597.7731 | 636.9449 | 46.7357 | 683.6806
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 48.1058 | 736.5046 | 784.6104 | 57.3948 | 842.0052
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 55.2645 | 850.8212 | 906.0857 | 65.9359 | 972.0215
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2025 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2025
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.3459 | 0.1329 |  | 6.5648
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.85906 | 12.0782 | 12.9373 | 1.0549 | 13.9922
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1454 | 16.1043 | 17.2497 | 1.4066 | 18.6563
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4604 | 20.2596 | 21.72 | 1.7934 | 23.5134
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9472 | 27.9239 | 29.8711 | 2.3912 | 32.2623
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.3481 | 32.4672 | 34.8152 | 2.8835 | 37.6987
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6327 | 36.3215 | 38.9542 | 3.233 | 42.1872
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1069 | 42.7263 | 45.8332 | 3.8153 | 49.6485
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.8657 | 52.9854 | 56.8512 | 4.7471 | 61.5983
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 3.9534 | 54.201 | 58.1544 | 4.8547 | 63.0091
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.136 | 56.7204 | 60.8565 | 5.0791 | 65.9356
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.4447 | 60.9567 | 65.4014 | 5.4582 | 70.8596
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.7534 | 65.1929 | 69.9464 | 5.8372 | 75.7836
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 5.8988 | 81.2972 | 87.196 | 7.2438 | 94.4398
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.44729 | 6.5565 | 7.0038 | 0.54928 | 7.5531
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.68726 | 9.9359 | 10.6231 | 0.84395 | 11.4671
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.3745 | 19.8717 | 21.2462 | 1.6879 | 22.9341
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7181 | 24.1564 | 25.8745 | 2.1099 | 27.9844
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.2908 | 32.2085 | 34.4994 | 2.8131 | 37.3125
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.379 | 48.0542 | 51.4332 | 4.1494 | 55.5826
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.0948 | 56.7529 | 60.8477 | 5.0285 | 65.8762
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.4359 | 61.9005 | 66.3364 | 5.4473 | 71.7837
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.7807 | 67.1195 | 71.9002 | 5.8707 | 77.7709
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.1257 | 72.3399 | 77.4656 | 6.2944 | 83.7601
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.2139 | 88.1856 | 94.3995 | 7.6307 | 102.0301
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.4022 | 160.39 | 170.7922 | 12.774 | 183.5662
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 11.7983 | 184.4582 | 196.2565 | 14.4884 | 210.7449
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.4636 | 233.8055 | 249.269 | 18.9893 | 268.2584
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.3536 | 264.2037 | 281.5573 | 21.3103 | 302.8676
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.1954 | 350.7082 | 373.9035 | 28.484 | 402.3875
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 27.6627 | 420.074 | 447.7366 | 33.9699 | 481.7065
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.2181 | 505.2854 | 538.5035 | 40.792 | 579.2955
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 39.1745 | 597.7731 | 636.9476 | 48.1065 | 685.0541
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 48.1092 | 736.5046 | 784.6138 | 59.0783 | 843.6921
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 55.2684 | 850.8212 | 906.0896 | 67.8699 | 973.9594
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard