## 2021-FULL
Dry Core Transformer Losses Proposed for 2021
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.3446 | 0.1329 |  | 5.3217
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.85885 | 12.0782 | 12.9371 | 0.85518 | 13.7922
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1451 | 16.1043 | 17.2494 | 1.1402 | 18.3896
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.46 | 20.2596 | 21.7197 | 1.4538 | 23.1735
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9467 | 27.9239 | 29.8706 | 1.9384 | 31.809
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3475 | 32.4672 | 34.8147 | 2.3375 | 37.1521
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6321 | 36.3215 | 38.9536 | 2.6208 | 41.5744
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1062 | 42.7263 | 45.8325 | 3.0929 | 48.9253 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.8648 | 52.9854 | 56.8502 | 3.8483 | 60.6985 | GS 50 to 1,499 kW | 0.02434 | 2.9017 | 2.0474 | 5.5079
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 3.9524 | 54.201 | 58.1534 | 3.9355 | 62.0889 | GS 1,500 to 4,999 kW | 0.02601 | 3.0128 | 2.1882 | 5.1438
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.135 | 56.7204 | 60.8555 | 4.1173 | 64.9728 | Large Use | 0.02929 | 3.3399 | 2.4642 | 5.3135
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4437 | 60.9567 | 65.4004 | 4.4246 | 69.825
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7523 | 65.1929 | 69.9452 | 4.7319 | 74.6771
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 5.8974 | 81.2972 | 87.1946 | 5.8722 | 93.0668 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.44718 | 6.5565 | 7.0037 | 0.44527 | 7.449
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68709 | 9.9359 | 10.6229 | 0.68415 | 11.3071 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.3742 | 19.8717 | 21.2459 | 1.3683 | 22.6142 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7177 | 24.1564 | 25.8741 | 1.7104 | 27.5845 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2903 | 32.2085 | 34.4988 | 2.2805 | 36.7793
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.3782 | 48.0542 | 51.4324 | 3.3637 | 54.7961
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.0938 | 56.7529 | 60.8467 | 4.0763 | 64.923
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.4348 | 61.9005 | 66.3353 | 4.4158 | 70.7511
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.7795 | 67.1195 | 71.8991 | 4.7591 | 76.6581
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1245 | 72.3399 | 77.4644 | 5.1026 | 82.567
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2124 | 88.1856 | 94.3979 | 6.1858 | 100.5837
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.3997 | 160.39 | 170.7897 | 10.3552 | 181.1449
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7955 | 184.4582 | 196.2536 | 11.745 | 207.9986
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4598 | 233.8055 | 249.2653 | 15.3936 | 264.6589
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3494 | 264.2037 | 281.5531 | 17.2751 | 298.8282
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1897 | 350.7082 | 373.8979 | 23.0905 | 396.9884
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.656 | 420.074 | 447.7299 | 27.5376 | 475.2675
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2101 | 505.2854 | 538.4955 | 33.0679 | 571.5634
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1651 | 597.7731 | 636.9381 | 38.9974 | 675.9355
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.0975 | 736.5046 | 784.6021 | 47.8916 | 832.4938
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.255 | 850.8212 | 906.0762 | 55.0185 | 961.0947
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2022-FULL
Dry Core Transformer Losses Proposed for 2022
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.345 | 0.1329 |  | 5.7403
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.85891 | 12.0782 | 12.9371 | 0.92244 | 13.8595
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1452 | 16.1043 | 17.2495 | 1.2299 | 18.4794
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4601 | 20.2596 | 21.7198 | 1.5681 | 23.2879
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9469 | 27.9239 | 29.8707 | 2.0909 | 31.9616
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3477 | 32.4672 | 34.8148 | 2.5213 | 37.3361
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6322 | 36.3215 | 38.9537 | 2.8269 | 41.7807
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1064 | 42.7263 | 45.8326 | 3.3361 | 49.1688 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.865 | 52.9854 | 56.8505 | 4.1509 | 61.0014 | GS 50 to 1,499 kW | 0.02465 | 2.9017 | 2.0474 | 5.9028
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 3.9527 | 54.201 | 58.1537 | 4.245 | 62.3987 | GS 1,500 to 4,999 kW | 0.02635 | 3.0128 | 2.1882 | 5.5669
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.1353 | 56.7204 | 60.8558 | 4.4412 | 65.2969 | Large Use | 0.02967 | 3.3399 | 2.4642 | 5.7512
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4439 | 60.9567 | 65.4006 | 4.7726 | 70.1733
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7526 | 65.1929 | 69.9455 | 5.1041 | 75.0496
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 5.8978 | 81.2972 | 87.195 | 6.334 | 93.529 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.44721 | 6.5565 | 7.0038 | 0.48029 | 7.4841
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68713 | 9.9359 | 10.623 | 0.73796 | 11.361 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.3743 | 19.8717 | 21.246 | 1.4759 | 22.7219 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7178 | 24.1564 | 25.8742 | 1.8449 | 27.7191 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2904 | 32.2085 | 34.499 | 2.4598 | 36.9588
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.3784 | 48.0542 | 51.4326 | 3.6283 | 55.0608
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.0941 | 56.7529 | 60.847 | 4.3969 | 65.2439
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.4351 | 61.9005 | 66.3356 | 4.7631 | 71.0987
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.7798 | 67.1195 | 71.8994 | 5.1334 | 77.0327
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1248 | 72.3399 | 77.4647 | 5.5039 | 82.9686
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2128 | 88.1856 | 94.3983 | 6.6723 | 101.0707
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.4004 | 160.39 | 170.7904 | 11.1696 | 181.96
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7962 | 184.4582 | 196.2544 | 12.6687 | 208.9231
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4608 | 233.8055 | 249.2663 | 16.6044 | 265.8707
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3505 | 264.2037 | 281.5542 | 18.6339 | 300.1881
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1912 | 350.7082 | 373.8994 | 24.9066 | 398.806
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.6577 | 420.074 | 447.7317 | 29.7035 | 477.4352
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2122 | 505.2854 | 538.4976 | 35.6688 | 574.1664
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1676 | 597.7731 | 636.9407 | 42.0646 | 679.0053
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.1006 | 736.5046 | 784.6052 | 51.6584 | 836.2636
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.2586 | 850.8212 | 906.0797 | 59.3458 | 965.4255
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2023-FULL
Dry Core Transformer Losses Proposed for 2023
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.3453 | 0.1329 |  | 6.1242
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.85896 | 12.0782 | 12.9372 | 0.98413 | 13.9213
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1453 | 16.1043 | 17.2495 | 1.3122 | 18.5617
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4602 | 20.2596 | 21.7199 | 1.673 | 23.3929
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.947 | 27.9239 | 29.8708 | 2.2307 | 32.1016
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3478 | 32.4672 | 34.815 | 2.6899 | 37.5049
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6324 | 36.3215 | 38.9539 | 3.016 | 41.9699
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1065 | 42.7263 | 45.8328 | 3.5592 | 49.3921 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.8653 | 52.9854 | 56.8507 | 4.4285 | 61.2792 | GS 50 to 1,499 kW | 0.02494 | 2.9017 | 2.0474 | 6.261
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 3.9529 | 54.201 | 58.1539 | 4.5289 | 62.6828 | GS 1,500 to 4,999 kW | 0.02666 | 3.0128 | 2.1882 | 5.9564
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.1356 | 56.7204 | 60.856 | 4.7382 | 65.5942 | Large Use | 0.03002 | 3.3399 | 2.4642 | 6.1552
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4442 | 60.9567 | 65.4009 | 5.0918 | 70.4927
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7529 | 65.1929 | 69.9458 | 5.4455 | 75.3913
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 5.8981 | 81.2972 | 87.1953 | 6.7576 | 93.953 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.44724 | 6.5565 | 7.0038 | 0.51241 | 7.5162
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68717 | 9.9359 | 10.623 | 0.78731 | 11.4103 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.3743 | 19.8717 | 21.2461 | 1.5746 | 22.8207 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7179 | 24.1564 | 25.8743 | 1.9683 | 27.8426 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2906 | 32.2085 | 34.4991 | 2.6243 | 37.1234
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.3786 | 48.0542 | 51.4328 | 3.8709 | 55.3037
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.0943 | 56.7529 | 60.8472 | 4.691 | 65.5382
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.4354 | 61.9005 | 66.3358 | 5.0817 | 71.4175
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.7801 | 67.1195 | 71.8996 | 5.4767 | 77.3763
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1251 | 72.3399 | 77.465 | 5.872 | 83.337
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2132 | 88.1856 | 94.3987 | 7.1186 | 101.5173
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.401 | 160.39 | 170.791 | 11.9166 | 182.7076
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7969 | 184.4582 | 196.2551 | 13.516 | 209.7711
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4617 | 233.8055 | 249.2672 | 17.7149 | 266.9821
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3516 | 264.2037 | 281.5552 | 19.8801 | 301.4353
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1926 | 350.7082 | 373.9008 | 26.5723 | 400.4731
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.6594 | 420.074 | 447.7333 | 31.69 | 479.4233
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2142 | 505.2854 | 538.4996 | 38.0542 | 576.5538
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1699 | 597.7731 | 636.943 | 44.8778 | 681.8208
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.1035 | 736.5046 | 784.6081 | 55.1132 | 839.7213
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.2618 | 850.8212 | 906.083 | 63.3147 | 969.3977
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2024-FULL
Dry Core Transformer Losses Proposed for 2024
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.3455 | 0.1329 |  | 6.3992
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.859 | 12.0782 | 12.9372 | 1.0283 | 13.9655
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1453 | 16.1043 | 17.2496 | 1.3711 | 18.6207
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4603 | 20.2596 | 21.7199 | 1.7481 | 23.4681
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9471 | 27.9239 | 29.8709 | 2.3309 | 32.2018
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3479 | 32.4672 | 34.8151 | 2.8107 | 37.6258
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6325 | 36.3215 | 38.954 | 3.1514 | 42.1055
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1067 | 42.7263 | 45.833 | 3.7191 | 49.552 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.8655 | 52.9854 | 56.8509 | 4.6274 | 61.4783 | GS 50 to 1,499 kW | 0.02518 | 2.9017 | 2.0474 | 6.5058
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 3.9531 | 54.201 | 58.1541 | 4.7323 | 62.8864 | GS 1,500 to 4,999 kW | 0.02691 | 3.0128 | 2.1882 | 6.2424
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.1358 | 56.7204 | 60.8562 | 4.951 | 65.8072 | Large Use | 0.0303 | 3.3399 | 2.4642 | 6.4494
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4444 | 60.9567 | 65.4011 | 5.3205 | 70.7216
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7531 | 65.1929 | 69.946 | 5.69 | 75.636
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 5.8984 | 81.2972 | 87.1956 | 7.0611 | 94.2567 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.44726 | 6.5565 | 7.0038 | 0.53542 | 7.5392
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68721 | 9.9359 | 10.6231 | 0.82267 | 11.4457 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.3744 | 19.8717 | 21.2461 | 1.6453 | 22.8915 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.718 | 24.1564 | 25.8744 | 2.0566 | 27.931 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2907 | 32.2085 | 34.4992 | 2.7422 | 37.2414
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.3787 | 48.0542 | 51.4329 | 4.0447 | 55.4777
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.0945 | 56.7529 | 60.8474 | 4.9016 | 65.749
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.4356 | 61.9005 | 66.3361 | 5.3099 | 71.6459
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.7803 | 67.1195 | 71.8999 | 5.7226 | 77.6225
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1254 | 72.3399 | 77.4653 | 6.1356 | 83.6009
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2135 | 88.1856 | 94.399 | 7.4382 | 101.8372
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.4015 | 160.39 | 170.7915 | 12.4517 | 183.2432
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7975 | 184.4582 | 196.2556 | 14.1229 | 210.3785
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4625 | 233.8055 | 249.2679 | 18.5103 | 267.7783
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3524 | 264.2037 | 281.556 | 20.7728 | 302.3288
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1937 | 350.7082 | 373.9019 | 27.7655 | 401.6674
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.6607 | 420.074 | 447.7347 | 33.113 | 480.8476
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2158 | 505.2854 | 538.5012 | 39.763 | 578.2642
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1718 | 597.7731 | 636.9449 | 46.893 | 683.8379
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.1058 | 736.5046 | 784.6104 | 57.588 | 842.1984
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.2645 | 850.8212 | 906.0857 | 66.1578 | 972.2435
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2025-FULL
Dry Core Transformer Losses Proposed for 2025
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.3459 | 0.1329 |  | 6.5877
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.85906 | 12.0782 | 12.9373 | 1.0586 | 13.9959
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1454 | 16.1043 | 17.2497 | 1.4115 | 18.6612
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4604 | 20.2596 | 21.72 | 1.7996 | 23.5197
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9472 | 27.9239 | 29.8711 | 2.3995 | 32.2706
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.3481 | 32.4672 | 34.8152 | 2.8935 | 37.7088
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6327 | 36.3215 | 38.9542 | 3.2443 | 42.1985
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1069 | 42.7263 | 45.8332 | 3.8286 | 49.6618 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.8657 | 52.9854 | 56.8512 | 4.7637 | 61.6149 | GS 50 to 1,499 kW | 0.02552 | 2.9017 | 2.0474 | 6.6955
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 3.9534 | 54.201 | 58.1544 | 4.8717 | 63.0261 | GS 1,500 to 4,999 kW | 0.02728 | 3.0128 | 2.1882 | 6.4281
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.136 | 56.7204 | 60.8565 | 5.0968 | 65.9533 | Large Use | 0.03072 | 3.3399 | 2.4642 | 6.6396
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.4447 | 60.9567 | 65.4014 | 5.4772 | 70.8786
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.7534 | 65.1929 | 69.9464 | 5.8576 | 75.804
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 5.8988 | 81.2972 | 87.196 | 7.2691 | 94.4651 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.44729 | 6.5565 | 7.0038 | 0.5512 | 7.555
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.68726 | 9.9359 | 10.6231 | 0.8469 | 11.47 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.3745 | 19.8717 | 21.2462 | 1.6938 | 22.94 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7181 | 24.1564 | 25.8745 | 2.1172 | 27.9918 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.2908 | 32.2085 | 34.4994 | 2.823 | 37.3223
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.379 | 48.0542 | 51.4332 | 4.1639 | 55.5971
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.0948 | 56.7529 | 60.8477 | 5.046 | 65.8937
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.4359 | 61.9005 | 66.3364 | 5.4663 | 71.8027
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.7807 | 67.1195 | 71.9002 | 5.8912 | 77.7914
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.1257 | 72.3399 | 77.4656 | 6.3164 | 83.7821
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.2139 | 88.1856 | 94.3995 | 7.6574 | 102.0568
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.4022 | 160.39 | 170.7922 | 12.8186 | 183.6108
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 11.7983 | 184.4582 | 196.2565 | 14.539 | 210.7955
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.4636 | 233.8055 | 249.269 | 19.0557 | 268.3247
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.3536 | 264.2037 | 281.5573 | 21.3848 | 302.942
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.1954 | 350.7082 | 373.9035 | 28.5835 | 402.4871
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 27.6627 | 420.074 | 447.7366 | 34.0886 | 481.8252
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.2181 | 505.2854 | 538.5035 | 40.9345 | 579.438
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 39.1745 | 597.7731 | 636.9476 | 48.2746 | 685.2222
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 48.1092 | 736.5046 | 784.6138 | 59.2847 | 843.8984
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 55.2684 | 850.8212 | 906.0896 | 68.107 | 974.1965
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1
New Transformers added 2021

## 2021 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2021
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.3446 | 0.1329 |  | 5.3217
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.85885 | 12.0782 | 12.9371 | 0.85518 | 13.7922
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1451 | 16.1043 | 17.2494 | 1.1402 | 18.3896
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.46 | 20.2596 | 21.7197 | 1.4538 | 23.1735
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9467 | 27.9239 | 29.8706 | 1.9384 | 31.809
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.3475 | 32.4672 | 34.8147 | 2.3375 | 37.1521
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6321 | 36.3215 | 38.9536 | 2.6208 | 41.5744
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1062 | 42.7263 | 45.8325 | 3.0929 | 48.9253
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.8648 | 52.9854 | 56.8502 | 3.8483 | 60.6985
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 3.9524 | 54.201 | 58.1534 | 3.9355 | 62.0889
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.135 | 56.7204 | 60.8555 | 4.1173 | 64.9728
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.4437 | 60.9567 | 65.4004 | 4.4246 | 69.825
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.7523 | 65.1929 | 69.9452 | 4.7319 | 74.6771
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 5.8974 | 81.2972 | 87.1946 | 5.8722 | 93.0668
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.44718 | 6.5565 | 7.0037 | 0.44527 | 7.449
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.68709 | 9.9359 | 10.6229 | 0.68415 | 11.3071
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.3742 | 19.8717 | 21.2459 | 1.3683 | 22.6142
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7177 | 24.1564 | 25.8741 | 1.7104 | 27.5845
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.2903 | 32.2085 | 34.4988 | 2.2805 | 36.7793
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.3782 | 48.0542 | 51.4324 | 3.3637 | 54.7961
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.0938 | 56.7529 | 60.8467 | 4.0763 | 64.923
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.4348 | 61.9005 | 66.3353 | 4.4158 | 70.7511
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.7795 | 67.1195 | 71.8991 | 4.7591 | 76.6581
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.1245 | 72.3399 | 77.4644 | 5.1026 | 82.567
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.2124 | 88.1856 | 94.3979 | 6.1858 | 100.5837
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.3997 | 160.39 | 170.7897 | 10.3552 | 181.1449
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 11.7955 | 184.4582 | 196.2536 | 11.745 | 207.9986
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.4598 | 233.8055 | 249.2653 | 15.3936 | 264.6589
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.3494 | 264.2037 | 281.5531 | 17.2751 | 298.8282
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.1897 | 350.7082 | 373.8979 | 23.0905 | 396.9884
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 27.656 | 420.074 | 447.7299 | 27.5376 | 475.2675
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.2101 | 505.2854 | 538.4955 | 33.0679 | 571.5634
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 39.1651 | 597.7731 | 636.9381 | 38.9974 | 675.9355
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 48.0975 | 736.5046 | 784.6021 | 47.8916 | 832.4938
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 55.255 | 850.8212 | 906.0762 | 55.0185 | 961.0947
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2022 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2022
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.345 | 0.1329 |  | 5.7403
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.85891 | 12.0782 | 12.9371 | 0.92244 | 13.8595
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1452 | 16.1043 | 17.2495 | 1.2299 | 18.4794
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4601 | 20.2596 | 21.7198 | 1.5681 | 23.2879
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9469 | 27.9239 | 29.8707 | 2.0909 | 31.9616
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.3477 | 32.4672 | 34.8148 | 2.5213 | 37.3361
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6322 | 36.3215 | 38.9537 | 2.8269 | 41.7807
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1064 | 42.7263 | 45.8326 | 3.3361 | 49.1688
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.865 | 52.9854 | 56.8505 | 4.1509 | 61.0014
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 3.9527 | 54.201 | 58.1537 | 4.245 | 62.3987
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.1353 | 56.7204 | 60.8558 | 4.4412 | 65.2969
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.4439 | 60.9567 | 65.4006 | 4.7726 | 70.1733
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.7526 | 65.1929 | 69.9455 | 5.1041 | 75.0496
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 5.8978 | 81.2972 | 87.195 | 6.334 | 93.529
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.44721 | 6.5565 | 7.0038 | 0.48029 | 7.4841
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.68713 | 9.9359 | 10.623 | 0.73796 | 11.361
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.3743 | 19.8717 | 21.246 | 1.4759 | 22.7219
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7178 | 24.1564 | 25.8742 | 1.8449 | 27.7191
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.2904 | 32.2085 | 34.499 | 2.4598 | 36.9588
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.3784 | 48.0542 | 51.4326 | 3.6283 | 55.0608
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.0941 | 56.7529 | 60.847 | 4.3969 | 65.2439
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.4351 | 61.9005 | 66.3356 | 4.7631 | 71.0987
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.7798 | 67.1195 | 71.8994 | 5.1334 | 77.0327
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.1248 | 72.3399 | 77.4647 | 5.5039 | 82.9686
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.2128 | 88.1856 | 94.3983 | 6.6723 | 101.0707
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.4004 | 160.39 | 170.7904 | 11.1696 | 181.96
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 11.7962 | 184.4582 | 196.2544 | 12.6687 | 208.9231
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.4608 | 233.8055 | 249.2663 | 16.6044 | 265.8707
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.3505 | 264.2037 | 281.5542 | 18.6339 | 300.1881
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.1912 | 350.7082 | 373.8994 | 24.9066 | 398.806
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 27.6577 | 420.074 | 447.7317 | 29.7035 | 477.4352
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.2122 | 505.2854 | 538.4976 | 35.6688 | 574.1664
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 39.1676 | 597.7731 | 636.9407 | 42.0646 | 679.0053
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 48.1006 | 736.5046 | 784.6052 | 51.6584 | 836.2636
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 55.2586 | 850.8212 | 906.0797 | 59.3458 | 965.4255
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2023 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2023
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.3453 | 0.1329 |  | 6.1242
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.85896 | 12.0782 | 12.9372 | 0.98413 | 13.9213
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1453 | 16.1043 | 17.2495 | 1.3122 | 18.5617
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4602 | 20.2596 | 21.7199 | 1.673 | 23.3929
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.947 | 27.9239 | 29.8708 | 2.2307 | 32.1016
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.3478 | 32.4672 | 34.815 | 2.6899 | 37.5049
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6324 | 36.3215 | 38.9539 | 3.016 | 41.9699
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1065 | 42.7263 | 45.8328 | 3.5592 | 49.3921
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.8653 | 52.9854 | 56.8507 | 4.4285 | 61.2792
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 3.9529 | 54.201 | 58.1539 | 4.5289 | 62.6828
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.1356 | 56.7204 | 60.856 | 4.7382 | 65.5942
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.4442 | 60.9567 | 65.4009 | 5.0918 | 70.4927
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.7529 | 65.1929 | 69.9458 | 5.4455 | 75.3913
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 5.8981 | 81.2972 | 87.1953 | 6.7576 | 93.953
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.44724 | 6.5565 | 7.0038 | 0.51241 | 7.5162
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.68717 | 9.9359 | 10.623 | 0.78731 | 11.4103
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.3743 | 19.8717 | 21.2461 | 1.5746 | 22.8207
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7179 | 24.1564 | 25.8743 | 1.9683 | 27.8426
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.2906 | 32.2085 | 34.4991 | 2.6243 | 37.1234
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.3786 | 48.0542 | 51.4328 | 3.8709 | 55.3037
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.0943 | 56.7529 | 60.8472 | 4.691 | 65.5382
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.4354 | 61.9005 | 66.3358 | 5.0817 | 71.4175
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.7801 | 67.1195 | 71.8996 | 5.4767 | 77.3763
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.1251 | 72.3399 | 77.465 | 5.872 | 83.337
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.2132 | 88.1856 | 94.3987 | 7.1186 | 101.5173
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.401 | 160.39 | 170.791 | 11.9166 | 182.7076
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 11.7969 | 184.4582 | 196.2551 | 13.516 | 209.7711
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.4617 | 233.8055 | 249.2672 | 17.7149 | 266.9821
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.3516 | 264.2037 | 281.5552 | 19.8801 | 301.4353
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.1926 | 350.7082 | 373.9008 | 26.5723 | 400.4731
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 27.6594 | 420.074 | 447.7333 | 31.69 | 479.4233
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.2142 | 505.2854 | 538.4996 | 38.0542 | 576.5538
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 39.1699 | 597.7731 | 636.943 | 44.8778 | 681.8208
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 48.1035 | 736.5046 | 784.6081 | 55.1132 | 839.7213
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 55.2618 | 850.8212 | 906.083 | 63.3147 | 969.3977
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2024 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2024
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.3455 | 0.1329 |  | 6.3992
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.859 | 12.0782 | 12.9372 | 1.0283 | 13.9655
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1453 | 16.1043 | 17.2496 | 1.3711 | 18.6207
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4603 | 20.2596 | 21.7199 | 1.7481 | 23.4681
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9471 | 27.9239 | 29.8709 | 2.3309 | 32.2018
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.3479 | 32.4672 | 34.8151 | 2.8107 | 37.6258
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6325 | 36.3215 | 38.954 | 3.1514 | 42.1055
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1067 | 42.7263 | 45.833 | 3.7191 | 49.552
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.8655 | 52.9854 | 56.8509 | 4.6274 | 61.4783
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 3.9531 | 54.201 | 58.1541 | 4.7323 | 62.8864
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.1358 | 56.7204 | 60.8562 | 4.951 | 65.8072
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.4444 | 60.9567 | 65.4011 | 5.3205 | 70.7216
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.7531 | 65.1929 | 69.946 | 5.69 | 75.636
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 5.8984 | 81.2972 | 87.1956 | 7.0611 | 94.2567
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.44726 | 6.5565 | 7.0038 | 0.53542 | 7.5392
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.68721 | 9.9359 | 10.6231 | 0.82267 | 11.4457
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.3744 | 19.8717 | 21.2461 | 1.6453 | 22.8915
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.718 | 24.1564 | 25.8744 | 2.0566 | 27.931
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.2907 | 32.2085 | 34.4992 | 2.7422 | 37.2414
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.3787 | 48.0542 | 51.4329 | 4.0447 | 55.4777
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.0945 | 56.7529 | 60.8474 | 4.9016 | 65.749
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.4356 | 61.9005 | 66.3361 | 5.3099 | 71.6459
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.7803 | 67.1195 | 71.8999 | 5.7226 | 77.6225
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.1254 | 72.3399 | 77.4653 | 6.1356 | 83.6009
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.2135 | 88.1856 | 94.399 | 7.4382 | 101.8372
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.4015 | 160.39 | 170.7915 | 12.4517 | 183.2432
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 11.7975 | 184.4582 | 196.2556 | 14.1229 | 210.3785
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.4625 | 233.8055 | 249.2679 | 18.5103 | 267.7783
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.3524 | 264.2037 | 281.556 | 20.7728 | 302.3288
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.1937 | 350.7082 | 373.9019 | 27.7655 | 401.6674
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 27.6607 | 420.074 | 447.7347 | 33.113 | 480.8476
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.2158 | 505.2854 | 538.5012 | 39.763 | 578.2642
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 39.1718 | 597.7731 | 636.9449 | 46.893 | 683.8379
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 48.1058 | 736.5046 | 784.6104 | 57.588 | 842.1984
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 55.2645 | 850.8212 | 906.0857 | 66.1578 | 972.2435
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2025 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2025
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.3459 | 0.1329 |  | 6.5877
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.85906 | 12.0782 | 12.9373 | 1.0586 | 13.9959
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1454 | 16.1043 | 17.2497 | 1.4115 | 18.6612
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4604 | 20.2596 | 21.72 | 1.7996 | 23.5197
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9472 | 27.9239 | 29.8711 | 2.3995 | 32.2706
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.3481 | 32.4672 | 34.8152 | 2.8935 | 37.7088
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6327 | 36.3215 | 38.9542 | 3.2443 | 42.1985
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1069 | 42.7263 | 45.8332 | 3.8286 | 49.6618
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.8657 | 52.9854 | 56.8512 | 4.7637 | 61.6149
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 3.9534 | 54.201 | 58.1544 | 4.8717 | 63.0261
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.136 | 56.7204 | 60.8565 | 5.0968 | 65.9533
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.4447 | 60.9567 | 65.4014 | 5.4772 | 70.8786
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.7534 | 65.1929 | 69.9464 | 5.8576 | 75.804
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 5.8988 | 81.2972 | 87.196 | 7.2691 | 94.4651
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.44729 | 6.5565 | 7.0038 | 0.5512 | 7.555
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.68726 | 9.9359 | 10.6231 | 0.8469 | 11.47
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.3745 | 19.8717 | 21.2462 | 1.6938 | 22.94
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7181 | 24.1564 | 25.8745 | 2.1172 | 27.9918
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.2908 | 32.2085 | 34.4994 | 2.823 | 37.3223
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.379 | 48.0542 | 51.4332 | 4.1639 | 55.5971
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.0948 | 56.7529 | 60.8477 | 5.046 | 65.8937
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.4359 | 61.9005 | 66.3364 | 5.4663 | 71.8027
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.7807 | 67.1195 | 71.9002 | 5.8912 | 77.7914
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.1257 | 72.3399 | 77.4656 | 6.3164 | 83.7821
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.2139 | 88.1856 | 94.3995 | 7.6574 | 102.0568
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.4022 | 160.39 | 170.7922 | 12.8186 | 183.6108
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 11.7983 | 184.4582 | 196.2565 | 14.539 | 210.7955
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.4636 | 233.8055 | 249.269 | 19.0557 | 268.3247
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.3536 | 264.2037 | 281.5573 | 21.3848 | 302.942
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.1954 | 350.7082 | 373.9035 | 28.5835 | 402.4871
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 27.6627 | 420.074 | 447.7366 | 34.0886 | 481.8252
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.2181 | 505.2854 | 538.5035 | 40.9345 | 579.438
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 39.1745 | 597.7731 | 636.9476 | 48.2746 | 685.2222
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 48.1092 | 736.5046 | 784.6138 | 59.2847 | 843.8984
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 55.2684 | 850.8212 | 906.0896 | 68.107 | 974.1965
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard