## Unit Cost
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR OEB-44 Attachment A ORIGINAL
Hydro Ottawa 2016-2018 Unit Costs
Asset Category / Capital | Unit of Measure | 2016 |  | 2017 |  | 2018 |  | UMS Group Input | Comments
|  | No. of Units | Cost | No. of Units | Cost | No. of Units | Cost | 3-YR Unit Cost
Wood Poles Replacement | Each | 466 | 4400863.42 | 416 | 3214081.03 | 210 | 1693335.09 | 8524.0655
UG Cable (XLPE) Replacement | Meter | 27453 | 1569360.83 | 11901 | 1694212.77 | 13928 | 994786.61 | 79.9212
OH Switches Replacement | Each | 2 | 28462.58 | 9 | 254146.47 | 12 | 220426.48 | 21871.11
OH Transformer Replacement | Each | 75 | 605105.48 | 52 | 443937.03 | 97 | 652312.28 | 7595.3339
UG Transformer Replacement | Each | 145 | 2034704.23 | 174 | 2559647.89 | 207 | 1964977.34 | 12470.2081
Station Breaker Replacement | Each |  |  |  |  | 6 | 638316 | 106386 | Provided separate from original submittal by Hydro Ottawa
Maintenance Programs / OM&A | Unit of Measure | 2016 |  | 2017 |  | 2018 |  | UMS Group Input | Comments
|  | No. of Units | Total Cost | No. of Units | Total Cost | No. of Units | Total Cost | 3-YR Unit Cost
Vegetation Management | Kilometer | 1494 | 4233697 | 1355 | 4394452 | 1244 | 3959768 | 3075.4745
Pole Test and Inspection | Each | 5230 | 269019 | 4731 | 250059 | 4630 | 112706 | 43.2996
Overhead Line Patrol | Kilometer | 932 | 23946 | 1179.6 | 25555 | 479.4 | 30499 | 30.8761
Station Breaker and Relay | Each | 80 | 273639.7 | 46 | 117849.8 | 147 | 405766.88 | 2920.353
Billing - paper | Bills | 2460532 | 3012993.6626 | 2367013 | 2795692.1811 | 2221365 | 2631314.9644 | 1.1973
Billing - online | Bills | 1508068 | 404682.9798 | 1617858 | 420017.636 | 1817481 | 432956.9641 | 0.25441
Meter Maintenance | Each | 3649 | 622949 | 5205 | 911148 | 4424 | 736963 | 171.0393 | Unit Cost adjusted to $173 based on update from Hydro Ottawa

## Accounting
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR OEB-44 Attachment A ORIGINAL
The following information will be used to apply adjustors based on how each utility calculates unit cost and the factors that comprise unit cost.
| Calculation of Unit Costs | Response | Comments
1 | Which of the following methods do you use to determine unit rates for your asset categories and / or maintenance programs?
| Divide total spent by number of units | Y | For overhead and underground programs, work order per program.
| Average individual costs of separate work orders | Y | For station maintenance programs, work order per activity per station. Number of assets per station devided number of assets, averaged over all stations
Other (please describe)
2 | In addition to Direct Labor and Material, which of the following costs are included in your unit costs for In-House work? | Response (Please indicate "Y" or "N") | Comments
| Design and Permitting costs | Y
| Project Management and Supervisory costs | Y | Project Management is captured. Supervisory is added as a burden along with other administrative costs
| Other project-related costs (e.g.; Fleet and Warehouse) | Y
| Other labor-related costs (e.g.; training, conferences and meetings) | N
| Employee-related costs (e.g.; vacation, sick time, insurances and pension) | N
| Administrative and General costs | Y | Added as a burden percent rate
| AFUDC / CWIP | Y
Other (please describe)
3 | In addition to Contractor's cost, which of the following costs are included in your unit costs for Contracted work? | Response (Please indicate "Y" or "N") | Comments
| Contractor Management/Supervision costs (please indicate in comments if these costs include overheads per question 2) | Y
| Permitting and Design Costs | Y
Other (please describe)
4 | Do you "net out" customer contributions from your unit costs?
5 | Do you use GAAP or IFRS accounting? (please specify which in Comments) |  | IFRS

## Local Factors
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR OEB-44 Attachment A ORIGINAL
The following table lists some of the more common factors that negatively impact worker productivity. Please indicate which ones apply to your operating and working environment and / or add others that are unique to your service territory.
Local Factors | "X" to those that apply | Comments
Which of the following factors impact the cost of you performing inspections and replacement work?
Excessive travel time (over 30 mins.) | X
Road restrictions which limit working hours | X
High water table
Working next to energized lines (requiring dedicated observer, gloves, etc.) | X
Requirements to perform work off hours (i.e., night/weekend) | X
Changed standards requiring rebuilds rather than like-for-like (i.e., clearances) | X
Excessive switching requirements (i.e., to isolate on dual radial construction) | X
Shoring requirements for UG work | X
Limitations on tree trimming (e.g.; unusually tight clearances) | X | List of "grandfathered" trees that have limited trimming
Prior use of lead cables | X
High fault currents (impacting equipment sourcing) | X | 13kV system has high available fault current which limits available equipment.
Paid duty for police presence on public roads | X
Extensive use of submersible transformers
Environmental regulations | X
Insufficient IT Enablement
Union Work Rules | X
City consent requirements (i.e., customer notification, restoration, progressive clean-up, etc.) | X
Other (please specify in Comments)