## Post Jul 2012
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR EPRF-84 Attachment A ORIGINAL
List of Outage Information - Post July 2012
OutageID | Date | Primary Cause | Secondary Cause | Reason for Outage | Primary Apparatus | Secondary Apparatus | Cust Count | Duration (min) | Cust Hours | Regiona | Circuit Name
1 | 2012-07-05 | Scheduled Outage | Preventive Maintenance | Transformer TE2109 was isolated to allow crew to allow crew to replace leaking transformer. | None | None | 7 | 454 | 53 | East | 77M5
2 | 2012-07-05 | Scheduled Outage | Construction | Transformer X44296 at 1380 Gibson St. isolated to change secondary | None | None | 18 | 297 | 89 | East | UP05
3 | 2012-07-05 | Scheduled Outage | Construction | Transformer X37372 at 48 Bayswater Ave. isolated to allow for service upgrade | None | None | 7 | 105 | 12 | Central | SM12
125002 | 2012-07-05 | Scheduled Outage | Repair | Transformer X36751 at 31 Spring Garden Ave. isolated to repair broken cutout,arrestor and live line clamp. | None | Fused Cutout | 7 | 102 | 12 | South | EPWF5
125003 | 2012-07-05 | Scheduled Outage | Construction | 43F3 red phase O/H between S24482 and Temp 32 was isolated to allow crew to cut in new transformer. | None | None | 9 | 396 | 59 | West | 43F3
125004 | 2012-07-06 | Defective Equipment | Imminent Failure | Transformer X29294 at 635 Industrial isolated to repair leed for cutout | O/H Switchgear | Fused Cutout | 1 | 30 | 0 | East | TB14
125007 | 2012-07-07 | Foreign Interference | Wildlife (Bird/Animal) | squirrel contact | O/H Transformer | O/H Transformer (1ph) | 5 | 63 | 5 | Central | TD14
125008 | 2012-07-07 | Scheduled Outage | Preventive Maintenance | Schedualled outage | None | Transformer | 1 | 252 | 4 | Central | UC05
125009 | 2012-07-07 | Scheduled Outage | Repair | to allow crews to cut secondary services clear after a stub pole was broken by a motor vehicle accident | None | None | 4 | 12 | 1 | East | AF05
125011 | 2012-07-08 | Foreign Interference | Animal | RX2010 Auto reclosed. Squirrel contact at X35526. Transformer refused to restore power. | O/H Transformer | O/H Transformer (1ph) | 4 | 259 | 17 | West | ALEXF3
125013 | 2012-07-08 | Defective Equipment | Equipment Failure - Cause Unknown | Broken switch | O/H Switchgear | Fused Cutout | 538 | 79 | 708 | East | LTM01
125014 | 2012-07-08 | Foreign Interference | Bird | Broken cutout at transformer 860 and dead bird found at base of pole. | O/H Transformer | O/H Transformer (1ph) | 4 | 106 | 7 | East | 7F4
125014 | 2012-07-08 | Foreign Interference | Bird | Broken cutout at transformer 860 and dead bird found at base of pole. | O/H Transformer | O/H Transformer (1ph) | 152 | 185 | 469 | East | 7F4
125015 | 2012-07-08 | Tree Contacts | Inadequate Trimming | Vines on the transformer | O/H Transformer | O/H Transformer (1ph) | 1 | 302 | 5 | East | BLKF5
125017 | 2012-07-08 | Tree Contacts | Inadequate Trimming | Vines around the transformer X32367 | O/H Transformer | O/H Transformer (1ph) | 2 | 230 | 8 | Central | TD06
125018 | 2012-07-08 | Scheduled Outage | Preventive Maintenance | Isolated customer owned primary line to remove tree branch for the line | None | Customer-Owned | 1 | 119 | 2 | West | 624F6
125019 | 2012-07-09 | Scheduled Outage | Preventive Maintenance | 15 redphase transformers out for elbow and insert replacement. | None | Padmount (1ph) | 115 | 226 | 433 | East | 77M2
125021 | 2012-07-09 | Foreign Interference | Animal | Squirrel contact | O/H Transformer | O/H Transformer (1ph) | 80 | 233 | 311 | Central | TD14
125022 | 2012-07-09 | Scheduled Outage | Construction | Isolated transformer X29345 at 255 Bradley Ave to transfer hydro plant | None | None | 35 | 126 | 74 | East | AC14
125024 | 2012-07-09 | Scheduled Outage | Construction | Isolated transformer X39671 to transfer hydro plant | None | None | 4 | 75 | 5 | South | 49F6
125026 | 2012-07-09 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer X33352 at 28 Canter Blvd. isolate to replace broken switch at transformer | O/H Switchgear | Fused Cutout | 5 | 144 | 12 | South | EPWF4
125028 | 2012-07-10 | Unknown/Other | No Apparent Cause | 4801F8 breaker opened, blue phase flag, instantaneous overcurrent trip. No cause found. | Unknown \ Other | Unknown \ Other | 5166 | 10 | 861 | East | 4801F8
125029 | 2012-07-10 | Foreign Interference | Animal | crews report squirrel contact | O/H Switchgear | Fused Cutout | 9 | 117 | 18 | Central | TW22
125030 | 2012-07-10 | Scheduled Outage | Repair | Transformer TP8180W isolated to allow crew to replace leaking transformer | None | None | 10 | 109 | 18 | East | 77M6
125033 | 2012-07-10 | Scheduled Outage | Construction | transfer plant | None | None | 1 | 45 | 1 | West | 43F3
125035 | 2012-07-10 | Scheduled Outage | Construction | transformers at poles X29341 & X29342 isolated to allow crews to tranfer plant | None | None | 20 | 300 | 100 | East | AC14
125036 | 2012-07-10 | Foreign Interference | Vehicle | Dump truck contacted AP04 overhead causing circuit to open. | O/H Conductor | O/H Conductor | 40 | 202 | 135 | East | AP04
125036 | 2012-07-10 | Foreign Interference | Vehicle | Dump truck contacted AP04 overhead causing circuit to open. | O/H Conductor | O/H Conductor | 45 | 181 | 136 | East | AP04
125037 | 2012-07-10 | Scheduled Outage | Construction | Transformer X33726 at 173 Faraday St. isolated to allow for transfer of plant | None | None | 14 | 210 | 49 | Central | SM05
125038 | 2012-07-10 | Foreign Interference | Vehicle | AP04 was hit by a Dump Truck and AP02 line got tangled up with AP04 conductor | O/H Conductor | O/H Conductor | 10 | 396 | 66 | East | AP02
125041 | 2012-07-10 | Defective Equipment | Equipment Failure - Cause Unknown | REPLACE DEFECTIVE SWITCH S22324 | O/H Switchgear | Fused Cutout | 1 | 137 | 2 | West | BRDF2
125042 | 2012-07-10 | Scheduled Outage | Construction | Transformer X28128 at 2589 Egan Rd. isolated to reconnect customer after a service upgrade | None | None | 8 | 60 | 8 | East | UZ04
125043 | 2012-07-10 | Foreign Interference | Animal | Transformer X34290 refused due to animal contact | O/H Transformer | O/H Transformer (1ph) | 10 | 59 | 10 | Central | TD06
125044 | 2012-07-11 | Foreign Interference | Bird | 24/7 CREWS CLEARED CROW FROM TX & REFUSED X24795 | O/H Switchgear | Fused Cutout | 5 | 140 | 12 | East | 8F1
125045 | 2012-07-11 | Scheduled Outage | Construction | TRANSFER PLANT | None | None | 6 | 195 | 20 | Central | SM05
125046 | 2012-07-11 | Defective Equipment | Equipment Failure - Cause Unknown | BROKEN CUTOUTS | O/H Switchgear | Fused Cutout | 3 | 100 | 5 | East | AL03
125048 | 2012-07-11 | Scheduled Outage | Maintenance | Scheduled outage to repair damaged mole sets. | None | None | 1 | 120 | 2 | East | 8F3
125049 | 2012-07-11 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer GLTE0433 at 2166 Loyola Ave. isolated to allow for reconnect after repairs. | Secondary \ Service | U/G Service | 16 | 4 | 1 | East | BCHF5
125050 | 2012-07-11 | Scheduled Outage | Construction | Transformer X29334 at 251 L'Allemand St. isolated to allow for transfer of plant | None | None | 9 | 540 | 81 | East | AC04
125051 | 2012-07-11 | Scheduled Outage | Construction | Transformers X29334 at 251 L'Allemand St., X29331 at 263 L'Allemand St. and X23022 at 267 L'Allemand St. isolated to allow for transfer of plant | None | None | 9 | 540 | 81 | East | AC04
125052 | 2012-07-11 | Scheduled Outage | Preventive Maintenance | To allow customer to upgrade ventialtion in vault. | None | Unknown \ Other | 1 | 474 | 8 | East | BLKF5
125053 | 2012-07-12 | Foreign Interference | Animal | squirrel contact caused xfmr to open | O/H Transformer | O/H Transformer (1ph) | 4 | 77 | 5 | South | 72F4
125054 | 2012-07-12 | Foreign Interference | Dig-In | Dig in | U/G Cable | Transition Splice | 1169 | 36 | 701 | Central | TL5SBTL
125055 | 2012-07-12 | Scheduled Outage | Repair |  | None | Secondary Pedestal | 7 | 43 | 5 | East | BLKF1
125056 | 2012-07-12 | Scheduled Outage | Construction | SERVICE UPGRADE | None | O/H Transformer (1ph) | 10 | 60 | 10 | Central | SB05
125057 | 2012-07-12 | Scheduled Outage | Construction | CREW TRANSFERRING PLANT | None | None | 13 | 30 | 6 | South | 49F6
125059 | 2012-07-12 | Scheduled Outage | Construction | SERVICE CONNECTION | None | None | 22 | 25 | 9 | Central | SB11
125060 | 2012-07-12 | Foreign Interference | Vehicle | delivery truck hit bell wire and pulled out wall clips that also held secondary service it place | Secondary \ Service | O/H Service | 1 | 120 | 2 | Central | SB10
125061 | 2012-07-12 | Foreign Interference | Vehicle | Cement Truck pulled Bell down and broke pole | Pole | Pole | 1 | 369 | 6 | East | 249F2
125061 | 2012-07-12 | Foreign Interference | Vehicle | Cement Truck pulled Bell down and broke pole | Pole | Pole | 15 | 43 | 11 | East | 249F2
125061 | 2012-07-12 | Foreign Interference | Vehicle | Cement Truck pulled Bell down and broke pole | Pole | Pole | 118 | 99 | 195 | East | 249F2
125062 | 2012-07-12 | Defective Equipment | Equipment Failure - Cause Unknown | DEFECTIVE CUTOUT FEED TX AT POLE X33875 | O/H Switchgear | Fused Cutout | 8 | 120 | 16 | Central | UC03
125063 | 2012-07-12 | Scheduled Outage | Repair | To make repairs to burnt secondaries | Secondary \ Service | U/G Service | 7 | 284 | 33 | East | 249F2
125064 | 2012-07-13 | Foreign Interference | Animal |  | U/G Switchgear | Live-Front | 23 | 45 | 17 | East | TB1UQ
125065 | 2012-07-13 | Defective Equipment | Equipment Failure - Cause Unknown | DEFECTIVE CUTOUT | O/H Switchgear | Fused Cutout | 14 | 270 | 63 | Central | UF08
125066 | 2012-07-13 | Scheduled Outage | Construction | SERVICE DIS/RECON | None | None | 12 | 45 | 9 | Central | UV02
125067 | 2012-07-13 | Scheduled Outage | Construction | NEW SERVICE | None | None | 3 | 15 | 1 | East | UQ07
125068 | 2012-07-13 | Foreign Interference | Foreign Object | REMOVAL OF VINES | O/H Transformer | O/H Transformer (1ph) | 6 | 35 | 4 | Central | UV07
125069 | 2012-07-14 | Unknown/Other | Unknown | SCADA indicates the MWDF2 circuit trip open on R phase instantaneous , Cause remains under investigation Crew to patrol circuit in day light SCADA indicate circuit has not auto reclosed | None | None | 1953 | 10 | 326 | West | MWDF2
125070 | 2012-07-14 | Scheduled Outage | Preventive Maintenance | Vault maintence | None | None | 1 | 260 | 4 | Central | UF04
125071 | 2012-07-14 | Foreign Interference | Animal | TRANSFORMER X5040 REFUSED DUE TO ANIMAL CONTACT - SQUIRREL | O/H Switchgear | Fused Cutout | 10 | 19 | 3 | East | 7F2
125072 | 2012-07-14 | Foreign Interference | Dig-In | TRANSFORMER 005704 AT 43 LAURIE ISOLATED TO DISCONNECT THE CUSTOMER AT 41 TO MAKE REPAIRS TO AN U/G SERVICE DUG INTO BY A CITY CONTRACTOR | Secondary \ Service | U/G Service | 7 | 21 | 2 | West | BRDF6
125073 | 2012-07-14 | Foreign Interference | Dig-In | TRANSFORMER 005704 AT 43 LAURIE ISOLATED TO DISCONNECT THE CUSTOMER AT 41 TO MAKE REPAIRS TO AN U/G SERVICE DUG INTO BY A CITY CONTRACTOR | Secondary \ Service | U/G Service | 7 | 9 | 1 | West | BRDF6
125074 | 2012-07-14 | Adverse Environment | Fire |  | None | None | 593 | 201 | 1987 | Central | TR15
125074 | 2012-07-14 | Adverse Environment | Fire |  | None | None | 1913 | 50 | 1594 | Central | TR15
125076 | 2012-07-14 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer 4102-50 at 5261 Driscoll opened due to defective transformer | U/G Transformer | Unknown \ Other | 11 | 589 | 108 | East | 7F4
125077 | 2012-07-14 | Defective Equipment | Electrical Failure | The (TR05)TR1FB circuit tripped open due to cable fault at Main and Beckwith causing an outage on the Bronson SBT4 and SBT3 transformers | U/G Cable | PILC | 8 | 107 | 14 | Central | TR1FB
125077 | 2012-07-14 | Defective Equipment | Electrical Failure | The (TR05)TR1FB circuit tripped open due to cable fault at Main and Beckwith causing an outage on the Bronson SBT4 and SBT3 transformers | U/G Cable | PILC | 2369 | 69 | 2724 | Central | TR1FB
125081 | 2012-07-15 | Lightning | Direct Strike | RX2017 auto-reclosed and locked out during lightning storm. Closed via SCADA and holding. | O/H Conductor | O/H Conductor | 2026 | 18 | 608 | East | 8F1
125082 | 2012-07-15 | Scheduled Outage | Construction | Transformer TE266 was isolated to allow crew to replace cable and transfer riser to new pole. | None | None | 1 | 560 | 9 | East | 6F1
125083 | 2012-07-15 | Foreign Interference | Bird | Crow Contact | O/H Transformer | O/H Transformer (1ph) | 1 | 470 | 8 | West | BECKF2
125084 | 2012-07-16 | Scheduled Outage | Preventive Maintenance | training | None | Padmount (1ph) | 6 | 10 | 1 | Central | UJ04
125085 | 2012-07-16 | Scheduled Outage | Construction | TRANSFERING SECONDARY | None | None | 7 | 40 | 5 | South | 49F6
125086 | 2012-07-16 | Scheduled Outage | Construction | CREW NEEDED ISOLATION TO STRING NEW SECONDARY | None | None | 7 | 100 | 12 | East | AC15
125088 | 2012-07-16 | Human Element | Switching Error | G553 blue phase blew after a crew unintentionally installed a set of grounds on a live conductor that was supposed to be isolated | None | None | 113 | 168 | 316 | East | 8F3
125089 | 2012-07-16 | Scheduled Outage | Construction | TRANSFERING PLANT | None | None | 8 | 235 | 31 | East | UP05
125090 | 2012-07-16 | Scheduled Outage | Construction | TRANSFERING PLANT | None | None | 14 | 255 | 60 | East | UP05
125091 | 2012-07-16 | Scheduled Outage | Construction | 8F3 overhead section in Hydro right of way off of Innes Rd near Blair was isolated to allow crew to replace poles. | None | None | 2 | 375 | 12 | East | 8F3
125092 | 2012-07-16 | Scheduled Outage | Preventive Maintenance | Customer's contractor working on customer's main switchgear in VT60CZZ | None | None | 1 | 612 | 10 | Central | 617
125093 | 2012-07-16 | Tree Contacts | Inadequate Trimming | Refused transformer X33153, trimmed trees and replaced switch | O/H Switchgear | Fused Cutout | 1 | 243 | 4 | West | 28F2
125094 | 2012-07-16 | Scheduled Outage | Construction | TRANSFORMER X27934 ISOLATED TO ALLOW FOR SERVICE UPGRADE | None | None | 6 | 45 | 4 | East | UZ05
125095 | 2012-07-17 | Scheduled Outage | Preventive Maintenance | VT717 was isolated to allow contractor to perform customer vault maintenance.86 Customers were affected | None | None | 86 | 207 | 297 | Central | TK5TS
125096 | 2012-07-17 | Defective Equipment | Equipment Deterioration Due To Age | REPLACE CUTOUT | None | None | 1 | 30 | 0 | East | 249F2
125097 | 2012-07-17 | Scheduled Outage | Construction | ISOLATION TO CUT IN THREE NEW TRANSFORMERS | None | None | 14 | 315 | 74 | West | 28F2
125098 | 2012-07-17 | Loss Of Supply | Transmission Inadvertent | The Beckwith BECKF2 CB open caused by the H1 M29C tripped open due to lightning | None | None | 631 | 4 | 42 | West | BECKF2
125100 | 2012-07-17 | Scheduled Outage | Construction | Isolated transformer TP6797 to install 3 new switchers | None | None | 10 | 503 | 84 | West | 28F2
125101 | 2012-07-17 | Scheduled Outage | Construction | Isolated transformer X23233 at 300 Ste Cecile St to install new pole | None | None | 5 | 530 | 44 | East | AC15
125102 | 2012-07-17 | Foreign Interference | Bird | Bird | O/H Transformer | O/H Transformer (1ph) | 5 | 114 | 10 | East | 7F1
125102 | 2012-07-17 | Foreign Interference | Bird | Bird | O/H Transformer | O/H Transformer (1ph) | 2954 | 1 | 49 | East | 7F1
125103 | 2012-07-17 | Foreign Interference | Bird | Replaced blown fuse feeding transformer X13017 at 520 RIVER RD (Crow) | O/H Transformer | O/H Transformer (1ph) | 5 | 92 | 8 | East | 7F1
125104 | 2012-07-17 | Defective Equipment | Equipment Deterioration Due To Age | Isolated and replaced transformer X32775 at 1965 Garfield Ave due to oil leak | O/H Transformer | O/H Transformer (1ph) | 5 | 188 | 16 | Central | UC05
125105 | 2012-07-18 | Scheduled Outage | Preventive Maintenance | 4kV vault VT407 at 2379 Holly Lane was isolated to allow crews to change PCB transformers | None | Transformer | 1 | 293 | 5 | East | UA06
125106 | 2012-07-18 | Scheduled Outage | Construction | ISOLATION OF X33853 FOR NEW SERVICE CONNECTION | None | O/H Transformer (1ph) | 12 | 57 | 11 | Central | TH01
125108 | 2012-07-18 | Scheduled Outage | Construction | ISOLATION OF X35054 FOR SERVICE CONNECTION | None | None | 6 | 40 | 4 | Central | UW04
125110 | 2012-07-18 | Scheduled Outage | Construction | ISOLATION OF X28178 FOR PLANT TRANSFER | None | None | 14 | 180 | 42 | East | UP05
125112 | 2012-07-18 | Defective Equipment | Equipment Deterioration Due To Age | BLOWN BLUE PHASE FUSE AT S961 | O/H Switchgear | Fused Cutout | 322 | 53 | 284 | South | 49F6
125113 | 2012-07-18 | Scheduled Outage | Repair | OIL REMEDIATION & NEW BASE INSTALLED | U/G Transformer | Padmount (1ph) | 13 | 543 | 118 | West | 39F2
125115 | 2012-07-19 | Foreign Interference | Animal | Transformer #X32852 located at 40 Roundhay Dr opened up due to animal contact | O/H Transformer | O/H Transformer (1ph) | 7 | 133 | 16 | South | 170F1
125116 | 2012-07-19 | Foreign Interference | Animal | Switch G334 at 1117 Elmlea opened due to animal contact at transformer X16855 at 2016 Ogilvie | O/H Transformer | O/H Transformer (1ph) | 1 | 7 | 0 | East | 8F4
125116 | 2012-07-19 | Foreign Interference | Animal | Switch G334 at 1117 Elmlea opened due to animal contact at transformer X16855 at 2016 Ogilvie | O/H Transformer | O/H Transformer (1ph) | 19 | 165 | 52 | East | 8F4
125117 | 2012-07-19 | Scheduled Outage | Construction | Transformer #X35819 located at 29 Tiverton Dr opened by crew for service upgrade | None | None | 8 | 55 | 7 | South | 190F5
125118 | 2012-07-19 | Scheduled Outage | Construction | Trasnformer GLTE2569 at 1753 Meadowbrook was isolated to allow crew to perform pole replacement | None | None | 1 | 155 | 3 | East | 8F3
125119 | 2012-07-19 | Scheduled Outage | Construction | Transformer #X25461 located at 5888 Perth St opened by crew to relocate to new pole | None | O/H Transformer (1ph) | 2 | 237 | 8 | West | 28F3
125120 | 2012-07-19 | Foreign Interference | Bird | Transformer #X12973 located at 3918 Shirley Ave opened up due to crow contact | O/H Transformer | O/H Transformer (1ph) | 8 | 119 | 16 | East | 7F2
125121 | 2012-07-19 | Scheduled Outage | Construction | TE2307 at 1419 Startop was isolated to allow crew to transfer cable dip to new pole | None | None | 1 | 135 | 2 | East | 6F1
125122 | 2012-07-19 | Scheduled Outage | Preventive Maintenance | Transformer TE0096 # 9 Nanaimo was isolated to allow crwe to replace transformer and install new grounding | None | None | 7 | 363 | 42 | South | 160F1
125123 | 2012-07-19 | Scheduled Outage | Preventive Maintenance | VT817 isolated for contractor as part of a planned vault shut down. | None | None | 1 | 137 | 2 | Central | TM1AH
125124 | 2012-07-19 | Foreign Interference | Animal | replaced blown fuse feeding transformer X23047 (squirrel contact) | O/H Transformer | O/H Transformer (1ph) | 4 | 91 | 6 | Central | TK2AC
125125 | 2012-07-20 | Foreign Interference | Animal | Transformer #X37960 located at 92 Southern Dr opened up due to squirrel interference | O/H Transformer | O/H Transformer (1ph) | 9 | 135 | 20 | Central | SR09
125126 | 2012-07-20 | Defective Equipment | Imminent Failure | Transformer #X29489 located at 383 Fullerton Ave opened up due to defective cut out and blown arrestor | O/H Transformer | O/H Transformer (1ph) | 11 | 220 | 40 | East | AA05
125127 | 2012-07-20 | Scheduled Outage | Repair | Transformer #X29491 located at 390 Spartan Ave opened up by crew to replace cutout and arrestor on transformer #X29489 | None | O/H Transformer (1ph) | 9 | 65 | 10 | East | AA05
125129 | 2012-07-20 | Scheduled Outage | Repair | The TEMP43 at Longfield and Paul Metivier was open to allow crew to perform out of phase switching to isolate 140F4 O/H section between TEMP 38 and TEMP43 on Longfield and Paul Metivier | None | Unknown \ Other | 124 | 7 | 14 | South | 140F4
125130 | 2012-07-21 | Defective Equipment | Equipment Failure - Cause Unknown | Line side lead burned off on Switch S10 | O/H Switchgear | Simple Solid Blade Switch | 0 | 1 | 0 | South | EPWF1
125130 | 2012-07-21 | Defective Equipment | Equipment Failure - Cause Unknown | Line side lead burned off on Switch S10 | O/H Switchgear | Simple Solid Blade Switch | 605 | 82 | 827 | South | EPWF1
125131 | 2012-07-21 | Scheduled Outage | Preventive Maintenance | V16 isolated for customer's contractor, performing vault maintenance | None | None | 1 | 123 | 2 | East | UQ08
125133 | 2012-07-21 | Scheduled Outage | Preventive Maintenance | VT233 @ 2020 Walkley Rd was isolated for vault maintenance. To clean and torque the connection and service the disconnects | None | Breaker \ Relay | 1 | 437 | 7 | East | 2203
125134 | 2012-07-21 | Foreign Interference | Animal | ANIMAL CONTACT, FUSE CUTOUT BLOWN @ X36094 | O/H Switchgear | Fused Cutout | 7 | 178 | 21 | Central | TD05
125136 | 2012-07-22 | Scheduled Outage | Preventive Maintenance | VT432 @ 50 Rideau was isolated by the by crew to allow the electricain to make repairs to the cell. | None | Switch | 1 | 139 | 2 | Central | 411
125137 | 2012-07-22 | Scheduled Outage | Preventive Maintenance | VT334 @ 3310 McCarthy was isolated by the crew to allow the contractor to remove asbestos,replace the PCB transformer and clean the vault and torque the connections. | Vault Equipment | Transformer | 1 | 349 | 6 | East | 2207
125139 | 2012-07-22 | Foreign Interference | Animal | 8kV transformer X5363 at 2279 Prince of Whales opened due to animal contact. | None | None | 2 | 41 | 1 | South | 180F4
125140 | 2012-07-22 | Unknown/Other | No Apparent Cause | GR6 locked out. Circuit was patrolled and no cause was found. GR6 also was found blocked in the field. | None | None | 490 | 63 | 514 | East | 249F2
125142 | 2012-07-22 | Foreign Interference | Animal | Refused transformer X39554 - cause due to animal contact - squirrel | O/H Transformer | O/H Transformer (1ph) | 5 | 88 | 7 | South | 84F2
125143 | 2012-07-22 | Foreign Interference | Animal | Refused transformer X37031 - cause due to animal contact - squirrel | O/H Transformer | O/H Transformer (1ph) | 5 | 234 | 20 | South | 49F6
125144 | 2012-07-22 | Unknown/Other | No Apparent Cause | Refused transformer X25226 - no cause found | O/H Switchgear | Fused Cutout | 13 | 245 | 53 | Central | TH11-NIU
125145 | 2012-07-22 | Scheduled Outage | Repair | Low hanging secondary services. | None | O/H Conductor | 10 | 604 | 101 | South | EPWF1
125178 | 2012-07-24 | Adverse Weather | Rain | crew refused transfomer tio restore all load | None | None | 8 | 84 | 11 | Central | TH11-NIU
125181 | 2012-07-24 | Unknown/Other | No Apparent Cause | unknown at this time | None | None | 1154 | 12 | 231 | East | 7F4
125185 | 2012-07-24 | Tree Contacts | Tree Limb Fallen | Transformer #X32816 located at 1253 Erindale Dr opened by crew for Tamarack to remove the branch over 2 triplex services | O/H Transformer | O/H Transformer (1ph) | 13 | 487 | 106 | Central | UW06
125186 | 2012-07-24 | Defective Equipment | Equipment Failure - Cause Unknown |  | U/G Transformer | Padmount (1ph) | 11 | 235 | 43 | West | BRDF3
125188 | 2012-07-25 | Scheduled Outage | Construction | K699 ISOLATED TO ALLOW CREWS TO REPLACE BROKEN POLE | None | Pole | 10 | 285 | 48 | East | UG10
125189 | 2012-07-25 | Scheduled Outage | Repair |  | None | Padmount (1ph) | 10 | 435 | 72 | West | 39F2
125191 | 2012-07-25 | Tree Contacts | Inadequate Trimming |  | None | None | 43 | 207 | 148 | East | 7F4
125192 | 2012-07-25 | Scheduled Outage | Construction | ISOLATION OF X21367 TO REPLACE POLE/PAIL | None | None | 2 | 301 | 10 | East | V11F2
125193 | 2012-07-25 | Scheduled Outage | Construction | ISOLATE X23182 FOR PLANT TRANSFER | None | None | 7 | 377 | 44 | East | AC15
125194 | 2012-07-25 | Foreign Interference | Animal | Transformer #925 located at 1425 Mulligan St opened up due to squirell contact | O/H Transformer | O/H Transformer (1ph) | 1 | 48 | 1 | East | 7F2
125196 | 2012-07-26 | Foreign Interference | Animal | 4kV transformer in the Rear of 32 Lindelea opened due to animal conatact | O/H Transformer | O/H Transformer (1ph) | 14 | 188 | 44 | East | UG09
125197 | 2012-07-26 | Foreign Interference | Animal | Replaced blown fuse feeding transformer X35790 at 2122 HONEYWELL AVE (Squirrel contact) | O/H Transformer | O/H Transformer (1ph) | 13 | 132 | 29 | Central | TD06
125198 | 2012-07-26 | Foreign Interference | Animal | REFUSED TRANSFORMER SWITCH S12446 AT 544 DOVERCOURT AVE. - CAUSE: ANIMAL CONTACT (SQUIRREL) | None | None | 13 | 86 | 19 | Central | TD01
125204 | 2012-07-27 | Foreign Interference | Vehicle | CONSTRUCTION TRUCK DAMAGED PLANT ON POLE X06611 WHEN IT STRUCK THE BELL CABLES | Pole | Pole | 10 | 504 | 84 | West | 624F1
125204 | 2012-07-27 | Foreign Interference | Vehicle | CONSTRUCTION TRUCK DAMAGED PLANT ON POLE X06611 WHEN IT STRUCK THE BELL CABLES | Pole | Pole | 375 | 45 | 281 | West | A9M3
125204 | 2012-07-27 | Foreign Interference | Vehicle | CONSTRUCTION TRUCK DAMAGED PLANT ON POLE X06611 WHEN IT STRUCK THE BELL CABLES | Pole | Pole | 1305 | 3 | 65 | West | A9M3
125204 | 2012-07-27 | Foreign Interference | Vehicle | CONSTRUCTION TRUCK DAMAGED PLANT ON POLE X06611 WHEN IT STRUCK THE BELL CABLES | Pole | Pole | 1365 | 195 | 4436 | West | A9M3
125204 | 2012-07-27 | Foreign Interference | Vehicle | CONSTRUCTION TRUCK DAMAGED PLANT ON POLE X06611 WHEN IT STRUCK THE BELL CABLES | Pole | Pole | 1956 | 36 | 1174 | West | 624F1
125204 | 2012-07-27 | Foreign Interference | Vehicle | CONSTRUCTION TRUCK DAMAGED PLANT ON POLE X06611 WHEN IT STRUCK THE BELL CABLES | Pole | Pole | 1965 | 99 | 3242 | West | 624F1
125204 | 2012-07-27 | Foreign Interference | Vehicle | CONSTRUCTION TRUCK DAMAGED PLANT ON POLE X06611 WHEN IT STRUCK THE BELL CABLES | Pole | Pole | 5766 | 74 | 7111 | West | A9M3
125205 | 2012-07-27 | Scheduled Outage | Construction | ISOLATION OF X34196 FOR SECONDARY TRANSFER | None | None | 12 | 95 | 19 | Central | AH05
125206 | 2012-07-27 | Scheduled Outage | Construction | X33932 ISOLATED FOR SECONDARY TRANSFER | None | None | 12 | 98 | 20 | Central | AH05
125207 | 2012-07-27 | Scheduled Outage | Construction | ISOLATION OF X35047 FOR SERVICE UPGRADE | None | None | 29 | 116 | 56 | Central | AH05
125208 | 2012-07-27 | Defective Equipment | Equipment Failure - Cause Unknown | CREWS FOUND BLOWN ARRESTOR AT S20989 DIP | Pole Attachement | Arrester | 90 | 3 | 4 | West | JKGF4
125208 | 2012-07-27 | Defective Equipment | Equipment Failure - Cause Unknown | CREWS FOUND BLOWN ARRESTOR AT S20989 DIP | Pole Attachement | Arrester | 350 | 12 | 70 | West | JKGF4
125208 | 2012-07-27 | Defective Equipment | Equipment Failure - Cause Unknown | CREWS FOUND BLOWN ARRESTOR AT S20989 DIP | Pole Attachement | Arrester | 354 | 132 | 779 | West | JKGF4
125210 | 2012-07-28 | Scheduled Outage | Preventive Maintenance | Routine vault maintenance & repair cracks in the concrete floor | None | None | 10 | 635 | 106 | Central | TL4TSTL
125211 | 2012-07-28 | Scheduled Outage | Preventive Maintenance | isolated for vault maintenance. | None | None | 1 | 332 | 6 | South | 87F6
125212 | 2012-07-28 | Scheduled Outage | Preventive Maintenance | Vault isolated for maintenance | None | None | 1 | 527 | 9 | East | TO5UB
125213 | 2012-07-28 | Scheduled Outage | Preventive Maintenance |  | None | None | 1 | 271 | 5 | South | 72F2
125214 | 2012-07-28 | Tree Contacts | Inadequate Trimming |  | None | None | 4 | 117 | 8 | West | 624F6
125215 | 2012-07-29 | Scheduled Outage | Preventive Maintenance | Scotia Bank Place Palladium Bay # 1 was isolated to allow Eaton Electric to perform routine vault maintenance. | None | None | 1 | 107 | 2 | West | 624F1
125217 | 2012-07-30 | Scheduled Outage | Preventive Maintenance | Customer owned substation QT131 at 185 Corkstown was isolated to allow contractor to perform customer substation maintenance | None | None | 1 | 448 | 7 | West | A9M2
125218 | 2012-07-30 | Scheduled Outage | Construction | Transformer bus isolated to allow for microfit install | None | None | 1 | 65 | 1 | Central | TR09
125220 | 2012-07-30 | Defective Equipment | Equipment Failure - Cause Unknown | PC10A # 5810 established on G128 to perform repairs. | O/H Switchgear | Recloser (3ph) | 4 | 41 | 3 | East | 6F1
125221 | 2012-07-30 | Scheduled Outage | Construction | Isolated transformer X21663 to replace pole | None | O/H Transformer (1ph) | 15 | 558 | 140 | Central | TR09
125222 | 2012-07-30 | Foreign Interference | Animal | Replaced blown fuse feeding transformer X30801 due to squirrel contact | O/H Transformer | O/H Transformer (1ph) | 24 | 376 | 150 | Central | UX04
125223 | 2012-07-30 | Scheduled Outage | Construction | Isolated and replaced transformer X27523 | None | None | 10 | 594 | 99 | East | UP05
125224 | 2012-07-30 | Scheduled Outage | Construction | Isolated transformer X23179 and X23180 to transfer hydro plant | None | None | 10 | 566 | 94 | East | AC15
125225 | 2012-07-30 | Scheduled Outage | Construction | Isolated transformer X39272 to transfer hydro plant | None | None | 10 | 176 | 29 | East | AC04
125226 | 2012-07-30 | Scheduled Outage | Construction | Isolated transformer X23227 to transfer hydro plant | None | None | 10 | 211 | 35 | East | AC15
125227 | 2012-07-30 | Scheduled Outage | Preventive Maintenance | TE980 at 1344 Youville was isolated to allow contactor to replace building main switch | None | Kiosk (3ph) | 12 | 546 | 109 | East | 77M5
125228 | 2012-07-31 | Scheduled Outage | Construction | TE2596 at 1753 Isolated to allow crews to transfer plant. | None | None | 1 | 165 | 3 | East | 8F3
125229 | 2012-07-31 | Foreign Interference | Animal | H1 bushing refused on transformer X32686 due to animal contact - all power restored | None | None | 9 | 118 | 18 | South | 190F5
125230 | 2012-07-31 | Foreign Interference | Animal | on drop wire from switch - isolated chunk and refused switch at transformer X35688 - due to animal contact | None | None | 5 | 93 | 8 | Central | TD14
125231 | 2012-07-31 | Scheduled Outage | Repair | TRANSFORMER X24840 ISOLATED TO REPLACE CONNECTIONS AT POLE FOR CUSTOMER AT 238 PRINCE ALBERT ST. | None | None | 13 | 34 | 7 | East | SO03
125232 | 2012-07-31 | Scheduled Outage | Preventive Maintenance | sheduled customer maintenance. | None | None | 1 | 158 | 3 | Central | TR1UN
125233 | 2012-07-31 | Scheduled Outage | Construction | Transformer X24636 at 294 Palace St. isolated to install new pole and transfer plant | None | None | 4 | 325 | 22 | East | UT05
125234 | 2012-07-31 | Scheduled Outage | Preventive Maintenance | TRANSFORMER X29897 AT 61 RALPH ST. ISOLATED TO REMOVE VINES | None | None | 7 | 17 | 2 | Central | TR09
125235 | 2012-07-31 | Tree Contacts | Tree Fallen | Isolated transformer X40802 to remove fallen tree from the secondaay | Secondary \ Service | O/H Service | 30 | 46 | 23 | East | TB06
125239 | 2012-07-31 | Adverse Weather | Wind | Replaced blown fuse at transformer X30481 | O/H Transformer | O/H Transformer (3ph) | 5 | 23 | 2 | Central | SM03
125240 | 2012-07-31 | Defective Equipment | Equipment Failure - Cause Unknown | CREWS FOUND DEFECTIVE FUSED CUTOUT & BLOWN LIGHTNING ARRESTOR AT X17764 | O/H Switchgear | Fused Cutout | 98 | 117 | 191 | East | 4801F8
125242 | 2012-07-31 | Scheduled Outage | Construction | Isolated transformer X24632 to transfer hydro plant to new pole | None | None | 10 | 258 | 43 | East | UT05
125243 | 2012-07-31 | Tree Contacts | Inadequate Trimming | Replaced blown fuse feeding transformer X32279 | O/H Transformer | O/H Transformer (1ph) | 4 | 200 | 13 | Central | TD01
125244 | 2012-08-01 | Scheduled Outage | Preventive Maintenance | Transformers TE3517 and TE3518 were isolated to allow crew to take an oil sample at TE3517 | None | Kiosk (3ph) | 1 | 35 | 1 | South | 87F6
125245 | 2012-08-01 | Scheduled Outage | Construction | Isolated transformer X30707 to transfer hydro plant to new pole | Pole | Pole | 14 | 536 | 125 | Central | UN11
125246 | 2012-08-01 | Scheduled Outage | Preventive Maintenance | Isolated transformer X23331 to repair 3 triplex service's | None | None | 10 | 350 | 58 | East | AA04
125247 | 2012-08-01 | Scheduled Outage | Construction | Isolated transformer X18512 to transfer hydro plant to new pole | None | None | 4 | 361 | 24 | East | 249F2
125248 | 2012-08-01 | Scheduled Outage | Construction | Transformer X27698 at 388 Summit Ave was isolated to allow crew to install new service. | None | None | 8 | 40 | 5 | East | TB06
125250 | 2012-08-02 | Scheduled Outage | Preventive Maintenance |  | None | None | 1 | 106 | 2 | Central | TL7TS
125252 | 2012-08-02 | Scheduled Outage | Repair | TRANSFORMER X33865 AT 24 HAMILTON AVE N. ISOLATED TO REPAIR BROKEN CUTOUT | None | Fused Cutout | 6 | 26 | 3 | Central | TH06
125254 | 2012-08-03 | Scheduled Outage | Construction | PC10A# 5757 established by J Lepage on dip pole to K1155 to replace a pole | None | Pole | 2 | 221 | 7 | Central | AK07
125256 | 2012-08-03 | Foreign Interference | Animal | Transformer X26921 was found open due to squirrel contact | O/H Switchgear | Fused Cutout | 13 | 71 | 15 | East | TB15
125257 | 2012-08-03 | Defective Equipment | Imminent Failure | Switch S666 at 33 Lavina Crescent was opened to allow crew to replace switch leads. | O/H Switchgear | Simple Solid Blade Switch | 35 | 22 | 13 | South | 84F6
125259 | 2012-08-04 | Foreign Interference | Bird | Nick Lavac found a dead bird which caused the fuse to blow at transformer X29124 which also caused the fuse to blow at S26818 | O/H Switchgear | Fused Cutout | 7 | 27 | 3 | East | TB15
125259 | 2012-08-04 | Foreign Interference | Bird | Nick Lavac found a dead bird which caused the fuse to blow at transformer X29124 which also caused the fuse to blow at S26818 | O/H Switchgear | Fused Cutout | 41 | 62 | 42 | East | TB15
125262 | 2012-08-05 | Foreign Interference | Animal | Replaced blown fuse at overhead swich SW1232 feeding two padmount transformers (Squirrel conact) | O/H Switchgear | Fused Cutout | 38 | 113 | 72 | West | BECKF2
125263 | 2012-08-05 | Foreign Interference | Animal | Replaced blown fuse feeding transformer X40194 (Squirrel contact ) | O/H Transformer | O/H Transformer (1ph) | 6 | 94 | 9 | South | 200F1
125270 | 2012-08-06 | Foreign Interference | Animal | Refused trans X35249.. Squirrel contact | O/H Transformer | O/H Transformer (1ph) | 8 | 89 | 12 | West | JKGF5
125271 | 2012-08-06 | Foreign Interference | Bird | S26818 re-fused by J Streng restoring all load except for 12 customers fed from X26869 - 20:09, X26869 refused after crow contact | O/H Transformer | O/H Transformer (1ph) | 12 | 18 | 4 | East | TB15
125271 | 2012-08-06 | Foreign Interference | Bird | S26818 re-fused by J Streng restoring all load except for 12 customers fed from X26869 - 20:09, X26869 refused after crow contact | O/H Transformer | O/H Transformer (1ph) | 41 | 71 | 49 | East | TB15
125272 | 2012-08-07 | Defective Equipment | Equipment Deterioration Due To Age | U/G repaired cable fault. | U/G Cable | PILC | 1 | 67 | 1 | East | 2209
125273 | 2012-08-07 | Adverse Environment | Fire | transformers 2622 T1 and T2 were isolated due to a fire in the electrical vault | Vault Equipment | Transformer | 1 | 687 | 11 | West | 624F2
125274 | 2012-08-07 | Scheduled Outage | Construction | INSTALLING NEW TX'S FROM TP6137 TO SC5445 | None | Kiosk (1ph) | 1 | 288 | 5 | West | MWDF3
125278 | 2012-08-07 | Scheduled Outage | Preventive Maintenance | VT229 on the TO3AP isolated for vault maintenance | None | None | 1 | 337 | 6 | East | TO3AP
125280 | 2012-08-07 | Defective Equipment | Equipment Failure - Cause Unknown | 19:04, OMS reports X07436 fuse blew as per customer, M Brown dispatched. | O/H Transformer | O/H Transformer (1ph) | 1 | 358 | 6 | West | 624F6
125281 | 2012-08-07 | Defective Equipment | Equipment Failure - Cause Unknown |  | O/H Switchgear | Unknown \ Other | 1 | 128 | 2 | East | AC15
125282 | 2012-08-07 | Lightning | Direct Strike | Transformer X36011 at 15 Cordova St. refused - cause lightning strike | O/H Switchgear | Fused Cutout | 5 | 109 | 9 | South | EPWF1
125283 | 2012-08-07 | Lightning | Direct Strike | Transformer X41478 at 95 Lotta Ave. refused due to lightning strike | O/H Switchgear | Fused Cutout | 4 | 56 | 4 | South | EPWF1
125285 | 2012-08-07 | Scheduled Outage | Construction | Transformer X23183 at 275 St. Denis St. isolated to allow crew to transfer plant to new pole | None | None | 9 | 240 | 36 | East | AC15
125287 | 2012-08-08 | Lightning | Direct Strike |  | U/G Transformer | Padmount (3ph) | 7 | 240 | 28 | West | JKGF5
125287 | 2012-08-08 | Lightning | Direct Strike |  | U/G Transformer | Padmount (3ph) | 11 | 26 | 5 | West | JKGF5
125290 | 2012-08-08 | Foreign Interference | Animal | SUIRREL | O/H Transformer | O/H Transformer (1ph) | 8 | 91 | 12 | Central | TW22
125292 | 2012-08-08 | Scheduled Outage | Preventive Maintenance |  | None | None | 1 | 201 | 3 | East | SO12
125295 | 2012-08-08 | Loss Of Supply | Transmission Inadvertent | Loss of Supply from Hydro One - Hydro One reports of Bad weather in the area at the time | None | None | 11795 | 7 | 1376 | East | M1R (South Gloucester DS)
125298 | 2012-08-09 | Foreign Interference | Animal | ANIMAL CONTACT | O/H Transformer | O/H Transformer (1ph) | 5 | 123 | 10 | Central | TR3UY
125299 | 2012-08-09 | Scheduled Outage | Preventive Maintenance | scheduled outage for vault cleaning. | None | Unknown \ Other | 3 | 148 | 7 | Central | TR1UN
125300 | 2012-08-09 | Scheduled Outage | Repair | change leaking transformer | None | O/H Transformer (1ph) | 9 | 430 | 64 | East | UA04
125303 | 2012-08-10 | Foreign Interference | Animal | squirrel contact caused fuse S1102 to open. | O/H Switchgear | Fused Cutout | 70 | 42 | 49 | South | 180F4
125304 | 2012-08-10 | Defective Equipment | Equipment Failure - Cause Unknown | Cable fault between G414W to TE1912 | U/G Cable | XLPE | 9 | 344 | 52 | East | LTM01
125305 | 2012-08-10 | Scheduled Outage | Construction | ISOLATION OF X36625 FOR SERVICE UPGRADE | None | O/H Service | 9 | 58 | 9 | South | EPWF1
125309 | 2012-08-11 | Unknown/Other | No Apparent Cause | MWDF2 triped on isnt. Overcurrent W&B phases. Breaker closed in by system and held. No cause found. | None | None | 1401 | 13 | 304 | West | MWDF2
125310 | 2012-08-11 | Defective Equipment | Equipment Failure - Cause Unknown | Defective cut-out caused pole fire at X35846. | Pole | Insulation Failure (Pole Fire) | 2 | 335 | 11 | South | EPWF4
125311 | 2012-08-11 | Foreign Interference | Vehicle | Pole X16136 struck by car. Pole broken and transfomer damaged, pole braced and transformer replaced by on-call. | Pole | Pole | 4 | 469 | 31 | East | 7F4
125313 | 2012-08-11 | Tree Contacts | Tree Fallen | Sleeved primary and refused transformer X39544 at 34 Stinson Ave. - caused by tree on primary on Evergreen. | O/H Conductor | O/H Conductor | 7 | 848 | 99 | South | 47F3
125314 | 2012-08-11 | Defective Equipment | Equipment Failure - Cause Unknown | Replaced transformer switch on X33375 located at 19 Lipstan Ave. | O/H Switchgear | Fused Cutout | 8 | 70 | 9 | South | 190F5
125315 | 2012-08-11 | Defective Equipment | Equipment Failure - Cause Unknown | Changed broken transformer switch on X30451 located at the rear of 131 First Ave. | O/H Switchgear | Fused Cutout | 19 | 123 | 39 | Central | SB06
125316 | 2012-08-11 | Defective Equipment | Equipment Failure - Cause Unknown | Broken cut out on X39144 | O/H Switchgear | Fused Cutout | 3 | 138 | 7 | East | UZ02
125318 | 2012-08-11 | Defective Equipment | Equipment Failure - Cause Unknown | Brokne cut-out at X26822 | O/H Switchgear | Fused Cutout | 9 | 102 | 15 | East | TA3AQ
125319 | 2012-08-11 | Defective Equipment | Equipment Failure - Cause Unknown | Over heated secondary paddle on X26652 due to loose connection | Secondary \ Service | O/H Service | 20 | 67 | 22 | Central | SH05
125320 | 2012-08-12 | Scheduled Outage | Preventive Maintenance | John Streng issued Mark Conrad of Carleton Electric PC10C# 009874 on the isolation of TN6125CZZ | None | Padmount (3ph) | 1 | 800 | 13 | East | 5306
125322 | 2012-08-12 | Tree Contacts | Tree Limb Fallen | Branch on the service to 216 Metcalfe, near transformer X30555 tree is filled with wild bees further complicating things. Decision was made to open the transformer. | None | None | 36 | 221 | 133 | Central | UX03
125323 | 2012-08-12 | Defective Equipment | Equipment Failure - Cause Unknown | Cable fault | U/G Cable | XLPE | 207 | 208 | 718 | East | BCHF5
125324 | 2012-08-12 | Tree Contacts | Inadequate Trimming | Crews opened switch to X23028 to remove a tree brach from the overhead | None | None | 5 | 10 | 1 | East | UG04
125329 | 2012-08-13 | Scheduled Outage | Construction | scheduled outage for transfer of plant | None | None | 8 | 210 | 28 | East | AC15
125330 | 2012-08-13 | Loss Of Supply | Transmission Inadvertent | Hydro One reports M32S tripped at South March on differential. More investigation to be done by Hydro One. An inspection has revealed a defective support insulator as the cause of the South March T1 differential operation. Repairs will be completed th | None | None | 27000 | 13 | 5850 | South | M32S (Nepean TS - T3/T4)
125331 | 2012-08-14 | Defective Equipment | Equipment Failure - Cause Unknown | Switch S19551 red phase at Decarie and Champlain was found blown due to cable fault between TE1196 and TP7052. | U/G Cable | Unknown \ Other | 116 | 14 | 27 | East | 77M6
125331 | 2012-08-14 | Defective Equipment | Equipment Failure - Cause Unknown | Switch S19551 red phase at Decarie and Champlain was found blown due to cable fault between TE1196 and TP7052. | U/G Cable | Unknown \ Other | 158 | 70 | 184 | East | 77M6
125332 | 2012-08-14 | Scheduled Outage | Preventive Maintenance | V639 at 445 richmond rd was isolated to allow contractor remove Asbestos and fro Hydro Crew to replace PCB transformer s | None | None | 1 | 334 | 6 | Central | AH02
125333 | 2012-08-15 | Lightning | Direct Strike | TH09 CB (TH2UL) breaker tripped due to lightning stirke on PPH outside TH STN | Pole Attachement | Arrester | 1498 | 13 | 325 | Central | TH2UL
125334 | 2012-08-15 | Scheduled Outage | Repair | K239 at 35 Corley Pvt was isolated to allow crew to perform remidiation of the soil | None | None | 23 | 582 | 223 | East | UA04
125335 | 2012-08-15 | Scheduled Outage | Preventive Maintenance | VT250 at 1481 Fisher was isolated to allow contractor to perform customer owned vault maintenance | None | None | 1 | 238 | 4 | Central | 303
125336 | 2012-08-15 | Scheduled Outage | Repair | 10 customers were effected in a planned outage to allow crews to reconnected Hydro Ottawa metering tanks on the Beckwith F2 circuit | None | Hot-Line Clamp | 10 | 20 | 3 | West | BECKF2
125337 | 2012-08-15 | Foreign Interference | Bird | Replaced blown fuse feeding transformer X26869 (Bird contact) | O/H Transformer | O/H Transformer (1ph) | 12 | 215 | 43 | East | TB15
125338 | 2012-08-15 | Tree Contacts | Inadequate Trimming | replaced blown fuse feeding tansformer X34212 (tree branch) | O/H Transformer | O/H Transformer (1ph) | 9 | 275 | 41 | Central | UL02
125339 | 2012-08-15 | Scheduled Outage | Preventive Maintenance | K527 at 301 Rochester was isolated to allow crew to replace Kisok transformer to new Pad mount transformer. | None | None | 15 | 196 | 49 | Central | SB14
125342 | 2012-08-15 | Defective Equipment | Equipment Failure - Cause Unknown | Cable fault between UW14 and PPH Switches | U/G Cable | PILC | 563 | 58 | 544 | Central | UW14
125343 | 2012-08-15 | Defective Equipment | Equipment Failure - Cause Unknown | 249F1 A/R when 24/7 attempted to close in a transformer at Bank & Findlay Creek. The transformer feeds City Of Ottawa traffic plant & lighting. The transformer blew when the crew tried to close it back in causing the circuit to A/R | O/H Transformer | O/H Transformer (3ph) | 1 | 95 | 2 | East | LTM01
125343 | 2012-08-16 | Defective Equipment | Equipment Failure - Cause Unknown | 249F1 A/R when 24/7 attempted to close in a transformer at Bank & Findlay Creek. The transformer feeds City Of Ottawa traffic plant & lighting. The transformer blew when the crew tried to close it back in causing the circuit to A/R | O/H Transformer | O/H Transformer (3ph) | 1 | 81 | 1 | East | LTM01
125343 | 2012-08-16 | Defective Equipment | Equipment Failure - Cause Unknown | 249F1 A/R when 24/7 attempted to close in a transformer at Bank & Findlay Creek. The transformer feeds City Of Ottawa traffic plant & lighting. The transformer blew when the crew tried to close it back in causing the circuit to A/R | O/H Transformer | O/H Transformer (3ph) | 3439 | 10 | 573 | East | LTM01
125345 | 2012-08-16 | Scheduled Outage | Preventive Maintenance | Vault Maintenance | None | None | 1 | 170 | 3 | Central | 409
125349 | 2012-08-17 | Scheduled Outage | Repair | TE2122 & TE2121 ISOLATED FOR CONTRACTOR TO REPAIR SECONDARY DAMAGES DUE TO MICE | None | U/G Service | 1 | 273 | 5 | South | 140F3
125350 | 2012-08-17 | Human Element | Switching Error | SWITCHING ERROR AT S75-3, CREWS TOUCHED METAL CLAD WHILE INSTALLING FUSE (RED PHASE) - CAUSED A FLASH | None | None | 7 | 105 | 12 | West | BRDF1
125350 | 2012-08-17 | Human Element | Switching Error | SWITCHING ERROR AT S75-3, CREWS TOUCHED METAL CLAD WHILE INSTALLING FUSE (RED PHASE) - CAUSED A FLASH | None | None | 20 | 60 | 20 | West | BRDF1
125350 | 2012-08-17 | Human Element | Switching Error | SWITCHING ERROR AT S75-3, CREWS TOUCHED METAL CLAD WHILE INSTALLING FUSE (RED PHASE) - CAUSED A FLASH | None | None | 301 | 13 | 65 | West | BRDF1
125350 | 2012-08-17 | Human Element | Switching Error | SWITCHING ERROR AT S75-3, CREWS TOUCHED METAL CLAD WHILE INSTALLING FUSE (RED PHASE) - CAUSED A FLASH | None | None | 301 | 36 | 181 | West | BRDF1
125350 | 2012-08-17 | Human Element | Switching Error | SWITCHING ERROR AT S75-3, CREWS TOUCHED METAL CLAD WHILE INSTALLING FUSE (RED PHASE) - CAUSED A FLASH | None | None | 2175 | 1 | 36 | West | BRDF1
125350 | 2012-08-17 | Human Element | Switching Error | SWITCHING ERROR AT S75-3, CREWS TOUCHED METAL CLAD WHILE INSTALLING FUSE (RED PHASE) - CAUSED A FLASH | None | None | 2175 | 9 | 326 | West | BRDF1
125352 | 2012-08-19 | Defective Equipment | Equipment Failure - Cause Unknown | AD06 breaker tripped open due to a blown arrestor at transformer X32226 at 1012 Silver. | Pole Attachement | Arrester | 16 | 76 | 20 | Central | AD06
125352 | 2012-08-19 | Defective Equipment | Equipment Failure - Cause Unknown | AD06 breaker tripped open due to a blown arrestor at transformer X32226 at 1012 Silver. | Pole Attachement | Arrester | 646 | 8 | 86 | Central | AD06
125354 | 2012-08-19 | Lightning | Direct Strike | Lightning storm, 140F4 opened due to a lightning strike. System closed it back in 5 mins later. | None | None | 988 | 5 | 82 | South | 140F4
125363 | 2012-08-20 | Tree Contacts | Inadequate Trimming | VINES WRAPPED AROUND EQUIPMENT - REMOVED AND REFUSED | O/H Switchgear | Fused Cutout | 6 | 165 | 16 | South | 200F1
125364 | 2012-08-20 | Scheduled Outage | Construction | At 09:45, transformer X27364 was isolated to upgrade service. 3 customers affected for 45 minutes. Queens (UQ07) Id #125364. | None | O/H Transformer (1ph) | 3 | 45 | 2 | East | UQ07
125365 | 2012-08-20 | Scheduled Outage | Construction | AT 08:30, TRANSFORMER X23183 WAS ISOLATED TO ALLOW CREWS TO TRANSFER PLANT. 9 CUSTOMERS AFFECTED. DAGMER (AC15) ID #125365 GREG BRASS - B&M | None | O/H Transformer (1ph) | 9 | 290 | 44 | East | AC15
125367 | 2012-08-20 | Foreign Interference | Dig-In | Dig in by sewer contractor. | U/G Cable | XLPE | 91 | 138 | 209 | West | BRDF4
125367 | 2012-08-20 | Foreign Interference | Dig-In | Dig in by sewer contractor. | U/G Cable | XLPE | 152 | 75 | 190 | West | BRDF4
125367 | 2012-08-20 | Foreign Interference | Dig-In | Dig in by sewer contractor. | U/G Cable | XLPE | 200 | 122 | 407 | West | BRDF4
125368 | 2012-08-20 | Scheduled Outage | Repair | Customer cable replacement by Hydro Ottawa Undeground crew | None | None | 1 | 445 | 7 | Central | 617
125369 | 2012-08-20 | Defective Equipment | Equipment Deterioration Due To Age | 77M6 Red Phase Cable Fault between TE1196 and TP7052 | U/G Cable | XLPE | 42 | 33 | 23 | East | 77M6
125369 | 2012-08-20 | Defective Equipment | Equipment Deterioration Due To Age | 77M6 Red Phase Cable Fault between TE1196 and TP7052 | U/G Cable | XLPE | 79 | 130 | 171 | East | 77M6
125370 | 2012-08-20 | Foreign Interference | Animal | Racoon contact on O/H transformer X32522 | O/H Transformer | O/H Transformer (1ph) | 10 | 134 | 22 | Central | TD01
125371 | 2012-08-21 | Scheduled Outage | Construction | Interruption required for voltage conversion cutover. | None | None | 140 | 333 | 777 | East | UP05
125372 | 2012-08-21 | Tree Contacts | Inadequate Trimming | REPLACED BLOWN FUSE FEEDING TRANSFORMER X24658 (TREE BRANCH ON THE SECONDAY BUSS) | O/H Transformer | O/H Transformer (1ph) | 6 | 177 | 18 | East | UG02
125373 | 2012-08-21 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X23437 TO TRANSFER HYDRO PLANT | None | None | 1 | 120 | 2 | East | AC04
125374 | 2012-08-21 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X26251 TO TRANSFER HYDRO PLANT | None | None | 10 | 170 | 28 | East | AC15
125378 | 2012-08-21 | Scheduled Outage | Construction | Transformer X26251 at 269 Montfort St. isolated to allow for transfer of plant | None | None | 2 | 300 | 10 | East | AC15
125379 | 2012-08-21 | Scheduled Outage | Construction | Transformer X29343 at 271 Montfort St. isolated to allow for transfer of plant | None | None | 10 | 222 | 37 | East | AC15
125380 | 2012-08-21 | Foreign Interference | Bird | Refused transformer X39575 at 15 Mowbray St. - caused by crow | O/H Transformer | O/H Transformer (1ph) | 1 | 174 | 3 | West | 624F6
125381 | 2012-08-22 | Scheduled Outage | Construction | AT 09:38: SECTION ISOLATED FROM S25763 TO INCLUDE TP8231 FOR ELBOW & INSERT REPLACEMENT. 65 CUSTOMERS AFFECTED. Billberry creek (77M2) ID #125381 | None | Elbow \ Insert | 65 | 271 | 294 | East | 77M2
125382 | 2012-08-22 | Scheduled Outage | Construction | At 09:10, BRDF7 sections isolated to allow crews to transfer load to the RED phase. 198 customers affected. Bridlewood (BRDF7) ID #125382 | None | Fused Cutout | 198 | 18 | 59 | West | BRDF7
125383 | 2012-08-22 | Scheduled Outage | Construction | transformer T323 was isolated to allow crews to connect secondary services. | None | Padmount (1ph) | 9 | 65 | 10 | East | BCHF8
125386 | 2012-08-22 | Foreign Interference | Bird | replaced blown fuse feeding transformer X31958 (Crow contact) | O/H Transformer | O/H Transformer (1ph) | 13 | 120 | 26 | Central | SR09
125387 | 2012-08-22 | Scheduled Outage | Repair | Isolated transformer X35564 to replace blown arrester | Pole Attachement | Arrester | 2 | 15 | 0 | South | 606F2
125388 | 2012-08-22 | Defective Equipment | Equipment Deterioration Due To Age | Replaced broken switch feeding transformer X34835 | O/H Switchgear | Fused Cutout | 19 | 83 | 26 | Central | UF07
125389 | 2012-08-22 | Unknown/Other | No Apparent Cause | Crew patrolled line and could not find reason for fuse to blow at G673W at 5140 Limebank Road. | None | None | 12 | 60 | 12 | East | 7F4
125391 | 2012-08-22 | Scheduled Outage | Construction | Transformer X29333 at 253 Carillon St. isolated to allow for transfer of plant | None | None | 7 | 360 | 42 | East | AC14
125394 | 2012-08-23 | Foreign Interference | Foreign Object | AT 08:45, O/H TX X002787 FUSED CUTOUT BLEW DUE BEING STRUCK BY A BELL WIRE. 1 CUSTOMER AFFECTED FOR 60 MINUTES. ALEXANDER (ALEXF1) ID #125394 | O/H Switchgear | Fused Cutout | 1 | 60 | 1 | West | ALXF1 (Alexander DS)
125396 | 2012-08-23 | Scheduled Outage | Construction | Isolated transformer X31791 to transfer hydro plant | None | None | 4 | 25 | 2 | Central | UJ06
125398 | 2012-08-23 | Human Element | Switching Error | 589 customers were affected on the BHCF5 circuit due to a switching error. | None | None | 589 | 31 | 304 | East | BCHF5
125399 | 2012-08-23 | Defective Equipment | Imminent Failure | Replaced transformer X29337 (Leaking oil) | O/H Transformer | O/H Transformer (1ph) | 13 | 65 | 14 | East | AC14
125400 | 2012-08-24 | Scheduled Outage | Preventive Maintenance | 19 customers on Rossland were affected to replace a defective TX at 36 Rossland. | None | None | 19 | 85 | 27 | South | EPWF2
125402 | 2012-08-24 | Foreign Interference | Vehicle | UZ12 CB tripped open due to downed conductor at 3767 Revelstoke caused by truck hitting O/H wires | O/H Conductor | O/H Conductor | 11 | 210 | 38 | East | UZ12
125402 | 2012-08-24 | Foreign Interference | Vehicle | UZ12 CB tripped open due to downed conductor at 3767 Revelstoke caused by truck hitting O/H wires | O/H Conductor | O/H Conductor | 275 | 6 | 28 | East | UZ12
125403 | 2012-08-24 | Foreign Interference | Bird | The 249F1 circuit tripped opened due to crow contact at 4120 Belgreen | O/H Switchgear | Fused Cutout | 18 | 105 | 32 | East | LTM01
125403 | 2012-08-24 | Foreign Interference | Bird | The 249F1 circuit tripped opened due to crow contact at 4120 Belgreen | O/H Switchgear | Fused Cutout | 3457 | 5 | 288 | East | LTM01
125404 | 2012-08-24 | Defective Equipment | Equipment Failure - Cause Unknown | Replaced defective switch S358 at 52 Holborn Ave. | O/H Switchgear | Inline Switch | 19 | 353 | 112 | South | 180F4
125406 | 2012-08-24 | Scheduled Outage | Repair | Replaced jumper between 2 bushings at transformer X25668 located at 93 Sherbrooke Ave. | None | None | 22 | 35 | 13 | Central | UJ07
125407 | 2012-08-24 | Defective Equipment | Equipment Failure - Cause Unknown | A leaking Transformer GLTE3066 (TP9659) was isolated for replacement. | U/G Transformer | Padmount (1ph) | 11 | 132 | 24 | East | 7F1
125408 | 2012-08-24 | Scheduled Outage | Repair | Transformer TP6894 at 6410 Glen Knolls Dr. isolated to reconnect service at 6413 Glen Knolls Drive after repairs completed by contractor. | None | None | 12 | 20 | 4 | East | 77M1
125409 | 2012-08-25 | Scheduled Outage | Construction | Planned outage for overhead reconfiguration | None | None | 3 | 345 | 17 | South | 200F6
125410 | 2012-08-25 | Scheduled Outage | Repair | Customer contractor performing fuse co-ordination study and cable repair | None | None | 1 | 440 | 7 | Central | 306
125411 | 2012-08-25 | Scheduled Outage | Repair | Customer contractor performing secondary work, no work in vault | None | None | 1 | 811 | 14 | Central | TR2TS
125412 | 2012-08-25 | Human Element | Commissioning Error | Human error while testing new OMS system | None | None | 2 | 1 | 0 | Central | 417
125412 | 2012-08-25 | Human Element | Commissioning Error | Human error while testing new OMS system | None | None | 130 | 1 | 2 | Central | 404
125413 | 2012-08-25 | Scheduled Outage | Preventive Maintenance | VT 54 was isolated to allow contractor to clean & torque connections | None | Customer-Owned | 1 | 1483 | 25 | Central | 602
125414 | 2012-08-26 | Scheduled Outage | Preventive Maintenance | Planned outage for vault maintenance | None | None | 1 | 172 | 3 | South | 87F1
125415 | 2012-08-26 | Foreign Interference | Animal | Animal contact on xfrmr X29859 | O/H Transformer | O/H Transformer (1ph) | 8 | 111 | 15 | Central | TR09
125416 | 2012-08-26 | Foreign Interference | Animal | TX X39337 FUSED CUT OUT BLOWN DUE TO ANIMAL CONTACT. | O/H Transformer | O/H Transformer (1ph) | 12 | 85 | 17 | Central | TR3UY
125417 | 2012-08-27 | Defective Equipment | Equipment Failure - Cause Unknown | fused cutout at X24026 found defective. | O/H Switchgear | Fused Cutout | 21 | 40 | 14 | East | UT06
125418 | 2012-08-27 | Scheduled Outage | Construction | Secondary installation of Microfit | None | None | 2 | 220 | 7 | South | 606F2
125419 | 2012-08-27 | Scheduled Outage | Construction | Transformer X16262 at 5741 Mitch Owens Rd isolated to relocate plant to new pole | None | None | 2 | 90 | 3 | East | 56F2
125420 | 2012-08-27 | Scheduled Outage | Construction | Transformer X16247 at 5517 Mitch Owens Rd isolated to relocate plant to new pole | None | None | 4 | 90 | 6 | East | 56F2
125421 | 2012-08-27 | Scheduled Outage | Construction | Isolated transformers X29330 and X26082 to transfer hydro plant to new poles | None | None | 22 | 390 | 143 | East | AC04
125422 | 2012-08-27 | Scheduled Outage | Construction | Isolated transformers X16264 and X16265 to transfer hydro plant to new poles | None | None | 5 | 75 | 6 | East | 56F2
125423 | 2012-08-28 | Scheduled Outage | Construction | Moving O/H conductor on cable dip pole feeding vault. V472 at 257 Lisgar isolated. | None | None | 1 | 295 | 5 | Central | UX10
125424 | 2012-08-28 | Scheduled Outage | Construction | V473 isolated to allow crew to move O//H Conductor | None | None | 1 | 260 | 4 | Central | UX10
125425 | 2012-08-28 | Scheduled Outage | Preventive Maintenance | Elbow and insert replacement. | None | None | 63 | 211 | 222 | East | 77M2
125426 | 2012-08-28 | Scheduled Outage | Construction | ISOLATION OF X33203 FOR PLANT TRANSFER | None | None | 9 | 63 | 9 | Central | TD05
125427 | 2012-08-28 | Scheduled Outage | Preventive Maintenance | Routine Vault maintenance | None | None | 1 | 328 | 5 | Central | UV02
125428 | 2012-08-28 | Scheduled Outage | Construction | V550 at 261 Montreal was isolated to allow crew to transfer plant to new pole | None | None | 1 | 274 | 5 | East | AC04
125429 | 2012-08-29 | Defective Equipment | Equipment Failure - Cause Unknown |  | U/G Cable | Unknown \ Other | 22 | 10 | 4 | East | 77M6
125429 | 2012-08-29 | Defective Equipment | Equipment Failure - Cause Unknown |  | U/G Cable | Unknown \ Other | 66 | 187 | 206 | East | 77M6
125430 | 2012-08-29 | Scheduled Outage | Construction | To transfer O/H plant to a new pole | None | None | 1 | 430 | 7 | East | AC04
125431 | 2012-08-29 | Adverse Environment | Fire | Vault was damage in vault fire. | Customer Owned | Customer-Owned | 1 | 1554 | 26 | Central | TK2AC
125432 | 2012-08-29 | Scheduled Outage | Construction | Transformer X26936 at 1730 Kilborn Ave. isolated to allow for tying in of neutral | None | None | 4 | 60 | 4 | East | AJ06
125434 | 2012-08-29 | Defective Equipment | Equipment Deterioration Due To Age | Isolated transformer X36625 to replace defectiv secondary connection at the transformer | Secondary \ Service | O/H Service | 9 | 15 | 2 | South | EPWF1
125435 | 2012-08-30 | Scheduled Outage | Repair | PC17-75478 completed by Mark Brown to isolate V281 @ 1030 Pere Charlebois to repair OCB and fence | None | None | 1 | 382 | 6 | East | SO12
125436 | 2012-08-30 | Scheduled Outage | Construction | ISOLATION OF TP7580 TO PULL NEW CABLE | None | None | 1 | 135 | 2 | East | 77M6
125437 | 2012-08-30 | Scheduled Outage | Construction | To re-insulate hydro pole | None | O/H Conductor | 15 | 315 | 79 | East | UP05
125438 | 2012-08-31 | Defective Equipment | Equipment Deterioration Due To Age | X33797 at 1139 Minnetonka had a broken cutout | O/H Switchgear | Fused Cutout | 11 | 210 | 38 | Central | UW04
125439 | 2012-08-31 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One, Hydro One reports trip on the S7M | None | None | 2476 | 6 | 248 | West | S7M (Richmond MTS)
125439 | 2012-08-31 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One, Hydro One reports trip on the S7M | None | None | 7593 | 6 | 759 | West | S7M (Marchwood MTS)
125439 | 2012-08-31 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One, Hydro One reports trip on the S7M | None | None | 11228 | 6 | 1123 | South | S7M (Fallowfield - T1/T2)
125439 | 2012-08-31 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One, Hydro One reports trip on the S7M | None | None | 15394 | 6 | 1539 | West | S7M (Bridlewood MTS - T1/T2)
125440 | 2012-08-31 | Scheduled Outage | Construction | Transformer X23107 at 117 Beechwood Ave. isolated to transfer plant to new pole | None | None | 14 | 32 | 7 | East | AC06
125441 | 2012-08-30 | Scheduled Outage | Construction | ISOLATION OF X27513 FOR PLANT TRANSFER | None | None | 6 | 1800 | 180 | East | UP05
125442 | 2012-08-31 | Lightning | Direct Strike | Lightning struck transformer X39608 which caused the fuse S23526 to blow at 4334 Cedarview | O/H Transformer | O/H Transformer (1ph) | 1 | 222 | 4 | South | 606F1
125443 | 2012-08-31 | Defective Equipment | Equipment Deterioration Due To Age | While repairing a customer service in K189. The primary insulators broke in the Kiosk. Oncall cable crew replaced the insulators and restored power to K189. | U/G Transformer | Kiosk (1ph) | 20 | 211 | 70 | East | UZ02
125444 | 2012-09-02 | Foreign Interference | Animal | Replaced blown fuse feeding transformer X35249 (Squirrel contact) | O/H Transformer | O/H Transformer (1ph) | 9 | 40 | 6 | West | JKGF5
125445 | 2012-09-02 | Foreign Interference | Animal | Replaced blown fuse feeding transformer X06230 (Squirrel contact) | O/H Transformer | O/H Transformer (1ph) | 1 | 100 | 2 | South | 180F4
125446 | 2012-09-02 | Foreign Interference | Animal | Animal Contact | None | None | 10 | 51 | 8 | Central | TD14
125447 | 2012-09-03 | Foreign Interference | Animal | Animal Contact | None | None | 12 | 45 | 9 | Central | TD06
125451 | 2012-09-03 | Unknown/Other | No Apparent Cause | replaced blown fuse feeding transformer 5830 | O/H Transformer | O/H Transformer (1ph) | 1 | 91 | 2 | East | 249F2
125452 | 2012-09-03 | Scheduled Outage | Preventive Maintenance | Customer vault isolated for maintenance. | None | None | 1 | 203 | 3 | West | A9M1
125453 | 2012-09-03 | Foreign Interference | Vehicle | reported farm equipment pulled down primary & secondary O/H | O/H Conductor | O/H Conductor | 14 | 175 | 41 | East | 7F4
125454 | 2012-09-04 | Scheduled Outage | Construction | Vault V198 at 175 Bronson was isolated to allow crew to ransfer conductores to new pole. | None | None | 131 | 155 | 338 | Central | AM04
125455 | 2012-09-04 | Foreign Interference | Vandalism | crew energized new cable from TP5385 @ 11 calderwood when power went out due to cut riser cable at pole X4723 with switch S7110. Vadalism is suspected. | U/G Cable | XLPE | 96 | 30 | 48 | South | 606F1
125456 | 2012-09-04 | Scheduled Outage | Construction | CYRF1 section on Renaud Rd and Mer Bleue was isolated to allow crew to relocate overhead lines to new pole. | None | None | 104 | 8 | 14 | East | CYRF1
125458 | 2012-09-04 | Scheduled Outage | Construction | ISOLATION OF X27597 FOR PLANT TRANSFER | None | None | 23 | 343 | 131 | Central | UN05
125459 | 2012-09-04 | Scheduled Outage | Construction | Transformer 55D4B-0005 at 44 Adelaide St. isolated for service work | None | None | 13 | 60 | 13 | Central | SB05
125460 | 2012-09-04 | Scheduled Outage | Construction | Transformer X23589 at 111 Putman Ave. isolated to allow for transfer of plant | None | None | 26 | 80 | 35 | East | AC06
125461 | 2012-09-05 | Tree Contacts | Tree Limb Fallen | Ottawa Fire reports wires down infront of substation. | O/H Conductor | O/H Conductor | 559 | 317 | 2953 | Central | UJ02
125462 | 2012-09-05 | Scheduled Outage | Construction | ISOLATION OF X23106 FOR PLANT TRANSFER | None | None | 10 | 148 | 25 | East | AC06
125463 | 2012-09-05 | Scheduled Outage | Construction | ISOLATION OF X27595 FOR PLANT TRANSFER | None | None | 11 | 240 | 44 | Central | UN05
125464 | 2012-09-05 | Scheduled Outage | Construction | ISOLATION OF X27593 FOR PLANT TRANSFER | None | None | 21 | 288 | 101 | Central | UN05
125465 | 2012-09-05 | Scheduled Outage | Repair | Transformer 3452B was isolated to change transformer. | None | Padmount (1ph) | 10 | 206 | 34 | West | 24F5
125466 | 2012-09-05 | Scheduled Outage | Construction | Transformers TE439, TE440 and TE441 on Loyola were isolated to allow crew to remove old cables and install and connect new ones. | None | None | 40 | 370 | 247 | East | BCHF5
125467 | 2012-09-05 | Scheduled Outage | Repair | Transformer at 4082 Canyon Walk was isolated to clean up a transformer leak. | None | None | 11 | 575 | 105 | East | 7F1
125468 | 2012-09-05 | Scheduled Outage | Construction | Transformer bus @ TP2969 in Casselman was isolated for a Microfit installation. | None | None | 1 | 103 | 2 | East | V11F1
125469 | 2012-09-05 | Loss Of Supply | Transmission Inadvertent | Loss of supply. No cause determined. | None | None | 6836 | 1 | 114 | West | A9M1
125470 | 2012-09-06 | Scheduled Outage | Repair |  | None | Padmount (1ph) | 9 | 138 | 21 | West | MWDF2
125471 | 2012-09-06 | Scheduled Outage | Preventive Maintenance |  | None | None | 1 | 222 | 4 | Central | SK10
125472 | 2012-09-06 | Scheduled Outage | Construction | ISOLATION OF 65A3B-0570 FOR CREW | None | None | 9 | 61 | 9 | East | AC06
125473 | 2012-09-06 | Scheduled Outage | Repair | LEAKING TRANSFORMER | None | None | 9 | 150 | 22 | West | MWDF2
125474 | 2012-09-06 | Scheduled Outage | Construction | ISOLATION OF X34726 FOR PLANT TRANSFER | None | None | 21 | 240 | 84 | Central | UN05
125475 | 2012-09-06 | Scheduled Outage | Construction | Voltage Upgrade from 4kV to 13kV | None | None | 121 | 200 | 403 | East | UP05
125476 | 2012-09-07 | Scheduled Outage | Preventive Maintenance | Routine Vault Maintenance | None | None | 1 | 193 | 3 | Central | SK13
125479 | 2012-09-08 | Unknown/Other | Unknown | S-254 W PHASE FUSE WAS FOUND BLOWN. SC2702-L WAS OPENED TO ALLOW CREW TO CLOSE S-254 W AFTER IT WAS REFUSED. | None | None | 132 | 1 | 2 | East | 2206
125483 | 2012-09-08 | Lightning | Lightning | TH04 CB opened during Thunder storm. Circuit was closed and held via SCADA after police, fire and Lemieux Island were contacted. | None | None | 50 | 30 | 25 | Central | 4301
125488 | 2012-09-08 | Scheduled Outage | Preventive Maintenance | VE69 & VE62 @ 1400 Blair Place was isolated by the crew to allow the electrician to preform vault maintenance and torque the connections | None | Unknown \ Other | 2 | 317 | 11 | East | 8F4
125490 | 2012-09-08 | Scheduled Outage | Repair | Transformer X35375 at Britannia and Regina isolated to allow for temporary repairs to primary bushing. | None | None | 10 | 11 | 2 | Central | TD14
125491 | 2012-09-08 | Adverse Weather | Rain | Refused G540 at 4476 Farmer's Way, patrolled, no cause found | O/H Switchgear | Fused Cutout | 48 | 192 | 154 | East | 249F2
125494 | 2012-09-08 | Lightning | Direct Strike | Storm in the Ottawa area, severe lightning and heavy rain, possible ligthing strike at 1635 Eagleson Rd causing damage to transformer X35907 and conductor down, switch S23681 was open to allow the crews repaired down conductor | O/H Transformer | O/H Transformer (1ph) | 1 | 55 | 1 | South | 145F3
125494 | 2012-09-08 | Lightning | Direct Strike | Storm in the Ottawa area, severe lightning and heavy rain, possible ligthing strike at 1635 Eagleson Rd causing damage to transformer X35907 and conductor down, switch S23681 was open to allow the crews repaired down conductor | O/H Transformer | O/H Transformer (1ph) | 3 | 55 | 3 | South | 145F3
125494 | 2012-09-08 | Lightning | Direct Strike | Storm in the Ottawa area, severe lightning and heavy rain, possible ligthing strike at 1635 Eagleson Rd causing damage to transformer X35907 and conductor down, switch S23681 was open to allow the crews repaired down conductor | O/H Transformer | O/H Transformer (1ph) | 5 | 120 | 10 | South | 145F3
125495 | 2012-09-08 | Lightning | Lightning | X32634 was found defective due to lightning strike. | None | None | 16 | 480 | 128 | Central | TD14
125497 | 2012-09-08 | Lightning | Lightning Strike On Adjacent Circuit | UJ03 CB auto-reclosed and locked out during storm. Time overcurrent trip flags on all three phases | Unknown \ Other | Unknown \ Other | 457 | 5 | 38 | Central | UJ03
125498 | 2012-09-08 | Lightning | Lightning Strike On Adjacent Circuit | 249F2 auto-reclosed and RX2041 tripped during lightning storm | Unknown \ Other | Unknown \ Other | 216 | 5 | 18 | East | 249F2
125499 | 2012-09-08 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer switch at X26061 was found to be defective. Crew replaced switch and restored all affected customers | O/H Transformer | O/H Transformer (1ph) | 16 | 189 | 50 | East | AE02
125500 | 2012-09-08 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer X36645 was opened to allow crew to replace hot line clamp | O/H Conductor | Hot-Line Clamp | 6 | 5 | 0 | South | EPWF1
125501 | 2012-09-08 | Defective Equipment | Equipment Failure - Cause Unknown | Possible lightning strike to S19551. | U/G Cable | XLPE | 44 | 230 | 169 | East | 77M6
125502 | 2012-09-07 | Adverse Weather | Rain | 606CST1 tripped out under differential. All load was tranfered to back up supply. | Unknown \ Other | Unknown \ Other | 3957 | 38 | 2506 | South | 606F2
125502 | 2012-09-07 | Adverse Weather | Rain | 606CST1 tripped out under differential. All load was tranfered to back up supply. | Unknown \ Other | Unknown \ Other | 4731 | 21 | 1656 | South | 606F1
125504 | 2012-09-09 | Scheduled Outage | Preventive Maintenance | VT242 at 300 Laurier isolated for vault maintenance. | None | None | 1 | 678 | 11 | Central | 5207
125505 | 2012-09-09 | Scheduled Outage | Repair | Transformer X17758 at 39 McGill Pvt isolated to allow for repairs to secondary connections | None | None | 19 | 14 | 4 | East | 4801F8
125506 | 2012-09-09 | Defective Equipment | Equipment Failure - Cause Unknown | DEFECTIVE TRANSFORMER AT VE74 - CREWS FOUND LID BLOWN OFF | Vault Equipment | Transformer | 1 | 602 | 10 | East | 7F2
125510 | 2012-09-10 | Defective Equipment | Equipment Failure - Cause Unknown | Suspected cable fault between TE540 and TP9364 | U/G Cable | XLPE | 87 | 336 | 487 | East | BCHF8
125512 | 2012-09-10 | Scheduled Outage | Construction | Isolated and relocated transformer X23589 to new pole | None | None | 26 | 238 | 103 | East | AC06
125513 | 2012-09-10 | Scheduled Outage | Construction | V210 at 180 Bruyere was isolated to allow customer to perform major vault maintenance. Customer will be on generator for 5 days. | None | None | 1 | 18 | 0 | Central | SK13
125515 | 2012-09-10 | Foreign Interference | Dig-In | Replaced blown fuse feeding transformer TP3111 (Possible dig in) | O/H Transformer | O/H Transformer (1ph) | 9 | 76 | 11 | East | BCHF3
125516 | 2012-09-10 | Scheduled Outage | Construction | ISOLATION OF X24458 FOR INSULATOR REPLACEMENT | None | None | 12 | 70 | 14 | East | 77M6
125517 | 2012-09-10 | Scheduled Outage | Preventive Maintenance | Elbow & insert upgrade | None | None | 65 | 310 | 336 | East | 77M2
125518 | 2012-09-10 | Scheduled Outage | Construction | Isolated transformers X17833 and X35608 to transfer hydro plant | None | None | 16 | 110 | 29 | Central | AH13
125521 | 2012-09-11 | Unknown/Other | No Apparent Cause | RX2017 opened under hold off protection, holder clear of line and circuit restored via SCADA | None | None | 1728 | 12 | 346 | East | 8F1
125522 | 2012-09-11 | Scheduled Outage | Construction | ISOLATION OF X16136 FOR TRANSFER OF PLANT | None | None | 4 | 120 | 8 | East | 56F1
125523 | 2012-09-11 | Scheduled Outage | Construction | ISOLATION OF X35662 FOR SERVICE UPGRADE | None | None | 8 | 45 | 6 | Central | AD04
125525 | 2012-09-12 | Scheduled Outage | Preventive Maintenance | Setting a new pole | None | None | 9 | 24 | 4 | East | AC15
125526 | 2012-09-12 | Scheduled Outage | Construction | To build red and white risers on same pole | None | None | 1 | 134 | 2 | South | 606F2
125527 | 2012-09-12 | Scheduled Outage | Preventive Maintenance | Transformer Change | None | Unknown \ Other | 6 | 200 | 20 | East | UP05
125528 | 2012-09-12 | Scheduled Outage | Construction | Tranformer replacement | None | None | 10 | 105 | 18 | East | UP05
125531 | 2012-09-12 | Tree Contacts | Inadequate Trimming | To provide working clearance | O/H Conductor | Unknown \ Other | 18 | 65 | 20 | East | UZ12
125533 | 2012-09-12 | Scheduled Outage | Construction | ISOLATION OF X06006 FOR PLANT TRANFER | None | None | 1 | 100 | 2 | South | 606F2
125534 | 2012-09-12 | Scheduled Outage | Preventive Maintenance |  | None | O/H Conductor | 11 | 75 | 14 | Central | AD05
125535 | 2012-09-12 | Tree Contacts | Tree Limb Fallen | Limb Fell on neutral conductor | O/H Conductor | O/H Conductor | 10 | 163 | 27 | East | 7F2
125536 | 2012-09-13 | Scheduled Outage | Construction | Vault V796 at 71 Sweetland was isolated to allow crew to transfer riser to new pole. | None | None | 5 | 185 | 15 | Central | UN05
125537 | 2012-09-13 | Scheduled Outage | Preventive Maintenance | Vault V187 at 385 Besserrer was isolated to allow contractor to perform vault maintenance. | None | None | 42 | 234 | 164 | Central | UD02
125540 | 2012-09-13 | Tree Contacts | Tree Limb Fallen | 505-B phase section feeding X27487 was isolated to allow crew to remove tree from O/H and repair broken insulator. | O/H Conductor | O/H Conductor | 12 | 83 | 17 | Central | 505
125545 | 2012-09-13 | Scheduled Outage | Construction | ISOLATION OF X27537 FOR POLE CHANGE | None | Pole | 8 | 135 | 18 | East | UP07
125546 | 2012-09-13 | Scheduled Outage | Construction | ISOLATION OF X27526 FOR POLE CHANGE | None | Pole | 6 | 135 | 14 | East | UP07
125547 | 2012-09-13 | Scheduled Outage | Construction | Isolated transformer X26928 to ttransfer hydro plant to new pole | None | None | 5 | 300 | 25 | East | AJ03
125548 | 2012-09-13 | Scheduled Outage | Construction | Isolated transformer X40597 to replace pole and transfer hydro plant | None | None | 12 | 75 | 15 | East | UP07
125551 | 2012-09-13 | Scheduled Outage | Preventive Maintenance | VT226 at 222 somerset was shut down for contractor to perform vault maintenance and removal of asbestos, shut down was cancelled due to access issue | None | None | 2 | 57 | 2 | Central | TL5TS
125552 | 2012-09-14 | Foreign Interference | Vehicle | MVC struck TP7774 | U/G Transformer | Padmount (1ph) | 16 | 415 | 111 | West | ALEXF2
125552 | 2012-09-14 | Foreign Interference | Vehicle | MVC struck TP7774 | U/G Transformer | Padmount (1ph) | 197 | 25 | 82 | West | ALEXF2
125552 | 2012-09-14 | Foreign Interference | Vehicle | MVC struck TP7774 | U/G Transformer | Padmount (1ph) | 1185 | 92 | 1817 | West | ALEXF2
125553 | 2012-09-14 | Defective Equipment | Equipment Deterioration Due To Age | To allow for isolation on S18-1 & S18-2 white opphase cables. | U/G Cable | XLPE | 35 | 45 | 26 | West | 44F1
125555 | 2012-09-14 | Scheduled Outage | Construction | ISOLATION OF TX AT POLE X23785 FOR SERVICE UPGRADE | None | None | 20 | 98 | 33 | East | AP03
125557 | 2012-09-14 | Tree Contacts | Inadequate Trimming | tree trimming, insulator replacement | Customer Owned | Customer-Owned | 10 | 496 | 83 | South | 47F2
125558 | 2012-09-15 | Scheduled Outage | Preventive Maintenance | Customer vault maintenance VT115 | None | None | 1 | 516 | 9 | Central | 615
125559 | 2012-09-15 | Scheduled Outage | Preventive Maintenance | Vault maintenance in VT128 | None | None | 1 | 697 | 12 | Central | 402
125560 | 2012-09-15 | Defective Equipment | Equipment Failure - Cause Unknown | blown cutout | O/H Switchgear | Fused Cutout | 65 | 38 | 41 | East | SO05
125561 | 2012-09-15 | Scheduled Outage | Construction | Stations changing PCB Transformers, Customer owned contractor performing vault mtdce. | None | None | 1 | 516 | 9 | Central | UC10
125562 | 2012-09-15 | Scheduled Outage | Construction | to allow crews to re-arrange the overhead conductor, replace hardware and elbows in the padmount transformers | None | None | 1 | 84 | 1 | South | 130F3
125562 | 2012-09-15 | Scheduled Outage | Construction | to allow crews to re-arrange the overhead conductor, replace hardware and elbows in the padmount transformers | None | None | 2 | 224 | 7 | South | 130F3
125563 | 2012-09-15 | Scheduled Outage | Construction | Upgrading the existing transformer | None | None | 2 | 330 | 11 | East | 6F4
125564 | 2012-09-15 | Scheduled Outage | Preventive Maintenance | Planned outage to allow contractor to perform customer owned equipment maintenace. | None | None | 2 | 480 | 16 | West | 624F6
125565 | 2012-09-15 | Tree Contacts | Tree Limb Fallen | tree on wires | Secondary \ Service | O/H Service | 14 | 85 | 20 | South | 170F3
125566 | 2012-09-16 | Scheduled Outage | Construction | Planned outage for transformer and base upgrade. | None | None | 8 | 526 | 70 | East | 77M2
125567 | 2012-09-16 | Scheduled Outage | Preventive Maintenance | To allow contarctor to perform routine vault maintenance | None | None | 37 | 101 | 62 | Central | 604
125568 | 2012-09-16 | Scheduled Outage | Preventive Maintenance | Routine vault maintenance | None | None | 1 | 332 | 6 | Central | 606
125569 | 2012-09-17 | Scheduled Outage | Construction | planned outage for elbow and insert replacment | None | None | 80 | 265 | 353 | East | 77M2
125570 | 2012-09-17 | Scheduled Outage | Preventive Maintenance | to allow a contractor to trim trees on a customer owned line. | None | Customer-Owned | 166 | 342 | 946 | South | 200F2
125571 | 2012-09-17 | Scheduled Outage | Construction | To allow crews to cut in 3 new xfmrs | None | None | 16 | 246 | 66 | West | 29F1
125572 | 2012-09-17 | Scheduled Outage | Construction | ISOLATION OF TX ON POLE X27594 FOR PLANT TRANSFER | None | None | 16 | 150 | 40 | Central | UN05
125573 | 2012-09-17 | Scheduled Outage | Construction | ISOLATION OF TX ON POLE X23699 FOR CONTRACTOR TREE TRIMMING | None | None | 9 | 220 | 33 | East | UB07
125574 | 2012-09-17 | Scheduled Outage | Construction | ISOLATION OF TX ON POLE X25762 FOR PLANT TRANSFER | None | None | 15 | 170 | 42 | Central | SB13
125575 | 2012-09-17 | Scheduled Outage | Construction | ISOLATION OF TRANSFORMER AT X29130 TO REMOVE 3 CXS AND ADD TO TRANSFORMER AT X29131 | None | None | 8 | 120 | 16 | East | UP07
125576 | 2012-09-17 | Unknown/Other | No Apparent Cause | Fuse fell open at switch feeding transformer X40088 when Bell crew was stringing new wire on customer owned poles | Customer Owned | Customer-Owned | 1 | 142 | 2 | West | MWDF3
125577 | 2012-09-18 | Scheduled Outage | Preventive Maintenance | Vault VT218 at 350 Driveway was isolated to allow contractor to perform customer vault maintenance | None | None | 1 | 180 | 3 | Central | TR2FB
125578 | 2012-09-19 | Scheduled Outage | Construction | Transfer of plant | None | None | 104 | 180 | 312 | East | CYRF1
125579 | 2012-09-19 | Scheduled Outage | Construction | TB06 O/H circuit form S14923 to EOL was isolated to allow crew to complete pole work for ESA inspection | None | None | 10 | 25 | 4 | East | TB06
125579 | 2012-09-19 | Scheduled Outage | Construction | TB06 O/H circuit form S14923 to EOL was isolated to allow crew to complete pole work for ESA inspection | None | None | 26 | 115 | 50 | East | TB06
125579 | 2012-09-19 | Scheduled Outage | Construction | TB06 O/H circuit form S14923 to EOL was isolated to allow crew to complete pole work for ESA inspection | None | None | 104 | 140 | 243 | East | TB06
125580 | 2012-09-19 | Defective Equipment | Imminent Failure | The TR21 CB tripped under W phase fault due to defective cable on the 501 circuit causing outage to half of Carlelton University campus. Restoration time was delayed due to defective breaker TR10 R phase not closing . | U/G Cable | PILC | 1 | 196 | 3 | Central | 501
125581 | 2012-09-19 | Unknown/Other | No Apparent Cause | 7F1 circuit tripped under hold off. Limebank, River Rooad, Prince of Wales, Crestway | Unknown \ Other | Unknown \ Other | 4561 | 2 | 152 | East | 7F1
125583 | 2012-09-20 | Scheduled Outage | Construction | REPLACING A POLE AT X29819 | None | None | 5 | 110 | 9 | Central | TR09
125584 | 2012-09-20 | Scheduled Outage | Construction | PCB transformer replacement and customer vault maintenance. | None | None | 1 | 220 | 4 | Central | TR3UQ
125585 | 2012-09-20 | Defective Equipment | Imminent Failure | 24/7 FOUND BURNT CONNECTIONS, UPON REPAIR FOUND TX DEFECTIVE X10131, TRANSFORMER REPLACED | O/H Transformer | O/H Transformer (1ph) | 8 | 200 | 27 | West | JKGF5
125586 | 2012-09-20 | Scheduled Outage | Preventive Maintenance | TE3067 was replaced due to oil leak | None | None | 12 | 124 | 25 | East | 7F1
125587 | 2012-09-20 | Scheduled Outage | Construction | transformers TP6823, TP6820 and TP6819 were interrupted to allow crews to cut in a new transformer loop | None | None | 33 | 129 | 71 | East | LTM01
125588 | 2012-09-20 | Scheduled Outage | Construction | Elbows and Inserts replacement | None | None | 78 | 199 | 259 | East | 77M2
125592 | 2012-09-21 | Scheduled Outage | Repair | Transformer TE2913 was intrrupted to allow crews to refuse a phase at S22377 that blew for an unknown reason. | None | None | 1 | 12 | 0 | South | LGFF2
125595 | 2012-09-22 | Adverse Weather | Wind | SCADA indicates the 200F1 CB A/R under instanteanous R & B phase faulted. Switch S1351 was found blown during high winds. | O/H Conductor | Unknown \ Other | 1 | 241 | 4 | South | 200F1
125598 | 2012-09-22 | Adverse Weather | Wind | Switch S25743 was found blown. Fully patrolled, no cause found. Re-fused and closed. | O/H Conductor | Unknown \ Other | 9 | 127 | 19 | West | 624F6
125601 | 2012-09-22 | Scheduled Outage | Construction | TP7135 secondary was isolated to allow contractor to install micro-fit. | None | None | 1 | 85 | 1 | West | MWDF3
125602 | 2012-09-22 | Defective Equipment | Equipment Failure - Cause Unknown | Blown arrestor at X33253 caused fuse S13175 to open. | Pole Attachement | Arrester | 1 | 255 | 4 | West | 43F3
125603 | 2012-09-22 | Tree Contacts | Tree Fallen | A Tree fell on the O/H conductors in behind 706 Southmore bringing them down and causing switch S21912 to open. | O/H Conductor | O/H Conductor | 121 | 620 | 1250 | East | UZ05
125604 | 2012-09-22 | Scheduled Outage | Preventive Maintenance | Vault VT261 at 234 Sparks was isolated to allow contractor to perform vault maintenance. | None | None | 1 | 688 | 11 | Central | 5208
125605 | 2012-09-23 | Scheduled Outage | Preventive Maintenance | Vault VT653 at 11 Holland was isolated to allow crew to perform vault maintenance. | None | None | 37 | 300 | 185 | Central | TH1SH
125606 | 2012-09-23 | Scheduled Outage | Repair | Transformer X28110 isolated to allow crew to replace defective transformer. | None | O/H Transformer (1ph) | 31 | 110 | 57 | East | AF06
125608 | 2012-09-23 | Defective Equipment | Equipment Deterioration Due To Age | Transformer X35195 was isolated to allow crew to replace hot line clamps and transformer switch. | O/H Conductor | Hot-Line Clamp | 7 | 17 | 2 | Central | AH02
125609 | 2012-09-23 | Defective Equipment | Equipment Failure - Cause Unknown | RCMP reports the power went out and they are on back up generator at 12:39. Crew reports one phase blown at G732 due to a defective stir up and hot line clamp on the riser pole at G732. G732 RWB opened at 15:27 to replace stir up and hot line clamp. | O/H Switchgear | Fused Cutout | 1 | 43 | 1 | East | 77M5
125610 | 2012-09-23 | Scheduled Outage | Preventive Maintenance | Vault VT512 was isolated to allow contractor to perform vault maintenance. | None | None | 2 | 170 | 6 | Central | TK6TS
125612 | 2012-09-24 | Scheduled Outage | Construction | Transformer isolated to allow for new secondary service | None | None | 7 | 56 | 7 | Central | UL04
125613 | 2012-09-24 | Scheduled Outage | Construction | ISOLATION OF TX ON POLE X19214 TO RELOCATE TX TO NEW POLE | None | None | 4 | 135 | 9 | East | CYRF1
125614 | 2012-09-24 | Defective Equipment | Equipment Failure - Cause Unknown | TH02 CB tripped due to a cable fault between Hinchey TS, VT653 and VT45. Cable section isolated and load restore from alternate source. | U/G Cable | PILC | 37 | 70 | 43 | Central | TH1SH
125615 | 2012-09-24 | Scheduled Outage | Construction | Isolated transformer X19222 to replace pole and transfer hydro plant | None | None | 5 | 155 | 13 | East | CYRF1
125616 | 2012-09-24 | Scheduled Outage | Preventive Maintenance | vault maintenance | None | None | 1 | 103 | 2 | Central | 415
125617 | 2012-09-25 | Scheduled Outage | Repair | TP8255 to TP8250 FOR ELBOWS & INSERTS REPLACED | None | None | 71 | 189 | 224 | East | 77M2
125618 | 2012-09-25 | Scheduled Outage | Construction | TP3844 BEING REPLACED | None | Kiosk (1ph) | 37 | 219 | 135 | Central | SK12
125619 | 2012-09-25 | Scheduled Outage | Repair | Replacing a pole in the rear of 85 Granton and transfer conductor and transformer to new pole | None | Pole | 13 | 218 | 47 | South | EPWF1
125620 | 2012-09-26 | Scheduled Outage | Preventive Maintenance | TE1995 was isolated to allow crews to replace transformer and add secondary service. | None | None | 1 | 2933 | 49 | South | 200F6
125622 | 2012-09-26 | Scheduled Outage | Preventive Maintenance | Elbow and insert replacement | None | Padmount (1ph) | 200 | 217 | 723 | East | 77M2
125623 | 2012-09-26 | Scheduled Outage | Construction | K1129 REPLACED WITH TP8844 | None | Kiosk (1ph) | 6 | 203 | 20 | Central | UD05
125624 | 2012-09-26 | Scheduled Outage | Construction | To remove cables due to road construction | None | Padmount (1ph) | 20 | 219 | 73 | East | CYRF1
125625 | 2012-09-26 | Tree Contacts | Tree Limb Fallen | ISOLATION OF TX ON POLE X40548 TO REMOVE TREE LIMB | None | None | 13 | 225 | 49 | East | TB06
125626 | 2012-09-26 | Scheduled Outage | Construction | ISOLATION OF TX ON POLE X44286 FOR PLANT TRANSFER | None | None | 5 | 105 | 9 | East | AA03
125627 | 2012-09-26 | Unknown/Other | No Apparent Cause | LINE PATROLLED, NO ISSUE FOUND | O/H Switchgear | Inline Switch | 12 | 143 | 29 | West | 43F3
125628 | 2012-09-27 | Scheduled Outage | Construction | 10 blue phase tranasformer between S23774 and S12537 were isolated to allow crew to perform Elbow and insert replacement | None | None | 144 | 216 | 518 | East | 77M2
125629 | 2012-09-27 | Scheduled Outage | Construction | ISOLATION OF TX ON POLE X35360 FOR SERVICE UPGRADE | None | None | 11 | 55 | 10 | Central | AD05
125631 | 2012-09-27 | Scheduled Outage | Construction | ISOLATION OF CAN ON POLE X43884 FOR SERVICE UPGRADE | None | None | 19 | 77 | 24 | Central | TR3UY
125632 | 2012-09-27 | Scheduled Outage | Preventive Maintenance | Vault Maintenance | None | None | 1 | 540 | 9 | East | TA2QZ
125634 | 2012-09-28 | Scheduled Outage | Construction | Transformers TP8265, TP8264, TP8263, TP8262 were isolated to allow crew to perform elbow and insert replacment. | None | None | 11 | 119 | 22 | East | 77M2
125634 | 2012-09-28 | Scheduled Outage | Construction | Transformers TP8265, TP8264, TP8263, TP8262 were isolated to allow crew to perform elbow and insert replacment. | None | None | 44 | 310 | 227 | East | 77M2
125635 | 2012-09-28 | Scheduled Outage | Preventive Maintenance | S669 at 18 Eastgate was opened to allow contractor to perform tree trimming | None | None | 166 | 309 | 855 | South | 200F2
125636 | 2012-09-28 | Scheduled Outage | Preventive Maintenance | Transformer TE3315 (210F1) at 12 Letourneau was isolated to allow crew to replace leaking transformer | None | None | 25 | 58 | 24 | South | LGFF1
125636 | 2012-09-28 | Scheduled Outage | Preventive Maintenance | Transformer TE3315 (210F1) at 12 Letourneau was isolated to allow crew to replace leaking transformer | None | None | 122 | 4 | 8 | South | LGFF1
125638 | 2012-09-28 | Defective Equipment | Equipment Failure - Cause Unknown | burnt up lead at bottom side of switch S18870 | U/G Cable Attachement | Termination \ Stress Cone | 5 | 115 | 10 | West | BECKF2
125639 | 2012-09-29 | Scheduled Outage | Repair | transformer isolation to clean up oil leak | None | Padmount (3ph) | 1 | 805 | 13 | South | 87F3
125640 | 2012-09-29 | Scheduled Outage | Construction | planned outage for vault maintenance and PCB transformer replacement | None | None | 1 | 425 | 7 | Central | 4303
125641 | 2012-09-29 | Foreign Interference | Animal | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32503 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 4 | 71 | 5 | Central | TD01
125642 | 2012-09-28 | Scheduled Outage | Repair | Secondary switchboard replacement | None | None | 1 | 1350 | 22 | Central | TL4TS
125643 | 2012-09-30 | Scheduled Outage | Construction | Planned outage to allow contractor to remove asbestos and to core drill vault wall and scope the ducts | None | None | 1 | 320 | 5 | Central | TK5TSTK
125644 | 2012-09-30 | Scheduled Outage | Preventive Maintenance | Isolated 3 phase transformer X24187 for maintenance | None | None | 1 | 330 | 6 | East | 6F1
125645 | 2012-10-01 | Defective Equipment | Equipment Failure - Cause Unknown | Defective R phase cable caused S14401 R phase to blow. Cable isolated and TE1323 restored from alternate source. | U/G Cable | XLPE | 1 | 36 | 1 | East | 8F3
125646 | 2012-10-01 | Defective Equipment | Equipment Failure - Cause Unknown | Cable fault | U/G Cable | XLPE | 27 | 72 | 32 | East | AA04
125646 | 2012-10-01 | Defective Equipment | Equipment Failure - Cause Unknown | Cable fault | U/G Cable | XLPE | 78 | 89 | 116 | East | AA04
125648 | 2012-10-01 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30960 TO TRANSFER HYDRO PLANE | None | None | 9 | 180 | 27 | Central | UN10
125651 | 2012-10-01 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | G672B phase opened due to cable fault between transformer TE1606 and TE2842. While restoring the B phase loop, the SC2425 B phase flashed causing the 77M5 CB to A/R/A. SC2425 was isolated and down stream customer fed from SC2425 were picked up from alter | U/G Cable | XLPE | 200 | 117 | 390 | East | 77M5
125651 | 2012-10-01 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | G672B phase opened due to cable fault between transformer TE1606 and TE2842. While restoring the B phase loop, the SC2425 B phase flashed causing the 77M5 CB to A/R/A. SC2425 was isolated and down stream customer fed from SC2425 were picked up from alter | U/G Cable | XLPE | 854 | 4 | 57 | East | 77M5
125651 | 2012-10-01 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | G672B phase opened due to cable fault between transformer TE1606 and TE2842. While restoring the B phase loop, the SC2425 B phase flashed causing the 77M5 CB to A/R/A. SC2425 was isolated and down stream customer fed from SC2425 were picked up from alter | U/G Cable | XLPE | 1024 | 127 | 2167 | East | 77M5
125651 | 2012-10-01 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | G672B phase opened due to cable fault between transformer TE1606 and TE2842. While restoring the B phase loop, the SC2425 B phase flashed causing the 77M5 CB to A/R/A. SC2425 was isolated and down stream customer fed from SC2425 were picked up from alter | U/G Cable | XLPE | 1360 | 362 | 8205 | East | 77M5
125651 | 2012-10-02 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | G672B phase opened due to cable fault between transformer TE1606 and TE2842. While restoring the B phase loop, the SC2425 B phase flashed causing the 77M5 CB to A/R/A. SC2425 was isolated and down stream customer fed from SC2425 were picked up from alter | U/G Cable | XLPE | 1020 | 110 | 1870 | East | 77M5
125651 | 2012-10-02 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | G672B phase opened due to cable fault between transformer TE1606 and TE2842. While restoring the B phase loop, the SC2425 B phase flashed causing the 77M5 CB to A/R/A. SC2425 was isolated and down stream customer fed from SC2425 were picked up from alter | U/G Cable | XLPE | 1024 | 127 | 2167 | East | 77M5
125651 | 2012-10-02 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | G672B phase opened due to cable fault between transformer TE1606 and TE2842. While restoring the B phase loop, the SC2425 B phase flashed causing the 77M5 CB to A/R/A. SC2425 was isolated and down stream customer fed from SC2425 were picked up from alter | U/G Cable | XLPE | 1194 | 10 | 199 | East | 77M5
125651 | 2012-10-02 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | G672B phase opened due to cable fault between transformer TE1606 and TE2842. While restoring the B phase loop, the SC2425 B phase flashed causing the 77M5 CB to A/R/A. SC2425 was isolated and down stream customer fed from SC2425 were picked up from alter | U/G Cable | XLPE | 1360 | 2 | 45 | East | 77M5
125651 | 2012-10-02 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | G672B phase opened due to cable fault between transformer TE1606 and TE2842. While restoring the B phase loop, the SC2425 B phase flashed causing the 77M5 CB to A/R/A. SC2425 was isolated and down stream customer fed from SC2425 were picked up from alter | U/G Cable | XLPE | 1560 | 1 | 26 | East | 77M5
125652 | 2012-10-01 | Tree Contacts | Tree Limb Fallen | Tree limb on O/H caused the S19017 at 4050 Dwyer Hill to open | None | None | 2 | 254 | 8 | West | 43F3
125656 | 2012-10-02 | Scheduled Outage | Construction | ISOLATION OF CAN ON POLE X30018 FOR SEVRICE UPGRADE | None | None | 9 | 75 | 11 | Central | SB05
125658 | 2012-10-02 | Scheduled Outage | Construction | ISOLATION OF TX ON POLE X29131 FOR PLANT TRANSFER | None | None | 5 | 120 | 10 | East | UP03
125659 | 2012-10-02 | Scheduled Outage | Construction | ISOLATION OF TX ON POLE X27525 FOR PLANT TRANSFER | None | None | 5 | 120 | 10 | East | UP03
125660 | 2012-10-02 | Scheduled Outage | Preventive Maintenance | To allow contractor to remove trees near customer owned line. | None | Fused Cutout | 1 | 247 | 4 | West | BECKF2
125661 | 2012-10-02 | Foreign Interference | Vehicle | Hit and run to Hydro One shared pole, caused top to break off and crossarm on the V11F1 needs to be replaced. Hydro One required clearance from our line as well. | Pole | Pole | 302 | 229 | 1153 | East | V11F1
125662 | 2012-10-02 | Scheduled Outage | Preventive Maintenance | Transformer 1912 was issolated to allow crew to replace leaking transformer | U/G Transformer | Padmount (1ph) | 13 | 548 | 119 | West | BRDF2
125663 | 2012-10-02 | Scheduled Outage | Repair | Transformer X29202 isolated to allow for repairs to switch | O/H Switchgear | Fused Cutout | 25 | 14 | 6 | East | UT05
125664 | 2012-10-02 | Scheduled Outage | Construction | Transformer X30978 isolated to allow for transfer of secondary services to new pole | None | None | 9 | 180 | 27 | Central | UN10
125665 | 2012-10-02 | Scheduled Outage | Construction | Transformer X31542 isolated to allow for transfer of plant to new pole | None | None | 14 | 210 | 49 | Central | TH11-NIU
125669 | 2012-10-04 | Scheduled Outage | Repair | To replace cable section between TP9189 and TP6385 | None | Padmount (1ph) | 8 | 609 | 81 | South | 87F3
125670 | 2012-10-04 | Scheduled Outage | Preventive Maintenance | VT479 ISOLATED FOR MAINT, SCOTT MAGEE FROM CARLETON | None | Switch | 1 | 186 | 3 | Central | 2802
125672 | 2012-10-04 | Scheduled Outage | Preventive Maintenance | R phase Transformer elbow replacement and inserts | None | Unknown \ Other | 125 | 245 | 510 | East | 77M2
125673 | 2012-10-04 | Scheduled Outage | Construction | ISOLATION OF TX AT POLE X08952 FOR SERVICE UPGRADE | None | None | 1 | 75 | 1 | West | 43F3
125674 | 2012-10-04 | Scheduled Outage | Construction | replace cable and dip pole to K987 | None | Pole | 20 | 141 | 47 | Central | SB05
125675 | 2012-10-06 | Defective Equipment | Equipment Failure - Cause Unknown | Not yet known. | Pole Attachement | Arrester | 1 | 46 | 1 | Central | TH11-NIU
125675 | 2012-10-06 | Defective Equipment | Equipment Failure - Cause Unknown | Not yet known. | Pole Attachement | Arrester | 484 | 141 | 1137 | Central | TH11-NIU
125678 | 2012-10-06 | Defective Equipment | Equipment Failure - Cause Unknown | Defective switch on the Dip to V592 force and outage on vault V592 and transformer X29068 was opened for work clearance affecting a total of 10 customers. | O/H Switchgear | Simple Solid Blade Switch | 10 | 100 | 17 | East | AJ03
125679 | 2012-10-06 | Defective Equipment | Equipment Deterioration Due To Age | Pole fire at pole X39329 burnt through the pole at the neutral. TH11 was dumped to make it safe for crews to isolate the area. 12 customers remained without power while crews braced the pole. Hinchey TH11 ID# 125679 | Pole | Insulation Failure (Pole Fire) | 12 | 236 | 47 | Central | TH11-NIU
125679 | 2012-10-06 | Defective Equipment | Equipment Deterioration Due To Age | Pole fire at pole X39329 burnt through the pole at the neutral. TH11 was dumped to make it safe for crews to isolate the area. 12 customers remained without power while crews braced the pole. Hinchey TH11 ID# 125679 | Pole | Insulation Failure (Pole Fire) | 1822 | 34 | 1032 | Central | TH11-NIU
125680 | 2012-10-06 | Defective Equipment | Electrical Failure | G268RWB opened to allow crew to hipot cables. | U/G Cable | XLPE | 1 | 185 | 3 | East | 77M6
125681 | 2012-10-07 | Defective Equipment | Electrical Failure | Cable fault on the B phase cable between TP5409-H1b and TX 3556 caused the switch 302 B phase to blow | U/G Cable | XLPE | 10 | 40 | 7 | West | BRDF5
125681 | 2012-10-07 | Defective Equipment | Electrical Failure | Cable fault on the B phase cable between TP5409-H1b and TX 3556 caused the switch 302 B phase to blow | U/G Cable | XLPE | 26 | 34 | 15 | West | BRDF5
125681 | 2012-10-07 | Defective Equipment | Electrical Failure | Cable fault on the B phase cable between TP5409-H1b and TX 3556 caused the switch 302 B phase to blow | U/G Cable | XLPE | 42 | 176 | 123 | West | BRDF5
125683 | 2012-10-08 | Foreign Interference | Bird | Transformer X35278 refused due to bird contact - crow | None | None | 9 | 88 | 13 | West | ALEXF3
125684 | 2012-10-08 | Foreign Interference | Bird | Transformer X24194 refused - cause pigeon | None | None | 18 | 41 | 12 | East | 8F3
125687 | 2012-10-09 | Scheduled Outage | Construction | Pole Change | None | None | 12 | 125 | 25 | East | AC15
125689 | 2012-10-09 | Defective Equipment | Equipment Failure - Cause Unknown | TK4TS cable fault between VT155 and VT5. | U/G Cable | PILC | 1 | 3 | 0 | Central | TK4TS
125689 | 2012-10-09 | Defective Equipment | Equipment Failure - Cause Unknown | TK4TS cable fault between VT155 and VT5. | U/G Cable | PILC | 2 | 18 | 1 | Central | TK4TS
125689 | 2012-10-09 | Defective Equipment | Equipment Failure - Cause Unknown | TK4TS cable fault between VT155 and VT5. | U/G Cable | PILC | 17 | 23 | 7 | Central | TK4TS
125689 | 2012-10-09 | Defective Equipment | Equipment Failure - Cause Unknown | TK4TS cable fault between VT155 and VT5. | U/G Cable | PILC | 42 | 102 | 71 | Central | TK4TS
125690 | 2012-10-10 | Scheduled Outage | Construction | Connect new secondary service | None | None | 1 | 56 | 1 | East | LTM01
125691 | 2012-10-10 | Scheduled Outage | Preventive Maintenance | Secondary Maintenance | None | Padmount (3ph) | 1 | 29 | 0 | East | 5310
125692 | 2012-10-10 | Scheduled Outage | Repair | Transformer TP2224 at 569 Mazari was isolated to allow crew to raise and install transformer base/cllar extension and gasket. | None | None | 8 | 100 | 13 | West | ALEXF3
125693 | 2012-10-10 | Scheduled Outage | Construction | ISOLATION OF TRANS ON POLE X36395 FOR SERVICE UPGRADE | None | None | 5 | 30 | 2 | South | 170F4
125694 | 2012-10-10 | Scheduled Outage | Construction | ISOLATION OF TP2224. CREW INSTALLING CONCRETE COLLAR TO RAISE TRANS | None | None | 8 | 180 | 24 | West | ALEXF3
125695 | 2012-10-10 | Scheduled Outage | Construction | 29 transfomers between Temp36 and switch 568 in the Terry Fox Dr. Area were isolated to allow crew to complete cable connections and connect them to a new section of over head. | None | None | 198 | 65 | 214 | West | BRDF7
125696 | 2012-10-10 | Scheduled Outage | Repair | Transformer TP2999 at 518 Mazari was isolated to allow crew to install transformer base collar extension and gasket. | None | None | 10 | 80 | 13 | West | ALEXF3
125697 | 2012-10-10 | Scheduled Outage | Construction | To put up covers for tree removal | None | None | 13 | 55 | 12 | Central | TD07
125698 | 2012-10-10 | Defective Equipment | Imminent Failure | Cable fault | U/G Cable | XLPE | 95 | 107 | 169 | East | CYRF4
125700 | 2012-10-11 | Scheduled Outage | Construction | ISOLATION OF TRANS ON POLE X29598 FOR SERVICE UPGRADE | None | None | 9 | 60 | 9 | East | UG07
125701 | 2012-10-11 | Scheduled Outage | Construction | ISOLATION OF TRANS ON X22393 FOR TRANSFORMER REPLACEPENT | None | None | 16 | 210 | 56 | Central | SM16
125702 | 2012-10-11 | Foreign Interference | Dig-In | Forced outage for due to pole fire. TM1UC cable was dug into at Clyde sub by a contractor (Teraflex). The cable faulted up the pole which caused a pole fire. | Pole | Insulation Failure (Pole Fire) | 0 | 43200 | 0 | Central | SM09
125702 | 2012-10-11 | Foreign Interference | Dig-In | Forced outage for due to pole fire. TM1UC cable was dug into at Clyde sub by a contractor (Teraflex). The cable faulted up the pole which caused a pole fire. | Pole | Insulation Failure (Pole Fire) | 31 | 8 | 4 | Central | TM2UC
125702 | 2012-10-11 | Foreign Interference | Dig-In | Forced outage for due to pole fire. TM1UC cable was dug into at Clyde sub by a contractor (Teraflex). The cable faulted up the pole which caused a pole fire. | Pole | Insulation Failure (Pole Fire) | 1317 | 8 | 176 | Central | TM3UC
125703 | 2012-10-11 | Defective Equipment | Imminent Failure | Pole fire at 820 Vick Ave. | Pole | Insulation Failure (Pole Fire) | 14 | 365 | 85 | Central | TD12
125704 | 2012-10-12 | Scheduled Outage | Construction | Mircofit program | None | Customer-Owned | 1 | 71 | 1 | East | 77M1
125705 | 2012-10-12 | Scheduled Outage | Repair | Transformer #X25570 opened by crew to replace triplex service due to power problems | Secondary \ Service | O/H Service | 11 | 74 | 14 | Central | SM13
125706 | 2012-10-12 | Scheduled Outage | Construction | ISOLATION OF PAIL AT X32941 FOR SERVICE UPGRADE | None | None | 6 | 60 | 6 | Central | TD05
125707 | 2012-10-12 | Scheduled Outage | Repair | Pllanned vault shudown to allow Hydro crews to pull in new primary cables | None | None | 1 | 188 | 3 | Central | TK4TS
125709 | 2012-10-12 | Defective Equipment | Imminent Failure | Suspected cable fault between VT779 and VT307 caused TS44 to open. | U/G Cable | PILC | 1 | 23 | 0 | Central | 625
125709 | 2012-10-12 | Defective Equipment | Imminent Failure | Suspected cable fault between VT779 and VT307 caused TS44 to open. | U/G Cable | PILC | 3 | 46 | 2 | Central | 625
125710 | 2012-10-13 | Scheduled Outage | Preventive Maintenance | Customer maintenance | None | None | 1 | 554 | 9 | Central | TH2UL
125712 | 2012-10-13 | Scheduled Outage | Construction | TP2905 ISOLATED TO ALLOW CONTRACTOR TO INSTAL MICROFIT | None | Padmount (3ph) | 1 | 31 | 1 | East | 2203
125713 | 2012-10-14 | Scheduled Outage | Preventive Maintenance | Customer maintenance | None | None | 1 | 289 | 5 | Central | 626
125714 | 2012-10-14 | Defective Equipment | Equipment Deterioration Due To Age | Defective arrestor. | Pole Attachement | Arrester | 41 | 106 | 72 | East | TB06
125715 | 2012-10-14 | Scheduled Outage | Preventive Maintenance | To allow crew to disconnect cable to jack bus. | None | None | 1 | 31 | 1 | Central | SA19
125716 | 2012-10-14 | Scheduled Outage | Preventive Maintenance | Customer maintenance. | None | None | 1 | 320 | 5 | Central | 601
125718 | 2012-10-14 | Scheduled Outage | Preventive Maintenance | V161 ISOLATED FOR ASBESTOS REMOVAL, PCB TX REPLACEMENT & VAULT MAINT. | None | None | 1 | 1168 | 19 | Central | AB02
125719 | 2012-10-14 | Defective Equipment | Equipment Deterioration Due To Age | Defective transformer. | O/H Transformer | O/H Transformer (1ph) | 2 | 65 | 2 | Central | UJ03
125720 | 2012-10-15 | Defective Equipment | Imminent Failure | Transformer BRDT1 tripped under gas accumulation. | Station Equipment | Transformer | 2471 | 17 | 700 | West | BRDF3
125720 | 2012-10-15 | Defective Equipment | Imminent Failure | Transformer BRDT1 tripped under gas accumulation. | Station Equipment | Transformer | 3987 | 41 | 2724 | West | BRDF1
125722 | 2012-10-15 | Tree Contacts | Tree Fallen | TREE ON PRIMARY WAS THE CAUSE, PRIMARY WAS DOWN. THEY REPLACED THE TRANSFORMER AND PICKED THE PRIMARY BACK UP. | None | None | 2 | 327 | 11 | East | 249F2
125723 | 2012-10-15 | Scheduled Outage | Preventive Maintenance | Secondary Maintenance | None | None | 1 | 209 | 3 | East | CYRF1
125724 | 2012-10-16 | Scheduled Outage | Repair | Soil remediation | None | Padmount (1ph) | 27 | 431 | 194 | South | 190F6
125725 | 2012-10-16 | Scheduled Outage | Construction | INSERT AND ELBOW UPGRADES | None | None | 147 | 257 | 630 | East | 77M2
125727 | 2012-10-16 | Scheduled Outage | Construction | Transformer #X30537 opened by crew to transfer plant | None | None | 37 | 195 | 120 | Central | UN07
125728 | 2012-10-16 | Defective Equipment | Equipment Deterioration Due To Age | Transformer #X36234 opened by crew to change switch | O/H Switchgear | Fused Cutout | 6 | 5 | 0 | South | 190F2
125729 | 2012-10-16 | Scheduled Outage | Construction | Transformer #X32427 opened by crew for a transformer change | None | None | 7 | 35 | 4 | Central | TW22
125730 | 2012-10-16 | Scheduled Outage | Repair | planned outage to allow Hydro Ottawa crew to pull in new cables into vault. | None | None | 1 | 278 | 5 | Central | TK4TS
125732 | 2012-10-17 | Scheduled Outage | Repair | Soli remediation | None | Padmount (3ph) | 31 | 618 | 319 | Central | TR1UN
125733 | 2012-10-17 | Scheduled Outage | Construction | ISOLATION OF TE0152 FOR SERVICE UPGRADE | None | None | 10 | 46 | 8 | East | BCHF5
125734 | 2012-10-17 | Foreign Interference | Vehicle | Conductors found wrapped together near pole X23834. Construction in the area but no direct cause found. | O/H Conductor | O/H Conductor | 56 | 61 | 57 | East | AP02
125736 | 2012-10-17 | Scheduled Outage | Construction | Transformer #X23449 opened by crew for a pole replacement | None | None | 9 | 165 | 25 | East | AC15
125737 | 2012-10-17 | Scheduled Outage | Construction | Transformer #X23154 opened by crew for pole replacement | None | None | 24 | 165 | 66 | East | AC15
125738 | 2012-10-18 | Scheduled Outage | Preventive Maintenance | Tree removal. | None | None | 18 | 425 | 128 | East | UZ07
125739 | 2012-10-18 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer replacement and soil remediation. | U/G Transformer | Padmount (1ph) | 10 | 432 | 72 | South | 190F6
125740 | 2012-10-18 | Scheduled Outage | Preventive Maintenance | Tree removal. | None | None | 34 | 295 | 167 | East | TB06
125741 | 2012-10-18 | Scheduled Outage | Construction | 145F3 blue phase between Temp11 and Temp 12 was isolated to allow crew to re-arrange and re-string overhead section. | None | None | 15 | 269 | 67 | South | 145F3
125742 | 2012-10-18 | Human Element | Switching Errors | Human error while testing SC2175. | None | None | 159 | 14 | 37 | West | MWDF4
125744 | 2012-10-18 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | at 12:19 rx'd call for exposed wires on pole and building at 99 cartier was out. Crews found defective cable feeding v271 | Customer Owned | Customer-Owned | 61 | 946 | 962 | Central | UX02
125745 | 2012-10-19 | Scheduled Outage | Repair | Transformer TP2989 at 462 Landswood was isolated to allow crew to raise transformer base. | None | None | 11 | 47 | 9 | West | ALEXF3
125746 | 2012-10-19 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer X30666 isolated to allow repairs to customer owned disconnect switch | Customer Owned | Customer-Owned | 7 | 34 | 4 | Central | AM03
125747 | 2012-10-20 | Scheduled Outage | Preventive Maintenance | 13kV transformer bus at VT660 isolated to allow customer to replace 4kV switch gear. | None | None | 1 | 445 | 7 | East | 2207
125748 | 2012-10-20 | Scheduled Outage | Preventive Maintenance | planned outage to allow contractor to complete customer owned vault maintenace. | None | None | 1 | 397 | 7 | Central | 5203
125749 | 2012-10-20 | Scheduled Outage | Preventive Maintenance | Transformer Maintance by Contractor | None | Padmount (3ph) | 1 | 265 | 4 | West | 624F2
125751 | 2012-10-20 | Scheduled Outage | Construction | To cut in new 8kv transformer TP8559 at 460 West Hunt Club | None | None | 2 | 471 | 16 | South | 180F6
125756 | 2012-10-21 | Scheduled Outage | Preventive Maintenance | planned outage for customer vault maintenace | None | None | 1 | 179 | 3 | Central | 415
125757 | 2012-10-22 | Scheduled Outage | Repair | Not yet known. | None | Unknown \ Other | 1 | 155 | 3 | East | 1808
125758 | 2012-10-22 | Scheduled Outage | Construction | Transfer hydro plant | None | None | 10 | 135 | 22 | Central | SK11
125759 | 2012-10-24 | Scheduled Outage | Preventive Maintenance | S18306 was opened to allow crew to perform tree trimming on Marilyne St | None | None | 28 | 311 | 145 | East | UZ12
125760 | 2012-10-24 | Scheduled Outage | Repair | Transformer X28042-1671438 isolated to repairs connections | None | None | 8 | 51 | 7 | East | TA3AF
125761 | 2012-10-24 | Scheduled Outage | Construction | Transformer X40593 isolated to allow for transfer of plant | None | None | 11 | 220 | 40 | East | AJ06
125762 | 2012-10-24 | Scheduled Outage | Repair | repairs | None | None | 6 | 54 | 5 | East | 7F4
125763 | 2012-10-24 | Scheduled Outage | Repair | remove the sand from a transformer base | None | None | 7 | 155 | 18 | West | MWDF1
125765 | 2012-10-25 | Scheduled Outage | Construction | Transformer replacement, Former 2231W new TP9692. | None | Padmount (1ph) | 12 | 209 | 42 | West | BRDF4
125766 | 2012-10-25 | Scheduled Outage | Repair | Soil remediation | None | Padmount (1ph) | 6 | 429 | 43 | South | 130F4
125767 | 2012-10-25 | Scheduled Outage | Construction | replacing the transformer | None | None | 13 | 389 | 84 | East | BCHF8
125768 | 2012-10-25 | Scheduled Outage | Construction | TD05 O/H re-configuration | None | O/H Conductor | 13 | 71 | 15 | Central | TD05
125769 | 2012-10-25 | Scheduled Outage | Construction | ISOLATION OF CAN ON X35464 FOR INSTALLATION OF NEW SERVICE | None | None | 10 | 50 | 8 | Central | TD01
125771 | 2012-10-26 | Scheduled Outage | Construction | INSTALLATION OF NEW SERVICE | None | None | 9 | 331 | 50 | Central | SR09
125772 | 2012-10-26 | Scheduled Outage | Repair | TRANSFORMER X32204 ISOLATED TO ALLOW FOR TREE REMOVAL | None | None | 7 | 295 | 34 | Central | SM02
125774 | 2012-10-26 | Human Element | Switching Error | switching for isolation | None | None | 7 | 70 | 8 | South | EPWF5
125775 | 2012-10-26 | Scheduled Outage | Preventive Maintenance | TO allow crew to reconnect cables feeding V161 from the Jack bus in V151 | None | None | 1 | 42 | 1 | Central | SA19
125776 | 2012-10-27 | Scheduled Outage | Repair | SC19821 was isolated to allow crew to replace defective SF6 pressure guage on the SC19821 switch gear | None | None | 1 | 29 | 0 | East | 2211
125777 | 2012-10-27 | Scheduled Outage | Repair | VT77 at 440 Coventry was isolated to allow contractor to repace disconnect in vault VT77 | None | None | 1 | 864 | 14 | East | 1806
125778 | 2012-10-27 | Scheduled Outage | Repair | Transformer TE800 at 1580 Merivale was isolated to allow crew to rebuild riser and allow contractor to perform secondary work. | None | None | 5 | 138 | 12 | South | EPWF2
125779 | 2012-10-27 | Scheduled Outage | Construction | Micro fit. | None | None | 1 | 385 | 6 | East | TA1JP
125780 | 2012-10-27 | Scheduled Outage | Preventive Maintenance | VT543 transformer bus at 155 Queen was isolated to allow crew to replace transformers in vault | None | None | 1 | 435 | 7 | Central | 602
125781 | 2012-10-27 | Scheduled Outage | Construction | TP7288 at 635 Industrial was isolated to allow contractor to connect new 800A service | None | None | 2 | 150 | 5 | East | 1806
125782 | 2012-10-28 | Scheduled Outage | Preventive Maintenance | VT736 at 111 Albert was isolated to allow contractor to perform customer vault maintenance | None | None | 32 | 327 | 174 | Central | 614
125783 | 2012-10-28 | Scheduled Outage | Preventive Maintenance | VT159 at 60 Queen was isolated to allow contractor to perform customer vault maintenance | None | None | 1 | 421 | 7 | Central | 628
125784 | 2012-10-28 | Scheduled Outage | Preventive Maintenance | Customer maintenance. | None | None | 1 | 453 | 8 | Central | TR3UQ
125785 | 2012-10-28 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer X37080 was opened to allow crew to replace defective live line clamp | O/H Conductor | Hot-Line Clamp | 41 | 30 | 20 | South | 72F7
125786 | 2012-10-29 | Scheduled Outage | Preventive Maintenance | 72F4 white phase section from X36371 to EOL was isolated to allow contractor to remove tree from primary. | None | None | 8 | 172 | 23 | South | 72F4
125787 | 2012-10-29 | Scheduled Outage | Repair | Transformer TP8219B at 6423 Nathan was isolated to allow crew to replace leaking transformer. | None | None | 12 | 129 | 26 | East | 77M2
125788 | 2012-10-29 | Scheduled Outage | Construction | Transformer TP4279 at 470 Bronson to include S23148 was isolated to allow crew to transfer riser to new pole. | None | None | 1 | 195 | 3 | Central | UF07
125789 | 2012-10-29 | Scheduled Outage | Construction | Vault V857 at 511 Bronson including riser was isolated to allow crew to transfer riser switch. | None | None | 40 | 205 | 137 | Central | UF07
125790 | 2012-10-29 | Scheduled Outage | Construction | Transformr P275 at 506 Bronson to include riser was isolated to allow crew to transfer riser to new pole. | None | None | 30 | 165 | 82 | Central | UF07
125791 | 2012-10-30 | Adverse Weather | Wind | Heavy winds in area caused phases to slap together. | O/H Conductor | Unknown \ Other | 0 | 6 | 0 | South | 72F6
125791 | 2012-10-30 | Adverse Weather | Wind | Heavy winds in area caused phases to slap together. | O/H Conductor | Unknown \ Other | 0 | 66 | 0 | South | 72F7
125791 | 2012-10-30 | Adverse Weather | Wind | Heavy winds in area caused phases to slap together. | O/H Conductor | Unknown \ Other | 100 | 32 | 53 | South | 72F6
125791 | 2012-10-30 | Adverse Weather | Wind | Heavy winds in area caused phases to slap together. | O/H Conductor | Unknown \ Other | 100 | 192 | 320 | South | 72F6
125791 | 2012-10-30 | Adverse Weather | Wind | Heavy winds in area caused phases to slap together. | O/H Conductor | Unknown \ Other | 198 | 241 | 795 | South | 72F7
125792 | 2012-10-30 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H-1, high winds suspected. | None | None | 302 | 11 | 55 | East | V11F1
125792 | 2012-10-30 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H-1, high winds suspected. | None | None | 397 | 11 | 73 | East | V11F3
125792 | 2012-10-30 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H-1, high winds suspected. | None | None | 978 | 11 | 179 | East | V11F2
125796 | 2012-10-30 | Scheduled Outage | Forced Switching | Switching to restore load on 72F6 | None | None | 145 | 2 | 5 | South | 130F3
125797 | 2012-10-30 | Scheduled Outage | Repair | wind damage to primary | None | Unknown \ Other | 1 | 579 | 10 | South | 72F6
125798 | 2012-10-30 | Defective Equipment | Equipment Failure - Cause Unknown | S960 WHITE PHASE FUSE BLOWN, S961 FOUND DEFECTIVE & REPLACED | O/H Switchgear | Inline Switch | 85 | 110 | 156 | South | 49F6
125799 | 2012-10-30 | Tree Contacts | Tree Fallen | tree leaning on primary | O/H Conductor | Unknown \ Other | 380 | 32 | 203 | East | 4801F8
125799 | 2012-10-30 | Tree Contacts | Tree Fallen | tree leaning on primary | O/H Conductor | Unknown \ Other | 570 | 61 | 580 | East | 4801F8
125801 | 2012-11-01 | Scheduled Outage | Preventive Maintenance | 664 secondary at 2206 Halifax was isolated to allow contractor Enerton Electric to replace secondary main switch | None | None | 15 | 524 | 131 | East | AE05
125802 | 2012-11-01 | Scheduled Outage | Preventive Maintenance | VT620 at 35 Murray was isolated to allow crew to perform customer vault maintenance. | None | None | 81 | 305 | 412 | Central | 415
125803 | 2012-11-01 | Defective Equipment | Equipment Deterioration Due To Age | S12659 blue phase fuse blew due to a cable fault on cable between TP3882 & SE17. | U/G Cable | XLPE | 20 | 119 | 40 | East | 77M2
125804 | 2012-11-01 | Defective Equipment | Equipment Deterioration Due To Age | Defective equipment | O/H Transformer | O/H Transformer (1ph) | 8 | 78 | 10 | West | JKGF5
125804 | 2012-11-02 | Defective Equipment | Equipment Deterioration Due To Age | Defective equipment | O/H Transformer | O/H Transformer (1ph) | 66 | 63 | 69 | West | JKGF5
125805 | 2012-11-02 | Defective Equipment | Imminent Failure | The S12018 RWB opened due to POLE# X3551 top burnt off due to tracking | Pole | Insulation Failure (Pole Fire) | 53 | 114 | 101 | South | 606F2
125805 | 2012-11-02 | Defective Equipment | Imminent Failure | The S12018 RWB opened due to POLE# X3551 top burnt off due to tracking | Pole | Insulation Failure (Pole Fire) | 75 | 7 | 9 | South | 606F2
125805 | 2012-11-02 | Defective Equipment | Imminent Failure | The S12018 RWB opened due to POLE# X3551 top burnt off due to tracking | Pole | Insulation Failure (Pole Fire) | 115 | 6 | 12 | South | 606F2
125805 | 2012-11-02 | Defective Equipment | Imminent Failure | The S12018 RWB opened due to POLE# X3551 top burnt off due to tracking | Pole | Insulation Failure (Pole Fire) | 150 | 78 | 195 | South | 606F2
125807 | 2012-11-03 | Scheduled Outage | Preventive Maintenance | TVM2855 CHZ vault maintenance | None | None | 1 | 334 | 6 | Central | TL3SB
125808 | 2012-11-03 | Scheduled Outage | Construction | decommisioning VT660 energize new TN9209 | None | None | 1 | 362 | 6 | East | 4801F8
125809 | 2012-11-03 | Foreign Interference | Vehicle | MVA | Pole | Pole | 162 | 125 | 338 | East | 249F2
125810 | 2012-11-03 | Defective Equipment | Equipment Failure - Cause Unknown | S469 burnt lead | O/H Switchgear | Fused Cutout | 4 | 128 | 9 | South | 160F1
125811 | 2012-11-04 | Scheduled Outage | Preventive Maintenance | VT713 customer vault maintenance. | None | None | 1 | 381 | 6 | East | 2203
125813 | 2012-11-04 | Scheduled Outage | Repair | VT435 and VT435A were isolated to allow contractor to perform repairs on the vault CB1 and -L switch | None | Switch | 131 | 375 | 819 | Central | 2804
125814 | 2012-11-05 | Scheduled Outage | Construction | 29F1 from S15723 to EOL was isolated for clearnace to allow a contractor to excavate for a pole installation | None | None | 1 | 356 | 6 | West | 29F1
125815 | 2012-11-05 | Scheduled Outage | Construction | X27579 Isolated to transfer plant to pole | None | None | 2 | 110 | 4 | West | BRDF2
125816 | 2012-11-06 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | No cause found at this time. Line has been patrolled and crew did not find and defective cable section or evident dammaged O/H that would of caused the CB to trip Crew found Tracking and the door blown open at VT908 (Rogers Cable, 475 Richmond Rd). I | Customer Owned | Customer-Owned | 555 | 77 | 712 | Central | TM1AH
125817 | 2012-11-06 | Scheduled Outage | Maintenance | Planned interruption due to out of phase condition. Transformer isolation of TP9683. Customers interrupted twice due to out of phase condition. | None | Padmount (1ph) | 10 | 414 | 69 | East | 7F2
125817 | 2012-11-06 | Scheduled Outage | Maintenance | Planned interruption due to out of phase condition. Transformer isolation of TP9683. Customers interrupted twice due to out of phase condition. | None | Padmount (1ph) | 100 | 1 | 2 | East | 7F2
125818 | 2012-11-06 | Loss Of Supply | Third Party | Crew found the CB2 at VT16 tripped with a ground fault indicator flagged. We opened 2210-L1 and closed the TA16 breaker at Albion to energize everything up to the vault. | None | None | 1 | 51 | 1 | East | 2210
125820 | 2012-11-07 | Defective Equipment | Equipment Failure Due To Incorrect Maintenance | Not yet known. Crew found Tracking and the door blown open at VT908 (Rogers Cable, 475 Richmond Rd). It is a customer owned mini pad switchgear. The vault is normally fed from TM1AH circuit. TM1AH circuit was transferred to TM3UC supply. | Customer Owned | Customer-Owned | 371 | 15 | 93 | Central | TM3UC
125822 | 2012-11-08 | Defective Equipment | Imminent Failure | Not yet known. | Customer Owned | Customer-Owned | 554 | 9 | 83 | Central | TM1AH
125823 | 2012-11-08 | Scheduled Outage | Repair | UL03 blue phase O/H section behind 340 Island Park to EOL isolated under PC10A 4154 by Mike Maclellan to allow crew for tree trimming. | None | None | 13 | 230 | 50 | Central | UL03
125825 | 2012-11-08 | Scheduled Outage | Construction | To allow Sega Electric to perform secondary work in the secondary room. | None | None | 1 | 50 | 1 | East | AJ05
125827 | 2012-11-09 | Scheduled Outage | Preventive Maintenance | To allow Eaton Electric to install new bus duct. | None | None | 1 | 3666 | 61 | Central | 5208
125828 | 2012-11-11 | Scheduled Outage | Repair | To replace leaking transformer. | Vault Equipment | Transformer | 1 | 502 | 8 | South | 72F7
125829 | 2012-11-11 | Scheduled Outage | Preventive Maintenance | Scheduled outage | None | None | 1 | 359 | 6 | South | 22M28
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 0 | 16 | 0 | West | BRDF2
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 0 | 83 | 0 | West | BRDF2
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 130 | 16 | 35 | West | BRDF1
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 130 | 74 | 160 | West | BRDF1
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 130 | 124 | 269 | West | BRDF1
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 1498 | 1 | 25 | West | BRDF1
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 1498 | 2 | 50 | West | BRDF1
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 2576 | 9 | 386 | West | BRDF1
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 3944 | 22 | 1446 | West | BRDF1
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 5488 | 1 | 91 | West | BRDF2
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 5488 | 2 | 183 | West | BRDF2
125830 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Defective equipment S153 | U/G Switchgear | Live-Front | 5488 | 22 | 2012 | West | BRDF2
125831 | 2012-11-12 | Scheduled Outage | Construction | Transfer hydro plant to new pole | None | None | 6 | 190 | 19 | Central | SB05
125833 | 2012-11-12 | Defective Equipment | Imminent Failure | Lead from top of switch broken | O/H Switchgear | Fused Cutout | 6 | 119 | 12 | Central | SB02
125834 | 2012-11-12 | Adverse Weather | Wind | X27162 opened due to tree contact. | O/H Transformer | O/H Transformer (1ph) | 11 | 103 | 19 | East | TB15
125835 | 2012-11-12 | Adverse Weather | Wind | X27172 opened due to tree contact | O/H Transformer | O/H Transformer (1ph) | 8 | 74 | 10 | East | TB15
125838 | 2012-11-12 | Adverse Weather | Wind | Broken conductors on Cartier and Argyle | O/H Conductor | O/H Conductor | 26 | 158 | 68 | Central | UX05
125838 | 2012-11-12 | Adverse Weather | Wind | Broken conductors on Cartier and Argyle | O/H Conductor | O/H Conductor | 245 | 30 | 122 | Central | UX05
125838 | 2012-11-13 | Adverse Weather | Wind | Broken conductors on Cartier and Argyle | O/H Conductor | O/H Conductor | 26 | 135 | 58 | Central | UX05
125838 | 2012-11-13 | Adverse Weather | Wind | Broken conductors on Cartier and Argyle | O/H Conductor | O/H Conductor | 245 | 112 | 457 | Central | UX05
125839 | 2012-11-12 | Adverse Weather | Wind | Blown Fuse at Overhead Xfmr X31168 | None | None | 13 | 224 | 49 | Central | AB06
125839 | 2012-11-12 | Adverse Weather | Wind | Blown Fuse at Overhead Xfmr X31168 | None | None | 602 | 27 | 271 | Central | AB06
125840 | 2012-11-12 | Adverse Weather | Wind | Open Bus wire made phase to phase contact at 381 Montreal | None | None | 633 | 24 | 253 | East | AA03
125842 | 2012-11-12 | Tree Contacts | Tree Limb Fallen | Trees in the overhead at 938 Woodroffe caused S13369 R and W phases to open. | O/H Conductor | O/H Conductor | 172 | 191 | 548 | Central | TW22
125843 | 2012-11-12 | Defective Equipment | Equipment Failure - Cause Unknown | Lead on switch feeding KT609 burnt off. | O/H Switchgear | Fused Cutout | 8 | 295 | 39 | East | TB15
125844 | 2012-11-13 | Scheduled Outage | Preventive Maintenance | VT392 at 390 Montreal was isolated to allow contractor to perform customer vualt maintenance | None | None | 234 | 266 | 1037 | East | TO3UT
125845 | 2012-11-13 | Scheduled Outage | Repair | Transformer TE585 was isolated to allow crew to replace leaking transformer | None | None | 13 | 215 | 47 | East | 77M1
125846 | 2012-11-13 | Human Element | Incorrect Protection Settings | 4801F7 tripped while doing testing on the 4801F8 CB at Uplands substation. | Station Equipment | Relay | 48 | 9 | 7 | East | 4801F7
125848 | 2012-11-13 | Human Element | Incorrect Protection Settings | Bridlewood 605 S7M, BRDCST2, BRDT2Q and BRDCST1 breakers have tripped open. Station crew reports they tripped it, but no other explanation. | Station Equipment | Relay | 2244 | 10 | 374 | West | S7M (Bridlewood MTS - T1/T2)
125849 | 2012-11-13 | Scheduled Outage | Preventive Maintenance | Trasformer X30717 at 216 Russell Ave. isolated for service upgrade | None | None | 9 | 35 | 5 | Central | UN10
125851 | 2012-11-14 | Scheduled Outage | Preventive Maintenance | Customer maintenance | None | None | 1 | 293 | 5 | East | 6F10
125852 | 2012-11-14 | Scheduled Outage | Construction | TRANSFER HYDRO PLANT TO NEW POLE | None | None | 4 | 200 | 13 | East | UT05
125853 | 2012-11-14 | Scheduled Outage | Construction | 77M1 transformers between TP7186W & TE826 were isolated to allow crew to perform cable and insert replacement. | None | None | 45 | 387 | 290 | East | 77M1
125854 | 2012-11-14 | Defective Equipment | Imminent Failure | Defective transformer, replaced by on call crew, X29221 | O/H Transformer | O/H Transformer (1ph) | 6 | 375 | 38 | East | UG09
125855 | 2012-11-14 | Defective Equipment | Imminent Failure | X23865 opened by crew to change bolt in secondary bushing | O/H Transformer | O/H Transformer (1ph) | 15 | 25 | 6 | East | 77M1
125857 | 2012-11-15 | Scheduled Outage | Construction | S21072 was opened to allow crew to perform transformer upgrade | None | None | 2 | 208 | 7 | West | MWDF3
125858 | 2012-11-15 | Scheduled Outage | Preventive Maintenance | Elbow & Insert replacement and nomenclature changes | None | None | 53 | 395 | 349 | East | 77M1
125859 | 2012-11-15 | Scheduled Outage | Preventive Maintenance | Customer Vault Maintenance | None | None | 1 | 161 | 3 | South | 190F6
125860 | 2012-11-16 | Defective Equipment | Equipment Failure - Cause Unknown | Blown Lightning Arrestor | Pole Attachement | Arrester | 46 | 69 | 53 | East | LTM01
125860 | 2012-11-16 | Defective Equipment | Equipment Failure - Cause Unknown | Blown Lightning Arrestor | Pole Attachement | Arrester | 538 | 62 | 556 | East | LTM01
125861 | 2012-11-16 | Scheduled Outage | Construction | TRANSFORMER X25702 AT 260 LORETTA AVE. ISOLATED TO ALLOW FOR SERVICE UPGRADE | None | None | 5 | 71 | 6 | Central | SB07
125862 | 2012-11-16 | Scheduled Outage | Repair | TRANSFORMER X24675 AT TREMBLAY/AVENUE L ISOLATED TO ALLOW FOR REPAIRS TO NEUTRAL | None | None | 8 | 21 | 3 | East | SO10
125863 | 2012-11-16 | Scheduled Outage | Repair | TRANSFORMER X27527 AT 2010 WOODCREST RD ISOLATED TO ALLOW FOR RELOCATION OF SERVICE | None | None | 8 | 32 | 4 | East | AJ06
125865 | 2012-11-17 | Scheduled Outage | Preventive Maintenance | Customer maintenance. | None | None | 1 | 268 | 4 | East | 8F3
125866 | 2012-11-17 | Defective Equipment | Imminent Failure | TP3613 found to have a defective elbow & CABLE FAULT FROM TP3613 TP S16193 | U/G Cable | XLPE | 10 | 457 | 76 | East | BCHF8
125867 | 2012-11-17 | Defective Equipment | Imminent Failure | X32786 OPENED UP DUE TO BROKEN CUT OUT. REPLACED BY CREW AND POWER RESTORED. | O/H Switchgear | Fused Cutout | 9 | 290 | 44 | Central | UW03
125868 | 2012-11-17 | Scheduled Outage | Preventive Maintenance | Repair CB3 cable and troubleshoot protection issues | None | None | 1 | 554 | 9 | Central | 306
125869 | 2012-11-17 | Defective Equipment | Equipment Failure - Cause Unknown | AN06 CB opened due to a phase down at S22713. | O/H Conductor | O/H Conductor | 90 | 53 | 80 | East | AN06
125869 | 2012-11-17 | Defective Equipment | Equipment Failure - Cause Unknown | AN06 CB opened due to a phase down at S22713. | O/H Conductor | O/H Conductor | 265 | 5 | 22 | East | AN06
125869 | 2012-11-17 | Defective Equipment | Equipment Failure - Cause Unknown | AN06 CB opened due to a phase down at S22713. | O/H Conductor | O/H Conductor | 265 | 224 | 989 | East | AN06
125870 | 2012-11-17 | Scheduled Outage | Preventive Maintenance | clean vault, remove asbestos. | None | None | 1 | 496 | 8 | Central | TK6TS
125871 | 2012-11-18 | Scheduled Outage | Construction | restring & reframe 44MV O/H conductor | None | None | 2 | 600 | 20 | East | 48M4
125872 | 2012-11-18 | Scheduled Outage | Construction | restring & reframe 44MV O/H conductor | None | None | 4 | 585 | 39 | East | 6F1
125875 | 2012-11-18 | Scheduled Outage | Preventive Maintenance | Vault Maintenance. | None | None | 1 | 263 | 4 | Central | 415
125876 | 2012-11-19 | Scheduled Outage | Construction | cable megger and replacement | None | Padmount (1ph) | 50 | 383 | 319 | East | 77M1
125877 | 2012-11-19 | Scheduled Outage | Preventive Maintenance | Customer vault maintenance | None | None | 1 | 246 | 4 | Central | TL5TS
125878 | 2012-11-19 | Scheduled Outage | Construction | Transformer #X28177 opened by crew to transfer secondary to new pole | None | None | 14 | 160 | 37 | East | UP05
125881 | 2012-11-20 | Scheduled Outage | Preventive Maintenance | TP6026 isolated for soil remediation | None | Padmount (1ph) | 4 | 289 | 19 | South | 145F3
125882 | 2012-11-20 | Scheduled Outage | Preventive Maintenance | customer mantenance | None | None | 1 | 162 | 3 | Central | TR2TS
125884 | 2012-11-20 | Scheduled Outage | Construction | Transformer X3784 at 22 Steeple Hill Cres. isolated to allow crew to cut out temporary switch on primary | None | None | 1 | 53 | 1 | South | 145F3
125885 | 2012-11-20 | Scheduled Outage | Construction | Transformer X3783 at 16 Steeple Hill Cres. isolated to allow crew to cut out temporary switch on primary | None | None | 2 | 53 | 2 | South | 145F3
125886 | 2012-11-21 | Scheduled Outage | Construction | Transformer X30659 at 551 Gilmour isolated to allow for service upgrade | None | None | 9 | 43 | 6 | Central | UF05
125887 | 2012-11-21 | Scheduled Outage | Construction | Transformer X27745 isolated to allow for pole change | None | None | 7 | 155 | 18 | Central | SB05
125889 | 2012-11-21 | Foreign Interference | Bird | Bird contact at S7006 LB caused 7F1 and 210F2 to open. | O/H Switchgear | Load Break Gang | 609 | 45 | 457 | South | LGFF2
125889 | 2012-11-21 | Foreign Interference | Bird | Bird contact at S7006 LB caused 7F1 and 210F2 to open. | O/H Switchgear | Load Break Gang | 4930 | 32 | 2629 | East | 7F1
125891 | 2012-11-21 | Defective Equipment | Equipment Deterioration Due To Age | Customer equipment failure at VT908, 475 Richmond rd | Customer Owned | Customer-Owned | 1 | 221 | 4 | Central | TM1AH
125891 | 2012-11-21 | Defective Equipment | Equipment Deterioration Due To Age | Customer equipment failure at VT908, 475 Richmond rd | Customer Owned | Customer-Owned | 2 | 14 | 0 | Central | TM1AH
125891 | 2012-11-21 | Defective Equipment | Equipment Deterioration Due To Age | Customer equipment failure at VT908, 475 Richmond rd | Customer Owned | Customer-Owned | 555 | 38 | 352 | Central | TM1AH
125892 | 2012-11-22 | Scheduled Outage | Repair | at 05:12, PC10a #3629 established by Rob Longpre at S29296, isolating TP5581 for transformerer upgrade | None | None | 2 | 148 | 5 | West | 44F1
125893 | 2012-11-22 | Scheduled Outage | Preventive Maintenance | TP7310 on Bruin Lane was isolated to allow crew to change taps on padmounted transformer and reduce voltages. | None | Padmount (3ph) | 2 | 7 | 0 | South | 47F3
125894 | 2012-11-22 | Scheduled Outage | Repair | Transformer TP9229 at 102 Chesterton was isolated to allow crews to perform soil remediation. | None | None | 16 | 412 | 110 | South | 190F6
125895 | 2012-11-22 | Scheduled Outage | Construction | Transformer X31849 at 694 Melborne Ave. isolated to rearange plant and hook up new service. | None | None | 17 | 80 | 23 | Central | UL06
125896 | 2012-11-22 | Scheduled Outage | Repair | Transformer X23943 isolated to allow for emergency repairs - crew changed corroded connections on the transformer | None | None | 3 | 56 | 3 | East | 6F1
125897 | 2012-11-22 | Scheduled Outage | Construction | Transformer X26656-1667711 at 46 Clarey Ave. isolated for pole change. | None | None | 8 | 145 | 19 | Central | SB05
125898 | 2012-11-22 | Scheduled Outage | Preventive Maintenance | TRANSFORMER X17271 ISOLATED TO CHANGE INSULATORS ON POLE | None | None | 13 | 39 | 8 | East | 77M6
125899 | 2012-11-23 | Scheduled Outage | Repair | Transformer X26887 at 836 Quinlan Rd. isolated to replace hotline clamp | None | None | 13 | 15 | 3 | East | TB06
125902 | 2012-11-23 | Foreign Interference | Animal | Transformer #X24194 opened up due to squirrel contact | O/H Transformer | O/H Transformer (1ph) | 18 | 54 | 16 | East | 8F3
125903 | 2012-11-23 | Scheduled Outage | Construction | Transformer TP9240 at 340 Industrial was isolated to allow crew to remove temporary service and install permanent service. | None | None | 1 | 321 | 5 | East | 1802
125904 | 2012-11-23 | Loss Of Supply | Transmission Inadvertent | Loss of Hydro One Supply | None | None | 397 | 16 | 106 | West | BECKF2
125905 | 2012-11-23 | Loss Of Supply | Transmission Inadvertent | Loss of Hydro One supply due to a broken pole in the Merivale yard. | None | None | 24281 | 12 | 4856 | South | M32S (Nepean TS - T3/T4)
125906 | 2012-11-24 | Adverse Weather | Wind (Not Trees) | R & B phases slapped together due to a temporary in-line switch that was cut-in and had too much slack. Temporary inline switch is located at 48 Harlowe. | O/H Switchgear | Fused Cutout | 166 | 139 | 385 | South | 49F6
125908 | 2012-11-24 | Defective Equipment | Equipment Deterioration Due To Age | AT TRANSFORMER X32433 REPLACED DEFECTIVE LIVE LINE CLAMP | O/H Conductor | Hot-Line Clamp | 10 | 124 | 21 | Central | TW22
125909 | 2012-11-24 | Defective Equipment | Equipment Failure - Cause Unknown | suspected white phase cable fault at 6212 Jean De Arc, S11940 white phase is the device that operated | U/G Cable | XLPE | 59 | 91 | 89 | East | 77M1
125910 | 2012-11-24 | Scheduled Outage | Preventive Maintenance | Customer vault maintenance | None | None | 1 | 225 | 4 | Central | 415
125912 | 2012-11-25 | Foreign Interference | Animal | REPLACED BLOWN FUSE FEEDING TRANSFORMER X30295 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 7 | 38 | 4 | Central | TH11-NIU
125913 | 2012-11-25 | Defective Equipment | Equipment Failure - Cause Unknown | Cable fault on the R phase | U/G Cable | XLPE | 23 | 12 | 5 | West | 39F2
125913 | 2012-11-25 | Defective Equipment | Equipment Failure - Cause Unknown | Cable fault on the R phase | U/G Cable | XLPE | 24 | 16 | 6 | West | 39F2
125913 | 2012-11-25 | Defective Equipment | Equipment Failure - Cause Unknown | Cable fault on the R phase | U/G Cable | XLPE | 27 | 106 | 48 | West | 39F2
125913 | 2012-11-25 | Defective Equipment | Equipment Failure - Cause Unknown | Cable fault on the R phase | U/G Cable | XLPE | 637 | 8 | 85 | West | 39F2
125915 | 2012-11-26 | Scheduled Outage | Preventive Maintenance | Routine vault maintenance | None | None | 1 | 170 | 3 | East | TO3UB
125919 | 2012-11-26 | Scheduled Outage | Preventive Maintenance | Transformer X33920 isolated to remove squirrell nest from transformer | None | None | 4 | 14 | 1 | Central | UW02
125920 | 2012-11-27 | Scheduled Outage | Repair | Transformer TP6879 at 3777 Strandherd was isolated to allow crew to perform soil remediation. | None | Padmount (3ph) | 4 | 1145 | 76 | South | 606F1
125921 | 2012-11-27 | Scheduled Outage | Repair | VT274 secondary bus at 1771 St Laurent was isolated to allow crew to change taps on the 120/208 transfromer bank to increase volatges at 1759 St Laurent | None | None | 2 | 23 | 1 | East | 5303
125922 | 2012-11-27 | Scheduled Outage | Preventive Maintenance | V396 was isolated to allow crew to replacecable between S25077 and V396 | None | None | 3 | 448 | 22 | Central | UN05
125923 | 2012-11-27 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer #X29694 opened by crew to replace the fuse holder for streetlighting problem | Customer Owned | Customer-Owned | 10 | 15 | 2 | East | SO03
125924 | 2012-11-27 | Scheduled Outage | Construction | Transformer #X40659 located at 1518 Kilborn opened by crew to transfer secondary to new pole | None | None | 9 | 210 | 32 | East | AJ06
125925 | 2012-11-27 | Scheduled Outage | Preventive Maintenance | Replace transformer and reconfigure plant. | None | None | 1 | 283 | 5 | West | JKGF4
125926 | 2012-11-27 | Scheduled Outage | Construction | Transformer #X30983 at 52 Henderson and #X30840 at 58 Henderson opened by crew for a pole change | None | None | 18 | 270 | 81 | Central | UN05
125927 | 2012-11-27 | Scheduled Outage | Preventive Maintenance | Cable replacement | None | None | 38 | 357 | 226 | East | 77M1
125928 | 2012-11-27 | Scheduled Outage | Preventive Maintenance | V454 at 222 Laurier was isolated to allow crew to reaplce cables between S18630 and V454 | None | None | 4 | 218 | 15 | Central | UN05
125929 | 2012-11-27 | Scheduled Outage | Construction | Transformer X30844 isolated to allow for pole change | None | None | 20 | 169 | 56 | Central | UN05
125930 | 2012-11-28 | Scheduled Outage | Preventive Maintenance | To allow crew to remove mud from transformer base. | None | None | 8 | 163 | 22 | East | 77M1
125931 | 2012-11-28 | Scheduled Outage | Preventive Maintenance | Transformer X29631 at 199 Renouf was isolated to allow crew to replace transformer (6 customers affected). | None | None | 6 | 169 | 17 | East | SO06
125932 | 2012-11-28 | Scheduled Outage | Construction | Transformer #X29131 opened by crew to re-arrange plant to new poles | None | None | 5 | 185 | 15 | East | AJ06
125933 | 2012-11-28 | Scheduled Outage | Construction | Transformer #X30769 opened by crew to pull up triplex beside the drop | None | None | 11 | 40 | 7 | Central | AB03
125934 | 2012-11-28 | Scheduled Outage | Construction | Transformer #X33381 opened by crew to transfer plant to new pole | None | None | 10 | 135 | 22 | Central | TD05
125935 | 2012-11-28 | Scheduled Outage | Preventive Maintenance | Transformer P290 at 57 Henderson was isolated to allow crew to replace cable between P290 and SS26812 | None | None | 2 | 150 | 5 | Central | UN05
125936 | 2012-11-29 | Scheduled Outage | Construction | To re-arrange cables to supply the TE3315 from SC6396 | None | None | 8 | 166 | 22 | South | 87F6
125936 | 2012-11-29 | Scheduled Outage | Construction | To re-arrange cables to supply the TE3315 from SC6396 | None | None | 8 | 234 | 31 | South | 87F6
125936 | 2012-11-29 | Scheduled Outage | Construction | To re-arrange cables to supply the TE3315 from SC6396 | None | None | 212 | 2 | 7 | South | 87F6
125937 | 2012-11-29 | Defective Equipment | Equipment Deterioration Due To Age | A defective line clamp caused a conductor to break on Nepean St. At Metcalfe. SA22 circuit opened by system due to live wires on the ground. | O/H Conductor | Hot-Line Clamp | 303 | 19 | 96 | Central | SA22
125938 | 2012-11-29 | Scheduled Outage | Construction | TP9394 isolated for transformer upgrade and cable replacement. | None | None | 10 | 488 | 81 | East | BCHF3
125939 | 2012-11-30 | Defective Equipment | Equipment Deterioration Due To Age | Cable fault between TP6154 and 2543B caused 39F2 to open. | U/G Cable | XLPE | 1 | 18 | 0 | West | 39F2
125939 | 2012-11-30 | Defective Equipment | Equipment Deterioration Due To Age | Cable fault between TP6154 and 2543B caused 39F2 to open. | U/G Cable | XLPE | 3 | 170 | 8 | West | 39F2
125939 | 2012-11-30 | Defective Equipment | Equipment Deterioration Due To Age | Cable fault between TP6154 and 2543B caused 39F2 to open. | U/G Cable | XLPE | 614 | 11 | 113 | West | 39F2
125940 | 2012-11-30 | Defective Equipment | Imminent Failure | TR23 CB tripped opened due to defective equppment at VT898 | Customer Owned | Customer-Owned | 1 | 313 | 5 | Central | 503
125940 | 2012-11-30 | Defective Equipment | Imminent Failure | TR23 CB tripped opened due to defective equppment at VT898 | Customer Owned | Customer-Owned | 333 | 37 | 205 | Central | 503
125940 | 2012-11-30 | Defective Equipment | Imminent Failure | TR23 CB tripped opened due to defective equppment at VT898 | Customer Owned | Customer-Owned | 337 | 60 | 337 | Central | 503
125941 | 2012-11-30 | Scheduled Outage | Repair | Transformer X25509 at 416 Bronson was isolated to allow crew to replace decfective secondary triplex. | None | O/H Service | 13 | 38 | 8 | Central | AM03
125942 | 2012-12-01 | Scheduled Outage | Preventive Maintenance | VT96 at 171 Slater was isolated to allow contractor to perform customer vault maintenance | None | None | 1 | 258 | 4 | Central | 602
125944 | 2012-12-01 | Scheduled Outage | Preventive Maintenance | Customer maintenance | None | None | 1 | 355 | 6 | South | 22M24
125945 | 2012-12-02 | Scheduled Outage | Preventive Maintenance | Vault VT807 transformer bus at 50 Beechwood was isolated to allow crew to replace vault transformers | None | None | 1 | 208 | 3 | Central | TK2AC
125946 | 2012-12-02 | Defective Equipment | Equipment Failure - Cause Unknown | At 15:09, SCADA indicates TK24 CB opened. TK5TS is abnormal due to vault partial isolation. 403 customers affected. Cable fault between VT566 and VT833. | U/G Cable | PILC | 7 | 13 | 2 | Central | 416
125946 | 2012-12-02 | Defective Equipment | Equipment Failure - Cause Unknown | At 15:09, SCADA indicates TK24 CB opened. TK5TS is abnormal due to vault partial isolation. 403 customers affected. Cable fault between VT566 and VT833. | U/G Cable | PILC | 403 | 64 | 430 | Central | 416
125948 | 2012-12-02 | Defective Equipment | Imminent Failure | faulty switch at K71 | U/G Transformer | Kiosk (1ph) | 18 | 320 | 96 | East | AQ03
125949 | 2012-12-02 | Scheduled Outage | Preventive Maintenance | Transfer customers fed from Hydro One Manotick DS were interrupted due to planned Hydro One work. | None | None | 2 | 180 | 6 | South | 81F2
125949 | 2012-12-02 | Scheduled Outage | Preventive Maintenance | Transfer customers fed from Hydro One Manotick DS were interrupted due to planned Hydro One work. | None | None | 5 | 180 | 15 | South | 81F5
125950 | 2012-12-03 | Tree Contacts | Tree Limb Fallen | S190 at 43 Pineglen opened due downed primary conductor. | O/H Conductor | O/H Conductor | 54 | 44 | 40 | South | 180F4
125951 | 2012-12-03 | Scheduled Outage | Preventive Maintenance | Cable, elbow and insert replacement. | None | None | 42 | 345 | 242 | East | 77M1
125953 | 2012-12-03 | Scheduled Outage | Construction | Transformer #X29131 opened by crew to transfer secondary to new pole | None | None | 5 | 165 | 14 | East | AJ06
125954 | 2012-12-04 | Scheduled Outage | Construction | energizing new cable to feed TE3515 | None | None | 1 | 62 | 1 | South | 87F6
125955 | 2012-12-04 | Scheduled Outage | Construction | 4 transformers in the Grey Nuns area were isolated for cable and elbow replacement. | None | None | 38 | 337 | 213 | East | 77M1
125957 | 2012-12-04 | Scheduled Outage | Preventive Maintenance | Clean Vault, torque connections, service breaker and upgrade metering | None | None | 1 | 304 | 5 | Central | 5404
125958 | 2012-12-04 | Scheduled Outage | Preventive Maintenance | S584 at 349 Terry Fox was isolated to allow HOL crews to clean the switchgear. | None | None | 1 | 130 | 2 | West | 624F5
125959 | 2012-12-04 | Scheduled Outage | Repair | To complete primary cable repairs in VT890 | None | None | 1 | 120 | 2 | Central | 503
125960 | 2012-12-05 | Scheduled Outage | Construction | TE3519 was isolated to allow crews to re-configure U/G circuit and energize a new transformer | None | None | 12 | 218 | 44 | South | 87F6
125961 | 2012-12-05 | Scheduled Outage | Preventive Maintenance | Vault maintenance | None | None | 1 | 112 | 2 | East | 1809
125962 | 2012-12-06 | Scheduled Outage | Repair | Transformer X31577 @ 1277 Highgate was isolated to allow crew to perform secondary work. | None | None | 12 | 61 | 12 | Central | UW13
125963 | 2012-12-06 | Scheduled Outage | Preventive Maintenance | Red phase transformers TP9415, 9416, 9417, 7016 on Grey Nuns were isolated to allow crew to replace elbows and inserts. | None | None | 38 | 295 | 187 | East | 77M1
125964 | 2012-12-06 | Scheduled Outage | Construction | Transformer X27687 isolated to allow for transfer of plant. | None | None | 5 | 444 | 37 | East | TA3AF
125965 | 2012-12-06 | Scheduled Outage | Construction | Transformer X29812-1665790 isolated to allow for pole replacement. | None | None | 12 | 293 | 59 | Central | SB05
125966 | 2012-12-06 | Scheduled Outage | Preventive Maintenance | ISOLATED TRANSFORMER X34922 FOR TREE REMOVAL | None | None | 17 | 390 | 110 | Central | UL04
125968 | 2012-12-07 | Scheduled Outage | Construction | Transformer X36540 at 7 Ashwood was isolated from switch S34 to allow crew rearrange secondary. | None | None | 6 | 189 | 19 | South | EPWF3
125969 | 2012-12-07 | Unknown/Other | No Apparent Cause | The 249F1 tripped open under fault, crew found FCI 2214 flagged and patrolled circuit down stream and found no evident cause for outage. Cause remains under investiagtion | None | None | 3592 | 7 | 419 | East | LTM01
125970 | 2012-12-08 | Scheduled Outage | Repair | to re-repair VT908 S-113 | None | None | 1 | 209 | 3 | Central | TM1AH
125971 | 2012-12-08 | Scheduled Outage | Construction | QT112 was isolated to allow HOL crews to install customer owned 44kV air break switch. | None | None | 1 | 415 | 7 | South | 22M26
125972 | 2012-12-09 | Scheduled Outage | Repair | replacing leaking transformer | U/G Transformer | Padmount (1ph) | 38 | 493 | 312 | East | TA3AE
125973 | 2012-12-09 | Scheduled Outage | Construction | replacing rpimary acbles and dip pole | None | None | 6 | 292 | 29 | Central | TD12
125974 | 2012-12-09 | Scheduled Outage | Preventive Maintenance | Transfer Secondary Services | None | None | 10 | 204 | 34 | Central | UL03
125975 | 2012-12-09 | Defective Equipment | Equipment Failure - Cause Unknown | Not yet known. | O/H Transformer | O/H Transformer (1ph) | 11 | 124 | 23 | East | V11F2
125976 | 2012-12-11 | Scheduled Outage | Construction | Vault VT888 at Robert A Bondar was isolated to allow contractor to install Micro-Fit. | None | None | 1 | 179 | 3 | East | 2204
125977 | 2012-12-11 | Scheduled Outage | Preventive Maintenance | Vault VT130 transformer bus was isolated to allow contractor to disconnect customer secondary cables. | None | None | 1 | 123 | 2 | East | TO3UT
125978 | 2012-12-11 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X29878 TO REPLACE POLE | None | None | 16 | 170 | 45 | Central | SB05
125979 | 2012-12-11 | Scheduled Outage | Construction | TRANSFORMER X25507 ISOLATED FOR POLE CHANGE | None | None | 11 | 217 | 40 | Central | AM03
125980 | 2012-12-11 | Scheduled Outage | Construction | TRANSFORMER X25506 ISOLATED FOR POLE CHANGE | None | None | 2 | 217 | 7 | Central | AM03
125982 | 2012-12-11 | Scheduled Outage | Construction | Vault VT130 transformer bus only was isolated to allow contractor to connect new 600V secondary. | None | None | 1 | 19 | 0 | East | TO3UT
125983 | 2012-12-11 | Scheduled Outage | Construction | Transformer #X25508, X25509 and X25510 located at 420, 416 and 390 Bronson Ave opened by crew for a pole change. | None | None | 36 | 270 | 162 | Central | AM03
125984 | 2012-12-12 | Scheduled Outage | Construction | Transformer TP5633 secondary bus was isolated to allow contractor to install microfit | None | None | 1 | 218 | 4 | South | 145F1
125985 | 2012-12-12 | Scheduled Outage | Repair | soil remediation and transformer base upgrade | None | None | 9 | 389 | 58 | West | ALEXF3
125986 | 2012-12-12 | Scheduled Outage | Repair | transformer replacment | None | None | 20 | 114 | 38 | South | 49F2
125987 | 2012-12-12 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31006 AND X31003 FOR POLE CHANGE | None | None | 22 | 270 | 99 | Central | AB03
125988 | 2012-12-12 | Scheduled Outage | Preventive Maintenance | tree trimming | None | None | 22 | 340 | 125 | Central | SM06
125989 | 2012-12-12 | Scheduled Outage | Construction | TRANSFORMER X25512 ISOLATED FOR POLE CHANGE | None | None | 27 | 370 | 166 | Central | AM03
125990 | 2012-12-12 | Scheduled Outage | Construction | TRANSFORMER X25513 ISOLATED FOR POLE CHANGE | None | None | 13 | 370 | 80 | Central | AM03
125991 | 2012-12-12 | Scheduled Outage | Preventive Maintenance | transformer upgrade | None | None | 10 | 408 | 68 | East | BCHF3
125992 | 2012-12-12 | Scheduled Outage | Construction | TRANSFORMER X29878 ISOLATED FOR POLE REPLACEMENT | None | None | 16 | 80 | 21 | Central | SB05
125993 | 2012-12-12 | Human Element | Improper Construction/installation | Out of phase condition | U/G Cable Attachement | Termination \ Stress Cone | 5178 | 13 | 1122 | West | BRDF2
125994 | 2012-12-12 | Scheduled Outage | Construction | Transformer #X31420 opened by crew for a pole change | None | None | 21 | 180 | 63 | Central | AM03
125995 | 2012-12-12 | Scheduled Outage | Preventive Maintenance | VT226 at 222 Somerset was isolated to allow contractor to perform customer vault maintenance | None | None | 126 | 287 | 603 | Central | TL5TS
125996 | 2012-12-13 | Scheduled Outage | Construction | P443 at 345 Ravenhill was isolated to allow contractor to install microfit | None | None | 1 | 135 | 2 | Central | UC02
125997 | 2012-12-12 | Scheduled Outage | Construction | cable reconfiguration | None | None | 24 | 157 | 63 | South | 87F6
125998 | 2012-12-13 | Scheduled Outage | Construction | TP9396W was isolated for cable and transformer replacement | None | None | 14 | 454 | 106 | East | BCHF3
125999 | 2012-12-13 | Foreign Interference | Vehicle | Car hit guy wire causing it to break and wrap into the overhead conductors. Pole also damaged. 7F4 CB auto reclosed and locked out. | Pole Attachement | Unknown \ Other | 1205 | 55 | 1105 | East | 7F4
126000 | 2012-12-13 | Defective Equipment | Equipment Failure - Cause Unknown | Blown lightning arrestor cause S546 R phase to open. | Pole Attachement | Arrester | 213 | 65 | 231 | South | 190F5
126003 | 2012-12-13 | Defective Equipment | Imminent Failure | Flash at S153 caused BRDF1 to auto reclose and BRDF2 to open and lock out under hold off. | U/G Switchgear | Live-Front | 110 | 61 | 112 | West | BRDF2
126003 | 2012-12-13 | Defective Equipment | Imminent Failure | Flash at S153 caused BRDF1 to auto reclose and BRDF2 to open and lock out under hold off. | U/G Switchgear | Live-Front | 3788 | 1 | 63 | West | BRDF1
126003 | 2012-12-13 | Defective Equipment | Imminent Failure | Flash at S153 caused BRDF1 to auto reclose and BRDF2 to open and lock out under hold off. | U/G Switchgear | Live-Front | 5311 | 24 | 2124 | West | BRDF2
126004 | 2012-12-13 | Scheduled Outage | Construction | Voltage conversion from 4kv to 13kv. | None | None | 111 | 221 | 409 | East | AJ06
126005 | 2012-12-13 | Scheduled Outage | Repair | TRANSFORMER X30303 ISOLATED TO REPAIR SECONDARY CONNECTIONS AT THE TRANSFORMER | None | None | 18 | 32 | 10 | Central | UF07
126006 | 2012-12-14 | Scheduled Outage | Construction | Vault VT745 was isolated to allow contractor to install a micro-fit system. | None | None | 1 | 170 | 3 | East | 2206
126007 | 2012-12-14 | Scheduled Outage | Construction | Secondary at TP5294 disconnected to allow contractor to perform microfit installation on customer secondary. | None | None | 61 | 73 | 74 | South | 47F6
126008 | 2012-12-15 | Scheduled Outage | Preventive Maintenance | To allow Schneider Electric to perform routine vault maintenance | None | None | 7 | 539 | 63 | Central | TK5TS
126009 | 2012-12-15 | Scheduled Outage | Preventive Maintenance | To allow Siemens-Westinghouse to perform routine vault maintenance | None | None | 1 | 110 | 2 | East | AJ07
126010 | 2012-12-16 | Scheduled Outage | Construction | Transformer TP6376 was isolated to allow crew to to convert the supply from the 145F4 to the FAL03 | None | None | 1 | 195 | 3 | South | 145F4
126011 | 2012-12-16 | Scheduled Outage | Repair | QT127 and QT125 were isolated to allow crew to make repairs to switch S23590 and arrestors at 127-L | None | None | 2 | 196 | 7 | South | 22M24
126012 | 2012-12-16 | Foreign Interference | Vehicle | W phase radial line section was forced out form S23681 to EOL to allow crew to make repairs to downed condutcor at 1601 Eagleson. Pole # X08860 | O/H Conductor | O/H Conductor | 5 | 46 | 4 | South | 145F3
126013 | 2012-12-17 | Foreign Interference | Vehicle | REPLACE DEFECTIVE TRANSFORMER TP5332, DUE TO HIT AND RUN. | U/G Transformer | Padmount (1ph) | 13 | 238 | 52 | South | 606F2
126014 | 2012-12-17 | Scheduled Outage | Preventive Maintenance | VT507 at 77 Clarence was isolated to allow contractor to perform customer vault maiontenance | None | None | 1 | 124 | 2 | Central | TK5TS
126015 | 2012-12-17 | Scheduled Outage | Construction | To allow crew to transfer plant to new pole. | None | None | 40 | 250 | 167 | Central | AM04
126016 | 2012-12-17 | Human Element | Incorrect Construction | Contractor drilled into primary conductor. | U/G Cable | PILC | 1 | 212 | 4 | East | TB1AL
126016 | 2012-12-17 | Human Element | Incorrect Construction | Contractor drilled into primary conductor. | U/G Cable | PILC | 2 | 8 | 0 | East | TB1AL
126016 | 2012-12-17 | Human Element | Incorrect Construction | Contractor drilled into primary conductor. | U/G Cable | PILC | 3 | 14 | 1 | East | TB1AL
126016 | 2012-12-17 | Human Element | Incorrect Construction | Contractor drilled into primary conductor. | U/G Cable | PILC | 341 | 25 | 142 | East | TB1AL
126018 | 2012-12-18 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer X28213 at 2132 Blossom opened due to a pole fire. | Pole | Insulation Failure (Pole Fire) | 10 | 1 | 0 | Central | 505
126018 | 2012-12-18 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer X28213 at 2132 Blossom opened due to a pole fire. | Pole | Insulation Failure (Pole Fire) | 10 | 256 | 43 | Central | 505
126018 | 2012-12-18 | Defective Equipment | Equipment Failure - Cause Unknown | Transformer X28213 at 2132 Blossom opened due to a pole fire. | Pole | Insulation Failure (Pole Fire) | 147 | 283 | 693 | Central | 505
126020 | 2012-12-18 | Scheduled Outage | Construction | To allow crew to re-configure plant. | None | None | 21 | 180 | 63 | Central | AM03
126021 | 2012-12-18 | Foreign Interference | Vehicle | Car hit pole. | Pole | Pole | 4 | 104 | 7 | East | 4801F7
126022 | 2012-12-19 | Scheduled Outage | Construction | Transformer X40589 at 2245 Webster was isolated to allow crew to re-arrange plant. | None | None | 12 | 82 | 16 | East | TA3AF
126023 | 2012-12-19 | Scheduled Outage | Construction | To allow contractor to install micro fit. | None | None | 75 | 84 | 105 | South | 130F4
126024 | 2012-12-19 | Scheduled Outage | Repair | VT221 was isolated to allow contractor to repair broken arc chutes | None | None | 11 | 60 | 11 | East | TB2AL
126025 | 2012-12-20 | Scheduled Outage | Construction | To install new primary cable and energize three new transformers | None | None | 50 | 332 | 277 | East | CYRF1
126027 | 2012-12-20 | Scheduled Outage | Construction | Transformer #X30426 opened by crew for an upgrade | None | None | 13 | 140 | 30 | Central | SB02
126028 | 2012-12-20 | Scheduled Outage | Construction | Transformer #X39484 opened by crew for an electrician for a meter change | None | None | 1 | 140 | 2 | East | 7F4
126029 | 2012-12-20 | Scheduled Outage | Construction | VT78 transformer bus at 158 McArthur was isolated to allow contractor to secondary work | None | None | 1 | 157 | 3 | East | TO3UT
126030 | 2012-12-20 | Scheduled Outage | Construction | VT78 13KV transformer bus at 158 McArthur was isolated to allow contractor to perform secondary work. | None | None | 1 | 21 | 0 | East | TO3UT
126032 | 2012-12-21 | Foreign Interference | Vehicle | snow plow hit pole and shook the lines | None | None | 16 | 118 | 31 | East | AN06
126034 | 2012-12-21 | Defective Equipment | Equipment Failure - Cause Unknown | Blown transformer fuse | O/H Switchgear | Fused Cutout | 5 | 34 | 3 | East | AN06
126035 | 2012-12-21 | Adverse Weather | Snow | Winter storm | None | None | 217 | 8 | 29 | West | 24F5
126036 | 2012-12-21 | Tree Contacts | Tree Limb Fallen | Tree on line | None | None | 19 | 10 | 3 | West | 624F6
126037 | 2012-12-21 | Adverse Weather | Snow | Conductor down | O/H Conductor | O/H Conductor | 149 | 186 | 462 | East | UB02
126038 | 2012-12-21 | Tree Contacts | Tree Limb Fallen | tree fell on overhead and pulled down a phase. | O/H Conductor | O/H Conductor | 18 | 22 | 7 | West | BECKF2
126038 | 2012-12-21 | Tree Contacts | Tree Limb Fallen | tree fell on overhead and pulled down a phase. | O/H Conductor | O/H Conductor | 171 | 78 | 222 | West | BECKF2
126038 | 2012-12-21 | Tree Contacts | Tree Limb Fallen | tree fell on overhead and pulled down a phase. | O/H Conductor | O/H Conductor | 202 | 21 | 71 | West | BECKF2
126038 | 2012-12-21 | Tree Contacts | Tree Limb Fallen | tree fell on overhead and pulled down a phase. | O/H Conductor | O/H Conductor | 202 | 63 | 212 | West | BECKF2
126038 | 2012-12-21 | Tree Contacts | Tree Limb Fallen | tree fell on overhead and pulled down a phase. | O/H Conductor | O/H Conductor | 373 | 17 | 106 | West | BECKF2
126038 | 2012-12-21 | Tree Contacts | Tree Limb Fallen | tree fell on overhead and pulled down a phase. | O/H Conductor | O/H Conductor | 622 | 13 | 135 | West | BECKF2
126038 | 2012-12-21 | Tree Contacts | Tree Limb Fallen | tree fell on overhead and pulled down a phase. | O/H Conductor | O/H Conductor | 622 | 35 | 363 | West | BECKF2
126039 | 2012-12-21 | Tree Contacts | Tree Limb Fallen | Trees on wires & downed conductor | O/H Conductor | O/H Conductor | 50 | 196 | 163 | East | UZ12
126040 | 2012-12-21 | Defective Equipment | Equipment Failure - Cause Unknown | Burnt off lead at S641 touching bottom phase circuit. | O/H Switchgear | Fused Cutout | 27 | 45 | 20 | South | 145F4
126040 | 2012-12-21 | Defective Equipment | Equipment Failure - Cause Unknown | Burnt off lead at S641 touching bottom phase circuit. | O/H Switchgear | Fused Cutout | 1046 | 110 | 1918 | South | 145F4
126041 | 2012-12-21 | Adverse Weather | Snow | primary wires down | O/H Conductor | O/H Conductor | 12 | 126 | 25 | East | 7F4
126042 | 2012-12-21 | Adverse Weather | Snow | Wire Down | O/H Conductor | O/H Conductor | 8 | 57 | 8 | East | 249F2
126043 | 2012-12-21 | Adverse Weather | Snow | Snow build up on line | O/H Conductor | O/H Conductor | 13 | 229 | 50 | East | BLKF4
126044 | 2012-12-21 | Adverse Weather | Snow | Broken cut-out | O/H Switchgear | Fused Cutout | 1 | 44 | 1 | Central | UC07
126046 | 2012-12-21 | Adverse Weather | Snow | Broken Cut-out | O/H Switchgear | Fused Cutout | 1 | 78 | 1 | Central | TD12
126047 | 2012-12-21 | Adverse Weather | Snow | broken insulators | Pole Attachement | Insulator | 16 | 113 | 30 | East | AN06
126048 | 2012-12-21 | Adverse Weather | Snow | G932B was found open during snow storm. Probable cause of outage is tree contact. | None | None | 11 | 334 | 61 | East | LTM01
126049 | 2012-12-21 | Adverse Weather | Snow | weather, snow. | None | None | 10 | 447 | 74 | East | 56F1
126052 | 2012-12-21 | Adverse Weather | Snow | S15827 was found open during snow storm. No cause found. | O/H Switchgear | Fused Cutout | 1 | 181 | 3 | South | 145F3
126053 | 2012-12-21 | Adverse Weather | Snow | weather | None | None | 6 | 528 | 53 | East | BLKF5
126054 | 2012-12-22 | Tree Contacts | Tree Limb Fallen | Phase contacted span guy had to be re-tensioned Jan 3 2013 | None | None | 361 | 45 | 271 | Central | SR02
126055 | 2012-12-22 | Adverse Weather | Snow | S. Barkley reports G53 2 fuses found opened and the 3 was opened to allow crew to make repairs on the overhead conductor. | O/H Conductor | O/H Conductor | 11 | 333 | 61 | East | 7F4
126056 | 2012-12-22 | Tree Contacts | Tree Limb Fallen | Tree Contact | None | None | 1 | 320 | 5 | West | BECKF2
126057 | 2012-12-22 | Adverse Weather | Wind | 624F6 CB auto-reclosed and RX2007 B phase locked out due to tree contact. | O/H Conductor | O/H Conductor | 264 | 161 | 708 | West | 624F6
126059 | 2012-12-24 | Defective Equipment | Equipment Failure - Cause Unknown | RX2003 reloser auto reclosed 1116 customers effected in momentary outage. OMS indicaties S11692W phase fuse opened. 24/7 reports defective transformer at 603 Clearbrook. 7 customer remain out of power until transformer is changed. | U/G Transformer | Padmount (1ph) | 7 | 230 | 27 | South | 606F1
126059 | 2012-12-24 | Defective Equipment | Equipment Failure - Cause Unknown | RX2003 reloser auto reclosed 1116 customers effected in momentary outage. OMS indicaties S11692W phase fuse opened. 24/7 reports defective transformer at 603 Clearbrook. 7 customer remain out of power until transformer is changed. | U/G Transformer | Padmount (1ph) | 126 | 109 | 229 | South | 606F1
126060 | 2012-12-24 | Defective Equipment | Equipment Failure - Cause Unknown | Defective transformer TE1731 | U/G Transformer | Padmount (3ph) | 1 | 422 | 7 | East | 7F2
126061 | 2012-12-26 | Adverse Weather | Snow | snow on top of XFMR, crossed between tank and sec. Legs | O/H Transformer | O/H Transformer (1ph) | 1 | 159 | 3 | West | BECKF2
126062 | 2012-12-27 | Defective Equipment | Equipment Deterioration Due To Age | Replace defective sec service | Secondary \ Service | O/H Service | 10 | 159 | 26 | Central | TD06
126063 | 2012-12-31 | Scheduled Outage | Repair | transformer X31139 was isolated to allow crews to clear a damaged down guy. | Unknown \ Other | Unknown \ Other | 6 | 17 | 2 | Central | AB05
126064 | 2012-12-31 | Scheduled Outage | Repair | MAKE TEMPORARY REPAIRS TO GUY WIRE | Unknown \ Other | Unknown \ Other | 6 | 32 | 3 | Central | AB05
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 180 | 122 | 366 | West | ALEXF3
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 250 | 14 | 58 | West | ALEXF3
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 300 | 26 | 130 | West | ALEXF3
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 370 | 16 | 99 | West | ALEXF3
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 610 | 109 | 1108 | West | ALEXF3
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 664 | 92 | 1018 | West | ALEXF3
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 1700 | 1 | 28 | West | ALEXF3
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 1900 | 2 | 63 | West | ALEXF3
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 1900 | 24 | 760 | West | ALEXF3
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 1900 | 89 | 2818 | West | ALEXF3
126066 | 2013-01-01 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 2100 | 23 | 805 | West | ALEXF3
126066 | 2013-01-02 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 730 | 355 | 4319 | West | ALEXF3
126066 | 2013-01-02 | Defective Equipment | Mechanical Failure | Switch 328 blue phase termination failure. | U/G Cable Attachement | Termination \ Stress Cone | 1030 | 16 | 275 | West | ALEXF3
126067 | 2013-01-01 | Human Element | Improper Construction/installation | Trunk cable cut at each SC9069-CB3 & SC9360-L2 | U/G Switchgear | Gas-Insulated Dead Front | 233 | 311 | 1208 | West | JKGF4
126067 | 2013-01-01 | Human Element | Improper Construction/installation | Trunk cable cut at each SC9069-CB3 & SC9360-L2 | U/G Switchgear | Gas-Insulated Dead Front | 2124 | 10 | 354 | West | JKGF4
126069 | 2013-01-02 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33064 FOR SERVICE UPGRADE | None | None | 2 | 25 | 1 | South | 180F4
126071 | 2013-01-03 | Scheduled Outage | Construction | Transformer #X33361 opened by crew to string a new service | None | None | 7 | 34 | 4 | South | EPWF4
126072 | 2013-01-03 | Scheduled Outage | Forced Switching | Transformer #X7575 opened by crew to fault locate a service | None | U/G Service | 5 | 80 | 7 | West | MWDF3
126073 | 2013-01-03 | Scheduled Outage | Maintenance | metering and maintencae | None | None | 1 | 154 | 3 | South | 130F1
126078 | 2013-01-04 | Tree Contacts | Broken Branch | Tree in wires at 4274 Eighth Line | O/H Conductor | O/H Conductor | 352 | 66 | 387 | East | 249F2
126078 | 2013-01-04 | Tree Contacts | Broken Branch | Tree in wires at 4274 Eighth Line | O/H Conductor | O/H Conductor | 1082 | 1 | 18 | East | 249F2
126082 | 2013-01-04 | Defective Equipment | Electrical Failure | faulted cable | U/G Cable | XLPE Splice | 296 | 181 | 893 | West | 44F1
126083 | 2013-01-05 | Adverse Weather | Wet Snow | 22M27 auto reclosed auto. Heavey snow squal in the area reported by OPD | O/H Conductor | O/H Conductor | 3824 | 23 | 1466 | South | 22M27
126083 | 2013-01-05 | Adverse Weather | Wet Snow | 22M27 auto reclosed auto. Heavey snow squal in the area reported by OPD | O/H Conductor | O/H Conductor | 6515 | 36 | 3909 | South | 22M27
126086 | 2013-01-05 | Unknown/Other | Unknown | Not yet known. | U/G Transformer | Padmount (3ph) | 1 | 487 | 8 | East | 6F10
126087 | 2013-01-05 | Defective Equipment | Defective Equipment/ Material | Defective transformer 540, replaced by on-call. | O/H Transformer | O/H Transformer (1ph) | 1 | 641 | 11 | South | 72F4
126091 | 2013-01-08 | Scheduled Outage | Forced Switching | Transformer TP7421 at 603 Clearbrook was isolated to allow crew to perform soil remediation. 3 customers were affected for 355 minutes. FALLOWFIELD DS (606F1) ID#126091. | None | Padmount (1ph) | 3 | 355 | 18 | South | 606F1
126092 | 2013-01-08 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X29993 FOR A SERVICE REPAIR | None | None | 5 | 20 | 2 | Central | TR09
126093 | 2013-01-08 | Scheduled Outage | Construction | ISOLATED XFMR X36241 AND REPLACED IT | None | None | 7 | 165 | 19 | South | 190F2
126094 | 2013-01-08 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 49 | 1 | 1 | East | 77M5
126101 | 2013-01-09 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X23146 FOR A SERVICE UPGRADE | None | None | 2 | 45 | 2 | East | UG12
126102 | 2013-01-09 | Scheduled Outage | Sectionalizing | ISOLATED TRANSFORMER X31496 TO RECONNECT SERVICE | None | None | 9 | 10 | 2 | Central | TH06
126103 | 2013-01-09 | Scheduled Outage | Sectionalizing | ISOLATED XFMR X39347 TO RE-CONNECT SERVICE | None | None | 30 | 19 | 10 | Central | UN07
126104 | 2013-01-09 | Scheduled Outage | Construction | S28882 isolated to install new Transformer, extend line and install new secondary. | None | None | 5 | 277 | 23 | East | 7F2
126106 | 2013-01-09 | Defective Equipment | Electrical Failure | S10-2 white phase fuse was found blown due to cable fault between TP5495W and 2555W on Borduias. | U/G Cable | Unknown \ Other | 7 | 49 | 6 | West | 39F3
126106 | 2013-01-09 | Defective Equipment | Electrical Failure | S10-2 white phase fuse was found blown due to cable fault between TP5495W and 2555W on Borduias. | U/G Cable | Unknown \ Other | 19 | 31 | 10 | West | 39F3
126106 | 2013-01-09 | Defective Equipment | Electrical Failure | S10-2 white phase fuse was found blown due to cable fault between TP5495W and 2555W on Borduias. | U/G Cable | Unknown \ Other | 56 | 131 | 122 | West | 39F3
126107 | 2013-01-09 | Scheduled Outage | Forced Switching | Isolated xfmr x32774 to make repairs to secondary service | None | None | 15 | 76 | 19 | Central | UW14
126108 | 2013-01-09 | Scheduled Outage | Construction | Transformer #X31496 opened by crew to run a new triplex service | None | None | 9 | 20 | 3 | Central | TH06
126110 | 2013-01-09 | Adverse Weather | Ice/Icing | REMOVE ICE FROM TRIPLEX | Secondary \ Service | O/H Service | 3 | 15 | 1 | West | 28F2
126111 | 2013-01-10 | Scheduled Outage | Construction | replace metering fuses | None | None | 0 | 30 | 0 | Central | 2806
126111 | 2013-01-10 | Scheduled Outage | Construction | replace metering fuses | None | None | 1 | 10 | 0 | Central | 2806
126111 | 2013-01-10 | Scheduled Outage | Construction | replace metering fuses | None | None | 1 | 24 | 0 | Central | 2806
126112 | 2013-01-10 | Scheduled Outage | Forced Switching | Transformer X30816 isolated to reattach triplex | None | None | 6 | 16 | 2 | Central | UF07
126114 | 2013-01-12 | Defective Equipment | Mechanical Failure | Transformer X30148 @ 729 Gladstone was found open due to a broken cut-out. | O/H Transformer | O/H Transformer (1ph) | 10 | 74 | 12 | Central | AM02
126115 | 2013-01-12 | Defective Equipment | Electrical Failure | blown lightening arrestor at overhead transformer X24017 | Pole Attachement | Arrester | 4 | 33 | 2 | East | 77M2
126115 | 2013-01-12 | Defective Equipment | Electrical Failure | blown lightening arrestor at overhead transformer X24017 | Pole Attachement | Arrester | 1807 | 71 | 2138 | East | 77M2
126116 | 2013-01-12 | Defective Equipment | Defective Equipment/ Material | Defective cut out at S105 | O/H Switchgear | Fused Cutout | 1 | 30 | 0 | South | 200F6
126118 | 2013-01-12 | Unknown/Other | Unknown | unknown | None | None | 5 | 111 | 9 | South | 200F1
126119 | 2013-01-13 | Scheduled Outage | Maintenance | Asbestos removal and customer vault maintenance | None | None | 1 | 337 | 6 | Central | UC05
126120 | 2013-01-13 | Unknown/Other | Unknown | Not yet known. | None | None | 308 | 12 | 62 | East | UG02
126121 | 2013-01-13 | Scheduled Outage | Construction | repair primary in the 13kv vault VT99 | None | Switch | 1 | 522 | 9 | Central | TK6TS
126122 | 2013-01-13 | Scheduled Outage | Sectionalizing | 44kv switching | None | None | 1 | 30 | 0 | East | 48M4
126123 | 2013-01-13 | Unknown/Other | Unknown | Transformer #X19797 opened up and crew had to refuse it, no cause found | O/H Transformer | Unknown \ Other | 3 | 150 | 8 | East | BLKF5
126124 | 2013-01-13 | Adverse Weather | Ice/Icing | Transformer #X30574 opened up due to ice falling and damaging the service | O/H Switchgear | Fused Cutout | 18 | 140 | 42 | Central | SA22
126125 | 2013-01-14 | Scheduled Outage | Maintenance | TX 2555W has defective Insert | None | Elbow \ Insert | 7 | 25 | 3 | West | 39F3
126126 | 2013-01-14 | Defective Equipment | Electrical Failure | Pole fire caused by a failed fused cutout | Pole | Insulation Failure (Pole Fire) | 6 | 52 | 5 | Central | TD01
126126 | 2013-01-14 | Defective Equipment | Electrical Failure | Pole fire caused by a failed fused cutout | Pole | Insulation Failure (Pole Fire) | 1378 | 24 | 551 | Central | TD01
126127 | 2013-01-14 | Defective Equipment | Mechanical Failure | ISOLATED TRANSFORMER X31528 TO REPLACE SECONDARY CONNECTIONS ON THE TRANSFORMER | O/H Transformer | O/H Transformer (1ph) | 20 | 15 | 5 | Central | UF07
126128 | 2013-01-15 | Scheduled Outage | Maintenance | change leaking transformer | O/H Transformer | O/H Transformer (1ph) | 11 | 475 | 87 | East | AQ10
126129 | 2013-01-15 | Scheduled Outage | Maintenance | Transformers 964, 966, 967, 1274, 1273, 972, 971 on Halkirk were isolated to allow Hydro Crew to perform elbow and insert replacement | None | Padmount (1ph) | 98 | 116 | 189 | West | BRDF2
126130 | 2013-01-15 | Scheduled Outage | Construction | cut in a new transformer | None | None | 14 | 276 | 64 | East | AP06
126131 | 2013-01-15 | Defective Equipment | Defective Equipment/ Material | Replace broken transformer cutout | O/H Transformer | O/H Transformer (1ph) | 12 | 30 | 6 | Central | AB03
126132 | 2013-01-15 | Foreign Interference | Foreign Objects | Replace ssecondary service conductor due to damaged service and stand pipe | Secondary \ Service | O/H Service | 13 | 55 | 12 | Central | UF07
126133 | 2013-01-15 | Scheduled Outage | Construction | Conductor size Upgrade to secondary service | None | U/G Service | 5 | 41 | 3 | East | UG02
126134 | 2013-01-15 | Defective Equipment | Corrosion | Replace broken sec conductor on Sec Buss | Secondary \ Service | O/H Service | 23 | 30 | 12 | Central | SB03
126135 | 2013-01-16 | Scheduled Outage | Forced Switching | TP9414 at 178 Foutainhead was isolated to allow crew to replace dammaged transformer TP9414 and defective secondary cable | None | Padmount (1ph) | 9 | 196 | 29 | East | CYRF1
126138 | 2013-01-16 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X26947 TO INSTALL NEW SERVICE | None | None | 10 | 22 | 4 | East | AJ04
126139 | 2013-01-16 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32017 FOR A SERVICE UP-GRADE | None | None | 23 | 84 | 32 | Central | UC01
126140 | 2013-01-17 | Scheduled Outage | Maintenance | Customer Vault Maintenance | None | None | 1 | 261 | 4 | East | TO3AP
126142 | 2013-01-17 | Scheduled Outage | Maintenance | Transformer TP9109 at 12 Colfax was isolated to allow crew to re-arranger primary cables. 8 Customers were affected for 43 minutes. Woodroffe (170F1) ID# 126142. | None | None | 8 | 43 | 6 | South | 170F1
126143 | 2013-01-17 | Tree Contacts | Tree Growth/ Untrimmed Tree | BLOWN FUSE AT SWITCH SW1232 FEEDING TWO PAD MOUNT TRANSFORMERS | O/H Switchgear | Fused Cutout | 40 | 50 | 33 | West | BECKF2
126144 | 2013-01-17 | Scheduled Outage | Forced Switching | Transformer 540 at 1929 Woodroffe was opened to allow crew to perform switching. 1 customer was interrupted for 9 minutes. Merivale (72F4) ID# 126144. | None | None | 1 | 9 | 0 | South | 72F4
126145 | 2013-01-18 | Defective Equipment | Electrical Failure | Cable fault feeding TVM2855, unable to determine which cable is defective | U/G Cable | PILC | 156 | 265 | 689 | Central | TL3SB
126145 | 2013-01-18 | Defective Equipment | Electrical Failure | Cable fault feeding TVM2855, unable to determine which cable is defective | U/G Cable | PILC | 157 | 22 | 58 | Central | TL3SB
126145 | 2013-01-18 | Defective Equipment | Electrical Failure | Cable fault feeding TVM2855, unable to determine which cable is defective | U/G Cable | PILC | 358 | 83 | 495 | Central | TL3SB
126146 | 2013-01-18 | Foreign Interference | Vehicle | Transformer #X34204 isolated by crew due to damages made by truck hitting triplex service and pulling out standpipe | Secondary \ Service | O/H Service | 15 | 60 | 15 | Central | UL14
126148 | 2013-01-19 | Human Element | Switching Error | While attempting to block a recloser from the ground, recloser tripped. | O/H Switchgear | Recloser (3ph) | 427 | 11 | 78 | West | 624F6
126149 | 2013-01-19 | Scheduled Outage | Construction | TVM2855 was isolated to allow Hydro Ottawa crews to repair a collapsed duct bank and damaged primary cables. Customers put on temp. generator for the duration of the outage. | None | PILC | 2 | 7788 | 260 | Central | TL3SB
126150 | 2013-01-19 | Human Element | Switching Error | While trying to block a hold off from the ground on an overhead recloser crew tripped the recloser. | O/H Switchgear | Recloser (3ph) | 149 | 5 | 12 | West | MWDF3
126151 | 2013-01-19 | Foreign Interference | Wildlife (Bird/Animal) | replaced blown fuse at transformer x39025 due to bird contact | O/H Transformer | O/H Transformer (1ph) | 5 | 64 | 5 | East | TB14
126152 | 2013-01-19 | Scheduled Outage | Maintenance | Hydro Ottawa crew to service S15401 and Contractor to service S10736 CHZ customer owned switch. | None | Inline Switch | 1 | 180 | 3 | South | 22M23
126153 | 2013-01-19 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X36335 DUE TO BIRD CONTACT | O/H Transformer | O/H Transformer (1ph) | 1 | 175 | 3 | West | BECKF2
126154 | 2013-01-20 | Scheduled Outage | Maintenance | 13kV vault VT301 at 1630 Star Top isolated for PCB transformer replacement and customer vault maintenance | None | Transformer | 1 | 435 | 7 | East | TB2AL
126155 | 2013-01-20 | Defective Equipment | Mechanical Failure | Crew found a burnt termination at switch S550 Blue. | O/H Switchgear | Fused Cutout | 53 | 210 | 186 | West | 24F8
126156 | 2013-01-20 | Adverse Weather | Extreme Wind | suspect red and white phase contact caused by wind gusts. | O/H Conductor | O/H Conductor | 85 | 16 | 23 | Central | TK2AC
126156 | 2013-01-20 | Adverse Weather | Extreme Wind | suspect red and white phase contact caused by wind gusts. | O/H Conductor | O/H Conductor | 130 | 96 | 208 | Central | TK2AC
126156 | 2013-01-20 | Adverse Weather | Extreme Wind | suspect red and white phase contact caused by wind gusts. | O/H Conductor | O/H Conductor | 196 | 8 | 26 | Central | TK2AC
126157 | 2013-01-20 | Defective Equipment | Electrical Failure | defective transformer switch | O/H Switchgear | Fused Cutout | 8 | 194 | 26 | Central | TD06
126158 | 2013-01-20 | Defective Equipment | Defective Equipment/ Material | Defective Transformer | O/H Transformer | O/H Transformer (1ph) | 1 | 294 | 5 | West | 624F6
126159 | 2013-01-21 | Unknown/Other | Unknown | overhead xfmr open affecting 4 customers on Newark and Fairhill. Crew found no evident cause for outage | O/H Transformer | O/H Transformer (1ph) | 4 | 65 | 4 | South | 84F2
126160 | 2013-01-21 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 300 | 8 | 40 | Central | UW03
126161 | 2013-01-21 | Scheduled Outage | Construction | ISOLATED TRANSFORMERS X45387 AND X33797 FOR POLE REPLACMENT | None | None | 20 | 30 | 10 | Central | UW04
126162 | 2013-01-22 | Unknown/Other | Unknown | Transformer #TP6821 opened up, cause not found by crew | U/G Transformer | Padmount (1ph) | 12 | 86 | 17 | East | 7F4
126163 | 2013-01-22 | Foreign Interference | Dig-In | Cable Dig in | U/G Cable | XLPE | 1 | 509 | 8 | West | BECKF2
126164 | 2013-01-22 | Defective Equipment | Electrical Failure | Cable fault between TO and VT363 on the TO3AP line. | U/G Cable | PILC | 527 | 39 | 343 | East | TO3AP
126165 | 2013-01-22 | Defective Equipment | Defective Equipment/ Material | Transformer TE1619 was isolated to allow crew to replace defective transformer. | U/G Transformer | Padmount (1ph) | 13 | 336 | 73 | East | 77M5
126166 | 2013-01-23 | Human Element | Improper Design | Transformer #TP6821 opened up due to possible over-loading, second day in a row | U/G Transformer | Padmount (1ph) | 16 | 98 | 26 | East | 7F4
126167 | 2013-01-23 | Defective Equipment | Electrical Failure | Blown internal transformer fuse | U/G Transformer | Unknown \ Other | 12 | 7 | 1 | East | 7F4
126170 | 2013-01-24 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X40060 DUE TO ANIMAL CONTACT | O/H Transformer | O/H Transformer (1ph) | 10 | 50 | 8 | South | 160F3
126171 | 2013-01-25 | Scheduled Outage | Construction | To allow contractor to install new service in transformer TP8577 @ 4772 Bank St. | None | None | 1 | 75 | 1 | East | LTM01
126172 | 2013-01-25 | Scheduled Outage | Construction | VE41G transformer bus was isolated to allow contractor to install microfit | None | None | 1 | 76 | 1 | East | 77M1
126175 | 2013-01-28 | Scheduled Outage | Maintenance | G483 was isolated by crews to replace cutout fuses and remove N.I.U. Secondary from transformer. | None | None | 1 | 109 | 2 | East | CYRF4
126176 | 2013-01-28 | Defective Equipment | Defective Equipment/ Material | Defective overhead transformer | O/H Transformer | O/H Transformer (1ph) | 16 | 120 | 32 | Central | UX06
126177 | 2013-01-29 | Scheduled Outage | Construction | transfer plant to new pole line & balance load | None | O/H Transformer (1ph) | 0 | 40 | 0 | Central | UW04
126177 | 2013-01-29 | Scheduled Outage | Construction | transfer plant to new pole line & balance load | None | O/H Transformer (1ph) | 27 | 195 | 88 | Central | UW04
126177 | 2013-01-29 | Scheduled Outage | Construction | transfer plant to new pole line & balance load | None | O/H Transformer (1ph) | 27 | 250 | 112 | Central | UW04
126178 | 2013-01-29 | Defective Equipment | Defective Equipment/ Material | Crew opened up transformer #X30891 to replace leads on transformer | O/H Transformer | O/H Transformer (1ph) | 26 | 55 | 24 | Central | SR01
126179 | 2013-01-29 | Defective Equipment | Defective Equipment/ Material | S11692 opened due to defective R phase U/G cable between S11692 and TP3150 causing also the recloser RX2003 to A/R | U/G Cable | XLPE | 120 | 93 | 186 | South | 606F1
126180 | 2013-01-30 | Defective Equipment | Mechanical Failure | Defective secondary at X12899 | O/H Transformer | O/H Transformer (1ph) | 4 | 12 | 1 | East | 7F2
126181 | 2013-01-30 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #GL3862 opened up due to animal contact | O/H Transformer | O/H Transformer (1ph) | 8 | 46 | 6 | East | 7F4
126182 | 2013-01-30 | Scheduled Outage | Construction | X32759 interrupted to allow crews to set new poles. | None | O/H Transformer (1ph) | 5 | 115 | 10 | Central | UW04
126183 | 2013-01-30 | Scheduled Outage | Construction | X33797 interrupted to allow crews to set new poles. | None | O/H Transformer (1ph) | 11 | 95 | 17 | Central | UW04
126184 | 2013-01-30 | Adverse Weather | Freezing Rain | Weather related | O/H Switchgear | Fused Cutout | 112 | 57 | 106 | East | 7F4
126185 | 2013-01-30 | Tree Contacts | Broken Branch | tree branch in the overhead | O/H Switchgear | Inline Switch | 51 | 73 | 62 | West | BECKF2
126186 | 2013-01-30 | Defective Equipment | Defective Equipment/ Material | BURNING line clamp feeding PT194 | O/H Switchgear | Fused Cutout | 3 | 15 | 1 | East | TB07
126187 | 2013-01-30 | Defective Equipment | Defective Equipment/ Material | Defective transformer switch | O/H Switchgear | Fused Cutout | 5 | 26 | 2 | Central | SK16
126188 | 2013-01-31 | Foreign Interference | Vehicle | Transformer X25608 was opened to allow crew to repair downed neutral conductor. | O/H Conductor | O/H Conductor | 1 | 95 | 2 | South | EPWF3
126189 | 2013-01-31 | Defective Equipment | Electrical Failure | S1180 R phase was found blown due to a cable fault between TP5947 and TP5951. | U/G Cable | XLPE | 21 | 25 | 9 | South | 145F1
126189 | 2013-01-31 | Defective Equipment | Electrical Failure | S1180 R phase was found blown due to a cable fault between TP5947 and TP5951. | U/G Cable | XLPE | 44 | 72 | 53 | South | 145F1
126189 | 2013-01-31 | Defective Equipment | Electrical Failure | S1180 R phase was found blown due to a cable fault between TP5947 and TP5951. | U/G Cable | XLPE | 56 | 22 | 21 | South | 145F1
126189 | 2013-01-31 | Defective Equipment | Electrical Failure | S1180 R phase was found blown due to a cable fault between TP5947 and TP5951. | U/G Cable | XLPE | 83 | 118 | 163 | South | 145F1
126190 | 2013-01-31 | Defective Equipment | Defective Equipment/ Material | 44/46 spedina centre phase is low and caused original outage, crews to re-sag overhead | O/H Transformer | O/H Transformer (1ph) | 741 | 7 | 86 | Central | UJ07
126194 | 2013-01-31 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X37910 opened up due to animal contact | O/H Transformer | O/H Transformer (1ph) | 4 | 80 | 5 | East | AJ07
126195 | 2013-01-31 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X36008 opened up due to tree contact | O/H Transformer | O/H Transformer (1ph) | 12 | 147 | 29 | South | EPWF1
126196 | 2013-01-31 | Adverse Weather | Extreme Wind | Defective overhead conductors. | O/H Conductor | O/H Conductor | 91 | 76 | 115 | Central | UJ07
126199 | 2013-01-31 | Defective Equipment | Electrical Failure | Customer secondary device fault | Customer Owned | Customer-Owned | 1 | 274 | 5 | Central | TL3SB
126200 | 2013-01-31 | Scheduled Outage | Maintenance | To make repairs to secondary service | None | None | 7 | 1468 | 171 | Central | TD07
126201 | 2013-02-01 | Scheduled Outage | Maintenance | To splice cables and change elbows and inserts. | None | Elbow \ Insert | 150 | 110 | 275 | West | BRDF2
126202 | 2013-02-01 | Scheduled Outage | Maintenance | Crew isolated TP2417 at 623 Ballycastle to replace a leaking transformer. | None | Padmount (1ph) | 6 | 135 | 14 | East | 7F4
126203 | 2013-02-01 | Defective Equipment | Mechanical Failure | Defective SOK1Y1 breaker. | Station Equipment | Breaker \ Relay | 9 | 7 | 1 | East | SO13
126204 | 2013-02-01 | Scheduled Outage | Maintenance | Transformer X16845 at 2013 Ogilvie Rd. isolated to replace switch. | None | None | 11 | 56 | 10 | East | 8F4
126205 | 2013-02-01 | Scheduled Outage | Construction | Transformer X3512 isolated to connect new service | None | None | 4 | 214 | 14 | South | 145F3
126206 | 2013-02-01 | Defective Equipment | Defective Equipment/ Material | To repair secondary cable. | Customer Owned | Customer-Owned | 1 | 246 | 4 | Central | TL3SB
126209 | 2013-02-01 | Defective Equipment | Mechanical Failure | 1 phase of overhead burned thru at crossarm on G82 at 3445 Navan Rd. Isolation required on all 3 phases from S26367 for repairs to be performed. | O/H Conductor | O/H Conductor | 19 | 447 | 142 | East | BLKF3
126209 | 2013-02-01 | Defective Equipment | Mechanical Failure | 1 phase of overhead burned thru at crossarm on G82 at 3445 Navan Rd. Isolation required on all 3 phases from S26367 for repairs to be performed. | O/H Conductor | O/H Conductor | 109 | 241 | 438 | East | BLKF3
126211 | 2013-02-02 | Defective Equipment | Mechanical Failure | Make temp repair to neutral conductor | O/H Conductor | O/H Conductor | 7 | 55 | 6 | East | UB07
126212 | 2013-02-02 | Defective Equipment | Defective Equipment/ Material | make repairs to downed neutral | O/H Conductor | O/H Conductor | 7 | 29 | 3 | East | UB07
126213 | 2013-02-02 | Unknown/Other | Unknown | Not yet known.OFS reported working fire | O/H Transformer | O/H Transformer (1ph) | 20 | 80 | 27 | Central | AD06
126214 | 2013-02-04 | Scheduled Outage | Construction | X45380 isolated to allow contractors to transfer secondary plant to new poles. | None | O/H Transformer (1ph) | 10 | 153 | 26 | Central | UW04
126215 | 2013-02-04 | Scheduled Outage | Maintenance | PLANNED OUTAGE TO CHANGE TERMINATION AT S550B AND CHANGE ELBOWS AND INSERTS TO 4 TRANSFORMERS. | None | None | 53 | 172 | 152 | West | 24F8
126216 | 2013-02-05 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | Unknown \ Other | 0 | 13 | 0 | East | 77M6
126216 | 2013-02-05 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | Unknown \ Other | 10 | 8 | 1 | East | 77M6
126216 | 2013-02-05 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | Unknown \ Other | 20 | 12 | 4 | East | 77M6
126216 | 2013-02-05 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | Unknown \ Other | 40 | 72 | 48 | East | 77M6
126216 | 2013-02-05 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | Unknown \ Other | 75 | 88 | 110 | East | 77M6
126216 | 2013-02-05 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | Unknown \ Other | 175 | 86 | 251 | East | 77M6
126216 | 2013-02-05 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | Unknown \ Other | 2003 | 11 | 367 | East | 77M6
126216 | 2013-02-05 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | Unknown \ Other | 2003 | 66 | 2203 | East | 77M6
126216 | 2013-02-05 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | Unknown \ Other | 4800 | 6 | 480 | East | 77M6
126219 | 2013-02-05 | Scheduled Outage | Construction | To allow contractor to steam the ducts for reconfigure of primary cables | None | None | 11 | 223 | 41 | South | 606F1
126221 | 2013-02-05 | Defective Equipment | Defective Equipment/ Material | Internal issued. the CB4 at VT855 (experimental farm) was found open. We re-engized our cable(305) and the Bus at VT855 but left the CB4 off for them to toubleshoot. | Customer Owned | Customer-Owned | 1 | 53 | 1 | Central | 306
126223 | 2013-02-06 | Scheduled Outage | Maintenance | Transformer X27207 at 426 Simpson Rd. isolated to rearrange secondary | None | None | 3 | 68 | 3 | East | UQ07
126224 | 2013-02-06 | Scheduled Outage | Maintenance | Tim Connell from K-Line changed out 2 transformers to one single one - new X45384. Removed transformer X32757 at 1159 Minnetonka Rd. and transformer 33797 at 1143 Minnetonka Rd | None | None | 11 | 230 | 42 | Central | UW04
126225 | 2013-02-06 | Scheduled Outage | Maintenance | Tim Connell from K-Line changed out 2 transformers to one single one - new X45384. Removed transformer X32757 at 1159 Minnetonka Rd. and transformer 33797 at 1143 Minnetonka Rd | None | None | 11 | 108 | 20 | Central | UW04
126226 | 2013-02-07 | Scheduled Outage | Construction | installing 2 new transformers on CYRF1 TP9332 and TP9332 | None | None | 5 | 213 | 18 | East | CYRF1
126229 | 2013-02-08 | Defective Equipment | Electrical Failure | Suspected cable fault between VT565 and VT733 at the St. Laurent shopping centre. | U/G Cable | PILC | 14 | 147 | 34 | East | 1808
126230 | 2013-02-09 | Scheduled Outage | Maintenance | 4kV transformer X23665 isolated to allow crews to remove a service after a house fire. | None | O/H Transformer (1ph) | 8 | 24 | 3 | East | UB07
126232 | 2013-02-09 | Defective Equipment | Defective Equipment/ Material | Broken bushing on the pothead for the TB06 riser. | U/G Cable Attachement | Pothead | 1518 | 66 | 1670 | East | TB06
126234 | 2013-02-10 | Defective Equipment | Defective Equipment/ Material | Transformer #X10580 opened up due to broken fuse link | O/H Transformer | O/H Transformer (1ph) | 3 | 97 | 5 | West | 28F2
126235 | 2013-02-11 | Scheduled Outage | Maintenance | Transformer X34431 at 599 Kirkwood Ave. isolated to make repairs to open buss and transfer plant. Work postponed. | None | None | 11 | 31 | 6 | Central | SM16
126236 | 2013-02-11 | Scheduled Outage | Maintenance | Equipment upgrade | None | O/H Transformer (1ph) | 6 | 270 | 27 | Central | UW04
126237 | 2013-02-11 | Defective Equipment | Defective Equipment/ Material | REPLACED BROKEN FUSE FEEDING TRANSFORMER X24091 | O/H Transformer | O/H Transformer (1ph) | 5 | 19 | 2 | East | 7F4
126238 | 2013-02-12 | Defective Equipment | Electrical Failure | Defective Insulator tracking | Pole Attachement | Insulator | 64 | 10 | 11 | East | 8F1
126238 | 2013-02-12 | Defective Equipment | Electrical Failure | Defective Insulator tracking | Pole Attachement | Insulator | 96 | 70 | 112 | East | 8F1
126239 | 2013-02-12 | Defective Equipment | Mechanical Failure | RX2010 A/R & RX2047 tripped due to a blown arrestor at X35280 @ 33 Evelyn. | Pole Attachement | Arrester | 587 | 88 | 861 | West | ALEXF3
126239 | 2013-02-12 | Defective Equipment | Mechanical Failure | RX2010 A/R & RX2047 tripped due to a blown arrestor at X35280 @ 33 Evelyn. | Pole Attachement | Arrester | 1598 | 68 | 1811 | West | ALEXF3
126239 | 2013-02-12 | Defective Equipment | Mechanical Failure | RX2010 A/R & RX2047 tripped due to a blown arrestor at X35280 @ 33 Evelyn. | Pole Attachement | Arrester | 2779 | 1 | 46 | West | ALEXF3
126241 | 2013-02-12 | Loss Of Supply | Transmission Inadvertent | Loss of Supply | None | None | 379 | 9 | 57 | East | V11F3
126241 | 2013-02-12 | Loss Of Supply | Transmission Inadvertent | Loss of Supply | None | None | 509 | 9 | 76 | East | V11F2
126241 | 2013-02-12 | Loss Of Supply | Transmission Inadvertent | Loss of Supply | None | None | 744 | 9 | 112 | East | V11F1
126242 | 2013-02-12 | Foreign Interference | Wildlife (Bird/Animal) | Recloser 1048 opened under holdoff and switch 841 at 2515 Marchurst was found open due to bird contact. | O/H Conductor | O/H Conductor | 35 | 4 | 2 | West | MWDF3
126242 | 2013-02-12 | Foreign Interference | Wildlife (Bird/Animal) | Recloser 1048 opened under holdoff and switch 841 at 2515 Marchurst was found open due to bird contact. | O/H Conductor | O/H Conductor | 36 | 14 | 8 | West | MWDF3
126242 | 2013-02-12 | Foreign Interference | Wildlife (Bird/Animal) | Recloser 1048 opened under holdoff and switch 841 at 2515 Marchurst was found open due to bird contact. | O/H Conductor | O/H Conductor | 81 | 7 | 9 | West | MWDF3
126242 | 2013-02-12 | Foreign Interference | Wildlife (Bird/Animal) | Recloser 1048 opened under holdoff and switch 841 at 2515 Marchurst was found open due to bird contact. | O/H Conductor | O/H Conductor | 149 | 198 | 492 | West | MWDF3
126243 | 2013-02-12 | Defective Equipment | Mechanical Failure | Transformer X35280 was opened by crew to replace blown arrestor. | O/H Transformer | O/H Transformer (1ph) | 2 | 48 | 2 | West | ALEXF3
126244 | 2013-02-12 | Defective Equipment | Defective Equipment/ Material | Transformer OTT4164 (55C4B-0325) at 891 Maitland Ave. isolated replace defective cutout which caused pole fire. Installed new cutout arrestor and bracket | Pole Attachement | Arrester | 16 | 59 | 16 | Central | TD01
126246 | 2013-02-13 | Scheduled Outage | Construction | BRDF2 Blue phase transformers between S10018 and PP2003 were isolated to allow crew to re-arrange primary cables. | None | None | 119 | 321 | 637 | West | BRDF2
126248 | 2013-02-13 | Scheduled Outage | Construction | ISOLATED AND RELOCATED TRANSFORMER X32757 | None | None | 11 | 195 | 36 | Central | UW04
126249 | 2013-02-13 | Defective Equipment | Defective Equipment/ Material | repair broken elbow | U/G Transformer | Padmount (3ph) | 11 | 218 | 40 | West | 624F5
126251 | 2013-02-14 | Scheduled Outage | Construction | Transformers 2148 and 2149 isolated to allow crews to perform cable reconfiguration. | None | Padmount (1ph) | 27 | 227 | 102 | West | BRDF2
126252 | 2013-02-14 | Defective Equipment | Defective Equipment/ Material | Transformer #X31661 opened up due to defective transformer that needed to be replaced. | O/H Transformer | O/H Transformer (1ph) | 16 | 334 | 89 | Central | SR08
126253 | 2013-02-14 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused fuses at G662 BW and S27791 W to blow. | None | None | 43 | 79 | 57 | East | 77M1
126254 | 2013-02-14 | Scheduled Outage | Construction | Transformer #X28080 opened by crew to re-arrange plant. | None | None | 8 | 180 | 24 | East | UZ11
126256 | 2013-02-14 | Scheduled Outage | Construction | Transformer #X30972 opened by crew to replace poles | None | None | 27 | 285 | 128 | Central | UN05
126257 | 2013-02-14 | Defective Equipment | Defective Equipment/ Material | 145F2 breaker opened under hold off protection due to a defective lightning arresstor. | Pole Attachement | Arrester | 618 | 9 | 93 | South | 145F2
126258 | 2013-02-15 | Scheduled Outage | Construction | Installing new pole | None | None | 4 | 90 | 6 | Central | UN10
126259 | 2013-02-15 | Scheduled Outage | Construction | Installing new pole and transfering sec bus | None | None | 11 | 255 | 47 | Central | SM16
126260 | 2013-02-15 | Scheduled Outage | Construction | Transformers 2147, 2151 and 2150 in the Meadow Creek area were isolated to allow crews to reconfigure primary cables. | None | Padmount (1ph) | 102 | 361 | 614 | West | BRDF2
126261 | 2013-02-15 | Scheduled Outage | Vegetation Management | Tree removal in the rear of 1380 Cavendish | None | None | 3 | 287 | 14 | East | TB06
126262 | 2013-02-16 | Defective Equipment | Mechanical Failure | REPLACED DEFECTIVE 3 PHASE POWER TRANSFORMER UINT X27763 | O/H Transformer | O/H Transformer (3ph) | 5 | 123 | 10 | East | AF05
126263 | 2013-02-16 | Defective Equipment | Mechanical Failure | Transformer X23611 at 10 Braemar was isolated by crew to replace defective switch. | O/H Switchgear | Fused Cutout | 6 | 45 | 4 | East | UB04
126266 | 2013-02-17 | Defective Equipment | Defective Equipment/ Material | Transformer X31757 was isolated to allow crew to replace defective connections on secondary. | O/H Transformer | O/H Transformer (1ph) | 34 | 30 | 17 | Central | AK04
126267 | 2013-02-19 | Scheduled Outage | Construction | Install Buss Bars at S275 | None | None | 1 | 207 | 3 | East | 2211
126268 | 2013-02-19 | Human Element | Protection Setting | Differential trip on BRHQ2T2 | None | None | 9 | 8 | 1 | South | 140F2
126268 | 2013-02-19 | Human Element | Protection Setting | Differential trip on BRHQ2T2 | None | None | 523 | 8 | 70 | South | 140F1
126268 | 2013-02-19 | Human Element | Protection Setting | Differential trip on BRHQ2T2 | None | None | 556 | 8 | 74 | South | 140F5
126268 | 2013-02-19 | Human Element | Protection Setting | Differential trip on BRHQ2T2 | None | None | 791 | 8 | 105 | South | 140F4
126268 | 2013-02-19 | Human Element | Protection Setting | Differential trip on BRHQ2T2 | None | None | 1635 | 8 | 218 | South | 140F3
126269 | 2013-02-19 | Tree Contacts | Broken Branch | tree on wires | None | None | 2 | 23 | 1 | South | 200F1
126270 | 2013-02-19 | Scheduled Outage | Construction | Transformer #X32242 opened by crew to re-do transformer and upgrade services. | None | None | 6 | 140 | 14 | Central | AD06
126271 | 2013-02-19 | Scheduled Outage | Construction | Remove old cable from base | None | None | 11 | 60 | 11 | South | FAL03
126272 | 2013-02-19 | Scheduled Outage | Maintenance | Transformer X24181 at 1332 Labrie Ave. isolated to allow for pole replacement. | None | Pole | 6 | 177 | 18 | East | 6F7
126273 | 2013-02-20 | Scheduled Outage | Construction | To replace defective u/g section which is on a temporary O/H Service. | None | None | 19 | 186 | 59 | East | 7F4
126276 | 2013-02-20 | Defective Equipment | Defective Equipment/ Material | Transformer P352 at 11 Rosemount Ave. isolated to allow for repairs to hotline clamps. | O/H Conductor | Hot-Line Clamp | 2 | 20 | 1 | Central | UJ05
126277 | 2013-02-20 | Defective Equipment | Mechanical Failure | Repairs made to line tap to radial feed Pamilla East of Preston St. | O/H Conductor | Ampact | 34 | 156 | 88 | Central | SB10
126278 | 2013-02-21 | Scheduled Outage | Maintenance | To increase tap on Padmounted transformer to adjust customer voltage | None | None | 1 | 28 | 0 | East | ELW12
126279 | 2013-02-21 | Defective Equipment | Imminent Equipment Failure Detected | Replace leaking transformer at elbows | None | None | 10 | 194 | 32 | East | BLKF3
126280 | 2013-02-21 | Scheduled Outage | Construction | Install underground cable and cut out PP2049. | None | None | 30 | 426 | 213 | East | CYRF1
126281 | 2013-02-21 | Scheduled Outage | Vegetation Management | TREE TRIMMMING BY CONTRACTOR | None | O/H Transformer (1ph) | 11 | 180 | 33 | Central | TW22
126282 | 2013-02-22 | Defective Equipment | Defective Equipment/ Material | cable fault between G140B & TE229 | U/G Cable | Unknown \ Other | 20 | 160 | 53 | East | BCHF5
126283 | 2013-02-22 | Scheduled Outage | Construction | TRANSFERRING SEC SERVICES | None | O/H Service | 8 | 60 | 8 | Central | SB02
126285 | 2013-02-22 | Scheduled Outage | Maintenance | CHANGE POLE AND XFER PLANT | None | O/H Transformer (1ph) | 6 | 165 | 16 | West | BECKF2
126286 | 2013-02-23 | Scheduled Outage | Maintenance | 13kV customer owned switch SW120 isolated for maintenacne. | None | Live-Front | 1 | 138 | 2 | East | 5310
126288 | 2013-02-24 | Adverse Environment | Fire | replace burnt triplex | None | None | 11 | 18 | 3 | Central | UL14
126289 | 2013-02-25 | Defective Equipment | Defective Equipment/ Material | Transformer #K258 opened by crew to fix pedestal #258P1 | U/G Transformer | Padmount (1ph) | 9 | 55 | 8 | Central | AK07
126290 | 2013-02-25 | Scheduled Outage | Construction | Transformer X23940 at 1376 Labrie Ave. isolated for pole replacement. | None | Pole | 2 | 169 | 6 | East | 6F7
126291 | 2013-02-25 | Scheduled Outage | Construction | Transformer X27535 at 218 Cunningham Ave isolated to rearrange secondary. | None | O/H Service | 9 | 306 | 46 | East | TB06
126292 | 2013-02-25 | Defective Equipment | Defective Equipment/ Material | Transformer X35056 at 1160 Adirondack Dr. isolated to replace transformer. | O/H Transformer | O/H Transformer (1ph) | 11 | 190 | 35 | Central | UW04
126293 | 2013-02-26 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at S20516 caused Red phase to flash over. | O/H Switchgear | Vega Switch | 3 | 10 | 0 | Central | 5401
126293 | 2013-02-26 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at S20516 caused Red phase to flash over. | O/H Switchgear | Vega Switch | 258 | 45 | 194 | Central | 5401
126294 | 2013-02-26 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X30718 TO DISCONNECT SECONDARY SERVICE | None | None | 10 | 155 | 26 | Central | UN10
126295 | 2013-02-26 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X30718 TO RECONNECT SECONDARY SERVICE | None | None | 10 | 10 | 2 | Central | UN10
126296 | 2013-02-26 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X11415 TO REPLACE X-ARM | None | None | 4 | 220 | 15 | West | 43F2
126298 | 2013-02-27 | Scheduled Outage | Maintenance | VT852 13kV transformer bus isolated by Glen Carswell to allow crew to transfer load to new supply. | None | None | 15 | 85 | 21 | Central | 413
126299 | 2013-02-27 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at transformer X24181 | O/H Transformer | O/H Transformer (1ph) | 6 | 28 | 3 | East | 6F7
126303 | 2013-02-27 | Foreign Interference | Vehicle | Dump truck hit Hydro pole. | Pole | Pole | 77 | 335 | 430 | East | LTM01
126304 | 2013-02-27 | Unknown/Other | Unknown | No cause found at this time | O/H Switchgear | Fused Cutout | 77 | 107 | 137 | South | 190F5
126311 | 2013-02-27 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 0 | 1 | 0 | East | 77M2
126311 | 2013-02-27 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 90 | 272 | 408 | East | 77M2
126311 | 2013-02-27 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 411 | 32 | 219 | East | 77M2
126311 | 2013-02-27 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 2992 | 1 | 50 | East | 77M2
126313 | 2013-02-27 | Tree Contacts | Broken Branch | Trees in wires at Riddell and March Valley caused RX2007 to open. | O/H Conductor | O/H Conductor | 51 | 69 | 59 | West | 624F6
126313 | 2013-02-27 | Tree Contacts | Broken Branch | Trees in wires at Riddell and March Valley caused RX2007 to open. | O/H Conductor | O/H Conductor | 409 | 84 | 573 | West | 624F6
126314 | 2013-02-27 | Adverse Weather | Wet Snow | WIRES DOWN | O/H Conductor | Unknown \ Other | 14 | 499 | 116 | East | CYRF2
126315 | 2013-02-27 | Tree Contacts | Broken Branch | Trees in wires on Berry Side Rd. Caused fuse 239B to open. | O/H Conductor | O/H Conductor | 18 | 355 | 106 | West | 624F6
126316 | 2013-02-27 | Adverse Weather | Extreme Wind | G950 opened due to phase to phase contact. | O/H Conductor | O/H Conductor | 4 | 410 | 27 | East | 4801F8
126317 | 2013-02-27 | Adverse Weather | Wet Snow | 2 phases of S11925 on Shea Rd. North of Akins found open, no direct cause found. Adverse weather in the area. | O/H Conductor | O/H Conductor | 75 | 338 | 422 | West | 29F1
126318 | 2013-02-27 | Adverse Weather | Extreme Wind | Phase to Phase contact caused G120 at 790 Andre St. To open during adverse weather | O/H Conductor | O/H Conductor | 807 | 207 | 2784 | East | 77M1
126319 | 2013-02-27 | Adverse Weather | Extreme Wind | S12018B found open, no direct cause found. Adverse weather in area. | O/H Conductor | O/H Conductor | 12 | 448 | 90 | South | FAL03
126320 | 2013-02-28 | Adverse Weather | Wet Snow | Not yet known. | Unknown \ Other | Unknown \ Other | 50 | 10 | 8 | Central | 4301
126322 | 2013-02-27 | Loss Of Supply | Transmission Inadvertent | Loos of supply from Hydro One to LTC customers on Old Carp Rd. due to adverse weather. | None | None | 9 | 492 | 74 | West | CRPF3
126323 | 2013-02-28 | Tree Contacts | Broken Branch | Trees in wires on Rammysville Rd. caused G59R to open. | O/H Conductor | O/H Conductor | 13 | 111 | 24 | East | BLKF5
126324 | 2013-02-28 | Tree Contacts | Broken Branch | G59R to EOL isolated to allow crew to repair broken conductor. | O/H Conductor | O/H Conductor | 13 | 14 | 3 | East | BLKF5
126325 | 2013-02-28 | Tree Contacts | Broken Branch | S21976 to EOL at 892 Hare isolated by crews to remove tree in overhead. | O/H Conductor | O/H Conductor | 82 | 10 | 14 | Central | TW22
126326 | 2013-02-28 | Adverse Weather | Wet Snow | TO DISCONNECT TRIPLEX SERVICE | Secondary \ Service | O/H Service | 1 | 99 | 2 | Central | TK2AC
126327 | 2013-02-28 | Loss Of Supply | Transmission Inadvertent | Hydro One loss of supply | None | None | 1632 | 1 | 27 | East | 62M2 (Casselman MS)
126330 | 2013-02-28 | Adverse Weather | Wet Snow | G497 at 4837 Albion opened due to adverse weather (Heavy snow accumulation) | O/H Conductor | Unknown \ Other | 1 | 84 | 1 | East | 7F4
126331 | 2013-02-28 | Defective Equipment | Defective Equipment/ Material | The TH03 cirucit tripped under fault suspected cable fault | U/G Cable | PILC | 181 | 106 | 320 | Central | 4303
126332 | 2013-02-28 | Tree Contacts | Falling Tree | trees on wires | None | None | 2 | 99 | 3 | West | MWDF3
126333 | 2013-02-28 | Adverse Weather | Wet Snow | fallen secondary and neutral | Secondary \ Service | O/H Service | 11 | 97 | 18 | East | AA04
126334 | 2013-02-28 | Defective Equipment | Electrical Failure | Dead end insulator let go at the rear of 30 Stroughten, and crossarm in the rear of 26 Stroughten needs to be replaced due to pole fire. | O/H Conductor | Unknown \ Other | 36 | 460 | 276 | West | 43F2
126335 | 2013-02-28 | Tree Contacts | Tree Growth/ Untrimmed Tree | To remove tree off circuit, Transformer X26054 opened. | None | None | 8 | 31 | 4 | East | UT03
126336 | 2013-02-28 | Adverse Weather | Wet Snow | Transformer #X31079 opened up by crew to remove triplex | O/H Transformer | O/H Transformer (1ph) | 13 | 30 | 6 | Central | UN07
126337 | 2013-02-28 | Adverse Weather | Wet Snow | Transformer #X29651 opened by crew due to secondary wire on the ground | O/H Transformer | O/H Transformer (1ph) | 2 | 98 | 3 | East | SO12
126338 | 2013-02-28 | Defective Equipment | Electrical Failure | R&W phases at S206-4 opened due to defective transformer 1109 at 13 Weaver. Outage expanded to the B phase to take the damaged transformer off potential as a precaution. | U/G Cable Attachement | Elbow \ Insert | 0 | 12 | 0 | West | MWDF1
126338 | 2013-02-28 | Defective Equipment | Electrical Failure | R&W phases at S206-4 opened due to defective transformer 1109 at 13 Weaver. Outage expanded to the B phase to take the damaged transformer off potential as a precaution. | U/G Cable Attachement | Elbow \ Insert | 1 | 324 | 5 | West | MWDF1
126338 | 2013-02-28 | Defective Equipment | Electrical Failure | R&W phases at S206-4 opened due to defective transformer 1109 at 13 Weaver. Outage expanded to the B phase to take the damaged transformer off potential as a precaution. | U/G Cable Attachement | Elbow \ Insert | 174 | 8 | 23 | West | MWDF1
126338 | 2013-02-28 | Defective Equipment | Electrical Failure | R&W phases at S206-4 opened due to defective transformer 1109 at 13 Weaver. Outage expanded to the B phase to take the damaged transformer off potential as a precaution. | U/G Cable Attachement | Elbow \ Insert | 309 | 11 | 57 | West | MWDF1
126338 | 2013-02-28 | Defective Equipment | Electrical Failure | R&W phases at S206-4 opened due to defective transformer 1109 at 13 Weaver. Outage expanded to the B phase to take the damaged transformer off potential as a precaution. | U/G Cable Attachement | Elbow \ Insert | 309 | 103 | 530 | West | MWDF1
126338 | 2013-02-28 | Defective Equipment | Electrical Failure | R&W phases at S206-4 opened due to defective transformer 1109 at 13 Weaver. Outage expanded to the B phase to take the damaged transformer off potential as a precaution. | U/G Cable Attachement | Elbow \ Insert | 417 | 17 | 118 | West | MWDF1
126339 | 2013-02-28 | Defective Equipment | Electrical Failure | Blown arrester to replace | Pole Attachement | Arrester | 2 | 107 | 4 | West | MWDF3
126340 | 2013-02-28 | Defective Equipment | Defective Equipment/ Material | ISOLATED TRANSFORMER X27664 TO REPAIR SECONDARY SERVICE | O/H Conductor | O/H Conductor | 6 | 45 | 4 | East | UQ08
126341 | 2013-02-28 | Defective Equipment | Defective Equipment/ Material | ISOLATED TRANSFORMER X27248 TO INSTALL TWO NEW TRIPLEX SERVICES | O/H Conductor | O/H Conductor | 3 | 100 | 5 | East | UZ12
126342 | 2013-02-28 | Defective Equipment | Mechanical Failure | ISOLATED TRANSFORMER X5302 TO REPAIRE TRIPLEX SERVICE | O/H Conductor | O/H Conductor | 4 | 145 | 10 | South | 130F2
126343 | 2013-03-01 | Scheduled Outage | Vegetation Management | Transformer X39653 isolated to resag secondary buss | None | O/H Conductor | 7 | 49 | 6 | South | 49F6
126345 | 2013-03-02 | Foreign Interference | Other Utilities | Water main flooded transformer 5725R. | U/G Transformer | Padmount (1ph) | 2 | 390 | 13 | West | 24F5
126346 | 2013-03-02 | Defective Equipment | Electrical Failure | faulted cable | U/G Cable | PILC | 14 | 92 | 21 | East | SO06
126347 | 2013-03-03 | Foreign Interference | Vehicle | Dump truck caught bell lines and broke 3 poles. WO# 144984. 200F1 circuit was opened for a few to allow crews to safely pick up load from the S1140 to minimize outage to 27 customers. | Pole | Pole | 27 | 570 | 256 | South | 200F6
126347 | 2013-03-03 | Foreign Interference | Vehicle | Dump truck caught bell lines and broke 3 poles. WO# 144984. 200F1 circuit was opened for a few to allow crews to safely pick up load from the S1140 to minimize outage to 27 customers. | Pole | Pole | 271 | 5 | 23 | South | 200F6
126347 | 2013-03-03 | Foreign Interference | Vehicle | Dump truck caught bell lines and broke 3 poles. WO# 144984. 200F1 circuit was opened for a few to allow crews to safely pick up load from the S1140 to minimize outage to 27 customers. | Pole | Pole | 288 | 300 | 1440 | South | 200F6
126347 | 2013-03-03 | Foreign Interference | Vehicle | Dump truck caught bell lines and broke 3 poles. WO# 144984. 200F1 circuit was opened for a few to allow crews to safely pick up load from the S1140 to minimize outage to 27 customers. | Pole | Pole | 468 | 77 | 601 | South | 200F6
126347 | 2013-03-03 | Foreign Interference | Vehicle | Dump truck caught bell lines and broke 3 poles. WO# 144984. 200F1 circuit was opened for a few to allow crews to safely pick up load from the S1140 to minimize outage to 27 customers. | Pole | Pole | 507 | 111 | 938 | South | 200F6
126347 | 2013-03-03 | Foreign Interference | Vehicle | Dump truck caught bell lines and broke 3 poles. WO# 144984. 200F1 circuit was opened for a few to allow crews to safely pick up load from the S1140 to minimize outage to 27 customers. | Pole | Pole | 906 | 13 | 196 | South | 200F6
126349 | 2013-03-04 | Scheduled Outage | Construction | P272 isolated to allow crew to move to different circuit. | None | None | 1 | 341 | 6 | Central | UW04
126351 | 2013-03-04 | Adverse Weather | Ice/Icing | Transformer #X31044 opened by crew to repair open wire that burnt down | O/H Transformer | O/H Transformer (1ph) | 16 | 35 | 9 | Central | UF08
126357 | 2013-03-05 | Foreign Interference | Vehicle | REPLACED DAMAGED TRANSFORMER 3589 | U/G Transformer | Padmount (1ph) | 10 | 332 | 55 | West | BRDF7
126358 | 2013-03-05 | Scheduled Outage | Construction | Construction, New riser & switch , S19157 installed to supply P272 from UW05. Performed by Tin Connell of K-Line | None | Fused Cutout | 1 | 444 | 7 | Central | UW04
126359 | 2013-03-05 | Scheduled Outage | Construction | Transformer #X23939 opened by crew to relocate transformer | None | None | 17 | 222 | 63 | East | 6F7
126361 | 2013-03-06 | Scheduled Outage | Maintenance | at 10:00am, TE2064 & G867 were isolated to allow crews to repair defect elbows & switch. 12 customers affected for 327 minutes. Lietrim (249F1) ID #126361 | None | Padmount (1ph) | 12 | 327 | 65 | East | LTM01
126362 | 2013-03-06 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30719 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 27 | 195 | 88 | Central | UN10
126364 | 2013-03-06 | Defective Equipment | Electrical Failure | Transformer X31616 was isolated due to it being found sparking with the lid blown off of it. | O/H Transformer | O/H Transformer (1ph) | 4 | 220 | 15 | Central | AK10
126366 | 2013-03-07 | Foreign Interference | Foreign Objects | Fault on O/H circuits due to balloons caught in O/H | O/H Conductor | O/H Conductor | 221 | 12 | 44 | Central | UL02
126366 | 2013-03-07 | Foreign Interference | Foreign Objects | Fault on O/H circuits due to balloons caught in O/H | O/H Conductor | O/H Conductor | 255 | 12 | 51 | Central | UL03
126366 | 2013-03-07 | Foreign Interference | Foreign Objects | Fault on O/H circuits due to balloons caught in O/H | O/H Conductor | O/H Conductor | 323 | 26 | 140 | Central | UC01
126366 | 2013-03-07 | Foreign Interference | Foreign Objects | Fault on O/H circuits due to balloons caught in O/H | O/H Conductor | O/H Conductor | 339 | 47 | 266 | Central | UL05
126366 | 2013-03-07 | Foreign Interference | Foreign Objects | Fault on O/H circuits due to balloons caught in O/H | O/H Conductor | O/H Conductor | 373 | 213 | 1324 | Central | UL06
126366 | 2013-03-07 | Foreign Interference | Foreign Objects | Fault on O/H circuits due to balloons caught in O/H | O/H Conductor | O/H Conductor | 412 | 26 | 179 | Central | UC02
126366 | 2013-03-07 | Foreign Interference | Foreign Objects | Fault on O/H circuits due to balloons caught in O/H | O/H Conductor | O/H Conductor | 425 | 12 | 85 | Central | UL04
126366 | 2013-03-07 | Foreign Interference | Foreign Objects | Fault on O/H circuits due to balloons caught in O/H | O/H Conductor | O/H Conductor | 436 | 26 | 189 | Central | UC03
126367 | 2013-03-07 | Scheduled Outage | Construction | INSTALLING NEW POLES | None | Pole | 34 | 195 | 110 | Central | UN10
126368 | 2013-03-07 | Defective Equipment | Defective Equipment/ Material | REPLACE XFMR | O/H Transformer | O/H Transformer (1ph) | 3 | 120 | 6 | West | 624F6
126371 | 2013-03-07 | Defective Equipment | Mechanical Failure | Transformer X29012 was isolated to allow crew to replace defective transformer. | O/H Transformer | O/H Transformer (3ph) | 1 | 471 | 8 | East | 2206
126373 | 2013-03-08 | Scheduled Outage | Maintenance | REPAIR A BROKEN CUTOUT SWITCH | None | Fused Cutout | 12 | 20 | 4 | Central | SB02
126374 | 2013-03-08 | Foreign Interference | Vehicle | Replace defective transformer. | U/G Transformer | Kiosk (3ph) | 1 | 301 | 5 | West | BECKF2
126375 | 2013-03-09 | Adverse Environment | Fire | Fire . Fire. Over head primary line affecting two transformers on Barrette were isolated from X25201 due to fire at 144 Barrette St. | O/H Transformer | O/H Transformer (1ph) | 29 | 572 | 276 | East | AC05
126375 | 2013-03-09 | Adverse Environment | Fire | Fire . Fire. Over head primary line affecting two transformers on Barrette were isolated from X25201 due to fire at 144 Barrette St. | O/H Transformer | O/H Transformer (1ph) | 58 | 239 | 231 | East | AC05
126379 | 2013-03-09 | Defective Equipment | Defective Equipment/ Material | at 17:46, TO51 breaker tripped (1808) due to cable fault between VT718 & VT564 on coventry rd. 14 customers affected for 327 minutes. Overbrook (TO51) ID #126379 | U/G Cable | PILC | 10 | 19 | 3 | East | 1808
126379 | 2013-03-09 | Defective Equipment | Defective Equipment/ Material | at 17:46, TO51 breaker tripped (1808) due to cable fault between VT718 & VT564 on coventry rd. 14 customers affected for 327 minutes. Overbrook (TO51) ID #126379 | U/G Cable | PILC | 11 | 42 | 8 | East | 1808
126379 | 2013-03-09 | Defective Equipment | Defective Equipment/ Material | at 17:46, TO51 breaker tripped (1808) due to cable fault between VT718 & VT564 on coventry rd. 14 customers affected for 327 minutes. Overbrook (TO51) ID #126379 | U/G Cable | PILC | 13 | 24 | 5 | East | 1808
126379 | 2013-03-09 | Defective Equipment | Defective Equipment/ Material | at 17:46, TO51 breaker tripped (1808) due to cable fault between VT718 & VT564 on coventry rd. 14 customers affected for 327 minutes. Overbrook (TO51) ID #126379 | U/G Cable | PILC | 14 | 152 | 35 | East | 1808
126380 | 2013-03-10 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One | None | None | 98 | 25 | 41 | South | 72F6
126380 | 2013-03-10 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One | None | None | 204 | 25 | 85 | South | 72F7
126381 | 2013-03-11 | Scheduled Outage | Construction | TP3547 secondary bus was isolated at 1755 Merviale was isolated to allow contractor to install micro fit. | None | None | 1 | 200 | 3 | South | 130F1
126382 | 2013-03-11 | Scheduled Outage | Construction | 49F6 R phase cable loop on Bedale between S138 & S139 was isolated to allow crew to excavate around cable for pole replacment | None | None | 45 | 93 | 70 | South | 49F6
126383 | 2013-03-11 | Scheduled Outage | Construction | Transformer X32770 at 1131 Parkway isolated for transfer of plant to new pole | None | None | 10 | 5 | 1 | Central | UW14
126384 | 2013-03-11 | Scheduled Outage | Construction | Transformer #X32774 opened by crew to transfer plant. Tim Connell from Kline | None | None | 15 | 15 | 4 | Central | UW14
126385 | 2013-03-11 | Scheduled Outage | Construction | Transformer X21549 at the rear of 1169 Parkway Dr. isolated to allow for transfer of plant to new pole | None | None | 3 | 5 | 0 | Central | UW14
126386 | 2013-03-11 | Scheduled Outage | Construction | Transformer #X32771 opened by Dan Crough from Kline to transfer plant | None | None | 3 | 15 | 1 | Central | UW14
126387 | 2013-03-11 | Adverse Environment | Fire | ISOLATED TRANSFORMER X37051 FOR FIRE DEPT DUE TO HOUSE FIRE | None | None | 2 | 120 | 4 | South | 72F7
126389 | 2013-03-12 | Adverse Environment | Fire | Fire | None | None | 4 | 16 | 1 | East | LTM01
126391 | 2013-03-12 | Scheduled Outage | Maintenance | TP5447 isolated to allow crews to change blown lightning arrestor at S11069. | None | Arrester | 1 | 21 | 0 | South | 72F7
126395 | 2013-03-12 | Defective Equipment | Electrical Failure | Transformer X30967 at 30 Russell Ave. isolated to repair broken cutout | O/H Switchgear | Fused Cutout | 19 | 93 | 29 | Central | UN05
126397 | 2013-03-12 | Defective Equipment | Electrical Failure | Pole fire caused pole top to break off and Trip TD01 circuit under hold off protection. | Pole | Insulation Failure (Pole Fire) | 14 | 431 | 101 | Central | TD01
126397 | 2013-03-12 | Defective Equipment | Electrical Failure | Pole fire caused pole top to break off and Trip TD01 circuit under hold off protection. | Pole | Insulation Failure (Pole Fire) | 27 | 1 | 0 | Central | TD01
126397 | 2013-03-12 | Defective Equipment | Electrical Failure | Pole fire caused pole top to break off and Trip TD01 circuit under hold off protection. | Pole | Insulation Failure (Pole Fire) | 39 | 22 | 14 | Central | TD01
126397 | 2013-03-12 | Defective Equipment | Electrical Failure | Pole fire caused pole top to break off and Trip TD01 circuit under hold off protection. | Pole | Insulation Failure (Pole Fire) | 1156 | 57 | 1098 | Central | TD01
126398 | 2013-03-13 | Scheduled Outage | Maintenance | 4kV transformers K914 and K915 isolated to allow crews to change a defective termination and dip switches. | None | Primary Pedestal | 36 | 164 | 98 | Central | AM06
126402 | 2013-03-13 | Defective Equipment | Electrical Failure | 58T2 high side switch and low side breaker opened. Relays at station indicate differential. | Station Equipment | Transformer | 157 | 9 | 24 | South | EPWF2
126402 | 2013-03-13 | Defective Equipment | Electrical Failure | 58T2 high side switch and low side breaker opened. Relays at station indicate differential. | Station Equipment | Transformer | 200 | 10 | 33 | South | EPWF3
126402 | 2013-03-13 | Defective Equipment | Electrical Failure | 58T2 high side switch and low side breaker opened. Relays at station indicate differential. | Station Equipment | Transformer | 634 | 9 | 95 | South | EPWF1
126403 | 2013-03-13 | Scheduled Outage | Construction | Transformer X34846 at 170 Russell Ave. isolated to allow for transfer of plant | None | O/H Transformer (1ph) | 26 | 87 | 38 | Central | UN10
126404 | 2013-03-13 | Defective Equipment | Defective Equipment/ Material | Transformer K00296 at 313 Kintyre Pvt. isolated to make elbow repairs in transformer | U/G Cable Attachement | Elbow \ Insert | 23 | 74 | 28 | Central | AK04
126405 | 2013-03-13 | Defective Equipment | Mechanical Failure | On isolating cable section for NRC testing a pin in TP5294 broke. | U/G Transformer | Padmount (3ph) | 61 | 107 | 109 | South | 47F6
126412 | 2013-03-14 | Scheduled Outage | Construction | Transformer 65A3B-0716 isolated to allow for transfer of plant | None | O/H Transformer (1ph) | 2 | 109 | 4 | East | UG07
126413 | 2013-03-14 | Scheduled Outage | Maintenance | Transformer X30891 at 26 Hawthorne Ave. isolated to replace transformer due to cracked bushing | None | O/H Transformer (1ph) | 26 | 143 | 62 | Central | SR01
126417 | 2013-03-15 | Scheduled Outage | Maintenance | INSTALLING NEW POLES | None | None | 7 | 135 | 16 | Central | UN05
126421 | 2013-03-16 | Scheduled Outage | Maintenance | P516 isolated to allow crews to replace defective elbows and change dip switches. | None | Padmount (1ph) | 1 | 88 | 1 | Central | UL03
126422 | 2013-03-16 | Scheduled Outage | Maintenance | 4kV transformer P530 at 778 Bank St. was isolated for elbow and switch replacement | None | Padmount (1ph) | 2 | 83 | 3 | Central | SB16
126425 | 2013-03-18 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30972 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 27 | 180 | 81 | Central | UN05
126426 | 2013-03-18 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X44361 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 2 | 85 | 3 | East | UG07
126427 | 2013-03-18 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35094 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 225 | 38 | Central | UW04
126428 | 2013-03-19 | Scheduled Outage | Construction | TP8907 and VT3 at 201 Bell were isolated to allow crew to decommission VT3 and to connect new secondary at TP8907. | None | None | 2 | 446 | 15 | Central | TL3SB
126429 | 2013-03-19 | Scheduled Outage | Maintenance | PT190 at 21 Hurdman was isolated to allow crew to replace defective connections in padmount and perform maintenance on switches. | None | None | 1 | 78 | 1 | Central | TR1UN
126430 | 2013-03-19 | Scheduled Outage | Construction | Transformer #X32766 opened by crew for upgrades and transferring plant. Crew is Tim Connell from Kline | None | None | 7 | 150 | 18 | Central | UW04
126431 | 2013-03-19 | Scheduled Outage | Construction | Transformer #K00227 opened by crew for primary connection repairs | None | None | 31 | 23 | 12 | Central | UV07
126432 | 2013-03-19 | Scheduled Outage | Maintenance | PT194 at 1481 Michael was isolated to allow crew to install K-Mate fuses. | None | None | 3 | 35 | 2 | East | TB07
126433 | 2013-03-19 | Defective Equipment | Defective Equipment/ Material | Transformer X34734 at 1682 Fisher Ave. isolated to replace defective mole set in secondary pedestal. | Secondary \ Service | Mole | 6 | 44 | 4 | Central | AK03
126435 | 2013-03-20 | Scheduled Outage | Construction | Transformer #X29594 opened by crew to transfer plant to new pole | None | None | 22 | 210 | 77 | East | UG07
126437 | 2013-03-20 | Scheduled Outage | Construction | Transformer X35060 located at 1212 Adirondack Dr. isolated to remove transformer. | None | None | 2 | 210 | 7 | Central | UW04
126439 | 2013-03-21 | Scheduled Outage | Maintenance | P191 isolated to allow crews to replace defective insulators and switches | None | Kiosk (3ph) | 4 | 44 | 3 | Central | SR07
126440 | 2013-03-21 | Scheduled Outage | Maintenance | K922 isolated to repair primary termination. | None | Kiosk (3ph) | 17 | 158 | 45 | Central | UD05
126442 | 2013-03-21 | Scheduled Outage | Construction | Transfer plant to new pole | None | O/H Transformer (1ph) | 6 | 50 | 5 | Central | UW04
126443 | 2013-03-21 | Scheduled Outage | Construction | Transformer X46615 isolated in order to transfer plant to new pole | None | O/H Transformer (1ph) | 7 | 45 | 5 | Central | UW04
126444 | 2013-03-21 | Scheduled Outage | Construction | Transformer X27206 was isolated in order to transfer plant to new pole | None | O/H Transformer (1ph) | 6 | 230 | 23 | East | UQ07
126445 | 2013-03-21 | Scheduled Outage | Construction | Transformer #X30834 opened by crew for a pole replacement | None | None | 9 | 120 | 18 | Central | UN10
126446 | 2013-03-22 | Scheduled Outage | Construction | VT77 isolated to allow crews to replace primary cables, switches and duct structure. | None | Unknown \ Other | 1 | 1461 | 24 | East | 1806
126447 | 2013-03-22 | Defective Equipment | Defective Equipment/ Material | Transformer #X23196 opened up, defective transformer had to be replaced by On Call crew. | O/H Transformer | O/H Transformer (1ph) | 20 | 429 | 143 | East | AC07
126451 | 2013-03-23 | Scheduled Outage | Maintenance | customer maintenance | None | None | 1 | 210 | 4 | Central | TL3SB
126454 | 2013-03-24 | Scheduled Outage | Construction | Transformer 65A3B-0716 (X44361) at 58 Vaughan St. isolated for transfer of plant. | None | None | 2 | 20 | 1 | East | UG07
126455 | 2013-03-25 | Defective Equipment | Electrical Failure | TK09 CB tripped due to defective vault equippment at VT339 | U/G Cable | PILC | 9 | 169 | 25 | Central | 409
126455 | 2013-03-25 | Defective Equipment | Electrical Failure | TK09 CB tripped due to defective vault equippment at VT339 | U/G Cable | PILC | 136 | 5 | 11 | Central | 409
126455 | 2013-03-25 | Defective Equipment | Electrical Failure | TK09 CB tripped due to defective vault equippment at VT339 | U/G Cable | PILC | 396 | 27 | 178 | Central | 409
126455 | 2013-03-25 | Defective Equipment | Electrical Failure | TK09 CB tripped due to defective vault equippment at VT339 | U/G Cable | PILC | 403 | 106 | 712 | Central | 409
126456 | 2013-03-25 | Scheduled Outage | Construction | Transformer #X46615 and X35060 opened by crew to remove transformers and upgrade. Done by Tim Connell from Kline | None | None | 12 | 165 | 33 | Central | UW04
126457 | 2013-03-26 | Scheduled Outage | Maintenance | Transformer K670 at 1180 Shillington was isolated to allow crew to make repairs to secondary | None | Unknown \ Other | 1 | 68 | 1 | Central | AD06
126459 | 2013-03-26 | Scheduled Outage | Construction | Transformer #X31570 opened by crew for a new service. | None | None | 8 | 70 | 9 | Central | UJ07
126460 | 2013-03-26 | Scheduled Outage | Maintenance | 58F2 O/H section from S173 to Eol was isolated on Capilano Dr to allow crew to make repiars to burnt neutral | None | O/H Conductor | 18 | 106 | 32 | South | EPWF2
126461 | 2013-03-26 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER TP3082 TO REPAIR SECONDARY UNDERGROUND SERVICE | None | None | 13 | 20 | 4 | East | BCHF5
126462 | 2013-03-26 | Scheduled Outage | Construction | Transformer #X35196 opened by crew for a new service. | None | None | 6 | 70 | 7 | Central | AH02
126463 | 2013-03-26 | Defective Equipment | Electrical Failure | two R1-F fuses have blown at VT384 due to defective transformers in vault | Vault Equipment | Transformer | 1 | 473 | 8 | Central | 5202
126464 | 2013-03-26 | Scheduled Outage | Construction | Transformer X32770 at 1131 Parkway Dr. Was isolated to allow crew to upgrade transformer. | None | None | 5 | 230 | 19 | Central | UW14
126465 | 2013-03-26 | Scheduled Outage | Construction | Transformer X32771 at 1115 Parkway was isolated to allow crew to upgrade transformer. | None | None | 3 | 230 | 12 | Central | UW14
126467 | 2013-03-27 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X07148 AND REPLACE SWITCH | None | None | 2 | 85 | 3 | West | MWDF3
126468 | 2013-03-27 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X09873 FOR SERVICE UPGRADE | None | None | 2 | 60 | 2 | South | FAL03
126469 | 2013-03-27 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X21549 TO TTRANSFER HYDRO PLANT TO NEW POLE | None | None | 3 | 230 | 12 | Central | UW14
126470 | 2013-03-27 | Scheduled Outage | Maintenance | To replace leaking xfmrs | None | Transformer | 1 | 139 | 2 | Central | 5202
126471 | 2013-03-28 | Scheduled Outage | Maintenance | To reconfigure cables. | None | None | 1 | 161 | 3 | South | LGFF1
126472 | 2013-03-28 | Scheduled Outage | Construction | Transformer #X34026 opened by crew to change a pole. Done by Doug Featherstone. | None | None | 14 | 260 | 61 | Central | TD01
126473 | 2013-03-28 | Scheduled Outage | Construction | Transformer #X24941 opened by crew for a change over. | None | None | 1 | 130 | 2 | East | UG04
126477 | 2013-03-29 | Foreign Interference | Vehicle | Vehicle accident. | O/H Conductor | O/H Conductor | 1 | 145 | 2 | South | 47F2
126477 | 2013-03-29 | Foreign Interference | Vehicle | Vehicle accident. | O/H Conductor | O/H Conductor | 59 | 62 | 61 | South | 47F2
126478 | 2013-03-29 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE AT SWITCH S16854 FEEDING TRANSFORMER X32972 | O/H Switchgear | Fused Cutout | 1 | 77 | 1 | West | BECKF2
126479 | 2013-03-30 | Defective Equipment | Electrical Failure | Defective termination at walkley and lancaster. | U/G Cable Attachement | Termination \ Stress Cone | 1 | 128 | 2 | East | 5310
126479 | 2013-03-30 | Defective Equipment | Electrical Failure | Defective termination at walkley and lancaster. | U/G Cable Attachement | Termination \ Stress Cone | 14 | 8 | 2 | East | 5310
126479 | 2013-03-30 | Defective Equipment | Electrical Failure | Defective termination at walkley and lancaster. | U/G Cable Attachement | Termination \ Stress Cone | 71 | 18 | 21 | East | 5310
126479 | 2013-03-30 | Defective Equipment | Electrical Failure | Defective termination at walkley and lancaster. | U/G Cable Attachement | Termination \ Stress Cone | 123 | 8 | 16 | East | 5310
126479 | 2013-03-30 | Defective Equipment | Electrical Failure | Defective termination at walkley and lancaster. | U/G Cable Attachement | Termination \ Stress Cone | 235 | 42 | 164 | East | 5310
126480 | 2013-03-31 | Foreign Interference | Wildlife (Bird/Animal) | Not yet known. Circuit to be patrolled in daylight. Crew patrolled the O/H and found a Dead Racoon outside the Station Yard. | None | None | 1559 | 11 | 286 | West | MWDF4
126481 | 2013-04-02 | Defective Equipment | Mechanical Failure | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X23242 | O/H Switchgear | Fused Cutout | 21 | 174 | 61 | East | AA02
126483 | 2013-04-02 | Scheduled Outage | Construction | To allow K-Line to install a new pole | None | Pole | 1 | 439 | 7 | Central | UW14
126484 | 2013-04-02 | Defective Equipment | Defective Equipment/ Material | Downed open wire secondary buss | Secondary \ Service | O/H Service | 7 | 29 | 3 | East | UB07
126485 | 2013-04-02 | Scheduled Outage | Construction | Leaking Transformer | None | None | 11 | 118 | 22 | East | UA02
126486 | 2013-04-03 | Scheduled Outage | Construction | TE3294 isolated to transfer the supply from existing Fal02 to new O/H section | None | Padmount (3ph) | 18 | 102 | 31 | South | FAL02
126488 | 2013-04-03 | Scheduled Outage | Vegetation Management | Working Clearance for Forestry crews | None | None | 9 | 93 | 14 | East | AE02
126489 | 2013-04-03 | Scheduled Outage | Vegetation Management | Working Clearance for Forestry Crews | None | None | 9 | 117 | 18 | East | AE02
126490 | 2013-04-03 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32774 TO TRANSFER HYDRO PLANT | None | None | 14 | 225 | 52 | Central | UW14
126491 | 2013-04-03 | Scheduled Outage | Construction | Transformer X40189 at 34 Bedale Dr. isolated to install new hardware on new pole. | None | Unknown \ Other | 17 | 46 | 13 | South | 49F6
126492 | 2013-04-03 | Scheduled Outage | Vegetation Management | Working clearance for forestry crews | None | None | 10 | 93 | 16 | East | TB06
126493 | 2013-04-03 | Scheduled Outage | Construction | Transformer #X32772 opened by crew to transfer Hydro plant. Tim Connell from Kline | None | None | 18 | 240 | 72 | Central | UW14
126494 | 2013-04-04 | Scheduled Outage | Construction | move switch to new line. | None | None | 1 | 130 | 2 | South | FAL01
126495 | 2013-04-05 | Tree Contacts | Broken Branch | Tree on fell on wires causing G50 to open. | O/H Conductor | O/H Conductor | 11 | 116 | 21 | East | BLKF5
126496 | 2013-04-05 | Scheduled Outage | Construction | ISOLATED TRANSFORMERS X30716 AND X30715 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 14 | 110 | 26 | Central | UN10
126497 | 2013-04-05 | Defective Equipment | Mechanical Failure | ISOLATED TRANSFORMER X16351 AND REPLACED LIVE LINE CLAMP | O/H Transformer | O/H Transformer (1ph) | 11 | 15 | 3 | East | 56F1
126498 | 2013-04-05 | Defective Equipment | Defective Equipment/ Material | Replace secondary service wires | Secondary \ Service | O/H Service | 16 | 52 | 14 | Central | 505
126499 | 2013-04-05 | Scheduled Outage | Maintenance | VT77 at 440 Coventry was isolated to allow crew to install new cable between VT77 and riser pole and terminates cable on riser pole | None | None | 1 | 1201 | 20 | East | 1806
126501 | 2013-04-06 | Loss Of Supply | Transmission Inadvertent | Not yet known. | None | None | 4 | 165 | 11 | West | ALEXF1
126503 | 2013-04-07 | Foreign Interference | Vehicle | To inspect for damage and reset transformer on it's pad after hit and run motor vehicle accident | U/G Transformer | Padmount (1ph) | 14 | 57 | 13 | West | BRDF3
126504 | 2013-04-08 | Defective Equipment | Electrical Failure | B1 bus at Lincoln Heights tripped under differential due to the TD11 pothead in the metalclad faulting. | Station Equipment | Primary Cable Termination | 733 | 77 | 941 | Central | TD07
126504 | 2013-04-08 | Defective Equipment | Electrical Failure | B1 bus at Lincoln Heights tripped under differential due to the TD11 pothead in the metalclad faulting. | Station Equipment | Primary Cable Termination | 1355 | 77 | 1739 | Central | TD01
126504 | 2013-04-08 | Defective Equipment | Electrical Failure | B1 bus at Lincoln Heights tripped under differential due to the TD11 pothead in the metalclad faulting. | Station Equipment | Primary Cable Termination | 1528 | 71 | 1808 | Central | TD05
126505 | 2013-04-09 | Tree Contacts | Falling Tree | The Tree on the O/H at Albion and Lester caused the 4801F8 CB to A/R and the RX2021 down stream to trip open | O/H Conductor | O/H Conductor | 1609 | 28 | 751 | East | 4801F8
126505 | 2013-04-09 | Tree Contacts | Falling Tree | The Tree on the O/H at Albion and Lester caused the 4801F8 CB to A/R and the RX2021 down stream to trip open | O/H Conductor | O/H Conductor | 1609 | 40 | 1073 | East | 4801F8
126506 | 2013-04-09 | Scheduled Outage | Maintenance | Hydro crew isolated to install new primary fusing | None | None | 28 | 161 | 75 | Central | SK12
126507 | 2013-04-09 | Scheduled Outage | Maintenance | customer vault maintenance | None | None | 1 | 107 | 2 | Central | TM1UJ
126508 | 2013-04-09 | Defective Equipment | Electrical Failure | Suspected cable fault | U/G Cable | Unknown \ Other | 9 | 63 | 9 | East | SO13
126512 | 2013-04-12 | Foreign Interference | Vehicle | Vehicle struck pole. | Pole | Pole | 3 | 321 | 16 | South | 140F5
126512 | 2013-04-12 | Foreign Interference | Vehicle | Vehicle struck pole. | Pole | Pole | 91 | 40 | 61 | South | 180F1
126512 | 2013-04-12 | Foreign Interference | Vehicle | Vehicle struck pole. | Pole | Pole | 130 | 40 | 87 | South | 180F2
126512 | 2013-04-12 | Foreign Interference | Vehicle | Vehicle struck pole. | Pole | Pole | 313 | 40 | 209 | South | 180F3
126512 | 2013-04-12 | Foreign Interference | Vehicle | Vehicle struck pole. | Pole | Pole | 348 | 40 | 232 | South | 180F6
126512 | 2013-04-12 | Foreign Interference | Vehicle | Vehicle struck pole. | Pole | Pole | 421 | 46 | 323 | South | 170F3
126512 | 2013-04-12 | Foreign Interference | Vehicle | Vehicle struck pole. | Pole | Pole | 460 | 47 | 360 | South | 140F5
126512 | 2013-04-12 | Foreign Interference | Vehicle | Vehicle struck pole. | Pole | Pole | 854 | 40 | 569 | South | 180F4
126512 | 2013-04-12 | Foreign Interference | Vehicle | Vehicle struck pole. | Pole | Pole | 1737 | 40 | 1158 | South | 22M24
126512 | 2013-04-12 | Foreign Interference | Vehicle | Vehicle struck pole. | Pole | Pole | 3546 | 61 | 3605 | South | LGFF1
126513 | 2013-04-13 | Scheduled Outage | Maintenance | VT13 at 1053 Carling was isolated to allow contractor to repair broken load break switch and perform customer vault maintenance | None | Unknown \ Other | 1 | 416 | 7 | Central | TH3SH
126514 | 2013-04-13 | Scheduled Outage | Maintenance | VT32 at 100 Sussex was isolated to allow contractor to install new duct work and perfrom customer vault maintenance | None | None | 5 | 374 | 31 | Central | 403
126517 | 2013-04-14 | Scheduled Outage | Construction | Upgrading 3 phase overhead bank | None | None | 8 | 311 | 41 | Central | AM04
126518 | 2013-04-14 | Scheduled Outage | Construction | UN05 O/H section from Temp 179 RWB at Osgoode and Russell was opened to allow crew to install new spun bus North of Temp 179. | None | None | 71 | 436 | 516 | Central | UN05
126519 | 2013-04-14 | Scheduled Outage | Maintenance | 13 Kv Vault VT281 at 361 Queen was isolated to allow contractor to perform customer vault maintenance | None | None | 4 | 249 | 17 | Central | 5202
126521 | 2013-04-15 | Defective Equipment | Mechanical Failure | REPLACED BROKEN PRIMARY CONNECTION AT THE SWITCH FEEDING TRANSFORMER X32090 | O/H Switchgear | Fused Cutout | 10 | 126 | 21 | Central | UL04
126522 | 2013-04-15 | Scheduled Outage | Construction | Transformer P449 at 1544 Chatelaine was isolated to allow crew to replace primary connection in transformer and replace switches on dip pole. | None | None | 1 | 89 | 1 | Central | AD02
126523 | 2013-04-15 | Defective Equipment | Electrical Failure | pole fire at X14997 | Pole | Insulation Failure (Pole Fire) | 1 | 112 | 2 | East | 48M2
126525 | 2013-04-16 | Defective Equipment | Defective Equipment/ Material | Transformer #26835 opened by crew to make emergency, temporary repairs to a leaning pole. | Pole | Pole | 4 | 41 | 3 | East | AE04
126526 | 2013-04-16 | Defective Equipment | Defective Equipment/ Material | burnt pole on customer owned primary | Customer Owned | Customer-Owned | 75 | 43 | 54 | East | 4801F8
126528 | 2013-04-17 | Scheduled Outage | Maintenance | 4kV transformers K423 and K422 were isolated to allow crws to change insulators and pole pothead switches. | None | Kiosk (1ph) | 29 | 315 | 152 | East | AN05
126529 | 2013-04-17 | Scheduled Outage | Maintenance | 13kV vault Vt102 at 1525 Alta Vista was isolated to allow crews to replace transformers containing PCBs | None | Transformer | 1 | 282 | 5 | East | 1802
126530 | 2013-04-17 | Unknown/Other | Unknown | Nothing found after patrol | None | None | 49 | 73 | 60 | East | 249F2
126531 | 2013-04-17 | Scheduled Outage | Maintenance | 4kVsidewal TV183 at 20 Patro was isolated to allow crews to install new primary fusing. | None | SIDT - Submersible (Turtle) | 15 | 99 | 25 | Central | UD05
126532 | 2013-04-17 | Scheduled Outage | Construction | to allow contractor to install new overhead transformer on customer owned line. | None | None | 1 | 85 | 1 | South | 145F3
126533 | 2013-04-17 | Scheduled Outage | Construction | Replace a rotten pole | None | None | 18 | 212 | 64 | South | 49F6
126535 | 2013-04-17 | Defective Equipment | Mechanical Failure | Transformer #X24089 opened by crew to test transformer | O/H Conductor | Hot-Line Clamp | 13 | 14 | 3 | East | 7F4
126536 | 2013-04-17 | Defective Equipment | Electrical Failure | S10518 opened due to defective cut-out | O/H Switchgear | Fused Cutout | 3 | 63 | 3 | Central | TD05
126537 | 2013-04-18 | Scheduled Outage | Maintenance | customer vault maintenance | None | None | 1 | 341 | 6 | Central | 5402
126539 | 2013-04-18 | Scheduled Outage | Maintenance | vt 298 AT 2495 Lancaster was isolated to allow contractor to perform Customer vault maintenance | None | None | 1 | 183 | 3 | East | 5310
126540 | 2013-04-18 | Loss Of Supply | Transmission Inadvertent | The A9M3 circuit tripped, cause currently under investigation. High winds were experienced in the area. No fault indicators were flagged on our section of A9M3. | None | None | 6714 | 8 | 895 | West | A9M3
126544 | 2013-04-19 | Adverse Weather | Extreme Wind | transformer X35346 was opened to allow crew to make repairs to secondary open bus | Secondary \ Service | O/H Service | 9 | 132 | 20 | Central | AD05
126545 | 2013-04-19 | Scheduled Outage | Maintenance | Elbow & insert repair at TP5993 | None | Elbow \ Insert | 10 | 133 | 22 | South | 140F3
126548 | 2013-04-19 | Adverse Weather | Extreme Wind | branch in wires | Secondary \ Service | O/H Service | 10 | 35 | 6 | East | TB06
126549 | 2013-04-19 | Adverse Weather | Extreme Wind | tree down on the primary | O/H Conductor | O/H Conductor | 109 | 368 | 669 | Central | SM16
126549 | 2013-04-19 | Adverse Weather | Extreme Wind | tree down on the primary | O/H Conductor | O/H Conductor | 369 | 8 | 49 | Central | SM16
126551 | 2013-04-19 | Adverse Weather | Extreme Wind | LARGE POPLAR BROKE THE CROSS ARM, IN THE BUSH | Pole | Crossarm | 13 | 403 | 87 | East | BLKF5
126552 | 2013-04-20 | Scheduled Outage | Maintenance | Customer vault maintenance | None | None | 1 | 612 | 10 | Central | TM3SH
126553 | 2013-04-20 | Scheduled Outage | Maintenance | To allow a contractor to perform routine customer vault maintenance. | None | None | 1 | 534 | 9 | Central | 602
126554 | 2013-04-20 | Unknown/Other | Unknown | Replaced blown fuse at transformer X26271 located at 337 Knox Cres. | None | None | 9 | 194 | 29 | East | UQ05
126555 | 2013-04-20 | Scheduled Outage | Maintenance | To allow a contractor to perform routine customer vault maintenance. | None | None | 1 | 167 | 3 | Central | SB02
126556 | 2013-04-21 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change defective primary connections in P517 and replace the UW02 dip switches feeding P517. | None | Termination \ Stress Cone | 10 | 90 | 15 | Central | UW02
126557 | 2013-04-21 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to straighten P9 padmount transformer on the concrete pad. | None | Unknown \ Other | 1 | 51 | 1 | Central | UX07
126558 | 2013-04-21 | Defective Equipment | Mechanical Failure | Cable fault | U/G Cable | PILC | 3 | 11 | 1 | Central | TL7TS
126558 | 2013-04-21 | Defective Equipment | Mechanical Failure | Cable fault | U/G Cable | PILC | 119 | 55 | 109 | Central | TL7TS
126558 | 2013-04-21 | Defective Equipment | Mechanical Failure | Cable fault | U/G Cable | PILC | 685 | 78 | 890 | Central | TL7TS
126559 | 2013-04-21 | Scheduled Outage | Construction | change PCB transformers. | None | None | 1 | 413 | 7 | Central | 617
126560 | 2013-04-22 | Scheduled Outage | Construction | Transformer #X27042 opened by crew for service upgarde. | None | None | 10 | 50 | 8 | East | AE02
126561 | 2013-04-22 | Scheduled Outage | Construction | Transformer #X35052 opened by crew for a disconnect/reconnect | None | None | 10 | 60 | 10 | Central | UW14
126563 | 2013-04-22 | Scheduled Outage | Maintenance | Replacing primary insulators in K418 & K419 and replace cut-outs S5708 W & S10411 W | None | Arrester | 31 | 324 | 167 | East | AN05
126565 | 2013-04-23 | Defective Equipment | Defective Equipment/ Material | defective switch feeding | Pole Attachement | Arrester | 1 | 286 | 5 | East | 77M6
126566 | 2013-04-23 | Scheduled Outage | Maintenance | K420 and K421 were isolated to allow crews to replace primary insulators. | None | Arrester | 28 | 297 | 139 | East | AN05
126567 | 2013-04-23 | Scheduled Outage | Maintenance | PCB Transformer Change and Vault Maintenance | None | None | 1 | 365 | 6 | Central | SR01
126568 | 2013-04-23 | Scheduled Outage | Maintenance | Transformer remediation | None | None | 10 | 692 | 115 | West | BRDF5
126569 | 2013-04-23 | Scheduled Outage | Maintenance | TP5620 was isolated to allow crew to replace elbows and inserts. | None | None | 9 | 47 | 7 | South | 140F3
126570 | 2013-04-23 | Scheduled Outage | Vegetation Management | Isolate primary O/h for tree removal @ 11 Lazy Nol | None | None | 34 | 71 | 40 | West | JKGF5
126571 | 2013-04-23 | Scheduled Outage | Maintenance | To repair defective elbows and insert at transformer TE1020 | None | Padmount (1ph) | 14 | 79 | 18 | South | 72F1
126572 | 2013-04-23 | Scheduled Outage | Maintenance | TP5682 was isolated to allow crew to repair broken insert. | None | None | 10 | 73 | 12 | South | 140F4
126575 | 2013-04-24 | Scheduled Outage | Maintenance | TP5997 was isolated to allow crew to repair broken insert. | None | None | 8 | 111 | 15 | South | 140F3
126576 | 2013-04-24 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X28163 opened by crew to replace triplex, neutral broke off in tree | O/H Conductor | O/H Conductor | 10 | 50 | 8 | Central | 505
126577 | 2013-04-24 | Scheduled Outage | Construction | ISOLATED 2 TRANSFORMERS X27552 AND X27557 TO INSTALL NEW POLES | None | None | 24 | 330 | 132 | Central | UN05
126579 | 2013-04-25 | Adverse Weather | Extreme Wind | Pole fire | Pole | Crossarm | 29 | 24 | 12 | Central | TM2UC
126579 | 2013-04-25 | Adverse Weather | Extreme Wind | Pole fire | Pole | Crossarm | 29 | 24 | 12 | Central | TM3UC
126580 | 2013-04-25 | Adverse Weather | Extreme Wind | Tree pulled down pole. | Pole | Pole | 263 | 166 | 728 | Central | AK03
126582 | 2013-04-25 | Defective Equipment | Defective Equipment/ Material | Tranformer #X33860 opened by crew to replace transformer lugs and secondary connections at pole and stand pipe | O/H Transformer | O/H Transformer (1ph) | 5 | 39 | 3 | Central | TH06
126583 | 2013-04-25 | Scheduled Outage | Construction | Transformer #X23893 opened by crew to install new O/H service | None | None | 10 | 30 | 5 | Central | TH06
126584 | 2013-04-25 | Defective Equipment | Electrical Failure | Pole #8 at 35 Robinson top burnt off. Pole is owned by Bell Canada. Gord Morris has called Bell for replacement. | Pole | Insulation Failure (Pole Fire) | 103 | 147 | 252 | Central | TR1UN
126584 | 2013-04-25 | Defective Equipment | Electrical Failure | Pole #8 at 35 Robinson top burnt off. Pole is owned by Bell Canada. Gord Morris has called Bell for replacement. | Pole | Insulation Failure (Pole Fire) | 189 | 88 | 277 | Central | TR1UN
126585 | 2013-04-25 | Scheduled Outage | Vegetation Management | Customer owned overhead line from S8249 isolated for tree trimming. | None | O/H Conductor | 1 | 233 | 4 | West | BECKF2
126586 | 2013-04-25 | Scheduled Outage | Maintenance | Transformer remediation | None | None | 18 | 410 | 123 | West | MWDF2
126587 | 2013-04-25 | Scheduled Outage | Forced Switching | Repair a burnt pole | None | Pole | 20 | 60 | 20 | South | 180F6
126591 | 2013-04-26 | Foreign Interference | Vehicle | Motor vehicle accident | Pole | Pole | 208 | 8 | 28 | East | 249F2
126591 | 2013-04-26 | Foreign Interference | Vehicle | Motor vehicle accident | Pole | Pole | 208 | 78 | 270 | East | 249F2
126592 | 2013-04-27 | Defective Equipment | Corrosion | Transformer TP7890 was isolated to allow crew to replace leaking transformer. | U/G Transformer | Padmount (1ph) | 7 | 201 | 23 | East | 77M2
126593 | 2013-04-27 | Defective Equipment | Mechanical Failure | S1395 blue phase was found blown due to defective switch. | O/H Switchgear | Fused Cutout | 75 | 58 | 72 | South | 87F7
126594 | 2013-04-27 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X15882 at 4903 Bowesville and G30R fuses were found blown due to pigeon contact. | O/H Switchgear | Fused Cutout | 49 | 91 | 74 | East | 7F4
126595 | 2013-04-27 | Scheduled Outage | Construction | Upgrading transformers in 4kv vault | None | None | 1 | 1821 | 30 | Central | UC02
126596 | 2013-04-27 | Scheduled Outage | Construction | Pole Replacement | None | Pole | 20 | 480 | 160 | Central | UN10
126597 | 2013-04-27 | Defective Equipment | Mechanical Failure | Fused cutout feeding transformer 2461 was found blown due to defective lightning arrestor. | O/H Switchgear | Fused Cutout | 1 | 83 | 1 | East | 7F4
126598 | 2013-04-28 | Scheduled Outage | Construction | 84F2 section from S11228 to EOL was isolated to allow crew to replace leaking transformer. | None | None | 49 | 617 | 504 | South | 84F2
126599 | 2013-04-28 | Defective Equipment | Defective Equipment/ Material | Defective Elbow at TX 176-2 blew the white phase fuses at S40 and switch 185 | U/G Cable Attachement | Elbow \ Insert | 112 | 167 | 312 | West | BRDF3
126600 | 2013-04-29 | Defective Equipment | Electrical Failure | defective U/G cable | U/G Cable | Unknown \ Other | 42 | 255 | 178 | West | BRDF5
126601 | 2013-04-29 | Scheduled Outage | Maintenance | change insulators and dip switch S17185 | None | None | 27 | 259 | 117 | Central | UN05
126602 | 2013-04-30 | Scheduled Outage | Maintenance | transformer isolated to allow crews to replace porcelain insulators. | None | None | 14 | 112 | 26 | East | AN05
126603 | 2013-04-30 | Defective Equipment | Defective Equipment/ Material | 140F4 O/H section was isolated to allow crew to make repairs to broken insulator at pole X06049. | Pole Attachement | Insulator | 105 | 63 | 110 | South | 140F4
126604 | 2013-04-30 | Defective Equipment | Defective Equipment/ Material | Transformer TE1119 was isolated to allow crew to replace defective transformer | U/G Transformer | Padmount (1ph) | 10 | 57 | 10 | South | 47F6
126605 | 2013-04-30 | Scheduled Outage | Construction | 140F4 O/H section between S179 and S25262 and section between S29587 and S267 was interrupted to allow crew to perform out of phase switching | None | None | 0 | 114 | 0 | South | 140F4
126605 | 2013-04-30 | Scheduled Outage | Construction | 140F4 O/H section between S179 and S25262 and section between S29587 and S267 was interrupted to allow crew to perform out of phase switching | None | None | 105 | 1 | 2 | South | 140F4
126605 | 2013-04-30 | Scheduled Outage | Construction | 140F4 O/H section between S179 and S25262 and section between S29587 and S267 was interrupted to allow crew to perform out of phase switching | None | None | 117 | 1 | 2 | South | 140F4
126606 | 2013-04-30 | Scheduled Outage | Maintenance | K428 was isolated to allow crew to replace Porcelain insulators | None | None | 14 | 135 | 32 | East | AN05
126607 | 2013-04-30 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30725 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 14 | 50 | 12 | Central | UD04
126609 | 2013-04-30 | Scheduled Outage | Construction | Transformer X36573 at 56 Benlark Rd. isolated to allow for transfer of plant. | None | None | 10 | 50 | 8 | South | 140F4
126610 | 2013-04-30 | Scheduled Outage | Construction | Transformer X09815 at 3160 Greenbank Rd. isolated to allow for transfer of plant. | None | None | 2 | 50 | 2 | South | 140F4
126611 | 2013-04-30 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X36554 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 5 | 30 | 2 | South | 140F4
126612 | 2013-04-30 | Scheduled Outage | Construction | Transformer X30726-1670695 at 355 Stewart St. isolated for transfer of plant | None | None | 22 | 117 | 43 | Central | UD04
126615 | 2013-05-01 | Scheduled Outage | Construction | Transformers 4141, 4140, 4139 and 4138 on Anik Way were isolated to allow crew to perform elbown and inserts replacement | None | None | 53 | 325 | 287 | West | 24F8
126616 | 2013-05-01 | Scheduled Outage | Maintenance | 4Kv O/H setion from S18892 to EOL on Denbury was isolated to allow crew to replace cutouts and for tree trimming crew to perform tree trimming | None | None | 32 | 303 | 162 | Central | AH13
126617 | 2013-05-01 | Scheduled Outage | Construction | Transformer X21539 at 197 Maple Street isolated to install new pole. | None | None | 4 | 50 | 3 | East | UT04
126618 | 2013-05-01 | Defective Equipment | Defective Equipment/ Material | While performing switching on the 77M1 & 77M6, defective elbow at transformer TP7056 caused the 77M1 and 77M6 circuit to trip open. | U/G Transformer | Unknown \ Other | 116 | 16 | 31 | East | 77M1
126618 | 2013-05-01 | Defective Equipment | Defective Equipment/ Material | While performing switching on the 77M1 & 77M6, defective elbow at transformer TP7056 caused the 77M1 and 77M6 circuit to trip open. | U/G Transformer | Unknown \ Other | 3455 | 44 | 2534 | East | 77M1
126618 | 2013-05-01 | Defective Equipment | Defective Equipment/ Material | While performing switching on the 77M1 & 77M6, defective elbow at transformer TP7056 caused the 77M1 and 77M6 circuit to trip open. | U/G Transformer | Unknown \ Other | 4800 | 22 | 1760 | East | 77M6
126619 | 2013-05-01 | Scheduled Outage | Construction | Transformer X30631-1670693 at 349 Stewart St. isolated to transfer hydro plant. | None | None | 10 | 180 | 30 | Central | UD04
126620 | 2013-05-01 | Scheduled Outage | Construction | Transformer X30634 at 341 Stewart St. isolated to transfer hydro plant. | None | None | 15 | 180 | 45 | Central | UD04
126621 | 2013-05-01 | Scheduled Outage | Construction | 140F4 O/H section between S179 and S25262 and section between S29587 and S267 was interrupted to allow crew to perform out of phase switching | None | None | 0 | 10 | 0 | South | 140F4
126621 | 2013-05-01 | Scheduled Outage | Construction | 140F4 O/H section between S179 and S25262 and section between S29587 and S267 was interrupted to allow crew to perform out of phase switching | None | None | 12 | 1 | 0 | South | 140F4
126621 | 2013-05-01 | Scheduled Outage | Construction | 140F4 O/H section between S179 and S25262 and section between S29587 and S267 was interrupted to allow crew to perform out of phase switching | None | None | 105 | 4 | 7 | South | 140F4
126622 | 2013-05-01 | Defective Equipment | Defective Equipment/ Material | Transformer #X27667 opened up due to broken cut out, crew replaced it, all power restored | O/H Switchgear | Fused Cutout | 5 | 146 | 12 | East | UQ08
126623 | 2013-05-02 | Scheduled Outage | Construction | Change a leaking transformer | U/G Transformer | Padmount (1ph) | 2 | 361 | 12 | South | 190F5
126625 | 2013-05-02 | Scheduled Outage | Maintenance | Transfer Plant to new poles | None | O/H Transformer (1ph) | 21 | 380 | 133 | Central | UN06
126627 | 2013-05-03 | Scheduled Outage | Maintenance | Elbow and insert replacement and repair | U/G Cable Attachement | Elbow \ Insert | 8 | 132 | 18 | South | 170F1
126628 | 2013-05-03 | Defective Equipment | Mechanical Failure | To megger investigate cable and replace blown fuse in isolated padmount. Padmount transformer found defective and requires replacement | U/G Transformer | Padmount (1ph) | 1 | 257 | 4 | East | 2206
126630 | 2013-05-05 | Scheduled Outage | Construction | U/G to pull in new cable for new TP9631 | None | None | 1 | 190 | 3 | East | 2203
126631 | 2013-05-05 | Defective Equipment | Electrical Failure | 48M5 pole pothead failed causing 48M5 circuit to trip. | U/G Cable Attachement | Pothead | 1 | 42 | 1 | East | 48M5
126631 | 2013-05-05 | Defective Equipment | Electrical Failure | 48M5 pole pothead failed causing 48M5 circuit to trip. | U/G Cable Attachement | Pothead | 4008 | 19 | 1269 | East | 48M5
126632 | 2013-05-05 | Scheduled Outage | Maintenance | Transformer 283 at 45 Dressler was isolated to allow crew to replace elbow and inserts on padmount transformer. | None | None | 6 | 148 | 15 | West | BRDF3
126633 | 2013-05-06 | Scheduled Outage | Maintenance | Change primary insulators | None | None | 27 | 257 | 116 | East | AN05
126634 | 2013-05-06 | Scheduled Outage | Maintenance | Metering to make repaires in vault | Vault Equipment | Unknown \ Other | 1 | 14 | 0 | East | TB15
126635 | 2013-05-06 | Scheduled Outage | Construction | PT264 isolated for replacement due to oil leak | U/G Transformer | Padmount (1ph) | 1 | 479 | 8 | East | TA3AQ
126636 | 2013-05-06 | Scheduled Outage | Construction | Transformer X30635 at 305 Stewart Street isolated for transfer of plant. | None | None | 19 | 205 | 65 | Central | UD04
126637 | 2013-05-07 | Scheduled Outage | Construction | Transformer & Cable replacement | U/G Transformer | Padmount (1ph) | 11 | 543 | 100 | East | BCHF3
126638 | 2013-05-07 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change primary insulators in the transformers & the S18380 cut out | None | Fused Cutout | 30 | 247 | 124 | East | AN05
126640 | 2013-05-08 | Scheduled Outage | Construction | TP9398 isolated for Transformer & cable replacement | U/G Transformer | Kiosk (1ph) | 10 | 469 | 78 | East | BCHF3
126641 | 2013-05-08 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change the primary insulators in the transformers & change the O/H cut out | None | Unknown \ Other | 30 | 249 | 124 | East | AN05
126642 | 2013-05-08 | Scheduled Outage | Construction | PCB transformer change | None | None | 1 | 164 | 3 | Central | 5405
126643 | 2013-05-08 | Human Element | Switching Error | Crew forgot to remove a set of grounds which casued the switchgear at VT179 at 265 Poulin to flash over and the 5405 line to trip. | Vault Equipment | Breaker \ Relay | 1 | 675 | 11 | Central | 5405
126643 | 2013-05-08 | Human Element | Switching Error | Crew forgot to remove a set of grounds which casued the switchgear at VT179 at 265 Poulin to flash over and the 5405 line to trip. | Vault Equipment | Breaker \ Relay | 22 | 89 | 33 | Central | 5405
126644 | 2013-05-08 | Scheduled Outage | Maintenance | TE767 at 1446 Lassiter was isolated to allow crews to perform soil remediation | None | Padmount (1ph) | 10 | 604 | 101 | East | BCHF1
126645 | 2013-05-09 | Defective Equipment | Electrical Failure | Cable fault between TP3964 and TP3965 | U/G Cable | XLPE | 11 | 23 | 4 | East | BCHF5
126645 | 2013-05-09 | Defective Equipment | Electrical Failure | Cable fault between TP3964 and TP3965 | U/G Cable | XLPE | 53 | 88 | 78 | East | BCHF5
126647 | 2013-05-09 | Scheduled Outage | Maintenance | B phase transformers 2212, TP9997, 4091. 4090, 4089 and 4088 on Castlefrank were isolated to allow crew to perform elbow and insert replacement | None | None | 59 | 238 | 234 | West | BRDF5
126648 | 2013-05-09 | Scheduled Outage | Construction | Transformer TE514 at 121 Woodridge was isolated to allow crew to replace transformer base and transformer | None | None | 21 | 508 | 178 | South | 49F2
126649 | 2013-05-09 | Loss Of Supply | Transmission Inadvertent | Hydro One lost of supply caused low voltage city wide and an outage at Centrepointe DS and Manordale DS. Hydro One reorts bad weather (lightning) in the Area. | None | None | 3344 | 10 | 557 | South | C7BM (Manordale MS - T1/T2)
126649 | 2013-05-09 | Loss Of Supply | Transmission Inadvertent | Hydro One lost of supply caused low voltage city wide and an outage at Centrepointe DS and Manordale DS. Hydro One reorts bad weather (lightning) in the Area. | None | None | 4764 | 10 | 794 | South | C7BM (Centrepointe MS - T1/T2)
126651 | 2013-05-09 | Foreign Interference | Wildlife (Bird/Animal) | Racoon | O/H Switchgear | Fused Cutout | 74 | 57 | 70 | East | 249F2
126653 | 2013-05-09 | Scheduled Outage | Maintenance | Vault shut down for routine maintenace | None | None | 1 | 336 | 6 | Central | 409
126654 | 2013-05-10 | Scheduled Outage | Construction | K429 at 3220 Southgate was isolated to allow crew to replace transformer and primary dip | U/G Transformer | Kiosk (1ph) | 14 | 222 | 52 | East | AN05
126655 | 2013-05-10 | Scheduled Outage | Construction | Transformer X32790 at 1217 Woodroffe Ave. isolated to run new service. | None | None | 7 | 52 | 6 | Central | UW03
126656 | 2013-05-10 | Scheduled Outage | Construction | Transformer X30490 at 103 Smirle Ave. isolated to install new service. | None | None | 8 | 100 | 13 | Central | TH01
126657 | 2013-05-10 | Scheduled Outage | Maintenance | Transformer X37017 at 555 Berry Side Rd. isolated to replace o/h switches | None | None | 2 | 66 | 2 | West | 624F6
126658 | 2013-05-10 | Foreign Interference | Foreign Objects | Branch across R & W phases in the rear of 67 Stillwater. Caused S961 R & W and S960 W to blow. | O/H Switchgear | Fused Cutout | 103 | 30 | 52 | South | 49F6
126658 | 2013-05-10 | Foreign Interference | Foreign Objects | Branch across R & W phases in the rear of 67 Stillwater. Caused S961 R & W and S960 W to blow. | O/H Switchgear | Fused Cutout | 199 | 55 | 182 | South | 49F6
126659 | 2013-05-10 | Defective Equipment | Defective Equipment/ Material | Replace defective switch and arrestor | O/H Transformer | O/H Transformer (1ph) | 19 | 36 | 11 | South | 47F3
126660 | 2013-05-10 | Defective Equipment | Moisture Ingress | Defective split connection on switch 328. | O/H Switchgear | Simple Solid Blade Switch | 317 | 111 | 586 | West | ALEXF3
126660 | 2013-05-10 | Defective Equipment | Moisture Ingress | Defective split connection on switch 328. | O/H Switchgear | Simple Solid Blade Switch | 377 | 9 | 57 | West | ALEXF3
126660 | 2013-05-10 | Defective Equipment | Moisture Ingress | Defective split connection on switch 328. | O/H Switchgear | Simple Solid Blade Switch | 567 | 6 | 57 | West | ALEXF3
126660 | 2013-05-10 | Defective Equipment | Moisture Ingress | Defective split connection on switch 328. | O/H Switchgear | Simple Solid Blade Switch | 776 | 62 | 802 | West | ALEXF3
126660 | 2013-05-10 | Defective Equipment | Moisture Ingress | Defective split connection on switch 328. | O/H Switchgear | Simple Solid Blade Switch | 946 | 30 | 473 | West | ALEXF3
126660 | 2013-05-10 | Defective Equipment | Moisture Ingress | Defective split connection on switch 328. | O/H Switchgear | Simple Solid Blade Switch | 1006 | 183 | 3068 | West | ALEXF3
126661 | 2013-05-11 | Adverse Environment | Fire | Pole fire at 900 Belfast caused PT98 to fall to the ground. | Pole | Insulation Failure (Pole Fire) | 1 | 500 | 8 | East | TB14
126661 | 2013-05-11 | Adverse Environment | Fire | Pole fire at 900 Belfast caused PT98 to fall to the ground. | Pole | Insulation Failure (Pole Fire) | 97 | 107 | 173 | East | TB14
126661 | 2013-05-11 | Adverse Environment | Fire | Pole fire at 900 Belfast caused PT98 to fall to the ground. | Pole | Insulation Failure (Pole Fire) | 105 | 89 | 156 | East | TB14
126663 | 2013-05-11 | Scheduled Outage | Maintenance | Transformer X16003 at 2540 Del Zotto was to allow crew upgrade services. | None | None | 7 | 200 | 23 | East | LTM01
126664 | 2013-05-11 | Scheduled Outage | Construction | Installing prespun and transferring plant to new poles | None | None | 50 | 425 | 354 | Central | UN10
126665 | 2013-05-11 | Scheduled Outage | Maintenance | Vault maintenance. | None | None | 1 | 215 | 4 | Central | 604
126666 | 2013-05-12 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27832 (SQUIRREL CONTACT) | O/H Switchgear | Fused Cutout | 12 | 79 | 16 | Central | TH06
126668 | 2013-05-12 | Tree Contacts | Falling Tree | Tree contact and burnt up lead at Goulbourn Rec Centre caused the A9M3 to auto-reclose and lock out. All of Beaverbrook, Janet King F4, F5, Munster and Bridlewood F3 were interrupted. | O/H Conductor | Hot-Line Clamp | 2099 | 88 | 3079 | West | A9M3
126668 | 2013-05-12 | Tree Contacts | Falling Tree | Tree contact and burnt up lead at Goulbourn Rec Centre caused the A9M3 to auto-reclose and lock out. All of Beaverbrook, Janet King F4, F5, Munster and Bridlewood F3 were interrupted. | O/H Conductor | Hot-Line Clamp | 4752 | 26 | 2059 | West | A9M3
126668 | 2013-05-12 | Tree Contacts | Falling Tree | Tree contact and burnt up lead at Goulbourn Rec Centre caused the A9M3 to auto-reclose and lock out. All of Beaverbrook, Janet King F4, F5, Munster and Bridlewood F3 were interrupted. | O/H Conductor | Hot-Line Clamp | 7599 | 19 | 2406 | West | A9M3
126671 | 2013-05-12 | Tree Contacts | Falling Tree | SCADA indicates 72F4 circuit auto-reclosed during wind storm. OMS calls rolled up to S407 W phase run off. | O/H Conductor | O/H Conductor | 63 | 458 | 481 | South | 72F4
126674 | 2013-05-12 | Tree Contacts | Falling Tree | Switch S28391 blew due to a tree bringing down wires at 3030 Steeplehill. | O/H Conductor | O/H Conductor | 30 | 236 | 118 | South | 145F3
126676 | 2013-05-12 | Tree Contacts | Falling Tree | Tree lying on overhead wires at Ivanhoe and Elmhurst caused S21516 RB to blow. | O/H Conductor | O/H Conductor | 304 | 136 | 689 | Central | TD05
126676 | 2013-05-12 | Tree Contacts | Falling Tree | Tree lying on overhead wires at Ivanhoe and Elmhurst caused S21516 RB to blow. | O/H Conductor | O/H Conductor | 457 | 66 | 503 | Central | TD05
126677 | 2013-05-12 | Adverse Weather | Extreme Wind | No cause found. Suspect wind slapped phases together or caused tree to contact the line | O/H Switchgear | Fused Cutout | 20 | 255 | 85 | Central | 503
126678 | 2013-05-12 | Tree Contacts | Broken Branch | Tree on wires caused transformer X23247 to open | O/H Switchgear | Fused Cutout | 22 | 302 | 111 | East | UT06
126679 | 2013-05-12 | Tree Contacts | Falling Tree | Tree fell & caused white phase conductor to come down | O/H Conductor | O/H Conductor | 23 | 167 | 64 | East | UG09
126679 | 2013-05-12 | Tree Contacts | Falling Tree | Tree fell & caused white phase conductor to come down | O/H Conductor | O/H Conductor | 29 | 277 | 134 | East | UG09
126680 | 2013-05-13 | Defective Equipment | Defective Equipment/ Material | defective O/H service | Secondary \ Service | O/H Service | 6 | 32 | 3 | Central | UV07
126681 | 2013-05-12 | Tree Contacts | Falling Tree | Transformer fuse. | O/H Conductor | O/H Conductor | 1 | 192 | 3 | West | 29F1
126682 | 2013-05-12 | Tree Contacts | Falling Tree | Defective transformer due to possible A9M3 causing surge to RHNF1. | O/H Transformer | O/H Transformer (1ph) | 1 | 622 | 10 | West | 29F1
126683 | 2013-05-12 | Tree Contacts | Falling Tree | Defective transformer due to A9M3 surging on the 8kv line. | O/H Transformer | O/H Transformer (1ph) | 1 | 441 | 7 | West | 29F1
126686 | 2013-05-13 | Scheduled Outage | Construction | Transformer X22654 was isolated to allow crew to remove secondary cables and install them to new transformer TP9946. | None | None | 1 | 385 | 6 | East | V11F3
126687 | 2013-05-13 | Scheduled Outage | Construction | Transformer X35065 at 2245 Tecumseh St . Isolated to transfer plant to new phase for future pole replacement | None | None | 5 | 40 | 3 | Central | UW04
126688 | 2013-05-13 | Scheduled Outage | Construction | Transformer X35069 at 2251 Tecumseh St . Isolated to transfer plant to new phase for future pole replacement | None | None | 3 | 40 | 2 | Central | UW04
126689 | 2013-05-13 | Scheduled Outage | Construction | Transformer X35054 at 1225 Adirondack Dr. Isolated to transfer plant to new phase for future pole replacement | None | None | 4 | 40 | 3 | Central | UW04
126690 | 2013-05-13 | Defective Equipment | Defective Equipment/ Material | Transformer TP2564 at 6 Huntings End was isolated to allow crwe to replace defective insert | U/G Transformer | Padmount (1ph) | 8 | 95 | 13 | West | BRDF1
126691 | 2013-05-13 | Scheduled Outage | Forced Switching | Transformer TP2574 at 24 Bluemeadow was isolated to allow crew to replace defective insert | None | Padmount (1ph) | 8 | 34 | 5 | West | BRDF1
126692 | 2013-05-13 | Defective Equipment | Defective Equipment/ Material | Transformer X25807 at 1720 Innes Rd. isolated to reattach a lead to the transformer. | O/H Transformer | O/H Transformer (3ph) | 1 | 43 | 1 | East | CYRF2
126693 | 2013-05-14 | Scheduled Outage | Construction | transformer and cable replacement | None | None | 10 | 560 | 93 | East | BCHF3
126694 | 2013-05-14 | Scheduled Outage | Construction | At 9:28am, 4 KV vault V341 at 40 driveway was isolated to allow crews to replace PCB transformers. 1 customer affecetd for minutes. Slater (SA23) ID #126694 | None | Transformer | 1 | 593 | 10 | Central | SA23
126696 | 2013-05-14 | Human Element | Switching Error | Switching error | None | None | 172 | 8 | 23 | West | ALEXF3
126696 | 2013-05-14 | Human Element | Switching Error | Switching error | None | None | 172 | 20 | 57 | West | ALEXF3
126696 | 2013-05-14 | Human Element | Switching Error | Switching error | None | None | 310 | 2 | 10 | West | ALEXF3
126697 | 2013-05-14 | Scheduled Outage | Construction | At 16:53, 4 KV O/H section isolated to allow crews to install new poles & reconfigure plant. 36 customers affected for minutes. Slater (SA23) ID # 126697 | None | None | 36 | 139 | 83 | Central | SA23
126698 | 2013-05-14 | Scheduled Outage | Maintenance | Isolation of TE2328 to allow crew to re-insulate o/h @ riser. | None | Insulator | 3 | 180 | 9 | East | 77M6
126699 | 2013-05-14 | Scheduled Outage | Maintenance | at 4:30pm, 4KV transformers (X31178, X31179, X30698, X30699, X30878 & X31013) were off potential to allow crews to adjust taps. 73 CUSTOMERS AFFECTED FOR 45 MINUTES. Slater (SA23) ID #126699 | None | O/H Transformer (1ph) | 73 | 45 | 55 | Central | SA23
126700 | 2013-05-14 | Scheduled Outage | Construction | Transformer X26880 at 2233 Carnegie St. isolated to replace AE02-E switches | None | None | 3 | 252 | 13 | East | AE03
126701 | 2013-05-14 | Scheduled Outage | Construction | Transformer X42391 at 215 Ivy Cres. Isolated to allow for pole replacement. | None | None | 27 | 185 | 83 | East | UG11
126702 | 2013-05-15 | Scheduled Outage | Maintenance | Soil remediation at TP7890 from previous leaker. | None | Padmount (1ph) | 8 | 526 | 70 | East | 77M2
126703 | 2013-05-15 | Scheduled Outage | Construction | cable and transformer replacement | None | None | 9 | 515 | 77 | East | BCHF3
126705 | 2013-05-15 | Scheduled Outage | Vegetation Management | At 09:45am, 4KV O/H section isolated to allow contractor to remove tree. 22 customers affected for 285 minutes. Carling (SM06) ID #126705 | None | None | 22 | 285 | 104 | Central | SM06
126707 | 2013-05-15 | Defective Equipment | Electrical Failure | Blown revenue meters | Station Equipment | Unknown \ Other | 1545 | 50 | 1288 | East | 77M5
126708 | 2013-05-15 | Foreign Interference | Vehicle | Possible MVA at Wellington & Mayfair | Pole | Pole | 43 | 306 | 219 | Central | TH01
126708 | 2013-05-15 | Foreign Interference | Vehicle | Possible MVA at Wellington & Mayfair | Pole | Pole | 248 | 92 | 380 | Central | TH01
126709 | 2013-05-15 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X17221 at 1708 St. Joseph Blvd. Cause - crowe | O/H Transformer | O/H Transformer (1ph) | 3 | 149 | 7 | East | 77M5
126710 | 2013-05-16 | Scheduled Outage | Construction | Change Leaking transformer PT124 | U/G Transformer | Kiosk (3ph) | 16 | 139 | 37 | East | ELW12
126711 | 2013-05-16 | Scheduled Outage | Maintenance | Clean, torque and service vault VT168 | None | None | 1 | 301 | 5 | East | TB1AL
126712 | 2013-05-16 | Scheduled Outage | Maintenance | Replace defective primary connections in padmount and PPH switches. | None | None | 1 | 123 | 2 | Central | UC03
126713 | 2013-05-16 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace leaking transformer TP2570 B | U/G Transformer | Padmount (1ph) | 9 | 137 | 21 | West | BRDF1
126714 | 2013-05-16 | Scheduled Outage | Maintenance | Vault maintenace and floor painting. | None | None | 1 | 344 | 6 | Central | 303
126715 | 2013-05-16 | Scheduled Outage | Construction | Transformer & cable replacement | None | Padmount (1ph) | 9 | 503 | 75 | East | BCHF5
126716 | 2013-05-16 | Adverse Environment | Fire | Fire Department need bulding isolated. | None | None | 1 | 492 | 8 | East | 5301
126717 | 2013-05-16 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X24605 opened up due to squirrel contact | O/H Transformer | O/H Transformer (1ph) | 7 | 122 | 14 | East | 8F1
126718 | 2013-05-16 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X6991 opened up due to bird contact | O/H Transformer | O/H Transformer (1ph) | 1 | 78 | 1 | West | MWDF3
126719 | 2013-05-18 | Foreign Interference | Wildlife (Bird/Animal) | Switch 126B at 269 Pinhey opened due to animal contact at pole X39517 | O/H Conductor | O/H Conductor | 13 | 171 | 37 | West | 624F6
126720 | 2013-05-18 | Foreign Interference | Vehicle | OFS reports wires down | Pole Attachement | Unknown \ Other | 30 | 60 | 30 | Central | TM3UC
126720 | 2013-05-18 | Foreign Interference | Vehicle | OFS reports wires down | Pole Attachement | Unknown \ Other | 30 | 61 | 30 | Central | TM2UC
126721 | 2013-05-20 | Scheduled Outage | Construction | Change leaking xfmr, replace switches on pole and have drain-all and Greely perform soil remediation. | U/G Transformer | Kiosk (3ph) | 6 | 451 | 45 | East | 2207
126722 | 2013-05-20 | Scheduled Outage | Maintenance | Transformer TE2248 at 1811 St. Joseph was isolated to allow crew to replace leaking transformer and replace O/H switch. | U/G Transformer | Padmount (3ph) | 1 | 430 | 7 | East | 77M5
126723 | 2013-05-20 | Scheduled Outage | Construction | Planned momentary outage to customers on Bren-Maur to allow crew to perform out of phase switching. | None | None | 119 | 1 | 2 | South | 140F4
126724 | 2013-05-21 | Adverse Weather | Extreme Wind | Weather related | O/H Transformer | O/H Transformer (1ph) | 8 | 127 | 17 | Central | TD06
126725 | 2013-05-21 | Scheduled Outage | Maintenance | Contractor to torque secondary main switrch | None | None | 1 | 21 | 0 | East | SO06
126726 | 2013-05-21 | Scheduled Outage | Maintenance | KT12 at 45 Rick Little was isolated to allow crews to tighten loose connections. | None | Kiosk (1ph) | 9 | 95 | 14 | East | 2207
126727 | 2013-05-21 | Scheduled Outage | Maintenance | Vault Maintenance | None | None | 1 | 156 | 3 | South | 49F1
126728 | 2013-05-21 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMERS X35065, X35054 AND X35069 TO INSTALL NEW POLES | None | None | 11 | 190 | 35 | Central | UW04
126729 | 2013-05-21 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32762 TO INSTALL NEW POLE | None | None | 2 | 150 | 5 | Central | UW04
126730 | 2013-05-21 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32763 TO INSTALL NEW POLE | None | None | 6 | 150 | 15 | Central | UW04
126731 | 2013-05-21 | Lightning | Lightning | 22M26 circuit opened under hold off protection during adverse weather, thunder storm. | None | None | 4770 | 2 | 159 | South | 22M26
126733 | 2013-05-21 | Scheduled Outage | Construction | change transformer and cables. | None | None | 12 | 498 | 100 | East | BCHF3
126734 | 2013-05-21 | Adverse Weather | Extreme Wind | Tree across the 3 phase conductor | O/H Conductor | O/H Conductor | 101 | 67 | 113 | West | 43F2
126734 | 2013-05-21 | Adverse Weather | Extreme Wind | Tree across the 3 phase conductor | O/H Conductor | O/H Conductor | 315 | 219 | 1150 | West | 43F2
126735 | 2013-05-22 | Adverse Weather | Extreme Wind | To repair damaged secondary overhead | Secondary \ Service | O/H Service | 12 | 27 | 5 | Central | AD05
126736 | 2013-05-22 | Scheduled Outage | Construction | transformer and cable replacement | None | None | 8 | 554 | 74 | East | BCHF3
126737 | 2013-05-22 | Scheduled Outage | Forced Switching | out of phase conditon | None | None | 120 | 2 | 4 | South | 140F4
126739 | 2013-05-22 | Scheduled Outage | Maintenance | Station maintenance | None | None | 1 | 290 | 5 | Central | 2804
126740 | 2013-05-22 | Scheduled Outage | Construction | PCB transformer replacement, vault Maintenance. | None | None | 1 | 342 | 6 | Central | TL3SB
126741 | 2013-05-22 | Scheduled Outage | Construction | Pole and conductor replacement | None | None | 30 | 297 | 148 | Central | UN07
126742 | 2013-05-22 | Scheduled Outage | Construction | replacing poles | None | None | 2 | 298 | 10 | South | 140F4
126744 | 2013-05-22 | Tree Contacts | Falling Tree | AD07 circuit opened by system due to a fallen tree on the overhead. Section of overhead isolated and tree removed. | O/H Conductor | O/H Conductor | 79 | 148 | 195 | Central | AD07
126744 | 2013-05-22 | Tree Contacts | Falling Tree | AD07 circuit opened by system due to a fallen tree on the overhead. Section of overhead isolated and tree removed. | O/H Conductor | O/H Conductor | 577 | 9 | 87 | Central | AD07
126744 | 2013-05-22 | Tree Contacts | Falling Tree | AD07 circuit opened by system due to a fallen tree on the overhead. Section of overhead isolated and tree removed. | O/H Conductor | O/H Conductor | 577 | 26 | 250 | Central | AD07
126746 | 2013-05-22 | Adverse Weather | Extreme Wind | Tree Removal | O/H Conductor | O/H Conductor | 13 | 84 | 18 | Central | UW06
126747 | 2013-05-22 | Tree Contacts | Falling Tree | heavy rain | Secondary \ Service | O/H Service | 3 | 203 | 10 | East | UQ07
126747 | 2013-05-22 | Tree Contacts | Falling Tree | heavy rain | Secondary \ Service | O/H Service | 6 | 229 | 23 | East | UQ07
126748 | 2013-05-23 | Scheduled Outage | Construction | At 08:10am, 8KV transformer TP9403 at 639 Gaines was isolated to allow crews to replace tansformer & supply cables. 9 customers affected for minutes. Beaconhill (BCHF3) ID #126748 | None | None | 9 | 597 | 90 | East | BCHF3
126749 | 2013-05-23 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X34112 opened up due to squirrel contact. | O/H Transformer | O/H Transformer (1ph) | 9 | 117 | 18 | Central | TH01
126750 | 2013-05-23 | Scheduled Outage | Maintenance | Transformer #TP3082 opened by crew for maintenance | None | None | 13 | 27 | 6 | East | BCHF5
126751 | 2013-05-23 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact at 53 Scissons | None | None | 7 | 126 | 15 | West | BRDF2
126751 | 2013-05-23 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact at 53 Scissons | None | None | 346 | 125 | 721 | West | BRDF2
126753 | 2013-05-23 | Tree Contacts | Tree Growth/ Untrimmed Tree | crews found wet branches in contact with G726W (N/O point), cleared and G666W refused. Uplands (4801F8) ID #126753 | O/H Switchgear | Fused Cutout | 73 | 80 | 97 | East | 4801F8
126754 | 2013-05-23 | Scheduled Outage | Vegetation Management | Transformer #X35006 opened by crew for tree trimming | None | None | 14 | 235 | 55 | Central | SM10
126756 | 2013-05-24 | Tree Contacts | Falling Tree | Fall Poplar tree damaged pole X27837, S12839 blown | Pole | Pole | 7 | 445 | 52 | East | 7F2
126757 | 2013-05-24 | Defective Equipment | Defective Equipment/ Material | Transformer #X31821 opened up due to broken cut out. | O/H Switchgear | Fused Cutout | 3 | 38 | 2 | Central | AM02
126758 | 2013-05-24 | Scheduled Outage | Construction | To replace leaking transformer 4474 @ 6 Curran | None | Padmount (1ph) | 5 | 98 | 8 | West | BRDF4
126759 | 2013-05-24 | Defective Equipment | Electrical Failure | TO3AP cable fault between TO & VT363 | U/G Cable | PILC | 527 | 53 | 466 | East | TO3AP
126760 | 2013-05-25 | Defective Equipment | Electrical Failure | Cable fault on TO2UB circuit caused TO46 to open. | U/G Cable | Unknown \ Other | 124 | 60 | 124 | East | TO2UB
126760 | 2013-05-25 | Defective Equipment | Electrical Failure | Cable fault on TO2UB circuit caused TO46 to open. | U/G Cable | Unknown \ Other | 565 | 25 | 235 | East | TO2UB
126760 | 2013-05-25 | Defective Equipment | Electrical Failure | Cable fault on TO2UB circuit caused TO46 to open. | U/G Cable | Unknown \ Other | 906 | 113 | 1706 | East | TO2UB
126760 | 2013-05-25 | Defective Equipment | Electrical Failure | Cable fault on TO2UB circuit caused TO46 to open. | U/G Cable | Unknown \ Other | 1870 | 7 | 218 | East | TO2UB
126762 | 2013-05-25 | Scheduled Outage | Maintenance | Vault maintenance | None | None | 2 | 589 | 20 | Central | 5201
126763 | 2013-05-25 | Foreign Interference | Wildlife (Bird/Animal) | squirrel contact, and broken switch | O/H Switchgear | Fused Cutout | 11 | 225 | 41 | West | ALEXF3
126764 | 2013-05-25 | Scheduled Outage | Maintenance | Vault maintenance | None | None | 1 | 133 | 2 | Central | 303
126765 | 2013-05-25 | Scheduled Outage | Maintenance | Vault maintenance | None | None | 1 | 215 | 4 | Central | 611
126766 | 2013-05-25 | Tree Contacts | Broken Branch | Tree branch fell on wires. | O/H Conductor | O/H Conductor | 47 | 39 | 31 | Central | UC03
126766 | 2013-05-25 | Tree Contacts | Broken Branch | Tree branch fell on wires. | O/H Conductor | O/H Conductor | 62 | 105 | 108 | Central | UC03
126770 | 2013-05-26 | Defective Equipment | Defective Equipment/ Material | Blown lightning arrestor on customer owned equipment | Customer Owned | Customer-Owned | 1 | 4 | 0 | West | 624F6
126771 | 2013-05-27 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35685 TO INSTALL NEW SECONDARY TRIPLEX | None | None | 10 | 115 | 19 | Central | TD14
126772 | 2013-05-27 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X36894 FOR POLE MAINTENACE | None | None | 1 | 30 | 0 | South | 49F5
126773 | 2013-05-27 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X27794 TO REMOVE TREE | None | None | 6 | 180 | 18 | East | UQ07
126774 | 2013-05-27 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X45134 AND X45135 TO INSTALL NEW POLES | None | None | 20 | 315 | 105 | East | UT06
126775 | 2013-05-27 | Unknown/Other | Unknown | No cause found | None | None | 3 | 425 | 21 | West | 28F1
126776 | 2013-05-27 | Scheduled Outage | Construction | Replace transformer & elbow and inserts | None | Padmount (1ph) | 10 | 2 | 0 | West | MWDF2
126776 | 2013-05-27 | Scheduled Outage | Construction | Replace transformer & elbow and inserts | None | Padmount (1ph) | 10 | 74 | 12 | West | MWDF2
126776 | 2013-05-27 | Scheduled Outage | Construction | Replace transformer & elbow and inserts | None | Padmount (1ph) | 20 | 228 | 76 | West | MWDF2
126777 | 2013-05-27 | Defective Equipment | Defective Equipment/ Material | suspected cable fault on 8F1 blue phase between TE905 and TE903 | U/G Cable | Unknown \ Other | 75 | 126 | 158 | East | 8F1
126780 | 2013-05-28 | Scheduled Outage | Construction | Crews repalced leaking transformer TE1723 | None | None | 9 | 216 | 32 | East | 4801F8
126781 | 2013-05-28 | Scheduled Outage | Construction | To change out transformer TP9404 under the beaconhill transformer replacement program. | None | None | 5 | 475 | 40 | East | BCHF3
126782 | 2013-05-28 | Scheduled Outage | Construction | At 9:28 am, Vault VT282 at 1785 Riverside was isolated to allow crew to replace PCB transformers. 1 customer was interrupted for minutes. Riverdale (TR3UQ) ID# 126782. | None | Transformer | 1 | 326 | 5 | Central | TR3UQ
126784 | 2013-05-28 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X45135 TO INSTALL NEW POLE | None | None | 8 | 150 | 20 | East | UT06
126785 | 2013-05-28 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X31849 TO RE-SAG SERVICE | None | None | 17 | 25 | 7 | Central | UL06
126788 | 2013-05-28 | Scheduled Outage | Construction | Leaking Transformer Change | None | None | 5 | 86 | 7 | West | BRDF4
126789 | 2013-05-28 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X34299 opened up due to squirrel contact | O/H Transformer | O/H Transformer (1ph) | 8 | 112 | 15 | Central | TD06
126790 | 2013-05-28 | Human Element | Commissioning Error | faulty controls on recloser RHNF1 | Station Equipment | Relay | 6438 | 1 | 107 | West | 29F1
126794 | 2013-05-29 | Unknown/Other | Unknown | G497 feeding Rideau carleton raceway barns found blown, line patroled and rabbits inspected, no problems found | None | None | 1 | 105 | 2 | East | 7F4
126795 | 2013-05-29 | Defective Equipment | Mechanical Failure | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X27449 | O/H Switchgear | Fused Cutout | 8 | 136 | 18 | East | UA07
126796 | 2013-05-29 | Defective Equipment | Mechanical Failure | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X28141 | O/H Switchgear | Fused Cutout | 5 | 93 | 8 | East | UZ04
126797 | 2013-05-29 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X18939 TO RE-INSULATE THE POLE | None | None | 14 | 90 | 21 | East | CYRF1
126798 | 2013-05-29 | Defective Equipment | Mechanical Failure | broke transformer cut-out at transformer# 4517 located at 682 Kama Cres, caused G529 R phase to open | O/H Switchgear | Fused Cutout | 21 | 96 | 34 | East | 8F1
126801 | 2013-05-30 | Scheduled Outage | Construction | TP9405 at 2006 Gtineau View Cres. Transformer and cable replacement | None | None | 12 | 505 | 101 | East | BCHF3
126803 | 2013-05-30 | Foreign Interference | Dig-In | Dig in at 17 Donland between TP2481 and TE502 caused S315 and S658 to open. | U/G Cable | XLPE | 22 | 10 | 4 | South | EPWF3
126803 | 2013-05-30 | Foreign Interference | Dig-In | Dig in at 17 Donland between TP2481 and TE502 caused S315 and S658 to open. | U/G Cable | XLPE | 35 | 49 | 29 | South | EPWF3
126803 | 2013-05-30 | Foreign Interference | Dig-In | Dig in at 17 Donland between TP2481 and TE502 caused S315 and S658 to open. | U/G Cable | XLPE | 122 | 43 | 87 | South | EPWF3
126805 | 2013-05-30 | Scheduled Outage | Construction | Transformer X32765 at 1283 Adirondack Dr. isolated to replace transformer and transfer hydro plant | None | None | 4 | 205 | 14 | Central | UW04
126806 | 2013-05-30 | Scheduled Outage | Construction | Transformer X32764 at 1282 Adirondack Dr. isolated to replace transformer and transfer hydro plant | None | None | 2 | 205 | 7 | Central | UW04
126808 | 2013-05-30 | Scheduled Outage | Construction | Transformer X18933 at 2767 Page Rd. isolated to reinsulate pole | None | None | 18 | 35 | 10 | East | CYRF1
126809 | 2013-05-31 | Scheduled Outage | Construction | Leaking transformer 1043R isolate for replacement | None | Padmount (1ph) | 9 | 102 | 15 | West | BRDF1
126810 | 2013-05-31 | Scheduled Outage | Construction | re-insulate overhead line and de commission overhead xfmrs and re-energize address from a new padmount xfmr TP9945. | None | None | 1 | 292 | 5 | East | 249F2
126811 | 2013-05-31 | Foreign Interference | Wildlife (Bird/Animal) | squirrel contact | Unknown \ Other | Unknown \ Other | 63 | 130 | 136 | Central | TD12
126812 | 2013-05-31 | Scheduled Outage | Maintenance | 13kV transformer bus at VT441 was isolated to allow customer to make secondary breaker repairs | None | Breaker \ Relay | 1 | 104 | 2 | Central | 2806
126814 | 2013-05-31 | Tree Contacts | Tree Growth/ Untrimmed Tree | Trimmed trees & refused transformer X24154 at 23 Seguin St. - done by Brendan Coker of 24/7 | O/H Transformer | O/H Transformer (1ph) | 12 | 145 | 29 | East | 8F1
126815 | 2013-05-31 | Defective Equipment | Defective Equipment/ Material | Defective Transformer - X33161 replaced | O/H Transformer | O/H Transformer (1ph) | 5 | 434 | 36 | West | 28F2
126817 | 2013-05-31 | Foreign Interference | Customer-Cut Trees | Transformer X35176 at 257 Remic Ave. isolated to disconnect hazardous service at 260 Island Park Dr. REF OMS R00165220 | Secondary \ Service | O/H Service | 7 | 30 | 4 | Central | UL02
126819 | 2013-06-01 | Scheduled Outage | Maintenance | At 07:35am, 4KV overhead was isolated to allow crews to replace switches and contractor to work within the limits of approached to remove sign. 6 customers affected for 200 minutes. Clyde (UC07) ID #126819 | None | Inline Switch | 6 | 200 | 20 | Central | UC07
126821 | 2013-06-01 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35466 opened up due to squirrel contact. | O/H Transformer | O/H Transformer (1ph) | 11 | 215 | 39 | Central | TD01
126823 | 2013-06-01 | Defective Equipment | Defective Equipment/ Material | emergency repairs to defective service | Secondary \ Service | O/H Service | 7 | 94 | 11 | Central | UL02
126825 | 2013-06-01 | Defective Equipment | Defective Equipment/ Material | Transformer #X33760 opened by crew to replace a broken transformer switch | O/H Switchgear | Fused Cutout | 11 | 77 | 14 | Central | TW22
126826 | 2013-06-01 | Foreign Interference | Customer-Cut Trees | Tree fell on primary | None | None | 63 | 99 | 104 | South | 72F4
126826 | 2013-06-01 | Foreign Interference | Customer-Cut Trees | Tree fell on primary | None | None | 319 | 1 | 5 | South | 72F4
126828 | 2013-06-01 | Unknown/Other | Unknown | Not yet known. | None | None | 13000 | 25 | 5417 | West | A9M3
126829 | 2013-06-01 | Foreign Interference | Wildlife (Bird/Animal) | S26818 and X26869 fuses were found blown. | O/H Transformer | O/H Transformer (1ph) | 41 | 109 | 74 | East | TB15
126831 | 2013-06-01 | Defective Equipment | Electrical Failure | 200F2 auto-reclosed. S683 RWB feeding TE2922 (Loblaws) was found blown due to customer owned secondary cable fault. | Customer Owned | Customer-Owned | 1 | 386 | 6 | South | 200F2
126835 | 2013-06-02 | Foreign Interference | Wildlife (Bird/Animal) | crow got into the transformer 2564 pole X14306 | O/H Switchgear | Fused Cutout | 1 | 204 | 3 | East | 7F4
126836 | 2013-06-02 | Adverse Weather | Extreme Wind | Switch S28458 feeding X35414 found blown due to adverse weather | O/H Switchgear | Fused Cutout | 1 | 334 | 6 | West | 43F3
126837 | 2013-06-02 | Defective Equipment | Electrical Failure | blown lightening arrestor | Pole Attachement | Arrester | 4 | 50 | 3 | West | 43F3
126838 | 2013-06-03 | Scheduled Outage | Maintenance | Vault VT1525 was isolated to allow crew to prepare area for future work. | None | None | 1 | 163 | 3 | Central | 622
126840 | 2013-06-03 | Scheduled Outage | Construction | To Change Rotten Pole | Pole | Pole | 5 | 255 | 21 | Central | 303
126841 | 2013-06-03 | Defective Equipment | Electrical Failure | 77M6 cable fault between TP8048 & T8049 on Richer drive. Billberry (77M6) ID #126841 | U/G Cable | Unknown \ Other | 48 | 12 | 10 | East | 77M6
126841 | 2013-06-03 | Defective Equipment | Electrical Failure | 77M6 cable fault between TP8048 & T8049 on Richer drive. Billberry (77M6) ID #126841 | U/G Cable | Unknown \ Other | 58 | 93 | 90 | East | 77M6
126842 | 2013-06-03 | Scheduled Outage | Construction | Off Load for planned switch replacement job 684. | None | None | 16 | 15 | 4 | West | 39F3
126843 | 2013-06-03 | Scheduled Outage | Maintenance | O/H line fed from S13016 isolated to allow crews to repair neutral conductor | None | O/H Conductor | 1 | 46 | 1 | West | 29F1
126844 | 2013-06-03 | Scheduled Outage | Construction | Vault construction | None | None | 48 | 425 | 340 | Central | 409
126845 | 2013-06-04 | Scheduled Outage | Construction | To replace transformer TE173 (new TP9112) | None | Padmount (1ph) | 15 | 487 | 122 | East | BCHF5
126846 | 2013-06-04 | Scheduled Outage | Construction | transformer P542 at 353 Firle was isolated to allow crew to upgrade transformer and repalce dip sws and install new nomenclature | None | None | 1 | 156 | 3 | Central | UN07
126848 | 2013-06-04 | Scheduled Outage | Vegetation Management | S29143 at 528 Thessaly was isolated to allow crew to peform tree trimming | None | None | 34 | 310 | 176 | East | TB06
126849 | 2013-06-04 | Scheduled Outage | Construction | To install secondary | None | Padmount (3ph) | 10 | 239 | 40 | West | MWDF2
126850 | 2013-06-04 | Scheduled Outage | Maintenance | Not yet known.Place KT95 back on its base and chang the insulators in KT96 | None | Unknown \ Other | 32 | 165 | 88 | East | ELW07
126851 | 2013-06-04 | Scheduled Outage | Construction | Replace transformer TP3598 | None | Kiosk (1ph) | 12 | 74 | 15 | West | 624F1
126852 | 2013-06-04 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X31503 at 2060 Carling Ave. - cause squirrell | None | None | 9 | 86 | 13 | Central | TW22
126855 | 2013-06-04 | Defective Equipment | Electrical Failure | Two arrestors and transformer fuse X30149 at 272 Bronson blew causing the AM00 breaker to trip. AM00 was carrying the AM04 circuit for planned work. | Pole Attachement | Arrester | 17 | 99 | 28 | Central | AM04
126855 | 2013-06-04 | Defective Equipment | Electrical Failure | Two arrestors and transformer fuse X30149 at 272 Bronson blew causing the AM00 breaker to trip. AM00 was carrying the AM04 circuit for planned work. | Pole Attachement | Arrester | 225 | 39 | 146 | Central | AM04
126857 | 2013-06-05 | Scheduled Outage | Construction | BeaconHill backyard transformer relacement, and rearrange cables. | None | None | 12 | 494 | 99 | East | BCHF3
126858 | 2013-06-05 | Scheduled Outage | Forced Switching | S12839 to EOL at 4200 Riverside was isolated to allow crew to replace pole dammaged by wind storm | None | Pole | 7 | 308 | 36 | East | 7F2
126859 | 2013-06-05 | Scheduled Outage | Construction | 4Kv Vault V583 at 171 O Connor was isolated to allow contractor to perform customer vault maintenance, and for Hol crew to replace PCB transformers | None | None | 163 | 273 | 742 | Central | SA22
126860 | 2013-06-05 | Scheduled Outage | Construction | Replace TE1027 transformer & base | None | Padmount (1ph) | 8 | 296 | 39 | South | 87F7
126861 | 2013-06-05 | Scheduled Outage | Construction | Transformer P554 at 344 O Connor was isolated to allow crew to transfer plant ot new pole | None | None | 1 | 263 | 4 | Central | UF10
126862 | 2013-06-05 | Scheduled Outage | Construction | Transformer X31841 at 458 Edison Ave isolated to remove a service. | None | None | 1 | 11 | 0 | Central | AH14
126863 | 2013-06-05 | Scheduled Outage | Construction | Transformer X36894 at 100 Bayshore Dr. isolated to rearrange plant. | None | None | 1 | 23 | 0 | South | 49F5
126866 | 2013-06-06 | Defective Equipment | Mechanical Failure | BECKF2 white phase from RX2005 | O/H Switchgear | Fused Cutout | 99 | 132 | 218 | West | BECKF2
126867 | 2013-06-06 | Scheduled Outage | Construction | Transformer TP3113 & TP3114 was isolated to allow the crews to transfer the transformer to the BCHF5 supply. | None | Unknown \ Other | 17 | 174 | 49 | East | BCHF5
126868 | 2013-06-06 | Scheduled Outage | Construction | Transformer TP3112 was isolated allow the crew to replace the transformer and cables | None | Unknown \ Other | 9 | 447 | 67 | East | BCHF3
126869 | 2013-06-06 | Tree Contacts | Broken Branch | At 15:26 SCADA indicates UW07 opened, UW03 auto-reclosed twice and held, TW10 (UWT2) opened, and UW07 closed. | O/H Conductor | O/H Conductor | 223 | 70 | 260 | Central | UW07
126869 | 2013-06-06 | Tree Contacts | Broken Branch | At 15:26 SCADA indicates UW07 opened, UW03 auto-reclosed twice and held, TW10 (UWT2) opened, and UW07 closed. | O/H Conductor | O/H Conductor | 262 | 13 | 57 | Central | UW05
126869 | 2013-06-06 | Tree Contacts | Broken Branch | At 15:26 SCADA indicates UW07 opened, UW03 auto-reclosed twice and held, TW10 (UWT2) opened, and UW07 closed. | O/H Conductor | O/H Conductor | 432 | 24 | 173 | Central | UW06
126870 | 2013-06-06 | Defective Equipment | Electrical Failure | Pole fire at Marie & Zephyr, crews made temporary repairs | Pole | Insulation Failure (Pole Fire) | 74 | 170 | 210 | Central | TD14
126870 | 2013-06-06 | Defective Equipment | Electrical Failure | Pole fire at Marie & Zephyr, crews made temporary repairs | Pole | Insulation Failure (Pole Fire) | 1549 | 39 | 1007 | Central | TD14
126870 | 2013-06-07 | Defective Equipment | Electrical Failure | Pole fire at Marie & Zephyr, crews made temporary repairs | Pole | Insulation Failure (Pole Fire) | 747 | 25 | 311 | Central | TD14
126871 | 2013-06-08 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27668 | O/H Transformer | O/H Transformer (1ph) | 5 | 86 | 7 | East | TB06
126872 | 2013-06-08 | Scheduled Outage | Construction | Transformer replacement | None | None | 1 | 281 | 5 | East | SO11
126874 | 2013-06-09 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X39577 | O/H Transformer | O/H Transformer (1ph) | 2 | 60 | 2 | West | 624F6
126875 | 2013-06-09 | Scheduled Outage | Construction | 8kV transfomer TP5488 on Comstock Rd was isolated to allow crews to transfer cable to new pole. | None | XLPE | 3 | 329 | 16 | East | 6F1
126877 | 2013-06-09 | Scheduled Outage | Construction | 8kV transformer X43384 at 16 Cleopatra was isolated to allow crews to replace secondary service. | None | O/H Service | 8 | 34 | 5 | South | 72F4
126878 | 2013-06-09 | Scheduled Outage | Construction | Transformer PT249 at Heron and Bank was isolated to allow crew to install a new service. | None | None | 1 | 50 | 1 | East | ELW11
126879 | 2013-06-09 | Defective Equipment | Defective Equipment/ Material | S827 B phase at 65 Hobart opened due to defective fuse barrel at S827. 67 customers affected | O/H Switchgear | Fused Cutout | 67 | 43 | 48 | South | 84F3
126881 | 2013-06-09 | Defective Equipment | Defective Equipment/ Material | Defective fuse cutout at 83 Holmwood caused transformer X29832 to open | O/H Switchgear | Fused Cutout | 13 | 205 | 44 | Central | SB05
126882 | 2013-06-09 | Defective Equipment | Mechanical Failure | Transformer X12872 at 1481 Jarvis opened due to defective switch at X12872. 3 customers were affected | O/H Switchgear | Fused Cutout | 3 | 451 | 23 | East | 7F2
126883 | 2013-06-10 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE AT SWITCH S173 | O/H Switchgear | Fused Cutout | 18 | 64 | 19 | South | EPWF2
126885 | 2013-06-10 | Defective Equipment | Electrical Failure | Defective transformer TE3517 at 1890 Baseline caused the CB3 to open at SC6396. | U/G Transformer | Padmount (3ph) | 188 | 90 | 282 | South | 87F6
126886 | 2013-06-10 | Scheduled Outage | Construction | Overhead primary reconfiguration for contractor at 61 McEwan | None | None | 1 | 280 | 5 | Central | TD07
126887 | 2013-06-10 | Scheduled Outage | Construction | Moving cable dip | None | None | 12 | 363 | 73 | Central | UN05
126888 | 2013-06-10 | Scheduled Outage | Construction | ISOLATED K1083 TO TRANSFER HYDRO PLANT TO NEW TRANSFORMER | None | None | 12 | 300 | 60 | Central | UN05
126889 | 2013-06-10 | Scheduled Outage | Construction | 13kV transformers 3261W, 3255W and 3256W on Jackson St. Were isolated to allow crews to connect a primary cable in the base of 3261W | None | None | 16 | 6 | 2 | West | 39F3
126891 | 2013-06-10 | Defective Equipment | Electrical Failure | 72F7 tripped and locked out due to a pole fire at S374 (Costco) | Pole | Insulation Failure (Pole Fire) | 24 | 305 | 122 | South | 72F7
126891 | 2013-06-10 | Defective Equipment | Electrical Failure | 72F7 tripped and locked out due to a pole fire at S374 (Costco) | Pole | Insulation Failure (Pole Fire) | 203 | 61 | 206 | South | 72F7
126892 | 2013-06-10 | Defective Equipment | Mechanical Failure | K447 PPH switches were found blown due to defective porcelain switches. | O/H Switchgear | Fused Cutout | 64 | 197 | 210 | East | AN04
126895 | 2013-06-11 | Tree Contacts | Broken Branch | Tree branch at 181 Switzer brought down overhead conductor from Kirkwood feeding to X17840. | O/H Conductor | O/H Conductor | 29 | 68 | 33 | Central | SM16
126895 | 2013-06-11 | Tree Contacts | Broken Branch | Tree branch at 181 Switzer brought down overhead conductor from Kirkwood feeding to X17840. | O/H Conductor | O/H Conductor | 29 | 354 | 171 | Central | SM16
126895 | 2013-06-11 | Tree Contacts | Broken Branch | Tree branch at 181 Switzer brought down overhead conductor from Kirkwood feeding to X17840. | O/H Conductor | O/H Conductor | 433 | 1 | 7 | Central | SM16
126897 | 2013-06-11 | Defective Equipment | Defective Equipment/ Material | Red Phase Cable Fault on the ALEXF3 | U/G Cable | Transition Splice | 34 | 42 | 24 | West | ALEXF3
126897 | 2013-06-11 | Defective Equipment | Defective Equipment/ Material | Red Phase Cable Fault on the ALEXF3 | U/G Cable | Transition Splice | 90 | 22 | 33 | West | ALEXF3
126897 | 2013-06-11 | Defective Equipment | Defective Equipment/ Material | Red Phase Cable Fault on the ALEXF3 | U/G Cable | Transition Splice | 104 | 66 | 114 | West | ALEXF3
126897 | 2013-06-11 | Defective Equipment | Defective Equipment/ Material | Red Phase Cable Fault on the ALEXF3 | U/G Cable | Transition Splice | 244 | 103 | 419 | West | ALEXF3
126900 | 2013-06-12 | Scheduled Outage | Construction | Transformer replacement and cable re-arrangement. | None | None | 8 | 465 | 62 | East | BCHF5
126901 | 2013-06-12 | Defective Equipment | Electrical Failure | blown UN07 cable riser from station to p/p/h switches. | U/G Cable | PILC | 538 | 84 | 753 | Central | UN07
126902 | 2013-06-13 | Defective Equipment | Mechanical Failure | Defective cut-out at S190 caused the fuse to open. | O/H Switchgear | Fused Cutout | 53 | 23 | 20 | South | 180F4
126904 | 2013-06-13 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X24038 TO REPLACE POLE | None | None | 10 | 60 | 10 | East | UT05
126905 | 2013-06-13 | Foreign Interference | Wildlife (Bird/Animal) | Single phase tx at pole X17481 opened due to animal inference. | O/H Transformer | O/H Transformer (1ph) | 6 | 82 | 8 | East | 77M6
126906 | 2013-06-14 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X07583 (RACCOON) | O/H Transformer | O/H Transformer (1ph) | 4 | 410 | 27 | West | MWDF3
126907 | 2013-06-14 | Scheduled Outage | Construction | 4 Kv vault V381 at 205 Gladstone was isolated to allow crew to verify integrity of spare duct from vault to pole for future cable replacement. | None | None | 1 | 55 | 1 | Central | UX07
126909 | 2013-06-15 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X28122 at 1044 Secord Ave. - cause found - squirrel | O/H Transformer | O/H Transformer (1ph) | 14 | 167 | 39 | Central | 505
126910 | 2013-06-15 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X33757 at 1941 Castlewood Ave. - cause found - squirrel | O/H Transformer | O/H Transformer (1ph) | 8 | 174 | 23 | Central | TW22
126911 | 2013-06-15 | Tree Contacts | Tree Growth/ Untrimmed Tree | AK04 tripped due to tree contact and AK07 opened at same time for unknown reason. | O/H Conductor | O/H Conductor | 159 | 70 | 186 | Central | AK04
126911 | 2013-06-15 | Tree Contacts | Tree Growth/ Untrimmed Tree | AK04 tripped due to tree contact and AK07 opened at same time for unknown reason. | O/H Conductor | O/H Conductor | 201 | 91 | 305 | Central | AK04
126911 | 2013-06-15 | Tree Contacts | Tree Growth/ Untrimmed Tree | AK04 tripped due to tree contact and AK07 opened at same time for unknown reason. | O/H Conductor | O/H Conductor | 407 | 106 | 719 | Central | AK07
126911 | 2013-06-15 | Tree Contacts | Tree Growth/ Untrimmed Tree | AK04 tripped due to tree contact and AK07 opened at same time for unknown reason. | O/H Conductor | O/H Conductor | 677 | 116 | 1309 | Central | AK04
126912 | 2013-06-15 | Scheduled Outage | Construction | To replace defective triplex. | None | None | 3 | 54 | 3 | South | 145F3
126914 | 2013-06-16 | Defective Equipment | Mechanical Failure | MWDF2 and 39F3 circuits tripped due to a broken pole causing the MWDF2 circuit to fall into the 39F3 circuit. | Pole | Crossarm | 143 | 3 | 7 | West | MWDF2
126914 | 2013-06-16 | Defective Equipment | Mechanical Failure | MWDF2 and 39F3 circuits tripped due to a broken pole causing the MWDF2 circuit to fall into the 39F3 circuit. | Pole | Crossarm | 286 | 3 | 14 | West | MWDF2
126914 | 2013-06-16 | Defective Equipment | Mechanical Failure | MWDF2 and 39F3 circuits tripped due to a broken pole causing the MWDF2 circuit to fall into the 39F3 circuit. | Pole | Crossarm | 379 | 34 | 215 | West | MWDF2
126914 | 2013-06-16 | Defective Equipment | Mechanical Failure | MWDF2 and 39F3 circuits tripped due to a broken pole causing the MWDF2 circuit to fall into the 39F3 circuit. | Pole | Crossarm | 401 | 161 | 1076 | West | 39F3
126914 | 2013-06-16 | Defective Equipment | Mechanical Failure | MWDF2 and 39F3 circuits tripped due to a broken pole causing the MWDF2 circuit to fall into the 39F3 circuit. | Pole | Crossarm | 660 | 126 | 1386 | West | MWDF2
126914 | 2013-06-16 | Defective Equipment | Mechanical Failure | MWDF2 and 39F3 circuits tripped due to a broken pole causing the MWDF2 circuit to fall into the 39F3 circuit. | Pole | Crossarm | 1641 | 40 | 1094 | West | MWDF2
126915 | 2013-06-16 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X28229 was open due to squirrel contact. | O/H Transformer | O/H Transformer (1ph) | 10 | 74 | 12 | Central | 505
126916 | 2013-06-16 | Loss Of Supply | Transmission Inadvertent | Lightning | None | None | 3344 | 1 | 56 | South | C7BM (Manordale MS - T1/T2)
126916 | 2013-06-16 | Loss Of Supply | Transmission Inadvertent | Lightning | None | None | 3816 | 1 | 64 | South | C7BM (Centrepointe MS - T1/T2)
126922 | 2013-06-16 | Foreign Interference | Vehicle | To place transformer back on its base after motor vehicle accident. | U/G Transformer | Padmount (1ph) | 16 | 130 | 35 | East | LTM01
126923 | 2013-06-16 | Lightning | Lightning | Lightning | Station Equipment | Transformer | 113 | 373 | 702 | West | 28F1
126923 | 2013-06-16 | Lightning | Lightning | Lightning | Station Equipment | Transformer | 211 | 122 | 429 | West | 28F3
126923 | 2013-06-16 | Lightning | Lightning | Lightning | Station Equipment | Transformer | 988 | 391 | 6438 | West | 28F2
126923 | 2013-06-16 | Lightning | Lightning | Lightning | Station Equipment | Transformer | 7537 | 10 | 1256 | West | S7M (Marchwood MTS)
126923 | 2013-06-16 | Lightning | Lightning | Lightning | Station Equipment | Transformer | 10096 | 10 | 1683 | South | S7M (Fallowfield - T1/T2)
126923 | 2013-06-16 | Lightning | Lightning | Lightning | Station Equipment | Transformer | 12097 | 10 | 2016 | West | S7M (Bridlewood MTS - T1/T2)
126926 | 2013-06-17 | Scheduled Outage | Construction | P165 at 376 Elgin isolated to allow crew to replace transformer, cables and cleanup oil. | None | Padmount (3ph) | 11 | 626 | 115 | Central | UX07
126928 | 2013-06-17 | Lightning | Lightning | Customer reported outage, crews refused S23526. customer reported that outage occured during storm, suspect lighting, Fallowfield (FAL01) ID #126928 | O/H Switchgear | Fused Cutout | 1 | 102 | 2 | South | FAL01
126929 | 2013-06-17 | Scheduled Outage | Construction | K1141 was isolated to allow crew to transfer plant. | None | None | 17 | 405 | 115 | Central | UN05
126930 | 2013-06-17 | Unknown/Other | Unknown | CUSTOMER REPORTED OUTAGE - CREWS REFUSED CUTOUT to X31534, 2 customers affected for 173 minutes. Hinchey (TH11) ID #126930 | O/H Switchgear | Fused Cutout | 2 | 173 | 6 | Central | TH11-NIU
126931 | 2013-06-17 | Unknown/Other | Unknown | Customer reported outage, crews refused cutout to X33390. cause unknown 12 customers affected for 65 mninutes. Lincoln Hieghts (TD05) ID #126931 | O/H Switchgear | Fused Cutout | 12 | 65 | 13 | Central | TD05
126932 | 2013-06-17 | Scheduled Outage | Maintenance | Transformer #X18933 opened by crew to change the porcelain insulator | None | None | 18 | 59 | 18 | East | CYRF1
126933 | 2013-06-17 | Foreign Interference | Wildlife (Bird/Animal) | SCADA indicated 249F1 auto-reclosed due to squirel contact at 2709 Stevenage which also blew the G216 red phase. | O/H Switchgear | Fused Cutout | 64 | 145 | 155 | East | LTM01
126934 | 2013-06-17 | Scheduled Outage | Construction | Transformer X15644 at 3101 Analdea Dr. isolated to transfer plant. | None | O/H Transformer (1ph) | 8 | 75 | 10 | East | LTM01
126936 | 2013-06-18 | Scheduled Outage | Construction | cable replacement to V381 | None | None | 1 | 320 | 5 | Central | UX07
126937 | 2013-06-18 | Defective Equipment | Defective Equipment/ Material | At 13:45, 27KV transformer TP2510 at 7 Palomino was isolated to allow crews to relace defective insert. 10 customers affected for 227 minutes. Bridlewood (BRDF1) ID #126937 | U/G Cable Attachement | Elbow \ Insert | 10 | 50 | 8 | West | BRDF1
126938 | 2013-06-18 | Scheduled Outage | Construction | Transformer #X41202 opened by crew to transfer circuits. | None | None | 2 | 10 | 0 | South | 140F4
126939 | 2013-06-18 | Scheduled Outage | Construction | Transformer #X35692 opened by crew for a service upgrade. | None | None | 5 | 70 | 6 | Central | TD12
126940 | 2013-06-18 | Scheduled Outage | Construction | Transformer #X35176 opened by crew for a service upgrade and to relocate triplex | None | None | 7 | 105 | 12 | Central | UL02
126942 | 2013-06-17 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | XLPE | 10 | 180 | 30 | West | BRDF5
126942 | 2013-06-17 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | XLPE | 42 | 98 | 69 | West | BRDF5
126942 | 2013-06-17 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | XLPE | 42 | 201 | 141 | West | BRDF5
126943 | 2013-06-18 | Scheduled Outage | Construction | Transformer P9 at 222 Gladstone was isolated to allow crew to replace primary cable from pole to transformer. | None | None | 1 | 181 | 3 | Central | UX07
126944 | 2013-06-19 | Scheduled Outage | Maintenance | At 08:15am, 8 KV transformer TP9979 was isolated to allow crews to perform oil remediation. 12 customers affected for minutes. Bridlewood (BRDF7) ID #126944 | None | Kiosk (1ph) | 12 | 770 | 154 | West | BRDF7
126945 | 2013-06-19 | Scheduled Outage | Vegetation Management | Tree removal | None | None | 16 | 230 | 61 | East | TB06
126946 | 2013-06-19 | Scheduled Outage | Construction | Transformer #X34448 opened by crew to relocate a service | None | None | 14 | 10 | 2 | Central | TR3UY
126947 | 2013-06-19 | Scheduled Outage | Vegetation Management | Transformer #x35791 opened by crew to drop a service for tree trimming | None | None | 9 | 5 | 1 | Central | TD06
126948 | 2013-06-19 | Foreign Interference | Vehicle | Vehicle broke off pedastal 338P2 isolation of P1 also required to disconnect P2 | U/G Transformer | Unknown \ Other | 3 | 147 | 7 | East | 2207
126948 | 2013-06-19 | Foreign Interference | Vehicle | Vehicle broke off pedastal 338P2 isolation of P1 also required to disconnect P2 | U/G Transformer | Unknown \ Other | 5 | 111 | 9 | East | 2207
126949 | 2013-06-19 | Scheduled Outage | Construction | clean up after oil spill at KT430 | None | None | 15 | 579 | 145 | East | 2206
126950 | 2013-06-19 | Scheduled Outage | Construction | replace the cable dip pole to KT380 | None | None | 5 | 167 | 14 | Central | 303
126951 | 2013-06-19 | Scheduled Outage | Construction | Transformer #X32704 opened by crew to move load over from one phase to another | None | None | 9 | 30 | 4 | Central | UW14
126952 | 2013-06-19 | Scheduled Outage | Construction | Transformer #X32652 opened by crew to move load over from one phase to another | None | None | 8 | 30 | 4 | Central | UW14
126953 | 2013-06-19 | Scheduled Outage | Construction | Transformer #X32653 opened by crew to move load over from one phase to another | None | None | 9 | 30 | 4 | Central | UW14
126954 | 2013-06-19 | Scheduled Outage | Construction | Transformer #X32655 opened by crew to move load over from one phase to another | None | None | 9 | 25 | 4 | Central | UW14
126955 | 2013-06-19 | Foreign Interference | Vehicle | Transformer #KT338 opened by crew to replace 338P2 because it was hit by a truck today | U/G Transformer | Padmount (1ph) | 5 | 19 | 2 | East | 2207
126957 | 2013-06-19 | Scheduled Outage | Maintenance | Transformer #X33451 opened by crew for tree trimming and to replace a service | None | None | 6 | 55 | 6 | South | 190F5
126958 | 2013-06-19 | Scheduled Outage | Construction | At 16:36, 27KV transformer TP2968 at 40 Granite was isolated to allow crews to replace transformer. 1 customer affected for minutes. Alexander (ALEXF3). ID #126958 | None | Kiosk (3ph) | 1 | 146 | 2 | West | ALEXF3
126959 | 2013-06-20 | Scheduled Outage | Maintenance | To change a broken insert | None | None | 10 | 144 | 24 | West | BRDF1
126960 | 2013-06-20 | Scheduled Outage | Maintenance | HOL metering repair | Secondary \ Service | Meter | 1 | 56 | 1 | South | 49F4
126963 | 2013-06-20 | Defective Equipment | Electrical Failure | TB1UQ pothead blew up | U/G Cable Attachement | Pothead | 94 | 35 | 55 | East | TB1UQ
126964 | 2013-06-21 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change an O/H service | None | O/H Conductor | 9 | 36 | 5 | Central | SM03
126965 | 2013-06-21 | Defective Equipment | Defective Equipment/ Material | Cable fault on TL1AM | U/G Cable | PILC | 24 | 41 | 16 | Central | 5211
126965 | 2013-06-21 | Defective Equipment | Defective Equipment/ Material | Cable fault on TL1AM | U/G Cable | PILC | 24 | 41 | 16 | Central | TL6SB
126965 | 2013-06-21 | Defective Equipment | Defective Equipment/ Material | Cable fault on TL1AM | U/G Cable | PILC | 174 | 42 | 122 | Central | 5210
126965 | 2013-06-21 | Defective Equipment | Defective Equipment/ Material | Cable fault on TL1AM | U/G Cable | PILC | 174 | 42 | 122 | Central | TL6TS
126965 | 2013-06-21 | Defective Equipment | Defective Equipment/ Material | Cable fault on TL1AM | U/G Cable | PILC | 1196 | 38 | 757 | Central | TL2SB
126965 | 2013-06-21 | Defective Equipment | Defective Equipment/ Material | Cable fault on TL1AM | U/G Cable | PILC | 1498 | 28 | 699 | Central | TL1AM
126970 | 2013-06-21 | Foreign Interference | Wildlife (Bird/Animal) | Squirell at 2709 Stevenage, O/H red phase transformer X18200, contacted the primary red phase of 249F1 causing the 249F1 breaker to auto reclose twice and blowing the fused cut out at X18200 | O/H Switchgear | Fused Cutout | 4 | 1 | 0 | East | LTM01
126970 | 2013-06-21 | Foreign Interference | Wildlife (Bird/Animal) | Squirell at 2709 Stevenage, O/H red phase transformer X18200, contacted the primary red phase of 249F1 causing the 249F1 breaker to auto reclose twice and blowing the fused cut out at X18200 | O/H Switchgear | Fused Cutout | 4 | 51 | 3 | East | LTM01
126971 | 2013-06-22 | Unknown/Other | Unknown | RX2044 tripped under fault al three phases indicate spike in amp. Crew patrolled circuit and did not find anything. Cause remains under investiagtion | Unknown \ Other | None | 1549 | 110 | 2840 | East | 8F1
126972 | 2013-06-22 | Defective Equipment | Electrical Failure | customer main burning up | Customer Owned | Customer-Owned | 8 | 426 | 57 | South | 145F2
126974 | 2013-06-22 | Defective Equipment | Defective Equipment/ Material | The TA19 CB out of Alion TS tripped open due to underground cable fault between VT224 and VT465 | U/G Cable | XLPE | 64 | 6 | 6 | East | 2208
126974 | 2013-06-22 | Defective Equipment | Defective Equipment/ Material | The TA19 CB out of Alion TS tripped open due to underground cable fault between VT224 and VT465 | U/G Cable | XLPE | 173 | 20 | 58 | East | 2208
126974 | 2013-06-22 | Defective Equipment | Defective Equipment/ Material | The TA19 CB out of Alion TS tripped open due to underground cable fault between VT224 and VT465 | U/G Cable | XLPE | 237 | 34 | 134 | East | 2208
126974 | 2013-06-22 | Defective Equipment | Defective Equipment/ Material | The TA19 CB out of Alion TS tripped open due to underground cable fault between VT224 and VT465 | U/G Cable | XLPE | 801 | 52 | 694 | East | 2208
126976 | 2013-06-22 | Defective Equipment | Mechanical Failure | 77M6 Blue phase cable fault between TP7562 & TP7561. Billberry Creek (77M6) ID #129976 | U/G Cable | XLPE | 39 | 12 | 8 | East | 77M6
126976 | 2013-06-22 | Defective Equipment | Mechanical Failure | 77M6 Blue phase cable fault between TP7562 & TP7561. Billberry Creek (77M6) ID #129976 | U/G Cable | XLPE | 152 | 131 | 332 | East | 77M6
126981 | 2013-06-23 | Loss Of Supply | Transmission Inadvertent | OGCC reported loss of the supply - H1 crews dispatched to close inline reclosure on 44KV feeding Greenland station 30 transfer customers affected | None | None | 30 | 95 | 48 | West | GNLF2
126982 | 2013-06-23 | Tree Contacts | Tree Growth/ Untrimmed Tree | fuse cutout to X37233 found blown, suspect tree contact during thunderstorm. 10 customers affected for 136 minutes. | O/H Transformer | O/H Transformer (1ph) | 10 | 136 | 23 | South | EPWF3
126983 | 2013-06-24 | Foreign Interference | Dig-In | Not yet known. | U/G Cable | PILC | 358 | 37 | 221 | Central | TL3SB
126984 | 2013-06-24 | Foreign Interference | Wildlife (Bird/Animal) | Not yet known. | O/H Transformer | O/H Transformer (1ph) | 20 | 52 | 17 | East | 8F1
126984 | 2013-06-24 | Foreign Interference | Wildlife (Bird/Animal) | Not yet known. | O/H Transformer | O/H Transformer (1ph) | 98 | 100 | 163 | East | 8F1
126985 | 2013-06-24 | Defective Equipment | Mechanical Failure | RX2044 defective recloser | O/H Switchgear | Vega Switch | 584 | 45 | 438 | East | 8F1
126985 | 2013-06-24 | Defective Equipment | Mechanical Failure | RX2044 defective recloser | O/H Switchgear | Vega Switch | 3000 | 35 | 1750 | East | 77M5
126986 | 2013-06-24 | Loss Of Supply | Transmission Inadvertent | Hydro C7BM Circuit tripped causing an outage to the Centrepointe DS, and Manordale DS | None | None | 8116 | 8 | 1082 | South | C7BM (Centrepointe MS - T1/T2)
126987 | 2013-06-24 | Scheduled Outage | Construction | Transformer #X32705 opened by crew for load transfer | None | None | 10 | 40 | 7 | Central | UW14
126988 | 2013-06-24 | Lightning | Lightning | Not yet known. | None | None | 3000 | 1 | 50 | West | JKGF4
126988 | 2013-06-24 | Lightning | Lightning | Not yet known. | None | None | 4000 | 1 | 67 | West | A9M3
126993 | 2013-06-24 | Scheduled Outage | Construction | Transformer #X29206 opened by crew for a pole replacement | None | None | 1 | 195 | 3 | East | UT05
126994 | 2013-06-24 | Defective Equipment | Defective Equipment/ Material | Defective transformer TP7606 | U/G Transformer | Padmount (1ph) | 9 | 295 | 44 | East | 77M2
126994 | 2013-06-24 | Defective Equipment | Defective Equipment/ Material | Defective transformer TP7606 | U/G Transformer | Padmount (1ph) | 16 | 21 | 6 | East | 77M2
126994 | 2013-06-24 | Defective Equipment | Defective Equipment/ Material | Defective transformer TP7606 | U/G Transformer | Padmount (1ph) | 55 | 160 | 147 | East | 77M2
126995 | 2013-06-24 | Adverse Weather | Extreme Wind | Tree contact due to high winds. | O/H Switchgear | Fused Cutout | 1 | 356 | 6 | East | 7F4
126996 | 2013-06-24 | Human Element | Improper Construction/installation | commishoning error | None | None | 2 | 65 | 2 | Central | UF00
126997 | 2013-06-25 | Scheduled Outage | Maintenance | maintenance | None | None | 1 | 172 | 3 | Central | 415
126998 | 2013-06-25 | Scheduled Outage | Forced Switching | collapsed duct bank inspection | None | None | 3 | 60 | 3 | Central | TS1AM
127002 | 2013-06-25 | Scheduled Outage | Construction | 4kV transformer X30348 isolated to allow crews to transfer services to new bus | None | O/H Service | 1 | 240 | 4 | Central | UX07
127003 | 2013-06-25 | Adverse Weather | Extreme Wind | Wind gusts | None | None | 393 | 20 | 131 | East | UA02
127004 | 2013-06-25 | Scheduled Outage | Construction | 8Kv overhead circuits from S27860 and S20081 to EOL on Tisdale were isolated for pole replacement | None | Pole | 190 | 401 | 1270 | East | BCHF5
127004 | 2013-06-25 | Scheduled Outage | Construction | 8Kv overhead circuits from S27860 and S20081 to EOL on Tisdale were isolated for pole replacement | None | Pole | 321 | 401 | 2145 | East | BCHF3
127007 | 2013-06-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | G59R opened due to tree contact. | O/H Conductor | O/H Conductor | 13 | 84 | 18 | East | BLKF5
127009 | 2013-06-25 | Loss Of Supply | Transmission Inadvertent | Lightning in area. C7BM restored from Merivale to South March north west end of circuit remains out. All Hydro Ottawa load restored. | None | None | 8116 | 3 | 406 | South | 87F1
127011 | 2013-06-25 | Defective Equipment | Electrical Failure | replace defective transformer | Vault Equipment | Transformer | 1 | 92 | 2 | East | AE07
127012 | 2013-06-26 | Defective Equipment | Defective Equipment/ Material | Defective transformer at V343 | Vault Equipment | Transformer | 1 | 686 | 11 | Central | SB06
127013 | 2013-06-26 | Scheduled Outage | Construction | planned work to transfer UX07 load to UX08 circuit. | None | None | 119 | 315 | 625 | Central | UX07
127014 | 2013-06-26 | Scheduled Outage | Maintenance | 8Kv transfomrer TP2521 and 177 Palimo Dr. Was isolated to allow crews to clean sand out of the base. | None | Padmount (1ph) | 8 | 177 | 24 | West | BRDF1
127015 | 2013-06-26 | Scheduled Outage | Construction | PCB transformer replacement | None | None | 1 | 351 | 6 | Central | UX09
127016 | 2013-06-26 | Tree Contacts | Tree Growth/ Untrimmed Tree | 8kV fuse G59R on Ridge Rd. Opened due to tree contact. Line isolated and tree crew dispatched to clear the ROW | O/H Conductor | O/H Conductor | 13 | 322 | 70 | East | BLKF5
127017 | 2013-06-26 | Scheduled Outage | Construction | 8kV transfomers TP7795, TP6931, TP6930 were isolated to allow crews to pull primary cable. | None | Padmount (1ph) | 25 | 196 | 82 | East | 7F4
127020 | 2013-06-26 | Tree Contacts | Broken Branch | Transformer #X23272 opened by crew for Forestry crew to remove branch from open wire buss | None | None | 6 | 25 | 2 | Central | TK2AC
127021 | 2013-06-26 | Scheduled Outage | Forced Switching | Transformer PT110 at 2020 Bantree was isolated to allow crew to make repairs to SW131 cable termination. | None | Termination \ Stress Cone | 1 | 376 | 6 | East | 5301
127022 | 2013-06-26 | Defective Equipment | Defective Equipment/ Material | Transformer #X35755 opened up due to a defective transformer. On call replaced it. | O/H Transformer | O/H Transformer (1ph) | 1 | 372 | 6 | West | 43F2
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 33 | 25 | 14 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 47 | 25 | 20 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 66 | 15 | 16 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 84 | 40 | 56 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 100 | 16 | 27 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 323 | 12 | 65 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 399 | 7 | 47 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 437 | 8 | 58 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 479 | 2 | 16 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 511 | 5 | 43 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 540 | 9 | 81 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 540 | 19 | 171 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 540 | 23 | 207 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 540 | 77 | 693 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 1152 | 2 | 38 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 1152 | 4 | 77 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 1152 | 6 | 115 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 1152 | 12 | 230 | South | 84F5
127023 | 2013-06-27 | Defective Equipment | Defective Equipment/ Material | 84F5 blue phase cable fault between TE617 & TE619 caused the 84F5 breaker to trip. Circuit sectionalized and circuit debugged through breaker operation & cable hipot | U/G Cable | XLPE | 1152 | 57 | 1094 | South | 84F5
127024 | 2013-06-27 | Foreign Interference | Wildlife (Bird/Animal) | Squirell got into a 13kv O/H transformer X32800 at 918 Winnington | O/H Switchgear | Fused Cutout | 13 | 29 | 6 | Central | TW22
127024 | 2013-06-27 | Foreign Interference | Wildlife (Bird/Animal) | Squirell got into a 13kv O/H transformer X32800 at 918 Winnington | O/H Switchgear | Fused Cutout | 22 | 7 | 3 | Central | TW22
127024 | 2013-06-27 | Foreign Interference | Wildlife (Bird/Animal) | Squirell got into a 13kv O/H transformer X32800 at 918 Winnington | O/H Switchgear | Fused Cutout | 45 | 194 | 146 | Central | TW22
127028 | 2013-06-27 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X27087 at 533 Brownrigg Ave., cause - squirrel | O/H Transformer | O/H Transformer (1ph) | 10 | 106 | 18 | East | TB14
127030 | 2013-06-28 | Foreign Interference | Wildlife (Bird/Animal) | S1271 found blown due to animal contact at X36542. | O/H Switchgear | Inline Switch | 11 | 102 | 19 | South | EPWF3
127032 | 2013-06-28 | Defective Equipment | Defective Equipment/ Material | Replaced broken switch S26221 at 826 High St. | O/H Switchgear | Fused Cutout | 17 | 141 | 40 | Central | TD12
127033 | 2013-06-28 | Scheduled Outage | Forced Switching | 13kV transfomrer X35637 at 82 Ritchie St. opened by crews due to a pole fire at that location. | None | Insulation Failure (Pole Fire) | 16 | 252 | 67 | Central | TD12
127035 | 2013-06-29 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #GL5965 opened up due to bird contact | O/H Transformer | O/H Transformer (1ph) | 9 | 159 | 24 | East | LTM01
127036 | 2013-06-29 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35529 opened up due to squirrel contact | O/H Transformer | O/H Transformer (1ph) | 4 | 155 | 10 | Central | TW22
127039 | 2013-06-29 | Foreign Interference | Customer-Cut Trees | Home owner was cut trees and tree limbs fell into conductor. | O/H Conductor | O/H Conductor | 17 | 390 | 110 | East | UZ12
127040 | 2013-06-30 | Defective Equipment | Defective Equipment/ Material | defective fuse | O/H Switchgear | Fused Cutout | 17 | 120 | 34 | West | 624F6
127043 | 2013-07-01 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X29978 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 5 | 66 | 6 | Central | TR09
127044 | 2013-07-02 | Scheduled Outage | Construction | Transformers TP9445 and TP9444 on Grey Nuns were isolated to allow crew to replace cables and inserts. 21 customers were interrupted for 222 minutes. Bilberry Creek (77M1) ID# 127044. | None | None | 21 | 222 | 78 | East | 77M1
127046 | 2013-07-02 | Scheduled Outage | Construction | Transformer X29859 isolated to transfer plant | None | None | 8 | 190 | 25 | Central | TR09
127049 | 2013-07-02 | Scheduled Outage | Maintenance | To Repair Broken Insert Pin | U/G Cable Attachement | Elbow \ Insert | 9 | 79 | 12 | West | BRDF1
127050 | 2013-07-02 | Foreign Interference | Wildlife (Bird/Animal) | At 21:20, customer reported outage. Crews found fused cutout to X24979 to blown due to animal contact (crow) Currently fed from Bilberry (77M5) | O/H Switchgear | Fused Cutout | 1 | 130 | 2 | East | 8F1
127051 | 2013-07-03 | Defective Equipment | Mechanical Failure | 77M6 A/R & RX2043 tripped. Circuit was picked up one section at a time. To be patrolled. After patrol, crew reports cause of outage is a blown arrestor at RX2053. | Pole Attachement | Arrester | 1589 | 1 | 26 | East | 77M6
127051 | 2013-07-03 | Defective Equipment | Mechanical Failure | 77M6 A/R & RX2043 tripped. Circuit was picked up one section at a time. To be patrolled. After patrol, crew reports cause of outage is a blown arrestor at RX2053. | Pole Attachement | Arrester | 1767 | 1 | 29 | East | 77M6
127051 | 2013-07-03 | Defective Equipment | Mechanical Failure | 77M6 A/R & RX2043 tripped. Circuit was picked up one section at a time. To be patrolled. After patrol, crew reports cause of outage is a blown arrestor at RX2053. | Pole Attachement | Arrester | 1851 | 20 | 617 | East | 77M6
127054 | 2013-07-03 | Scheduled Outage | Maintenance | Cable and Transformer insert replacement | None | None | 25 | 256 | 107 | East | 77M1
127055 | 2013-07-03 | Scheduled Outage | Construction | Transformer X32769 was isolated to allow crew to install new poles. | None | None | 10 | 150 | 25 | Central | UW14
127056 | 2013-07-03 | Scheduled Outage | Construction | Transformer X32768 was isolated to allow crew to install new poles. | None | None | 10 | 136 | 23 | Central | UW14
127060 | 2013-07-03 | Defective Equipment | Defective Equipment/ Material | At 19:42, OMS reported outage, crews found blown elbow at TE1431. 36 customers affected for 88 minutes. Startop (6F1) ID #127060 | U/G Cable Attachement | Elbow \ Insert | 36 | 88 | 53 | East | 6F1
127062 | 2013-07-04 | Scheduled Outage | Maintenance | To replace a broken elbow & insert | None | Elbow \ Insert | 10 | 87 | 14 | West | BRDF1
127063 | 2013-07-04 | Scheduled Outage | Vegetation Management | 13kV overhead circuit from S21395 to EOL isolated for tree removal. | None | O/H Conductor | 24 | 274 | 110 | Central | TD01
127065 | 2013-07-04 | Defective Equipment | Mechanical Failure | TE1431 broken insert | U/G Cable Attachement | Elbow \ Insert | 12 | 80 | 16 | East | 6F1
127067 | 2013-07-05 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to complete a new service connection | None | None | 29 | 131 | 63 | South | FAL02
127069 | 2013-07-05 | Defective Equipment | Electrical Failure | 5210 circuit tripped due to defective switchgear at VT548. VT548 was isolated to allow customer's contractor to make necessary repairs. | Customer Owned | Customer-Owned | 111 | 955 | 1767 | Central | 5210
127069 | 2013-07-05 | Defective Equipment | Electrical Failure | 5210 circuit tripped due to defective switchgear at VT548. VT548 was isolated to allow customer's contractor to make necessary repairs. | Customer Owned | Customer-Owned | 346 | 29 | 167 | Central | 5210
127069 | 2013-07-05 | Defective Equipment | Electrical Failure | 5210 circuit tripped due to defective switchgear at VT548. VT548 was isolated to allow customer's contractor to make necessary repairs. | Customer Owned | Customer-Owned | 349 | 79 | 460 | Central | 5210
127070 | 2013-07-06 | Defective Equipment | Mechanical Failure | 210F2 tripped open and S7039 red phase was found blown due to a blown insert at TE2554. | U/G Cable Attachement | Elbow \ Insert | 9 | 220 | 33 | South | LGFF2
127070 | 2013-07-06 | Defective Equipment | Mechanical Failure | 210F2 tripped open and S7039 red phase was found blown due to a blown insert at TE2554. | U/G Cable Attachement | Elbow \ Insert | 83 | 9 | 12 | South | LGFF2
127070 | 2013-07-06 | Defective Equipment | Mechanical Failure | 210F2 tripped open and S7039 red phase was found blown due to a blown insert at TE2554. | U/G Cable Attachement | Elbow \ Insert | 181 | 81 | 244 | South | LGFF2
127070 | 2013-07-06 | Defective Equipment | Mechanical Failure | 210F2 tripped open and S7039 red phase was found blown due to a blown insert at TE2554. | U/G Cable Attachement | Elbow \ Insert | 2909 | 26 | 1261 | South | LGFF2
127071 | 2013-07-06 | Foreign Interference | Wildlife (Bird/Animal) | crews report G30R blown, patrolled line and found signs of animal contact & fused cutout blown at X15882. refused | O/H Switchgear | Fused Cutout | 49 | 68 | 56 | East | 7F4
127073 | 2013-07-06 | Foreign Interference | Wildlife (Bird/Animal) | crews reports 88W open, patrol found BIRD CONTACT AT X39846, FUSED CUTOUT & SWITCH 88W REFUSE. 25 customers for 166 minuts. Marchwood (MWDF3) ID #127073 | O/H Switchgear | Fused Cutout | 25 | 166 | 69 | West | MWDF3
127074 | 2013-07-06 | Foreign Interference | Wildlife (Bird/Animal) | S23476W feeding WX2051 found blown due to bird contact. 27 customers affected for 90 minutes. Limebank (7F2) ID #127074 | O/H Switchgear | Fused Cutout | 27 | 90 | 40 | East | 7F2
127075 | 2013-07-06 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X42020 (Crow) | O/H Transformer | O/H Transformer (1ph) | 1 | 249 | 4 | East | 77M2
127076 | 2013-07-07 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X36346 fuse blew due to racoon contact. | O/H Transformer | O/H Transformer (1ph) | 6 | 58 | 6 | West | JKGF5
127077 | 2013-07-07 | Scheduled Outage | Construction | To replace pole X46001 | None | Pole | 7 | 179 | 21 | East | UT05
127078 | 2013-07-07 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X39180 (CROW) | O/H Transformer | O/H Transformer (1ph) | 1 | 113 | 2 | South | 140F4
127079 | 2013-07-07 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X43929 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 19 | 152 | 48 | Central | TR3UY
127080 | 2013-07-07 | Defective Equipment | Electrical Failure | REPLACED PRIMARY LEAD AT POLE X38642 FEEDING S22947 (LEAD BURNT OFF) | O/H Conductor | Hot-Line Clamp | 42 | 73 | 51 | West | 28F2
127083 | 2013-07-07 | Defective Equipment | Mechanical Failure | crews found S151 red phase blown due to defective hot line clamp at 12 oakwood. 64 customers affected for minutes. Parkwood hills ID #127083 | O/H Conductor | Hot-Line Clamp | 64 | 165 | 176 | South | 190F5
127084 | 2013-07-07 | Foreign Interference | Wildlife (Bird/Animal) | X39846 blown from animal contact | O/H Switchgear | Fused Cutout | 25 | 47 | 20 | West | MWDF3
127085 | 2013-07-07 | Foreign Interference | Wildlife (Bird/Animal) | An animal contact caused the fuse to blow that feeds transformer X36091. | O/H Transformer | O/H Transformer (1ph) | 16 | 49 | 13 | Central | TD05
127087 | 2013-07-08 | Tree Contacts | Other Vegetation | vegitation issue | O/H Switchgear | Fused Cutout | 1 | 34 | 1 | South | 72F7
127089 | 2013-07-08 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X10728 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 4 | 120 | 8 | West | 29F1
127091 | 2013-07-08 | Scheduled Outage | Construction | Re-arrange o/h plant | None | None | 15 | 200 | 50 | Central | UX03
127092 | 2013-07-08 | Defective Equipment | Defective Equipment/ Material | Transformer X35864 at 21 Newbury Ave. isolated to replace triplex to 2 services on Meadowlands Dr. | Secondary \ Service | O/H Service | 16 | 168 | 45 | South | 190F5
127093 | 2013-07-09 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact caused fuse at X27136 to open. | O/H Transformer | O/H Transformer (1ph) | 4 | 110 | 7 | East | TB06
127094 | 2013-07-09 | Scheduled Outage | Construction | X30344 at 344 Gladeston isolated for pole change. | None | Pole | 5 | 189 | 16 | Central | UF10
127095 | 2013-07-09 | Scheduled Outage | Maintenance | TP10004 at 79 Seabrooke was isolated to allow crew to perform soil remediation and install new transformer base. | None | Padmount (1ph) | 9 | 407 | 61 | West | BRDF5
127097 | 2013-07-09 | Scheduled Outage | Construction | Installing poles Transformer X32657 was isolated in order to set new poles | None | O/H Transformer (1ph) | 1 | 154 | 3 | Central | UW14
127098 | 2013-07-09 | Scheduled Outage | Maintenance | Replace transformer ground Transformer X35191 was isolated in order to replace transformer grounding | None | Ground | 9 | 34 | 5 | Central | AH02
127100 | 2013-07-09 | Scheduled Outage | Construction | Transformer X32650 at 1165 Gateway Rd. isolated for installation of new poles. | None | None | 7 | 300 | 35 | Central | UW14
127101 | 2013-07-09 | Scheduled Outage | Construction | Transformer X32651 at 1139 Gateway Rd isolated for installation of new poles. | None | None | 17 | 300 | 85 | Central | UW14
127103 | 2013-07-09 | Tree Contacts | Other Vegetation | Transformer X37076 at 37 Grenfell Ave. isolated to remove vines from transformer | None | None | 1 | 17 | 0 | South | 72F7
127104 | 2013-07-09 | Scheduled Outage | Construction | G796 to EOL feeding Rogers Tower at 2244 Inness was isolated to allow contractor to install cew new cales from exiting O/H to new transformer and install secondary connection to new transformer. | None | None | 1 | 1431 | 24 | East | BLKF4
127105 | 2013-07-10 | Scheduled Outage | Maintenance | Transformer TP6961 at 1456 Foxwell was isolated to allow crew to remove transformer for soil remediation | None | Padmount (1ph) | 12 | 391 | 78 | East | 6F1
127106 | 2013-07-10 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X34270 at 1852 Carling Ave. - animal contact | None | None | 7 | 57 | 7 | Central | TD01
127109 | 2013-07-11 | Scheduled Outage | Maintenance | VE4 at 15 Woodridge was isolated to allow crew to Metering repairs. | None | None | 1 | 47 | 1 | East | BLKF4
127110 | 2013-07-11 | Scheduled Outage | Maintenance | To change inserts | None | None | 18 | 71 | 21 | West | BRDF4
127112 | 2013-07-12 | Scheduled Outage | Construction | 3 phase transformer upgrade | None | O/H Transformer (3ph) | 3 | 180 | 9 | East | V11F2
127113 | 2013-07-12 | Scheduled Outage | Construction | Decommisioning of old transformer and energization of new transformer | None | None | 1 | 166 | 3 | East | BCHF5
127114 | 2013-07-12 | Scheduled Outage | Construction | Set Poles | None | None | 7 | 210 | 24 | East | UT06
127115 | 2013-07-13 | Defective Equipment | Defective Equipment/ Material | Defective elbow at TP5893 caused the 140F4 CB to A/R and blow S1114W phase | U/G Cable Attachement | Elbow \ Insert | 8 | 282 | 38 | South | 140F4
127115 | 2013-07-13 | Defective Equipment | Defective Equipment/ Material | Defective elbow at TP5893 caused the 140F4 CB to A/R and blow S1114W phase | U/G Cable Attachement | Elbow \ Insert | 24 | 43 | 17 | South | 140F4
127115 | 2013-07-13 | Defective Equipment | Defective Equipment/ Material | Defective elbow at TP5893 caused the 140F4 CB to A/R and blow S1114W phase | U/G Cable Attachement | Elbow \ Insert | 25 | 123 | 51 | South | 140F4
127116 | 2013-07-13 | Scheduled Outage | Construction | 13kV vault VT53 at 250 Tremblay isolated to allow underground crew to terminates new cables inside vault. | None | PILC | 1 | 568 | 9 | East | 1807
127118 | 2013-07-14 | Scheduled Outage | Construction | 13kV vault VT53 at 250 Tremblay was isolated to allow crews o terminate in cables at the riser. | None | PILC | 1 | 436 | 7 | East | 1807
127119 | 2013-07-14 | Defective Equipment | Defective Equipment/ Material | Transformer X31322 isolated to replace one leg of O/H bus burnt off at ampact connection. Spliced in new piece. | Secondary \ Service | O/H Service | 39 | 109 | 71 | Central | SB16
127120 | 2013-07-14 | Tree Contacts | Broken Branch | Tree contact at pole X06225 at 2770 Prince of Whales caused 180F4 CB to auto reclose and open. Affected section of overhead isolated to allow crews to clear the tree. | O/H Conductor | O/H Conductor | 20 | 203 | 68 | South | 180F4
127120 | 2013-07-14 | Tree Contacts | Broken Branch | Tree contact at pole X06225 at 2770 Prince of Whales caused 180F4 CB to auto reclose and open. Affected section of overhead isolated to allow crews to clear the tree. | O/H Conductor | O/H Conductor | 866 | 54 | 779 | South | 180F4
127121 | 2013-07-14 | Scheduled Outage | Construction | relocation of the overhead conductor for road widening | None | None | 8 | 319 | 43 | South | 47F2
127124 | 2013-07-14 | Defective Equipment | Defective Equipment/ Material | Primary overhead conductor down and broken crossarm | O/H Conductor | O/H Conductor | 222 | 456 | 1687 | Central | UW07
127125 | 2013-07-15 | Foreign Interference | Wildlife (Bird/Animal) | crow at overhead transformer X09339. | None | None | 5 | 134 | 11 | West | ALEXF3
127125 | 2013-07-15 | Foreign Interference | Wildlife (Bird/Animal) | crow at overhead transformer X09339. | None | None | 3590 | 11 | 658 | West | ALEXF3
127126 | 2013-07-15 | Scheduled Outage | Construction | 13kV vaults VT788, VT789 and transformers KT510 and KT511 isolated to allow crews to install new riser switches and replace leaking transformer at KT511. | None | Kiosk (3ph) | 8 | 310 | 41 | Central | TH06
127126 | 2013-07-15 | Scheduled Outage | Construction | 13kV vaults VT788, VT789 and transformers KT510 and KT511 isolated to allow crews to install new riser switches and replace leaking transformer at KT511. | None | Kiosk (3ph) | 52 | 70 | 61 | Central | TH06
127127 | 2013-07-15 | Scheduled Outage | Maintenance | Remove asbestos, replace broken switches and porcelain | None | None | 8 | 91 | 12 | East | AQ06
127128 | 2013-07-15 | Defective Equipment | Electrical Failure | Cable fault inside VT868 caused TR23 CB to open. | Vault Equipment | Cable | 399 | 10 | 66 | Central | 503
127128 | 2013-07-15 | Defective Equipment | Electrical Failure | Cable fault inside VT868 caused TR23 CB to open. | Vault Equipment | Cable | 412 | 41 | 282 | Central | 503
127129 | 2013-07-15 | Defective Equipment | Defective Equipment/ Material | Blown insert elbow at TE2696 | U/G Transformer | Padmount (1ph) | 22 | 217 | 80 | East | CYRF4
127129 | 2013-07-15 | Defective Equipment | Defective Equipment/ Material | Blown insert elbow at TE2696 | U/G Transformer | Padmount (1ph) | 170 | 120 | 340 | East | CYRF4
127130 | 2013-07-16 | Scheduled Outage | Construction | Replace a defective transformer & cleanup the concrete pad | U/G Transformer | Kiosk (1ph) | 11 | 101 | 19 | Central | TD14
127131 | 2013-07-16 | Scheduled Outage | Maintenance | Transformer K418 & K419 was isolated for TDR cable testing. | None | Unknown \ Other | 35 | 474 | 276 | East | AN05
127133 | 2013-07-16 | Defective Equipment | Defective Equipment/ Material | Blown fuse in vault | Vault Equipment | Transformer | 1 | 374 | 6 | Central | UX03
127134 | 2013-07-16 | Scheduled Outage | Construction | To replace leaking transformer at TE3668 | None | Unknown \ Other | 13 | 76 | 16 | East | 7F2
127135 | 2013-07-16 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to place the transformer back on its base after it was hit by a truck | None | None | 1 | 11 | 0 | East | UT07
127136 | 2013-07-16 | Scheduled Outage | Construction | ISOLATED SWITCH P308 FEEDING PADMOUNT TRANSFORMER P308 TO TRANSFER SWITCH TO NEW POLE | None | None | 2 | 180 | 6 | Central | SA23
127137 | 2013-07-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31010 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 4 | 180 | 12 | Central | SA23
127138 | 2013-07-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31014 TO TRANSFER HDYRO PLANT TO NEW POLE | None | None | 10 | 180 | 30 | Central | SA23
127140 | 2013-07-16 | Scheduled Outage | Maintenance | Soil remediation | None | None | 7 | 519 | 61 | East | 77M2
127141 | 2013-07-16 | Scheduled Outage | Maintenance | Soil remediation. | None | None | 5 | 332 | 28 | West | BRDF4
127142 | 2013-07-16 | Foreign Interference | Customer-Cut Trees | Tree contractor dropped tree on our wires and took them down. | O/H Conductor | O/H Conductor | 19 | 274 | 87 | South | 180F4
127145 | 2013-07-16 | Defective Equipment | Mechanical Failure | 249F1 auto-reclosed and G321 blew due to a guy wire falling into conductor and a defective fused cutout at X15351. | O/H Switchgear | Fused Cutout | 0 | 2 | 0 | East | LTM01
127145 | 2013-07-16 | Defective Equipment | Mechanical Failure | 249F1 auto-reclosed and G321 blew due to a guy wire falling into conductor and a defective fused cutout at X15351. | O/H Switchgear | Fused Cutout | 9 | 53 | 8 | East | LTM01
127145 | 2013-07-16 | Defective Equipment | Mechanical Failure | 249F1 auto-reclosed and G321 blew due to a guy wire falling into conductor and a defective fused cutout at X15351. | O/H Switchgear | Fused Cutout | 68 | 37 | 42 | East | LTM01
127145 | 2013-07-16 | Defective Equipment | Mechanical Failure | 249F1 auto-reclosed and G321 blew due to a guy wire falling into conductor and a defective fused cutout at X15351. | O/H Switchgear | Fused Cutout | 68 | 187 | 212 | East | LTM01
127145 | 2013-07-16 | Defective Equipment | Mechanical Failure | 249F1 auto-reclosed and G321 blew due to a guy wire falling into conductor and a defective fused cutout at X15351. | O/H Switchgear | Fused Cutout | 3669 | 1 | 61 | East | LTM01
127146 | 2013-07-16 | Defective Equipment | Defective Equipment/ Material | Defective overhead transformer X24089 | O/H Transformer | O/H Transformer (1ph) | 13 | 359 | 78 | East | 7F4
127146 | 2013-07-16 | Defective Equipment | Defective Equipment/ Material | Defective overhead transformer X24089 | O/H Transformer | O/H Transformer (1ph) | 55 | 217 | 199 | East | 7F4
127146 | 2013-07-16 | Defective Equipment | Defective Equipment/ Material | Defective overhead transformer X24089 | O/H Transformer | O/H Transformer (1ph) | 325 | 33 | 179 | East | 7F4
127147 | 2013-07-16 | Defective Equipment | Electrical Failure | 249F1 auto-reclosed due to defective transformer X14462 at 1719 Rosebella | O/H Transformer | O/H Transformer (1ph) | 10 | 131 | 22 | East | LTM01
127147 | 2013-07-16 | Defective Equipment | Electrical Failure | 249F1 auto-reclosed due to defective transformer X14462 at 1719 Rosebella | O/H Transformer | O/H Transformer (1ph) | 10 | 269 | 45 | East | LTM01
127147 | 2013-07-16 | Defective Equipment | Electrical Failure | 249F1 auto-reclosed due to defective transformer X14462 at 1719 Rosebella | O/H Transformer | O/H Transformer (1ph) | 3610 | 4 | 241 | East | LTM01
127149 | 2013-07-17 | Scheduled Outage | Construction | To allow a contractor to remove asbestos & perform vault maintenance. Also to allow Hydro Ottawa crews to change out PCB transformers | None | None | 1 | 262 | 4 | Central | AM04
127151 | 2013-07-17 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMERS X32652, X32653 AND X62354 TO INSTALL NEW POLES | None | None | 21 | 150 | 52 | Central | UW14
127154 | 2013-07-17 | Human Element | Commissioning Error | Commisioning Error | None | None | 635 | 4 | 42 | West | BECKF2
127159 | 2013-07-17 | Defective Equipment | Defective Equipment/ Material | The 249F1 auto reclosed , the fuse that feeds transformer X15351 also blew, when the crew went to refuse X15351 it auto the 249F1 and blew G321B 3 ORVILLE KEMP ST | O/H Transformer | O/H Transformer (1ph) | 9 | 39 | 6 | East | LTM01
127159 | 2013-07-17 | Defective Equipment | Defective Equipment/ Material | The 249F1 auto reclosed , the fuse that feeds transformer X15351 also blew, when the crew went to refuse X15351 it auto the 249F1 and blew G321B 3 ORVILLE KEMP ST | O/H Transformer | O/H Transformer (1ph) | 9 | 158 | 24 | East | LTM01
127159 | 2013-07-17 | Defective Equipment | Defective Equipment/ Material | The 249F1 auto reclosed , the fuse that feeds transformer X15351 also blew, when the crew went to refuse X15351 it auto the 249F1 and blew G321B 3 ORVILLE KEMP ST | O/H Transformer | O/H Transformer (1ph) | 68 | 27 | 31 | East | LTM01
127160 | 2013-07-17 | Lightning | Lightning | Lightning in the area caused the fuse to blow at 443. | O/H Conductor | Unknown \ Other | 27 | 96 | 43 | West | 28F3
127161 | 2013-07-17 | Lightning | Lightning | Lightning in the area caused S17705 to crew patrolled nothing found. | O/H Switchgear | Inline Switch | 2 | 98 | 3 | West | 43F3
127162 | 2013-07-17 | Lightning | Lightning | Lightning in the area caused the RX2038 to trip under hold off | O/H Conductor | Unknown \ Other | 11 | 138 | 25 | West | BECKF2
127163 | 2013-07-18 | Foreign Interference | Dig-In | Dig in on primary cble at S3-8 to TE266 by backhoe by Bradley Kelly | U/G Cable | Unknown \ Other | 26 | 12 | 5 | South | 190F6
127163 | 2013-07-18 | Foreign Interference | Dig-In | Dig in on primary cble at S3-8 to TE266 by backhoe by Bradley Kelly | U/G Cable | Unknown \ Other | 53 | 4 | 4 | South | 190F6
127163 | 2013-07-18 | Foreign Interference | Dig-In | Dig in on primary cble at S3-8 to TE266 by backhoe by Bradley Kelly | U/G Cable | Unknown \ Other | 169 | 71 | 200 | South | 190F6
127165 | 2013-07-18 | Foreign Interference | Vehicle | Dump Truck came in contact with O/H Primary at Earl Armstrong and High Rd causing the G823B and G263B to open | O/H Conductor | O/H Conductor | 2 | 40 | 1 | East | 7F4
127165 | 2013-07-18 | Foreign Interference | Vehicle | Dump Truck came in contact with O/H Primary at Earl Armstrong and High Rd causing the G823B and G263B to open | O/H Conductor | O/H Conductor | 6 | 42 | 4 | East | 7F4
127169 | 2013-07-18 | Adverse Environment | Fire | TE1525 secondary at 46 Auriga was opened by request of fire department due fire at 46 Aurigua | None | None | 1 | 972 | 16 | South | 180F3
127209 | 2013-07-20 | Adverse Weather | Extreme Wind | To remove tree from the overhead | None | None | 14 | 86 | 20 | East | TB06
127212 | 2013-07-20 | Defective Equipment | Mechanical Failure | Defective switch S414 white phase | O/H Switchgear | Fused Cutout | 34 | 211 | 120 | West | JKGF5
127213 | 2013-07-20 | Adverse Environment | Fire | Transformer X44491 caught fire. | O/H Transformer | O/H Transformer (1ph) | 24 | 39 | 16 | Central | UJ03
127213 | 2013-07-20 | Adverse Environment | Fire | Transformer X44491 caught fire. | O/H Transformer | O/H Transformer (1ph) | 24 | 287 | 115 | Central | UJ03
127213 | 2013-07-20 | Adverse Environment | Fire | Transformer X44491 caught fire. | O/H Transformer | O/H Transformer (1ph) | 160 | 37 | 99 | Central | AM06
127213 | 2013-07-20 | Adverse Environment | Fire | Transformer X44491 caught fire. | O/H Transformer | O/H Transformer (1ph) | 407 | 37 | 251 | Central | UJ03
127214 | 2013-07-20 | Adverse Weather | Extreme Wind | Tree took down primary. | O/H Conductor | O/H Conductor | 1 | 60 | 1 | South | FAL03
127215 | 2013-07-21 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X43575 opened due to animal contact. | O/H Transformer | O/H Transformer (1ph) | 9 | 85 | 13 | Central | TR3UY
127217 | 2013-07-21 | Scheduled Outage | Construction | Defective phase transformer of three phase bank | O/H Transformer | O/H Transformer (1ph) | 1 | 30 | 0 | East | V11F1
127218 | 2013-07-21 | Scheduled Outage | Construction | To remove TP5978 from service & install cables to R1-F and energize new transformer vault at VT359 | None | None | 47 | 535 | 419 | Central | TK5TS
127220 | 2013-07-22 | Scheduled Outage | Construction | To change defective cuttout | O/H Switchgear | Fused Cutout | 15 | 25 | 6 | South | EPWF3
127222 | 2013-07-22 | Scheduled Outage | Maintenance | Transformer #X32215 opened by crew to replace defective fuse holder for streetlighting. | None | None | 5 | 14 | 1 | Central | AD06
127223 | 2013-07-22 | Defective Equipment | Defective Equipment/ Material | Transformer #X35422 opened up due to blown line fuse | O/H Switchgear | Inline Switch | 1 | 310 | 5 | West | 43F3
127224 | 2013-07-22 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27907 opened up due to squirrel contact | O/H Transformer | O/H Transformer (1ph) | 10 | 148 | 25 | Central | TH06
127225 | 2013-07-23 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X33131 opened due to animal contact | O/H Transformer | O/H Transformer (1ph) | 11 | 66 | 12 | Central | TD05
127226 | 2013-07-23 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X29882 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 11 | 73 | 13 | Central | TR09
127227 | 2013-07-23 | Scheduled Outage | Maintenance | xfmr isolated for soil remediation | None | None | 5 | 462 | 38 | West | BRDF4
127228 | 2013-07-23 | Scheduled Outage | Maintenance | At 09:07, 4KV AN05 transformer loop was isolated to allow crews to perform cable injection . 28 customers affected for 33 minutes. Cahill (AN05) ID #127228 | None | None | 28 | 333 | 155 | East | AN05
127229 | 2013-07-23 | Scheduled Outage | Maintenance | At 09:35, 13KV transformer KT461 isolated to repair broken insulators. 13 customers affected for 67 minutes. Hinchy (TH11) ID #127229 | None | Kiosk (1ph) | 13 | 67 | 15 | Central | TH11-NIU
127230 | 2013-07-23 | Foreign Interference | Wildlife (Bird/Animal) | At 12:15 4KV transformer Kiosk K255 was isolated to allow crews to replace defective transformer due to an animal nest. 7 customers affected for 375 minutes. Fisher (AK02) ID #1272 | U/G Transformer | Kiosk (1ph) | 7 | 375 | 44 | Central | AK02
127232 | 2013-07-23 | Tree Contacts | Falling Tree | At 09:35, UQ02 4KV O/H section isolated to allow crews to remove fallen tree across primary. 54 customers affected for 142 minutes. Queens (UQ02) ID #127232 | O/H Conductor | O/H Conductor | 54 | 142 | 128 | East | UQ02
127233 | 2013-07-23 | Tree Contacts | Falling Tree | During the Wind and lightning storm the UW07 circuit A/R/A due to fallen tree at 1202 Whitmore on the primary | Pole Attachement | Arrester | 223 | 77 | 286 | Central | UW07
127235 | 2013-07-23 | Adverse Weather | Extreme Wind | STORM | O/H Conductor | O/H Conductor | 154 | 164 | 421 | East | AL10
127236 | 2013-07-23 | Tree Contacts | Falling Tree | S21976 opened due to downed O/H primary at rear 934 Hare caused by falling tree. | O/H Conductor | O/H Conductor | 11 | 262 | 48 | Central | TW22
127236 | 2013-07-23 | Tree Contacts | Falling Tree | S21976 opened due to downed O/H primary at rear 934 Hare caused by falling tree. | O/H Conductor | O/H Conductor | 82 | 658 | 899 | Central | TW22
127237 | 2013-07-23 | Unknown/Other | Unknown | During the wind and lightning storm the S10247 opened, crew patrolled line and did not find anything | O/H Switchgear | Fused Cutout | 517 | 101 | 870 | Central | TH01
127239 | 2013-07-23 | Tree Contacts | Falling Tree | 331 Fullerton Ave wires down in the backyard. | O/H Conductor | O/H Conductor | 32 | 147 | 78 | East | AA05
127239 | 2013-07-23 | Tree Contacts | Falling Tree | 331 Fullerton Ave wires down in the backyard. | O/H Conductor | O/H Conductor | 391 | 11 | 72 | East | AA05
127240 | 2013-07-23 | Tree Contacts | Falling Tree | BECKF2 B phase section on Ashton Station Rd was isolated due to downed O/H primary at 2486 Ashton Station Rd during wind and lightning storm. | O/H Conductor | O/H Conductor | 3 | 89 | 4 | West | BECKF2
127240 | 2013-07-23 | Tree Contacts | Falling Tree | BECKF2 B phase section on Ashton Station Rd was isolated due to downed O/H primary at 2486 Ashton Station Rd during wind and lightning storm. | O/H Conductor | O/H Conductor | 7 | 116 | 14 | West | BECKF2
127241 | 2013-07-24 | Scheduled Outage | Maintenance | soil remediation | None | None | 17 | 470 | 133 | South | 170F1
127242 | 2013-07-24 | Tree Contacts | Falling Tree | SWITCH FEEDING TRANSFORMER X33897 OPENED WHEN TREE FELL ON SECONDARY OPEN BUSS | O/H Conductor | O/H Conductor | 11 | 253 | 46 | Central | TW22
127245 | 2013-07-24 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X37062 | None | None | 1 | 75 | 1 | South | 72F4
127247 | 2013-07-24 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32704 TO REPLACE THE POLE | None | None | 9 | 255 | 38 | Central | UW14
127248 | 2013-07-24 | Scheduled Outage | Construction | Transformer #X32700 opened up by crew for a pole change | None | None | 18 | 240 | 72 | Central | UW14
127253 | 2013-07-25 | Scheduled Outage | Construction | Transformer X30939-1671407 at 244 Wilbrod St. isolated for pole change | None | Pole | 8 | 150 | 20 | Central | SK11
127257 | 2013-07-26 | Scheduled Outage | Construction | Removal of old cable by contractor | None | None | 7 | 138 | 16 | West | 624F1
127258 | 2013-07-26 | Scheduled Outage | Construction | Transformer TP3748 isolated for leaking transformer | U/G Transformer | Padmount (1ph) | 9 | 96 | 14 | West | BRDF1
127259 | 2013-07-27 | Scheduled Outage | Construction | At 01:15am, 8 KV transformer was isolated to allow crews to replace leaking transformer. 6 customers affected for 125 minutes. Startop (6F10) ID#127259 | U/G Transformer | Padmount (1ph) | 6 | 125 | 12 | East | 6F10
127261 | 2013-07-27 | Scheduled Outage | Construction | 48M5 O/H section between S13220, MC2019, MC2023 and CS16826 was isolated to allow crew to replace switches and pole at S11442 | None | Pole | 1 | 281 | 5 | East | 48M5
127264 | 2013-07-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X39605 opened up due to defective fuse | O/H Switchgear | Fused Cutout | 1 | 105 | 2 | South | FAL03
127265 | 2013-07-28 | Foreign Interference | Vehicle | 7F4 O/H section on River Rd was Isolated due to Dump Truck hitting secondary O/H conductor and dammaging Hydro Pole | Pole | Pole | 3 | 301 | 15 | East | 7F4
127266 | 2013-07-28 | Defective Equipment | Defective Equipment/ Material | Transformer X17129 was isolated due to defecitve transformer | O/H Transformer | O/H Transformer (1ph) | 11 | 266 | 49 | East | BLKF1
127267 | 2013-07-28 | Defective Equipment | Electrical Failure | Customer reported outage - crews investigated and found VT519 had one blown fuse in reyrolle gear | Vault Equipment | Transformer | 1 | 480 | 8 | Central | TD07
127268 | 2013-07-29 | Scheduled Outage | Maintenance | Complete cable injection | None | Padmount (1ph) | 55 | 393 | 360 | East | AN05
127269 | 2013-07-29 | Scheduled Outage | Construction | Transformer X33714 at 1000 Wellington St. isolated for pole change | None | None | 12 | 120 | 24 | Central | UJ05
127271 | 2013-07-29 | Unknown/Other | Unknown | During the lightning storm in the Orleans Area the RX2058 tripped opened. Circuit was patrolled and nothing was found Cause remains under investigation. | Unknown \ Other | Unknown \ Other | 1808 | 11 | 331 | East | 77M2
127273 | 2013-07-29 | Scheduled Outage | Construction | Transformer #X43937 opened by crew to change secondary buss | None | None | 27 | 150 | 68 | Central | TR3UY
127274 | 2013-07-29 | Foreign Interference | Vehicle | RX2001 A/R and caused the G325R to opened due to Transport Truck hitting O/H conductor and breaking 2 Hydro Poles at 418 River Rd | Pole | Pole | 1 | 646 | 11 | East | 7F2
127274 | 2013-07-29 | Foreign Interference | Vehicle | RX2001 A/R and caused the G325R to opened due to Transport Truck hitting O/H conductor and breaking 2 Hydro Poles at 418 River Rd | Pole | Pole | 93 | 146 | 226 | East | 7F2
127275 | 2013-07-29 | Defective Equipment | Mechanical Failure | Broken cutout at X24624, caused G228B and G297B phases to blow. | O/H Switchgear | Fused Cutout | 121 | 115 | 232 | East | 8F1
127277 | 2013-07-29 | Adverse Weather | Extreme Wind | 2 phases on the ground due to thunderstorms in the area | O/H Conductor | O/H Conductor | 20 | 14 | 5 | Central | TK2AC
127277 | 2013-07-29 | Adverse Weather | Extreme Wind | 2 phases on the ground due to thunderstorms in the area | O/H Conductor | O/H Conductor | 108 | 87 | 157 | Central | TK2AC
127277 | 2013-07-29 | Adverse Weather | Extreme Wind | 2 phases on the ground due to thunderstorms in the area | O/H Conductor | O/H Conductor | 128 | 72 | 154 | Central | TK2AC
127277 | 2013-07-29 | Adverse Weather | Extreme Wind | 2 phases on the ground due to thunderstorms in the area | O/H Conductor | O/H Conductor | 128 | 99 | 211 | Central | TK2AC
127277 | 2013-07-29 | Adverse Weather | Extreme Wind | 2 phases on the ground due to thunderstorms in the area | O/H Conductor | O/H Conductor | 622 | 1 | 10 | Central | TK2AC
127278 | 2013-07-29 | Adverse Weather | Extreme Wind | Wind blew tree onto overhead secondary open wire buss. | O/H Conductor | O/H Conductor | 9 | 256 | 38 | South | 47F6
127279 | 2013-07-29 | Defective Equipment | Mechanical Failure | Faulty Transformer | O/H Transformer | O/H Transformer (1ph) | 1 | 498 | 8 | West | BECKF2
127280 | 2013-07-30 | Defective Equipment | Defective Equipment/ Material | SE17 is defective. | U/G Switchgear | Live-Front | 103 | 171 | 294 | East | 77M2
127280 | 2013-07-30 | Defective Equipment | Defective Equipment/ Material | SE17 is defective. | U/G Switchgear | Live-Front | 248 | 97 | 401 | East | 77M6
127282 | 2013-07-30 | Scheduled Outage | Construction | Transformer X30934-1652983 at 338 Wilbrod Street isolated to install new pole | None | Pole | 9 | 122 | 18 | Central | UN03
127285 | 2013-07-30 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32651 AND X32650 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 24 | 270 | 108 | Central | UW14
127286 | 2013-07-31 | Scheduled Outage | Construction | P224 was isolated to transfer transfer cables and switches to new pole | None | Kiosk (3ph) | 1 | 130 | 2 | East | UT05
127287 | 2013-07-31 | Scheduled Outage | Vegetation Management | Isolated for tree trimming. | None | None | 46 | 60 | 46 | East | UZ11
127288 | 2013-07-31 | Scheduled Outage | Construction | change a leaking transformer. | U/G Transformer | Kiosk (1ph) | 15 | 75 | 19 | Central | TW22
127289 | 2013-07-31 | Scheduled Outage | Construction | To re-arrange cables. | None | None | 14 | 314 | 73 | West | MWDF3
127293 | 2013-07-31 | Scheduled Outage | Construction | Transformer X30938 at 256 Wilbrod St. isolated to install new pole | None | None | 17 | 201 | 57 | Central | UX02
127295 | 2013-08-01 | Scheduled Outage | Vegetation Management | 49F6 from temp 12 to EOL isolated for tree removal. | None | None | 17 | 113 | 32 | South | 49F6
127298 | 2013-08-02 | Defective Equipment | Defective Equipment/ Material | Replaced switch leed to the primary at transformer X27321 at 3705 Riverside Dr. | O/H Switchgear | Fused Cutout | 2 | 91 | 3 | East | 2207
127300 | 2013-08-02 | Defective Equipment | Mechanical Failure | Ampacts burnt off of switch G216 blue | O/H Conductor | Ampact | 64 | 323 | 345 | East | LTM01
127301 | 2013-08-03 | Scheduled Outage | Vegetation Management | To allow Tamarack Tree Care forestry crews to clear trees off the secondary open wire buss | None | Fused Cutout | 9 | 170 | 26 | Central | UC07
127302 | 2013-08-03 | Defective Equipment | Mechanical Failure | REPLACED BROKEN FUSE FEEDING TRANSFORMER X17131 | O/H Switchgear | Fused Cutout | 9 | 209 | 31 | East | BLKF1
127304 | 2013-08-04 | Defective Equipment | Mechanical Failure | Defective cut out. | O/H Switchgear | Fused Cutout | 136 | 88 | 199 | East | 7F4
127305 | 2013-08-04 | Adverse Environment | Fire | Working fire on wires feeding transformer X29047 | O/H Conductor | O/H Conductor | 1162 | 26 | 504 | East | TB14
127306 | 2013-08-04 | Scheduled Outage | Maintenance | To brace transformer pole and repair conductor at X29047 | None | None | 1 | 284 | 5 | East | TB14
127307 | 2013-08-04 | Foreign Interference | Wildlife (Bird/Animal) | blown transformer fuse caused by racoon | O/H Transformer | O/H Transformer (1ph) | 9 | 40 | 6 | Central | TW22
127308 | 2013-08-05 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at transformer X24263 caused G918R to blow. | O/H Transformer | O/H Transformer (1ph) | 15 | 37 | 9 | East | 8F3
127308 | 2013-08-05 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at transformer X24263 caused G918R to blow. | O/H Transformer | O/H Transformer (1ph) | 109 | 70 | 127 | East | 8F3
127309 | 2013-08-05 | Defective Equipment | Electrical Failure | cable fault | U/G Cable | XLPE | 14 | 103 | 24 | East | AN05
127310 | 2013-08-05 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33143 (SQUIRREL CONTACT) | O/H Switchgear | Fused Cutout | 14 | 44 | 10 | Central | TD05
127311 | 2013-08-06 | Scheduled Outage | Construction | Vault VE45 including G531 were isolated to allow crew to replace switches and insulators and allow contractor to perform vault maintenance. | None | None | 13 | 181 | 39 | East | CYRF1
127312 | 2013-08-06 | Scheduled Outage | Construction | Transformer #X27195 opened by crew to relocate a service | None | None | 7 | 59 | 7 | East | TB06
127313 | 2013-08-06 | Scheduled Outage | Maintenance | Vt330 @ 550 Cote St was isolated by the crew to allow the metering dept to mekae meter repairs | None | Unknown \ Other | 1 | 90 | 2 | East | TO1UB
127314 | 2013-08-06 | Defective Equipment | Mechanical Failure | TB06 opened by System office as per 24/7 request for safety reason to open X27348 due to broken switch. | O/H Switchgear | Fused Cutout | 1537 | 1 | 26 | East | TB06
127315 | 2013-08-06 | Defective Equipment | Defective Equipment/ Material | Transformer #X27348 opened by crew to replace secondary connections and transformer switch. | O/H Switchgear | Fused Cutout | 11 | 60 | 11 | East | TB06
127316 | 2013-08-06 | Scheduled Outage | Construction | S26227 opened up by crew for a pole replacement | None | None | 61 | 360 | 366 | Central | UX02
127317 | 2013-08-06 | Scheduled Outage | Construction | Transformers #X33985, X33983 and X33984 opened by crew for an upgrade (to replace 3 transformers with 1). | None | None | 32 | 195 | 104 | Central | UW14
127319 | 2013-08-07 | Scheduled Outage | Construction | Vault VE4 to include S20063 at 2602 Innes was isolated to allow crew to tranfer cables to a new pole. | None | None | 1 | 1734 | 29 | East | BLKF8
127320 | 2013-08-07 | Scheduled Outage | Construction | Transformer #X30014 opened by crew to relocate service | None | None | 8 | 45 | 6 | Central | SB09
127321 | 2013-08-07 | Scheduled Outage | Construction | Replace leaking overhead transformer X38565 | None | None | 2 | 150 | 5 | Central | TD06
127322 | 2013-08-07 | Scheduled Outage | Maintenance | Transformer #X40435 opened by crew for an upgrade | None | None | 3 | 139 | 7 | West | 624F6
127323 | 2013-08-07 | Scheduled Outage | Construction | To transfer 4kV customers to new 13kV circuit | None | None | 149 | 248 | 616 | Central | UW04
127327 | 2013-08-08 | Lightning | Lightning | Lightning | O/H Conductor | O/H Conductor | 1131 | 4 | 75 | East | ELW05
127328 | 2013-08-08 | Lightning | Lightning | Lightning | O/H Conductor | O/H Conductor | 1102 | 4 | 73 | East | ELW09
127329 | 2013-08-08 | Lightning | Lightning | Lightning | O/H Conductor | O/H Conductor | 23 | 3 | 1 | East | AP02
127331 | 2013-08-08 | Lightning | Lightning | Lightning | O/H Conductor | O/H Conductor | 1279 | 3 | 64 | East | TO2UB
127336 | 2013-08-08 | Lightning | Lightning | Adverse weather -lightning | O/H Switchgear | Recloser (1ph) | 351 | 52 | 304 | West | MWDF3
127344 | 2013-08-08 | Lightning | Lightning | Adverse weather-lightning | O/H Switchgear | Fused Cutout | 47 | 159 | 125 | East | UZ11
127345 | 2013-08-08 | Lightning | Lightning | Lightning | None | None | 73 | 54 | 66 | East | AA02
127346 | 2013-08-07 | Lightning | Lightning | Adverse weather-lightning | O/H Switchgear | Fused Cutout | 7 | 249 | 29 | South | 47F6
127348 | 2013-08-08 | Tree Contacts | Falling Tree | Fallen tree cause TO49, TO37 and AA05 breakers to open. | O/H Conductor | O/H Conductor | 2 | 386 | 13 | East | TO3AC
127348 | 2013-08-08 | Tree Contacts | Falling Tree | Fallen tree cause TO49, TO37 and AA05 breakers to open. | O/H Conductor | O/H Conductor | 391 | 407 | 2652 | East | AA05
127348 | 2013-08-08 | Tree Contacts | Falling Tree | Fallen tree cause TO49, TO37 and AA05 breakers to open. | O/H Conductor | O/H Conductor | 3032 | 50 | 2527 | East | TO3AC
127350 | 2013-08-08 | Scheduled Outage | Construction | TP1916 was isolated to allow electrician to connect new secondary in base. | None | Padmount (3ph) | 12 | 64 | 13 | Central | 303
127351 | 2013-08-08 | Scheduled Outage | Maintenance | SK10 from S22204 to EOL isolated for plant upgrade. | None | Unknown \ Other | 101 | 387 | 651 | Central | SK10
127353 | 2013-08-08 | Defective Equipment | Electrical Failure | Defective PPH caused UA07 breaker to open. | U/G Cable Attachement | Pothead | 289 | 44 | 212 | East | UA07
127354 | 2013-08-08 | Scheduled Outage | Maintenance | perform repairs to transformer | None | None | 1 | 127 | 2 | East | 6F1
127355 | 2013-08-08 | Scheduled Outage | Construction | ID cable in tench | None | None | 1 | 22 | 0 | South | 190F6
127356 | 2013-08-08 | Defective Equipment | Defective Equipment/ Material | Transformer #K00279 opened by crew to replace current limitor fuse | O/H Switchgear | Fused Cutout | 20 | 20 | 7 | Central | AK04
127357 | 2013-08-09 | Unknown/Other | Unknown | Not yet known. | None | None | 509 | 8 | 68 | South | 200F6
127358 | 2013-08-09 | Defective Equipment | Electrical Failure | CB1 at VT181 tripped due to defective transformer in the vault | Vault Equipment | Transformer | 1 | 484 | 8 | Central | 5402
127359 | 2013-08-10 | Scheduled Outage | Construction | Oil clean up at TE1595 and TE1409 and transformer replacement also interupting TP5278, affecting 3 customers | None | Padmount (3ph) | 3 | 676 | 34 | South | 130F3
127360 | 2013-08-10 | Scheduled Outage | Construction | To disconnect defective primary service and to refuse TP2021 | U/G Cable | PILC | 1 | 10 | 0 | East | 5303
127361 | 2013-08-11 | Scheduled Outage | Construction | At 00:36, Transformer TE1291 at 1235 Donald street was isolated to allow crew to replace base. 4 customers were affected for MANY! Minutes. Startop (6F10) ID#127361. | None | None | 4 | 1013 | 68 | East | 6F10
127362 | 2013-08-11 | Scheduled Outage | Maintenance | To complete required ESA Metering Repairs | None | None | 1 | 570 | 10 | Central | 615
127365 | 2013-08-11 | Tree Contacts | Broken Branch | Transformer X32351 at 383 Ravenhill Ave. isolated for removal of tree branch | None | None | 17 | 41 | 12 | Central | AH14
127366 | 2013-08-11 | Foreign Interference | Wildlife (Bird/Animal) | crews found blown fuse at X26298 due to animal contact. 9 customers affected for 63 minutes | O/H Switchgear | Fused Cutout | 9 | 63 | 9 | Central | TD07
127368 | 2013-08-12 | Defective Equipment | Mechanical Failure | Cable fault between TP7051 and TE1189 caused S19551 white phase to blow. | U/G Cable | XLPE | 42 | 18 | 13 | East | 77M6
127368 | 2013-08-12 | Defective Equipment | Mechanical Failure | Cable fault between TP7051 and TE1189 caused S19551 white phase to blow. | U/G Cable | XLPE | 50 | 25 | 21 | East | 77M6
127368 | 2013-08-12 | Defective Equipment | Mechanical Failure | Cable fault between TP7051 and TE1189 caused S19551 white phase to blow. | U/G Cable | XLPE | 75 | 111 | 139 | East | 77M6
127369 | 2013-08-12 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at Tx X43878 caused S27308 to blow. | None | None | 41 | 105 | 72 | Central | TR3UY
127370 | 2013-08-12 | Scheduled Outage | Construction | Transformer #X23793 opened by crew to relocate a service. | None | None | 15 | 45 | 11 | East | AA04
127371 | 2013-08-12 | Scheduled Outage | Construction | At 09:20am, 4KV O/H section from S25404 to EOL islatedto allow crews to install new pole and transfer primary. 18 customers affected for 285 minutes. Walkley (UZ12) ID #127371 | None | None | 18 | 285 | 86 | East | UZ12
127372 | 2013-08-12 | Defective Equipment | Electrical Failure | Defective O/H transformer X35574 @ 21 Lockview caused S249 to blow | O/H Transformer | O/H Transformer (1ph) | 2 | 260 | 9 | South | FAL03
127372 | 2013-08-12 | Defective Equipment | Electrical Failure | Defective O/H transformer X35574 @ 21 Lockview caused S249 to blow | O/H Transformer | O/H Transformer (1ph) | 17 | 100 | 28 | South | FAL03
127373 | 2013-08-12 | Scheduled Outage | Construction | Transformer #X30686 at 102 Lewis St and X30683 at 8 Hartington Pl opened by crew for pole replacement. | None | None | 12 | 210 | 42 | Central | UX02
127375 | 2013-08-12 | Scheduled Outage | Construction | Pole replacement | None | None | 11 | 165 | 30 | Central | UX02
127376 | 2013-08-12 | Scheduled Outage | Construction | Relocating Transformer and conductors to new poles | None | None | 9 | 396 | 59 | Central | UW14
127377 | 2013-08-12 | Scheduled Outage | Construction | Replace 600A switch | None | None | 1 | 108 | 2 | South | FAL02
127378 | 2013-08-13 | Foreign Interference | Vehicle | Construction equipment made contact and broke system neutral at Bank and Arena Pl. | O/H Conductor | O/H Conductor | 3678 | 5 | 306 | East | LTM01
127379 | 2013-08-13 | Scheduled Outage | Vegetation Management | UC08 o/h line from X44250 to EOL for tree removal. | None | None | 40 | 286 | 191 | Central | UC08
127380 | 2013-08-13 | Scheduled Outage | Vegetation Management | Transformer #X27343 opened up by crew to drop 2 services for Forestry | None | None | 6 | 15 | 2 | East | TB06
127381 | 2013-08-13 | Scheduled Outage | Construction | Transformer #X23016 opened by crew to relocate plant for an up coming pole installation | None | None | 3 | 60 | 3 | East | AC14
127382 | 2013-08-13 | Scheduled Outage | Vegetation Management | Transformer #X27343 opened by crew for Forestry Dept | None | None | 6 | 30 | 3 | East | TB06
127383 | 2013-08-13 | Scheduled Outage | Construction | Relocating Plant to new poles | None | None | 18 | 240 | 72 | Central | UW14
127384 | 2013-08-13 | Scheduled Outage | Construction | Pole Replacement | None | None | 11 | 210 | 38 | Central | UX09
127385 | 2013-08-13 | Scheduled Outage | Construction | replace leaking transformer | None | None | 16 | 142 | 38 | West | BRDF1
127386 | 2013-08-14 | Scheduled Outage | Construction | Transformer K1278 at 8 Lewis was isolated to allow crew to perform pole replacement. 15 customers were affected | None | None | 15 | 210 | 52 | Central | UX09
127387 | 2013-08-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X23857 opened up due to squirrel contact | O/H Transformer | O/H Transformer (1ph) | 13 | 57 | 12 | East | 77M6
127388 | 2013-08-14 | Scheduled Outage | Construction | Transformer #X31088 opened by crew to relocate plant | None | None | 3 | 10 | 0 | Central | UN03
127389 | 2013-08-14 | Scheduled Outage | Construction | Transformer TP10077 at Iness and 417 was isolated to allow crew to replace rusty transformer | None | Unknown \ Other | 1 | 243 | 4 | East | CYRF4
127390 | 2013-08-14 | Scheduled Outage | Construction | Transformer P232 at University of Ottawa was isolated to allow crew to replace defective transformer and upgrade switches on pole | None | Padmount (3ph) | 2 | 492 | 16 | Central | UN04
127391 | 2013-08-14 | Scheduled Outage | Construction | Trasnfromers 3556, TP5409, 2569 and 2521 were isolated to allow crews to replace cables and transformer 2521 | None | Padmount (1ph) | 32 | 480 | 256 | West | BRDF5
127393 | 2013-08-14 | Scheduled Outage | Construction | 2 transformers opened by crew (X33987 and X33988) for a transformer replacement. | None | None | 25 | 180 | 75 | Central | UW13
127394 | 2013-08-14 | Scheduled Outage | Construction | Transformer #X30680 and X30802 opened by crew due to pole change | None | None | 19 | 210 | 66 | Central | UX09
127395 | 2013-08-14 | Scheduled Outage | Maintenance | Transformer #X28161 opened by crew to replace connections. | None | None | 8 | 50 | 7 | Central | 505
127396 | 2013-08-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32741 opened up due to squirrel contact. | O/H Transformer | O/H Transformer (1ph) | 8 | 59 | 8 | Central | TD05
127397 | 2013-08-14 | Scheduled Outage | Construction | TP2529 isolated for replacement due to defective insert | None | None | 8 | 138 | 18 | West | BRDF1
127400 | 2013-08-15 | Scheduled Outage | Construction | HOL Crew to change defective transformer | None | None | 8 | 115 | 15 | Central | 307
127402 | 2013-08-15 | Scheduled Outage | Construction | Transformer #X24115 opened by crew to install new pole | None | None | 4 | 180 | 12 | East | 56F1
127403 | 2013-08-15 | Scheduled Outage | Construction | Transformer #X35179 opened up by crew to remove a service | None | None | 6 | 20 | 2 | Central | UL14
127404 | 2013-08-15 | Lightning | Lightning | Previous lightning strike damaged 1 Tx of 3 at X23894, bad transformer then caused pole fire. | O/H Transformer | O/H Transformer (3ph) | 1 | 175 | 3 | Central | TH06
127406 | 2013-08-16 | Scheduled Outage | Construction | ISOLATRED TRANSFORMER X32303 TO REPLACE TRIPLAX SERVICE | None | None | 7 | 65 | 8 | Central | UC08
127409 | 2013-08-17 | Defective Equipment | Defective Equipment/ Material | Defective Transformer | O/H Transformer | O/H Transformer (1ph) | 8 | 421 | 56 | South | 200F2
127411 | 2013-08-18 | Defective Equipment | Electrical Failure | Defective cables | U/G Cable | Unknown \ Other | 8 | 102 | 14 | West | 39F2
127411 | 2013-08-18 | Defective Equipment | Electrical Failure | Defective cables | U/G Cable | Unknown \ Other | 100 | 29 | 48 | West | 39F2
127411 | 2013-08-18 | Defective Equipment | Electrical Failure | Defective cables | U/G Cable | Unknown \ Other | 638 | 107 | 1138 | West | 39F2
127413 | 2013-08-19 | Scheduled Outage | Maintenance | vault maintenance | None | None | 1 | 241 | 4 | East | 8F4
127414 | 2013-08-20 | Unknown/Other | Unknown | The O/H was patrolled but found nothing | O/H Switchgear | Fused Cutout | 18 | 84 | 25 | South | EPWF1
127415 | 2013-08-20 | Scheduled Outage | Construction | To allow crew to transfer plant to SK10 circuit and install new switches. | None | None | 6 | 173 | 17 | Central | UN03
127418 | 2013-08-20 | Scheduled Outage | Construction | At 8:10 am, transformer X33086 at 470 Hartleigh was isolated to allow crew to perform a service upgrade. 16 customers were interrupted for 20 minutes. Lincoln Heights (TD07) ID# 127418. | None | None | 16 | 20 | 5 | Central | TD07
127419 | 2013-08-20 | Scheduled Outage | Construction | At 2:35 pm, transformer 371B at Pickford and Lombardo was isolated to allow crew to replace leaking transformer. 12 customers were interrupted for 136 minutes. Bridlewood (BRDF3) ID# 127419. | None | None | 12 | 136 | 27 | West | BRDF3
127420 | 2013-08-20 | Defective Equipment | Defective Equipment/ Material | Transformer #X4365 opened by crew to repair a service | Secondary \ Service | O/H Service | 4 | 10 | 1 | South | 170F1
127421 | 2013-08-20 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30843 TO TRANSFER HYDRO PLANT | None | None | 3 | 200 | 10 | Central | UN07
127422 | 2013-08-20 | Scheduled Outage | Construction | At 4:15 pm, Transformers TP2525W at 7 Appaloosa and TP2514W at 113 Chickasaw were isolated to allow crew to replace defective transformer TP2514 and replace broken insert at TP2525. 17 customers were interrupted for minutes. Bridlewood (BRDF3) ID# 127422. | None | Elbow \ Insert | 17 | 160 | 45 | West | BRDF3
127423 | 2013-08-21 | Foreign Interference | Wildlife (Bird/Animal) | A squirrel made contact at RX2011 | O/H Switchgear | Recloser (3ph) | 1974 | 9 | 296 | West | BRDF3
127424 | 2013-08-21 | Scheduled Outage | Construction | At 9:23 am, transformer TP6436 at 20 Knollsbrook was isolated to allow crew to replace leaking transformer and perform soil remediation. 9 customers were be interrupted for approximately 382 minutes. Barrhaven DS (140F1). | None | Kiosk (1ph) | 9 | 382 | 57 | South | 140F1
127425 | 2013-08-21 | Scheduled Outage | Construction | At 9:36am, Transformer 372B was isolated to allow crew to replace defective transformer. 11 customers were interrupted for 204 minutes. Bridlewood (BRDF3) ID# 127425. | None | None | 11 | 204 | 37 | West | BRDF3
127426 | 2013-08-21 | Scheduled Outage | Construction | PCB transformer replacement. | None | None | 516 | 330 | 2838 | East | UZ06
127428 | 2013-08-21 | Scheduled Outage | Maintenance | To allow crew to replace leaking pothead. | None | None | 1 | 289 | 5 | East | TB2AL
127429 | 2013-08-21 | Scheduled Outage | Construction | ISOLATED TTRANSFORMER X30637 TO TRTANSFER HYDRO PLANT TO NEW POLE | None | None | 21 | 150 | 52 | Central | SK10
127430 | 2013-08-21 | Scheduled Outage | Construction | ISOLATED TRANSFOMER X23017 TO INSTALL NEW POLE | None | None | 13 | 40 | 9 | East | AA02
127432 | 2013-08-22 | Loss Of Supply | Transmission Inadvertent | Not yet known. | None | None | 3881 | 3 | 194 | South | C7BM (Manordale MS - T1/T2)
127432 | 2013-08-22 | Loss Of Supply | Transmission Inadvertent | Not yet known. | None | None | 4091 | 3 | 205 | South | C7BM (Centrepointe MS - T1/T2)
127433 | 2013-08-22 | Scheduled Outage | Construction | V365 at 1303 Fellow was isolated to allow crew to rebuild barrier in vault | None | None | 1 | 119 | 2 | Central | UW14
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 2 | 388 | 13 | East | TO3AC
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 14 | 372 | 87 | East | 1808
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 51 | 289 | 246 | East | 1806
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 68 | 357 | 405 | East | TR02UQ
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 96 | 265 | 424 | East | 1802
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 184 | 318 | 975 | East | TO2UT
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 527 | 240 | 2108 | East | TO3AP
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 679 | 227 | 2569 | East | TO3UB
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 1312 | 112 | 2449 | East | TO2UB
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 1723 | 9 | 258 | Central | TK1AC
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 2606 | 148 | 6428 | East | TO1UT
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 3044 | 15 | 761 | Central | TK1AC
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 3991 | 74 | 4922 | Central | TK1AC
127436 | 2013-08-22 | Defective Equipment | Electrical Failure | A flash at both TO3AC-L and the TO49 CB caused the Q1 and Q2 busses at Overbrook to trip on differential protection. Direct cause not yet determined. | Station Equipment | Primary Switchgear | 4479 | 274 | 20454 | Central | TK1AC
127438 | 2013-08-22 | Tree Contacts | Falling Tree | Tree contact caused conductor to break and damaged transformer X24089. Overhead line from G677W to EOL isolated to repair the conductor. | O/H Conductor | O/H Conductor | 12 | 310 | 62 | East | 7F4
127438 | 2013-08-23 | Tree Contacts | Falling Tree | Tree contact caused conductor to break and damaged transformer X24089. Overhead line from G677W to EOL isolated to repair the conductor. | O/H Conductor | O/H Conductor | 55 | 157 | 144 | East | 7F4
127439 | 2013-08-23 | Scheduled Outage | Construction | crews replacing elbows and inserts | None | None | 10 | 86 | 14 | West | BRDF3
127442 | 2013-08-23 | Foreign Interference | Vehicle | MVA accident at Russell and South Vale caused the AL02 CB to take the 13KV TB1AL out of Russell and gallopping span guy to trip the TB3LE circuirt to trip | None | None | 223 | 170 | 632 | East | TB1AL
127442 | 2013-08-23 | Foreign Interference | Vehicle | MVA accident at Russell and South Vale caused the AL02 CB to take the 13KV TB1AL out of Russell and gallopping span guy to trip the TB3LE circuirt to trip | None | None | 339 | 56 | 316 | East | TB1AL
127442 | 2013-08-23 | Foreign Interference | Vehicle | MVA accident at Russell and South Vale caused the AL02 CB to take the 13KV TB1AL out of Russell and gallopping span guy to trip the TB3LE circuirt to trip | None | None | 2083 | 56 | 1944 | East | TB3LE
127443 | 2013-08-23 | Defective Equipment | Defective Equipment/ Material | RX2011 blew up while performing test operations and caused the BRDF3 circuit to trip. | O/H Switchgear | Recloser (3ph) | 1974 | 8 | 263 | West | BRDF3
127444 | 2013-08-24 | Scheduled Outage | Construction | At 7:52 am, transformer TE1653 at 24 Colonnade was isolated to allow crew to replace leaking transformer and perform soil remediation. 1 customer was interrupted for 581 minutes. Merivale DS (72F6) ID# 127444. | None | None | 1 | 581 | 10 | South | 72F6
127445 | 2013-08-24 | Scheduled Outage | Construction | Transformer #X32783 opened by crew for a transformer replacement | None | None | 5 | 415 | 35 | Central | TD06
127447 | 2013-08-24 | Defective Equipment | Electrical Failure | To repair defective switch. | O/H Switchgear | Fused Cutout | 34 | 5 | 3 | East | UA03
127448 | 2013-08-25 | Defective Equipment | Defective Equipment/ Material | ELW05 PPH was found defective. | Station Equipment | Relay | 163 | 73 | 198 | East | ELW05
127448 | 2013-08-25 | Defective Equipment | Defective Equipment/ Material | ELW05 PPH was found defective. | Station Equipment | Relay | 1131 | 36 | 679 | East | ELW05
127450 | 2013-08-25 | Foreign Interference | Wildlife (Bird/Animal) | Switch 88W was found blown due to animal contact. | O/H Switchgear | Fused Cutout | 25 | 73 | 30 | West | MWDF2
127451 | 2013-08-26 | Unknown/Other | Unknown | Andy Laneville (24/7) patrolled the circuit and found no direct cause for the outage but he did report a pecker hole with squirrels living in it. | Unknown \ Other | Unknown \ Other | 730 | 7 | 85 | South | 160F2
127453 | 2013-08-26 | Scheduled Outage | Construction | Transformer X30639 at 183 Stewart St. Isolated to transfer plant to new pole | None | None | 18 | 180 | 54 | Central | SK10
127455 | 2013-08-26 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30800 TO REPLACE POLE | None | None | 13 | 255 | 55 | Central | UX02
127456 | 2013-08-26 | Scheduled Outage | Construction | To replace damaged switches (FireCall) | None | None | 1 | 41 | 1 | East | UT12
127457 | 2013-08-27 | Scheduled Outage | Construction | crew to replace pole and transfer plant to new pole | None | None | 7 | 210 | 24 | Central | UX02
127458 | 2013-08-27 | Scheduled Outage | Maintenance | cable injection | None | None | 16 | 405 | 108 | East | AN05
127461 | 2013-08-27 | Scheduled Outage | Construction | Transformer X 30641 at 125 Stewart St. isolated to transfer secondary to new buss. | None | None | 3 | 205 | 10 | Central | SK10
127462 | 2013-08-27 | Scheduled Outage | Construction | Transformer X30640 at 133 Stewart St. isolated to transfer secondary to new buss | None | None | 8 | 205 | 27 | Central | SK10
127463 | 2013-08-27 | Scheduled Outage | Construction | Transformer 34641-1670682 at 139 Stewart St. isolated to transfer secondary to new buss | None | None | 19 | 205 | 65 | Central | SK10
127464 | 2013-08-27 | Scheduled Outage | Construction | Transformer X23009 at 298 Levis Ave. isolated for pole change | None | None | 24 | 160 | 64 | East | AC14
127465 | 2013-08-27 | Scheduled Outage | Construction | Transformer X30939-1671407 at 244 Wilbrod St. isolated for pole change | None | None | 8 | 120 | 16 | Central | SK11
127466 | 2013-08-27 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32653 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 9 | 180 | 27 | Central | UW13
127467 | 2013-08-28 | Scheduled Outage | Construction | UX02 O/H section from X44267 to EOL was isolated to allow crew to perform pole replacement. | None | None | 169 | 134 | 377 | Central | UX02
127468 | 2013-08-28 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change a leaking transformer | None | None | 14 | 575 | 134 | South | 140F4
127470 | 2013-08-28 | Scheduled Outage | Maintenance | At 09:33, 8 KV transformer TE1078 at 1220 Bowmount was isolated to to allow crews to replace elbows and transformer. 13 customers affected for 163 minutes. Startop (6F10) ID #127470 | None | None | 13 | 163 | 35 | East | 6F10
127473 | 2013-08-28 | Foreign Interference | Crane | Contractor lifting equipment made contact with primary O/H lines. | O/H Conductor | O/H Conductor | 62 | 48 | 50 | Central | SK16
127473 | 2013-08-28 | Foreign Interference | Crane | Contractor lifting equipment made contact with primary O/H lines. | O/H Conductor | O/H Conductor | 294 | 138 | 676 | Central | SK16
127474 | 2013-08-28 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree in o/h primary line | None | None | 86 | 25 | 36 | East | TB06
127475 | 2013-08-28 | Adverse Environment | Fire | A fire caused damage to a secondary electrical panel. This caused the CB1 @ VT140 to trip. | Customer Owned | Customer-Owned | 1 | 304 | 5 | Central | 2802
127477 | 2013-08-29 | Unknown/Other | Unknown | Transformer X31934 fuse was found blown for an unknown cause. | None | None | 16 | 46 | 12 | Central | TD14
127478 | 2013-08-29 | Scheduled Outage | Maintenance | Soil Remediation | None | None | 10 | 492 | 82 | East | BLKF3
127479 | 2013-08-29 | Defective Equipment | Defective Equipment/ Material | S28226 R phase termination was found defective. | U/G Cable Attachement | Termination \ Stress Cone | 2 | 245 | 8 | Central | 303
127482 | 2013-08-29 | Scheduled Outage | Construction | Transformer r GL000078 at 16 Briarcliffe Dr. isolated for service change | None | None | 3 | 12 | 1 | East | 8F1
127483 | 2013-08-29 | Scheduled Outage | Construction | Transformer X23735 at 300 Ducharme Blvd. isolated to install new 1/0 service | None | None | 14 | 60 | 14 | East | AA03
127484 | 2013-08-30 | Scheduled Outage | Construction | Remove VT899 and energize new TP10010 | None | None | 1 | 251 | 4 | East | TB14
127485 | 2013-08-30 | Defective Equipment | Defective Equipment/ Material | 5301 circuit tripped due to defective tranition splice at S1176 (1705 St. Laurent) | U/G Cable | Transition Splice | 25 | 84 | 35 | East | 5301
127499 | 2013-08-31 | Scheduled Outage | Vegetation Management | Transformer X32033 was isolated to allow crew to clear vines off the overhead circuit in front of 466 Kenwood | None | None | 5 | 9 | 1 | Central | AH14
127500 | 2013-08-31 | Defective Equipment | Defective Equipment/ Material | Transformer X32033 was isolated to allow crew to replace defective transformer | O/H Transformer | O/H Transformer (1ph) | 5 | 234 | 20 | Central | AH14
127501 | 2013-09-01 | Unknown/Other | Unknown | Tomlinson Pit reports fuse at road is blown (S7003), two weeks previous the switch was maintained and fuse repalced. Crews could not find problem, customer owned O/H, they are to have Dundas power to investigate. Refused and held. | Customer Owned | Customer-Owned | 1 | 105 | 2 | South | FAL02
127502 | 2013-09-02 | Unknown/Other | Unknown | Crews reports no fault found. FCI indicated clear and no flags indicated. G544 red phase fuse closed all load restored. | None | None | 134 | 79 | 176 | East | CYRF4
127505 | 2013-09-02 | Defective Equipment | Defective Equipment/ Material | S20710 opened due to defective U/G cable | U/G Cable | XLPE | 35 | 104 | 61 | East | AJ06
127506 | 2013-09-02 | Lightning | Lightning | Lightning | O/H Switchgear | Fused Cutout | 146 | 68 | 165 | East | 249F2
127515 | 2013-09-02 | Lightning | Lightning | Lightning storm | Pole | Pole | 75 | 521 | 651 | West | A9M3
127515 | 2013-09-02 | Lightning | Lightning | Lightning storm | Pole | Pole | 202 | 87 | 293 | West | A9M3
127515 | 2013-09-02 | Lightning | Lightning | Lightning storm | Pole | Pole | 382 | 10 | 64 | West | A9M3
127515 | 2013-09-02 | Lightning | Lightning | Lightning storm | Pole | Pole | 509 | 23 | 195 | West | A9M3
127515 | 2013-09-02 | Lightning | Lightning | Lightning storm | Pole | Pole | 810 | 132 | 1782 | West | A9M3
127515 | 2013-09-02 | Lightning | Lightning | Lightning storm | Pole | Pole | 5653 | 16 | 1507 | West | A9M3
127515 | 2013-09-02 | Lightning | Lightning | Lightning storm | Pole | Pole | 7030 | 133 | 15583 | West | A9M3
127516 | 2013-09-03 | Scheduled Outage | Construction | To allow Hydro Ottawa On-call crews to replace a defective transformer | None | None | 10 | 175 | 29 | West | BRDF2
127517 | 2013-09-02 | Defective Equipment | Mechanical Failure | Defective cable section. | U/G Cable | XLPE | 7 | 235 | 27 | East | AJ06
127521 | 2013-09-03 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at X15595 at 4836 Bank St. Caused 249F1 to auto reclose and the R and B phase fuses at S14366 to open. | O/H Transformer | O/H Transformer (3ph) | 1 | 336 | 6 | East | LTM01
127521 | 2013-09-03 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at X15595 at 4836 Bank St. Caused 249F1 to auto reclose and the R and B phase fuses at S14366 to open. | O/H Transformer | O/H Transformer (3ph) | 1595 | 193 | 5131 | East | LTM01
127522 | 2013-09-03 | Scheduled Outage | Construction | TE2416 isolated to allow crews to replace insert after it was damaged by lightning. | U/G Cable Attachement | Elbow \ Insert | 1 | 46 | 1 | South | 140F5
127523 | 2013-09-03 | Scheduled Outage | Construction | Leaking Transformer | None | None | 10 | 208 | 35 | West | BRDF2
127524 | 2013-09-03 | Scheduled Outage | Construction | replace defective transformer. | None | None | 11 | 91 | 17 | West | BRDF2
127525 | 2013-09-04 | Scheduled Outage | Vegetation Management | Tree Trimming | None | None | 21 | 370 | 130 | Central | TD01
127526 | 2013-09-04 | Defective Equipment | Defective Equipment/ Material | S11772 opened up due to burnt switch | O/H Switchgear | Inline Switch | 1 | 114 | 2 | West | RHNF3
127529 | 2013-09-04 | Scheduled Outage | Construction | Transformer #X35157 opened by crew to transfer plant to new pole. | None | None | 19 | 130 | 41 | Central | SH02
127530 | 2013-09-04 | Scheduled Outage | Construction | Transformer #X33951 and X33957 opened up by crew for upgrades and transformer replacements. | None | None | 36 | 150 | 90 | Central | UW14
127531 | 2013-09-04 | Scheduled Outage | Construction | Transformer #X30802 opened up by crew for a pole change | None | None | 10 | 120 | 20 | Central | UX09
127532 | 2013-09-04 | Foreign Interference | Vehicle | Black and Mac reports they hit a guy wire and caused circuits to slap together | Pole Attachement | Unknown \ Other | 244 | 13 | 53 | East | UZ02
127532 | 2013-09-04 | Foreign Interference | Vehicle | Black and Mac reports they hit a guy wire and caused circuits to slap together | Pole Attachement | Unknown \ Other | 268 | 13 | 58 | East | UZ12
127533 | 2013-09-04 | Scheduled Outage | Construction | replace a leaking transformer | None | None | 1 | 58 | 1 | West | MWDF4
127534 | 2013-09-04 | Scheduled Outage | Construction | Transformer #X33950 and X33956 opened by crew for upgrades and transformer replacement | None | None | 48 | 165 | 132 | Central | UW14
127535 | 2013-09-04 | Scheduled Outage | Construction | Transformer #X27789 opened by crew to install new U/G service. | None | None | 6 | 54 | 5 | East | UQ08
127536 | 2013-09-05 | Scheduled Outage | Construction | Primary conductor upgrade | None | None | 40 | 110 | 73 | East | UG04
127537 | 2013-09-05 | Scheduled Outage | Maintenance | At 09:05, 27KV transformer TP2538 at 18 Chickasaw was isolated to allow crews to replace Elbows & Inserts. 9 customers affected for minutes. Briddlewood (BRDF1) ID #127537 | None | None | 9 | 63 | 9 | West | BRDF1
127538 | 2013-09-05 | Defective Equipment | Defective Equipment/ Material | Customer reported Partial power, crews confirmed 1 phase blown at Dip S19598. | U/G Cable | XLPE | 1 | 688 | 11 | West | 624F5
127539 | 2013-09-05 | Scheduled Outage | Construction | At 0:46, 27KV transformer TP9178 was isolated and replaced due to leaking oil. 9 customers affected for 86 minutes. Janet King (JKGF4) ID #127539 | None | None | 9 | 86 | 13 | West | JKGF4
127540 | 2013-09-05 | Defective Equipment | Mechanical Failure | 22M23 tripped due to equipment failure on 49T1-L. | O/H Switchgear | Load Break Gang | 3360 | 21 | 1176 | South | 22M23
127543 | 2013-09-05 | Foreign Interference | Vehicle | TM3UC line tripped due to truck hitting down guy at rear of Westgate shopping centre | O/H Conductor | Unknown \ Other | 1 | 70 | 1 | Central | TM3UC
127543 | 2013-09-05 | Foreign Interference | Vehicle | TM3UC line tripped due to truck hitting down guy at rear of Westgate shopping centre | O/H Conductor | Unknown \ Other | 3 | 15 | 1 | Central | TM3UC
127543 | 2013-09-05 | Foreign Interference | Vehicle | TM3UC line tripped due to truck hitting down guy at rear of Westgate shopping centre | O/H Conductor | Unknown \ Other | 4 | 20 | 1 | Central | TM3UC
127543 | 2013-09-05 | Foreign Interference | Vehicle | TM3UC line tripped due to truck hitting down guy at rear of Westgate shopping centre | O/H Conductor | Unknown \ Other | 8 | 49 | 7 | Central | TM3UC
127545 | 2013-09-05 | Defective Equipment | Defective Equipment/ Material | Transformer #TP029 opened up due to leads to the switch burnt up. | O/H Switchgear | Simple Solid Blade Switch | 7 | 178 | 21 | East | V11F1
127546 | 2013-09-06 | Defective Equipment | Defective Equipment/ Material | Red phase splice defective at TP6650, 3 phase cable replaced | U/G Cable | XLPE | 1 | 766 | 13 | West | 624F5
127547 | 2013-09-06 | Scheduled Outage | Construction | At 09:10, PC10a #11036 established at P415 at 1195 Bank was isolated to allow crews to decommision transformer and transfer customer to new service. 1 customer affected for 170 minutes. Cahill (AN06) ID #127547 | None | None | 1 | 170 | 3 | East | AN06
127554 | 2013-09-08 | Defective Equipment | Defective Equipment/ Material | Defective cable. | U/G Cable | XLPE | 37 | 183 | 113 | East | 77M6
127556 | 2013-09-08 | Scheduled Outage | Construction | Transformer X30584 at 955 Somerset St W. isolated for transformer & O/H quad change | None | None | 6 | 236 | 24 | Central | UJ03
127557 | 2013-09-08 | Defective Equipment | Electrical Failure | cable fault | U/G Cable | PILC Splice | 113 | 121 | 228 | East | 77M1
127559 | 2013-09-08 | Scheduled Outage | Maintenance | 4kV transformer X27091 at 574 Shelly was isolated to allow crews to change secondary connections. 6 customs affected for | None | None | 6 | 79 | 8 | East | TB14
127561 | 2013-09-09 | Scheduled Outage | Maintenance | cable injection testing 2 transformers are isolated | None | None | 30 | 280 | 140 | East | AN05
127563 | 2013-09-09 | Scheduled Outage | Construction | Transformer #X33799 and X33954 opened by crew due to relocating plant and upgrade. | None | None | 38 | 135 | 86 | Central | UW14
127564 | 2013-09-10 | Scheduled Outage | Maintenance | Cable injection testing | None | None | 15 | 262 | 66 | East | AN05
127565 | 2013-09-10 | Scheduled Outage | Construction | At 8:30 am, vault V742 was isolated to allow crew to transfer switches and cables to new pole. 1 customer was interrupted for 354 minutes. King Edward (SK10) ID# 127565. | None | None | 1 | 354 | 6 | Central | SK10
127566 | 2013-09-10 | Defective Equipment | Mechanical Failure | X25729 FUSE WAS FOUND BLOWN DUE TO A DEFECTIVE CUTOUT. | O/H Switchgear | Fused Cutout | 15 | 95 | 24 | Central | AM05
127567 | 2013-09-10 | Scheduled Outage | Construction | Replace leaking transformer TE2581 @ 2213 Nature trail Cr | None | None | 10 | 151 | 25 | East | CYRF1
127569 | 2013-09-10 | Foreign Interference | Wildlife (Bird/Animal) | A crow made contact with transformer X13864 which caused G316 to blow. | O/H Transformer | O/H Transformer (1ph) | 13 | 66 | 14 | East | LTM01
127569 | 2013-09-10 | Foreign Interference | Wildlife (Bird/Animal) | A crow made contact with transformer X13864 which caused G316 to blow. | O/H Transformer | O/H Transformer (1ph) | 74 | 92 | 113 | East | LTM01
127570 | 2013-09-10 | Foreign Interference | Foreign Objects | S14558 WB BLEW DUE TO A TREE CONTRACTOR STICK FALLING INTO THE OVERHEAD. NO CONTACT OR INJURIES. | O/H Conductor | O/H Conductor | 83 | 89 | 123 | East | UZ05
127574 | 2013-09-10 | Scheduled Outage | Construction | To replace defective transformer TP4277W @ 111 Patriot Place | None | Padmount (1ph) | 28 | 109 | 51 | West | BRDF2
127577 | 2013-09-11 | Scheduled Outage | Maintenance | Transformer K424 & K426 at 3240 Southgate was isolated for cable injection program | None | None | 28 | 333 | 155 | East | AN05
127578 | 2013-09-11 | Scheduled Outage | Construction | S523 was open in the Crystal Beach area to allow the crews to tranfer the Overhead conductor | None | None | 150 | 451 | 1128 | South | 49F6
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 0 | 84960 | 0 | East | 5305
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 3 | 166 | 8 | East | TB3LE
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 11 | 81 | 15 | East | 5307
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 38 | 10 | 6 | East | TB3LE
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 38 | 155 | 98 | East | TB3LE
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 132 | 331 | 728 | East | 5303
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 203 | 346 | 1171 | East | AE06
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 211 | 128 | 450 | East | AE05
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 248 | 128 | 529 | East | AE03
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 251 | 128 | 535 | East | AE04
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 256 | 128 | 546 | East | AE02
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 416 | 128 | 887 | East | AE07
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 440 | 131 | 961 | East | AE01
127580 | 2013-09-11 | Defective Equipment | Mechanical Failure | Rudy Grisel reports the TB-55 fell apart on the TB3LE circuit causing the red phase to drop onto the city bus while it was turning onto Smyth Rd. The wire was also found lying across the 5303 circuit and the AE06 circuit but did not energize the AE06 circ | O/H Switchgear | Inline Switch | 1569 | 81 | 2118 | East | TB06
127581 | 2013-09-11 | Scheduled Outage | Construction | To install new Poles | None | None | 19 | 185 | 59 | Central | UW13
127583 | 2013-09-11 | Scheduled Outage | Construction | Connect new primary and transfer plant supply to new circuit | None | None | 45 | 275 | 206 | Central | UN03
127586 | 2013-09-11 | Defective Equipment | Defective Equipment/ Material | Defective Transformer | O/H Transformer | O/H Transformer (1ph) | 9 | 256 | 38 | South | 84F2
127590 | 2013-09-11 | Lightning | Lightning | Adverse weather (lightning) caused G36 to burn up and trip the 7F1 CB | O/H Switchgear | Fused Cutout | 0 | 3 | 0 | East | 7F1
127590 | 2013-09-11 | Lightning | Lightning | Adverse weather (lightning) caused G36 to burn up and trip the 7F1 CB | O/H Switchgear | Fused Cutout | 71 | 238 | 282 | East | 7F1
127590 | 2013-09-11 | Lightning | Lightning | Adverse weather (lightning) caused G36 to burn up and trip the 7F1 CB | O/H Switchgear | Fused Cutout | 175 | 8 | 23 | East | 7F1
127590 | 2013-09-11 | Lightning | Lightning | Adverse weather (lightning) caused G36 to burn up and trip the 7F1 CB | O/H Switchgear | Fused Cutout | 239 | 2 | 8 | East | 7F1
127590 | 2013-09-11 | Lightning | Lightning | Adverse weather (lightning) caused G36 to burn up and trip the 7F1 CB | O/H Switchgear | Fused Cutout | 374 | 39 | 243 | East | 7F1
127590 | 2013-09-11 | Lightning | Lightning | Adverse weather (lightning) caused G36 to burn up and trip the 7F1 CB | O/H Switchgear | Fused Cutout | 3442 | 42 | 2409 | East | 7F1
127593 | 2013-09-11 | Defective Equipment | Electrical Failure | Suspected failed switch gear at SC3735 | U/G Switchgear | Live-Front | 71 | 246 | 291 | East | 7F1
127594 | 2013-09-11 | Lightning | Lightning | Lightning | O/H Transformer | O/H Transformer (1ph) | 1 | 187 | 3 | Central | TD05
127594 | 2013-09-11 | Lightning | Lightning | Lightning | O/H Transformer | O/H Transformer (1ph) | 463 | 228 | 1759 | Central | TD05
127596 | 2013-09-12 | Scheduled Outage | Construction | transfer switches and cable to new pole. | None | None | 1 | 181 | 3 | Central | SK10
127597 | 2013-09-12 | Scheduled Outage | Construction | Transformers #X33961 and X33962 opened by crew for circuit reconfiguration | None | None | 48 | 150 | 120 | Central | UW13
127598 | 2013-09-12 | Scheduled Outage | Construction | Transformer #X23017 opened by crew for pole replacement | None | None | 13 | 210 | 46 | East | AA02
127599 | 2013-09-12 | Scheduled Outage | Maintenance | cable injections | None | None | 29 | 228 | 110 | East | AN05
127600 | 2013-09-12 | Scheduled Outage | Construction | change leaker | None | None | 8 | 152 | 20 | East | 77M1
127602 | 2013-09-12 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One Almonte transformer gas. Munster F3 load was being carried by Rabbits from Beckwith. Load from 43F3 being supplied through rabbits from Beckwith restored to Munster F2 supply 07:57 RX2048 closed picking up load from Beckwi | None | None | 53 | 123 | 109 | West | BECKF2
127602 | 2013-09-12 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One Almonte transformer gas. Munster F3 load was being carried by Rabbits from Beckwith. Load from 43F3 being supplied through rabbits from Beckwith restored to Munster F2 supply 07:57 RX2048 closed picking up load from Beckwi | None | None | 159 | 39 | 103 | West | BECKF2
127602 | 2013-09-12 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One Almonte transformer gas. Munster F3 load was being carried by Rabbits from Beckwith. Load from 43F3 being supplied through rabbits from Beckwith restored to Munster F2 supply 07:57 RX2048 closed picking up load from Beckwi | None | None | 358 | 12 | 72 | West | BECKF2
127602 | 2013-09-12 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One Almonte transformer gas. Munster F3 load was being carried by Rabbits from Beckwith. Load from 43F3 being supplied through rabbits from Beckwith restored to Munster F2 supply 07:57 RX2048 closed picking up load from Beckwi | None | None | 422 | 207 | 1456 | West | 43F3
127602 | 2013-09-12 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One Almonte transformer gas. Munster F3 load was being carried by Rabbits from Beckwith. Load from 43F3 being supplied through rabbits from Beckwith restored to Munster F2 supply 07:57 RX2048 closed picking up load from Beckwi | None | None | 637 | 356 | 3780 | West | BECKF2
127604 | 2013-09-12 | Foreign Interference | Dig-In | cable fault | U/G Cable | Unknown \ Other | 8 | 860 | 115 | East | BCHF5
127604 | 2013-09-12 | Foreign Interference | Dig-In | cable fault | U/G Cable | Unknown \ Other | 42 | 50 | 35 | East | BCHF5
127607 | 2013-09-13 | Adverse Environment | Fire | Fire Dept reports electrical contact at 320 Olmstead on the secondary side. Power off for fire rescue. | None | None | 588 | 59 | 578 | East | UT06
127609 | 2013-09-13 | Scheduled Outage | Maintenance | TN8906CZZ was isolated to allow the crew to make repair at the metering cabinnet that was damage during previous storm. | None | None | 1 | 67 | 1 | West | ALEXF2
127610 | 2013-09-13 | Scheduled Outage | Maintenance | TN8906CZZ was isolated the second time to make minor adjusments with the metering cabinet | None | None | 1 | 37 | 1 | West | ALEXF2
127611 | 2013-09-14 | Scheduled Outage | Construction | replace damaged transformer | None | None | 7 | 299 | 35 | East | 77M2
127612 | 2013-09-14 | Scheduled Outage | Construction | transferring primary to new pole | None | None | 13 | 280 | 61 | Central | UN03
127613 | 2013-09-14 | Scheduled Outage | Construction | Installing new primary cables & replacing o/h switches at V403 | None | None | 1 | 625 | 10 | Central | SH02
127614 | 2013-09-14 | Scheduled Outage | Construction | Transfer hydro plant to new poles | None | None | 15 | 455 | 114 | Central | UN03
127615 | 2013-09-14 | Scheduled Outage | Construction | replace a defective switch. | None | None | 1 | 285 | 5 | South | 200F1
127617 | 2013-09-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X31721 fuse was found blown due to squirrel contact. | None | None | 11 | 146 | 27 | Central | TH11-NIU
127618 | 2013-09-15 | Scheduled Outage | Construction | Replace transformer & o/h switch | None | None | 1 | 600 | 10 | Central | UC01
127619 | 2013-09-15 | Scheduled Outage | Construction | VOLTAGE CONVERSION FROM 8KV TO 27KV | None | None | 1 | 347 | 6 | South | 145F4
127622 | 2013-09-16 | Scheduled Outage | Maintenance | Cable injection program | None | None | 16 | 303 | 81 | East | AN05
127623 | 2013-09-16 | Scheduled Outage | Construction | At 09:32, 27Kv transformer 20048 was isolated to allow crews to replace leaking transformer. 1 customer affected for 103 minutes. Beckwith (BECKF2) ID #127623 | None | None | 1 | 103 | 2 | West | BECKF2
127625 | 2013-09-16 | Scheduled Outage | Maintenance | At 09:20, 27KV transformer TP9901 was isolated to allow crews to repair ground bushing. 16 customers affected for 70 minutes. Briddlewood (BRDF2) ID #127625 | None | None | 16 | 70 | 19 | West | BRDF2
127626 | 2013-09-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33960 AND X33961 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 49 | 130 | 106 | Central | UW13
127628 | 2013-09-16 | Scheduled Outage | Construction | Transformer #X31597 opened up by crew for a service upgrade | None | None | 8 | 45 | 6 | Central | UC06
127629 | 2013-09-16 | Scheduled Outage | Construction | Transformer #X23017 opened by crew to install a new pole | None | None | 13 | 180 | 39 | East | AA02
127630 | 2013-09-16 | Scheduled Outage | Construction | Transformer #X30939 opened by crew to transfer plant | None | None | 8 | 180 | 24 | Central | SK11
127631 | 2013-09-17 | Scheduled Outage | Maintenance | Cable injection program. | None | None | 15 | 6 | 2 | East | AN05
127631 | 2013-09-17 | Scheduled Outage | Maintenance | Cable injection program. | None | None | 30 | 280 | 140 | East | AN05
127632 | 2013-09-17 | Scheduled Outage | Construction | Transformer TE1388 at 2 Woodvale was isolated to allow crew to replace leaking transformer | None | None | 22 | 475 | 174 | South | 170F1
127633 | 2013-09-17 | Scheduled Outage | Construction | 15 R phas epadmount transformers on Glen Meadows and Glenrill were isolated to allow crew to re arrange feeds coming out of new SC1576 | None | None | 177 | 297 | 876 | West | BRDF2
127634 | 2013-09-17 | Adverse Environment | Flood | Water damage in customer main switch. | Vault Equipment | Switch | 1 | 1567 | 26 | Central | UC03
127635 | 2013-09-17 | Scheduled Outage | Construction | Transformer X30939-1671407 at 244 Wilbrod St. isolated to transfer secondary buss to new pole | None | None | 8 | 223 | 30 | Central | SK11
127637 | 2013-09-17 | Scheduled Outage | Construction | Transformer X31579 at 1255 Highgate Rd. isolated to install new poles with a crane. | None | None | 10 | 150 | 25 | Central | UW13
127638 | 2013-09-17 | Scheduled Outage | Construction | Transformer X32703 at 2415 Cheshire Rd. isolated to install new poles with a crane. | None | None | 13 | 150 | 32 | Central | UW13
127639 | 2013-09-17 | Scheduled Outage | Construction | Transformer X23016 at 309 Altha Ave. isolated for pole replacement | None | None | 3 | 165 | 8 | East | AC14
127642 | 2013-09-17 | Scheduled Outage | Construction | Transformers #X31576 and X31577 opened by crew to install new poles with crane | None | None | 29 | 285 | 138 | Central | UW13
127644 | 2013-09-18 | Scheduled Outage | Construction | To refeeed existing vault from new Hydro pole. | None | None | 1 | 325 | 5 | Central | UD02
127646 | 2013-09-18 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | XLPE | 2 | 19 | 1 | Central | TR2TS
127646 | 2013-09-18 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | XLPE | 178 | 6 | 18 | Central | TR2TS
127646 | 2013-09-18 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | XLPE | 178 | 9 | 27 | Central | TR2TS
127646 | 2013-09-18 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | XLPE | 360 | 59 | 354 | Central | TR2TS
127647 | 2013-09-18 | Scheduled Outage | Construction | Transformer VE7 at 90 Woodridge was isolated to alow crew to remove VE7 from service and energize new TP7672. | None | None | 1 | 451 | 8 | South | 49F4
127649 | 2013-09-18 | Scheduled Outage | Construction | Transformer #X35116 opened by crew to transfer hydro plant | None | None | 16 | 455 | 121 | Central | UW13
127650 | 2013-09-18 | Scheduled Outage | Maintenance | Cable injection program. | None | None | 17 | 223 | 63 | West | BRDF1
127651 | 2013-09-18 | Loss Of Supply | Transmission Inadvertent | Loss of Supply from Hydro One. BECKF2 Blue phase only. H1 Crews dispatched, found defective switch | None | None | 195 | 232 | 754 | West | BECKF2
127652 | 2013-09-19 | Scheduled Outage | Construction | Transfer cables to new pole | None | None | 13 | 250 | 54 | Central | UN03
127653 | 2013-09-19 | Scheduled Outage | Construction | At 9:08 am, vault V132 at 100 Cobourg was isolated to allow crews to replace PCB transformers. 1 customer was interrupted for 370 minutes. Augusta UD (UD06) ID# 127653. | None | None | 1 | 370 | 6 | Central | UD06
127656 | 2013-09-19 | Scheduled Outage | Construction | 8kv transformer TE1031 at 42 Brockington was isolated to allow for replacement of leaking transformer and soil remediation affecting 8 customers for 570 minutes, 87F7, Centerpoint, ID # 127656 | None | None | 8 | 570 | 76 | South | 87F7
127657 | 2013-09-19 | Defective Equipment | Defective Equipment/ Material | Customers main defective at 19 Grenfell, PC10c #8252 established at O/H TX X37073 by Sam Gibson, issued to I-Tech electric. 1 customer affected for 350 minutes. Merivale (72F7) ID #127657 | Customer Owned | Customer-Owned | 1 | 350 | 6 | South | 72F7
127659 | 2013-09-20 | Foreign Interference | Dig-In | TM3UC circuit tripped due to contactor cutting live underground primary cable between S27059 and VT131. PPH at S27059 blew as well. | U/G Cable | XLPE | 1 | 5 | 0 | Central | TM3UC
127659 | 2013-09-20 | Foreign Interference | Dig-In | TM3UC circuit tripped due to contactor cutting live underground primary cable between S27059 and VT131. PPH at S27059 blew as well. | U/G Cable | XLPE | 34 | 5 | 3 | Central | TM3UC
127659 | 2013-09-20 | Foreign Interference | Dig-In | TM3UC circuit tripped due to contactor cutting live underground primary cable between S27059 and VT131. PPH at S27059 blew as well. | U/G Cable | XLPE | 35 | 4 | 2 | Central | TM3UC
127659 | 2013-09-20 | Foreign Interference | Dig-In | TM3UC circuit tripped due to contactor cutting live underground primary cable between S27059 and VT131. PPH at S27059 blew as well. | U/G Cable | XLPE | 38 | 2 | 1 | Central | TM3UC
127659 | 2013-09-20 | Foreign Interference | Dig-In | TM3UC circuit tripped due to contactor cutting live underground primary cable between S27059 and VT131. PPH at S27059 blew as well. | U/G Cable | XLPE | 39 | 39 | 25 | Central | TM3UC
127660 | 2013-09-20 | Defective Equipment | Defective Equipment/ Material | Transformer X24293 at 1359 Gosset St. isolated to replace connections at pole for 1118 Parisien St. | O/H Conductor | O/H Conductor | 5 | 35 | 3 | East | 6F4
127662 | 2013-09-21 | Scheduled Outage | Construction | Transformer #X21682 opened by crew to replace connections at the transformer | None | None | 5 | 60 | 5 | Central | AD07
127663 | 2013-09-21 | Defective Equipment | Defective Equipment/ Material | Transformer X32589 at 612 Rowandwood opened due to defective transformer cut out. | O/H Switchgear | Fused Cutout | 5 | 46 | 4 | Central | TD01
127665 | 2013-09-22 | Defective Equipment | Mechanical Failure | The Epworth 58F2 A/R due to defective cut out and arrester at transformer fuse at X36225 at 6 Leaver. | U/G Cable Attachement | Arrester | 119 | 119 | 236 | South | EPWF2
127668 | 2013-09-22 | Scheduled Outage | Construction | moving plant to new pole | None | None | 1 | 314 | 5 | Central | UC01
127669 | 2013-09-22 | Unknown/Other | Unknown | Crews found Red and White phase of S22309 blown, no cause found after patrolling they refused and restored power. Hinchey (TH01) ID#127669 | None | None | 261 | 149 | 648 | Central | TH01
127671 | 2013-09-23 | Scheduled Outage | Construction | TP3963 and TP3964 on Rivershore Cres. Isolated to allow crews to terminate new cables. | None | None | 21 | 200 | 70 | East | BCHF5
127672 | 2013-09-23 | Scheduled Outage | Construction | Transformer #X29795 opened by crew to transfer plant to new pole. | None | None | 4 | 180 | 12 | Central | SR03
127673 | 2013-09-23 | Scheduled Outage | Construction | Transformer X30984 at 386 Wilbrod St. Isolated to allow for pole change and to change a broken cutout. | None | None | 11 | 180 | 33 | Central | UN03
127674 | 2013-09-23 | Scheduled Outage | Construction | TP5103 isolated to change leaking transfromer. | None | None | 5 | 150 | 12 | West | JKGF4
127675 | 2013-09-23 | Defective Equipment | Electrical Failure | White phase cable fault between TE1055 and TP6992. First stage of restoration residential customers restored. Second stage was school off 3 phase transformer. | U/G Cable | Transition Splice | 1 | 53 | 1 | East | 77M1
127675 | 2013-09-23 | Defective Equipment | Electrical Failure | White phase cable fault between TE1055 and TP6992. First stage of restoration residential customers restored. Second stage was school off 3 phase transformer. | U/G Cable | Transition Splice | 113 | 95 | 179 | East | 77M1
127676 | 2013-09-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35116 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 16 | 295 | 79 | Central | UW13
127679 | 2013-09-24 | Scheduled Outage | Construction | Install new poles and transfer plant. | None | None | 25 | 421 | 175 | South | 49F6
127681 | 2013-09-24 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31577 AND X31576 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 29 | 300 | 145 | Central | UW13
127682 | 2013-09-25 | Scheduled Outage | Construction | Install new poles & transfer O/H plant | None | None | 25 | 350 | 146 | South | 49F6
127683 | 2013-09-25 | Scheduled Outage | Construction | 145F4 ovehead from S22011 to EOL isolated to allow crews to change insulators | None | None | 1 | 303 | 5 | South | 145F4
127684 | 2013-09-25 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change a defective transformer | None | None | 10 | 122 | 20 | East | CYRF4
127685 | 2013-09-25 | Foreign Interference | Vandalism/Sabotage | B phase fuse at S28321 opened due to 2 broken poles on Via Venus Pvt. On the Rockcliffe Airbase. Evidence of vandalism found on poles. Affected section of overhead cut clear and line restored. | Pole | Pole | 14 | 110 | 26 | East | AP04
127686 | 2013-09-26 | Scheduled Outage | Construction | Transformer TP6399 at 56 Knollsbrook was isolated to allow crew to replace leaking transformer. | None | None | 12 | 563 | 113 | South | 140F1
127687 | 2013-09-26 | Scheduled Outage | Vegetation Management | TD01-B blue was isolated from S16415 to end of line. To allow tree trimmers to trim trees in the area. | None | None | 23 | 270 | 104 | Central | TD01
127688 | 2013-09-26 | Foreign Interference | Wildlife (Bird/Animal) | The Limebank 7F1 circuit A/Rdue to cro contact at pole X06319 at 57 Fairpark | None | None | 1 | 134 | 2 | East | 7F1
127691 | 2013-09-26 | Scheduled Outage | Construction | To cut over TP9261 from the R phase to the B phase | None | None | 12 | 174 | 35 | West | BRDF2
127692 | 2013-09-26 | Scheduled Outage | Construction | To transfer secondary plant to a new pole | None | None | 50 | 260 | 217 | Central | UN03
127693 | 2013-09-26 | Unknown/Other | Unknown | Fuse at S314 opened. Patroled, found no cause. | None | None | 4 | 96 | 6 | East | 77M5
127695 | 2013-09-26 | Foreign Interference | Vehicle | 27kV transformer TE1329 at 2646 Hunters Pointisolated to allow crews to place it back on its base after it was hit by a car. 8 customers affected for 26 min. Uplands (4801F8) | None | None | 8 | 23 | 3 | East | 4801F8
127696 | 2013-09-27 | Scheduled Outage | Construction | Transformer TP8412 at 120 Terrence Mathews was isolated to allow contractor to install secondary cables into TP8412 | None | None | 22 | 286 | 105 | West | BRDF1
127697 | 2013-09-27 | Foreign Interference | Vehicle | MVA destroyed pole on Prince of Wales | Pole | Pole | 6 | 351 | 35 | East | 7F2
127697 | 2013-09-27 | Foreign Interference | Vehicle | MVA destroyed pole on Prince of Wales | Pole | Pole | 37 | 105 | 65 | East | 7F2
127697 | 2013-09-27 | Foreign Interference | Vehicle | MVA destroyed pole on Prince of Wales | Pole | Pole | 46 | 27 | 21 | East | 7F2
127698 | 2013-09-28 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace the concrete base & transformer 7628 | None | None | 22 | 430 | 158 | West | JKGF4
127699 | 2013-09-29 | Adverse Environment | Fire | Transformer X27326 opened to allow crew to disconnect secondary service due to fire. | None | None | 17 | 28 | 8 | East | TB06
127700 | 2013-09-29 | Scheduled Outage | Construction | VE27 @ 10 BowhillVE27 was isolated to the crews to pull in cable | None | None | 1 | 225 | 4 | South | 190F6
127701 | 2013-09-29 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X31712 (SQUIRREL CONTACT) | None | None | 5 | 58 | 5 | Central | TH11-NIU
127702 | 2013-09-30 | Scheduled Outage | Construction | At 8:47 am, UW14 white phase was isolated from S17304 at Rideout and Rustic to allow crew to install poles and transfer plant. 21 customers were interrupted for 328 minutes. Woodroffe DS (UW14) ID#127702. | None | None | 21 | 328 | 115 | Central | UW14
127705 | 2013-09-30 | Defective Equipment | Mechanical Failure | 5301 cable riser feeding VT217 at 2575 Sheffield blew causing 5301 circuit to trip. Cable riser blew due to the cable pinching caused by the pole sinking. | Pole | Pole | 1 | 4871 | 81 | East | 5301
127705 | 2013-09-30 | Defective Equipment | Mechanical Failure | 5301 cable riser feeding VT217 at 2575 Sheffield blew causing 5301 circuit to trip. Cable riser blew due to the cable pinching caused by the pole sinking. | Pole | Pole | 25 | 40 | 17 | East | 5301
127706 | 2013-09-30 | Scheduled Outage | Construction | At 12:39 pm, UW14 red phase section fed from S11001 was isolated to allow crew to install poles and transfer plant. 33 customers were interrupted for 281 minutes. Woodroffe DS (UW14) ID# 127706. | None | None | 33 | 281 | 155 | Central | UW14
127708 | 2013-10-01 | Scheduled Outage | Construction | At 08:35, 49F6 O/H sectyion from S12290 to S961 was isolated to alow crews to install new poles and transfer plant. 33 customers affected for minutes. Bayshore (49F6) ID 127708 | None | None | 33 | 340 | 187 | South | 49F6
127709 | 2013-10-01 | Scheduled Outage | Vegetation Management | Transformer #X17835 opened by crew to drop a service for Forestry crew | None | None | 16 | 50 | 13 | East | AA02
127710 | 2013-10-01 | Scheduled Outage | Construction | To allow customer to pull in new service | None | None | 1 | 155 | 3 | East | 77M1
127711 | 2013-10-01 | Scheduled Outage | Construction | Replace poles | None | None | 21 | 170 | 60 | Central | UD04
127712 | 2013-10-01 | Scheduled Outage | Construction | At 13:35, 27KV transformer 4146 at 53 Haywood was isolated to allow crews to replace leaking transformer. 13 customers affected for 117 minutes. Briddlewood (BRDF4) ID #127712 | None | None | 13 | 117 | 25 | West | BRDF4
127713 | 2013-10-01 | Scheduled Outage | Construction | Transformer #X32701 opened by crew to transfer plant | None | None | 6 | 210 | 21 | Central | UW13
127714 | 2013-10-01 | Defective Equipment | Defective Equipment/ Material | Transformer X32291 at 613 Highland Ave. Isolated to replace transformer switch | O/H Switchgear | Fused Cutout | 13 | 19 | 4 | Central | AH04
127715 | 2013-10-02 | Scheduled Outage | Construction | tp2788 AT 196 Tandalee was isolated for soil remediation affecting 16 customers, BRDF2 Bridlewood | None | None | 16 | 500 | 133 | West | BRDF2
127716 | 2013-10-02 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X22829 opened up due to squirrel contact | None | None | 12 | 75 | 15 | East | 4801F8
127717 | 2013-10-02 | Scheduled Outage | Construction | Install new plant between S961 and S12290 | None | None | 33 | 239 | 131 | South | 49F6
127718 | 2013-10-02 | Scheduled Outage | Construction | At 12:09 pm, UW13 red phase fed from S13406 on Cheshire was isolated to allow crew to transfer customers from UW13 to UW14. 27 customer were interrupted for 311 minutes. Woodroffe (UW13) ID# 127718. | None | None | 27 | 311 | 140 | Central | UW14
127719 | 2013-10-02 | Scheduled Outage | Maintenance | At 10:15, 8 KV transformer was isolated to allow crews to perform a transformer test and contractor to perform secodary maintenance. 1 customer affected for 195 minutes. Rideau Heights (180F6) ID 127719 | None | None | 1 | 195 | 3 | South | 180F6
127720 | 2013-10-02 | Scheduled Outage | Construction | At 09:40 27KV tansformer TP8018 at Kennacraig Rd was isolated to allow crews to install new cable between TP8018 and TP8026. 30 customers affecetd for 102 minutes. Fallow Field (FAL03) ID #127720 | None | None | 30 | 102 | 51 | South | FAL03
127721 | 2013-10-02 | Scheduled Outage | Vegetation Management | Tree trimming | None | None | 3 | 210 | 10 | South | 130F2
127723 | 2013-10-03 | Scheduled Outage | Construction | To allow Sproule Electric line crews to transfer cables & switches to a new pole | None | None | 42 | 200 | 140 | Central | SK10
127725 | 2013-10-03 | Scheduled Outage | Vegetation Management | Tree Removal | None | None | 12 | 260 | 52 | Central | TD01
127726 | 2013-10-03 | Scheduled Outage | Construction | Energize 3 new transformers | None | None | 7 | 100 | 12 | West | BRDF2
127727 | 2013-10-03 | Scheduled Outage | Forced Switching | Load transfers through the rabbits | None | None | 210 | 17 | 60 | West | 43F3
127728 | 2013-10-03 | Scheduled Outage | Forced Switching | Load transfer through Rabbits | None | None | 213 | 5 | 18 | West | 43F2
127729 | 2013-10-03 | Unknown/Other | Unknown | Circuit patrolled nothing found refused Swith 412 white and held. | None | None | 88 | 66 | 97 | South | 170F1
127730 | 2013-10-03 | Scheduled Outage | Construction | Transformer #X29944 opened by crew to drop a triplex service | None | None | 17 | 44 | 12 | Central | SR02
127731 | 2013-10-04 | Scheduled Outage | Construction | Replace defective transformer | None | None | 10 | 20 | 3 | South | 140F2
127733 | 2013-10-04 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32446 opened up due to squirrel contact. | None | None | 4 | 154 | 10 | Central | TW22
127734 | 2013-10-04 | Scheduled Outage | Construction | Replacing Pothead on S159 in VT890 | None | None | 102 | 180 | 306 | Central | 503
127735 | 2013-05-10 | Scheduled Outage | Construction | A9M3 from S26807 to EOL including the ALEXF3 betweenS18527, SC4528-L1 and RX2047 and RHNF1 between Temp 148 and X09298 was isolated toa llow crew to commission new 44KV O/H line at Shea and Fernbank, installing pole and transfering plant at River Oaks an | None | None | 0 | 213120 | 0 | West | ALEXF3
127735 | 2013-05-10 | Scheduled Outage | Construction | A9M3 from S26807 to EOL including the ALEXF3 betweenS18527, SC4528-L1 and RX2047 and RHNF1 between Temp 148 and X09298 was isolated toa llow crew to commission new 44KV O/H line at Shea and Fernbank, installing pole and transfering plant at River Oaks an | None | None | 0 | 213120 | 0 | West | RHNF1
127735 | 2013-10-05 | Scheduled Outage | Construction | A9M3 from S26807 to EOL including the ALEXF3 betweenS18527, SC4528-L1 and RX2047 and RHNF1 between Temp 148 and X09298 was isolated toa llow crew to commission new 44KV O/H line at Shea and Fernbank, installing pole and transfering plant at River Oaks an | None | None | 1 | 1 | 0 | West | A9M3
127735 | 2013-10-05 | Scheduled Outage | Construction | A9M3 from S26807 to EOL including the ALEXF3 betweenS18527, SC4528-L1 and RX2047 and RHNF1 between Temp 148 and X09298 was isolated toa llow crew to commission new 44KV O/H line at Shea and Fernbank, installing pole and transfering plant at River Oaks an | None | None | 2 | 539 | 18 | West | A9M3
127737 | 2013-10-05 | Scheduled Outage | Maintenance | Planned isolation of TVM2855CHZ to clean and torque vault , and service main breaker. | None | None | 1 | 318 | 5 | Central | TL3SB
127738 | 2013-10-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | branches in the wires and transformer X29473 | None | None | 5 | 89 | 7 | East | SO12
127739 | 2013-10-06 | Scheduled Outage | Construction | VE27 at 10 Bowhill was isolated to allow crew to abandon old cables from SE7 and energize new cable from new riser S25922 | None | None | 1 | 330 | 6 | South | 190F6
127740 | 2013-10-06 | Scheduled Outage | Maintenance | Hydro Ottawa Metering department to repair defective metering device. | None | None | 1 | 60 | 1 | Central | 618
127743 | 2013-10-06 | Foreign Interference | Wildlife (Bird/Animal) | Installed new cutout and bird guard on top of transformer X09703. | O/H Switchgear | Fused Cutout | 12 | 150 | 30 | West | JKGF4
127744 | 2013-10-06 | Foreign Interference | Wildlife (Bird/Animal) | Refused X40220 at 120 John Aselford Dr. - crow | None | None | 1 | 121 | 2 | West | MWDF3
127745 | 2013-10-06 | Defective Equipment | Moisture Ingress | The 7F4 CB A/R due to defective cut out at 5217 Downey | O/H Switchgear | Fused Cutout | 17 | 81 | 23 | East | 7F4
127747 | 2013-10-07 | Scheduled Outage | Construction | Transformer #X44323 opened by crew for a voltage conversion | None | None | 4 | 28 | 2 | South | 145F4
127748 | 2013-10-07 | Scheduled Outage | Construction | NPTE0313 WAS OPENED BY CREW FOR A CUSTOMER UPGRADE | None | None | 21 | 31 | 11 | South | 200F5
127749 | 2013-10-07 | Scheduled Outage | Construction | Transformer X31218-1668248 isolated for transfer of plant to new pole. | None | None | 14 | 191 | 45 | Central | UN03
127750 | 2013-10-07 | Scheduled Outage | Construction | Transformer X31219 at 199 Daly Ave. isolated to allow for transfer of plant | None | None | 15 | 191 | 48 | Central | UN03
127752 | 2013-10-07 | Scheduled Outage | Construction | The 43F3 Load at Munster DS was inerrupted to allow crew to perform out of phase switching through the rabbits | None | None | 210 | 3 | 10 | West | 43F2
127753 | 2013-10-07 | Scheduled Outage | Construction | The 43F2 Load at Munster DS was inerrupted to allow crew to perform out of phase switching through the rabbits | None | None | 213 | 2 | 7 | West | 43F2
127754 | 2013-10-07 | Scheduled Outage | Construction | Transformer 2241 at 51 Aird Place was isolated to allow crew to replace leaking transformer. | None | None | 9 | 158 | 24 | West | BRDF4
127755 | 2013-10-07 | Defective Equipment | Defective Equipment/ Material | G605B at 5079 Downey opened due to defective fuse. | O/H Switchgear | Fused Cutout | 17 | 94 | 27 | East | 7F4
127756 | 2013-10-07 | Scheduled Outage | Construction | Transformer #TE313 isolated by crew for a service upgrade | None | None | 21 | 29 | 10 | South | 200F5
127757 | 2013-10-07 | Defective Equipment | Electrical Failure | Blown Arrestor on the TO3UT white phase at the VT180 riser and on the TO3UT blue phase at the TO-50 riser caused the TO30 (TO3UT) breaker to open. | Pole Attachement | Arrester | 598 | 71 | 708 | East | TO3UT
127758 | 2013-10-07 | Unknown/Other | Unknown | TO30 (TO3UT) circuit tripped open again 10 minutes after restoring. Power restored to the backup circuits. Circuit was patrolled by Greg Bell, nothing was found. Circuit isolated for crew to check out. | Unknown \ Other | Unknown \ Other | 1 | 8 | 0 | East | TO3UT
127758 | 2013-10-07 | Unknown/Other | Unknown | TO30 (TO3UT) circuit tripped open again 10 minutes after restoring. Power restored to the backup circuits. Circuit was patrolled by Greg Bell, nothing was found. Circuit isolated for crew to check out. | Unknown \ Other | Unknown \ Other | 2 | 10 | 0 | East | TO3UT
127758 | 2013-10-07 | Unknown/Other | Unknown | TO30 (TO3UT) circuit tripped open again 10 minutes after restoring. Power restored to the backup circuits. Circuit was patrolled by Greg Bell, nothing was found. Circuit isolated for crew to check out. | Unknown \ Other | Unknown \ Other | 356 | 2 | 12 | East | TO3UT
127758 | 2013-10-07 | Unknown/Other | Unknown | TO30 (TO3UT) circuit tripped open again 10 minutes after restoring. Power restored to the backup circuits. Circuit was patrolled by Greg Bell, nothing was found. Circuit isolated for crew to check out. | Unknown \ Other | Unknown \ Other | 598 | 40 | 399 | East | TO3UT
127760 | 2013-10-08 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X37122 opened up due to squirrel contact. | None | None | 9 | 41 | 6 | South | EPWF6
127761 | 2013-10-08 | Scheduled Outage | Construction | 58F1 overhead isolated from S169 to Eol to allow crews to replace a pole. | None | None | 16 | 443 | 118 | South | EPWF1
127763 | 2013-10-08 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32658 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 240 | 40 | Central | UW13
127764 | 2013-10-08 | Scheduled Outage | Forced Switching | Transformers #X21530 and X30107 opened by crew for the Fire Dept due to a gas leak | None | None | 19 | 46 | 15 | Central | SB11
127765 | 2013-10-08 | Scheduled Outage | Construction | Transfomrer 3739 B isolated to replace leaking transformer | None | None | 13 | 118 | 26 | West | MWDF2
127766 | 2013-10-08 | Scheduled Outage | Vegetation Management | Tree Trimming | None | None | 91 | 185 | 281 | East | AE05
127767 | 2013-10-08 | Unknown/Other | Unknown | When energizing new cables at VE50 to check phasing the 6F10 breaker opened. No reason was found. | None | None | 1185 | 18 | 356 | East | 6F10
127769 | 2013-10-08 | Unknown/Other | Unknown | While energizing VE48 to check phasing the 6F7 breaker opened. No reason was found. | None | None | 58 | 26 | 25 | East | 6F7
127770 | 2013-10-08 | Scheduled Outage | Maintenance | PCB transformer replacement and Vault maintenance. | None | None | 1 | 297 | 5 | East | TB2JP
127771 | 2013-10-08 | Scheduled Outage | Construction | VE48 and VE50 were isolated to allow crews to replace primary cables. | None | None | 1 | 450 | 8 | East | 6F10
127771 | 2013-10-08 | Scheduled Outage | Construction | VE48 and VE50 were isolated to allow crews to replace primary cables. | None | None | 1 | 450 | 8 | East | 6F7
127772 | 2013-10-08 | Scheduled Outage | Construction | Transfer plant to new pole | None | None | 23 | 328 | 126 | Central | UW14
127773 | 2013-10-08 | Defective Equipment | Mechanical Failure | Live line lead at switch S709 burned off | O/H Conductor | Hot-Line Clamp | 49 | 46 | 38 | South | 87F4
127774 | 2013-10-09 | Scheduled Outage | Construction | TP7420, TP8561, TP7418 and TP7417 isolated to allow crews to re-arrange primary cables and transfer TP7420 and TP8561 to another phase. | None | None | 33 | 189 | 104 | South | FAL01
127775 | 2013-10-09 | Scheduled Outage | Construction | Transformer #X30952 isolated by crew to transfer hydro plant | None | None | 4 | 180 | 12 | Central | UD04
127776 | 2013-10-09 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32435 opened up due to squirrel contact | None | None | 7 | 171 | 20 | Central | TW22
127777 | 2013-10-10 | Scheduled Outage | Construction | Transformer #X31084 isolated by crew for a pole change | None | None | 17 | 35 | 10 | Central | UN03
127778 | 2013-10-10 | Scheduled Outage | Construction | Transformer upgrade & installation of new secondary | None | None | 15 | 125 | 31 | West | BRDF2
127779 | 2013-10-10 | Scheduled Outage | Construction | At 09:05am, 27KV transformer TP7590 at 1670 Barrington was isolated to allow crews to replace leaking transformer. 13 customers affected for minutes. Billberry (77M6) ID #127779 | None | None | 13 | 452 | 98 | East | 77M6
127780 | 2013-10-10 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27820 opened up due to squirrel contact | None | None | 5 | 42 | 4 | Central | 505
127781 | 2013-10-10 | Scheduled Outage | Construction | Transformer #X31855 opened by crew for a service upgrade | None | None | 5 | 150 | 12 | Central | UF07
127782 | 2013-10-11 | Scheduled Outage | Construction | At 09:20am, 13KV transformer kiosk, KT538 located at 103 Ritchie was isolated to allow crews to replace leaking transformer. 18 customers affected for minutes. Lincoln Heights (TD12) ID /127782 | None | None | 18 | 80 | 24 | Central | TD12
127783 | 2013-10-11 | Scheduled Outage | Construction | replace transformer. | None | None | 7 | 276 | 32 | Central | AK02
127784 | 2013-10-11 | Scheduled Outage | Construction | to change leaking transformer | None | None | 1 | 61 | 1 | East | TB2JP
127785 | 2013-10-11 | Scheduled Outage | Maintenance | Transformer #X18971 isolated by crew to replace broken insulator | Pole Attachement | Insulator | 8 | 55 | 7 | East | CYRF1
127786 | 2013-10-11 | Scheduled Outage | Construction | Transformer #X27116 opened by crew to install fly taps | None | None | 5 | 180 | 15 | East | TB14
127787 | 2013-10-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | REFUSED SWITCH FEEDING TRANSFORMER X36078 | None | None | 6 | 189 | 19 | South | 190F5
127788 | 2013-10-11 | Foreign Interference | Wildlife (Bird/Animal) | REFUSED SWITCH FEEDING TRANSFORMER X27820 (SQUIRREL CONTACT) | None | None | 8 | 56 | 7 | Central | 505
127789 | 2013-10-11 | Unknown/Other | Unknown | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32407 | None | None | 6 | 41 | 4 | Central | TD01
127790 | 2013-10-12 | Tree Contacts | Broken Branch | Disconnect sec service for elec to make repairs to S/P | None | None | 3 | 24 | 1 | East | SO03
127791 | 2013-10-12 | Foreign Interference | Wildlife (Bird/Animal) | A squirrel caused transformer X31929 at the rear of 2707 Conn St to open. Hydro Ottawa crews installed squirrel guard on the tranformer bushings and re-fused the transformer. 11 customers were affected for 78 minutes. Lincoln TS (TD14) ID# 127791 | None | None | 11 | 78 | 14 | Central | TD14
127792 | 2013-10-13 | Defective Equipment | Mechanical Failure | Cable fault between S27734 B & TP8273B | U/G Cable | XLPE | 128 | 148 | 316 | East | 77M2
127793 | 2013-10-13 | Foreign Interference | Wildlife (Bird/Animal) | Hot line clamp burnt off and primary broken at X32938 due to squirrel contact. S21516 RWB opened to allow repairs made to primary cct. | None | None | 18 | 40 | 12 | Central | TD05
127793 | 2013-10-13 | Foreign Interference | Wildlife (Bird/Animal) | Hot line clamp burnt off and primary broken at X32938 due to squirrel contact. S21516 RWB opened to allow repairs made to primary cct. | None | None | 40 | 61 | 41 | Central | TD05
127793 | 2013-10-13 | Foreign Interference | Wildlife (Bird/Animal) | Hot line clamp burnt off and primary broken at X32938 due to squirrel contact. S21516 RWB opened to allow repairs made to primary cct. | None | None | 311 | 51 | 264 | Central | TD05
127794 | 2013-10-13 | Foreign Interference | Wildlife (Bird/Animal) | A squirrel made contact with transformer X24103 causing the fused cut-out to open. | None | None | 10 | 86 | 14 | East | 7F4
127795 | 2013-10-13 | Scheduled Outage | Maintenance | Clean & Torque vault Repair ventialation | None | None | 2 | 159 | 5 | Central | TK5TS
127798 | 2013-10-15 | Scheduled Outage | Construction | Transformer replacement | None | None | 19 | 452 | 143 | South | 84F1
127799 | 2013-10-15 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMERS X46734 AND X46732 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 16 | 30 | 8 | Central | UW13
127801 | 2013-10-15 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X23044 opened up due to squirrel contact | None | None | 5 | 131 | 11 | Central | TK2AC
127802 | 2013-10-16 | Scheduled Outage | Maintenance | Transfomer #X29473 isolated by crew to re-insulate primary | None | None | 5 | 81 | 7 | East | SO12
127803 | 2013-10-16 | Defective Equipment | Electrical Failure | S886 red phase on the 200F5 was found blown due to cable fault on the cable section between TE1159 and TE467. | U/G Cable | XLPE | 30 | 36 | 18 | South | 200F5
127803 | 2013-10-16 | Defective Equipment | Electrical Failure | S886 red phase on the 200F5 was found blown due to cable fault on the cable section between TE1159 and TE467. | U/G Cable | XLPE | 50 | 14 | 12 | South | 200F5
127803 | 2013-10-16 | Defective Equipment | Electrical Failure | S886 red phase on the 200F5 was found blown due to cable fault on the cable section between TE1159 and TE467. | U/G Cable | XLPE | 67 | 16 | 18 | South | 200F5
127803 | 2013-10-16 | Defective Equipment | Electrical Failure | S886 red phase on the 200F5 was found blown due to cable fault on the cable section between TE1159 and TE467. | U/G Cable | XLPE | 85 | 33 | 47 | South | 200F5
127803 | 2013-10-16 | Defective Equipment | Electrical Failure | S886 red phase on the 200F5 was found blown due to cable fault on the cable section between TE1159 and TE467. | U/G Cable | XLPE | 107 | 142 | 253 | South | 200F5
127804 | 2013-10-16 | Scheduled Outage | Construction | Transformer #X35061 isolated by crew to install a pole | None | None | 6 | 195 | 20 | Central | UW14
127806 | 2013-10-17 | Scheduled Outage | Maintenance | Vault Maintenance | None | None | 1 | 160 | 3 | East | TO2UB
127807 | 2013-10-17 | Scheduled Outage | Construction | replace transformer | None | None | 30 | 227 | 114 | South | 190F6
127809 | 2013-10-17 | Scheduled Outage | Construction | 4kV vault V779 at 286 wilbrod isolated to allow HOL crews to transfer overhead line to new pole. | None | None | 1 | 311 | 5 | Central | UN03
127811 | 2013-10-17 | Defective Equipment | Electrical Failure | faulted cable section between TE242 and TE241 | U/G Cable | XLPE | 7 | 129 | 15 | East | 8F1
127811 | 2013-10-17 | Defective Equipment | Electrical Failure | faulted cable section between TE242 and TE241 | U/G Cable | XLPE | 130 | 111 | 240 | East | 8F1
127812 | 2013-10-17 | Scheduled Outage | Construction | replace leaking transformer TP8222 | None | None | 14 | 460 | 107 | East | 77M2
127814 | 2013-10-17 | Scheduled Outage | Construction | Transformer X35090-13272641 at 1261 Fellows Rd. Isolated by crew to change a transformer. | None | None | 10 | 186 | 31 | Central | UW14
127815 | 2013-10-17 | Scheduled Outage | Construction | transformer replacment | None | None | 14 | 431 | 101 | South | 190F6
127816 | 2013-10-17 | Scheduled Outage | Construction | Crew removed transformer X44903 at 5897 Fernbank and installed a new one. | None | None | 10 | 150 | 25 | West | RHNF1
127817 | 2013-10-17 | Scheduled Outage | Construction | Transfer existing K704 cable dip to new pole and install new cutout. | None | None | 6 | 106 | 11 | Central | UN03
127818 | 2013-10-17 | Defective Equipment | Defective Equipment/ Material | Melted secondary wiring & burnt off secondary connections causing part power. Burnt seondary lead is causing sparks. Crew had to open X39652 affecting 16 customers. | Secondary \ Service | O/H Service | 16 | 20 | 5 | South | 49F6
127819 | 2013-10-17 | Defective Equipment | Defective Equipment/ Material | Hydro Ottawa on-call crew had to open tranformer X39652 to allow for repairs to melted/damaged secondary conductor | Secondary \ Service | O/H Service | 16 | 100 | 27 | South | 49F6
127820 | 2013-10-18 | Foreign Interference | Wildlife (Bird/Animal) | Replaced blown fuse feeding transformer X23527 | None | None | 8 | 123 | 16 | East | AA04
127821 | 2013-10-18 | Defective Equipment | Electrical Failure | S26669 white phase blew due to cable fault on 77M1 white phase between TP6992 and TE1055. | U/G Cable | XLPE | 112 | 22 | 41 | East | 77M1
127821 | 2013-10-18 | Defective Equipment | Electrical Failure | S26669 white phase blew due to cable fault on 77M1 white phase between TP6992 and TE1055. | U/G Cable | XLPE | 113 | 79 | 149 | East | 77M1
127822 | 2013-10-19 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X31503 opened up due to squirrel contact. Crew refused and installed more squirrel guard. Many squirrel nests around the pole | None | None | 12 | 116 | 23 | Central | TW22
127823 | 2013-10-19 | Scheduled Outage | Construction | At 6:15 am, Transformer 570 at 580 Eagleson was isolated to allow crew to re-arrange overhead conductors. 1 customer was affected for 525 minutes. Bridlewood DS (BRDF2) ID# 127823. | None | None | 1 | 525 | 9 | West | BRDF2
127826 | 2013-10-19 | Lightning | Lightning | Lightening Storm | None | None | 511 | 9 | 77 | Central | UW13
127830 | 2013-10-20 | Scheduled Outage | Construction | At 7:30 am 4kv vault V420 at 64 Isabella and 4kv overhead transformer X30457 at 30 Pretoria were isolated to rearranging overhead primary and secondary for building construction work affecting 8 customers for XX minutes, SB02, Bronson, ID # 127830 | None | None | 1 | 9 | 0 | Central | SB02
127830 | 2013-10-20 | Scheduled Outage | Construction | At 7:30 am 4kv vault V420 at 64 Isabella and 4kv overhead transformer X30457 at 30 Pretoria were isolated to rearranging overhead primary and secondary for building construction work affecting 8 customers for XX minutes, SB02, Bronson, ID # 127830 | None | None | 8 | 265 | 35 | Central | SB02
127831 | 2013-10-20 | Scheduled Outage | Construction | 13kv transformer TP9882 at 2000 Thurston was isolated to allow for transformer base reconstruction, affecting 2 customers for 263 minutes, Elwood, ELW13, ID # 127831 | None | None | 2 | 263 | 9 | East | ELW13
127832 | 2013-10-20 | Scheduled Outage | Construction | At 09:30, 8Kv O/H sections on Mulvagh & Walgate were isolated to allow crews to replace poles. 84 customers were affected for 295 minutes. Parkwood Hills (190F2 & F6) ID#127832 | None | None | 84 | 295 | 413 | South | 190F6
127834 | 2013-10-20 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X38567 opened up due to tree contact | None | None | 5 | 101 | 8 | Central | TD06
127835 | 2013-10-21 | Scheduled Outage | Construction | At 9:50 am 4kv transformer P29 at 190 Dalhousie was isolated to allow replacement of defective transformer and replace dip switches affecting 1 customer for 200 minutes, King Edward sub, SK13, ID # 127835 | None | None | 1 | 200 | 3 | Central | SK13
127836 | 2013-10-21 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35057 (REMOVED FROM SERVICE) AND X35053 TO TRANSFER HYDRO PLANT TO NEW POLE AND TRANSFORMER | None | None | 9 | 232 | 35 | Central | UW14
127838 | 2013-10-21 | Defective Equipment | Electrical Failure | cable fault between TE940 and TE939 | U/G Cable | XLPE | 73 | 48 | 58 | East | 77M6
127838 | 2013-10-21 | Defective Equipment | Electrical Failure | cable fault between TE940 and TE939 | U/G Cable | XLPE | 108 | 83 | 149 | East | 77M6
127839 | 2013-10-22 | Defective Equipment | Defective Equipment/ Material | defective cutout | O/H Switchgear | Fused Cutout | 11 | 80 | 15 | South | 49F6
127840 | 2013-10-22 | Scheduled Outage | Construction | V327 at 119 Daly was isolated to allow crew to install new primary cable from new pole to V327 | None | None | 1 | 58 | 1 | Central | SK10
127841 | 2013-10-22 | Scheduled Outage | Construction | Transformer TE134 at 35 Woodmount was isolated to allow crew to replace transformer and cables | None | None | 12 | 409 | 82 | South | 190F6
127843 | 2013-10-22 | Scheduled Outage | Construction | ISOLATED PAD MOUNT TRANSFORMER NPTE0134 TO TRANSFER HYDRO PLANT | None | None | 12 | 417 | 83 | South | 190F6
127844 | 2013-10-22 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X15155 TO REPLACE BROKEN SWITCH | O/H Switchgear | Fused Cutout | 9 | 10 | 2 | East | 249F2
127845 | 2013-10-23 | Unknown/Other | Unknown | Not yet known. | None | None | 1 | 32 | 1 | Central | 5408
127845 | 2013-10-23 | Unknown/Other | Unknown | Not yet known. | None | None | 74 | 55 | 68 | Central | 5408
127846 | 2013-10-23 | Scheduled Outage | Construction | S20150 to EOL was isolated to allow crew to convert 4KV O/H section to 13KV | None | None | 67 | 232 | 259 | Central | UW14
127847 | 2013-10-23 | Scheduled Outage | Vegetation Management | 624F6 overhead circuit from switch 2198 to EOL isolated tp allow costumer to trim trees | None | None | 1 | 233 | 4 | West | 624F6
127848 | 2013-10-23 | Scheduled Outage | Vegetation Management | tree trimming on customer owned line. | None | None | 1 | 158 | 3 | West | BECKF2
127851 | 2013-10-23 | Scheduled Outage | Construction | Transformer X39654 at 49 Stillwater Dr. isolated for pole change. | None | None | 3 | 120 | 6 | South | 49F6
127852 | 2013-10-23 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X18983 TO REPLACE PRIMARY INSULATORS | None | None | 7 | 210 | 24 | East | CYRF1
127853 | 2013-10-23 | Human Element | Switching Error | 28F2 R phase reclosure tripped open during switching. 238 customers affected for 14 minutes. Richmond South ID #127853 | None | None | 238 | 14 | 56 | West | 28F2
127854 | 2013-10-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X40244 TO REPLACE POLE | None | None | 4 | 180 | 12 | South | 49F6
127855 | 2013-10-24 | Scheduled Outage | Construction | At 9:16 am, transformer TE137 at 9 Bowhill was isolated to allow crew to replace transformer and cables. 12 customers were interrupted for 422 minutes. Parkwood Hills (190F6) ID# 127855. | None | None | 12 | 422 | 84 | South | 190F6
127856 | 2013-10-24 | Scheduled Outage | Maintenance | Repair K348 | None | None | 20 | 81 | 27 | East | AE01
127857 | 2013-10-24 | Scheduled Outage | Construction | Change TE230 | None | None | 10 | 584 | 97 | East | BCHF5
127858 | 2013-10-24 | Scheduled Outage | Construction | At 8:40am, transformer TE306 at 35 Chesterton was isolated to allow crew to replace transformer. 33 customers were interrupted for 240 minutes. Parkwood Hills (190F6) ID# 127858. | None | None | 33 | 240 | 132 | South | 190F6
127860 | 2013-10-24 | Scheduled Outage | Construction | At 9:40am, transformer TP10134 at 1167 Amberwood was isolated to allow crew to perform soil remediation. 10 customers were interrupted for 680 minutes. Cyrville (CYRF4) ID# 127860. | None | None | 10 | 680 | 113 | East | CYRF4
127861 | 2013-10-24 | Scheduled Outage | Construction | Transformer #829 opened by crew to hook up new service | None | None | 4 | 25 | 2 | South | 180F4
127862 | 2013-10-24 | Scheduled Outage | Construction | S19348 opened by crew to install a new pole | None | None | 1 | 70 | 1 | East | LTM01
127863 | 2013-10-24 | Foreign Interference | Wildlife (Bird/Animal) | Switch 215 opened up due to squirrel contact. Crew changed switch, arrestor and installed squirrel guard | O/H Switchgear | Inline Switch | 6 | 168 | 17 | West | 624F6
127864 | 2013-10-24 | Human Element | Improper Construction/installation | Pedastel not connected after TE230 at 2053 Kings grove replaced (now TP9977) affecting 3 customers. TP9977 secondary BUS isolated to allow crews to make connection affecting 10 customers in total. | None | None | 3 | 113 | 6 | East | BCHF5
127864 | 2013-10-24 | Human Element | Improper Construction/installation | Pedastel not connected after TE230 at 2053 Kings grove replaced (now TP9977) affecting 3 customers. TP9977 secondary BUS isolated to allow crews to make connection affecting 10 customers in total. | None | None | 10 | 18 | 3 | East | BCHF5
127865 | 2013-10-25 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X23044 opened up due to squirrel contact | None | None | 5 | 81 | 7 | Central | TK2AC
127866 | 2013-10-25 | Scheduled Outage | Maintenance | To repair G576W | None | None | 12 | 120 | 24 | East | CYRF1
127867 | 2013-10-25 | Foreign Interference | Vehicle | Broken hydro pole due to MVA. Pole is down in trees. | Pole | Pole | 1 | 291 | 5 | South | 200F1
127868 | 2013-10-25 | Defective Equipment | Defective Equipment/ Material | defective eblow on TP9342 caused transformer fuse to open. | U/G Cable Attachement | Elbow \ Insert | 8 | 305 | 41 | South | 49F6
127869 | 2013-10-25 | Foreign Interference | Vehicle | Transformer X35663 at 920 Fisher was opened due to vehicle pulling down triplex at 962 Fisher causing transformer bushing to break | O/H Transformer | Unknown \ Other | 4 | 316 | 21 | Central | AD06
127870 | 2013-10-27 | Scheduled Outage | Construction | P318 at 1804 Carling isolated for transformer change. | None | None | 3 | 574 | 29 | Central | UC03
127871 | 2013-10-27 | Scheduled Outage | Vegetation Management | Painting bldg, and removing weeds in 44KV corridor. | None | None | 1 | 283 | 5 | West | A9M1
127872 | 2013-10-27 | Scheduled Outage | Construction | Install 3 new poles and relocate transformer bank | None | None | 5 | 488 | 41 | South | 180F6
127873 | 2013-10-28 | Scheduled Outage | Construction | V327 at 60 Daly isolated to connect new primary cable from riser. | None | None | 1 | 93 | 2 | Central | SK10
127874 | 2013-10-28 | Scheduled Outage | Construction | replacing minipad and replacing elbows | None | None | 11 | 425 | 78 | East | BCHF5
127875 | 2013-10-28 | Scheduled Outage | Construction | Transformer and cable replacement | None | None | 17 | 435 | 123 | South | 190F6
127876 | 2013-10-28 | Scheduled Outage | Forced Switching | TR09 circuit forced out of service due to pole fire. | Pole | Insulation Failure (Pole Fire) | 1490 | 235 | 5836 | Central | TR09
127877 | 2013-10-28 | Scheduled Outage | Construction | ISOLATED AND REPLACED PAD MOUNT TRANSFORMER NPTE0130 | None | None | 17 | 435 | 123 | South | 190F6
127878 | 2013-10-28 | Scheduled Outage | Construction | P1722 at 1501 Carling isolated to allow crews to connect new secondary service. | None | None | 1 | 135 | 2 | Central | SM16
127879 | 2013-10-29 | Foreign Interference | Vehicle | MVA at Princess and Lisgar caused the white and blue phases at S27812 to blow. | None | None | 3 | 96 | 5 | Central | TK2AC
127880 | 2013-10-29 | Tree Contacts | Falling Tree | A tree brought down the 72F4 white phase conductor west of 109 Burnbank. S407 did not blow. The conductor burnt clear without blowing the fuse. Crew reports it looks like someone cut the tree which in turn fell into the overhead. | O/H Conductor | O/H Conductor | 63 | 131 | 138 | South | 72F4
127881 | 2013-10-29 | Scheduled Outage | Construction | Install new base and transformer. | None | None | 11 | 448 | 82 | East | BCHF3
127882 | 2013-10-29 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 8 | 435 | 58 | East | 77M2
127883 | 2013-10-29 | Scheduled Outage | Construction | Transformer #X39751 opened by crew for a pole change | None | None | 9 | 185 | 28 | South | 49F6
127884 | 2013-10-29 | Scheduled Outage | Construction | Transformer #X39752 opened by crew for a pole change | None | None | 5 | 120 | 10 | South | 49F6
127885 | 2013-10-29 | Foreign Interference | Dig-In | Cable between 676-2 and 6008-1 was core drilled | U/G Cable | Unknown \ Other | 1 | 10 | 0 | West | 624F2
127885 | 2013-10-29 | Foreign Interference | Dig-In | Cable between 676-2 and 6008-1 was core drilled | U/G Cable | Unknown \ Other | 5 | 63 | 5 | West | 624F2
127885 | 2013-10-29 | Foreign Interference | Dig-In | Cable between 676-2 and 6008-1 was core drilled | U/G Cable | Unknown \ Other | 120 | 31 | 62 | West | MWDF4
127885 | 2013-10-29 | Foreign Interference | Dig-In | Cable between 676-2 and 6008-1 was core drilled | U/G Cable | Unknown \ Other | 740 | 31 | 382 | West | 624F2
127886 | 2013-10-29 | Scheduled Outage | Construction | To replace defective conductor. | None | None | 93 | 95 | 147 | South | 49F6
127887 | 2013-10-29 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace defective O/H transformer inside the kiosk enclosure | None | None | 19 | 71 | 22 | Central | AB06
127888 | 2013-10-30 | Scheduled Outage | Construction | Beaconhill Cable replacement project. Transformer TP3963 required replacement along with a new concrete base | None | None | 13 | 412 | 89 | East | BCHF5
127889 | 2013-10-30 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 8 | 115 | 15 | East | 77M6
127890 | 2013-10-30 | Scheduled Outage | Construction | Transformer and cable replacement. | None | None | 29 | 378 | 183 | South | 190F6
127894 | 2013-10-31 | Defective Equipment | Electrical Failure | 8F3 cable fault between TE1669 and TE1249 on the white phase | U/G Cable | XLPE | 22 | 26 | 10 | East | 8F3
127894 | 2013-10-31 | Defective Equipment | Electrical Failure | 8F3 cable fault between TE1669 and TE1249 on the white phase | U/G Cable | XLPE | 1588 | 104 | 2753 | East | 8F3
127895 | 2013-10-31 | Scheduled Outage | Construction | 249F1 B phase section from G321 to Eol was isolated to allow crew to connect B phase O/H from S14366 to S21306 and transfer B phase O/H taps to new B phase | None | None | 68 | 81 | 92 | East | LTM01
127896 | 2013-10-31 | Unknown/Other | Unknown | 7F2 and GR2 A/R, GR1 B phase fuse found open. Circuit patrolled nothing found, GR1 re-fused and closed. | Unknown \ Other | Unknown \ Other | 146 | 126 | 307 | East | 7F4
127897 | 2013-10-31 | Defective Equipment | Mechanical Failure | defective fused cutout at X26967 | O/H Switchgear | Fused Cutout | 17 | 150 | 42 | East | SO03
127899 | 2013-11-01 | Tree Contacts | Falling Tree | Not yet known. | None | None | 81 | 203 | 274 | East | 249F2
127900 | 2013-11-01 | Defective Equipment | Defective Equipment/ Material | S18175 opened due to broken insulator 1 span down of S18175 | Pole Attachement | Insulator | 27 | 199 | 90 | East | UZ12
127901 | 2013-11-01 | Adverse Weather | Extreme Wind | During the wind storm in the Ottawa area the AA03 triped open. Circuit was cosed via SCADA and all load was restored. Circuit to be patrolled | Unknown \ Other | Unknown \ Other | 663 | 123 | 1359 | East | AA03
127902 | 2013-11-01 | Tree Contacts | Falling Tree | Large tree on O/H at rear of 42 Holland | O/H Conductor | O/H Conductor | 27 | 94 | 42 | Central | SM10
127902 | 2013-11-01 | Tree Contacts | Falling Tree | Large tree on O/H at rear of 42 Holland | O/H Conductor | O/H Conductor | 27 | 113 | 51 | Central | SM10
127902 | 2013-11-01 | Tree Contacts | Falling Tree | Large tree on O/H at rear of 42 Holland | O/H Conductor | O/H Conductor | 187 | 15 | 47 | Central | SM10
127903 | 2013-11-01 | Tree Contacts | Falling Tree | tree on overhead at cambrian, and Cedarview | O/H Conductor | O/H Conductor | 4756 | 65 | 5152 | South | FAL03
127903 | 2013-11-01 | Tree Contacts | Falling Tree | tree on overhead at cambrian, and Cedarview | O/H Conductor | O/H Conductor | 4778 | 65 | 5176 | South | FAL01
127906 | 2013-11-01 | Defective Equipment | Defective Equipment/ Material | AN06 A/R/A due to down conductor at Huntclub and Mac St during wind storm | O/H Conductor | Unknown \ Other | 16 | 95 | 25 | East | AN06
127906 | 2013-11-01 | Defective Equipment | Defective Equipment/ Material | AN06 A/R/A due to down conductor at Huntclub and Mac St during wind storm | O/H Conductor | Unknown \ Other | 247 | 70 | 288 | East | AN06
127907 | 2013-11-01 | Adverse Weather | Extreme Wind | The AA03 CB tripped open on during the wind storm. | Unknown \ Other | Unknown \ Other | 663 | 103 | 1138 | East | AA03
127908 | 2013-11-01 | Adverse Weather | Extreme Wind | The TB15 CB A/R and caused the S21380 to open during the wind storm in the Ottawa area | None | None | 192 | 181 | 579 | East | TB15
127909 | 2013-11-01 | Defective Equipment | Defective Equipment/ Material | broken switch pole S987. | Pole | Pole | 793 | 66 | 872 | South | 72F1
127911 | 2013-11-01 | Adverse Weather | Extreme Wind | During the wind storm in the Ottawa area the S503B opened. | None | None | 80 | 110 | 147 | South | 170F3
127912 | 2013-11-01 | Defective Equipment | Defective Equipment/ Material | S26669 W at 6339 Fairgate opened due to burnt off line tap at S26669 | O/H Conductor | Hot-Line Clamp | 70 | 182 | 212 | East | 77M1
127913 | 2013-11-01 | Adverse Weather | Extreme Wind | During the wind strom in the Ottawa Area the AA03 CB tripped open and locked out. Circuit was patrolled and nothing was found. | Unknown \ Other | Unknown \ Other | 663 | 6 | 66 | East | AA03
127914 | 2013-11-01 | Tree Contacts | Falling Tree | During the wind storm in the Ottawa area the S17689 W phase opened due to fallen tree at rear of Adams St | O/H Conductor | O/H Conductor | 34 | 193 | 109 | East | TB06
127915 | 2013-11-01 | Tree Contacts | Falling Tree | tree on overhead at 82 Rothwell. | O/H Conductor | O/H Conductor | 119 | 139 | 276 | East | 8F1
127917 | 2013-11-01 | Defective Equipment | Defective Equipment/ Material | SR01 CB A/R due to down conductor at 141 Concord.Crew reported down conductor burning on the ground. Circuit was then open at request of crew to allow crew to make repairs to down phase. | O/H Conductor | O/H Conductor | 466 | 140 | 1087 | Central | SR01
127918 | 2013-11-01 | Tree Contacts | Falling Tree | Switch 248W on John Aselford opened due to tree on wire at 7 John Aselford. | O/H Conductor | O/H Conductor | 17 | 302 | 86 | West | MWDF3
127920 | 2013-11-01 | Adverse Weather | Extreme Wind | AM00 carrying the AM04 load tripped open during the wind storm. Circuit was closed in and all load was restored. | Unknown \ Other | Unknown \ Other | 228 | 11 | 42 | Central | AM00
127921 | 2013-11-01 | Adverse Weather | Extreme Wind | During the wind storm in the Ottawa area the S13037B opened | O/H Conductor | O/H Conductor | 14 | 563 | 131 | Central | TD01
127922 | 2013-11-01 | Adverse Weather | Extreme Wind | line tap on the white phase broke due to high winds. | O/H Conductor | Ampact | 1400 | 351 | 8190 | South | FAL01
127923 | 2013-11-01 | Tree Contacts | Falling Tree | tree on 170F1 blue phase overhead fed from S202. | O/H Conductor | O/H Conductor | 51 | 158 | 134 | South | 170F1
127924 | 2013-11-01 | Tree Contacts | Falling Tree | S202B opened due to tree on the O/H line at 30 Westwood | None | None | 51 | 213 | 181 | South | 170F1
127925 | 2013-11-01 | Tree Contacts | Falling Tree | tree on overhead | O/H Conductor | O/H Conductor | 84 | 188 | 263 | South | 49F6
127926 | 2013-11-01 | Adverse Weather | Extreme Wind | High winds caused a tree to fall & take down the conductor | O/H Conductor | O/H Conductor | 42 | 422 | 295 | East | TB2JP
127927 | 2013-11-01 | Tree Contacts | Falling Tree | AN04 cct isolated to allow crew to remove tree off primary cct. | O/H Conductor | O/H Conductor | 352 | 133 | 780 | East | AN04
127928 | 2013-11-01 | Adverse Weather | Extreme Wind | High winds caused a tree to fall on the conductor which also caused S206 W to blow. | O/H Conductor | O/H Conductor | 22 | 271 | 99 | East | 7F2
127929 | 2013-11-01 | Defective Equipment | Defective Equipment/ Material | Defective pothead & cable | U/G Cable Attachement | Pothead | 1 | 9523 | 159 | Central | UC06
127930 | 2013-11-02 | Defective Equipment | Defective Equipment/ Material | Transformer X29741 opened to allow crew to repair defective live line clamp. | O/H Conductor | Hot-Line Clamp | 20 | 36 | 12 | East | UQ05
127932 | 2013-11-02 | Tree Contacts | Falling Tree | Tree fell into conductors, causing S13369 R & W phases to blow. The switches had to be jumpered out on the R & W phases. The TW 22 CB was opened to allow Hydro Ottawa crews to safely do this. | None | None | 174 | 360 | 1044 | Central | TW22
127932 | 2013-11-02 | Tree Contacts | Falling Tree | Tree fell into conductors, causing S13369 R & W phases to blow. The switches had to be jumpered out on the R & W phases. The TW 22 CB was opened to allow Hydro Ottawa crews to safely do this. | None | None | 1298 | 4 | 87 | Central | TW22
127933 | 2013-11-02 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 1 | 447 | 7 | East | SO04
127934 | 2013-11-02 | Scheduled Outage | Maintenance | Maintenance | None | None | 1 | 544 | 9 | East | 7F2
127935 | 2013-11-02 | Scheduled Outage | Construction | PCB and switch replacement | None | None | 7 | 181 | 21 | East | UA06
127936 | 2013-11-02 | Defective Equipment | Defective Equipment/ Material | Primary conductor fell while crews were attempting to clear primary that was tangled on the transformer switch. Crews had to do this because they were attempting to open the transfomrer switch to remove an un-safe service. While moving the primary with a | O/H Conductor | O/H Conductor | 60 | 202 | 202 | East | UQ05
127936 | 2013-11-02 | Defective Equipment | Defective Equipment/ Material | Primary conductor fell while crews were attempting to clear primary that was tangled on the transformer switch. Crews had to do this because they were attempting to open the transfomrer switch to remove an un-safe service. While moving the primary with a | O/H Conductor | O/H Conductor | 426 | 27 | 192 | East | UQ05
127937 | 2013-11-02 | Tree Contacts | Broken Branch | Circuit isolated to remove large limb off primary cct. | None | None | 56 | 13 | 12 | West | BECKF2
127938 | 2013-11-03 | Scheduled Outage | Maintenance | To repair ESA deficiencies and broken insulators | None | None | 1 | 385 | 6 | East | 48M4
127939 | 2013-11-04 | Scheduled Outage | Construction | Install new base and primary cables. | None | None | 5 | 431 | 36 | East | BCHF3
127940 | 2013-11-04 | Scheduled Outage | Construction | Transformer and cable replacement. | None | None | 10 | 353 | 59 | South | 190F6
127941 | 2013-11-04 | Scheduled Outage | Vegetation Management | Tree removal | None | None | 46 | 91 | 70 | East | 8F1
127942 | 2013-11-04 | Defective Equipment | Defective Equipment/ Material | Conductor on the ground 5 Pretoria on the SB02 | O/H Conductor | O/H Conductor | 25 | 94 | 39 | Central | SB02
127943 | 2013-11-04 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at transfomer X15666 caused the 249F1 breaker to open and stay open as a crew had hold off protection on the circuit. Crew replaced blown transformer fuse. | None | None | 1 | 44 | 1 | East | LTM01
127943 | 2013-11-04 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at transfomer X15666 caused the 249F1 breaker to open and stay open as a crew had hold off protection on the circuit. Crew replaced blown transformer fuse. | None | None | 3759 | 10 | 626 | East | LTM01
127944 | 2013-11-04 | Scheduled Outage | Construction | Transformer #X35492 opened by crew to make repairs, 110 service burnt clear at the pole | None | None | 4 | 40 | 3 | Central | UC07
127945 | 2013-11-04 | Scheduled Outage | Construction | V365 at 1303 Fellows was isolated to allow crew to transfer O/H taps to new conductor | None | None | 1 | 150 | 2 | Central | UW14
127946 | 2013-11-05 | Scheduled Outage | Construction | 8kV transfromer TP3961 at 534 Rivershore isolated to install new base and connect new primary cable. | None | None | 8 | 568 | 76 | East | BCHF5
127948 | 2013-11-05 | Scheduled Outage | Construction | planned transformer & cable replacement | None | None | 21 | 265 | 93 | South | 190F6
127949 | 2013-11-05 | Scheduled Outage | Construction | Planned interruption, replacing underground cable and transformer. | None | None | 8 | 258 | 34 | South | 190F6
127950 | 2013-11-05 | Scheduled Outage | Maintenance | 8kv transformer TP8544 at 2447 Braeburn was isolated to replace all secondary service connections affecting 17 customers for 251 minutes, Blackburn, 4F8, ID # 127950 | None | None | 17 | 251 | 71 | East | BLKF8
127951 | 2013-11-05 | Unknown/Other | Unknown | REPLACED BLOWN FUSE FEEDING TRANSFORMER X24195 (CAUSE UNKNOWN) | Unknown \ Other | Unknown \ Other | 14 | 98 | 23 | East | 8F3
127952 | 2013-11-05 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X20853 (SQUIRREL CONTACT) | None | None | 12 | 127 | 25 | East | BCHF5
127953 | 2013-11-05 | Foreign Interference | Vehicle | 4kV overhead circuit from pole 54B1D-0130 to EOL isolated to allow crews to repair primary neutral that was broken by a passing truck. | O/H Conductor | O/H Conductor | 16 | 305 | 81 | Central | AK05
127954 | 2013-11-06 | Scheduled Outage | Construction | 8kv transformer TP3860 at 516 Rivershore isolated for replacement affecting 8 customers for XX min, Beaconhill, BCHF3, ID # 127954 | None | None | 8 | 484 | 65 | East | BCHF3
127955 | 2013-11-06 | Scheduled Outage | Construction | Transformer & primary cable replacement | None | None | 11 | 318 | 58 | South | 190F6
127956 | 2013-11-06 | Scheduled Outage | Construction | Soil remediation. (transformer has already been replaced) | None | None | 8 | 424 | 57 | West | BRDF4
127957 | 2013-11-06 | Scheduled Outage | Construction | Transformer #X32001 opened by crew to install a new service | None | None | 8 | 25 | 3 | Central | UL06
127958 | 2013-11-06 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMERS X45489 AND X45485 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 15 | 180 | 45 | Central | UW14
127959 | 2013-11-06 | Tree Contacts | Broken Branch | Crews found S13369 RW fuses blown, patrol discovered branch across two phases at rear of 969 Winnington Ave. | None | None | 151 | 88 | 221 | Central | TW22
127960 | 2013-11-06 | Scheduled Outage | Construction | At 10:15, 4KV vault V460 at 373 Laurier was isolated to allow crews to replace transformers. 1 customer affected for 202 minutes. Henderson (UN07) ID #127960 | None | None | 1 | 202 | 3 | Central | UN07
127961 | 2013-11-07 | Tree Contacts | Broken Branch | Not yet known | None | None | 235 | 81 | 317 | South | 130F2
127963 | 2013-11-07 | Scheduled Outage | Construction | TP3550 isolated to replace leaking transformer. | None | None | 8 | 61 | 8 | West | 624F6
127964 | 2013-11-07 | Scheduled Outage | Construction | Voltage conversion. | None | None | 1 | 193 | 3 | South | 145F4
127965 | 2013-11-07 | Scheduled Outage | Construction | Voltage conversion. | None | None | 1 | 333 | 6 | South | 145F4
127966 | 2013-11-07 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMERS X35061 AND X35055 TO INSTALL NEW POLES | None | None | 16 | 390 | 104 | Central | UW14
127969 | 2013-11-08 | Scheduled Outage | Maintenance | Transformer #X32684 opened by crew for maintenance | None | None | 6 | 100 | 10 | Central | UC02
127970 | 2013-11-08 | Scheduled Outage | Construction | Transformer #X30907 opened by crew to transfer plant | None | None | 10 | 80 | 13 | Central | SK10
127971 | 2013-11-08 | Scheduled Outage | Construction | Transformer X20814 at 2050 Kings Grove Cres. Isolated to transfer plant to new pole. | None | None | 11 | 225 | 41 | East | BCHF3
127972 | 2013-11-08 | Unknown/Other | Unknown | To allow the Hydro Ottawa Metering Dept. To replace a blown fuse | Unknown \ Other | Unknown \ Other | 1 | 45 | 1 | East | TO3UT
127975 | 2013-11-10 | Tree Contacts | Broken Branch | Crews found blown fuse at X32094 due to tree contact. 14 customers affcetd for 77 min. Lincoln Heights (TD01) ID 127975 | None | None | 14 | 77 | 18 | Central | TD01
127976 | 2013-11-10 | Tree Contacts | Broken Branch | Crews found RW fuses blown (Switch not on maps and no nomenclature in field). Patrol found branch across 2 phases | None | None | 60 | 115 | 115 | Central | TW22
127977 | 2013-11-10 | Adverse Environment | Fire | UJ06 CB was opened at the request of Fire department and Hydro Crew to allow crew to cut clear UJ06 R phase O/H section due to working fire at 14 Lebreton | None | None | 17 | 255 | 72 | Central | UJ06
127977 | 2013-11-10 | Adverse Environment | Fire | UJ06 CB was opened at the request of Fire department and Hydro Crew to allow crew to cut clear UJ06 R phase O/H section due to working fire at 14 Lebreton | None | None | 277 | 2 | 9 | Central | UJ06
127979 | 2013-11-10 | Scheduled Outage | Construction | PCB Transformer replacement & customer maintenance | None | None | 1 | 255 | 4 | Central | UX10
127981 | 2013-11-10 | Scheduled Outage | Construction | TP2321 at 4000 Riverside Dr was isolated to allow contractor to install new service. | None | None | 1 | 120 | 2 | East | ELW08
127982 | 2013-11-10 | Tree Contacts | Broken Branch | Branch in the blue phase primary in the rear of 33 Dunvegan caused the conductor to fail with live wires down. This required the breaker to be opened by SCADA to allow for isolation off the damaged primary which left 2 transformers, X24485 and X24482, off | O/H Conductor | O/H Conductor | 9 | 64 | 10 | East | UB04
127982 | 2013-11-10 | Tree Contacts | Broken Branch | Branch in the blue phase primary in the rear of 33 Dunvegan caused the conductor to fail with live wires down. This required the breaker to be opened by SCADA to allow for isolation off the damaged primary which left 2 transformers, X24485 and X24482, off | O/H Conductor | O/H Conductor | 19 | 74 | 23 | East | UB04
127982 | 2013-11-10 | Tree Contacts | Broken Branch | Branch in the blue phase primary in the rear of 33 Dunvegan caused the conductor to fail with live wires down. This required the breaker to be opened by SCADA to allow for isolation off the damaged primary which left 2 transformers, X24485 and X24482, off | O/H Conductor | O/H Conductor | 275 | 1 | 5 | East | UB04
127982 | 2013-11-10 | Tree Contacts | Broken Branch | Branch in the blue phase primary in the rear of 33 Dunvegan caused the conductor to fail with live wires down. This required the breaker to be opened by SCADA to allow for isolation off the damaged primary which left 2 transformers, X24485 and X24482, off | O/H Conductor | O/H Conductor | 275 | 34 | 156 | East | UB04
127982 | 2013-11-11 | Tree Contacts | Broken Branch | Branch in the blue phase primary in the rear of 33 Dunvegan caused the conductor to fail with live wires down. This required the breaker to be opened by SCADA to allow for isolation off the damaged primary which left 2 transformers, X24485 and X24482, off | O/H Conductor | O/H Conductor | 285 | 7 | 33 | East | UB04
127983 | 2013-11-11 | Defective Equipment | Mechanical Failure | Faulty cut out on overhead transformer X30271 | O/H Switchgear | Fused Cutout | 21 | 120 | 42 | Central | UC03
127984 | 2013-11-11 | Scheduled Outage | Construction | To allow contractor for connection to new O/H circuit. | None | None | 2 | 281 | 9 | East | LTM01
127985 | 2013-11-11 | Scheduled Outage | Construction | At 09:10, TE123 at 47 Chesterton was isolated for transformer & cable replacement. 10 customers affected for 345 minutes. Due to Live front transformers addition 65 customers were interupted in the process of isolation for 10 minutes. Parkwood Hills (190F | None | None | 10 | 335 | 56 | South | 190F3
127985 | 2013-11-11 | Scheduled Outage | Construction | At 09:10, TE123 at 47 Chesterton was isolated for transformer & cable replacement. 10 customers affected for 345 minutes. Due to Live front transformers addition 65 customers were interupted in the process of isolation for 10 minutes. Parkwood Hills (190F | None | None | 75 | 10 | 12 | South | 190F3
127987 | 2013-11-11 | Scheduled Outage | Maintenance | Vault V450 at 2380 Lancaster was isolated to allow crew to replace PCB transformer and contractor to perform customer vault maintenance | None | None | 1 | 222 | 4 | East | AL02
127988 | 2013-11-11 | Scheduled Outage | Construction | Replace leaking transformer | None | None | 9 | 85 | 13 | West | 624F1
127989 | 2013-11-11 | Scheduled Outage | Construction | At 10:10, PC10a #5976 was established by John Lepage at S1351 to allow crews to replace a defective pole. 1 customer affected for 106 minutes. Stafford (200F1) ID #127989 | None | None | 1 | 106 | 2 | South | 200F1
127991 | 2013-11-11 | Foreign Interference | Vehicle | 200F5 tripped due to O/H contact. S1097 isolated at line taps to make repairs. 1222 customers affected for 47 minutes, 8 customers affected for 196 minutes. | O/H Conductor | O/H Conductor | 8 | 149 | 20 | South | 200F5
127991 | 2013-11-11 | Foreign Interference | Vehicle | 200F5 tripped due to O/H contact. S1097 isolated at line taps to make repairs. 1222 customers affected for 47 minutes, 8 customers affected for 196 minutes. | O/H Conductor | O/H Conductor | 1222 | 47 | 957 | South | 200F5
127992 | 2013-11-11 | Scheduled Outage | Construction | To replace leaking transformer TP3619R at 234 Badgeley Ave. | None | None | 7 | 72 | 8 | West | 624F1
127995 | 2013-11-11 | Defective Equipment | Defective Equipment/ Material | ISOLATED TRANSFORMER 55C4B-0325 TO REPLACE BURNT SECONDARY SERVICE | Secondary \ Service | O/H Service | 16 | 45 | 12 | Central | TD01
127996 | 2013-11-11 | Tree Contacts | Broken Branch | SM16 and UC00 breakers tripped. UC00 wire down at Avondale and Tweedsmuir due to broken branch. | O/H Conductor | O/H Conductor | 497 | 61 | 505 | Central | SM16
127997 | 2013-11-11 | Scheduled Outage | Maintenance | Transformer #X30492 opened by crew to make repairs to the service at 79 Ross | None | None | 10 | 4 | 1 | Central | TH01
127999 | 2013-11-11 | Scheduled Outage | Construction | Defective transformers on three phase bank. | None | None | 9 | 440 | 66 | West | 28F3
128000 | 2013-11-12 | Scheduled Outage | Construction | ISOLATED 5 TRANSFORMERS X30602, X28262, X30604, X30617, AND X30605 | None | None | 39 | 260 | 169 | Central | SK13
128001 | 2013-11-12 | Defective Equipment | Mechanical Failure | REPLACED BROKEN SWITCH AND LIVE LINE CLAMP FEEDING TRANSFORMER X30118 | O/H Switchgear | Fused Cutout | 12 | 95 | 19 | Central | SB11
128003 | 2013-11-12 | Scheduled Outage | Construction | 4kV transformers X3399 and X33798 on Bloomsbury Rd. Were isolated to allow crews to transfer plant. | None | None | 49 | 90 | 74 | Central | UW13
128004 | 2013-11-12 | Foreign Interference | Crane | Crane contacted the overhead | None | None | 260 | 96 | 416 | Central | AB03
128005 | 2013-11-12 | Scheduled Outage | Construction | 4kV transformers X46734 and X46732 isolated to allow crews to transfer primary plant to new poles. | None | None | 49 | 60 | 49 | Central | UW13
128006 | 2013-11-12 | Scheduled Outage | Construction | 4kV transformers X46736, X46738, X46740 and X46742 on Westburry Rd. Isolated yo allow crews to transfrer primary plant to new poles. | None | None | 94 | 90 | 141 | Central | UW13
128007 | 2013-11-13 | Scheduled Outage | Vegetation Management | AD07 O/H line from pole 55D3C-0152 at Merivale and Kingston to EOL for tree removal by city of ottawa | None | None | 166 | 376 | 1040 | Central | AD07
128008 | 2013-11-13 | Scheduled Outage | Construction | TP9169W at 17 Carwood Cir isolated to allow crews to pull in new primary cable. | None | None | 19 | 95 | 30 | East | TO2UT
128011 | 2013-11-13 | Scheduled Outage | Construction | Replacing transformer and cables. | None | None | 14 | 371 | 87 | South | 190F6
128012 | 2013-11-13 | Scheduled Outage | Construction | replace a leaking transformer | None | None | 1 | 241 | 4 | West | MWDF3
128013 | 2013-11-13 | Scheduled Outage | Construction | Transformer X20845 at 2070 Kings Grove Cres. Isolated to transfer secondary to new pole. | None | None | 11 | 137 | 25 | East | BCHF3
128014 | 2013-11-13 | Scheduled Outage | Maintenance | Transformer X33635 at 604 Tweedsmuir Ave. isolated to repair conductor | O/H Conductor | O/H Conductor | 6 | 89 | 9 | Central | SM16
128015 | 2013-11-13 | Scheduled Outage | Construction | soil remediation | None | None | 11 | 410 | 75 | West | JKGF4
128016 | 2013-11-13 | Scheduled Outage | Construction | replacing transformer and cables. | None | None | 44 | 319 | 234 | South | 190F6
128017 | 2013-11-13 | Scheduled Outage | Construction | Transformer #X30906 opened up by crew due to an upgrade and pole change | None | None | 2 | 62 | 2 | Central | SK09
128018 | 2013-11-13 | Scheduled Outage | Construction | Transformer #X15316 opened by crew to transfer service to new Bell pole | None | None | 3 | 16 | 1 | East | LTM01
128019 | 2013-11-13 | Scheduled Outage | Construction | Transformer #X15316 opened by crew to transfer service to new Bell pole | None | None | 3 | 25 | 1 | East | LTM01
128020 | 2013-11-13 | Scheduled Outage | Construction | Transformer #X15316 opened by crew to transfer service to new Bell pole. | None | None | 3 | 25 | 1 | East | LTM01
128021 | 2013-11-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35226 opened up due to squirrel contact | None | None | 4 | 60 | 4 | West | ALEXF3
128022 | 2013-11-13 | Scheduled Outage | Maintenance | P416 opened up by crew to replace 3 hot line clamps | None | None | 1 | 45 | 1 | East | UQ03
128023 | 2013-11-14 | Foreign Interference | Wildlife (Bird/Animal) | Squirell caused transformer fuse to blow. | None | None | 9 | 123 | 18 | South | 47F3
128025 | 2013-11-14 | Scheduled Outage | Construction | Rearrranging primary cables on U/G transformer loop. | None | None | 71 | 276 | 327 | West | 624F1
128026 | 2013-11-14 | Defective Equipment | Defective Equipment/ Material | Transformer X25707 at 452 Preston St. isolated to allow crew to renew connections at 482 Preston St. | Secondary \ Service | O/H Service | 9 | 31 | 5 | Central | SB10
128027 | 2013-11-14 | Defective Equipment | Defective Equipment/ Material | Transformer TP3888 at 2392 Ogilvie Rd. isolated to allow crew to replace secondary conductor in the transformer | Secondary \ Service | U/G Service | 9 | 31 | 5 | East | BCHF5
128028 | 2013-11-14 | Scheduled Outage | Construction | To disconnect the UW13 section & connect to TW 17 to complete the 4KV to 13KV conversion of this section. | None | None | 130 | 205 | 444 | Central | UW13
128031 | 2013-11-15 | Defective Equipment | Defective Equipment/ Material | Transformer X39647 at 4075 Twin Elm Rd. isolated for pole change. | Pole | Pole | 1 | 119 | 2 | South | 145F3
128032 | 2013-11-15 | Scheduled Outage | Construction | Transformer x31581 at 1270 Highgate Rd. isolated to allow contractor to transfer load. | None | None | 10 | 40 | 7 | Central | UW13
128033 | 2013-11-15 | Scheduled Outage | Construction | Replace leaking transformer 652 | None | None | 2 | 210 | 7 | West | 624F2
128034 | 2013-11-15 | Scheduled Outage | Construction | Replacing leaking Transformer. | None | None | 4 | 173 | 12 | East | 6F10
128035 | 2013-11-16 | Scheduled Outage | Construction | To allow crew and contractor to remove cables from pole and energize new transformer.- | None | None | 4 | 325 | 22 | East | 6F1
128036 | 2013-11-16 | Scheduled Outage | Maintenance | Customer maintenace. | None | None | 1 | 63 | 1 | South | 180F3
128037 | 2013-11-16 | Scheduled Outage | Construction | TP7243 ISOLATED TO ALLOW CREW TO TRANSFER CABLE RISER TO NEW POLE AND UPGRADE TRANSFORMER. | None | None | 1 | 485 | 8 | West | BRDF2
128038 | 2013-11-16 | Scheduled Outage | Maintenance | Customer maintenace. | None | None | 1 | 230 | 4 | West | A9M4
128039 | 2013-11-16 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X9764 opened up due to animal contact | None | None | 2 | 136 | 5 | West | JKGF4
128040 | 2013-11-17 | Scheduled Outage | Maintenance | Vault Maintenance, clean and torque, service main breaker. | None | None | 1 | 271 | 5 | Central | TK4TS
128041 | 2013-11-17 | Scheduled Outage | Construction | Micro Fit | None | None | 1 | 187 | 3 | East | 77M6
128042 | 2013-11-18 | Defective Equipment | Mechanical Failure | G696B phase blew due to broken wire from insulator contacting the streetlight. | O/H Conductor | O/H Conductor | 51 | 158 | 134 | East | 4801F8
128043 | 2013-11-18 | Defective Equipment | Defective Equipment/ Material | Transformer #X33351 opened up due to defective fuse | O/H Switchgear | Fused Cutout | 5 | 162 | 14 | South | EPWF4
128044 | 2013-11-18 | Tree Contacts | Tree Growth/ Untrimmed Tree | Removed vine from Transformer X09910 and closed in transformer | None | None | 6 | 178 | 18 | South | 200F2
128045 | 2013-11-18 | Defective Equipment | Mechanical Failure | LEAD TO S17114 BURNT OFF AND WAS VERY CLOSE TO SECONDARY. TB14 BREAKER OPENED BY SYSTEM TO ALLOW CREW TO SAFELY CUT LEAD CLEAR. | O/H Conductor | Hot-Line Clamp | 24 | 43 | 17 | East | TB14
128045 | 2013-11-18 | Defective Equipment | Mechanical Failure | LEAD TO S17114 BURNT OFF AND WAS VERY CLOSE TO SECONDARY. TB14 BREAKER OPENED BY SYSTEM TO ALLOW CREW TO SAFELY CUT LEAD CLEAR. | O/H Conductor | Hot-Line Clamp | 1161 | 22 | 426 | East | TB14
128047 | 2013-11-18 | Scheduled Outage | Maintenance | Transformer X33372 at 97 Norice St. Isolated to make repairs to secondary buss. | None | None | 9 | 96 | 14 | South | EPWF3
128048 | 2013-11-19 | Scheduled Outage | Construction | At 9:32 am, transformer TP7228 at 7882 Decarie was isolated to allow crew to replace leaking transformer. 10 customers were interrupted for 163 minutes. Bilberry (77M6) ID# 128048. | None | None | 10 | 163 | 27 | East | 77M6
128049 | 2013-11-19 | Scheduled Outage | Maintenance | Customer Vault Maintenance | None | None | 1 | 430 | 7 | Central | TC2TL
128050 | 2013-11-19 | Scheduled Outage | Construction | Transformer X30849 at 415 Wilbrod St. isolated to allow for pole change. | None | None | 10 | 290 | 48 | Central | UN07
128051 | 2013-11-19 | Tree Contacts | Tree Growth/ Untrimmed Tree | 24/7 Crew refused transformer X27162 at 1812 Haig Dr. Cause of outage - tree branches grown up through open buss secondary. | None | None | 2 | 70 | 2 | East | TB15
128052 | 2013-11-19 | Defective Equipment | Defective Equipment/ Material | Replaced primary leed in transformer X27230 at 3338 Riverside Dr. | O/H Conductor | O/H Conductor | 4 | 90 | 6 | East | UZ12
128055 | 2013-11-20 | Scheduled Outage | Construction | At 9:32 am, transformer TP6378 at 1826 Maplegrove was isolated to allow crew to replace cable. 17 customers were interrupted for 125 minutes. Bridlewood (BRDF3) ID# 128055. | None | None | 17 | 125 | 35 | West | BRDF3
128056 | 2013-11-20 | Unknown/Other | Unknown | FAL01 circuit tripped due to unknown reason. Cause is under investigation. | Unknown \ Other | Unknown \ Other | 4794 | 15 | 1198 | South | FAL01
128057 | 2013-11-20 | Scheduled Outage | Construction | Transformer X31578 at 1252 Highgate Rd. isolated by contractor to install new pole. | None | None | 10 | 88 | 15 | Central | UW13
128058 | 2013-11-20 | Scheduled Outage | Construction | Transformer X30913 at 122 Daly Ave. isolated for pole replacement. | None | None | 10 | 245 | 41 | Central | SK10
128059 | 2013-11-20 | Scheduled Outage | Construction | Transformer X31581 at 1270 Highgate Rd. isolated for installation of new pole by contractor. | None | None | 10 | 150 | 25 | Central | UW13
128060 | 2013-11-20 | Scheduled Outage | Construction | TER266 @ 66 Chesterton isolated for transformer and cable replacement program. | None | None | 28 | 327 | 153 | South | 190F6
128061 | 2013-11-20 | Scheduled Outage | Construction | Transformer X25716 at 44 Ruskin St. isolated to allow crew to rearrange primary. | None | None | 10 | 215 | 36 | Central | SH04
128062 | 2013-11-21 | Scheduled Outage | Maintenance | 2 transformers (X33963 and X33971) opened up by crew to repair a wire | None | None | 38 | 13 | 8 | Central | UW13
128063 | 2013-11-21 | Scheduled Outage | Maintenance | Transformer #X33249 opened by crew to replace triplex | None | None | 12 | 55 | 11 | South | 190F5
128064 | 2013-11-21 | Scheduled Outage | Construction | 2 transformers (X33568 and X26238) opened by crew to re-arrange a service | None | None | 24 | 85 | 34 | Central | AK04
128065 | 2013-11-21 | Scheduled Outage | Construction | 2 transformers (X31575 and X35074) opened by crew to install new poles | None | None | 17 | 150 | 42 | Central | UW13
128066 | 2013-11-21 | Defective Equipment | Electrical Failure | cable fault between TP8650 and TP8649 caused SC4528-CB4 to open and auto reclose the RX2010. | U/G Cable | XLPE | 411 | 109 | 747 | West | ALEXF3
128067 | 2013-11-21 | Scheduled Outage | Construction | Transformer #X32838 opened by crew to re-arrange plant | None | None | 1 | 115 | 2 | West | 43F3
128068 | 2013-11-21 | Scheduled Outage | Maintenance | soil remediation | None | None | 7 | 636 | 74 | East | 6F10
128069 | 2013-11-18 | Scheduled Outage | Forced Switching | X24833 isolated to allow crews to replace transfromer due to defective secondary bushing and oil leak. SHANE: PLEASE CORRECT THE DATE OF THIS OUTAGE TO NOV 18TH, 2013. | None | O/H Transformer (1ph) | 10 | 348 | 58 | East | UQ05
128070 | 2013-11-21 | Scheduled Outage | Construction | 2 transformers (X35064 and X35059) opened by crew to install new poles | None | None | 16 | 255 | 68 | Central | UW13
128071 | 2013-11-21 | Scheduled Outage | Maintenance | planned work | None | None | 2 | 125 | 4 | South | 145F4
128073 | 2013-11-22 | Scheduled Outage | Construction | Prep work for upcoming 13kV conversion and to change the O/H switches feeding V752 | None | None | 1 | 123 | 2 | Central | UW13
128074 | 2013-11-22 | Scheduled Outage | Maintenance | Transformer #X27111 opened by crew to replace hot line clamp | None | None | 9 | 21 | 3 | East | TB14
128075 | 2013-11-22 | Defective Equipment | Electrical Failure | Cable fault between TP3613 and S26277 caused S26277 fuse to blow. | U/G Cable | XLPE | 10 | 253 | 42 | East | BCHF8
128076 | 2013-11-23 | Scheduled Outage | Construction | At 07:40 13KV vault VT261 at 234 Wellington was isolated to allow for construction clearance. 1 customer affected for 150 minutes. Lisgar (5208) ID #128076 | None | None | 1 | 150 | 2 | Central | 5208
128077 | 2013-11-23 | Scheduled Outage | Maintenance | At 08:53, 13KV vault VT96 at 171 Slater was isolated to allow contractor to perform vault maintenance. 1 customer affected for 317 minutes. Slater (602) ID #128077 | None | None | 1 | 317 | 5 | Central | 602
128078 | 2013-11-23 | Defective Equipment | Defective Equipment/ Material | at 12:00, 8 kv O/H transormer X4364 at 42 knowdale was isolated to allow crews to repair defective cutout. 8 customers affected for 50 minutes. Woodrofe DS (170F1) ID #128078 | O/H Switchgear | Fused Cutout | 8 | 50 | 7 | South | 170F1
128079 | 2013-11-23 | Scheduled Outage | Maintenance | Customer Vault Repairs | None | None | 1 | 299 | 5 | Central | 615
128080 | 2013-11-24 | Scheduled Outage | Maintenance | Vault Maintenance | None | None | 1 | 257 | 4 | Central | 303
128081 | 2013-11-24 | Scheduled Outage | Maintenance | At 5:31, 13KV vault VT123 at 60 Chapel was isolated to allow crews to peform vault maintenance. 1 customer affected for 389 minutes. King Edward (413) ID #128081 | None | None | 1 | 389 | 6 | Central | 413
128082 | 2013-11-24 | Scheduled Outage | Construction | 28kv transformer TP10126 at 525 March Rd was isolated to allow for oil remediation affecting 1 customer for xx minutes, Kanata 624F6 | None | None | 1 | 430 | 7 | West | 624F6
128083 | 2013-11-24 | Unknown/Other | Unknown | RX2039 tripped, blue phase flagged | Unknown \ Other | Unknown \ Other | 7 | 182 | 21 | West | ALEXF2
128083 | 2013-11-24 | Unknown/Other | Unknown | RX2039 tripped, blue phase flagged | Unknown \ Other | Unknown \ Other | 93 | 28 | 43 | West | ALEXF2
128083 | 2013-11-24 | Unknown/Other | Unknown | RX2039 tripped, blue phase flagged | Unknown \ Other | Unknown \ Other | 247 | 14 | 58 | West | ALEXF2
128083 | 2013-11-24 | Unknown/Other | Unknown | RX2039 tripped, blue phase flagged | Unknown \ Other | Unknown \ Other | 1196 | 63 | 1256 | West | ALEXF2
128084 | 2013-11-24 | Scheduled Outage | Maintenance | AT 09:13, 13KV vault VT892 at 60 Cambridge was isolated to allow contractor to perform vault maintenance. 1 customer affected for 367 minutes. Lisgar (5210) ID #128084 | None | None | 1 | 367 | 6 | Central | 5210
128085 | 2013-11-24 | Human Element | Incorrect Records/ labelling | TL22 breaker tripped during switching to restore VT892. Crews investigated & reported that SPARE-L @ SW184 is NIU with permanent grounds installed. Not captured on maps. Prior to retore crews inspected SPARE-L compartment and were not able to see the gr | U/G Switchgear | Unknown \ Other | 348 | 30 | 174 | Central | 5210
128086 | 2013-11-24 | Defective Equipment | Corrosion | Defective primary lead at S1627 feeding TE3290 | O/H Switchgear | Fused Cutout | 4 | 65 | 4 | South | 180F2
128087 | 2013-11-24 | Foreign Interference | Dig-In | transformers 5847, 6008 and 676 at 535 Legget were isolated to allow crew to repair cable damaged by dig in affecting 5 customers for 1022 minutes when 676 was restored left the remaining 3 customers off for an additional 113 minutes , Kanata, 624F2, ID # | U/G Cable | Unknown \ Other | 3 | 113 | 6 | West | 624F2
128087 | 2013-11-24 | Foreign Interference | Dig-In | transformers 5847, 6008 and 676 at 535 Legget were isolated to allow crew to repair cable damaged by dig in affecting 5 customers for 1022 minutes when 676 was restored left the remaining 3 customers off for an additional 113 minutes , Kanata, 624F2, ID # | U/G Cable | Unknown \ Other | 5 | 1022 | 85 | West | 624F2
128088 | 2013-11-25 | Unknown/Other | Unknown | UW14 tripped - cause not found tripped under hold ofr Brian Brooks(Black & Mac) & Tim Connel(K-line), crews cleared and breaker closed | Unknown \ Other | Unknown \ Other | 448 | 5 | 37 | Central | UW14
128089 | 2013-11-25 | Scheduled Outage | Maintenance | at 13:50, 4KV transformer P1666 at 1850 Baseline was isolated to allow crews to replace bayonette fuse. 1 customer affected for 46 minutes. Woodroffe DS (UW01) ID #128089 | None | None | 1 | 46 | 1 | Central | UW01
128090 | 2013-11-26 | Scheduled Outage | Construction | Switch replacement program. | None | None | 1 | 29 | 0 | East | 77M1
128091 | 2013-11-26 | Scheduled Outage | Construction | Switch replacement program | None | None | 1 | 40 | 1 | East | 77M6
128092 | 2013-11-26 | Scheduled Outage | Maintenance | Soil Remediation | None | None | 13 | 541 | 117 | West | BRDF4
128093 | 2013-11-26 | Scheduled Outage | Construction | Secondary service upgrade | None | None | 6 | 40 | 4 | South | 170F1
128095 | 2013-11-26 | Foreign Interference | Vehicle | Broken hydro pole in tree at 767 Rockcliffe Parkway caused by MVA. ( hit and run) | Pole | Pole | 7 | 16 | 2 | East | UG12
128097 | 2013-11-27 | Defective Equipment | Electrical Failure | white phase lead burnt off switch G901W. | O/H Switchgear | Inline Switch | 89 | 188 | 279 | East | 249F2
128098 | 2013-11-27 | Tree Contacts | Broken Branch | tree on overhead | None | None | 651 | 177 | 1920 | Central | TR3UY
128099 | 2013-11-27 | Defective Equipment | Defective Equipment/ Material | S994R phase opened due to cable fault between TE1101 and TE753. While restoring the load on the S994 (200F6) the 47F6 CB tripped when normal open point S94R phase was closed. | U/G Cable | XLPE | 43 | 13 | 9 | South | 200F6
128099 | 2013-11-27 | Defective Equipment | Defective Equipment/ Material | S994R phase opened due to cable fault between TE1101 and TE753. While restoring the load on the S994 (200F6) the 47F6 CB tripped when normal open point S94R phase was closed. | U/G Cable | XLPE | 50 | 34 | 28 | South | 200F6
128099 | 2013-11-27 | Defective Equipment | Defective Equipment/ Material | S994R phase opened due to cable fault between TE1101 and TE753. While restoring the load on the S994 (200F6) the 47F6 CB tripped when normal open point S94R phase was closed. | U/G Cable | XLPE | 59 | 12 | 12 | South | 200F6
128099 | 2013-11-27 | Defective Equipment | Defective Equipment/ Material | S994R phase opened due to cable fault between TE1101 and TE753. While restoring the load on the S994 (200F6) the 47F6 CB tripped when normal open point S94R phase was closed. | U/G Cable | XLPE | 68 | 26 | 29 | South | 200F6
128099 | 2013-11-27 | Defective Equipment | Defective Equipment/ Material | S994R phase opened due to cable fault between TE1101 and TE753. While restoring the load on the S994 (200F6) the 47F6 CB tripped when normal open point S94R phase was closed. | U/G Cable | XLPE | 78 | 252 | 328 | South | 200F6
128099 | 2013-11-27 | Defective Equipment | Defective Equipment/ Material | S994R phase opened due to cable fault between TE1101 and TE753. While restoring the load on the S994 (200F6) the 47F6 CB tripped when normal open point S94R phase was closed. | U/G Cable | XLPE | 759 | 18 | 228 | South | 47F6
128100 | 2013-11-27 | Tree Contacts | Broken Branch | AK07 circuit was opened due to tree on fire across 2 phases at the request of crew. | None | None | 423 | 30 | 212 | Central | AK07
128101 | 2013-11-27 | Tree Contacts | Tree Growth/ Untrimmed Tree | AB00 and AB04 circuits isolated to allow tree trimmers to clear tree out of the overhead circuits. Doug McKay reports trees has been removed from O/H circuits . All power restored to normal. | None | None | 113 | 106 | 200 | Central | AB04
128102 | 2013-11-27 | Scheduled Outage | Vegetation Management | tree removal | None | None | 46 | 158 | 121 | East | 8F1
128103 | 2013-11-28 | Defective Equipment | Mechanical Failure | sparking hot line clamp had to be changed | O/H Conductor | Hot-Line Clamp | 7 | 10 | 1 | South | EPWF1
128105 | 2013-11-28 | Scheduled Outage | Maintenance | To transfer transformer TP9229 from White phase to Blue phase | None | None | 16 | 34 | 9 | South | 190F6
128107 | 2013-11-28 | Scheduled Outage | Construction | Re-arrange plant for service upgrade | None | None | 2 | 60 | 2 | West | 28F2
128109 | 2013-11-28 | Scheduled Outage | Maintenance | Transformer TE131 @ 32 Bowhill was isolated to allow the crew to transfer the transformer from W phase to R phase | None | None | 11 | 361 | 66 | South | 130F4
128110 | 2013-11-28 | Scheduled Outage | Construction | Defective transformer X37105 | None | None | 9 | 180 | 27 | South | EPWF1
128112 | 2013-11-29 | Defective Equipment | Defective Equipment/ Material | Switch to V856 defective connections. | O/H Conductor | Hot-Line Clamp | 1 | 54 | 1 | East | UT03
128113 | 2013-11-29 | Scheduled Outage | Construction | Transformer TP6876 at 3777 Stranherd was isolated to allow crew to upgrade transformer and to allow crew to connect new service. | None | None | 3 | 238 | 12 | South | FAL01
128114 | 2013-11-29 | Scheduled Outage | Maintenance | Vault maintenance on customer owned 13KV vault. | None | None | 1 | 269 | 4 | East | 5304
128115 | 2013-11-29 | Scheduled Outage | Maintenance | 13KV vault VT257 @ 1335 Carling Ave to be isolated for vault maintenance. | None | None | 1 | 46 | 1 | Central | 301
128117 | 2013-11-30 | Scheduled Outage | Maintenance | Secondary work by Contractor | None | None | 1 | 217 | 4 | West | BRDF3
128118 | 2013-12-02 | Unknown/Other | Unknown | 200F2 breaker opened on inst. Overcurrent W phase. Closed back in by system, cause unknown. Circuit to be patrolled. | Unknown \ Other | Unknown \ Other | 200 | 11 | 37 | South | 200F2
128119 | 2013-12-02 | Human Element | Switching Error | Apprentice accidentally opened the 44F1 RWB reclosers, instead of placing them in hold off | None | None | 489 | 2 | 16 | West | 44F1
128121 | 2013-12-02 | Scheduled Outage | Construction | Transformer X33972 & K1013 at 2 Barbara Ann Pvt. Isolated by H/O crew to install new pole | None | None | 31 | 148 | 76 | Central | UW13
128122 | 2013-12-02 | Tree Contacts | Broken Branch | Transformer X39147 at 182 Kamloops Ave. isolated by crew to allow Forestry contractor to remove tree. | None | None | 6 | 15 | 2 | East | UZ12
128123 | 2013-12-02 | Tree Contacts | Falling Tree | Transformer X30535 at 261 Laurier Ave. isolated by 24/7 crew to allow removal of tree by City. | None | None | 19 | 22 | 7 | Central | UN07
128124 | 2013-12-02 | Scheduled Outage | Construction | Transformer #X39186 opened by crew to put up a new service | None | None | 1 | 55 | 1 | Central | SM12
128127 | 2013-12-04 | Scheduled Outage | Maintenance | VE18N was isolated by HOL crew to repair metering unit. | Unknown \ Other | Unknown \ Other | 1 | 45 | 1 | South | 190F5
128128 | 2013-12-04 | Scheduled Outage | Construction | Reconfiguration of overhead lines. | None | None | 113 | 164 | 309 | Central | UW14
128129 | 2013-12-04 | Scheduled Outage | Construction | Remove concrete collars | None | None | 9 | 228 | 34 | West | BRDF5
128130 | 2013-12-04 | Scheduled Outage | Construction | Transformer replacement and soil remediation. | None | None | 7 | 429 | 50 | East | V11F1
128131 | 2013-12-04 | Scheduled Outage | Construction | Transformer #X26055 opened by crew to replace service | None | None | 1 | 60 | 1 | East | UT07
128132 | 2013-12-04 | Scheduled Outage | Maintenance | To allow forestry crew to trim trees near primary | None | None | 1 | 239 | 4 | East | 7F4
128134 | 2013-12-04 | Scheduled Outage | Maintenance | Transformer #264 opened by crew to change triplex and transformer lugs | None | None | 17 | 148 | 42 | South | 47F3
128135 | 2013-12-04 | Defective Equipment | Defective Equipment/ Material | Transformer #X29709 opened up due to broken switch | O/H Switchgear | Fused Cutout | 13 | 186 | 40 | East | AE07
128136 | 2013-12-04 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30847 TO REPLACE POLE | None | None | 1 | 295 | 5 | Central | UN07
128137 | 2013-12-04 | Foreign Interference | Vehicle | Primary fault at Carleton University caused TR2UY circuit to trip. | None | None | 1 | 26 | 0 | Central | TR2UY
128138 | 2013-12-05 | Foreign Interference | Foreign Objects | Sign blow off building and was wrapped in the overhead circuit TH06 circuit. | None | None | 738 | 196 | 2411 | Central | TH06
128139 | 2013-12-05 | Scheduled Outage | Construction | Transformer #X35112 isolated by crew to replace the service and connections | None | None | 6 | 45 | 4 | Central | UV03
128140 | 2013-12-05 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33967 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 5 | 230 | 19 | Central | UW13
128142 | 2013-12-05 | Defective Equipment | Electrical Failure | defective transformer K35 | U/G Transformer | Kiosk (1ph) | 10 | 515 | 86 | East | AQ09
128143 | 2013-12-06 | Scheduled Outage | Construction | Pullin gnew XLPE cable into spare ductgoing to V780 @ 474 Wilbrod. | None | None | 1 | 364 | 6 | Central | UN07
128144 | 2013-12-06 | Scheduled Outage | Construction | Transformer #X31773 isolated by crew to install new service | None | None | 9 | 60 | 9 | Central | TW22
128146 | 2013-12-06 | Scheduled Outage | Construction | To replace defective transformer | None | None | 1 | 170 | 3 | Central | 36F1
128147 | 2013-12-07 | Scheduled Outage | Construction | Chris Hallam of Eco-Energy Res had transformer TP7161 isolated for retro fit | None | None | 1 | 105 | 2 | West | JKGF4
128148 | 2013-12-07 | Scheduled Outage | Maintenance | Vault isolation for contractor | None | None | 1 | 234 | 4 | Central | UW13
128149 | 2013-12-07 | Unknown/Other | Unknown | Not yet known. | None | None | 2110 | 21 | 738 | East | TA1UZ
128150 | 2013-12-08 | Scheduled Outage | Maintenance | VE74G (Airport Data Center) was isolated for customer owned mtce. | None | None | 1 | 128 | 2 | East | 7F2
128151 | 2013-12-08 | Scheduled Outage | Construction | overhead transformer change | None | None | 15 | 430 | 108 | Central | UN07
128153 | 2013-12-09 | Scheduled Outage | Maintenance | Contractor taking oil samples from transformers | None | None | 1 | 97 | 2 | West | 624F6
128154 | 2013-12-09 | Scheduled Outage | Construction | At 10:12 am, transformer TP9148 at 1491 Stittsville main was isolated to allow crew to pull in new secondary service. 26 customer were interrupted for 271 minutes. Janet King (44F1) ID# 128154. | None | None | 26 | 271 | 117 | West | 44F1
128155 | 2013-12-09 | Scheduled Outage | Construction | ISOLATED TRANSFORMER `X37158 TO REPLACE SECONDARY CONNECTIONS | None | None | 4 | 25 | 2 | Central | UV03
128156 | 2013-12-09 | Tree Contacts | Broken Branch | 84F3 CB A/RA due to branch on the O/H primary at rear of 17 Woodfern | None | None | 565 | 57 | 537 | South | 84F3
128157 | 2013-12-10 | Scheduled Outage | Construction | at 09:00, 27KV red phase transformer loop on Birchbank, Stone weadow & Salt Spring was interupted due to out of phase condition while transfering load to BRDF2. 103 customers affected for 20 minutes. ID #128157 | None | None | 103 | 20 | 34 | West | BRDF1
128158 | 2013-12-10 | Scheduled Outage | Maintenance | At 09:53, 27KV transformer TP3754 at 38 Huntsman was isolated to allow crews to repair defective insert. 6 customers affected for 91 minutes. Bridlewood (BRDF2) ID #128158 | None | None | 6 | 91 | 9 | West | BRDF2
128159 | 2013-12-10 | Scheduled Outage | Maintenance | At 09:15, 27KV transformer TP3550 at 105 Streamside was isolated to allow contractor to perform soil remediation. 8 customers affected for 540 minutes. Kanata (624F6) ID #128159 | None | None | 8 | 540 | 72 | West | 624F6
128160 | 2013-12-10 | Scheduled Outage | Maintenance | Not yet known.13kv vault VT241 at 31 McEwen isolated to allow the metering dept. To make repairs affecting 1 customer for 70 minutes, Lincoln, 5401, ID # 128160 | None | None | 1 | 70 | 1 | Central | 5401
128161 | 2013-12-10 | Scheduled Outage | Maintenance | 13kv vault VT241 at 31 McEwen isolated to allow the metering dept. To make repairs affecting 1 customer for 34 minutes, Lincoln, 5401, ID # 128161 | None | None | 1 | 34 | 1 | Central | 5401
128162 | 2013-12-10 | Scheduled Outage | Construction | 4kv transformers X33603, X37924 and K1085 isoated from overhead to allow transfer of these transformers from UL03 to UL05 affecting 21 customers for 96 minutes, Clifton, UL03, ID # 128162 | None | None | 21 | 96 | 34 | Central | UL03
128164 | 2013-12-10 | Scheduled Outage | Construction | Transformer X30991 at 238 Daly Ave. isolated by crew for pole replacement. | None | None | 4 | 45 | 3 | Central | SK10
128165 | 2013-12-10 | Scheduled Outage | Construction | Transformer X26016 at 371 Berkley Ave. isolated by crew for transformer upgrade. | None | None | 9 | 90 | 14 | Central | AH02
128166 | 2013-12-10 | Scheduled Outage | Forced Switching | TP10024-H1A opened to allow crews to open nonvented elbow at 1046R-1. 24 customers affected for 2 minutes. Bridlewood (BRDF1) ID #128166 | None | None | 24 | 2 | 1 | West | BRDF1
128167 | 2013-12-10 | Scheduled Outage | Forced Switching | TX 2508B-1 opened to allow crews to open nonvented elbow at 2004B-1. 65 customers affected for 2 minutes. Bridlewood (BRDF1) ID #128167 | None | None | 65 | 3 | 3 | West | BRDF1
128168 | 2013-12-10 | Scheduled Outage | Construction | Planned shut down to allow custumer to have a microfit installed. | None | None | 1 | 171 | 3 | East | 5309
128169 | 2013-12-11 | Defective Equipment | Defective Equipment/ Material | The TO3UT circuit caryying part of the TO2UT circuit tripped due to down TO3UT and TO2UT conductor at 251 Donald and blow pot heads at VT227 and VT207. | U/G Cable Attachement | Pothead | 1 | 16 | 0 | East | 1804
128169 | 2013-12-11 | Defective Equipment | Defective Equipment/ Material | The TO3UT circuit caryying part of the TO2UT circuit tripped due to down TO3UT and TO2UT conductor at 251 Donald and blow pot heads at VT227 and VT207. | U/G Cable Attachement | Pothead | 62 | 174 | 180 | East | 1804
128169 | 2013-12-11 | Defective Equipment | Defective Equipment/ Material | The TO3UT circuit caryying part of the TO2UT circuit tripped due to down TO3UT and TO2UT conductor at 251 Donald and blow pot heads at VT227 and VT207. | U/G Cable Attachement | Pothead | 416 | 19 | 132 | East | TO3UT
128169 | 2013-12-11 | Defective Equipment | Defective Equipment/ Material | The TO3UT circuit caryying part of the TO2UT circuit tripped due to down TO3UT and TO2UT conductor at 251 Donald and blow pot heads at VT227 and VT207. | U/G Cable Attachement | Pothead | 416 | 294 | 2038 | East | 1804
128169 | 2013-12-11 | Defective Equipment | Defective Equipment/ Material | The TO3UT circuit caryying part of the TO2UT circuit tripped due to down TO3UT and TO2UT conductor at 251 Donald and blow pot heads at VT227 and VT207. | U/G Cable Attachement | Pothead | 460 | 30 | 230 | East | TO3UT
128169 | 2013-12-11 | Defective Equipment | Defective Equipment/ Material | The TO3UT circuit caryying part of the TO2UT circuit tripped due to down TO3UT and TO2UT conductor at 251 Donald and blow pot heads at VT227 and VT207. | U/G Cable Attachement | Pothead | 609 | 15 | 152 | East | 1804
128169 | 2013-12-11 | Defective Equipment | Defective Equipment/ Material | The TO3UT circuit caryying part of the TO2UT circuit tripped due to down TO3UT and TO2UT conductor at 251 Donald and blow pot heads at VT227 and VT207. | U/G Cable Attachement | Pothead | 2060 | 56 | 1923 | East | TO3UT
128170 | 2013-12-11 | Defective Equipment | Defective Equipment/ Material | At 09:58, 47F6 tripped on Instantanous & timed. Stations crew working in cell removing fuse block on secondary side of 47B2PT. | Station Equipment | Primary Switchgear | 759 | 19 | 240 | South | 47F6
128170 | 2013-12-11 | Defective Equipment | Defective Equipment/ Material | At 09:58, 47F6 tripped on Instantanous & timed. Stations crew working in cell removing fuse block on secondary side of 47B2PT. | Station Equipment | Primary Switchgear | 759 | 26 | 329 | South | 47F6
128171 | 2013-12-11 | Scheduled Outage | Construction | Isolated transformer X31350 to replace pole | None | None | 5 | 145 | 12 | Central | AK12
128172 | 2013-12-11 | Scheduled Outage | Construction | Transformers X35059 at 1341 Bloomsbury and X35071 at 1357 Bloomsbury Cres. Isolated to allow contractor to transfer plant to new poles. | None | None | 10 | 270 | 45 | Central | UW13
128174 | 2013-12-12 | Scheduled Outage | Construction | Cable replacement and vault maintenance. | None | None | 55 | 260 | 238 | Central | UN03
128175 | 2013-12-12 | Scheduled Outage | Construction | isolate transformer x30994, to install new pole | None | None | 14 | 240 | 56 | Central | SK10
128176 | 2013-12-12 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMERS X33970, X33966, X33964 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 23 | 285 | 109 | Central | UW13
128177 | 2013-12-12 | Defective Equipment | Defective Equipment/ Material | 24/7 crew found broken fuse at S24737B. Fuse replaced and switch closed. | Unknown \ Other | Unknown \ Other | 33 | 84 | 46 | West | RHNF3
128178 | 2013-12-12 | Defective Equipment | Defective Equipment/ Material | While isolating transformer 1147 at 55 McCurdy for Fit installation, S51-2 RB phase fuses blew when crew opened white phase elbow to isolate the transformer. Crew re-fused S51-2 and closed and the fuses held. See outage ID 128179 and ID 128180 | U/G Transformer | Padmount (3ph) | 254 | 44 | 186 | West | BRDF4
128179 | 2013-12-13 | Defective Equipment | Defective Equipment/ Material | S51-2 RWB phases blew while restoring transformer 1147 which was isolated for Fit install. See Outage ID 128178, 128180 | U/G Transformer | Padmount (3ph) | 447 | 107 | 797 | West | BRDF4
128181 | 2013-12-13 | Defective Equipment | Defective Equipment/ Material | During switching 24/7 crew closed 1147-1 on 17-9401 and caused S51-2 blue phase to blow. Crew later advised defective transformer and it needs to be changed. | U/G Transformer | Padmount (3ph) | 198 | 7 | 23 | West | BRDF4
128182 | 2013-12-13 | Defective Equipment | Defective Equipment/ Material | During restoration from planned outage the transformer 1147 was not restored until replacement at 11:49 | U/G Transformer | Padmount (3ph) | 1 | 569 | 9 | West | BRDF4
128183 | 2013-12-13 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 1497 | 3 | 75 | Central | TR09
128184 | 2013-12-13 | Scheduled Outage | Construction | Install cables in spare duct. | None | None | 13 | 32 | 7 | Central | UN07
128185 | 2013-12-13 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 109 | 283 | 514 | East | UB07
128186 | 2013-12-14 | Scheduled Outage | Construction | Transformer #X30993 and X30994 isolated by crew to re-arrange plant | None | None | 35 | 300 | 175 | Central | SK10
128187 | 2013-12-14 | Adverse Environment | Fire | Transfomer X29550 was opened by crew at the request of the fire department to allow fire fighter to exinguish house fire at 78 Union St | None | None | 14 | 195 | 46 | East | UG02
128188 | 2013-12-14 | Scheduled Outage | Construction | 4Kv vault was isolated to be decommissioned. A new TP9984 was cut in to energize building. | None | None | 1 | 537 | 9 | Central | UW13
128189 | 2013-12-14 | Adverse Environment | Fire | 4kv transformer X29566 at 82 Union was opened for clearance for the Fire Department at 78 Union, affecting 3 customers for 283 minutes, Vaughan, UG02, ID # 128189 | None | None | 3 | 283 | 14 | East | UG02
128190 | 2013-12-15 | Scheduled Outage | Construction | SK09 O/H section on St Patrick St was isolated to allow crew to re string O/H conductor on St Patrick and Parent. 147 customers were affected for . King Edward (SK09). ID#128190 | None | None | 2 | 92 | 3 | Central | SK09
128190 | 2013-12-15 | Scheduled Outage | Construction | SK09 O/H section on St Patrick St was isolated to allow crew to re string O/H conductor on St Patrick and Parent. 147 customers were affected for . King Edward (SK09). ID#128190 | None | None | 147 | 209 | 512 | Central | SK09
128192 | 2013-12-15 | Defective Equipment | Defective Equipment/ Material | Transformer #X27449 at 1239 Foxbar was isolated by crew due to neutral down. Albion (UA07). ID# 128192 | O/H Conductor | O/H Conductor | 8 | 31 | 4 | East | UA07
128193 | 2013-12-15 | Defective Equipment | Defective Equipment/ Material | Transformer #X27448 at 1233 Foxbar was isolated by crew due to neutral down. Albion (UA07). | O/H Conductor | O/H Conductor | 8 | 295 | 39 | East | UA07
128194 | 2013-12-16 | Scheduled Outage | Construction | S12393 to EOL at 3330 Cedarview was isolated to allow crew to replace O/H switch | None | None | 1 | 211 | 4 | South | FAL01
128195 | 2013-12-16 | Scheduled Outage | Construction | S28310 to Eol at 3270 Cedarview was isolated to allow crew to replace SMD switches. 1 customer was affected for 32 minutes. Fallowfield (FAL01). ID# 128195 | None | None | 1 | 32 | 1 | South | FAL01
128196 | 2013-12-16 | Defective Equipment | Defective Equipment/ Material | S102 at Riviere / Principale (Casselman) opened due to defective fuse cut-out. 7 customers were affected for 55 minutes. Casselman (V11F2). ID# 128196 | O/H Switchgear | Fused Cutout | 7 | 55 | 6 | East | V11F2
128197 | 2013-12-16 | Scheduled Outage | Construction | Transformer #X33889 isolated by crew to hook up a new service | None | None | 7 | 50 | 6 | Central | UL14
128198 | 2013-12-16 | Defective Equipment | Defective Equipment/ Material | Transformer #X39710 isolated by crew to replace connections and triplex | O/H Conductor | Ampact | 1 | 50 | 1 | South | 84F2
128199 | 2013-12-16 | Scheduled Outage | Construction | Transformer #X31212 isolated by crew to transfer to new pole. | None | None | 10 | 180 | 30 | Central | SK09
128201 | 2013-12-16 | Defective Equipment | Mechanical Failure | Cable fault between TP3613 and S26277 | U/G Cable | XLPE | 10 | 270 | 45 | East | BCHF8
128202 | 2013-12-17 | Foreign Interference | Vehicle | Refused transformer X37061 at 27 Caesar Ave. - caused possibly by bump of pole by snow removal equipment. | None | None | 14 | 100 | 23 | South | 72F4
128203 | 2013-12-17 | Scheduled Outage | Construction | Transfer plant to new pole | None | None | 1 | 135 | 2 | Central | SK09
128203 | 2013-12-17 | Scheduled Outage | Construction | Transfer plant to new pole | None | None | 2 | 10 | 0 | Central | SK09
128204 | 2013-12-17 | Scheduled Outage | Construction | transfer vault supply to new conductor. | None | None | 1 | 116 | 2 | Central | SK13
128205 | 2013-12-17 | Scheduled Outage | Construction | Transformer x31213 at 227 St. Patrick and x31214 at 101 Parent Ave. Isolated by contractor for transfer of plant. | None | None | 70 | 218 | 254 | Central | SK09
128206 | 2013-12-17 | Scheduled Outage | Construction | To convert 4kV overhead to 13kV supply out of Woodroffe Terminal and Sub. | None | None | 183 | 190 | 580 | Central | UW13
128207 | 2013-12-18 | Scheduled Outage | Maintenance | Customer Insulator Change on Private Line | Secondary \ Service | Unknown \ Other | 1 | 304 | 5 | South | 145F4
128209 | 2013-12-18 | Scheduled Outage | Construction | Trans X30987 was isolated in order to transfer plant to new pole | None | None | 2 | 90 | 3 | Central | SK10
128210 | 2013-12-18 | Scheduled Outage | Maintenance | transformer and riser switch change | None | None | 1 | 236 | 4 | Central | AD02
128211 | 2013-12-18 | Scheduled Outage | Maintenance | To repair broken insert on transformer elbow | U/G Cable Attachement | Elbow \ Insert | 10 | 64 | 11 | West | BRDF2
128213 | 2013-12-18 | Scheduled Outage | Construction | Voltage conversion | None | None | 383 | 137 | 875 | Central | UW13
128214 | 2013-12-18 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30608 TO TRANSFER HYDRO PLANTE | None | None | 1 | 60 | 1 | Central | SK13
128216 | 2013-12-18 | Scheduled Outage | Construction | ISOLATED TRANSFORMERS X26243 AND X30618 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 23 | 225 | 86 | Central | SK13
128217 | 2013-12-18 | Scheduled Outage | Construction | Isolated to allow contractor to install a Microfit. | None | None | 1 | 918 | 15 | East | 1806
128220 | 2013-12-19 | Defective Equipment | Electrical Failure | Not yet known. | Unknown \ Other | Unknown \ Other | 2369 | 2 | 79 | West | BRDF1
128220 | 2013-12-19 | Defective Equipment | Electrical Failure | Not yet known. | Unknown \ Other | Unknown \ Other | 2415 | 47 | 1892 | West | BRDF1
128220 | 2013-12-19 | Defective Equipment | Electrical Failure | Not yet known. | Unknown \ Other | Unknown \ Other | 2743 | 40 | 1829 | West | BRDF3
128220 | 2013-12-19 | Defective Equipment | Electrical Failure | Not yet known. | Unknown \ Other | Unknown \ Other | 3774 | 5 | 314 | West | JKGF5
128220 | 2013-12-19 | Defective Equipment | Electrical Failure | Not yet known. | Unknown \ Other | Unknown \ Other | 3833 | 102 | 6516 | West | BRDF1
128220 | 2013-12-19 | Defective Equipment | Electrical Failure | Not yet known. | Unknown \ Other | Unknown \ Other | 5760 | 19 | 1824 | West | BRDF2
128221 | 2013-12-19 | Scheduled Outage | Maintenance | At 09:05, 27KV transformer at 412 Brunskill was isolated to allow crews to perform oil remediation, 9 customers affected for 467 minutes. Kanata (624F1) ID #128221. | None | None | 9 | 467 | 70 | West | 624F1
128222 | 2013-12-19 | Scheduled Outage | Construction | TP7508 at 58 Sweetman was isolated to allow crew to install new secondary affecting 16 customers for 139 minutes, Alexander, ALEX F3, ID # 128222 | None | None | 16 | 139 | 37 | West | ALEXF3
128226 | 2013-12-21 | Scheduled Outage | Maintenance | perform repairs to swich and clamp. | Unknown \ Other | Unknown \ Other | 13 | 23 | 5 | East | UB06
128227 | 2013-12-22 | Scheduled Outage | Maintenance | asbestos removal, PCB transformer change. | None | None | 1 | 299 | 5 | Central | TK4TS
128229 | 2013-12-22 | Scheduled Outage | Forced Switching | Emergency switching to allow crew to reposition a broken crossarm. | None | Crossarm | 0 | 40 | 0 | West | A9M3
128229 | 2013-12-22 | Scheduled Outage | Forced Switching | Emergency switching to allow crew to reposition a broken crossarm. | None | Crossarm | 736 | 24 | 294 | West | A9M3
128229 | 2013-12-22 | Scheduled Outage | Forced Switching | Emergency switching to allow crew to reposition a broken crossarm. | None | Crossarm | 6019 | 7 | 702 | West | A9M3
128230 | 2013-12-23 | Adverse Environment | Fire | House fire at 150 Third Avenue | None | None | 7 | 142 | 17 | Central | SB03
128230 | 2013-12-23 | Adverse Environment | Fire | House fire at 150 Third Avenue | None | None | 540 | 11 | 99 | Central | SB03
128233 | 2013-12-24 | Scheduled Outage | Construction | Transformer #X25377 isolated by crew for transformer replacement | O/H Transformer | O/H Transformer (3ph) | 1 | 75 | 1 | East | V11F3
128235 | 2013-12-27 | Scheduled Outage | Maintenance | Transformer #K360 isolated by crew to replace fuse in transformer | None | None | 12 | 10 | 2 | East | AL10
128237 | 2013-12-30 | Foreign Interference | Vehicle | Snow removal equipment knocked pedastals P2 and P3 fed from K250 | U/G Transformer | Kiosk (1ph) | 7 | 71 | 8 | East | UA04
128237 | 2013-12-30 | Foreign Interference | Vehicle | Snow removal equipment knocked pedastals P2 and P3 fed from K250 | U/G Transformer | Kiosk (1ph) | 21 | 15 | 5 | East | UA04
128237 | 2013-12-30 | Foreign Interference | Vehicle | Snow removal equipment knocked pedastals P2 and P3 fed from K250 | U/G Transformer | Kiosk (1ph) | 21 | 197 | 69 | East | UA04
128241 | 2014-01-02 | Foreign Interference | Vehicle | TE2833 at 261 Centrepointe was isolated to allow crew to replace transformer due to it being hit by snow plow. | None | None | 14 | 347 | 81 | South | 87F1
128244 | 2014-01-03 | Defective Equipment | Electrical Failure | Transformer fuse at TE820 opened again, transformer was found to be defective. | U/G Transformer | Padmount (1ph) | 8 | 275 | 37 | East | LTM01
128245 | 2014-01-04 | Scheduled Outage | Forced Switching | 8kV overhead transformer X09120 at 6531 Franktown Rd. Opened by crews to due high secondary voltages. Transformer replaced by on-call crew. | None | O/H Transformer (1ph) | 2 | 222 | 7 | West | 28F1
128246 | 2014-01-05 | Defective Equipment | Defective Equipment/ Material | At transformer 5687R at 195 castlefrank the barrier board fell into the insulator causing the SC4708-4R fuse to open. | U/G Transformer | Padmount (1ph) | 16 | 52 | 14 | West | BRDF6
128246 | 2014-01-05 | Defective Equipment | Defective Equipment/ Material | At transformer 5687R at 195 castlefrank the barrier board fell into the insulator causing the SC4708-4R fuse to open. | U/G Transformer | Padmount (1ph) | 16 | 227 | 61 | West | BRDF6
128246 | 2014-01-05 | Defective Equipment | Defective Equipment/ Material | At transformer 5687R at 195 castlefrank the barrier board fell into the insulator causing the SC4708-4R fuse to open. | U/G Transformer | Padmount (1ph) | 30 | 2 | 1 | West | BRDF6
128246 | 2014-01-05 | Defective Equipment | Defective Equipment/ Material | At transformer 5687R at 195 castlefrank the barrier board fell into the insulator causing the SC4708-4R fuse to open. | U/G Transformer | Padmount (1ph) | 52 | 105 | 91 | West | BRDF6
128247 | 2014-01-05 | Defective Equipment | Defective Equipment/ Material | Broken Lead. | O/H Conductor | Pigtail | 13 | 68 | 15 | East | TB06
128249 | 2014-01-06 | Defective Equipment | Defective Equipment/ Material | Defective quad plex. | Secondary \ Service | O/H Service | 7 | 43 | 5 | Central | UF08
128250 | 2014-01-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | fuse at transfromer 409 at 5497 West River open due to tree contact. | O/H Transformer | O/H Transformer (1ph) | 8 | 103 | 14 | East | 7F4
128251 | 2014-01-06 | Defective Equipment | Electrical Failure | Blown lightning arrestor at Fernbank and Blacks Side Rd. | Pole Attachement | Arrester | 74 | 158 | 195 | West | ALEXF3
128252 | 2014-01-08 | Scheduled Outage | Maintenance | To re-connect a 600V cable | None | None | 1 | 37 | 1 | Central | TC2TL
128253 | 2014-01-08 | Scheduled Outage | Maintenance | pole equipment maintenance | None | None | 1 | 248 | 4 | East | 7F2
128254 | 2014-01-08 | Defective Equipment | Mechanical Failure | DEFECTIVE SWITCH S24291 BLUE PHASE WAS REPLACED. | O/H Switchgear | Fused Cutout | 38 | 121 | 77 | Central | TD01
128256 | 2014-01-08 | Defective Equipment | Defective Equipment/ Material | At 21:20, crews reported O/H TX X34051 openned up when investigating flicker lights. ONCALL crews replaced TX. 10 customers affected for 370 minutes. Hinchey (TH01) ID #128256 | O/H Transformer | O/H Transformer (1ph) | 10 | 370 | 62 | Central | TH01
128257 | 2014-01-09 | Scheduled Outage | Construction | To install a new service.. | None | Padmount (1ph) | 8 | 164 | 22 | South | FAL03
128258 | 2014-01-09 | Scheduled Outage | Forced Switching | Defective transformer TP6880 isolated for replacement. Momentary outage to TP6879 due to mapping issues. | None | Padmount (3ph) | 2 | 270 | 9 | South | FAL01
128258 | 2014-01-09 | Scheduled Outage | Forced Switching | Defective transformer TP6880 isolated for replacement. Momentary outage to TP6879 due to mapping issues. | None | Padmount (3ph) | 6 | 1 | 0 | South | FAL01
128259 | 2014-01-09 | Defective Equipment | Defective Equipment/ Material | Barrier board fell into primary. | O/H Switchgear | Fused Cutout | 10 | 15 | 2 | East | BCHF5
128259 | 2014-01-09 | Defective Equipment | Defective Equipment/ Material | Barrier board fell into primary. | O/H Switchgear | Fused Cutout | 20 | 22 | 7 | East | BCHF5
128259 | 2014-01-09 | Defective Equipment | Defective Equipment/ Material | Barrier board fell into primary. | O/H Switchgear | Fused Cutout | 52 | 131 | 114 | East | BCHF5
128260 | 2014-01-10 | Unknown/Other | Unknown | AP02 circuit A/R/A due to vandalism to hydro plant on Berma and Via Venus | None | None | 0 | 5 | 0 | East | AP02
128260 | 2014-01-10 | Unknown/Other | Unknown | AP02 circuit A/R/A due to vandalism to hydro plant on Berma and Via Venus | None | None | 4 | 143 | 10 | East | AP02
128261 | 2014-01-10 | Loss Of Supply | Transmission Planned | Hydro One reports SC2 breaker has failed and is stuck closed. Hydro One has dumped load on the B bus at Hawthrone. | None | None | 1839 | 8 | 245 | East | 48M4
128261 | 2014-01-10 | Loss Of Supply | Transmission Planned | Hydro One reports SC2 breaker has failed and is stuck closed. Hydro One has dumped load on the B bus at Hawthrone. | None | None | 3149 | 8 | 420 | East | 48M3
128261 | 2014-01-10 | Loss Of Supply | Transmission Planned | Hydro One reports SC2 breaker has failed and is stuck closed. Hydro One has dumped load on the B bus at Hawthrone. | None | None | 4010 | 8 | 535 | East | 48M5
128262 | 2014-01-10 | Scheduled Outage | Maintenance | Maintenace on secondary. | None | None | 21 | 45 | 16 | East | UA04
128263 | 2014-01-11 | Foreign Interference | Vandalism/Sabotage | Vandilism, and copper theft caused AP02 breaker to Trip. Circuit isolated, for repair. City of Ottawa pumping station to remain on generator. | O/H Conductor | O/H Conductor | 4 | 220 | 15 | East | AP02
128264 | 2014-01-11 | Adverse Environment | Contamination (Dirt, pollution, other external particles) | System Office attempted to close the AP02 CB back in after it had opened. AP02 & AP04 circuits run parallel to one another on Langs Rd. A flash caused the AP04 circuit to open. 41 customers were affected for 46 minutes. Langs Rd DS (AP04) ID# 128264 | Unknown \ Other | Unknown \ Other | 41 | 46 | 31 | East | AP04
128265 | 2014-01-11 | Defective Equipment | Mechanical Failure | TS41 (TK6TS) tripped due to cable fault between VT463 and VT408. | U/G Cable | PILC | 159 | 13 | 34 | Central | TK6TS
128265 | 2014-01-11 | Defective Equipment | Mechanical Failure | TS41 (TK6TS) tripped due to cable fault between VT463 and VT408. | U/G Cable | PILC | 166 | 160 | 443 | Central | TK6TS
128266 | 2014-01-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X32627 opened up due to tree interference. | O/H Switchgear | Fused Cutout | 10 | 205 | 34 | Central | TD12
128267 | 2014-01-11 | Scheduled Outage | Construction | Transformer #X31399 opened by crew to re-energize a service after fire | None | None | 7 | 45 | 5 | Central | SB03
128269 | 2014-01-11 | Defective Equipment | Defective Equipment/ Material | Broken fuse in cut-out | O/H Switchgear | Fused Cutout | 8 | 33 | 4 | South | EPWF6
128270 | 2014-01-11 | Scheduled Outage | Construction | Allow contractor to pull in secondary | None | None | 2 | 179 | 6 | West | BRDF2
128271 | 2014-01-12 | Scheduled Outage | Maintenance | Sagging conductor slapping together on open wire services causing sparking | None | O/H Conductor | 26 | 10 | 4 | East | UB03
128272 | 2014-01-11 | Scheduled Outage | Construction | Construction at Bayshore. | None | None | 1 | 338 | 6 | South | 49F5
128273 | 2014-01-12 | Scheduled Outage | Maintenance | Transformer #X23225 opened by crew to replace triplex service. | None | None | 25 | 45 | 19 | East | AC04
128276 | 2014-01-13 | Scheduled Outage | Construction | The taps at pole X42587 on Parent/Guigues were cut by the O/H crew to allow them restring new O/H conductor | None | O/H Conductor | 6 | 210 | 21 | Central | SK09
128277 | 2014-01-13 | Defective Equipment | Defective Equipment/ Material | Transformer X28190 isolated to allow crew to repair connections at 2359 Tampa Ave. | O/H Conductor | O/H Conductor | 10 | 59 | 10 | East | TB2JP
128278 | 2014-01-13 | Defective Equipment | Defective Equipment/ Material | Transformer X19149 at 2899 Innes Rd. isolated so crew could change insulators. | Pole Attachement | Insulator | 1 | 93 | 2 | East | BLKF3
128279 | 2014-01-14 | Scheduled Outage | Construction | Transformer X30991 at 238 Daly Ave. isolated by crew to upgrade plant to new spun buss | None | None | 2 | 115 | 4 | Central | SK10
128280 | 2014-01-14 | Scheduled Outage | Construction | Transformer X35215 isolated by contractor to transfer load to new phase. | None | None | 7 | 50 | 6 | Central | UW07
128281 | 2014-01-14 | Scheduled Outage | Construction | To upgrade TP7697 from 150 to 300 kva | None | None | 1 | 70 | 1 | West | 624F6
128282 | 2014-01-14 | Scheduled Outage | Maintenance | At 13:15, 4KV O/H transformers X31178 & X31179 were openned to allow crews to rearrange O/H. 16 customers affected for 9 minutes. Slater (SA23) ID #128282. | None | None | 16 | 9 | 2 | Central | SA23
128283 | 2014-01-14 | Scheduled Outage | Construction | Transformers X33833 at 1193 Cline Cres, X32458 at 1156 Whitmore Ave and X33842 at 1151 Cline Cres. Isolated by contractor to move tranformer loads to new phase. | None | None | 17 | 30 | 8 | Central | UW07
128284 | 2014-01-15 | Defective Equipment | Electrical Failure | Defective submersible transfromer at sidewalk vault TV92 caused the fuse at SC72 to open. | U/G Transformer | SIDT - Submersible (Turtle) | 59 | 823 | 809 | Central | UD08
128285 | 2014-01-15 | Scheduled Outage | Maintenance | 13kv transformer X25688 at 2 Armstrong opened for crew replacing transformer cut out affecting 11 customers for xx min, Hinchey, TH11, ID # 128285 | None | None | 11 | 79 | 14 | Central | TH11-NIU
128286 | 2014-01-15 | Scheduled Outage | Construction | Transformer X19155 at 9 Alder Cres. Isolated by crew to upgrade insulators | None | None | 16 | 120 | 32 | East | BLKF8
128287 | 2014-01-15 | Scheduled Outage | Construction | Transformer X25690 at 36 Armstrong isolated by crew to change cutout and arrestors | None | None | 7 | 78 | 9 | Central | TH11-NIU
128288 | 2014-01-15 | Scheduled Outage | Construction | Transformer X32457 at 1219 Whitmore Ave., X35216 at 1167 Whitmore Ave and 1121 Cline Cres. Isolated by contractor to transfer plant | None | None | 13 | 40 | 9 | Central | UW07
128289 | 2014-01-15 | Scheduled Outage | Construction | Transformer X30287 at 77 Armstrong St. isolated by crew to change cutout and arrestors | None | None | 13 | 74 | 16 | Central | TH11-NIU
128290 | 2014-01-15 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X337777 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 30 | 5 | Central | UW07
128291 | 2014-01-15 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35341 TO RE-SAG SECONDARY SERVICE | None | None | 7 | 20 | 2 | Central | AD07
128292 | 2014-01-15 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X24675 DUE TO VOLTAGE PROBLEM | None | None | 7 | 60 | 7 | East | SO10
128293 | 2014-01-16 | Scheduled Outage | Construction | Installing new cable in spare duct. | None | Padmount (3ph) | 13 | 251 | 54 | Central | UN07
128294 | 2014-01-16 | Tree Contacts | Broken Branch | Transformer X31504 at 870 Hare Ave. isolated by 24/7 to allow forestry crew to remove tree branch from primary. | None | None | 11 | 34 | 6 | Central | TW22
128295 | 2014-01-16 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 crew refused transformer X33552 due to foreign interference - bird contact | O/H Switchgear | Fused Cutout | 3 | 82 | 4 | Central | 303
128296 | 2014-01-16 | Scheduled Outage | Construction | Transformer X35047 isolated to allow crew to transfer plant to new pole. | None | None | 24 | 108 | 43 | Central | AH05
128297 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | TO2UB circuit (TO46) tripped for unknown reason. | U/G Cable | PILC | 549 | 84 | 769 | East | TO2UB
128297 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | TO2UB circuit (TO46) tripped for unknown reason. | U/G Cable | PILC | 553 | 16 | 147 | East | TO2UB
128297 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | TO2UB circuit (TO46) tripped for unknown reason. | U/G Cable | PILC | 554 | 13 | 120 | East | TO2UB
128297 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | TO2UB circuit (TO46) tripped for unknown reason. | U/G Cable | PILC | 687 | 9 | 103 | East | TO2UB
128297 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | TO2UB circuit (TO46) tripped for unknown reason. | U/G Cable | PILC | 688 | 11 | 126 | East | TO2UB
128297 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | TO2UB circuit (TO46) tripped for unknown reason. | U/G Cable | PILC | 865 | 18 | 260 | East | TO2UB
128297 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | TO2UB circuit (TO46) tripped for unknown reason. | U/G Cable | PILC | 866 | 14 | 202 | East | TO2UB
128297 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | TO2UB circuit (TO46) tripped for unknown reason. | U/G Cable | PILC | 867 | 16 | 231 | East | TO2UB
128297 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | TO2UB circuit (TO46) tripped for unknown reason. | U/G Cable | PILC | 880 | 61 | 895 | East | TO2UB
128298 | 2014-01-17 | Scheduled Outage | Construction | To replace defective cut out, insulator and arrester. | None | None | 1 | 65 | 1 | West | ALEXF3
128299 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | Defective streetlight cable, caused transformer fuse to blow in KT523. Transformer isolated and disconnected cable. TO2UB TO 46 breaker tripped originally at 12:08 am (Outage report#128297), calls from customers on KT523 came in later in the morning. | U/G Transformer | Kiosk (1ph) | 14 | 720 | 168 | East | TO2UB
128300 | 2014-01-17 | Defective Equipment | Defective Equipment/ Material | Secondary cable fault, customer owned issued. When Hydro Ottawa crew re-energized vault, the OCB tripped. | Vault Equipment | Cable | 1 | 1133 | 19 | East | AF03
128303 | 2014-01-18 | Defective Equipment | Electrical Failure | changing transformer | O/H Transformer | O/H Transformer (1ph) | 18 | 185 | 56 | East | AC07
128304 | 2014-01-19 | Defective Equipment | Electrical Failure | 304 (TM12 Breaker) tripped due to cable fault between VT910 and VT677 on Baseline Rd. VT910 was isolated by request of customer for customer inspection and repairs. | U/G Cable | PILC | 1 | 1343 | 22 | Central | 304
128304 | 2014-01-19 | Defective Equipment | Electrical Failure | 304 (TM12 Breaker) tripped due to cable fault between VT910 and VT677 on Baseline Rd. VT910 was isolated by request of customer for customer inspection and repairs. | U/G Cable | PILC | 3 | 25 | 1 | Central | 304
128304 | 2014-01-19 | Defective Equipment | Electrical Failure | 304 (TM12 Breaker) tripped due to cable fault between VT910 and VT677 on Baseline Rd. VT910 was isolated by request of customer for customer inspection and repairs. | U/G Cable | PILC | 4 | 74 | 5 | Central | 304
128305 | 2014-01-20 | Scheduled Outage | Construction | ISOLATED OVERHEAD PRIMARY LINE FEEDING 4 TRANSFORMERS ON EAST OF FIELD ST TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 29 | 45 | 22 | Central | UW07
128306 | 2014-01-20 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | PILC | 199 | 3 | 10 | East | TO2AP
128306 | 2014-01-20 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | PILC | 726 | 3 | 36 | East | TO2UB
128307 | 2014-01-20 | Scheduled Outage | Construction | Transformer X31346 at 797 Bank St. isolated for pole change by contractor | None | None | 13 | 120 | 26 | Central | SB05
128313 | 2014-01-24 | Unknown/Other | Unknown | SC4399-CB3 tripped, No apparent cause, suspect cold weather | None | None | 410 | 60 | 410 | West | 624F4
128314 | 2014-01-25 | Foreign Interference | Wildlife (Bird/Animal) | A pigeon hit the primary bushing on transformer X31939 at the rear of 2692 Regina St. This caused S26046 to open affecting two other transformers on this line. | O/H Transformer | O/H Transformer (1ph) | 34 | 119 | 67 | Central | TD14
128317 | 2014-01-26 | Defective Equipment | Defective Equipment/ Material | Unknown issues with SC4399-CB3 | Unknown \ Other | Unknown \ Other | 410 | 40 | 273 | West | 624F4
128318 | 2014-01-26 | Defective Equipment | Defective Equipment/ Material | Suspected issues with SC4399-CB3 | U/G Switchgear | Unknown \ Other | 410 | 72 | 492 | West | 624F4
128319 | 2014-01-27 | Scheduled Outage | Maintenance | Customer Vault Maintenance | None | None | 1 | 202 | 3 | Central | TC2TL
128320 | 2014-01-27 | Scheduled Outage | Construction | Transformer #X31800 isolated by crew to transfer plant | None | None | 18 | 185 | 56 | Central | AM05
128321 | 2014-01-27 | Defective Equipment | Defective Equipment/ Material | Transformer #X32352 isolated by crew to make repairs. One spade on sec bushing was burnt off | O/H Transformer | O/H Transformer (1ph) | 14 | 40 | 9 | Central | TD06
128322 | 2014-01-27 | Scheduled Outage | Maintenance | To remove a car that is sitting on top of the transformer and replace TP7404 | None | Kiosk (1ph) | 8 | 158 | 21 | South | FAL04
128323 | 2014-01-28 | Foreign Interference | Vehicle | ISOLATED TRANSFORMER X23904 TO ATTACH BOOM TRUCK TO THE POLE (POLE BROKEN MVA) | Pole | Pole | 14 | 17 | 4 | East | 6F7
128324 | 2014-01-28 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31179 AND X31178 TO INSTALL NEW POLE | None | None | 15 | 250 | 62 | Central | SA23
128325 | 2014-01-29 | Tree Contacts | Off Right of Way Tree | Transformer X23659 @ 744 Longsdale was isolated to allow the crews to remove a tree 10 customers affected | O/H Conductor | O/H Conductor | 10 | 316 | 53 | East | UB07
128326 | 2014-01-29 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33963 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 14 | 210 | 49 | Central | UW13
128327 | 2014-01-29 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X37962 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 180 | 18 | Central | AM05
128328 | 2014-01-29 | Scheduled Outage | Construction | Pole Change | None | None | 25 | 225 | 94 | Central | UX09
128329 | 2014-01-29 | Adverse Environment | Fire | At the request of the fire department | None | None | 1 | 793 | 13 | East | 77M6
128330 | 2014-01-30 | Scheduled Outage | Maintenance | VT197 at 30 Cartire was isolated to allow metering crew to perform meter repairs at VT197 | None | None | 1 | 40 | 1 | Central | 616
128331 | 2014-01-30 | Scheduled Outage | Maintenance | Transformer X32477 at 839 Iroquois Rd. Isolated to change triplex. | None | None | 1 | 105 | 2 | Central | TW22
128332 | 2014-01-30 | Scheduled Outage | Construction | Transformer #X37962 isolated by crew to transfer plant. | None | None | 6 | 185 | 18 | Central | AM05
128334 | 2014-01-30 | Scheduled Outage | Construction | Transformer X3467 at 5367 Old Richmond Rd. Isolated by Sam Baird crew to rearange plant. | None | None | 5 | 51 | 4 | South | 145F3
128335 | 2014-01-30 | Scheduled Outage | Construction | Transformer TP6931 at 510 Creekview was isolated to allow crew to cut in 6 new transformer between TP6931 and TP9463. | None | None | 7 | 242 | 28 | East | LTM01
128338 | 2014-01-31 | Loss Of Supply | Transmission Inadvertent | Fault on Hydro One customer owned primary equipment caused A8M A/R, supply to Uplands & Merivale T1. | None | None | 5198 | 13 | 1126 | East | A8M (Uplands - T3)
128340 | 2014-02-01 | Scheduled Outage | Construction | 4kv vault V628 at 2199 Regency Terr was isolated to allow crew to de-commision the vault and replace it with a new pad mount, affecting 1 customer for 260 minutes, Woodroffe sub, UW13, ID # 128340 | None | None | 1 | 260 | 4 | Central | UW13
128343 | 2014-02-01 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 22 | 62 | 23 | West | BRDF4
128343 | 2014-02-01 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 1063 | 41 | 726 | West | BRDF4
128343 | 2014-02-01 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 1118 | 41 | 764 | West | BRDF4
128343 | 2014-02-01 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 2830 | 146 | 6886 | West | BRDF4
128343 | 2014-02-02 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 1 | 120 | 2 | West | BRDF4
128343 | 2014-02-02 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 2 | 590 | 20 | West | BRDF4
128343 | 2014-02-02 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 4 | 18 | 1 | West | BRDF4
128343 | 2014-02-02 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 22 | 62 | 23 | West | BRDF4
128343 | 2014-02-02 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 129 | 6 | 13 | West | BRDF4
128343 | 2014-02-02 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 719 | 35 | 419 | West | BRDF4
128343 | 2014-02-02 | Defective Equipment | Electrical Failure | BRDF4 CB tripped due to a confirmed cable fault between S52 and S64 and a suspected cable fault between 234 and 232. | U/G Cable | Unknown \ Other | 1497 | 50 | 1248 | West | BRDF4
128345 | 2014-02-03 | Scheduled Outage | Maintenance | Replace defective transformer cutout | None | None | 10 | 60 | 10 | Central | TH11-NIU
128346 | 2014-02-03 | Scheduled Outage | Construction | Replace defective Trans cutout | None | None | 8 | 40 | 5 | Central | TH11-NIU
128347 | 2014-02-03 | Scheduled Outage | Maintenance | Transformer #X29030 isolated by crew to check the transformer for a defective neutral | None | None | 9 | 45 | 7 | East | SO04
128349 | 2014-02-04 | Human Element | Switching Error | Switching error | None | None | 402 | 29 | 194 | Central | 503
128350 | 2014-02-04 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32611 (SQUIRREL ) | O/H Transformer | O/H Transformer (1ph) | 11 | 54 | 10 | Central | TD14
128351 | 2014-02-04 | Scheduled Outage | Construction | Transformer X30563 at 16 Somerset W and X 30300 at 45 Somerset St isolated by contractor to install new poles and transfer buss. Installed new transformer X45391 to replace the 2 transformers listed above. | None | None | 55 | 234 | 214 | Central | UX09
128352 | 2014-02-04 | Scheduled Outage | Construction | Install new overhead conductors. | None | None | 2 | 322 | 11 | South | 145F3
128353 | 2014-02-04 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact | O/H Transformer | O/H Transformer (1ph) | 8 | 81 | 11 | East | 7F4
128354 | 2014-02-05 | Scheduled Outage | Construction | TP9976 isolated to allow crews to install new secondary service. | None | None | 1 | 2894 | 48 | East | BCHF5
128355 | 2014-02-05 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32500 (SQUIRREL) | O/H Transformer | O/H Transformer (1ph) | 8 | 39 | 5 | Central | TD01
128356 | 2014-02-05 | Scheduled Outage | Vegetation Management | To Remove tree. | None | None | 30 | 327 | 164 | East | AF02
128357 | 2014-02-05 | Scheduled Outage | Construction | To allow crew to install new overhead conductors. | None | None | 2 | 294 | 10 | South | 145F3
128358 | 2014-01-09 | Human Element | Improper Construction/installation | Incorrect secondary connections at TP6880. | Secondary \ Service | U/G Service | 3 | 10470 | 524 | South | FAL01
128359 | 2014-02-06 | Scheduled Outage | Vegetation Management | The crew open switch S12386 to isolate the O/H on PARKHILL CIR to allow tree contractors to remove a tree, 4 custromer affect | None | O/H Conductor | 4 | 305 | 20 | East | AF02
128360 | 2014-02-06 | Scheduled Outage | Construction | To transfer plant on pole to make room for pole replacement. Switch G59R opened. | None | None | 12 | 99 | 20 | East | BLKF5
128361 | 2014-02-06 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X30091 TO RE-ARRANG HYDRO PLANT | None | None | 16 | 270 | 72 | Central | SB03
128363 | 2014-02-06 | Defective Equipment | Mechanical Failure | V140 @ 52 BAYSWATER AVE was isolated to replace the defective transformers | Vault Equipment | Transformer | 1 | 273 | 5 | Central | UJ06
128365 | 2014-02-07 | Scheduled Outage | Construction | Secondary service upgrade | None | None | 11 | 73 | 13 | Central | SB05
128366 | 2014-02-08 | Defective Equipment | Mechanical Failure | 24/7 crew opened transformer # X33995 to repair connects at transformer. | O/H Transformer | O/H Transformer (1ph) | 10 | 20 | 3 | Central | UV05
128367 | 2014-02-09 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X40809 opened up due to squirrel interference | O/H Switchgear | Fused Cutout | 20 | 66 | 22 | East | TB06
128368 | 2014-02-09 | Scheduled Outage | Construction | Switch replacement. | None | None | 1 | 99 | 2 | South | FAL01
128369 | 2014-02-10 | Scheduled Outage | Construction | Switch replacement | None | None | 1 | 130 | 2 | South | FAL01
128371 | 2014-02-11 | Scheduled Outage | Maintenance | TP9594 isolated to upgrade transformer. Temporary interruption to 10 transformers due to out of phase condition. | None | Padmount (1ph) | 0 | 10 | 0 | West | 624F1
128371 | 2014-02-11 | Scheduled Outage | Maintenance | TP9594 isolated to upgrade transformer. Temporary interruption to 10 transformers due to out of phase condition. | None | Padmount (1ph) | 14 | 104 | 24 | West | 624F1
128371 | 2014-02-11 | Scheduled Outage | Maintenance | TP9594 isolated to upgrade transformer. Temporary interruption to 10 transformers due to out of phase condition. | None | Padmount (1ph) | 65 | 3 | 3 | West | 624F1
128371 | 2014-02-11 | Scheduled Outage | Maintenance | TP9594 isolated to upgrade transformer. Temporary interruption to 10 transformers due to out of phase condition. | None | Padmount (1ph) | 65 | 5 | 5 | West | 624F1
128374 | 2014-02-11 | Scheduled Outage | Construction | Transformer X30678 isolated by contractor and replaced with X47601 | None | None | 10 | 170 | 28 | Central | SA23
128375 | 2014-02-11 | Defective Equipment | Defective Equipment/ Material | Transformer X27880 isolated for 24/7 crew to replace customer owned fuses (fuses supplied by customer). | Customer Owned | Customer-Owned | 4 | 32 | 2 | East | UZ11
128377 | 2014-02-11 | Defective Equipment | Electrical Failure | BRDF7 circuit auto-reclosed and S33 white phase fuse blew due to cable fault between transformers 1396 and 2988. | U/G Cable | Unknown \ Other | 2 | 59 | 2 | West | BRDF7
128377 | 2014-02-11 | Defective Equipment | Electrical Failure | BRDF7 circuit auto-reclosed and S33 white phase fuse blew due to cable fault between transformers 1396 and 2988. | U/G Cable | Unknown \ Other | 3 | 44 | 2 | West | BRDF7
128377 | 2014-02-11 | Defective Equipment | Electrical Failure | BRDF7 circuit auto-reclosed and S33 white phase fuse blew due to cable fault between transformers 1396 and 2988. | U/G Cable | Unknown \ Other | 4 | 84 | 6 | West | BRDF7
128377 | 2014-02-11 | Defective Equipment | Electrical Failure | BRDF7 circuit auto-reclosed and S33 white phase fuse blew due to cable fault between transformers 1396 and 2988. | U/G Cable | Unknown \ Other | 38 | 123 | 78 | West | BRDF7
128378 | 2014-02-12 | Scheduled Outage | Maintenance | S22980 Blue phase opened to allow crew to change connections. | None | None | 14 | 119 | 28 | East | LTM01
128379 | 2014-02-12 | Scheduled Outage | Construction | Upgrade transformer | None | None | 10 | 195 | 32 | Central | UX09
128380 | 2014-02-12 | Scheduled Outage | Vegetation Management | tree removal | None | None | 12 | 305 | 61 | East | TB14
128381 | 2014-02-12 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30868 TO UP-GRADE TRANSFORMER | None | None | 15 | 105 | 26 | Central | UX02
128383 | 2014-02-14 | Scheduled Outage | Construction | Voltage conversion from 8kv to 27kv. | None | None | 1 | 213 | 4 | South | 145F4
128385 | 2014-02-15 | Scheduled Outage | Maintenance | checking metering fuses. | None | None | 1 | 91 | 2 | Central | 602
128386 | 2014-02-15 | Scheduled Outage | Maintenance | The 13Kv vault VT146 @ 525 MacKenzie was isolated by the crew to allow the contractor to preform breaker maintenance and trouble shoot remote breaker, 1 customer affected. | None | Customer-Owned | 1 | 235 | 4 | Central | 608
128387 | 2014-02-15 | Foreign Interference | Wildlife (Bird/Animal) | 160F3 circuit tripped due to squirrel contact. | None | None | 25 | 56 | 23 | South | 160F3
128387 | 2014-02-15 | Foreign Interference | Wildlife (Bird/Animal) | 160F3 circuit tripped due to squirrel contact. | None | None | 50 | 19 | 16 | South | 160F3
128388 | 2014-02-15 | Defective Equipment | Mechanical Failure | Fuse blown at overhead transformer. Tired fuse, Replaced fuse and closed. | O/H Switchgear | Fused Cutout | 1 | 83 | 1 | West | RHNF3
128389 | 2014-02-17 | Defective Equipment | Electrical Failure | REPLACED DEFECTIVE OVERHEAD TTRANSFORMER X27883 | O/H Transformer | O/H Transformer (1ph) | 2 | 318 | 11 | East | UZ11
128390 | 2014-02-17 | Defective Equipment | Defective Equipment/ Material | Defective PILC cable a VT866 is blown on the 615-L3 side. | U/G Cable | PILC | 39 | 83 | 54 | Central | 615
128391 | 2014-02-18 | Scheduled Outage | Construction | Transformer #X30802 isolated by crew for a pole change | None | None | 10 | 150 | 25 | Central | UX09
128392 | 2014-02-19 | Defective Equipment | Defective Equipment/ Material | TM1UC PPH blown at UC. | O/H Switchgear | Simple Solid Blade Switch | 367 | 11 | 67 | Central | TM1UC
128394 | 2014-02-19 | Foreign Interference | Vehicle | G606R opened due to vehicle hitting Hydro pole at 5793 Leitrim Rd | Pole | Pole | 47 | 21 | 16 | East | 249F2
128394 | 2014-02-19 | Foreign Interference | Vehicle | G606R opened due to vehicle hitting Hydro pole at 5793 Leitrim Rd | Pole | Pole | 161 | 135 | 362 | East | 249F2
128395 | 2014-02-19 | Scheduled Outage | Construction | Transformer #X35044 isolated by crew to transfer plant | None | None | 24 | 245 | 98 | Central | AH05
128396 | 2014-02-19 | Defective Equipment | Defective Equipment/ Material | Tranformer #X36332 isolated by crew to replace defective cut out | O/H Switchgear | Fused Cutout | 1 | 20 | 0 | West | BECKF2
128397 | 2014-02-19 | Defective Equipment | Defective Equipment/ Material | Transformer #X35773 isolated by crew to replace defective cut out | O/H Switchgear | Fused Cutout | 1 | 19 | 0 | West | BECKF2
128398 | 2014-02-19 | Scheduled Outage | Construction | At 7:20 am, K1267 & V813 at 299 Bronson were isolated to transfer plant to new poles. 44 customers afected for 160 min. Cambridge AM04. ID#128398. | None | None | 44 | 160 | 117 | Central | AM04
128399 | 2014-02-19 | Defective Equipment | Defective Equipment/ Material | Transformer #X32027 isolated by crew to replace defective cut out (by Sam Baird) | O/H Switchgear | Fused Cutout | 1 | 25 | 0 | West | BECKF2
128400 | 2014-02-20 | Adverse Environment | Contamination (Salt) | P551 was isolated to allow crew to repair secondary cable fault in MH2817. | U/G Cable Attachement | Termination \ Stress Cone | 15 | 188 | 47 | Central | SR08
128402 | 2014-02-20 | Defective Equipment | Electrical Failure | Cable fault between VT98 and SC2 on Bank St near Kilborn. | U/G Cable | PILC | 0 | 54 | 0 | Central | 505
128402 | 2014-02-20 | Defective Equipment | Electrical Failure | Cable fault between VT98 and SC2 on Bank St near Kilborn. | U/G Cable | PILC | 1 | 76 | 1 | East | TA3AF
128402 | 2014-02-20 | Defective Equipment | Electrical Failure | Cable fault between VT98 and SC2 on Bank St near Kilborn. | U/G Cable | PILC | 256 | 86 | 367 | East | TA3AF
128402 | 2014-02-20 | Defective Equipment | Electrical Failure | Cable fault between VT98 and SC2 on Bank St near Kilborn. | U/G Cable | PILC | 1810 | 1 | 30 | Central | 505
128402 | 2014-02-20 | Defective Equipment | Electrical Failure | Cable fault between VT98 and SC2 on Bank St near Kilborn. | U/G Cable | PILC | 1810 | 4 | 121 | Central | 505
128403 | 2014-02-21 | Defective Equipment | Defective Equipment/ Material | 28F2 tripped with a white phase flag. A broken insulator was found at 3449 Mcbean St | Pole Attachement | Insulator | 214 | 87 | 310 | West | 28F2
128403 | 2014-02-21 | Defective Equipment | Defective Equipment/ Material | 28F2 tripped with a white phase flag. A broken insulator was found at 3449 Mcbean St | Pole Attachement | Insulator | 394 | 10 | 66 | West | 28F2
128403 | 2014-02-21 | Defective Equipment | Defective Equipment/ Material | 28F2 tripped with a white phase flag. A broken insulator was found at 3449 Mcbean St | Pole Attachement | Insulator | 448 | 157 | 1172 | West | 28F2
128403 | 2014-02-21 | Defective Equipment | Defective Equipment/ Material | 28F2 tripped with a white phase flag. A broken insulator was found at 3449 Mcbean St | Pole Attachement | Insulator | 466 | 2 | 16 | West | 28F2
128403 | 2014-02-21 | Defective Equipment | Defective Equipment/ Material | 28F2 tripped with a white phase flag. A broken insulator was found at 3449 Mcbean St | Pole Attachement | Insulator | 557 | 3 | 28 | West | 28F2
128404 | 2014-02-21 | Defective Equipment | Electrical Failure | 160F1 breaker tripped. RTU communicaion to QCH DS was down. Crew patrolled circuit and found broken cutout at S278. Switch cleared, and 160F1 still tripped. Crew sectionalized cct and found defective ca cables between 160F1 breaker and S10133. | U/G Cable | XLPE | 861 | 166 | 2382 | South | 160F1
128405 | 2014-02-21 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X44258 opened up due to bird contact | O/H Switchgear | Fused Cutout | 17 | 141 | 40 | Central | UN11
128406 | 2014-02-21 | Defective Equipment | Mechanical Failure | Broken cut-out S278 feeding 417 lighting transformer TE2449 caused the initial trip on 160F1 | O/H Switchgear | Fused Cutout | 1 | 399 | 7 | South | 160F1
128408 | 2014-02-21 | Defective Equipment | Mechanical Failure | On call crew replaced defective cut-out at S24899, 7176 Flewellyn. 1 customer affected for 290 min. BECKF2. ID#128408. | O/H Switchgear | Fused Cutout | 1 | 290 | 5 | West | BECKF2
128409 | 2014-02-22 | Adverse Environment | Fire | Pole Fire at S1000 required isolation for safety and repair | Pole | Insulation Failure (Pole Fire) | 43 | 351 | 252 | South | 180F2
128409 | 2014-02-22 | Adverse Environment | Fire | Pole Fire at S1000 required isolation for safety and repair | Pole | Insulation Failure (Pole Fire) | 67 | 218 | 243 | South | 180F6
128409 | 2014-02-22 | Adverse Environment | Fire | Pole Fire at S1000 required isolation for safety and repair | Pole | Insulation Failure (Pole Fire) | 89 | 10 | 15 | South | 180F6
128410 | 2014-02-21 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact. | O/H Switchgear | Fused Cutout | 4 | 345 | 23 | Central | UN04
128411 | 2014-02-22 | Scheduled Outage | Maintenance | Vault mainenance of VT314 @ 275 Wellington ave | None | Unknown \ Other | 1 | 394 | 7 | Central | 5203
128412 | 2014-02-22 | Defective Equipment | Defective Equipment/ Material | Replaced defective hotline clamp and refused switch at X36382 - 36 Vaan Dr. | O/H Switchgear | Fused Cutout | 2 | 195 | 6 | South | 170F3
128413 | 2014-02-22 | Defective Equipment | Defective Equipment/ Material | 24/7 crew replaced broken transformer switch at X30824 located at 403 Bank Street. | O/H Switchgear | Fused Cutout | 7 | 147 | 17 | Central | UX08
128414 | 2014-02-22 | Defective Equipment | Corrosion | Defective cutout in a 3 phase padmount transformer P216. | O/H Switchgear | Fused Cutout | 2 | 60 | 2 | Central | UC01
128415 | 2014-02-23 | Scheduled Outage | Construction | Reconfiguration of existing overhead line. | None | None | 5 | 413 | 34 | East | LTM01
128418 | 2014-02-24 | Scheduled Outage | Forced Switching | 13kV overhead section from fuse at pole 54B2D/1066 to EOL isolated to allow crews to replace buring hot line clamp | None | Hot-Line Clamp | 47 | 31 | 24 | Central | 505
128419 | 2014-02-24 | Scheduled Outage | Construction | Transformer #X35375 isolated by crew to re-arrange secondary. | None | None | 10 | 180 | 30 | Central | TD14
128420 | 2014-02-24 | Scheduled Outage | Maintenance | Secondary service repairs and switch change at dip pole X33627. | None | Padmount (1ph) | 10 | 123 | 20 | Central | UL05
128421 | 2014-02-24 | Scheduled Outage | Construction | Defective transformer. | None | None | 26 | 84 | 36 | South | 87F7
128421 | 2014-02-24 | Scheduled Outage | Construction | Defective transformer. | None | None | 39 | 11 | 7 | South | 87F7
128422 | 2014-02-24 | Scheduled Outage | Construction | Contractor removed X30301 at 180 Gladstone Ave. and upgraded X30302 to 75kVA transformer at 170 Gladstone Ave. | None | None | 29 | 220 | 106 | Central | UX05
128423 | 2014-02-25 | Scheduled Outage | Construction | 2 transformers (X35210 and X33847) isolated by crew to install a new pole (Jordan Foote from K line) | None | None | 11 | 35 | 6 | Central | UC10
128424 | 2014-02-25 | Defective Equipment | Defective Equipment/ Material | Transformer #X24759 isolated by crew to replace broken cut out | O/H Switchgear | Fused Cutout | 3 | 20 | 1 | East | 8F1
128425 | 2014-02-25 | Scheduled Outage | Maintenance | QT133 RMOC at 2 Aero was isolated to allow crew to re-insluate 44KV switch 44LB51 due to insulator flash over | None | Load Break Gang | 1 | 282 | 5 | South | 22M23
128426 | 2014-02-25 | Scheduled Outage | Construction | new pole installation | None | Pole | 1 | 255 | 4 | Central | UX05
128429 | 2014-02-26 | Scheduled Outage | Construction | At 09:50am, PC10a #11352 established by Bruce baker at S18533, to restring RHNF1 O/H. 1 customer affected for 345 minutes. Richmond North (RHNF1) ID #128429 | None | None | 1 | 345 | 6 | West | RHNF1
128430 | 2014-02-26 | Scheduled Outage | Maintenance | Transformer #X23758 isolated by crew due to streetlight sitting on the H1 bushing | None | None | 8 | 30 | 4 | East | SO02
128431 | 2014-02-26 | Scheduled Outage | Construction | Transformer #X23594 isolated by crew to connect 2 new homes. | None | None | 18 | 91 | 27 | East | UG04
128432 | 2014-02-26 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30302 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 7 | 195 | 23 | Central | UX05
128433 | 2014-02-26 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X46771 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 17 | 200 | 57 | Central | SK09
128434 | 2014-02-26 | Scheduled Outage | Construction | Transferring secondary conductor | None | None | 16 | 70 | 19 | West | BECKF2
128435 | 2014-02-27 | Scheduled Outage | Construction | At 9:26 am 4kv transformer X31155 at 514 Bay was isolated to allow installation of new under ground service, affecting 18 customers for 103 minutes, Florence, UC08, ID # 128435 | None | None | 18 | 103 | 31 | Central | UF08
128436 | 2014-02-27 | Defective Equipment | Defective Equipment/ Material | Transformer #X26631 opened by crew to replace a switch (Sam Baird) | O/H Switchgear | Inline Switch | 1 | 25 | 0 | West | MWDF3
128437 | 2014-02-27 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X43573 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 16 | 95 | 25 | Central | TR3UY
128438 | 2014-02-27 | Scheduled Outage | Maintenance | Preparatory work for future cable work. M1453 was isolated to free cables from mud & ice to allow switching for planned cable & duct work. Only streetlights & traffic lights fed from this Tx. | None | Kiosk (1ph) | 1 | 160 | 3 | Central | SK16
128439 | 2014-02-28 | Scheduled Outage | Maintenance | Asbestos removal and vault inspection | None | Unknown \ Other | 1 | 159 | 3 | East | 1802
128441 | 2014-02-28 | Scheduled Outage | Construction | Transformer #X32238 isolated by crew to transfer plant | None | None | 14 | 195 | 46 | Central | AD05
128442 | 2014-02-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X40114 isolated by crew to replace switch (Sam Baird) | O/H Switchgear | Inline Switch | 1 | 13 | 0 | West | MWDF3
128443 | 2014-02-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X40115 isolated by crew to replace switch (Sam Baird) | O/H Switchgear | Inline Switch | 1 | 40 | 1 | West | MWDF3
128444 | 2014-02-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X40102 isolated by crew to replace switch (Sam Baird) | O/H Switchgear | Inline Switch | 1 | 10 | 0 | West | MWDF3
128445 | 2014-02-28 | Defective Equipment | Electrical Failure | Customer investigating blown primary fuse at VT893, found blown Hydro Ottawa metering CT. Metering crew repaired blown CT. | Vault Equipment | Unknown \ Other | 1 | 225 | 4 | East | 5301
128447 | 2014-03-01 | Scheduled Outage | Maintenance | contractor to change transformer and perform vault maintenance. | None | None | 1 | 258 | 4 | East | 1806
128448 | 2014-03-01 | Scheduled Outage | Construction | Allow crew to transfer overhead to new pole. | None | None | 7 | 354 | 41 | Central | AD05
128449 | 2014-03-01 | Foreign Interference | Vehicle | KT385 dmagaed by snow plow, customers restored via CABTIRES and transformer to be repaired at a later date. | U/G Transformer | Kiosk (1ph) | 0 | 10 | 0 | Central | 303
128449 | 2014-03-01 | Foreign Interference | Vehicle | KT385 dmagaed by snow plow, customers restored via CABTIRES and transformer to be repaired at a later date. | U/G Transformer | Kiosk (1ph) | 6 | 234 | 23 | Central | 303
128449 | 2014-03-01 | Foreign Interference | Vehicle | KT385 dmagaed by snow plow, customers restored via CABTIRES and transformer to be repaired at a later date. | U/G Transformer | Kiosk (1ph) | 14 | 15 | 4 | Central | 303
128449 | 2014-03-01 | Foreign Interference | Vehicle | KT385 dmagaed by snow plow, customers restored via CABTIRES and transformer to be repaired at a later date. | U/G Transformer | Kiosk (1ph) | 20 | 99 | 33 | Central | 303
128451 | 2014-03-03 | Scheduled Outage | Forced Switching | ISOLATED TRANSFORMER X32003 TO DISCONNECT SERVICE TO 612 TWEEDSMUIR AVE DUE TO FIRE | None | None | 6 | 80 | 8 | Central | UL06
128453 | 2014-03-04 | Scheduled Outage | Construction | Hydro crew isolated transformer X30135 at 94 Cambridge St. to change switch on pole and at transformer. | None | None | 7 | 180 | 21 | Central | AM05
128454 | 2014-03-04 | Scheduled Outage | Construction | Contractor isolated X32751 at 1237 Field St. to transfer hydro plant | None | None | 6 | 75 | 8 | Central | UW07
128455 | 2014-03-04 | Scheduled Outage | Construction | Contractor isolated X32750 at 1277 Field St. for pole change with crane. | None | None | 8 | 210 | 28 | Central | UW07
128456 | 2014-03-04 | Scheduled Outage | Construction | Crew isolated transformer X30293 at 50 Pinhey St. to replace switch at transformer. | None | None | 12 | 207 | 41 | Central | TH11-NIU
128457 | 2014-03-04 | Scheduled Outage | Construction | Crew isolated transformer X27847 at 110 Stirling to replace switch and arrester. | None | None | 9 | 50 | 8 | Central | TH11-NIU
128458 | 2014-03-04 | Scheduled Outage | Construction | Crew isolated transformer X34681 at 76 Stirling Ave. to replace switch. | None | None | 18 | 80 | 24 | Central | TH11-NIU
128461 | 2014-03-05 | Scheduled Outage | Construction | Crew isolated transformer X27969 at 202 Carruthers to replace cutout and broken arrestor. | None | None | 16 | 53 | 14 | Central | TH11-NIU
128462 | 2014-03-05 | Scheduled Outage | Construction | Transformer #X27849 isolated by crew to replace cutout and arrestor | None | None | 15 | 107 | 27 | Central | TH11-NIU
128463 | 2014-03-05 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X27843 TO REPLACE SWITCH | None | None | 11 | 45 | 8 | Central | TH11-NIU
128464 | 2014-03-05 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X27842 TO REPLACE TRANSFORMER SWITCH | None | None | 31 | 65 | 34 | Central | TH11-NIU
128465 | 2014-03-05 | Scheduled Outage | Maintenance | Transformer #X27841 isolated by crew to replace cutout and arrestor | None | None | 16 | 43 | 11 | Central | TH11-NIU
128466 | 2014-03-05 | Defective Equipment | Electrical Failure | Defective transformer TE392 | U/G Transformer | SIDT - Submersible (Turtle) | 12 | 479 | 96 | East | BLKF3
128467 | 2014-03-06 | Defective Equipment | Moisture Ingress | The S12659 RWB and S13785 B opened on Orleans Blvd due to SE17 switch gear flash over. | U/G Switchgear | Live-Front | 103 | 206 | 354 | East | 77M2
128468 | 2014-03-06 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X40136 TO RE-INSULATE THE POLE | None | None | 1 | 45 | 1 | West | MWDF3
128469 | 2014-03-06 | Foreign Interference | Wildlife (Bird/Animal) | At 11:24, GR2 red phase reclosure tripped under holdoff, patrol found fused cutout to X13184 located at 821 River Rd, blown due to animal contact. 95 customers affected for 81 minutes. Limebank (7F4) ID #128469 | O/H Transformer | O/H Transformer (1ph) | 95 | 81 | 128 | East | 7F4
128472 | 2014-03-07 | Scheduled Outage | Construction | S989 to EOL pn Lytle was isolated to allow crew to perform pole replacement. 6 customers were affected for 199 mintes. Jockvale (145F2). ID# 128472 | None | None | 6 | 199 | 20 | South | 145F2
128473 | 2014-03-07 | Scheduled Outage | Construction | Replace transformer cutout and arrestor | None | None | 12 | 65 | 13 | Central | TH11-NIU
128474 | 2014-03-07 | Scheduled Outage | Construction | Replace transformer cut out and arrestor | None | None | 12 | 40 | 8 | Central | TH11-NIU
128476 | 2014-03-07 | Scheduled Outage | Construction | Transformer X47160 at 5769 isolated by crew for pole conversion | None | None | 1 | 255 | 4 | Central | TH11-NIU
128477 | 2014-03-07 | Scheduled Outage | Maintenance | Transformer X23898 at 86 Carruthers Ave. isolated by crew to replace switch | None | None | 12 | 85 | 17 | Central | TH11-NIU
128479 | 2014-03-08 | Scheduled Outage | Construction | To replace damaged 1500 kva transformer at Walmart. TE3833 | None | None | 1 | 259 | 4 | East | 1802
128480 | 2014-03-08 | Scheduled Outage | Maintenance | QT205 was interupted to provide isolation for Hydro Ottawa crew to repair MSO175 | None | Simple Solid Blade Switch | 1 | 168 | 3 | South | 22M28
128481 | 2014-03-08 | Scheduled Outage | Construction | TN9576 was interupted to allow Hydro Ottawa crew to install new VBM CS18774 | None | None | 1 | 250 | 4 | East | 48M5
128482 | 2014-03-08 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X19007 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 8 | 168 | 22 | East | CYRF1
128484 | 2014-03-10 | Scheduled Outage | Construction | Transformer X27627 at 66 Stonehurst Ave. Isolated by crew to replace cutout and arrestor | None | Fused Cutout | 11 | 65 | 12 | Central | TH11-NIU
128485 | 2014-03-10 | Scheduled Outage | Construction | Transformer X23897 at 52 Stonehurst Ave. Isolated to allow crew to replace cutout and arrestor | None | Fused Cutout | 10 | 64 | 11 | Central | TH11-NIU
128486 | 2014-03-10 | Scheduled Outage | Construction | X36297 at 5687 Fernbank was isolated to perform voltage convertion work, affecting 1 customer for 121 minutes, Richmond North, RHNF2, ID # 128486 | None | None | 1 | 121 | 2 | West | RHNF2
128487 | 2014-03-10 | Scheduled Outage | Construction | 8kV overhead circuit from S23796 to EOL at 4945 Piperville Rd. Was isolated to allow crews to replace primary switches. | None | Fused Cutout | 1 | 36 | 1 | East | 249F2
128488 | 2014-03-10 | Scheduled Outage | Maintenance | Transformer #X7437 isolated by crew to replace switch (Sam Baird) | None | None | 1 | 15 | 0 | West | 624F6
128489 | 2014-03-10 | Scheduled Outage | Maintenance | Transformer #X36602 isolated by crew to replace switch (Sam Baird) | None | None | 1 | 15 | 0 | West | 624F6
128490 | 2014-03-10 | Scheduled Outage | Construction | Transformer #X11431 isolated by crew to transfer load | None | None | 1 | 5 | 0 | West | 43F3
128491 | 2014-03-10 | Scheduled Outage | Maintenance | Transformer #X30296 isolated by crew to replace cut out and arrestor | None | None | 17 | 53 | 15 | Central | TH11-NIU
128492 | 2014-03-10 | Scheduled Outage | Maintenance | Transformer X27629 at 39 Lyndale Ave. Isolated by crew to change switch and arrestor | None | Inline Switch | 9 | 25 | 4 | Central | TH11-NIU
128493 | 2014-03-10 | Scheduled Outage | Maintenance | Transformer X30294 at 62 Pinehy St. Isolated by crew to change switch | None | Inline Switch | 7 | 40 | 5 | Central | TH11-NIU
128494 | 2014-03-10 | Scheduled Outage | Maintenance | Transformer X27627 at 66 Stonehurst Ave. Isolated for crew to change switch and arrestor | None | Inline Switch | 11 | 65 | 12 | Central | TH11-NIU
128495 | 2014-03-10 | Scheduled Outage | Maintenance | Transformer 003477 at 2495 Fifth Line Rd. Isolated by crew to change switch | None | Inline Switch | 1 | 40 | 1 | West | 624F6
128496 | 2014-03-10 | Scheduled Outage | Construction | Transformer X11425 at 7597 Bleeks Rd isolated for crew to transfer load for future conversion | None | None | 2 | 18 | 1 | West | 43F3
128497 | 2014-03-10 | Unknown/Other | Unknown | S13187 W found blown, no apparant cause. Line patrolled, nothing found, fuse replaced & line patrolled again. | O/H Switchgear | Fused Cutout | 64 | 150 | 160 | East | TB2JP
128498 | 2014-03-10 | Scheduled Outage | Construction | Transformer X11428 at 7549 Bleeks Rd isolated to allow crew to transfer load for future conversion | None | None | 1 | 8 | 0 | West | 43F3
128499 | 2014-03-10 | Defective Equipment | Defective Equipment/ Material | Transformer #X5487 isolated by crew to replace broken porcelain insulator | Pole Attachement | Insulator | 1 | 65 | 1 | South | 140F4
128500 | 2014-03-11 | Scheduled Outage | Construction | KT385 isolated to allow crews to replace secondary pedastel and conductor. | None | Secondary Pedestal | 6 | 248 | 25 | Central | 303
128502 | 2014-03-11 | Scheduled Outage | Maintenance | Transformer X25651 at 44 Ladouceur St. isolated by crew to replace switch and arrestor | None | None | 25 | 40 | 17 | Central | TH11-NIU
128503 | 2014-03-11 | Scheduled Outage | Maintenance | Transformer X07076 at 1370 Murphy Side Rd. isolated by crew to replace switch | None | None | 1 | 32 | 1 | West | MWDF3
128504 | 2014-03-11 | Scheduled Outage | Maintenance | Transformer X07032 at 1755 Old Second Line Rd. isolated for crew to replace switch (Sam Baird) | None | None | 1 | 35 | 1 | West | MWDF3
128505 | 2014-03-11 | Scheduled Outage | Maintenance | Transformer X40168 at 1 Grierson Lane isolated by Sam Baird crew to change switch | None | None | 4 | 27 | 2 | West | MWDF3
128506 | 2014-03-11 | Scheduled Outage | Maintenance | Transformer X25693 at 24 Lowrey St. isolated by crew to change switch | None | None | 21 | 45 | 16 | Central | TH11-NIU
128507 | 2014-03-11 | Scheduled Outage | Maintenance | Replaced arrestor at Switch G461W | None | None | 46 | 147 | 113 | East | 56F1
128508 | 2014-03-11 | Scheduled Outage | Maintenance | Sam Baird crew changed switch at transformer X40163 at 11 Grierson Lane | None | None | 2 | 33 | 1 | West | MWDF3
128510 | 2014-03-11 | Scheduled Outage | Construction | Transfer Plant to new poles | None | None | 2 | 120 | 4 | East | 7F2
128511 | 2014-03-11 | Scheduled Outage | Construction | replace trans switch | None | None | 4 | 25 | 2 | West | MWDF3
128512 | 2014-03-12 | Scheduled Outage | Construction | To install new primary insert. | None | None | 12 | 60 | 12 | East | BLKF3
128513 | 2014-03-12 | Scheduled Outage | Maintenance | Transformer X31705 isolated by crew to replace switch and arrestor | None | None | 16 | 61 | 16 | Central | TH11-NIU
128514 | 2014-03-12 | Scheduled Outage | Maintenance | Transformer x31721 at 59 Elm Street isolated for crew to change switch and arrestor | None | None | 11 | 67 | 12 | Central | TH11-NIU
128515 | 2014-03-12 | Scheduled Outage | Maintenance | Transformer x31722 at 65 Elm Street isolated for crew to change switch and arrestor | None | None | 12 | 61 | 12 | Central | TH11-NIU
128516 | 2014-03-12 | Scheduled Outage | Maintenance | Transformer x36642 at 125 Rita Ave. isolated for crew to change switch and arrestor | None | None | 1 | 188 | 3 | South | EPWF1
128517 | 2014-03-12 | Scheduled Outage | Maintenance | Transformer X31710 at 132 Elm St. isolated for crew to replace swithc and arrestor | None | None | 10 | 65 | 11 | Central | TH11-NIU
128518 | 2014-03-12 | Scheduled Outage | Maintenance | Transformer X31718 at 146 Elm St. isolated for crew to change switch and arrestor | None | None | 8 | 67 | 9 | Central | TH11-NIU
128519 | 2014-03-12 | Scheduled Outage | Maintenance | Transformer X31700 at 142 Elm St. isolated for crew to change switch and arrestor | None | None | 13 | 67 | 15 | Central | TH11-NIU
128520 | 2014-03-12 | Scheduled Outage | Maintenance | Transformer X31546 at 83 Spruce St. isolated for crew to change switch and arrestor | None | None | 11 | 43 | 8 | Central | TH11-NIU
128521 | 2014-03-12 | Scheduled Outage | Maintenance | Transformer X31547 at 59 Spruce St. isolated for crew to change switch and arrestor | None | None | 12 | 43 | 9 | Central | TH11-NIU
128522 | 2014-03-13 | Scheduled Outage | Forced Switching | At 9:30 am, switches 1548 were opened by crew to isolate and megger radial cables due to re-occuring single phasing of customer transformer cables checked out good. 2 customers were interrupted for 125 minutes. Kanata MTS (624F1) ID# 128522. | None | None | 2 | 125 | 4 | West | 624F1
128524 | 2014-03-13 | Scheduled Outage | Maintenance | Transformer X31476 at 9 Spruce Street isolated by crew to change switch and arrestor. | None | None | 14 | 59 | 14 | Central | TH11-NIU
128525 | 2014-03-13 | Scheduled Outage | Maintenance | Transformer X30168 at 131 Spruce St. isolated by crew to change switch and arrestor. | None | None | 16 | 79 | 21 | Central | TH11-NIU
128527 | 2014-03-14 | Scheduled Outage | Maintenance | Transformer X40231 at 4 Panandrick View Drive isolated by Sam Baird crew to replace switch and arrestors | None | None | 2 | 90 | 3 | West | MWDF3
128528 | 2014-03-14 | Scheduled Outage | Maintenance | Transformer X40238 at 5 Panandrick View Drive isolated by Sam Baird crew to replace switch and arrestors | None | None | 4 | 90 | 6 | West | MWDF3
128529 | 2014-03-14 | Defective Equipment | Defective Equipment/ Material | Transformer X31760 at 1419 Bellany St. isolated for crew to replace connections at 1423 Bellamy St. | Secondary \ Service | O/H Service | 13 | 85 | 18 | Central | AK04
128531 | 2014-03-15 | Scheduled Outage | Maintenance | At 08:40, PC10a #9515 establish at S21279 to isolate TE505 & to allow crews to transfer plant at pole. 1 customer affected for 440 minutes. Bells corners (47F6) ID #128531 | None | Kiosk (3ph) | 1 | 440 | 7 | South | 47F6
128533 | 2014-03-15 | Defective Equipment | Electrical Failure | Suspected cable fault. | U/G Cable | PILC | 1 | 15 | 0 | Central | TR1FB
128533 | 2014-03-15 | Defective Equipment | Electrical Failure | Suspected cable fault. | U/G Cable | PILC | 3 | 18 | 1 | Central | TR1FB
128533 | 2014-03-15 | Defective Equipment | Electrical Failure | Suspected cable fault. | U/G Cable | PILC | 5 | 32 | 3 | Central | TR1FB
128534 | 2014-03-16 | Scheduled Outage | Maintenance | 13kV transfomer bus at VT396 at 223 Main was isolated to allow metering crew to change PT fuse. 1 customer affected for min. Riverdale (502) ID#128534 | None | Unknown \ Other | 1 | 102 | 2 | Central | 502
128535 | 2014-03-16 | Defective Equipment | Electrical Failure | Cable termination burnt off at S19515 W phase. | U/G Cable Attachement | Termination \ Stress Cone | 119 | 152 | 301 | East | LTM01
128536 | 2014-03-16 | Defective Equipment | Defective Equipment/ Material | Defective secondary cables | U/G Cable Attachement | Termination \ Stress Cone | 17 | 515 | 146 | West | 44F1
128537 | 2014-03-17 | Scheduled Outage | Construction | to transfer plant and transformer to new pole. | None | Pole | 17 | 175 | 50 | East | UZ12
128538 | 2014-03-17 | Defective Equipment | Mechanical Failure | Tomlinson Gravel pit customer equipment problem. | Customer Owned | Customer-Owned | 1 | 431 | 7 | South | FAL02
128540 | 2014-03-18 | Scheduled Outage | Construction | Transformer X26234 at 2511 Junction Ave. isolated for streetlight service transfer | None | None | 1 | 282 | 5 | East | AF06
128543 | 2014-03-18 | Defective Equipment | Electrical Failure | S26061 red phase fuse blew due to cable fault on 77M6 red phase between TE1699 and TP7069. | U/G Cable | Unknown \ Other | 26 | 32 | 14 | East | 77M6
128543 | 2014-03-18 | Defective Equipment | Electrical Failure | S26061 red phase fuse blew due to cable fault on 77M6 red phase between TE1699 and TP7069. | U/G Cable | Unknown \ Other | 63 | 46 | 48 | East | 77M6
128543 | 2014-03-18 | Defective Equipment | Electrical Failure | S26061 red phase fuse blew due to cable fault on 77M6 red phase between TE1699 and TP7069. | U/G Cable | Unknown \ Other | 69 | 69 | 79 | East | 77M6
128543 | 2014-03-18 | Defective Equipment | Electrical Failure | S26061 red phase fuse blew due to cable fault on 77M6 red phase between TE1699 and TP7069. | U/G Cable | Unknown \ Other | 262 | 127 | 555 | East | 77M6
128545 | 2014-03-20 | Defective Equipment | Defective Equipment/ Material | S262W phase blew open due to defective transformer TE 2378 at 81 Dalecroft | U/G Transformer | Padmount (1ph) | 14 | 295 | 69 | South | 87F5
128545 | 2014-03-20 | Defective Equipment | Defective Equipment/ Material | S262W phase blew open due to defective transformer TE 2378 at 81 Dalecroft | U/G Transformer | Padmount (1ph) | 35 | 10 | 6 | South | 87F5
128545 | 2014-03-20 | Defective Equipment | Defective Equipment/ Material | S262W phase blew open due to defective transformer TE 2378 at 81 Dalecroft | U/G Transformer | Padmount (1ph) | 76 | 97 | 123 | South | 87F5
128546 | 2014-03-20 | Scheduled Outage | Vegetation Management | UQ07 from S14555 to EOL isolated to allow crews to trim trees. | None | O/H Conductor | 9 | 209 | 31 | East | UQ07
128547 | 2014-03-20 | Scheduled Outage | Construction | UC01 overhead circuit from TEMP 76 to EOL isolated to allow crews to install new poles. | None | Pole | 796 | 180 | 2388 | Central | UC01
128548 | 2014-03-20 | Scheduled Outage | Forced Switching | TH11 from S10489 to EOL isolated due to pole fire | None | None | 27 | 180 | 81 | Central | TD12
128549 | 2014-03-20 | Scheduled Outage | Construction | To change defective switch. | None | Inline Switch | 135 | 46 | 104 | South | FAL01
128550 | 2014-03-20 | Scheduled Outage | Construction | Replace defective switch. | None | None | 39 | 34 | 22 | South | FAL02
128551 | 2014-03-20 | Scheduled Outage | Construction | Transformer X09390 isolated to allow crews to change cut out and arrestor. | None | None | 1 | 30 | 0 | West | BECKF2
128552 | 2014-03-20 | Scheduled Outage | Construction | X30291 isolated to allow crews to replace the cut out and arrestor | None | Arrester | 10 | 70 | 12 | Central | TH11-NIU
128553 | 2014-03-20 | Scheduled Outage | Construction | X27974 isolated to allow crews to replace the cut out and arrestor. | None | Arrester | 24 | 60 | 24 | Central | TH11-NIU
128554 | 2014-03-20 | Scheduled Outage | Construction | X27972 isolated to allow crews to change the cut out and arrestor. | None | Arrester | 26 | 60 | 26 | Central | TH11-NIU
128555 | 2014-03-20 | Scheduled Outage | Construction | X38797 isolated to allow crews to repair the primary cut out. | None | Fused Cutout | 9 | 50 | 8 | West | JKGF4
128556 | 2014-03-20 | Defective Equipment | Electrical Failure | Red phase cable failure between 2547 & 2548 on Varley Dr. | U/G Cable | XLPE | 15 | 46 | 12 | West | 39F3
128556 | 2014-03-20 | Defective Equipment | Electrical Failure | Red phase cable failure between 2547 & 2548 on Varley Dr. | U/G Cable | XLPE | 51 | 153 | 130 | West | 39F3
128557 | 2014-03-21 | Defective Equipment | Electrical Failure | Failed cable termination on the TFXF4 breaker at Terry Fox MS Caused the BRDF2 breaker to open. TFXF4 cable on potential from BRDF2 at the time of the fault. | Station Equipment | Primary Cable Termination | 477 | 58 | 461 | West | BRDF2
128557 | 2014-03-21 | Defective Equipment | Electrical Failure | Failed cable termination on the TFXF4 breaker at Terry Fox MS Caused the BRDF2 breaker to open. TFXF4 cable on potential from BRDF2 at the time of the fault. | Station Equipment | Primary Cable Termination | 6148 | 76 | 7787 | West | BRDF2
128558 | 2014-03-21 | Scheduled Outage | Maintenance | Transformer #X38833 isolated by crew to repair switch and arrestor | None | None | 12 | 32 | 6 | West | JKGF4
128559 | 2014-03-21 | Scheduled Outage | Maintenance | Transformer #X38799 isolated by crew to repair switch and arrestor (Sam Baird) | None | None | 6 | 27 | 3 | West | JKGF4
128560 | 2014-03-21 | Scheduled Outage | Maintenance | Transformer #X15173 isolated by crew to repair switch and arrestor | None | None | 11 | 11 | 2 | East | 249F2
128561 | 2014-03-21 | Scheduled Outage | Maintenance | Transformer #X31545 isolated by crew to repair switch and arrestor | None | None | 9 | 33 | 5 | Central | TH11-NIU
128562 | 2014-03-21 | Scheduled Outage | Maintenance | Transformer #X30295 isolated by crew to repair switch and arrestor | None | None | 7 | 82 | 10 | Central | TH11-NIU
128563 | 2014-03-21 | Scheduled Outage | Construction | Transformer #X31541 isolated by crew to replace switch | None | None | 12 | 44 | 9 | Central | TH11-NIU
128564 | 2014-03-21 | Scheduled Outage | Maintenance | Transformer #X25700 isolated by crew to repair switch and arrestor | None | None | 15 | 72 | 18 | Central | TH11-NIU
128565 | 2014-03-21 | Scheduled Outage | Maintenance | Complete repairs to duct structure. | None | Padmount (3ph) | 1 | 206 | 3 | South | EPWF4
128567 | 2014-03-22 | Scheduled Outage | Construction | At 8:30 am, switch S14727 at 4889 Bank was isolated to allow crew to replace switches. 1 customer was interrupted for minutes. Leitrim (249F1) ID# 128567. | None | Fused Cutout | 1 | 27 | 0 | East | LTM01
128571 | 2014-03-22 | Foreign Interference | Wildlife (Bird/Animal) | Transformer fuse blown on X39131 at 548 Thessally Cres. Animal contact. | O/H Switchgear | Fused Cutout | 5 | 43 | 4 | East | TB06
128573 | 2014-03-22 | Scheduled Outage | Maintenance | customer maintenance. | None | None | 2 | 361 | 12 | West | 624F2
128574 | 2014-03-23 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer switch at X35798 at 2048 Knightsbridge Rd. due to animal contact. - squirrel | O/H Switchgear | Fused Cutout | 8 | 51 | 7 | Central | TD06
128576 | 2014-03-24 | Scheduled Outage | Construction | Transformer #X26079 isolated by crew to replace switch | None | None | 15 | 30 | 8 | Central | TH11-NIU
128577 | 2014-03-24 | Scheduled Outage | Construction | Transformer #X31475 isolated by crew to replace switch for maintenance | None | None | 12 | 25 | 5 | Central | TH11-NIU
128578 | 2014-03-24 | Scheduled Outage | Construction | To disconnect temporary service at 108 Richmond Rd and connect to TV8863-CB3 supply. Building had been on generator for sometime. | None | None | 2 | 30 | 1 | Central | TH2UL
128579 | 2014-03-24 | Scheduled Outage | Construction | Transformer #X30166 isolated by crew to replace cutout and arrestor | None | None | 10 | 55 | 9 | Central | TH11-NIU
128581 | 2014-03-24 | Scheduled Outage | Construction | Transformer X30167 at 123 Spruce St. Isolated for crew to change switch | None | None | 9 | 45 | 7 | Central | TH11-NIU
128583 | 2014-03-24 | Scheduled Outage | Construction | At 10:09 am, S19569 at 4860 Bank was isolated to allow crew to replace defective switches. 1 customer was interrupted for 33 minutes. Leitrim (249F1) ID# 128583. | None | None | 1 | 40 | 1 | East | LTM01
128584 | 2014-03-24 | Scheduled Outage | Construction | Transformer #X31544 isolated by crew to replace switch for maintenance | None | None | 18 | 78 | 23 | Central | TH11-NIU
128585 | 2014-03-24 | Scheduled Outage | Construction | Transformer X34743 at 323 Besserer St. Isolated for crew to transfer plant | None | None | 10 | 120 | 20 | Central | UN03
128586 | 2014-03-24 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact cause X36646 and S420 red phase to blow. | None | None | 8 | 102 | 14 | South | EPWF5
128587 | 2014-03-24 | Scheduled Outage | Construction | Transformer #X31477 isolated by crew to replace cut out and arrestor for maintenance | None | None | 10 | 75 | 12 | Central | TH11-NIU
128588 | 2014-03-24 | Scheduled Outage | Construction | Transformer X26499 at 8405 Copeland Rd. Isolated so crew could change the switch | None | None | 1 | 24 | 0 | West | BECKF2
128589 | 2014-03-24 | Scheduled Outage | Construction | Transformer #X34791 isolated by crew to replace switch for maintenance | None | None | 1 | 11 | 0 | West | BECKF2
128590 | 2014-03-24 | Scheduled Outage | Construction | Transformer X31478 at 29 Elm Street isolated for crew to change switch | None | None | 19 | 65 | 21 | Central | TH11-NIU
128591 | 2014-03-24 | Scheduled Outage | Maintenance | Transformer X06054 at 25 Bren-Maur Rd. isolated for crew to change insulator | None | None | 8 | 127 | 17 | South | 140F4
128592 | 2014-03-24 | Defective Equipment | Defective Equipment/ Material | Transformer X36514 at 18 David Drive isolated so crew could replace the hot line clamp. | O/H Conductor | Hot-Line Clamp | 9 | 28 | 4 | South | EPWF4
128593 | 2014-03-24 | Defective Equipment | Mechanical Failure | Broken insulator at 35 Orville cause the A9M3 circuit to auto-reclose and lock out. | Pole Attachement | Insulator | 355 | 297 | 1757 | West | RHNF3
128593 | 2014-03-24 | Defective Equipment | Mechanical Failure | Broken insulator at 35 Orville cause the A9M3 circuit to auto-reclose and lock out. | Pole Attachement | Insulator | 386 | 3 | 19 | West | A9M3
128593 | 2014-03-24 | Defective Equipment | Mechanical Failure | Broken insulator at 35 Orville cause the A9M3 circuit to auto-reclose and lock out. | Pole Attachement | Insulator | 2105 | 177 | 6210 | West | A9M3
128593 | 2014-03-24 | Defective Equipment | Mechanical Failure | Broken insulator at 35 Orville cause the A9M3 circuit to auto-reclose and lock out. | Pole Attachement | Insulator | 6723 | 67 | 7507 | West | A9M3
128594 | 2014-03-24 | Scheduled Outage | Construction | Transformer X34743 at 323 Besserer St. isolated to allow contractor to transfer plant. | None | None | 3 | 120 | 6 | Central | UN03
128595 | 2014-03-25 | Scheduled Outage | Construction | Replace transformer. At 06:30 transformer X30124 at 29 Clemo was isolated to allow crew to replace transformer and reconfigure plant. 1 customer was affected for 70 minutes. Bronson (SB03) ID#128595 | None | None | 1 | 70 | 1 | Central | SB03
128596 | 2014-03-25 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X37778 TO REPLACE SWITCH | None | None | 1 | 10 | 0 | East | 249F2
128597 | 2014-03-25 | Scheduled Outage | Construction | Transformer #X07390 isolated by crew to replace switch for maintenance | None | None | 1 | 20 | 0 | West | 624F6
128598 | 2014-03-25 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X07389 TO REPLACE SWITCH | None | None | 1 | 25 | 0 | West | 624F6
128599 | 2014-03-25 | Scheduled Outage | Construction | Transformer #X07397 isolated by crew to replace switch for maintenance | None | None | 2 | 35 | 1 | West | 624F6
128600 | 2014-03-25 | Scheduled Outage | Construction | Transformer #X07399 isolated by crew to replace switch for maintenance | None | None | 1 | 25 | 0 | West | 624F6
128601 | 2014-03-25 | Scheduled Outage | Construction | ISOLATED TRANSFOPMER X25699 TO REPLACE SWITCH AND ARRESTER | None | None | 10 | 40 | 7 | Central | TH11-NIU
128602 | 2014-03-25 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X25655 TO REPLACE SWITCH AND ARRESTER | None | None | 22 | 60 | 22 | Central | TH11-NIU
128603 | 2014-03-25 | Scheduled Outage | Construction | ISOLATED TRANSFORMER KT0385 TO CONNECT NEW PEDESTAL | None | None | 6 | 60 | 6 | Central | 303
128604 | 2014-03-26 | Scheduled Outage | Construction | to allow crews to replace defective switches | None | Fused Cutout | 1 | 42 | 1 | East | LTM01
128605 | 2014-03-26 | Scheduled Outage | Construction | To allow crews to replace defective switches | None | Fused Cutout | 1 | 33 | 1 | East | LTM01
128606 | 2014-03-26 | Scheduled Outage | Construction | part of UW07 overhead was opened to transfer transformers to new primary overhead as part of the voltage conversion project, affecting 71 customers for 280 minutes, Woodroffe sub, UW07, ID # 128606 | None | None | 71 | 280 | 331 | Central | UW07
128607 | 2014-03-26 | Scheduled Outage | Maintenance | Transformer #X31543 isolated by crew to replace cutout and maintenance | None | None | 7 | 35 | 4 | Central | TH11-NIU
128608 | 2014-03-26 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMERS X30633 AND REMOVED FROM SERVICE AND X30646 HAS BEEN REPLACED FROM A 50KV TO A 75KV AND CUSTOMERS FROM X30633 TRANSFERED TO X30646 | None | None | 22 | 255 | 94 | Central | UN03
128609 | 2014-03-26 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X27535 FOR TREE CONTRACTOR TO REMOVE A TREE | None | None | 8 | 250 | 33 | East | TB06
128610 | 2014-03-27 | Scheduled Outage | Construction | To install new riser and pole, replace old cable | None | None | 1 | 360 | 6 | Central | UN03
128611 | 2014-03-27 | Scheduled Outage | Construction | To replace defective switches at G625. | None | None | 1 | 57 | 1 | East | LTM01
128612 | 2014-03-27 | Scheduled Outage | Construction | To reconfigure new o/h conductor. | None | None | 20 | 198 | 66 | West | BECKF2
128613 | 2014-03-27 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change porcelain switches. | None | Fused Cutout | 25 | 148 | 62 | Central | TH11-NIU
128614 | 2014-03-27 | Scheduled Outage | Construction | Transformer #X31547 isolated by crew to replace cut out for maintenance | None | None | 12 | 30 | 6 | Central | TH11-NIU
128615 | 2014-03-27 | Scheduled Outage | Construction | Transformer #X31482 isolated by crew to replace switch for maintenance | None | None | 13 | 35 | 8 | Central | TH11-NIU
128616 | 2014-03-27 | Scheduled Outage | Construction | Transformer #X25698 isolated by crew to replace cut out for maintenance | None | None | 14 | 35 | 8 | Central | TH11-NIU
128617 | 2014-03-27 | Scheduled Outage | Maintenance | Transformer #X25659 isolated by crew to repair switch for maintenance | None | None | 3 | 15 | 1 | Central | TH11-NIU
128618 | 2014-03-27 | Scheduled Outage | Construction | Transformer #X31711 isolated by crew to replace cutouts and arrestor | None | None | 5 | 69 | 6 | Central | TH11-NIU
128619 | 2014-03-27 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31497 TO REPLACE SWITCH AND ARRESTER | None | None | 6 | 45 | 4 | Central | TH11-NIU
128620 | 2014-03-27 | Defective Equipment | Mechanical Failure | Downed phase and neutral conductors caused the 47F6 to auto-reclose and lock out. | O/H Conductor | O/H Conductor | 25 | 38 | 16 | South | 47F6
128620 | 2014-03-27 | Defective Equipment | Mechanical Failure | Downed phase and neutral conductors caused the 47F6 to auto-reclose and lock out. | O/H Conductor | O/H Conductor | 626 | 2 | 21 | South | 47F6
128620 | 2014-03-27 | Defective Equipment | Mechanical Failure | Downed phase and neutral conductors caused the 47F6 to auto-reclose and lock out. | O/H Conductor | O/H Conductor | 759 | 59 | 746 | South | 47F6
128620 | 2014-03-28 | Defective Equipment | Mechanical Failure | Downed phase and neutral conductors caused the 47F6 to auto-reclose and lock out. | O/H Conductor | O/H Conductor | 11 | 158 | 29 | South | 47F6
128620 | 2014-03-28 | Defective Equipment | Mechanical Failure | Downed phase and neutral conductors caused the 47F6 to auto-reclose and lock out. | O/H Conductor | O/H Conductor | 25 | 38 | 16 | South | 47F6
128620 | 2014-03-28 | Defective Equipment | Mechanical Failure | Downed phase and neutral conductors caused the 47F6 to auto-reclose and lock out. | O/H Conductor | O/H Conductor | 759 | 60 | 759 | South | 47F6
128621 | 2014-03-28 | Scheduled Outage | Construction | replacing the switchs G253 and G406 | None | None | 16 | 28 | 7 | East | LTM01
128622 | 2014-03-28 | Scheduled Outage | Construction | Transformer #X38777 isolated by crew to replace switch for maintenance | None | None | 6 | 10 | 1 | West | JKGF4
128623 | 2014-03-28 | Scheduled Outage | Maintenance | to perform repairs to riser | None | None | 1 | 31 | 1 | East | LTM01
128624 | 2014-03-28 | Defective Equipment | Electrical Failure | insulator flashed over | Pole Attachement | Insulator | 93 | 111 | 172 | East | 7F2
128625 | 2014-03-28 | Defective Equipment | Mechanical Failure | broken primary fused switch S12386 caused the outage to X28204 | O/H Switchgear | Fused Cutout | 4 | 149 | 10 | East | AF02
128628 | 2014-03-29 | Scheduled Outage | Construction | To replace defective 27KV switch S13667 feeding transformer # TP6599. | None | Unknown \ Other | 1 | 34 | 1 | East | LTM01
128629 | 2014-03-29 | Scheduled Outage | Construction | To replace defective switch S14939 @ 4070 Belgreen. | None | Fused Cutout | 6 | 21 | 2 | East | LTM01
128630 | 2014-03-29 | Foreign Interference | Vehicle | Make repairs after MVA | Pole | Pole | 4 | 270 | 18 | East | LTM01
128631 | 2014-03-29 | Scheduled Outage | Construction | Isolation of G661. To allow crews to replace defective 28 Kv switches, Planned power outage to TE2175 effecting 23 customers. | None | Fused Cutout | 23 | 12 | 5 | East | LTM01
128632 | 2014-03-29 | Scheduled Outage | Construction | To allow crews to replace defective 28KV switch S24883. Planned power outage to TP7493 affecting 2 customers at this location. | None | Fused Cutout | 2 | 26 | 1 | East | LTM01
128633 | 2014-03-30 | Defective Equipment | Mechanical Failure | Broken standoff pin and vegitation caused the fuse to open on X32510 | O/H Switchgear | Fused Cutout | 7 | 124 | 14 | Central | TD01
128634 | 2014-03-30 | Defective Equipment | Electrical Failure | Replace defective transformer cut out and arrestor | O/H Switchgear | Fused Cutout | 1 | 40 | 1 | West | BECKF2
128636 | 2014-03-30 | Adverse Weather | Ice/Icing | Ice falling on the service caused the outage to X23414, Beechwood, UB04, ID # 128636 | Customer Owned | Customer-Owned | 6 | 15 | 2 | East | UB04
128637 | 2014-03-31 | Scheduled Outage | Construction | AF02 overhead from S12386 to Eol isolated to allow crews to replace defective primary switch. | None | Fused Cutout | 4 | 16 | 1 | East | AF02
128638 | 2014-03-31 | Scheduled Outage | Maintenance | transformer maintenance | None | O/H Transformer (1ph) | 12 | 210 | 42 | West | 43F3
128639 | 2014-03-31 | Scheduled Outage | Construction | Replace transformer switch | None | Fused Cutout | 8 | 15 | 2 | West | JKGF5
128640 | 2014-03-31 | Scheduled Outage | Construction | To allow to connect perminate secondary service. | None | None | 1 | 84 | 1 | West | BRDF3
128641 | 2014-03-31 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X25697 TO REPLACE SWITCH AND ARRESTER | None | None | 17 | 30 | 8 | Central | TH11-NIU
128642 | 2014-03-31 | Defective Equipment | Mechanical Failure | Repair transformer primary lead | O/H Conductor | Hot-Line Clamp | 4 | 15 | 1 | South | 200F1
128643 | 2014-03-31 | Scheduled Outage | Construction | 2 transformers, #X30253 and X30255 isolated by crew for a pole change | None | None | 16 | 150 | 40 | Central | UL06
128644 | 2014-03-31 | Adverse Weather | Ice/Icing | A large piece of ice fell and hit KT513, causing the transformer fuse to fall out of the switch inside KT513. | U/G Switchgear | Live-Front | 26 | 89 | 39 | East | TO2UB
128645 | 2014-04-01 | Defective Equipment | Mechanical Failure | 4F3 Breaker tripped, 24/7 patrol found NIU 44KV O/H fallen into 8KV O/H on Bearbrook JOB #346 created to remove NIU O/H | O/H Conductor | O/H Conductor | 1065 | 23 | 408 | East | BLKF3
128646 | 2014-04-01 | Scheduled Outage | Maintenance | ISOLATED AND REPLACED SWITCH S27840 | None | None | 1 | 30 | 0 | West | BECKF2
128647 | 2014-04-01 | Scheduled Outage | Maintenance | ISOLATED AND REPLACED SWITCH S16369 | None | None | 1 | 22 | 0 | West | BECKF2
128648 | 2014-04-01 | Scheduled Outage | Maintenance | ISOLATED AND REPLACED SWITCH S24447 | None | None | 2 | 15 | 0 | West | BECKF2
128649 | 2014-04-01 | Scheduled Outage | Construction | Transformer X30254 at 654 Churchill and X28400 at 694 Churchill Ave. isolated for pole change | None | None | 23 | 120 | 46 | Central | UC02
128650 | 2014-04-01 | Scheduled Outage | Construction | 2 Transformers (X26011 and X30268) isolated by crew due to pole change | None | None | 44 | 120 | 88 | Central | UC01
128651 | 2014-04-01 | Defective Equipment | Mechanical Failure | 4F3 patrol found NIU 44KV section had fallen into the 4F3 O/H on Bearbrook. 4F3 section between G343, G160RB, G162R & G134 isolated to allow cews to remove and repair NIU 44KV O/H section. 61 customers affected for 102 minutes. Blackburn (4F3) ID #128 | O/H Conductor | O/H Conductor | 61 | 102 | 104 | East | BLKF3
128653 | 2014-04-02 | Scheduled Outage | Maintenance | replace defective switches. | None | Fused Cutout | 1 | 53 | 1 | East | LTM01
128654 | 2014-04-02 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X27388 TO REPLACE SECONDARY SERVICE | None | None | 8 | 45 | 6 | East | AN04
128655 | 2014-04-02 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X07118 TO REPLACE SWITCH | None | None | 1 | 20 | 0 | West | MWDF3
128656 | 2014-04-02 | Scheduled Outage | Maintenance | Transformer X07130 at 1620 Marchurst Rd. isolated by crew to replace defective switch | None | None | 4 | 25 | 2 | West | MWDF3
128657 | 2014-04-02 | Scheduled Outage | Maintenance | At 16:24, 27KV switch S24677 located at 3815 Sixth street was isolated to allow crews to replace defective switch. 3 customers affected for 32 minutes. Leitrim (249F1) ID #128657 | None | Fused Cutout | 3 | 32 | 2 | East | LTM01
128658 | 2014-04-02 | Scheduled Outage | Maintenance | At 17:00, 27KV switch G548 located at 4561 Bank was isolated to allow crews to replaced defective switch. 1 customer affected for 70 minutes. Lietrim (249F1) ID #128658 | None | Fused Cutout | 1 | 70 | 1 | East | LTM01
128659 | 2014-04-02 | Defective Equipment | Defective Equipment/ Material | Transformer #X26252 opened up due to a triplex service that fell down and mast was down also with hit pulled off house. | Secondary \ Service | O/H Service | 6 | 72 | 7 | Central | UN07
128660 | 2014-04-02 | Scheduled Outage | Construction | 5 transformers isolated by crew to transfer plant to new poles (X35215, X35214, X33833, X32458, X33842) | None | None | 34 | 190 | 108 | Central | UW07
128661 | 2014-04-02 | Scheduled Outage | Construction | Transformer #X24675 isolated by crew to transfer to new plant | None | None | 7 | 237 | 28 | East | SO10
128663 | 2014-04-03 | Scheduled Outage | Construction | At 8:30 am, TP6967 at 682 Carling was isolated to allow crew to transfer plant. 34 customers were interrupted for 145 minutes. Clyde (UC01) ID# 128663. | None | None | 34 | 145 | 82 | Central | UC01
128664 | 2014-04-03 | Scheduled Outage | Maintenance | At 9:23 am, transformer TP2515 at 115 Palomino was isolated to allow crew to replace inserts. 8 customers were interrupted for 75 minutes. Bridlewood (BRDF1) ID#128664. | None | None | 8 | 75 | 10 | West | BRDF1
128666 | 2014-04-03 | Scheduled Outage | Maintenance | ISOLATED 3 PHASE TRANSFORMER BANK X30286 TO REPLACE SWITCHERS AND ARRESTERS | None | None | 2 | 100 | 3 | Central | TH11-NIU
128667 | 2014-04-03 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X25656 TO REPLACE SWITCH AND ARRESTER | None | None | 16 | 41 | 11 | Central | TH11-NIU
128668 | 2014-04-03 | Scheduled Outage | Maintenance | Replace transformer cutout | None | Fused Cutout | 4 | 60 | 4 | South | 140F4
128669 | 2014-04-03 | Scheduled Outage | Maintenance | Transformer X27846 at 143 Armstrong St. isolated for crew to replace switch | None | None | 11 | 20 | 4 | Central | TH11-NIU
128670 | 2014-04-03 | Defective Equipment | Mechanical Failure | transformer X26252 at 229 Augusta opened to allow crew to replace a service affecting 6 customers for xx minutes, Henderson, UN07, ID # 128670 | Secondary \ Service | O/H Service | 6 | 46 | 5 | Central | UN07
128671 | 2014-04-04 | Scheduled Outage | Construction | At 8:05 am, transformer TP9980 at 19 Frank Nighbor Place was isolated to allow crew to install new secondary service. 2 customers were interrupted for 371 minutes. Kanata MTS, 624F1, ID # 128671. | None | None | 2 | 371 | 12 | West | 624F1
128672 | 2014-04-04 | Scheduled Outage | Maintenance | At 9:30 am, transformer KT512 at 47 Merton was isolated to allow crew to replace switches. 6 customers were interupted for 42 minutes. Hinchey, TH11, ID # 128672 | None | None | 6 | 42 | 4 | Central | TH11-NIU
128674 | 2014-04-04 | Scheduled Outage | Construction | TP2318 at 154 Spruce was isolated to allow crew to replace porcelin insulators on dip switch S28807, affecting 33 customers for 42 minutes, Hinchey TH11, ID # 128674 | None | None | 33 | 42 | 23 | Central | TH11-NIU
128675 | 2014-04-04 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X27829 TO REPLACE SWITCH AND ARRESTER | None | None | 17 | 20 | 6 | Central | TH11-NIU
128676 | 2014-04-04 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X38092 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 35 | 1 | West | BECKF2
128677 | 2014-04-04 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32309 TO TRANSFER HYDRO PLANT | None | None | 5 | 45 | 4 | Central | UC03
128678 | 2014-04-04 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X11009 TO REPLACE SWITCH AND ARRESTER | None | None | 2 | 30 | 1 | West | BECKF2
128679 | 2014-04-04 | Unknown/Other | Unknown | Closed switch S24662 at 2268 Iris St.. No cause found. Outage was on TW17 but Interruptions Database would not accept this circuit | None | None | 27 | 81 | 36 | Central | TW17
128680 | 2014-04-04 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer x45377 at 1153 Adirondack Dr. outage caused by squirrell. | None | None | 15 | 58 | 14 | Central | TW17
128683 | 2014-04-05 | Scheduled Outage | Maintenance | To allow for voltage conversion/upgrade | None | None | 2 | 145 | 5 | Central | SR03
128684 | 2014-04-06 | Scheduled Outage | Forced Switching | Transformer TE256 at 193 Woodridge was isolated to allow contracotr to excavate broken water main. | None | None | 19 | 435 | 138 | South | 49F1
128686 | 2014-04-06 | Scheduled Outage | Maintenance | replace porcelaine switches | None | None | 15 | 30 | 8 | Central | TH11-NIU
128687 | 2014-04-06 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change insulators & switches. | None | Fused Cutout | 1 | 65 | 1 | Central | TH11-NIU
128688 | 2014-04-06 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change porcelain switches and insulators | O/H Switchgear | Fused Cutout | 3 | 25 | 1 | Central | TH11-NIU
128689 | 2014-04-06 | Defective Equipment | Mechanical Failure | TE260 defective bushing, on call crew called into replace bushing. | U/G Transformer | Padmount (1ph) | 31 | 250 | 129 | South | 49F1
128690 | 2014-04-06 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change porcelain insulators & switches | None | Fused Cutout | 2 | 50 | 2 | Central | TH11-NIU
128691 | 2014-04-06 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One | None | None | 644 | 7 | 75 | West | BECKF2
128692 | 2014-04-06 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to replace porcelain insulators & switches | O/H Switchgear | Fused Cutout | 1 | 56 | 1 | Central | TH11-NIU
128693 | 2014-04-06 | Scheduled Outage | Maintenance | to allow Hydro Ottawa crews to change porcelain insulators & switches | O/H Switchgear | Fused Cutout | 2 | 24 | 1 | Central | TH11-NIU
128694 | 2014-04-07 | Scheduled Outage | Construction | Transformer PT140 at 106 Merton was isolated to allow crew to replace porcelain switch on pole feeding PT140. Hinchey (TH11) | None | None | 6 | 99 | 10 | Central | TH11-NIU
128695 | 2014-04-07 | Human Element | Switching Error | Switching error | None | None | 475 | 14 | 111 | Central | AM00
128696 | 2014-04-07 | Scheduled Outage | Construction | X35511 at 581 Golden was isolated to allow crew to do load transfer | None | None | 6 | 50 | 5 | Central | UC03
128697 | 2014-04-07 | Scheduled Outage | Maintenance | changing cables to xlp | None | None | 48 | 356 | 285 | Central | UN03
128698 | 2014-04-07 | Scheduled Outage | Construction | 3 transformers, X34391, X32312 and X34394 isolated by crew to transfer load | None | None | 29 | 60 | 29 | Central | UC03
128700 | 2014-04-07 | Scheduled Outage | Construction | Transformer #X32360 isolated by crew for circuit balancing | None | None | 8 | 55 | 7 | Central | UC03
128701 | 2014-04-07 | Scheduled Outage | Vegetation Management | Transformer #X35134 isolated by crew to reconnect a service that was dropped for Forestry Dept | None | None | 10 | 70 | 12 | Central | UW02
128702 | 2014-04-07 | Scheduled Outage | Construction | Transformer #X32750 and X32751 isolated by crew to transfer plant | None | None | 14 | 255 | 60 | Central | UW07
128703 | 2014-04-08 | Defective Equipment | Mechanical Failure | Single span of 1 phase primary down to X32312 | O/H Conductor | O/H Conductor | 10 | 159 | 26 | Central | UC03
128704 | 2014-04-08 | Scheduled Outage | Maintenance | Vault VE26 & VE27 @ 2755 Innes Rd was isolated to allow the contractor to clean the vault and torque the connections and service the econdaries. 2 customers affected | None | Transformer | 2 | 237 | 8 | East | BLKF1
128705 | 2014-04-08 | Defective Equipment | Mechanical Failure | Fuse cutout (no switch number) at Mariposa and Sir Guy Carleton feeding a white phase runoff on Sir Guy Carleton was found to be broken. Crew replaced cutout. | O/H Switchgear | Fused Cutout | 9 | 118 | 18 | Central | TK2AC
128706 | 2014-04-08 | Foreign Interference | Foreign Objects | Balloons in the overhead caused the TD14 to auto-reclose and lock out and caused the three phase conductors on bond to disintegrate and fall to the ground. | O/H Conductor | O/H Conductor | 14 | 389 | 91 | Central | TD14
128706 | 2014-04-08 | Foreign Interference | Foreign Objects | Balloons in the overhead caused the TD14 to auto-reclose and lock out and caused the three phase conductors on bond to disintegrate and fall to the ground. | O/H Conductor | O/H Conductor | 1522 | 45 | 1142 | Central | TD14
128707 | 2014-04-09 | Scheduled Outage | Maintenance | Transformer TP7285 @ 3559 Greenbank was isolated by the crew to replace exiting transformer to a 1500Kva, 2 customers were affected,. | None | Unknown \ Other | 2 | 436 | 15 | South | FAL04
128709 | 2014-04-09 | Foreign Interference | Customer-Cut Trees | Private tree contractor cut limb that fell on primary overhead causing S190 fuse to blow. | O/H Conductor | Unknown \ Other | 53 | 121 | 107 | East | 1804
128710 | 2014-04-09 | Scheduled Outage | Maintenance | Transformer TE615 @ 21 Nancy Ave was isolated by the crew to make secondary repairs. | None | Unknown \ Other | 7 | 183 | 21 | South | 84F3
128711 | 2014-04-09 | Defective Equipment | Defective Equipment/ Material | Transformer X25692 at 52 Garland St. isolated to replace defective switch. | O/H Switchgear | Fused Cutout | 16 | 77 | 21 | Central | TH11-NIU
128712 | 2014-04-09 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMER X32751 AND X32752 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 9 | 195 | 29 | Central | UW07
128715 | 2014-04-10 | Defective Equipment | Mechanical Failure | broken pole top in. | Pole Attachement | Insulator | 10 | 46 | 8 | West | 624F1
128716 | 2014-04-10 | Adverse Weather | Extreme Wind | Not yet known. | None | None | 644 | 99 | 1063 | West | BECKF2
128717 | 2014-04-10 | Adverse Weather | Extreme Wind | High winds caused tree branches to contact the UC00 on Tweedsmuir Ave. UC00 is carrying the SM15 circuit currently. All 458 SM15 customers were affected. | None | None | 51 | 8 | 7 | Central | UC07
128717 | 2014-04-10 | Adverse Weather | Extreme Wind | High winds caused tree branches to contact the UC00 on Tweedsmuir Ave. UC00 is carrying the SM15 circuit currently. All 458 SM15 customers were affected. | None | None | 142 | 8 | 19 | Central | UC06
128717 | 2014-04-10 | Adverse Weather | Extreme Wind | High winds caused tree branches to contact the UC00 on Tweedsmuir Ave. UC00 is carrying the SM15 circuit currently. All 458 SM15 customers were affected. | None | None | 299 | 8 | 40 | Central | UC05
128717 | 2014-04-10 | Adverse Weather | Extreme Wind | High winds caused tree branches to contact the UC00 on Tweedsmuir Ave. UC00 is carrying the SM15 circuit currently. All 458 SM15 customers were affected. | None | None | 458 | 95 | 725 | Central | SM15
128718 | 2014-04-10 | Human Element | Incorrect Records/ labelling | Pinning error on System ST16 map. | None | None | 1 | 43 | 1 | East | 5306
128718 | 2014-04-10 | Human Element | Incorrect Records/ labelling | Pinning error on System ST16 map. | None | None | 98 | 1 | 2 | East | 5306
128719 | 2014-04-11 | Defective Equipment | Electrical Failure | DEFECTIVE TRANSFORMER X12985 | O/H Transformer | O/H Transformer (1ph) | 8 | 498 | 66 | East | 7F2
128720 | 2014-04-11 | Unknown/Other | Unknown | The VT901 R1-F tripped open, crew tested cable and transformer and did not find anything wrong. R1-F was refused and all load was restore | U/G Switchgear | Unknown \ Other | 2 | 380 | 13 | Central | 301
128721 | 2014-04-11 | Defective Equipment | Electrical Failure | At 08:06 customer reported outage fed from K621. Crews found defective U/G cable. 20 customers affected for 139 minutes. Langs (AP06) ID# 128721 | U/G Cable | XLPE | 20 | 139 | 46 | East | AP06
128722 | 2014-04-11 | Scheduled Outage | Maintenance | Transformer X32967 at 20 Lucas Lane isolated for crew to change defective cutout | None | None | 1 | 10 | 0 | West | BECKF2
128723 | 2014-04-11 | Scheduled Outage | Maintenance | Transformer X32968 at 20 Lucas Lane isolated for crew to change defective cutout | None | None | 1 | 30 | 0 | West | BECKF2
128724 | 2014-04-11 | Scheduled Outage | Maintenance | Transformer X38789 at 16 Ember Glow Crt isolated so crew could change defective cutout | None | None | 8 | 24 | 3 | West | JKGF4
128725 | 2014-04-11 | Scheduled Outage | Forced Switching | Transformer X35455 at 2176 Benjamin was isolated to allow crew to make repairs to defective secondary connections. 11 customers were affected for 48 minutes. Woodroffe TW22. ID# 128725 | None | O/H Service | 11 | 48 | 9 | Central | TW22
128726 | 2014-04-11 | Adverse Environment | Flood | customer having flooding problems, isolated to investigate and make repairs. | None | None | 1 | 64 | 1 | Central | 5407
128727 | 2014-04-12 | Scheduled Outage | Maintenance | SC7505 at 1810 St Laurent was isolated to allow crew to replace the switchgear affecting 2 customers for xx minutes, Russell TB, TB3LE, ID # 128 | None | Gas-Insulated Dead Front | 2 | 256 | 9 | East | TB3LE
128728 | 2014-04-13 | Scheduled Outage | Construction | TV9640CHZ at Bayshore Mall was isolated to allow the construction crews access to vault to install temporary support posts | None | None | 1 | 184 | 3 | South | 49F3
128729 | 2014-04-13 | Scheduled Outage | Maintenance | ISOLATED 3 PHASE TRANSFORMER BANK X27948 TO REPLACE SWITCHERS AND ARRESTERS | None | None | 4 | 115 | 8 | Central | TH11-NIU
128731 | 2014-04-13 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X18246 (RACCOON ON THE TRANSFORMER) | None | None | 2 | 69 | 2 | East | LTM01
128732 | 2014-04-13 | Lightning | Lightning | 180F6 circuit tripped open during lightning storm. | None | None | 67 | 7 | 8 | South | 180F6
128733 | 2014-04-14 | Scheduled Outage | Construction | At 08:29 4kv transformers X30265 and X26013, on Robin Lane, were isolated to allow contractor to replace poles affecting 38 customers for 181 minutes, Clyde, UC01, ID # 128733 | None | None | 38 | 181 | 115 | Central | UC01
128735 | 2014-04-14 | Scheduled Outage | Maintenance | To replace defective cut-out | None | Fused Cutout | 1 | 30 | 0 | West | MWDF2
128737 | 2014-04-14 | Defective Equipment | Defective Equipment/ Material | lead fell out of pothead to VT597 at S18798 | U/G Cable Attachement | Pothead | 67 | 38 | 42 | Central | TD06
128737 | 2014-04-14 | Defective Equipment | Defective Equipment/ Material | lead fell out of pothead to VT597 at S18798 | U/G Cable Attachement | Pothead | 1414 | 1 | -24 | Central | TD06
128738 | 2014-04-14 | Defective Equipment | Electrical Failure | BRDF5 section between S12675 and S16789 was forced to be isolated due to pole fire at pole X06493 at rear of 136 Glamorgan | Pole | Insulation Failure (Pole Fire) | 63 | 185 | 194 | West | BRDF5
128739 | 2014-04-15 | Defective Equipment | Mechanical Failure | replaced drefective switch and lead to o/h 13kv transformer X27195. | O/H Switchgear | Fused Cutout | 7 | 122 | 14 | East | TB06
128740 | 2014-04-15 | Scheduled Outage | Maintenance | Transformer #X27195 isolated by crew to reconnect service | None | None | 7 | 23 | 3 | East | TB06
128742 | 2014-04-15 | Scheduled Outage | Maintenance | At 19:45, 27KV transformer TE932 located at 1103 Burgundy was isolated due to leaking oil & allow crews to replace it. 10 customers affected for 210 minutes. Billberry creek (77M6). ID #128742 | None | Padmount (1ph) | 10 | 210 | 35 | East | 77M6
128743 | 2014-04-16 | Scheduled Outage | Maintenance | Transformer #X38382 isolated by crew to replace switch for maintenance | None | None | 3 | 20 | 1 | West | BECKF2
128744 | 2014-04-16 | Scheduled Outage | Maintenance | Transformer #X32965 isolated by crew to replace switch for maintenance | None | None | 6 | 25 | 2 | West | BECKF2
128745 | 2014-04-16 | Defective Equipment | Mechanical Failure | Replace defective trans sw | O/H Switchgear | Fused Cutout | 1 | 22 | 0 | West | BECKF2
128747 | 2014-04-16 | Scheduled Outage | Construction | allow crew to relocate O/H to new poles | None | None | 10 | 180 | 30 | Central | UW07
128748 | 2014-04-16 | Defective Equipment | Mechanical Failure | Replace defective primary Switch | O/H Switchgear | Fused Cutout | 1 | 30 | 0 | West | MWDF3
128749 | 2014-04-16 | Scheduled Outage | Maintenance | Transformer #X07086 isolated by crew to replace switch for maintenance | None | None | 1 | 8 | 0 | West | MWDF3
128750 | 2014-04-16 | Scheduled Outage | Construction | Relocate primary conductors to new poles. | None | None | 20 | 148 | 49 | Central | UW07
128751 | 2014-04-17 | Scheduled Outage | Maintenance | 06:05 13kv transfomer TP2335 was isolated to allow crew to replace porcelain insulators on S29482 the dip to TP2335 affecting 1 customer for minutes, Hinchey, TH11, ID # 128 | None | None | 1 | 73 | 1 | Central | TH11-NIU
128753 | 2014-04-17 | Scheduled Outage | Maintenance | PC10A#3957 used to open S12137 (Bleeks Rd at Caddy CRT) to isolate overhead for part of re-insulating of poles at Munster DS | None | None | 31 | 253 | 131 | West | 43F2
128754 | 2014-04-17 | Scheduled Outage | Maintenance | Transformer #X23527 isolated by crew to replace live line clamp, switch and arrestor | None | None | 8 | 20 | 3 | East | AA04
128755 | 2014-04-17 | Defective Equipment | Mechanical Failure | TE2468 was tracking crew requested the circuit dumped before inspection and corrective action taken to secure a loose fuse | U/G Transformer | Padmount (1ph) | 1170 | 5 | 98 | East | BLKF8
128759 | 2014-04-19 | Defective Equipment | Defective Equipment/ Material | 4F5 White phase circuit from Weir Rd. At Anderson to EOL isolated to broken pole from a pole fire. | Pole | Insulation Failure (Pole Fire) | 1 | 48 | 1 | East | BLKF5
128759 | 2014-04-19 | Defective Equipment | Defective Equipment/ Material | 4F5 White phase circuit from Weir Rd. At Anderson to EOL isolated to broken pole from a pole fire. | Pole | Insulation Failure (Pole Fire) | 4 | 349 | 23 | East | BLKF5
128760 | 2014-04-20 | Defective Equipment | Mechanical Failure | The Walkleu UZ12 CB triped opened. Caused by a downed red phase conductor at X27411. | O/H Conductor | Hot-Line Clamp | 18 | 115 | 34 | East | UZ12
128760 | 2014-04-20 | Defective Equipment | Mechanical Failure | The Walkleu UZ12 CB triped opened. Caused by a downed red phase conductor at X27411. | O/H Conductor | Hot-Line Clamp | 276 | 6 | 28 | East | UZ12
128760 | 2014-04-20 | Defective Equipment | Mechanical Failure | The Walkleu UZ12 CB triped opened. Caused by a downed red phase conductor at X27411. | O/H Conductor | Hot-Line Clamp | 276 | 19 | 87 | East | UZ12
128761 | 2014-04-20 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact | None | None | 401 | 91 | 608 | West | 39F3
128761 | 2014-04-20 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact | None | None | 641 | 80 | 855 | West | 39F2
128762 | 2014-04-21 | Foreign Interference | Wildlife (Bird/Animal) | animal contact opened fuse feeding two overhead transformers. | None | None | 14 | 115 | 27 | East | LTM01
128763 | 2014-04-21 | Scheduled Outage | Construction | At 08:35 am, UW13 O/H section from S17686 to EOL including V752 and K1013 on Regency was isolated to allow crew to decomission V752 and energize new TP7669 and transfer plant to new pole. 31 customers were affected for 440 minutes. Woodroffe (UW13). ID#12 | None | None | 31 | 440 | 227 | Central | UW13
128764 | 2014-04-21 | Scheduled Outage | Maintenance | VT866 at 77 Metcalfe was isoalted to allow contractor to perfrom customer vault maintenance. 1 customer was affected for 196 minutes . Slater (615). ID# 128764 | None | None | 1 | 196 | 3 | Central | 615
128765 | 2014-04-21 | Defective Equipment | Electrical Failure | DEFECTIVE SWITCH ON TRANSFORMER X15327 | O/H Switchgear | Fused Cutout | 5 | 40 | 3 | East | LTM01
128766 | 2014-04-22 | Scheduled Outage | Construction | 3 transformers (#X31704, X31703 and X31717) isolated by crew for a pole change | None | None | 46 | 280 | 215 | Central | UX04
128767 | 2014-04-22 | Defective Equipment | Mechanical Failure | To allow Hydro Ottawa crews to change defective dead end insulators. | Pole Attachement | Insulator | 3 | 105 | 5 | East | 249F2
128768 | 2014-04-22 | Scheduled Outage | Construction | Transfer Plant to new poles | None | None | 10 | 210 | 35 | Central | UW05
128769 | 2014-04-23 | Scheduled Outage | Maintenance | Switch S15837 @ 650 EARL ARMSTRONG RD was isolated to allow the crew to replace defective switches | None | Fused Cutout | 12 | 29 | 6 | East | 7F1
128770 | 2014-04-23 | Scheduled Outage | Maintenance | Switch S15339 @ 668 River Rd was isolated by the crew to replace defective switches | None | Fused Cutout | 1 | 33 | 1 | East | 7F2
128771 | 2014-04-23 | Scheduled Outage | Maintenance | to allow duct sealing | None | None | 12 | 138 | 28 | East | 7F1
128772 | 2014-04-23 | Scheduled Outage | Construction | transfer cables to new poles | None | None | 1 | 80 | 1 | Central | UX05
128774 | 2014-04-23 | Scheduled Outage | Construction | To allow Black & Macdonald to re-route secondary cables | None | U/G Service | 1 | 388 | 6 | East | TB1UQ
128775 | 2014-04-23 | Scheduled Outage | Construction | To allow Black & Macdonald crews to transfer plant to new poles | None | None | 20 | 415 | 138 | Central | UW07
128776 | 2014-04-23 | Scheduled Outage | Maintenance | replace defective switches | None | None | 1 | 85 | 1 | East | 7F1
128777 | 2014-04-23 | Scheduled Outage | Construction | To allow Black & Macdonald crews to change poles & transfer all plant to the new poles | None | Pole | 95 | 200 | 317 | Central | UX04
128778 | 2014-04-23 | Tree Contacts | Falling Tree | A large spruce tree fell onto the ELW09 circuit | None | None | 33 | 116 | 64 | East | 2207
128778 | 2014-04-23 | Tree Contacts | Falling Tree | A large spruce tree fell onto the ELW09 circuit | None | None | 2000 | 36 | 1200 | East | ELW09
128779 | 2014-04-23 | Tree Contacts | Broken Branch | tree on primary | None | None | 43 | 78 | 56 | East | BLKF5
128779 | 2014-04-23 | Tree Contacts | Broken Branch | tree on primary | None | None | 747 | 43 | 535 | East | BLKF4
128779 | 2014-04-23 | Tree Contacts | Broken Branch | tree on primary | None | None | 920 | 43 | 659 | East | BLKF3
128780 | 2014-04-23 | Scheduled Outage | Maintenance | remove transformer for soil removal. | None | None | 1 | 642 | 11 | West | MWDF3
128782 | 2014-04-23 | Defective Equipment | Mechanical Failure | Replace LLC and transformer lead | O/H Transformer | O/H Transformer (1ph) | 6 | 48 | 5 | Central | SB03
128783 | 2014-04-24 | Scheduled Outage | Construction | To install new poles and relocate overhead. | None | None | 27 | 315 | 142 | Central | UW07
128785 | 2014-04-24 | Defective Equipment | Defective Equipment/ Material | Transformer #X36683 opened up due to broken fuse link | O/H Switchgear | Fused Cutout | 3 | 23 | 1 | West | 43F2
128786 | 2014-04-24 | Scheduled Outage | Construction | TE2180 at 2643 Innes isolated to allow crews to change insulators. | None | Insulator | 2 | 155 | 5 | East | BLKF3
128787 | 2014-04-24 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X23669 TO REMOVE BROKEN TREE BRANCH OFF THE OPEN BUSS AND REPLACED THE TRANSFORMER SWITCH | None | None | 5 | 30 | 2 | East | UB07
128788 | 2014-04-25 | Scheduled Outage | Construction | TP6082 isolated to allow crews to disconnect primary cable for cable re-location. | None | XLPE | 1 | 2498 | 42 | South | 49F6
128789 | 2014-04-25 | Defective Equipment | Defective Equipment/ Material | Defective blue phase switch V139 | O/H Switchgear | Fused Cutout | 70 | 54 | 63 | East | UA11
128790 | 2014-04-26 | Scheduled Outage | Maintenance | At 8:06 am, switch S14209 feeding VE78 at 3545 Leitrim Rd was isolated to allow crew to replace defective SMD switches. 1 customer was interrupted for 21 minutes. Leitrim Sub (249F1 circuit) | None | Fused Cutout | 1 | 21 | 0 | East | LTM01
128791 | 2014-04-26 | Scheduled Outage | Maintenance | At 9:10 am, switch S19476 at 3545 Leitrim Rd feeding TP7225 was isolated to allow crew to replace defective SMD switches. 1 customer was interrupted for 23 minutes. Leitrim Sub (249F1) | O/H Switchgear | Fused Cutout | 1 | 23 | 0 | East | LTM01
128792 | 2014-04-26 | Scheduled Outage | Maintenance | all crew to transfer plant to new pole. | None | None | 15 | 345 | 86 | East | CYRF1
128793 | 2014-04-27 | Defective Equipment | Defective Equipment/ Material | Defective S/L feed blew trans KT0429 fuse | Secondary \ Service | U/G Service | 11 | 134 | 25 | East | 2206
128794 | 2014-04-28 | Scheduled Outage | Construction | Transfer plant to new poles | None | None | 64 | 60 | 64 | Central | UJ05
128795 | 2014-04-28 | Scheduled Outage | Maintenance | At 9:15 am, Vault VT253 transformer bus at 100 Empress was isolated to allow crew to make metering repairs. 1 customer was interrupted for 26 minutes. Slater TS (TS1AM) ID# 128795. | None | None | 1 | 26 | 0 | Central | TS1AM
128796 | 2014-04-28 | Scheduled Outage | Maintenance | Circuit load balancing | None | None | 7 | 45 | 5 | Central | SH05
128797 | 2014-04-28 | Scheduled Outage | Construction | Transformer #X32458 isolated by crew to transfer plant | None | None | 10 | 135 | 22 | Central | UW07
128798 | 2014-04-28 | Scheduled Outage | Construction | Transformer #X33833 isolated by crew to transfer plant | None | None | 7 | 210 | 24 | Central | UW07
128799 | 2014-04-29 | Scheduled Outage | Construction | At 09:40, 145F4 O/H section on Stranherd & McKenna was isolated to allow crews to new pole line. 2 customers affected for minutes. Bayshore (49F5) ID #128 | None | O/H Conductor | 2 | 378 | 13 | South | 49F5
128800 | 2014-04-29 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32307 TO REPLACE CONNECTIONS ON SECONDARY SERVICE | None | None | 9 | 50 | 8 | Central | UC07
128801 | 2014-04-29 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35852 TO REPLACE SWITCH ARRESTER AND SECONDARY CONNECTIONS | None | None | 9 | 105 | 16 | South | 190F2
128802 | 2014-04-29 | Scheduled Outage | Construction | Transformer #X35211 isolated by crew to transfer plant to another phase | None | None | 16 | 40 | 11 | Central | UC10
128803 | 2014-04-29 | Scheduled Outage | Construction | Transformer #X33849 isolated by crew to transfer plant to another phase | None | None | 6 | 45 | 4 | Central | UC10
128804 | 2014-04-29 | Scheduled Outage | Construction | Transformer #X35212 isolated by crew to transfer plant to another phase | None | None | 6 | 45 | 4 | Central | UC10
128805 | 2014-04-29 | Scheduled Outage | Construction | Transformer #X35960 isolated by crew to transfer plant to another phase | None | None | 8 | 20 | 3 | Central | UC10
128806 | 2014-04-29 | Scheduled Outage | Construction | 2 transformers, #X32453 and X32454 isolated by crew to transfer plant to another phase | None | None | 17 | 45 | 13 | Central | UC10
128807 | 2014-04-29 | Scheduled Outage | Construction | 3 transformers, #X33845, X32463 and X32462 isolated by crew to transfer plant to another phase | None | None | 21 | 20 | 7 | Central | UC10
128808 | 2014-04-29 | Scheduled Outage | Construction | 2 transformers, #X35221 and X35222 isolated by crew to transfer plant to another phase | None | None | 21 | 30 | 10 | Central | UC10
128809 | 2014-04-29 | Scheduled Outage | Maintenance | Transformer #X23594 isolated by crew to replace connections | None | None | 19 | 70 | 22 | East | UG04
128810 | 2014-04-29 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X36803 opened up due to tree interference | O/H Switchgear | Fused Cutout | 1 | 40 | 1 | South | 200F1
128811 | 2014-04-29 | Defective Equipment | Defective Equipment/ Material | Transformer #X40032 opened up due to broken fuse | O/H Switchgear | Fused Cutout | 1 | 123 | 2 | South | 145F3
128812 | 2014-04-29 | Defective Equipment | Mechanical Failure | Defective insulator | U/G Transformer | Kiosk (1ph) | 12 | 189 | 38 | East | TB14
128813 | 2014-04-30 | Defective Equipment | Electrical Failure | Pole fire caused pole to break off at switch G971 at 5380 Canotek Rd. Causing S21787 fuses to open. | Pole | Insulation Failure (Pole Fire) | 2 | 292 | 10 | East | BCHF4
128813 | 2014-04-30 | Defective Equipment | Electrical Failure | Pole fire caused pole to break off at switch G971 at 5380 Canotek Rd. Causing S21787 fuses to open. | Pole | Insulation Failure (Pole Fire) | 222 | 234 | 866 | East | BCHF4
128813 | 2014-04-30 | Defective Equipment | Electrical Failure | Pole fire caused pole to break off at switch G971 at 5380 Canotek Rd. Causing S21787 fuses to open. | Pole | Insulation Failure (Pole Fire) | 261 | 69 | 300 | East | BCHF4
128814 | 2014-05-01 | Scheduled Outage | Maintenance | To replace faulted cable section and replace porcelain cutout. | None | None | 13 | 154 | 33 | East | AP06
128815 | 2014-05-01 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35162 TO TRANSFER FEED TO ANOTHER PHASE | None | None | 8 | 45 | 6 | Central | SH02
128816 | 2014-05-01 | Scheduled Outage | Maintenance | ISOLATED TRANSFROMER KT0460 TO FAULT FIND ON SECONDARY SERVICE. | None | None | 14 | 32 | 7 | Central | TH11-NIU
128817 | 2014-05-01 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X37909 TO REPLACE SWITCH AND ARRESTER | None | None | 11 | 38 | 7 | Central | UJ05
128822 | 2014-05-01 | Foreign Interference | Foreign Objects | flag pole on conductor. | None | None | 871 | 59 | 856 | West | BRDF5
128823 | 2014-05-01 | Tree Contacts | Falling Tree | S21205 fuse blew due to tree taking down overhead wires. | None | None | 3 | 437 | 22 | West | RHNF3
128824 | 2014-05-01 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X26948 fuse blew due to squirrel. Playfair (AJ04) ID#128824. | None | None | 13 | 81 | 18 | East | AJ04
128825 | 2014-05-02 | Scheduled Outage | Maintenance | replaced a leaking transformer. | None | Padmount (1ph) | 10 | 103 | 17 | East | BCHF1
128826 | 2014-05-02 | Scheduled Outage | Maintenance | To re-terminate and install new pole mounted switches. | None | Fused Cutout | 6 | 158 | 16 | Central | UX08
128827 | 2014-05-02 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35157 TO REPLACE SWITCH AND RELOCATE TO ANOTHER PHASE FOR LOAD BALANCE | None | None | 19 | 55 | 17 | Central | SH02
128828 | 2014-05-03 | Foreign Interference | Vehicle | MVA damaged a guy wire | None | None | 827 | 63 | 868 | South | 47F6
128829 | 2014-05-03 | Defective Equipment | Electrical Failure | suspected cable fault at VT65 at 250 Lanark | U/G Cable Attachement | Pothead | 3 | 13 | 1 | Central | TH2UL
128829 | 2014-05-03 | Defective Equipment | Electrical Failure | suspected cable fault at VT65 at 250 Lanark | U/G Cable Attachement | Pothead | 4 | 55 | 4 | Central | TH2UL
128829 | 2014-05-03 | Defective Equipment | Electrical Failure | suspected cable fault at VT65 at 250 Lanark | U/G Cable Attachement | Pothead | 6 | 17 | 2 | Central | TH2UL
128829 | 2014-05-03 | Defective Equipment | Electrical Failure | suspected cable fault at VT65 at 250 Lanark | U/G Cable Attachement | Pothead | 326 | 44 | 239 | Central | TH2UL
128829 | 2014-05-03 | Defective Equipment | Electrical Failure | suspected cable fault at VT65 at 250 Lanark | U/G Cable Attachement | Pothead | 1522 | 47 | 1192 | Central | TH2UL
128830 | 2014-05-03 | Unknown/Other | Unknown | Transformer #X32686 opened up, crew refused but could not find an apparent cause. | O/H Switchgear | Fused Cutout | 9 | 118 | 18 | South | 190F5
128831 | 2014-05-04 | Foreign Interference | Wildlife (Bird/Animal) | Squirell made contact at transformer X36008 causing the 58F1 breaker to auto reclose and burned off the connection to the blue phase run off feed ing X36008 and X36629 Epworth, 58F1, ID # 128831 | O/H Conductor | O/H Conductor | 20 | 119 | 40 | South | EPWF1
128832 | 2014-05-04 | Defective Equipment | Electrical Failure | A pole fire caused S412 B phase to open affecting 109 customers. The pole was comprimised and the primary dead-end insulator let go and could not be re-attached. 6 customers fed out of X4149 were transfered to X32852. | Pole | Insulation Failure (Pole Fire) | 6 | 67 | 7 | South | 170F1
128832 | 2014-05-04 | Defective Equipment | Electrical Failure | A pole fire caused S412 B phase to open affecting 109 customers. The pole was comprimised and the primary dead-end insulator let go and could not be re-attached. 6 customers fed out of X4149 were transfered to X32852. | Pole | Insulation Failure (Pole Fire) | 109 | 74 | 134 | South | 170F1
128833 | 2014-05-04 | Defective Equipment | Defective Equipment/ Material | Blown cut-out and arrestor at transformer X29277 | O/H Switchgear | Fused Cutout | 6 | 40 | 4 | East | CYRF1
128833 | 2014-05-04 | Defective Equipment | Defective Equipment/ Material | Blown cut-out and arrestor at transformer X29277 | O/H Switchgear | Fused Cutout | 78 | 109 | 142 | East | CYRF1
128835 | 2014-05-05 | Scheduled Outage | Maintenance | Transformer #NP000863 isolated by crew to remove a meter for the Meter Dept | None | None | 2 | 35 | 1 | South | 47F6
128836 | 2014-05-05 | Scheduled Outage | Construction | Transformer #X29649 isolated by crew due to transformer upgrade | None | None | 12 | 180 | 36 | East | UT07
128837 | 2014-05-05 | Scheduled Outage | Maintenance | Transformer #X25654 isolated by crew to replace a switch for maintenance | None | None | 15 | 37 | 9 | Central | TH11-NIU
128838 | 2014-05-05 | Scheduled Outage | Maintenance | Transformer #X39262 isolated by crew to replace switch for maintenance | None | None | 1 | 20 | 0 | West | ALEXF3
128839 | 2014-05-05 | Scheduled Outage | Maintenance | Transformer #X25652 isolated by crew to replace switch for maintenance | None | None | 4 | 25 | 2 | Central | TH11-NIU
128840 | 2014-05-05 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMERS X32452, X33847 AND XX35210 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 26 | 185 | 80 | Central | UC10
128841 | 2014-05-05 | Defective Equipment | Electrical Failure | REPLACED DEFECTIVE TRANSFORMER X2396 FEEDING THE TRAFFIC LIGHTS | O/H Transformer | O/H Transformer (1ph) | 1 | 285 | 5 | South | 160F2
128846 | 2014-05-06 | Scheduled Outage | Maintenance | At 12:30, PC10a #11620 established by Tom Connel (K-Line) at S25656 to allow crews to install pole & transfer plant. 9 customers affected for 152 minutes. Woodroffe (UW07) ID #128846 | None | O/H Conductor | 9 | 152 | 23 | Central | UW07
128855 | 2014-05-07 | Scheduled Outage | Construction | at 10:10, 4KV transformer P456 at 255 Argyle, to aloow crews to make new terminations. 46 customers affected for 185 minutes. Gladstone (UX08) ID #128855 | None | Inline Switch | 46 | 185 | 142 | Central | UX08
128856 | 2014-05-07 | Scheduled Outage | Construction | At 08:30, 4KV O/H isolated on Laxton to allow crews to install new poles & transfer plant, 9 customers affected for 475 minutes. Woodroffe (UW07) ID #128856 | None | Pole | 9 | 475 | 71 | Central | UW07
128858 | 2014-05-07 | Defective Equipment | Corrosion | Defective LLC at S414 on blue phase crew had to open a gang switch to allow for repairs. Manordale (84F4) ID#128858 | O/H Conductor | Hot-Line Clamp | 2 | 191 | 6 | South | 84F4
128858 | 2014-05-07 | Defective Equipment | Corrosion | Defective LLC at S414 on blue phase crew had to open a gang switch to allow for repairs. Manordale (84F4) ID#128858 | O/H Conductor | Hot-Line Clamp | 3 | 44 | 2 | South | 84F4
128859 | 2014-05-07 | Defective Equipment | Electrical Failure | 27kV transformer X21812 was found to be defective. | O/H Transformer | O/H Transformer (1ph) | 1 | 287 | 5 | West | 624F1
128861 | 2014-05-08 | Scheduled Outage | Maintenance | transformer 5886W at 31 Inuvik was off to allow for NRC cable testing isolation and due to out of phase condition affecting 6 customers for 63 minutes, Beaverbrook, 24F8, ID # 128861 | None | None | 6 | 63 | 6 | West | 24F8
128862 | 2014-05-08 | Scheduled Outage | Construction | Replace defective tranformer cutout | None | Fused Cutout | 1 | 20 | 0 | West | ALEXF3
128863 | 2014-05-08 | Scheduled Outage | Vegetation Management | Transformer X27206 at rear of 417 Roger opened to permit tree trimming. 6 customers affected for 510 min. Queens UQ07. | None | None | 6 | 510 | 51 | East | UQ07
128864 | 2014-05-08 | Scheduled Outage | Maintenance | transformer TP9176 at 40 Hesse was isolated to allow crew to repair a broken pin in the insert affecting 11 customers for 18 minutes, Janet King, JKGF4, ID # 128864 | None | Padmount (1ph) | 11 | 18 | 3 | West | JKGF4
128865 | 2014-05-08 | Foreign Interference | Dig-In | Customer dug up secondary, caused transformerr fuse to blow, crew then found defective insulators in TE76 (live front ) | U/G Transformer | Padmount (1ph) | 1 | 111 | 2 | East | BLKF4
128865 | 2014-05-08 | Foreign Interference | Dig-In | Customer dug up secondary, caused transformerr fuse to blow, crew then found defective insulators in TE76 (live front ) | U/G Transformer | Padmount (1ph) | 5 | 359 | 30 | East | BLKF4
128866 | 2014-05-08 | Scheduled Outage | Construction | At 1:27 pm, 145F4 between S310 and Temp 114 was isolated to allow crew to install new poles. 2 customers were interrupted for 285 minutes. Jockvale (145F4) ID# 128866. | None | None | 2 | 285 | 10 | South | 145F4
128867 | 2014-05-09 | Scheduled Outage | Construction | At 9:14 am, transformer TP6931 at 506 Creekview Way was isolated to allow crew to remove an N.I.U. Cable section. 7 customers were interrupted for 67 minutes. Leitrim (249F1) ID# 128867. | None | None | 7 | 67 | 8 | East | LTM01
128868 | 2014-05-09 | Scheduled Outage | Construction | Replace defective cutout | None | Fused Cutout | 1 | 20 | 0 | South | FAL04
128869 | 2014-05-09 | Scheduled Outage | Construction | Replace transformer cutout | None | None | 1 | 20 | 0 | South | FAL04
128870 | 2014-05-09 | Scheduled Outage | Construction | Trans at 3809 Cedaar View Rd was isolated in order to replace the trans cutout | None | None | 1 | 15 | 0 | South | FAL03
128871 | 2014-05-09 | Scheduled Outage | Construction | Replace trans cutout | None | None | 1 | 20 | 0 | West | 624F6
128872 | 2014-05-09 | Scheduled Outage | Construction | Replace trans cutout | None | None | 1 | 10 | 0 | West | 624F6
128873 | 2014-05-09 | Scheduled Outage | Construction | Relocate 3 Ph trans bank to new pole | None | None | 2 | 170 | 6 | Central | UX08
128874 | 2014-05-09 | Scheduled Outage | Forced Switching | Transformer X30305 was opened to allow crew to replace LLC | None | Fused Cutout | 6 | 23 | 2 | Central | UF07
128875 | 2014-05-10 | Defective Equipment | Defective Equipment/ Material | Transformer X36003 opened due to broken transformer bushing. Transformer X35839 was interrupted to allow crew to replace defective primary inuslator and transfer customer fed off transformer X36003 to transformer X35839. Epworth (58F1). ID# 128875 | O/H Transformer | O/H Transformer (1ph) | 3 | 222 | 11 | South | EPWF1
128875 | 2014-05-10 | Defective Equipment | Defective Equipment/ Material | Transformer X36003 opened due to broken transformer bushing. Transformer X35839 was interrupted to allow crew to replace defective primary inuslator and transfer customer fed off transformer X36003 to transformer X35839. Epworth (58F1). ID# 128875 | O/H Transformer | O/H Transformer (1ph) | 7 | 129 | 15 | South | EPWF1
128879 | 2014-05-10 | Defective Equipment | Defective Equipment/ Material | 140F3 O/H from S109 to EOL was open forced open by crew due to W down phase conductor. 7 customers were affected for 10 minutes. Jockvale (140F3) ID#128879 | O/H Conductor | O/H Conductor | 7 | 10 | 1 | South | 140F3
128881 | 2014-05-10 | Defective Equipment | Mechanical Failure | Crews found loose connction at transformer X39598. Marchwood (MWDF3) ID #128880 | Secondary \ Service | O/H Service | 1 | 30 | 0 | West | MWDF3
128882 | 2014-05-11 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X33527at 1965 Bromley opened due to animal contact. Lincoln Height (TD06). ID# 128882 | None | None | 8 | 52 | 7 | Central | TD06
128883 | 2014-05-11 | Defective Equipment | Electrical Failure | Defective transformer. | U/G Transformer | Padmount (3ph) | 1 | 407 | 7 | Central | TH06
128884 | 2014-05-11 | Scheduled Outage | Maintenance | Changing a leaking transformer. | None | None | 1 | 200 | 3 | East | 6F10
128885 | 2014-05-11 | Tree Contacts | Falling Tree | At 14:56 white phase customers past the Rabbits on Greenbank reported their power was out. Crews patrolled but found a down tree on Greenbank south of Barnsdale. They refused | None | None | 4 | 138 | 9 | South | FAL03
128886 | 2014-05-11 | Human Element | Switching Error | The while blocking the RX2009 recloser the recloser inadveratenly tripped open | O/H Switchgear | Recloser (1ph) | 192 | 5 | 16 | West | 624F6
128887 | 2014-05-12 | Scheduled Outage | Maintenance | Customer vault mtce. | None | None | 1 | 253 | 4 | Central | AK05
128888 | 2014-05-12 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X07471 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 5 | 0 | West | 624F6
128889 | 2014-05-12 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X37477 TO REPLACE SWITCH AND ARRESTER | None | None | 5 | 20 | 2 | West | 624F6
128891 | 2014-05-12 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X26806 AND X37910 TO REPLACE POLES | None | None | 10 | 130 | 22 | East | AJ07
128892 | 2014-05-12 | Scheduled Outage | Maintenance | Transfomer 1824 was defective and replaced with new TP10429 at 360 Terry Fox Dr on 624F5 | None | Padmount (3ph) | 1 | 338 | 6 | West | 624F5
128895 | 2014-05-13 | Scheduled Outage | Vegetation Management | Transformer #X33107 isolated by crew for tree contractor | None | None | 12 | 55 | 11 | Central | TD05
128896 | 2014-05-13 | Scheduled Outage | Maintenance | Transformer #X32853 isolated by crew to remove a transformer that is no longer in use | None | None | 5 | 55 | 5 | South | 170F1
128897 | 2014-05-13 | Scheduled Outage | Construction | A section of UX05 O/H on Cartier was isolated by the crew to install a new pole and transfer plant to that new pole. | None | Pole | 100 | 288 | 480 | Central | UX05
128898 | 2014-05-13 | Scheduled Outage | Maintenance | A 13Kv transformer PT208 @ 2090 Neepawa was isolated to allow the contractor to perform secondary maintenance. | None | Unknown \ Other | 2 | 270 | 9 | Central | TD06
128899 | 2014-05-13 | Scheduled Outage | Maintenance | VE29G at 2020 Jasmine Cres 8F4 isolated for customer vault mtce. And upgrade fencing. | None | None | 1 | 355 | 6 | East | 8F4
128900 | 2014-05-13 | Scheduled Outage | Maintenance | The crews isolated a section of UW07 O/H at 1821 Iris to allow them to replace a pole and transfer of plant | None | Pole | 27 | 494 | 222 | Central | UW07
128901 | 2014-05-14 | Scheduled Outage | Maintenance | At 9:25 am, transformer TP10134 at 1167 Ambercrest was isolated to allow crew to perform oil cleanup. 10 customers were interrupted for minutes. Cyrville (CYRF4) ID# 128901. | None | None | 10 | 567 | 94 | East | CYRF4
128902 | 2014-05-14 | Scheduled Outage | Maintenance | At 9:27 am, V516 at 201 McLeod was isolated top allow the crew to prove spare duct from pole to vault for future cable replacement. | None | Unknown \ Other | 1 | 55 | 1 | Central | UX06
128903 | 2014-05-14 | Scheduled Outage | Vegetation Management | Transformer #X23411 isolated by crew for Forestry Dept | None | None | 9 | 87 | 13 | East | UB04
128904 | 2014-05-14 | Scheduled Outage | Maintenance | At 9:13 am, vault VT141 at 1845 Baseline was isolated to allow contractor to perform vault maintenance. 1 customer was interrupted for 244 mimutes. Woodroffe (2802) ID# 128904. | None | None | 1 | 244 | 4 | Central | 2802
128905 | 2014-05-14 | Scheduled Outage | Maintenance | Three 4Kv Overhead circuit on Gladestone and Cartier was isolated to allow the crews to complete the installation and transfer plant to the new poles. | None | Pole | 75 | 294 | 368 | Central | UX05
128906 | 2014-05-14 | Tree Contacts | Falling Tree | A fallen tree broke the secondary service and Transformer X33888 on Piccadilly was opened to allow crew to disconnect the triplex. | Secondary \ Service | O/H Service | 6 | 20 | 2 | Central | SM06
128909 | 2014-05-15 | Scheduled Outage | Construction | Transformer TP9976 at 2192 Bickerton was isolated to allow crew to remove temp service and connect permant service. Beaconhill (BCHF5). ID 128909 | None | None | 2 | 14 | 0 | East | BCHF5
128910 | 2014-05-15 | Defective Equipment | Defective Equipment/ Material | Transformer #X24506 opened up due to defective switch | O/H Switchgear | Fused Cutout | 6 | 80 | 8 | East | UG06
128911 | 2014-05-15 | Scheduled Outage | Maintenance | Transformer TP10134 at 1167 Ambercrest was isolated to allow crew to perform transformer soil remediation. 10 Customers were affected. Cyrville (CYRF4). | None | Padmount (1ph) | 10 | 178 | 30 | East | CYRF4
128912 | 2014-05-15 | Scheduled Outage | Construction | Transformer #X31035 isolated by crew to transfer plant | None | None | 2 | 190 | 6 | Central | UX06
128914 | 2014-05-16 | Defective Equipment | Mechanical Failure | Pole Fire at 5482D-0166 caused by 2 defective porcelain cutouts | O/H Switchgear | Fused Cutout | 798 | 128 | 1702 | Central | 505
128914 | 2014-05-16 | Defective Equipment | Mechanical Failure | Pole Fire at 5482D-0166 caused by 2 defective porcelain cutouts | O/H Switchgear | Fused Cutout | 1809 | 19 | 573 | Central | 505
128915 | 2014-05-16 | Defective Equipment | Defective Equipment/ Material | G285 opened due to brken insulator at pole X24170 at 35 Seguin. Moulton (8F1). ID# 128915 | Pole Attachement | Insulator | 311 | 78 | 404 | East | 8F1
128915 | 2014-05-16 | Defective Equipment | Defective Equipment/ Material | G285 opened due to brken insulator at pole X24170 at 35 Seguin. Moulton (8F1). ID# 128915 | Pole Attachement | Insulator | 714 | 149 | 1773 | East | 8F1
128916 | 2014-05-16 | Tree Contacts | Broken Branch | crews established PC10a #9033 at fused switch feeding radial O/H to remove b fallen branch on O/H conductor. 25 customers affected for 10 minutes. Bronson (SB09) ID #128916 | None | None | 25 | 10 | 4 | Central | SB09
128917 | 2014-05-16 | Scheduled Outage | Forced Switching | Transformer #X34159 isolated by crew to replace burning live line clamp | None | Inline Switch | 6 | 15 | 2 | Central | UL04
128918 | 2014-05-16 | Scheduled Outage | Maintenance | Transformer #P467 isolated by crew to replace defective transformer switch, replaced all 3. | None | None | 1 | 73 | 1 | East | UA02
128921 | 2014-05-17 | Defective Equipment | Mechanical Failure | A blown arrestor cause the G30R @ 1987 Rideau Rd to blow and the 7F4 to auto reclosed. | Pole Attachement | Arrester | 49 | 148 | 121 | East | 7F4
128922 | 2014-05-17 | Defective Equipment | Defective Equipment/ Material | A bad underground feeding 14, 16, 18 CHANNONHOUSE AND 77 DALLAIRE om RHNF1 burnt going under the street | Secondary \ Service | U/G Service | 4 | 700 | 47 | West | RHNF1
128923 | 2014-05-18 | Foreign Interference | Wildlife (Bird/Animal) | 7F1 auto reclosed because a racoon made contact with the O/H transformer causing two phases to blow. | O/H Transformer | O/H Transformer (3ph) | 1 | 282 | 5 | East | 7F1
128924 | 2014-05-18 | Adverse Environment | Fire | Fire call at 65 Lennox underground service cut clear from overhead. Then power restored to other 9 customers.28F2 white phase Transformer X36028 | Secondary \ Service | U/G Service | 9 | 186 | 28 | West | 28F2
128925 | 2014-05-18 | Foreign Interference | Wildlife (Bird/Animal) | RX2010 auto-reclosed and X35226 at 19 John Woods fuse blew due to animal contact. | None | None | 5 | 79 | 7 | West | ALEXF3
128926 | 2014-05-19 | Defective Equipment | Mechanical Failure | Transformer X37013 was found open due to crack cut-out. | O/H Switchgear | Fused Cutout | 5 | 88 | 7 | South | 200F1
128927 | 2014-05-19 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X28228 was found open due to squirrel contact. Riverdale (505) | None | None | 4 | 188 | 13 | Central | 505
128929 | 2014-05-19 | Unknown/Other | Unknown | a | None | None | 2196 | 188 | 6881 | East | LTM01
128933 | 2014-05-19 | Tree Contacts | Broken Branch | Tree Limb cause overhead xfmr to open | None | None | 14 | 102 | 24 | Central | TD01
128934 | 2014-05-20 | Scheduled Outage | Construction | TE2339 at 5 Glenarden isolated to allow crews to replace swollen elbow. | None | Padmount (1ph) | 8 | 201 | 27 | South | 87F1
128935 | 2014-05-20 | Scheduled Outage | Forced Switching | Crews isolate overhead section between G325R and G3R to replace broken insulator. | None | Insulator | 93 | 12 | 19 | East | 7F2
128936 | 2014-05-20 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMERS X48963 AND X48960 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 21 | 210 | 74 | Central | UW07
128937 | 2014-05-20 | Scheduled Outage | Maintenance | ISOLATED AND REPLACED TRANSFORMER X32965 | None | None | 6 | 100 | 10 | West | BECKF2
128938 | 2014-05-20 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35246 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 10 | 0 | South | FAL01
128939 | 2014-05-20 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X39609 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 10 | 0 | South | FAL01
128940 | 2014-05-20 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X41759 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 15 | 0 | South | FAL01
128941 | 2014-05-20 | Defective Equipment | Defective Equipment/ Material | SC5176 on Glenrill tripped open due to defective elbow at TP7690. Bridlewood (BRDF2) | U/G Cable Attachement | Elbow \ Insert | 7 | 15 | 2 | West | BRDF2
128941 | 2014-05-20 | Defective Equipment | Defective Equipment/ Material | SC5176 on Glenrill tripped open due to defective elbow at TP7690. Bridlewood (BRDF2) | U/G Cable Attachement | Elbow \ Insert | 198 | 181 | 597 | West | BRDF2
128942 | 2014-05-21 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33224 (SQUIRREL) | O/H Transformer | O/H Transformer (1ph) | 17 | 95 | 27 | South | 190F2
128944 | 2014-05-21 | Scheduled Outage | Construction | Soil remidiation. | None | None | 10 | 871 | 145 | East | BCHF1
128945 | 2014-05-21 | Foreign Interference | Vehicle | ISOLATED TRANSFORMER X34116 TO DISCONNECT DAMAGED TRIPLEX SERVICE (HIT BY A TRUCK) | None | None | 2 | 35 | 1 | Central | TH01
128947 | 2014-05-21 | Scheduled Outage | Construction | To allow crew to connect new conductors and switches both at the transformer and overhead. | None | None | 10 | 261 | 44 | East | BCHF8
128949 | 2014-05-21 | Scheduled Outage | Construction | BRDF2 R phase transfromer TP7688 isolated to allow crews to change it due to defective primary switch and elbow. TP10136 at 1 Summitview interrupted during switching due to out of phase condtion. | None | Padmount (1ph) | 3 | 95 | 5 | West | BRDF2
128949 | 2014-05-21 | Scheduled Outage | Construction | BRDF2 R phase transfromer TP7688 isolated to allow crews to change it due to defective primary switch and elbow. TP10136 at 1 Summitview interrupted during switching due to out of phase condtion. | None | Padmount (1ph) | 10 | 15 | 2 | West | BRDF2
128950 | 2014-05-21 | Foreign Interference | Wildlife (Bird/Animal) | Crow made contact at S23015 and caused the blue phase fuse to blow | O/H Switchgear | Inline Switch | 80 | 118 | 157 | West | 624F1
128951 | 2014-05-21 | Scheduled Outage | Construction | re-frame pole & replace terminations at dip to P11 | None | None | 1 | 225 | 4 | Central | UX06
128952 | 2014-05-22 | Scheduled Outage | Construction | Pole installation & to transfer plant | None | None | 127 | 195 | 413 | Central | UX02
128953 | 2014-05-22 | Scheduled Outage | Construction | At 9:17 am, transformer TE286 at 88 Bowhill was isolated to allow crew to replace transformer. 17 customers were interrupted for 441 minutes. Borden Farms (130F4) ID# 128953. | None | Padmount (1ph) | 17 | 441 | 125 | South | 130F4
128954 | 2014-05-22 | Foreign Interference | Wildlife (Bird/Animal) | An animal made contact with the 170F1 O/H in the Knoxdale area causing the S412B phase to blow. | None | None | 80 | 73 | 97 | South | 170F1
128956 | 2014-05-22 | Scheduled Outage | Maintenance | Transformer #X31429 isolated by crew to replace switch and run new triplex | None | None | 10 | 45 | 8 | Central | AM05
128958 | 2014-05-22 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One (M29C) | None | None | 644 | 5 | 54 | West | BECKF2
128959 | 2014-05-23 | Scheduled Outage | Maintenance | maintenance work by contractor | None | None | 1 | 333 | 6 | East | 1802
128960 | 2014-05-22 | Scheduled Outage | Maintenance | vault maintenance and replace switches and cables. | None | None | 1 | 540 | 9 | Central | UX08
128962 | 2014-05-23 | Scheduled Outage | Construction | At 9:15 am, TD01 from S25769 to End of Line on Windermere was isolated to allow crew to remove a tree and to convert runoff to white phase. 42 customers were interrupted for 200 minutes. Lincoln Heights (TD01) ID# 128962. | None | None | 42 | 200 | 140 | Central | TD01
128963 | 2014-05-23 | Scheduled Outage | Forced Switching | Transformer #K801 isolated by crew to disconnect service due to U/G cable dig in | None | None | 7 | 9 | 1 | East | UZ07
128964 | 2014-05-23 | Scheduled Outage | Forced Switching | Transformer #K801 isolated by crew to reconnect service after repairs made from dig in. | None | None | 7 | 10 | 1 | East | UZ07
128966 | 2014-05-23 | Scheduled Outage | Construction | TP9693 on MWDF2 isolated to upgrade transformer from 750KVA to 200KVA | None | Unknown \ Other | 1 | 469 | 8 | West | MWDF2
128967 | 2014-05-23 | Unknown/Other | Unknown | S412B has blown second day in a row nothing found Mark B believes it could be possible overload for fuse, Long blue phase run now supplied from S421 B with S11117 open, | None | None | 73 | 106 | 129 | South | 170F1
128969 | 2014-05-24 | Defective Equipment | Electrical Failure | UC10 breaker opened due to suspected cable fault between station and PPH | U/G Cable | PILC | 147 | 166 | 407 | Central | UC10
128972 | 2014-05-24 | Foreign Interference | Vehicle | Customer reported MVC, pole hit at 1131 Newmarket st. 206 customers affected for 98 minutes | None | None | 206 | 98 | 336 | East | TB07
128973 | 2014-05-24 | Defective Equipment | Defective Equipment/ Material | Transformer X33445 at 13 Kingsmill opened due to defective cut out and arrestor. 4 customers were affected for 81 minutes. Parkwoodhills (190F5). ID# 128973 | O/H Switchgear | Fused Cutout | 4 | 81 | 5 | South | 190F5
128974 | 2014-05-24 | Foreign Interference | Customer Equipment | Sproule (Gord MacDonald) foud S145 at X22727 blown, customer reported that someone removing a TV antenna hit the primary and blew fuse. 2 customers affected for 342 minutes. Casselman DS (V11F3) ID #128974 | None | None | 2 | 342 | 11 | East | V11F3
128975 | 2014-05-25 | Scheduled Outage | Maintenance | World Exchanged building isolation for vault maintenance. | None | None | 1 | 354 | 6 | Central | 614
128976 | 2014-05-25 | Scheduled Outage | Construction | At 6:41 am, vault V420 at 64 Pretoria was isolated to allow crew to re-arrange cables on pole. 1 customer was interrupted for 101 minute. Bronson (SB02) ID# 128976. | None | None | 1 | 101 | 2 | Central | SB02
128977 | 2014-05-25 | Scheduled Outage | Construction | At 8:22 am, transformer X30468 at 18 Pretoria was isolated to allow crew to replace transformer. 3 customer were interrupted for 167 minute. Bronson (SB02) ID# 128977. | None | None | 3 | 167 | 8 | Central | SB02
128979 | 2014-05-26 | Foreign Interference | Wildlife (Bird/Animal) | Squirel contact at 48 majestic caused the S412 W phase to open. 89 cusotmers were affected. Woodroffe (170F1). ID# 128979 | None | None | 89 | 62 | 92 | South | 170F1
128980 | 2014-05-26 | Scheduled Outage | Construction | Transformer TE133 was isolated to allow crew to replace transformer and base and terminate new primary. 14 customers were affected for 439 minutes. Parkwoodhills (190F6). ID# 128980 | None | None | 14 | 439 | 102 | South | 190F6
128984 | 2014-05-26 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X30863 TO REPLACE SWITCH AND ARRESTER | None | None | 32 | 62 | 33 | Central | UF07
128985 | 2014-05-26 | Scheduled Outage | Forced Switching | Transformer TP8661 and TP8660 on Hedgerow Lane were isolated to allow crew to perform switching to isolate switch S2 on Trail Way. 15 customers were affected for 7 minutes. Alexander (ALEXF3). ID# 128985 | None | None | 15 | 7 | 2 | West | ALEXF2
128986 | 2014-05-26 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X37022 AND X37021 TO REPLACE LINE SWITCH SW1803 | None | None | 2 | 68 | 2 | West | 624F6
128987 | 2014-05-26 | Defective Equipment | Defective Equipment/ Material | Transformer #X33014 opened up due to broken transformer switch | O/H Switchgear | Fused Cutout | 7 | 93 | 11 | South | 47F4
128988 | 2014-05-27 | Defective Equipment | Defective Equipment/ Material | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X35678 | O/H Switchgear | Fused Cutout | 8 | 113 | 15 | Central | TD12
128989 | 2014-05-27 | Scheduled Outage | Construction | To allow crew to replace transformer and base. | None | Padmount (1ph) | 19 | 355 | 112 | South | 190F6
128992 | 2014-05-27 | Scheduled Outage | Maintenance | Elbow and Insert replacment program to 5 transformers, TP7648, TP7647, TP7639, TP7638, TP7642 | None | None | 85 | 143 | 203 | East | 77M2
128993 | 2014-05-27 | Scheduled Outage | Maintenance | Transformer GL000472 at 5331 Long Island Rd. isolated by crew to replace switch | None | None | 1 | 35 | 1 | East | 7F4
128994 | 2014-05-27 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to replace transformer 745 | None | None | 1 | 80 | 1 | South | 145F4
128995 | 2014-05-27 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change the transformer elbows, perform cleaning & maintenance and change the nomenclature | None | Elbow \ Insert | 2 | 325 | 11 | West | MWDF3
128996 | 2014-05-27 | Foreign Interference | Crane | Contractor hit the overhead primary with his boom truck and damaged conductor. | None | None | 25 | 6 | 2 | East | 4801F8
128996 | 2014-05-27 | Foreign Interference | Crane | Contractor hit the overhead primary with his boom truck and damaged conductor. | None | None | 105 | 114 | 200 | East | 4801F8
128997 | 2014-05-27 | Foreign Interference | Foreign Objects | Contractor dropped equipement in to our primary. | None | None | 1 | 23 | 0 | Central | UF10
128997 | 2014-05-27 | Foreign Interference | Foreign Objects | Contractor dropped equipement in to our primary. | None | None | 20 | 127 | 42 | Central | UF10
128997 | 2014-05-27 | Foreign Interference | Foreign Objects | Contractor dropped equipement in to our primary. | None | None | 204 | 11 | 37 | Central | UF10
128997 | 2014-05-27 | Foreign Interference | Foreign Objects | Contractor dropped equipement in to our primary. | None | None | 204 | 41 | 139 | Central | UF10
128998 | 2014-05-27 | Scheduled Outage | Maintenance | Transformer #X27789 isolated by crew to transfer load | None | None | 6 | 40 | 4 | East | UQ08
128999 | 2014-05-27 | Defective Equipment | Electrical Failure | Transformer at 4903 Farmer's Way fuse blew due to defective transformer. Leitrim (249F2) ID# 128999. | O/H Transformer | O/H Transformer (1ph) | 3 | 501 | 25 | East | 249F2
129000 | 2014-05-27 | Foreign Interference | Vehicle | AC02 circuit tripped open due to MVA. | None | None | 293 | 284 | 1387 | East | AC02
129003 | 2014-05-28 | Scheduled Outage | Maintenance | To replace leaking transformer TE2916 | None | Padmount (1ph) | 8 | 102 | 14 | East | CYRF4
129004 | 2014-05-28 | Scheduled Outage | Maintenance | To repair a small leak in transfromer 79B. | None | Padmount (1ph) | 3 | 56 | 3 | West | MWDF4
129006 | 2014-05-28 | Tree Contacts | Other Vegetation | Replaced blown fuse feeding transformer X24452 (Vines grown around switch) | None | None | 1 | 84 | 1 | East | 77M6
129007 | 2014-05-28 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMERS X30154, X30155, AND X30156 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 35 | 240 | 140 | Central | UX05
129008 | 2014-05-28 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X25727 TO REPLACE OPEN WIRE SECONDARY BUSS WITH TRIPLAX | None | None | 6 | 235 | 24 | Central | AM05
129009 | 2014-05-28 | Scheduled Outage | Maintenance | ISOLATED TWO TRANSFORMERS X30737 AND X30736 TO RE-ARRANG HYDRO PLANT | None | None | 32 | 70 | 37 | Central | UD04
129010 | 2014-05-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X32546 opened up due to primary switch lead burnt off | O/H Conductor | Hot-Line Clamp | 10 | 64 | 11 | Central | TD06
129012 | 2014-05-29 | Scheduled Outage | Construction | Transformer replacement | None | None | 15 | 485 | 121 | South | 190F6
129014 | 2014-05-29 | Scheduled Outage | Maintenance | K999 at 24 Huntview isolated to allow crews to repair elbow and insert. | None | Elbow \ Insert | 21 | 182 | 64 | East | AQ04
129015 | 2014-05-29 | Scheduled Outage | Construction | TP8443, TP8442, TP8420, TP8419, TP6346 and TP7664 isolated for elbow and insert replacement. | None | Elbow \ Insert | 46 | 252 | 193 | East | 77M5
129018 | 2014-05-29 | Scheduled Outage | Maintenance | Transformer X24678 at 888 River Rd isolated by crew to replace switch | None | None | 3 | 250 | 12 | East | 7F4
129019 | 2014-05-29 | Scheduled Outage | Maintenance | Transformer X13275 at 856 River Rd isolated by crew to replace switch | None | None | 3 | 10 | 0 | East | 7F4
129020 | 2014-05-29 | Scheduled Outage | Construction | Transformer X27667 at 257 Billings Ave. isolated by crew to transfer load to another phase | None | None | 5 | 40 | 3 | East | UQ08
129022 | 2014-05-29 | Scheduled Outage | Construction | Transformer X35075 at 2145 Dublin Ave., X32777 at 2163 Dublin Ave. and X32780 at 2171 Dublin Ave. isolated by contractor to transfer hydro plant | None | None | 18 | 45 | 14 | Central | UW03
129024 | 2014-05-30 | Foreign Interference | Vehicle | Not yet known. | None | None | 110 | 255 | 468 | Central | 303
129025 | 2014-05-30 | Scheduled Outage | Maintenance | 13 KV vault at VT563 was isolated to allow crews to replace switches on hydro pole. | None | Simple Solid Blade Switch | 1 | 55 | 1 | Central | TH11-NIU
129026 | 2014-05-30 | Defective Equipment | Defective Equipment/ Material | Blown arresters in K835 and K833. | U/G Cable Attachement | Arrester | 30 | 102 | 51 | East | AQ08
129027 | 2014-05-30 | Defective Equipment | Defective Equipment/ Material | To replace broken cutout. | O/H Switchgear | Fused Cutout | 1 | 73 | 1 | Central | 303
129028 | 2014-05-30 | Scheduled Outage | Construction | Soil remediations | None | None | 2 | 502 | 17 | West | MWDF4
129029 | 2014-05-30 | Defective Equipment | Defective Equipment/ Material | Transformer X15891 at 4720 Bowesville Rd. isolated to repair defective overhead service | Secondary \ Service | O/H Service | 3 | 65 | 3 | East | 7F4
129030 | 2014-05-31 | Scheduled Outage | Maintenance | customer vault maintenance | None | None | 3 | 480 | 24 | Central | 5208
129031 | 2014-05-31 | Defective Equipment | Electrical Failure | Broken Cutout caused outage to transformer X24873. | O/H Switchgear | Fused Cutout | 7 | 67 | 8 | East | SO03
129032 | 2014-05-31 | Unknown/Other | Unknown | S27347 white phase fuse blew for unknown reason. Line was patrolled, crew re-fused and closed. Lincoln Heights (TD07) ID# 129032. | None | None | 113 | 55 | 104 | Central | TD07
129033 | 2014-05-31 | Unknown/Other | Unknown | 160F4 breaker tripped for unknown reason. 160F4 breaker closed back in from station due to no communication on SCADA. | Unknown \ Other | Unknown \ Other | 1164 | 24 | 466 | South | 160F4
129034 | 2014-05-31 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27825 opened up due to squirrel interference | None | None | 15 | 49 | 12 | Central | TH06
129036 | 2014-05-31 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27697 opened up due to animal contact | None | None | 5 | 226 | 19 | East | TB06
129037 | 2014-05-31 | Scheduled Outage | Maintenance | TP9679 @ 1172 walkley was isolated to allow the contractor to remove temporary service and install permanent service. | None | U/G Service | 1 | 356 | 6 | East | ELW11
129038 | 2014-05-31 | Scheduled Outage | Maintenance | VT423 @ 2280 Stevenage was isolated to allow the crew to change the 347V transformers and replace the O/H switches. | Vault Equipment | Transformer | 1 | 589 | 10 | East | 2206
129039 | 2014-05-31 | Defective Equipment | Defective Equipment/ Material | replace a leaking tranformer | O/H Transformer | O/H Transformer (3ph) | 3 | 255 | 13 | Central | TR09
129040 | 2014-06-01 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35799 opened up due to animal contact | O/H Switchgear | Fused Cutout | 7 | 67 | 8 | Central | TD06
129041 | 2014-06-01 | Scheduled Outage | Maintenance | Customer Vault maintenance circuit 624 | None | None | 1 | 314 | 5 | Central | 624
129042 | 2014-06-01 | Tree Contacts | Broken Branch | Transformer #X38386 opened up due to tree contact | None | None | 1 | 56 | 1 | West | 624F6
129043 | 2014-06-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transforer X38386 opened due to tree contact. | Customer Owned | Customer-Owned | 1 | 98 | 2 | West | 624F6
129047 | 2014-06-02 | Scheduled Outage | Construction | TE2631 opened to allow new secondary cable to be pulled in to transformer base. FAL02 | None | Unknown \ Other | 20 | 96 | 32 | South | FAL02
129048 | 2014-06-02 | Scheduled Outage | Construction | Transformer #NP001719 isolated by crew to set a new pole | None | None | 1 | 270 | 4 | South | 130F4
129049 | 2014-06-02 | Scheduled Outage | Construction | Transformer #X38561 isolated by crew to install new service | None | None | 6 | 44 | 4 | Central | TD07
129050 | 2014-06-02 | Scheduled Outage | Maintenance | Transformer #X39291 isolated by crew to replace triplex service | None | None | 17 | 90 | 26 | East | SO03
129051 | 2014-06-02 | Scheduled Outage | Construction | Transformer and cable replacement on blue phase of 130F4. Old TE348 replaced with new TP9836 | None | Padmount (1ph) | 21 | 319 | 112 | South | 130F4
129052 | 2014-06-03 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One A8M Circuit | None | None | 47 | 6 | 5 | East | 4801F7
129052 | 2014-06-03 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One A8M Circuit | None | None | 5153 | 12 | 1031 | East | 4801F8
129054 | 2014-06-03 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One, A8M tripped due to 115kV tap to NAC at the airport had an insulator let go. | None | None | 262 | 11 | 48 | South | 72F4
129054 | 2014-06-03 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One, A8M tripped due to 115kV tap to NAC at the airport had an insulator let go. | None | None | 379 | 11 | 69 | South | 72F2
129054 | 2014-06-03 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One, A8M tripped due to 115kV tap to NAC at the airport had an insulator let go. | None | None | 931 | 11 | 171 | South | 72F1
129055 | 2014-06-03 | Scheduled Outage | Construction | TE345 at 19 Keewatin was isolated as part of a cable reconfiguration, affecting 14 customers for 368 minutes, Parkwoodhills 190F6, ID # 129055 | None | None | 14 | 368 | 86 | South | 190F6
129056 | 2014-06-03 | Scheduled Outage | Construction | Transformer X30160-1665520 at 106 Cartier St isolated by contractor for pole change | None | None | 1 | 178 | 3 | Central | UX05
129057 | 2014-06-03 | Scheduled Outage | Construction | Transformer X30159-1665521 at 117 Cartier St isolated by contractor for pole change | None | None | 11 | 105 | 19 | Central | UX09
129059 | 2014-06-03 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact on line section fed from S72W. | O/H Switchgear | Fused Cutout | 14 | 50 | 12 | South | EPWF1
129061 | 2014-06-03 | Adverse Weather | Extreme Wind | Crews found trees in close proximity to the overhead that could have made contact during high winds. | O/H Conductor | O/H Conductor | 14 | 53 | 12 | South | EPWF1
129062 | 2014-06-04 | Scheduled Outage | Forced Switching | 4kV transformer X29745 at 216 Lennox Park was isolated to allow crews to disconnect damaged service. | None | O/H Transformer (1ph) | 5 | 32 | 3 | East | UQ05
129063 | 2014-06-04 | Defective Equipment | Electrical Failure | RX2043 opened due to defective cut-out at transformer 5517 | O/H Switchgear | Fused Cutout | 2 | 459 | 15 | East | 77M6
129063 | 2014-06-04 | Defective Equipment | Electrical Failure | RX2043 opened due to defective cut-out at transformer 5517 | O/H Switchgear | Fused Cutout | 178 | 22 | 65 | East | 77M6
129063 | 2014-06-04 | Defective Equipment | Electrical Failure | RX2043 opened due to defective cut-out at transformer 5517 | O/H Switchgear | Fused Cutout | 1767 | 21 | 618 | East | 77M6
129063 | 2014-06-04 | Defective Equipment | Electrical Failure | RX2043 opened due to defective cut-out at transformer 5517 | O/H Switchgear | Fused Cutout | 1857 | 10 | 310 | East | 77M6
129064 | 2014-06-04 | Loss Of Supply | Transmission Inadvertent | Loss of supply. OGCC reports Q bus at South March TS tripped on diferential | None | None | 1045 | 11 | 192 | West | A9M2
129064 | 2014-06-04 | Loss Of Supply | Transmission Inadvertent | Loss of supply. OGCC reports Q bus at South March TS tripped on diferential | None | None | 4823 | 11 | 884 | West | A9M5
129064 | 2014-06-04 | Loss Of Supply | Transmission Inadvertent | Loss of supply. OGCC reports Q bus at South March TS tripped on diferential | None | None | 7095 | 11 | 1301 | West | A9M3
129066 | 2014-06-04 | Scheduled Outage | Maintenance | Elbow & insert replacement | None | Elbow \ Insert | 159 | 229 | 607 | East | 77M5
129067 | 2014-06-04 | Scheduled Outage | Maintenance | Replace transformer bases & terminate cables | None | Unknown \ Other | 12 | 381 | 76 | South | 72F6
129068 | 2014-06-04 | Scheduled Outage | Construction | To restore O/H plant on dip pole to normal following clearance issues for a contractors project | None | Unknown \ Other | 1 | 162 | 3 | Central | UX10
129069 | 2014-06-04 | Loss Of Supply | Transmission Inadvertent | Loss of supply, Hydro - 1 defective PT on Q bus | None | None | 1045 | 59 | 1028 | West | A9M2
129069 | 2014-06-04 | Loss Of Supply | Transmission Inadvertent | Loss of supply, Hydro - 1 defective PT on Q bus | None | None | 4823 | 49 | 3939 | West | A9M5
129069 | 2014-06-04 | Loss Of Supply | Transmission Inadvertent | Loss of supply, Hydro - 1 defective PT on Q bus | None | None | 7095 | 66 | 7804 | West | A9M3
129070 | 2014-06-04 | Scheduled Outage | Construction | transfer plant to new riser for V816 | None | None | 1 | 303 | 5 | Central | SA23
129071 | 2014-06-04 | Scheduled Outage | Construction | Restore O/H plant on dip pole to normal following clearance issues for a contractors project | None | None | 1 | 200 | 3 | Central | UX10
129072 | 2014-06-04 | Scheduled Outage | Construction | At 8:30 am V717 at 130 Somerset was removed from service to allow crew to transfer plant affecting 2 customers for 240 minutes, Gladstone UX02, ID # 129072 | None | None | 2 | 240 | 8 | Central | UX02
129073 | 2014-06-04 | Scheduled Outage | Maintenance | Prove Spare duct from riser pole to vault for future cable replacement | None | None | 1 | 59 | 1 | Central | UX08
129074 | 2014-06-04 | Scheduled Outage | Maintenance | To prove the spare duct from the riser pole to the kiosk transformer for future cable replacement | None | None | 10 | 35 | 6 | Central | UX08
129075 | 2014-06-04 | Foreign Interference | Dig-In | Excavation at 370 Metcalfe collapsed a cable duct causing a cable fault on TR2TS between VT51 and VT587 and the TR19 breaker to trip | U/G Cable | PILC | 160 | 23 | 61 | Central | TR2TS
129075 | 2014-06-04 | Foreign Interference | Dig-In | Excavation at 370 Metcalfe collapsed a cable duct causing a cable fault on TR2TS between VT51 and VT587 and the TR19 breaker to trip | U/G Cable | PILC | 161 | 3 | 8 | Central | TR2TS
129075 | 2014-06-04 | Foreign Interference | Dig-In | Excavation at 370 Metcalfe collapsed a cable duct causing a cable fault on TR2TS between VT51 and VT587 and the TR19 breaker to trip | U/G Cable | PILC | 183 | 53 | 162 | Central | TR2TS
129075 | 2014-06-04 | Foreign Interference | Dig-In | Excavation at 370 Metcalfe collapsed a cable duct causing a cable fault on TR2TS between VT51 and VT587 and the TR19 breaker to trip | U/G Cable | PILC | 360 | 67 | 402 | Central | TR2TS
129076 | 2014-06-04 | Scheduled Outage | Forced Switching | Cable feeding VT51 from VT488 in same ducts as faulted cable from VT587 was suspected to have been damaged, requested to isolate until inspected | None | None | 1 | 33 | 1 | Central | TR2TS
129077 | 2014-06-04 | Scheduled Outage | Maintenance | Cable from VT488 to VT51 needed to be dug out andd closely inspected requiring isolation for the excavation. | None | None | 1 | 248 | 4 | Central | TR2TS
129078 | 2014-06-04 | Scheduled Outage | Construction | Radial overhead from S20183 was isolated to allow for a transfer from UW03 to UW07 affecting 10 customers for 480 minutes, Woodroffe UW03, ID # 129078 | None | None | 10 | 480 | 80 | Central | UW03
129080 | 2014-06-05 | Scheduled Outage | Maintenance | Elbow and Transformer replacement. | None | Padmount (1ph) | 70 | 194 | 226 | East | 77M5
129083 | 2014-06-05 | Scheduled Outage | Vegetation Management | Transformer X33446 at 95 Hilliard Ave. isolated for Hydro Ottawa forestry contractor to trim trees at 1179 Deer Park Rd. Also to replace cutout at the same location | None | None | 12 | 27 | 5 | South | 190F5
129084 | 2014-06-05 | Scheduled Outage | Vegetation Management | Transformer X32687 at 1171 Deer Park Dr isolated to allow Hydro Ottawa Forestry contractor to trim trees. | None | None | 8 | 14 | 2 | South | 190F5
129085 | 2014-06-05 | Scheduled Outage | Maintenance | Transformer X32755 at 1117 Bedbrooke St. isolated by contractor to raise wire on neutral. | None | None | 12 | 13 | 3 | Central | UW03
129086 | 2014-06-05 | Scheduled Outage | Maintenance | To replace primary CAble terminations, connection & primary insulators. | None | Termination \ Stress Cone | 11 | 135 | 25 | East | ELW08
129087 | 2014-06-05 | Scheduled Outage | Maintenance | Leaking transformer replaced. BLKF4 Eastpark | None | Padmount (1ph) | 13 | 640 | 139 | East | BLKF3
129089 | 2014-06-06 | Scheduled Outage | Construction | To replace defective transformer. | None | None | 12 | 185 | 37 | East | BLKF3
129090 | 2014-06-06 | Scheduled Outage | Construction | Repair defective cable caused by a dig in. | None | None | 1 | 112 | 2 | Central | TR2TS
129091 | 2014-06-06 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X39694 at 81 Stinson Ave. refused due to animal contact. | O/H Transformer | O/H Transformer (1ph) | 5 | 74 | 6 | South | 200F3
129093 | 2014-06-06 | Scheduled Outage | Maintenance | Transformer X27632 at 120 Carruthers Ave. isolated for crew to change arrestor, switch and bracket. | None | None | 7 | 40 | 5 | Central | TH11-NIU
129094 | 2014-06-06 | Human Element | Switching Error | switching error. | None | None | 191 | 5 | 16 | West | BRDF1
129095 | 2014-06-06 | Scheduled Outage | Maintenance | Transformer X26671 at 104 Pinhey St. isolated so crew could change porcelain switch and arrestor. | None | None | 9 | 67 | 10 | Central | TH11-NIU
129096 | 2014-06-06 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X29111 at 881 Smyth Rd. refused by crew due to animal contact - squirrel | O/H Transformer | O/H Transformer (1ph) | 14 | 70 | 16 | East | TB15
129097 | 2014-06-06 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X26866 at 2126 Arch St. refused by crew due to animal contact - squirrell | O/H Transformer | O/H Transformer (1ph) | 12 | 71 | 14 | East | TB06
129098 | 2014-06-06 | Foreign Interference | Crane | Boom truck struck overhead wires. | O/H Conductor | O/H Conductor | 9 | 71 | 11 | East | 4801F8
129098 | 2014-06-06 | Foreign Interference | Crane | Boom truck struck overhead wires. | O/H Conductor | O/H Conductor | 105 | 64 | 112 | East | 4801F8
129101 | 2014-06-07 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27840 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 19 | 46 | 15 | Central | TH06
129102 | 2014-06-08 | Scheduled Outage | Maintenance | Customer vault maintenance. | None | Unknown \ Other | 1 | 325 | 5 | Central | 624
129103 | 2014-06-08 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X29817 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 6 | 39 | 4 | Central | TR09
129104 | 2014-06-08 | Foreign Interference | Wildlife (Bird/Animal) | REFUSED SWITCH FEEDING TRANSFORMER X21491 (FOUND BLOWN DUE TO SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 8 | 99 | 13 | East | V11F2
129106 | 2014-06-09 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact. | O/H Conductor | O/H Conductor | 7 | 34 | 4 | South | 160F3
129108 | 2014-06-09 | Scheduled Outage | Maintenance | PT139 was isolated to allow crews to replace porelain cutouts on pole. | None | Insulator | 1 | 127 | 2 | Central | TH11-NIU
129109 | 2014-06-09 | Scheduled Outage | Construction | TP2853 at 2720 Richmond Rd. Isolated to allow crew to replace cutouts and reconnect service. | None | None | 1 | 52 | 1 | Central | TD05
129110 | 2014-06-09 | Scheduled Outage | Construction | TE352 at 31 Biscayne isolated to allow crews to replace the transformer and base. | None | Padmount (1ph) | 9 | 374 | 56 | South | 130F4
129112 | 2014-06-09 | Scheduled Outage | Construction | Transformer X32754 at 1136 Field St. isolated by contractor to transfer plant | None | None | 10 | 202 | 34 | Central | UW07
129113 | 2014-06-09 | Scheduled Outage | Maintenance | Transformer X29842 at 79 Fifth Ave. isolated by crew to do load balancing. | None | None | 6 | 60 | 6 | Central | SB05
129115 | 2014-06-09 | Scheduled Outage | Construction | Transformer X39297 at 211 Ethel St. isolated by crew to change a leaking transformer. | O/H Transformer | O/H Transformer (1ph) | 18 | 57 | 17 | East | AC14
129117 | 2014-06-10 | Scheduled Outage | Maintenance | V301 at 245 Cooper was isolated to allow contractor make repairs to vault ceiling and Hydro crew to rod spare duct.m 1 customer was affected for minutes. Gladstone (UX10). ID# 129117 | None | None | 1 | 482 | 8 | Central | UX10
129118 | 2014-06-10 | Scheduled Outage | Construction | UW03 W phase from S22909 to Eol was isoalted to allow crew to remove O/H from UW03 and transfer to UW07 circuit. 51 custoimers were affected for 500 minutes. Woodroffe (UW03). ID# 129118 | None | None | 51 | 500 | 425 | Central | UW03
129120 | 2014-06-10 | Scheduled Outage | Maintenance | Transformer TP9584. TP8413, TP8414, TP8415, TP8416, TP6348, TP8417 and TP8418 on Forest Valley were isolated to allow crew to replace elbows and inserts. 71 customers were affected for 130 minutes Billberry (77M5). ID# 129120 | None | None | 71 | 130 | 154 | East | 77M5
129121 | 2014-06-10 | Scheduled Outage | Construction | At 13:30, 27KV transformer TP7762 located at 16 Thesher was isolated to allow crews to replace leaking transformer. 10 customers affected for 85 minutes. Alexander (ALXF2) ID #129121 | U/G Transformer | Padmount (1ph) | 10 | 85 | 14 | West | ALEXF2
129123 | 2014-06-10 | Scheduled Outage | Maintenance | Transformer X26853 at 2130 Balharrie Ave. isolated by crew to replace switch | None | None | 6 | 157 | 16 | East | AE01
129124 | 2014-06-10 | Scheduled Outage | Maintenance | Transformer X13229 at 489 Rideau Rd. isolated by crew to replace switch | None | None | 5 | 68 | 6 | East | 7F4
129125 | 2014-06-10 | Scheduled Outage | Maintenance | Transformer X30939 at 244 Wilbrod St. isolated by crew for load balancing | None | None | 10 | 34 | 6 | Central | UN03
129126 | 2014-06-10 | Defective Equipment | Electrical Failure | Not yet known. | Vault Equipment | Switch | 1 | 35 | 1 | Central | AB06
129127 | 2014-06-10 | Scheduled Outage | Maintenance | change O/H swtiches repair hot elbow connection and change insert at P56. | None | None | 1 | 138 | 2 | Central | AK06
129128 | 2014-06-11 | Scheduled Outage | Construction | Transformer TE349 at 59 Assiniboine was isolated to allow crew to replace elbows and inserts and install new transformer and base. 13 customers were affected for 300 minutes. Borden Farm (130F4). ID# 129128 | None | None | 13 | 300 | 65 | South | 130F4
129129 | 2014-06-11 | Scheduled Outage | Vegetation Management | SM03 O/H section on Mayfair and Piccadilly was isolated was isolated to allow forestry crew to remove to remove branch over line and HOL crew to replace switch on transformers. 36 customers were affected for 192 minutes. Carling (SM03). ID# 129129 | None | None | 36 | 192 | 115 | Central | SM03
129130 | 2014-06-11 | Scheduled Outage | Maintenance | At 09:30, 8KV transforme at 4326 Stella was isolated to allow crews to relocate transformer. 7 customers affected for 250 minutes. Startop (6F10) ID #129130 | None | None | 7 | 250 | 29 | East | 6F10
129131 | 2014-06-11 | Defective Equipment | Defective Equipment/ Material | Patrol found Blown arrestor at 1035 march. 1 customer affecetd for 122 minutes. Marchwood (624F6) ID #129131 repaired under PC10a #8350 by Jeff D'Aoust | Pole Attachement | Arrester | 1 | 122 | 2 | West | 624F6
129132 | 2014-06-11 | Scheduled Outage | Vegetation Management | Transformer at 58 Crichton was isolated to allow crew to remove tree due to close proximity to Hydro wires. 2 customers were affected for 112 minuites. Vaughn (UG02). ID# 129132 | None | None | 2 | 112 | 4 | East | UG02
129134 | 2014-06-11 | Scheduled Outage | Construction | Temp 72 RWB to EOL on Cartier and Argyle was isolated to allow crew to reconfigure pole line and equipment. 30 customers were affected for 231 minutes. Gladstone (UX05). ID# 129134. | None | None | 30 | 231 | 116 | Central | UX05
129135 | 2014-06-11 | Scheduled Outage | Vegetation Management | Allow forestry to remove trees from line | None | None | 6 | 50 | 5 | East | UG06
129136 | 2014-06-11 | Scheduled Outage | Maintenance | At 13:30, 4KV O/H transformer X42503 at 191 Ethel was interupted for phase balancing. 20 customers affected for 10 minutes. Dagmar (AC02) ID #192136 | None | None | 20 | 10 | 3 | East | AC02
129137 | 2014-06-11 | Scheduled Outage | Maintenance | At 13:40, 4KV O/H transformer X39297 at 205 Ethel was interupted for phase balancing. 18 customers affected for 10 minutes. Dagmar (AC14) ID #129137 | None | None | 18 | 10 | 3 | East | AC14
129139 | 2014-06-11 | Scheduled Outage | Construction | Transformer X32756 at 1145 Bedbrooke St. isolated by contractor to transfer plant | None | None | 10 | 167 | 28 | Central | UW03
129140 | 2014-06-11 | Scheduled Outage | Maintenance | TV9914 at 90 Elgin St was isolated to allow contractor to clean vault after building construction. 1 Customer affected in planned outage for 134 mins. ID# 129140 on TK4TS circuit. | None | Customer-Owned | 1 | 116 | 2 | Central | TK4TSTS
129143 | 2014-06-12 | Defective Equipment | Mechanical Failure | Defective hot line clamp. | O/H Conductor | Hot-Line Clamp | 17 | 95 | 27 | West | 43F3
129144 | 2014-06-12 | Defective Equipment | Mechanical Failure | Primary drop at X32862 contacting neutral. | O/H Conductor | O/H Conductor | 17 | 80 | 23 | South | 170F1
129144 | 2014-06-12 | Defective Equipment | Mechanical Failure | Primary drop at X32862 contacting neutral. | O/H Conductor | O/H Conductor | 73 | 85 | 103 | South | 170F1
129145 | 2014-06-12 | Scheduled Outage | Maintenance | REPLACED BLOWN ARRESTER AND SWITCH FEEDING TRANSFORMER X32990 | None | None | 10 | 35 | 6 | West | 28F2
129146 | 2014-06-12 | Tree Contacts | Falling Tree | Fallen tree at 2723 Flannery Dr. Caused UZ06 and UZ07 breakers opened. | O/H Conductor | O/H Conductor | 234 | 524 | 2044 | East | UZ07
129146 | 2014-06-12 | Tree Contacts | Falling Tree | Fallen tree at 2723 Flannery Dr. Caused UZ06 and UZ07 breakers opened. | O/H Conductor | O/H Conductor | 654 | 524 | 5712 | East | UZ06
129147 | 2014-06-13 | Scheduled Outage | Maintenance | To allow crews to repair secondary mole set in MH1061. 10 customers affected in planned power outage for 172 mins on 413 circuit ID# 129147. | None | Elbow \ Insert | 10 | 170 | 28 | Central | 413
129148 | 2014-06-13 | Scheduled Outage | Maintenance | CB1 & CB7 at VTM644CHZ was opened to allow contractor to preform internal switching. One customer affected for 67 mins. On 5211 circuit ID#129148. | None | Customer-Owned | 1 | 64 | 1 | Central | 5211
129149 | 2014-06-13 | Defective Equipment | Electrical Failure | Cable fault between TP7593 & TP7594 | U/G Cable | XLPE | 60 | 27 | 27 | East | 77M6
129149 | 2014-06-13 | Defective Equipment | Electrical Failure | Cable fault between TP7593 & TP7594 | U/G Cable | XLPE | 90 | 53 | 80 | East | 77M6
129150 | 2014-06-14 | Defective Equipment | Defective Equipment/ Material | The Richmond South Station transformer opened due to animal contact with transformer secondary insulators. Ricmond South (S7M). ID# 129150 | Station Equipment | Arrester | 95 | 59 | 93 | West | 28F1
129150 | 2014-06-14 | Defective Equipment | Defective Equipment/ Material | The Richmond South Station transformer opened due to animal contact with transformer secondary insulators. Ricmond South (S7M). ID# 129150 | Station Equipment | Arrester | 115 | 23 | 44 | West | 28F1
129150 | 2014-06-14 | Defective Equipment | Defective Equipment/ Material | The Richmond South Station transformer opened due to animal contact with transformer secondary insulators. Ricmond South (S7M). ID# 129150 | Station Equipment | Arrester | 183 | 59 | 180 | West | 28F3
129150 | 2014-06-14 | Defective Equipment | Defective Equipment/ Material | The Richmond South Station transformer opened due to animal contact with transformer secondary insulators. Ricmond South (S7M). ID# 129150 | Station Equipment | Arrester | 219 | 33 | 120 | West | 28F3
129150 | 2014-06-14 | Defective Equipment | Defective Equipment/ Material | The Richmond South Station transformer opened due to animal contact with transformer secondary insulators. Ricmond South (S7M). ID# 129150 | Station Equipment | Arrester | 721 | 59 | 709 | West | 28F2
129150 | 2014-06-14 | Defective Equipment | Defective Equipment/ Material | The Richmond South Station transformer opened due to animal contact with transformer secondary insulators. Ricmond South (S7M). ID# 129150 | Station Equipment | Arrester | 1047 | 23 | 401 | West | 28F2
129151 | 2014-06-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X29893 at 318 Fifth Ave. refused by 245/7 due to animal contact | O/H Transformer | O/H Transformer (1ph) | 13 | 75 | 16 | Central | TR09
129152 | 2014-06-14 | Scheduled Outage | Maintenance | Vault Maintenance | None | None | 1 | 217 | 4 | Central | 408
129154 | 2014-06-15 | Foreign Interference | Wildlife (Bird/Animal) | SC8233-CB4 opened due to squirel contact at 481 Sunnyside | U/G Switchgear | Gas-Insulated Dead Front | 686 | 63 | 720 | Central | TR3UY
129155 | 2014-06-16 | Defective Equipment | Defective Equipment/ Material | G474 B phase opened due to cable fault between TE810 and TE811. | U/G Cable | XLPE | 32 | 22 | 12 | East | LTM01
129155 | 2014-06-16 | Defective Equipment | Defective Equipment/ Material | G474 B phase opened due to cable fault between TE810 and TE811. | U/G Cable | XLPE | 42 | 98 | 69 | East | LTM01
129156 | 2014-06-16 | Scheduled Outage | Maintenance | Transformer TP2309 isolated to make secondary repairs. | None | None | 15 | 265 | 66 | West | RHNF1
129157 | 2014-06-16 | Scheduled Outage | Maintenance | 11 transformers isolated for elbow and insert replacement. | None | Padmount (1ph) | 79 | 280 | 369 | East | 77M5
129158 | 2014-06-16 | Scheduled Outage | Construction | 7 transformers, X35958, X33787, X33788, X33789, X32793, X32794, X35097 isolated by crews to transfer load (per Tim Connell all were opened at the same time from several different crews) | None | None | 57 | 60 | 57 | Central | UW03
129159 | 2014-06-16 | Scheduled Outage | Construction | Transformer #X34831 isolated by crew to disconnect a service | None | None | 14 | 30 | 7 | Central | SB05
129160 | 2014-06-16 | Scheduled Outage | Maintenance | Transformer #X17675 isolated by crew to replace connections on open buss | None | None | 8 | 45 | 6 | East | 4801F8
129161 | 2014-06-16 | Scheduled Outage | Maintenance | Transformer #X27621 isolated by crew re:phase re-balancing | None | None | 16 | 65 | 17 | Central | UN11
129163 | 2014-06-16 | Defective Equipment | Defective Equipment/ Material | BRDF3 27.6 kV conductor fell into the BRDF7 8kV conductor tripping off the entire Bridlewood Station | O/H Conductor | Sleeve | 431 | 88 | 632 | West | BRDF7
129163 | 2014-06-16 | Defective Equipment | Defective Equipment/ Material | BRDF3 27.6 kV conductor fell into the BRDF7 8kV conductor tripping off the entire Bridlewood Station | O/H Conductor | Sleeve | 871 | 93 | 1350 | West | BRDF5
129163 | 2014-06-16 | Defective Equipment | Defective Equipment/ Material | BRDF3 27.6 kV conductor fell into the BRDF7 8kV conductor tripping off the entire Bridlewood Station | O/H Conductor | Sleeve | 940 | 93 | 1457 | West | BRDF6
129163 | 2014-06-16 | Defective Equipment | Defective Equipment/ Material | BRDF3 27.6 kV conductor fell into the BRDF7 8kV conductor tripping off the entire Bridlewood Station | O/H Conductor | Sleeve | 4190 | 57 | 3980 | West | BRDF3
129163 | 2014-06-16 | Defective Equipment | Defective Equipment/ Material | BRDF3 27.6 kV conductor fell into the BRDF7 8kV conductor tripping off the entire Bridlewood Station | O/H Conductor | Sleeve | 5171 | 102 | 8791 | West | BRDF1
129164 | 2014-06-16 | Foreign Interference | Wildlife (Bird/Animal) | Crow came in contact with primary at G986 1600 St. Joseph causing the 77M5 breaker to trip | None | None | 1549 | 6 | 155 | East | 77M5
129165 | 2014-06-17 | Scheduled Outage | Maintenance | Transformer #X14141 isolated by crew to replace connections at the transformer | None | None | 3 | 30 | 2 | East | 7F4
129166 | 2014-06-17 | Scheduled Outage | Maintenance | At 10:18 am, transformer TP6456 at 94 Knollsbrook was isolated to allow crew to replace transformer. 9 customers were interrupted for 106 minutes. Barrhaven (140F1) ID# 129166. | None | None | 9 | 106 | 16 | South | 140F1
129167 | 2014-06-17 | Scheduled Outage | Maintenance | Transformer #X44639 isolated by crew to repair neutral on transformer | None | None | 21 | 25 | 9 | East | 77M6
129168 | 2014-06-17 | Scheduled Outage | Maintenance | 11 transformers in the MEADOWFIELD Pl were isolated to allow the crews preform elbow and inserts changes. | None | Elbow \ Insert | 105 | 198 | 346 | East | 77M5
129169 | 2014-06-17 | Scheduled Outage | Construction | K-Line pole replacement off switch S12843 north of Iris 31 customers transferred from UW03 to UW07 | None | Pole | 31 | 441 | 228 | Central | UW03
129170 | 2014-06-18 | Foreign Interference | Wildlife (Bird/Animal) | An animal contact on the O/H at 988 Pinecrest Rd cause the W phase fuse to blow at S17474 at the rear 2620 MONCTON RD | O/H Switchgear | Fused Cutout | 210 | 81 | 284 | Central | TD05
129171 | 2014-06-18 | Scheduled Outage | Maintenance | At 9:28 am, transformer TE932 at 1103 Burgundy was isolated to allow crew to do some oil clean up. 10 customer were interrupted for 548 minutes. Bilberry (77M6) ID# 129171. | None | None | 10 | 548 | 91 | East | 77M6
129172 | 2014-06-18 | Scheduled Outage | Construction | At 9:18 am, Transformer X35838 at 230 Viewmount was isolated to allow crew to install new poles. 2 customers were interrupted for 409 minutes. Borden Farms (130F1) ID# 129172. | None | None | 2 | 409 | 14 | South | 130F1
129173 | 2014-06-18 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X39505 opened up due to tree contact | O/H Switchgear | Inline Switch | 1 | 125 | 2 | West | 624F6
129174 | 2014-06-18 | Scheduled Outage | Maintenance | At 9:40 am, transformer TP6398 at 78 Knollsbrook was isolated to allow crew to replace transformer. 10 customers were interrupted for 123 minutes. Barrhaven (140F1) ID# 129174. | None | None | 10 | 123 | 20 | South | 140F1
129175 | 2014-06-18 | Scheduled Outage | Construction | Transformer #X35389 isolated by crew for a new service | None | None | 8 | 55 | 7 | Central | TD12
129176 | 2014-06-18 | Scheduled Outage | Construction | Transformer #X27300 isolated by crew for a service upgrade | None | None | 11 | 51 | 9 | East | UZ12
129177 | 2014-06-18 | Scheduled Outage | Construction | At 9:05 am, switch S29653 to end of line was isolated to allow crew to re-insulate line. 33 customers were interrupted for 212 minutes. Munster (43F2) ID# 129177. | None | None | 33 | 212 | 117 | West | 43F2
129178 | 2014-06-18 | Scheduled Outage | Maintenance | V721 isolated for customer vault maintenance 1 customer performed by Carleton Electric. SA22 circuit | None | None | 1 | 247 | 4 | Central | SA23
129179 | 2014-06-18 | Scheduled Outage | Maintenance | Transformer #X32095 isolated by crew to replace porcelain cut out | None | None | 7 | 110 | 13 | Central | TD01
129180 | 2014-06-18 | Scheduled Outage | Maintenance | Transformer #X24896 isolated by crew to replace triplex and fly tap board | None | None | 7 | 75 | 9 | East | SO06
129181 | 2014-06-18 | Scheduled Outage | Vegetation Management | S17480 opened to allow forestry crew to remove 2 trees. 22 customers effected under PC10A# 4239 to Louie Lauzon. | None | O/H Conductor | 22 | 450 | 165 | East | TB2JP
129182 | 2014-06-18 | Scheduled Outage | Construction | S14906 opened to isolate overhead south at Iris & Checkers for pole and conductor replacement by K-Line Tim Connell. Load moved from UW03 to UW07 supply. | None | O/H Conductor | 40 | 490 | 327 | Central | UW03
129183 | 2014-06-18 | Scheduled Outage | Maintenance | allow contrator to install secondary metering. | None | None | 1 | 316 | 5 | East | 5310
129184 | 2014-06-18 | Scheduled Outage | Construction | decommisson transformer P6 and replace it with new TP9879 and new S17159 | None | None | 1 | 100 | 2 | East | UB03
129185 | 2014-06-19 | Defective Equipment | Defective Equipment/ Material | The RX2019 A/R and caused the S19837 B to open due to cable fault at 1705 Sunview dr. Billberry (77M6). ID# 129185 | U/G Cable | Unknown \ Other | 50 | 27 | 22 | East | 77M6
129185 | 2014-06-19 | Defective Equipment | Defective Equipment/ Material | The RX2019 A/R and caused the S19837 B to open due to cable fault at 1705 Sunview dr. Billberry (77M6). ID# 129185 | U/G Cable | Unknown \ Other | 166 | 103 | 285 | East | 77M6
129186 | 2014-06-19 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32282 opened up due to animal contact | O/H Switchgear | Fused Cutout | 10 | 101 | 17 | Central | TD01
129187 | 2014-06-19 | Scheduled Outage | Construction | At 10:20, 3 phase O/H transformer at 1220 baseline was isolated to allow crews to upgrade service bus. 2 customers affected for 10 minutes. Fisher (AK06) ID #129187 | None | None | 2 | 10 | 0 | Central | AK06
129188 | 2014-06-19 | Scheduled Outage | Maintenance | At 9:10 11 U/G transformers were isolated for elbow and insert replacement on Innes and Orleans Blvd. 89 customers affected. CYRF3 Cyrville DS. | None | None | 89 | 240 | 356 | East | CYRF3
129189 | 2014-06-19 | Scheduled Outage | Construction | Transformer #X17759 isolated by crew to re-arrange secondary | None | None | 14 | 85 | 20 | East | 4801F8
129190 | 2014-06-19 | Scheduled Outage | Maintenance | Transformer #X09180 isolated by crew to replace defective switch for maintenance | None | None | 1 | 10 | 0 | West | BECKF2
129191 | 2014-06-19 | Scheduled Outage | Maintenance | Transformer #X09390 isolated by crew to replace defective switch for maintenance | None | None | 1 | 10 | 0 | West | BECKF2
129192 | 2014-06-19 | Defective Equipment | Mechanical Failure | At 22:02 crews isolated switch to K536 because the live line clamp was burning. 20 customers for 34 mins. Carling (SM15) | O/H Conductor | Hot-Line Clamp | 20 | 34 | 11 | Central | SM15
129193 | 2014-06-20 | Scheduled Outage | Maintenance | Contractor maintenance | None | None | 1 | 295 | 5 | Central | 5211
129194 | 2014-06-20 | Scheduled Outage | Maintenance | Not yet known. | None | None | 2 | 359 | 12 | Central | AK06
129195 | 2014-06-20 | Scheduled Outage | Vegetation Management | At 08:50, O/H radial feed at 17 Lucas lane was isolated to allow customer to trim trees. 1 customer affected for minutes. Beckwith (BECKF2) ID #129 | None | None | 1 | 370 | 6 | West | BECKF2
129196 | 2014-06-20 | Scheduled Outage | Construction | S26046 to EOL was isolated to allow crew to install new poles and transfer plant. 34 customers were affected for 276 minutes. Lincoln Heights (TD14) ID# 129196 | None | None | 34 | 276 | 156 | Central | TD14
129197 | 2014-06-20 | Scheduled Outage | Maintenance | Repair defective connections in secondary pedestal | Secondary \ Service | Secondary Pedestal | 3 | 120 | 6 | South | 190F6
129198 | 2014-06-21 | Defective Equipment | Defective Equipment/ Material | Suspected cable fault on the BRDF3 between SC4281 and S15729 caused the BRDT1 to open under protection and trip the circuit switcher 605-S7M. | U/G Cable Attachement | Arrester | 433 | 84 | 606 | West | BRDF7
129198 | 2014-06-21 | Defective Equipment | Defective Equipment/ Material | Suspected cable fault on the BRDF3 between SC4281 and S15729 caused the BRDT1 to open under protection and trip the circuit switcher 605-S7M. | U/G Cable Attachement | Arrester | 871 | 84 | 1219 | West | BRDF5
129198 | 2014-06-21 | Defective Equipment | Defective Equipment/ Material | Suspected cable fault on the BRDF3 between SC4281 and S15729 caused the BRDT1 to open under protection and trip the circuit switcher 605-S7M. | U/G Cable Attachement | Arrester | 940 | 84 | 1316 | West | BRDF6
129198 | 2014-06-21 | Defective Equipment | Defective Equipment/ Material | Suspected cable fault on the BRDF3 between SC4281 and S15729 caused the BRDT1 to open under protection and trip the circuit switcher 605-S7M. | U/G Cable Attachement | Arrester | 1496 | 43 | 1072 | West | BRDF1
129198 | 2014-06-21 | Defective Equipment | Defective Equipment/ Material | Suspected cable fault on the BRDF3 between SC4281 and S15729 caused the BRDT1 to open under protection and trip the circuit switcher 605-S7M. | U/G Cable Attachement | Arrester | 2050 | 109 | 3724 | West | BRDF4
129198 | 2014-06-21 | Defective Equipment | Defective Equipment/ Material | Suspected cable fault on the BRDF3 between SC4281 and S15729 caused the BRDT1 to open under protection and trip the circuit switcher 605-S7M. | U/G Cable Attachement | Arrester | 2142 | 80 | 2856 | West | BRDF3
129198 | 2014-06-21 | Defective Equipment | Defective Equipment/ Material | Suspected cable fault on the BRDF3 between SC4281 and S15729 caused the BRDT1 to open under protection and trip the circuit switcher 605-S7M. | U/G Cable Attachement | Arrester | 3872 | 43 | 2775 | West | BRDF2
129201 | 2014-06-21 | Scheduled Outage | Maintenance | Vault mtce clean and torque and service disconnects and breakers. Troy Wilson TL4TS | None | Breaker \ Relay | 1 | 137 | 2 | Central | TL4TS
129202 | 2014-06-22 | Scheduled Outage | Maintenance | Customer vault maintenance | None | None | 1 | 115 | 2 | Central | 5211
129203 | 2014-06-22 | Scheduled Outage | Construction | V282 at 168 Charlotte was isolated to allow crew to replace dip pole and cable to V282 affecting 1 customer for minutes, Augusta UD04, ID # 129203 | None | None | 1 | 248 | 4 | Central | UD04
129204 | 2014-06-22 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact inside SE26, Leikin Dr | U/G Switchgear | Live-Front | 1 | 23 | 0 | South | LGFF2
129204 | 2014-06-22 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact inside SE26, Leikin Dr | U/G Switchgear | Live-Front | 931 | 57 | 884 | South | LGFF2
129205 | 2014-06-22 | Defective Equipment | Defective Equipment/ Material | Not yet known.Transformer UCT2 triped on gas | Station Equipment | Transformer | 51 | 45 | 38 | Central | UC07
129205 | 2014-06-22 | Defective Equipment | Defective Equipment/ Material | Not yet known.Transformer UCT2 triped on gas | Station Equipment | Transformer | 142 | 45 | 106 | Central | UC06
129205 | 2014-06-22 | Defective Equipment | Defective Equipment/ Material | Not yet known.Transformer UCT2 triped on gas | Station Equipment | Transformer | 297 | 45 | 223 | Central | UC05
129207 | 2014-06-23 | Scheduled Outage | Construction | PT73 at 1017 Prince of Wales was isolated to allow crew to replace a rusty padmount affecting 1 customer for 209 minutes, Carling TS 303, ID # 129207 | None | Padmount (3ph) | 1 | 209 | 3 | Central | 303
129208 | 2014-06-23 | Defective Equipment | Electrical Failure | cable fault between S51-2 & 00168R | U/G Cable | Unknown \ Other | 59 | 165 | 162 | West | BRDF4
129209 | 2014-06-23 | Defective Equipment | Electrical Failure | S29777 white phase fuse opened because of a blown lighten in K769 | U/G Cable Attachement | Arrester | 8 | 147 | 20 | East | UZ02
129210 | 2014-06-23 | Defective Equipment | Electrical Failure | Defective transformer MT1429 caused elbow to separate at MT1429 causing outage to remaining B phase Tx s. MT1429 replaced. | U/G Transformer | Padmount (1ph) | 15 | 278 | 70 | East | 2204
129210 | 2014-06-23 | Defective Equipment | Electrical Failure | Defective transformer MT1429 caused elbow to separate at MT1429 causing outage to remaining B phase Tx s. MT1429 replaced. | U/G Transformer | Padmount (1ph) | 196 | 90 | 294 | East | 2204
129211 | 2014-06-23 | Defective Equipment | Defective Equipment/ Material | faulty, old style cutouts. | O/H Switchgear | Fused Cutout | 1 | 213 | 4 | East | AN06
129212 | 2014-06-24 | Unknown/Other | Unknown | Circuit was patrolled and nothing was found | Unknown \ Other | Unknown \ Other | 931 | 35 | 543 | South | LGFF2
129213 | 2014-06-24 | Scheduled Outage | Construction | 4kV overhead circuit from TEMP19 to EOL on McLeod St. Was isolated to allow crew to transfer plant to new pole. | None | None | 71 | 270 | 320 | Central | UX06
129214 | 2014-06-24 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact. | O/H Transformer | O/H Transformer (1ph) | 9 | 27 | 4 | Central | TW22
129215 | 2014-06-24 | Defective Equipment | Defective Equipment/ Material | REPLACED CONNECTION AT THE PRIMARY BUSING ON TRANSFORMER X28235 | O/H Transformer | O/H Transformer (1ph) | 14 | 16 | 4 | Central | 505
129216 | 2014-06-24 | Defective Equipment | Defective Equipment/ Material | Hydro Ottawa crews reports blown lightening arrester at this location. Which caused a fireball between the white and blue phases. | U/G Cable Attachement | Arrester | 1 | 72 | 1 | East | 77M5
129216 | 2014-06-24 | Defective Equipment | Defective Equipment/ Material | Hydro Ottawa crews reports blown lightening arrester at this location. Which caused a fireball between the white and blue phases. | U/G Cable Attachement | Arrester | 1548 | 33 | 851 | East | 77M5
129218 | 2014-06-24 | Scheduled Outage | Construction | UW13 circuit isolated for voltage conversion from 4kV to 13kV. | None | O/H Conductor | 146 | 271 | 659 | Central | UW13
129218 | 2014-06-24 | Scheduled Outage | Construction | UW13 circuit isolated for voltage conversion from 4kV to 13kV. | None | O/H Conductor | 191 | 53 | 169 | Central | UW13
129219 | 2014-06-24 | Defective Equipment | Defective Equipment/ Material | The BCHF5 A/R/A due to defective insulator at 492 Tisdale and wrapped conductors at 709 Elmval. ID# 129219 | Pole Attachement | Insulator | 426 | 73 | 518 | East | BCHF5
129219 | 2014-06-24 | Defective Equipment | Defective Equipment/ Material | The BCHF5 A/R/A due to defective insulator at 492 Tisdale and wrapped conductors at 709 Elmval. ID# 129219 | Pole Attachement | Insulator | 496 | 57 | 471 | East | BCHF5
129219 | 2014-06-24 | Defective Equipment | Defective Equipment/ Material | The BCHF5 A/R/A due to defective insulator at 492 Tisdale and wrapped conductors at 709 Elmval. ID# 129219 | Pole Attachement | Insulator | 1275 | 56 | 1190 | East | BCHF5
129220 | 2014-06-24 | Defective Equipment | Defective Equipment/ Material | Transformer #X23374 opened up due to broken cut out | O/H Switchgear | Fused Cutout | 1 | 172 | 3 | Central | TK2AC
129221 | 2014-06-25 | Defective Equipment | Mechanical Failure | BCHF5 circuit dumped so crews could install jumper to repair defective inline switch G1031. Beaconhill (BCHF5) ID #129221 | O/H Switchgear | Inline Switch | 12 | 87 | 17 | East | BCHF5
129221 | 2014-06-25 | Defective Equipment | Mechanical Failure | BCHF5 circuit dumped so crews could install jumper to repair defective inline switch G1031. Beaconhill (BCHF5) ID #129221 | O/H Switchgear | Inline Switch | 1275 | 11 | 234 | East | BCHF5
129222 | 2014-06-25 | Tree Contacts | Falling Tree | Wire down accross the Rideau River due to large tree fallen on the O/H accross from Nicolls Island | O/H Conductor | O/H Conductor | 22 | 449 | 165 | East | 7F2
129223 | 2014-06-25 | Scheduled Outage | Construction | UX06 overhead circuit from TEMP 43 to EOL on Mcleod St. Was isolate to allow crews to transfer plant to new poles. | None | O/H Conductor | 29 | 326 | 158 | Central | UX06
129224 | 2014-06-25 | Scheduled Outage | Construction | At 9:30 am, transformer TP3274 at 188 Meandering Brook to allow crew to install new secondary. 20 customers were interrupted for minutes. Leitrim (249F1) ID# 129224. | None | None | 20 | 279 | 93 | East | LTM01
129225 | 2014-06-25 | Scheduled Outage | Construction | To replace transformer and base. | None | Padmount (1ph) | 11 | 420 | 77 | South | 190F6
129226 | 2014-06-25 | Scheduled Outage | Construction | 4kV vault V769 isolated to allow crew to prove spare duct for future work | None | Cable | 1 | 46 | 1 | Central | UX08
129227 | 2014-06-25 | Human Element | Switching Error | RX2010 tripped under hold-off during switching due to a live elbow making contact with a concentric neutral. | None | None | 1624 | 2 | 54 | West | ALEXF3
129227 | 2014-06-25 | Human Element | Switching Error | RX2010 tripped under hold-off during switching due to a live elbow making contact with a concentric neutral. | None | None | 3615 | 45 | 2711 | West | ALEXF3
129229 | 2014-06-25 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X38617 TO REPLACE SWITCH AND ARRESTER | None | None | 2 | 5 | 0 | West | BECKF2
129230 | 2014-06-25 | Scheduled Outage | Construction | Transformer #X32086 isolated by crew for a service upgrade | None | None | 6 | 20 | 2 | Central | SM15
129231 | 2014-06-25 | Scheduled Outage | Construction | 2 Transformers, #X35089 and X47533 isolated by crew to transfer plant | None | None | 15 | 210 | 52 | Central | UW07
129232 | 2014-06-25 | Scheduled Outage | Construction | Transformer #X30203 isolated by crew to change the feed. | None | None | 16 | 10 | 3 | Central | UL06
129233 | 2014-06-25 | Scheduled Outage | Construction | Transformer #X30205 isolated by crew to change the feed | None | None | 21 | 6 | 2 | Central | UL06
129236 | 2014-06-26 | Scheduled Outage | Construction | At 9:25 am, Transformer TP7428 at 613C Chapman Mills was isolated to allow crew to re-arrange plant. 34 customers were interrupted for 266 minutes. Fallowfield (FAL02) ID# 129236. | None | None | 34 | 266 | 151 | South | FAL02
129237 | 2014-06-26 | Scheduled Outage | Construction | At 9:40 am, transformer TE364 was isolated to allow crew to replace transformer. 20 customers were interrupted for 410 minutes. Parkwood Hills (130F4) ID# 129237. | None | None | 20 | 410 | 137 | South | 130F4
129238 | 2014-06-26 | Tree Contacts | Tree Growth/ Untrimmed Tree | Trees in the O/H @ 979 PRINCE OF WALES DR caused the R phase fuse to blow in the SC21. | None | None | 41 | 209 | 143 | Central | 303
129240 | 2014-06-26 | Scheduled Outage | Construction | The AJ03 O/H on Sharel from S29124 was isolated to allow the crews to install new poles. | None | Pole | 36 | 360 | 216 | East | AJ03
129241 | 2014-06-26 | Scheduled Outage | Maintenance | Transformer TV0181-T1 at 25 Murray St. isolated by crew to replace connections on transformer | None | None | 36 | 170 | 102 | Central | UD05
129246 | 2014-06-27 | Scheduled Outage | Maintenance | Planned outage for Hydro Ottawa crew to replace NX fusing at S16686, 1 customer | None | Fused Cutout | 1 | 58 | 1 | East | AN05
129247 | 2014-06-27 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X23567 TO REPLACE OPEN WIRE SECONDARY BUSS | None | None | 10 | 195 | 32 | East | SO02
129249 | 2014-06-27 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X40863 TO REPLACE OPEN WIRE SERVICE | None | None | 16 | 50 | 13 | East | TA3AF
129250 | 2014-06-27 | Defective Equipment | Defective Equipment/ Material | 72F2 auto-reclosed and S801 blew. Blown Blue phase cable section between S871B and TE427. | U/G Cable | XLPE | 113 | 50 | 94 | South | 72F2
129250 | 2014-06-27 | Defective Equipment | Defective Equipment/ Material | 72F2 auto-reclosed and S801 blew. Blown Blue phase cable section between S871B and TE427. | U/G Cable | XLPE | 113 | 138 | 260 | South | 72F2
129251 | 2014-06-27 | Defective Equipment | Mechanical Failure | Transformer X5604 at 50 Bentley Ave. isolated so crew could replace connections at pole and at standpipe | Secondary \ Service | O/H Service | 5 | 66 | 6 | South | 180F6
129252 | 2014-06-27 | Defective Equipment | Electrical Failure | Defective transformer X36008 at 47 St. Claire Ave. removed and replaced | O/H Transformer | O/H Transformer (1ph) | 12 | 151 | 30 | South | EPWF1
129253 | 2014-06-27 | Defective Equipment | Defective Equipment/ Material | Red phase cable fault between TP8255 @ 6351 Mattice and TP8254 @ 6361 Mattice. 149 Customers affected in power outage for 141 mins. On 77M2 circuit ID# 129253. | U/G Cable | XLPE | 149 | 122 | 303 | East | 77M2
129254 | 2014-06-28 | Defective Equipment | Defective Equipment/ Material | A second cable fault caused the S29837 R to open. Billberry (77M2). ID# 129254 | U/G Cable | XLPE | 23 | 657 | 252 | East | 77M2
129254 | 2014-06-28 | Defective Equipment | Defective Equipment/ Material | A second cable fault caused the S29837 R to open. Billberry (77M2). ID# 129254 | U/G Cable | XLPE | 57 | 175 | 166 | East | 77M2
129256 | 2014-06-28 | Scheduled Outage | Maintenance | change leaking transformer. | None | Padmount (3ph) | 1 | 195 | 3 | East | AL10
129258 | 2014-06-28 | Tree Contacts | Other Vegetation | Vines growing on the O/H on Farmer's Way caused the G540R to open. 49 customers were affected for 54 minutes. Leitrim (249F2). ID# 129258 | O/H Switchgear | Fused Cutout | 49 | 54 | 44 | East | 249F2
129259 | 2014-06-29 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X20853 at 1908 Oakdean opened due to animal contact. 12 customers were affected for 75 minutes. Beaconhill (BCHF3). ID#129259 | O/H Transformer | O/H Transformer (1ph) | 12 | 75 | 15 | East | BCHF3
129260 | 2014-06-29 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X24503 opened up due to animal contact | O/H Switchgear | Fused Cutout | 5 | 137 | 11 | East | TB07
129261 | 2014-06-29 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27511 opened up due to animal contact | O/H Switchgear | Fused Cutout | 7 | 131 | 15 | East | TB06
129262 | 2014-06-29 | Scheduled Outage | Maintenance | Transformer 3573 at 77 Morton was isolated to allow crew to repalce leaking transformer. 10 customers were affected for 134 minutes. Bridlewood (BRDF7). ID# 129262 | None | Padmount (1ph) | 10 | 134 | 22 | West | BRDF7
129263 | 2014-06-29 | Tree Contacts | Other Vegetation | Transformer #NP3196 opened up due to vine interference | O/H Switchgear | Fused Cutout | 5 | 153 | 13 | South | 200F1
129264 | 2014-06-29 | Tree Contacts | Tree Growth/ Untrimmed Tree | At 4:33 pm , transformer X33549 at 209 Wilshire opened due to overgown trees on secondary. 10 customers were affected for 95 minutes. Fisher (AK02). ID# 129264 | O/H Transformer | O/H Transformer (1ph) | 10 | 95 | 16 | Central | AK02
129265 | 2014-06-30 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X41275 opened up due to animal contact | O/H Switchgear | Fused Cutout | 17 | 52 | 15 | Central | 505
129266 | 2014-06-30 | Scheduled Outage | Maintenance | 11 B phase transformers on CYRF3 iasolated for insery and elbow replacement | None | Elbow \ Insert | 94 | 164 | 257 | East | CYRF3
129267 | 2014-06-30 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X19945 opened up due to animal contact | O/H Switchgear | Fused Cutout | 4 | 99 | 7 | East | 249F2
129268 | 2014-06-30 | Scheduled Outage | Construction | Transformer #X33862 isolated by crew to run a new service | None | None | 13 | 40 | 9 | Central | UJ02
129269 | 2014-06-30 | Defective Equipment | Defective Equipment/ Material | V405 at 474 Holland was isolated to allow crew to replace brken fuse in vault. 3 customers were affected for 11 minutes. Holland (SH02). ID# 129269 | Vault Equipment | Unknown \ Other | 3 | 11 | 1 | Central | SH02
129270 | 2014-07-01 | Scheduled Outage | Maintenance | SW1498 isolated for SF6 top-up. TO2UT | None | None | 1 | 130 | 2 | East | TO2UT
129271 | 2014-07-01 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One BECKF2 circuit | None | None | 2 | 97 | 3 | West | BECKF2
129271 | 2014-07-01 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One BECKF2 circuit | None | None | 646 | 45 | 484 | West | BECKF2
129272 | 2014-07-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | Refused transformer X23328 at 751 Borthwick Ave. - cause - tree contact | O/H Transformer | O/H Transformer (1ph) | 17 | 54 | 15 | East | AP03
129273 | 2014-07-01 | Defective Equipment | Electrical Failure | suspected cable fault between VT575 and VT267 on the 415 cable. | U/G Cable | PILC | 473 | 90 | 710 | Central | 415
129274 | 2014-07-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | Trees caused the fuse to blow that feeds transformer X39481 @ 723 Fraser Ave, TD01 | O/H Transformer | O/H Transformer (1ph) | 10 | 225 | 38 | Central | TD01
129276 | 2014-07-01 | Defective Equipment | Defective Equipment/ Material | A defective elbow at Transformer TE2824 caused the 210F1 to A/R. | U/G Cable Attachement | Elbow \ Insert | 12 | 39 | 8 | South | LGFF1
129276 | 2014-07-01 | Defective Equipment | Defective Equipment/ Material | A defective elbow at Transformer TE2824 caused the 210F1 to A/R. | U/G Cable Attachement | Elbow \ Insert | 66 | 104 | 114 | South | LGFF1
129277 | 2014-07-01 | Defective Equipment | Defective Equipment/ Material | V0117 has one defective transformer that needs replacing. On call brought in to replace transformer. Old age residence (190 people) | Vault Equipment | Transformer | 1 | 201 | 3 | Central | UW05
129278 | 2014-07-01 | Foreign Interference | Wildlife (Bird/Animal) | Transfomer X27079 fuse blown due to racoon contact. Fuse replaced. | O/H Transformer | O/H Transformer (1ph) | 7 | 231 | 27 | East | TB14
129279 | 2014-07-02 | Scheduled Outage | Construction | To allow K-line to change poles & re-configure the O/H | None | None | 16 | 360 | 96 | Central | UW07
129279 | 2014-07-02 | Scheduled Outage | Construction | To allow K-line to change poles & re-configure the O/H | None | None | 70 | 144 | 168 | Central | UW07
129280 | 2014-07-02 | Scheduled Outage | Construction | At 9:18am crews isolated TP8509 to replace leaking transformer. 12 customers affected for 102 mins. Bilberry (77M5) ID# 129280. | U/G Transformer | Padmount (1ph) | 12 | 102 | 20 | East | 77M5
129281 | 2014-07-02 | Scheduled Outage | Construction | At 10:04am crew isolated TE1695 to replace leaking transformer. 12 customers affected for 112 mins. Centrepoint 87F3 ID#129281 | U/G Transformer | Padmount (1ph) | 12 | 112 | 22 | South | 87F3
129282 | 2014-07-02 | Scheduled Outage | Construction | At 10:32 am, transformer TE1121 at 224 Viewmount was isolated to allow crew to reconfigure underground cables. 1 customer was interupted for 359 minutes. Parkwood Hills (190F6) ID# 129282. | None | None | 1 | 359 | 6 | South | 190F6
129283 | 2014-07-02 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X32417 in front of 917 Richmond Rd. refused due to animal contact | O/H Transformer | O/H Transformer (3ph) | 1 | 64 | 1 | Central | TD01
129284 | 2014-07-02 | Scheduled Outage | Maintenance | Transformer X40150 at 2 Wild Acre Lane isolated by crew to replace defective switch | None | None | 2 | 72 | 2 | West | MWDF3
129285 | 2014-07-02 | Scheduled Outage | Construction | Replace leaking transformer | U/G Transformer | Padmount (1ph) | 12 | 117 | 23 | South | 87F3
129287 | 2014-07-02 | Tree Contacts | Broken Branch | REPLACED BLOWN FUSE FEED TRANSFORMER X34603 CAUSED BY TREE BRANCH DUE TO STORM | O/H Transformer | O/H Transformer (1ph) | 3 | 100 | 5 | East | CYRF3
129288 | 2014-07-03 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X26692 at 21 Craig St. due to animal contact - squirrel | None | None | 8 | 80 | 11 | Central | TR09
129289 | 2014-07-03 | Scheduled Outage | Maintenance | Elbow and insert replacement. | None | None | 101 | 199 | 335 | East | CYRF3
129290 | 2014-07-03 | Scheduled Outage | Maintenance | To remove transformer from the base, and remove sand in the transformer base. | None | Padmount (1ph) | 10 | 137 | 23 | West | BRDF1
129293 | 2014-07-03 | Scheduled Outage | Construction | 4kV transfomrer X30809 isolated to allow crew to frame new pole. | None | Crossarm | 7 | 47 | 5 | Central | UX09
129294 | 2014-07-04 | Foreign Interference | Wildlife (Bird/Animal) | Squirel contact cause the TR2UY to trip open and the SC8233-CB4 to trip open. | U/G Cable Attachement | Pothead | 1 | 57 | 1 | Central | TR2UY
129294 | 2014-07-04 | Foreign Interference | Wildlife (Bird/Animal) | Squirel contact cause the TR2UY to trip open and the SC8233-CB4 to trip open. | U/G Cable Attachement | Pothead | 466 | 47 | 365 | Central | TR3UY
129295 | 2014-07-04 | Scheduled Outage | Maintenance | Transformer X33145 at 8586 Copeland Rd. isolated for crew to replace defective switch. | None | Fused Cutout | 1 | 24 | 0 | West | BECKF2
129298 | 2014-07-04 | Scheduled Outage | Maintenance | Transformer X33287 at 8555 Copeland Rd. isolated by crew to replace defective switch | None | Fused Cutout | 1 | 54 | 1 | West | BECKF2
129299 | 2014-07-04 | Foreign Interference | Foreign Objects | UW05 auto-reclosed and locked out. UW00 tripped at same time. | None | None | 255 | 41 | 174 | Central | UW05
129300 | 2014-07-04 | Scheduled Outage | Maintenance | At 12:48 pm, switch S11146 was isolated to allow crew to replace switches. 2 customers were interrupted for 95 minutes. Alexander DS (ALXF2) ID# 129300. | None | None | 2 | 95 | 3 | West | ALEXF2
129302 | 2014-07-05 | Defective Equipment | Electrical Failure | G369B fuse blew due to cable fault between G214B and TE389. | U/G Cable | XLPE | 25 | 131 | 55 | East | BLKF1
129303 | 2014-07-05 | Unknown/Other | Unknown | No apparent cause found | O/H Switchgear | Fused Cutout | 211 | 140 | 492 | East | AE05
129304 | 2014-07-05 | Foreign Interference | Wildlife (Bird/Animal) | Dead birds found at bottom of pole, animal guard installed, transformer refused. | O/H Transformer | O/H Transformer (1ph) | 1 | 204 | 3 | West | 43F2
129305 | 2014-07-06 | Defective Equipment | Electrical Failure | White phase cable fault between TE981 and TE1296. | U/G Cable | XLPE | 79 | 79 | 104 | East | 8F1
129307 | 2014-07-06 | Scheduled Outage | Maintenance | Tap change requested by James Robinson on transformers . | None | Padmount (3ph) | 1 | 10 | 0 | Central | TH1SH
129308 | 2014-07-06 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X39576 CAUSED BY SQUIRREL CONTACT | O/H Transformer | O/H Transformer (1ph) | 2 | 109 | 4 | West | 624F6
129309 | 2014-07-06 | Foreign Interference | Wildlife (Bird/Animal) | G608W fuse blew due to crow at X24753. | None | None | 31 | 79 | 41 | East | 8F1
129310 | 2014-07-06 | Scheduled Outage | Maintenance | The Palladium Bay #1 was isolated to all the contractor to perform vault maintenance. | None | Breaker \ Relay | 1 | 137 | 2 | West | 624F1
129311 | 2014-07-07 | Scheduled Outage | Construction | Service upgrade | None | None | 4 | 30 | 2 | Central | UW06
129312 | 2014-07-07 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32634 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 16 | 96 | 26 | Central | TD14
129313 | 2014-07-07 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X47545 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 13 | 180 | 39 | Central | UW07
129314 | 2014-07-07 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31735 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 14 | 167 | 39 | Central | UW07
129317 | 2014-07-08 | Defective Equipment | Electrical Failure | Fuse at S19308 failed and opened. | O/H Switchgear | Fused Cutout | 16 | 93 | 25 | Central | TD14
129320 | 2014-07-08 | Scheduled Outage | Construction | Plant upgrade, replace switches & cables to vault. | None | None | 1 | 312 | 5 | Central | UX06
129322 | 2014-07-08 | Scheduled Outage | Construction | Replace porcelain dip switches, S11396 | None | None | 1 | 65 | 1 | Central | TH11-NIU
129325 | 2014-07-08 | Tree Contacts | Tree Growth/ Untrimmed Tree | tree contact in Overbrook station yard. | O/H Conductor | O/H Conductor | 288 | 38 | 182 | East | SO10
129326 | 2014-07-08 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X09715 at 1237 Carp Rd. - animal contact | O/H Switchgear | Fused Cutout | 15 | 38 | 10 | West | JKGF4
129327 | 2014-07-08 | Human Element | Protection Setting | Under sized fuses at G296RW | O/H Switchgear | Fused Cutout | 80 | 42 | 56 | East | CYRF1
129329 | 2014-07-08 | Defective Equipment | Defective Equipment/ Material | RX2018 at 881 Champlain St failed during power outage on 77M6 circuit. | O/H Switchgear | Recloser (3ph) | 1588 | 48 | 1270 | East | 77M6
129329 | 2014-07-08 | Defective Equipment | Defective Equipment/ Material | RX2018 at 881 Champlain St failed during power outage on 77M6 circuit. | O/H Switchgear | Recloser (3ph) | 4833 | 18 | 1450 | East | 77M6
129329 | 2014-07-08 | Defective Equipment | Defective Equipment/ Material | RX2018 at 881 Champlain St failed during power outage on 77M6 circuit. | O/H Switchgear | Recloser (3ph) | 4833 | 25 | 2014 | East | 77M6
129330 | 2014-07-08 | Unknown/Other | Unknown | Circuit was patrolled no fault was found. S1059R was refused and closed restoring all load. Outage effected 42 customers on 200F3 circuit ID#129330. | Unknown \ Other | Unknown \ Other | 8 | 275 | 37 | South | 200F3
129330 | 2014-07-08 | Unknown/Other | Unknown | Circuit was patrolled no fault was found. S1059R was refused and closed restoring all load. Outage effected 42 customers on 200F3 circuit ID#129330. | Unknown \ Other | Unknown \ Other | 42 | 120 | 84 | South | 200F3
129331 | 2014-07-08 | Unknown/Other | Unknown | Fuse at S18943 opened, cause unknown. | None | None | 1 | 354 | 6 | West | BECKF2
129332 | 2014-07-09 | Foreign Interference | Wildlife (Bird/Animal) | Fuse at transfomrer X31948 opened due to animal contact. | O/H Transformer | O/H Transformer (1ph) | 2 | 81 | 3 | Central | TD14
129334 | 2014-07-09 | Scheduled Outage | Vegetation Management | Clearance for customer contractor removing trees. | None | None | 56 | 328 | 306 | Central | TD01
129336 | 2014-07-09 | Scheduled Outage | Construction | Pole & cable replacement | None | None | 11 | 263 | 48 | Central | UX08
129337 | 2014-07-09 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X23193 TO TRANSFER HYDRO PLANT | None | None | 27 | 180 | 81 | East | AC15
129338 | 2014-07-09 | Scheduled Outage | Maintenance | Elbow & insert replacement and replace G762 RWB | None | Elbow \ Insert | 97 | 242 | 391 | East | CYRF3
129339 | 2014-07-09 | Scheduled Outage | Maintenance | replace defective elbow and insert | None | Elbow \ Insert | 9 | 75 | 11 | South | 140F3
129340 | 2014-07-09 | Scheduled Outage | Construction | Transformer X48562 at 2144 Irist St. isolated by contractor to transfer plant. | None | None | 12 | 220 | 44 | Central | UW07
129341 | 2014-07-10 | Scheduled Outage | Construction | At 12:07 am, transformers 8358, TP10132, 8449 and TP5237 at 1 Ravencroft were isolated to allow crew to re-configure cables. 60 customers were interrupted for minutes. Janet King (JKGF4) ID# 129341. | None | None | 60 | 320 | 320 | West | JKGF4
129344 | 2014-07-10 | Scheduled Outage | Construction | To allow Hydro Ottawa crew to replace the transformers in the vault. | None | None | 111 | 228 | 422 | Central | 5210
129345 | 2014-07-10 | Scheduled Outage | Vegetation Management | At 9:25am crews opened S13474 to allow tree trimming.130 customers affect for 365 mins and 16 customers affected for 449 mins. Russell (TB14) ID#129345 | None | None | 16 | 84 | 22 | East | TB14
129345 | 2014-07-10 | Scheduled Outage | Vegetation Management | At 9:25am crews opened S13474 to allow tree trimming.130 customers affect for 365 mins and 16 customers affected for 449 mins. Russell (TB14) ID#129345 | None | None | 146 | 365 | 888 | East | TB14
129346 | 2014-07-11 | Defective Equipment | Mechanical Failure | Switch 550 was found open due to defective fuse barrel. | O/H Switchgear | Fused Cutout | 42 | 102 | 71 | West | 24F8
129347 | 2014-07-11 | Unknown/Other | Unknown | Transformer X29874 fuse blew for unknown reason . Riverdale (TR09) ID# 129347. | None | None | 8 | 35 | 5 | Central | TR09
129349 | 2014-07-11 | Scheduled Outage | Construction | At 9:36am crews isolated TE227 to install new secondaries. 12 customers affected for 74 mins. Blackburn (4F1) ID#129349 | None | None | 12 | 74 | 15 | East | BLKF1
129350 | 2014-07-11 | Scheduled Outage | Construction | At 9:33am crews isolated 58F1 overhead from S14963 to allow crews to re-arrange overhead plant. 14 customers affected for 194 mins. Epworth (58F1) ID #129350 | None | None | 14 | 194 | 45 | South | EPWF1
129351 | 2014-07-11 | Defective Equipment | Defective Equipment/ Material | Cable fault | U/G Cable | Unknown \ Other | 1 | 716 | 12 | Central | UX03
129352 | 2014-07-11 | Scheduled Outage | Maintenance | To inspect & repair 415,416 & 608 cables in MH299 | None | None | 1 | 253 | 4 | Central | 416
129353 | 2014-07-11 | Scheduled Outage | Maintenance | Transformer X27345 at 664 Portage opened to allow crews to replace a defective service affecting 11 customers for 30 minutes, Russell TB06, ID # 129353 | None | O/H Service | 11 | 30 | 6 | East | TB06
129354 | 2014-07-12 | Defective Equipment | Corrosion | To replace defective dip switches | O/H Switchgear | Fused Cutout | 1 | 55 | 1 | Central | UX03
129355 | 2014-07-12 | Scheduled Outage | Construction | To de-commision transformer TE2235 and replacing it with TP10298 @ 6224 Auriga st. 2 customers affected in planned outage on 180F3 circuit ID# 129355. | None | Padmount (3ph) | 2 | 464 | 15 | South | 180F3
129357 | 2014-07-12 | Defective Equipment | Defective Equipment/ Material | Changed broken cutout at transformer X30615 at 146 St. Andrew St. | O/H Switchgear | Fused Cutout | 27 | 67 | 30 | Central | SK09
129358 | 2014-07-12 | Adverse Environment | Fire | Transformer X29664 opened at request of OFD due to live secondary on the ground. | Secondary \ Service | O/H Service | 12 | 31 | 6 | East | SO03
129362 | 2014-07-13 | Lightning | Lightning | customer reported seeing a lightning strike when power went out. | O/H Transformer | O/H Transformer (1ph) | 1 | 121 | 2 | East | 77M1
129364 | 2014-07-14 | Scheduled Outage | Maintenance | switch S22014 feeding TP6360 at 4100 Strandherd was isolated to allow crew to replace SMD20 switches affecting 21 customers for xx minutes, Fallowfield FAL01, ID # 129364 | None | None | 21 | 40 | 14 | South | FAL01
129365 | 2014-07-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X25305 opened up due to animal contact | O/H Switchgear | Fused Cutout | 49 | 225 | 184 | East | 77M6
129367 | 2014-07-14 | Scheduled Outage | Construction | Transformer #X32474 isolated by crew to transfer plant | None | None | 11 | 30 | 6 | Central | UW05
129368 | 2014-07-14 | Scheduled Outage | Construction | Transformer #X36141 isolated by crew for a service upgrade | None | None | 22 | 30 | 11 | South | 190F5
129369 | 2014-07-14 | Scheduled Outage | Maintenance | Elbow and insert replacement program. | None | None | 77 | 138 | 177 | East | CYRF3
129370 | 2014-07-14 | Scheduled Outage | Construction | Relocate TE459 to original location and install new cable and terminations. | None | None | 21 | 368 | 129 | South | 200F5
129370 | 2014-07-14 | Scheduled Outage | Construction | Relocate TE459 to original location and install new cable and terminations. | None | None | 24 | 15 | 6 | South | 200F5
129370 | 2014-07-14 | Scheduled Outage | Construction | Relocate TE459 to original location and install new cable and terminations. | None | None | 45 | 140 | 105 | South | 200F5
129371 | 2014-07-14 | Scheduled Outage | Construction | Transformer #X35219 isolated by crew to transfer plant | None | None | 12 | 30 | 6 | Central | UW05
129372 | 2014-07-14 | Tree Contacts | Other Vegetation | At 7:14pm SCADA indicated that RX2043 tripped, crews found fuses at S14057 blown due to vines. Bilberry Creek (77M6) ID# 129372 | None | None | 90 | 155 | 232 | East | 77M6
129372 | 2014-07-14 | Tree Contacts | Other Vegetation | At 7:14pm SCADA indicated that RX2043 tripped, crews found fuses at S14057 blown due to vines. Bilberry Creek (77M6) ID# 129372 | None | None | 1851 | 19 | 586 | East | 77M6
129373 | 2014-07-14 | Defective Equipment | Electrical Failure | At 9:45pm SCADA indicated an auto-reclose on the 84F6, crews found S965 blown. A cable fault was determined as the cause of the outage. 95 customers affected for 182 mins. Manordale (84F6) ID# 129373 | U/G Cable | XLPE | 95 | 182 | 288 | South | 84F6
129375 | 2014-07-15 | Scheduled Outage | Construction | To relocate transformer 2541 | None | None | 15 | 140 | 35 | West | 39F2
129376 | 2014-07-15 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER NPTE2824 TO REPLACE DEFECTIVE ELBOW | None | None | 12 | 135 | 27 | South | LGFF1
129377 | 2014-07-15 | Scheduled Outage | Maintenance | To replace switches and contractor customer maintenance | None | None | 1 | 44 | 1 | East | AQ04
129379 | 2014-07-15 | Foreign Interference | Vehicle | Truck hit a utility pole according to OPD. | None | None | 351 | 10 | 58 | East | AC14
129380 | 2014-07-16 | Scheduled Outage | Construction | O/H section from S15152 to EOL was iolated at 721 Hemlock to allow crew to install new poles and transfer primary. 221 customers were affected for 547 minutes. Beechwood (UB07). ID#129380 | None | None | 221 | 547 | 2015 | East | UB07
129381 | 2014-07-16 | Scheduled Outage | Vegetation Management | UF07-R O/H from pole 55D2B-033 to X31161 on Bay St was isolated to allow crew to replace neutral, remove vines and straighten pole. 15 customers were affected for 237 minutes. Florence (UF07). ID# 129381 | None | None | 15 | 237 | 59 | Central | UF07
129382 | 2014-07-16 | Scheduled Outage | Maintenance | Service the Main Secondary Switch | None | None | 1 | 37 | 1 | Central | UJ06
129383 | 2014-07-16 | Scheduled Outage | Construction | change defective transformer TP3275. | None | Kiosk (1ph) | 12 | 129 | 26 | East | 4801F8
129384 | 2014-07-16 | Scheduled Outage | Construction | replace leaking transformer TE1821 | None | Padmount (1ph) | 6 | 165 | 16 | South | 49F6
129385 | 2014-07-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30823 TO REPLACE POLE | None | None | 22 | 210 | 77 | Central | UX09
129386 | 2014-07-16 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER TP3275 DUE TO OIL LEAK | None | None | 12 | 208 | 42 | East | 4801F8
129387 | 2014-07-16 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X35464 CAUSED BY SQUIRREL CONTACT | O/H Transformer | O/H Transformer (1ph) | 10 | 86 | 14 | Central | TD01
129388 | 2014-07-16 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X29065 TO REPAIR PRIMARY NEUTRAL BUSHING | None | None | 9 | 65 | 10 | East | AJ03
129390 | 2014-07-16 | Scheduled Outage | Construction | Replace poles | None | None | 11 | 210 | 38 | Central | UX09
129392 | 2014-07-16 | Foreign Interference | Wildlife (Bird/Animal) | Crow contact at 805 Rideau | O/H Switchgear | Unknown \ Other | 1 | 91 | 2 | East | 7F4
129394 | 2014-07-17 | Scheduled Outage | Construction | To allow crew to install new primary cables | None | None | 5 | 53 | 4 | Central | SA23
129395 | 2014-07-17 | Scheduled Outage | Maintenance | planned outage for elbow and insert replacement | None | None | 79 | 146 | 192 | East | CYRF3
129397 | 2014-07-17 | Scheduled Outage | Maintenance | transformer TE1695 at 182 Craig Henry was isolated for soil remediation affecting 12 customers for 392 minutes, Centerpoint 87F3, ID # 129397 | None | None | 12 | 392 | 78 | South | 87F3
129398 | 2014-07-17 | Scheduled Outage | Construction | planned outage, xfmr replacement | None | None | 10 | 460 | 77 | South | 160F1
129399 | 2014-07-17 | Scheduled Outage | Maintenance | remove excess sand from xfmr base | None | None | 9 | 78 | 12 | West | MWDF2
129400 | 2014-07-17 | Scheduled Outage | Construction | Transformer #X29998 isolated by crew for a service upgrade | None | None | 8 | 55 | 7 | Central | TR09
129401 | 2014-07-17 | Scheduled Outage | Construction | Replacing primary cables to V379 | None | None | 1 | 57 | 1 | Central | SA23
129402 | 2014-07-17 | Unknown/Other | Unknown | unknown | None | None | 1 | 91 | 2 | West | BECKF2
129403 | 2014-07-18 | Scheduled Outage | Maintenance | Transformer #X36334 isolated by crew to replace defective cutout for maintenance | None | None | 1 | 26 | 0 | West | BECKF2
129404 | 2014-07-18 | Scheduled Outage | Maintenance | Transformer #X36335 isolated by crew to replace defective cut out for maintenance | None | None | 1 | 45 | 1 | West | BECKF2
129405 | 2014-07-18 | Scheduled Outage | Maintenance | Transformer #X26412 isolated by crew to replace defective cut out for maintenance | None | None | 1 | 40 | 1 | West | BECKF2
129406 | 2014-07-18 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X11610 opened up due to bird contact | O/H Switchgear | Fused Cutout | 1 | 78 | 1 | West | BECKF2
129407 | 2014-07-18 | Scheduled Outage | Maintenance | Transformer #X36336 isolated by crew to replace defective cut out for maintenance | None | None | 1 | 15 | 0 | West | BECKF2
129408 | 2014-07-18 | Foreign Interference | Dig-In | Transformer #X40198 opened up due to a dig in | O/H Switchgear | Fused Cutout | 10 | 123 | 20 | South | 200F1
129409 | 2014-07-18 | Defective Equipment | Electrical Failure | 8kv o/h transformer x36011 crew replaced defective switch and arrestor. | O/H Switchgear | Fused Cutout | 5 | 103 | 9 | South | EPWF1
129410 | 2014-07-18 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33129 FOUND BLOWN DUE TO RACCOON CONTACT | O/H Transformer | O/H Transformer (1ph) | 8 | 58 | 8 | Central | TD05
129411 | 2014-07-19 | Foreign Interference | Wildlife (Bird/Animal) | The 249F1 circuit tripped open under hold off, crew found the G474R at 1537 Queensdale (fuse) blown due to squirel contact. Leitrim 249F1. ID# 129411 | O/H Switchgear | Fused Cutout | 32 | 68 | 36 | East | LTM01
129411 | 2014-07-19 | Foreign Interference | Wildlife (Bird/Animal) | The 249F1 circuit tripped open under hold off, crew found the G474R at 1537 Queensdale (fuse) blown due to squirel contact. Leitrim 249F1. ID# 129411 | O/H Switchgear | Fused Cutout | 3800 | 2 | 127 | East | LTM01
129412 | 2014-07-19 | Scheduled Outage | Maintenance | To remove transformer to allow for soil remediation | None | None | 34 | 443 | 251 | East | AL10
129414 | 2014-07-19 | Scheduled Outage | Maintenance | Replace broken trans cutout | None | Fused Cutout | 8 | 20 | 3 | East | 249F2
129415 | 2014-07-20 | Defective Equipment | Electrical Failure | Cable Fault | U/G Cable | XLPE | 88 | 58 | 85 | South | 200F5
129415 | 2014-07-20 | Defective Equipment | Electrical Failure | Cable Fault | U/G Cable | XLPE | 133 | 160 | 355 | South | 200F5
129416 | 2014-07-20 | Defective Equipment | Electrical Failure | faulted blue phase cable section between S119 and S29097. | U/G Cable | XLPE | 207 | 116 | 400 | West | BRDF3
129417 | 2014-07-20 | Foreign Interference | Wildlife (Bird/Animal) | A squirrel caused transformer X33075 to open. This transformer feeds the City Of Ottawa Pumping Station. Field Operators re-fused the transformer. There was a mapping discrepency that caused delays in restoring power. 1 customer was affected for 306 minut | O/H Switchgear | Fused Cutout | 1 | 306 | 5 | Central | TD07
129418 | 2014-07-21 | Foreign Interference | Wildlife (Bird/Animal) | A squirrel caused the transformer fuse to open. Field Operators re-fused the transformer | O/H Switchgear | Fused Cutout | 6 | 44 | 4 | Central | TH06
129419 | 2014-07-21 | Scheduled Outage | Construction | To upgrade transformer from 150 MVA to 300MVA TP4868 | None | None | 1 | 1502 | 25 | Central | SB05
129420 | 2014-07-21 | Scheduled Outage | Construction | At 9:40am crew isolated a section of the 72F4 to install a pole. 17 customers affected for 45 mins. Merivale (72F4) ID#129420 | None | None | 17 | 45 | 13 | South | 72F4
129421 | 2014-07-21 | Scheduled Outage | Construction | TP8901 at 313 Centerra was isolated to allow crew to replace dammaged transformer. 10 customer were affected for 124 minutes. Fallowfield (FAL03). ID# 129421 | None | None | 10 | 124 | 21 | South | FAL03
129422 | 2014-07-21 | Scheduled Outage | Construction | Transformer TE389 at 18 Northpark was isoalted to allow crwe to connect new XPL cable in live front transformer. 10 customers were affected for 211 minutes. Blackburn (4F1). ID# 129422 | None | None | 14 | 211 | 49 | East | BLKF1
129424 | 2014-07-21 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel | None | None | 8 | 79 | 11 | Central | AH04
129425 | 2014-07-21 | Scheduled Outage | Construction | At 12h30 crews isolated transformer X30851 to replace a pole. 12 customers affected for 230 mins. Gladstone (UX09) ID#129425 | None | None | 12 | 230 | 46 | Central | UX09
129426 | 2014-07-21 | Foreign Interference | Wildlife (Bird/Animal) | Bird contact at transformer X33482 at 7661 Mansfield caused the fused cut out to open | O/H Switchgear | Fused Cutout | 1 | 147 | 2 | West | BECKF2
129427 | 2014-07-21 | Scheduled Outage | Forced Switching | Restriction on use of customer switchgear | None | None | 1 | 8 | 0 | Central | TL3TS
129429 | 2014-07-22 | Scheduled Outage | Construction | At 9:00 am, UW05 from TEMP 25 to EOL on Mallard Ave was isolated to allow crew to transfer overhead to UW07. 29 customers were interrupted for 490 minutes. Woodroffe (UW05) ID# 129429. | None | None | 29 | 490 | 237 | Central | UW05
129431 | 2014-07-22 | Scheduled Outage | Maintenance | Elbow insert replacement on 9 tranformers Meadowglen Dr and Willowbark Dr in Orleans | None | Kiosk (1ph) | 102 | 143 | 243 | East | 77M5
129432 | 2014-07-22 | Scheduled Outage | Construction | TE8 at 40 Beaumaris was isolated by the crew to allow them replace the transformer and its base. | None | None | 10 | 326 | 54 | South | 160F1
129433 | 2014-07-22 | Scheduled Outage | Maintenance | Transformer GL000961 at 1058 Bravar Dr. isolated by crew to replace defective switch | None | None | 2 | 23 | 1 | East | 7F4
129434 | 2014-07-22 | Scheduled Outage | Construction | Transformer X30809 at 127 Waverley St. isolated by contractor for pole change | None | None | 7 | 290 | 34 | Central | UX09
129437 | 2014-07-22 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X27511 at 2000 Fairbanks Ave. - bird contact | O/H Transformer | O/H Transformer (1ph) | 7 | 30 | 4 | East | TB06
129438 | 2014-07-22 | Foreign Interference | Wildlife (Bird/Animal) | Refused switch G980R at 1104 Gabriel St. - squirrel contact | O/H Switchgear | Inline Switch | 11 | 101 | 19 | East | 77M6
129439 | 2014-07-22 | Scheduled Outage | Construction | Transformer X30808 at 119 Waverley St. isolated by contractor for pole change | None | None | 12 | 290 | 58 | Central | UX09
129440 | 2014-07-22 | Scheduled Outage | Construction | Transformer X30852 at 111 Waverley St. isolated by contractor for pole change | None | None | 11 | 290 | 53 | Central | UX09
129441 | 2014-07-22 | Scheduled Outage | Maintenance | Transformer #X13470 isolated by crew to replace switch | None | None | 10 | 24 | 4 | East | 7F4
129442 | 2014-07-22 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | Unknown \ Other | 28 | 44 | 21 | East | 77M1
129442 | 2014-07-22 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | Unknown \ Other | 139 | 109 | 253 | East | 77M1
129443 | 2014-07-23 | Foreign Interference | Wildlife (Bird/Animal) | TW05 tripped and X45428 fuse blew due to squirrel contact. | None | None | 17 | 43 | 12 | Central | TW05
129443 | 2014-07-23 | Foreign Interference | Wildlife (Bird/Animal) | TW05 tripped and X45428 fuse blew due to squirrel contact. | None | None | 379 | 15 | 95 | Central | TW05
129444 | 2014-07-23 | Scheduled Outage | Maintenance | At 9:57 am, transformer KT73 at 108 Gillespie Cr. Was isolated to allow crew to replace terminations. 7 customers were interrupted for 118 minutes. Albion (2211) ID# 129444. | None | None | 7 | 118 | 14 | East | 2211
129445 | 2014-07-23 | Scheduled Outage | Construction | Transformer 3267 @ 10 McKitrick was isolated by the crew to allow them to change it out. | None | None | 10 | 151 | 25 | West | BRDF6
129446 | 2014-07-23 | Scheduled Outage | Construction | Replacement on leaking transformer TE1816 with TP10523 | None | None | 24 | 107 | 43 | South | 160F2
129448 | 2014-07-23 | Scheduled Outage | Construction | 2 rusting transformers replaced on Craig Henry DR. New transformers no nomenclature change. | None | None | 19 | 162 | 51 | South | 87F3
129449 | 2014-07-23 | Scheduled Outage | Maintenance | Cable section repaired and power interruption to out of phase customers to return to normal. | None | None | 113 | 1 | 2 | South | 72F2
129450 | 2014-07-23 | Scheduled Outage | Construction | Transformer X30813 at 110 Cartier St, X30814 at 183 Waverley St and X30853 at 177 Waverley St. isolated by contractor for pole change | None | None | 26 | 270 | 117 | Central | UX09
129451 | 2014-07-23 | Defective Equipment | Mechanical Failure | G54 blue phase blew due to | O/H Switchgear | Fused Cutout | 510 | 82 | 697 | East | LTM01
129452 | 2014-07-23 | Scheduled Outage | Construction | TE460 new transformer and base installed Bells Corners | None | Kiosk (1ph) | 24 | 517 | 207 | South | 200F5
129453 | 2014-07-24 | Scheduled Outage | Construction | Allow crews to reconfigure cables. | None | None | 36 | 286 | 172 | West | JKGF4
129457 | 2014-07-24 | Scheduled Outage | Maintenance | Elbow and Insert Changes | None | None | 111 | 171 | 316 | East | 77M5
129458 | 2014-07-24 | Tree Contacts | Broken Branch | Transformer X24506 at 238 Tudor Place isolated to remove tree limb from secondary | None | None | 6 | 15 | 2 | East | UG06
129460 | 2014-07-24 | Scheduled Outage | Maintenance | Transformer X35460 at 609 Mansfield Ave. isolated by crew to replace open wire service | None | None | 2 | 66 | 2 | Central | TD01
129463 | 2014-07-24 | Tree Contacts | Falling Tree | A very large tree brought down the W phase primary & neutral conductors causing K634 to open | O/H Conductor | O/H Conductor | 5 | 177 | 15 | West | MWDF3
129464 | 2014-07-25 | Defective Equipment | Defective Equipment/ Material | B phase cable fault between S13702 B & TP8476 B | U/G Cable | XLPE | 202 | 86 | 290 | East | CYRF3
129465 | 2014-07-25 | Defective Equipment | Defective Equipment/ Material | A blue phase cable fault on the 77M2 caused S22262 B phase to open. | U/G Cable | XLPE | 68 | 50 | 57 | East | 77M2
129465 | 2014-07-25 | Defective Equipment | Defective Equipment/ Material | A blue phase cable fault on the 77M2 caused S22262 B phase to open. | U/G Cable | XLPE | 183 | 98 | 299 | East | 77M2
129466 | 2014-07-25 | Scheduled Outage | Vegetation Management | Transformer X33541 at 156 Baseline Rd. isolated by 24/7 crew to change open wire service to triplex | None | None | 12 | 19 | 4 | Central | AK02
129469 | 2014-07-25 | Scheduled Outage | Maintenance | Transformer X30165 at 191 Louisa St. isolated to change transformer not open wire service (previous outage for same address deleted) | O/H Transformer | O/H Transformer (1ph) | 27 | 168 | 76 | Central | SB14
129470 | 2014-07-25 | Scheduled Outage | Maintenance | Transformer X33939 at 197 Latchford Rd. isolated by crew to replace connections | None | None | 11 | 26 | 5 | Central | UL02
129471 | 2014-07-25 | Scheduled Outage | Maintenance | Transformer X40152 at 7 Wild Acre Lane isolated for crew to change SMU switch | None | None | 3 | 24 | 1 | West | MWDF3
129472 | 2014-07-25 | Scheduled Outage | Maintenance | Transformer X40151 at 10 Wild Acre Lane isolated for crew to change SMU switch | None | None | 2 | 31 | 1 | West | MWDF3
129475 | 2014-07-26 | Tree Contacts | Tree Growth/ Untrimmed Tree | S15431 fuse blew due to tree contact. | None | None | 4 | 80 | 5 | West | 624F6
129476 | 2014-07-27 | Tree Contacts | Broken Branch | Transformer #X41424 opened up due to branch on primary | O/H Switchgear | Fused Cutout | 2 | 57 | 2 | South | 130F2
129479 | 2014-07-27 | Defective Equipment | Defective Equipment/ Material | Transformer #X37485 opened up due to broken cut out | O/H Switchgear | Fused Cutout | 1 | 97 | 2 | West | 624F6
129480 | 2014-07-27 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X40084 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 2 | 52 | 2 | West | 624F6
129481 | 2014-07-27 | Scheduled Outage | Maintenance | 3 transformers, X40793, X32446 and X32447 isolated by crew to re-arrange plant | None | None | 21 | 237 | 83 | Central | TW22
129482 | 2014-07-27 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35290 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 7 | 35 | 4 | West | ALEXF3
129483 | 2014-07-27 | Defective Equipment | Electrical Failure | On call crew called in to replace defective transformer. | Vault Equipment | Transformer | 1 | 166 | 3 | Central | TH01
129484 | 2014-07-27 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X34109 opened up due to animal contact | O/H Switchgear | Fused Cutout | 1 | 63 | 1 | Central | TH01
129485 | 2014-07-27 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | Unknown \ Other | 133 | 23 | 51 | South | 130F1
129485 | 2014-07-27 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | Unknown \ Other | 133 | 60 | 133 | South | 130F1
129485 | 2014-07-27 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | Unknown \ Other | 379 | 1 | 6 | South | 130F1
129485 | 2014-07-27 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | Unknown \ Other | 399 | 1 | 7 | South | 130F1
129486 | 2014-07-27 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X06319 fuse blew due to bird contact. | None | None | 1 | 39 | 1 | East | 7F1
129487 | 2014-07-28 | Tree Contacts | Other Vegetation | S181 and X39866 fuse blew due to vines in the transformer at X39866. | None | None | 17 | 203 | 58 | South | 47F6
129489 | 2014-07-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X17372 opened up due to defective switch | O/H Switchgear | Fused Cutout | 9 | 101 | 15 | East | 77M2
129490 | 2014-07-28 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X24466 opened up due to animal contact | O/H Switchgear | Fused Cutout | 28 | 123 | 57 | East | 77M6
129491 | 2014-07-28 | Scheduled Outage | Construction | Transformer #X30740 opened by crew to re-arrange plant | None | None | 21 | 70 | 24 | Central | UD04
129492 | 2014-07-28 | Scheduled Outage | Maintenance | Transformer #X40152 isolated by crew to replace a switch | None | None | 3 | 25 | 1 | West | MWDF3
129493 | 2014-07-28 | Foreign Interference | Customer Equipment | A blown switch in VT432 caused 3 circuits to trip out. | Customer Owned | Customer-Owned | 1 | 643 | 11 | Central | TK20
129493 | 2014-07-28 | Foreign Interference | Customer Equipment | A blown switch in VT432 caused 3 circuits to trip out. | Customer Owned | Customer-Owned | 1 | 655 | 11 | Central | 630
129493 | 2014-07-28 | Foreign Interference | Customer Equipment | A blown switch in VT432 caused 3 circuits to trip out. | Customer Owned | Customer-Owned | 5 | 37 | 3 | Central | 630
129493 | 2014-07-28 | Foreign Interference | Customer Equipment | A blown switch in VT432 caused 3 circuits to trip out. | Customer Owned | Customer-Owned | 40 | 42 | 28 | Central | 412
129493 | 2014-07-28 | Foreign Interference | Customer Equipment | A blown switch in VT432 caused 3 circuits to trip out. | Customer Owned | Customer-Owned | 682 | 49 | 557 | Central | TK20
129494 | 2014-07-28 | Scheduled Outage | Construction | 2 transformers, #X32551 and X35957 isolated by crew to re-locate plant | None | None | 13 | 190 | 41 | Central | UW05
129495 | 2014-07-28 | Unknown/Other | Unknown | REPLACED BLOWN FUSE FEEDING TRANSFORMER X35790 (CAUSE UNKNOWN) | O/H Transformer | O/H Transformer (1ph) | 14 | 69 | 16 | Central | TD06
129496 | 2014-07-28 | Tree Contacts | Other Vegetation | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33332 (VINES AROUND TRANSFORMER) | O/H Transformer | O/H Transformer (1ph) | 5 | 121 | 10 | West | 43F2
129497 | 2014-07-29 | Scheduled Outage | Maintenance | Elbow and Insert change program. | None | Kiosk (1ph) | 37 | 135 | 83 | East | 77M5
129499 | 2014-07-29 | Scheduled Outage | Maintenance | 5, 4kV overhead transformers along Sherman Dr N of Matthews were isolated to allow crew to replace rotten cross arm. | None | Crossarm | 62 | 25 | 26 | Central | UW05
129500 | 2014-07-29 | Scheduled Outage | Maintenance | TP10497 isolated for soil remediation . | None | Padmount (1ph) | 10 | 425 | 71 | West | BRDF7
129501 | 2014-07-29 | Scheduled Outage | Construction | To transfer plant to new poles. | None | None | 32 | 510 | 272 | Central | UW05
129504 | 2014-07-30 | Scheduled Outage | Construction | Transfer plant to new poles. | None | None | 19 | 105 | 33 | Central | UX08
129505 | 2014-07-30 | Scheduled Outage | Construction | P418 at 1675 Mallard isolated to allow crew to transfer plant to new pole | None | None | 1 | 262 | 4 | Central | UW07
129506 | 2014-07-30 | Scheduled Outage | Construction | Transfer plant to new pole. | None | None | 19 | 240 | 76 | Central | UX08
129507 | 2014-07-30 | Scheduled Outage | Construction | PCB transformer removal and connect new primary cables. | None | None | 1 | 335 | 6 | East | UQ02
129508 | 2014-07-30 | Tree Contacts | Other Vegetation | Vine contact at G414W caused fuse at G477W phase to open. | O/H Switchgear | Fused Cutout | 9 | 158 | 24 | East | LTM01
129512 | 2014-07-30 | Tree Contacts | Tree Growth/ Untrimmed Tree | c | O/H Transformer | O/H Transformer (1ph) | 10 | 213 | 36 | East | LTM01
129513 | 2014-07-30 | Scheduled Outage | Maintenance | Transformer X36677 at 33 Dogwood Dr. isolated by crew to replace triplex. | None | None | 4 | 70 | 5 | West | 43F2
129514 | 2014-07-30 | Scheduled Outage | Construction | Transformer X29212 at 1809 Riverside Dr. isolated by crew to rearange secondary at 1801 Riverside Dr. | None | None | 10 | 150 | 25 | East | UQ03
129515 | 2014-07-30 | Scheduled Outage | Maintenance | Transformer X21505 at 87 Clearview Ave. isolated by crew to change cutout and arrestor | None | None | 6 | 41 | 4 | Central | TH01
129516 | 2014-07-30 | Tree Contacts | Falling Tree | Emergancy tree removal with a crane. | None | None | 50 | 225 | 188 | East | TB06
129517 | 2014-07-30 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32464 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 7 | 210 | 24 | Central | UW05
129518 | 2014-07-30 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X06259 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 8 | 183 | 24 | South | 180F4
129520 | 2014-07-31 | Tree Contacts | Tree Growth/ Untrimmed Tree | transformer X26914 at 519 Avalon was opened to allow crew to replace a damaged service affecting 9 customers for 61 minutes, Russell TB14, ID # 129520 | Secondary \ Service | O/H Service | 9 | 61 | 9 | East | TB14
129521 | 2014-07-31 | Defective Equipment | Electrical Failure | blown fuse caused an interuption to traffic lights on Terry Fox | O/H Switchgear | Unknown \ Other | 1 | 207 | 3 | West | 624F1
129524 | 2014-07-31 | Lightning | Lightning | Lightning strike at S22011 that damaged pole and transformer. S22011 opened. Moodie Dr south of Fallowfield Rd | O/H Transformer | O/H Transformer (1ph) | 5200 | 54 | 4680 | South | FAL03
129525 | 2014-07-31 | Scheduled Outage | Maintenance | Transformer X33670 at 811 Rex Ave. isolated by crew to change arrestor and rearrange an open wire service | Pole Attachement | Arrester | 7 | 105 | 12 | Central | UC03
129526 | 2014-07-31 | Scheduled Outage | Vegetation Management | At 9:00am crews opened S19398 to allow contractor to remove tree. 37 customers affected 333 mins. Russel (TB06) ID#129526 | None | None | 37 | 333 | 205 | East | TB06
129528 | 2014-07-31 | Lightning | Lightning | Transformer was replaced due to lightning strike | O/H Transformer | O/H Transformer (1ph) | 12 | 295 | 59 | East | LTM01
129530 | 2014-08-01 | Defective Equipment | Electrical Failure | suspected cable fault between TA01 breaker at Albion and SW182 on Bank St. | U/G Cable | XLPE | 31 | 24 | 12 | East | TA3AQ
129530 | 2014-08-01 | Defective Equipment | Electrical Failure | suspected cable fault between TA01 breaker at Albion and SW182 on Bank St. | U/G Cable | XLPE | 850 | 35 | 496 | East | TA3AQ
129531 | 2014-08-02 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27511 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 7 | 118 | 14 | East | TB06
129533 | 2014-08-03 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X28243 | O/H Transformer | O/H Transformer (1ph) | 14 | 77 | 18 | Central | 505
129534 | 2014-08-04 | Unknown/Other | Unknown | Replaced blown fuse feeding transformer X40447 (cause unknown) | O/H Transformer | O/H Transformer (1ph) | 1 | 55 | 1 | West | BECKF2
129535 | 2014-08-04 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X29441 TO TRANSFER LOAD TO ANOTHER PHASE | None | None | 15 | 7 | 2 | East | AC07
129536 | 2014-08-04 | Scheduled Outage | Vegetation Management | QT125 was isolated to allow contractor to remove vines from customer secondary. | None | None | 1 | 161 | 3 | South | 22M28
129538 | 2014-08-04 | Scheduled Outage | Construction | TE1558 at 15 Coolspring was isolated to replace defective transformer. 6 customers affected for min. Parkwood Hills (190F2) | None | None | 6 | 374 | 37 | South | 190F2
129539 | 2014-08-05 | Scheduled Outage | Vegetation Management | Tree removal | None | None | 21 | 237 | 83 | East | 8F1
129540 | 2014-08-05 | Scheduled Outage | Construction | Replace transformer & cables | None | None | 15 | 337 | 84 | South | 140F3
129541 | 2014-08-05 | Scheduled Outage | Construction | Tim Connell of K-Line Construction isolated transformers X32561, X32562 & X31749 on Laxton St to change utility poles. 22 customers were interrupted for 390 minutes and 3 customers were interrupted for 570 minutes. Woodroffe DS (UW05) ID# 129541 | None | None | 3 | 180 | 9 | Central | UW05
129541 | 2014-08-05 | Scheduled Outage | Construction | Tim Connell of K-Line Construction isolated transformers X32561, X32562 & X31749 on Laxton St to change utility poles. 22 customers were interrupted for 390 minutes and 3 customers were interrupted for 570 minutes. Woodroffe DS (UW05) ID# 129541 | None | None | 25 | 390 | 162 | Central | UW05
129542 | 2014-08-05 | Scheduled Outage | Construction | Hydro Ottawa crews isolated transformer X33305 so that a new transformer could be added and the service upgraded. 2 customers were interrupted for 175 minutes. Richmond North DS (RHNF3) ID# 129542 | None | None | 2 | 175 | 6 | West | RHNF3
129543 | 2014-08-05 | Scheduled Outage | Maintenance | Hydro Ottawa crews isolated transformer X28170 at the rear of 1528 Lasalle St to allow the service at 1043 Aldea Ave to be changed. 8 customers were interrupted for 42 minutes. Riverdale TS (505) ID# 129543 | None | O/H Service | 8 | 42 | 6 | Central | 505
129544 | 2014-08-05 | Scheduled Outage | Construction | Trans X29711 and X29710 were isolated in order to transfer plant | None | None | 17 | 135 | 38 | East | AE07
129548 | 2014-08-06 | Scheduled Outage | Construction | Replace both transformer and primary cable. | None | None | 21 | 313 | 110 | South | 140F3
129552 | 2014-08-06 | Scheduled Outage | Construction | Transformer #X29647 isolated by crew to re-arrange primary | None | None | 7 | 138 | 16 | East | SO03
129553 | 2014-08-06 | Scheduled Outage | Maintenance | Tranformer #X27653 isolated by crew for phase balancing | None | None | 5 | 5 | 0 | East | UQ02
129555 | 2014-08-06 | Scheduled Outage | Construction | At 9:00am crews isolated V379 to allow pull in new cables. 1 customer affected for 216 mins. Slater (SA23) ID#129555 | None | None | 1 | 216 | 4 | Central | SA23
129556 | 2014-08-06 | Unknown/Other | Unknown | The SC2101 R phase blew, Crew patrolled the circuit and found nothg, cause remains under investigation. Carling(303). ID# 129556 | U/G Switchgear | Unknown \ Other | 42 | 115 | 80 | Central | 303
129557 | 2014-08-07 | Scheduled Outage | Maintenance | Hydro Ottawa crews isolated S12024 to replace defective SMD switches. 1 custmer was interrupted for minutes. Limebank DS (7F2) | None | None | 1 | 57 | 1 | East | 7F2
129559 | 2014-08-07 | Scheduled Outage | Construction | Change both transformer and primary cable. | None | None | 15 | 305 | 76 | South | 140F3
129560 | 2014-08-07 | Scheduled Outage | Maintenance | Hydro Ottawa crews isolated transformer X16759 on Ogilvie Rd so that a guy wire could be lowered. The guy wire was making contact with the 27.6 CYRF4 circuit and causing burning. | None | None | 1 | 85 | 1 | East | CYRF4
129561 | 2014-08-07 | Scheduled Outage | Vegetation Management | Tree removal | None | None | 43 | 294 | 211 | East | UZ03
129563 | 2014-08-07 | Scheduled Outage | Construction | Cable & transformer replacement | None | None | 33 | 603 | 332 | South | 200F5
129564 | 2014-08-07 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32488 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 1 | 132 | 2 | Central | TD06
129565 | 2014-08-08 | Scheduled Outage | Maintenance | To allow metering department to replace equipment. | None | None | 1 | 34 | 1 | Central | 5405
129568 | 2014-08-08 | Scheduled Outage | Construction | TE398 & TE1954 @ 3550 Downpatrick was isolated to allow the crew to replace two leaking transformers. 38 customers were affected.ID129568 | U/G Transformer | Padmount (1ph) | 38 | 229 | 145 | East | 4801F8
129569 | 2014-08-08 | Scheduled Outage | Maintenance | Transformer #X33530 isolated by crew to replace switch and arrestor | None | None | 1 | 45 | 1 | Central | 303
129570 | 2014-08-06 | Foreign Interference | Dig-In | Contractor dig in. | U/G Cable | XLPE | 2 | 15 | 0 | East | 77M2
129572 | 2014-08-09 | Defective Equipment | Moisture Ingress | Switch S14275 blue phase was found to be defective during switching. Beaconhill (BCHF3) ID# 129572 | O/H Switchgear | Fused Cutout | 136 | 15 | 34 | East | BCHF3
129573 | 2014-08-09 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X29861 at 25 Gordon, cause was animal contact - squirrel | None | None | 9 | 46 | 7 | Central | TR09
129574 | 2014-08-11 | Scheduled Outage | Construction | Transformer #X33047 isolated by crew to connect a new service | None | None | 4 | 15 | 1 | South | 180F4
129575 | 2014-08-11 | Scheduled Outage | Maintenance | Transformer #X38775 isolated by crew to replace defective switch | None | None | 6 | 20 | 2 | West | JKGF4
129577 | 2014-08-11 | Scheduled Outage | Construction | TP6092 at 53 Bridle Crest isolated to allow crews to rearrange primary cables in transformer base. | None | Padmount (1ph) | 8 | 288 | 38 | West | BRDF1
129578 | 2014-08-11 | Scheduled Outage | Vegetation Management | 2 transformer #X32283 & X32105 isolated by crew for Forestry | None | None | 9 | 275 | 41 | Central | TD01
129579 | 2014-08-11 | Scheduled Outage | Maintenance | Transformer #X38780 isolated by crew to replace defective switch | None | None | 7 | 15 | 2 | West | JKGF4
129580 | 2014-08-11 | Scheduled Outage | Maintenance | switches G933 isolated to allow crews to change cracked cut-outs | None | None | 1 | 67 | 1 | East | 7F2
129582 | 2014-08-12 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X27475 opened up due to tree contact | O/H Switchgear | Fused Cutout | 12 | 48 | 10 | Central | 505
129585 | 2014-08-12 | Defective Equipment | Defective Equipment/ Material | Transformer #X31756 opened up due to broken switch | O/H Switchgear | Fused Cutout | 8 | 110 | 15 | Central | SM13
129586 | 2014-08-12 | Scheduled Outage | Construction | Transformer #X47965 isolated by crew to transfer plant | None | None | 10 | 150 | 25 | Central | UW05
129587 | 2014-08-12 | Foreign Interference | Vehicle | MVA broke pole and guy wire wraped around UB05 and UB07 circuits. | Pole | Pole | 103 | 4 | 7 | East | UB05
129587 | 2014-08-12 | Foreign Interference | Vehicle | MVA broke pole and guy wire wraped around UB05 and UB07 circuits. | Pole | Pole | 374 | 4 | 25 | East | UB07
129590 | 2014-08-13 | Defective Equipment | Defective Equipment/ Material | Transformer #X33097 opened up due to defective transformer switch | O/H Switchgear | Fused Cutout | 9 | 163 | 24 | Central | TD07
129593 | 2014-08-13 | Defective Equipment | Electrical Failure | replaced defective transformer x24282 | O/H Transformer | O/H Transformer (1ph) | 1 | 316 | 5 | East | 6F1
129594 | 2014-08-13 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMERS X31749, X32562, AND X32561 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 25 | 30 | 12 | Central | UW05
129595 | 2014-08-13 | Scheduled Outage | Construction | ISOLATED 5 TRANSFORMERS X34468, X35220, X35219, X32474, AND X32564 | None | None | 62 | 60 | 62 | Central | UW05
129596 | 2014-08-13 | Scheduled Outage | Construction | schedualled outage to allow crew to prove spare duct. | None | None | 1 | 47 | 1 | Central | SA23
129597 | 2014-08-13 | Scheduled Outage | Construction | Install Poles / Transfer Plant | None | None | 5 | 270 | 22 | Central | UW05
129598 | 2014-08-13 | Defective Equipment | Electrical Failure | S965 B was found blown due to cable fault between TE666 and TE665 | U/G Cable | XLPE | 62 | 83 | 86 | South | 84F6
129598 | 2014-08-13 | Defective Equipment | Electrical Failure | S965 B was found blown due to cable fault between TE666 and TE665 | U/G Cable | XLPE | 95 | 249 | 394 | South | 84F6
129599 | 2014-08-14 | Unknown/Other | Unknown | Transformer X35788 fuse blew for unknown reason. Lincoln Heights (TD06) ID# 129599. | Unknown \ Other | Unknown \ Other | 7 | 87 | 10 | Central | TD06
129600 | 2014-08-14 | Scheduled Outage | Maintenance | schedualled outage to allow crew to change primary terminations and porcielin insulators. | None | None | 10 | 130 | 22 | East | 2211
129601 | 2014-08-14 | Scheduled Outage | Construction | scheduled outage to allow crew to perform cable and transformer replacement. | None | None | 28 | 415 | 194 | South | 200F5
129602 | 2014-08-14 | Scheduled Outage | Maintenance | At 9:24am crew isolated V104 to allow contrator to perform vault maintenance. 1 customers affected for 146 mins. Shillington (AD02) ID# 129602 | None | None | 1 | 146 | 2 | Central | AD02
129603 | 2014-08-14 | Scheduled Outage | Maintenance | At 09:18am crews isolated VT843 to allow contractor to perform vault maintenance. 1 customer affected for 147mins. Overbrook (1808) ID# 129603 | None | None | 1 | 147 | 2 | East | 1808
129604 | 2014-08-14 | Scheduled Outage | Construction | Transformer #X32910 isolated by crew to re-arrange plant | None | None | 7 | 120 | 14 | West | 28F2
129605 | 2014-08-14 | Defective Equipment | Defective Equipment/ Material | ISOLATED AND REPLACED DEFECTIVE SWITCH FEEDING TRANSFORMER X29890 | O/H Switchgear | Fused Cutout | 6 | 20 | 2 | Central | TR09
129606 | 2014-08-15 | Scheduled Outage | Construction | Transformer #X32910 isolated by crew to transfer plant | None | None | 7 | 120 | 14 | West | 28F2
129607 | 2014-08-15 | Scheduled Outage | Construction | Transformer #X23662 isolated by crew for a pole replacement | None | None | 9 | 165 | 25 | East | UB07
129608 | 2014-08-15 | Scheduled Outage | Construction | Transformer #X32900 isolated by crew to transfer plant | None | None | 6 | 75 | 8 | West | 28F2
129609 | 2014-08-16 | Foreign Interference | Wildlife (Bird/Animal) | S29395 opened due to animal contact at X38797 | O/H Transformer | O/H Transformer (1ph) | 129 | 64 | 138 | West | JKGF4
129610 | 2014-08-17 | Defective Equipment | Mechanical Failure | Replace broken transformer cutout | O/H Switchgear | Fused Cutout | 6 | 132 | 13 | East | BLKF3
129611 | 2014-08-17 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact. | O/H Switchgear | Fused Cutout | 1 | 166 | 3 | Central | TD06
129613 | 2014-08-17 | Defective Equipment | Electrical Failure | Defective u/g cable between TE389 & G214B | U/G Cable | XLPE | 14 | 40 | 9 | East | BLKF1
129613 | 2014-08-17 | Defective Equipment | Electrical Failure | Defective u/g cable between TE389 & G214B | U/G Cable | XLPE | 25 | 45 | 19 | East | BLKF1
129617 | 2014-08-18 | Scheduled Outage | Construction | Replacement of transformer and cut outs. | None | None | 66 | 120 | 132 | Central | TH11-NIU
129618 | 2014-08-18 | Human Element | Incorrect Records/ labelling | Transfomer 4068B interrupted during switching due to incorrect nomenclature at the transformer. | U/G Transformer | Padmount (1ph) | 14 | 61 | 14 | West | BRDF6
129619 | 2014-08-18 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X23661 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 165 | 28 | East | UB07
129622 | 2014-08-18 | Scheduled Outage | Maintenance | TP5997 at 5 Live Oak isolated to allow crews to replace the transformer base. | None | None | 8 | 471 | 63 | South | 140F3
129623 | 2014-08-18 | Defective Equipment | Electrical Failure | Cable fault S27734 W to TP8249-H1A | U/G Cable | XLPE | 167 | 129 | 359 | East | 77M2
129625 | 2014-08-19 | Scheduled Outage | Construction | Crews isolated X30904 and X30533 to set a pole | None | None | 9 | 120 | 18 | Central | UN07
129626 | 2014-08-19 | Scheduled Outage | Construction | Transformer TP5994 at 13 Live Oak was isolated to allow crew to replace transformer and base. 9 customer were affected for 398 minutes. Barrahven (140F3). ID# 129626 | None | None | 9 | 398 | 60 | South | 140F3
129629 | 2014-08-19 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change broken crossarms & broken porcelain insulators. Transformers X22685 & X24948 were interupted during this work | None | None | 14 | 499 | 116 | East | BCHF3
129632 | 2014-08-19 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X29602 (PCB OIL) | None | None | 4 | 236 | 16 | East | SO10
129633 | 2014-08-19 | Scheduled Outage | Construction | install new riser and switches to P182 on AQ11 circuit. | None | None | 1 | 67 | 1 | East | AQ11
129634 | 2014-08-19 | Scheduled Outage | Maintenance | Transformer #X32910 isolated by crew for transformer maintenance | None | None | 7 | 290 | 34 | West | 28F2
129635 | 2014-08-19 | Scheduled Outage | Construction | replace primary cables and rider switches S21290 feeding V769 | None | None | 1 | 312 | 5 | Central | UX08
129636 | 2014-08-19 | Scheduled Outage | Construction | Transformer #X47969 isolated by crew to transfer plant | None | None | 11 | 240 | 44 | Central | UW05
129637 | 2014-08-19 | Scheduled Outage | Construction | Transformer #X47974 isolated by crew to transfer plant | None | None | 11 | 345 | 63 | Central | UW05
129638 | 2014-08-19 | Scheduled Outage | Maintenance | Transformer #X5732 isolated by crew to replace blown arrestors and switches | None | None | 5 | 130 | 11 | South | 180F6
129639 | 2014-08-19 | Foreign Interference | Vehicle | A pole was hit at Dwyer Hill and Golfclub way, in a MVA. Also on Ashton Station Rd, and Ormrod at S22783, a phase and neutral came down. Circuit isolated for repairs. | Pole | Unknown \ Other | 183 | 239 | 729 | West | BECKF2
129639 | 2014-08-19 | Foreign Interference | Vehicle | A pole was hit at Dwyer Hill and Golfclub way, in a MVA. Also on Ashton Station Rd, and Ormrod at S22783, a phase and neutral came down. Circuit isolated for repairs. | Pole | Unknown \ Other | 250 | 186 | 775 | West | BECKF2
129639 | 2014-08-19 | Foreign Interference | Vehicle | A pole was hit at Dwyer Hill and Golfclub way, in a MVA. Also on Ashton Station Rd, and Ormrod at S22783, a phase and neutral came down. Circuit isolated for repairs. | Pole | Unknown \ Other | 646 | 187 | 2013 | West | BECKF2
129640 | 2014-08-20 | Unknown/Other | Unknown | No apparant cause found | None | None | 22 | 148 | 54 | South | 160F3
129641 | 2014-08-20 | Scheduled Outage | Construction | Transformer TP5993 at 34 Live Oak was isolated to allow crew to replace transformer and base. 10 Customers were affectedfor 463 minutes. Barrhaven (140F3). ID# 129641 | None | None | 10 | 463 | 77 | South | 140F3
129643 | 2014-08-20 | Scheduled Outage | Maintenance | Transformer TP3231 at 169 Moresby was isolated to allow crew to remove sand from transformer base. 10 customer were affected. Bridlewood (BRF1). ID# | None | None | 10 | 167 | 28 | West | BRDF1
129644 | 2014-08-20 | Scheduled Outage | Maintenance | Transformer TP10523 at 10 Offenbach was isolated to allow crew perform transformer soil remediation. 23 customer affected for 361 minutes. Queens Way Carelton (160F2). ID# 129644 | None | None | 10 | 361 | 60 | South | 160F2
129645 | 2014-08-20 | Scheduled Outage | Forced Switching | 11 W phase transformers on Westphalian, Tapadero and Balikun were forced out of service to allow crew to perform out of phase switching. 106 customers were affected for 16 minutes. TerryFox (TFXF4). ID# 129645 | None | None | 106 | 16 | 28 | West | BRDF1
129646 | 2014-08-20 | Scheduled Outage | Construction | Transformer TP9855 at 161 Westphalian was isolated to allow crew to install 4 new transformers. 4 customers were affected for 178 minutes. TerryFox (TFXF4). ID# 129646 | None | None | 4 | 178 | 12 | West | BRDF1
129647 | 2014-08-20 | Scheduled Outage | Maintenance | follow up repairs from previous maintenance. | None | None | 1 | 106 | 2 | East | 2201
129648 | 2014-08-20 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER TP3231 FOR MAINTENANCE | None | None | 10 | 202 | 34 | West | BRDF1
129649 | 2014-08-20 | Scheduled Outage | Construction | replace primary cable from vault to dip pole and replace cutouts at pole. | None | None | 1 | 192 | 3 | Central | UX08
129650 | 2014-08-20 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X09829 TO TRANSFER HYDRO PLANT TO NEW TRANSFORMER | None | None | 2 | 120 | 4 | South | 140F4
129651 | 2014-08-20 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X07250 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 50 | 1 | West | 624F6
129654 | 2014-08-20 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32259 opened up due to bird interference | O/H Switchgear | Fused Cutout | 1 | 119 | 2 | West | BECKF2
129655 | 2014-08-21 | Scheduled Outage | Maintenance | schedualled outage to allow crew to replace a defective switch and replace insulators. | None | None | 10 | 126 | 21 | East | AJ06
129656 | 2014-08-21 | Scheduled Outage | Maintenance | schedualled outage to allow crew to prove spare duct. | None | None | 132 | 55 | 121 | Central | UX08
129657 | 2014-08-21 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace a leaking transformer, TE2965 | None | None | 1 | 114 | 2 | South | LGFF1
129658 | 2014-08-21 | Scheduled Outage | Maintenance | K732 isolated to allow crew to replace terminations and clean and tighten connections | None | None | 27 | 128 | 58 | East | AQ07
129659 | 2014-08-21 | Scheduled Outage | Building/ High Load Move | ISOLATED TRANSFORMER X29257 AND TRANSFERED TO ANOTHER PHASE FOR PHASE BALANCING | None | None | 6 | 5 | 0 | East | UG02
129660 | 2014-08-21 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32900 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 209 | 21 | West | 28F2
129661 | 2014-08-21 | Defective Equipment | Mechanical Failure | RX2024 R phase recloser is faulted | O/H Switchgear | Recloser (1ph) | 125 | 28 | 58 | West | BECKF2
129661 | 2014-08-21 | Defective Equipment | Mechanical Failure | RX2024 R phase recloser is faulted | O/H Switchgear | Recloser (1ph) | 125 | 55 | 115 | West | BECKF2
129661 | 2014-08-21 | Defective Equipment | Mechanical Failure | RX2024 R phase recloser is faulted | O/H Switchgear | Recloser (1ph) | 125 | 60 | 125 | West | BECKF2
129661 | 2014-08-21 | Defective Equipment | Mechanical Failure | RX2024 R phase recloser is faulted | O/H Switchgear | Recloser (1ph) | 158 | 7 | 18 | West | BECKF2
129661 | 2014-08-21 | Defective Equipment | Mechanical Failure | RX2024 R phase recloser is faulted | O/H Switchgear | Recloser (1ph) | 186 | 7 | 22 | West | BECKF2
129661 | 2014-08-21 | Defective Equipment | Mechanical Failure | RX2024 R phase recloser is faulted | O/H Switchgear | Recloser (1ph) | 186 | 16 | 50 | West | BECKF2
129661 | 2014-08-21 | Defective Equipment | Mechanical Failure | RX2024 R phase recloser is faulted | O/H Switchgear | Recloser (1ph) | 186 | 146 | 453 | West | BECKF2
129664 | 2014-08-21 | Defective Equipment | Electrical Failure | RX2005 auto reclosed due to defective transfomrer at X35765. RX2005 auto reclosed twice when crews tried to enerigze the bad transformer. | O/H Transformer | O/H Transformer (1ph) | 1 | 30 | 0 | West | BECKF2
129664 | 2014-08-21 | Defective Equipment | Electrical Failure | RX2005 auto reclosed due to defective transfomrer at X35765. RX2005 auto reclosed twice when crews tried to enerigze the bad transformer. | O/H Transformer | O/H Transformer (1ph) | 1 | 69 | 1 | West | BECKF2
129664 | 2014-08-21 | Defective Equipment | Electrical Failure | RX2005 auto reclosed due to defective transfomrer at X35765. RX2005 auto reclosed twice when crews tried to enerigze the bad transformer. | O/H Transformer | O/H Transformer (1ph) | 1 | 250 | 4 | West | BECKF2
129665 | 2014-08-21 | Lightning | Lightning | Fuse at S23923 opened due to lightning strike. | O/H Transformer | O/H Transformer (1ph) | 1 | 198 | 3 | West | BECKF2
129668 | 2014-08-22 | Defective Equipment | Electrical Failure | defective xfmr | O/H Transformer | O/H Transformer (1ph) | 1 | 324 | 5 | West | 43F3
129670 | 2014-08-23 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X29729 at 488 Bloor opened due to animal contact, Russell (TB14) | O/H Transformer | O/H Transformer (1ph) | 6 | 70 | 7 | East | TB14
129671 | 2014-08-23 | Defective Equipment | Defective Equipment/ Material | SE15B opened due to defective cable section between TP6450 and TP6449. | U/G Cable | XLPE | 37 | 14 | 9 | South | 140F1
129671 | 2014-08-23 | Defective Equipment | Defective Equipment/ Material | SE15B opened due to defective cable section between TP6450 and TP6449. | U/G Cable | XLPE | 50 | 22 | 18 | South | 140F1
129671 | 2014-08-23 | Defective Equipment | Defective Equipment/ Material | SE15B opened due to defective cable section between TP6450 and TP6449. | U/G Cable | XLPE | 90 | 86 | 129 | South | 140F1
129672 | 2014-08-24 | Defective Equipment | Defective Equipment/ Material | S28404 W phase termination found defective | U/G Cable Attachement | Termination \ Stress Cone | 33 | 59 | 32 | Central | AK07
129673 | 2014-08-24 | Scheduled Outage | Construction | 27 KV O/H section on Hazeldan between Johnwoods and Fringewood Dr was isolated to allow crew to upgrade circuit and extens 44KV circuit down on Iber Rd | None | None | 114 | 490 | 931 | West | JKGF5
129674 | 2014-08-24 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crew to change the elbows at TE1162 and switches & arrestors at S1136 | None | None | 8 | 166 | 22 | South | 200F3
129675 | 2014-08-24 | Unknown/Other | Unknown | A cable fault between SW92 & SW116 | Unknown \ Other | Unknown \ Other | 32 | 75 | 40 | East | 2202
129676 | 2014-08-24 | Scheduled Outage | Maintenance | Vault maintenance | None | None | 1 | 291 | 5 | East | TB1UQ
129678 | 2014-08-24 | Defective Equipment | Defective Equipment/ Material | Defective fuse cut out caused the transformer X3185 at 11 Panama to open. | O/H Switchgear | Fused Cutout | 25 | 170 | 71 | South | 200F2
129681 | 2014-08-25 | Scheduled Outage | Construction | UN07 W phase o/h section on Friel east of Laurier to install new poles and transfer plant. | None | None | 12 | 167 | 33 | Central | UN07
129682 | 2014-08-25 | Scheduled Outage | Construction | Isolate K041 to install new poles and transfer plant | None | None | 12 | 167 | 33 | Central | UN07
129683 | 2014-08-25 | Scheduled Outage | Maintenance | Replace transformer Base and terminate new primary cable | None | None | 7 | 385 | 45 | South | 200F5
129684 | 2014-08-25 | Scheduled Outage | Construction | Transformer X21506 at 1319 Avenue O isolated for transformer replacement | None | None | 4 | 282 | 19 | East | SO10
129685 | 2014-08-25 | Scheduled Outage | Vegetation Management | At 9:00 crews isolated section of TB06 from S18618 to end of line for tree removal. 16 customers affect. Russell (TB06) ID# 129685 | None | None | 16 | 300 | 80 | East | TB06
129687 | 2014-08-25 | Defective Equipment | Defective Equipment/ Material | Replaced broken fuse feeding transformer X21828 | O/H Switchgear | Fused Cutout | 8 | 55 | 7 | West | 28F1
129689 | 2014-08-26 | Scheduled Outage | Construction | UW07 overhead section between S24393 and Temp 152 was isolated to allow crew to crane in new poles. Woodroffe (UW07) ID# 129689. | None | None | 26 | 388 | 168 | Central | UW07
129690 | 2014-08-26 | Scheduled Outage | Construction | Transformer TP5325 was isolated to allow crew to replace leaking transformer. Centrepointe (87F3) ID# 129690. | None | None | 23 | 162 | 62 | South | 87F3
129692 | 2014-08-26 | Scheduled Outage | Construction | Transformer K573 @ 2816 Sandlewood was isolated to allow the crew to replace the transformer from a live front to a dead front. | None | None | 20 | 256 | 85 | East | UA05
129693 | 2014-08-26 | Scheduled Outage | Maintenance | Transformer TP3399 @ 5965 RENAUD RD was isolated to allow the crews to replace defective switches S20267. | None | None | 1 | 60 | 1 | East | CYRF1
129694 | 2014-08-26 | Scheduled Outage | Vegetation Management | The crews isolated the O/H from switch S20246 to EOL on COCHRANE ST to allow the crews to remove a tree. | None | None | 8 | 273 | 36 | East | UA07
129695 | 2014-08-26 | Scheduled Outage | Construction | 140F3 cable replacment by Steve Rutherford | None | None | 36 | 193 | 116 | South | 140F3
129696 | 2014-08-26 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X21356 | O/H Transformer | O/H Transformer (1ph) | 5 | 116 | 10 | East | V11F2
129697 | 2014-08-27 | Scheduled Outage | Construction | Transformer TE461 was isolated to allow crew to replace base and cable terminations. Stafford Rd (200F5) ID# 129697. | None | None | 13 | 392 | 85 | South | 200F5
129698 | 2014-08-27 | Scheduled Outage | Maintenance | TE1274 isolated to allow crew to clean and tighten connections IR scan showed hot spots. | None | None | 10 | 138 | 23 | East | 77M1
129699 | 2014-08-27 | Scheduled Outage | Construction | crew moving TP5989 from red to blue phase. | None | None | 12 | 142 | 28 | South | 140F3
129700 | 2014-08-27 | Scheduled Outage | Maintenance | changing SMD switches. | None | None | 1 | 30 | 0 | East | 7F4
129701 | 2014-08-27 | Scheduled Outage | Maintenance | changing SMD switch | None | None | 1 | 40 | 1 | East | 7F4
129702 | 2014-08-27 | Scheduled Outage | Vegetation Management | The O/H on Navo Dr from temp 18 was isolated to the EOL to allow the tree contractor to remove a tree from the O/H. | None | None | 45 | 294 | 220 | Central | UW06
129703 | 2014-08-27 | Scheduled Outage | Construction | Transformer X29610 at 1319 Avenue R isolated for transformer replacement. | None | None | 4 | 301 | 20 | East | SO10
129704 | 2014-08-27 | Scheduled Outage | Construction | Transformer X39679 at 2025 Sixth Line Rd. isolated for pole change | None | None | 1 | 145 | 2 | West | 624F6
129705 | 2014-08-27 | Scheduled Outage | Maintenance | A 4Kv vault V307 @ 335 Cooper was isolated to allow the contractor to remove asbestos and vault maintenance. | None | None | 1 | 310 | 5 | Central | UX03
129706 | 2014-08-27 | Scheduled Outage | Maintenance | Transformer X32781 at 1099 Maitland Ave. isolated to allow crew to reinsulate pole and install switches | None | None | 1 | 76 | 1 | Central | UC10
129707 | 2014-08-27 | Scheduled Outage | Maintenance | Transformer 269 was isolated to allow crew to replace defective insert. Bridlewood (BRDF4) ID# 129707. | None | None | 13 | 43 | 9 | West | BRDF4
129709 | 2014-08-28 | Scheduled Outage | Construction | Transformer TE117 was isolated to allow crew to replace transformer base. Startop (6F7) ID# 129709. | None | None | 1 | 2383 | 40 | East | 6F7
129710 | 2014-08-28 | Scheduled Outage | Vegetation Management | S27798 to EOL was isolated to allow Tree Removal by Contractor | None | None | 14 | 485 | 113 | Central | TD06
129711 | 2014-08-28 | Scheduled Outage | Maintenance | Routine Scheduled Vault Maintenance by Contractor | None | None | 1 | 113 | 2 | Central | TH11-NIU
129712 | 2014-08-28 | Scheduled Outage | Construction | Transformer TE2425 at 145 Woodridge was isolated to allow crew to replace transformer base and install new primary cable. | None | None | 1 | 394 | 7 | South | 49F2
129713 | 2014-08-28 | Scheduled Outage | Construction | Transformer TP5983 at 191 Thistledown was isolated to allow crew to replace transformer and base. 12 customers were affected for 350 minutes. Barrhaven (140F3). | None | None | 12 | 350 | 70 | South | 140F3
129714 | 2014-08-28 | Scheduled Outage | Maintenance | Transformer GLTE0104 at 654 Glenhurst Cres isolated to replace defective pedestal | None | None | 3 | 172 | 9 | East | BCHF1
129714 | 2014-08-28 | Scheduled Outage | Maintenance | Transformer GLTE0104 at 654 Glenhurst Cres isolated to replace defective pedestal | None | None | 8 | 23 | 3 | East | BCHF1
129714 | 2014-08-28 | Scheduled Outage | Maintenance | Transformer GLTE0104 at 654 Glenhurst Cres isolated to replace defective pedestal | None | None | 8 | 40 | 5 | East | BCHF1
129715 | 2014-08-28 | Scheduled Outage | Construction | Transformer X31096 at 180 Augusta St. isolated to allow crew to rearrange secondary. | None | None | 39 | 115 | 75 | Central | UD04
129716 | 2014-08-28 | Scheduled Outage | Vegetation Management | Change Transformer and clear vegetation | None | None | 17 | 262 | 74 | East | AA05
129717 | 2014-08-28 | Scheduled Outage | Vegetation Management | Tree Removal | None | None | 14 | 480 | 112 | Central | TD06
129718 | 2014-08-29 | Scheduled Outage | Construction | Transformer TE1577 at 994 Terra Nova was isolated to allow crew to replace leaking transformer. (Billberry 77M6). ID# 129718 | None | None | 10 | 132 | 22 | East | 77M6
129719 | 2014-08-29 | Foreign Interference | Wildlife (Bird/Animal) | Refused Transformer X33075 feeding VT122 at 61 McEwen Ave., cause of outage - squirrel | O/H Transformer | O/H Transformer (1ph) | 1 | 35 | 1 | Central | TD07
129721 | 2014-08-30 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X29873 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 7 | 57 | 7 | Central | TR09
129722 | 2014-08-29 | Defective Equipment | Electrical Failure | cable fault on radial feed to TP5878. | U/G Cable | XLPE | 1 | 665 | 11 | East | 77M6
129723 | 2014-08-31 | Unknown/Other | Unknown | UX04 & 06 A/R/A, Reports of lightning in the area,crews found nothing, UX04 trip RWB Inst wphase Time,UX06 RW Inst Wphase time, UXK1Y1(UX02) Wphase time | O/H Conductor | O/H Conductor | 207 | 43 | 148 | Central | UX04
129723 | 2014-08-31 | Unknown/Other | Unknown | UX04 & 06 A/R/A, Reports of lightning in the area,crews found nothing, UX04 trip RWB Inst wphase Time,UX06 RW Inst Wphase time, UXK1Y1(UX02) Wphase time | O/H Conductor | O/H Conductor | 275 | 43 | 197 | Central | UX02
129723 | 2014-08-31 | Unknown/Other | Unknown | UX04 & 06 A/R/A, Reports of lightning in the area,crews found nothing, UX04 trip RWB Inst wphase Time,UX06 RW Inst Wphase time, UXK1Y1(UX02) Wphase time | O/H Conductor | O/H Conductor | 334 | 44 | 245 | Central | UX06
129727 | 2014-09-01 | Scheduled Outage | Construction | Replace rusted TP10240 & extend primary cables | None | None | 1 | 452 | 8 | East | 6F10
129729 | 2014-09-01 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer x25004, bird contact - crow | O/H Transformer | O/H Transformer (1ph) | 5 | 81 | 7 | East | 7F4
129730 | 2014-09-01 | Defective Equipment | Defective Equipment/ Material | VE19B phase at 614 Eastvale opened due to defective B phase transformer at VE19. VE19 vault complete was isolated to allow crew to replace defective transformer. Beaconhill (BCHF3). ID#129730 | Vault Equipment | Transformer | 0 | 24 | 0 | East | BCHF3
129730 | 2014-09-01 | Defective Equipment | Defective Equipment/ Material | VE19B phase at 614 Eastvale opened due to defective B phase transformer at VE19. VE19 vault complete was isolated to allow crew to replace defective transformer. Beaconhill (BCHF3). ID#129730 | Vault Equipment | Transformer | 1 | 4 | 0 | East | BCHF3
129730 | 2014-09-01 | Defective Equipment | Defective Equipment/ Material | VE19B phase at 614 Eastvale opened due to defective B phase transformer at VE19. VE19 vault complete was isolated to allow crew to replace defective transformer. Beaconhill (BCHF3). ID#129730 | Vault Equipment | Transformer | 1 | 269 | 4 | East | BCHF3
129731 | 2014-09-02 | Defective Equipment | Defective Equipment/ Material | defective switch blue phase | O/H Switchgear | Fused Cutout | 19 | 114 | 36 | East | LTM01
129733 | 2014-09-02 | Scheduled Outage | Construction | Construction. | None | None | 10 | 143 | 24 | West | BRDF3
129734 | 2014-09-02 | Foreign Interference | Vehicle | 249F1 O/H section between CS24363 and TEMP 120 was isolated to allow crew to replace dammaged pole hit by MOV. ID# 129734 | None | None | 6 | 295 | 30 | East | LTM01
129735 | 2014-09-02 | Defective Equipment | Defective Equipment/ Material | Transformer X36946 opened due to defective transformer. ON call crew replaced defective transformer and all customers were restored. Richmond North (RHNF1). ID# 129735 | O/H Transformer | O/H Transformer (1ph) | 2 | 597 | 20 | West | RHNF1
129736 | 2014-09-02 | Defective Equipment | Mechanical Failure | Broken Cuttout at transformer | O/H Switchgear | Fused Cutout | 8 | 799 | 107 | East | UQ07
129737 | 2014-09-03 | Scheduled Outage | Construction | To in service and energize new overhead | None | None | 50 | 223 | 186 | Central | UN07
129739 | 2014-09-03 | Scheduled Outage | Construction | Construction | None | None | 10 | 419 | 70 | South | 140F3
129740 | 2014-09-03 | Scheduled Outage | Vegetation Management | Planned outage to allow tree crews to remove trees | None | None | 15 | 315 | 79 | East | UQ03
129741 | 2014-09-03 | Scheduled Outage | Construction | TE1590 isolated to change leaking transfomrer | None | None | 10 | 92 | 15 | South | 190F2
129742 | 2014-09-03 | Scheduled Outage | Construction | Hydro Pole replacement on Laurier ave. | None | None | 50 | 199 | 166 | Central | UN07
129743 | 2014-09-03 | Scheduled Outage | Construction | Transformer 4068 isolated to raise base to grade and install new transfmrer | None | None | 14 | 442 | 103 | West | BRDF6
129744 | 2014-09-03 | Scheduled Outage | Construction | UN07 hydro pole replacement | None | None | 20 | 303 | 101 | Central | UN07
129746 | 2014-09-03 | Scheduled Outage | Construction | To allow crews to upgrade supply cables. | None | None | 1 | 275 | 5 | Central | UX08
129747 | 2014-09-03 | Scheduled Outage | Construction | To allow Black & Mac to replace hydro pole on UN07 circuit. | None | None | 30 | 54 | 27 | Central | UN07
129749 | 2014-09-03 | Scheduled Outage | Construction | Transformer X24433 at 694 Morgan St. isolated for transformer change | None | None | 12 | 443 | 89 | East | AA03
129750 | 2014-09-03 | Scheduled Outage | Construction | Transformer X45166 at 1680 Cannon Cres. Isolated to allow contractor to transfer plant | None | None | 17 | 180 | 51 | Central | UW07
129751 | 2014-09-04 | Scheduled Outage | Construction | S14294 was opened to allow crew to upgrade overhead conductors. Janet King (JKGF5) ID# 129751. | None | None | 119 | 237 | 470 | West | JKGF5
129753 | 2014-09-04 | Scheduled Outage | Vegetation Management | schedualled outage for tree removal with a crane in backyards. | None | None | 10 | 305 | 51 | Central | UV03
129754 | 2014-09-04 | Scheduled Outage | Construction | Transformer TE462 was isolated to allow crew to replace transformer and cable. Stafford Road (200F5) ID# 129754. | None | None | 23 | 488 | 187 | South | 200F5
129755 | 2014-09-04 | Scheduled Outage | Maintenance | schedualled outage to allow crews to replace terminations, insulators and lightning arrestors. | None | None | 8 | 72 | 10 | East | ELW07
129756 | 2014-09-04 | Scheduled Outage | Construction | Transformer M34 was isolated to allow crew to upgrade transformer. Augusta (UD01) ID# 129756. | None | None | 40 | 205 | 137 | Central | UD01
129757 | 2014-09-04 | Scheduled Outage | Construction | pole replacement | None | None | 21 | 105 | 37 | Central | UN07
129758 | 2014-09-04 | Human Element | Switching Error | switching was being done to isolate MT26 and at MT25 to cable tgas fadded. Crew unable to identify which cable went to MT26. Wrong switch opened. Closed back in to restore power. | None | None | 17 | 1 | 0 | East | 2204
129761 | 2014-09-04 | Scheduled Outage | Construction | Leaking MT26 replaced and swollen elbow replaced. Scott Barkley. | None | None | 20 | 117 | 39 | East | 2204
129762 | 2014-09-04 | Scheduled Outage | Construction | schedualled outage to allow crews to transfer plant to new poles. | None | None | 13 | 130 | 28 | Central | UW07
129763 | 2014-09-04 | Scheduled Outage | Construction | Base and transformer replacement and cable re-configuration. Barrhaven Steve Rutherford | None | None | 23 | 349 | 134 | South | 140F3
129798 | 2014-09-06 | Adverse Weather | Extreme Wind | SB07 primary is down in the street. | O/H Conductor | O/H Conductor | 517 | 185 | 1594 | Central | SB07
129811 | 2014-09-06 | Lightning | Lightning | Downed conductor | O/H Conductor | O/H Conductor | 517 | 185 | 1594 | Central | SB07
129816 | 2014-09-06 | Lightning | Lightning | Lightning | O/H Conductor | O/H Conductor | 91 | 11 | 17 | Central | 5408
129816 | 2014-09-06 | Lightning | Lightning | Lightning | O/H Conductor | O/H Conductor | 786 | 11 | 144 | Central | 5407
129816 | 2014-09-06 | Lightning | Lightning | Lightning | O/H Conductor | O/H Conductor | 1601 | 11 | 294 | Central | TD12
129825 | 2014-09-06 | Adverse Weather | Extreme Wind | Tree on the O/H between Cedarvie and Greenbank caused the 22M26 CB to trip open | O/H Conductor | O/H Conductor | 1 | 16 | 0 | South | 22M26
129825 | 2014-09-06 | Adverse Weather | Extreme Wind | Tree on the O/H between Cedarvie and Greenbank caused the 22M26 CB to trip open | O/H Conductor | O/H Conductor | 1189 | 12 | 238 | South | 22M26
129825 | 2014-09-06 | Adverse Weather | Extreme Wind | Tree on the O/H between Cedarvie and Greenbank caused the 22M26 CB to trip open | O/H Conductor | O/H Conductor | 5329 | 131 | 11635 | South | 22M26
129826 | 2014-09-06 | Defective Equipment | Defective Equipment/ Material | S28190 opened due to defective cut out. | O/H Switchgear | Fused Cutout | 99 | 87 | 144 | West | ALEXF3
129827 | 2014-09-06 | Adverse Weather | Extreme Wind | S25440 R opened during the wind and lightning storm. Marchwood (MWDF3). | O/H Switchgear | Fused Cutout | 10 | 222 | 37 | West | MWDF3
129833 | 2014-09-06 | Adverse Weather | Extreme Wind | UV04 white phase primary down at rear of 19 Donnington | O/H Conductor | O/H Conductor | 66 | 147 | 162 | Central | UV04
129834 | 2014-09-06 | Adverse Weather | Extreme Wind | Tree Obstruction on the overhead | O/H Conductor | O/H Conductor | 80 | 27 | 36 | South | 170F3
129836 | 2014-09-06 | Defective Equipment | Defective Equipment/ Material | S14581 R opened due to defective transformer TP6084 and defective. While restoring the TP6084 crew found TP2311 at 80 Bradley defective. | U/G Transformer | Padmount (1ph) | 10 | 80 | 13 | West | MWDF3
129836 | 2014-09-06 | Defective Equipment | Defective Equipment/ Material | S14581 R opened due to defective transformer TP6084 and defective. While restoring the TP6084 crew found TP2311 at 80 Bradley defective. | U/G Transformer | Padmount (1ph) | 10 | 269 | 45 | West | MWDF3
129836 | 2014-09-06 | Defective Equipment | Defective Equipment/ Material | S14581 R opened due to defective transformer TP6084 and defective. While restoring the TP6084 crew found TP2311 at 80 Bradley defective. | U/G Transformer | Padmount (1ph) | 114 | 207 | 393 | West | MWDF3
129839 | 2014-09-06 | Adverse Weather | Extreme Wind | Trees on O/H run caused fuse to open. S10518 to EOL | O/H Switchgear | Fused Cutout | 12 | 1149 | 230 | Central | TD05
129842 | 2014-09-06 | Lightning | Lightning | Lightning storm | O/H Switchgear | Fused Cutout | 12 | 555 | 111 | Central | TW17
129854 | 2014-09-06 | Adverse Weather | Extreme Wind | S222 opened due to wires down at rear of 12 Trilium, due to storm activity | O/H Conductor | O/H Conductor | 16 | 2087 | 557 | South | 190F5
129856 | 2014-09-07 | Scheduled Outage | Vegetation Management | Isolated to allow for tree removal from overhead | None | None | 31 | 70 | 36 | Central | TD05
129859 | 2014-09-06 | Lightning | Lightning | S11180 RWB blew at 1929 Ogilvie suspected lightning stike from storm in the Ottawa area | O/H Switchgear | Fused Cutout | 1 | 1908 | 32 | East | 8F1
129860 | 2014-09-07 | Tree Contacts | Falling Tree | broken insulator at X46264 and tree on overhead 1 span away. | Pole Attachement | Insulator | 70 | 98 | 114 | Central | UW05
129861 | 2014-09-07 | Tree Contacts | Tree Growth/ Untrimmed Tree | G821 opened due to tree in proximity to the O/H primary line. | O/H Switchgear | Fused Cutout | 1 | 384 | 6 | East | 77M5
129862 | 2014-09-07 | Adverse Environment | Fire | TP6752 was forced out of service at request of fire department | None | None | 26 | 237 | 103 | East | LTM01
129866 | 2014-09-07 | Tree Contacts | Falling Tree | Tree contact. | O/H Conductor | O/H Conductor | 2 | 115 | 4 | East | BLKF5
129867 | 2014-09-08 | Scheduled Outage | Construction | Transformer TP3729 at 167 Romain was isolated to allow crew to install 8 new B phase transformers. Terry Fox (TFXF4 ). ID# 129867 | None | None | 34 | 131 | 74 | West | BRDF3
129868 | 2014-09-08 | Scheduled Outage | Maintenance | Board change, termination replace, secondary clean and torque | None | None | 13 | 135 | 29 | East | AQ09
129869 | 2014-09-08 | Scheduled Outage | Maintenance | Transformer #X38273 isolated by crew due to bad connections on the neutral | None | None | 11 | 45 | 8 | South | 180F4
129870 | 2014-09-08 | Scheduled Outage | Vegetation Management | Transformer #X35800 isolated by crew to remove vines and tree from transformer | None | None | 8 | 5 | 1 | South | 190F5
129871 | 2014-09-08 | Scheduled Outage | Construction | Transformer #X27426 isolated to transfer plant | None | None | 6 | 165 | 16 | East | AN05
129872 | 2014-09-08 | Defective Equipment | Defective Equipment/ Material | Defective Pot Head to VT200 at 1000 Castle Hill caused the TM28 CB to open | U/G Cable Attachement | Pothead | 39 | 4 | 3 | Central | TM3UC
129872 | 2014-09-08 | Defective Equipment | Defective Equipment/ Material | Defective Pot Head to VT200 at 1000 Castle Hill caused the TM28 CB to open | U/G Cable Attachement | Pothead | 41 | 9 | 6 | Central | TM3UC
129872 | 2014-09-08 | Defective Equipment | Defective Equipment/ Material | Defective Pot Head to VT200 at 1000 Castle Hill caused the TM28 CB to open | U/G Cable Attachement | Pothead | 519 | 2 | 17 | Central | TM3UC
129872 | 2014-09-08 | Defective Equipment | Defective Equipment/ Material | Defective Pot Head to VT200 at 1000 Castle Hill caused the TM28 CB to open | U/G Cable Attachement | Pothead | 1396 | 25 | 582 | Central | TM3UC
129872 | 2014-09-08 | Defective Equipment | Defective Equipment/ Material | Defective Pot Head to VT200 at 1000 Castle Hill caused the TM28 CB to open | U/G Cable Attachement | Pothead | 1398 | 61 | 1421 | Central | TM3UC
129873 | 2014-09-09 | Scheduled Outage | Maintenance | QT133 at 2 Aero Drive isolated to allow repairs to tower structure by contractor. | None | Transformer | 1 | 243 | 4 | South | 22M26
129874 | 2014-09-09 | Scheduled Outage | Construction | Transformers TE521 and TE522 isolated for cable and transformer replacement | None | None | 44 | 480 | 352 | South | 49F2
129875 | 2014-09-09 | Scheduled Outage | Construction | install new cables in base | None | None | 21 | 426 | 149 | South | 200F5
129877 | 2014-09-09 | Scheduled Outage | Construction | 2 transformers, X30730 and X30731 isolated by crew to add conductor to allow crews to install R & B phases to O/H | None | None | 27 | 205 | 92 | Central | UD04
129878 | 2014-09-09 | Scheduled Outage | Construction | Transformer #X23342 isolated by crew to replace pole | None | None | 1 | 235 | 4 | East | AA05
129879 | 2014-09-09 | Scheduled Outage | Maintenance | Transformer X35872 isolated by crew to replace service | None | None | 5 | 80 | 7 | South | EPWF1
129881 | 2014-09-09 | Tree Contacts | Falling Tree | To remove a downed tree from the conductor & replace an insulator | Pole Attachement | Insulator | 1 | 60 | 1 | East | BLKF5
129882 | 2014-09-09 | Human Element | Incorrect Records/ labelling | Wrong cable tags in the field | None | None | 8 | 1 | 0 | West | BRDF1
129884 | 2014-09-09 | Defective Equipment | Electrical Failure | Transformer TP9985 was isolated to allow crew to replace defective transformer. Marchwood (MWDF2) ID# . | U/G Transformer | Padmount (3ph) | 1 | 170 | 3 | West | MWDF2
129885 | 2014-09-10 | Scheduled Outage | Maintenance | Transformer #X25872 isolated by crew to investigate flickering lights | None | None | 2 | 10 | 0 | Central | SB11
129887 | 2014-09-10 | Foreign Interference | Wildlife (Bird/Animal) | S27730 fuse blew due to squirell contact at transformer X 35249. At the same time during switching, RX2010 was in parallel and it auto reclosed the same time as this fault. | O/H Transformer | O/H Transformer (1ph) | 9 | 47 | 7 | West | ALEXF3
129887 | 2014-09-10 | Foreign Interference | Wildlife (Bird/Animal) | S27730 fuse blew due to squirell contact at transformer X 35249. At the same time during switching, RX2010 was in parallel and it auto reclosed the same time as this fault. | O/H Transformer | O/H Transformer (1ph) | 27 | 72 | 32 | West | ALEXF3
129888 | 2014-09-10 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change 3 rotten poles & remove 2 dead ash trees | None | None | 121 | 384 | 774 | Central | TD06
129890 | 2014-09-10 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30556 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 53 | 30 | 26 | Central | UX03
129891 | 2014-09-10 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMERS TP5970 AND TP5976 | None | None | 42 | 380 | 266 | South | 140F3
129893 | 2014-09-10 | Scheduled Outage | Construction | Transformer TE550R isolated to allow crwes to replace cables and transformers | None | None | 22 | 425 | 156 | South | 200F5
129894 | 2014-09-10 | Scheduled Outage | Construction | reconfiguring cables | None | None | 42 | 388 | 272 | South | 140F3
129895 | 2014-09-10 | Scheduled Outage | Maintenance | Transformer TP3202 isolated to remove sand from base and cable injection on both sides of cables. | None | None | 9 | 345 | 52 | West | BRDF1
129897 | 2014-09-11 | Defective Equipment | Defective Equipment/ Material | Transformer TP5281 was isolated to allow crew to make repair defective S1475 hot line clamp, stir up and switch. Rideau Heights (180F1). ID# 129897 | O/H Conductor | Hot-Line Clamp | 2 | 59 | 2 | South | 72F6
129900 | 2014-09-11 | Scheduled Outage | Maintenance | KT9 isolated to allow crews to replace insulatros and arrestors. | None | None | 11 | 217 | 40 | East | 2211
129901 | 2014-09-11 | Scheduled Outage | Maintenance | Transformer #X40024 isolated by crew to repair 2 triplex services | None | None | 7 | 75 | 9 | South | 200F1
129902 | 2014-09-11 | Scheduled Outage | Construction | Construction. | None | None | 9 | 376 | 56 | South | 140F3
129903 | 2014-09-11 | Unknown/Other | Unknown | Crew reports a customer heard overhead wires arcing in the bush along Davidson road. Crews have walked the bush and no problem was found. | None | None | 3774 | 111 | 6982 | East | LTM01
129905 | 2014-09-11 | Tree Contacts | Other Vegetation | Transformer #X33664 opened up due to vine interference | O/H Switchgear | Fused Cutout | 8 | 70 | 9 | Central | TW22
129906 | 2014-09-11 | Scheduled Outage | Vegetation Management | UT03 from X24629 to EOL was isolated to allow crew to remove fallen tree. | None | None | 6 | 78 | 8 | East | UT03
129907 | 2014-09-11 | Scheduled Outage | Vegetation Management | X29635 and X34767 isolated to allow crew to remove trees from secondary. | None | None | 15 | 208 | 52 | East | SO03
129907 | 2014-09-11 | Scheduled Outage | Vegetation Management | X29635 and X34767 isolated to allow crew to remove trees from secondary. | None | None | 20 | 207 | 69 | East | SO03
129908 | 2014-09-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | TB07 breaker auto reclosed twice and was opened by system due to broken conductor at the R of 1152 Kenaston caused by an overgrown tree. | O/H Conductor | O/H Conductor | 0 | 28 | 0 | East | TB07
129908 | 2014-09-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | TB07 breaker auto reclosed twice and was opened by system due to broken conductor at the R of 1152 Kenaston caused by an overgrown tree. | O/H Conductor | O/H Conductor | 2 | 90 | 3 | East | TB07
129908 | 2014-09-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | TB07 breaker auto reclosed twice and was opened by system due to broken conductor at the R of 1152 Kenaston caused by an overgrown tree. | O/H Conductor | O/H Conductor | 280 | 58 | 271 | East | TB07
129910 | 2014-09-11 | Tree Contacts | Other Vegetation | Vines growing into S469 | O/H Switchgear | Fused Cutout | 2 | 70 | 2 | South | 160F1
129910 | 2014-09-11 | Tree Contacts | Other Vegetation | Vines growing into S469 | O/H Switchgear | Fused Cutout | 4 | 15 | 1 | South | 160F1
129915 | 2014-09-11 | Tree Contacts | Broken Branch | Limb contact shorted out 2 phases downstream of primary fuse S20150 | O/H Conductor | Unknown \ Other | 85 | 75 | 106 | Central | TW17
129915 | 2014-09-11 | Tree Contacts | Broken Branch | Limb contact shorted out 2 phases downstream of primary fuse S20150 | O/H Conductor | Unknown \ Other | 129 | 98 | 211 | Central | TW17
129916 | 2014-09-12 | Scheduled Outage | Construction | Replace leaking transformer. | U/G Transformer | Padmount (1ph) | 16 | 177 | 47 | East | 4801F8
129917 | 2014-09-12 | Scheduled Outage | Construction | Defective transformer. | U/G Transformer | Padmount (1ph) | 12 | 94 | 19 | East | 6F10
129918 | 2014-09-12 | Scheduled Outage | Construction | Transformer #X32319 isolated by crew for a new service | None | None | 15 | 65 | 16 | Central | UC03
129920 | 2014-09-13 | Scheduled Outage | Construction | 27kv transformer TP10286 isolated to allow crew to remove excess sand and core drill base. Transformers 7557 and 7558 were also affected by the outage. | None | None | 19 | 272 | 86 | West | JKGF4
129921 | 2014-09-13 | Tree Contacts | Broken Branch | 200F2 A/R because a limb fell on the O/H at swicth S107 @ 31 VIRGIL RD which caused switch to burn up. | O/H Switchgear | Fused Cutout | 8 | 26 | 3 | South | 200F2
129921 | 2014-09-13 | Tree Contacts | Broken Branch | 200F2 A/R because a limb fell on the O/H at swicth S107 @ 31 VIRGIL RD which caused switch to burn up. | O/H Switchgear | Fused Cutout | 457 | 120 | 914 | South | 200F2
129922 | 2014-09-13 | Defective Equipment | Mechanical Failure | While offloading Hinchey for Hydro One, System Office was forced to open TH03 breaker which was feeding TM3SH to allow crew to open a defective switch (only 2 phases closed) at VT579 which caused the TM3SH to trip when it was closed. Lemieux Island and th | Customer Owned | Customer-Owned | 50 | 2 | 2 | Central | TM3SH
129922 | 2014-09-13 | Defective Equipment | Mechanical Failure | While offloading Hinchey for Hydro One, System Office was forced to open TH03 breaker which was feeding TM3SH to allow crew to open a defective switch (only 2 phases closed) at VT579 which caused the TM3SH to trip when it was closed. Lemieux Island and th | Customer Owned | Customer-Owned | 181 | 2 | 6 | Central | 4301
129923 | 2014-09-13 | Defective Equipment | Mechanical Failure | Transformer X35641 fuse was found blown due to defective switch. Lincoln Heights (TD12) ID# 129923. | O/H Switchgear | Fused Cutout | 9 | 76 | 11 | Central | TD12
129924 | 2014-09-14 | Scheduled Outage | Construction | Transformer X21586 was isolated to allow crew to relocate transformer and replace cutouts and insulators. Leitrim (249F1) ID# 129924. | None | None | 1 | 284 | 5 | East | LTM01
129925 | 2014-09-14 | Scheduled Outage | Construction | Transformer P352 was isolated to allow crew to replace leaking transformer. Bayswater (UJ05) ID# 129925. | None | None | 2 | 437 | 15 | Central | UJ05
129926 | 2014-09-14 | Foreign Interference | Customer-Cut Trees | Transformer X24550 fuse blew due to customer cutting a tree and it falling into wires. Blackburn (4F5) ID# 129926. | None | None | 1 | 82 | 1 | East | BLKF5
129927 | 2014-09-14 | Tree Contacts | Broken Branch | UT04 circuit was opened by System to allow crew to remove tree limb from primary overhead that was burning up. Eastview (UT04) ID# 129927. | None | None | 400 | 2 | 13 | East | UT04
129929 | 2014-09-15 | Scheduled Outage | Construction | UW07 overhead section between Temp 152 and Temp 154 was isolated to allow crew to install new poles and transfer plant. Woodroffe (UW07) ID# 129929. | None | None | 47 | 422 | 331 | Central | UW07
129930 | 2014-09-15 | Scheduled Outage | Maintenance | Transformer TP3181 was isolated to allow crew to replace riser switches. Limebank (7F1) ID# 129930. | None | None | 1 | 54 | 1 | East | 7F1
129932 | 2014-09-15 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X23550 | None | None | 6 | 245 | 24 | East | AA04
129933 | 2014-09-15 | Scheduled Outage | Construction | UW07 overhead section between S29157 and Temp 154 was isolated to allow crew to install new poles and transfer plant. Woodroffe (UW07) ID# 129933. | None | None | 40 | 221 | 147 | Central | UW07
129934 | 2014-09-15 | Scheduled Outage | Construction | Transformer TE520 and TE519 were isolated to allow crew to replace transformers and bases. Bayshore (49F2) ID# 129934. | None | None | 34 | 633 | 359 | South | 49F2
129935 | 2014-09-15 | Scheduled Outage | Vegetation Management | TW17 overhead section from S24252 to EOL was isolated to allow crew to remove tree. Woodroffe (TW17) ID# 129935. | None | None | 19 | 44 | 14 | Central | TW17
129936 | 2014-09-16 | Scheduled Outage | Construction | Transfer vault to new primary feed. | None | None | 7 | 258 | 30 | Central | UD02
129937 | 2014-09-16 | Scheduled Outage | Construction | TP5892 isolated to replace transformer & base, energize new cable section. | None | None | 11 | 373 | 68 | South | 140F4
129939 | 2014-09-16 | Scheduled Outage | Construction | TE518 & TP10001 isolated for transformer & cable replacement | None | None | 43 | 392 | 281 | South | 49F2
129940 | 2014-09-16 | Scheduled Outage | Construction | TE548 isolated for cable & transformer replacement | None | None | 18 | 420 | 126 | South | 200F5
129941 | 2014-09-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X45162 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 16 | 10 | 3 | Central | UW07
129942 | 2014-09-16 | Scheduled Outage | Construction | Transformer #X33395 isolated by crew to replace service | None | None | 5 | 36 | 3 | Central | TD05
129943 | 2014-09-16 | Scheduled Outage | Construction | Transformer #X45163 isolated by crew to transfer plant | None | None | 6 | 65 | 6 | Central | UW07
129946 | 2014-09-16 | Scheduled Outage | Maintenance | Transformer #X24190 isolated by crew to replace hot line clamp | None | None | 16 | 10 | 3 | East | 8F3
129947 | 2014-09-16 | Defective Equipment | Defective Equipment/ Material | Cable fault between VT2 and VT40. | U/G Cable | PILC | 1 | 25 | 0 | Central | 601
129947 | 2014-09-16 | Defective Equipment | Defective Equipment/ Material | Cable fault between VT2 and VT40. | U/G Cable | PILC | 2 | 16 | 1 | Central | 601
129947 | 2014-09-16 | Defective Equipment | Defective Equipment/ Material | Cable fault between VT2 and VT40. | U/G Cable | PILC | 23 | 79 | 30 | Central | 601
129947 | 2014-09-17 | Defective Equipment | Defective Equipment/ Material | Cable fault between VT2 and VT40. | U/G Cable | PILC | 23 | 2 | 1 | Central | 601
129948 | 2014-09-17 | Scheduled Outage | Construction | Crews opened transformer X30964 infront of 295 Nelson to replace hydro pole. | None | None | 5 | 185 | 15 | Central | UN03
129949 | 2014-09-17 | Scheduled Outage | Construction | To allow hydro crews to replace hydro pole. | None | None | 14 | 187 | 44 | Central | UN07
129950 | 2014-09-17 | Scheduled Outage | Construction | Transformer at this location was opened to allow crews to replace hydro pole. | None | None | 10 | 187 | 31 | Central | UN07
129952 | 2014-09-17 | Scheduled Outage | Construction | TE464 isolated for transformer & primary cable replacement | None | None | 20 | 469 | 156 | South | 200F5
129953 | 2014-09-17 | Scheduled Outage | Construction | Schedualled outage to rearrange underground cables | None | None | 205 | 328 | 1121 | West | TFXF4
129954 | 2014-09-17 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X14148 FOR LOAD BALANCING | None | None | 2 | 15 | 0 | East | 7F4
129955 | 2014-09-17 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X14158 FOR LOAD BALANCING | None | None | 4 | 20 | 1 | East | 7F4
129956 | 2014-09-17 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X14141 FOR LOAD BALANCING | None | None | 3 | 30 | 2 | East | 7F4
129957 | 2014-09-17 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X14151 FOR LOAD BALANCING | None | None | 2 | 5 | 0 | East | 7F4
129958 | 2014-09-17 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X42417 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 7 | 46 | 5 | Central | TR09
129959 | 2014-09-17 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30535 AND X30534 TO REPLACE POLES | None | None | 28 | 200 | 93 | Central | UN07
129962 | 2014-09-17 | Scheduled Outage | Construction | UW07 overhead section isolated to repair damaged primary conductor causing an outage to transformer X47507 | None | None | 16 | 53 | 14 | Central | UW07
129963 | 2014-09-17 | Scheduled Outage | Construction | transformer X47501 opened to allow for transfer of plant and transformer replacement | None | None | 14 | 500 | 117 | Central | UW07
129964 | 2014-09-17 | Scheduled Outage | Construction | Transformer #X33430 isolated by crew to replace transformer | None | None | 5 | 95 | 8 | Central | UW02
129965 | 2014-09-17 | Scheduled Outage | Construction | 2 transformer #X30537 and X30538 isolated by crew for a pole change | None | None | 45 | 170 | 128 | Central | UN07
129966 | 2014-09-17 | Scheduled Outage | Maintenance | Transformer #X34240 isolated by crew to replace connections at house and pole | None | None | 7 | 40 | 5 | Central | SM06
129967 | 2014-09-17 | Scheduled Outage | Maintenance | Transformer #X37059 isolated by crew to replace connections at pole and replace service | None | None | 19 | 85 | 27 | South | 72F4
129968 | 2014-09-18 | Foreign Interference | Vehicle | UG04 tripped open due to motor vehicle accident at 67 Beechwood. | Pole | Pole | 9 | 101 | 15 | East | UG04
129968 | 2014-09-18 | Foreign Interference | Vehicle | UG04 tripped open due to motor vehicle accident at 67 Beechwood. | Pole | Pole | 18 | 418 | 125 | East | UG04
129968 | 2014-09-18 | Foreign Interference | Vehicle | UG04 tripped open due to motor vehicle accident at 67 Beechwood. | Pole | Pole | 59 | 3 | 3 | East | UG04
129968 | 2014-09-18 | Foreign Interference | Vehicle | UG04 tripped open due to motor vehicle accident at 67 Beechwood. | Pole | Pole | 396 | 307 | 2026 | East | UG04
129969 | 2014-09-18 | Scheduled Outage | Construction | Transformer X30527 was isolated to allow crew to replace pole. Henderson (UN07) ID# 129969. | None | None | 5 | 170 | 14 | Central | UN07
129970 | 2014-09-18 | Scheduled Outage | Construction | Transformer X30528 was isolated to allow crew to replace pole. Henderson (UN07) ID# 129970. | None | None | 10 | 170 | 28 | Central | UN07
129972 | 2014-09-18 | Scheduled Outage | Maintenance | At 08:52am crews isolated TE1954 @ 3444 Wyman to allow crews to perform soil remediation. 21 customers affected for __mins. Uplands (4801F8) ID#129972 | None | None | 21 | 627 | 219 | East | 4801F8
129975 | 2014-09-18 | Scheduled Outage | Construction | To allow K-Line to install new poles & transfer plant to from the B phase to the W phase | None | None | 21 | 184 | 64 | Central | UW07
129978 | 2014-09-19 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 9 | 9 | 1 | East | 2203
129978 | 2014-09-19 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 31 | 6 | 3 | East | 2203
129978 | 2014-09-19 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 156 | 2 | 5 | East | 2203
129978 | 2014-09-19 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 157 | 1 | 3 | East | 2203
129978 | 2014-09-19 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 160 | 82 | 219 | East | 2203
129979 | 2014-09-19 | Scheduled Outage | Construction | install secondary in transformer | None | None | 9 | 149 | 22 | East | 8F1
129981 | 2014-09-20 | Scheduled Outage | Construction | V339 isolated to replace primary cables from overhead to vault. | None | None | 1 | 391 | 7 | Central | SA23
129983 | 2014-09-20 | Loss Of Supply | Transmission Inadvertent | Tree caused Hydro One's conductor to fall down and open the BECKF2 circuit. | None | None | 649 | 67 | 725 | West | BECKF2
129984 | 2014-09-20 | Defective Equipment | Defective Equipment/ Material | Red phase line tap broken off O/H circuit at the rear of 1685 Altra Vista. | O/H Conductor | Ampact | 66 | 223 | 245 | East | UQ05
129985 | 2014-09-21 | Unknown/Other | Unknown | Crew patrolled circuit and faund no issues. | Unknown \ Other | Unknown \ Other | 433 | 13 | 94 | West | BRDF7
129986 | 2014-09-21 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 103 | 58 | 100 | South | 72F6
129987 | 2014-09-21 | Defective Equipment | Mechanical Failure | SUSPECTED CABLE FAULT ON ELW07 CABLE BETWEEN TA, S16503 AND SC4 | U/G Cable | PILC | 20 | 77 | 26 | East | ELW07
129987 | 2014-09-21 | Defective Equipment | Mechanical Failure | SUSPECTED CABLE FAULT ON ELW07 CABLE BETWEEN TA, S16503 AND SC4 | U/G Cable | PILC | 1142 | 29 | 552 | East | ELW07
129987 | 2014-09-21 | Defective Equipment | Mechanical Failure | SUSPECTED CABLE FAULT ON ELW07 CABLE BETWEEN TA, S16503 AND SC4 | U/G Cable | PILC | 1751 | 36 | 1051 | East | ELW07
129988 | 2014-09-21 | Defective Equipment | Electrical Failure | Blue phase cable fault found between TE1496 and S27791 | U/G Cable | XLPE | 19 | 156 | 49 | East | 77M1
129990 | 2014-09-21 | Scheduled Outage | Forced Switching | Transformer #K284 opened by crew due to: bad underground from K284 feeding pedistal 284P1, disconnected in kiosk | None | None | 19 | 25 | 8 | Central | AK04
129991 | 2014-09-21 | Scheduled Outage | Maintenance | Metering repair | None | None | 1 | 24 | 0 | Central | TL6TS
129992 | 2014-09-21 | Scheduled Outage | Maintenance | Replace defective insulators. | None | None | 1 | 139 | 2 | East | 48M4
129993 | 2014-09-21 | Defective Equipment | Defective Equipment/ Material | Transformer #X23043 opened up due to blown transformer fuse | O/H Switchgear | Fused Cutout | 1 | 78 | 1 | Central | TK2AC
129994 | 2014-09-21 | Scheduled Outage | Maintenance | 2 transformers, X30176 and X30175 isolated by crew to change the wire | None | None | 14 | 168 | 39 | Central | UJ03
129995 | 2014-09-21 | Loss Of Supply | Transmission Inadvertent | Hydro One had issue with tap changers at Hawthorne. | None | None | 1094 | 10 | 182 | East | 249F2
129995 | 2014-09-21 | Loss Of Supply | Transmission Inadvertent | Hydro One had issue with tap changers at Hawthorne. | None | None | 3810 | 5 | 318 | East | LTM01
129997 | 2014-09-22 | Scheduled Outage | Construction | Transformer replacement and set up for cable replacement. | None | None | 8 | 432 | 58 | South | 140F4
129998 | 2014-09-22 | Scheduled Outage | Construction | TP5511 isolated to allow crews to replace leaking transformer. | None | None | 8 | 464 | 62 | South | 190F5
129999 | 2014-09-22 | Scheduled Outage | Construction | Transformer #X23673 isolated by crew to replace transformer | None | None | 10 | 300 | 50 | East | UB07
130001 | 2014-09-22 | Scheduled Outage | Construction | Transformer #X47959 isolated by crew to string in new wire | None | None | 10 | 17 | 3 | Central | UW05
130002 | 2014-09-23 | Foreign Interference | Dig-In | The 160F1 CB A/R due to cable dig in at 47 Woodridge. | U/G Cable | XLPE | 34 | 77 | 44 | South | 160F1
130002 | 2014-09-23 | Foreign Interference | Dig-In | The 160F1 CB A/R due to cable dig in at 47 Woodridge. | U/G Cable | XLPE | 62 | 129 | 133 | South | 160F1
130003 | 2014-09-23 | Scheduled Outage | Construction | Transformer Base Replacement | None | None | 8 | 386 | 51 | South | 140F4
130005 | 2014-09-23 | Foreign Interference | Wildlife (Bird/Animal) | squirrel contact at transformer X45446 at rear of 1136 Bloomsbury | O/H Transformer | O/H Transformer (1ph) | 15 | 28 | 7 | Central | TW05
130005 | 2014-09-23 | Foreign Interference | Wildlife (Bird/Animal) | squirrel contact at transformer X45446 at rear of 1136 Bloomsbury | O/H Transformer | O/H Transformer (1ph) | 379 | 34 | 215 | Central | TW05
130006 | 2014-09-23 | Scheduled Outage | Maintenance | reframe pole X26491 | None | None | 9 | 120 | 18 | Central | UN07
130008 | 2014-09-23 | Scheduled Outage | Maintenance | change transformer taps to B | None | None | 1 | 15 | 0 | East | TR02UQ
130009 | 2014-09-24 | Scheduled Outage | Construction | To allow Black & Macdonald Line crews to change poles | None | None | 11 | 60 | 11 | Central | UN07
130011 | 2014-09-24 | Scheduled Outage | Construction | replace primary cables, porcelain insulators, and upgrade overhead connection on dead end pole. | None | None | 1 | 275 | 5 | Central | UX08
130012 | 2014-09-24 | Foreign Interference | Vandalism/Sabotage | RX2050 and RX2020 opened due to sabotage to XPLE cable dips feeding TE2377 at Innes and Jeanne D'Arc. Billberry (77M2). ID# 130012 | O/H Switchgear | Fused Cutout | 1 | 140 | 2 | East | 77M2
130012 | 2014-09-24 | Foreign Interference | Vandalism/Sabotage | RX2050 and RX2020 opened due to sabotage to XPLE cable dips feeding TE2377 at Innes and Jeanne D'Arc. Billberry (77M2). ID# 130012 | O/H Switchgear | Fused Cutout | 1809 | 97 | 2925 | East | 77M2
130012 | 2014-09-24 | Foreign Interference | Vandalism/Sabotage | RX2050 and RX2020 opened due to sabotage to XPLE cable dips feeding TE2377 at Innes and Jeanne D'Arc. Billberry (77M2). ID# 130012 | O/H Switchgear | Fused Cutout | 2982 | 10 | 497 | East | 77M2
130014 | 2014-09-24 | Scheduled Outage | Construction | to allow contractor to replace hydro poles | None | None | 14 | 217 | 51 | Central | UW05
130014 | 2014-09-24 | Scheduled Outage | Construction | to allow contractor to replace hydro poles | None | None | 48 | 320 | 256 | Central | UW05
130015 | 2014-09-24 | Scheduled Outage | Vegetation Management | Tree removal | None | None | 1 | 19 | 0 | West | BECKF2
130016 | 2014-09-24 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X24241 | None | None | 8 | 205 | 27 | East | AF06
130017 | 2014-09-24 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 2 | 111 | 4 | East | 77M2
130018 | 2014-09-24 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X14232 TO REPLACE POLE | None | None | 1 | 102 | 2 | East | 7F4
130019 | 2014-09-24 | Defective Equipment | Mechanical Failure | ISOLATED TRANSFORMER X4163 TO REPLACE LIVE LINE CLAMP DUE TO SPARKING WIRES CALLED IN BY CUSTOMER | Secondary \ Service | O/H Service | 5 | 24 | 2 | South | 170F1
130020 | 2014-09-25 | Scheduled Outage | Maintenance | schedualled outage to remove basse for oil clean up | None | None | 16 | 456 | 122 | East | 4801F8
130023 | 2014-09-25 | Scheduled Outage | Construction | transfering plant | None | None | 18 | 195 | 58 | Central | UW05
130024 | 2014-09-25 | Scheduled Outage | Construction | transformer change | None | None | 5 | 197 | 16 | East | UB07
130025 | 2014-09-26 | Scheduled Outage | Construction | Soil remediation & transformer replacement | None | Padmount (1ph) | 6 | 516 | 52 | South | 130F5
130026 | 2014-09-26 | Scheduled Outage | Construction | Transformer X35922 at 5496 Fallowfield Rd. isolated by crew to hang a new transformer (old one not being removed). | None | None | 1 | 73 | 1 | West | RHNF1
130027 | 2014-09-26 | Scheduled Outage | Maintenance | Transformer X11794 at 7440 Flewellyn Rd. isolated by crew to change switch | None | None | 1 | 47 | 1 | West | BECKF2
130028 | 2014-09-26 | Scheduled Outage | Maintenance | Transformer X11791 at 7479 Flewellyn Rd. isolated by crew to change switch | None | None | 3 | 24 | 1 | West | BECKF2
130029 | 2014-09-26 | Scheduled Outage | Construction | Transformer X47883 at 1073 Cline Cres. Isolated by contractor to transfer plant | None | None | 15 | 254 | 64 | Central | UW05
130030 | 2014-09-26 | Scheduled Outage | Construction | Transformer X12855 at 354 River Rd. isolated by crew to rearange plant | None | None | 4 | 35 | 2 | East | 7F2
130031 | 2014-09-27 | Defective Equipment | Mechanical Failure | REPLACED DEFECTIVE SWITCH FEEDING TRANSFORMER X22583 | O/H Switchgear | Fused Cutout | 9 | 252 | 38 | East | V11F2
130032 | 2014-09-27 | Scheduled Outage | Construction | To allow contractor to replace cable inside substation. | None | None | 1 | 348 | 6 | West | 624F6
130034 | 2014-09-27 | Scheduled Outage | Maintenance | Clean and Torque | None | None | 1 | 197 | 3 | East | TB2JP
130035 | 2014-09-26 | Defective Equipment | Electrical Failure | Defective underground cable | U/G Cable | XLPE | 12 | 10 | 2 | East | BLKF4
130035 | 2014-09-26 | Defective Equipment | Electrical Failure | Defective underground cable | U/G Cable | XLPE | 25 | 107 | 45 | East | BLKF4
130036 | 2014-09-28 | Scheduled Outage | Maintenance | To allow Kroon Electric to make repairs to S-552 in VT736 | None | None | 1 | 279 | 5 | Central | 614
130039 | 2014-09-29 | Scheduled Outage | Maintenance | To remove sand from base. | None | None | 11 | 93 | 17 | South | LGFF2
130040 | 2014-09-29 | Scheduled Outage | Construction | Transformer & Base replacement TP5900 and new cable section from S22535. | None | None | 9 | 352 | 53 | South | 140F4
130041 | 2014-09-29 | Scheduled Outage | Maintenance | To repair TP3189 defective insert. | None | None | 9 | 209 | 31 | West | BRDF1
130042 | 2014-09-29 | Scheduled Outage | Construction | To re align U/G cables | None | None | 13 | 198 | 43 | East | 7F2
130043 | 2014-09-29 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X25037 (TRANSFORMER UP-GRADE FROM A 50KVA TO A 75KVA) | None | None | 24 | 60 | 24 | East | AF06
130044 | 2014-09-29 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER TP5900 | None | None | 11 | 435 | 80 | South | 140F4
130045 | 2014-09-29 | Human Element | Switching Error | 24/7 crew opened the wrong switch | None | None | 1 | 10 | 0 | East | 5309
130046 | 2014-09-29 | Defective Equipment | Electrical Failure | On-Call crew replaced defective transformer X40189 at 34 Bedale. | O/H Transformer | O/H Transformer (1ph) | 9 | 316 | 47 | South | 49F6
130048 | 2014-09-30 | Scheduled Outage | Construction | Transformers TE512, TE513 and TE517 were isolated to allow crew to replace transformers and cables. Bayshore 49F4, ID# 130048. | None | None | 83 | 573 | 793 | South | 49F4
130049 | 2014-09-30 | Scheduled Outage | Maintenance | Switch S24415 was isolated to allow crew to replace switches. Uplands (4801F8) ID# 130049. | None | None | 49 | 46 | 38 | East | 4801F8
130050 | 2014-09-30 | Defective Equipment | Electrical Failure | K-Line reports old arrester has flashed near where crew was working. S13876 1126 Sherman found blown, replaced and closed. | Pole Attachement | Arrester | 55 | 19 | 17 | Central | UW07
130051 | 2014-09-30 | Scheduled Outage | Construction | Transformer #X27089 isolated by crew to replace transformer | None | None | 13 | 95 | 21 | East | TB14
130052 | 2014-09-30 | Scheduled Outage | Maintenance | Transformer #X33147 isolated by crew to repair a service | None | None | 6 | 80 | 8 | Central | TD05
130053 | 2014-09-30 | Scheduled Outage | Construction | Transformer TP5901 @ 33 Alberni was isolated by the crew to allow them to replace the transformer and base | None | None | 11 | 358 | 66 | South | 140F4
130054 | 2014-09-30 | Scheduled Outage | Construction | Contractor isolated transformer X47863 to move plant for pole replacement next week. | None | None | 17 | 30 | 8 | Central | UW07
130056 | 2014-10-01 | Scheduled Outage | Construction | Transformers TP9864, TP9857, TP9858, TP9859 and TP9860 were isolated to allow crew to re-configure primary. Terry Fox (TFXF4) ID# 130056. | None | None | 50 | 265 | 221 | West | TFXF4
130057 | 2014-10-01 | Scheduled Outage | Construction | Transformer TE465 was isolated to allow crew to replace transformer and cables. Stafford Rd (200F5) ID# 130057. | None | None | 22 | 444 | 163 | South | 200F5
130058 | 2014-10-02 | Scheduled Outage | Construction | Transformer TP5893 isolated to allow for transformer and base replacement, Barrhaven 140F5, ID # 130058 | None | None | 8 | 444 | 59 | South | 140F5
130059 | 2014-10-02 | Scheduled Outage | Construction | Transformers TP10287 and TP5237 isolated for cable reconfiguration, Janet King JKGF4, ID # 130059 | None | None | 36 | 155 | 93 | West | JKGF4
130060 | 2014-10-02 | Scheduled Outage | Construction | Transformer TE1772 isolated to replace a leaking transformer, Barrhaven 140F5, ID # 130060 | None | None | 9 | 138 | 21 | South | 140F5
130062 | 2014-10-02 | Scheduled Outage | Construction | installation of new hydro poles. | None | None | 43 | 536 | 384 | Central | UW07
130063 | 2014-10-02 | Scheduled Outage | Construction | Transformer and Base replacements | None | None | 34 | 161 | 91 | South | 49F4
130063 | 2014-10-02 | Scheduled Outage | Construction | Transformer and Base replacements | None | None | 68 | 236 | 267 | South | 49F4
130067 | 2014-10-03 | Scheduled Outage | Vegetation Management | Transformer #X32511 isolated by crew to remove branch from open buss service | None | None | 11 | 106 | 19 | Central | TD01
130068 | 2014-10-03 | Foreign Interference | Crane | Downed Primary by contractor contact | None | None | 63 | 12 | 13 | South | 72F4
130068 | 2014-10-03 | Foreign Interference | Crane | Downed Primary by contractor contact | None | None | 63 | 34 | 36 | South | 72F4
130068 | 2014-10-03 | Foreign Interference | Crane | Downed Primary by contractor contact | None | None | 349 | 27 | 157 | South | 72F4
130073 | 2014-10-04 | Foreign Interference | Foreign Objects | Refused transformer X26770 at 1782 McMaster Ave. | None | None | 6 | 20 | 2 | East | AJ06
130074 | 2014-10-05 | Scheduled Outage | Construction | planned outage to allow crew to replace leaking transformer TE1872 | None | None | 3 | 288 | 14 | South | 47F6
130076 | 2014-10-06 | Scheduled Outage | Construction | Transformer K734 interupted to isolate switch S29606 to transfer plant to new pole, Gladstone UX04 ID # 130076 | None | None | 10 | 195 | 32 | Central | UX04
130077 | 2014-10-06 | Scheduled Outage | Construction | Transformer K1124 interupted to isolate S23330 and transfer plant to new pole, Gladstone UX04, ID # 130077 | None | None | 13 | 194 | 42 | Central | UX04
130078 | 2014-10-06 | Scheduled Outage | Construction | PLANNED OUTAGE FOR TRANSFORMER BASE REPLACMENT | None | None | 9 | 342 | 51 | South | 140F4
130079 | 2014-10-06 | Scheduled Outage | Construction | UW07 overhead section at S13876 isolated to transfer to reconfigure to new plant, Woodroffe UW07, ID # 130079 | None | None | 12 | 431 | 86 | Central | UW07
130081 | 2014-10-06 | Scheduled Outage | Maintenance | planned outage to replace arc stranglers | None | None | 34 | 79 | 45 | East | 77M1
130082 | 2014-10-06 | Scheduled Outage | Construction | Transformer #X24633 isolated by crew for a service upgrade | None | None | 12 | 45 | 9 | East | UT03
130083 | 2014-10-06 | Scheduled Outage | Construction | Transformer #X35922 isolated by crew to re-arrange plant | None | None | 1 | 60 | 1 | West | RHNF1
130084 | 2014-10-06 | Scheduled Outage | Construction | Transformer K1075 interupted to isolate switch S18608 to transfer plant to new pole, Florence UF08 ID # 130084 | None | None | 9 | 230 | 34 | Central | UF08
130085 | 2014-10-06 | Scheduled Outage | Construction | Transformer K984 interupted to isolate switch S19891 to transfer plant to new pole, Gladstone UX04 ID # 130085 | None | None | 9 | 230 | 34 | Central | UF08
130086 | 2014-10-06 | Scheduled Outage | Construction | Vault V296 isolated for cable replacement, Gladstone UX10, ID # 130086 | None | None | 1 | 356 | 6 | Central | UX10
130087 | 2014-10-06 | Defective Equipment | Electrical Failure | defective 13kv transformer on three phase bank | O/H Transformer | O/H Transformer (3ph) | 1 | 238 | 4 | Central | TK1UN
130088 | 2014-10-07 | Adverse Environment | Fire | working fire | None | None | 11 | 21 | 4 | Central | TW22
130089 | 2014-10-07 | Scheduled Outage | Construction | TP5670 isolated for transformer replacment. | None | None | 10 | 373 | 62 | South | 140F3
130091 | 2014-10-07 | Scheduled Outage | Construction | TE510 isolated to replace transformer. | None | None | 22 | 304 | 111 | South | 160F1
130094 | 2014-10-07 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 66 | 296 | 326 | Central | TH11-NIU
130095 | 2014-10-07 | Defective Equipment | Defective Equipment/ Material | Customer secondary connections have failed. | Secondary \ Service | U/G Service | 1 | 499 | 8 | West | 624F6
130096 | 2014-10-07 | Scheduled Outage | Construction | Transformer replacement. | None | None | 18 | 517 | 155 | South | 200F5
130097 | 2014-10-08 | Tree Contacts | Broken Branch | Branch found on 624F6 overhead section at 5 Campbell Ried. | None | None | 2 | 139 | 5 | West | 624F6
130097 | 2014-10-08 | Tree Contacts | Broken Branch | Branch found on 624F6 overhead section at 5 Campbell Ried. | None | None | 1693 | 146 | 4120 | West | 624F6
130098 | 2014-10-08 | Tree Contacts | Other Vegetation | Transformer X31652 at 140 Fenitman opened due to vines on the O/H . Riverdale (SR07). ID# 130098 | O/H Transformer | O/H Transformer (1ph) | 5 | 208 | 17 | Central | SR07
130099 | 2014-10-08 | Scheduled Outage | Construction | UX08 circuit from TEMP 32 to EOL isolated to allow crews to transfer plant to new poles. | None | None | 27 | 181 | 81 | Central | UX08
130100 | 2014-10-08 | Scheduled Outage | Construction | P221 isolated to allow crew to transfer plant to new poles. | None | None | 14 | 10 | 2 | Central | UX09
130101 | 2014-10-08 | Scheduled Outage | Construction | TP5887 isolated for transformer replacment. | None | None | 11 | 398 | 73 | South | 140F4
130102 | 2014-10-08 | Scheduled Outage | Construction | To replace 2 transformers, and broken inserts | None | None | 30 | 289 | 144 | West | TFXF6
130104 | 2014-10-08 | Scheduled Outage | Construction | 2 transformers, X32786 and X33781 isolated by crew to re-locate plant | None | None | 13 | 30 | 6 | Central | UW03
130105 | 2014-10-08 | Scheduled Outage | Construction | Switch replacement and sand removal from transformer bases. | None | None | 41 | 237 | 162 | East | 7F4
130107 | 2014-10-08 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMERS X32787 AND X32789 TO TRANSFER HYDRO PLANT | None | None | 15 | 60 | 15 | Central | UW03
130108 | 2014-10-08 | Adverse Weather | Extreme Wind | Wind caused RW phases to wrap together. | None | None | 149 | 104 | 258 | Central | TW17
130108 | 2014-10-08 | Adverse Weather | Extreme Wind | Wind caused RW phases to wrap together. | None | None | 573 | 37 | 353 | Central | TW17
130108 | 2014-10-08 | Adverse Weather | Extreme Wind | Wind caused RW phases to wrap together. | None | None | 878 | 86 | 1258 | Central | TW17
130109 | 2014-10-08 | Defective Equipment | Defective Equipment/ Material | Cable fault. | U/G Cable | XLPE | 22 | 19 | 7 | East | ELW10
130109 | 2014-10-08 | Defective Equipment | Defective Equipment/ Material | Cable fault. | U/G Cable | XLPE | 759 | 28 | 354 | East | ELW10
130110 | 2014-10-08 | Adverse Weather | Extreme Wind | RX2032 Red phase only opened. Circuit was patrolled no problem found. | Unknown \ Other | Unknown \ Other | 33 | 95 | 52 | West | 43F3
130111 | 2014-10-08 | Scheduled Outage | Construction | Broken pole | None | None | 1 | 102 | 2 | South | 170F1
130112 | 2014-10-09 | Scheduled Outage | Construction | Transformer TP5682W was isolated to allow crew to replace transformer. Barrhaven (140F4) ID# 130112. | None | None | 10 | 347 | 58 | South | 140F4
130114 | 2014-10-09 | Scheduled Outage | Construction | Transformer TE2533 was isolated to allow crew to upgrade transformer. QCH (160F3) ID# 130114. | None | None | 1 | 122 | 2 | South | 160F3
130115 | 2014-10-09 | Scheduled Outage | Construction | Switch G468 was isolated to allow crew to replace defective switch. Limebank (7F2) ID# 130115. | None | None | 1 | 45 | 1 | East | 7F2
130116 | 2014-10-09 | Scheduled Outage | Construction | TFXF4 transformers between PP2179 and TP9924 were interrupted to allow crew to perform switching on out of phase condition. Terry Fox (TFXF4) ID# 130116. | None | None | 74 | 11 | 14 | West | TFXF4
130117 | 2014-10-09 | Scheduled Outage | Construction | Transformers fed from S18823 were interrupted to allow crew to switch on out of phase condition. Fallowfield (FAL02) ID# 130117. | None | None | 98 | 10 | 16 | South | FAL03
130118 | 2014-10-09 | Scheduled Outage | Construction | Transformer TP9923 was isolated to allow crew to replace leaking transformer. Terry Fox (TFXF4) ID# 130118. | None | None | 4 | 80 | 5 | West | TFXF4
130119 | 2014-10-09 | Scheduled Outage | Construction | S12985 was isolated to allow crew to replace switches. Limebank (7F2) ID# 130119. | None | None | 110 | 27 | 50 | East | 7F2
130120 | 2014-10-09 | Scheduled Outage | Construction | Transformer #X27294 isolated by crew for PCB replacement | None | None | 10 | 200 | 33 | East | UA07
130121 | 2014-10-09 | Scheduled Outage | Construction | The crews isolate the O/H at 732 Courtney and Wembley area to allow them to transfer plant to new poles. | None | None | 121 | 313 | 631 | Central | TD06
130122 | 2014-10-09 | Scheduled Outage | Construction | Vault isolated to allow crew to install new cable and transfer hydro plant to new pole. Bob Rolland. | None | None | 1 | 278 | 5 | Central | UX10
130123 | 2014-10-09 | Scheduled Outage | Construction | Westcliffe transformer and cable replacement. New TP10480. | None | None | 24 | 393 | 157 | South | 200F5
130124 | 2014-10-09 | Defective Equipment | Defective Equipment/ Material | A defective cable at TP10480 R phase caused the fuse to blow at S16684. | U/G Cable | Unknown \ Other | 141 | 79 | 186 | South | 200F5
130125 | 2014-10-10 | Scheduled Outage | Construction | White phase transformers between G395 and S10218 were isolated to allow crerw to replace both switches, and replace TE2048. Limebank (7F4) ID# 130125. | None | None | 29 | 169 | 82 | East | 7F4
130126 | 2014-10-10 | Scheduled Outage | Construction | Transformer TE3043 @ 3748 Twinn Falls was isolated to allow the crew to change out leaking transformer. | None | None | 7 | 128 | 15 | East | 7F1
130127 | 2014-10-10 | Scheduled Outage | Construction | Transformer TP2590 @ 32 Windbrook Cres was isolated to allow the crews to replace defective transformer | None | None | 6 | 184 | 18 | West | BRDF1
130128 | 2014-10-11 | Scheduled Outage | Maintenance | Vault maintenance on VT702 and VT769, CMHC | None | None | 1 | 254 | 4 | East | TO2UB
130129 | 2014-10-11 | Scheduled Outage | Maintenance | Equipment Maintenance by Contractor and HOL Crew | None | None | 1 | 314 | 5 | East | 77M5
130130 | 2014-10-12 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact caused fuse at X23272 to open. | None | None | 6 | 108 | 11 | Central | TK2AC
130131 | 2014-10-12 | Defective Equipment | Defective Equipment/ Material | Defective transformer feeding the Giant Tiger store. | O/H Transformer | O/H Transformer (3ph) | 1 | 273 | 5 | East | V11F1
130132 | 2014-10-13 | Defective Equipment | Electrical Failure | Faulty opening mechanism on the AFT1 breaker at Brookfield was arching and station was filling with smoke. Dumped the ELW11 circuit. | Station Equipment | Primary Switchgear | 574 | 5 | 48 | East | ELW11
130133 | 2014-10-13 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31149 TO REPLACE TRIPLEX SERVICE | None | None | 5 | 117 | 10 | Central | SA22
130134 | 2014-10-13 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X301170 TO REPLACE TRIPLEX SERVICE | None | None | 3 | 65 | 3 | Central | TH11-NIU
130135 | 2014-10-14 | Scheduled Outage | Vegetation Management | Tree Trimming | None | None | 30 | 303 | 152 | Central | 505
130136 | 2014-10-14 | Scheduled Outage | Construction | To install new poles and transfer plant. | None | None | 28 | 508 | 237 | Central | UW07
130137 | 2014-10-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X10653 TO REPLACE PRIMARY INSULATORS | None | None | 4 | 90 | 6 | West | 28F3
130138 | 2014-10-14 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMER X30676, X30861, AND X31868 TO REPLACE POLES | None | None | 34 | 180 | 102 | Central | UF08
130139 | 2014-10-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33785 AND X32790 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 19 | 30 | 10 | Central | UW03
130141 | 2014-10-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35095 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 13 | 30 | 6 | Central | UW03
130142 | 2014-10-14 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to repair transformer | None | None | 11 | 70 | 13 | South | FAL02
130143 | 2014-10-14 | Scheduled Outage | Construction | Transformer #X27879 isolated by crew to transfer plant | None | None | 9 | 230 | 34 | East | UZ11
130144 | 2014-10-14 | Scheduled Outage | Vegetation Management | Transformer #X26037 isolated by crew to remove large branch from triplex | None | None | 7 | 20 | 2 | Central | TK2AC
130145 | 2014-10-15 | Scheduled Outage | Construction | Allow crews to replace SMD switches. | None | None | 25 | 26 | 11 | South | FAL02
130146 | 2014-10-15 | Defective Equipment | Corrosion | ISOLATED TRANSFORMER X34789 TO REPLACE DEFECTIVE SECONDAY CONNECTIONS | Secondary \ Service | O/H Service | 14 | 15 | 4 | Central | TD06
130148 | 2014-10-15 | Scheduled Outage | Vegetation Management | To allow forestry crews to clear a large tree from the vicinity of the O/H conductor | None | None | 41 | 137 | 94 | Central | TR3UY
130152 | 2014-10-15 | Scheduled Outage | Construction | to transfer plant to new poles | None | None | 16 | 210 | 56 | Central | UW07
130153 | 2014-10-16 | Scheduled Outage | Maintenance | Soil remediation. | None | None | 17 | 400 | 113 | East | 77M1
130154 | 2014-10-16 | Scheduled Outage | Construction | To allow crew to reconfigure overhead line for future transformer installation. | None | None | 30 | 470 | 235 | Central | UW05
130155 | 2014-10-16 | Tree Contacts | Broken Branch | Fuse at S501 opened due to tree contact. | None | None | 79 | 21 | 28 | South | 72F4
130157 | 2014-10-16 | Scheduled Outage | Construction | Transformer X48441 at 1192 Field St. isolated to allow contractor to rearrange plant - called in by Jordan Foot of K-Line. | None | None | 16 | 23 | 6 | Central | UW07
130158 | 2014-10-17 | Scheduled Outage | Construction | planned outage to allow crew to replace a leaking xfmr | None | None | 8 | 136 | 18 | West | TFXF4
130159 | 2014-10-17 | Scheduled Outage | Construction | To install 11 new transformers. | None | None | 58 | 197 | 190 | East | LTM01
130160 | 2014-10-17 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 34 | 244 | 138 | East | 77M1
130164 | 2014-10-18 | Scheduled Outage | Construction | Transformer #X27707 isolated by crew to replace triplex | None | None | 8 | 27 | 4 | East | AJ06
130167 | 2014-10-18 | Tree Contacts | Broken Branch | Tree Branch across insulator caused S14715 RW to blow as well as SCV66901-F RW to blow. Circuit sectionalized to restore power. | O/H Switchgear | Fused Cutout | 67 | 34 | 38 | Central | TK2AC
130167 | 2014-10-18 | Tree Contacts | Broken Branch | Tree Branch across insulator caused S14715 RW to blow as well as SCV66901-F RW to blow. Circuit sectionalized to restore power. | O/H Switchgear | Fused Cutout | 232 | 95 | 367 | Central | TK2AC
130169 | 2014-10-18 | Scheduled Outage | Construction | To allow contractors to install temp ''hording'' inside the vault to protect the electrical equipment from construction work over the next few weeks. | None | None | 1 | 332 | 6 | South | 49F5
130170 | 2014-10-19 | Scheduled Outage | Construction | Vault 63 was isolated to allow crew to reconfigure cable riser. Richmond South (28F3) ID# 130170. | None | None | 2 | 345 | 12 | West | 28F3
130171 | 2014-10-19 | Scheduled Outage | Construction | Fuller Building vault maintenance and Hydro Crew to repair leaking transformer. | None | None | 1 | 349 | 6 | Central | 613
130173 | 2014-10-20 | Scheduled Outage | Construction | Transformer TP5888 was isolated to allow crew to reconfigure the primary cables. Barrhaven (140F4) ID# 130173. | None | None | 9 | 436 | 65 | South | 140F4
130174 | 2014-10-20 | Unknown/Other | Unknown | S23425 white phase fuse blew due to unknown reason. Church (AA04) ID# 130174. | Unknown \ Other | Unknown \ Other | 78 | 90 | 117 | East | AA04
130175 | 2014-10-20 | Scheduled Outage | Construction | Transformer NPTE0081 at 62A Horner Dr. isolated by crew to make secondary repairs. | None | None | 10 | 38 | 6 | South | 49F6
130176 | 2014-10-20 | Scheduled Outage | Construction | Transformer X30557 at 224 Cooper St. isolated by crew for pole change. | None | None | 7 | 195 | 23 | Central | UX10
130177 | 2014-10-20 | Scheduled Outage | Construction | Transformer X28085 at 768 Garner Ave isolated by crew to change PCB transformer | None | None | 7 | 185 | 22 | East | UZ04
130178 | 2014-10-20 | Scheduled Outage | Construction | Transformer X28142 at 2626 Hobson Rd isolated by crew to change PCB transformer | None | None | 7 | 180 | 21 | East | UZ04
130179 | 2014-10-20 | Scheduled Outage | Construction | V301 isolated to install new cable and transfer to new pole. | None | None | 1 | 195 | 3 | Central | UX10
130180 | 2014-10-20 | Scheduled Outage | Construction | Transformer TP9877 @ 259 Livery was isolated to allow the crews to install and energize 5 new transformer | None | None | 12 | 198 | 40 | West | TFXF4
130181 | 2014-10-20 | Scheduled Outage | Construction | Transformer TP3696 was isolated to allow crew to replace leaking transformer. Limebank (7F2) ID# 130181. | None | None | 25 | 281 | 117 | East | 7F2
130182 | 2014-10-20 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X27966 (PCB OIL) | None | None | 2 | 195 | 6 | East | UZ07
130183 | 2014-10-21 | Defective Equipment | Mechanical Failure | Cable fault | U/G Cable | XLPE | 15 | 60 | 15 | West | 39F3
130183 | 2014-10-21 | Defective Equipment | Mechanical Failure | Cable fault | U/G Cable | XLPE | 51 | 116 | 99 | West | 39F3
130184 | 2014-10-21 | Scheduled Outage | Construction | Changing customer to new transformer | None | None | 4 | 60 | 4 | West | 624F6
130185 | 2014-10-21 | Scheduled Outage | Construction | replace transformer base | None | None | 12 | 536 | 107 | West | BRDF6
130187 | 2014-10-21 | Scheduled Outage | Construction | To transfer plant | None | None | 21 | 243 | 85 | Central | UN07
130188 | 2014-10-21 | Scheduled Outage | Vegetation Management | Section of UQ05 W from X14452 isolated for tree removal by crane | None | None | 10 | 280 | 47 | East | UQ05
130191 | 2014-10-22 | Scheduled Outage | Construction | S26866 isolated to allow crew to crane in a new pole in backyard and re-insulate 9 poles, Munster 43F3, ID # 130191 | None | None | 17 | 315 | 89 | West | 43F3
130192 | 2014-10-22 | Unknown/Other | Unknown | Fused switch S14366 white phase opened, no cause found, Lietrim 249F1, ID # 13019 | Unknown \ Other | Unknown \ Other | 468 | 61 | 476 | East | LTM01
130197 | 2014-10-22 | Human Element | Protection Setting | C from Hydro One, Nepean TS was affected. | None | None | 16 | 79 | 21 | South | 200F2
130197 | 2014-10-22 | Human Element | Protection Setting | C from Hydro One, Nepean TS was affected. | None | None | 234 | 79 | 308 | South | 200F3
130197 | 2014-10-22 | Human Element | Protection Setting | C from Hydro One, Nepean TS was affected. | None | None | 692 | 79 | 911 | South | 200F1
130197 | 2014-10-22 | Human Element | Protection Setting | C from Hydro One, Nepean TS was affected. | None | None | 2073 | 108 | 3731 | South | 22M24
130197 | 2014-10-22 | Human Element | Protection Setting | C from Hydro One, Nepean TS was affected. | None | None | 2408 | 108 | 4334 | South | 22M25
130197 | 2014-10-22 | Human Element | Protection Setting | C from Hydro One, Nepean TS was affected. | None | None | 2954 | 77 | 3791 | South | 22M28
130197 | 2014-10-22 | Human Element | Protection Setting | C from Hydro One, Nepean TS was affected. | None | None | 3168 | 68 | 3590 | South | LGFF1
130197 | 2014-10-22 | Human Element | Protection Setting | C from Hydro One, Nepean TS was affected. | None | None | 3520 | 95 | 5573 | South | 22M23
130197 | 2014-10-22 | Human Element | Protection Setting | C from Hydro One, Nepean TS was affected. | None | None | 5695 | 66 | 6264 | South | 22M27
130197 | 2014-10-22 | Human Element | Protection Setting | C from Hydro One, Nepean TS was affected. | None | None | 5841 | 63 | 6133 | South | 22M26
130198 | 2014-10-23 | Scheduled Outage | Maintenance | P265 isolated to repair transformer and replalce switches on pole. | None | None | 1 | 111 | 2 | Central | SB06
130199 | 2014-10-23 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to remove TP10553 from its base and cleanup spilled oil | None | None | 8 | 441 | 59 | East | 77M6
130201 | 2014-10-23 | Scheduled Outage | Construction | To allow Hydro Ottawa crews & Sproule Electric crews to install utility poles | None | None | 1 | 369 | 6 | South | 200F1
130203 | 2014-10-23 | Scheduled Outage | Vegetation Management | S12538 opened, to EOL affecting 3 overhead transformers, X27804, 5484A-0285H, X27801, to allow crew to allow forestry crew to remove tree. | None | None | 23 | 335 | 128 | East | UZ05
130204 | 2014-10-23 | Scheduled Outage | Construction | replace transformer | None | None | 1 | 212 | 4 | West | MWDF4
130205 | 2014-10-23 | Scheduled Outage | Maintenance | 13kv vault VT350 isolated for customer vault mtce. | None | None | 1 | 137 | 2 | East | ELW09
130206 | 2014-10-23 | Defective Equipment | Mechanical Failure | Primary neutral broke and fell down | O/H Conductor | Unknown \ Other | 4 | 100 | 7 | East | LTM01
130207 | 2014-10-24 | Scheduled Outage | Maintenance | S19731 to isolate PT190 to allow crew to replace fuses. | None | None | 1 | 96 | 2 | Central | TR1UN
130209 | 2014-10-25 | Scheduled Outage | Construction | V307 at 255 Cooper isolated to allow crew to change primary cables. | None | None | 71 | 153 | 181 | Central | UX03
130210 | 2014-10-25 | Scheduled Outage | Construction | V306 at 311 Cooper was isolated to allow crews to change primary cables and customer to perform vault maintenance. | None | None | 1 | 474 | 8 | Central | UX03
130211 | 2014-10-25 | Scheduled Outage | Construction | V304 at 309 Cooper was isolated to allow crews to change primary cables and customer to perform vault maintenance. Gladestone (UX03) | None | None | 1 | 475 | 8 | Central | UX03
130213 | 2014-10-25 | Scheduled Outage | Maintenance | Substation maintenance. | None | None | 1 | 396 | 7 | East | 48M5
130217 | 2014-10-27 | Scheduled Outage | Maintenance | Soil remidation. | None | None | 6 | 256 | 26 | South | 190F2
130219 | 2014-10-27 | Scheduled Outage | Construction | To transfer TP5889 from the 140F4 to the FAL02. | None | None | 1 | 311 | 5 | South | 140F4
130221 | 2014-10-27 | Scheduled Outage | Maintenance | To remove TE3043 from base for oil clean up. | None | None | 15 | 420 | 105 | East | 7F1
130223 | 2014-10-27 | Scheduled Outage | Construction | V770 isolated to allow crews to replace priamry cables. | None | None | 1 | 348 | 6 | Central | UX08
130226 | 2014-10-27 | Unknown/Other | Unknown | UW07 breaker opened under hold off protection. No cause found. | Unknown \ Other | Unknown \ Other | 1 | 217 | 4 | Central | UW07
130226 | 2014-10-27 | Unknown/Other | Unknown | UW07 breaker opened under hold off protection. No cause found. | Unknown \ Other | Unknown \ Other | 540 | 42 | 378 | Central | UW07
130227 | 2014-10-27 | Foreign Interference | Dig-In | Dig in | U/G Transformer | Padmount (1ph) | 9 | 226 | 34 | South | 87F1
130227 | 2014-10-27 | Foreign Interference | Dig-In | Dig in | U/G Transformer | Padmount (1ph) | 9 | 235 | 35 | South | 87F1
130227 | 2014-10-27 | Foreign Interference | Dig-In | Dig in | U/G Transformer | Padmount (1ph) | 20 | 26 | 9 | South | 87F1
130228 | 2014-10-27 | Scheduled Outage | Construction | allow contractor to connect new secondaries. | None | None | 2 | 65 | 2 | East | LTM01
130231 | 2014-10-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X20236 opened up due to broken transformer switch | O/H Switchgear | Fused Cutout | 9 | 210 | 32 | East | 249F2
130232 | 2014-10-28 | Defective Equipment | Defective Equipment/ Material | V117 was isolated from S16091 to allow crew to replace defectvie R phase transformer. | U/G Transformer | Padmount (1ph) | 1 | 82 | 1 | Central | UW05
130233 | 2014-10-28 | Scheduled Outage | Maintenance | Transformer #X32429 isolated by crew to replace connections at pole | None | None | 6 | 135 | 14 | Central | TW22
130234 | 2014-10-28 | Scheduled Outage | Maintenance | replace defective insert on transformer TP2598 | U/G Cable Attachement | Elbow \ Insert | 10 | 102 | 17 | West | TFXF6
130235 | 2014-10-29 | Tree Contacts | Falling Tree | Tree fell into the lines. | None | None | 940 | 88 | 1379 | East | LTM01
130236 | 2014-10-29 | Scheduled Outage | Construction | To Replace single phase mini-pad transformer | None | None | 11 | 151 | 28 | East | CYRF3
130237 | 2014-10-29 | Scheduled Outage | Construction | UW07 O/H line from X48441 to EOL on Berwick was isolated to allow crew to transfer plant to new pole.36 customers were affected for 257 minutes. Woodroffe (UW07). ID# 130237 | None | None | 36 | 257 | 154 | Central | UW07
130238 | 2014-10-29 | Scheduled Outage | Construction | V238 was isolated from S25958 to allow crew to transfer O/H conductor to new pole. 1 customer was affected for 212 minutes. Carling SM01.ID# 130238 | None | None | 1 | 212 | 4 | Central | SM01
130239 | 2014-10-29 | Scheduled Outage | Vegetation Management | Transformer #X27051 isolated by crew for tree removal | None | None | 10 | 30 | 5 | East | TB06
130240 | 2014-10-29 | Scheduled Outage | Construction | Transformer #X24835 isolated by crew due to service upgrade | None | None | 12 | 55 | 11 | East | UQ05
130241 | 2014-10-29 | Scheduled Outage | Construction | TP2080 was isolated for replacement of leaking transformer and soil remediation. | None | None | 37 | 205 | 126 | South | FAL01
130242 | 2014-10-29 | Scheduled Outage | Vegetation Management | Transformer #X27051 isolated by crew to reconnect after tree removal | None | None | 10 | 35 | 6 | East | TB06
130244 | 2014-10-30 | Scheduled Outage | Maintenance | transformer TP2592 isolated to repair broken pin, Bridlewood BRDF1, ID # 130244 | U/G Cable Attachement | Elbow \ Insert | 7 | 99 | 12 | West | BRDF1
130245 | 2014-10-30 | Scheduled Outage | Construction | Pole change | None | None | 10 | 277 | 46 | Central | UL02
130246 | 2014-10-30 | Scheduled Outage | Construction | Overhead from G50B isolated to reconfigure plant, Blackburn BLKF5, ID # 130246 | None | None | 11 | 119 | 22 | East | BLKF5
130247 | 2014-10-30 | Scheduled Outage | Maintenance | transformer TE3174 isolated for repairs, Fallowfield FAL02, ID # 130 | None | None | 14 | 108 | 25 | South | FAL02
130248 | 2014-10-30 | Scheduled Outage | Construction | transformer TP4870 isolated to transfer supply from 140F4 to FAL02, Barrhaven 140F4, ID # 130248 | None | None | 6 | 199 | 20 | South | 140F4
130249 | 2014-10-30 | Scheduled Outage | Maintenance | transformer TP2133 isolated for soil remediation, Marchwood MWDF3, ID # 130249 | None | None | 18 | 532 | 160 | West | MWDF3
130250 | 2014-10-30 | Defective Equipment | Mechanical Failure | S264 opened up::line switch was open/ we opened all txs on radial feed then when refusing line switch we saw that the fuse had come apart not blown so we refused and closed line switch then txs | O/H Switchgear | Inline Switch | 25 | 99 | 41 | South | 170F1
130251 | 2014-10-30 | Defective Equipment | Defective Equipment/ Material | Transformer #X29001 opened up due to defective cutout arrestor and bracket | O/H Switchgear | Fused Cutout | 6 | 121 | 12 | East | UQ04
130252 | 2014-10-30 | Scheduled Outage | Maintenance | Transformer #X33657 isolated by crew to repair secondary lead at transformer | None | None | 6 | 25 | 2 | Central | TW22
130253 | 2014-10-31 | Scheduled Outage | Construction | Transformer TP5393 isolated to replace leaking transformer, Fallowfield FAL03, ID # 130253 | None | None | 7 | 75 | 9 | South | FAL03
130254 | 2014-10-31 | Scheduled Outage | Construction | BECKF2 overhead isolated from S19608 make connections for future primary loop, Beckwith BECKF2, ID # 130254 | None | None | 11 | 151 | 28 | West | BECKF2
130255 | 2014-10-31 | Scheduled Outage | Maintenance | clean vault and torque connections | None | None | 1 | 95 | 2 | East | 5307
130260 | 2014-11-01 | Scheduled Outage | Maintenance | 13kv Vault VT268 at 255 Albert, was isolated to allow crew to make metering repairs. | None | None | 1 | 85 | 1 | Central | 5213
130262 | 2014-11-02 | Defective Equipment | Defective Equipment/ Material | Transformer X33657 at 2040 Killarney was isolated to allow crew to replace defective transformer. ID# 1306262. 6 customers affected for 113 minutes. | O/H Transformer | O/H Transformer (1ph) | 6 | 113 | 11 | Central | TW22
130264 | 2014-11-02 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X28150 at 1126 Rockingham Ave. - cause, squirrel | None | None | 6 | 47 | 5 | Central | 505
130267 | 2014-11-03 | Scheduled Outage | Construction | Transfer Plant to new pole | None | None | 5 | 255 | 21 | Central | UW07
130268 | 2014-11-03 | Scheduled Outage | Forced Switching | due to switching through rabbits a short outage to customers was required to feed them through another source. | None | None | 276 | 6 | 28 | West | 43F3
130268 | 2014-11-03 | Scheduled Outage | Forced Switching | due to switching through rabbits a short outage to customers was required to feed them through another source. | None | None | 471 | 1 | 8 | West | 43F2
130269 | 2014-11-03 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to establish isolation so that the O/H conductor could be upgraded & a new circuit installed. The W phase from S23320 will be energized every night under PC14 test condtions to restore load to the one customer that is affected | None | None | 1 | 239 | 4 | West | JKGF5
130270 | 2014-11-04 | Scheduled Outage | Construction | change leaking transformer | None | None | 11 | 141 | 26 | West | BRDF1
130271 | 2014-11-04 | Scheduled Outage | Construction | change SMD switches | None | None | 3 | 64 | 3 | East | 7F2
130272 | 2014-11-04 | Scheduled Outage | Construction | replace transformer and base | None | None | 11 | 589 | 108 | South | 200F5
130273 | 2014-11-04 | Scheduled Outage | Construction | change switches | None | None | 1 | 47 | 1 | East | 7F2
130274 | 2014-11-04 | Scheduled Outage | Construction | Transformer #X37169 isolated by crew to transfer plant | None | None | 6 | 215 | 22 | Central | UV07
130275 | 2014-11-04 | Scheduled Outage | Maintenance | change broken insert | U/G Cable Attachement | Elbow \ Insert | 10 | 81 | 14 | West | BRDF1
130276 | 2014-11-04 | Scheduled Outage | Vegetation Management | Transformer #X32634 isolated by crew to remove a branch | None | None | 16 | 22 | 6 | Central | TD14
130278 | 2014-11-04 | Tree Contacts | Falling Tree | RX2048 tripped, carrying 43F2 and 43F3 on transfer, tree came down on red phase overhead at 8574 McCarton S18347 found blown. | O/H Switchgear | Fused Cutout | 471 | 14 | 110 | West | BECKF2
130278 | 2014-11-04 | Tree Contacts | Falling Tree | RX2048 tripped, carrying 43F2 and 43F3 on transfer, tree came down on red phase overhead at 8574 McCarton S18347 found blown. | O/H Switchgear | Fused Cutout | 717 | 4 | 48 | West | BECKF2
130278 | 2014-11-04 | Tree Contacts | Falling Tree | RX2048 tripped, carrying 43F2 and 43F3 on transfer, tree came down on red phase overhead at 8574 McCarton S18347 found blown. | O/H Switchgear | Fused Cutout | 1397 | 84 | 1956 | West | BECKF2
130279 | 2014-11-05 | Scheduled Outage | Construction | S20528 isolated to replace defective switches, Moulton 8F4, ID # 130279 | None | None | 3 | 46 | 2 | East | 8F4
130281 | 2014-11-05 | Scheduled Outage | Maintenance | 2 transformers, X39138 and X28112 isolated by crew for secondary repairs | None | None | 28 | 120 | 56 | East | AF06
130282 | 2014-11-05 | Scheduled Outage | Construction | New cable installed but still old transformer remains Crane not big enough. 200F5 | None | None | 11 | 312 | 57 | South | 200F5
130283 | 2014-11-05 | Scheduled Outage | Construction | TP10564 isolated for soil remediation. | None | None | 6 | 353 | 35 | South | 190F2
130284 | 2014-11-05 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER TP10564 FOR SOIL CLEAN-UP (OIL LEAKED FROM TRANSFORMER) | None | None | 6 | 360 | 36 | South | 130F3
130285 | 2014-11-05 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35095 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 13 | 225 | 49 | Central | UW03
130289 | 2014-11-06 | Scheduled Outage | Vegetation Management | Transformer X32331 was isolated to allow tree trimming crew to remove trees on Larose St. | None | None | 10 | 302 | 50 | Central | AD05
130290 | 2014-11-06 | Scheduled Outage | Construction | Transformer replacement | None | None | 30 | 542 | 271 | South | 200F5
130291 | 2014-11-06 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X43064 opened up due to squirrel contact | None | None | 1 | 102 | 2 | East | 8F3
130292 | 2014-11-06 | Scheduled Outage | Construction | 2 transformers, X32778 and X35085 isolated by crew to relocate plant | None | None | 13 | 80 | 17 | Central | UW03
130293 | 2014-11-06 | Scheduled Outage | Construction | pulling in and energizing new service to TP7508. | None | None | 32 | 145 | 77 | West | ALEXF3
130294 | 2014-11-06 | Scheduled Outage | Construction | Transformer #X35939 isolated by crew due to a secondary connection | None | None | 10 | 50 | 8 | South | 190F5
130295 | 2014-11-06 | Scheduled Outage | Maintenance | Soil Remediation Continued | None | None | 37 | 326 | 201 | South | FAL01
130296 | 2014-11-06 | Scheduled Outage | Construction | Replace Transformer | None | None | 30 | 547 | 274 | South | 200F5
130298 | 2014-11-06 | Loss Of Supply | Third Party | A dig in on the customer owned secondary of transformer TE1869. The first splice made by Schneider Electric did not hold and TE1869 was isolated again. Schneider Electric made the necessary repairs again. | None | None | 21 | 725 | 254 | South | 190F5
130299 | 2014-11-07 | Scheduled Outage | Construction | TP9953 was isolated to replace same. | None | None | 26 | 113 | 49 | South | LGFF1
130300 | 2014-11-07 | Scheduled Outage | Construction | Transformer #X23416 isolated by crew to replace old secondary open buss | None | None | 14 | 165 | 38 | East | AP03
130301 | 2014-11-07 | Tree Contacts | Broken Branch | S22505 opened due to tree branch on the O/H line at 4 Birch. 115 customers were affected for 119 minutes. Beechwood (UB07). ID# 130301 | None | None | 115 | 119 | 228 | East | UB07
130302 | 2014-11-07 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X30556 | None | None | 53 | 165 | 146 | Central | UX03
130304 | 2014-11-07 | Scheduled Outage | Forced Switching | ISOLATED TRANSFORMER NPTE0455 TO REPAIR UNDERGROUND SERVICE (DAMAGED BY DIG-IN) | None | None | 13 | 155 | 34 | South | 84F4
130305 | 2014-11-07 | Scheduled Outage | Construction | Switch S11070 @ 651 EARL ARMSTRONG RD was isolated to allow crews to replace defective SMU cutouts. | None | None | 1 | 37 | 1 | East | 7F2
130309 | 2014-11-09 | Defective Equipment | Electrical Failure | TR15 breaker (TR3UY) circuit trippped open due to cable fault between VT900 and TV10050. | U/G Cable | Unknown \ Other | 1 | 29 | 0 | Central | TR3UY
130309 | 2014-11-09 | Defective Equipment | Electrical Failure | TR15 breaker (TR3UY) circuit trippped open due to cable fault between VT900 and TV10050. | U/G Cable | Unknown \ Other | 1 | 60 | 1 | Central | TR3UY
130309 | 2014-11-09 | Defective Equipment | Electrical Failure | TR15 breaker (TR3UY) circuit trippped open due to cable fault between VT900 and TV10050. | U/G Cable | Unknown \ Other | 56 | 3 | 3 | Central | TR3UY
130309 | 2014-11-09 | Defective Equipment | Electrical Failure | TR15 breaker (TR3UY) circuit trippped open due to cable fault between VT900 and TV10050. | U/G Cable | Unknown \ Other | 56 | 24 | 22 | Central | TR3UY
130309 | 2014-11-09 | Defective Equipment | Electrical Failure | TR15 breaker (TR3UY) circuit trippped open due to cable fault between VT900 and TV10050. | U/G Cable | Unknown \ Other | 1332 | 35 | 777 | Central | TR3UY
130310 | 2014-11-09 | Defective Equipment | Defective Equipment/ Material | Transformer X32601 transformer blew due to age. Lincoln Heights (TD14) ID# 130310. | O/H Transformer | O/H Transformer (1ph) | 15 | 112 | 28 | Central | TD14
130312 | 2014-11-09 | Scheduled Outage | Construction | Transformer TP3385 @ 2501 Greenbank was isolated to allow the crew to transfer cable to new pole. | None | None | 1 | 220 | 4 | South | FAL02
130313 | 2014-11-10 | Scheduled Outage | Forced Switching | outage due to switching through beckwith/munster rabbits - out of phase condition | None | None | 471 | 2 | 16 | West | 43F2
130314 | 2014-11-10 | Scheduled Outage | Forced Switching | outage due to switching through beckwith / munster rabbits - out of phase condition | None | None | 276 | 3 | 14 | West | 43F3
130315 | 2014-11-10 | Scheduled Outage | Construction | Section of UW07 between S15333 & Temp 82 isolated to install new poles & conductor | None | None | 30 | 485 | 242 | Central | UW07
130316 | 2014-11-10 | Scheduled Outage | Maintenance | Transformer #X35834 isolated by crew to repair neutral connection in the transformer | None | None | 7 | 20 | 2 | South | EPWF1
130317 | 2014-11-11 | Scheduled Outage | Construction | Transfer of plant to new pole | None | None | 18 | 291 | 87 | South | FAL02
130318 | 2014-11-11 | Scheduled Outage | Construction | SMD Switch Replacements | None | None | 4 | 46 | 3 | South | FAL02
130320 | 2014-11-11 | Scheduled Outage | Maintenance | TE3171 isolated for soil remediation. | None | None | 13 | 257 | 56 | East | 7F2
130322 | 2014-11-11 | Defective Equipment | Electrical Failure | SC6396-CB3 opened due to defective arrestor at S794. | Pole Attachement | Arrester | 188 | 63 | 197 | South | 87F6
130323 | 2014-11-11 | Scheduled Outage | Construction | Transformer #X27773 isolated by crew to replace transformer | None | None | 1 | 305 | 5 | East | AE03
130324 | 2014-11-11 | Scheduled Outage | Construction | Replace transformer TE456 and teminate cable from TE467. | None | None | 20 | 377 | 126 | South | 200F5
130325 | 2014-11-11 | Scheduled Outage | Construction | Transformer NPTE0456 at 19 Oberon St. isolated by crew to replace transformer | None | None | 20 | 406 | 135 | South | 200F5
130326 | 2014-11-11 | Scheduled Outage | Vegetation Management | Transformer X32553 at 1377 Ferguson St. isolated to clear vines from lines. | None | None | 9 | 51 | 8 | Central | UW01
130329 | 2014-11-12 | Scheduled Outage | Construction | Install new poles, conductor and re-arrange plant. | None | None | 20 | 473 | 158 | Central | UW07
130330 | 2014-11-12 | Scheduled Outage | Vegetation Management | Transformer NP000929 at 1141 Deer Park Rd isolated by 24/7 crew Jeff D'Aoust and Patrick Brisson to untangle secondary buss caused by tree trimmers | None | None | 12 | 7 | 1 | South | 190F5
130331 | 2014-11-12 | Scheduled Outage | Construction | Transformer #X27733 isolated by crew to install new services | None | None | 14 | 55 | 13 | Central | SB05
130332 | 2014-11-12 | Scheduled Outage | Maintenance | Transformer #X36369 isolated by crew to replace transformer switch | None | None | 5 | 24 | 2 | South | 72F4
130333 | 2014-11-13 | Scheduled Outage | Construction | X30941 opened to re-arrange plant | None | None | 15 | 120 | 30 | Central | UN06
130336 | 2014-11-13 | Scheduled Outage | Construction | ISOLATED TP3117 TO CONNECT NEW STREETLIGHT | None | None | 11 | 10 | 2 | West | BRDF5
130338 | 2014-11-13 | Scheduled Outage | Construction | Transformer TE457 @ 55 Oberon was isolated to allow the crew to replace the transformer and its base and terminate the new primary cables | None | None | 18 | 352 | 106 | South | 200F5
130339 | 2014-11-13 | Scheduled Outage | Vegetation Management | The O/H at the rear of Moncton and Kelly was isolated to allow the contractor to remove a large tree. | None | None | 34 | 420 | 238 | Central | TD05
130342 | 2014-11-14 | Scheduled Outage | Construction | Transformer TP6675 was isolated to allow crew to replace switches feeding it. Fallowfield (FAL02) ID# . | None | None | 19 | 82 | 26 | South | FAL02
130345 | 2014-11-16 | Unknown/Other | Unknown | Transformer #X5079 opened up, crew could not determine cause | Unknown \ Other | Unknown \ Other | 3 | 40 | 2 | South | 180F4
130346 | 2014-11-16 | Defective Equipment | Defective Equipment/ Material | Transformer KT657 at 64 Splinter was forced out of service and isolated due to defective secondary cable. Lincoln Heights (TD05). ID# 130346 | Secondary \ Service | U/G Service | 21 | 643 | 225 | Central | TD05
130347 | 2014-11-16 | Scheduled Outage | Construction | replace transformer base and transformer 1396. | None | None | 1 | 466 | 8 | West | BRDF7
130350 | 2014-11-17 | Scheduled Outage | Construction | Transformer X30558 at 215 Cooper St. isolated for crew to do a pole replacement. | None | None | 3 | 62 | 3 | Central | UX10
130351 | 2014-11-17 | Scheduled Outage | Construction | Transformer X37965 at 235 Cooper St. isolated by crew for pole change | None | None | 36 | 25 | 15 | Central | UX10
130353 | 2014-11-17 | Scheduled Outage | Construction | New Primary Cable installation | None | None | 18 | 271 | 81 | South | 200F5
130354 | 2014-11-17 | Scheduled Outage | Construction | SMD Switch Replacement | None | None | 1 | 40 | 1 | East | 77M6
130355 | 2014-11-17 | Scheduled Outage | Construction | G415 to EOL was isoalted to allow crew to replace SMD switches. Billberry (77M6). ID# 130355 | None | None | 1 | 37 | 1 | East | 77M6
130356 | 2014-11-17 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X48546 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 12 | 245 | 49 | Central | UW07
130357 | 2014-11-17 | Scheduled Outage | Construction | Switch S29204 @ 6684 Carriere was isolated to allow the crew to replace the SMD switches. | None | None | 1 | 83 | 1 | East | 77M6
130358 | 2014-11-17 | Scheduled Outage | Construction | Switch S29373 @ 2543 St Joseph was isolated to aloow the crew to relpace the SMD switches | None | None | 1 | 23 | 0 | East | 77M6
130359 | 2014-11-17 | Scheduled Outage | Construction | Switch G840 was isolated to allow the crew replace the SMD switches | None | None | 1 | 30 | 0 | East | 77M5
130360 | 2014-11-17 | Scheduled Outage | Construction | Switch G407 @ 1344 Youvile was isolated to allow the crew to replace SMD switches. | None | None | 1 | 69 | 1 | East | 77M5
130361 | 2014-11-18 | Defective Equipment | Defective Equipment/ Material | The fuse G821 feeding VE4208 @ 1403 FOREST VALLEY DR was burning up | O/H Switchgear | Fused Cutout | 1 | 73 | 1 | East | 77M5
130362 | 2014-11-18 | Scheduled Outage | Construction | Switch S27181 @ 3484 Limebank was isolated to allow the crew to replace the SMD20 switch | None | None | 1 | 62 | 1 | East | 7F2
130363 | 2014-11-18 | Defective Equipment | Mechanical Failure | A quick sleeve let go causing the 249F1 O/H conductor to come down | O/H Conductor | Sleeve | 27 | 159 | 72 | East | LTM01
130363 | 2014-11-18 | Defective Equipment | Mechanical Failure | A quick sleeve let go causing the 249F1 O/H conductor to come down | O/H Conductor | Sleeve | 81 | 102 | 138 | East | LTM01
130363 | 2014-11-18 | Defective Equipment | Mechanical Failure | A quick sleeve let go causing the 249F1 O/H conductor to come down | O/H Conductor | Sleeve | 3856 | 27 | 1735 | East | LTM01
130365 | 2014-11-18 | Scheduled Outage | Maintenance | Replace defective insert | U/G Cable Attachement | Elbow \ Insert | 6 | 112 | 11 | West | BRDF1
130366 | 2014-11-18 | Scheduled Outage | Construction | Change leaking transformer. | None | None | 7 | 177 | 21 | West | BRDF4
130367 | 2014-11-18 | Defective Equipment | Mechanical Failure | AJ05 circuit tripped open due to downed conductors at Haig and Kilborn. Playfair (AJ05) ID# 130367. | O/H Conductor | O/H Conductor | 63 | 144 | 151 | East | AJ05
130367 | 2014-11-18 | Defective Equipment | Mechanical Failure | AJ05 circuit tripped open due to downed conductors at Haig and Kilborn. Playfair (AJ05) ID# 130367. | O/H Conductor | O/H Conductor | 291 | 9 | 44 | East | AJ05
130367 | 2014-11-18 | Defective Equipment | Mechanical Failure | AJ05 circuit tripped open due to downed conductors at Haig and Kilborn. Playfair (AJ05) ID# 130367. | O/H Conductor | O/H Conductor | 291 | 79 | 383 | East | AJ05
130368 | 2014-11-18 | Scheduled Outage | Construction | To allow Sproule Power Line crews to change out SMD switches | None | None | 1 | 36 | 1 | East | 77M5
130369 | 2014-11-18 | Scheduled Outage | Construction | To allow Sproule Power Lines to change SMD switches | None | None | 1 | 47 | 1 | East | 77M5
130370 | 2014-11-18 | Scheduled Outage | Vegetation Management | To allow forestry contractors to clear power lines as part of the Hydro Ottawa storm hardening project | None | None | 1 | 354 | 6 | West | MWDF3
130371 | 2014-11-18 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change the transformer & base | None | None | 11 | 455 | 83 | South | 200F5
130372 | 2014-11-18 | Scheduled Outage | Construction | To allow Sproule Power Lines to change SMD switches | None | None | 8 | 24 | 3 | East | 77M5
130373 | 2014-11-18 | Scheduled Outage | Construction | Switch s18607 @ 1921 St.Joseph was isolated to allow the crew to replace SMD switches | None | None | 33 | 37 | 20 | East | 77M6
130374 | 2014-11-18 | Scheduled Outage | Construction | switch G822 @ 2543 St Joseph was isolated to allow the crew to replace the SMD switch | None | None | 8 | 26 | 3 | East | 77M6
130375 | 2014-11-19 | Scheduled Outage | Maintenance | Switch S28296 was isolated to allow the crew to replace the SMD switches | None | Fused Cutout | 1 | 42 | 1 | East | 7F2
130379 | 2014-11-19 | Scheduled Outage | Construction | to allow Hydro Ottawa crews to replace flashed over primary bushings | None | None | 12 | 30 | 6 | East | 7F2
130381 | 2014-11-19 | Scheduled Outage | Construction | Pole replacement | None | None | 17 | 95 | 27 | Central | TH01
130382 | 2014-11-19 | Defective Equipment | Mechanical Failure | REPLACED BROKEN FUSE FEEDING TRANSFORMER X07822 | O/H Switchgear | Fused Cutout | 1 | 257 | 4 | West | MWDF3
130383 | 2014-11-19 | Scheduled Outage | Construction | V530 at 260 Metcalfe was isolated to allow crew to verify ducts for future cable repalcement. Gladstone (UX03). | None | None | 1 | 192 | 3 | Central | UX03
130384 | 2014-11-20 | Scheduled Outage | Construction | S10763 switch replacement. | None | None | 40 | 71 | 47 | South | FAL03
130385 | 2014-11-20 | Scheduled Outage | Construction | Isolation of TP10481 to allow crews to splice new secondary cables. | None | None | 15 | 292 | 73 | South | 200F5
130387 | 2014-11-20 | Scheduled Outage | Construction | 7F4 circuit from S11014 to EOL isolated to allow crew to replace SMD switches. | None | None | 47 | 73 | 57 | East | 7F4
130388 | 2014-11-20 | Scheduled Outage | Maintenance | TP6175 at 7 Birkett isolated for soil remediation. | None | None | 7 | 282 | 33 | South | 140F3
130389 | 2014-11-20 | Scheduled Outage | Maintenance | Transformer #X26815 isolated by crew to make secondary repairs | None | None | 6 | 20 | 2 | East | AE05
130391 | 2014-11-20 | Scheduled Outage | Construction | Transfer plant to new pole. | None | None | 19 | 75 | 24 | East | AF06
130392 | 2014-11-20 | Scheduled Outage | Construction | To replace S24624 switches. | None | None | 1 | 25 | 0 | South | FAL01
130393 | 2014-11-20 | Scheduled Outage | Construction | To reconnect 120/240V banks. | None | None | 2 | 13 | 0 | East | AE05
130395 | 2014-11-21 | Scheduled Outage | Maintenance | Transformer TP2583 was isolated to allow crews to replace a broken insert. | None | None | 15 | 60 | 15 | West | TFXF6
130396 | 2014-11-21 | Scheduled Outage | Construction | To reconfiguration plant and terminate new switches. | None | None | 5 | 418 | 35 | Central | UW07
130397 | 2014-11-21 | Scheduled Outage | Construction | Switches 3604 isolated for SMD replacement | None | None | 1 | 23 | 0 | West | 624F6
130399 | 2014-11-21 | Scheduled Outage | Construction | S29325 at 645 Longfields isolated for SMD replacement. | None | None | 1 | 43 | 1 | South | LGFF1
130400 | 2014-11-21 | Scheduled Outage | Construction | Primary fuse at 2292 Fifth Line isolated for SMD replacement. | None | None | 1 | 28 | 0 | West | 624F6
130401 | 2014-11-21 | Defective Equipment | Defective Equipment/ Material | Transformer #X35798 opened up due to defective cutout | O/H Switchgear | Fused Cutout | 8 | 88 | 12 | Central | TD06
130403 | 2014-11-21 | Scheduled Outage | Construction | Planned outage re-arrange O/H plante. | None | None | 15 | 45 | 11 | East | 7F1
130404 | 2014-11-21 | Scheduled Outage | Construction | S28569 isolated to allow crew to change SMD switches. | None | None | 3 | 68 | 3 | South | LGFF1
130406 | 2014-11-21 | Defective Equipment | Mechanical Failure | Blown elbows | U/G Cable Attachement | Elbow \ Insert | 11 | 8 | 1 | South | 84F1
130406 | 2014-11-21 | Defective Equipment | Mechanical Failure | Blown elbows | U/G Cable Attachement | Elbow \ Insert | 43 | 38 | 27 | South | 84F1
130406 | 2014-11-21 | Defective Equipment | Mechanical Failure | Blown elbows | U/G Cable Attachement | Elbow \ Insert | 111 | 1 | 2 | South | 84F1
130406 | 2014-11-21 | Defective Equipment | Mechanical Failure | Blown elbows | U/G Cable Attachement | Elbow \ Insert | 135 | 9 | 20 | South | 84F1
130406 | 2014-11-21 | Defective Equipment | Mechanical Failure | Blown elbows | U/G Cable Attachement | Elbow \ Insert | 136 | 78 | 177 | South | 84F1
130406 | 2014-11-21 | Defective Equipment | Mechanical Failure | Blown elbows | U/G Cable Attachement | Elbow \ Insert | 147 | 226 | 554 | South | 84F1
130406 | 2014-11-21 | Defective Equipment | Mechanical Failure | Blown elbows | U/G Cable Attachement | Elbow \ Insert | 468 | 110 | 858 | South | 84F1
130408 | 2014-11-22 | Scheduled Outage | Maintenance | To replace a broken W phase insert | None | None | 10 | 29 | 5 | South | 87F3
130409 | 2014-11-22 | Loss Of Supply | Transmission Inadvertent | To allow customer to repair secondary switch | None | None | 1 | 112 | 2 | West | A9M4
130411 | 2014-11-22 | Loss Of Supply | Transmission Inadvertent | The crew disconnect the Transfomer X30049 to allow them to reconnect 61 GLENDALE Ave | None | None | 8 | 53 | 7 | Central | SB11
130412 | 2014-11-22 | Scheduled Outage | Maintenance | scheduled maintenance. | None | None | 1 | 321 | 5 | Central | 503
130413 | 2014-11-22 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace a tracking transformer & upgrade the elbows | None | None | 11 | 360 | 66 | East | 77M2
130413 | 2014-11-22 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace a tracking transformer & upgrade the elbows | None | None | 20 | 360 | 120 | East | 77M6
130416 | 2014-11-23 | Defective Equipment | Electrical Failure | S16331R phase fuse was found blown due to suspected cable fault. Bilberry (77M1) ID# 130416. | U/G Cable | Unknown \ Other | 33 | 93 | 51 | East | 77M1
130417 | 2014-11-23 | Scheduled Outage | Construction | The O/H from pole X42103 to EOL was isolated to allow the crew to upgrade the O/H | None | None | 2 | 181 | 6 | South | 72F3
130418 | 2014-11-23 | Scheduled Outage | Construction | Transformer X26223 was isolated to allow the crew to change SMD switches that feeds that transformer | None | None | 2 | 63 | 2 | West | JKGF4
130420 | 2014-11-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X09765 TO REPLACE SWITCES | None | None | 2 | 70 | 2 | West | JKGF4
130421 | 2014-11-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X26217 TO REPLACE SWITCH | None | None | 1 | 60 | 1 | West | ALXF4 (Alexander DS)
130422 | 2014-11-23 | Scheduled Outage | Construction | Switch S22763 was isolated to allow the crew to change the SMD switch | None | None | 1 | 67 | 1 | West | JKGF5
130423 | 2014-11-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X09484 TO REPLACE SWITCH | None | None | 2 | 60 | 2 | West | ALEXF2
130424 | 2014-11-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X12766 TO REPLACE SWITCHES | None | None | 1 | 50 | 1 | West | BECKF2
130425 | 2014-11-23 | Scheduled Outage | Construction | Switch S21769 @ 126 Iber was isolated to allow the crew to change the SMD switch,JGKF5 | None | None | 1 | 79 | 1 | West | JKGF5
130458 | 2014-11-25 | Scheduled Outage | Construction | TP2569 isolated to allow crews to replace transformer. | None | None | 9 | 118 | 18 | West | TFXF6
130459 | 2014-11-25 | Tree Contacts | Falling Tree | tree brought down primary and secondary - 2 spans | O/H Conductor | O/H Conductor | 18 | 477 | 143 | East | TB06
130460 | 2014-11-25 | Scheduled Outage | Maintenance | Tranformer #X31482 opened by crew to re-sag service | None | None | 13 | 35 | 8 | Central | TH11-NIU
130463 | 2014-11-26 | Scheduled Outage | Construction | Transformer TP5732 isolated for replacement of a leaking transformer, Kanata 624F1, ID # 130463 | None | None | 21 | 153 | 54 | West | 624F1
130465 | 2014-11-26 | Scheduled Outage | Construction | Vault VT290 isolated to allow cable to be replaced between VT290 and VT561, Lisgar 5202, ID # 130465 | None | None | 1 | 414 | 7 | Central | 5202
130466 | 2014-11-26 | Defective Equipment | Defective Equipment/ Material | Transformer #X23128 opened up due to broken switch | O/H Switchgear | Fused Cutout | 2 | 102 | 3 | East | UG12
130467 | 2014-11-26 | Scheduled Outage | Construction | To replace S12907 White phase fuse and switch. | None | None | 35 | 39 | 23 | South | FAL03
130468 | 2014-11-26 | Scheduled Outage | Vegetation Management | Transformer #X40754 isolated by crew for tree removal | None | None | 5 | 140 | 12 | East | TB2JP
130469 | 2014-11-26 | Scheduled Outage | Construction | Transformer X48543 at 1128 Checkers Rd. isolated by contractor to transfer plant. Jordan Foote of K-Line was the person who called this in | None | None | 15 | 162 | 40 | Central | UW07
130471 | 2014-11-26 | Defective Equipment | Defective Equipment/ Material | Transformer X36403 at 96 Grenfell Cres isolated so crew could change broken cutout | O/H Switchgear | Fused Cutout | 10 | 38 | 6 | South | 140F5
130473 | 2014-11-26 | Scheduled Outage | Forced Switching | Transformer X35199 was isolated to allow crew to reconnect services at 803 and 807. Woodroffe (TW22) ID# 130473. | None | None | 8 | 107 | 14 | Central | TW22
130474 | 2014-11-27 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace TP2558 B phase | None | None | 7 | 121 | 14 | West | TFXF6
130475 | 2014-11-27 | Scheduled Outage | Construction | To allow Hydro Ottawa & J.W Leslie crews to install & terminate new cable | None | None | 10 | 88 | 15 | East | LTM01
130477 | 2014-11-27 | Scheduled Outage | Maintenance | To relocate SMD Switches G301. | None | None | 40 | 30 | 20 | East | 77M6
130478 | 2014-11-27 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace a defective transformer. | None | None | 12 | 356 | 71 | West | 24F2
130479 | 2014-11-27 | Scheduled Outage | Construction | Allow contractor to install new duct work. | None | None | 1 | 279 | 5 | Central | UX03
130480 | 2014-11-28 | Scheduled Outage | Vegetation Management | To allow a forestry contractor to remove 5 large, dead ash trees with a crane. | None | None | 70 | 434 | 506 | South | 190F2
130481 | 2014-11-28 | Scheduled Outage | Forced Switching | replace switches that were burning up. | O/H Switchgear | Unknown \ Other | 1 | 55 | 1 | Central | SH07
130483 | 2014-11-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X36538 opened up due to defective cutout | O/H Switchgear | Fused Cutout | 5 | 68 | 6 | South | 130F1
130484 | 2014-11-28 | Defective Equipment | Electrical Failure | UA11 red phase cable fault between K577 and normal open point at UA05 overhead | U/G Cable | Unknown \ Other | 35 | 173 | 101 | East | UA11
130485 | 2014-11-29 | Scheduled Outage | Construction | TP10164, TP10173, TP10172 and TP10324 isolated to allow crews to re-arrange primary and energize 5 new transformers. | None | None | 5 | 258 | 22 | West | TFXF4
130486 | 2014-11-30 | Defective Equipment | Electrical Failure | Defective pothead at VT187 at 2980 Carling Ave. | U/G Cable Attachement | Pothead | 1 | 1 | 0 | Central | 5408
130486 | 2014-11-30 | Defective Equipment | Electrical Failure | Defective pothead at VT187 at 2980 Carling Ave. | U/G Cable Attachement | Pothead | 24 | 8 | 3 | Central | 5408
130486 | 2014-11-30 | Defective Equipment | Electrical Failure | Defective pothead at VT187 at 2980 Carling Ave. | U/G Cable Attachement | Pothead | 25 | 16 | 7 | Central | 5408
130486 | 2014-11-30 | Defective Equipment | Electrical Failure | Defective pothead at VT187 at 2980 Carling Ave. | U/G Cable Attachement | Pothead | 58 | 15 | 14 | Central | 5408
130486 | 2014-11-30 | Defective Equipment | Electrical Failure | Defective pothead at VT187 at 2980 Carling Ave. | U/G Cable Attachement | Pothead | 59 | 9 | 9 | Central | 5408
130486 | 2014-11-30 | Defective Equipment | Electrical Failure | Defective pothead at VT187 at 2980 Carling Ave. | U/G Cable Attachement | Pothead | 60 | 9 | 9 | Central | 5408
130486 | 2014-11-30 | Defective Equipment | Electrical Failure | Defective pothead at VT187 at 2980 Carling Ave. | U/G Cable Attachement | Pothead | 61 | 5 | 5 | Central | 5408
130486 | 2014-11-30 | Defective Equipment | Electrical Failure | Defective pothead at VT187 at 2980 Carling Ave. | U/G Cable Attachement | Pothead | 82 | 14 | 19 | Central | 5408
130486 | 2014-11-30 | Defective Equipment | Electrical Failure | Defective pothead at VT187 at 2980 Carling Ave. | U/G Cable Attachement | Pothead | 91 | 56 | 85 | Central | 5408
130490 | 2014-11-30 | Foreign Interference | Wildlife (Bird/Animal) | Refused S26552 at 596 Pleasant Park Rd - animal contact-squirrel - Doug Featherstone of 24/7 completed this call | None | None | 20 | 89 | 30 | East | TB06
130491 | 2014-11-30 | Tree Contacts | Falling Tree | Tree contact on overhead at S20206 caused interuption to X33294, Beckwith BECKF2, ID # 130491 | None | None | 1 | 137 | 2 | West | BECKF2
130492 | 2014-11-30 | Tree Contacts | Falling Tree | Tree contact at S20071 caused outage at X33276, Beckwith BECKF2, ID # 130492 | None | None | 1 | 48 | 1 | West | BECKF2
130493 | 2014-12-01 | Scheduled Outage | Construction | To transfer cables to new pole. | None | None | 21 | 311 | 109 | Central | UX03
130494 | 2014-12-01 | Scheduled Outage | Construction | S13315 opened to allow 24/7 to replace switch | None | None | 16 | 9 | 2 | West | 624F6
130495 | 2014-12-01 | Scheduled Outage | Construction | Transformer X30750 at 110 Gloucester St isolated by contractor to install new poles and transfer plant | None | None | 52 | 150 | 130 | Central | SA22
130496 | 2014-12-01 | Scheduled Outage | Construction | Transformer #X7258 isolated by crew to replace switch | None | None | 1 | 15 | 0 | West | 624F6
130497 | 2014-12-01 | Defective Equipment | Mechanical Failure | Defective cable. | U/G Cable | XLPE | 1 | 475 | 8 | Central | UJ05
130498 | 2014-12-02 | Scheduled Outage | Construction | S216600 to EOL was isolated to allow crew to replace SMD switches | None | None | 1 | 27 | 0 | East | 77M5
130499 | 2014-12-02 | Scheduled Outage | Maintenance | Transformer TE701 was isolated to allow crew to complete transformer soil remediation. | None | None | 14 | 333 | 78 | South | 180F4
130500 | 2014-12-02 | Scheduled Outage | Construction | Transformer from TP9288, TP9272 and TP9261 to EOL were isolated to allow crew to reconfigure cable sections. | None | None | 107 | 360 | 642 | West | BRDF2
130501 | 2014-12-02 | Scheduled Outage | Construction | Transformer #X30798 isolated by crew to transer plant | None | None | 8 | 215 | 29 | Central | SA22
130502 | 2014-12-02 | Scheduled Outage | Vegetation Management | Dead Tree removal by contractor | None | None | 13 | 280 | 61 | Central | SH07
130503 | 2014-12-02 | Scheduled Outage | Maintenance | Clean and torque of vault connections by contractor | None | None | 1 | 491 | 8 | Central | 5412
130504 | 2014-12-02 | Scheduled Outage | Construction | Transformer #X27031 isolated by crew for a service upgrade | None | None | 13 | 35 | 8 | East | TB06
130505 | 2014-12-03 | Scheduled Outage | Construction | Transfer of Plant | None | None | 12 | 191 | 38 | Central | SA22
130506 | 2014-12-03 | Scheduled Outage | Construction | Isolation and removal of transformer | None | None | 3 | 435 | 22 | Central | 303
130507 | 2014-12-03 | Scheduled Outage | Maintenance | Transformer TP2669B was isolated to allow crew to replace defective insert. | None | None | 8 | 160 | 21 | West | TFXF6
130508 | 2014-12-03 | Scheduled Outage | Construction | Transformer #X18447 isolated by crew to replace switch | None | None | 2 | 25 | 1 | East | 249F2
130509 | 2014-12-03 | Scheduled Outage | Construction | SMD Switch replacement | None | None | 32 | 22 | 12 | West | ALEXF3
130510 | 2014-12-03 | Scheduled Outage | Construction | Transformer #X35972 isolated by crew to relocate service | None | None | 6 | 40 | 4 | Central | TW22
130511 | 2014-12-03 | Scheduled Outage | Maintenance | repair broken insert on transformer TP2669. | None | None | 8 | 168 | 22 | West | TFXF6
130512 | 2014-12-03 | Defective Equipment | Defective Equipment/ Material | Transformer NP001408 opened up due to leed burnt off | O/H Switchgear | Fused Cutout | 4 | 114 | 8 | East | 7F2
130513 | 2014-12-03 | Scheduled Outage | Construction | Transformer #X31799 isolated by crew to transfer plant | None | None | 1 | 235 | 4 | Central | AM06
130514 | 2014-12-03 | Scheduled Outage | Maintenance | Transformer 352 at 12 Oakview was isolated to allow crew to repair broken insert. Bridlewood (BRDF4). ID# 130514. | None | None | 9 | 140 | 21 | West | BRDF4
130515 | 2014-12-03 | Scheduled Outage | Construction | re-terminate the connections by contractor | None | None | 12 | 110 | 22 | Central | SA22
130516 | 2014-12-03 | Scheduled Outage | Construction | Vault Maintenance, Asbestos Removal, Primary Cable replacement | None | None | 1 | 460 | 8 | Central | SA22
130518 | 2014-12-04 | Scheduled Outage | Construction | TP8579 at 3580 Strandherd isolated to allow crews to replace S27853 SMD switches. | None | None | 17 | 49 | 14 | South | FAL01
130519 | 2014-12-04 | Loss Of Supply | Transmission Inadvertent | Loss of supply from provincial grid circuit M31A. Cause under investigation. Customers fed from Albion TS, Albion DS, Brookfield DS, McCarthy DS and Walkley DS affected. | None | None | 15934 | 7 | 1859 | East | M31A (Albion - T1)
130521 | 2014-12-04 | Scheduled Outage | Construction | Switch S16335 @ 4244 Rideau Valley Dr was isolated to allow the crew replace the SMD switches | None | None | 1 | 33 | 1 | East | 7F2
130522 | 2014-12-04 | Scheduled Outage | Construction | Switch S14983 @ 4344 Rideau Valley Dr was isolated to allow the crew replace the SMD switches | None | None | 1 | 24 | 0 | East | 7F2
130523 | 2014-12-04 | Scheduled Outage | Construction | To replace rusted Tx 4067 | None | None | 14 | 130 | 30 | West | BRDF6
130524 | 2014-12-04 | Scheduled Outage | Vegetation Management | S10476 opened to clear trees from O/H line | None | None | 1 | 184 | 3 | East | 249F2
130525 | 2014-12-04 | Scheduled Outage | Construction | Transformer #X39764 isolated by crew to replace triplex service | None | None | 9 | 55 | 8 | South | 200F3
130526 | 2014-12-04 | Scheduled Outage | Construction | Switch S14174 @ 3676 Innes was isolated to allow the crew repair the SMD switches | None | None | 1 | 17 | 0 | East | 77M2
130527 | 2014-12-05 | Scheduled Outage | Construction | Transformer X06884 at 1083 Klondyke Rd isolated for crew to replace the switch | None | None | 2 | 23 | 1 | West | 624F6
130528 | 2014-12-05 | Scheduled Outage | Construction | At 07:34am crews isolated TP9662 to connect new transformer at 300 Huntclub. 3 customers affected for 46 mins. Rideau Heights (180F6)ID#130528 | None | None | 3 | 46 | 2 | South | 180F6
130529 | 2014-12-06 | Foreign Interference | Vehicle | S14366 opened due to MVA at Bank and Conroy, tow truck hit Hydro pole. | Pole | Pole | 75 | 130 | 162 | East | LTM01
130529 | 2014-12-06 | Foreign Interference | Vehicle | S14366 opened due to MVA at Bank and Conroy, tow truck hit Hydro pole. | Pole | Pole | 90 | 226 | 339 | East | LTM01
130529 | 2014-12-06 | Foreign Interference | Vehicle | S14366 opened due to MVA at Bank and Conroy, tow truck hit Hydro pole. | Pole | Pole | 1397 | 76 | 1770 | East | LTM01
130532 | 2014-12-07 | Scheduled Outage | Maintenance | vault maintenance | None | None | 1 | 227 | 4 | Central | TL6TS
130533 | 2014-12-07 | Scheduled Outage | Forced Switching | Forced ouage to allow Hydro Ottawa crews to reconfigure the O/H at Bank St & Conroy to its normal configuration after a motor vehicle accident took out a utility pole. | None | None | 68 | 7 | 8 | East | LTM01
130533 | 2014-12-07 | Scheduled Outage | Forced Switching | Forced ouage to allow Hydro Ottawa crews to reconfigure the O/H at Bank St & Conroy to its normal configuration after a motor vehicle accident took out a utility pole. | None | None | 91 | 83 | 126 | East | LTM01
130534 | 2014-12-08 | Scheduled Outage | Construction | To allow crew to replace primary cable from pole to vault. | None | None | 1 | 418 | 7 | Central | UF08
130535 | 2014-12-08 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32476 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 55 | 9 | Central | UW01
130537 | 2014-12-08 | Scheduled Outage | Maintenance | At 9:39am crews isolated V139 to allow contractor to perform vault maintenance. 1 customer affected for 237mins. Albion (UA11) ID# 130537 | None | None | 1 | 237 | 4 | East | UA11
130538 | 2014-12-08 | Scheduled Outage | Construction | Transformer #X32465 isolated by crew to transfer hydro plant, done by Shawn Evans from K-Line | None | None | 7 | 20 | 2 | Central | UW01
130539 | 2014-12-09 | Scheduled Outage | Construction | Transformer 4069 was isolated to allow crew to upgrade transformer. Bridlewood (BRDF6) ID# 130539. | None | None | 14 | 372 | 87 | West | BRDF6
130540 | 2014-12-09 | Scheduled Outage | Construction | Transformer K1225 was isolated to allow crew to replace transformer. Dagmar (AC07) ID# 130540. | None | None | 6 | 152 | 15 | East | AC07
130541 | 2014-12-09 | Scheduled Outage | Maintenance | To make repairs to leaking transformer. | None | None | 10 | 114 | 19 | West | TFXF6
130542 | 2014-12-09 | Scheduled Outage | Construction | Transformer X10590 at 102 Fortune St. isolated by crew to rearange underground plant | None | None | 7 | 60 | 7 | West | 28F2
130543 | 2014-12-09 | Scheduled Outage | Construction | Transformer X32468 at 1765 Baseline Rd. isolated by contractor to transfer load and remove transformer X32554 from 1739 Baseline Rd. | None | None | 24 | 40 | 16 | Central | UW01
130544 | 2014-12-09 | Scheduled Outage | Construction | Transformer X31739 at 1735 Baseline Rd. isolated by contractor for clearance to remove X32554 at 1739 Baseline Rd. | None | None | 8 | 40 | 5 | Central | UW01
130545 | 2014-12-09 | Scheduled Outage | Maintenance | Transformer X14141 at 5030 Limebank Rd. isolated by crew to change the top leed on a switch. | None | None | 3 | 44 | 2 | East | 7F4
130546 | 2014-12-09 | Scheduled Outage | Construction | Transformer X48266 at 1768 Ainsley Dr. isolated by contractor to transfer plant. | None | None | 1 | 30 | 0 | Central | UW01
130547 | 2014-12-09 | Scheduled Outage | Construction | Transformer X48268 at 1579 Baseline Rd. isolated by contractor to transfer plant. | None | None | 1 | 30 | 0 | Central | UW01
130548 | 2014-12-09 | Scheduled Outage | Construction | Transformer X34450 at 1689 Baseline Rd. isolated by contractor to transfer plant to a different phase. | None | None | 24 | 20 | 8 | Central | UW01
130549 | 2014-12-09 | Scheduled Outage | Construction | Scheduled shutdown to allow crew to replace primary cable from pole to vault. | None | None | 1 | 323 | 5 | Central | UX08
130551 | 2014-12-10 | Scheduled Outage | Construction | Transformers TP7104, TP7850 and TP7851 were isolated to allow crew to replace elbows at TP7104. Marchwood (MWDF3) ID# 130551. | None | None | 8 | 39 | 5 | West | MWDF3
130552 | 2014-12-10 | Scheduled Outage | Construction | Installing new cable between G214B and TE389 | None | None | 14 | 177 | 41 | East | BLKF1
130553 | 2014-12-10 | Defective Equipment | Electrical Failure | S19837 red phase fuse blew due to cable fault between TP8090 and TP8091. Bilberry (77M6) ID# 130553. | U/G Cable | Unknown \ Other | 49 | 35 | 29 | East | 77M6
130553 | 2014-12-10 | Defective Equipment | Electrical Failure | S19837 red phase fuse blew due to cable fault between TP8090 and TP8091. Bilberry (77M6) ID# 130553. | U/G Cable | Unknown \ Other | 95 | 86 | 136 | East | 77M6
130554 | 2014-12-10 | Scheduled Outage | Construction | Transformer X46293 at 2453 Iris St. isolated by contractor to transfer plant to new pole | None | None | 36 | 75 | 45 | Central | TW05
130555 | 2014-12-10 | Scheduled Outage | Construction | The following 9 transformers were isolated by contractor to transfer plant to new poles. X32472, X32565, X31742, X32560, X33846, X32559, X33843, X32470 and X32471. | None | None | 56 | 105 | 98 | Central | UW01
130556 | 2014-12-10 | Scheduled Outage | Construction | Transformer X31558 at 1812 Gilbert Ave. and X32555 at 1822 Gilbert Ave. isolated by contractor to transfer plant to new poles. | None | None | 17 | 45 | 13 | Central | UW01
130557 | 2014-12-10 | Defective Equipment | Mechanical Failure | Defective Elbow at TP2677BH1B TO TP2680 | U/G Cable Attachement | Elbow \ Insert | 99 | 35 | 58 | West | TFXF6
130557 | 2014-12-10 | Defective Equipment | Mechanical Failure | Defective Elbow at TP2677BH1B TO TP2680 | U/G Cable Attachement | Elbow \ Insert | 99 | 80 | 132 | West | TFXF6
130557 | 2014-12-10 | Defective Equipment | Mechanical Failure | Defective Elbow at TP2677BH1B TO TP2680 | U/G Cable Attachement | Elbow \ Insert | 108 | 7 | 13 | West | TFXF6
130558 | 2014-12-10 | Scheduled Outage | Maintenance | At 9:54pm crews isolated SB15, SB15-Y and V607 to allow Stations to perform maintenance on SB15-Y and contractor to perform vault maintenance. Bronson (SB15) ID#130558 | None | None | 1 | 199 | 3 | Central | SB15
130559 | 2014-12-11 | Scheduled Outage | Vegetation Management | Clear tree contact from the overhead primary | None | None | 104 | 72 | 125 | East | TB06
130560 | 2014-12-12 | Scheduled Outage | Maintenance | Tap Changer adjustment | None | None | 1 | 41 | 1 | Central | 301
130561 | 2014-12-12 | Scheduled Outage | Construction | Transformer TP9104 at 11 Talum was isolated to allow crew to pull new underground conductor into transformer base. Terry Fox (TFXF5). ID# 130561 | None | None | 11 | 155 | 28 | West | TFXF5
130562 | 2014-12-12 | Scheduled Outage | Construction | To install new riser cables and switch S19734 | None | None | 1 | 248 | 4 | Central | UX03
130563 | 2014-12-12 | Scheduled Outage | Construction | Transformer X25739 at 46 Champagne Ave. S isolated by crew to upgrade and replace transformer from 37.5kVA to 50kVA | None | None | 10 | 160 | 27 | Central | SB07
130564 | 2014-12-12 | Scheduled Outage | Construction | Secondary overhead damaged by contractor contact | Secondary \ Service | O/H Service | 36 | 7 | 4 | Central | UJ02
130565 | 2014-12-13 | Scheduled Outage | Construction | Vault V530 was isolated to allow crew to install new riser cable and switches. Gladstone (UX03) ID# 130565. | None | None | 3 | 175 | 9 | Central | UX03
130567 | 2014-12-13 | Scheduled Outage | Construction | Transformers TP7241, 5624 and 5625 isolated to allow crew to replace TP7241 and install new cable between transformers TP7241 and 5624, South March 24F2, ID # 130567 | None | None | 1 | 10 | 0 | West | 39F2
130567 | 2014-12-13 | Scheduled Outage | Construction | Transformers TP7241, 5624 and 5625 isolated to allow crew to replace TP7241 and install new cable between transformers TP7241 and 5624, South March 24F2, ID # 130567 | None | None | 2 | 20 | 1 | West | 39F2
130567 | 2014-12-13 | Scheduled Outage | Construction | Transformers TP7241, 5624 and 5625 isolated to allow crew to replace TP7241 and install new cable between transformers TP7241 and 5624, South March 24F2, ID # 130567 | None | None | 6 | 2 | 0 | West | 39F2
130567 | 2014-12-13 | Scheduled Outage | Construction | Transformers TP7241, 5624 and 5625 isolated to allow crew to replace TP7241 and install new cable between transformers TP7241 and 5624, South March 24F2, ID # 130567 | None | None | 7 | 288 | 34 | West | 39F2
130568 | 2014-12-13 | Scheduled Outage | Construction | To install new pole at QT132 | None | None | 5 | 608 | 51 | South | 22M23
130569 | 2014-12-13 | Scheduled Outage | Construction | scheduled outage to allow crew to install new riser cable and new switches feeding V531. | None | None | 1 | 175 | 3 | Central | UX03
130570 | 2014-12-13 | Scheduled Outage | Construction | Switching to isolate switchgear S8 required outage to transformers TP7241 and 3515, South March 39F2, ID # 130570 | None | None | 2 | 18 | 1 | West | 39F2
130574 | 2014-12-14 | Scheduled Outage | Maintenance | P530 (Metro) isolated to allow crew to pull in new XLPE cable. | None | XLPE | 1 | 55 | 1 | Central | SB16
130575 | 2014-12-15 | Scheduled Outage | Maintenance | VE34G isolated for customer vault maintenance. | None | Customer-Owned | 1 | 155 | 3 | East | BCHF1
130576 | 2014-12-15 | Defective Equipment | Electrical Failure | S2-2 red phase blew due to cable fault between 3048 and TP5405. Beaverbrook (24F1) ID# 130576. | U/G Cable | XLPE | 52 | 21 | 18 | West | 24F1
130576 | 2014-12-15 | Defective Equipment | Electrical Failure | S2-2 red phase blew due to cable fault between 3048 and TP5405. Beaverbrook (24F1) ID# 130576. | U/G Cable | XLPE | 53 | 154 | 136 | West | 24F1
130577 | 2014-12-15 | Scheduled Outage | Construction | schedualled outage to allow crew to splice new cables in the splice pit | None | None | 10 | 127 | 21 | East | 77M6
130578 | 2014-12-15 | Scheduled Outage | Vegetation Management | schedualled outage to remove trees from secondary | None | None | 10 | 450 | 75 | Central | SR04
130579 | 2014-12-15 | Scheduled Outage | Maintenance | Transformer #X34105 isolated by crew to repair a service | None | None | 11 | 20 | 4 | Central | TH01
130580 | 2014-12-15 | Scheduled Outage | Construction | Transformer #X36798 isolated by crew to relocate plant | None | None | 86 | 60 | 86 | Central | UX10
130581 | 2014-12-15 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER KT0674 TO TO CHANGE PRIMARY TAP SETTING TO LOWER THE SECONDARY VOLTAGE | None | None | 10 | 618 | 103 | Central | TD12
130582 | 2014-12-15 | Scheduled Outage | Vegetation Management | Transformer #X30355 isolated by crew to allow contractor to remove a tree | None | None | 10 | 450 | 75 | Central | SR04
130583 | 2014-12-15 | Defective Equipment | Defective Equipment/ Material | S281 W at 23 Sullivan opened due to defective switch. 39 customers were affected for 217 minutes. ID# 130583 | O/H Switchgear | Inline Switch | 39 | 217 | 141 | South | 170F1
130585 | 2014-12-15 | Scheduled Outage | Construction | Crew installing new riser cables and switches S25626 | None | None | 5 | 339 | 28 | Central | SA23
130587 | 2014-12-17 | Scheduled Outage | Construction | S14789 to EOL was isolated to allow crew to replace defective switches. Cyrville (CYRF2). ID# 130587 | None | None | 6 | 32 | 3 | East | CYRF2
130588 | 2014-12-17 | Scheduled Outage | Construction | Switch replacement. | None | None | 3 | 51 | 3 | East | CYRF3
130590 | 2014-12-17 | Scheduled Outage | Construction | Cable replacement. | None | None | 1 | 252 | 4 | Central | UX03
130591 | 2014-12-17 | Scheduled Outage | Construction | To allow crews to install new secondary services. | None | None | 15 | 102 | 26 | South | FAL02
130592 | 2014-12-17 | Scheduled Outage | Vegetation Management | SH04 from S18254 to EOL isolated for tree removal | None | None | 16 | 190 | 51 | Central | SH04
130595 | 2014-12-17 | Scheduled Outage | Forced Switching | Vault V471 interupted at CB1 to allow refusing of 600v transformer in the vault, Gladstone UX03, ID # 130595 | None | None | 69 | 10 | 12 | Central | UX03
130597 | 2014-12-18 | Scheduled Outage | Construction | Transformer TP8797 was isolated to allow crew to replace leaking transformer. Kanata MTS (624F1) ID# 130597. | None | None | 6 | 90 | 9 | West | 624F1
130598 | 2014-12-18 | Scheduled Outage | Construction | Transformer #X49424 isolated by crew for a pole replacement | None | None | 4 | 81 | 5 | East | 7F4
130599 | 2014-12-18 | Scheduled Outage | Forced Switching | Transformer X31641 was isolated to allow crew to make repairs to primary dead end. Riverdale (SR07) ID# 130599. | None | None | 16 | 64 | 17 | Central | SR07
130600 | 2014-12-19 | Scheduled Outage | Maintenance | To repair damaged cable at dip to TE2923, S730 | None | None | 1 | 73 | 1 | South | 87F6
130601 | 2014-12-19 | Scheduled Outage | Construction | Isolated to allow contractor to energize new minisub. | None | None | 2 | 207 | 7 | East | 4801F7
130603 | 2014-12-20 | Scheduled Outage | Maintenance | Transformer TP8105 at 1760 Sunview was isolated to allow crew to repair broken transformer pins and sleeves.Billberry (77M6). 1 customer was affected for 154 minutes. ID# 130603 | None | None | 1 | 154 | 3 | East | 77M6
130605 | 2014-12-20 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X29716 TO REPLACE TRIPLEX SERVICE | None | None | 10 | 30 | 5 | East | AE07
130606 | 2014-12-22 | Scheduled Outage | Construction | G269 to EOL was isoalted to allow crew to replace SMD switches. 2 customers were affected for 31 minutes. Limebank (7F4). ID# 130606 | None | None | 2 | 31 | 1 | East | 7F4
130607 | 2014-12-22 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30758 TO REPLACE GUY WIRE | None | None | 3 | 50 | 2 | Central | AB03
130608 | 2014-12-22 | Scheduled Outage | Construction | Transformer X23759 at 560 Wolffdale Cres isolated by crew to transfer plant | None | None | 7 | 95 | 11 | East | SO02
130609 | 2014-12-23 | Foreign Interference | Foreign Objects | The AM02 CB A/R/A due to construction tarp blew on the O/H circuit at 406 Arlington. Cambridge (AM02). ID# 130609 | None | None | 490 | 36 | 294 | Central | AM02
130610 | 2014-12-23 | Foreign Interference | Wildlife (Bird/Animal) | S29204 opened due to animal contact at 6686 Carriere causing the G279W to open also. Billberry (77M6) | None | None | 1 | 12 | 0 | East | 77M6
130610 | 2014-12-23 | Foreign Interference | Wildlife (Bird/Animal) | S29204 opened due to animal contact at 6686 Carriere causing the G279W to open also. Billberry (77M6) | None | None | 8 | 68 | 9 | East | 77M6
130611 | 2014-12-24 | Tree Contacts | Falling Tree | S25834B opened due to tree limb on the O/H. Woodroffe TW22. ID# 130611 | None | None | 29 | 86 | 42 | Central | TW22
130614 | 2014-12-25 | Adverse Weather | Extreme Wind | The Church AAT1 and AA03 Triped open during the wind storm in the Ottawa area. | None | None | 624 | 5 | 52 | East | AA03
130614 | 2014-12-25 | Adverse Weather | Extreme Wind | The Church AAT1 and AA03 Triped open during the wind storm in the Ottawa area. | None | None | 1874 | 2 | 62 | East | AA03
130615 | 2014-12-25 | Adverse Weather | Extreme Wind | Not yet known. | None | None | 267 | 5 | 22 | East | UZ12
130616 | 2014-12-25 | Adverse Weather | Extreme Wind | During the wind strom the AA03 triped open. Church (AA03). | None | None | 674 | 5 | 56 | East | AA03
130618 | 2014-12-25 | Adverse Weather | Extreme Wind | Tree fell on the O/H causing the SO05 to A/R/R during the wind storm | None | None | 479 | 44 | 351 | East | SO05
130619 | 2014-12-25 | Adverse Weather | Extreme Wind | S10247 RWB opened during the wind storm in the Ottawa area. Hinchey (TH01) | None | None | 171 | 67 | 191 | Central | TH01
130620 | 2014-12-25 | Adverse Weather | Extreme Wind | During the Wind Strom the GR6 tripped open, crew closed the GR6 and all load was restored. Leitrim 249F2 | None | None | 508 | 94 | 796 | East | 249F2
130621 | 2014-12-25 | Defective Equipment | Defective Equipment/ Material | W phase radial on Braemar opened due to defective line cut out. Beechwood (UB04). ID# 130621 | O/H Switchgear | Fused Cutout | 13 | 150 | 32 | East | UB04
130622 | 2014-12-25 | Adverse Weather | Extreme Wind | S1304 R phases opened during extreme wind. No direct cause found. | None | None | 127 | 185 | 392 | South | 49F6
130623 | 2014-12-25 | Adverse Weather | Extreme Wind | S1232 opened due to broken conductor caused by extreme wind. | O/H Conductor | O/H Conductor | 1 | 289 | 5 | South | 180F4
130624 | 2014-12-25 | Adverse Weather | Extreme Wind | Transformer fuse opened at X15530 during extreme wind | None | None | 9 | 374 | 56 | East | LTM01
130625 | 2014-12-25 | Tree Contacts | Falling Tree | Tree in overhead across from 221 Melrose ave. City tree crew on site at this time. | None | None | 327 | 31 | 169 | Central | SH04
130626 | 2014-12-27 | Tree Contacts | Broken Branch | Transformer X27424 at 1326 Paardeburgh Ave. isolated to cut down limb on wires. | None | None | 9 | 39 | 6 | East | UA07
130627 | 2014-12-27 | Scheduled Outage | Forced Switching | To allow Hydro Ottawa crews to replace a blown fuse on the 347/600 V secondary fed out of VT856 | None | Fused Cutout | 71 | 1 | 1 | Central | 413
130628 | 2014-12-28 | Defective Equipment | Defective Equipment/ Material | Crew found a burnt B phase HLC which caused the B phase wall fuse in the vault V0058 to blow. | O/H Conductor | Hot-Line Clamp | 14 | 120 | 28 | Central | AB05
130629 | 2014-12-29 | Defective Equipment | Defective Equipment/ Material | Defective transformer. | U/G Transformer | Padmount (1ph) | 10 | 375 | 62 | East | 77M5
130631 | 2015-01-04 | Defective Equipment | Electrical Failure | suspected cable fault caused the TD24 breaker (5412) to trip | U/G Cable | Unknown \ Other | 1 | 68 | 1 | Central | 5412
130632 | 2015-01-04 | Tree Contacts | Broken Branch | G884R fuse blew due to tree contact at 853 Blair. Moulton (8F1) ID# 130632. | None | None | 19 | 115 | 36 | East | 8F1
130634 | 2015-01-04 | Adverse Weather | Freezing Rain | Freezing rain resulted in tree contacts with primary line at 5845 Thunder rd causing G308B to open | None | None | 64 | 135 | 144 | East | 249F2
130635 | 2015-01-04 | Adverse Weather | Freezing Rain | Freezing rain resulted in tree contacts on a private line at 4180 Farmers Way causing G540R to open. Customer line left off & G540R closed. | None | None | 2 | 1192 | 40 | East | 249F2
130635 | 2015-01-04 | Adverse Weather | Freezing Rain | Freezing rain resulted in tree contacts on a private line at 4180 Farmers Way causing G540R to open. Customer line left off & G540R closed. | None | None | 49 | 109 | 89 | East | 249F2
130636 | 2015-01-04 | Adverse Weather | Freezing Rain | Unknown | Unknown \ Other | Unknown \ Other | 217 | 15 | 54 | East | AE05
130637 | 2015-01-04 | Adverse Weather | Ice/Icing | Downed Overhead Conductor | O/H Conductor | O/H Conductor | 4 | 449 | 30 | East | BLKF5
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 0 | 210240 | 0 | Central | 4304
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 0 | 210240 | 0 | Central | 4305
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 0 | 210240 | 0 | Central | TH00
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 0 | 210240 | 0 | Central | TH1UL
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 0 | 210240 | 0 | Central | TH2SH
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 0 | 210240 | 0 | Central | TL1TH
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 1 | 56 | 1 | Central | TH10-NIU
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 37 | 11 | 7 | Central | TH1SH
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 50 | 41 | 34 | Central | 4301
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 117 | 9 | 18 | Central | TH3SH
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 181 | 56 | 169 | Central | 4303
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 1366 | 41 | 933 | Central | TH2UJ
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 1450 | 49 | 1184 | Central | TH01
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 1514 | 56 | 1413 | Central | TH06
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 1968 | 49 | 1607 | Central | TH11-NIU
130638 | 2015-01-06 | Loss Of Supply | Transmission Inadvertent | Relay problem from Hydro One | None | None | 2203 | 40 | 1469 | Central | TH2UL
130639 | 2015-01-06 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 17 | 291 | 82 | East | TB06
130640 | 2015-01-06 | Scheduled Outage | Maintenance | Transformer X49414 at 4929 Limebank Rd. isolated by crew for pole replacement | None | None | 5 | 55 | 5 | East | 7F4
130642 | 2015-01-06 | Scheduled Outage | Vegetation Management | Transformer X23951 at 698 Roanoke St. isolated by 24/7 for tree trimming. | None | None | 18 | 277 | 83 | East | AP06
130643 | 2015-01-06 | Scheduled Outage | Construction | Transformer #X40724 isolated by crew to hook up a new service at 1991 Merivale | None | None | 2 | 70 | 2 | South | 72F7
130644 | 2015-01-07 | Unknown/Other | Unknown | The AE05 CB tripped under hold off. Cause remains under investiagtion. | None | None | 217 | 6 | 22 | East | AE05
130647 | 2015-01-07 | Scheduled Outage | Maintenance | To allow crews to repair our metering equipment. | None | None | 1 | 58 | 1 | South | 47F6
130649 | 2015-01-07 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #TP9342 opened up due to tree interference | O/H Switchgear | Fused Cutout | 8 | 119 | 16 | South | 49F6
130650 | 2015-01-07 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One 230KV line M29C | None | None | 0 | 252000 | 0 | West | TFXF3
130650 | 2015-01-07 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One 230KV line M29C | None | None | 624 | 7 | 73 | West | TFXF1
130650 | 2015-01-07 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One 230KV line M29C | None | None | 1628 | 9 | 244 | West | TFXF4
130650 | 2015-01-07 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One 230KV line M29C | None | None | 2144 | 9 | 322 | West | TFXF2
130650 | 2015-01-07 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One 230KV line M29C | None | None | 2308 | 9 | 346 | West | TFXF6
130650 | 2015-01-07 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One 230KV line M29C | None | None | 3404 | 7 | 397 | West | TFXF5
130651 | 2015-01-07 | Defective Equipment | Electrical Failure | cable fault | U/G Cable | XLPE | 25 | 216 | 90 | East | BLKF4
130652 | 2015-01-08 | Scheduled Outage | Vegetation Management | Isolation required for tree trimming | None | None | 23 | 74 | 28 | East | TB06
130654 | 2015-01-08 | Scheduled Outage | Maintenance | Transformer X3189 isolated so 24/7 could check the connections in the transformer. | None | None | 21 | 35 | 12 | South | 200F2
130657 | 2015-01-09 | Unknown/Other | Unknown | Unknown, to be patrolled | Unknown \ Other | Unknown \ Other | 512 | 14 | 119 | South | 200F6
130658 | 2015-01-09 | Scheduled Outage | Maintenance | Transformer X33682 at 21 Garrison St. isolated by crew to replace switch and arrestor | None | None | 7 | 28 | 3 | Central | TH01
130659 | 2015-01-09 | Scheduled Outage | Maintenance | Transformer X33740 at 336 Rockhurst Rd. isolated by crew to replace switch and arrestor | None | None | 5 | 60 | 5 | Central | TH01
130660 | 2015-01-09 | Scheduled Outage | Maintenance | Transformer x33725 at 41 Garrison St. isolated by crew to replace switch and arrestor | None | None | 7 | 60 | 7 | Central | TH01
130662 | 2015-01-09 | Unknown/Other | Unknown | Both the AM00 AM04 breakers opened and customerrs report seeing a flash, also the City of Ottawa reported a side walk plow struck a Hydro pole. Crews could not find any cause and circuits were re-energized. | O/H Conductor | O/H Conductor | 446 | 18 | 134 | Central | AM04
130663 | 2015-01-09 | Scheduled Outage | Maintenance | Transformer X33676 at 323 Oakdale Ave. isolated by crew to replace switch and arrestor | None | None | 10 | 60 | 10 | Central | TH01
130664 | 2015-01-09 | Defective Equipment | Mechanical Failure | Defective cable. | U/G Cable | XLPE | 8 | 145 | 19 | South | 49F6
130665 | 2015-01-09 | Defective Equipment | Defective Equipment/ Material | Replace broken cutout at transformer X14675 in front of 3136 Conroy Rd. Circuit was 249F4 | O/H Transformer | O/H Transformer (1ph) | 1 | 180 | 3 | East | LTM01
130666 | 2015-01-09 | Defective Equipment | Mechanical Failure | Downed primary conductor. | Pole Attachement | Insulator | 44 | 62 | 45 | West | 43F3
130669 | 2015-01-11 | Scheduled Outage | Construction | installation of customer owned FIT | None | None | 1 | 235 | 4 | East | 1807
130670 | 2015-01-11 | Scheduled Outage | Maintenance | to allow customer to remove asbestos, clean and torque vault, and Micro Fit installation. | None | None | 1 | 319 | 5 | East | 5306
130671 | 2015-01-11 | Scheduled Outage | Construction | Transformer TN9537 at 145 Richmond was isolated to allow contractor to install new switchgear. Hinchey (TH1UL). ID# 130671 | None | None | 1 | 224 | 4 | Central | TH1UL
130672 | 2015-01-11 | Defective Equipment | Electrical Failure | S18487 RWB opened to allow contractor make repairs to customer owned switch S29273CHZ | Customer Owned | Customer-Owned | 1 | 662 | 11 | South | 47F6
130673 | 2015-01-11 | Defective Equipment | Defective Equipment/ Material | Defective secondary open bus conductor. | O/H Conductor | O/H Conductor | 4 | 40 | 3 | South | 160F1
130674 | 2015-01-12 | Scheduled Outage | Construction | 2 tranformers, X49510 and X31390 isolated by crew to remove pole | None | None | 9 | 140 | 21 | Central | SB16
130675 | 2015-01-12 | Defective Equipment | Defective Equipment/ Material | S21789 B blew due to defective insulators at KT98 at 7 Rastila causing the ELW07 CB to A/R. Ellwood (ELW07). ID# 130675 | U/G Transformer | Padmount (1ph) | 11 | 341 | 63 | East | ELW07
130675 | 2015-01-12 | Defective Equipment | Defective Equipment/ Material | S21789 B blew due to defective insulators at KT98 at 7 Rastila causing the ELW07 CB to A/R. Ellwood (ELW07). ID# 130675 | U/G Transformer | Padmount (1ph) | 56 | 53 | 49 | East | ELW07
130675 | 2015-01-12 | Defective Equipment | Defective Equipment/ Material | S21789 B blew due to defective insulators at KT98 at 7 Rastila causing the ELW07 CB to A/R. Ellwood (ELW07). ID# 130675 | U/G Transformer | Padmount (1ph) | 118 | 110 | 216 | East | ELW07
130676 | 2015-01-13 | Scheduled Outage | Forced Switching | Transformer X39724 at 9 Goodwood Dr. isolated for 24/7 to disconnect service due to fire. | None | None | 4 | 38 | 3 | South | 140F4
130677 | 2015-01-13 | Defective Equipment | Electrical Failure | G474W opened caused by suspected cable fault on 249F4 white phase cable section between TE812 and TE801, Lietrim 249F4 ID # 130677 | U/G Cable | Unknown \ Other | 8 | 37 | 5 | East | LTM01
130677 | 2015-01-13 | Defective Equipment | Electrical Failure | G474W opened caused by suspected cable fault on 249F4 white phase cable section between TE812 and TE801, Lietrim 249F4 ID # 130677 | U/G Cable | Unknown \ Other | 13 | 23 | 5 | East | LTM01
130677 | 2015-01-13 | Defective Equipment | Electrical Failure | G474W opened caused by suspected cable fault on 249F4 white phase cable section between TE812 and TE801, Lietrim 249F4 ID # 130677 | U/G Cable | Unknown \ Other | 46 | 81 | 62 | East | LTM01
130678 | 2015-01-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32473 TO INSTALL NEW POLE | None | None | 5 | 90 | 8 | Central | UW01
130679 | 2015-01-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32472 TO INSTALL NEW POLE | None | None | 10 | 255 | 42 | Central | UW01
130680 | 2015-01-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32465 TO INSTALL NEW POLE | None | None | 7 | 255 | 30 | Central | UW01
130681 | 2015-01-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32476 TO INSTALL NEW POLE | None | None | 10 | 165 | 28 | Central | UW01
130682 | 2015-01-14 | Defective Equipment | Defective Equipment/ Material | Transformer X31878 opened due to defective transformer | O/H Transformer | O/H Transformer (1ph) | 19 | 195 | 62 | Central | AD06
130683 | 2015-01-15 | Scheduled Outage | Maintenance | planned outage to allow crew to make repairs to the overhead. | None | None | 15 | 56 | 14 | West | 43F3
130684 | 2015-01-15 | Scheduled Outage | Construction | planned outage to allow crew to install new service | None | None | 7 | 79 | 9 | South | 84F5
130684 | 2015-01-15 | Scheduled Outage | Construction | planned outage to allow crew to install new service | None | None | 21 | 1 | 0 | South | 84F5
130684 | 2015-01-15 | Scheduled Outage | Construction | planned outage to allow crew to install new service | None | None | 21 | 2 | 1 | South | 84F5
130685 | 2015-01-15 | Tree Contacts | Broken Branch | Transformer #X3484 opened up due to tree limb contact | O/H Switchgear | Fused Cutout | 4 | 59 | 4 | South | 145F3
130686 | 2015-01-15 | Scheduled Outage | Construction | Transformer #X31083 isolated by crew to install a new service | None | None | 22 | 75 | 28 | Central | UN03
130687 | 2015-01-15 | Scheduled Outage | Maintenance | Primary cable replacement in new duct bank | None | None | 12 | 108 | 22 | Central | UL03
130688 | 2015-01-16 | Defective Equipment | Defective Equipment/ Material | S26061 B opened due to defective underground cable. Bilberry (77M6). ID# 130688 | U/G Cable | XLPE | 29 | 17 | 8 | East | 77M6
130688 | 2015-01-16 | Defective Equipment | Defective Equipment/ Material | S26061 B opened due to defective underground cable. Bilberry (77M6). ID# 130688 | U/G Cable | XLPE | 264 | 146 | 642 | East | 77M6
130688 | 2015-01-16 | Defective Equipment | Defective Equipment/ Material | S26061 B opened due to defective underground cable. Bilberry (77M6). ID# 130688 | U/G Cable | XLPE | 761 | 16 | 203 | East | 77M6
130691 | 2015-01-17 | Scheduled Outage | Forced Switching | Crew replaced arcing fuse at X2429. | None | Fused Cutout | 3 | 5 | 0 | South | 200F1
130692 | 2015-01-18 | Defective Equipment | Defective Equipment/ Material | Blown fuse on vault repalced by 24/7. Fuse appears to have blown due to age. | Secondary \ Service | Unknown \ Other | 72 | 5 | 6 | East | UG09
130693 | 2015-01-18 | Loss Of Supply | Transmission Inadvertent | BECKF2 circuit tripped upon due to bird contact at Hydro One Beckwith Station. BECKF2 ID# 130693. | None | None | 2 | 40 | 1 | West | BECKF2
130693 | 2015-01-18 | Loss Of Supply | Transmission Inadvertent | BECKF2 circuit tripped upon due to bird contact at Hydro One Beckwith Station. BECKF2 ID# 130693. | None | None | 653 | 44 | 479 | West | BECKF2
130694 | 2015-01-18 | Unknown/Other | Unknown | S21789 B phase opened. Cause unknown. | None | None | 12 | 131 | 26 | East | ELW07
130694 | 2015-01-18 | Unknown/Other | Unknown | S21789 B phase opened. Cause unknown. | None | None | 20 | 47 | 16 | East | ELW07
130694 | 2015-01-18 | Unknown/Other | Unknown | S21789 B phase opened. Cause unknown. | None | None | 35 | 8 | 5 | East | ELW07
130694 | 2015-01-18 | Unknown/Other | Unknown | S21789 B phase opened. Cause unknown. | None | None | 48 | 23 | 18 | East | ELW07
130694 | 2015-01-18 | Unknown/Other | Unknown | S21789 B phase opened. Cause unknown. | None | None | 115 | 95 | 182 | East | ELW07
130695 | 2015-01-19 | Scheduled Outage | Construction | To install new poles and transferring overhead plant | None | None | 29 | 251 | 121 | East | AJ03
130695 | 2015-01-19 | Scheduled Outage | Construction | To install new poles and transferring overhead plant | None | None | 49 | 165 | 135 | East | AJ03
130695 | 2015-01-19 | Scheduled Outage | Construction | To install new poles and transferring overhead plant | None | None | 78 | 123 | 160 | East | AJ03
130698 | 2015-01-20 | Scheduled Outage | Vegetation Management | Tree trimming & removal for storm hardening | None | None | 23 | 335 | 128 | East | TB06
130699 | 2015-01-20 | Scheduled Outage | Construction | Fit program | None | None | 1 | 93 | 2 | Central | UV04
130700 | 2015-01-21 | Defective Equipment | Defective Equipment/ Material | blown elbow and flashed cables. | U/G Transformer | Padmount (3ph) | 1 | 185 | 3 | East | 4801F8
130700 | 2015-01-21 | Defective Equipment | Defective Equipment/ Material | blown elbow and flashed cables. | U/G Transformer | Padmount (3ph) | 4 | 19 | 1 | East | 4801F8
130701 | 2015-01-21 | Scheduled Outage | Construction | To reconfigure o/h line | None | None | 35 | 370 | 216 | Central | UW01
130702 | 2015-01-21 | Scheduled Outage | Construction | To de-commission V626 & energize new supply from TP10296. | None | None | 1 | 253 | 4 | Central | UN04
130703 | 2015-01-21 | Scheduled Outage | Construction | Transformer #X29054 isolated by crew for pole replacement. | None | None | 16 | 170 | 45 | East | AJ03
130704 | 2015-01-21 | Scheduled Outage | Maintenance | Transformer #X31196 isolated by crew for a service upgrade | None | None | 8 | 60 | 8 | Central | UF08
130705 | 2015-01-21 | Scheduled Outage | Maintenance | 2 transformers #X22776 and X22780 isolated by crew to repair primary, Gord McDonald from Sproule | None | None | 2 | 37 | 1 | East | V11F2
130706 | 2015-01-21 | Scheduled Outage | Construction | Transformer #T350 isolated by crew to reconnect a service after an upgrade | None | None | 13 | 10 | 2 | East | BCHF8
130707 | 2015-01-21 | Scheduled Outage | Construction | Transformer #X29064 isolated by crew for pole replacement | None | None | 13 | 160 | 35 | East | AJ03
130709 | 2015-01-22 | Scheduled Outage | Vegetation Management | 170F1 overhead section from X2729 to EOL isolated for tree trimming. | None | None | 17 | 199 | 56 | South | 170F1
130710 | 2015-01-22 | Scheduled Outage | Construction | V114 isolated to allow crew to re-arrange connections at S27005 | None | Fused Cutout | 1 | 70 | 1 | Central | UW02
130714 | 2015-01-23 | Scheduled Outage | Vegetation Management | 624F6 overhead from Switch 1682 to EOL isolates for tree trimming. | None | O/H Conductor | 1 | 169 | 3 | West | 624F6
130715 | 2015-01-23 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X36165 TO REPLACE GUY WIRE | None | None | 3 | 10 | 0 | West | 28F2
130716 | 2015-01-23 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change a pole | None | Pole | 1 | 78 | 1 | West | BECKF2
130717 | 2015-01-23 | Defective Equipment | Electrical Failure | AP05 W phase fuse to K631 opened due to defectvie cut out. | O/H Switchgear | Fused Cutout | 13 | 79 | 17 | East | AP05
130717 | 2015-01-23 | Defective Equipment | Electrical Failure | AP05 W phase fuse to K631 opened due to defectvie cut out. | O/H Switchgear | Fused Cutout | 25 | 86 | 36 | East | AP05
130719 | 2015-01-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X49424 TO INSTALL NEW POLE | None | None | 4 | 120 | 8 | East | 7F4
130720 | 2015-01-24 | Defective Equipment | Defective Equipment/ Material | Transformer X26961 at 2252 Fife Cres. Isolated so 24/7 crew could replace the triplex to 2256 Fife Cres. And the box switch at the transformer. | O/H Conductor | O/H Conductor | 6 | 45 | 4 | East | AJ05
130722 | 2015-01-25 | Defective Equipment | Mechanical Failure | Not yet known. | Pole Attachement | Insulator | 28 | 9 | 4 | West | ALEXF2
130722 | 2015-01-25 | Defective Equipment | Mechanical Failure | Not yet known. | Pole Attachement | Insulator | 138 | 1 | 2 | West | ALEXF2
130722 | 2015-01-25 | Defective Equipment | Mechanical Failure | Not yet known. | Pole Attachement | Insulator | 150 | 154 | 385 | West | ALEXF2
130723 | 2015-01-25 | Scheduled Outage | Maintenance | planned outage to Nortel and Algonquin College to allow crews to maintain 44LB09 and 44LB24. | None | None | 1 | 9 | 0 | South | 22M24
130723 | 2015-01-25 | Scheduled Outage | Maintenance | planned outage to Nortel and Algonquin College to allow crews to maintain 44LB09 and 44LB24. | None | None | 2 | 5 | 0 | South | 22M24
130723 | 2015-01-25 | Scheduled Outage | Maintenance | planned outage to Nortel and Algonquin College to allow crews to maintain 44LB09 and 44LB24. | None | None | 3 | 413 | 21 | South | 22M24
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 8 | 70 | 9 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 19 | 20 | 6 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 19 | 49 | 16 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 30 | 14 | 7 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 42 | 66 | 46 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 68 | 140 | 159 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 174 | 19 | 55 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 200 | 22 | 73 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 200 | 50 | 167 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 263 | 38 | 167 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 626 | 31 | 323 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 626 | 80 | 835 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 871 | 13 | 189 | West | BRDF5
130725 | 2015-01-26 | Defective Equipment | Electrical Failure | BRDF5 and F7 load was interrupted due to cable fault between transformers 3117B and 3118B. Bridlewood (BRDF5, BRDF7) ID# 130725 | U/G Cable | XLPE | 871 | 326 | 4732 | West | BRDF5
130728 | 2015-01-26 | Scheduled Outage | Construction | Transformer X29066 was isolated to allow crew to replace pole. Playfair (AJ03) ID# 130728. | None | None | 18 | 425 | 128 | East | AJ03
130730 | 2015-01-26 | Scheduled Outage | Construction | Transformer X32566 (new #X48266) at 1772 Ainsley Dr. isolated by contractor for pole change | None | None | 9 | 255 | 38 | Central | UW01
130731 | 2015-01-26 | Scheduled Outage | Construction | Transformer X23102-1652681 at 154 Barrette St. isolated by crew for transformer upgrade | None | None | 22 | 61 | 22 | East | AC05
130732 | 2015-01-27 | Scheduled Outage | Vegetation Management | TD01 line from S27544 to end of line was isolated to allow crew to perform tree trimming. Lincoln Heights (TD01) ID# 130732. | None | None | 26 | 127 | 55 | Central | TD01
130735 | 2015-01-27 | Defective Equipment | Mechanical Failure | REPLACED DEFECTIVE SWITCH FEEDING TRANSFORMER X33042 | O/H Transformer | O/H Transformer (1ph) | 5 | 55 | 5 | South | 180F4
130736 | 2015-01-28 | Scheduled Outage | Maintenance | Transformer 3051B was isolated to allow crew to replace leaking transformer | None | Padmount (1ph) | 9 | 180 | 27 | West | 24F1
130737 | 2015-01-28 | Scheduled Outage | Construction | AJ03 section between Temp 31 and Temp 24 switches was isolated to allow crew to install poles and reconfigure overhead. Playfair (AJ03) ID# 130737. | None | None | 38 | 276 | 175 | East | AJ03
130738 | 2015-01-28 | Scheduled Outage | Vegetation Management | TB2JP red phase line from S15844 to end of line was isolated to allow crew to remove tree from overhead. Russell (TB2JP) ID# 130738. | None | None | 20 | 79 | 26 | East | TB2JP
130739 | 2015-01-28 | Scheduled Outage | Maintenance | ISOLATED AND REPLACED TRANSFORMER X24692 DUE TO HIGH VOLTAGE ISSUES ON THE SECONDARY BUSS | None | None | 15 | 140 | 35 | East | AP03
130740 | 2015-01-28 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X29098 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 9 | 185 | 28 | East | UZ11
130741 | 2015-01-28 | Scheduled Outage | Construction | AJ03 white phase from 1841 Lorraine to EOL was isolated to allow crew to install poles and reconfigure overhead. Playfair (AJ03) ID# 130741. | None | None | 18 | 427 | 128 | East | AJ03
130743 | 2015-01-29 | Scheduled Outage | Vegetation Management | UB07 B phase from pole 65A4a-0402 to EOL was isolated for tree trimming | None | None | 15 | 61 | 15 | East | UB07
130744 | 2015-01-29 | Scheduled Outage | Vegetation Management | To remove large tree from rear of 883 Ivanhoe | None | None | 18 | 326 | 98 | Central | TD05
130745 | 2015-01-29 | Scheduled Outage | Construction | To re-arrange O/H line | None | None | 28 | 75 | 35 | East | SO10
130746 | 2015-01-29 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X27004 TO UN-WRAP THE SECONDARY NEUTRAL | None | None | 9 | 10 | 2 | East | AE01
130747 | 2015-01-29 | Human Element | Switching Error | Switching error | Station Equipment | Primary Switchgear | 267 | 9 | 40 | Central | TM3UC
130748 | 2015-01-29 | Defective Equipment | Mechanical Failure | phase of UC10 down at 1777 woodward | O/H Conductor | O/H Conductor | 138 | 97 | 223 | Central | UC06
130748 | 2015-01-29 | Defective Equipment | Mechanical Failure | phase of UC10 down at 1777 woodward | O/H Conductor | O/H Conductor | 611 | 97 | 988 | Central | UC10
130749 | 2015-01-30 | Adverse Weather | Extreme Wind | Transformer #X23247 opened up due to secondary got wrapped together due to wind | O/H Switchgear | Fused Cutout | 22 | 66 | 24 | East | UT06
130750 | 2015-01-30 | Scheduled Outage | Construction | Transformer #X29097 isolated by crew for a pole replacement | None | None | 9 | 135 | 20 | East | UZ11
130751 | 2015-01-30 | Foreign Interference | Vehicle | Hydro One pole broken at Beckwith D.S. Hydro One reported a MVA broke a guy wire causing hydro pole to break at HWY29 and Seventh Line Rd Beckwith. | Pole | Pole | 651 | 40 | 434 | West | BECKF2
130752 | 2015-02-01 | Scheduled Outage | Maintenance | Customers on UW01 transferred to UW05 part of pole and line replacement by K-Line. Work done on Sunday due to Agincourt school affected. | None | None | 350 | 191 | 1114 | Central | UW01
130753 | 2015-02-02 | Scheduled Outage | Construction | Black and MAC to install new poles and reconfigure conductor on Lorraine Ave and Arizona Ave | None | None | 50 | 321 | 268 | East | AJ03
130754 | 2015-02-02 | Scheduled Outage | Maintenance | Transformer 3118B isolated to allow crew to pull in new cable through transformer base. | None | Unknown \ Other | 8 | 99 | 13 | West | BRDF5
130755 | 2015-02-02 | Defective Equipment | Electrical Failure | cable fault | U/G Cable | XLPE | 496 | 90 | 744 | South | 49F1
130755 | 2015-02-02 | Defective Equipment | Electrical Failure | cable fault | U/G Cable | XLPE | 1190 | 134 | 2658 | South | 160F1
130755 | 2015-02-03 | Defective Equipment | Electrical Failure | cable fault | U/G Cable | XLPE | 26 | 3 | 1 | South | 160F3
130756 | 2015-02-03 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer X49011 at 1856 Lorraine Ave. isolated by contractor to remove tree limbs from open wire bus | None | None | 15 | 12 | 3 | East | AJ03
130757 | 2015-02-03 | Scheduled Outage | Maintenance | Transformer X33853 at 123 Huron Ave. N isolated by crew to replace cutout and arrestor | None | None | 13 | 58 | 13 | Central | TH01
130758 | 2015-02-04 | Scheduled Outage | Construction | replacing transformer | None | None | 10 | 272 | 45 | West | MWDF4
130759 | 2015-02-04 | Scheduled Outage | Vegetation Management | TW22 white phase overhead section from S27404 isolated to allow for tree removal, Woodroffe TS TW22, ID #130759 | None | None | 25 | 215 | 90 | Central | TW22
130760 | 2015-02-04 | Scheduled Outage | Maintenance | 4801F8 from switch G991 to EOL was isolated to allow crew to replace switches and trim trees. Uplands (4801F8) ID# 130760. | None | None | 1 | 238 | 4 | East | 4801F8
130761 | 2015-02-04 | Scheduled Outage | Construction | TP10177 isolated to verify the unit connected to the transforemer, Bayshore 49F2, ID # 130761 | None | None | 16 | 41 | 11 | South | 49F2
130762 | 2015-02-04 | Unknown/Other | Unknown | 7F4 circuit breaker tripped open under hold off due to blown fuse at G30R. Patrol found no cause. Limebank (7F4) ID# 130762. | Unknown \ Other | Unknown \ Other | 49 | 20 | 16 | East | 7F4
130762 | 2015-02-04 | Unknown/Other | Unknown | 7F4 circuit breaker tripped open under hold off due to blown fuse at G30R. Patrol found no cause. Limebank (7F4) ID# 130762. | Unknown \ Other | Unknown \ Other | 1237 | 35 | 722 | East | 7F4
130763 | 2015-02-05 | Scheduled Outage | Vegetation Management | Remove trees for storm hardening. | None | None | 25 | 400 | 167 | Central | TW22
130764 | 2015-02-05 | Scheduled Outage | Vegetation Management | X16931 to EOL was isolated to allow City of Ottawa tree crew to trim trees on city owned primary and secondary line. | None | None | 1 | 328 | 5 | East | BCHF2
130766 | 2015-02-05 | Defective Equipment | Defective Equipment/ Material | REPLACED DEFECTIVE SWITCH FEEDING TRANSFORMER X29358 | O/H Switchgear | Fused Cutout | 5 | 82 | 7 | East | UG03
130770 | 2015-02-07 | Scheduled Outage | Forced Switching | Transformer X34470 was isolated to allow crew to cut down service to 3340 Kodiak for Fire Dept. Cahill (AN04) ID# 130770. | None | None | 14 | 6 | 1 | East | AN04
130771 | 2015-02-08 | Scheduled Outage | Construction | Pole change and service upgrade. At pole # X18760. | None | Pole | 1 | 210 | 4 | East | BLKF8
130772 | 2015-02-09 | Scheduled Outage | Construction | Pole replacement & re-arrange o/h. | None | None | 56 | 199 | 186 | East | AJ03
130773 | 2015-02-09 | Scheduled Outage | Construction | To transfer plant to new o/h. | None | None | 30 | 80 | 40 | Central | UW05
130774 | 2015-02-09 | Scheduled Outage | Maintenance | 2 transformers, #X33874 and X33720 isolated by crew to replace cut outs and arrestors | None | None | 22 | 64 | 23 | Central | TH01
130775 | 2015-02-09 | Scheduled Outage | Maintenance | Transformer X13340 at 1102 Sunrise Ave. isolated by crew to replace cutout and arrestor. | None | None | 10 | 37 | 6 | East | 7F4
130776 | 2015-02-09 | Scheduled Outage | Maintenance | Transformer X33858 at 53 Huron isolated by crew to replace cutout and arrestor | None | None | 10 | 55 | 9 | Central | TH01
130777 | 2015-02-09 | Scheduled Outage | Maintenance | Transformer X31470 at 33 Granve Ave. isolated by crew to replace cutout and arrestor | None | None | 10 | 44 | 7 | Central | TH01
130778 | 2015-02-09 | Scheduled Outage | Maintenance | Transformer #X30499 isolated by crew to replace switch | None | None | 10 | 90 | 15 | Central | TH01
130779 | 2015-02-09 | Scheduled Outage | Maintenance | Transformer X31471 at 43 Granve Ave isolated by crew to change cutout and arrestor | None | None | 5 | 46 | 4 | Central | TH01
130780 | 2015-02-09 | Scheduled Outage | Maintenance | Transformer X31469 at 53 Granve Ave. isolated by crew to replace cutout and arrestor | None | None | 9 | 46 | 7 | Central | TH01
130781 | 2015-02-09 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X49011 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 100 | 10 | East | AJ03
130782 | 2015-02-10 | Scheduled Outage | Construction | To transfer plant from the UX03 to the UX06. | None | O/H Transformer (3ph) | 49 | 190 | 155 | Central | UX03
130783 | 2015-02-10 | Scheduled Outage | Construction | To transfer plant to new overhead. | None | O/H Conductor | 20 | 353 | 118 | Central | UW05
130784 | 2015-02-10 | Scheduled Outage | Construction | Transformer X49013 at 1819 Lorraine Ave. isolated by contractor for pole replacement | None | None | 2 | 100 | 3 | East | AJ03
130785 | 2015-02-10 | Scheduled Outage | Vegetation Management | Transformer X27822 at 1381 Orillia St. isolated by crew to remove tree limb from secondary | None | None | 15 | 24 | 6 | Central | 505
130786 | 2015-02-10 | Scheduled Outage | Construction | Transformer X31742 at 1774 Forman Ave. isolated by contractor for pole change. | None | None | 4 | 240 | 16 | Central | UW05
130787 | 2015-02-10 | Scheduled Outage | Construction | Transformer X32560 at 1791 Paisley Ave isolated by contractor for pole replacement | None | None | 5 | 240 | 20 | Central | UW05
130795 | 2015-02-10 | Defective Equipment | Defective Equipment/ Material | Defective RX2005 white phase and lightning arrestor caused crews to perform to trouble shoot the overhead line into sections. Alexander (ALEXF2) ID#130795 | Pole Attachement | Arrester | 27 | 13 | 6 | West | ALEXF2
130795 | 2015-02-10 | Defective Equipment | Defective Equipment/ Material | Defective RX2005 white phase and lightning arrestor caused crews to perform to trouble shoot the overhead line into sections. Alexander (ALEXF2) ID#130795 | Pole Attachement | Arrester | 27 | 75 | 34 | West | ALEXF2
130795 | 2015-02-10 | Defective Equipment | Defective Equipment/ Material | Defective RX2005 white phase and lightning arrestor caused crews to perform to trouble shoot the overhead line into sections. Alexander (ALEXF2) ID#130795 | Pole Attachement | Arrester | 51 | 14 | 12 | West | ALEXF2
130795 | 2015-02-10 | Defective Equipment | Defective Equipment/ Material | Defective RX2005 white phase and lightning arrestor caused crews to perform to trouble shoot the overhead line into sections. Alexander (ALEXF2) ID#130795 | Pole Attachement | Arrester | 61 | 5 | 5 | West | ALEXF2
130795 | 2015-02-10 | Defective Equipment | Defective Equipment/ Material | Defective RX2005 white phase and lightning arrestor caused crews to perform to trouble shoot the overhead line into sections. Alexander (ALEXF2) ID#130795 | Pole Attachement | Arrester | 67 | 26 | 29 | West | ALEXF2
130795 | 2015-02-10 | Defective Equipment | Defective Equipment/ Material | Defective RX2005 white phase and lightning arrestor caused crews to perform to trouble shoot the overhead line into sections. Alexander (ALEXF2) ID#130795 | Pole Attachement | Arrester | 85 | 6 | 8 | West | ALEXF2
130795 | 2015-02-10 | Defective Equipment | Defective Equipment/ Material | Defective RX2005 white phase and lightning arrestor caused crews to perform to trouble shoot the overhead line into sections. Alexander (ALEXF2) ID#130795 | Pole Attachement | Arrester | 88 | 45 | 66 | West | ALEXF2
130795 | 2015-02-10 | Defective Equipment | Defective Equipment/ Material | Defective RX2005 white phase and lightning arrestor caused crews to perform to trouble shoot the overhead line into sections. Alexander (ALEXF2) ID#130795 | Pole Attachement | Arrester | 116 | 50 | 97 | West | ALEXF2
130795 | 2015-02-10 | Defective Equipment | Defective Equipment/ Material | Defective RX2005 white phase and lightning arrestor caused crews to perform to trouble shoot the overhead line into sections. Alexander (ALEXF2) ID#130795 | Pole Attachement | Arrester | 116 | 90 | 174 | West | ALEXF2
130796 | 2015-02-11 | Scheduled Outage | Construction | planned outage to allow crew to transfer plant | None | None | 1 | 240 | 4 | Central | AM06
130798 | 2015-02-11 | Scheduled Outage | Construction | Transfer plant to new pole | None | None | 6 | 120 | 12 | East | AJ03
130799 | 2015-02-11 | Scheduled Outage | Construction | To allow contractor to install new secondary cables. | None | Padmount (3ph) | 25 | 252 | 105 | East | 2206
130800 | 2015-02-11 | Scheduled Outage | Construction | planned outage to allow crew to transfer plant | None | None | 20 | 407 | 136 | Central | UW05
130801 | 2015-02-12 | Scheduled Outage | Construction | Transformer TP3522 was isolated to allow crew to replace SMD switches. Uplands (4801F8) ID# 130801. | None | None | 1 | 36 | 1 | East | 4801F8
130802 | 2015-02-12 | Scheduled Outage | Vegetation Management | Vegetation Management on Firestone | None | None | 64 | 47 | 50 | Central | UV05
130803 | 2015-02-12 | Scheduled Outage | Construction | Transformer TP3452 was isolated to allow crew to replace SMD switches. Uplands (4801F8) ID#130803. | None | None | 147 | 22 | 54 | East | 4801F8
130804 | 2015-02-12 | Scheduled Outage | Construction | Transformer TP3643 was isolated to allow crew to energize 4 new transformers. Leitrim (249F1) ID# 130804. | None | None | 8 | 160 | 21 | East | LTM01
130805 | 2015-02-12 | Scheduled Outage | Maintenance | Transformer TP3985 was isolated to allow crew to replace SMD switches. Uplands (4801F8) ID# 130805. | None | None | 143 | 35 | 83 | East | 4801F8
130806 | 2015-02-12 | Scheduled Outage | Construction | Transformers TE389 and TE599 were isolated to allow crews to install new cables. Blackburn (BLKF1) ID# 130806. | None | None | 25 | 190 | 79 | East | BLKF1
130807 | 2015-02-12 | Scheduled Outage | Maintenance | Transformer X33690 at 33 Garrison St isolated by crew to replace switch | None | None | 3 | 15 | 1 | Central | TH01
130808 | 2015-02-12 | Scheduled Outage | Maintenance | Transformer X34050 was isolated to change the defective cutout, Hinchey TH01, ID #130808 | None | Fused Cutout | 9 | 61 | 9 | Central | TH01
130809 | 2015-02-12 | Scheduled Outage | Maintenance | Transformer X33742 at 316 Carleton Ave isolated by crew to replace a switch | None | None | 9 | 30 | 4 | Central | TH01
130810 | 2015-02-12 | Scheduled Outage | Maintenance | Transformer X33741 at 290 Carleton Ave isolated by crew to replace switch | None | None | 7 | 45 | 5 | Central | TH01
130811 | 2015-02-13 | Unknown/Other | Unknown | S13095 red phase fuse opened, no cause found, Russell TB14, ID # 130811 | O/H Switchgear | Fused Cutout | 62 | 149 | 154 | East | TB14
130812 | 2015-02-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X29729 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 6 | 100 | 10 | East | TB14
130813 | 2015-02-13 | Defective Equipment | Electrical Failure | S20938 red phase opened caused by a suspected cable fault between TP8105 and TP8107, Bilberry 77M6, ID # 130813 | U/G Cable | XLPE | 82 | 122 | 167 | East | 77M6
130814 | 2015-02-13 | Defective Equipment | Electrical Failure | repaired red phase cable fault. | U/G Cable | Unknown \ Other | 1 | 1637 | 27 | West | 28F2
130816 | 2015-02-15 | Scheduled Outage | Construction | planned outage to cutover to new switchgear. | None | None | 1 | 359 | 6 | East | 1809
130818 | 2015-02-17 | Scheduled Outage | Construction | Fit Project | None | None | 1 | 211 | 4 | South | 200F6
130819 | 2015-02-17 | Scheduled Outage | Construction | Hydro Ottawa crews isolated TP7676R to allow J.W Leslie crews to remove old primary cable and connect & commission 2 new transformers. | None | None | 11 | 244 | 45 | South | FAL03
130820 | 2015-02-17 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to replace a defective transformer elbow | None | Elbow \ Insert | 52 | 48 | 42 | South | 72F2
130821 | 2015-02-17 | Tree Contacts | Broken Branch | A tree branch fell into the O/H at Parcia & Wallford | Unknown \ Other | Unknown \ Other | 61 | 29 | 29 | South | 190F5
130821 | 2015-02-17 | Tree Contacts | Broken Branch | A tree branch fell into the O/H at Parcia & Wallford | Unknown \ Other | Unknown \ Other | 1093 | 36 | 656 | South | 190F5
130821 | 2015-02-17 | Tree Contacts | Broken Branch | A tree branch fell into the O/H at Parcia & Wallford | Unknown \ Other | Unknown \ Other | 1713 | 113 | 3226 | South | 190F5
130822 | 2015-02-17 | Scheduled Outage | Construction | SC3098 isolated to upgrade to SC19919. | None | None | 2 | 271 | 9 | Central | TM1AH
130823 | 2015-02-17 | Scheduled Outage | Vegetation Management | SM02 from S15670 to EOL isolated fomr tree removal. | None | O/H Conductor | 28 | 212 | 99 | Central | SM02
130824 | 2015-02-17 | Scheduled Outage | Construction | Transformer X48600 at 2154 Navaho Dr. isolated by contractor for transfer of plant | None | None | 10 | 240 | 40 | Central | UW01
130825 | 2015-02-17 | Defective Equipment | Electrical Failure | transformer X26828 failed, transformer X29077 opened to allow transfer of secondary bus, Urbandale AE03, ID # 130825 | O/H Transformer | O/H Transformer (1ph) | 11 | 226 | 41 | East | AE03
130825 | 2015-02-18 | Defective Equipment | Electrical Failure | transformer X26828 failed, transformer X29077 opened to allow transfer of secondary bus, Urbandale AE03, ID # 130825 | O/H Transformer | O/H Transformer (1ph) | 15 | 68 | 17 | East | AE03
130827 | 2015-02-18 | Scheduled Outage | Construction | AJ03 isolated between TEMP 31 and TEMP 36 for pole change. | None | Pole | 18 | 234 | 70 | East | AJ03
130828 | 2015-02-18 | Scheduled Outage | Vegetation Management | SM02 from rear of 184 Crerar to EOL isolated for tree removal. | None | O/H Conductor | 13 | 324 | 70 | Central | SM02
130829 | 2015-02-18 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crew to change a defective transformer (X33152) | None | O/H Transformer (1ph) | 1 | 79 | 1 | West | RHNF1
130830 | 2015-02-18 | Scheduled Outage | Maintenance | To transfer customers back to their original transformer. | None | None | 11 | 55 | 10 | East | AE03
130830 | 2015-02-18 | Scheduled Outage | Maintenance | To transfer customers back to their original transformer. | None | None | 15 | 24 | 6 | East | AE03
130831 | 2015-02-18 | Defective Equipment | Electrical Failure | Barrier board inside disconnect switch at TN6126CZZ fell and caused a flash. RWB fuses at SC5441CHZ opened. | Customer Owned | Customer-Owned | 3 | 266 | 13 | East | 1808
130832 | 2015-02-19 | Scheduled Outage | Vegetation Management | planned outage to allow for tree trimming | None | None | 12 | 276 | 55 | Central | TD06
130833 | 2015-02-19 | Defective Equipment | Defective Equipment/ Material | Not yet known. | U/G Cable | XLPE | 47 | 36 | 28 | South | 87F5
130833 | 2015-02-19 | Defective Equipment | Defective Equipment/ Material | Not yet known. | U/G Cable | XLPE | 67 | 94 | 105 | South | 87F5
130834 | 2015-02-19 | Foreign Interference | Crane | R W Tomlinson backhow made contact witht the overhead wires. Contact Mike LeFebvre 613-913-8457 | None | None | 287 | 22 | 105 | East | SO10
130836 | 2015-02-20 | Defective Equipment | Defective Equipment/ Material | 8808 Flewellyen Fuse Holder is broken at X10964 and the the clamp is burnt off, and there is arcing marks on the pole,. | O/H Switchgear | Fused Cutout | 1 | 71 | 1 | West | BECKF2
130836 | 2015-02-20 | Defective Equipment | Defective Equipment/ Material | 8808 Flewellyen Fuse Holder is broken at X10964 and the the clamp is burnt off, and there is arcing marks on the pole,. | O/H Switchgear | Fused Cutout | 56 | 28 | 26 | West | BECKF2
130836 | 2015-02-20 | Defective Equipment | Defective Equipment/ Material | 8808 Flewellyen Fuse Holder is broken at X10964 and the the clamp is burnt off, and there is arcing marks on the pole,. | O/H Switchgear | Fused Cutout | 106 | 107 | 189 | West | BECKF2
130836 | 2015-02-20 | Defective Equipment | Defective Equipment/ Material | 8808 Flewellyen Fuse Holder is broken at X10964 and the the clamp is burnt off, and there is arcing marks on the pole,. | O/H Switchgear | Fused Cutout | 274 | 11 | 50 | West | BECKF2
130836 | 2015-02-20 | Defective Equipment | Defective Equipment/ Material | 8808 Flewellyen Fuse Holder is broken at X10964 and the the clamp is burnt off, and there is arcing marks on the pole,. | O/H Switchgear | Fused Cutout | 477 | 52 | 413 | West | BECKF2
130836 | 2015-02-20 | Defective Equipment | Defective Equipment/ Material | 8808 Flewellyen Fuse Holder is broken at X10964 and the the clamp is burnt off, and there is arcing marks on the pole,. | O/H Switchgear | Fused Cutout | 677 | 145 | 1636 | West | BECKF2
130837 | 2015-02-19 | Unknown/Other | Unknown | Distribution 400A 600V red phase fuse. | Secondary \ Service | U/G Service | 20 | 55 | 18 | Central | 413
130839 | 2015-02-20 | Scheduled Outage | Forced Switching | To allow Hydro Ottawa crews to replace a padmount transformer that was hit by a snow plow. | None | Padmount (1ph) | 18 | 102 | 31 | East | BLKF1
130843 | 2015-02-23 | Defective Equipment | Defective Equipment/ Material | Transformer #PT189 opened up due to blown arrestor | O/H Switchgear | Fused Cutout | 8 | 254 | 34 | East | TB07
130845 | 2015-02-24 | Scheduled Outage | Construction | Transformer #X49026 isolated by crew to transfer plant | None | None | 5 | 157 | 13 | East | AJ03
130846 | 2015-02-24 | Scheduled Outage | Vegetation Management | At 08:45am crews isolated TD01 from S22582 to EOL to allow for tree removal. Lincoln Heights (TD01) ID#130846 | None | None | 47 | 238 | 186 | Central | TD01
130847 | 2015-02-24 | Scheduled Outage | Vegetation Management | At 10:00am crews isolated a section of UZ12 from S18175 to EOL to allow for tree removal. Walkley (UZ12)ID#130847 | None | None | 50 | 192 | 160 | East | UZ12
130848 | 2015-02-24 | Scheduled Outage | Construction | At 10:38 crews isolated section of UW05 to install poles and transfer plant. Woodroffe (UW05) ID#130848 | None | None | 16 | 307 | 82 | Central | UW05
130849 | 2015-02-25 | Scheduled Outage | Construction | Transformer #X29068 isolated by crew to transfer plant | None | None | 10 | 190 | 32 | East | AJ03
130850 | 2015-02-25 | Scheduled Outage | Vegetation Management | At 9:14am crews isolated TD01 from S19379 to end of line to allow crew to remove a tree. 22 customers affected for 170 mins. Lincoln Heights (TD01) ID#130850 | None | None | 22 | 170 | 62 | Central | TD01
130851 | 2015-02-25 | Scheduled Outage | Construction | Install new hydro poles and transfer plant. | None | Pole | 20 | 142 | 47 | Central | UW05
130853 | 2015-02-26 | Scheduled Outage | Vegetation Management | planned outage for tree trimming | None | None | 26 | 200 | 87 | East | UZ11
130854 | 2015-02-26 | Scheduled Outage | Vegetation Management | To allow forestry crews to remove large dead trees in the rear of 30 St. Claire | None | None | 16 | 137 | 37 | South | EPWF1
130855 | 2015-02-26 | Scheduled Outage | Forced Switching | To allow Hydro Ottawa crews, Drain All & Antrim Contracting to perform emergency soil remediation at transformer 2156 R. This transformer feeds lighting only. | None | None | 1 | 1919 | 32 | West | MWDF4
130856 | 2015-02-26 | Scheduled Outage | Maintenance | Transformer #X13372 isolated by crew to replace cut out and insulator. | None | None | 9 | 25 | 4 | East | 7F4
130857 | 2015-02-26 | Scheduled Outage | Forced Switching | Blown insulator in TE1091, center insulator W phase | None | Arrester | 1 | 290 | 5 | South | 180F1
130858 | 2015-02-26 | Unknown/Other | Unknown | Red phase fuse in VT852 blown again. Fuse replaced. Fault recorder on line will be looked at tomorrow | None | None | 72 | 47 | 56 | Central | 403
130859 | 2015-02-26 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X13370 TO REPLACE THE SWITCH AND ARRESTER | None | None | 4 | 35 | 2 | East | 7F4
130860 | 2015-02-27 | Scheduled Outage | Maintenance | Transformer #X29154 isolated by crew to redo connections | None | None | 10 | 30 | 5 | East | UT02
130862 | 2015-02-27 | Scheduled Outage | Construction | Transformer #X29088 isolated by crew due to a pole replacement | None | None | 6 | 165 | 16 | East | UZ11
130863 | 2015-02-27 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change the transformer switch on transformer X33681. | None | Fused Cutout | 11 | 50 | 9 | Central | TH01
130864 | 2015-02-27 | Human Element | Improper Equipment/Tool/ Maintenance | tree trimmers dropped a limb on the overhead | None | None | 277 | 79 | 365 | East | UZ12
130866 | 2015-02-27 | Human Element | Improper Equipment/Tool/ Maintenance | Forestry contractors dropped a tree limb on the O/H lines | None | None | 23 | 304 | 117 | East | UZ12
130867 | 2015-02-27 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER K525 TO REPLACE BLOWN SECONDARY FUSE | None | None | 23 | 10 | 4 | Central | AD04
130868 | 2015-02-28 | Scheduled Outage | Construction | Crew transfering cables to new pole | None | None | 2 | 285 | 10 | Central | UJ07
130869 | 2015-02-28 | Defective Equipment | Defective Equipment/ Material | Defective arrestor. | Pole Attachement | Arrester | 654 | 160 | 1744 | West | BECKF2
130871 | 2015-02-28 | Defective Equipment | Electrical Failure | At 5:30pm customers reported no power on transofmer X23543 at the rear of 882 Trojan Ave. Upon arrival crew found a defective cutout and proceeded to replace it. Church (AA04) ID# 130871 | O/H Switchgear | Fused Cutout | 12 | 190 | 38 | East | AA04
130872 | 2015-03-01 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 7 | 135 | 16 | East | 7F2
130872 | 2015-03-01 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 57 | 55 | 52 | East | 7F2
130873 | 2015-03-02 | Scheduled Outage | Maintenance | SMD switch replacement program at S26543 | None | None | 10 | 49 | 8 | East | 77M2
130874 | 2015-03-02 | Scheduled Outage | Construction | Replace defective elbow and inserts. | U/G Cable Attachement | Elbow \ Insert | 11 | 110 | 20 | East | 6F1
130875 | 2015-03-02 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32143 TO REPLACE SWITCH AND ARRESTER | None | None | 8 | 45 | 6 | West | BECKF2
130877 | 2015-03-02 | Scheduled Outage | Construction | S20356 switches open to replace SMD20 switches. | None | None | 1 | 37 | 1 | East | 77M2
130879 | 2015-03-02 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER GL04644 TO REPLACE SWITCH AND ARRESTER | None | None | 8 | 25 | 3 | East | 7F4
130880 | 2015-03-02 | Scheduled Outage | Construction | Transformer #X33420 isolated by crew to transfer hydro plant | None | None | 10 | 45 | 8 | Central | UW06
130881 | 2015-03-02 | Scheduled Outage | Maintenance | Transformer #X31759 isolated by crew to replace hot line clamp | None | None | 7 | 30 | 4 | Central | SM13
130882 | 2015-03-02 | Scheduled Outage | Construction | Transformer #X32811 isolated by crew to transfer plant | None | None | 10 | 60 | 10 | Central | UW06
130883 | 2015-03-02 | Scheduled Outage | Construction | Transformer #X33419 isolated by crew to transfer plant | None | None | 11 | 45 | 8 | Central | UW06
130884 | 2015-03-03 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to relocate a riser pole & replace the overhead conductor | None | None | 20 | 1620 | 540 | South | 200F6
130885 | 2015-03-03 | Scheduled Outage | Construction | 600V service fed from V815 isolated to allow crew to replace secondary cables | None | None | 2 | 140 | 5 | Central | SK16
130886 | 2015-03-03 | Scheduled Outage | Construction | S28561 isolated for SMD replacment. | None | Fused Cutout | 7 | 35 | 4 | East | 77M2
130887 | 2015-03-03 | Scheduled Outage | Construction | S18125 to Eol was isolated to allow cres to replace defective SMD switches. Billberry (77M2). | None | None | 3 | 29 | 1 | East | 77M2
130888 | 2015-03-03 | Scheduled Outage | Construction | Transformer TE1439 at 1346 foxwell was isolated to alow crew to replace defective transformer. Startop (6F1) | None | None | 11 | 128 | 23 | East | 6F1
130889 | 2015-03-03 | Scheduled Outage | Vegetation Management | The O/H section in the rear of 160 Fanshaw was isolated to allow the crews remove a tree limb. | None | Unknown \ Other | 24 | 176 | 70 | Central | 504
130890 | 2015-03-03 | Scheduled Outage | Maintenance | ISOLATED AND REPLACED SWITCH AND ARRESTER AT TRANSFORMER X10971 | None | None | 1 | 15 | 0 | West | BECKF2
130892 | 2015-03-03 | Scheduled Outage | Maintenance | Transformer X10971 at 8736 Flewellyn Rd. isolated by crew to replace arrestor | None | None | 1 | 13 | 0 | West | BECKF2
130893 | 2015-03-03 | Scheduled Outage | Maintenance | Transformer X19875 at 8665 Flewellyn Rd. isolated by crew to replace arrestor | None | None | 3 | 20 | 1 | West | BECKF2
130894 | 2015-03-03 | Scheduled Outage | Construction | Transformer X33418 at 1211 Tara Dr isolated by contractor to transfer load (Jordan Foote of K-Line working with Tim Connell) | None | None | 10 | 46 | 8 | Central | UW06
130895 | 2015-03-03 | Scheduled Outage | Construction | Transformer X35104 at 1243 Tara Dr isolated by contractor to transfer plant | None | None | 12 | 30 | 6 | Central | UW06
130896 | 2015-03-03 | Scheduled Outage | Construction | Transformer X29095 at 3056 Southmore Dr E isolated by crew for pole replacement | None | None | 8 | 258 | 34 | East | UZ11
130897 | 2015-03-03 | Scheduled Outage | Vegetation Management | Transformer X28218 at 132 Fanshaw Ave. isolated by crew to remove branch at 160 Fanshaw Ave. | None | None | 7 | 167 | 19 | Central | 505
130898 | 2015-03-03 | Scheduled Outage | Vegetation Management | Transformer X28217 at 140 Fanshaw Ave. isolated by crew to remove tree at 160 Fanshaw Ave. | None | None | 8 | 167 | 22 | Central | 505
130899 | 2015-03-03 | Scheduled Outage | Vegetation Management | Transformer X28215 at 164 Fanshaw Ave. isolated by crew to remove tree at 160 Fanshaw Ave. | None | None | 9 | 167 | 25 | Central | 505
130900 | 2015-03-03 | Scheduled Outage | Construction | Transformer X31347 at 122 third Ave. and transformer X31376 at 126 Third Ave. isolated by crew to replace transformers. New transformer installed under nomenclature X31376. | None | None | 17 | 319 | 90 | Central | SB03
130901 | 2015-03-03 | Scheduled Outage | Construction | Transformer #X33416 isolated by crew to transfer load | None | None | 10 | 150 | 25 | Central | UW06
130902 | 2015-03-03 | Scheduled Outage | Construction | Transformer #X32449 isolated by crew to transfer load | None | None | 11 | 60 | 11 | Central | UW06
130903 | 2015-03-03 | Scheduled Outage | Construction | Transformer #X29070 isolated by crew for a pole change | None | None | 7 | 120 | 14 | East | AJ07
130909 | 2015-03-04 | Adverse Environment | Contamination (Salt) | Inclement weather & salt contaminated insulators caused tracking in multiple pole locations | Pole | Insulation Failure (Pole Fire) | 1770 | 14 | 413 | East | 77M6
130909 | 2015-03-04 | Adverse Environment | Contamination (Salt) | Inclement weather & salt contaminated insulators caused tracking in multiple pole locations | Pole | Insulation Failure (Pole Fire) | 1852 | 37 | 1142 | East | 77M6
130910 | 2015-03-04 | Scheduled Outage | Construction | Transofmer K1060 was isolated to allow crew transfer primary feed from UT03W to UT05 R | None | None | 8 | 255 | 34 | East | UT03
130911 | 2015-03-04 | Scheduled Outage | Construction | Isolate cable section and connect and commission 5 new TPs on the white phase. | None | None | 157 | 241 | 631 | South | FAL03
130912 | 2015-03-04 | Scheduled Outage | Construction | Transformer X35204 at 1101 Agincourt Rd isolated by contractor Jordan Foote of K-Line to transfer plant | None | None | 2 | 30 | 1 | Central | UW06
130913 | 2015-03-04 | Scheduled Outage | Construction | Transformer X33848 at 1118 Maitland Ave isolated by Jordan Foote of K-Line to transfer load | None | None | 8 | 25 | 3 | Central | UW06
130914 | 2015-03-04 | Scheduled Outage | Construction | Transformer X32448 at 1115 Agincourt Rd isolated by Jordan Foote of K-Line to transfer load | None | None | 8 | 20 | 3 | Central | UW06
130915 | 2015-03-04 | Scheduled Outage | Construction | The UW05 O/H from Temp 21 to EOL at Ferguson & Gage was isolated to allow the crew to install new poles | None | Pole | 33 | 254 | 140 | Central | UW05
130916 | 2015-03-04 | Scheduled Outage | Construction | Transformer X32050 at 1280 Erindale Dr., X35129 at 1262 Erindale Dr. and X31595 at 1248 Erindale Dr. isolated by Jordan Foote of K-Line to transfer plant | None | None | 18 | 64 | 19 | Central | UW06
130917 | 2015-03-04 | Scheduled Outage | Construction | Transformer X32816 at 1253 Erindale Dr. isolated by Jordan Foote of K-Line to transfer plant | None | None | 13 | 19 | 4 | Central | UW06
130918 | 2015-03-04 | Scheduled Outage | Construction | Transformer #X33424 isolated by crew to transfer hydro plant | None | None | 6 | 55 | 6 | Central | UW06
130919 | 2015-03-04 | Scheduled Outage | Construction | Transformer #X35134 isolated by crew to transfer plant | None | None | 10 | 40 | 7 | Central | UW06
130920 | 2015-03-04 | Scheduled Outage | Maintenance | Transformer #X36891 isolated by crew to change connections on buss and tighten connections on transfromer | None | None | 3 | 40 | 2 | South | EPWF1
130921 | 2015-03-04 | Defective Equipment | Defective Equipment/ Material | defective transformer | U/G Transformer | Padmount (3ph) | 1 | 2864 | 48 | East | TB14
130922 | 2015-03-04 | Unknown/Other | Unknown | To allow Hydro Ottawa crews to replace a blown fuse on the 347/600 V secondary fed out of VT856 | Unknown \ Other | Unknown \ Other | 71 | 2 | 2 | Central | 413
130924 | 2015-03-05 | Scheduled Outage | Construction | At 10:05am crews isolated S13662 to replace SMD swtiches. 2 customers affected for 20 mins. Uplands (4801F8) ID#130924 | None | None | 2 | 22 | 1 | East | 4801F8
130925 | 2015-03-05 | Scheduled Outage | Construction | At 10:52am crews isolated S20734 to replace SMD swtiches. 1 customer affected for 23 mins. Uplands (4801F8) ID# 130925 | None | None | 1 | 23 | 0 | East | 4801F8
130926 | 2015-03-05 | Scheduled Outage | Vegetation Management | At 8:53am crews isolated S25457 to allow removal of trees. 79 customers affected for 123 mins. Bronson (SB09) ID#130926 | None | None | 79 | 123 | 162 | Central | SB09
130927 | 2015-03-05 | Scheduled Outage | Maintenance | isolated transformer x24220 to replace connections on the secondary | None | None | 11 | 10 | 2 | East | BLKF3
130928 | 2015-03-06 | Scheduled Outage | Vegetation Management | At 8:32am crews isolated a blue phase section of UV05 on Firestone to allow for tree removal. 10 customers affected for 185 mins. Edwin (UV05) ID#130928 | None | None | 10 | 185 | 31 | Central | UV05
130929 | 2015-03-06 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X34132 TO REPLACE SWITCH | None | None | 6 | 74 | 7 | Central | TH01
130930 | 2015-03-06 | Scheduled Outage | Construction | At 4:21pm crews isolated TP3901 at 2129 Arch for a FIT installation. 1 customer affected. Urbandale (AE02) ID# 130930 | None | None | 1 | 119 | 2 | East | AE02
130931 | 2015-03-06 | Defective Equipment | Electrical Failure | A defective W phase cable bet bet K550 and K552 on AJ06. | U/G Cable | XLPE | 17 | 62 | 18 | East | AJ06
130931 | 2015-03-06 | Defective Equipment | Electrical Failure | A defective W phase cable bet bet K550 and K552 on AJ06. | U/G Cable | XLPE | 25 | 31 | 13 | East | AJ06
130931 | 2015-03-06 | Defective Equipment | Electrical Failure | A defective W phase cable bet bet K550 and K552 on AJ06. | U/G Cable | XLPE | 35 | 153 | 89 | East | AJ06
130932 | 2015-03-07 | Defective Equipment | Electrical Failure | A second cable fault on the AJ06 W phase cable at K552 at 1955 FAIRMEADOW CRES | U/G Cable | XLPE | 10 | 438 | 73 | East | AJ06
130932 | 2015-03-07 | Defective Equipment | Electrical Failure | A second cable fault on the AJ06 W phase cable at K552 at 1955 FAIRMEADOW CRES | U/G Cable | XLPE | 27 | 69 | 31 | East | AJ06
130934 | 2015-03-07 | Scheduled Outage | Construction | K1161 isolated to allow crew to replace damaged pole. | None | Pole | 18 | 49 | 15 | Central | AD04
130935 | 2015-03-07 | Scheduled Outage | Forced Switching | To allow Hydro Ottawa line crews to safely operate switches. Customers downstream of RX2048 were affected for 22 minutes. | None | None | 4 | 22 | 1 | West | BECKF2
130936 | 2015-03-07 | Defective Equipment | Defective Equipment/ Material | The SE8 R phase feeding transfomer TE573 opened due to defective U/G cable. Parkwoodhills (190F5) | U/G Cable | XLPE | 42 | 722 | 505 | South | 190F5
130938 | 2015-03-09 | Scheduled Outage | Vegetation Management | SB05 from S19748 to EOL isolated for tree removal. | None | O/H Conductor | 33 | 289 | 159 | Central | SB05
130939 | 2015-03-09 | Scheduled Outage | Construction | Transformer #4975 isolated by crew to upgrade Hydro plant | None | None | 6 | 40 | 4 | East | 7F4
130940 | 2015-03-09 | Defective Equipment | Defective Equipment/ Material | Transformer #X23519 opened up due to broken cutout | O/H Switchgear | Fused Cutout | 6 | 145 | 14 | East | SO02
130941 | 2015-03-09 | Scheduled Outage | Maintenance | Transformer #X23517 isolated by crew to replace broken cutout for 707 Alesther | None | None | 6 | 30 | 3 | East | SO02
130942 | 2015-03-09 | Scheduled Outage | Construction | Transformer X43418 at 4305 Trail Rd. isolated by crew to install collector meter on pole | None | None | 1 | 20 | 0 | South | FAL01
130944 | 2015-03-09 | Scheduled Outage | Construction | Transformer X34780 at 4799 Fallowfield Rd. isolated by crew to install collector meter on pole | None | None | 1 | 102 | 2 | South | 145F3
130945 | 2015-03-09 | Scheduled Outage | Construction | Transformer X39963 at 4077 Twin Elm Rd. isolated by crew to install collector meter on pole | None | None | 1 | 15 | 0 | South | 145F3
130946 | 2015-03-09 | Scheduled Outage | Construction | Transformer X47191 at 3024 Welland St. isolated by crew for pole transfer | None | None | 12 | 340 | 68 | East | UZ11
130947 | 2015-03-09 | Scheduled Outage | Construction | ISOLATED SECONDARY 600V SERVICE IN VT852 TO REPLACE CONDUCTOR BETWEEN TWO MAN HOLES DUE TO FAULT | None | None | 75 | 250 | 312 | Central | 413
130948 | 2015-03-10 | Scheduled Outage | Vegetation Management | Remove Large trees at 2190 Woodcrest for storm hardening | None | None | 5 | 488 | 41 | East | TB2JP
130949 | 2015-03-10 | Scheduled Outage | Maintenance | Change Arresters at Transformer | None | None | 6 | 83 | 8 | Central | TR1UN
130950 | 2015-03-11 | Scheduled Outage | Construction | Pole change and plant re-build | None | None | 2 | 122 | 4 | Central | UW05
130951 | 2015-03-11 | Scheduled Outage | Vegetation Management | Vegetation management | None | None | 18 | 165 | 50 | East | UQ07
130952 | 2015-03-11 | Scheduled Outage | Construction | Transformer X23624 was isolated to allow crew to upgrade a service. Beechwood (UB04) ID# 130952. | None | None | 12 | 58 | 12 | East | UB04
130954 | 2015-03-11 | Scheduled Outage | Construction | Transformer X23270 was isolated to allow crew to upgrade a service. Vaughan (UG09) ID# 130954. | None | None | 4 | 60 | 4 | East | UG09
130955 | 2015-03-11 | Scheduled Outage | Construction | Transformers TP10157, TP10150 and TP9855 isolated to allow for re-configuration of white phase cables, Terry Fox TFXF4, ID # 130955 | None | None | 20 | 289 | 96 | West | TFXF4
130956 | 2015-03-11 | Scheduled Outage | Maintenance | Transformers TE792, TE791, TE790, TE789, TE788 and TE424 isolated to repair defective elbows at TE788 and TE789, Merivale 72F2, ID # 130956 | None | Elbow \ Insert | 76 | 169 | 214 | South | 72F2
130957 | 2015-03-11 | Scheduled Outage | Maintenance | K396 isolated to allow crew to disconnect defective secondary cable. | None | None | 24 | 35 | 14 | East | UA02
130958 | 2015-03-12 | Defective Equipment | Defective Equipment/ Material | S16331 R phase opened due to defective cable between TP7082 and TE847 | U/G Cable | XLPE | 22 | 35 | 13 | East | 77M1
130958 | 2015-03-12 | Defective Equipment | Defective Equipment/ Material | S16331 R phase opened due to defective cable between TP7082 and TE847 | U/G Cable | XLPE | 33 | 137 | 75 | East | 77M1
130960 | 2015-03-12 | Scheduled Outage | Maintenance | Transformer TE2547 at 72 Stucliffe was isolated to allow crew to repiar secondary transformer connection | None | None | 16 | 104 | 28 | South | LGFF1
130961 | 2015-03-12 | Defective Equipment | Defective Equipment/ Material | S3-3 b opened due to defective cable section between TP6154B and 2543B on Varley Lane | U/G Cable | XLPE | 1 | 5 | 0 | West | 39F2
130961 | 2015-03-12 | Defective Equipment | Defective Equipment/ Material | S3-3 b opened due to defective cable section between TP6154B and 2543B on Varley Lane | U/G Cable | XLPE | 2 | 62 | 2 | West | 39F2
130961 | 2015-03-12 | Defective Equipment | Defective Equipment/ Material | S3-3 b opened due to defective cable section between TP6154B and 2543B on Varley Lane | U/G Cable | XLPE | 3 | 118 | 6 | West | 39F2
130964 | 2015-03-12 | Scheduled Outage | Maintenance | Transformer X08542 at 2043 Ashton Station Rd. isolated by crew to chnge cutout, arrestor and insulator | None | None | 3 | 60 | 3 | West | BECKF2
130965 | 2015-03-12 | Scheduled Outage | Vegetation Management | The AF02 O/H from S12386 to EOL at 2095 Chalmers was isolated by the crew to allow the forestery to remove a large tree. | None | None | 4 | 455 | 30 | East | AF02
130966 | 2015-03-12 | Scheduled Outage | Construction | Transformer TP9926 at 259 Shinny Ave. isolated by crew to rearange primary | None | None | 8 | 141 | 19 | West | TFXF4
130967 | 2015-03-13 | Scheduled Outage | Construction | Transformer X29088 at 911 Stanstead Rd isolated for pole change | None | None | 10 | 149 | 25 | East | UZ11
130968 | 2015-03-13 | Scheduled Outage | Construction | Transformer X29093 at 912 Stanstead Rd isolated for pole change | None | None | 8 | 149 | 20 | East | UZ11
130969 | 2015-03-13 | Scheduled Outage | Construction | Transformer X25499 at 1140 Wellington St. isolated by crew to move primary | None | None | 10 | 120 | 20 | Central | UJ05
130970 | 2015-03-13 | Scheduled Outage | Vegetation Management | The UQ07 O/H from temp 48 to EOL at 1928 Highridge was isolated to remove a tree | None | None | 37 | 395 | 244 | East | UQ07
130976 | 2015-03-15 | Adverse Environment | Contamination (Salt) | To repair pole damaged by fire | Pole | Insulation Failure (Pole Fire) | 146 | 125 | 304 | Central | 303
130977 | 2015-03-15 | Loss Of Supply | Transmission Inadvertent | A9M3 circuit auto-reclosed when crews were opening switch S12919 to allow Hydro One crews to restore all of their affected customers from pole fire on Huntmar. Janet King 8kv, and Munster Stations were also affected. South March (A9M3) ID# 130977. | None | None | 1272 | 53 | 1124 | West | A9M3
130978 | 2015-03-15 | Adverse Environment | Contamination (Salt) | TW2UC line tripped due to pole fire at 2168 Queensgrove. Clyde T3 transformer affected. Woodroffe (TW2UC) ID# 130978. | Pole | Insulation Failure (Pole Fire) | 1095 | 63 | 1150 | Central | TW2UC
130979 | 2015-03-15 | Adverse Environment | Contamination (Salt) | TW22 white phase from S20908 to end of line was isolated to allow crew to extinguish and repair pole due to pole fire at 2168 Queensgrove. Woodroffe (TW22) ID# 130979. | Pole | Insulation Failure (Pole Fire) | 26 | 284 | 123 | Central | TW22
130980 | 2015-03-15 | Scheduled Outage | Construction | To Sleeve out G357 and relocate BLKF1 to allow future stringing of new 77M5 section. | None | O/H Conductor | 1 | 326 | 5 | East | BLKF1
130982 | 2015-03-16 | Scheduled Outage | Vegetation Management | To remove branches burning in primary. | None | None | 20 | 417 | 139 | East | UZ12
130983 | 2015-03-16 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X10992 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 45 | 1 | West | BECKF2
130984 | 2015-03-16 | Scheduled Outage | Vegetation Management | At 11:04am crews opened S28427 for tree trimming. 19 customers affected for 123 mins. Riverdale(505) ID# 130984 | None | None | 19 | 123 | 39 | Central | 505
130985 | 2015-03-16 | Scheduled Outage | Vegetation Management | At 9:05am crews opened Temp49 at 1371 Kilborn to allow crews to trim trees, 12 customers affected for 285 mins. Riverdale (505) ID# 130985 | None | None | 12 | 285 | 57 | Central | 505
130987 | 2015-03-17 | Defective Equipment | Defective Equipment/ Material | Defective termination. | U/G Cable Attachement | Termination \ Stress Cone | 19 | 50 | 16 | East | 4801F8
130988 | 2015-03-17 | Scheduled Outage | Vegetation Management | Tree removal | None | None | 103 | 468 | 803 | East | TB06
130989 | 2015-03-17 | Adverse Environment | Contamination (Salt) | pole fire | Pole | Insulation Failure (Pole Fire) | 1249 | 156 | 3247 | South | 200F1
130992 | 2015-03-17 | Adverse Environment | Contamination (Salt) | Not yet known. | Pole Attachement | Insulator | 3989 | 48 | 3191 | South | 22M27
130992 | 2015-03-17 | Adverse Environment | Contamination (Salt) | Not yet known. | Pole Attachement | Insulator | 8522 | 19 | 2699 | South | 22M27
130994 | 2015-03-17 | Defective Equipment | Defective Equipment/ Material | damaged Primary due to defective lead | O/H Conductor | Hot-Line Clamp | 6 | 45 | 4 | East | BLKF5
130995 | 2015-03-17 | Scheduled Outage | Maintenance | Transformer X39194 at 162 Ruskin St. isolated so crew could replace customer triplex. At the same time they replaced an old switch and arrester | None | None | 14 | 47 | 11 | Central | SM10
130996 | 2015-03-17 | Defective Equipment | Mechanical Failure | Defective switch S269 was replaced. | O/H Switchgear | Fused Cutout | 25 | 184 | 77 | South | 190F5
130997 | 2015-03-17 | Scheduled Outage | Vegetation Management | Transformer X29150 at 220 McArthur Ave. isolated by 24/7 to have a forestry crew remove a tree from the primary | None | None | 20 | 197 | 66 | East | UT04
130998 | 2015-03-17 | Defective Equipment | Defective Equipment/ Material | 24/7 repaired primary and neutral and refused transformer X19767 at 5585 Ridge Rd. | O/H Transformer | O/H Transformer (1ph) | 1 | 357 | 6 | East | BLKF5
130999 | 2015-03-17 | Tree Contacts | Other Vegetation | Transformer X35973 at 992 Merivale Rd isolated to remove vine and refuse transformer. | O/H Transformer | O/H Transformer (1ph) | 4 | 329 | 22 | Central | AD05
131000 | 2015-03-18 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 5 | 142 | 12 | East | AF04
131001 | 2015-03-18 | Scheduled Outage | Construction | Transfer plant to new pole. | None | None | 17 | 140 | 40 | Central | TH11-NIU
131002 | 2015-03-18 | Scheduled Outage | Construction | planned outage to allow crew to cut in 3 new transformers. | None | None | 1 | 103 | 2 | West | 28F2
131003 | 2015-03-18 | Scheduled Outage | Construction | replace rusty xfmr | None | None | 12 | 165 | 33 | South | 200F5
131004 | 2015-03-19 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X08540 TO REPLACE SWITCH AND ARRESTER | None | None | 7 | 20 | 2 | West | BECKF2
131005 | 2015-03-19 | Scheduled Outage | Vegetation Management | Tree Trimming for Storm Hardening | None | None | 11 | 244 | 45 | Central | TR09
131007 | 2015-03-19 | Scheduled Outage | Maintenance | Transformer TP10699B isolated to allow for soil remediation from leaking transformer, Beaverbrook 24F1, ID # 131007 | None | Padmount (1ph) | 9 | 554 | 83 | West | 24F1
131008 | 2015-03-19 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X31460 TO REPLACE SWITCH AND ARRESTER | None | None | 12 | 66 | 13 | Central | TH01
131009 | 2015-03-19 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30043 TO INSTALL A NEW SECONDARY SERVICE | None | None | 8 | 25 | 3 | Central | SB09
131010 | 2015-03-19 | Foreign Interference | Wildlife (Bird/Animal) | Fuse G247R blew due to squirrel contact. Moulton (8F1) ID# 131010. | None | None | 48 | 64 | 51 | East | 8F1
131012 | 2015-03-20 | Scheduled Outage | Forced Switching | 43F3 circuit from switch SW644 to end of line was interrupted to allow crew to transfer load to the BeckF2 through Rabbits. Munster (43F3) ID# 131012. | None | None | 278 | 4 | 19 | West | 43F3
131013 | 2015-03-20 | Scheduled Outage | Forced Switching | 43F2 load was interrupted to allow crew to transfer circuit to the BECKF2 through Rabbits. Munster (43F2) ID# 131013. | None | None | 471 | 6 | 47 | West | 43F2
131014 | 2015-03-21 | Loss Of Supply | Transmission Inadvertent | Loss of Supply on the Beckwith BECKF2 due to pole fire on Hydro One circuit. The 43F2 and 43F3 customers affecetd by outage due to load transferred to BECKF2 for planned outage . | None | None | 3 | 81 | 4 | West | BECKF2
131014 | 2015-03-21 | Loss Of Supply | Transmission Inadvertent | Loss of Supply on the Beckwith BECKF2 due to pole fire on Hydro One circuit. The 43F2 and 43F3 customers affecetd by outage due to load transferred to BECKF2 for planned outage . | None | None | 132 | 6 | 13 | West | 43F3
131014 | 2015-03-21 | Loss Of Supply | Transmission Inadvertent | Loss of Supply on the Beckwith BECKF2 due to pole fire on Hydro One circuit. The 43F2 and 43F3 customers affecetd by outage due to load transferred to BECKF2 for planned outage . | None | None | 278 | 187 | 866 | West | 43F3
131014 | 2015-03-21 | Loss Of Supply | Transmission Inadvertent | Loss of Supply on the Beckwith BECKF2 due to pole fire on Hydro One circuit. The 43F2 and 43F3 customers affecetd by outage due to load transferred to BECKF2 for planned outage . | None | None | 471 | 149 | 1170 | West | 43F2
131014 | 2015-03-21 | Loss Of Supply | Transmission Inadvertent | Loss of Supply on the Beckwith BECKF2 due to pole fire on Hydro One circuit. The 43F2 and 43F3 customers affecetd by outage due to load transferred to BECKF2 for planned outage . | None | None | 654 | 49 | 534 | West | BECKF2
131015 | 2015-03-21 | Defective Equipment | Mechanical Failure | Circuit patrolled and found broken insulator, and primary hangining. Also burnt neutral at 819 Champlain. | Pole Attachement | Insulator | 1588 | 24 | 635 | East | 77M6
131016 | 2015-03-21 | Adverse Environment | Contamination (Salt) | S22540 opened to isolate pole fire at 2845 Adhern Ave and downed primary. On call to make repairs to downed primary due to top of pole burning off. | Pole | Pole | 1 | 224 | 4 | Central | TD12
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 3 | 8 | 0 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 33 | 4 | 2 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 121 | 6 | 12 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 127 | 57 | 121 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 206 | 21 | 72 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 380 | 9 | 57 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 380 | 16 | 101 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 380 | 23 | 146 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 380 | 51 | 323 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 441 | 9 | 66 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 441 | 13 | 96 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 441 | 14 | 103 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 441 | 129 | 948 | West | BECKF2
131017 | 2015-03-21 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 677 | 7 | 79 | West | BECKF2
131017 | 2015-03-22 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 1 | 5 | 0 | West | BECKF2
131017 | 2015-03-22 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 2 | 4 | 0 | West | BECKF2
131017 | 2015-03-22 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 127 | 57 | 121 | West | BECKF2
131017 | 2015-03-22 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 130 | 2 | 4 | West | BECKF2
131017 | 2015-03-22 | Human Element | Protection Setting | RX2005 and RX2024 tripped due to suspected overload and coordination issues. Alexander (ALEXF2) | None | None | 405 | 7 | 47 | West | BECKF2
131020 | 2015-03-23 | Scheduled Outage | Vegetation Management | S25457 to Eol was isolated to allow crew to remove tree at rear of 405, 397 and 383 Third Ave. Bronson (SB09) | None | None | 79 | 273 | 359 | Central | SB09
131021 | 2015-03-23 | Scheduled Outage | Maintenance | Transformer #GL409 isolated by crew to replace insulators | None | None | 8 | 60 | 8 | East | 7F4
131022 | 2015-03-23 | Scheduled Outage | Construction | Transformer #X32459 isolated by crew to transfer plant | None | None | 11 | 27 | 5 | Central | UW05
131023 | 2015-03-23 | Scheduled Outage | Maintenance | Transformer X34102 at 127 Carleton Ave. isolated by crew to replace switch | None | None | 6 | 48 | 5 | Central | TH01
131024 | 2015-03-23 | Scheduled Outage | Maintenance | Transformer X36417 at 3 Carlisle Circle isolated by crew to replace switch | None | None | 5 | 11 | 1 | Central | TH01
131025 | 2015-03-23 | Scheduled Outage | Maintenance | Transformer X31463 at 17 Caroline Ave. isolated by crew to replace switch | None | None | 14 | 60 | 14 | Central | TH01
131026 | 2015-03-24 | Scheduled Outage | Vegetation Management | Storm Hardening Project- To allow forestry crews to clear trees from the O/H. | None | None | 54 | 435 | 392 | East | UQ07
131027 | 2015-03-24 | Scheduled Outage | Vegetation Management | Storm Hardening- to allow forestry crews to clear trees from the O/H | None | None | 17 | 197 | 56 | East | TB06
131028 | 2015-03-24 | Scheduled Outage | Maintenance | Transformer #X34104 isolated by crew to replace switch and cutout | None | None | 18 | 35 | 10 | Central | TH01
131029 | 2015-03-24 | Scheduled Outage | Maintenance | Transformer #X34103 isolated by crew to replace cut out and arrestor | None | None | 5 | 62 | 5 | Central | TH01
131030 | 2015-03-24 | Scheduled Outage | Maintenance | Transformer #X36420 isolated by crew to replace primary insulator | None | None | 4 | 50 | 3 | West | BECKF2
131031 | 2015-03-24 | Scheduled Outage | Maintenance | Transformer #X36421 isolated by crew to replace insulator | None | None | 5 | 55 | 5 | West | BECKF2
131032 | 2015-03-24 | Scheduled Outage | Maintenance | Tranformer #X31998 isolated by crew to disc service at the mast and replace triplex | None | None | 13 | 30 | 6 | Central | SH04
131033 | 2015-03-24 | Scheduled Outage | Maintenance | Transformer #X34110 isolated by crew to replace switch | None | None | 8 | 40 | 5 | Central | TH01
131034 | 2015-03-24 | Scheduled Outage | Maintenance | Transformer #X39818 isolated by crew for the Metering Dept | None | None | 1 | 27 | 0 | South | 47F6
131035 | 2015-03-24 | Scheduled Outage | Maintenance | Transformer #X34113 isolated by crew for a switch replacement | None | None | 10 | 20 | 3 | Central | TH01
131037 | 2015-03-24 | Scheduled Outage | Maintenance | Transformer #X34114 isolated by crew to replace cutout and arrestor | None | None | 8 | 51 | 7 | Central | TH01
131038 | 2015-03-24 | Scheduled Outage | Maintenance | Transformer #X34115 isolated by crew for a switch replacement | None | None | 7 | 35 | 4 | Central | TH01
131039 | 2015-03-24 | Scheduled Outage | Maintenance | Transformer #X36422 isolated by crew to replace insulator | None | None | 6 | 55 | 6 | West | BECKF2
131040 | 2015-03-25 | Scheduled Outage | Vegetation Management | Storm Hardening Project- to allow forestry crews to clear trees from the O/H | None | None | 18 | 459 | 138 | East | TB06
131041 | 2015-03-25 | Scheduled Outage | Maintenance | VT330 transformer bus isolated for HOL metering repair. | None | None | 1 | 17 | 0 | East | TO1UB
131042 | 2015-03-25 | Scheduled Outage | Construction | Outtage fron S16704 to EOL to allow contractor (Sproule) to string new conductor | None | None | 2 | 435 | 14 | East | 77M2
131043 | 2015-03-25 | Scheduled Outage | Construction | Transfer Plant to new pole | None | None | 6 | 105 | 10 | Central | UW05
131044 | 2015-03-25 | Adverse Environment | Contamination (Salt) | Humity in vault caused insulators to flash over. | Customer Owned | Customer-Owned | 1 | 938 | 16 | Central | TL3SB
131045 | 2015-03-26 | Foreign Interference | Wildlife (Bird/Animal) | An animal caused the fuse to blow at transformer X32586 at 676 COURTENAY AVE OTTAWA | O/H Transformer | O/H Transformer (1ph) | 10 | 59 | 10 | Central | TD01
131046 | 2015-03-26 | Scheduled Outage | Vegetation Management | tree trimming - planned outage | None | None | 61 | 163 | 166 | South | 190F5
131046 | 2015-03-26 | Scheduled Outage | Vegetation Management | tree trimming - planned outage | None | None | 99 | 5 | 8 | South | 190F5
131047 | 2015-03-26 | Scheduled Outage | Vegetation Management | Storm Hardening | None | None | 24 | 259 | 104 | Central | SB02
131048 | 2015-03-26 | Scheduled Outage | Maintenance | Transformer #GL3647 isolated by crew to replace switch | None | None | 5 | 40 | 3 | East | 7F4
131049 | 2015-03-26 | Scheduled Outage | Maintenance | Transformer #X24103 isolated by crew to replace switch | None | None | 10 | 23 | 4 | East | 7F4
131050 | 2015-03-26 | Defective Equipment | Defective Equipment/ Material | Transformer #K664 opened up due to blown fuse | U/G Transformer | Kiosk (1ph) | 15 | 58 | 14 | East | AE05
131051 | 2015-03-26 | Scheduled Outage | Maintenance | Transformer #GL5611 isolated by crew to replace switch | None | None | 8 | 45 | 6 | East | 7F4
131053 | 2015-03-26 | Defective Equipment | Defective Equipment/ Material | Defective customer secondary cable out of transformer K664 | U/G Cable | Customer-Owned | 15 | 5467 | 1367 | East | AE05
131054 | 2015-03-27 | Scheduled Outage | Maintenance | Transformer #X36418 isolated by crew to replace switch | None | None | 4 | 38 | 3 | West | BECKF2
131055 | 2015-03-27 | Scheduled Outage | Maintenance | Transformer #X33746 isolated by crew to replace switch | None | None | 9 | 62 | 9 | Central | TH01
131056 | 2015-03-27 | Scheduled Outage | Maintenance | Transformer #X33691 isolated by crew to replace switch | None | None | 4 | 50 | 3 | Central | TH01
131057 | 2015-03-27 | Scheduled Outage | Vegetation Management | Storm Hardening in rear of 525 westminster, and 545 Windermere. | None | None | 42 | 202 | 141 | Central | TD01
131058 | 2015-03-27 | Scheduled Outage | Maintenance | Transformer #X33734 isolated by crew to replace switch | None | None | 7 | 50 | 6 | Central | TH01
131059 | 2015-03-27 | Scheduled Outage | Maintenance | Transformer #X30498 isolated by crew to replace switch | None | None | 11 | 45 | 8 | Central | TH01
131060 | 2015-03-27 | Scheduled Outage | Maintenance | Transformer #X34051 isolated by crew to replace switch | None | None | 10 | 40 | 7 | Central | TH01
131061 | 2015-03-27 | Scheduled Outage | Maintenance | Transformer #X34134 isolated by crew to replace switch | None | None | 7 | 65 | 8 | Central | TH01
131062 | 2015-03-27 | Scheduled Outage | Vegetation Management | Storm Hardening in the rear of 617 Wavell. | None | None | 18 | 240 | 72 | Central | TD01
131064 | 2015-03-28 | Defective Equipment | Mechanical Failure | SC1002-F B phase opened due to defective primary disconnect at KT373. | U/G Switchgear | Live-Front | 22 | 307 | 113 | East | 2206
131064 | 2015-03-28 | Defective Equipment | Mechanical Failure | SC1002-F B phase opened due to defective primary disconnect at KT373. | U/G Switchgear | Live-Front | 62 | 23 | 24 | East | 2206
131064 | 2015-03-28 | Defective Equipment | Mechanical Failure | SC1002-F B phase opened due to defective primary disconnect at KT373. | U/G Switchgear | Live-Front | 82 | 62 | 85 | East | 2206
131064 | 2015-03-28 | Defective Equipment | Mechanical Failure | SC1002-F B phase opened due to defective primary disconnect at KT373. | U/G Switchgear | Live-Front | 141 | 104 | 244 | East | 2206
131065 | 2015-03-28 | Foreign Interference | Customer-Cut Trees | X33386 & X33223 isolated to repair broken secondary bus behind 17 Greenwich | O/H Switchgear | Fused Cutout | 6 | 175 | 18 | South | 190F2
131065 | 2015-03-28 | Foreign Interference | Customer-Cut Trees | X33386 & X33223 isolated to repair broken secondary bus behind 17 Greenwich | O/H Switchgear | Fused Cutout | 14 | 40 | 9 | South | 190F2
131067 | 2015-03-30 | Defective Equipment | Defective Equipment/ Material | Crews located a broken lead feeding overhead transformer X26881, made repairs and restored power to customers on the TB15 out of Russell Terminal. 10 Customers affected. | O/H Conductor | Hot-Line Clamp | 10 | 174 | 29 | East | TB15
131068 | 2015-03-30 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X25656 TO REPLACE POLE | None | None | 16 | 85 | 23 | Central | TH11-NIU
131069 | 2015-03-30 | Scheduled Outage | Construction | To perform transfer of overhead plant | None | None | 20 | 278 | 93 | Central | UW05
131070 | 2015-03-30 | Scheduled Outage | Forced Switching | Transformer #X31044 isolated by crew for Ottawa Fire due to gas leak | None | None | 17 | 40 | 11 | Central | UF08
131071 | 2015-03-30 | Scheduled Outage | Construction | Transformer TE599 was isolated to allow crew to install new cables. Blackburn (BLKF1) ID# 131071. | None | None | 11 | 228 | 42 | East | BLKF1
131073 | 2015-03-31 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X34125 TO REPLACE SWITCH AND ARRESTER | None | None | 4 | 31 | 2 | Central | TH01
131074 | 2015-03-31 | Scheduled Outage | Maintenance | Transformer X31498 at 67 Ross Ave. isolated by crew to change cutout and arrestor | None | None | 9 | 63 | 9 | Central | TH01
131075 | 2015-03-31 | Scheduled Outage | Maintenance | Transformer X34122 at 236 Cowley Ave isolated by crew to change cutout and arrestor | None | None | 5 | 95 | 8 | Central | TH01
131076 | 2015-03-31 | Scheduled Outage | Maintenance | Transformer X34123 at 264 Cowley Ave isolated by crew to change cutout and arrestor | None | None | 10 | 55 | 9 | Central | TH01
131077 | 2015-03-31 | Scheduled Outage | Maintenance | Transformer X26228 at 240 Cowley Ave isolated by crew to change cutout and arrestor | None | None | 10 | 57 | 10 | Central | TH01
131078 | 2015-03-31 | Scheduled Outage | Maintenance | Transformer X33688 at 280 Spencer St. isolated by crew to change cutout and arrestor | None | None | 10 | 41 | 7 | Central | TH01
131079 | 2015-03-31 | Scheduled Outage | Construction | Transformer X35066 at 1917 Baseline Rd. isolated by contractor to transfer plant | None | None | 1 | 120 | 2 | Central | UW05
131080 | 2015-03-31 | Scheduled Outage | Construction | Transformer #X48624 isolated by crew to transfer plant | None | None | 5 | 263 | 22 | Central | UW01
131082 | 2015-04-01 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X11903 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 30 | 0 | West | RHNF3
131083 | 2015-04-01 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X34144 TO REPLACE SWITCH AND ARRESTER | None | None | 6 | 45 | 4 | Central | TH01
131084 | 2015-04-01 | Scheduled Outage | Construction | To transfer UW06 customers on the white phase, and make new connections to new O/H line. | None | O/H Conductor | 17 | 260 | 74 | Central | UW06
131084 | 2015-04-01 | Scheduled Outage | Construction | To transfer UW06 customers on the white phase, and make new connections to new O/H line. | None | O/H Conductor | 20 | 93 | 31 | Central | UW06
131085 | 2015-04-01 | Scheduled Outage | Construction | Transformer X10801 at 7825 Fallowfield Rd. isolated by crew to replace primary insulator and switches | None | None | 2 | 43 | 1 | West | BECKF2
131086 | 2015-04-01 | Defective Equipment | Electrical Failure | cable fault between K629 & K628 | U/G Cable | Unknown \ Other | 12 | 48 | 10 | East | AP05
131086 | 2015-04-01 | Defective Equipment | Electrical Failure | cable fault between K629 & K628 | U/G Cable | Unknown \ Other | 35 | 179 | 104 | East | AP05
131087 | 2015-04-01 | Scheduled Outage | Construction | Transformer X12565 at 3464 Joys Rd. isolated by crew to replace switch and arrester | None | None | 2 | 51 | 2 | West | 28F1
131088 | 2015-04-01 | Scheduled Outage | Construction | Transformer X10594 at 118 Fortune St. isolated by crew to replace switch | None | None | 8 | 55 | 7 | West | 28F2
131089 | 2015-04-01 | Scheduled Outage | Construction | Transformer X34128 at 240 Keyworth Ave. isolated by crew to replace switch | None | None | 9 | 60 | 9 | Central | TH01
131090 | 2015-04-01 | Defective Equipment | Corrosion | Transformer TP3026 at 2550 Queensview Dr. isolated by 24/7 crew to renew corroded connections at transformer | U/G Transformer | Padmount (3ph) | 1 | 45 | 1 | Central | 5408
131091 | 2015-04-01 | Foreign Interference | Wildlife (Bird/Animal) | A bird dropped a branch cross the phases of AA04 O/H conductor. Also S15570 white phase fuse found blown at 618 Burn st. | O/H Conductor | O/H Conductor | 80 | 24 | 32 | East | AA04
131091 | 2015-04-01 | Foreign Interference | Wildlife (Bird/Animal) | A bird dropped a branch cross the phases of AA04 O/H conductor. Also S15570 white phase fuse found blown at 618 Burn st. | O/H Conductor | O/H Conductor | 610 | 46 | 468 | East | AA04
131092 | 2015-04-02 | Scheduled Outage | Vegetation Management | Storm hardening project- to allow forestry contractors to clear trees from the O/H lines | None | None | 115 | 396 | 759 | East | UB07
131093 | 2015-04-02 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to rebuild cable risers, replace elbows & inserts and change transformer nomenclature. | None | None | 66 | 236 | 260 | West | ALEXF3
131094 | 2015-02-04 | Foreign Interference | Wildlife (Bird/Animal) | Customer call in MBNA on generator and Telesat part power.G854 blue phase blown, SC4813-L2 closed to restore full power to Telesat (part power 82 minutes) MBNA to remain on generator. On restore Telesat again part power (4 minutes) due to G854W phase fuse | O/H Conductor | O/H Conductor | 0 | 82080 | 0 | East | 8F3
131095 | 2015-04-02 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change the cutout & arrestor at transformer X26658 | None | Fused Cutout | 6 | 57 | 6 | Central | TH01
131100 | 2015-04-03 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X37099 | O/H Transformer | O/H Transformer (1ph) | 7 | 52 | 6 | South | 180F4
131103 | 2015-04-04 | Defective Equipment | Defective Equipment/ Material | Secondary fire. | Customer Owned | Customer-Owned | 11 | 60 | 11 | East | 5303
131104 | 2015-04-04 | Defective Equipment | Defective Equipment/ Material | Pole fire at X32057 | Pole | Unknown \ Other | 1 | 59 | 1 | Central | UC06
131106 | 2015-04-05 | Defective Equipment | Defective Equipment/ Material | Transformer #x34047 opened up due to broken glass switch | O/H Switchgear | Inline Switch | 6 | 96 | 10 | Central | TW22
131107 | 2015-04-05 | Scheduled Outage | Construction | Overhead pail X24610 isolated to allow crew to make repairs to secondary triplex. | None | None | 19 | 26 | 8 | East | 8F1
131109 | 2015-04-07 | Scheduled Outage | Vegetation Management | S22257 RB phases to EOL were isolated to allow crew to perform tree trimming. Walkley UZ03. ID# 131109 | None | None | 43 | 450 | 322 | East | UZ03
131110 | 2015-04-07 | Scheduled Outage | Construction | To allow Sproule Power Line crews to have working clearance to string in new conductor. | None | None | 80 | 97 | 129 | East | CYRF3
131112 | 2015-04-07 | Scheduled Outage | Construction | Transformer X34139 at 237 Island Park Dr isolated by crew to replace switch and arrestor | None | None | 10 | 53 | 9 | Central | TH01
131113 | 2015-04-07 | Scheduled Outage | Construction | Transformer X34136 at 180 Patricia Ave isolated by crew to replace switch and arrestor | None | None | 11 | 36 | 7 | Central | TH01
131115 | 2015-04-07 | Scheduled Outage | Construction | Transformer X34109 at 249 Northwestern Ave isolated by crew to replace switch and arrestor | None | None | 1 | 40 | 1 | Central | TH01
131116 | 2015-04-08 | Scheduled Outage | Construction | UW06 O/H section between Temp 94, Temp 23, and Temp 31 was isoalted to allow crew to install new pole and reconfigure the O/H. | None | None | 26 | 390 | 169 | Central | UW06
131118 | 2015-04-08 | Scheduled Outage | Maintenance | The vault VE18N @ 77 Inverness was isolated to allow the metering dept repair the meter | None | None | 1 | 15 | 0 | South | 190F5
131119 | 2015-04-08 | Defective Equipment | Defective Equipment/ Material | Transformer X24772 at 5 Davidson Dr isolated by crew to change a porcelain insulator | Pole Attachement | Insulator | 10 | 45 | 8 | East | 8F1
131122 | 2015-04-08 | Scheduled Outage | Maintenance | Transformer TP8088 @ 1584 Sunview was isolated to allow the crews to replace a leaking transformers | None | None | 7 | 135 | 16 | East | 77M6
131123 | 2015-04-09 | Foreign Interference | Vehicle | Pole taken down by car. | Pole | Pole | 2 | 115 | 4 | South | 140F4
131125 | 2015-04-09 | Defective Equipment | Defective Equipment/ Material | Transformer X37150 at 250 Thorold Rd isolated by crew to change transformer - Ref IRScan issue P0004495 | O/H Transformer | O/H Transformer (1ph) | 3 | 100 | 5 | East | UG05
131126 | 2015-04-09 | Defective Equipment | Electrical Failure | At 10:01am crews isolated TE49 at 17 Britton to allow crew to repair secondary connections. 10 customers affected for 107 mins. QCH (160F1) ID#131126 | Secondary \ Service | U/G Service | 10 | 107 | 18 | South | 160F1
131127 | 2015-04-09 | Scheduled Outage | Construction | Uw05 Blue phase opened from Temp 21 to end of line. | None | Unknown \ Other | 33 | 255 | 140 | Central | UW05
131128 | 2015-04-09 | Scheduled Outage | Construction | Transformer X19335 at 2302 Mer Bleue Rd. isolated by contractor to transfer u/g feed to new pole | None | None | 1 | 50 | 1 | East | CYRF3
131129 | 2015-04-09 | Scheduled Outage | Construction | Transformer X31380 isolated by crew to rearrange secondary | None | None | 9 | 90 | 14 | Central | SB03
131130 | 2015-04-09 | Unknown/Other | Unknown | Not yet known. | None | None | 1 | 85 | 1 | West | ALEXF2
131132 | 2015-04-09 | Defective Equipment | Mechanical Failure | No obvisous reason lots of trees in the area. | O/H Switchgear | Fused Cutout | 9 | 134 | 20 | Central | TD05
131134 | 2015-04-10 | Adverse Environment | Fire | For fire department to get close to overhead to fight a fire. | None | None | 724 | 323 | 3898 | Central | SB05
131135 | 2015-04-10 | Adverse Weather | Wind | Primary overhead was down in the rear of 236 Marilyn | O/H Conductor | Unknown \ Other | 28 | 398 | 186 | East | UZ12
131136 | 2015-04-10 | Defective Equipment | Mechanical Failure | Defective cut-out at dip to K528 | O/H Switchgear | Fused Cutout | 29 | 189 | 91 | Central | TD12
131137 | 2015-04-10 | Unknown/Other | Unknown | At 9:00am SCADA indicates TH05 breaker tripped. Crews sectionalize but did not find the cause. 117 customers affected for 67mins. Hinchey (TH05) ID#131137 | None | None | 117 | 67 | 131 | Central | TH3SH
131138 | 2015-04-10 | Foreign Interference | Vehicle | Phase down of 3 phase overhead in the front of 349 Winston. | Pole Attachement | Unknown \ Other | 67 | 193 | 216 | Central | AH05
131138 | 2015-04-10 | Foreign Interference | Vehicle | Phase down of 3 phase overhead in the front of 349 Winston. | Pole Attachement | Unknown \ Other | 242 | 69 | 278 | Central | AH05
131139 | 2015-04-10 | Adverse Weather | Extreme Wind | At 1:59pm SCADA indicates Beckwith Red phase amps went to 0. Crews were dispatched and found FC2250 flagged and proceeded to open Rx2024 red phase then close the Beckwith F2 recloser. Crew patrolled BeckF2 red phase from RX2024 to end of line but did not | None | None | 131 | 54 | 118 | West | BECKF2
131139 | 2015-04-10 | Adverse Weather | Extreme Wind | At 1:59pm SCADA indicates Beckwith Red phase amps went to 0. Crews were dispatched and found FC2250 flagged and proceeded to open Rx2024 red phase then close the Beckwith F2 recloser. Crew patrolled BeckF2 red phase from RX2024 to end of line but did not | None | None | 232 | 75 | 290 | West | BECKF2
131140 | 2015-04-10 | Loss Of Supply | Transmission Inadvertent | A loss of H1 supply on the W phase | None | None | 225 | 105 | 394 | West | BECKF2
131141 | 2015-04-10 | Human Element | Protection Setting | The RX2005 R phase trip while in parrellel causing an outage when S16277 RB was open. An rush current caused the trip. | None | None | 232 | 23 | 89 | West | BECKF2
131143 | 2015-04-10 | Defective Equipment | Mechanical Failure | V862 at 459 Lisgar was isolated to allow crew to replace defective fuse cut out. Nepean (AB05). ID# 131143 | O/H Switchgear | Fused Cutout | 1 | 46 | 1 | Central | AB05
131146 | 2015-04-12 | Unknown/Other | Unknown | Unknown, circuit to be patrolled in daylight. | None | None | 1795 | 34 | 1017 | West | MWDF2
131150 | 2015-04-12 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace secondary conductor & change a pole. Hydro Ottawa crews isolated transformers X12619 & X12648 | None | None | 7 | 445 | 52 | West | 28F3
131151 | 2015-04-12 | Tree Contacts | Broken Branch | TREE BRANCH ON SECONDARY SERVICE CAUSED FUSE TO BLOW FEEDING TRANSFORMER X14734 | O/H Transformer | O/H Transformer (1ph) | 5 | 138 | 12 | East | LTM04
131152 | 2015-04-12 | Scheduled Outage | Forced Switching | To provide working clearance for the Ottawa Fire Dept. | None | None | 520 | 97 | 841 | Central | SB07
131155 | 2015-04-13 | Defective Equipment | Defective Equipment/ Material | R1-F at VT775 tripped open due to defective customer disconnect on the secondary equipment | Vault Equipment | Unknown \ Other | 1 | 184 | 3 | East | TO3UT
131156 | 2015-04-13 | Scheduled Outage | Vegetation Management | To allow forestry to clear the O/H lines | None | None | 8 | 300 | 40 | Central | TK2AC
131157 | 2015-04-13 | Loss Of Supply | Third Party | Customer secondary main has faulted | None | None | 3 | 630 | 32 | Central | 5208
131158 | 2015-04-13 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X24893 TO REMOVE BROKEN TREE FORM SECONDARY SERVICE | None | None | 6 | 115 | 12 | East | UG04
131159 | 2015-04-13 | Scheduled Outage | Construction | Insulator replacment from S28075 to EOL at Canadian Golf Course, Golf Links Dr. | None | None | 110 | 168 | 308 | West | BECKF2
131160 | 2015-04-13 | Tree Contacts | Broken Branch | Not yet known. | O/H Conductor | O/H Conductor | 77 | 154 | 198 | Central | TW22
131160 | 2015-04-13 | Tree Contacts | Broken Branch | Not yet known. | O/H Conductor | O/H Conductor | 156 | 124 | 322 | Central | TW22
131161 | 2015-04-13 | Defective Equipment | Defective Equipment/ Material | Transformer X3790 at 186 Lebreton St. N isolated by crew to replace customer connnections | Secondary \ Service | O/H Service | 1 | 32 | 1 | Central | UJ06
131162 | 2015-04-13 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 1 | 4 | 0 | East | 2206
131162 | 2015-04-13 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 1 | 149 | 2 | East | 48M2
131162 | 2015-04-13 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 2 | 568 | 19 | East | 2206
131162 | 2015-04-13 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 67 | 62 | 69 | East | ELW13
131162 | 2015-04-13 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 71 | 24 | 28 | East | ELW13
131162 | 2015-04-13 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 82 | 63 | 86 | East | ELW13
131162 | 2015-04-13 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 1570 | 82 | 2146 | East | 48M2
131162 | 2015-04-13 | Defective Equipment | Electrical Failure | Pole fire | Pole | Insulation Failure (Pole Fire) | 3478 | 58 | 3362 | East | 2206
131164 | 2015-04-13 | Defective Equipment | Electrical Failure | At 7:29pm City of Ottawa called to report traffic lights without power. Crews found a defective transformer and On-Call changed the defective transformer. Rideau Heights (180F3) ID#131164 | O/H Transformer | O/H Transformer (1ph) | 1 | 413 | 7 | South | 180F3
131165 | 2015-04-14 | Scheduled Outage | Construction | AJ07 from Temp 55 to EOL was isolated to allow crew to place poles. Playfair (AJ07) ID# 131165. | None | None | 42 | 386 | 270 | East | AJ07
131166 | 2015-04-14 | Scheduled Outage | Vegetation Management | TB15 section from S12168 W to EOL was isolated to allow crew to remove tree. Russell (TB15) ID# 131166. | None | None | 31 | 145 | 75 | East | TB15
131167 | 2015-04-14 | Scheduled Outage | Maintenance | Transformer TE748 on the Manordale 84F3 isolated from Hydro Ottawa Sources at 15 Sundance to perform IR Scan. | None | None | 8 | 82 | 11 | South | 84F3
131168 | 2015-04-14 | Scheduled Outage | Vegetation Management | SB02 white phase overhead section from S11913 to EOL isolated to allow for branch removal, Bronson SB02, ID # 131168 | None | None | 19 | 98 | 31 | Central | SB02
131169 | 2015-04-14 | Scheduled Outage | Maintenance | Overhead GL000320 interrupted by HOL crew to replace defective transformer. 1 Customer affected on the BLKF4 Red Phase | None | None | 1 | 155 | 3 | East | BLKF4
131170 | 2015-04-14 | Scheduled Outage | Construction | UW05 from 1325 Ferguson St to End of Line was isolated to allow crew to rearrange plant. Woodroffe (UW05) ID# 131170. | None | None | 18 | 122 | 37 | Central | UW05
131171 | 2015-04-14 | Scheduled Outage | Vegetation Management | Transformer #X07017 isolated by crew to remove tree from neutral | None | None | 1 | 18 | 0 | West | MWDF3
131172 | 2015-04-14 | Scheduled Outage | Maintenance | Transformer X28209 at 135 Mountbatten Ave. isolated by crew to make repairs to :open wire bus in backlot, neutral wire sag was very low and made contact with the bottom 120V hot leg, brought the sag back up and sleeved | None | O/H Service | 8 | 68 | 9 | East | UQ03
131174 | 2015-04-15 | Scheduled Outage | Construction | To upgrade transformer and transfer riser to a new pole. | None | None | 1 | 249 | 4 | Central | UW05
131175 | 2015-04-15 | Scheduled Outage | Construction | AJ07 between Temp 117 and Temp 55 was isolated to allow crew to replace poles. Playfair (AJ07) ID# 131175. | None | None | 42 | 327 | 229 | East | AJ07
131177 | 2015-04-15 | Scheduled Outage | Maintenance | transformer TP10893 isolated to remove excess sand from the transformer base, Alexander ALEXF2, ID # 131177 | None | None | 7 | 143 | 17 | West | ALEXF3
131178 | 2015-04-15 | Scheduled Outage | Vegetation Management | 115 customers affected for forestry to clear lines from S22505 to End Of Line on the Beechwood UB07 | None | None | 115 | 447 | 857 | East | UB07
131179 | 2015-04-15 | Scheduled Outage | Construction | Transformer #X37972 isolated by crew to remove NIU cable | None | None | 5 | 15 | 1 | Central | SB05
131180 | 2015-04-15 | Scheduled Outage | Construction | Transformer X34143 was isolated to allow crews to replace switches, Hinchey TH01, ID # 131180 | None | None | 1 | 60 | 1 | Central | TH01
131181 | 2015-04-15 | Scheduled Outage | Maintenance | Transformer #3156 isolated by crew for contractor to get sand out of basement | None | None | 13 | 220 | 48 | West | 24F1
131182 | 2015-04-15 | Scheduled Outage | Construction | Transformer 3156 isolated affecting 13 customers on the 24F1 out of Beaverbrook for removal, cleaning and re-configuration. | None | None | 13 | 217 | 47 | West | 24F1
131183 | 2015-04-15 | Scheduled Outage | Maintenance | To attempt locate of secondary underground fault | None | None | 14 | 233 | 54 | East | BCHF5
131184 | 2015-04-15 | Scheduled Outage | Construction | Transformer X48280 at 1313 Ferguson St. isolated by contractor to transfer plant to new pole | None | None | 5 | 180 | 15 | Central | UW01
131185 | 2015-04-16 | Scheduled Outage | Vegetation Management | S23456 to Eol was isolated to allow crew to perform tree trimming. Russell TB14 | None | None | 37 | 198 | 122 | East | TB14
131186 | 2015-04-16 | Scheduled Outage | Maintenance | To located secondary cable fault. | None | None | 14 | 105 | 24 | East | BCHF5
131188 | 2015-04-16 | Scheduled Outage | Construction | Transfer Secondary Services | None | None | 13 | 45 | 10 | Central | AD07
131190 | 2015-04-16 | Scheduled Outage | Construction | ISOLATED 3 PHASE TRANSFORMER BANK X31324 TO TRANSFER HYDRO PLANT | None | None | 5 | 75 | 6 | Central | SB06
131191 | 2015-04-16 | Defective Equipment | Mechanical Failure | PT262 was isolated to allow crew to replace defctive cut out. Lincoln (TD14). ID# 131191 | O/H Switchgear | Fused Cutout | 18 | 25 | 8 | Central | TD14
131192 | 2015-04-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X109899 TO REPLACE SWITCH AND ARRESTER | None | None | 2 | 40 | 1 | West | BECKF2
131193 | 2015-04-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X10907 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 30 | 0 | West | BECKF2
131194 | 2015-04-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X10909 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 40 | 1 | West | BECKF2
131196 | 2015-04-16 | Scheduled Outage | Maintenance | To repair secondary cable fault. | None | None | 14 | 89 | 21 | East | BCHF5
131198 | 2015-04-17 | Scheduled Outage | Vegetation Management | S10303 to EOL was isolated to allow crew to perform tree triming. King Edward (TK2AC). ID# 131198 | None | None | 8 | 223 | 30 | Central | TK2AC
131200 | 2015-04-17 | Loss Of Supply | Transmission Inadvertent | Contractor was moving a machine that puts siding on the house and contacted the 115kv L2M line at 910 Wild Carrot Cres. MOL contacted. | None | None | 13644 | 6 | 1364 | East | L2M (Limebank MS - T1/T2)
131201 | 2015-04-17 | Defective Equipment | Defective Equipment/ Material | TV90 at 135 Beausoleil was isolated to allow crew to replace dammaged elbow. Augusta (UD08). | U/G Cable Attachement | Elbow \ Insert | 47 | 29 | 23 | Central | UD08
131203 | 2015-04-18 | Defective Equipment | Mechanical Failure | Lead fell out of the top of the switch. Changed switch, moved stirrup out further and tightened conductor at transformer X39829 located at . | O/H Switchgear | Fused Cutout | 9 | 101 | 15 | South | 49F6
131204 | 2015-04-18 | Scheduled Outage | Construction | Transformer X37972 located at 273 First Ave. isolated by crew to transfer plant to new pole | None | None | 5 | 217 | 18 | Central | SB05
131205 | 2015-04-18 | Scheduled Outage | Forced Switching | off loading Munster DS for planned work on A9M3, can not parallel at rabbits | None | None | 278 | 10 | 46 | West | 43F3
131206 | 2015-04-18 | Scheduled Outage | Forced Switching | Off loading Munster DS for planned work on A9M3. Can not parallel at rabbits. | None | None | 471 | 3 | 24 | West | 43F2
131208 | 2015-04-18 | Defective Equipment | Mechanical Failure | Transformer X27075 fuse blew due to defective switch lead. Russell (TB14) ID# 131208. | O/H Switchgear | Fused Cutout | 7 | 163 | 19 | East | TB14
131209 | 2015-04-18 | Scheduled Outage | Construction | Extensive overhead work on the 44kV Fernbank and Shea | None | None | 1 | 344 | 6 | West | A9M3
131211 | 2015-04-18 | Scheduled Outage | Construction | Goulbourn Rec Centre Outage required for crews to perform extensive overhead work on the 44kV Fernbank and Shea | None | None | 1 | 339 | 6 | West | A9M3
131212 | 2015-04-19 | Scheduled Outage | Forced Switching | SC3926 was isolated to allow crew to replace defective gas gauge and top up SF6 gas. Albion (2211) ID# 131212. | None | None | 5 | 153 | 13 | East | 2211
131213 | 2015-04-19 | Scheduled Outage | Forced Switching | Switching with out of phase conditon. | None | None | 153 | 8 | 20 | West | 43F3
131213 | 2015-04-19 | Scheduled Outage | Forced Switching | Switching with out of phase conditon. | None | None | 321 | 8 | 43 | West | 43F2
131214 | 2015-04-19 | Scheduled Outage | Forced Switching | Forced outage due to out of phase condtion | None | None | 278 | 2 | 9 | West | 43F3
131217 | 2015-04-19 | Human Element | Incorrect Records/ labelling | unknown at this time. | Vault Equipment | Switch | 1 | 8 | 0 | Central | TM3SH
131218 | 2015-04-19 | Defective Equipment | Defective Equipment/ Material | Transformer X14858 at 1450 Hunt isolated by crew to replace switch and arrestor, done by Matt Stuyt of 24/7 | O/H Switchgear | Fused Cutout | 12 | 27 | 5 | East | AN06
131221 | 2015-04-20 | Scheduled Outage | Vegetation Management | Transformer #X39326 isolated by crew to drop service for Forestry | None | None | 4 | 40 | 3 | Central | TH01
131223 | 2015-04-20 | Defective Equipment | Electrical Failure | Broken insulator and burtn conductor on cross arm at 311 River RD caused the RX2001 to trip opened. ON call made repairs | O/H Conductor | Insulator | 103 | 119 | 204 | East | 7F2
131223 | 2015-04-20 | Defective Equipment | Electrical Failure | Broken insulator and burtn conductor on cross arm at 311 River RD caused the RX2001 to trip opened. ON call made repairs | O/H Conductor | Insulator | 197 | 135 | 443 | East | 7F2
131224 | 2015-04-20 | Defective Equipment | Defective Equipment/ Material | R phase tap from pole 65C1D-0493 to EOL was isolated to allow crew to make repairs to defective crossarm. Overbrook (SO06). | Pole Attachement | Crossarm | 30 | 108 | 54 | East | SO06
131225 | 2015-04-21 | Unknown/Other | Unknown | The UF05 CB tripped and did not auto reclosed. Cause remainsunder investigation | None | None | 246 | 49 | 201 | Central | UF05
131226 | 2015-04-21 | Defective Equipment | Mechanical Failure | phase down at blair place. | Pole Attachement | Arrester | 1 | 116 | 2 | East | 8F4
131226 | 2015-04-21 | Defective Equipment | Mechanical Failure | phase down at blair place. | Pole Attachement | Arrester | 3 | 15 | 1 | East | 8F4
131226 | 2015-04-21 | Defective Equipment | Mechanical Failure | phase down at blair place. | Pole Attachement | Arrester | 4 | 17 | 1 | East | 8F4
131226 | 2015-04-21 | Defective Equipment | Mechanical Failure | phase down at blair place. | Pole Attachement | Arrester | 339 | 16 | 90 | East | 8F4
131226 | 2015-04-21 | Defective Equipment | Mechanical Failure | phase down at blair place. | Pole Attachement | Arrester | 354 | 30 | 177 | East | 8F4
131226 | 2015-04-21 | Defective Equipment | Mechanical Failure | phase down at blair place. | Pole Attachement | Arrester | 630 | 6 | 63 | East | 8F4
131226 | 2015-04-21 | Defective Equipment | Mechanical Failure | phase down at blair place. | Pole Attachement | Arrester | 630 | 53 | 556 | East | 8F4
131227 | 2015-04-21 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 28 | 463 | 216 | East | UZ12
131230 | 2015-04-21 | Scheduled Outage | Maintenance | Transformer #X20613 isolated by crew to make repairs to transformer | None | None | 1 | 34 | 1 | East | 249F2
131231 | 2015-04-21 | Scheduled Outage | Construction | X48618 isolated to allow crew to transfer plant | None | None | 10 | 240 | 40 | Central | UW01
131233 | 2015-04-22 | Scheduled Outage | Construction | Soil remediation. | None | None | 7 | 515 | 60 | East | 77M6
131234 | 2015-04-22 | Scheduled Outage | Construction | Reconfigure overhead. | None | None | 24 | 240 | 96 | West | RHNF3
131235 | 2015-04-22 | Scheduled Outage | Construction | Repair downed neutral. | None | None | 1 | 172 | 3 | West | 28F3
131236 | 2015-04-22 | Defective Equipment | Defective Equipment/ Material | crew isolated X27019 to replace a service | Secondary \ Service | O/H Service | 8 | 44 | 6 | East | AE01
131237 | 2015-04-22 | Scheduled Outage | Construction | 2 transformers #X49066 and X49063, isolated by crew for a pole change | None | None | 20 | 180 | 60 | East | AJ07
131239 | 2015-04-22 | Scheduled Outage | Construction | Defective switch | None | None | 1 | 21 | 0 | West | MWDF3
131240 | 2015-04-22 | Scheduled Outage | Maintenance | permanent repairs to customer owned switchgear at TN6126CZZ | None | Switch | 1 | 362 | 6 | East | 1808
131241 | 2015-04-22 | Foreign Interference | Dig-In | Contractor dug into our plant | U/G Cable | PILC | 75 | 149 | 186 | South | 145F1
131242 | 2015-04-23 | Scheduled Outage | Construction | Vault V717 will be isolated to allow crew to replace cables and risers. Gladstone (UX02) ID# 131242. | None | None | 1 | 83 | 1 | Central | UX02
131245 | 2015-04-23 | Scheduled Outage | Maintenance | Transformer #X24370 isolated by crew to transfer transformer to new pole | None | None | 4 | 150 | 10 | East | UT12
131246 | 2015-04-23 | Scheduled Outage | Construction | Transformer #X27611 isolated by crew for a service upgrade | None | None | 13 | 58 | 13 | Central | UN04
131247 | 2015-04-23 | Scheduled Outage | Construction | Transformer #X35574 isolated by crew to re-arrange plant | None | None | 2 | 100 | 3 | South | FAL03
131248 | 2015-04-23 | Scheduled Outage | Construction | Transformer #X27813 isolated by crew to install new pole. | None | None | 12 | 249 | 50 | East | UZ11
131249 | 2015-04-23 | Tree Contacts | Falling Tree | Customer trimming trees at 1274 Brookline dropped limb on overhead and downed the 4kv primary conductors. Albion (UA07) ID# 131249. | O/H Conductor | O/H Conductor | 13 | 120 | 26 | East | UA07
131251 | 2015-04-23 | Scheduled Outage | Construction | Transformer X27811 at 3005 McCarthy Rd isolated by crew to install new pole | None | None | 12 | 183 | 37 | East | UZ11
131252 | 2015-04-23 | Scheduled Outage | Construction | Transformer X30524 at 629 MacLaren St. isolated by crew to install replace transformer and run in new secondary | None | None | 41 | 310 | 212 | Central | UF07
131253 | 2015-04-23 | Scheduled Outage | Construction | Transformer X30325 at 645 MacLaren St. isolated by crew to install replace transformer and run in new secondary | None | None | 10 | 310 | 52 | Central | UF07
131254 | 2015-04-23 | Scheduled Outage | Construction | Transformer X30564 at 61 Cartier St. isolated by contractor to transfer plant to new pole | None | None | 29 | 130 | 63 | Central | UX05
131255 | 2015-04-23 | Scheduled Outage | Maintenance | To allow customer to make repairs in VT50. | None | Switch | 1 | 322 | 5 | East | 1802
131256 | 2015-04-24 | Scheduled Outage | Construction | Service replaced at X33218, 8 Customers interrupted on the Parkwood Hills 190F2 White Phase for 56 mins at 35 Attwood | None | None | 8 | 56 | 7 | South | 190F2
131257 | 2015-04-24 | Scheduled Outage | Construction | Elbow, Insert and Cutout Changes interrupting a string of underground transformers between S26652 and S20103 on the ALEXF3 affecting 41 customers at Morningsun and Sona for 146 mins. | None | None | 41 | 146 | 100 | West | ALEXF3
131258 | 2015-04-24 | Scheduled Outage | Construction | Transformer #X33942 isolated by crew to run new secondary in | None | None | 5 | 150 | 12 | Central | UL02
131259 | 2015-04-24 | Scheduled Outage | Construction | Transformer #X41730 isolated by crew to relocate to new pole | None | None | 5 | 130 | 11 | East | CYRF3
131260 | 2015-04-24 | Scheduled Outage | Construction | Transformer #X34107 isolated by crew to connect new service | None | None | 12 | 25 | 5 | Central | TH01
131261 | 2015-04-24 | Scheduled Outage | Construction | Transformer #X34138 isolated by crew to replace cut out | None | None | 4 | 37 | 2 | Central | TH01
131262 | 2015-04-24 | Scheduled Outage | Construction | Crews isolated Epworth 58F6 overhead along David Drive to replace defective insulators and cross arm affecting 51 customers for 92 mins. | None | None | 51 | 92 | 78 | South | EPWF6
131263 | 2015-04-24 | Foreign Interference | Vehicle | MVA broke pole X26548. | Pole | Pole | 1 | 241 | 4 | East | 77M2
131263 | 2015-04-24 | Foreign Interference | Vehicle | MVA broke pole X26548. | Pole | Pole | 11 | 8 | 1 | East | 77M2
131263 | 2015-04-24 | Foreign Interference | Vehicle | MVA broke pole X26548. | Pole | Pole | 16 | 48 | 13 | East | 77M2
131263 | 2015-04-24 | Foreign Interference | Vehicle | MVA broke pole X26548. | Pole | Pole | 971 | 27 | 437 | East | 77M2
131263 | 2015-04-24 | Foreign Interference | Vehicle | MVA broke pole X26548. | Pole | Pole | 1806 | 83 | 2498 | East | 77M2
131266 | 2015-04-26 | Foreign Interference | Wildlife (Bird/Animal) | Bird contact | O/H Transformer | O/H Transformer (1ph) | 10 | 85 | 14 | Central | TD01
131268 | 2015-04-27 | Scheduled Outage | Construction | TP109001 was isolated to allow crew to resplace defective live front transformer. Blackburn MS (BLKF1) | None | None | 6 | 193 | 19 | East | BLKF1
131270 | 2015-04-27 | Scheduled Outage | Construction | Temp 118 B to EOL at 1 Sunnyside was isolated to allow crew to re string conductor. Richmond North (RHNF3). ID# 131270 | None | None | 24 | 354 | 142 | West | RHNF1
131271 | 2015-04-27 | Scheduled Outage | Construction | RHNF1 from TEMP122W to TEMP77 isolated for pole and conductor replacement | None | None | 7 | 370 | 43 | West | RHNF1
131272 | 2015-04-28 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30566 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 5 | 85 | 7 | Central | UX09
131273 | 2015-04-28 | Scheduled Outage | Construction | K-Line has reconfigured overhead on UW06 on Woodside. Part of pole replacement project | None | None | 26 | 361 | 156 | Central | UW06
131274 | 2015-04-28 | Defective Equipment | Mechanical Failure | Blown pothead on the TA2AF riser pole on Albion Rd just South of Kithener Ave | U/G Cable Attachement | Pothead | 1104 | 28 | 515 | East | TA2AF
131275 | 2015-04-28 | Defective Equipment | Electrical Failure | 6T1 transformer tripped on gas surge protection. | Station Equipment | Transformer | 16 | 66 | 18 | East | 6F10
131275 | 2015-04-28 | Defective Equipment | Electrical Failure | 6T1 transformer tripped on gas surge protection. | Station Equipment | Transformer | 17 | 11 | 3 | East | 6F1
131275 | 2015-04-28 | Defective Equipment | Electrical Failure | 6T1 transformer tripped on gas surge protection. | Station Equipment | Transformer | 28 | 112 | 52 | East | 6F2
131275 | 2015-04-28 | Defective Equipment | Electrical Failure | 6T1 transformer tripped on gas surge protection. | Station Equipment | Transformer | 70 | 73 | 85 | East | 6F7
131275 | 2015-04-28 | Defective Equipment | Electrical Failure | 6T1 transformer tripped on gas surge protection. | Station Equipment | Transformer | 101 | 112 | 189 | East | 6F1
131275 | 2015-04-28 | Defective Equipment | Electrical Failure | 6T1 transformer tripped on gas surge protection. | Station Equipment | Transformer | 164 | 73 | 200 | East | 6F4
131275 | 2015-04-28 | Defective Equipment | Electrical Failure | 6T1 transformer tripped on gas surge protection. | Station Equipment | Transformer | 787 | 7 | 92 | East | BLKF4
131275 | 2015-04-28 | Defective Equipment | Electrical Failure | 6T1 transformer tripped on gas surge protection. | Station Equipment | Transformer | 943 | 57 | 896 | East | 6F10
131276 | 2015-04-29 | Scheduled Outage | Construction | To allow Hydro Ottawa crews & J.W Leslie crews to re-configure primary cables & cut-in & commission one new transformer (Limebank DS- LMBF7 (this circuit is not in this database)) | None | None | 45 | 237 | 178 | East | L2M (Limebank MS - T1/T2)
131277 | 2015-04-29 | Scheduled Outage | Construction | V717 isolated to allow Sproule to replace cables cables and install new riser. | None | None | 2 | 238 | 8 | Central | UX02
131278 | 2015-04-29 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X34138 TO REPLACE TRIPLEX SERVICE | None | None | 4 | 45 | 3 | Central | TH01
131279 | 2015-04-29 | Scheduled Outage | Construction | To allow Black & Macdonald to replace utility poles | None | None | 27 | 340 | 153 | East | AJ07
131280 | 2015-04-29 | Scheduled Outage | Maintenance | Customer vault mtce by Eaton Electric | None | None | 383 | 330 | 2106 | East | 2206
131283 | 2015-04-30 | Scheduled Outage | Construction | insulator replacement along Hwy417 | None | None | 26 | 319 | 138 | Central | TW22
131285 | 2015-04-30 | Scheduled Outage | Construction | to replace broken pole at 920 Dresden cres. | None | Pole | 9 | 30 | 4 | Central | TD07
131285 | 2015-04-30 | Scheduled Outage | Construction | to replace broken pole at 920 Dresden cres. | None | Pole | 17 | 218 | 62 | Central | TD07
131287 | 2015-04-30 | Scheduled Outage | Construction | Vault Maintenance, suite metering setup, in secondary main switch outside vault. | None | None | 1 | 353 | 6 | Central | UN05
131288 | 2015-05-01 | Unknown/Other | Unknown | Circuit Patrolled, nothing found. To be patrolled in daylight. | Station Equipment | Unknown \ Other | 387 | 93 | 600 | East | BCHF3
131288 | 2015-05-01 | Unknown/Other | Unknown | Circuit Patrolled, nothing found. To be patrolled in daylight. | Station Equipment | Unknown \ Other | 1275 | 89 | 1891 | East | BCHF5
131289 | 2015-05-01 | Scheduled Outage | Construction | Upgrade transformer for future work. | None | None | 1 | 127 | 2 | West | ALEXF1
131290 | 2015-05-01 | Scheduled Outage | Vegetation Management | Not yet known.storm hardening in front of 155 and 157 Acacia. | None | None | 54 | 154 | 139 | Central | TK2AC
131292 | 2015-05-01 | Defective Equipment | Defective Equipment/ Material | 24/7 changed a broken cutout at pole X27796 located at 1887 Logan Ave. | O/H Switchgear | Fused Cutout | 12 | 372 | 74 | East | UQ07
131297 | 2015-05-02 | Human Element | Protection Setting | S21899 R and B phases blew due to undersized fuse on trunk and carrying both the AJ03 and AJ05. | O/H Switchgear | Fused Cutout | 72 | 30 | 36 | East | AJ05
131297 | 2015-05-02 | Human Element | Protection Setting | S21899 R and B phases blew due to undersized fuse on trunk and carrying both the AJ03 and AJ05. | O/H Switchgear | Fused Cutout | 201 | 30 | 100 | East | AJ03
131297 | 2015-05-02 | Human Element | Protection Setting | S21899 R and B phases blew due to undersized fuse on trunk and carrying both the AJ03 and AJ05. | O/H Switchgear | Fused Cutout | 203 | 49 | 166 | East | AJ05
131297 | 2015-05-02 | Human Element | Protection Setting | S21899 R and B phases blew due to undersized fuse on trunk and carrying both the AJ03 and AJ05. | O/H Switchgear | Fused Cutout | 377 | 49 | 308 | East | AJ03
131299 | 2015-05-03 | Unknown/Other | Unknown | No cause found | None | None | 672 | 87 | 974 | Central | UD04
131300 | 2015-05-03 | Defective Equipment | Electrical Failure | Transformer K0022 opened to investigate burning smell. 5 secondary leads disconnected and trans former placed back inservice. Oncall to repair leads. | U/G Cable | Unknown \ Other | 5 | 757 | 63 | East | AQ02
131300 | 2015-05-03 | Defective Equipment | Electrical Failure | Transformer K0022 opened to investigate burning smell. 5 secondary leads disconnected and trans former placed back inservice. Oncall to repair leads. | U/G Cable | Unknown \ Other | 12 | 82 | 16 | East | AQ02
131301 | 2015-05-03 | Defective Equipment | Mechanical Failure | 7F1 breaker was opened by System Office for safety reasons. | U/G Transformer | Padmount (3ph) | 1 | 294 | 5 | East | 7F1
131301 | 2015-05-03 | Defective Equipment | Mechanical Failure | 7F1 breaker was opened by System Office for safety reasons. | U/G Transformer | Padmount (3ph) | 3114 | 72 | 3737 | East | 7F1
131302 | 2015-05-04 | Scheduled Outage | Vegetation Management | Overhead section from S22505 RWB isolated to allow for tree trimming, Beechwood UB07, ID # 131 | None | None | 115 | 396 | 759 | East | UB07
131304 | 2015-05-04 | Scheduled Outage | Construction | Transformer X30661 545 Gilmour St. isolated by crew to install a new pole | None | None | 15 | 330 | 82 | Central | UF05
131305 | 2015-05-04 | Scheduled Outage | Construction | Transformer X30325 at 645 MacLaren St isolated by crew to rearange plant | None | None | 12 | 236 | 47 | Central | UF07
131306 | 2015-05-04 | Scheduled Outage | Construction | Transformer X25750 at 35 Adeline St. isolated by crew to rearange plant | None | None | 6 | 190 | 19 | Central | SB10
131307 | 2015-05-04 | Scheduled Outage | Construction | Transformer X32469 at 1773 Baseline Rd isolated by crew to transfer plant | None | None | 2 | 130 | 4 | Central | UW05
131308 | 2015-05-04 | Defective Equipment | Mechanical Failure | Defective mid span taps. | O/H Conductor | Ampact | 1 | 400 | 7 | East | 48M2
131309 | 2015-05-05 | Scheduled Outage | Construction | Transformer X33417 at 1215 Woodside Dr. isolated by contractor to transfer plant - Shawn Evans of K-line had this outage | None | None | 4 | 61 | 4 | Central | UW06
131310 | 2015-05-05 | Scheduled Outage | Maintenance | To fix-up water issues and check on previous repairs. | None | None | 2 | 314 | 10 | East | BCHF4
131312 | 2015-05-05 | Scheduled Outage | Construction | ISOLATED AND REPLACED 3 BANK OF TRANSFORMERS X24280 | None | None | 1 | 330 | 6 | East | 6F1
131313 | 2015-05-05 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32808 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 135 | 14 | Central | UW06
131315 | 2015-05-06 | Scheduled Outage | Construction | A section of AJ07 between Temp 55 & Temp 96 was isolated for planned pole replacement. 35 customers affected for 284 min. Playfair AJ07. ID#131315 | None | None | 35 | 284 | 166 | East | AJ07
131316 | 2015-05-06 | Scheduled Outage | Construction | A section of UC10 from Temp18B to EOL was isolated to transfer plant to new O/H. 51 customers affected for 545 min. Clyde UC10. ID#131316. | None | None | 51 | 545 | 463 | Central | UC10
131317 | 2015-05-07 | Scheduled Outage | Maintenance | Transformer 306 isolated to allow crews to level the transfomrer base. | None | None | 1 | 472 | 8 | West | 624F3
131318 | 2015-05-07 | Human Element | Protection Setting | Bus tie breaker (TKYE) tripped on overload due to the 10 circuits it was carrying. The TK J bus was offloaded to accommodate a Hydro One outage. | None | None | 1 | 33 | 1 | Central | 417
131318 | 2015-05-07 | Human Element | Protection Setting | Bus tie breaker (TKYE) tripped on overload due to the 10 circuits it was carrying. The TK J bus was offloaded to accommodate a Hydro One outage. | None | None | 22 | 40 | 15 | Central | TK4TS
131318 | 2015-05-07 | Human Element | Protection Setting | Bus tie breaker (TKYE) tripped on overload due to the 10 circuits it was carrying. The TK J bus was offloaded to accommodate a Hydro One outage. | None | None | 84 | 33 | 46 | Central | 416
131318 | 2015-05-07 | Human Element | Protection Setting | Bus tie breaker (TKYE) tripped on overload due to the 10 circuits it was carrying. The TK J bus was offloaded to accommodate a Hydro One outage. | None | None | 125 | 33 | 69 | Central | TK6TS
131318 | 2015-05-07 | Human Element | Protection Setting | Bus tie breaker (TKYE) tripped on overload due to the 10 circuits it was carrying. The TK J bus was offloaded to accommodate a Hydro One outage. | None | None | 260 | 33 | 143 | Central | 404
131318 | 2015-05-07 | Human Element | Protection Setting | Bus tie breaker (TKYE) tripped on overload due to the 10 circuits it was carrying. The TK J bus was offloaded to accommodate a Hydro One outage. | None | None | 501 | 33 | 276 | Central | 408
131318 | 2015-05-07 | Human Element | Protection Setting | Bus tie breaker (TKYE) tripped on overload due to the 10 circuits it was carrying. The TK J bus was offloaded to accommodate a Hydro One outage. | None | None | 723 | 33 | 398 | Central | 411
131318 | 2015-05-07 | Human Element | Protection Setting | Bus tie breaker (TKYE) tripped on overload due to the 10 circuits it was carrying. The TK J bus was offloaded to accommodate a Hydro One outage. | None | None | 760 | 33 | 418 | Central | TK2AC
131319 | 2015-05-07 | Defective Equipment | Defective Equipment/ Material | Crew replaced defective transformer X30832 at 140 Blackburn Ave. | O/H Transformer | O/H Transformer (1ph) | 24 | 103 | 41 | Central | UN04
131320 | 2015-05-07 | Scheduled Outage | Construction | New fire panel installation in the vault VE32 | None | None | 1 | 188 | 3 | East | 8F3
131322 | 2015-05-08 | Scheduled Outage | Construction | TE748 isolated for transformer change. | None | Padmount (1ph) | 8 | 111 | 15 | South | 84F3
131323 | 2015-05-08 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to disconnect TP9690 from the TB14 circuit and connect & energize TP9690 from the 5311 circuit. VT689 is also being decommissioned. | None | None | 1 | 188 | 3 | East | TB14
131324 | 2015-05-08 | Defective Equipment | Electrical Failure | Cable fault between V105 and S11943 | U/G Cable | PILC | 2 | 809 | 27 | Central | AD04
131326 | 2015-05-08 | Defective Equipment | Defective Equipment/ Material | Customer called in part power. Crew found blown primary side fuse on on transformer. TX tested good new fuse installed and power restored. | U/G Transformer | Unknown \ Other | 3 | 55 | 3 | East | UA06
131328 | 2015-05-08 | Scheduled Outage | Construction | Transformer X24912 at 2721 Colman St. isolated by crew to replace triplex service and linkets at the standpipe | None | None | 16 | 72 | 19 | East | UZ03
131332 | 2015-05-09 | Tree Contacts | Falling Tree | Tree took down triplex. | None | None | 8 | 20 | 3 | Central | TW22
131333 | 2015-05-09 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X23859 (SQUIRREL CONTACT ) | O/H Transformer | O/H Transformer (1ph) | 3 | 134 | 7 | East | 77M6
131339 | 2015-05-11 | Tree Contacts | Broken Branch | Customer reports fuse on transformer at 9 Elvine st is blown and OMS indicates red phase fuse at G247 also is blown G247. | O/H Switchgear | Fused Cutout | 48 | 157 | 126 | East | 8F1
131341 | 2015-05-11 | Scheduled Outage | Construction | ISOLATED TRANDFORMER X32450 TO INSTALL NEW POLE | None | None | 8 | 60 | 8 | Central | UW06
131342 | 2015-05-11 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMERS X35204, X32448 AND 55C4D-0008 TO INSTALL NEW POLES | None | None | 17 | 60 | 17 | Central | UW06
131343 | 2015-05-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | trees on customer owned line | O/H Conductor | O/H Conductor | 52 | 96 | 83 | East | 249F2
131344 | 2015-05-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | Not yet known.trees in wires | O/H Conductor | O/H Conductor | 48 | 111 | 89 | East | 8F1
131345 | 2015-05-11 | Scheduled Outage | Construction | Transformer X32449 at 1165 Agincourt Rd, X35205 at 1191 Agincourt Rd and X35206 at 1215 Agincourt Rd isolated by Jordan Foote of K-Line to install new poles | None | None | 33 | 502 | 276 | Central | UW06
131347 | 2015-05-12 | Scheduled Outage | Construction | AJ07 O/H section between TEMP96 and S14422 RWB was isolated to allow crew to perform pole replacement at rear lot of Connectivcuit Ave. Playfair (AJ07). | None | None | 35 | 394 | 230 | East | AJ07
131349 | 2015-05-12 | Scheduled Outage | Construction | UW06 O/H section from TEMP18 to EOL was isolated to allow crew to transfer plant to new pole. Woodroffe (UW06) | None | None | 40 | 436 | 291 | Central | UW06
131353 | 2015-05-12 | Defective Equipment | Electrical Failure | Defective cable/elbow/insert at TP2574 caused S39-4 W phase fuse to open. Transformer replaced by on-call. | U/G Cable Attachement | Elbow \ Insert | 8 | 225 | 30 | West | TFXF6
131353 | 2015-05-12 | Defective Equipment | Electrical Failure | Defective cable/elbow/insert at TP2574 caused S39-4 W phase fuse to open. Transformer replaced by on-call. | U/G Cable Attachement | Elbow \ Insert | 43 | 11 | 8 | West | TFXF6
131353 | 2015-05-12 | Defective Equipment | Electrical Failure | Defective cable/elbow/insert at TP2574 caused S39-4 W phase fuse to open. Transformer replaced by on-call. | U/G Cable Attachement | Elbow \ Insert | 166 | 83 | 230 | West | TFXF6
131354 | 2015-05-13 | Scheduled Outage | Construction | Transformers TE2954 and TE2850 were isolated to allow crew to clean out transformer base and install new cable to connect new transformer TP10885 at 30 Daffodil. Limebank (LMBF7) | None | None | 24 | 333 | 133 | East | 7F4
131355 | 2015-05-13 | Scheduled Outage | Vegetation Management | Transformer X27157 at 1814 Edgecome was isolated to allow tree contractor to remove tree branches in proximity of O/H wires. Russell (TB15) | None | None | 15 | 170 | 42 | East | TB15
131356 | 2015-05-13 | Scheduled Outage | Construction | Transformer X33546 at 221 Chandler Ave. isolated by Matt Stuyt to replace triplex service to 212 Sanford Ave. | None | None | 10 | 104 | 17 | Central | AK02
131358 | 2015-05-14 | Scheduled Outage | Construction | To allow contractor to pull in and make new secondary connections. | None | None | 3 | 114 | 6 | East | TO2AP
131359 | 2015-05-14 | Scheduled Outage | Construction | S20908 to EOL isolated to remove pole from rear of 2172 Queensgrove. | None | Pole | 26 | 186 | 81 | Central | TW22
131361 | 2015-05-14 | Defective Equipment | Electrical Failure | High side fuse blown on 28T1 transformer. | O/H Switchgear | Fused Cutout | 236 | 78 | 307 | West | 28F3
131361 | 2015-05-14 | Defective Equipment | Electrical Failure | High side fuse blown on 28T1 transformer. | O/H Switchgear | Fused Cutout | 241 | 65 | 261 | West | 28F1
131361 | 2015-05-14 | Defective Equipment | Electrical Failure | High side fuse blown on 28T1 transformer. | O/H Switchgear | Fused Cutout | 1072 | 89 | 1590 | West | 28F2
131362 | 2015-05-14 | Scheduled Outage | Construction | Transformer #3089 isolated by crew to connect a service (Joe Mckenna) | None | None | 10 | 7 | 1 | West | 39F3
131363 | 2015-05-14 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact | None | None | 1 | 94 | 2 | West | MWDF3
131368 | 2015-05-17 | Scheduled Outage | Maintenance | Isolation of Central Heating Plant on Heron Rd to make reapirs to metering. | None | None | 1 | 73 | 1 | East | 2209
131369 | 2015-05-15 | Scheduled Outage | Maintenance | VT55 isolated to megger and ratio transformers and inspect and torque AC panels | None | None | 1 | 2502 | 42 | East | 2208
131371 | 2015-05-18 | Scheduled Outage | Maintenance | Transformer #X32818 isolated by crew to replace blown fuse for streetlighting | None | None | 8 | 11 | 1 | Central | UW06
131372 | 2015-05-18 | Defective Equipment | Electrical Failure | Bayonet fuse in TP3068 opned due to secondary cable fault | Secondary \ Service | U/G Service | 11 | 5568 | 1021 | South | 160F2
131372 | 2015-05-18 | Defective Equipment | Electrical Failure | Bayonet fuse in TP3068 opned due to secondary cable fault | Secondary \ Service | U/G Service | 15 | 287 | 72 | South | 160F2
131373 | 2015-05-18 | Defective Equipment | Electrical Failure | Defective customer owned equipment cause the TS58 breaker to trip. 4 customers affected. Slater (611/609) ID#131373 | Customer Owned | Customer-Owned | 4 | 65 | 4 | Central | 611
131374 | 2015-05-19 | Scheduled Outage | Construction | Transformer TP9590 was isolated to allow crew to pull new secondary cables. Casselman (V11F1) ID# 131374. | None | None | 3 | 427 | 21 | East | V11F1
131375 | 2015-05-19 | Scheduled Outage | Maintenance | VE4 at 15 Woodridge was interrupted for vault maintenenance on the 49F4 out of Bayshore DS affecting 1 customer for 127 minutes | None | None | 1 | 127 | 2 | South | 49F4
131376 | 2015-05-19 | Foreign Interference | Vehicle | Transformer MT1381 minipad replaced because of damage from vehicle accident, Carling TS 307, ID # 131376 | U/G Transformer | Padmount (1ph) | 19 | 107 | 34 | Central | 307
131378 | 2015-05-19 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35148 FOR A SERVICE UPGRADE | None | None | 7 | 45 | 5 | South | 190F5
131379 | 2015-05-19 | Foreign Interference | Foreign Objects | 22M27 auto-reclosed and the 210F2 tripped open due to a tarp blowing into the overhead. Jockvale, Barrhaven and Longfields T2 affected by Auto-Reclose. Nepean TS (22M27) ID# 131379. | None | None | 926 | 95 | 1466 | South | LGFF2
131380 | 2015-05-19 | Unknown/Other | Unknown | Transformer X30392 opened no cause found, Hinchey TH11, ID # 131380 | O/H Transformer | Unknown \ Other | 1 | 99 | 2 | Central | TH11-NIU
131381 | 2015-05-19 | Defective Equipment | Mechanical Failure | 200F1 section between S1067 and S353 was taken off potential to allow crew to install jumper across defective switch. Stafford Rd (200F1) ID# 131381 | O/H Switchgear | Inline Switch | 2 | 42 | 1 | South | 200F1
131382 | 2015-05-20 | Unknown/Other | Unknown | Transformer #X32275 opened up, cause unknown | O/H Switchgear | Fused Cutout | 11 | 87 | 16 | Central | TD01
131385 | 2015-05-20 | Scheduled Outage | Construction | section of UW06 and UC10 overhead isolated reconfigure and connect to UW07, Woodroffe UW06 and UW07, ID # 131385 | None | None | 10 | 25 | 4 | Central | UW06
131385 | 2015-05-20 | Scheduled Outage | Construction | section of UW06 and UC10 overhead isolated reconfigure and connect to UW07, Woodroffe UW06 and UW07, ID # 131385 | None | None | 195 | 365 | 1186 | Central | UW06
131386 | 2015-05-21 | Unknown/Other | Unknown | Transformer #X26658 and switch S22869 opened up, no apparent cause. | O/H Switchgear | Inline Switch | 15 | 139 | 35 | Central | TH01
131389 | 2015-05-21 | Scheduled Outage | Construction | Transformer TP8382 at 1326 Halton Terr was isolated to allow crew to reaplce transformer. Marchwood MS. (MWDF4) | None | None | 20 | 189 | 63 | West | MWDF4
131390 | 2015-05-21 | Scheduled Outage | Maintenance | Transformer TP7480 @ 64 Bald Eagle Cres was isolated by the crew to remove primary cable from the duct | None | None | 10 | 218 | 36 | West | 28F2
131391 | 2015-05-21 | Scheduled Outage | Construction | Transformer #K01161 isolated by crew to change secondary | None | None | 18 | 220 | 66 | Central | AD04
131392 | 2015-05-21 | Scheduled Outage | Construction | Transformer #X35574 isolated by crew to transfer plant | None | None | 2 | 205 | 7 | South | FAL03
131393 | 2015-05-21 | Scheduled Outage | Construction | Transformer #X29084 isolated by crew for a pole replacement | None | None | 8 | 175 | 23 | East | UZ11
131394 | 2015-05-21 | Scheduled Outage | Construction | Transformer #TP8382 isolated by crew to replace rusty transformer | None | None | 20 | 270 | 90 | West | MWDF4
131395 | 2015-05-21 | Scheduled Outage | Construction | Transformer TP9590 @ 17 Industriel Casselman was isolated by Sproule to connect secondary cables | None | Unknown \ Other | 3 | 370 | 18 | East | V11F1
131397 | 2015-05-21 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X27884 TO REPLACED POLE | None | None | 3 | 220 | 11 | East | UZ11
131399 | 2015-05-22 | Scheduled Outage | Construction | Transformer #X34111 isolated by crew for a switch replacement | None | None | 8 | 40 | 5 | Central | TH01
131402 | 2015-05-22 | Scheduled Outage | Construction | Transformer #X34112 isolated by crew to replace switch | None | None | 10 | 45 | 8 | Central | TH01
131403 | 2015-05-22 | Defective Equipment | Mechanical Failure | A pole fire at switch G360 @ 1135 Gable field require the BCHF8 and the 8F1 O/H from CS21699 to be dump for fire department to exinguish pole fire. Beaconhill (BCHF8), Moulton (8F1). | Pole | Pole | 314 | 223 | 1167 | East | BCHF8
131403 | 2015-05-22 | Defective Equipment | Mechanical Failure | A pole fire at switch G360 @ 1135 Gable field require the BCHF8 and the 8F1 O/H from CS21699 to be dump for fire department to exinguish pole fire. Beaconhill (BCHF8), Moulton (8F1). | Pole | Pole | 580 | 34 | 329 | East | BCHF8
131403 | 2015-05-22 | Defective Equipment | Mechanical Failure | A pole fire at switch G360 @ 1135 Gable field require the BCHF8 and the 8F1 O/H from CS21699 to be dump for fire department to exinguish pole fire. Beaconhill (BCHF8), Moulton (8F1). | Pole | Pole | 956 | 95 | 1514 | East | 8F1
131403 | 2015-05-22 | Defective Equipment | Mechanical Failure | A pole fire at switch G360 @ 1135 Gable field require the BCHF8 and the 8F1 O/H from CS21699 to be dump for fire department to exinguish pole fire. Beaconhill (BCHF8), Moulton (8F1). | Pole | Pole | 1072 | 59 | 1054 | East | BCHF8
131403 | 2015-05-22 | Defective Equipment | Mechanical Failure | A pole fire at switch G360 @ 1135 Gable field require the BCHF8 and the 8F1 O/H from CS21699 to be dump for fire department to exinguish pole fire. Beaconhill (BCHF8), Moulton (8F1). | Pole | Pole | 1595 | 42 | 1116 | East | 8F1
131404 | 2015-05-22 | Scheduled Outage | Construction | Transformer TP10136 and TP7690 were isolated to allow crew to splice and reconfigure cable loop. Terry Fox (TFXF5) | None | None | 16 | 150 | 40 | West | TFXF5
131405 | 2015-05-22 | Defective Equipment | Electrical Failure | Line clamp burnt off at S29465 | O/H Conductor | Hot-Line Clamp | 40 | 80 | 53 | East | AA03
131406 | 2015-05-23 | Scheduled Outage | Maintenance | Switchgear SC15807 was isolated to allow crew to replace defective SF6 gas gauge, Elwood ELW05, ID # 131406 | None | Gas-Insulated Dead Front | 109 | 100 | 182 | East | ELW05
131408 | 2015-05-23 | Scheduled Outage | Maintenance | To allow HOL and contractors to remediate area from oil contamination. | None | Padmount (3ph) | 1 | 499 | 8 | South | 72F6
131409 | 2015-05-23 | Unknown/Other | Unknown | 180F4 auto-reclosed and locked out and transformer X33031 fuse was found blown. No cause could be found. Rideau Heights (180F4) ID# 131409 | Unknown \ Other | Unknown \ Other | 4 | 93 | 6 | South | 180F4
131409 | 2015-05-23 | Unknown/Other | Unknown | 180F4 auto-reclosed and locked out and transformer X33031 fuse was found blown. No cause could be found. Rideau Heights (180F4) ID# 131409 | Unknown \ Other | Unknown \ Other | 990 | 37 | 610 | South | 180F4
131410 | 2015-05-23 | Defective Equipment | Mechanical Failure | S21557 white phase fuse blew due to suspected cable fault between TP6986 and TE1017. Bilberry 77M6 ID# 131410 | U/G Cable | Unknown \ Other | 8 | 40 | 5 | East | 77M6
131410 | 2015-05-23 | Defective Equipment | Mechanical Failure | S21557 white phase fuse blew due to suspected cable fault between TP6986 and TE1017. Bilberry 77M6 ID# 131410 | U/G Cable | Unknown \ Other | 15 | 42 | 10 | East | 77M6
131410 | 2015-05-23 | Defective Equipment | Mechanical Failure | S21557 white phase fuse blew due to suspected cable fault between TP6986 and TE1017. Bilberry 77M6 ID# 131410 | U/G Cable | Unknown \ Other | 97 | 125 | 202 | East | 77M6
131412 | 2015-05-24 | Foreign Interference | Wildlife (Bird/Animal) | Field Operators refused transformer X29729 at 1491 Crestwood Pl. Cause was animal contact - squirrel | O/H Transformer | O/H Transformer (1ph) | 6 | 61 | 6 | East | TB14
131414 | 2015-05-24 | Unknown/Other | Unknown | At 3:03pm SCADA indicates breaker tripped. Crews patrolled but did not find a cause at this time. Walkley (UZ03) ID#131414 | None | None | 332 | 65 | 360 | East | UZ03
131415 | 2015-05-25 | Scheduled Outage | Construction | Pole replacement project. | None | None | 35 | 288 | 168 | East | AJ07
131416 | 2015-05-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | Trees in primary O/H circuit of BRDF5 circuit. | None | None | 0 | 21 | 0 | West | BRDF5
131416 | 2015-05-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | Trees in primary O/H circuit of BRDF5 circuit. | None | None | 870 | 117 | 1696 | West | BRDF5
131417 | 2015-05-25 | Scheduled Outage | Construction | Transformer #X33559 isolated by crew for a new service | None | None | 14 | 30 | 7 | Central | AK03
131418 | 2015-05-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X36536 opened up due to vines on the pole that made contact with high voltage equipment | O/H Switchgear | Fused Cutout | 7 | 53 | 6 | South | EPWF3
131419 | 2015-05-25 | Defective Equipment | Electrical Failure | Transformer #X34407 isolated by crew, (defective transformer to be replaced later), is now temporarily fed from X27963 | O/H Transformer | O/H Transformer (1ph) | 8 | 80 | 11 | East | UZ07
131420 | 2015-05-25 | Scheduled Outage | Forced Switching | Transformer #X27963 isolated by crew to jumper buss to restore power to customers fed from X34407 (defective transformer) | None | None | 10 | 25 | 4 | East | UZ07
131421 | 2015-05-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X27445 opened up due to vine interference | O/H Switchgear | Fused Cutout | 3 | 179 | 9 | East | UA07
131422 | 2015-05-25 | Scheduled Outage | Maintenance | At 3:39pm crews isolated TE2935 to remove a leaking transformer, customers are on generator until new transformer is installed at which point they will require another short outage. Rideau Heights (180F4) ID#131422 | None | Padmount (3ph) | 2 | 44 | 1 | South | 180F4
131423 | 2015-05-26 | Defective Equipment | Defective Equipment/ Material | G114 opened due to defective fuse holder at Goth and Albion | O/H Switchgear | Fused Cutout | 235 | 89 | 349 | East | LTM01
131424 | 2015-05-26 | Scheduled Outage | Construction | replace primary conductor | None | None | 27 | 113 | 51 | Central | TH01
131426 | 2015-05-26 | Scheduled Outage | Construction | To re-insulate and change transformer for future voltage conversion. | None | None | 1 | 138 | 2 | South | FAL02
131427 | 2015-05-26 | Scheduled Outage | Construction | install new poles and transfer plant | None | None | 54 | 575 | 518 | Central | UW07
131428 | 2015-05-26 | Scheduled Outage | Construction | To re-insulate and change transformer for future voltage conversion. | None | None | 1 | 271 | 5 | South | FAL02
131429 | 2015-05-26 | Scheduled Outage | Construction | replace primary conductor | None | None | 33 | 111 | 61 | Central | TH01
131430 | 2015-05-26 | Foreign Interference | Wildlife (Bird/Animal) | animal contact caused transformer fuse and line fuse to blow | O/H Transformer | O/H Transformer (1ph) | 1 | 27 | 0 | East | 8F1
131430 | 2015-05-26 | Foreign Interference | Wildlife (Bird/Animal) | animal contact caused transformer fuse and line fuse to blow | O/H Transformer | O/H Transformer (1ph) | 35 | 63 | 37 | East | 8F1
131431 | 2015-05-26 | Scheduled Outage | Forced Switching | ISOLATED 2 TRANSFORMERS X26246 AND X30498 TO RE-ARRANGE THE HYDRO PLANT | None | None | 27 | 145 | 65 | Central | TH01
131433 | 2015-05-26 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 7 | 189 | 22 | East | CYRF3
131434 | 2015-05-26 | Scheduled Outage | Maintenance | remove asbestos, clean vault, and torque connections. | None | None | 1 | 355 | 6 | East | 77M5
131436 | 2015-05-27 | Foreign Interference | Wildlife (Bird/Animal) | A racoon caused the fuse to blow on the O/H transformer X36549 | O/H Transformer | O/H Transformer (1ph) | 7 | 110 | 13 | South | EPWF3
131437 | 2015-05-27 | Scheduled Outage | Construction | STEVE RUTHERFORD (SPROULE POWERLINE) ISOALATAD TRANSFORMER FEEDING 263 ELGIN ST TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 1 | 105 | 2 | Central | UX10
131439 | 2015-05-27 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 29 | 145 | 70 | East | SO12
131440 | 2015-05-27 | Scheduled Outage | Construction | transfer new plant | None | None | 3 | 239 | 12 | East | UZ11
131442 | 2015-05-27 | Scheduled Outage | Forced Switching | temporary outage due to out of phase condition, to isolate transformer TP6909 Glenlivet. | None | None | 68 | 2 | 2 | East | CYRF3
131443 | 2015-05-27 | Scheduled Outage | Forced Switching | outage due to an out of phase condition. | None | None | 68 | 1 | 1 | East | CYRF3
131444 | 2015-05-27 | Scheduled Outage | Construction | To upgrade of insulators and transformer for future voltage conversion. | None | None | 1 | 187 | 3 | South | FAL03
131445 | 2015-05-27 | Scheduled Outage | Construction | replace switch and arrestors | None | None | 6 | 50 | 5 | Central | TH01
131446 | 2015-05-27 | Scheduled Outage | Construction | replace switch and arrestors | None | None | 9 | 60 | 9 | Central | TH01
131447 | 2015-05-27 | Human Element | Protection Setting | Outage was caused by a blown red phase fuse in S35-4. | None | None | 370 | 8 | 49 | West | JKGF4
131447 | 2015-05-27 | Human Element | Protection Setting | Outage was caused by a blown red phase fuse in S35-4. | None | None | 668 | 84 | 935 | West | JKGF4
131448 | 2015-05-27 | Scheduled Outage | Construction | K-Line installing new poles | None | None | 22 | 480 | 176 | Central | UW07
131449 | 2015-05-27 | Tree Contacts | Broken Branch | tree trimming at X27965 | Secondary \ Service | O/H Service | 2 | 30 | 1 | East | UZ07
131451 | 2015-05-28 | Scheduled Outage | Construction | Vault V719 isolated to allow crew to transfer plant feeding the vault, Gladstone UX06, ID # 131 | None | None | 1 | 138 | 2 | Central | UX06
131452 | 2015-05-28 | Scheduled Outage | Maintenance | Transformer TE1402 was isolated to allow crew to perform IR scan repair work. Jockvale (145F2) ID# 131452. | None | None | 5 | 103 | 9 | South | 145F2
131453 | 2015-05-28 | Scheduled Outage | Forced Switching | Transformer TP6808 was isolated to allow crew to replace leaking transformer. Cyrville (CYRF3) ID# 131453. | None | None | 18 | 107 | 32 | East | CYRF3
131454 | 2015-05-28 | Scheduled Outage | Forced Switching | Transformer TP6779 was isolated to allow crew to replace leaking transformer. Cyrville (CYRF3) ID# 131454. | None | None | 6 | 122 | 12 | East | CYRF3
131455 | 2015-05-28 | Adverse Environment | Fire | BLKF5 red phase from G60R to EOL was isolated to allow crew to remove tree on fire from overhead line. Blackburn (BLKF5) ID# 131455. | O/H Conductor | O/H Conductor | 6 | 85 | 8 | East | BLKF5
131456 | 2015-05-28 | Defective Equipment | Electrical Failure | 58F2 tripped open due to pole fire. | Pole | Insulation Failure (Pole Fire) | 1 | 128 | 2 | South | EPWF2
131456 | 2015-05-28 | Defective Equipment | Electrical Failure | 58F2 tripped open due to pole fire. | Pole | Insulation Failure (Pole Fire) | 9 | 175 | 26 | South | EPWF2
131456 | 2015-05-28 | Defective Equipment | Electrical Failure | 58F2 tripped open due to pole fire. | Pole | Insulation Failure (Pole Fire) | 11 | 141 | 26 | South | 190F3
131456 | 2015-05-28 | Defective Equipment | Electrical Failure | 58F2 tripped open due to pole fire. | Pole | Insulation Failure (Pole Fire) | 13 | 7 | 2 | South | EPWF2
131456 | 2015-05-28 | Defective Equipment | Electrical Failure | 58F2 tripped open due to pole fire. | Pole | Insulation Failure (Pole Fire) | 153 | 125 | 319 | South | EPWF2
131456 | 2015-05-28 | Defective Equipment | Electrical Failure | 58F2 tripped open due to pole fire. | Pole | Insulation Failure (Pole Fire) | 550 | 6 | 55 | South | 190F3
131456 | 2015-05-28 | Defective Equipment | Electrical Failure | 58F2 tripped open due to pole fire. | Pole | Insulation Failure (Pole Fire) | 1394 | 139 | 3229 | South | 190F3
131458 | 2015-05-28 | Scheduled Outage | Forced Switching | X25751 isolated for load transfer. Bronson SB10. ID#131458 | None | None | 7 | 38 | 4 | Central | SB10
131459 | 2015-05-28 | Scheduled Outage | Forced Switching | X25748 isolated for load transfer. Bronson SB10. ID#131459. | None | None | 4 | 58 | 4 | Central | SB10
131461 | 2015-05-29 | Scheduled Outage | Maintenance | VT751 and VT720 at 316 and 318 Lorry Greenberg isolated for Vault clean and Torque on the 2204 out of Albion Terminal with 2 customers affected for 155 minutes. | None | None | 2 | 155 | 5 | East | 2204
131462 | 2015-05-29 | Scheduled Outage | Maintenance | TP8410 at 504 Egret was isolated to repair damaged transformer lid on the FAL03 out of Fallowfield DS affecting 6 customers. | None | None | 6 | 57 | 6 | South | FAL03
131463 | 2015-05-29 | Scheduled Outage | Construction | Transformer TP10112 was isolated to allow crew to replace temp service with permanent. Fallowfield (FAL01) ID# 131463. | None | None | 1 | 145 | 2 | South | FAL01
131464 | 2015-05-29 | Scheduled Outage | Forced Switching | 43F3 from SW644 to EOL was offloaded to allow crew to transfer load to BECKF2. Munster (43F3) ID# 131464. | None | None | 278 | 8 | 37 | West | 43F3
131465 | 2015-05-29 | Scheduled Outage | Forced Switching | 43F3 load from Station to SW644 and 43F2 were interrupted to allow crew to move load to BECKF2. Munster (43F2, 43F3) ID# 131465. | None | None | 473 | 2 | 16 | West | 43F2
131466 | 2015-05-29 | Loss Of Supply | Third Party | TR2FB circuit tripped open due defective vault at VT218. | None | None | 1 | 8256 | 138 | Central | TR2FB
131466 | 2015-05-29 | Loss Of Supply | Third Party | TR2FB circuit tripped open due defective vault at VT218. | None | None | 38 | 59 | 37 | Central | TR2FB
131466 | 2015-05-29 | Loss Of Supply | Third Party | TR2FB circuit tripped open due defective vault at VT218. | None | None | 1178 | 45 | 884 | Central | TR2FB
131467 | 2015-05-29 | Scheduled Outage | Construction | Transformer X23394 at 623 Center St. isolated to change service to 625 Center St. | None | None | 10 | 37 | 6 | East | UB03
131470 | 2015-05-30 | Human Element | Incorrect Records/ labelling | RX2011 TRIPPED DUE TO LOADING | None | None | 3451 | 16 | 920 | West | TFXF1
131472 | 2015-05-30 | Lightning | Lightning | A severe thunder storm was passing through the Ottawa area which cause the 7F4 to autreclose and S18183 R phase @ 5271 LONG ISLAND RD to blow | O/H Conductor | O/H Conductor | 146 | 80 | 195 | East | 7F4
131474 | 2015-05-30 | Loss Of Supply | Transmission Inadvertent | A loss of Hydro One supply on the C7BM affecting Centrepointe/Manordale DS station 8002 customers | None | None | 3441 | 13 | 746 | South | C7BM (Manordale MS - T1/T2)
131474 | 2015-05-30 | Loss Of Supply | Transmission Inadvertent | A loss of Hydro One supply on the C7BM affecting Centrepointe/Manordale DS station 8002 customers | None | None | 4561 | 13 | 988 | South | C7BM (Centrepointe MS - T1/T2)
131475 | 2015-05-30 | Adverse Weather | Extreme Wind | Adverse weather caused outage to radial line. | None | None | 2 | 220 | 7 | West | 43F3
131476 | 2015-05-30 | Loss Of Supply | Transmission Planned | planned outage for hydro one maintenance at South March TS. | None | None | 2 | 413 | 14 | West | A9M3
131477 | 2015-05-30 | Loss Of Supply | Transmission Planned | to allow hydro one to perform maintenance on the A9M5-E and install new pole at south march TS. | None | None | 2 | 457 | 15 | West | A9M4
131478 | 2015-05-31 | Defective Equipment | Defective Equipment/ Material | Transformer #X5732 opened up due to lead @ top of switch fell out/broke off | O/H Switchgear | Inline Switch | 4 | 92 | 6 | South | 180F6
131479 | 2015-05-31 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X36463 opened up due to animal contact | None | None | 10 | 123 | 20 | West | JKGF4
131480 | 2015-05-31 | Defective Equipment | Defective Equipment/ Material | Transformer #X33027 opened up due to neutral in open buss was sagging into the 120v hot legs causing transfomer switch fuse to blow | O/H Conductor | O/H Conductor | 7 | 105 | 12 | South | 180F4
131481 | 2015-05-31 | Defective Equipment | Defective Equipment/ Material | Transformer #X27280 opened up due to broken porcelain switch | O/H Switchgear | Fused Cutout | 11 | 115 | 21 | East | UA07
131483 | 2015-06-01 | Foreign Interference | Wildlife (Bird/Animal) | Possible animal/Bird contact caused X37960 to blow. | O/H Transformer | O/H Transformer (1ph) | 11 | 65 | 12 | Central | SR09
131484 | 2015-06-01 | Scheduled Outage | Construction | S20630 to Eol was isolated to allow crew to preform pole reaplcement and transfer conductor. Walkley (UZ11). ID# 131484 | None | None | 73 | 180 | 219 | East | UZ11
131486 | 2015-06-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X38568 opened up due to contact from vines | O/H Switchgear | Fused Cutout | 5 | 91 | 8 | Central | TD06
131487 | 2015-06-01 | Scheduled Outage | Construction | Transformer #X25568 isolated by crew to run new secondary | None | None | 2 | 90 | 3 | Central | SM13
131488 | 2015-06-01 | Scheduled Outage | Maintenance | Transformer TP5135 at 323 Saddleridge was isolated to allow crew to repair leaking transformer. Cyrville CYRF3. ID# 131488 | None | None | 10 | 101 | 17 | East | CYRF3
131489 | 2015-06-01 | Scheduled Outage | Maintenance | Transformer #X28162 isolated by crew to replace the leads | None | None | 12 | 69 | 14 | Central | 505
131491 | 2015-06-01 | Scheduled Outage | Forced Switching | The village of Munster was interrupted during switching to transfer supply to Beckwith DS due to out of phase condition Munster (43F3). | None | Unknown \ Other | 278 | 2 | 9 | West | 43F3
131492 | 2015-06-01 | Defective Equipment | Electrical Failure | Blown arrester lead was found and cleared at 124 Dufferin. Circuit under holdoff when tripped. | O/H Conductor | Unknown \ Other | 57 | 37 | 35 | East | UG03
131494 | 2015-06-01 | Scheduled Outage | Maintenance | Transformer #X08553 isolated by crew to replace arrestor. | None | None | 1 | 45 | 1 | West | BECKF2
131495 | 2015-06-01 | Scheduled Outage | Maintenance | Transformer #X25749 isolated by crew to straighten pole | None | None | 9 | 110 | 16 | Central | SB10
131496 | 2015-06-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X31773 opened up due to tree contact | O/H Switchgear | Fused Cutout | 9 | 96 | 14 | Central | TW22
131497 | 2015-06-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X33903 opened up due to tree contact | O/H Switchgear | Fused Cutout | 6 | 146 | 15 | Central | TW22
131499 | 2015-06-01 | Scheduled Outage | Vegetation Management | Transformer #X23328 isolated by crew for forestry to remove tree | None | None | 17 | 91 | 26 | East | AP03
131500 | 2015-06-01 | Tree Contacts | Falling Tree | Transformer #X23326 opened up due to tree contact | O/H Switchgear | Fused Cutout | 15 | 229 | 57 | East | AP03
131502 | 2015-06-01 | Tree Contacts | Broken Branch | Transformer S27700 blew due to tree contact and was isolated for removal, Queens UQ07, ID # 131502 | O/H Transformer | O/H Transformer (1ph) | 12 | 318 | 64 | East | UQ07
131503 | 2015-06-02 | Defective Equipment | Defective Equipment/ Material | A9M1 and BRDF4 auto-reclosed and tripped due to an insulator pin breaking loose and causing the conductor to let go. The flashover also started a pole fire | Pole Attachement | Insulator | 49 | 122 | 100 | West | A9M1
131503 | 2015-06-02 | Defective Equipment | Defective Equipment/ Material | A9M1 and BRDF4 auto-reclosed and tripped due to an insulator pin breaking loose and causing the conductor to let go. The flashover also started a pole fire | Pole Attachement | Insulator | 693 | 10 | 116 | South | 200F1
131503 | 2015-06-02 | Defective Equipment | Defective Equipment/ Material | A9M1 and BRDF4 auto-reclosed and tripped due to an insulator pin breaking loose and causing the conductor to let go. The flashover also started a pole fire | Pole Attachement | Insulator | 1724 | 125 | 3592 | West | BRDF4
131504 | 2015-06-02 | Foreign Interference | Wildlife (Bird/Animal) | animal contact caused S23425 fuse to open and AA04 to auto reclose. | O/H Conductor | O/H Conductor | 78 | 117 | 152 | East | AA04
131505 | 2015-06-02 | Scheduled Outage | Maintenance | TB14 from S11511 to EOL isolated for insulator change. | None | Insulator | 5 | 33 | 3 | East | TB14
131506 | 2015-06-02 | Scheduled Outage | Construction | Transformer X39745 at 4013 Rideau Valley Dr. isolated by crew to install new pole | None | None | 2 | 133 | 4 | South | FAL03
131507 | 2015-06-02 | Scheduled Outage | Vegetation Management | To allow forestry crews to clear the O/H circuitry in this area. | None | None | 41 | 494 | 338 | South | 49F6
131508 | 2015-06-02 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32951 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 7 | 105 | 12 | Central | TD07
131510 | 2015-06-03 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to make emergency repairs to the O/H line & transformer cutout at the rear of 3 Vanson | None | None | 32 | 139 | 74 | South | 190F5
131513 | 2015-06-03 | Scheduled Outage | Construction | Transfer plant to new poles | None | None | 20 | 240 | 80 | Central | UW07
131514 | 2015-06-03 | Scheduled Outage | Construction | Transformer X30079 at 323 Clemow Ave isolated by crew to relocate service | None | None | 11 | 49 | 9 | Central | SB03
131515 | 2015-06-03 | Scheduled Outage | Construction | UZ11 overhead from S22442 to EOL isolated for pole replacement | None | Pole | 46 | 357 | 274 | East | UZ11
131516 | 2015-06-04 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to install a pole & transfer plant to the new pole | None | None | 1 | 253 | 4 | East | UT04
131518 | 2015-06-04 | Scheduled Outage | Vegetation Management | to remove dead ash trees from rear of 10 dante | None | None | 20 | 53 | 18 | South | 160F3
131519 | 2015-06-04 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to repair primary & secondary connections | None | Hot-Line Clamp | 4 | 41 | 3 | South | 180F4
131520 | 2015-06-04 | Defective Equipment | Defective Equipment/ Material | Transformer x27140 at 2012 Dorval Ave isolated by crew to replace broken cutout | O/H Switchgear | Fused Cutout | 6 | 131 | 13 | East | TB06
131521 | 2015-06-04 | Defective Equipment | Defective Equipment/ Material | Refused transformer X24280 at 1282 Algoma Rd.; Refuse 2 blown cut outs. May have been a ground fault | O/H Switchgear | Fused Cutout | 1 | 170 | 3 | East | 6F1
131522 | 2015-06-04 | Scheduled Outage | Maintenance | for contractor to install a main secondary switch for 120/240 service. | None | None | 1 | 300 | 5 | South | 190F2
131523 | 2015-06-04 | Defective Equipment | Electrical Failure | defective overhead transformer | O/H Transformer | O/H Transformer (3ph) | 2 | 215 | 7 | Central | UC10
131524 | 2015-06-05 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X09910 opened due to animal contact. Stafford (200F2). ID# 131524 | O/H Transformer | O/H Transformer (1ph) | 6 | 197 | 20 | South | 200F2
131525 | 2015-06-05 | Scheduled Outage | Construction | Transformer X23533 at 419 McArthur Ave isolated for crew to rearange plant on pole | None | None | 8 | 16 | 2 | East | SO07
131527 | 2015-06-05 | Defective Equipment | Mechanical Failure | burnt off line tap. | O/H Conductor | Ampact | 109 | 25 | 45 | East | AL03
131528 | 2015-06-05 | Scheduled Outage | Maintenance | replace leaking transformer TP4622. | None | Padmount (3ph) | 12 | 69 | 14 | East | 4801F8
131529 | 2015-06-05 | Foreign Interference | Vehicle | TP7331 was hit by vehicle, and blew fuse at SE8. | U/G Transformer | Padmount (1ph) | 22 | 178 | 65 | South | 190F5
131531 | 2015-06-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | Patrol found tree at 4160 Hawthorne (Customer owned) about a foot away from primary. | Unknown \ Other | Unknown \ Other | 2600 | 80 | 3467 | East | LTM01
131534 | 2015-06-06 | Foreign Interference | Wildlife (Bird/Animal) | Fuse G247R blew due to sanimal contact. Moutlon (8F1) ID# 131534. | None | None | 48 | 98 | 78 | East | 8F1
131535 | 2015-06-06 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING X33411 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 9 | 56 | 8 | Central | TW22
131537 | 2015-06-07 | Scheduled Outage | Construction | PT130 isolated to replace procelain switches. | None | Kiosk (3ph) | 12 | 104 | 21 | Central | TH01
131540 | 2015-06-07 | Unknown/Other | Unknown | Not yet known. | None | None | 1 | 63 | 1 | East | ELW06
131542 | 2015-06-07 | Defective Equipment | Electrical Failure | Suspected cable fault caused SE13-3 red phase fuse to open, Cyrville CYRF3, ID # 131542 | U/G Cable | Unknown \ Other | 7 | 7 | 1 | East | CYRF3
131542 | 2015-06-07 | Defective Equipment | Electrical Failure | Suspected cable fault caused SE13-3 red phase fuse to open, Cyrville CYRF3, ID # 131542 | U/G Cable | Unknown \ Other | 15 | 55 | 14 | East | CYRF3
131542 | 2015-06-07 | Defective Equipment | Electrical Failure | Suspected cable fault caused SE13-3 red phase fuse to open, Cyrville CYRF3, ID # 131542 | U/G Cable | Unknown \ Other | 63 | 37 | 39 | East | CYRF3
131542 | 2015-06-07 | Defective Equipment | Electrical Failure | Suspected cable fault caused SE13-3 red phase fuse to open, Cyrville CYRF3, ID # 131542 | U/G Cable | Unknown \ Other | 109 | 56 | 102 | East | CYRF3
131544 | 2015-06-07 | Defective Equipment | Electrical Failure | Defective cut out caused fuses at S29608 to open. Clyde (UC02) | O/H Switchgear | Fused Cutout | 1 | 253 | 4 | Central | UC02
131546 | 2015-06-08 | Scheduled Outage | Construction | Transformers K505, K507, K508 and K509 isolated to upgrade and remove asbestos, Woodroffe UW02, ID # 131546 | None | None | 66 | 211 | 232 | Central | UW02
131547 | 2015-06-09 | Scheduled Outage | Construction | At 8:36am crews isolated K516,K515,K514,K513 and K512 to upgrade transformers and remove asbestos. 80 customers affected. Woodroffe UW02 ID#131547 | None | None | 80 | 262 | 349 | Central | UW02
131548 | 2015-06-09 | Scheduled Outage | Maintenance | At 10:38am crews isolated VT241 to allow metering to make repairs. Lincoln Heights (5409) ID#131548 | None | None | 1 | 105 | 2 | Central | 5409
131549 | 2015-06-09 | Scheduled Outage | Vegetation Management | At 8:55am 25 customers were affected to allow tree crews to remove a dead ash tree in front of 29 Arlington. Florence (UF08) ID# 131549 | None | None | 25 | 258 | 108 | Central | UF08
131550 | 2015-06-09 | Scheduled Outage | Construction | At 09:05am V472 at 257 Lisgar was isolated for cable replacement. Gladstone (UX10) ID# | None | None | 1 | 205 | 3 | Central | UX10
131551 | 2015-06-09 | Foreign Interference | Wildlife (Bird/Animal) | squirrel contact blew an arrestor and a line fuse. | Pole Attachement | Arrester | 25 | 125 | 52 | Central | UN04
131552 | 2015-06-10 | Scheduled Outage | Maintenance | Isolation of TP3223 to remove sand from transformer base. | None | Padmount (1ph) | 10 | 160 | 27 | West | BRDF1
131553 | 2015-06-10 | Scheduled Outage | Maintenance | At 9:56am crews isolated V856 to allow contractor to perform maintenance. (Eastview) UT03 ID#131553 | None | None | 54 | 129 | 116 | East | UT03
131555 | 2015-06-10 | Scheduled Outage | Maintenance | At 09:16am crews isolated V227 to change the S21899 RWB and S17397 RWB cutouts. Urbandale (AE04) ID#131555 | None | None | 179 | 113 | 337 | East | AE04
131556 | 2015-06-10 | Scheduled Outage | Construction | At 08:50am crews isolated K503,K504, K506,K510 and K511 to upgrade kiosks anf remove asbestos. Woodroffe (UW02) ID#131556 | None | None | 72 | 292 | 350 | Central | UW02
131557 | 2015-06-10 | Scheduled Outage | Construction | Leaking Transformer on the pole | None | None | 4 | 85 | 6 | Central | SB03
131558 | 2015-06-10 | Scheduled Outage | Construction | At 08:47am crews isolated UZ11 from TEMP106 to end of line to intall new poles with a crane. Walkley UZ11 ID#131558 | None | None | 20 | 390 | 130 | East | UZ11
131560 | 2015-06-11 | Scheduled Outage | Vegetation Management | Transformer X36507 was isolated to allow crew to remove tree from services. Epworth (58F1) ID# 131560. | None | None | 6 | 81 | 8 | South | EPWF1
131562 | 2015-06-11 | Scheduled Outage | Forced Switching | At 08:40am crews had a forced outage due to an out of phase conditon affecting 198 customers. Work is part of project # 92008877. Terry Fox (TFXF5) ID#131562 | None | None | 198 | 35 | 116 | West | TFXF5
131563 | 2015-06-11 | Scheduled Outage | Forced Switching | At 11:37am crews had a forced outage due to an out of phase conditon affecting 198 customers. Work is part of project # 92008877. Terry Fox (TFXF5) ID#131563 | None | None | 198 | 20 | 66 | West | TFXF5
131564 | 2015-06-11 | Scheduled Outage | Construction | At 8:02am crews isolated a section of V11F2 to replace poles and upgrade the overhead. Casselman V11F2. (Casselman) V11F2 ID#131564 | None | None | 8 | 331 | 44 | East | V11F2
131565 | 2015-06-11 | Scheduled Outage | Vegetation Management | At 08:53am crews isolated a white phase section of the 200F3 between S396 and S394 for tree trimming. Stafford DS (200F3) ID#131565 | None | None | 25 | 382 | 159 | South | 200F3
131566 | 2015-06-11 | Scheduled Outage | Construction | At 11:07am crews isolated TE1402 to replace a defective transformer. Jockvale (145F2) ID#131566 | None | None | 5 | 145 | 12 | South | 145F2
131567 | 2015-06-11 | Scheduled Outage | Construction | Transformer #X25747 isolated by crew for O/H re-configuration | None | None | 9 | 80 | 12 | Central | SB10
131568 | 2015-06-11 | Unknown/Other | Unknown | Fused switch S417 blue phase and transformer X39537 fuse were found blown. No cause found. S417 was broken when removed and no replacement found, circuit dumped so that crew could jumper out fuse. Stafford Rd (200F2) ID# 131568. | Unknown \ Other | Unknown \ Other | 25 | 383 | 160 | South | 200F2
131568 | 2015-06-12 | Unknown/Other | Unknown | Fused switch S417 blue phase and transformer X39537 fuse were found blown. No cause found. S417 was broken when removed and no replacement found, circuit dumped so that crew could jumper out fuse. Stafford Rd (200F2) ID# 131568. | Unknown \ Other | Unknown \ Other | 475 | 3 | 24 | South | 200F2
131569 | 2015-06-12 | Scheduled Outage | Vegetation Management | TD05 from S18662 to EOL isolated for tree removal. Lincoln Heights (TD05) | None | O/H Conductor | 14 | 140 | 33 | Central | TD05
131570 | 2015-06-12 | Scheduled Outage | Construction | Tx 1135 was isolated to replace leaking transformer & perform soil remediation. Bridlewood BRDF3. ID#131570 | None | Padmount (3ph) | 1 | 598 | 10 | West | BRDF3
131571 | 2015-06-13 | Tree Contacts | Broken Branch | Broken tree branch caused G303W to blow. Leitrim 249F4. ID#131571. | None | None | 78 | 95 | 124 | East | LTM04
131573 | 2015-06-13 | Scheduled Outage | Construction | customer installing HRG system. | None | None | 1 | 93 | 2 | East | 7F1
131574 | 2015-06-13 | Foreign Interference | Wildlife (Bird/Animal) | Crew resagged buss; open wire bus wrapped together due to bird contact on the neutral of buss | O/H Transformer | O/H Transformer (1ph) | 9 | 68 | 10 | East | UB04
131575 | 2015-06-13 | Tree Contacts | Tree Growth/ Untrimmed Tree | 24/7 refused transformer X39647 at 4075 Twin Elm Rd - tree contact | O/H Transformer | O/H Transformer (3ph) | 1 | 213 | 4 | South | 145F3
131576 | 2015-06-13 | Scheduled Outage | Construction | Transformer X29010 at 3188 Swansea and X29011 at 3105 Swansea isolated so crew could rearrange plant | None | None | 1 | 352 | 6 | East | 2206
131577 | 2015-06-13 | Unknown/Other | Unknown | 24/7 refused transformer at 85 Lotta Ave. - no cause found | O/H Transformer | O/H Transformer (1ph) | 10 | 118 | 20 | South | EPWF1
131578 | 2015-06-13 | Defective Equipment | Electrical Failure | Cable fault between K628 and K629 | U/G Cable | Unknown \ Other | 35 | 122 | 71 | East | AP05
131579 | 2015-06-14 | Scheduled Outage | Construction | At 6:30am crews isolated VT594 to replace porcelain switches. Hinchey (TH01) ID#131579 | None | None | 4 | 139 | 9 | Central | TH01
131580 | 2015-06-14 | Foreign Interference | Wildlife (Bird/Animal) | animal contact - bird | O/H Conductor | O/H Conductor | 31 | 53 | 27 | East | 8F1
131582 | 2015-06-13 | Unknown/Other | Unknown | 24/7 crew refused transformer X35259 at 7449 Fallowfield Rd - no apparent cause found | O/H Transformer | O/H Transformer (1ph) | 1 | 183 | 3 | West | BECKF2
131584 | 2015-06-14 | Scheduled Outage | Construction | planned outage for switch replacement | None | None | 4 | 140 | 9 | Central | TH01
131585 | 2015-06-14 | Tree Contacts | Tree Growth/ Untrimmed Tree | blown transformer at 715 Industrial | O/H Transformer | O/H Transformer (3ph) | 4 | 54 | 4 | East | TB14
131585 | 2015-06-14 | Tree Contacts | Tree Growth/ Untrimmed Tree | blown transformer at 715 Industrial | O/H Transformer | O/H Transformer (3ph) | 1095 | 10 | 182 | East | TB14
131586 | 2015-06-14 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 crew refused transformer X17367 - bird contact | O/H Transformer | O/H Transformer (1ph) | 13 | 129 | 28 | East | 77M2
131588 | 2015-06-15 | Scheduled Outage | Construction | Construction. | None | None | 1 | 390 | 6 | Central | UX10
131589 | 2015-06-15 | Scheduled Outage | Construction | Construction. | None | None | 1 | 450 | 8 | Central | UX10
131590 | 2015-06-15 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X23273 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 5 | 46 | 4 | Central | TK2AC
131591 | 2015-06-15 | Scheduled Outage | Vegetation Management | tree trimming - storm hardning | None | None | 18 | 206 | 62 | Central | SR02
131592 | 2015-06-15 | Scheduled Outage | Maintenance | Trans #X5281 isolated by crew to check UG secondary | None | None | 6 | 10 | 1 | South | 180F3
131593 | 2015-06-15 | Scheduled Outage | Construction | isolated to allow crew to change phases. | None | None | 29 | 14 | 7 | Central | UW02
131594 | 2015-06-15 | Scheduled Outage | Construction | Transformer replacement. | None | None | 9 | 228 | 34 | East | BLKF1
131595 | 2015-06-15 | Scheduled Outage | Construction | replace cutout at S25885 | None | Fused Cutout | 3 | 95 | 5 | West | BECKF2
131597 | 2015-06-15 | Scheduled Outage | Construction | Transformers #X31467 and X31468 isolated for a switch replacement | None | None | 16 | 45 | 12 | Central | TH01
131598 | 2015-06-15 | Scheduled Outage | Maintenance | Transformer #GL3862 isolated by crew for an insulator replacement | None | None | 8 | 60 | 8 | East | 7F4
131599 | 2015-06-16 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change a transformer cut-out on transformer X08690 | None | Fused Cutout | 1 | 58 | 1 | West | BECKF2
131601 | 2015-06-16 | Defective Equipment | Mechanical Failure | RX2010 tripped open due to switch lead at switch 53 lying on crossarm. | O/H Switchgear | Fused Cutout | 94 | 34 | 53 | West | ALEXF3
131601 | 2015-06-16 | Defective Equipment | Mechanical Failure | RX2010 tripped open due to switch lead at switch 53 lying on crossarm. | O/H Switchgear | Fused Cutout | 2362 | 90 | 3543 | West | ALEXF3
131602 | 2015-06-16 | Scheduled Outage | Construction | Vault V511 was isolated to allow crew to de-commission vault and energize new TP10644. Overbrook (SO07) ID# 131602. | None | None | 1 | 120 | 2 | East | SO07
131603 | 2015-06-16 | Defective Equipment | Electrical Failure | UZ05 CB to trip under hold-off (for tree trimmers) due to burnt tap at 2988 Rankin. Walkley (UZ05) ID# 131603. | O/H Conductor | Hot-Line Clamp | 39 | 95 | 62 | East | UZ05
131603 | 2015-06-16 | Defective Equipment | Electrical Failure | UZ05 CB to trip under hold-off (for tree trimmers) due to burnt tap at 2988 Rankin. Walkley (UZ05) ID# 131603. | O/H Conductor | Hot-Line Clamp | 102 | 134 | 228 | East | UZ05
131603 | 2015-06-16 | Defective Equipment | Electrical Failure | UZ05 CB to trip under hold-off (for tree trimmers) due to burnt tap at 2988 Rankin. Walkley (UZ05) ID# 131603. | O/H Conductor | Hot-Line Clamp | 367 | 82 | 502 | East | UZ05
131605 | 2015-06-16 | Foreign Interference | Agricultural Equipment | REMOVED TREE BRANCH FROM DROP WIRE AT TRANSFORMER X29038 AND REFUSED SWITCH | O/H Transformer | O/H Transformer (1ph) | 1 | 92 | 2 | East | TB14
131607 | 2015-06-16 | Foreign Interference | Wildlife (Bird/Animal) | S108 blew open due to animal contact. Parkwood Hills (190F5). ID# 131607 | O/H Switchgear | Fused Cutout | 77 | 101 | 130 | South | 190F5
131608 | 2015-06-16 | Defective Equipment | Defective Equipment/ Material | TP7943 opened due to defective secondary cables. Billberry. ID# 131608 | Secondary \ Service | U/G Service | 16 | 770 | 205 | East | 77M5
131609 | 2015-06-16 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X24439 TO REPLACE SWITCH AND ARRESTER | None | None | 4 | 40 | 3 | East | 7F4
131611 | 2015-06-16 | Tree Contacts | Tree Growth/ Untrimmed Tree | The G190 B blew open due to tree growth in the O/H at X24153. Moulton (8F1) | O/H Switchgear | Fused Cutout | 35 | 109 | 64 | East | 8F1
131612 | 2015-06-16 | Scheduled Outage | Construction | UZ11 overhead from Temp 61 to end of line was isolated to allow crew to replace poles. Walkley (UZ11) ID# 131612. | None | None | 17 | 198 | 56 | East | UZ11
131613 | 2015-06-16 | Foreign Interference | Vehicle | A motor vehicle accident broke pole X13732 on Uplands Drive East of Alert Rd. On Call crews were required to replace the pole. | Pole | Pole | 0 | 217 | 0 | East | 4801F7
131613 | 2015-06-17 | Foreign Interference | Vehicle | A motor vehicle accident broke pole X13732 on Uplands Drive East of Alert Rd. On Call crews were required to replace the pole. | Pole | Pole | 1 | 198 | 3 | East | 4801F7
131614 | 2015-06-17 | Scheduled Outage | Vegetation Management | SR04 white phase from S19799 to end of line was isolated to allow crew to perform tree trimming. Riverdale (SR04) ID# 131614. | None | None | 38 | 273 | 173 | Central | SR04
131616 | 2015-06-17 | Foreign Interference | Wildlife (Bird/Animal) | Replaced blown fuse feeding transformer x34043 (Squirrel contact) | O/H Transformer | O/H Transformer (1ph) | 8 | 61 | 8 | Central | TD01
131617 | 2015-06-17 | Scheduled Outage | Construction | Transformer TP6933 was isolated to allow crew to upgrade transformer. Florence (UF06) ID# 131617. | None | None | 1 | 373 | 6 | Central | UF06
131619 | 2015-06-17 | Scheduled Outage | Construction | UW06 between S28304 and Temp 96 was isolated to allow crew to replace poles. Woodroffe (UW06) ID# 131619. | None | None | 29 | 402 | 194 | Central | UW06
131620 | 2015-06-17 | Scheduled Outage | Construction | Vault V471 was isolated to allow crew to replace cable and switches. Gladstone (UX10) ID# 131620. | None | None | 69 | 236 | 271 | Central | UX10
131622 | 2015-06-17 | Scheduled Outage | Construction | Transformer #X31464 isolated by crew for a switch replacement | None | None | 11 | 45 | 8 | Central | TH01
131623 | 2015-06-17 | Scheduled Outage | Construction | Transformers 20039 and 8856 on Forest Grove were isolated to allow crew to re configure primary cable loop. Richmond North (RHNF3). | None | None | 10 | 100 | 17 | West | RHNF3
131624 | 2015-06-17 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X24437 TO REPLACE SWITCH AND ARRESTER | None | None | 4 | 71 | 5 | East | 7F4
131625 | 2015-06-17 | Scheduled Outage | Construction | Transformer #X27888 isolated by crew for a pole replacement | None | None | 6 | 160 | 16 | East | UZ05
131626 | 2015-06-17 | Scheduled Outage | Construction | Transformer #X30490 isolated by crew for a switch replacement | None | None | 6 | 40 | 4 | Central | TH01
131627 | 2015-06-17 | Scheduled Outage | Maintenance | Transformer #X33531 isolated by crew to replace cut out and arrestor | None | None | 6 | 120 | 12 | Central | 303
131628 | 2015-06-17 | Scheduled Outage | Construction | Transfer Plant to new poles | None | None | 22 | 285 | 104 | Central | UW07
131629 | 2015-06-17 | Scheduled Outage | Construction | Vault V58 was isolated to allow crew to transfer cables to new pole and install new switch. Nepean (AB05) ID# 131629. | None | None | 14 | 232 | 54 | Central | AB05
131630 | 2015-06-17 | Scheduled Outage | Construction | Vault VT637 was isolated to allow crew to replace porcelain cutouts. Hinchey (TH01) ID# 131630. | None | None | 1 | 77 | 1 | Central | TH01
131631 | 2015-06-18 | Scheduled Outage | Maintenance | Transformer #X24438 isolated by crew for an insulator change | None | None | 5 | 95 | 8 | East | 7F4
131632 | 2015-06-18 | Scheduled Outage | Maintenance | TP7892 isolated from all Hydro Ottawa sources. To change leaking transformer. | None | Padmount (1ph) | 8 | 112 | 15 | East | 77M2
131633 | 2015-06-18 | Scheduled Outage | Construction | Transformer #X29828 isolated by crew for a service upgrade and to replace transformer | None | None | 9 | 130 | 20 | Central | TR09
131634 | 2015-06-18 | Scheduled Outage | Maintenance | Transformer #X24444 isolated by crew for an insulator change | None | None | 8 | 35 | 5 | East | 7F4
131635 | 2015-06-18 | Defective Equipment | Defective Equipment/ Material | Transformer #X27367 opened up due to a broken transformer switch | O/H Switchgear | Fused Cutout | 5 | 118 | 10 | East | UQ07
131636 | 2015-06-18 | Scheduled Outage | Construction | Transformer #55D1D-0388 isolated by crew to run a new secondary U/G service | None | None | 5 | 90 | 8 | Central | SM00
131637 | 2015-06-18 | Scheduled Outage | Construction | At 09:12am crews isolated V444 to allow crews to install new cables from pole to V444. Eastview (UT04) ID#131637 | None | None | 1 | 433 | 7 | East | UT04
131640 | 2015-06-18 | Tree Contacts | Broken Branch | tree caused G59R to open. | O/H Conductor | Unknown \ Other | 16 | 98 | 26 | East | BLKF5
131641 | 2015-06-18 | Tree Contacts | Falling Tree | tree fell on primary and broke the conductor and now tree is on the secondary | O/H Conductor | O/H Conductor | 10 | 129 | 22 | East | UG04
131641 | 2015-06-18 | Tree Contacts | Falling Tree | tree fell on primary and broke the conductor and now tree is on the secondary | O/H Conductor | O/H Conductor | 20 | 296 | 99 | East | UG04
131643 | 2015-06-19 | Tree Contacts | Falling Tree | tree fell on secondary | Secondary \ Service | O/H Service | 6 | 861 | 86 | Central | AD05
131643 | 2015-06-19 | Tree Contacts | Falling Tree | tree fell on secondary | Secondary \ Service | O/H Service | 11 | 30 | 6 | Central | AD05
131644 | 2015-06-19 | Tree Contacts | Falling Tree | tree on primary and on Fire, G476 opened. | O/H Conductor | O/H Conductor | 2 | 234 | 8 | East | LTM04
131647 | 2015-06-20 | Scheduled Outage | Construction | To upgrade the existing 300kVa transformer to 500kVA | None | None | 1 | 367 | 6 | East | LTM01
131649 | 2015-06-20 | Scheduled Outage | Maintenance | 13kV vault TN8678TR2 isolated for metering repair. Albion (2202) | None | Unknown \ Other | 1 | 277 | 5 | East | 2202
131650 | 2015-06-20 | Defective Equipment | Defective Equipment/ Material | S16847 blew opened. Crew patrolled circuit and found nothing. Leitrim (249F1) 3 customers were affected for 104 minutes. | O/H Switchgear | Fused Cutout | 3 | 104 | 5 | East | LTM01
131651 | 2015-06-21 | Scheduled Outage | Construction | VE61 was isolated to allow crew to render VE61 N.I.U and temporarily transfer secondaries from VE61 to TP10628. Epworth (58F4). 41 customers affected for 204 minutes | None | None | 41 | 204 | 139 | South | 130F1
131652 | 2015-06-21 | Adverse Environment | Fire | To allow Hydro Ottawa crews to cut clear the secondary service feeding 331 Iona St, due to a fire. | None | None | 4 | 21 | 1 | Central | UL05
131653 | 2015-06-21 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X09910 opened due to squirrel contact. Stafford (200F2). ID# 131653 | O/H Switchgear | Fused Cutout | 6 | 70 | 7 | South | 200F2
131656 | 2015-06-22 | Scheduled Outage | Maintenance | To prove spare duct from pole to vault. | None | None | 1 | 70 | 1 | Central | AB07
131657 | 2015-06-22 | Scheduled Outage | Construction | Cable replacement | None | None | 25 | 260 | 108 | East | AJ03
131660 | 2015-06-22 | Scheduled Outage | Vegetation Management | Tree removal. | None | None | 54 | 213 | 192 | Central | SR02
131661 | 2015-06-22 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32815 TO TRANSFER HYDRO P[LANT TO NEW POLE | None | None | 8 | 135 | 18 | Central | UW06
131662 | 2015-06-22 | Scheduled Outage | Vegetation Management | Tree triming | None | None | 9 | 355 | 53 | Central | SR02
131663 | 2015-06-22 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace the switch & arrstor | None | Fused Cutout | 12 | 26 | 5 | Central | TH01
131664 | 2015-06-22 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to replace transformer X27808 | None | O/H Transformer (1ph) | 8 | 180 | 24 | East | UZ11
131665 | 2015-06-22 | Scheduled Outage | Forced Switching | At 9:10pm crew opened transformer X23704 to allow for pole replacement. Overbrook (SO02) ID# 131665 | None | None | 9 | 194 | 29 | East | SO02
131666 | 2015-06-23 | Scheduled Outage | Construction | Transformer X29099 isolated for pole changes, Walkley UZ11, ID # 131 | None | None | 14 | 153 | 36 | East | UZ11
131668 | 2015-06-23 | Scheduled Outage | Construction | 33 Customers were affected on Maitland Ave to install poles by contractor. Circuit UW02 out of Woodroffe Sub | None | None | 33 | 394 | 217 | Central | UW02
131669 | 2015-06-23 | Scheduled Outage | Construction | V583 at 171 O'Connor was isolated to prove spare duct from pole to the vault affecting 163 customers on the UX10 out of Gladstone for 51 minutes. | None | None | 163 | 51 | 139 | Central | UX10
131672 | 2015-06-23 | Tree Contacts | Tree Growth/ Untrimmed Tree | UZ03 CB tripped under hold-off. Closed via SCADA and held. Line to be patrolled. | Unknown \ Other | Unknown \ Other | 332 | 28 | 155 | East | UZ03
131674 | 2015-06-23 | Tree Contacts | Tree Growth/ Untrimmed Tree | SCADA indicates UB07 tripped open, flagged on the red phase overcurrent instantaneous. To be patrolled | Unknown \ Other | Unknown \ Other | 380 | 16 | 101 | East | UB07
131675 | 2015-06-23 | Tree Contacts | Tree Growth/ Untrimmed Tree | SCADA indicates UZ03 tripped open again. Patrol found nothing. | Unknown \ Other | Unknown \ Other | 332 | 75 | 415 | East | UZ03
131677 | 2015-06-23 | Tree Contacts | Broken Branch | Switch 109B fuse blew due to tree contact at 12 Grierson, tree removed and switch refused and closed. Marhwood (MWDF3) ID# 131677. | None | None | 34 | 113 | 64 | West | MWDF3
131678 | 2015-06-23 | Tree Contacts | Broken Branch | Switch G739 WB phases fuses blew due to tree across both phases. Switch refused and closed by crew. Uplands (4801F8) ID# 131678. | None | None | 269 | 82 | 368 | East | 4801F8
131679 | 2015-06-23 | Tree Contacts | Other Vegetation | Transformer X33116 fuse blew due to vines covering the transformer. Lincoln Heights (TD05) ID# 131679. | None | None | 12 | 48 | 10 | Central | TD05
131680 | 2015-06-23 | Foreign Interference | Wildlife (Bird/Animal) | G190 fuse blew due to animal contact. Moulton 8F1 ID# 131680. | None | None | 35 | 292 | 170 | East | 8F1
131681 | 2015-06-23 | Tree Contacts | Tree Growth/ Untrimmed Tree | Burnt down primary over head required isolation for repair, Limebank 7F4. ID#131681 | O/H Conductor | O/H Conductor | 24 | 220 | 88 | East | 7F4
131681 | 2015-06-23 | Tree Contacts | Tree Growth/ Untrimmed Tree | Burnt down primary over head required isolation for repair, Limebank 7F4. ID#131681 | O/H Conductor | O/H Conductor | 34 | 197 | 112 | East | 7F4
131686 | 2015-06-23 | Defective Equipment | Mechanical Failure | Fuse S916 fuse blew open due to downed conductor. Parkwood Hills (190F2) ID# . | O/H Conductor | O/H Conductor | 164 | 243 | 664 | South | 190F2
131687 | 2015-06-23 | Tree Contacts | Broken Branch | Tree on primary required isolation to clear and repair, Parkwoodhills 190F5. ID#131687 | O/H Conductor | Unknown \ Other | 45 | 258 | 194 | South | 190F5
131688 | 2015-06-23 | Foreign Interference | Other Utilities | AM02 circuit tripped open due to insulation bringing down the overhead at 201 Bell St. Cambridge (AM02) ID# 131688. | None | None | 20 | 157 | 52 | Central | AM02
131688 | 2015-06-23 | Foreign Interference | Other Utilities | AM02 circuit tripped open due to insulation bringing down the overhead at 201 Bell St. Cambridge (AM02) ID# 131688. | None | None | 488 | 164 | 1334 | Central | AM02
131689 | 2015-06-23 | Adverse Weather | Extreme Wind | ELW11 CB tripped open during wind storm. To be patrolled. Ellwood (ELW11) ID# . | None | None | 3 | 8 | 0 | East | ELW11
131689 | 2015-06-23 | Adverse Weather | Extreme Wind | ELW11 CB tripped open during wind storm. To be patrolled. Ellwood (ELW11) ID# . | None | None | 17 | 7 | 2 | East | ELW11
131689 | 2015-06-23 | Adverse Weather | Extreme Wind | ELW11 CB tripped open during wind storm. To be patrolled. Ellwood (ELW11) ID# . | None | None | 137 | 13 | 30 | East | ELW11
131689 | 2015-06-23 | Adverse Weather | Extreme Wind | ELW11 CB tripped open during wind storm. To be patrolled. Ellwood (ELW11) ID# . | None | None | 161 | 14 | 38 | East | ELW11
131689 | 2015-06-23 | Adverse Weather | Extreme Wind | ELW11 CB tripped open during wind storm. To be patrolled. Ellwood (ELW11) ID# . | None | None | 163 | 23 | 62 | East | ELW11
131689 | 2015-06-23 | Adverse Weather | Extreme Wind | ELW11 CB tripped open during wind storm. To be patrolled. Ellwood (ELW11) ID# . | None | None | 757 | 90 | 1136 | East | ELW11
131690 | 2015-06-23 | Scheduled Outage | Construction | Isolated to allow crews to prove spare duct from pole to vault. 4KV vault V586 on AB07 circuit | None | None | 1 | 35 | 1 | Central | AB07
131692 | 2015-06-23 | Tree Contacts | Broken Branch | Transformer #X39476 opened up due to branch in wires | O/H Switchgear | Fused Cutout | 5 | 266 | 22 | Central | TR09
131693 | 2015-06-23 | Foreign Interference | Foreign Objects | At 8:40pm SCADA indicated that the SR00N and The SR03 breakers both opened. Crews patrolled circuits and believe cause to be kids with hellium ballons that flew into the lines. Riverside (SR03) ID#131693 | O/H Conductor | O/H Conductor | 283 | 85 | 401 | Central | SR03
131694 | 2015-06-23 | Tree Contacts | Broken Branch | Tree contacts caused S1088 to open. Queensway Carleton 160F3. ID#131694 | None | None | 22 | 225 | 82 | South | 160F3
131695 | 2015-06-24 | Tree Contacts | Broken Branch | Switch 310B opened to repalce switch & clear trees from primary line. Kanata 624F6. ID#131695. | None | None | 2 | 109 | 4 | West | 624F6
131696 | 2015-06-24 | Tree Contacts | Broken Branch | At 00:10 crew opened transformer X30089 to allow removal of trees in the overhead. Bronson (SB11) ID#131696 | O/H Conductor | O/H Conductor | 12 | 103 | 21 | Central | SB11
131699 | 2015-06-24 | Scheduled Outage | Vegetation Management | AD06 overhead section out of Shillington was isolated from TEMP 104 to End Of Line to remove a tree at 1313 Emperor affecting 109 customers for 325 mins | None | None | 109 | 325 | 590 | Central | AD06
131700 | 2015-06-24 | Scheduled Outage | Construction | UW02 overhead section along Maitland out of Woodroffe Sub isolated for pole installation by contractor affecting 44 customers | None | None | 44 | 479 | 351 | Central | UW02
131701 | 2015-06-24 | Scheduled Outage | Construction | V592 at 2383 Palm on the AJ03 out of Playfair isolated from Hydro Ottawa Sources by contractor to do some preliminary pole work affecting 1 customer for 246 minutes | None | None | 1 | 246 | 4 | East | AJ03
131702 | 2015-06-24 | Defective Equipment | Mechanical Failure | Blackburn BLKF8 auto-reclosed and fuse S16763 red phase blew due to cable fault between TP9459 and TP8542. BLKF3 also auto-reclosed during restoration attempts, Blackburn BLKF3/BLKF8 ID # 131702 | U/G Cable | Unknown \ Other | 0 | 101 | 0 | East | BLKF3
131702 | 2015-06-24 | Defective Equipment | Mechanical Failure | Blackburn BLKF8 auto-reclosed and fuse S16763 red phase blew due to cable fault between TP9459 and TP8542. BLKF3 also auto-reclosed during restoration attempts, Blackburn BLKF3/BLKF8 ID # 131702 | U/G Cable | Unknown \ Other | 73 | 64 | 78 | East | BLKF8
131702 | 2015-06-24 | Defective Equipment | Mechanical Failure | Blackburn BLKF8 auto-reclosed and fuse S16763 red phase blew due to cable fault between TP9459 and TP8542. BLKF3 also auto-reclosed during restoration attempts, Blackburn BLKF3/BLKF8 ID # 131702 | U/G Cable | Unknown \ Other | 129 | 177 | 381 | East | BLKF8
131702 | 2015-06-24 | Defective Equipment | Mechanical Failure | Blackburn BLKF8 auto-reclosed and fuse S16763 red phase blew due to cable fault between TP9459 and TP8542. BLKF3 also auto-reclosed during restoration attempts, Blackburn BLKF3/BLKF8 ID # 131702 | U/G Cable | Unknown \ Other | 970 | 39 | 630 | East | BLKF8
131702 | 2015-06-24 | Defective Equipment | Mechanical Failure | Blackburn BLKF8 auto-reclosed and fuse S16763 red phase blew due to cable fault between TP9459 and TP8542. BLKF3 also auto-reclosed during restoration attempts, Blackburn BLKF3/BLKF8 ID # 131702 | U/G Cable | Unknown \ Other | 1012 | 69 | 1164 | East | BLKF8
131702 | 2015-06-24 | Defective Equipment | Mechanical Failure | Blackburn BLKF8 auto-reclosed and fuse S16763 red phase blew due to cable fault between TP9459 and TP8542. BLKF3 also auto-reclosed during restoration attempts, Blackburn BLKF3/BLKF8 ID # 131702 | U/G Cable | Unknown \ Other | 1066 | 17 | 302 | East | BLKF8
131703 | 2015-06-24 | Scheduled Outage | Maintenance | To closely inspect 284P1 at 913 Greenbriar | None | None | 19 | 13 | 4 | Central | AK04
131704 | 2015-06-24 | Scheduled Outage | Vegetation Management | Transformer #X49882 isolated by crew to remove large branch from secondary buss | None | None | 4 | 30 | 2 | East | UT05
131705 | 2015-06-24 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X30441 opened up due to animal contact | O/H Switchgear | Fused Cutout | 11 | 137 | 25 | Central | SB02
131706 | 2015-06-24 | Scheduled Outage | Maintenance | Transformer #K00284 isolated by crew to reconnect secondary services | None | None | 19 | 13 | 4 | Central | AK04
131707 | 2015-06-24 | Unknown/Other | Unknown | Not yet known. | O/H Switchgear | Fused Cutout | 61 | 77 | 78 | South | 190F5
131709 | 2015-06-25 | Defective Equipment | Electrical Failure | Cable fault between SC80 and SC81 caused TM01 breaker to open | U/G Cable | XLPE | 493 | 1 | 8 | Central | 307
131709 | 2015-06-25 | Defective Equipment | Electrical Failure | Cable fault between SC80 and SC81 caused TM01 breaker to open | U/G Cable | XLPE | 1065 | 19 | 337 | Central | 307
131709 | 2015-06-25 | Defective Equipment | Electrical Failure | Cable fault between SC80 and SC81 caused TM01 breaker to open | U/G Cable | XLPE | 1544 | 3 | 77 | Central | 307
131709 | 2015-06-25 | Defective Equipment | Electrical Failure | Cable fault between SC80 and SC81 caused TM01 breaker to open | U/G Cable | XLPE | 1544 | 6 | 154 | Central | 307
131709 | 2015-06-25 | Defective Equipment | Electrical Failure | Cable fault between SC80 and SC81 caused TM01 breaker to open | U/G Cable | XLPE | 1544 | 45 | 1158 | Central | 307
131710 | 2015-06-25 | Unknown/Other | Unknown | The 84F5 circuit tripped under hold off. Circuit was closed via SCADA and held. Cause of outage remains under investigation. Manordale (84F5) | None | None | 1169 | 16 | 312 | South | 84F5
131711 | 2015-06-25 | Scheduled Outage | Construction | 822B Transformer Replacement. | None | Padmount (1ph) | 9 | 130 | 20 | West | MWDF2
131712 | 2015-06-25 | Scheduled Outage | Sectionalizing | S51-4 was opened to allow crew to sectonalise cable fault between S51-4 and S40-1. Bridlewood BRDF4. ID# 131712 | None | None | 52 | 84 | 73 | West | BRDF4
131713 | 2015-06-25 | Scheduled Outage | Construction | PT32 @ 10 HOLLAND AVE was isolated by the crew to allow them to replace the porcelin cutouts. | None | Insulator | 1 | 73 | 1 | Central | TH01
131715 | 2015-06-25 | Human Element | Switching Error | Crew was opening S1383 and the lead contacted the bracket causing a flash and S1381 fuse to blow. | O/H Switchgear | Unknown \ Other | 95 | 28 | 44 | South | 87F1
131716 | 2015-06-25 | Foreign Interference | Foreign Objects | REPLACED BLOWN FUSE FEEDING TRANSFORMER X36169 (FLAG WRAPPED AROUND BUSHING OF TRANSFORMER) | O/H Transformer | O/H Transformer (1ph) | 5 | 99 | 8 | South | 84F6
131717 | 2015-06-25 | Scheduled Outage | Vegetation Management | The O/H from pole X55c2B0101 at 456 Byron Ave was isolated to allow the crews do some tree trimming | O/H Conductor | Unknown \ Other | 10 | 341 | 57 | Central | AH07
131718 | 2015-06-25 | Unknown/Other | Unknown | Switch 103 W phase found blown. Crew patrolled and found transformer X39582 open. No cause found | None | None | 14 | 119 | 28 | West | 624F6
131720 | 2015-06-25 | Scheduled Outage | Construction | Transformer X47382 at 193 Lisgar St. isolated by contractor to replace a pole | None | None | 8 | 130 | 17 | Central | UX10
131721 | 2015-06-26 | Scheduled Outage | Vegetation Management | The UQ03 O/H from switch S21315 was isolated to allow a contractor remove a for tree @ 81 Pleasant Park | None | Unknown \ Other | 19 | 127 | 40 | East | UQ03
131722 | 2015-06-26 | Defective Equipment | Mechanical Failure | Blown egress cable pole pothead blew causing the breaker to trip, Shillington AD03, ID # 131722 | U/G Cable Attachement | Pothead | 476 | 60 | 476 | Central | AD03
131724 | 2015-06-26 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER K284 TO RECONNECT SERVICE TO PED 284P1 | None | None | 19 | 35 | 11 | Central | AK04
131726 | 2015-06-26 | Defective Equipment | Defective Equipment/ Material | 24/7 replaced broken cutout and changed 2 porceline cutouts at X31128 located at 244 Arlington Ave. | O/H Transformer | O/H Transformer (3ph) | 10 | 27 | 4 | Central | UF07
131728 | 2015-06-27 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X33083 opened up due to animal contact | O/H Switchgear | Fused Cutout | 3 | 154 | 8 | Central | TD07
131731 | 2015-06-28 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X32538 opened because of animal contact, Lincoln TD06, ID # 1317 | O/H Transformer | O/H Transformer (1ph) | 7 | 90 | 10 | Central | TD06
131732 | 2015-06-28 | Scheduled Outage | Construction | Tx 8272 isolated for replacement & to install bollards. Janet King 44F1. ID#131732. | None | Padmount (3ph) | 1 | 345 | 6 | West | 44F1
131733 | 2015-06-28 | Foreign Interference | Wildlife (Bird/Animal) | Transformer fuses opened causing G918R phase fuse to blow @ 1397 Maxime st. | O/H Switchgear | Fused Cutout | 103 | 45 | 77 | East | 8F3
131734 | 2015-06-28 | Tree Contacts | Falling Tree | Dead ash tree contacing O/H line at Long Island rd & Driscol caused S18183 R & B to open. W phase opened to isolate line & clear tree. Limebank LMBF5. ID#131734 | None | None | 147 | 125 | 306 | East | 7F4
131734 | 2015-06-28 | Tree Contacts | Falling Tree | Dead ash tree contacing O/H line at Long Island rd & Driscol caused S18183 R & B to open. W phase opened to isolate line & clear tree. Limebank LMBF5. ID#131734 | None | None | 301 | 63 | 316 | East | 7F4
131735 | 2015-06-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X35387 opened up due to defective switch | O/H Switchgear | Fused Cutout | 9 | 152 | 23 | Central | TD12
131736 | 2015-06-28 | Tree Contacts | Falling Tree | Transformer # X37913 opened due to tree in open secondary bus. Robin reports secondary bus is now burning up. | Secondary \ Service | O/H Service | 9 | 60 | 9 | Central | UC03
131737 | 2015-06-28 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer X35964 opened to allow for secondary and neutral repair and clearing tree branches that caused the damage. Shillington AD07, ID # 131737 | O/H Conductor | O/H Conductor | 29 | 64 | 31 | Central | AD07
131738 | 2015-06-29 | Scheduled Outage | Construction | At 9:07am crews isolated K387 to install and terminate new cables. Playfair (AJ03) ID#131738 | None | None | 25 | 93 | 39 | East | AJ03
131739 | 2015-06-29 | Scheduled Outage | Vegetation Management | At 2:52pm crews opened S22505 blue phase to allow tree crew to remove a tree in the overhead primary. Beechwood (UB07) ID#131739 | None | None | 63 | 26 | 27 | East | UB07
131740 | 2015-06-29 | Scheduled Outage | Vegetation Management | A section of Munster 43F3 from pole X12242 to EOL was isolated for storm hardening. ID#131740. | None | None | 2 | 292 | 10 | West | 43F3
131742 | 2015-06-29 | Scheduled Outage | Construction | At 9:40am crew isolated P225 to relocate overhead. Queens (UQ02) ID#131742 | None | None | 1 | 224 | 4 | East | UQ02
131743 | 2015-06-29 | Foreign Interference | Customer Equipment | At 4:11pm crews isolated V578 at 2660 Norberry after a electrical contact in the customer's secondary room blew 2 fuses in our main vault. Walkley (UZ06) ID#131743 | None | None | 1 | 96 | 2 | East | UZ06
131747 | 2015-06-30 | Scheduled Outage | Maintenance | VT1442 @ 801 King Edward was isolated to the crews to take oil samples from the transformer | None | Unknown \ Other | 1 | 60 | 1 | Central | TR1UN
131750 | 2015-06-30 | Scheduled Outage | Construction | Transformer X24907 at 925 Garwood Ave. isolated by crew for pole replacement | None | None | 8 | 324 | 43 | East | UZ11
131751 | 2015-06-30 | Scheduled Outage | Construction | Transformer X24908 at 986 Walkley Rd. isolated by crew for pole replacement | None | None | 3 | 324 | 16 | East | UZ11
131752 | 2015-06-30 | Scheduled Outage | Construction | Transformer X31457 at 37 Huron Ave N isolated by crew for switch replacement | None | Fused Cutout | 5 | 44 | 4 | Central | TH01
131753 | 2015-06-30 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X48319 TO TRANSFER HYDRO PLANTE TO NEW POLE | None | None | 6 | 222 | 22 | Central | UW02
131754 | 2015-07-01 | Defective Equipment | Defective Equipment/ Material | 24/7 refused X35777 at 2090 Honeywell Ave. - no cause found | O/H Switchgear | Fused Cutout | 8 | 42 | 6 | Central | TD06
131755 | 2015-07-01 | Foreign Interference | Wildlife (Bird/Animal) | Field Operators refused transformer at 24 Madawaska Dr - animal interferrence, squirrel | O/H Transformer | O/H Transformer (1ph) | 4 | 132 | 9 | Central | TR09
131756 | 2015-07-01 | Adverse Weather | Extreme Wind | Secondary services wrapped together and burnt down in storm. | Secondary \ Service | O/H Service | 7 | 364 | 42 | South | EPWF4
131757 | 2015-07-02 | Foreign Interference | Wildlife (Bird/Animal) | Refused transformer X35231 at 7 Sweetnam Dr - cause, animal interferrence | O/H Switchgear | Fused Cutout | 8 | 132 | 18 | West | JKGF5
131758 | 2015-07-02 | Scheduled Outage | Construction | Transformer X33703 isolated by crew for switch replacement | None | None | 14 | 42 | 10 | Central | TH06
131759 | 2015-07-02 | Defective Equipment | Defective Equipment/ Material | defective arrester on S116 is causing the crossarm on Hydro Pole to catch on fire. | Pole Attachement | Arrester | 38 | 25 | 16 | East | V11F3
131760 | 2015-07-03 | Defective Equipment | Electrical Failure | 24/7 refused transformer 005479 at 1169 Murphy Side Rd - no cause found, voltage checked ok | O/H Transformer | O/H Transformer (1ph) | 1 | 178 | 3 | West | MWDF3
131761 | 2015-07-03 | Scheduled Outage | Construction | Transformer X34688 at 97 Smirle Ave. isolated by crew for switch replacement | None | Inline Switch | 10 | 72 | 12 | Central | TH01
131762 | 2015-07-03 | Scheduled Outage | Construction | Transformer X30489 at 107 Smirle Ave isolated by crew for switch replacement | None | Inline Switch | 10 | 29 | 5 | Central | TH01
131763 | 2015-07-05 | Scheduled Outage | Vegetation Management | QT125 customer owned substation at 1941 Robertson was isolated to allow contractor to clear brush from sustation enclosure. Nepean (22M28). 1 customer was affected for 181 minutes. | None | None | 1 | 181 | 3 | South | 22M28
131764 | 2015-07-05 | Foreign Interference | Wildlife (Bird/Animal) | raccoon contact at X32192 | O/H Transformer | O/H Transformer (1ph) | 14 | 48 | 11 | Central | TD01
131765 | 2015-07-06 | Scheduled Outage | Maintenance | V570 @ 153 Nepean was isolated by Brain Brooks for vault maintenance and to inspect the spare duct for future work. | None | Unknown \ Other | 92 | 114 | 175 | Central | AB07
131767 | 2015-07-06 | Defective Equipment | Electrical Failure | The 77M6 CB tripped due to flash in the SC2449. While restoring the load and isolating the SC2449 the 77M2 circuit tripped due to cold load pick up from the CS26844. Bilberry 77M6. ID# 131767 | U/G Switchgear | Gas-Insulated Dead Front | 68 | 57 | 65 | East | 77M6
131767 | 2015-07-06 | Defective Equipment | Electrical Failure | The 77M6 CB tripped due to flash in the SC2449. While restoring the load and isolating the SC2449 the 77M2 circuit tripped due to cold load pick up from the CS26844. Bilberry 77M6. ID# 131767 | U/G Switchgear | Gas-Insulated Dead Front | 552 | 12 | 110 | East | 77M6
131767 | 2015-07-06 | Defective Equipment | Electrical Failure | The 77M6 CB tripped due to flash in the SC2449. While restoring the load and isolating the SC2449 the 77M2 circuit tripped due to cold load pick up from the CS26844. Bilberry 77M6. ID# 131767 | U/G Switchgear | Gas-Insulated Dead Front | 1848 | 4 | 123 | East | 77M6
131767 | 2015-07-06 | Defective Equipment | Electrical Failure | The 77M6 CB tripped due to flash in the SC2449. While restoring the load and isolating the SC2449 the 77M2 circuit tripped due to cold load pick up from the CS26844. Bilberry 77M6. ID# 131767 | U/G Switchgear | Gas-Insulated Dead Front | 2988 | 2 | 100 | East | 77M2
131767 | 2015-07-06 | Defective Equipment | Electrical Failure | The 77M6 CB tripped due to flash in the SC2449. While restoring the load and isolating the SC2449 the 77M2 circuit tripped due to cold load pick up from the CS26844. Bilberry 77M6. ID# 131767 | U/G Switchgear | Gas-Insulated Dead Front | 4046 | 5 | 337 | East | 77M6
131767 | 2015-07-06 | Defective Equipment | Electrical Failure | The 77M6 CB tripped due to flash in the SC2449. While restoring the load and isolating the SC2449 the 77M2 circuit tripped due to cold load pick up from the CS26844. Bilberry 77M6. ID# 131767 | U/G Switchgear | Gas-Insulated Dead Front | 4652 | 25 | 1938 | East | 77M6
131767 | 2015-07-06 | Defective Equipment | Electrical Failure | The 77M6 CB tripped due to flash in the SC2449. While restoring the load and isolating the SC2449 the 77M2 circuit tripped due to cold load pick up from the CS26844. Bilberry 77M6. ID# 131767 | U/G Switchgear | Gas-Insulated Dead Front | 5204 | 49 | 4250 | East | 77M6
131768 | 2015-07-06 | Scheduled Outage | Maintenance | Transformer TE481 @ 6082 longleaf was isolated by the crew to remove sand from the base | None | Padmount (1ph) | 8 | 210 | 28 | East | CYRF3
131770 | 2015-07-06 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X30056 | None | None | 8 | 310 | 41 | Central | SB06
131771 | 2015-07-06 | Human Element | Switching Error | Unknown, cause under investigation. | None | None | 1380 | 13 | 299 | South | FAL01
131771 | 2015-07-06 | Human Element | Switching Error | Unknown, cause under investigation. | None | None | 2740 | 45 | 2055 | South | FAL01
131771 | 2015-07-06 | Human Element | Switching Error | Unknown, cause under investigation. | None | None | 6360 | 6 | 636 | South | FAL01
131771 | 2015-07-06 | Human Element | Switching Error | Unknown, cause under investigation. | None | None | 8130 | 51 | 6910 | South | FAL01
131771 | 2015-07-06 | Human Element | Switching Error | Unknown, cause under investigation. | None | None | 13773 | 63 | 14462 | South | FAL01
131772 | 2015-07-06 | Scheduled Outage | Construction | Transformer X33422 at 1297 Erindale Dr isolated by contractor to transfer plant | None | None | 6 | 252 | 25 | Central | UW02
131777 | 2015-07-09 | Scheduled Outage | Construction | To allow crew to set a new pole for future work. | None | None | 2 | 108 | 4 | West | 624F1
131778 | 2015-07-09 | Defective Equipment | Electrical Failure | REPLACE DEFECTIVE TRANS | O/H Transformer | O/H Transformer (1ph) | 17 | 205 | 58 | Central | TD06
131779 | 2015-07-09 | Scheduled Outage | Construction | secondary service work | None | None | 12 | 60 | 12 | East | TB15
131780 | 2015-07-09 | Unknown/Other | Unknown | G120 B fuse was faund blown crew patrolled line and couldn't find cause. | O/H Switchgear | Fused Cutout | 365 | 73 | 444 | East | 77M1
131781 | 2015-07-09 | Defective Equipment | Defective Equipment/ Material | The S3-3B phase tripped due to cable fault between TP6154B and 2543B on Varley Lane. South March (39F2). ID# 131781 | U/G Cable | XLPE | 1 | 14 | 0 | West | 39F2
131781 | 2015-07-09 | Defective Equipment | Defective Equipment/ Material | The S3-3B phase tripped due to cable fault between TP6154B and 2543B on Varley Lane. South March (39F2). ID# 131781 | U/G Cable | XLPE | 3 | 67 | 3 | West | 39F2
131782 | 2015-07-10 | Scheduled Outage | Construction | Replace a Leaker | None | None | 7 | 92 | 11 | South | 49F6
131784 | 2015-07-10 | Foreign Interference | Wildlife (Bird/Animal) | bird contact on 249F1 overhead at 3216 Blais caused S20370 to open. | None | None | 5 | 69 | 6 | East | LTM01
131786 | 2015-07-11 | Scheduled Outage | Construction | Overhead line section from S12971 isolated to allow crew to work on lowering streetlight heads, reconfigure feed to overhead and allow customer contractor to perform vault maintenance at VE78, Leitrim 249F1, ID # 131786 | None | None | 3 | 280 | 14 | East | LTM01
131788 | 2015-07-12 | Loss Of Supply | Transmission Inadvertent | Hydro 1 reports large bird got into the B bus at Hawthorne caused an outage to 48T7, Hawthorne 48T7B, ID # 131788 | None | None | 3 | 8 | 0 | East | 48M4
131788 | 2015-07-12 | Loss Of Supply | Transmission Inadvertent | Hydro 1 reports large bird got into the B bus at Hawthorne caused an outage to 48T7, Hawthorne 48T7B, ID # 131788 | None | None | 3880 | 8 | 517 | East | 48M3
131788 | 2015-07-12 | Loss Of Supply | Transmission Inadvertent | Hydro 1 reports large bird got into the B bus at Hawthorne caused an outage to 48T7, Hawthorne 48T7B, ID # 131788 | None | None | 5179 | 8 | 691 | East | 48M5
131789 | 2015-07-12 | Scheduled Outage | Construction | PC10A #0754 established at S17619 to replace porcelain cutouts, feeding PT80, 1 customer affected | None | None | 1 | 158 | 3 | Central | TH01
131790 | 2015-07-12 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 refused transformer X29894 at 310 Holmwood Ave. Cause found - bird | O/H Transformer | O/H Transformer (1ph) | 8 | 142 | 19 | Central | TR09
131791 | 2015-07-12 | Unknown/Other | Unknown | 24/7 refused transformer X40245 at 47 Ullswater Dr. No Cause found | O/H Transformer | O/H Transformer (1ph) | 9 | 105 | 16 | South | 200F1
131792 | 2015-07-12 | Defective Equipment | Mechanical Failure | The meter base at this address faulted due the secondary cables sagging and causing arcing across the jaws of the meter base | Secondary \ Service | Meter | 1 | 1034 | 17 | West | BRDF6
131793 | 2015-07-13 | Defective Equipment | Electrical Failure | RB fuses in secondary disconnect at VT867 opened due to defective dry core transformer. | Vault Equipment | Transformer | 6 | 626 | 63 | Central | 408
131794 | 2015-07-13 | Scheduled Outage | Maintenance | 65 customers affected for 147 minutes at 270 Somerset on the Slater Sub SA22 for contractor to prove ducts | None | None | 65 | 147 | 159 | Central | SA22
131795 | 2015-07-13 | Scheduled Outage | Maintenance | Pedestal inspection | None | None | 12 | 20 | 4 | East | 2207
131796 | 2015-07-13 | Scheduled Outage | Forced Switching | Customer Phase transfers | None | None | 34 | 3 | 2 | Central | UW02
131797 | 2015-07-13 | Scheduled Outage | Forced Switching | Customer Load Transfer | None | None | 32 | 4 | 2 | Central | UW02
131798 | 2015-07-13 | Scheduled Outage | Construction | Transformer #X24905 isolated by crew to transfer plant to new pole | None | None | 6 | 269 | 27 | East | UZ11
131799 | 2015-07-13 | Unknown/Other | Unknown | No Apparent Cause | Unknown \ Other | Unknown \ Other | 5263 | 11 | 965 | East | 4801F8
131800 | 2015-07-14 | Tree Contacts | Broken Branch | Tree branches caused transformer fuse to blow. | O/H Transformer | O/H Transformer (1ph) | 3 | 66 | 3 | West | 44F1
131801 | 2015-07-14 | Scheduled Outage | Construction | Pole replacement | None | None | 15 | 247 | 62 | Central | AB07
131802 | 2015-07-14 | Scheduled Outage | Construction | To allow crews to replace primary cable to vault. | None | Cable | 1 | 256 | 4 | Central | SA22
131803 | 2015-07-14 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X37158 TO RELOCATE TRIPLEX SERVICE | None | None | 4 | 75 | 5 | Central | UV03
131804 | 2015-07-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31978 TO REPLACE SECONDARY SERVICE | None | None | 12 | 46 | 9 | Central | SM12
131805 | 2015-07-14 | Scheduled Outage | Construction | To replace primary cable in V570. | None | Cable | 1 | 281 | 5 | Central | AB07
131806 | 2015-07-14 | Scheduled Outage | Construction | At 9:07am crew isolated Transformers 3421 and 3422 to allow crews to replace transformers. Terry Fox (TFXF6) ID#131806 | None | None | 13 | 123 | 27 | West | TFXF6
131807 | 2015-07-14 | Scheduled Outage | Maintenance | At 09:53am crews isolated TE1677W to allow crew to replace a leaking transformer. Billberry (77M6) ID# 131807 | None | None | 10 | 194 | 32 | East | 77M6
131808 | 2015-07-14 | Unknown/Other | Unknown | Not yet known. | None | None | 1 | 62 | 1 | Central | 507
131810 | 2015-07-14 | Defective Equipment | Defective Equipment/ Material | G Bell reports at Cartier and MacLaren the UX02 wires are wrapped together. | O/H Conductor | O/H Conductor | 278 | 83 | 385 | Central | UX02
131810 | 2015-07-14 | Defective Equipment | Defective Equipment/ Material | G Bell reports at Cartier and MacLaren the UX02 wires are wrapped together. | O/H Conductor | O/H Conductor | 361 | 51 | 307 | Central | UX05
131811 | 2015-07-14 | Adverse Environment | Flood | Vault VT179 had water leaking into the vault causing their CB1 to open. | Customer Owned | Customer-Owned | 1 | 444 | 7 | Central | 5404
131812 | 2015-07-14 | Tree Contacts | Tree Growth/ Untrimmed Tree | High wind caused a tree brach to make contact with overhead conductors. | O/H Conductor | O/H Conductor | 278 | 155 | 718 | Central | UX02
131812 | 2015-07-14 | Tree Contacts | Tree Growth/ Untrimmed Tree | High wind caused a tree brach to make contact with overhead conductors. | O/H Conductor | O/H Conductor | 361 | 154 | 927 | Central | UX05
131813 | 2015-07-14 | Tree Contacts | Broken Branch | Tree branch caused K344R fused cut out to break. | O/H Switchgear | Fused Cutout | 24 | 269 | 108 | East | AL10
131816 | 2015-07-15 | Scheduled Outage | Construction | Transformer #X30062 isolated by crew to transfer secondary | None | None | 7 | 185 | 22 | Central | SB06
131817 | 2015-07-15 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30572 TO TTRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 120 | 20 | Central | SA22
131818 | 2015-07-15 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30571 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 4 | 85 | 6 | Central | SA22
131819 | 2015-07-15 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30570 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 75 | 12 | Central | SA22
131820 | 2015-07-15 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X34445 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 315 | 52 | East | UZ11
131821 | 2015-07-15 | Defective Equipment | Defective Equipment/ Material | ISOLATED 3 PHASE OVERHEAD BANK X28029 TO REPAIR SECONDARY 600V LINE | Secondary \ Service | O/H Service | 2 | 95 | 3 | Central | 505
131822 | 2015-07-15 | Scheduled Outage | Construction | Replace primary cable to vault | None | None | 48 | 241 | 193 | Central | SA22
131823 | 2015-07-15 | Scheduled Outage | Construction | 1 customer affected at 190 O'Connor on the AB07 circuit out of Nepean Sub for contractor to Replace primary cable to vault. | None | None | 1 | 300 | 5 | Central | AB07
131824 | 2015-07-16 | Scheduled Outage | Vegetation Management | To allow the customer to remove trees from their O/H line. The O/H line is customer owned | None | None | 2 | 153 | 5 | West | 624F6
131825 | 2015-07-16 | Defective Equipment | Electrical Failure | 7F1 breaker open (under hold off) Blue phase cable fault found between G36B and SC3735. Some of LMBF7 load on 7F1 | U/G Cable | Unknown \ Other | 135 | 126 | 284 | East | 7F1
131825 | 2015-07-16 | Defective Equipment | Electrical Failure | 7F1 breaker open (under hold off) Blue phase cable fault found between G36B and SC3735. Some of LMBF7 load on 7F1 | U/G Cable | Unknown \ Other | 3967 | 8 | 529 | East | 7F1
131826 | 2015-07-16 | Scheduled Outage | Construction | Transformer #X27832 isolated by crew for a switch replacement | None | None | 12 | 44 | 9 | Central | TH06
131827 | 2015-07-16 | Foreign Interference | Wildlife (Bird/Animal) | G953 R phase found blown, cause was a crow. New fuse install power restored | O/H Conductor | Unknown \ Other | 40 | 137 | 91 | East | LTM04
131828 | 2015-07-16 | Scheduled Outage | Construction | Transformer #X27913 isolated by crew for a switch replacement | None | None | 10 | 64 | 11 | Central | TH06
131830 | 2015-07-16 | Scheduled Outage | Construction | Transformer #X32163 isolated by crew to replace a service | None | None | 8 | 45 | 6 | Central | SM15
131831 | 2015-07-16 | Scheduled Outage | Construction | Transformer #X27840 isolated by crew for a switch replacement | None | None | 19 | 50 | 16 | Central | TH06
131832 | 2015-07-16 | Scheduled Outage | Maintenance | At 10:30pm, TE1324 was isolated to replace transformer and elbows. Blackburn (BLKF8) ID #131832 | None | Padmount (3ph) | 10 | 230 | 38 | East | BLKF8
131833 | 2015-07-17 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X31931 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 16 | 115 | 31 | Central | TD14
131835 | 2015-07-18 | Scheduled Outage | Maintenance | clean vault and torque connections | None | None | 1 | 138 | 2 | East | TA3AE
131839 | 2015-07-18 | Foreign Interference | Wildlife (Bird/Animal) | At 10:40 pm customers reported a outage to transformer X36034 in Richmond. Crews found a blown transformer fuse due to a bird. Richmond South DS (28F2) ID#131839 | O/H Transformer | O/H Transformer (1ph) | 8 | 89 | 12 | West | 28F2
131842 | 2015-07-19 | Foreign Interference | Wildlife (Bird/Animal) | bird contact at 2240 Belcourt | O/H Transformer | O/H Transformer (1ph) | 17 | 181 | 51 | East | 77M6
131843 | 2015-07-19 | Defective Equipment | Electrical Failure | cable fault between TE919 and TE652 red phase on 8F1 circuit | U/G Cable | Unknown \ Other | 65 | 144 | 156 | East | 8F1
131845 | 2015-07-20 | Scheduled Outage | Construction | ISOLATED AND REPLACED SWITCH AND ARRESTER FEEDING TRANSFORMER X34105 | None | None | 12 | 50 | 10 | Central | TH01
131847 | 2015-07-20 | Scheduled Outage | Construction | ISOLATED AND REPLACED SWITCH AND ARRESTER FEEDING TRANSFORMER X34106 | None | None | 9 | 45 | 7 | Central | TH01
131848 | 2015-07-20 | Scheduled Outage | Construction | ISOLATED AND REPLACED SWITCH AND ARRESTER FEEDING TRANSFORMER X34108 | None | None | 14 | 60 | 14 | Central | TH01
131849 | 2015-07-20 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X34021 TO REPLACE SECONDARY CONNECTIONS | None | None | 7 | 45 | 5 | Central | UL04
131850 | 2015-07-20 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X24903 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 305 | 30 | East | UZ11
131851 | 2015-07-20 | Scheduled Outage | Construction | planned outage to allow crew to replace a pole and transfer plant. | None | None | 6 | 372 | 37 | South | FAL03
131852 | 2015-07-20 | Scheduled Outage | Construction | Transformer #X32818 isolated by crew to transfer plant | None | None | 8 | 21 | 3 | Central | UW06
131853 | 2015-07-20 | Scheduled Outage | Construction | Transformer #X32566 isolated by crew to transfer plant | None | None | 9 | 20 | 3 | Central | UW05
131854 | 2015-07-20 | Scheduled Outage | Construction | Transformer #X35139 isolated by crew to transfer plant | None | None | 9 | 16 | 2 | Central | UW06
131855 | 2015-07-20 | Scheduled Outage | Construction | Transformer #X33426 isolated by crew to transfer plant | None | None | 10 | 42 | 7 | Central | UW06
131856 | 2015-07-20 | Scheduled Outage | Construction | Transformer #X21529 isolated by crew to transfer plant | None | None | 8 | 18 | 2 | Central | UW06
131857 | 2015-07-20 | Scheduled Outage | Construction | Transformer #X33909 isolated by crew to transfer plant | None | None | 4 | 15 | 1 | Central | UW06
131858 | 2015-07-20 | Scheduled Outage | Construction | Transformer #X48750 isolated by crew to transfer plant | None | None | 17 | 36 | 10 | Central | UW06
131859 | 2015-07-20 | Scheduled Outage | Construction | Transformer #X33421 isolated by crew to transfer plant | None | None | 10 | 36 | 6 | Central | UW06
131860 | 2015-07-20 | Scheduled Outage | Forced Switching | X29597 isolated to replace leaking transformer | O/H Transformer | O/H Transformer (1ph) | 17 | 187 | 53 | East | UG07
131861 | 2015-07-21 | Scheduled Outage | Construction | V572 at 171 Nepean was isoated to allow crew to verify duct from riser to vault. Nepean (AB07) | None | None | 1 | 135 | 2 | Central | AB07
131862 | 2015-07-21 | Unknown/Other | Unknown | RE-FUSED SWITCH FEEDING X27110 | O/H Transformer | O/H Transformer (1ph) | 8 | 121 | 16 | East | TB14
131863 | 2015-07-21 | Scheduled Outage | Construction | REPLACED SWITCH AND ARRESTER FEEDING TRANSFORMER X34107 | None | None | 12 | 35 | 7 | Central | TH01
131865 | 2015-07-21 | Scheduled Outage | Construction | Transformer bus outage to Ecole Jean-Robert Gauthier to allow contractor to instll fit connection on the line side of the secondary main breaker. | None | None | 1 | 78 | 1 | East | LMBF7
131866 | 2015-07-21 | Scheduled Outage | Construction | Transformer #X06766 isolated by crew to replace switch and arrestor | None | None | 2 | 45 | 2 | West | MWDF1
131868 | 2015-07-21 | Scheduled Outage | Forced Switching | UZ02 RWB radial O/H from pole 54838-0320 going S to EOL was isolated for emergency tree removal by crane at 678 Walkley. Wlakley (UZ02) | None | None | 50 | 245 | 204 | East | UZ02
131869 | 2015-07-21 | Tree Contacts | Broken Branch | Transformer #X39476 opened up due to tree contact | O/H Switchgear | Fused Cutout | 5 | 64 | 5 | Central | TR09
131870 | 2015-07-22 | Defective Equipment | Electrical Failure | TB21 and TB24 opened due to SW131 switch gear flash over at 2020 Bantree. Russell TB2AL, 5301. ID# 1318170 | U/G Cable Attachement | Termination \ Stress Cone | 1 | 667 | 11 | East | TB2AL
131870 | 2015-07-22 | Defective Equipment | Electrical Failure | TB21 and TB24 opened due to SW131 switch gear flash over at 2020 Bantree. Russell TB2AL, 5301. ID# 1318170 | U/G Cable Attachement | Termination \ Stress Cone | 25 | 90 | 38 | East | 5301
131870 | 2015-07-22 | Defective Equipment | Electrical Failure | TB21 and TB24 opened due to SW131 switch gear flash over at 2020 Bantree. Russell TB2AL, 5301. ID# 1318170 | U/G Cable Attachement | Termination \ Stress Cone | 125 | 24 | 50 | East | TB2AL
131870 | 2015-07-22 | Defective Equipment | Electrical Failure | TB21 and TB24 opened due to SW131 switch gear flash over at 2020 Bantree. Russell TB2AL, 5301. ID# 1318170 | U/G Cable Attachement | Termination \ Stress Cone | 126 | 12 | 25 | East | TB2AL
131870 | 2015-07-22 | Defective Equipment | Electrical Failure | TB21 and TB24 opened due to SW131 switch gear flash over at 2020 Bantree. Russell TB2AL, 5301. ID# 1318170 | U/G Cable Attachement | Termination \ Stress Cone | 191 | 59 | 188 | East | TB2AL
131870 | 2015-07-22 | Defective Equipment | Electrical Failure | TB21 and TB24 opened due to SW131 switch gear flash over at 2020 Bantree. Russell TB2AL, 5301. ID# 1318170 | U/G Cable Attachement | Termination \ Stress Cone | 476 | 45 | 357 | East | TB2AL
131873 | 2015-07-22 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X37230 TO REMOVE VINES | None | None | 5 | 36 | 3 | South | EPWF3
131874 | 2015-07-22 | Scheduled Outage | Construction | Transformer #X24901 isolated by crew to transfer hydro plant | None | None | 8 | 290 | 39 | East | UZ11
131875 | 2015-07-22 | Tree Contacts | Broken Branch | The UV03 O/H line was isolated to allow the forestery dept remove a large limb of the three phase | O/H Conductor | O/H Conductor | 510 | 105 | 892 | Central | UV03
131876 | 2015-07-22 | Scheduled Outage | Construction | The O/H in the GLENMOUNT AVE and MAITLAND AREA was isolated by K Line to allow the crew to replace the poles and re-arrange some overhead and make repairs to K503 riser | None | O/H Conductor | 147 | 537 | 1316 | Central | UC05
131877 | 2015-07-23 | Scheduled Outage | Maintenance | Vault maintenance of V381 to clean and torque connection and trip test OCB. | None | Breaker \ Relay | 1 | 213 | 4 | Central | UX07
131878 | 2015-07-23 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X36092 AND REPLACED ALL SECONDARY CONNECTIONS | None | None | 24 | 125 | 50 | Central | TD05
131879 | 2015-07-23 | Scheduled Outage | Maintenance | At 09:47am crews isolated TE317 to replace defective transformer. Blackburn (BLKF8) ID#131879 | None | None | 14 | 155 | 36 | East | BLKF8
131880 | 2015-07-23 | Scheduled Outage | Construction | At 08:34am crews isolated TE921 to replace and upgrade cables . Manordale (84F5) ID#131880 | None | None | 11 | 476 | 87 | South | 84F5
131881 | 2015-07-23 | Scheduled Outage | Construction | Transformer X34905 at 908 Rand Ave. isolated by crew to transfer hydro plant | None | None | 6 | 423 | 42 | East | UZ11
131882 | 2015-07-23 | Scheduled Outage | Construction | VT615 was isolated to tie in new secondary to the Hydro Vault at the CB1 transformer bus | None | None | 1 | 849 | 14 | East | UZ11
131883 | 2015-07-24 | Unknown/Other | Unknown | At 7:49am SCADA indicates that the 160F3 breaker tripped open. Crews did not find the cause and breaker was closed via SCADA. QCH (160F3) ID#131883 | None | None | 53 | 11 | 10 | South | 160F3
131884 | 2015-07-24 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X25531 DUE TO BROKEN PRIMARY BUSHING | None | None | 10 | 120 | 20 | Central | SM12
131887 | 2015-07-24 | Scheduled Outage | Construction | At 08:35am crews isolated 624F1 from S1548 to end of line of construction. Kanata (624F1) ID#131887 | None | None | 2 | 311 | 10 | West | 624F1
131888 | 2015-07-24 | Defective Equipment | Defective Equipment/ Material | TP702 secondary isolated to replace derfective meter. | Secondary \ Service | Meter | 2 | 432 | 14 | East | 4801F8
131889 | 2015-07-24 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 refused transformer X14354 at 5575 Spratt Rd - outage cause, crow | O/H Transformer | O/H Transformer (1ph) | 1 | 111 | 2 | East | LMBF5
131891 | 2015-07-25 | Defective Equipment | Defective Equipment/ Material | Transformer X31504 at 845 Kingsmere opened. Crew patrolled line and found nothing. Transformer was refused and all customers restored. Woodroffe (TW22) | O/H Switchgear | Fused Cutout | 11 | 68 | 12 | Central | TW22
131893 | 2015-07-25 | Scheduled Outage | Construction | V721 isolated to replace riser cables. | None | None | 65 | 275 | 298 | Central | SA22
131894 | 2015-07-25 | Unknown/Other | Unknown | Transformer #X26917 opened up, crew could not find cause | O/H Switchgear | Fused Cutout | 12 | 120 | 24 | East | TB14
131895 | 2015-07-25 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X17642 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 6 | 150 | 15 | East | 4801F8
131896 | 2015-07-25 | Scheduled Outage | Construction | 5 transformers isolated (X30576, X30575, X30574, X30572 and X30570) by crew to re-arrange circuitry | None | None | 50 | 210 | 175 | Central | SA22
131897 | 2015-07-25 | Loss Of Supply | Transmission Inadvertent | Auto reclose on Hydro One E34M and M29C causing Terry Fox MTS to trip | None | None | 657 | 7 | 77 | West | BECKF2
131897 | 2015-07-25 | Loss Of Supply | Transmission Inadvertent | Auto reclose on Hydro One E34M and M29C causing Terry Fox MTS to trip | None | None | 3804 | 7 | 444 | West | TFXF1
131899 | 2015-07-26 | Scheduled Outage | Maintenance | Transformer #X32346 isolated by crew for a service upgrade | None | None | 8 | 94 | 13 | Central | AD06
131900 | 2015-07-26 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X13510 opened up due to bird contact | O/H Switchgear | Fused Cutout | 2 | 123 | 4 | East | 4801F8
131902 | 2015-07-26 | Scheduled Outage | Maintenance | Old S964 and TE1457 removed and new S24406 and TP10372 installed by Sproule as part of cable and transformer upgrade. | None | None | 6 | 264 | 26 | South | 84F6
131903 | 2015-07-26 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32186 opened up due to animal contact | O/H Switchgear | Fused Cutout | 1 | 137 | 2 | Central | TD01
131904 | 2015-07-26 | Defective Equipment | Defective Equipment/ Material | Cable fault between S341 and S12 caused the 24F5 to open. 24F5 was also carrying the 32F2 and 39F3 load at the time. | U/G Cable | XLPE | 209 | 6 | 21 | West | 24F5
131904 | 2015-07-26 | Defective Equipment | Defective Equipment/ Material | Cable fault between S341 and S12 caused the 24F5 to open. 24F5 was also carrying the 32F2 and 39F3 load at the time. | U/G Cable | XLPE | 211 | 6 | 21 | West | 24F5
131904 | 2015-07-26 | Defective Equipment | Defective Equipment/ Material | Cable fault between S341 and S12 caused the 24F5 to open. 24F5 was also carrying the 32F2 and 39F3 load at the time. | U/G Cable | XLPE | 457 | 4 | 30 | West | 24F5
131904 | 2015-07-26 | Defective Equipment | Defective Equipment/ Material | Cable fault between S341 and S12 caused the 24F5 to open. 24F5 was also carrying the 32F2 and 39F3 load at the time. | U/G Cable | XLPE | 1156 | 76 | 1464 | West | 24F5
131904 | 2015-07-26 | Defective Equipment | Defective Equipment/ Material | Cable fault between S341 and S12 caused the 24F5 to open. 24F5 was also carrying the 32F2 and 39F3 load at the time. | U/G Cable | XLPE | 1159 | 129 | 2492 | West | 24F5
131905 | 2015-07-27 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X29817 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 8 | 85 | 11 | Central | TR09
131906 | 2015-07-27 | Scheduled Outage | Construction | V224 isolated to change primary switches and customer vault rebuild. | None | Transformer | 3 | 33 | 2 | East | AJ05
131907 | 2015-07-27 | Scheduled Outage | Construction | To replace dip switches at pole | None | Fused Cutout | 1 | 75 | 1 | Central | TH01
131908 | 2015-07-27 | Scheduled Outage | Construction | Transformer X10445 at 2981 Shea Rd isolated by crew (Erin Murphy) to change insulators | None | None | 1 | 50 | 1 | West | RHNF1
131909 | 2015-07-27 | Foreign Interference | Vehicle | Refused transformer X09075, customer vehicle caught Bell wires causing fuse to open | O/H Switchgear | Fused Cutout | 1 | 122 | 2 | West | 28F1
131910 | 2015-07-27 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 crew refused transformer X07282 at 1040 Riddell Dr, cause - animal contact | O/H Switchgear | Fused Cutout | 1 | 184 | 3 | West | 624F6
131911 | 2015-07-27 | Defective Equipment | Electrical Failure | Fuse at transformer X24437 at 5248 Mclean opened, GR2 W also tripped as it was set on non reclosing for tree trimming crews. GR2 W restored, 24/7 crew jumpered secondary bus to restore customers. | O/H Transformer | O/H Transformer (1ph) | 4 | 189 | 13 | East | LMBF5
131911 | 2015-07-27 | Defective Equipment | Electrical Failure | Fuse at transformer X24437 at 5248 Mclean opened, GR2 W also tripped as it was set on non reclosing for tree trimming crews. GR2 W restored, 24/7 crew jumpered secondary bus to restore customers. | O/H Transformer | O/H Transformer (1ph) | 442 | 24 | 177 | East | LMBF5
131912 | 2015-07-27 | Lightning | Lightning | Lightning storm in area caused GR2 RWB to trip. | None | None | 754 | 40 | 503 | East | LMBF5
131915 | 2015-07-27 | Tree Contacts | Broken Branch | Storm in area caused large tree limb to contact primary line and G605B to open. On call crew required to remove tree limb. Limebank 7F4. ID#131915 | None | None | 17 | 257 | 73 | East | 7F4
131916 | 2015-07-27 | Defective Equipment | Mechanical Failure | Storm in area caused a broken pole & S15728W to open. On call crew required to make repairs. Limebank 7F4. ID#131916. | Pole | Pole | 27 | 457 | 206 | East | 7F4
131917 | 2015-07-28 | Scheduled Outage | Maintenance | 4 customers affected on the Manordale 84F1 as crews isolated TE1467 to replace the transformer at 8 Roselawn | None | None | 4 | 329 | 22 | South | 84F1
131918 | 2015-07-28 | Scheduled Outage | Maintenance | Overhead plant transfer at Fringewood and Hazeldean affecting 119 customers on the JKGF5 out of Janet King | None | None | 119 | 57 | 113 | West | JKGF5
131919 | 2015-07-28 | Scheduled Outage | Maintenance | Customer Vault Maintenance at V669 - 507 Riverdale affecting 80 customers on the SR08 out of Riverdale | None | None | 80 | 187 | 249 | Central | SR08
131920 | 2015-07-28 | Scheduled Outage | Maintenance | At 17:05, S713 to EOL & S715 to EOL was isolated to replace poles (Merivale (72F4) ID #131920 | None | None | 35 | 192 | 112 | South | 72F4
131922 | 2015-07-28 | Unknown/Other | Unknown | Crew found cut out open at KT292, transformer tested OK, fuse replaced & all power restored. Albion 2206. ID#131922 | U/G Transformer | Kiosk (1ph) | 24 | 170 | 68 | East | 2206
131923 | 2015-07-29 | Scheduled Outage | Construction | V571 isolated for pole replacement program & clearance to break out concrete curb. Nepean AB07. ID#131923 | None | None | 1 | 145 | 2 | Central | AB07
131924 | 2015-07-29 | Unknown/Other | Unknown | 24/7 refused transformer X33363 at 44 Harris Place. No cause found | O/H Switchgear | Fused Cutout | 12 | 103 | 21 | South | EPWF6
131930 | 2015-07-29 | Scheduled Outage | Vegetation Management | OH transformer X26876 was isolated for clearence for tree trimmers. 9 customers affected. Brookfiled (AF06) ID #131930 | None | None | 9 | 165 | 25 | East | AF06
131931 | 2015-07-29 | Scheduled Outage | Forced Switching | To transfer TP7200 from North Circuit to the South Circuit on Hazeldean. JKGF5 Janet King, 1 customer affected. | None | None | 1 | 146 | 2 | West | JKGF5
131932 | 2015-07-30 | Scheduled Outage | Construction | TE139 isolated for cable and transformer replacement. Beacon Hill (BCHF5) | None | Padmount (1ph) | 9 | 447 | 67 | East | BCHF5
131933 | 2015-07-30 | Scheduled Outage | Construction | TE3653 isolated to remove old primary cable. Limebank (LMBF7) | None | Padmount (1ph) | 13 | 29 | 6 | East | LMBF7
131934 | 2015-07-30 | Scheduled Outage | Construction | Transformer TP9606 @ 265 Mission was isolated to replace a leaking transformer, 8 other transformers were affected because of a radial feed. | None | Padmount (1ph) | 45 | 66 | 50 | West | 624F1
131935 | 2015-07-30 | Scheduled Outage | Maintenance | Transformer TE803 and TE805 was isolated to allow the crews replace a leaking transformer and a defective transformer | None | Padmount (1ph) | 16 | 187 | 50 | South | 84F1
131936 | 2015-07-30 | Scheduled Outage | Maintenance | VT177 @ 800 St Laurent was isolated to allow the contractor clean the vault,torque the connection and service the breaker | None | Breaker \ Relay | 1 | 265 | 4 | East | TO1UB
131937 | 2015-07-30 | Scheduled Outage | Construction | Transformer X35921 at 2974 Shea Rd and X35901 at 2981 Shea Rd. isolated by crew (Erin Murphy) for insulator change | None | None | 2 | 156 | 5 | West | RHNF1
131939 | 2015-07-30 | Scheduled Outage | Construction | REPLACING TRANSFORMER AND BASE | None | None | 9 | 450 | 68 | East | BCHF5
131947 | 2015-07-31 | Scheduled Outage | Construction | Transformer X36092 at 848 Norton Ave. isolated by crew for a transformer change. | None | None | 24 | 126 | 50 | Central | TD05
131948 | 2015-07-31 | Scheduled Outage | Construction | Transformer X46070 was isolated to allow crew to perform transformer upgrade. BECKF2. ID# 131948 | None | None | 1 | 66 | 1 | West | BECKF2
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 115 | 5 | 10 | West | 28F1
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 220 | 5 | 18 | West | 28F3
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 435 | 5 | 36 | West | BRDF7
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 870 | 5 | 72 | West | BRDF5
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 940 | 5 | 78 | West | BRDF6
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 1080 | 5 | 90 | West | 28F2
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 1115 | 5 | 93 | West | BRDF2
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 1465 | 5 | 122 | West | BRDF1
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 1575 | 19 | 499 | West | MWDF4
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 1850 | 5 | 154 | West | BRDF4
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 2105 | 19 | 667 | West | MWDF3
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 2260 | 19 | 716 | West | MWDF1
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 2685 | 19 | 850 | West | MWDF2
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 2950 | 5 | 246 | South | FAL01
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 4130 | 5 | 344 | South | FAL03
131949 | 2015-07-31 | Loss Of Supply | Transmission Inadvertent | S7M loss of supply from Hydro One, MWDT1 & MWDT2 high side and low side breakers tripped. | None | None | 5910 | 5 | 492 | South | FAL02
131951 | 2015-08-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | REPLACED BLOWN FUSE FEEDING TRANSFORMER X34224 | O/H Transformer | O/H Transformer (1ph) | 3 | 149 | 7 | Central | TW22
131952 | 2015-08-01 | Scheduled Outage | Maintenance | Secondary equipment maintenance. | None | Padmount (3ph) | 2 | 143 | 5 | Central | 2806
131954 | 2015-08-01 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X31483 | O/H Transformer | O/H Transformer (1ph) | 17 | 58 | 16 | Central | TH11-NIU
131955 | 2015-08-01 | Scheduled Outage | Maintenance | To remove asbestos , repair metering issues and take measurements for future CB1 replacemant. | None | Breaker \ Relay | 1 | 316 | 5 | Central | 611
131956 | 2015-08-01 | Lightning | Lightning | Transformer X35739 replaced due to suspected lightning strike making it defective. | None | None | 1 | 467 | 8 | West | BECKF2
131957 | 2015-08-02 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27550 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 14 | 64 | 15 | Central | TR1UN
131958 | 2015-08-02 | Scheduled Outage | Maintenance | overhead transformer X45608 was isolated to repair secondary connections | None | O/H Service | 15 | 35 | 9 | Central | UF07
131959 | 2015-02-08 | Loss Of Supply | Transmission Inadvertent | Loss of H1 supply E34M , suspected lightning strike | None | None | 0 | 252000 | 0 | West | TFXF2
131959 | 2015-02-08 | Loss Of Supply | Transmission Inadvertent | Loss of H1 supply E34M , suspected lightning strike | None | None | 0 | 252000 | 0 | West | TFXF3
131959 | 2015-08-02 | Loss Of Supply | Transmission Inadvertent | Loss of H1 supply E34M , suspected lightning strike | None | None | 1780 | 7 | 208 | West | TFXF4
131959 | 2015-08-02 | Loss Of Supply | Transmission Inadvertent | Loss of H1 supply E34M , suspected lightning strike | None | None | 1942 | 7 | 227 | West | TFXF6
131959 | 2015-08-02 | Loss Of Supply | Transmission Inadvertent | Loss of H1 supply E34M , suspected lightning strike | None | None | 4364 | 7 | 509 | West | TFXF5
131959 | 2015-08-02 | Loss Of Supply | Transmission Inadvertent | Loss of H1 supply E34M , suspected lightning strike | None | None | 5450 | 7 | 636 | West | TFXF1
131960 | 2015-08-03 | Defective Equipment | Mechanical Failure | transformer X32413 had the lead to the switch break, Lincoln TD01, ID # 131960 | O/H Conductor | Pigtail | 16 | 61 | 16 | Central | TD01
131961 | 2015-08-03 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at S20299 caused SC7949 CB3 to trip. Crew replaced damaged arrestors & power restored. Riverdale 503. ID#131961 | Pole Attachement | Arrester | 265 | 137 | 605 | Central | 503
131962 | 2015-08-03 | Scheduled Outage | Maintenance | At 12:03 crews isolated customer owned primary to allow crew to replace a tracking insulator. Beckwith (BeckF2) ID# 131962 | None | None | 1 | 31 | 1 | West | BECKF2
131965 | 2015-08-04 | Scheduled Outage | Construction | Pole replacement | None | None | 26 | 198 | 86 | South | 72F4
131966 | 2015-08-04 | Defective Equipment | Defective Equipment/ Material | VT855 at 980 Carling was isolated to allow metering crew to repair metering problem. Carling (305). ID# 131966 | Unknown \ Other | Unknown \ Other | 1 | 150 | 2 | Central | 306
131967 | 2015-08-04 | Unknown/Other | Unknown | Crew patrolled line, nothing found. Refused S294. | O/H Switchgear | Fused Cutout | 1 | 244 | 4 | East | 249F2
131968 | 2015-08-05 | Scheduled Outage | Vegetation Management | Tree removal | None | None | 24 | 217 | 87 | Central | TD01
131969 | 2015-08-05 | Scheduled Outage | Construction | Replace leaking transformer. | None | None | 11 | 170 | 31 | East | 77M6
131970 | 2015-07-09 | Defective Equipment | Defective Equipment/ Material | Defective relay tripped to 4801T3 protection. | Station Equipment | Unknown \ Other | 110 | 44 | 81 | East | 4801F7
131970 | 2015-07-09 | Defective Equipment | Defective Equipment/ Material | Defective relay tripped to 4801T3 protection. | Station Equipment | Unknown \ Other | 5173 | 15 | 1293 | East | 4801F8
131973 | 2015-08-05 | Defective Equipment | Defective Equipment/ Material | ground tail contacted live circuit, that caused it to trip. | O/H Conductor | O/H Conductor | 120 | 3 | 6 | Central | UW01
131974 | 2015-08-05 | Scheduled Outage | Construction | Patrick Brisson crew isolated transformer X30543 at 27 Stewart St. to install new triplex and perform maintenance on the transformer | None | None | 14 | 153 | 36 | Central | SK11
131975 | 2015-08-06 | Scheduled Outage | Maintenance | TE1499 isolated for cable injection | None | None | 8 | 193 | 26 | South | 84F1
131976 | 2015-08-06 | Scheduled Outage | Maintenance | Cable and Transformer Replacement on Tisdale | None | None | 21 | 467 | 163 | East | BCHF5
131977 | 2015-08-06 | Scheduled Outage | Maintenance | Transformer TE1314 isolated to change out leaker, Moulton 8F3, ID # 131977 | None | None | 12 | 233 | 47 | East | 8F3
131978 | 2015-08-06 | Scheduled Outage | Maintenance | VT378 was isolated for vault maintenance, 1 customer affected for 290 min. Lincoln Heights (5402) ID #131978 | None | None | 1 | 290 | 5 | Central | 5402
131979 | 2015-08-06 | Scheduled Outage | Construction | SB07 overhead to EOL isolated for conductor upgrade. Bronson (SB07). ID #131979 | None | None | 29 | 160 | 77 | Central | SB07
131980 | 2015-08-06 | Scheduled Outage | Maintenance | VT136 transforemr bus was isolated for metering repairs. King Edward (405) ID #131980 | None | None | 1 | 47 | 1 | Central | 405
131981 | 2015-08-06 | Scheduled Outage | Construction | Transformer P479 isolated to allow crew to re-arrange primary overhead, Overbrook SO07, ID # 131981 | None | None | 1 | 65 | 1 | East | SO07
131982 | 2015-08-06 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35790 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 14 | 58 | 14 | Central | TD06
131983 | 2015-08-06 | Scheduled Outage | Vegetation Management | Tree Removal and leaking transformer replacement | None | None | 7 | 135 | 16 | South | 200F2
131984 | 2015-08-06 | Scheduled Outage | Maintenance | At 10:26am crews isolated leaking transformer 731 to replace it with new TP11068. Bridlewood (BRDF6) ID#131984 | None | None | 1 | 616 | 10 | West | BRDF6
131985 | 2015-08-07 | Scheduled Outage | Vegetation Management | Overhead section isolated for storm hardening, Lincoln TD01, ID # 131985 | None | None | 22 | 337 | 124 | Central | TD01
131986 | 2015-08-07 | Foreign Interference | Customer Equipment | To make repairs to downed pole and damaged primary conductor. | None | None | 11 | 250 | 46 | West | 43F3
131987 | 2015-08-07 | Scheduled Outage | Construction | REPLACE POLE | None | None | 4 | 350 | 23 | East | UT12
131988 | 2015-08-07 | Scheduled Outage | Maintenance | TE3102 at 2436 Ogilvie was isolated on the BCHF5 out of Beacon for cable and transformer replacement affecting 11 customers for 412 mins. | None | None | 11 | 412 | 76 | East | BCHF5
131989 | 2015-08-07 | Scheduled Outage | Maintenance | Transformer #X25676 isolated by crew to clean up connections at the transformer | None | None | 15 | 10 | 2 | Central | SB10
131991 | 2015-08-08 | Scheduled Outage | Maintenance | TP4264 transformer bus isolated to allow contractor to perform secondary mtce. | None | Padmount (3ph) | 1 | 107 | 2 | West | BRDF3
131992 | 2015-08-08 | Scheduled Outage | Construction | Transformer X15998 at 2508 Del Zotto Ave. isolated by crew for service upgrade | None | None | 6 | 330 | 33 | East | LTM01
131993 | 2015-08-08 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 crew refused transformer X33859 at 77 Huron Ave. N - animal contact, squirrel | O/H Transformer | O/H Transformer (1ph) | 10 | 69 | 12 | Central | TH01
131994 | 2015-08-08 | Defective Equipment | Defective Equipment/ Material | Transformer X30981 was isolated to allow crew to crew to make repairs to burnt dowb open wires service .Augusta (UD04). ID# 131994 | Secondary \ Service | O/H Service | 11 | 27 | 5 | Central | UD04
131995 | 2015-08-08 | Defective Equipment | Electrical Failure | At 11:10 pm a cable fault on the BLKF8 white phase between S16763W and TE284W caused the BLKF8 to auto reclose and the S16763W to blow. Blackburn (BLKF8) ID#131995 | U/G Cable | XLPE | 14 | 14 | 3 | East | BLKF8
131995 | 2015-08-08 | Defective Equipment | Electrical Failure | At 11:10 pm a cable fault on the BLKF8 white phase between S16763W and TE284W caused the BLKF8 to auto reclose and the S16763W to blow. Blackburn (BLKF8) ID#131995 | U/G Cable | XLPE | 28 | 16 | 7 | East | BLKF8
131995 | 2015-08-08 | Defective Equipment | Electrical Failure | At 11:10 pm a cable fault on the BLKF8 white phase between S16763W and TE284W caused the BLKF8 to auto reclose and the S16763W to blow. Blackburn (BLKF8) ID#131995 | U/G Cable | XLPE | 41 | 23 | 16 | East | BLKF8
131995 | 2015-08-08 | Defective Equipment | Electrical Failure | At 11:10 pm a cable fault on the BLKF8 white phase between S16763W and TE284W caused the BLKF8 to auto reclose and the S16763W to blow. Blackburn (BLKF8) ID#131995 | U/G Cable | XLPE | 60 | 124 | 124 | East | BLKF8
131995 | 2015-08-08 | Defective Equipment | Electrical Failure | At 11:10 pm a cable fault on the BLKF8 white phase between S16763W and TE284W caused the BLKF8 to auto reclose and the S16763W to blow. Blackburn (BLKF8) ID#131995 | U/G Cable | XLPE | 177 | 121 | 357 | East | BLKF8
131996 | 2015-08-09 | Scheduled Outage | Construction | Transformer X24965 was isolated to allow crew to perform transformer upgrade. Bantree (AL06). ID# 131996 | None | None | 1 | 321 | 5 | East | AL06
131997 | 2015-08-09 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 refused the transformer at 3150 Dwyer Hill Rd, cause of outage due to bird - crow | O/H Transformer | O/H Transformer (1ph) | 1 | 201 | 3 | West | BECKF2
131998 | 2015-08-09 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 crew refused S23343 which supplied transformer X49707 at 318 Terry Fox Dr. - cause bird (crow) | O/H Transformer | O/H Transformer (1ph) | 1 | 64 | 1 | West | 624F6
131999 | 2015-08-10 | Scheduled Outage | Vegetation Management | S28295 to EOL was isoalted on Maple Lane to allow forestry crew to remove tree at 555 Maple Lane. Vaughn UG04 | None | None | 6 | 328 | 33 | East | UG04
132000 | 2015-08-10 | Scheduled Outage | Construction | Transformer #X27837 isolated by crew for a switch replacement | None | None | 13 | 60 | 13 | Central | TH06
132001 | 2015-08-10 | Scheduled Outage | Construction | Transformer #X27839 isolated by crew for a switch replacement | None | None | 21 | 60 | 21 | Central | TH06
132002 | 2015-08-10 | Scheduled Outage | Maintenance | Transformer #X35765 isolated by crew for a switch replacement | None | None | 1 | 131 | 2 | West | BECKF2
132003 | 2015-08-10 | Scheduled Outage | Construction | Transformer #X33727 isolated by crew for a PCB transformer replacement | None | None | 13 | 160 | 35 | Central | AH02
132004 | 2015-08-10 | Scheduled Outage | Maintenance | Pedestal fed from TE0062 isolated by crew to replace pedestal that was burning up | None | None | 4 | 80 | 5 | South | 160F1
132005 | 2015-08-10 | Scheduled Outage | Maintenance | Transformer #X11129 isolated by crew for a switch replacement | None | None | 1 | 60 | 1 | West | BECKF2
132007 | 2015-08-10 | Scheduled Outage | Maintenance | Replaced leaking transformer TE1143 | None | Padmount (1ph) | 12 | 190 | 38 | East | 77M6
132011 | 2015-08-10 | Scheduled Outage | Maintenance | Transformer TE720 @ 65 Shoreham Ave was isolated to allow the crew replace a broken insert | None | Elbow \ Insert | 17 | 128 | 36 | South | 84F1
132012 | 2015-08-10 | Scheduled Outage | Construction | Transformer #X35521 isolated by crew for a PCB transformer replacement | None | None | 6 | 105 | 10 | Central | AH14
132013 | 2015-08-10 | Scheduled Outage | Construction | Transformer #X32109 isolated by crew to set a new pole | None | None | 9 | 60 | 9 | Central | UW02
132014 | 2015-08-11 | Scheduled Outage | Construction | Removed P462 from service to install new TP10712 and S24585. Transformer upgrade from 150KVA to 300 kva. Outage time to remove temporary generator. | None | None | 2 | 11 | 0 | Central | UL06
132016 | 2015-08-11 | Tree Contacts | Falling Tree | 1 phase fell due to a large poplar tree that was touching the conductor | O/H Conductor | O/H Conductor | 45 | 134 | 100 | South | 180F4
132017 | 2015-08-11 | Defective Equipment | Mechanical Failure | Transformer #X34176 opened up due to defective equipment (fuse let go) | O/H Switchgear | Fused Cutout | 3 | 50 | 2 | Central | UL03
132018 | 2015-08-11 | Scheduled Outage | Construction | Transformer #X32106 isolated by crew to install new pole | None | None | 4 | 75 | 5 | Central | UW02
132019 | 2015-08-11 | Scheduled Outage | Construction | 72F4 from S16681 and S24390 to EOL isolated for pole replacment. Merivale (72F4) | None | None | 34 | 148 | 84 | South | 72F4
132020 | 2015-08-11 | Foreign Interference | Vehicle | Complete circuit out due excavator contact with bell wires that caused pole to break on AL10 circuit.Pole replace and all power restored. | Pole | Pole | 131 | 441 | 963 | East | AL10
132021 | 2015-08-11 | Lightning | Lightning | UC06 , TM28 (TM3UC) and TM32 (TM1UC), tripped, no reclose, suspected due to lightening storm | None | None | 5 | 15 | 1 | Central | TM3UC
132021 | 2015-08-11 | Lightning | Lightning | UC06 , TM28 (TM3UC) and TM32 (TM1UC), tripped, no reclose, suspected due to lightening storm | None | None | 139 | 12 | 28 | Central | UC06
132021 | 2015-08-11 | Lightning | Lightning | UC06 , TM28 (TM3UC) and TM32 (TM1UC), tripped, no reclose, suspected due to lightening storm | None | None | 960 | 16 | 256 | Central | TM1UC
132023 | 2015-08-11 | Lightning | Lightning | Small thunderstorm going through the region tripped the Kanata 624F6. | None | None | 1677 | 19 | 531 | West | 624F6
132027 | 2015-08-12 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to string new 27.6kV conductor | None | None | 12 | 345 | 69 | East | LMBF7
132028 | 2015-08-12 | Human Element | Switching Error | Hydro Ottawa line crews accidentally opened the 28F2 RWB recloser when attempting to block the recloser for a hold off | None | None | 1082 | 5 | 90 | West | 28F2
132029 | 2015-08-12 | Scheduled Outage | Construction | TP9701, TP9708 and TP9716 were isolated for primary switch, elbow and insert replacement. Cyrvill (CYRF4) | None | Padmount (1ph) | 42 | 277 | 194 | East | CYRF4
132030 | 2015-08-12 | Scheduled Outage | Construction | X34176 PCB transformer change and upgrade by Marty Link | None | None | 3 | 195 | 10 | Central | UL03
132031 | 2015-08-12 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to make the cable vetween TE443 & S883 N.I.U | None | None | 1 | 76 | 1 | South | EPWF1
132032 | 2015-08-12 | Defective Equipment | Electrical Failure | GR2 W phase opened under hold off protection. Cause not found at time of trip. Limebank (LMBF5) Later in evening, crew replaced burning up fuse at 938 River Road. (Called in by Ottawa Fire). | O/H Switchgear | Fused Cutout | 442 | 39 | 287 | East | LMBF5
132033 | 2015-08-12 | Scheduled Outage | Vegetation Management | Storm hardening project | None | None | 27 | 386 | 174 | East | UB07
132034 | 2015-08-12 | Scheduled Outage | Maintenance | UQ03 section of overhead isolated to isolated to remove N.I.U. section and rearrange new section. | None | None | 2 | 373 | 12 | East | UQ03
132035 | 2015-08-12 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFOMER X27152 TO REMOVE VINES | None | None | 4 | 15 | 1 | East | AE06
132036 | 2015-08-12 | Scheduled Outage | Maintenance | TE725 isolated to replace defective elebow and insert. Manordale (84F1) | None | Elbow \ Insert | 16 | 51 | 14 | South | 84F1
132037 | 2015-08-12 | Scheduled Outage | Construction | Pole Replacement. | None | Pole | 19 | 160 | 51 | South | 72F4
132038 | 2015-08-12 | Scheduled Outage | Construction | TV10625CHZ was isoalted to allow contractor to install trench cover plates. Russell (5312). | None | None | 1 | 208 | 3 | East | TB00
132039 | 2015-08-13 | Scheduled Outage | Maintenance | Transformer X47054 was isolated to allow crew to re-arrange secondaries. Nepean AB07 | None | None | 9 | 40 | 6 | Central | AB07
132041 | 2015-08-13 | Scheduled Outage | Construction | planned outage to relocate to a different circuit | None | None | 66 | 90 | 99 | West | ALEXF3
132042 | 2015-08-13 | Scheduled Outage | Construction | Elbow and insert replacement | None | None | 25 | 127 | 53 | East | CYRF4
132043 | 2015-08-13 | Scheduled Outage | Construction | Transformer #X25667 isolated by crew to transfer plant | None | None | 28 | 80 | 37 | Central | UJ07
132044 | 2015-08-13 | Scheduled Outage | Construction | Elbow and insert replacement | None | None | 32 | 120 | 64 | East | CYRF4
132045 | 2015-08-13 | Scheduled Outage | Vegetation Management | storm hardning | None | None | 25 | 154 | 64 | East | UB04
132047 | 2015-08-13 | Scheduled Outage | Construction | transfer plant | None | None | 1 | 210 | 4 | Central | UJ07
132048 | 2015-08-13 | Defective Equipment | Corrosion | primary lads to the transformer were defective. | O/H Transformer | Step Transformer (Rabbit) | 1 | 15 | 0 | East | 77M5
132049 | 2015-08-13 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X30482 | None | None | 7 | 80 | 9 | Central | SM03
132051 | 2015-08-14 | Scheduled Outage | Construction | xfmr TE487 isolated to allow crew to connect a new service. | None | None | 18 | 45 | 14 | South | 160F1
132052 | 2015-08-14 | Scheduled Outage | Maintenance | Transformer #X35279 isolated by crew to replace arrestor | None | None | 6 | 40 | 4 | West | ALEXF3
132053 | 2015-08-14 | Scheduled Outage | Construction | Transformer #X27607 isolated by crew to cut down triplex and replace switch | None | None | 23 | 65 | 25 | Central | UN04
132054 | 2015-08-14 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X34224 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 3 | 69 | 3 | Central | TW22
132055 | 2015-08-14 | Loss Of Supply | Transmission Inadvertent | Hydro One gas accumulation alarm on South March T1 | None | None | 28255 | 9 | 4238 | South | M32S (Nepean TS - T3/T4)
132057 | 2015-08-16 | Defective Equipment | Mechanical Failure | Blown cable termination | U/G Cable Attachement | Termination \ Stress Cone | 1 | 245 | 4 | South | 140F3
132058 | 2015-08-17 | Foreign Interference | Wildlife (Bird/Animal) | Vine over growth & a racoon caused transformer X27389 to open. | O/H Switchgear | Fused Cutout | 10 | 124 | 21 | East | AN04
132059 | 2015-08-17 | Scheduled Outage | Vegetation Management | Overhead section from S16128 blue isolated for storm hardening, Beechwood UB06, ID # 132059 | None | None | 7 | 191 | 22 | East | UB06
132060 | 2015-08-17 | Scheduled Outage | Maintenance | New Elbows and Inserts | None | None | 29 | 191 | 92 | East | CYRF4
132061 | 2015-08-17 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X34179 | None | None | 16 | 120 | 32 | Central | UL14
132062 | 2015-08-17 | Scheduled Outage | Construction | To transfer plant to new pole that supplies K534 and radial blue phase section of OH. Walkley (UZ11) ID #132062 | None | None | 41 | 160 | 109 | East | UZ11
132063 | 2015-08-17 | Scheduled Outage | Maintenance | Elbow and Inserts | None | None | 15 | 67 | 17 | East | CYRF4
132064 | 2015-08-17 | Defective Equipment | Electrical Failure | pole fire | Pole | Insulation Failure (Pole Fire) | 12 | 58 | 12 | East | 6F4
132064 | 2015-08-17 | Defective Equipment | Electrical Failure | pole fire | Pole | Insulation Failure (Pole Fire) | 82 | 311 | 425 | East | 6F4
132066 | 2015-08-18 | Scheduled Outage | Vegetation Management | Tree Trimming at rear of 41 Dunvegan. | None | None | 19 | 298 | 94 | East | UB04
132067 | 2015-08-18 | Scheduled Outage | Maintenance | Replace Elbows and inserts | None | Padmount (1ph) | 30 | 108 | 54 | East | CYRF4
132068 | 2015-08-18 | Scheduled Outage | Vegetation Management | Tree trimming on customer owned line. | None | Customer-Owned | 1 | 552 | 9 | West | 624F6
132069 | 2015-08-18 | Scheduled Outage | Construction | To replace defective transformer | None | Padmount (1ph) | 17 | 380 | 108 | South | 84F1
132070 | 2015-08-18 | Scheduled Outage | Maintenance | To allow crews to isolate transformer do to noise complaints, and check transformer and oil. | None | Padmount (3ph) | 1 | 10 | 0 | East | CYRF3
132071 | 2015-08-18 | Foreign Interference | Dig-In | To repair damaged secondary services. | U/G Transformer | Padmount (1ph) | 20 | 282 | 94 | East | BLKF3
132072 | 2015-08-18 | Scheduled Outage | Maintenance | Replace elbows and inserts | None | Padmount (1ph) | 30 | 91 | 46 | East | CYRF4
132074 | 2015-08-18 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X32343 (PCB OIL) | None | None | 12 | 100 | 20 | Central | AD07
132075 | 2015-08-18 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X25768 TO TRANSFER HYDRO PLANT | None | None | 13 | 105 | 23 | Central | SB04
132077 | 2015-08-19 | Foreign Interference | Dig-In | Dig-in on construction site at Waller & Daly | U/G Cable | PILC | 1 | 13 | 0 | Central | TK20
132077 | 2015-08-19 | Foreign Interference | Dig-In | Dig-in on construction site at Waller & Daly | U/G Cable | PILC | 682 | 67 | 762 | Central | TK20
132080 | 2015-08-19 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X23900 TO REPLACE SWITCH AND ARRESTER | None | None | 8 | 20 | 3 | Central | TH06
132081 | 2015-08-19 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X26047 TO REPLACE SWITCH AND ARRESTER | None | None | 14 | 70 | 16 | Central | TH06
132082 | 2015-08-19 | Scheduled Outage | Maintenance | Replace elbows and inserts | None | Padmount (1ph) | 30 | 110 | 55 | East | CYRF4
132085 | 2015-08-19 | Scheduled Outage | Vegetation Management | A section of Walkley UZ12 from S14132 was opened for tree removal at rear of 123 & 129 Dorothea. Storm hardening. ID#132085. | None | None | 20 | 369 | 123 | East | UZ12
132086 | 2015-08-19 | Scheduled Outage | Construction | V671 at 1725 Riverside was isolated to replace primary cables. Queens UQ03. ID#132086. | None | None | 144 | 198 | 475 | East | UQ03
132087 | 2015-08-19 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X39481 TO TRANSFER HYDRO PLANT | None | None | 10 | 165 | 28 | Central | TD01
132088 | 2015-08-19 | Scheduled Outage | Maintenance | Elbow and inserts replacment | None | Padmount (1ph) | 30 | 93 | 46 | East | CYRF4
132089 | 2015-08-19 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X21679 TO TRANSFER HYDRO PLANT | None | None | 30 | 145 | 72 | Central | SB06
132090 | 2015-08-19 | Scheduled Outage | Maintenance | Transformer #X41959 isolated by crew due to leads burning up | None | None | 2 | 18 | 1 | East | 77M5
132091 | 2015-08-19 | Scheduled Outage | Construction | Overhead section isolated for pole replacement, Merivale 72F4, ID # 132091 | None | Pole | 41 | 192 | 131 | South | 72F4
132092 | 2015-08-19 | Defective Equipment | Defective Equipment/ Material | Defective overhead transformer | O/H Transformer | O/H Transformer (1ph) | 7 | 266 | 31 | East | 249F2
132093 | 2015-08-20 | Scheduled Outage | Vegetation Management | Planned outage for tree trimming | None | None | 20 | 357 | 119 | East | UZ12
132094 | 2015-08-20 | Scheduled Outage | Construction | Transformers TP9707, TP9715, TP9721 and TP9722 were isolated for elbow and insert replacement. Cyrville (CYRF4) | None | Elbow \ Insert | 44 | 355 | 260 | East | CYRF4
132096 | 2015-08-20 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to cut in new TP10700, replace TP5857 & pull in new cable | None | Padmount (1ph) | 63 | 354 | 372 | South | FAL03
132097 | 2015-08-20 | Unknown/Other | Unknown | No apparent cause found | None | None | 22 | 248 | 91 | South | 160F3
132099 | 2015-08-20 | Tree Contacts | Falling Tree | W and R phases at G53 opened due to tree contact. Limebank (LMBF5) | O/H Conductor | O/H Conductor | 2 | 96 | 3 | East | LMBF5
132101 | 2015-08-20 | Scheduled Outage | Maintenance | PT64 at 2285 St Laurent isolated from Hydro Ottawa Sources on the 2203 out of Alibion Terminal for contractor to replace 800A main switch affecting 53 customers | None | None | 53 | 283 | 250 | East | 2203
132103 | 2015-08-20 | Tree Contacts | Falling Tree | Tree in wires caused white and blue phases at S25743 to open, red phase opened for isolation for tree removal, Kanata 624F6, ID # 132103 | O/H Conductor | O/H Conductor | 10 | 328 | 55 | West | 624F6
132105 | 2015-08-20 | Tree Contacts | Falling Tree | Tree Contact near 1969 Rideau back yard Auto Reclosed 7F4 and blew fuse G30 Red Phase Twice before dead tree on overhead was located | None | None | 1 | 24 | 0 | East | 7F4
132105 | 2015-08-20 | Tree Contacts | Falling Tree | Tree Contact near 1969 Rideau back yard Auto Reclosed 7F4 and blew fuse G30 Red Phase Twice before dead tree on overhead was located | None | None | 49 | 157 | 128 | East | 7F4
132105 | 2015-08-20 | Tree Contacts | Falling Tree | Tree Contact near 1969 Rideau back yard Auto Reclosed 7F4 and blew fuse G30 Red Phase Twice before dead tree on overhead was located | None | None | 49 | 241 | 197 | East | 7F4
132106 | 2015-08-20 | Tree Contacts | Falling Tree | Transformer X23830 opened to remove tree, Langs AP06, ID # 132106 | Secondary \ Service | O/H Service | 8 | 23 | 3 | East | AP06
132107 | 2015-08-20 | Defective Equipment | Mechanical Failure | Transformer X35634 was opened to replace defective cutout, Lincoln TD12, ID # 132107 | O/H Switchgear | Fused Cutout | 4 | 15 | 1 | Central | TD12
132108 | 2015-08-20 | Defective Equipment | Electrical Failure | Transformer X30550 opened to replace damaged 600v service, Nepean AB05, ID # 132108 | Secondary \ Service | O/H Service | 1 | 33 | 1 | Central | AB05
132109 | 2015-08-20 | Defective Equipment | Mechanical Failure | Transformer X24654 opened to repair services and replace cutout, Russell TB14, ID # 132109 | Secondary \ Service | O/H Service | 6 | 120 | 12 | East | TB14
132110 | 2015-08-21 | Defective Equipment | Electrical Failure | At 06:03am customers reported G517R was blown affecting 50 customers. Crews proceeded to find the cable fault and restore power to customers. Leitrim (249F4) ID#132110 | U/G Cable | PILC | 50 | 167 | 139 | East | LTM04
132111 | 2015-08-21 | Scheduled Outage | Vegetation Management | To allow forestry crews to trim trees | None | None | 50 | 301 | 251 | East | UZ12
132114 | 2015-08-21 | Unknown/Other | Unknown | No apparent cause found | Unknown \ Other | Unknown \ Other | 439 | 15 | 110 | East | UT12
132114 | 2015-08-21 | Unknown/Other | Unknown | No apparent cause found | Unknown \ Other | Unknown \ Other | 1075 | 15 | 269 | East | TO3UT
132115 | 2015-08-22 | Scheduled Outage | Maintenance | VT1442 @ 801 King Edward was isolated to replace transformers. King Edward TR1UN. ID#132115. | None | None | 1 | 163 | 3 | Central | TR1UN
132116 | 2015-08-22 | Scheduled Outage | Maintenance | Customer sub-station maintenance | None | Customer-Owned | 1 | 757 | 13 | West | A9M4
132120 | 2015-08-23 | Foreign Interference | Wildlife (Bird/Animal) | Crow contact caused transformer fuse to blow and a line fuse to blow. | O/H Transformer | O/H Transformer (1ph) | 56 | 145 | 135 | East | 7F4
132122 | 2015-08-23 | Scheduled Outage | Construction | core drilling and installing conduit in preparation for new vault installation. | None | None | 1 | 203 | 3 | Central | SA23
132123 | 2015-08-24 | Defective Equipment | Electrical Failure | Possible cable fault caused Albion TA05(TA3AF) to trip. Customers transferred to alternate source. ID#132123 | U/G Cable | Unknown \ Other | 1 | 6 | 0 | East | TA3AF
132123 | 2015-08-24 | Defective Equipment | Electrical Failure | Possible cable fault caused Albion TA05(TA3AF) to trip. Customers transferred to alternate source. ID#132123 | U/G Cable | Unknown \ Other | 6 | 27 | 3 | East | TA3AF
132123 | 2015-08-24 | Defective Equipment | Electrical Failure | Possible cable fault caused Albion TA05(TA3AF) to trip. Customers transferred to alternate source. ID#132123 | U/G Cable | Unknown \ Other | 8 | 22 | 3 | East | TA3AF
132123 | 2015-08-24 | Defective Equipment | Electrical Failure | Possible cable fault caused Albion TA05(TA3AF) to trip. Customers transferred to alternate source. ID#132123 | U/G Cable | Unknown \ Other | 238 | 10 | 40 | East | TA3AF
132123 | 2015-08-24 | Defective Equipment | Electrical Failure | Possible cable fault caused Albion TA05(TA3AF) to trip. Customers transferred to alternate source. ID#132123 | U/G Cable | Unknown \ Other | 415 | 35 | 242 | East | TA3AF
132124 | 2015-08-24 | Scheduled Outage | Construction | Cable and transformer replacement. | None | None | 8 | 590 | 79 | South | 84F6
132125 | 2015-08-24 | Scheduled Outage | Construction | To allow contractor to pull in secondaries. | None | None | 1 | 188 | 3 | East | LTM01
132126 | 2015-08-24 | Scheduled Outage | Maintenance | Transformer #X35990 isolated by crew to replace blown arrestor | None | None | 8 | 20 | 3 | South | EPWF2
132127 | 2015-08-24 | Scheduled Outage | Construction | Transformer #X23877 isolated by crew due to switch replacement | None | None | 17 | 55 | 16 | Central | TH06
132128 | 2015-08-24 | Scheduled Outage | Maintenance | Transformer #X34467 isolated by crew for a pole replacement | None | None | 15 | 130 | 32 | East | UG03
132129 | 2015-08-24 | Unknown/Other | Unknown | Transformer #X33116 opened up, crew unable to determine cause | O/H Switchgear | Fused Cutout | 12 | 20 | 4 | Central | TD05
132130 | 2015-08-24 | Tree Contacts | Tree Growth/ Untrimmed Tree | REPLACED BLOWN FUSE FEEDING TRANSFORMER X3876 | O/H Transformer | O/H Transformer (1ph) | 2 | 56 | 2 | South | 145F3
132131 | 2015-08-24 | Scheduled Outage | Construction | To install new poles. | None | None | 35 | 120 | 70 | South | 72F4
132132 | 2015-08-24 | Scheduled Outage | Forced Switching | 7F1 isolated from G593W to EOL to replace hot line clamp | O/H Conductor | Hot-Line Clamp | 12 | 17 | 3 | East | 7F1
132134 | 2015-08-25 | Scheduled Outage | Construction | At 10:00am crews isolated leaking transformer TP2540 to replace it. Bridlewood (BRDF1) ID#132134 | None | None | 8 | 517 | 69 | West | BRDF1
132135 | 2015-08-25 | Scheduled Outage | Construction | At 09:40am crews isolated TE443 to reconfigure cables. Epworth (58F1) ID#132135 | None | None | 1 | 348 | 6 | South | EPWF1
132136 | 2015-08-25 | Scheduled Outage | Construction | At 08:47am crews isolated TE667 to allow crews to replace transformer and cables. Manordale (84F6) ID#132136 | None | None | 18 | 431 | 129 | South | 84F6
132137 | 2015-08-25 | Scheduled Outage | Construction | Transformer X33006 @ 3201 Moodie was isolate to allow the crew upgrade the service from 10 Kva to a 25 Kva transformer | None | O/H Transformer (1ph) | 1 | 148 | 2 | South | FAL03
132138 | 2015-08-25 | Scheduled Outage | Construction | Transformer X37063 at 27 Caesar Ave. isolated by contractor for pole change | None | None | 3 | 180 | 9 | South | 72F4
132139 | 2015-08-25 | Scheduled Outage | Construction | Transformers X27887 at 2998 Linton Rd, X29089 at 2953 Southmore Dr. E and 1038 Walkley Rd isolated by crew for pole change | None | None | 25 | 405 | 169 | East | UZ11
132140 | 2015-08-25 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER NPTE0667 | None | None | 18 | 440 | 132 | South | 84F6
132141 | 2015-08-25 | Scheduled Outage | Construction | 72F4 from S400 to EOL and 180F6 between S637 and TEMP 123 isolated for pole replacment. | None | Pole | 4 | 150 | 10 | South | 72F4
132141 | 2015-08-25 | Scheduled Outage | Construction | 72F4 from S400 to EOL and 180F6 between S637 and TEMP 123 isolated for pole replacment. | None | Pole | 12 | 224 | 45 | South | 180F6
132142 | 2015-08-25 | Tree Contacts | Other Vegetation | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33388 (VINES AROUND TRANSFORMER) | O/H Transformer | O/H Transformer (1ph) | 4 | 53 | 4 | South | 190F5
132143 | 2015-08-26 | Scheduled Outage | Construction | X37822 was isolated for PCB transfomrer repalcement. Cambridge (AM02). ID# 132143 | None | O/H Transformer (1ph) | 1 | 109 | 2 | Central | AM02
132144 | 2015-08-26 | Scheduled Outage | Vegetation Management | S29048 to EOL was isolated to allow crew to perform tree trimming at rear of 1174 Whitemore. Woodroffe (UW07). ID# 132144 | None | None | 28 | 260 | 121 | Central | UW07
132145 | 2015-08-26 | Scheduled Outage | Construction | Transformer X31157 at 490 Bay St. isolated by crew to work in a pedestal | None | None | 12 | 36 | 7 | Central | UF07
132146 | 2015-08-26 | Scheduled Outage | Construction | Transformer X34116 at 202 Northwestern Ave. isolated by crew for porcelain switch replacement | None | None | 10 | 25 | 4 | Central | TH01
132147 | 2015-08-26 | Scheduled Outage | Construction | Transformer X23878 at 18 Pinehurst Ave. isolated by crew to replace porcelain switch replacement | None | None | 10 | 58 | 10 | Central | TH06
132148 | 2015-08-26 | Scheduled Outage | Construction | Transformer X31552 at 49 Bayswater Ave. isolated by crew for transformer change | None | None | 9 | 202 | 30 | Central | UJ03
132149 | 2015-08-26 | Scheduled Outage | Construction | Transformer X31157 at 490 Bay St. isolated by crew to work in a pedestal | None | None | 12 | 22 | 4 | Central | UF07
132150 | 2015-08-26 | Scheduled Outage | Construction | Transformer X31496 at 10 Oxford St. isolated by crew to replace cutout | None | None | 9 | 57 | 9 | Central | TH06
132151 | 2015-08-26 | Scheduled Outage | Construction | Transformer X33123 at 1110 Morrison Dr. isolated by crew to change PCB transformer | None | None | 1 | 135 | 2 | Central | UV07
132152 | 2015-08-26 | Scheduled Outage | Construction | Transformer X33858 at 53 Huron Ave. N isolated by crew for switch replacement | None | None | 6 | 59 | 6 | Central | TH01
132153 | 2015-08-26 | Scheduled Outage | Construction | TP10380 TE665)at 55 Bainbridge was isolated to allow the crews to replace the transformer and cables affecting 22 customers | None | Padmount (1ph) | 22 | 440 | 161 | South | 84F6
132154 | 2015-08-26 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER NPTE0665 | None | None | 22 | 435 | 160 | South | 84F6
132155 | 2015-08-26 | Scheduled Outage | Maintenance | The 72F4 O/H from S18523 @ 17 CAESAR AVE NEPEAN to EOL was isolated to allow the contractor replace poles | None | Pole | 30 | 185 | 92 | South | 72F4
132156 | 2015-08-27 | Scheduled Outage | Construction | K534 isolated to transfer cables to new pole. Walkley UZ11. ID#132156. | None | None | 17 | 337 | 95 | East | UZ11
132157 | 2015-08-27 | Scheduled Outage | Construction | A section of Walkley UZ11 from pole 54B4A-0132 to eol was isolated to transfer plant to new pole & perform tree trimming. ID#132157. | None | None | 24 | 337 | 135 | East | UZ11
132158 | 2015-08-27 | Scheduled Outage | Vegetation Management | A section of Woodroffe UW07 from S27031 to eol was isolated for tree trimming / storm hardening. ID#132158. | None | None | 55 | 305 | 280 | Central | UW07
132159 | 2015-08-27 | Scheduled Outage | Construction | Transformer X25768 at 522 Cambridge St S isolated by crew to transfer secondary to new transformer | None | None | 13 | 241 | 52 | Central | SB04
132160 | 2015-08-27 | Scheduled Outage | Construction | Transformer X35120 at 2345 Riley Ave. isolated by crew for PCB transformer change | None | None | 6 | 117 | 12 | Central | UV03
132161 | 2015-08-27 | Scheduled Outage | Construction | Transformer X27656 at 153 Roger Rd. isolated by crew to run a new service to a new house | None | None | 11 | 53 | 10 | East | UQ07
132162 | 2015-08-27 | Scheduled Outage | Construction | Transformer X34467 at 1 Noel St. isolated by crew to transfer secondary | None | None | 15 | 221 | 55 | East | UG03
132163 | 2015-08-27 | Scheduled Outage | Construction | At 09:15am crews isolated 8 transformers from TP9605 to allow crews to replace leaking transformer TP9606. Kanata MTS 624F1 ID#132163 | None | None | 53 | 267 | 236 | West | 624F1
132164 | 2015-08-27 | Scheduled Outage | Maintenance | SW107 isolated to replace leaking PT62 with new TP11074. Ellwood ELW13. ID#132164. | None | Padmount (3ph) | 1 | 201 | 3 | East | ELW13
132166 | 2015-08-28 | Scheduled Outage | Vegetation Management | Storm harding | None | O/H Conductor | 82 | 194 | 265 | South | 47F6
132170 | 2015-08-29 | Scheduled Outage | Construction | To de-commission VT259 and install new TV10659 | None | None | 2 | 7790 | 260 | Central | 5203
132171 | 2015-08-29 | Scheduled Outage | Construction | TP11075 isolated to install new base and grounding. | None | Padmount (1ph) | 1 | 260 | 4 | South | 200F2
132173 | 2015-08-30 | Scheduled Outage | Construction | ALEXF3 overhead between TEMP22, S13670 and S17095 isolated to transfer S12089 to JKGF5 | None | O/H Conductor | 8 | 219 | 29 | West | ALEXF3
132175 | 2015-08-31 | Scheduled Outage | Construction | Replace cables & transformer | None | None | 22 | 435 | 160 | South | 84F6
132176 | 2015-08-31 | Scheduled Outage | Maintenance | To replace a leaking transformer | None | Padmount (1ph) | 1 | 108 | 2 | East | LMBF7
132177 | 2015-08-31 | Scheduled Outage | Construction | SERVICE UPGRADE | None | None | 4 | 177 | 12 | Central | AK10
132178 | 2015-08-31 | Scheduled Outage | Forced Switching | Crews replaced defective transformer TP10528 | U/G Transformer | Padmount (3ph) | 2 | 430 | 14 | East | BCHF4
132179 | 2015-08-31 | Scheduled Outage | Construction | ISOLATED 2 TRANSFORMERS X32109 AND 32106 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 13 | 135 | 29 | Central | UW02
132180 | 2015-09-01 | Scheduled Outage | Construction | TE662 at 107 Craig Henry isolated to Replace Cables and Transformer affecting 10 customers on the Manordale 84F6 | None | None | 10 | 410 | 68 | South | 84F6
132181 | 2015-09-01 | Scheduled Outage | Maintenance | OH transformer X4222 was isolated for clearance to repair S155. Woodroffe (170F1) ID #132181 | None | Inline Switch | 13 | 245 | 53 | South | 170F1
132182 | 2015-09-01 | Scheduled Outage | Maintenance | S155 was isolated and repaired. Woodroffe (170F1) ID #132182 | None | Inline Switch | 20 | 220 | 73 | South | 170F1
132183 | 2015-09-01 | Scheduled Outage | Vegetation Management | At 08:34am crews isolated AN04 from Temp39 to end of line for storm hardening. Cahill (AN04) ID#132183 | None | None | 51 | 291 | 247 | East | AN04
132184 | 2015-09-01 | Scheduled Outage | Construction | 200F1 OH from S15660 to end of line was isolated to install new poles and transfer OH Stafford (200F1) ID #132184 | None | None | 157 | 183 | 479 | South | 200F1
132185 | 2015-09-01 | Scheduled Outage | Construction | 72F4 OH from S652 to end of line was isolated for pole replacement. Merivale (72F4) ID #132185 | None | None | 41 | 174 | 119 | South | 72F4
132186 | 2015-09-02 | Scheduled Outage | Construction | TE661 isolated for cable and transformer upgrade. Manordale (84F6) ID #132186 | None | None | 17 | 355 | 101 | South | 84F6
132187 | 2015-09-02 | Loss Of Supply | Transmission Inadvertent | Hydro One reported 48M2 tripped at Hawthorne Terminal. 24/7 Crew reports 249T2LA2 Red and White arresters are blown. Defective phases cut clear from the structure for repair at a later date. | None | None | 5104 | 7 | 595 | East | 48M2
132188 | 2015-09-02 | Scheduled Outage | Construction | TRANSFER PLANT TO NEW POLES | None | None | 9 | 240 | 36 | Central | SB07
132190 | 2015-09-02 | Scheduled Outage | Construction | Transformer X29084 at 1038 Walkley Rd isolated by crew to transfer plant | None | None | 8 | 151 | 20 | East | UZ11
132193 | 2015-09-02 | Lightning | Lightning | 58F2 circuit opened during lightning storm, circuit patrolled, nothing found. Epworth (58F2) | O/H Conductor | O/H Conductor | 170 | 48 | 136 | South | EPWF2
132197 | 2015-09-02 | Lightning | Lightning | MWDF2 circuit opened during lightning storm. Circuit patrolled, nothing found. Marchwood (MWDF2) | None | None | 651 | 36 | 391 | West | MWDF2
132197 | 2015-09-02 | Lightning | Lightning | MWDF2 circuit opened during lightning storm. Circuit patrolled, nothing found. Marchwood (MWDF2) | None | None | 2686 | 122 | 5462 | West | MWDF2
132199 | 2015-09-02 | Lightning | Lightning | Lightning strike burnt wires the 4kv under build UC02 | None | None | 19 | 39 | 12 | Central | TM3UC
132199 | 2015-09-02 | Lightning | Lightning | Lightning strike burnt wires the 4kv under build UC02 | None | None | 810 | 35 | 472 | Central | TM1AH
132199 | 2015-09-02 | Lightning | Lightning | Lightning strike burnt wires the 4kv under build UC02 | None | None | 864 | 36 | 518 | Central | TH2UL
132202 | 2015-09-02 | Lightning | Lightning | RX2054 auto reclosed and G739 opened during lightning storm. Circuit patrolled, nothing found. Uplands (4801F8) | O/H Conductor | O/H Conductor | 572 | 351 | 3346 | East | 4801F8
132203 | 2015-09-02 | Lightning | Lightning | Lightning storm in area possible strike. Line patrolled and nothing found breaker closed. | None | None | 918 | 214 | 3274 | Central | TH1UL
132205 | 2015-09-02 | Lightning | Lightning | Wire down at 497 Golden Ave on circuit UL1AH. Fire department requests circuit open due to burning branches. TM28 breaker opened then line switch opened to remve section of circuit on potential only. | O/H Conductor | Unknown \ Other | 19 | 34 | 11 | Central | TM3UC
132209 | 2015-09-02 | Loss Of Supply | Transmission Inadvertent | A9M5 breaker opened during lightning storm. Circuit patrolled by Hydro One, nothing found. South March (A9M5) | None | None | 4917 | 138 | 11309 | West | A9M5
132211 | 2015-09-02 | Tree Contacts | Tree Growth/ Untrimmed Tree | WB phases at S755 opened during lightning storm. Possible tree contact found by crew. Jockvale (145F3) | O/H Conductor | O/H Conductor | 7 | 199 | 23 | South | 145F3
132212 | 2015-09-02 | Lightning | Lightning | Fuse feeding transformer at 4878 Cambrian found open after lightning storm. Jockvale (145F3) ID#132112 | O/H Conductor | O/H Conductor | 1 | 240 | 4 | South | 145F3
132213 | 2015-09-02 | Lightning | Lightning | UL06 and UC02 circuits opened due to broken conductor caused by lightning storm | O/H Conductor | O/H Conductor | 150 | 456 | 1140 | Central | UC02
132213 | 2015-09-02 | Lightning | Lightning | UL06 and UC02 circuits opened due to broken conductor caused by lightning storm | O/H Conductor | O/H Conductor | 320 | 470 | 2507 | Central | UL06
132214 | 2015-09-02 | Lightning | Lightning | S15700 W,B fuses blown. Line patrolled and nothing found on overhead, Line sectionalized and restored in stages. | None | None | 200 | 14 | 47 | Central | TW22
132214 | 2015-09-02 | Lightning | Lightning | S15700 W,B fuses blown. Line patrolled and nothing found on overhead, Line sectionalized and restored in stages. | None | None | 375 | 27 | 169 | Central | TW22
132214 | 2015-09-02 | Lightning | Lightning | S15700 W,B fuses blown. Line patrolled and nothing found on overhead, Line sectionalized and restored in stages. | None | None | 550 | 345 | 3162 | Central | TW22
132215 | 2015-09-03 | Scheduled Outage | Vegetation Management | S22442 at 918 Rand to EOL was isolated to allow crew to perform tree trimming for storm hardening. 267 minutes. Walkley (UZ11) | None | None | 46 | 267 | 205 | East | UZ11
132216 | 2015-09-03 | Scheduled Outage | Construction | SERVICE UPGRADE | None | None | 4 | 45 | 3 | Central | UL05
132217 | 2015-09-03 | Scheduled Outage | Construction | To replace a defective transformer & a broken insert | None | Padmount (1ph) | 17 | 197 | 56 | South | 87F3
132218 | 2015-09-03 | Scheduled Outage | Construction | REPLACE TRANSFORMER | None | None | 10 | 120 | 20 | Central | UV03
132220 | 2015-09-03 | Scheduled Outage | Construction | 1 Blown arrestors on a 3 phase transformer. X39647 | None | Arrester | 1 | 36 | 1 | South | 145F3
132221 | 2015-09-03 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change blown arrestors | None | Arrester | 4 | 138 | 9 | East | LMBF5
132222 | 2015-09-04 | Defective Equipment | Electrical Failure | Cable fault caused fuse at S19551 to open. Bilberry (77M6) | U/G Cable | XLPE | 66 | 104 | 114 | East | 77M6
132224 | 2015-09-04 | Scheduled Outage | Vegetation Management | S17953 to EOL was isolated to allow tree trimming crew to perfrom tree trimming for storm hardening. Walkley (UZ02) | None | None | 50 | 209 | 174 | East | UZ02
132225 | 2015-09-04 | Scheduled Outage | Construction | Transformer TE1438 @ 163 Craig Henry was isolated by the crew to replace defective transformer | None | Kiosk (1ph) | 11 | 183 | 34 | South | 84F1
132226 | 2015-09-04 | Scheduled Outage | Forced Switching | Due to an out of phase condition at PP2152, Hydro Ottawa crews had to have an outage in order to isolate a cable section. | None | None | 101 | 13 | 22 | East | LMBF5
132227 | 2015-09-05 | Foreign Interference | Wildlife (Bird/Animal) | At 9:22am SCADA indicated RX2010 auto reclosed, OMS calls rolled up to S28471 Blue phase. Crews determined that a squrriel caused the outage. Alexander (AlexF3) ID#132227 | None | None | 19 | 74 | 23 | West | ALEXF3
132228 | 2015-09-05 | Foreign Interference | Foreign Objects | Customer owned pole line at pole X20564. Transformer is covered in vines which caused transformer fuse to open at the road and G180W to blow. | O/H Switchgear | Fused Cutout | 9 | 131 | 20 | East | 249F2
132229 | 2015-09-06 | Foreign Interference | Customer Equipment | Refused transformer X36132 at 23 Argue Drive. | Customer Owned | Customer-Owned | 5 | 56 | 5 | South | 190F2
132230 | 2015-09-06 | Defective Equipment | Mechanical Failure | Transformer X31095 had a defective cut out Augusta UD04, ID # 132230 | O/H Switchgear | Fused Cutout | 10 | 117 | 20 | Central | UD04
132231 | 2015-09-07 | Foreign Interference | Wildlife (Bird/Animal) | At 9:17am SCADA indicated the TO46 breaker tripped open. Breaker was closed via SCADA a few minutes later. Outage was a squirrel making contact to the overhead at Beachwood Station. Overbrook (TO2UB) ID#132231 | Unknown \ Other | Unknown \ Other | 878 | 9 | 132 | East | TO2UB
132233 | 2015-09-07 | Tree Contacts | Falling Tree | Tree fell down, causing two phases to blow at S14558, and one phase of downed primary | O/H Conductor | O/H Conductor | 94 | 30 | 47 | East | UZ05
132233 | 2015-09-07 | Tree Contacts | Falling Tree | Tree fell down, causing two phases to blow at S14558, and one phase of downed primary | O/H Conductor | O/H Conductor | 162 | 463 | 1250 | East | UZ05
132235 | 2015-09-07 | Lightning | Lightning | With lightning in the area an insulator at 5970 Russel Rd blew causing the G606R to blow | Pole Attachement | Insulator | 161 | 310 | 832 | East | 249F2
132236 | 2015-09-08 | Scheduled Outage | Construction | Transformer #X30769 isolated by crew for a service upgrade | None | None | 12 | 39 | 8 | Central | AB03
132237 | 2015-09-08 | Scheduled Outage | Vegetation Management | Transformer #X28202 isolated by crew due to tree trimming on secondary, Shawn from Dundas | None | None | 12 | 205 | 41 | East | UQ03
132238 | 2015-09-08 | Scheduled Outage | Construction | Transformer #X21679 isolated by crew to transfer secondary | None | None | 30 | 160 | 80 | Central | SB06
132239 | 2015-09-08 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 8 | 55 | 7 | East | UZ07
132240 | 2015-09-08 | Scheduled Outage | Construction | replace leaking transformer | None | Padmount (1ph) | 6 | 133 | 13 | South | 87F3
132241 | 2015-09-08 | Defective Equipment | Electrical Failure | Faulted 6F1 egress cable | U/G Cable | Unknown \ Other | 1 | 16 | 0 | East | 6F1
132241 | 2015-09-08 | Defective Equipment | Electrical Failure | Faulted 6F1 egress cable | U/G Cable | Unknown \ Other | 12 | 63 | 13 | East | 6F1
132241 | 2015-09-08 | Defective Equipment | Electrical Failure | Faulted 6F1 egress cable | U/G Cable | Unknown \ Other | 112 | 34 | 63 | East | 6F1
132241 | 2015-09-08 | Defective Equipment | Electrical Failure | Faulted 6F1 egress cable | U/G Cable | Unknown \ Other | 145 | 74 | 179 | East | 6F1
132242 | 2015-09-09 | Scheduled Outage | Construction | instaslling temp barriers for futur construction | None | None | 1 | 293 | 5 | Central | UW01
132244 | 2015-09-09 | Scheduled Outage | Vegetation Management | storm hardening | None | None | 56 | 224 | 209 | Central | UW07
132245 | 2015-09-09 | Scheduled Outage | Construction | Transformer #X23884 isolated by crew to replace switch and arrestor | None | None | 7 | 40 | 5 | Central | TH06
132246 | 2015-09-09 | Scheduled Outage | Construction | Transformer #X27970 isolated by crew to replace insulator | None | None | 6 | 60 | 6 | Central | TH06
132247 | 2015-09-09 | Scheduled Outage | Maintenance | Transformer #X23019 isolated by crew to replace live line clamp | None | None | 14 | 10 | 2 | East | AA02
132248 | 2015-09-09 | Scheduled Outage | Construction | Transformer #X36767 isolated by crew for working clearances | None | None | 8 | 205 | 27 | West | BRDF1
132249 | 2015-09-09 | Scheduled Outage | Construction | Transformer #X32346 isolated by crew to upgrade Bell service | None | None | 8 | 89 | 12 | Central | AD06
132250 | 2015-09-09 | Scheduled Outage | Construction | Transformer #X24904 isolated by crew for a pole change | None | None | 10 | 280 | 47 | East | UZ11
132251 | 2015-09-09 | Scheduled Outage | Construction | TE923 was isolated to replace cables and transformer. | None | None | 13 | 393 | 85 | South | 84F6
132252 | 2015-09-09 | Foreign Interference | Wildlife (Bird/Animal) | 249F4 auto reclosed and customers calls indicated G216RWB is now opened. 24/7 reports animal contact in overhead circuit. | O/H Conductor | O/H Conductor | 76 | 99 | 125 | East | LTM04
132253 | 2015-09-10 | Scheduled Outage | Construction | Vault VT143 isolated to install new primary cable in the vault. Riverdale TR3UQ, ID # 132253 | None | None | 1 | 280 | 5 | Central | TR3UQ
132254 | 2015-09-10 | Scheduled Outage | Construction | TE666 isolated for transformer and cable cable upgrade. Manordale (84F6) ID #132254 15 customers affected | None | None | 15 | 453 | 113 | South | 84F6
132255 | 2015-09-10 | Scheduled Outage | Construction | Transformer #X30299 isolated by crew for a porcelain replacement | None | None | 8 | 70 | 9 | Central | TH06
132256 | 2015-09-10 | Scheduled Outage | Vegetation Management | FAL03 overhead to end of line isolated for tree trimmers to clear customer owned line. Fallowfiled (FAL03) ID #1322 | None | None | 2 | 291 | 10 | South | FAL03
132257 | 2015-09-10 | Foreign Interference | Customer Equipment | Contractor equipment caused contact of the overhead at 51 Coupal affecting 594 customers on the UG06 | None | None | 594 | 56 | 554 | East | UG06
132258 | 2015-09-10 | Scheduled Outage | Construction | Transformer #X32233 isolated by crew to install new triplex | None | None | 6 | 35 | 4 | Central | AD06
132259 | 2015-09-10 | Scheduled Outage | Construction | Transformer #X33997 isolated by crew for a PCB replacement | None | None | 10 | 145 | 24 | Central | UV05
132260 | 2015-09-10 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER TE666 | None | None | 15 | 455 | 114 | South | 84F6
132262 | 2015-09-10 | Scheduled Outage | Construction | Transformers 4268 and 4269 isolated on the BRDF4 out of Bridlewood affecting 31 customers to change leaking transformer and to repair a broken pin and insert. | None | None | 31 | 109 | 56 | West | BRDF4
132264 | 2015-09-10 | Scheduled Outage | Construction | At 4:30pm crews isolated V572 at 171 Nepean to prove spare duct and install new secondary. Nepean (AB07) ID# 132264 | None | None | 1 | 215 | 4 | Central | AB07
132265 | 2015-09-11 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X33411 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 9 | 71 | 11 | Central | TW22
132266 | 2015-09-11 | Scheduled Outage | Construction | Transformer #X30297 isolated by crew for a switch replacement | None | None | 17 | 35 | 10 | Central | TH06
132267 | 2015-09-11 | Scheduled Outage | Construction | TE1439 isolated from Hydro Ottawa Sources to change defective transformer at 183 Craig Henry on the Centrepointe 87F3. | None | None | 10 | 151 | 25 | South | 87F3
132268 | 2015-09-11 | Scheduled Outage | Construction | Transformer #X23893 isolated by crew for a switch replacement | None | None | 12 | 18 | 4 | Central | TH06
132270 | 2015-09-11 | Scheduled Outage | Construction | Transformer #X35487 isolated by crew to replace leaking transformer | None | None | 63 | 75 | 79 | Central | UC08
132272 | 2015-09-11 | Defective Equipment | Defective Equipment/ Material | TH05 breaker tripped due to suspected cable fault. Hinchy (Th3SH/TL1TH) ID #132272 | U/G Cable | PILC | 458 | 12 | 92 | Central | TH3SH
132272 | 2015-09-11 | Defective Equipment | Defective Equipment/ Material | TH05 breaker tripped due to suspected cable fault. Hinchy (Th3SH/TL1TH) ID #132272 | U/G Cable | PILC | 575 | 73 | 700 | Central | TH3SH
132275 | 2015-09-12 | Defective Equipment | Mechanical Failure | DEFECTIVE TRANSFORMER CUTOUT | O/H Transformer | O/H Transformer (1ph) | 7 | 84 | 10 | South | EPWF3
132276 | 2015-09-12 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer X15324 opened due to over grown vines on pole. Leitrim (249F4) | O/H Transformer | O/H Transformer (1ph) | 5 | 45 | 4 | East | LTM04
132278 | 2015-09-13 | Tree Contacts | Broken Branch | secondary bus down at 113 Viewmount plus a broken switch at X36590 | O/H Conductor | O/H Conductor | 21 | 266 | 93 | South | EPWF3
132281 | 2015-09-13 | Tree Contacts | Other Vegetation | VINES GROWING INTO THE TRANS / WIRES | O/H Transformer | O/H Transformer (1ph) | 9 | 153 | 23 | Central | TD05
132284 | 2015-09-13 | Defective Equipment | Electrical Failure | DEFECTIVE TRANS HAS TO BE REPLACED | O/H Transformer | O/H Transformer (1ph) | 8 | 480 | 64 | East | LTM01
132285 | 2015-09-13 | Unknown/Other | Unknown | Closed in fuse to K796, and held. Nothing found. | None | None | 12 | 107 | 21 | East | AQ07
132286 | 2015-09-14 | Scheduled Outage | Maintenance | Storm hardening at the rear of 1274 Brookline. | None | None | 13 | 77 | 17 | East | UA07
132287 | 2015-09-14 | Scheduled Outage | Maintenance | Transformer TP8086 was isolated to change out the leaking transformer. Billberry 77M6, ID # 132287 | None | Kiosk (1ph) | 10 | 135 | 22 | East | 77M6
132289 | 2015-09-14 | Scheduled Outage | Construction | TEMP 111 to EOL on Baseline was isolated to allow crew to transfer plant to new pole. Fisher (AK06) | None | None | 1 | 396 | 7 | Central | AK06
132290 | 2015-09-14 | Scheduled Outage | Maintenance | Transformer TP3290 was isolated for the cable and transformer replacement program. | None | Kiosk (1ph) | 9 | 324 | 49 | East | BCHF5
132291 | 2015-09-14 | Defective Equipment | Defective Equipment/ Material | The TK21 Circuit breaker tripped due to defective cable between Kin Edward cell and VT403. | U/G Cable | PILC | 2 | 63 | 2 | Central | 407
132292 | 2015-09-15 | Scheduled Outage | Vegetation Management | UZ05 from S21912 to EOL isolated for storm hardening. Walkley (UZ05) | None | O/H Conductor | 118 | 408 | 802 | East | UZ05
132294 | 2015-09-15 | Scheduled Outage | Maintenance | To allow Sproule Electric to replace a transformer | None | Padmount (1ph) | 9 | 343 | 51 | East | BCHF5
132295 | 2015-09-15 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to replace a pole | None | Pole | 1 | 176 | 3 | East | 7F4
132296 | 2015-09-15 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change insulators, Switches and a cross arm | None | Fused Cutout | 7 | 105 | 12 | East | 6F10
132297 | 2015-09-15 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X33533 TO RE-ARRANG HYDRO PLANT | None | None | 5 | 190 | 16 | Central | 303
132298 | 2015-09-15 | Scheduled Outage | Construction | Transformer #X32055 isolated by crew to replace pole | None | None | 15 | 360 | 90 | Central | UW02
132299 | 2015-09-16 | Scheduled Outage | Construction | Overhead transformer X31489 isolated and replaced. Bayswater (UJ04) ID #132299 | None | None | 1 | 227 | 4 | Central | UJ04
132300 | 2015-09-16 | Scheduled Outage | Vegetation Management | TW22 isolated from S11177 to EOL for storm hardening. Woodroffe (TW22) | None | O/H Conductor | 37 | 309 | 191 | Central | TW22
132301 | 2015-09-16 | Scheduled Outage | Construction | UX09 overhead between TEMP 61 and TMEP98 isolated for pole replacmenet on McLaren at McDonald. Gladestone (UX09) | None | Pole | 165 | 294 | 808 | Central | UX09
132302 | 2015-09-16 | Scheduled Outage | Maintenance | To allow Sproule Power Lines to replace transformer TE42 and the primary cables feeding it. | None | Padmount (1ph) | 10 | 348 | 58 | East | BCHF5
132305 | 2015-09-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X24909 TO INSTALL NEW POLE | None | None | 8 | 225 | 30 | East | UZ11
132306 | 2015-09-16 | Scheduled Outage | Construction | 2 transformers #X32108 and X32107 isolated by crew to replace transformer | None | None | 10 | 445 | 74 | Central | UW02
132307 | 2015-09-17 | Scheduled Outage | Construction | Pole Replacement. | None | None | 4 | 126 | 8 | East | TB07
132308 | 2015-09-17 | Scheduled Outage | Construction | replace a pole with a crane | None | None | 20 | 258 | 86 | East | TB06
132309 | 2015-09-17 | Scheduled Outage | Vegetation Management | storm Hardening | None | None | 15 | 280 | 70 | Central | UW06
132310 | 2015-09-17 | Defective Equipment | Defective Equipment/ Material | Defective equipment | O/H Switchgear | Fused Cutout | 218 | 87 | 316 | East | 8F1
132311 | 2015-09-17 | Scheduled Outage | Maintenance | to replace leaking transformer | None | Padmount (1ph) | 15 | 147 | 37 | East | CYRF4
132312 | 2015-09-17 | Scheduled Outage | Construction | TP9115 isolated to connect new customer owned secondary service. | None | None | 25 | 38 | 16 | South | FAL02
132313 | 2015-09-17 | Scheduled Outage | Construction | Defective transformer. | None | None | 12 | 67 | 13 | East | CYRF4
132314 | 2015-09-17 | Scheduled Outage | Construction | Transformer X24527 at 5218 McLean Cres isolated for insulator replacement | None | Insulator | 5 | 131 | 11 | East | LMBF5
132315 | 2015-09-17 | Human Element | Commissioning Error | While performing switching at CHEO, TV10697 D bus load was dumped due to the C-D breaker found not beeing racked onto the bus. | None | None | 3 | 82 | 4 | Central | 508
132316 | 2015-09-18 | Scheduled Outage | Construction | planned outage to transfer primary plant to new poles | None | None | 13 | 89 | 19 | East | UQ07
132317 | 2015-09-18 | Scheduled Outage | Construction | planned outage for switch replacement | None | None | 42 | 88 | 62 | Central | TH06
132318 | 2015-09-18 | Scheduled Outage | Construction | Removal of old pole. | None | None | 17 | 71 | 20 | East | UZ11
132319 | 2015-09-18 | Scheduled Outage | Construction | switch replacment | None | None | 24 | 107 | 43 | Central | TH06
132321 | 2015-09-18 | Scheduled Outage | Maintenance | Hydro Ottawa to repair metering problem | None | None | 2 | 30 | 1 | Central | TL5TS
132323 | 2015-09-19 | Human Element | Switching Error | S17673 was inadvertantly openned by crew while working on an overhaed pail on the same pole. Leitrim (249F4) ID #132323 | None | None | 92 | 7 | 11 | East | LTM04
132324 | 2015-09-19 | Scheduled Outage | Maintenance | 249F4 overhead section between TEMP 137, TEMP108 and G290R isolated for insulator replacement. Leitrim (249F4) ID #132324 | None | None | 31 | 270 | 140 | East | LTM04
132325 | 2015-09-19 | Scheduled Outage | Maintenance | Transformer #X34427 isolated by crew to repair neutral | None | None | 7 | 45 | 5 | Central | AK07
132327 | 2015-09-19 | Defective Equipment | Electrical Failure | Defective transfomrer X24168 casued fuse G247 to open. Transformer changed by on-call. Moulton (8F1) | O/H Transformer | O/H Transformer (1ph) | 9 | 281 | 42 | East | 8F1
132327 | 2015-09-19 | Defective Equipment | Electrical Failure | Defective transfomrer X24168 casued fuse G247 to open. Transformer changed by on-call. Moulton (8F1) | O/H Transformer | O/H Transformer (1ph) | 48 | 55 | 44 | East | 8F1
132328 | 2015-09-19 | Defective Equipment | Electrical Failure | TH01 overhead from S27382 to EOL isolated to replace burnt cross arm caused by defective insulator. | Pole Attachement | Insulator | 25 | 71 | 30 | Central | TH01
132331 | 2015-09-19 | Scheduled Outage | Forced Switching | X27186 isolated to remove damaged service. Lincoln Heights (TD06) | O/H Transformer | O/H Transformer (1ph) | 14 | 35 | 8 | East | TB06
132332 | 2015-09-19 | Tree Contacts | Tree Growth/ Untrimmed Tree | Fuse at X32526 opened due to tree contact. Lincoln Heights (TD06) ID#132332 | O/H Conductor | O/H Conductor | 7 | 86 | 10 | Central | TD06
132333 | 2015-09-20 | Scheduled Outage | Vegetation Management | X26977 isolated to remove large tree that broke and fell into secondary. Playfair (AJ05) | None | None | 10 | 276 | 46 | East | AJ05
132336 | 2015-09-20 | Scheduled Outage | Vegetation Management | S936 to end of line was isolated to remove tree on overhead at 46 Milford. Woodrofe (170F1) ID #132336 | None | None | 37 | 50 | 31 | South | 170F1
132337 | 2015-09-20 | Scheduled Outage | Maintenance | Overhead 3 phase transformer X14465 isolated to repair fused cutout damaged by animal contact. Leitrim (249F4) ID #132337 | O/H Switchgear | Fused Cutout | 9 | 15 | 2 | East | LTM04
132339 | 2015-09-20 | Scheduled Outage | Vegetation Management | Transformer #X27186 isolated by crew to install new service | None | None | 14 | 25 | 6 | East | TB06
132340 | 2015-09-21 | Scheduled Outage | Construction | Transformer TE43 was isolated to allow crew to replace transformer and replace cable. Beaconhill (BCHF5) | None | None | 10 | 337 | 56 | East | BCHF5
132341 | 2015-09-21 | Scheduled Outage | Construction | Transformer PT114 isolated to change switches S10974, Hinchey TH06, ID # 132341 | None | None | 1 | 19 | 0 | Central | TH06
132342 | 2015-09-21 | Scheduled Outage | Construction | Vault V480 isolated to allow replacement of primary cable, Gladstone UX09, ID # 132342 | None | None | 1 | 237 | 4 | Central | UX09
132343 | 2015-09-21 | Scheduled Outage | Construction | Transformer X27912 at 214 Hinchey Ave. isolated by crew to install guy wires to support primary | None | None | 7 | 48 | 6 | Central | TH06
132346 | 2015-09-21 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 refused transformer X35535 at 873 Dundee Ave. animal interference (squirrel) | O/H Switchgear | Fused Cutout | 10 | 51 | 8 | Central | TD05
132348 | 2015-09-21 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMERS X32567 AND X32478 | None | None | 18 | 375 | 112 | Central | UW02
132349 | 2015-09-22 | Defective Equipment | Electrical Failure | faulty switch at transformer X20722 at 4389 thunder rd. | O/H Switchgear | Fused Cutout | 87 | 125 | 181 | East | 249F2
132350 | 2015-09-22 | Tree Contacts | Other Vegetation | O/H crew refused transformer X32925 at 2440 Georgina Drive - cause: vines | O/H Switchgear | Fused Cutout | 7 | 57 | 7 | Central | TD07
132352 | 2015-09-22 | Scheduled Outage | Construction | Broken elbow and insert @ TX#3213. | None | None | 7 | 28 | 3 | West | 24F1
132353 | 2015-09-22 | Scheduled Outage | Maintenance | 5 B phase transformers (TP10382, TP10380, TP10378, TP10377 & TP10376) were isolated to replace inserts. Manordale 84F6. ID#132353. | None | None | 89 | 92 | 136 | South | 84F6
132354 | 2015-09-22 | Scheduled Outage | Construction | At 09:55am crews isolated TP8880 and TP8881 to cut in new transformers. Due to out of phase condition 9 additional transformers were off for 7 mins. Limebank (LMBF5) ID#132354 | None | None | 15 | 100 | 25 | East | LMBF5
132354 | 2015-09-22 | Scheduled Outage | Construction | At 09:55am crews isolated TP8880 and TP8881 to cut in new transformers. Due to out of phase condition 9 additional transformers were off for 7 mins. Limebank (LMBF5) ID#132354 | None | None | 116 | 7 | 14 | East | LMBF5
132355 | 2015-09-22 | Foreign Interference | Dig-In | Contractor dug into U/G primary cables causing S16592 & S25105 to open. Edwin UV04. ID#132355. | U/G Cable | Unknown \ Other | 53 | 396 | 350 | Central | UV04
132356 | 2015-09-22 | Scheduled Outage | Construction | At 08:36am Crews isolated a section of UX09 and UX06 affecting 81 customers to allow pole and conductor to be replaced. Gladstone (UX09 & UX06) ID# 132356 | None | None | 12 | 167 | 33 | Central | UX06
132356 | 2015-09-22 | Scheduled Outage | Construction | At 08:36am Crews isolated a section of UX09 and UX06 affecting 81 customers to allow pole and conductor to be replaced. Gladstone (UX09 & UX06) ID# 132356 | None | None | 69 | 167 | 192 | Central | UX09
132357 | 2015-09-22 | Unknown/Other | Unknown | REPLACED BLOWN FUSE FEEDING TRANSFORMER X11575 | O/H Switchgear | Fused Cutout | 2 | 67 | 2 | West | BECKF2
132358 | 2015-09-22 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X26071 TO REPLACE SWITCH AND ARRESTER | None | None | 8 | 210 | 28 | Central | TH06
132359 | 2015-09-22 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X25560 FOR TREE REMOVAL | None | None | 18 | 193 | 58 | Central | SM12
132360 | 2015-09-22 | Scheduled Outage | Construction | transformer 2650B was isolated to replace leaking transformer, and full remediation. | None | None | 11 | 725 | 133 | West | 24F1
132361 | 2015-09-23 | Defective Equipment | Electrical Failure | Albion Y Bus diferential | U/G Cable | PILC | 14 | 39 | 9 | East | 2201
132361 | 2015-09-23 | Defective Equipment | Electrical Failure | Albion Y Bus diferential | U/G Cable | PILC | 1991 | 42 | 1394 | East | 2204
132361 | 2015-09-23 | Defective Equipment | Electrical Failure | Albion Y Bus diferential | U/G Cable | PILC | 2888 | 28 | 1348 | East | TA1UZ
132362 | 2015-09-23 | Scheduled Outage | Construction | Planned outage to P1666 to move from 1UW01 circuit to UW05 circuit. | None | None | 1 | 140 | 2 | Central | UW01
132363 | 2015-09-23 | Scheduled Outage | Construction | planned outage to extend primary overhead | None | None | 2 | 113 | 4 | Central | UX06
132364 | 2015-09-23 | Scheduled Outage | Construction | TE44 & TE45 on Eastvale were isolated to replace transformers & upgrade cables. Beacon Hill BCHF5. ID#132364. | None | None | 17 | 452 | 128 | East | BCHF5
132365 | 2015-09-23 | Scheduled Outage | Construction | At 9:15 V114 was isolated to move riser and prepare vault for de-commisioning. Woodroffe (UW01) ID#132365 | None | None | 1 | 225 | 4 | Central | UW01
132366 | 2015-09-23 | Scheduled Outage | Construction | TRANSFER PLANT TO NEW POLES | None | None | 24 | 180 | 72 | Central | UJ07
132367 | 2015-09-23 | Scheduled Outage | Maintenance | REPLACE DEFECTIVE CONNECTIONS | None | None | 13 | 20 | 4 | East | TB06
132368 | 2015-09-23 | Scheduled Outage | Construction | TRANSFER CONDUCTORS | None | None | 3 | 75 | 4 | Central | TK2AC
132369 | 2015-09-23 | Scheduled Outage | Construction | TRANSFER PLANT TO NEW POLES | None | None | 11 | 120 | 22 | East | UZ05
132371 | 2015-09-24 | Scheduled Outage | Construction | Transformer X34695 isolated for primary upgrade. Clifton UL14, ID # 132 | None | None | 10 | 133 | 22 | Central | UL14
132373 | 2015-09-24 | Scheduled Outage | Maintenance | To allow Sproule Power Lines to replace cables & transformers | None | Padmount (1ph) | 21 | 424 | 148 | East | BCHF5
132374 | 2015-09-24 | Scheduled Outage | Construction | Transformer #X29925 isolated by crew to install new service | None | None | 8 | 25 | 3 | Central | SR02
132375 | 2015-09-24 | Scheduled Outage | Construction | S21575 switch brackets and arrestors have been replaced | None | None | 1 | 52 | 1 | Central | TH06
132376 | 2015-09-24 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change a damaged transformer. | None | Padmount (1ph) | 22 | 80 | 29 | South | FAL03
132377 | 2015-09-24 | Scheduled Outage | Construction | 3 transformers (X27899, X27895, X27926) isolated by crew for a pole replacement | None | None | 18 | 170 | 51 | East | UZ05
132378 | 2015-09-24 | Scheduled Outage | Maintenance | Isolated to remove asbestos clean vault and check breaker. Bradley Kelly to prove spare conduit back to pole. | None | None | 56 | 259 | 242 | Central | UX06
132379 | 2015-09-24 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree limbs on the conductor caused it to burn down. | O/H Conductor | O/H Conductor | 8 | 372 | 50 | West | 28F3
132380 | 2015-09-24 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change insulators | None | None | 2 | 97 | 3 | East | LMBF5
132381 | 2015-09-24 | Scheduled Outage | Construction | To allow an electrical contractor to pull in & connect a new secondary service at TP10314 | None | None | 13 | 206 | 45 | East | LTM01
132382 | 2015-09-23 | Scheduled Outage | Construction | Transfer Plant | None | None | 3 | 315 | 16 | Central | UW01
132384 | 2015-09-25 | Loss Of Supply | Transmission Inadvertent | Customer owned line and transformer TN8906CZZ had an undetermined event that caused RX2060 to trip. Alexander ALXF2 ID # 132384 | None | None | 196 | 29 | 95 | West | ALEXF2
132385 | 2015-09-25 | Scheduled Outage | Construction | TD07 from TEMP 25 to EOL isolated for pole and transformer replacement. | None | Pole | 17 | 272 | 77 | Central | TD07
132386 | 2015-09-25 | Scheduled Outage | Construction | Transformer X33684 isolated by crew to upgrade primary | None | None | 1 | 273 | 5 | Central | SH05
132387 | 2015-09-26 | Defective Equipment | Defective Equipment/ Material | Replaced defective 50kv overhead transformer | O/H Transformer | O/H Transformer (1ph) | 8 | 270 | 36 | Central | SH04
132389 | 2015-09-26 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32775 TO REPLACE SECONDARY SERVICE CONNECTIONS | None | None | 5 | 43 | 4 | Central | UC05
132391 | 2015-09-27 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact | O/H Conductor | O/H Conductor | 184 | 38 | 117 | East | TO2UT
132392 | 2015-09-27 | Scheduled Outage | Maintenance | Insulator and pole change. | None | None | 32 | 301 | 161 | East | LMBF5
132393 | 2015-09-27 | Scheduled Outage | Maintenance | insulator and pole replacement. | None | None | 147 | 376 | 921 | East | LMBF5
132394 | 2015-09-28 | Scheduled Outage | Construction | relocate primary circuit to allow contractor to repair the building. | None | None | 33 | 229 | 126 | Central | TR1UN
132395 | 2015-09-28 | Scheduled Outage | Construction | Replace pole | None | None | 3 | 110 | 6 | East | UZ05
132396 | 2015-09-28 | Scheduled Outage | Construction | RECONFIGURE O/H PRIMARY LINES | None | None | 1 | 243 | 4 | West | BECKF2
132397 | 2015-09-28 | Scheduled Outage | Vegetation Management | replace cutouts and tree trimming. | None | None | 1 | 315 | 5 | East | 77M5
132398 | 2015-09-28 | Defective Equipment | Mechanical Failure | broken switch at ransformer X18126 | O/H Transformer | O/H Transformer (1ph) | 118 | 102 | 201 | East | 249F2
132400 | 2015-09-29 | Defective Equipment | Electrical Failure | blown fuse at S24684 on Hartin caused RX2010 to auto reclose, cause of the blown fuse was a defective switch. | O/H Switchgear | Fused Cutout | 17 | 176 | 50 | West | ALEXF3
132402 | 2015-09-29 | Scheduled Outage | Maintenance | Transformer KT412 @ 85 saddle Cres was isolated by the crew to replace leaking trasformer | None | Kiosk (1ph) | 14 | 60 | 14 | East | 2206
132404 | 2015-09-29 | Defective Equipment | Electrical Failure | Cable fault between TP5572 and TP5573 on Queenston and Lundy's Ln. | U/G Cable | Unknown \ Other | 55 | 140 | 128 | West | RHNF1
132404 | 2015-09-29 | Defective Equipment | Electrical Failure | Cable fault between TP5572 and TP5573 on Queenston and Lundy's Ln. | U/G Cable | Unknown \ Other | 66 | 25 | 28 | West | RHNF1
132404 | 2015-09-29 | Defective Equipment | Electrical Failure | Cable fault between TP5572 and TP5573 on Queenston and Lundy's Ln. | U/G Cable | Unknown \ Other | 75 | 29 | 36 | West | RHNF1
132404 | 2015-09-29 | Defective Equipment | Electrical Failure | Cable fault between TP5572 and TP5573 on Queenston and Lundy's Ln. | U/G Cable | Unknown \ Other | 146 | 171 | 416 | West | RHNF1
132406 | 2015-09-29 | Scheduled Outage | Construction | REPLACE POLE | None | None | 63 | 210 | 220 | Central | UX06
132407 | 2015-09-29 | Scheduled Outage | Maintenance | REPLACE DEFECTIVE SECONDARY SERVICE | None | O/H Service | 12 | 40 | 8 | East | TB2JP
132410 | 2015-09-29 | Scheduled Outage | Maintenance | Transformer #X31652 isolated by crew to replace defective secondary service | None | None | 5 | 61 | 5 | Central | SR07
132411 | 2015-09-29 | Defective Equipment | Mechanical Failure | blue phase termination burnt off. | U/G Cable Attachement | Termination \ Stress Cone | 1 | 226 | 4 | South | 200F6
132412 | 2015-09-29 | Scheduled Outage | Maintenance | soil remediation at TP11070 at 64 Charing | None | None | 8 | 425 | 57 | South | 84F1
132413 | 2015-09-30 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact and tree contact on the O/H at Saunderson and Dakota caused the AE02 O/H conductor to gallop and break causing the AE02 CB to trip open. | O/H Conductor | O/H Conductor | 265 | 327 | 1444 | East | AE02
132414 | 2015-09-30 | Scheduled Outage | Construction | Transformer TP3083 was isolated to allow crew to replace cable and transformer. Beaconhill (BCHF5) | None | None | 10 | 281 | 47 | East | BCHF5
132416 | 2015-09-30 | Scheduled Outage | Construction | The Overhead line from S27382 to EOL at Scott and Island Park was isolated to allow the crew replace the porcelain insulators and transformer switches | None | Insulator | 25 | 225 | 94 | Central | TH01
132417 | 2015-09-30 | Foreign Interference | Foreign Objects | Glass Cleaner came into contact with O/h circuit | O/H Conductor | O/H Conductor | 1 | 23 | 0 | Central | TH2UL
132417 | 2015-09-30 | Foreign Interference | Foreign Objects | Glass Cleaner came into contact with O/h circuit | O/H Conductor | O/H Conductor | 2 | 20 | 1 | Central | TH2UL
132417 | 2015-09-30 | Foreign Interference | Foreign Objects | Glass Cleaner came into contact with O/h circuit | O/H Conductor | O/H Conductor | 4 | 25 | 2 | Central | TH2UL
132417 | 2015-09-30 | Foreign Interference | Foreign Objects | Glass Cleaner came into contact with O/h circuit | O/H Conductor | O/H Conductor | 5 | 11 | 1 | Central | TH2UL
132417 | 2015-09-30 | Foreign Interference | Foreign Objects | Glass Cleaner came into contact with O/h circuit | O/H Conductor | O/H Conductor | 1179 | 39 | 766 | Central | TH2UL
132418 | 2015-09-30 | Scheduled Outage | Construction | The UX06 O/H bet Temp20 and Temp145 on MacLaren was isolated to allow the contractor to replace the pole and transfer the cable that feeds V484 to the new pole | None | Pole | 56 | 262 | 245 | Central | UX06
132421 | 2015-09-30 | Foreign Interference | Vehicle | Transformer K1239 was isolated for clearance to allow crew to replace dammaged pole hit by vehicle at 1567 Fisher. Fisher (AK12) | Pole | Pole | 13 | 521 | 113 | Central | AK12
132422 | 2015-09-30 | Scheduled Outage | Maintenance | K692 @ 541 Acadia was isolated to allow the contractor to install a new 400 amp combination meter base | None | Customer-Owned | 2 | 464 | 15 | East | UG05
132423 | 2015-09-30 | Foreign Interference | Vehicle | vehicle knocked transformer off base. | None | None | 19 | 135 | 43 | East | 77M5
132425 | 2015-10-01 | Scheduled Outage | Maintenance | TP11071 isolated for soil remediation. Woodroffe 170F1. ID#132425. | None | None | 8 | 502 | 67 | South | 170F1
132426 | 2015-10-01 | Scheduled Outage | Construction | At 10:10am TP6447 was isolated to relocate transformer. Barrhaven (140F4) ID# 132426 | None | None | 17 | 356 | 101 | South | 140F4
132427 | 2015-10-01 | Scheduled Outage | Construction | TRANSFER PLANT TO NEW POLES | None | None | 9 | 165 | 25 | Central | TR1UN
132428 | 2015-10-01 | Scheduled Outage | Maintenance | At 12:17pm transformer TP9708 was isolated for elbow and insert replacement. Cyrville (CYRF4) ID# 132428 | None | None | 12 | 60 | 12 | East | CYRF4
132430 | 2015-10-01 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X31720 opened up due to animal contact | O/H Switchgear | Fused Cutout | 13 | 135 | 29 | Central | TH11-NIU
132431 | 2015-10-02 | Foreign Interference | Vehicle | vehicle accident brought down hydro pole and wires. | Pole | Pole | 5 | 440 | 37 | South | 145F3
132432 | 2015-10-02 | Scheduled Outage | Maintenance | Excavate around transformer and fill holes in base and backfill. | None | None | 35 | 103 | 60 | West | 624F3
132433 | 2015-10-03 | Defective Equipment | Electrical Failure | UQ03 breaker autoreclosed autoed due to a cable fault between SC7885-L2 and SW125-L2 | U/G Cable | PILC | 47 | 8 | 6 | East | UQ03
132433 | 2015-10-03 | Defective Equipment | Electrical Failure | UQ03 breaker autoreclosed autoed due to a cable fault between SC7885-L2 and SW125-L2 | U/G Cable | PILC | 47 | 55 | 43 | East | UQ03
132433 | 2015-10-03 | Defective Equipment | Electrical Failure | UQ03 breaker autoreclosed autoed due to a cable fault between SC7885-L2 and SW125-L2 | U/G Cable | PILC | 549 | 65 | 595 | East | UQ03
132435 | 2015-10-03 | Scheduled Outage | Construction | V572 isolated to decommission vault. Nepean (AB07) | None | None | 1 | 199 | 3 | Central | AB07
132437 | 2015-10-03 | Tree Contacts | Broken Branch | a tree branch fell into the O/H due to high winds. This caused RX2009 to open & blew fuse 65 B. | None | None | 192 | 79 | 253 | West | 624F6
132439 | 2015-10-03 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contacted overhead causeing UT02 breaker to open. | O/H Conductor | O/H Conductor | 652 | 73 | 793 | East | UT02
132440 | 2015-10-03 | Scheduled Outage | Maintenance | Transfomrer X24227 isolated to replace secondary connections. Fisher (AK06) ID#132440 | None | O/H Transformer (1ph) | 10 | 83 | 14 | Central | AK06
132441 | 2015-10-03 | Scheduled Outage | Vegetation Management | Transformer X11749 isolated to remove tree from overhead service. Terry Fox (TFXF1) ID# | None | None | 2 | 70 | 2 | West | TFXF1
132443 | 2015-10-04 | Scheduled Outage | Maintenance | TV9451 isolated to allow crew to add SF6 Gas and check for leaks. | None | None | 1 | 124 | 2 | Central | 606
132444 | 2015-10-04 | Tree Contacts | Falling Tree | A tree fell into the overhead conductor | None | None | 390 | 50 | 325 | South | 84F1
132445 | 2015-10-04 | Foreign Interference | Wildlife (Bird/Animal) | Refused X45480 at 2374 Cheshire Ave. Cause of outage - animal contact | O/H Transformer | O/H Transformer (1ph) | 12 | 46 | 9 | Central | TW17
132447 | 2015-10-05 | Scheduled Outage | Maintenance | To allow Sproule Power Lines to replace elbows & inserts | U/G Cable Attachement | Elbow \ Insert | 26 | 170 | 74 | East | CYRF4
132448 | 2015-10-05 | Scheduled Outage | Construction | Transformer #X27826 isolated by crew for a switch replacement | None | None | 5 | 10 | 1 | Central | TH06
132449 | 2015-10-05 | Scheduled Outage | Construction | X43753 iolated to install new service. Limebank (7F1) ID#132449 | Secondary \ Service | O/H Service | 2 | 70 | 2 | East | 7F1
132450 | 2015-10-05 | Scheduled Outage | Construction | Transformer #X34696 isolated by crew to transfer plant to new pole | None | None | 30 | 220 | 110 | Central | SB06
132451 | 2015-10-05 | Scheduled Outage | Construction | Transformer #X27827 isolated by crew for a switch replacement | None | None | 24 | 8 | 3 | Central | TH06
132453 | 2015-10-05 | Scheduled Outage | Construction | Transformer #X38561 isolated by crew to transfer secondary | None | None | 6 | 255 | 26 | Central | TD07
132454 | 2015-10-05 | Scheduled Outage | Construction | Transformer #X23886 isolated by crew for a switch replacement | None | None | 14 | 29 | 7 | Central | TH06
132455 | 2015-10-05 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused G4W phase to open | O/H Switchgear | Fused Cutout | 4 | 31 | 2 | East | 7F1
132455 | 2015-10-05 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused G4W phase to open | O/H Switchgear | Fused Cutout | 35 | 75 | 44 | East | 7F1
132456 | 2015-10-06 | Scheduled Outage | Maintenance | V482 interrupted on the UX06 out of Gladstone to replace cables affecting 37 customers at 207 Maclaren | None | None | 37 | 176 | 109 | Central | UX06
132457 | 2015-10-06 | Scheduled Outage | Maintenance | TP9724, TP9725 & TP9726 were isolated for cable and transformer upgrade. Cyrville (CYRF4) ID #132457 | None | None | 35 | 108 | 63 | East | CYRF4
132458 | 2015-10-06 | Scheduled Outage | Maintenance | 1 Customer affected on the Florence (UF10), V490 isolated to replace cables at 335 Maclaren | None | None | 1 | 206 | 3 | Central | UF10
132459 | 2015-10-06 | Scheduled Outage | Maintenance | Affecting 54 customers on the Hinchey (TH11), overhead on Stirling was isolated to re-frme a pole | None | None | 54 | 284 | 256 | Central | TH11-NIU
132461 | 2015-10-06 | Scheduled Outage | Construction | Transformer #X27927 isolated by crew for a pole replacement | None | None | 13 | 90 | 20 | East | UZ05
132462 | 2015-10-06 | Scheduled Outage | Construction | Transformer #X25700 isolated by crew for a service upgrade | None | None | 11 | 25 | 5 | Central | TH11-NIU
132463 | 2015-10-06 | Scheduled Outage | Construction | Transformer #X27925 isolated by crew for a pole replacement | None | None | 12 | 10 | 2 | East | UZ05
132464 | 2015-10-06 | Scheduled Outage | Construction | Transformer #X34095 isolated by crew to install new service | None | None | 9 | 30 | 4 | Central | SM06
132465 | 2015-10-06 | Unknown/Other | Unknown | Customer reported outage - patrol found switch 886 red phase blown and down stream OH looks good. Upon restoring crews found SC9981-1 red phase fuse blown and S15922 red phase blown. Janet King (JKGF5) ID #132465 | None | None | 91 | 111 | 168 | West | JKGF5
132466 | 2015-10-06 | Scheduled Outage | Maintenance | elbow and insert replacement | None | None | 16 | 56 | 15 | East | CYRF4
132467 | 2015-10-07 | Scheduled Outage | Maintenance | TP9729 & TP9730 were isolated for elbow & insert replacement. CYRF4. ID#132467. | None | None | 32 | 115 | 61 | East | CYRF4
132468 | 2015-10-07 | Scheduled Outage | Vegetation Management | 7 Customers were interrupted on the Shillington AD06 to remove a tree at 196 General | None | None | 7 | 303 | 35 | Central | AD06
132469 | 2015-10-07 | Scheduled Outage | Vegetation Management | 13 Customers were interrupted on the Shillington AD06 to remove a tree at 176 General | None | None | 13 | 363 | 79 | Central | AD06
132470 | 2015-10-07 | Scheduled Outage | Maintenance | G677W to EOL isolated to allow crews to replace insulators. Limebank (LMBF5) ID #132470 | None | None | 68 | 255 | 289 | East | LMBF5
132471 | 2015-10-07 | Scheduled Outage | Construction | A section of O/H line on Fernbank at Shea was isolated for upgrade & voltage conversion. ID#132471. | None | None | 19 | 276 | 87 | West | RHNF1
132472 | 2015-10-07 | Scheduled Outage | Construction | 2 transformers (X30512 and X30513) isolated by crew for a pole change | None | None | 18 | 105 | 32 | Central | UF10
132473 | 2015-10-07 | Scheduled Outage | Maintenance | pole change | None | None | 34 | 150 | 85 | Central | UF10
132474 | 2015-10-07 | Scheduled Outage | Construction | Transformer #X27891 isolated by crew for a pole replacement | None | None | 11 | 288 | 53 | East | UZ05
132475 | 2015-10-07 | Scheduled Outage | Construction | PORCELIN SWITCH REPLACEMENT | None | None | 4 | 60 | 4 | Central | TH01
132476 | 2015-10-07 | Scheduled Outage | Maintenance | POLE CHANGE | None | None | 12 | 180 | 36 | Central | UF10
132477 | 2015-10-07 | Scheduled Outage | Maintenance | pole change | None | None | 54 | 180 | 162 | Central | UF10
132479 | 2015-10-08 | Scheduled Outage | Construction | W phase transformers TP9734, TP9735, TP9736 were isolated to allow crew to reaplce elbows and inserts. Cyrville (CYRF4) | None | None | 28 | 94 | 44 | East | CYRF4
132480 | 2015-10-08 | Scheduled Outage | Construction | Transformer #X24494 isolated by crew to drop old service | None | None | 3 | 11 | 1 | East | UB07
132481 | 2015-10-08 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to upgrade the primary conductor | None | None | 31 | 91 | 47 | Central | TH01
132482 | 2015-10-08 | Scheduled Outage | Vegetation Management | To allow forestry crews to clear the AE01 overhead downstream of pole# 64A2C-0015. | None | None | 6 | 205 | 20 | East | AE01
132483 | 2015-10-08 | Scheduled Outage | Maintenance | Transformers TP9739 and TP9740 were isolated to allow crew to replace elbows and insert | None | None | 21 | 59 | 21 | East | CYRF4
132484 | 2015-10-08 | Scheduled Outage | Construction | Transformer #X27892 and X27925 isolated by crew for a pole replacement | None | None | 26 | 200 | 87 | East | UZ05
132486 | 2015-10-08 | Scheduled Outage | Construction | Transformer #X28111 isolated by crew for a pole replacement | None | None | 25 | 238 | 99 | East | AF06
132487 | 2015-10-08 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X31477 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 10 | 62 | 10 | Central | TH11-NIU
132489 | 2015-10-09 | Scheduled Outage | Forced Switching | TD06 W from pole 55020-543 to EOL isolated to repair broken pole caused by pole fire. | None | Pole | 15 | 202 | 50 | Central | TD06
132490 | 2015-10-09 | Scheduled Outage | Construction | To replace a pole in the rear of 1846 Edgecombe. | None | None | 16 | 146 | 39 | East | TB15
132491 | 2015-10-09 | Scheduled Outage | Vegetation Management | Transformer #X37238 isolated by crew due to vines that grew into transformer and switch and caused a fire. Switch and fuse had to be replaced. | None | None | 13 | 285 | 62 | South | 72F1
132492 | 2015-10-09 | Scheduled Outage | Maintenance | Vault VE33N was isolated to allow crew to make repairs to metering problem. Bayhsore (49F1) | None | None | 1 | 58 | 1 | South | 160F1
132494 | 2015-10-09 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to replace the pole at the rear of 1327 Avenue ''S'' | None | Pole | 12 | 207 | 41 | East | SO10
132497 | 2015-10-09 | Scheduled Outage | Maintenance | Transformer #TP5512 isolated by crew to make repairs to secondary pedestal | None | None | 8 | 60 | 8 | South | 84F4
132498 | 2015-10-09 | Scheduled Outage | Maintenance | To allow Hydro Ottawa metering to repair a metering problem | None | Meter | 1 | 26 | 0 | Central | 2806
132499 | 2015-10-10 | Loss Of Supply | Third Party | GR2 R phase tripped under H/O. Arrestor on customer owned primary at 720 River rd blew causing cut-out to open Limebank LMBF5. ID#132499 | None | None | 378 | 25 | 158 | East | LMBF5
132501 | 2015-10-12 | Scheduled Outage | Maintenance | Transformer 004964 isolated to replace switch & arrestor. Limebank LMBF5. ID#132501. | None | Arrester | 1 | 51 | 1 | East | LMBF5
132502 | 2015-10-12 | Scheduled Outage | Construction | The Overhead @ 1304 ADIRONDACK DR on the UW05 circuit was isolated by K Line to allow them to transfer the load and tear out the old overhead | None | O/H Conductor | 4 | 418 | 28 | Central | UW05
132503 | 2015-10-13 | Scheduled Outage | Maintenance | planned outage for elbow and insert replacment | None | None | 25 | 73 | 30 | East | CYRF4
132504 | 2015-10-13 | Scheduled Outage | Construction | Trnasformer P390 was isolated to allow for cable riser relocation. | None | None | 1 | 190 | 3 | Central | UF10
132507 | 2015-10-13 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32174 TO REPLACE PRIMARY DROP LEAD | None | None | 7 | 53 | 6 | Central | UL06
132508 | 2015-10-13 | Scheduled Outage | Maintenance | elbow and insert replacement. | None | None | 24 | 147 | 59 | East | CYRF4
132509 | 2015-10-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32643 opened up due to bird contact | O/H Switchgear | Fused Cutout | 1 | 43 | 1 | Central | TD05
132510 | 2015-10-13 | Scheduled Outage | Construction | Transformer #X27892 isolated by crew to replace the pole | None | None | 14 | 377 | 88 | East | UZ05
132511 | 2015-10-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27485 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 10 | 39 | 6 | Central | 505
132512 | 2015-10-14 | Scheduled Outage | Construction | Brain Brooks from B & M isolated V571 @ 177 Nepean to allow him replace the primary cable to the vault. | U/G Cable | Unknown \ Other | 1 | 195 | 3 | Central | AB07
132513 | 2015-10-14 | Scheduled Outage | Construction | Replace pole and transformer at X27796 | None | None | 11 | 368 | 67 | East | UQ07
132516 | 2015-10-14 | Scheduled Outage | Maintenance | elbow and insert replacement | None | None | 45 | 88 | 66 | East | CYRF4
132517 | 2015-10-14 | Scheduled Outage | Construction | elbow and insert replacement | None | None | 16 | 108 | 29 | West | TFXF2
132518 | 2015-10-14 | Scheduled Outage | Construction | planned outage to install a new pole and transfer plant. | None | None | 33 | 208 | 114 | South | 180F4
132519 | 2015-10-14 | Foreign Interference | Vehicle | Transformer #X37151 opened up due to a truck backed into the pole | O/H Switchgear | Fused Cutout | 9 | 70 | 10 | East | AA02
132520 | 2015-10-14 | Scheduled Outage | Maintenance | Transformer #X39743 isolated by crew to check connections at the transformer | None | None | 2 | 40 | 1 | East | LMBF7
132521 | 2015-10-14 | Scheduled Outage | Maintenance | Transformer #X31931 isolated by crew to replace connections at pole | None | None | 16 | 18 | 5 | Central | TD14
132522 | 2015-10-14 | Defective Equipment | Electrical Failure | At 10:32pm SCADA indicated the TO38 breaker tripped open. Crews found that the cable between Overbrook and VT74 was faulted. Overbrook (1809) ID#132522 | U/G Cable | PILC | 1 | 47 | 1 | East | 1809
132524 | 2015-10-15 | Scheduled Outage | Vegetation Management | Switch 223 to EOL isolated for tree trimming. Kanata (624F6) ID #132 | None | None | 1 | 63 | 1 | West | 624F6
132525 | 2015-10-15 | Scheduled Outage | Maintenance | VE17 isolated for vault maintenance. Parkwood Hills DS (190F5) ID #132525 | None | None | 1 | 123 | 2 | South | 190F5
132526 | 2015-10-15 | Scheduled Outage | Maintenance | LMBF5 OH from G280 to TE461 to repair defective line and reoplace G280. Limebank (LMBF5) ID #13254 | None | None | 24 | 152 | 61 | East | LMBF5
132527 | 2015-10-15 | Scheduled Outage | Construction | TP9751, TP9752 & TP9763 isolated for elbow and insert upgrade. Brdilewood (BRDF4) ID #13254 | None | None | 45 | 113 | 85 | West | BRDF4
132528 | 2015-10-15 | Defective Equipment | Electrical Failure | Cable fault between VT345 and VT196. Recalled TR22 breaker to restore power to 6 vaults. | U/G Cable | Unknown \ Other | 2 | 9 | 0 | Central | 502
132528 | 2015-10-15 | Defective Equipment | Electrical Failure | Cable fault between VT345 and VT196. Recalled TR22 breaker to restore power to 6 vaults. | U/G Cable | Unknown \ Other | 5 | 36 | 3 | Central | 502
132528 | 2015-10-15 | Defective Equipment | Electrical Failure | Cable fault between VT345 and VT196. Recalled TR22 breaker to restore power to 6 vaults. | U/G Cable | Unknown \ Other | 329 | 107 | 587 | Central | 502
132530 | 2015-10-15 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33082 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 15 | 35 | 9 | Central | TD07
132531 | 2015-10-15 | Scheduled Outage | Maintenance | VT204 at 100 Boteler on the King Edward (404) was isolated for vault maintenance affecting 1 customer. | None | None | 1 | 328 | 5 | Central | 404
132532 | 2015-10-15 | Scheduled Outage | Maintenance | TP9754 & TP9755 isolated for Elbow & insert upgrade. Billberry Creek (77M6) ID #132532 | None | None | 24 | 148 | 59 | East | 77M6
132533 | 2015-10-15 | Scheduled Outage | Maintenance | LMBF5 OH from Fused cutout to EOL isolated to repair defective cutout. Limebank (LMBF5) ID #132533 | None | None | 1 | 50 | 1 | East | LMBF5
132535 | 2015-10-15 | Lightning | Lightning Strike On Adjacent Circuit | TM32, TM19 and SM09 tripped due to lighting strike at P240 riser. | Pole Attachement | Insulator | 1 | 580 | 10 | Central | SM09
132535 | 2015-10-15 | Lightning | Lightning Strike On Adjacent Circuit | TM32, TM19 and SM09 tripped due to lighting strike at P240 riser. | Pole Attachement | Insulator | 17 | 77 | 22 | Central | TM2UC
132535 | 2015-10-15 | Lightning | Lightning Strike On Adjacent Circuit | TM32, TM19 and SM09 tripped due to lighting strike at P240 riser. | Pole Attachement | Insulator | 981 | 17 | 278 | Central | TM1UC
132536 | 2015-10-15 | Scheduled Outage | Construction | Transformer X30659-1667107 at 551 Gilmour St. isolated by crew to transfer plant | None | None | 9 | 302 | 45 | Central | UF05
132537 | 2015-10-15 | Defective Equipment | Defective Equipment/ Material | Transformer X23955 at 618B Hochelaga St isolated by crew to replace hot line clamp. | O/H Conductor | Hot-Line Clamp | 15 | 14 | 4 | East | AP06
132538 | 2015-10-15 | Lightning | Lightning | Crew requested TM19 (TM2UC) & TM28 (TM3UC) circuits opened to extinguish pole fire caused by earlier lightning strike. | Pole Attachement | Insulator | 17 | 7 | 2 | Central | TM2UC
132538 | 2015-10-15 | Lightning | Lightning | Crew requested TM19 (TM2UC) & TM28 (TM3UC) circuits opened to extinguish pole fire caused by earlier lightning strike. | Pole Attachement | Insulator | 19 | 7 | 2 | Central | TM3UC
132539 | 2015-10-16 | Scheduled Outage | Maintenance | 13 customers were affected on the Albion (2204) when transformer KT281 was isolated for change out at 30 Sturbridge. | None | None | 13 | 198 | 43 | East | 2204
132540 | 2015-10-16 | Scheduled Outage | Maintenance | 50 customers were affected on the Church (AA03) for HOL crew to replace a pole and transfer plant at 388 Iberville. | None | None | 50 | 262 | 218 | East | AA03
132541 | 2015-10-16 | Foreign Interference | Wildlife (Bird/Animal) | Replaced blown fuse at switch 109B (bird contact) | None | None | 25 | 63 | 26 | West | MWDF3
132544 | 2015-10-16 | Scheduled Outage | Construction | Cable sections and 10 transformers isolated from S18823 to end of line to transfer feed from red to white phase. Fallowfield FAL03, ID # 132544 | None | None | 101 | 13 | 22 | South | FAL03
132545 | 2015-10-16 | Scheduled Outage | Construction | Transformer 4043 isolated to replace transformer with TP11155, Bridlewood BRDF4, ID # 132545 | None | None | 18 | 113 | 34 | West | BRDF4
132546 | 2015-10-17 | Foreign Interference | Wildlife (Bird/Animal) | Squirel contact at transformer X46285 caused the TW05 CB to open. Woodroffe (TW05). ID# 132546 | Station Equipment | Relay | 406 | 44 | 298 | Central | TW05
132547 | 2015-10-17 | Scheduled Outage | Maintenance | TV4233 @ 215 slater was isolated to allow the contractor to preform vault manitenance. | None | Breaker \ Relay | 1 | 169 | 3 | Central | 604
132553 | 2015-10-18 | Scheduled Outage | Construction | The crews isolated TP3525 @ 101 Hinton to replace the overhead switches | None | Fused Cutout | 6 | 36 | 4 | Central | TH06
132554 | 2015-10-18 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32402 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 28 | 99 | 46 | Central | TD06
132555 | 2015-10-18 | Scheduled Outage | Construction | Transformer #X39198 isolated by crew for a switch replacement | None | None | 5 | 60 | 5 | Central | TH06
132556 | 2015-10-18 | Scheduled Outage | Maintenance | Transformer P402 @ 205 Catherine was isolated to allow the crew to disconnect and rerout cables to accommodate the construction project at 205 Catherine. UF06 | U/G Cable | PILC | 3 | 113 | 6 | Central | UF06
132557 | 2015-10-18 | Scheduled Outage | Construction | Transformer PT218 @ 319 Parkdale was isolated to allow the crew to replace the switches at pole 55D1B-0621 on TH06 | None | Fused Cutout | 2 | 69 | 2 | Central | TH06
132559 | 2015-10-18 | Scheduled Outage | Construction | Transformer #X33703 isolated by crew for a switch replacement | None | None | 14 | 35 | 8 | Central | TH06
132560 | 2015-10-18 | Scheduled Outage | Construction | Transformer #X27835 isolated by crew for a switch replacement | None | None | 2 | 40 | 1 | Central | TH06
132561 | 2015-10-19 | Scheduled Outage | Construction | TE1287 isolated to install new transformer base and civil work. | None | None | 1 | 391 | 7 | South | 130F2
132562 | 2015-10-19 | Scheduled Outage | Maintenance | S29635 to EOL was isolated to allow crew to perform transformer soil remedisation. BECKWITH (BECKF2) | None | None | 1 | 345 | 6 | West | BECKF2
132564 | 2015-10-19 | Scheduled Outage | Construction | Transformer #X27893 isolated by crew for a pole replacement | None | None | 10 | 90 | 15 | East | UZ05
132565 | 2015-10-19 | Scheduled Outage | Vegetation Management | The Overhead line at 117Sunnyside was isolated by the crew to allow the tree contractor remove large trees at the rear of 95 and 101 Sunnyside | None | O/H Conductor | 26 | 147 | 64 | Central | SR09
132566 | 2015-10-19 | Unknown/Other | Unknown | Refused transformer x28321 and switch S27488. No cause found. | O/H Transformer | O/H Transformer (1ph) | 10 | 91 | 15 | Central | 505
132567 | 2015-10-19 | Scheduled Outage | Construction | Transformer #X30659 isolated by crew to install a pole | None | None | 9 | 292 | 44 | Central | UF05
132568 | 2015-10-19 | Defective Equipment | Mechanical Failure | During switching crew had a flash at TP9730 causing S18955 W phase to blow. Crew repaired defective elbow | U/G Cable Attachement | Elbow \ Insert | 87 | 55 | 80 | East | CYRF4
132569 | 2015-10-19 | Scheduled Outage | Construction | Transformer KT141 @ 811 Connaught was isolated to allow the crew to clean up the oil leak and replace the transformer. TD14 | None | Padmount (1ph) | 8 | 478 | 64 | Central | TD14
132570 | 2015-10-19 | Defective Equipment | Defective Equipment/ Material | REPLACED BROKEN FUSE FEEDING TRANSFORMER X31963 | O/H Transformer | O/H Transformer (1ph) | 11 | 154 | 28 | Central | SR09
132571 | 2015-10-20 | Scheduled Outage | Construction | Transformer X30758 on the Nepean (AB03) overhead was interrupted for contractor to replace poles affecting 3 customers at 356 Gloucester St. | None | Pole | 3 | 224 | 11 | Central | AB03
132572 | 2015-10-20 | Scheduled Outage | Vegetation Management | To allow forestry crews to perform tree trimming under the storm hardening program | None | None | 11 | 29 | 5 | East | AE05
132572 | 2015-10-20 | Scheduled Outage | Vegetation Management | To allow forestry crews to perform tree trimming under the storm hardening program | None | None | 17 | 173 | 49 | East | AE05
132573 | 2015-10-20 | Scheduled Outage | Maintenance | TP6448 isolated for insert replacement. Barhaven (140F4) | None | Padmount (1ph) | 15 | 126 | 32 | South | 140F4
132574 | 2015-10-20 | Scheduled Outage | Construction | To allow Black & Macdonald crews to replace the cables feeding V486 | None | Unknown \ Other | 1 | 216 | 4 | Central | UF10
132576 | 2015-10-20 | Scheduled Outage | Construction | Transformer X30758 at 356 Gloucester St. isolated by contractor to reframe pole and replace transformer. | None | None | 3 | 285 | 14 | Central | AB03
132578 | 2015-10-20 | Scheduled Outage | Construction | To allow K-Line to replace a pole & transfer plant to the new pole. | None | Pole | 19 | 243 | 77 | Central | AB03
132579 | 2015-10-20 | Scheduled Outage | Construction | Transformer X33676 at 323 Oakdale Ave. isolated by crew to relocate service | None | None | 10 | 60 | 10 | Central | TH01
132580 | 2015-10-20 | Scheduled Outage | Construction | Transformer X29525 at 285 Glynn Ave isolated by crew to install new pole | None | None | 16 | 233 | 62 | East | UT07
132581 | 2015-10-20 | Scheduled Outage | Construction | Transformer X33108 at 2688 Moncton Rd isolated by crew to install new service for Bell | None | None | 14 | 42 | 10 | Central | TD05
132582 | 2015-10-20 | Scheduled Outage | Construction | Transformers X27899 at 695 Buxton, X27895 at 707 Buxton and X27926 at 711 Buxton Cres isolated by crew for pole replacement | None | None | 18 | 345 | 104 | East | UZ05
132583 | 2015-10-20 | Defective Equipment | Defective Equipment/ Material | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X32663 | O/H Transformer | O/H Transformer (1ph) | 11 | 159 | 29 | Central | UV05
132584 | 2015-10-21 | Scheduled Outage | Maintenance | Reconfiguration of plant affecting 3 customers on the Nepean AB03 by Contractor | None | None | 3 | 230 | 12 | Central | AB03
132585 | 2015-10-21 | Unknown/Other | Unknown | No apparent cause found | Unknown \ Other | Unknown \ Other | 878 | 14 | 205 | East | TO2UB
132586 | 2015-10-21 | Scheduled Outage | Vegetation Management | To allow forestry crews to trim trees under the storm hardening program | None | None | 153 | 192 | 490 | East | UB07
132587 | 2015-10-21 | Defective Equipment | Mechanical Failure | Not yet known. | U/G Cable | Unknown \ Other | 1 | 85 | 1 | East | 2209
132589 | 2015-10-21 | Scheduled Outage | Construction | Transformer X27174 at 1847 Botsford St. isolated by crew to transfer plant to new pole | None | None | 16 | 186 | 50 | East | TB15
132590 | 2015-10-21 | Scheduled Outage | Construction | Transformer X27928 at 698 Fielding Dr isolated by crew for pole replacement | None | None | 14 | 48 | 11 | East | UZ05
132591 | 2015-10-21 | Defective Equipment | Defective Equipment/ Material | Red phase cable fault between TE1592 and TE354 caused S148 red fuse to blow. | U/G Cable | XLPE | 55 | 179 | 164 | South | 190F2
132592 | 2015-10-21 | Scheduled Outage | Maintenance | To allow Sproule Electric to replace elbows, inserts & defective transformers | None | Elbow \ Insert | 30 | 229 | 114 | East | CYRF4
132594 | 2015-10-21 | Scheduled Outage | Forced Switching | AB06 circuit isolated by system office for saftey reasons due to a fire at 126 Percy St. | None | None | 13 | 9 | 2 | Central | AB06
132594 | 2015-10-21 | Scheduled Outage | Forced Switching | AB06 circuit isolated by system office for saftey reasons due to a fire at 126 Percy St. | None | None | 28 | 372 | 174 | Central | AB06
132594 | 2015-10-21 | Scheduled Outage | Forced Switching | AB06 circuit isolated by system office for saftey reasons due to a fire at 126 Percy St. | None | None | 41 | 40 | 27 | Central | AB06
132594 | 2015-10-21 | Scheduled Outage | Forced Switching | AB06 circuit isolated by system office for saftey reasons due to a fire at 126 Percy St. | None | None | 41 | 52 | 36 | Central | AB06
132594 | 2015-10-21 | Scheduled Outage | Forced Switching | AB06 circuit isolated by system office for saftey reasons due to a fire at 126 Percy St. | None | None | 592 | 126 | 1243 | Central | AB06
132595 | 2015-10-21 | Defective Equipment | Mechanical Failure | To trouble shoot a defective Hydro Ottawa owned secondary cable | U/G Cable | Unknown \ Other | 15 | 24 | 6 | East | AQ02
132596 | 2015-10-21 | Defective Equipment | Mechanical Failure | To repair Hydro Ottawa owned secondary cables | U/G Cable | Unknown \ Other | 8 | 252 | 34 | East | AQ02
132596 | 2015-10-21 | Defective Equipment | Mechanical Failure | To repair Hydro Ottawa owned secondary cables | U/G Cable | Unknown \ Other | 15 | 155 | 39 | East | AQ02
132598 | 2015-10-22 | Scheduled Outage | Maintenance | The overthead at 198 MACLAREN ST was isolated to Black & mac to transfer the cables that feeds V351 to new overhead | None | O/H Conductor | 38 | 211 | 134 | Central | UX06
132599 | 2015-10-22 | Scheduled Outage | Construction | Elbow and insert replacement | None | None | 43 | 80 | 57 | East | CYRF4
132600 | 2015-10-22 | Scheduled Outage | Vegetation Management | Storm Hardening. | None | None | 21 | 250 | 88 | East | UB07
132601 | 2015-10-22 | Scheduled Outage | Construction | To reconfigure white phase overhead section. | None | None | 31 | 522 | 270 | Central | UW07
132604 | 2015-10-22 | Scheduled Outage | Maintenance | planned outage for elbow and insert replacement. | None | None | 27 | 67 | 30 | East | CYRF4
132606 | 2015-10-22 | Scheduled Outage | Maintenance | Transformer X30659-1667107 at 551 Gilmour St. isolated to replace secondary in transformer | None | None | 9 | 247 | 37 | Central | UF05
132610 | 2015-10-22 | Scheduled Outage | Construction | Transformer X23155 at 186 Marier Ave. isolated transformer to install a 1/0 triplex | None | None | 12 | 30 | 6 | East | AC06
132611 | 2015-10-22 | Scheduled Outage | Construction | Transformer X27890 at 744 Southmore Dr W isolated by crew for pole replacement | None | None | 15 | 240 | 60 | East | UZ05
132612 | 2015-10-22 | Scheduled Outage | Construction | Replacing transformer and primary cables for voltage conversion. | None | None | 1 | 320 | 5 | Central | UW01
132613 | 2015-10-23 | Scheduled Outage | Construction | Switch and arrestor replacement. | None | None | 1 | 29 | 0 | Central | TH06
132614 | 2015-10-23 | Scheduled Outage | Vegetation Management | Storm hardening. | None | None | 97 | 153 | 247 | East | AE05
132615 | 2015-10-23 | Scheduled Outage | Construction | replace leaking transformer | None | None | 7 | 86 | 10 | West | 24F1
132617 | 2015-10-23 | Foreign Interference | Wildlife (Bird/Animal) | Squrrel contact | O/H Transformer | O/H Transformer (1ph) | 8 | 55 | 7 | Central | TD01
132618 | 2015-10-23 | Scheduled Outage | Construction | TP10294 @ 320 titan was isolated to connect new service. | None | None | 1 | 196 | 3 | South | 130F4
132619 | 2015-10-24 | Scheduled Outage | Construction | VT603 at 250 Slater isolated from HOL Sources to replace transformers in the vault on the Slater (601) | None | None | 1 | 454 | 8 | Central | 601
132621 | 2015-10-25 | Tree Contacts | Broken Branch | REPLACED BLOWN FUSES AT G555 FEEDING VE7 DUE TO TREE BRANCH FALLING ON THE 3 PHASE OVERHEAD CONDUCTOR | O/H Switchgear | Fused Cutout | 1 | 52 | 1 | East | BLKF4
132622 | 2015-10-25 | Scheduled Outage | Maintenance | Overhead section from S16847 to end of line isolated to replace airbreak switch S12971, Leitrim 249F1, ID # 132622 | None | None | 3 | 203 | 10 | East | LTM01
132623 | 2015-10-25 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X27035 AND REPLACED DEFECTIVE OVERHEAD TRIPLEX SERVICE | None | None | 11 | 35 | 6 | East | TB06
132624 | 2015-10-25 | Scheduled Outage | Construction | 3 customers were affected on the Albion (2202) for isolation of SW157 in order to cut in new TP11038 at 1010 Thomas. | None | None | 3 | 198 | 10 | East | 2202
132625 | 2015-10-26 | Scheduled Outage | Maintenance | Repalcement of transformer and insert elbow replacement . By Sproule. B McNabb | None | None | 1 | 137 | 2 | East | 8F1
132626 | 2015-10-26 | Scheduled Outage | Maintenance | Transformer TP6205 isolated for replacement of rusted not leaking transformer, Limebank LMBF5, ID # 132626 | None | Padmount (1ph) | 10 | 170 | 28 | East | LMBF5
132627 | 2015-10-26 | Tree Contacts | Falling Tree | Tamarack tree trimmer dropped a lard brank on the service wire and damaged a single phase primary line. S14558 openned to make repairs. | O/H Conductor | O/H Conductor | 162 | 130 | 351 | East | UZ05
132627 | 2015-10-26 | Tree Contacts | Falling Tree | Tamarack tree trimmer dropped a lard brank on the service wire and damaged a single phase primary line. S14558 openned to make repairs. | O/H Conductor | O/H Conductor | 375 | 74 | 462 | East | UZ05
132630 | 2015-10-26 | Scheduled Outage | Construction | Woodroffe (UW07) overhead sections were isolated to transfer services to new plant and to prepare old plant for removal affecting 40 customers. | None | None | 40 | 440 | 293 | Central | UW07
132631 | 2015-10-26 | Loss Of Supply | Transmission Inadvertent | Hydro One 115KV overhead line. | None | None | 4628 | 7 | 540 | East | A6R (Russell - T1)
132631 | 2015-10-26 | Loss Of Supply | Transmission Inadvertent | Hydro One 115KV overhead line. | None | None | 5164 | 7 | 602 | East | A5RK (Russell - T2)
132631 | 2015-10-26 | Loss Of Supply | Transmission Inadvertent | Hydro One 115KV overhead line. | None | None | 15799 | 7 | 1843 | Central | A5RK (Riverdale - T2)
132632 | 2015-10-27 | Scheduled Outage | Maintenance | planned outage for elbow and insert replacment and SMD switch replacment | None | None | 2 | 102 | 3 | East | 8F1
132633 | 2015-10-27 | Scheduled Outage | Construction | To complete the removal of old white phase O/H section. | None | O/H Conductor | 45 | 480 | 360 | Central | UW07
132635 | 2015-10-27 | Scheduled Outage | Construction | TE2881 at 43 Locheland was isolated for replacement. Fallowfield FAL02. ID#132635. | None | None | 12 | 85 | 17 | South | FAL02
132636 | 2015-10-27 | Scheduled Outage | Construction | Transformer #X27208 isolated by crew to replace defective transformer | None | None | 9 | 150 | 22 | East | UQ07
132637 | 2015-10-27 | Scheduled Outage | Construction | At 09:28am FAL03 overhead between TEMP116 RWB and TEMP29RWB was isolated to allow crew to re-arrange overhead. Fallowfield (FAL03) ID# 132637 | None | None | 9 | 314 | 47 | South | FAL03
132638 | 2015-10-27 | Scheduled Outage | Construction | Transformer #X35372 isolated by crew to transfer plant to new poles | None | None | 5 | 225 | 19 | Central | AD05
132639 | 2015-10-27 | Defective Equipment | Electrical Failure | At 05:51am customsers fed from TP9342 at the rear of 23 Erskine reported a outage. Crews found a defective elbow to be the cause of outage. Bayshore (49F6) ID#132639 | U/G Cable Attachement | Elbow \ Insert | 8 | 507 | 68 | South | 49F6
132640 | 2015-10-28 | Scheduled Outage | Maintenance | planned outage for elbow and insert replacement | None | None | 14 | 87 | 20 | East | 8F4
132642 | 2015-10-28 | Scheduled Outage | Construction | Service upgrade | None | None | 8 | 84 | 11 | Central | TW22
132643 | 2015-10-28 | Scheduled Outage | Construction | SET POLES WITH CRANE | None | None | 13 | 225 | 49 | East | UZ05
132644 | 2015-10-29 | Scheduled Outage | Construction | Transformer TP9787 and switch S26268 to be isolated to allow for switch, elbow and insert replacement Moulton 8F1 | None | None | 1 | 116 | 2 | East | 8F1
132645 | 2015-10-29 | Unknown/Other | Unknown | Transformer X34133 cutout opened by squirel, Hinchey TH01 | None | None | 9 | 90 | 14 | Central | TH01
132646 | 2015-10-29 | Scheduled Outage | Maintenance | Trans Mtce | None | None | 7 | 45 | 5 | East | 8F1
132647 | 2015-10-29 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to rearranging the 347/600 V transformer bank and barricade the vault to provide working space for Broder Electric | None | None | 1 | 328 | 5 | Central | UW01
132649 | 2015-10-29 | Tree Contacts | Falling Tree | Inclement weather. High winds & driving rain | Pole Attachement | Insulator | 3 | 39 | 2 | Central | UJ03
132649 | 2015-10-29 | Tree Contacts | Falling Tree | Inclement weather. High winds & driving rain | Pole Attachement | Insulator | 22 | 96 | 35 | Central | UJ03
132650 | 2015-10-29 | Tree Contacts | Broken Branch | Fallen tree branch caused two fueses to open at G579. | O/H Conductor | O/H Conductor | 572 | 97 | 925 | East | 4801F8
132652 | 2015-10-29 | Tree Contacts | Falling Tree | A dead tree fell into the O/H wires causing an un-nomenclated fuse W & B to open | O/H Switchgear | Fused Cutout | 83 | 130 | 180 | Central | TW22
132653 | 2015-10-29 | Adverse Weather | Extreme Wind | With high winds the SR04 breaker trip, the crew patrolled the circuit and found nothing | O/H Conductor | O/H Conductor | 316 | 74 | 390 | Central | SR04
132654 | 2015-10-29 | Tree Contacts | Falling Tree | S1203 fuse opened due to fallen tree. | O/H Conductor | O/H Conductor | 19 | 353 | 112 | South | 200F3
132655 | 2015-10-29 | Tree Contacts | Falling Tree | a large tree in the back yard fell on the wires. Te customer at 184 Anna also heard a loud thump on the side of her building | O/H Switchgear | Fused Cutout | 28 | 91 | 42 | Central | SM02
132656 | 2015-10-29 | Scheduled Outage | Forced Switching | SR04 isolated to remove broken guy wire from overhead. | None | O/H Conductor | 316 | 27 | 142 | Central | SR04
132657 | 2015-10-29 | Tree Contacts | Falling Tree | A tree fell on the primary | O/H Switchgear | Fused Cutout | 49 | 119 | 97 | East | 7F4
132658 | 2015-10-29 | Tree Contacts | Tree Growth/ Untrimmed Tree | G443W and G766W fuses blown. Crew believes slake in the conductor allowed contact with tree. Conductor tightened, fuses replaced. | O/H Conductor | O/H Conductor | 68 | 9 | 10 | East | LMBF7
132658 | 2015-10-29 | Tree Contacts | Tree Growth/ Untrimmed Tree | G443W and G766W fuses blown. Crew believes slake in the conductor allowed contact with tree. Conductor tightened, fuses replaced. | O/H Conductor | O/H Conductor | 89 | 115 | 171 | East | LMBF7
132659 | 2015-10-29 | Scheduled Outage | Maintenance | Transformer #X33655 isolated by crew to replace triplex | None | None | 3 | 70 | 4 | Central | TW22
132660 | 2015-10-29 | Scheduled Outage | Vegetation Management | Transformer #X24894 isolated by crew to remove limb from service | None | None | 8 | 15 | 2 | Central | TK2AC
132661 | 2015-10-30 | Scheduled Outage | Construction | 3 customers on Woodroffe (UW01) were interrupted when P289 transformer was interrupted in order to transfer plant to new pole. | None | None | 3 | 110 | 6 | Central | UW01
132662 | 2015-10-30 | Scheduled Outage | Forced Switching | 8F1 from G529 to end of line isolated to remove fallen tree branch. | None | O/H Conductor | 21 | 15 | 5 | East | 8F1
132663 | 2015-10-30 | Scheduled Outage | Construction | TRANSFER PLANT TO NEW POLE | None | None | 8 | 180 | 24 | Central | UW06
132664 | 2015-10-30 | Scheduled Outage | Maintenance | Transformer isolated to allow contractor to remove old secondary and install new. | None | None | 19 | 214 | 68 | East | LTM01
132667 | 2015-10-31 | Scheduled Outage | Maintenance | Planned outage to allow crew to dead end and remove NIU conductor. | None | None | 1 | 485 | 8 | South | FAL01
132667 | 2015-10-31 | Scheduled Outage | Maintenance | Planned outage to allow crew to dead end and remove NIU conductor. | None | None | 1 | 500 | 8 | South | 47F6
132668 | 2015-11-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | possible tree contact | None | None | 479 | 39 | 311 | West | BECKF2
132670 | 2015-11-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact. | O/H Switchgear | Fused Cutout | 7 | 125 | 15 | Central | TD06
132671 | 2015-11-02 | Scheduled Outage | Maintenance | VT147 isolated for customer vault maintenance | None | None | 1 | 263 | 4 | Central | 5405
132672 | 2015-11-02 | Scheduled Outage | Maintenance | TP9701 isolated on the Cyrville (CYRF4) to replace base and soil remediation | None | None | 15 | 395 | 99 | East | CYRF4
132673 | 2015-11-02 | Scheduled Outage | Construction | Transformer TP2651 at 3 Hamilton Ave isolated by crew to replace porcelain switch | None | None | 63 | 30 | 32 | Central | TH06
132674 | 2015-11-02 | Scheduled Outage | Construction | Switch replacement | None | None | 1 | 43 | 1 | Central | TH06
132675 | 2015-11-02 | Scheduled Outage | Construction | Porcelain switch replacement | None | None | 2 | 68 | 2 | Central | TH06
132676 | 2015-11-02 | Scheduled Outage | Construction | Transfer and reconfigure plant to new poles. | None | None | 29 | 260 | 126 | East | AQ00
132677 | 2015-11-02 | Scheduled Outage | Vegetation Management | Storm Hardening | None | None | 27 | 338 | 152 | South | 47F3
132678 | 2015-11-02 | Scheduled Outage | Construction | Contractor transfering plant to new transformer X48261; removing X33909 at 1273 Amesbrooke Dr, X26034 at 1298 Henry Farm Dr and X33426 at 1318 Henry Farm Dr. | None | None | 23 | 230 | 88 | Central | UW06
132679 | 2015-11-02 | Scheduled Outage | Construction | Transformer X27892 at 703 Southmore Dr W isolated by crew for pole replacement | None | None | 14 | 141 | 33 | East | UZ05
132680 | 2015-11-03 | Scheduled Outage | Construction | S12538 to EOL was isolated to allow crew to install new pole and transfer plant. Walkley (UZ05) | None | None | 35 | 332 | 194 | East | UZ05
132681 | 2015-11-03 | Scheduled Outage | Vegetation Management | S24582 to EOL was isolated to allow crew to perform tree trimming for storm hardening. Riverdale (505) | None | None | 64 | 348 | 371 | Central | 505
132683 | 2015-11-03 | Scheduled Outage | Vegetation Management | S22364 open to allow for customer owned tree trimming. | None | None | 1 | 88 | 1 | West | TFXF1
132684 | 2015-11-03 | Scheduled Outage | Construction | ISOLATED TRANSFORMER 65C1A-0580 AND RELOCATED IT TO A NEW POLE | None | None | 20 | 130 | 43 | Central | SK11
132685 | 2015-11-03 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X34427 TO REPLACE POLE | None | None | 7 | 185 | 22 | Central | AK07
132686 | 2015-11-03 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30755 TO INSTALL NEW POLE | None | None | 8 | 300 | 40 | Central | AB03
132687 | 2015-11-03 | Scheduled Outage | Maintenance | S26956 to EOL was isoalted to allow crew to change porcelaine cutouts feeding VT526 | None | None | 1 | 22 | 0 | Central | TH06
132688 | 2015-11-03 | Scheduled Outage | Construction | Transfer plant to new poles | None | None | 29 | 350 | 169 | Central | UW06
132689 | 2015-11-04 | Scheduled Outage | Vegetation Management | S15173 to EOL was isolated to allow crew to perfrom tree trimming for storm hardening. Russell (TB15) | None | None | 13 | 242 | 52 | East | TB15
132690 | 2015-11-04 | Scheduled Outage | Construction | S12538 to EOL was isolated to allow crew to install new pole and transfer plant to new pole. Walkley (UZ05) | None | None | 35 | 348 | 203 | East | UZ05
132691 | 2015-11-04 | Scheduled Outage | Construction | Transformer #X26943 isolated by crew for a service upgrade | None | None | 7 | 27 | 3 | East | AJ04
132692 | 2015-11-04 | Scheduled Outage | Construction | Temp 86 to EOL was isolated to allow crew to perfrom pole repalcement. Nepean (AB03) | None | None | 23 | 354 | 136 | Central | AB03
132693 | 2015-11-04 | Scheduled Outage | Construction | Transformer #X32543 isolated by crew to replace open wire services | None | None | 16 | 45 | 12 | Central | TD06
132694 | 2015-11-04 | Scheduled Outage | Construction | 3 transformers isolated (X32818, X32819, X32820) to transfer services from 3 transformers to one | None | None | 22 | 240 | 88 | Central | UW06
132695 | 2015-11-04 | Scheduled Outage | Maintenance | Transformers TP9707,TP9714 & TP 9722 @ 1350 Ogilvie was isolated by Sproule to replace the bases and soil remediation and replace transformer TP9714. | None | Kiosk (1ph) | 28 | 547 | 255 | East | CYRF4
132696 | 2015-11-04 | Scheduled Outage | Maintenance | At 09:56am TP11137 was isolated to allow crews to perform soil remediation. Centrepoint (87F3) ID#132696 | None | None | 6 | 424 | 42 | South | 87F3
132697 | 2015-11-05 | Scheduled Outage | Construction | At 09:10am transformers TP9771, TP9772, TP9769 and TP9764 were isolated for elbow and insert replacement. Cyrville (CYRF4) ID#132697 | None | None | 70 | 159 | 186 | East | CYRF4
132698 | 2015-11-05 | Scheduled Outage | Vegetation Management | storm hardening at rear of 2212 Tawney and 2403 Howland. | None | None | 236 | 325 | 1278 | East | AE07
132699 | 2015-11-05 | Scheduled Outage | Maintenance | white phase cable replacement. | None | None | 24 | 162 | 65 | East | AP05
132700 | 2015-11-05 | Scheduled Outage | Construction | S904 opened to string new conductor & transfer plant. Limebank LMBF7. ID#132700. | None | None | 14 | 263 | 61 | East | LMBF7
132701 | 2015-11-05 | Scheduled Outage | Construction | pole installation, transfer plant and remove old o/h conductor. | None | None | 27 | 326 | 147 | Central | UW01
132702 | 2015-11-05 | Scheduled Outage | Maintenance | At 9:25am TP7658 was isolated to replace defective transformer. Bilberry (77M5) ID#132702 | None | None | 10 | 88 | 15 | East | 77M5
132704 | 2015-11-05 | Scheduled Outage | Construction | Transformer X27925 at 722 Buxton Cres. Isolated by crew for pole replacement | None | None | 12 | 246 | 49 | East | UZ05
132705 | 2015-11-05 | Scheduled Outage | Construction | Transformer X27406 at 113 Leopolds Dr isolated by 24/7 for emergency repairs | None | None | 6 | 60 | 6 | East | UZ12
132706 | 2015-11-06 | Scheduled Outage | Construction | to allow contractor to remove temporary service, and connect new service. | None | None | 1 | 175 | 3 | East | TO2UB
132707 | 2015-11-06 | Scheduled Outage | Maintenance | replace transformer P272 (TP10548) | None | None | 1 | 59 | 1 | Central | UW00
132708 | 2015-11-06 | Scheduled Outage | Construction | Transformer X27928 at 698 Fielding Dr isolated by crew for pole replacement | None | None | 14 | 215 | 50 | East | UZ05
132709 | 2015-11-06 | Scheduled Outage | Construction | Transformer #X27929 isolated by crew for a pole replacement | None | None | 14 | 115 | 27 | East | UZ05
132710 | 2015-11-06 | Scheduled Outage | Construction | Transformer X27019 at 1031 Edmond Ave. isolated by 24/7 crew to replace service | None | None | 8 | 69 | 9 | East | AE01
132711 | 2015-11-06 | Defective Equipment | Defective Equipment/ Material | Replaced broken lead frow switch to transformer X32527 | O/H Transformer | O/H Transformer (1ph) | 8 | 163 | 22 | Central | TD06
132714 | 2015-11-07 | Unknown/Other | Unknown | Blown transformer fuse at X41262, nothing found new fuse installed | Unknown \ Other | Unknown \ Other | 10 | 127 | 21 | East | 249F2
132715 | 2015-11-08 | Scheduled Outage | Forced Switching | BLKF4 O/H section between G134 and G343 was isolated to allow ON CALL crew to make repair to broken porcelain switch G162R | None | Fused Cutout | 61 | 149 | 151 | East | BLKF4
132718 | 2015-11-09 | Scheduled Outage | Maintenance | Transformer TP9785 and TP9786 at 2385 City Park wasisolated to allow the contarctor replace a transformer and replace the elbow and inserts. | None | Padmount (1ph) | 2 | 140 | 5 | East | 8F4
132719 | 2015-11-09 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry crews to clear trees under the Storm Hardening project | None | None | 38 | 174 | 110 | East | AE05
132720 | 2015-11-09 | Scheduled Outage | Vegetation Management | Tree removal from customer ownd line | None | None | 1 | 80 | 1 | East | 7F1
132722 | 2015-11-09 | Scheduled Outage | Maintenance | TP9758 and TP9759 isolated by Sproule for insert and elbow replacement. | None | None | 112 | 186 | 347 | East | CYRF4
132723 | 2015-11-10 | Scheduled Outage | Construction | Transformer TE354 isolated to allow for transformer replacement and final cable repair, Parkwoodhills 190F2, ID # 132723 | None | Padmount (1ph) | 23 | 345 | 132 | South | 190F2
132724 | 2015-11-10 | Scheduled Outage | Maintenance | Vault V665 isolated to allow Metering to correct problems with primary meters. Dagmar AC06, ID # 132724 | None | None | 1 | 18 | 0 | East | AC06
132725 | 2015-11-10 | Scheduled Outage | Maintenance | TP9760 was isolated on the Cyrville CYRF4 for Elbow and Insert replacement affecting 1 customer at 1441 Palmerstone. | None | None | 1 | 142 | 2 | East | CYRF4
132727 | 2015-11-10 | Scheduled Outage | Construction | overhead transformer X49663 isolated to allow crews to transfer plant to new pole. McCarthy (AQ00) ID #132 | None | None | 13 | 175 | 38 | East | AQ00
132729 | 2015-11-10 | Scheduled Outage | Maintenance | Transformers on City Park isolated to perform Elbow and Insert work on the Moulton 8F4 affecting 66 customers | None | None | 66 | 206 | 227 | East | 8F4
132730 | 2015-11-10 | Foreign Interference | Crane | Transformer X39223 opened to repair secondaries damaged by crane making accidental contact, Limebank LMBF7, ID # 132730 | Secondary \ Service | O/H Service | 2 | 41 | 1 | East | LMBF7
132731 | 2015-11-10 | Defective Equipment | Defective Equipment/ Material | Transformer X32305 at 1486 Laperriere Ave. isolated by crew to repair burnt neutral. | O/H Transformer | O/H Transformer (1ph) | 7 | 174 | 20 | Central | UC08
132732 | 2015-11-10 | Scheduled Outage | Construction | Transformer X35570 at 18 Lodge Rd. isolated by crew to transfer plant to new pole. | None | None | 6 | 300 | 30 | East | LMBF7
132733 | 2015-11-10 | Scheduled Outage | Construction | Transformer X49665 at 3067 Cowan Cres. Isolated by contractor to relocate open wire buss | None | None | 13 | 128 | 28 | East | AQ00
132734 | 2015-11-10 | Scheduled Outage | Construction | Transformer X34833 at 14 Ross Ave. isolated by crew to connect new service | None | None | 9 | 50 | 8 | Central | TH01
132735 | 2015-11-11 | Scheduled Outage | Maintenance | Transformers TP9775, TP9776, TP9777 isolated for elbow, insert and transformer replacement program on the Moulton 8F4. | None | None | 45 | 71 | 53 | East | 8F4
132735 | 2015-11-11 | Scheduled Outage | Maintenance | Transformers TP9775, TP9776, TP9777 isolated for elbow, insert and transformer replacement program on the Moulton 8F4. | None | None | 78 | 79 | 103 | East | 8F4
132736 | 2015-11-11 | Scheduled Outage | Construction | TE1383 on the Woodroffe 170F1 was isolated affecting 9 customers to replace leaking transformer. | None | None | 9 | 341 | 51 | South | 170F1
132737 | 2015-11-11 | Unknown/Other | Unknown | fused switch S20783 R found open, no apparent cause found, Woodroffe TW17, ID # 132737 | None | None | 29 | 96 | 46 | Central | TW17
132738 | 2015-11-11 | Scheduled Outage | Maintenance | Transformer TE1361 was isolated for replacement, Blackburn BLKF8, ID # 132738 | None | Padmount (1ph) | 10 | 172 | 29 | East | BLKF8
132739 | 2015-11-11 | Scheduled Outage | Construction | Transformer X33708 at 92 Holland Ave. isolated by crew for switch replacement | None | None | 6 | 105 | 10 | South | 130F1
132739 | 2015-11-11 | Scheduled Outage | Construction | Transformer X33708 at 92 Holland Ave. isolated by crew for switch replacement | None | None | 6 | 163 | 16 | Central | TH06
132740 | 2015-11-11 | Scheduled Outage | Maintenance | Transformer X27803 at 3001 Rankin St. isolated by contractor to transfer open wire buss | None | None | 18 | 145 | 44 | East | UZ05
132743 | 2015-11-11 | Scheduled Outage | Construction | Transformer X27898 at 647 Tubman Cres isolated by crew for pole replacement. | None | None | 13 | 132 | 29 | East | UZ05
132744 | 2015-11-11 | Scheduled Outage | Maintenance | TP9781, TP9782, TP9783 isolated from Hydro Ottawa Sources for Elbow and Insert and transformer replacement on the Moulton 8F4 | None | None | 64 | 150 | 160 | East | 8F4
132745 | 2015-11-11 | Scheduled Outage | Construction | Transformer X29291 at 1 Donald isolated by crew to install new streetlighting service | None | None | 2 | 29 | 1 | East | UT12
132746 | 2015-11-11 | Scheduled Outage | Construction | Transformer #X49660 isolated by crew to re-locate plant | None | None | 18 | 134 | 40 | East | UZ05
132747 | 2015-11-11 | Scheduled Outage | Construction | Transformer #X27929 isolated by crew to install new poles with crane. | None | None | 14 | 135 | 32 | East | UZ05
132748 | 2015-11-11 | Scheduled Outage | Construction | Transformer #X27897 isolated by crew to install new poles with cranes | None | None | 13 | 75 | 16 | East | UZ05
132749 | 2015-11-11 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X34126 opened up due to bird contact | O/H Switchgear | Fused Cutout | 11 | 40 | 7 | Central | TH01
132751 | 2015-11-11 | Scheduled Outage | Construction | Crew isolated TD06 o/h line at X32490 to replace defective transformer. | None | O/H Transformer (3ph) | 1 | 162 | 3 | Central | TD06
132752 | 2015-11-12 | Scheduled Outage | Construction | Vault V117 was isolated to allow crew to perfrom volatge conversion. Woodroffe (UW01). ID# 132752 | None | None | 1 | 256 | 4 | Central | UW01
132756 | 2015-11-12 | Defective Equipment | Defective Equipment/ Material | Broken dead end insulator at Appleford and Crownhill and defective cut outs at transformer X24604 at 1810 Appleford caused the S285 to blow. RX2017 auto reclosed during restoration attempt. Moulton (8F1). ID# 132756 | O/H Transformer | O/H Transformer (3ph) | 2 | 81 | 3 | East | 8F1
132756 | 2015-11-12 | Defective Equipment | Defective Equipment/ Material | Broken dead end insulator at Appleford and Crownhill and defective cut outs at transformer X24604 at 1810 Appleford caused the S285 to blow. RX2017 auto reclosed during restoration attempt. Moulton (8F1). ID# 132756 | O/H Transformer | O/H Transformer (3ph) | 711 | 77 | 912 | East | 8F1
132756 | 2015-11-12 | Defective Equipment | Defective Equipment/ Material | Broken dead end insulator at Appleford and Crownhill and defective cut outs at transformer X24604 at 1810 Appleford caused the S285 to blow. RX2017 auto reclosed during restoration attempt. Moulton (8F1). ID# 132756 | O/H Transformer | O/H Transformer (3ph) | 711 | 113 | 1339 | East | 8F1
132757 | 2015-11-13 | Scheduled Outage | Maintenance | Transformer KT51 was isolated to allow crew to replace brken insulator at KT51 and repalce porcelain cut out at pole. Russell (5310). ID# 132757 | None | None | 16 | 71 | 19 | East | 5310
132758 | 2015-11-13 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33708 TO REPLACE SWITCH AND ARRESTER | None | None | 6 | 35 | 4 | Central | TH06
132759 | 2015-11-13 | Scheduled Outage | Construction | UC05 between TMEP55 and TEMP83 to include the S10281 and S12119 was isolated to allow crew to transfer the S10281 and S12119 to new circuit. Clyde (UC05) | None | None | 66 | 274 | 301 | Central | UC05
132760 | 2015-11-13 | Scheduled Outage | Construction | Relocate switches. | None | None | 34 | 120 | 68 | South | 200F1
132761 | 2015-11-13 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X24992 TO CONNECT NEW STREETLIGHT SERVICE | None | None | 7 | 20 | 2 | East | AE01
132762 | 2015-11-13 | Defective Equipment | Defective Equipment/ Material | 24/7 crew repaired burnt off secondary leed and replaced connections on the other at transformer X13918 at 2925 Bank St. | O/H Transformer | O/H Transformer (1ph) | 5 | 45 | 4 | East | LTM04
132763 | 2015-11-14 | Scheduled Outage | Maintenance | 35 customers were interrupted for crews to make repairs to pole damaged by motor vehicle accident on the Jockvale 145F3 on Old Richmond Road | None | None | 35 | 125 | 73 | South | 145F3
132764 | 2015-11-14 | Scheduled Outage | Maintenance | 3 customers affected when transformers TP9773 and TP9774 were interrupted for Elbow and insert replacement on the Moulton 8F4 | None | None | 3 | 116 | 6 | East | 8F4
132765 | 2015-11-14 | Scheduled Outage | Maintenance | At 7:49am TP9791 was isolated to allow crew to replace elbows and inserts. Moulton (8F4) ID# 132765 | None | None | 1 | 74 | 1 | East | 8F4
132766 | 2015-11-14 | Scheduled Outage | Construction | Transformer #X32153 isolated by crew to transfer load to another phase | None | None | 12 | 25 | 5 | Central | TD01
132768 | 2015-11-15 | Scheduled Outage | Maintenance | At 09:03am crews isolated section of the LMBF5 to replace insulators.Limebank (LMBF5) ID# 132768 | None | None | 14 | 91 | 21 | East | LMBF5
132769 | 2015-11-15 | Scheduled Outage | Construction | At 08:54am crews isolated S206 to end of line to re-arrange overhead conductor. Limebank (LMBF7)ID#132769 | None | None | 18 | 216 | 65 | East | LMBF7
132770 | 2015-11-15 | Scheduled Outage | Construction | At 09:15am a section of the 145F3 was isolated to allow crews to install new poles. Jockvale (145F3) ID# 132770 | None | None | 9 | 498 | 75 | South | 145F3
132771 | 2015-11-15 | Scheduled Outage | Construction | At 08:52am TE1455 was isolated to allow crew to re-arrange the overhead. Limebank (LMBF5) ID# 132771 | None | None | 1 | 407 | 7 | East | LMBF5
132773 | 2015-11-16 | Scheduled Outage | Maintenance | Customer removing existing service and replacing with temp service. Also U/G group repairing leakage ROKSS switch gear. | None | Switch | 1 | 433 | 7 | Central | 608
132775 | 2015-11-16 | Scheduled Outage | Construction | Transformer #X30759 isolated by crew for a transformer replacement | None | None | 9 | 200 | 30 | Central | AB03
132776 | 2015-11-16 | Scheduled Outage | Construction | At 9:35am TP4004 and TP4005 were isolated to allow crew to move TP4005 to a new location. Jockvale(145F2)ID#132776 | None | None | 11 | 393 | 72 | South | 145F2
132777 | 2015-11-16 | Scheduled Outage | Construction | At 11:19am 145F3 between temp63W and temp69W was re-isolated to allow crew to continue installing new pole. Jockvale (145F3) ID# 132777 | None | None | 9 | 198 | 30 | South | 145F3
132778 | 2015-11-16 | Human Element | Switching Error | The UW01 circuit tripped due to overload on the W phase circuit from incorrect field switching by contractor. | Station Equipment | Relay | 0 | 1 | 0 | Central | UW01
132778 | 2015-11-16 | Human Element | Switching Error | The UW01 circuit tripped due to overload on the W phase circuit from incorrect field switching by contractor. | Station Equipment | Relay | 192 | 12 | 38 | Central | UW01
132778 | 2015-11-16 | Human Element | Switching Error | The UW01 circuit tripped due to overload on the W phase circuit from incorrect field switching by contractor. | Station Equipment | Relay | 204 | 2 | 7 | Central | UW01
132778 | 2015-11-16 | Human Element | Switching Error | The UW01 circuit tripped due to overload on the W phase circuit from incorrect field switching by contractor. | Station Equipment | Relay | 504 | 16 | 134 | Central | UW01
132778 | 2015-11-16 | Human Element | Switching Error | The UW01 circuit tripped due to overload on the W phase circuit from incorrect field switching by contractor. | Station Equipment | Relay | 1717 | 13 | 372 | Central | UW01
132778 | 2015-11-16 | Human Element | Switching Error | The UW01 circuit tripped due to overload on the W phase circuit from incorrect field switching by contractor. | Station Equipment | Relay | 1717 | 23 | 658 | Central | UW01
132778 | 2015-11-16 | Human Element | Switching Error | The UW01 circuit tripped due to overload on the W phase circuit from incorrect field switching by contractor. | Station Equipment | Relay | 1717 | 32 | 916 | Central | UW01
132779 | 2015-11-16 | Scheduled Outage | Construction | Switch Temp17 to end of line was isolated to allow crew to transfer P517 to new O/H. Woodroffe (UW01). | None | None | 11 | 171 | 31 | Central | UW01
132780 | 2015-11-16 | Defective Equipment | Electrical Failure | Defective red phase cable between S10-3 and transformer 3085. | U/G Cable | XLPE | 61 | 126 | 128 | West | 39F3
132781 | 2015-11-16 | Scheduled Outage | Construction | SMD Switch replacement S11213. | None | None | 1 | 39 | 1 | West | JKGF5
132782 | 2015-11-16 | Scheduled Outage | Construction | SMD Switch replacement on S20786. | None | None | 1 | 37 | 1 | West | JKGF5
132783 | 2015-11-16 | Scheduled Outage | Construction | SMD Switch Replacement on S22953 | None | None | 1 | 31 | 1 | West | JKGF5
132784 | 2015-11-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30755 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 8 | 140 | 19 | Central | AB03
132785 | 2015-11-17 | Scheduled Outage | Construction | SMD Switch Replacement, S27604 | None | None | 1 | 27 | 0 | West | JKGF5
132786 | 2015-11-17 | Scheduled Outage | Construction | SMD Switch Replacement S11920 | None | None | 1 | 28 | 0 | West | JKGF5
132787 | 2015-11-17 | Scheduled Outage | Construction | SMD Replacement at X10131 | None | None | 8 | 72 | 10 | West | JKGF5
132788 | 2015-11-17 | Scheduled Outage | Construction | SMD Replacment at X26570. | None | None | 1 | 50 | 1 | West | JKGF5
132789 | 2015-11-17 | Scheduled Outage | Maintenance | replace broken insulators at K148 and K149, replace porecelin cutouts at the riser pole. | None | None | 18 | 216 | 65 | East | UZ02
132791 | 2015-11-17 | Scheduled Outage | Construction | SMD Switch Replacement on S28768 | None | None | 1 | 24 | 0 | West | BRDF3
132792 | 2015-11-17 | Scheduled Outage | Construction | S18005 to Eol was isolated to allow crew to perfrom SMD switch replacement. Janet King JKGF5 | None | None | 1 | 29 | 0 | West | JKGF5
132793 | 2015-11-17 | Scheduled Outage | Construction | SMD Switch replacement at X40348 | None | None | 1 | 15 | 0 | West | JKGF5
132794 | 2015-11-17 | Scheduled Outage | Construction | SMD Switch Replacement at X39258 | None | None | 1 | 40 | 1 | West | JKGF5
132795 | 2015-11-18 | Scheduled Outage | Construction | SMD Switch Replacement at X12744 | None | None | 1 | 73 | 1 | West | JKGF5
132796 | 2015-11-18 | Scheduled Outage | Construction | SMD Switch replacement at S21153. | None | None | 1 | 7 | 0 | West | JKGF4
132797 | 2015-11-18 | Scheduled Outage | Construction | planned outage to 19 customers for pole replacement project with a crane. | None | None | 19 | 399 | 126 | East | UZ05
132798 | 2015-11-18 | Scheduled Outage | Maintenance | planned outage for secondary work | None | None | 1 | 163 | 3 | Central | 626
132799 | 2015-11-18 | Scheduled Outage | Maintenance | to replace broken insulators, and remove asbestos | None | None | 12 | 28 | 6 | East | AQ07
132800 | 2015-11-18 | Scheduled Outage | Vegetation Management | Storm Hardening | None | None | 6 | 291 | 29 | East | AJ04
132801 | 2015-11-18 | Scheduled Outage | Construction | reconfiguration of overhead | None | None | 70 | 194 | 226 | Central | UC05
132802 | 2015-11-18 | Scheduled Outage | Construction | to rearrange connections and correct phasing in Vaut V120 | None | None | 1 | 121 | 2 | Central | AB03
132803 | 2015-11-18 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X31019 TO REPLACE OPEN WIRE SECONDARY SERVICE | None | None | 17 | 45 | 13 | Central | UF05
132804 | 2015-11-18 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35471 TO UP-GRADE SECONDARY SERVICE | None | None | 8 | 10 | 1 | Central | TD01
132805 | 2015-11-18 | Scheduled Outage | Maintenance | pole replacement | None | None | 6 | 135 | 14 | East | UZ05
132806 | 2015-11-19 | Foreign Interference | Foreign Objects | Balloons in O/H at Elgin & Waverly caused UX04 to A/R & UX06 to trip. Circuit tried, tripped, tested UX06 riser cable, OK. UX06 closed & held. | None | None | 665 | 78 | 864 | Central | UX06
132807 | 2015-11-19 | Scheduled Outage | Construction | At 03:06 am S20091 was isolated of SMD switch replacement. Kanata MTS (624F6) ID # 132807 | None | None | 1 | 35 | 1 | West | 624F6
132808 | 2015-11-19 | Scheduled Outage | Construction | At 02:23 am S22842 was isolated to allow crew to replace SMD swtiches. Kanata MTS (624F6) ID# 132808 | None | None | 10 | 22 | 4 | West | 624F6
132809 | 2015-11-19 | Scheduled Outage | Construction | At 1:36 am S22627 was isolated to allow crew to replace SMD switches. Kanata MTS (624F6) ID# 132809 | None | None | 1 | 27 | 0 | West | 624F6
132810 | 2015-11-19 | Scheduled Outage | Construction | At 00:09 am crews isolated switch 4439 to allow crew to replace SMD swtiches. Kanata MTS (624F5) ID# 132810 | None | None | 3 | 37 | 2 | West | 624F5
132811 | 2015-11-18 | Scheduled Outage | Construction | At 10:23 pm S24873 was isolated to allow crew to replace SMD swtiches. Kanata MTS (624F5) ID# 132811 | None | None | 1 | 91 | 2 | West | 624F5
132812 | 2015-11-18 | Scheduled Outage | Construction | At 9:17 pm S23498 was isolated to allow crew to replace SMD switch. Kanata MTS (624F1) ID# 132812 | None | None | 3 | 43 | 2 | West | 624F1
132814 | 2015-11-19 | Scheduled Outage | Maintenance | transformer K759 was isolated to replace broken insulators and asbestos boards. McCarthy (AQ05) ID #132814 | None | Kiosk (1ph) | 9 | 112 | 17 | East | AQ05
132815 | 2015-11-19 | Scheduled Outage | Construction | OH transformer X003497 was isolated to allow creqws to transfer plant. Kanata (624F6) ID #132815 | None | None | 1 | 335 | 6 | West | 624F4
132816 | 2015-11-19 | Scheduled Outage | Maintenance | Limebank LMBF7 overhead was isolated on Prince Of Wales Drive interrupting a customer so that primary plant could be transferred | None | None | 1 | 253 | 4 | East | LMBF7
132817 | 2015-11-19 | Scheduled Outage | Maintenance | Soil Remediation at TP11182 on the Beaverbrook 24F1 affecting 7 customers at 153 Rutherford | None | None | 7 | 379 | 44 | West | 24F1
132818 | 2015-11-19 | Scheduled Outage | Construction | V117 decommisioned and TP10307 energized. Woodroffe (UW01) ID #132818 | None | None | 1 | 260 | 4 | Central | UW01
132819 | 2015-11-19 | Scheduled Outage | Maintenance | Crew transferred primary run-off to new pole interrupting 1 customer at 1027 Moodie on the Bells Corners 47F6 | None | None | 1 | 177 | 3 | South | 47F6
132821 | 2015-11-19 | Scheduled Outage | Construction | At 10:36pm switch S22992 was isolated for SMD switch replacement. Beckwith DS (BECKF2) ID#132821 | None | None | 1 | 41 | 1 | West | BECKF2
132822 | 2015-11-20 | Scheduled Outage | Construction | At 2:15am S19497 was isolated for SMD switch replacement. Bridlewood (BRDF4) ID# 132822 | None | None | 1 | 37 | 1 | West | BRDF4
132823 | 2015-11-20 | Scheduled Outage | Construction | At 04:00am switch 668 was isolated to allow SMD swtich replacement. Bridlewood (BRDF2) ID# 132823 | None | None | 1 | 74 | 1 | West | BRDF2
132824 | 2015-11-20 | Scheduled Outage | Construction | TD01 from TEMP 95 to EOL isolated to install new pole and transfer plant. | None | O/H Conductor | 33 | 189 | 104 | Central | TD01
132826 | 2015-11-20 | Scheduled Outage | Maintenance | k144 isolated to repair insulators and remove Asbestos boards. Walkey (UZ02) ID #1328 | None | None | 10 | 115 | 19 | East | UZ02
132827 | 2015-11-20 | Scheduled Outage | Construction | 2 transformers, X39373 and X39371 isolated by crew for a pole replacement | None | None | 5 | 405 | 34 | East | UZ05
132830 | 2015-11-22 | Adverse Weather | Extreme Wind | High winds caused transformer to open. | None | None | 5 | 48 | 4 | South | EPWF4
132831 | 2015-11-22 | Scheduled Outage | Construction | Switch TEMP106 to end of line was isolated to allow crew to install new pole and transfer plant. Walkley (UZ05). ID#132831 | None | None | 356 | 288 | 1709 | East | UZ05
132833 | 2015-11-22 | Scheduled Outage | Construction | LMBF7 redphase o/h line isoalted from S1024 to allow crew to remove primary and replace with secondary conductor. | None | O/H Conductor | 5 | 252 | 21 | East | LMBF7
132835 | 2015-11-22 | Foreign Interference | Wildlife (Bird/Animal) | Replaced blown fuse feeding transformer X11148 (Squirrel contact) | None | None | 4 | 53 | 4 | West | BECKF2
132836 | 2015-11-22 | Scheduled Outage | Construction | S23449 to EOL was isolated to allow crew to install new pole and transfer plant. Walkley (UZ05). ID# 132836 | None | None | 24 | 150 | 60 | East | UZ05
132837 | 2015-11-22 | Defective Equipment | Defective Equipment/ Material | Defective underground secondary. | U/G Cable | XLPE | 1 | 560 | 9 | West | MWDF3
132838 | 2015-11-23 | Scheduled Outage | Maintenance | Vault VT120 transformer bus at 200 Clearview was isolated to allow contractor to repair CB1 breaker. Hinchey TH2UL | None | None | 2 | 53 | 2 | Central | TH2UL
132839 | 2015-11-23 | Scheduled Outage | Maintenance | Transformer KT47 was isolated to allow crew to repalce broken insulator. Russell (5310) | None | None | 13 | 90 | 20 | East | 5310
132840 | 2015-11-23 | Scheduled Outage | Construction | Sproule isolated switch 138B phase at 15 Panandrick View in part of the SMD switch replacement program | None | None | 9 | 35 | 5 | West | MWDF3
132841 | 2015-11-23 | Scheduled Outage | Construction | Sproule replace switch S11923 @ 1845 OLD SECOND LINE R under the SMD switch replacement program | None | None | 1 | 5 | 0 | West | MWDF3
132842 | 2015-11-23 | Scheduled Outage | Construction | Sproule isolated switch 88W phase at 1902 McCord under the SMD switch replacement program | None | None | 26 | 26 | 11 | West | MWDF3
132843 | 2015-11-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X25673 TO REPLACE SWITCH AND ARRESTER | None | None | 14 | 20 | 5 | Central | SH05
132844 | 2015-11-23 | Scheduled Outage | Construction | Sproule isolated switch 1739 R phase at 1180 MURPHY SIDE RD under the SMD switch replacement program | None | None | 28 | 24 | 11 | West | MWDF3
132845 | 2015-11-23 | Scheduled Outage | Construction | Sproule isolated switch 248W at 9 JOHN ASELFORD DRIVEWAY to replace the switch under the SMD swit replacement program | None | None | 17 | 15 | 4 | West | MWDF3
132846 | 2015-11-23 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMERS X27982, X27980, AND X27995 AND TRANSFERRED ALL CUSTOMER TO ONE TRANSFORMER X27982 | None | None | 28 | 150 | 70 | Central | SK16
132847 | 2015-11-23 | Scheduled Outage | Construction | Sproule isolated switch S25440 under the SMD switch replacement program | None | None | 10 | 82 | 14 | West | MWDF3
132848 | 2015-11-23 | Human Element | Commissioning Error | While performing switching to transfer partial load from UW07 to UC05 the crew opened a switch that was belived to be unloaded at the time. Our System Maps did not reflect what was out in the field. Cables feeding out of SC7865 were going to different s | None | None | 195 | 13 | 42 | Central | UW07
132849 | 2015-11-23 | Defective Equipment | Mechanical Failure | While the crew was performing switching for a plan job they closed switch 582 and the W phase fuse link broke | O/H Switchgear | Inline Switch | 75 | 36 | 45 | West | 44F1
132850 | 2015-11-23 | Scheduled Outage | Maintenance | 24/7 repaired switch G318 at 5500 Bank Street. | None | None | 10 | 40 | 7 | East | 56F1
132851 | 2015-11-24 | Scheduled Outage | Construction | To Allow K-Line crews to replace the cables feeding V386 | None | Unknown \ Other | 1 | 474 | 8 | Central | AB03
132852 | 2015-11-24 | Scheduled Outage | Construction | Transformer #X41274 isolated by crew for a switch replacement | None | None | 1 | 15 | 0 | West | ALEXF2
132853 | 2015-11-24 | Scheduled Outage | Construction | Transformer #X49841 isolated by crew for a pole replacement | None | None | 10 | 165 | 28 | East | UZ05
132854 | 2015-11-24 | Scheduled Outage | Construction | Transformer #X27613 isolated by crew to drop a service for clearance | None | None | 14 | 8 | 2 | Central | UN04
132855 | 2015-11-24 | Scheduled Outage | Forced Switching | Sec. transformer bus at TE788 isolated for Fire Dept. due to gas leak | None | Padmount (1ph) | 12 | 173 | 35 | East | 8F1
132856 | 2015-11-24 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change poles at 2252 & 2274 Rembrandt | None | Pole | 29 | 252 | 122 | Central | TW22
132857 | 2015-11-24 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H1 due to defective capacitor breaker. Lisgar TS ID #132857 | None | None | 2 | 79 | 3 | Central | TC1TL
132857 | 2015-11-24 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H1 due to defective capacitor breaker. Lisgar TS ID #132857 | None | None | 48 | 69 | 55 | Central | 5211
132857 | 2015-11-24 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H1 due to defective capacitor breaker. Lisgar TS ID #132857 | None | None | 349 | 91 | 529 | Central | 5210
132857 | 2015-11-24 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H1 due to defective capacitor breaker. Lisgar TS ID #132857 | None | None | 733 | 44 | 538 | Central | TL2SB
132857 | 2015-11-24 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H1 due to defective capacitor breaker. Lisgar TS ID #132857 | None | None | 1781 | 31 | 920 | Central | TL1AM
132858 | 2015-11-25 | Scheduled Outage | Construction | TE944 isolated to reconfigure primary cables. | None | XLPE | 6 | 24 | 2 | South | 87F7
132859 | 2015-11-25 | Scheduled Outage | Construction | S17183 isolated for SMD switch replacement. Marchwood (MWDF3) | None | None | 25 | 10 | 4 | West | MWDF3
132860 | 2015-11-25 | Scheduled Outage | Construction | Transformer #X06896 isoalted by crew to replace switch | None | None | 2 | 10 | 0 | West | MWDF3
132862 | 2015-11-25 | Scheduled Outage | Construction | REPLACE SMD SWITCH S28063 | None | None | 59 | 35 | 34 | West | MWDF3
132863 | 2015-11-25 | Scheduled Outage | Construction | Transformer #X19158 isolated by crew to transfer plant | None | None | 2 | 145 | 5 | East | BLKF3
132864 | 2015-11-25 | Scheduled Outage | Construction | S28063 isolated for SMD switch replacement. Marchwood (MWDF3) | None | None | 59 | 30 | 30 | West | MWDF3
132865 | 2015-11-25 | Defective Equipment | Electrical Failure | TO2AP cable fault between TO and S-375 | U/G Cable | Unknown \ Other | 57 | 138 | 131 | East | TO2AP
132866 | 2015-11-25 | Scheduled Outage | Construction | SET A NEW POLE | None | None | 13 | 283 | 61 | East | UZ05
132867 | 2015-11-25 | Scheduled Outage | Construction | set/ transfer plant to nw pole | None | None | 7 | 265 | 31 | East | UZ05
132868 | 2015-11-25 | Scheduled Outage | Construction | Switch 1050 isolated for SMD switch replacment. Kanata (624F6) | None | None | 3 | 60 | 3 | West | 624F6
132869 | 2015-11-25 | Scheduled Outage | Construction | Switch 1103 isolated for smd switch replacment. Kanata (624F6) | None | None | 3 | 57 | 3 | West | 624F6
132871 | 2015-11-26 | Scheduled Outage | Construction | REPLACE SMD SWITCH | None | None | 10 | 30 | 5 | West | JKGF5
132873 | 2015-11-26 | Scheduled Outage | Maintenance | V114 at 1800 Baseline Rd was isolated by K Line to de-commission the old vault and energize a new TP10550 | None | Transformer | 1 | 221 | 4 | Central | UW01
132874 | 2015-11-26 | Scheduled Outage | Construction | REPLACING OVERHEAD TRANS AND REARRANGE PLANT | None | None | 6 | 210 | 21 | Central | AB03
132875 | 2015-11-26 | Scheduled Outage | Maintenance | Not yet known. | None | None | 1 | 240 | 4 | East | LMBF7
132876 | 2015-11-26 | Defective Equipment | Defective Equipment/ Material | Transformer #X21828 opened up due to broken switch | O/H Switchgear | Fused Cutout | 8 | 60 | 8 | West | 28F1
132878 | 2015-11-26 | Human Element | Improper Construction/installation | The 22M27 ARA due to S15785 W latch was not hinged properly and switch opened causing flash across all three phases. Nepean TS | O/H Switchgear | Inline Switch | 3596 | 43 | 2577 | South | 22M27
132878 | 2015-11-26 | Human Element | Improper Construction/installation | The 22M27 ARA due to S15785 W latch was not hinged properly and switch opened causing flash across all three phases. Nepean TS | O/H Switchgear | Inline Switch | 7650 | 3 | 382 | South | 22M27
132880 | 2015-11-27 | Defective Equipment | Defective Equipment/ Material | A cable fault on the B phase bet K579 and S20165 at 1561 Heron Rd | U/G Cable | Unknown \ Other | 78 | 60 | 78 | East | UA11
132880 | 2015-11-27 | Defective Equipment | Defective Equipment/ Material | A cable fault on the B phase bet K579 and S20165 at 1561 Heron Rd | U/G Cable | Unknown \ Other | 94 | 15 | 24 | East | UA11
132880 | 2015-11-27 | Defective Equipment | Defective Equipment/ Material | A cable fault on the B phase bet K579 and S20165 at 1561 Heron Rd | U/G Cable | Unknown \ Other | 118 | 20 | 39 | East | UA11
132880 | 2015-11-27 | Defective Equipment | Defective Equipment/ Material | A cable fault on the B phase bet K579 and S20165 at 1561 Heron Rd | U/G Cable | Unknown \ Other | 118 | 240 | 472 | East | UA11
132880 | 2015-11-27 | Defective Equipment | Defective Equipment/ Material | A cable fault on the B phase bet K579 and S20165 at 1561 Heron Rd | U/G Cable | Unknown \ Other | 212 | 10 | 35 | East | UA11
132881 | 2015-11-28 | Scheduled Outage | Maintenance | VT508 was isolated for vault maintenance. Slater (606) ID #132881 | None | None | 1 | 362 | 6 | Central | 606
132883 | 2015-11-28 | Scheduled Outage | Maintenance | VE84 was isolated from HOL Sources to replace overhead switches and repair defective pothead at 17 DeNiverville affecting 1 customer on the Uplands 4801F8 | None | None | 1 | 388 | 6 | East | 4801F8
132885 | 2015-11-29 | Scheduled Outage | Maintenance | Vault isolated for routine customer vault maintenance. | None | None | 1 | 280 | 5 | Central | 614
132886 | 2015-11-29 | Scheduled Outage | Maintenance | HOL Crews isolated TP4837 on the Fallowfield FAL03 affecting 1 customer to transfer overhead plant. | None | None | 1 | 405 | 7 | South | FAL03
132887 | 2015-11-29 | Defective Equipment | Mechanical Failure | Not yet known, Crew performed the patrol with no results for the cause of outage | O/H Switchgear | Unknown \ Other | 184 | 18 | 55 | East | TO2UT
132890 | 2015-11-30 | Scheduled Outage | Maintenance | Routine customer vault maintenance | None | None | 1 | 195 | 3 | Central | 602
132891 | 2015-11-30 | Scheduled Outage | Construction | TP8911 isolated for transformer replacement and soil remediaition. Janet King (JKGF4) | None | None | 1 | 716 | 12 | West | JKGF4
132892 | 2015-11-30 | Scheduled Outage | Maintenance | Overhead section from TEMP 23 to end of line isolated for civil work on the building at 30 Mountain. Cahill AN06, ID # 132892 | None | None | 2 | 315 | 10 | East | AN06
132893 | 2015-11-30 | Scheduled Outage | Construction | 9 customers affected on the Janet King JKGF4, crew isolated overhead X38792 to replace transformer switch and brackets. | None | None | 9 | 19 | 3 | West | JKGF4
132894 | 2015-11-30 | Scheduled Outage | Construction | Transformer X27936 isolated as part of the pole replacement program. Walkley UZ05 ID # 132894 | None | None | 9 | 164 | 25 | East | UZ05
132895 | 2015-11-30 | Scheduled Outage | Construction | Janet King JKGF5 equipment isolated by contractor to replace switches affecting 138 customers | None | None | 138 | 56 | 129 | West | JKGF5
132896 | 2015-11-30 | Scheduled Outage | Construction | UW07 OH isolated to allow crews to completed connection for 13KV conversion project. Woodroffe UW07) ID #132 | None | O/H Conductor | 400 | 250 | 1667 | Central | UW07
132897 | 2015-11-30 | Scheduled Outage | Maintenance | Transformer X30501 at 52 Maclaren St. isolated by contractor to change neutral | None | None | 19 | 277 | 88 | Central | UX09
132898 | 2015-11-30 | Scheduled Outage | Construction | Transformer #X30443 (streetlighting) isolated by crew to replace transformer | None | None | 1 | 259 | 4 | Central | SB02
132899 | 2015-11-30 | Defective Equipment | Electrical Failure | Cable between TE27 and TE621 suspected fault caused S20555 to open. Manordale 84F2 | U/G Cable | Unknown \ Other | 22 | 10 | 4 | South | 84F2
132899 | 2015-11-30 | Defective Equipment | Electrical Failure | Cable between TE27 and TE621 suspected fault caused S20555 to open. Manordale 84F2 | U/G Cable | Unknown \ Other | 29 | 5 | 2 | South | 84F2
132899 | 2015-11-30 | Defective Equipment | Electrical Failure | Cable between TE27 and TE621 suspected fault caused S20555 to open. Manordale 84F2 | U/G Cable | Unknown \ Other | 48 | 140 | 112 | South | 84F2
132900 | 2015-11-30 | Scheduled Outage | Maintenance | PT260 was isolated to repair defective riser switches. Lincoln Hieghts (TD05) ID #132 | None | Fused Cutout | 1 | 50 | 1 | Central | TD05
132902 | 2015-12-01 | Scheduled Outage | Construction | A section of Woodroffe UW07 (4KV) was isolated for conversiion to 13 KV. ID#132902. | None | None | 290 | 191 | 923 | Central | UW07
132903 | 2015-12-01 | Scheduled Outage | Construction | Transformer #X27934 isolated by crew for a pole replacement | None | None | 7 | 210 | 24 | East | UZ05
132904 | 2015-12-01 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35542 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 20 | 40 | 13 | Central | TD05
132905 | 2015-12-01 | Defective Equipment | Defective Equipment/ Material | While isolating RWB cable section between 196RWB and transformer 3032 @ 297 Didsbury Rd. Crews pulled the transformer bushing out of the transformer while isolation the red phase cable. A flash caused S211-CB3 to open causing an outage to 37 customers. | U/G Transformer | Padmount (3ph) | 1 | 156 | 3 | West | 624F1
132905 | 2015-12-01 | Defective Equipment | Defective Equipment/ Material | While isolating RWB cable section between 196RWB and transformer 3032 @ 297 Didsbury Rd. Crews pulled the transformer bushing out of the transformer while isolation the red phase cable. A flash caused S211-CB3 to open causing an outage to 37 customers. | U/G Transformer | Padmount (3ph) | 37 | 75 | 46 | West | 624F1
132906 | 2015-12-01 | Defective Equipment | Electrical Failure | Cable fault between SC19919 & TV3491 on Richmond rd caused TM23 to trip. Some load transferred to alternate supply, fault finding performed to locate defective cable. VT549, VT908 & SC19919 were on radial supply due to cable reconfiguration feeding VT549 | U/G Cable | XLPE | 4 | 526 | 35 | Central | TM1AH
132906 | 2015-12-01 | Defective Equipment | Electrical Failure | Cable fault between SC19919 & TV3491 on Richmond rd caused TM23 to trip. Some load transferred to alternate supply, fault finding performed to locate defective cable. VT549, VT908 & SC19919 were on radial supply due to cable reconfiguration feeding VT549 | U/G Cable | XLPE | 263 | 137 | 601 | Central | TM1AH
132906 | 2015-12-01 | Defective Equipment | Electrical Failure | Cable fault between SC19919 & TV3491 on Richmond rd caused TM23 to trip. Some load transferred to alternate supply, fault finding performed to locate defective cable. VT549, VT908 & SC19919 were on radial supply due to cable reconfiguration feeding VT549 | U/G Cable | XLPE | 556 | 20 | 185 | Central | TM1AH
132906 | 2015-12-01 | Defective Equipment | Electrical Failure | Cable fault between SC19919 & TV3491 on Richmond rd caused TM23 to trip. Some load transferred to alternate supply, fault finding performed to locate defective cable. VT549, VT908 & SC19919 were on radial supply due to cable reconfiguration feeding VT549 | U/G Cable | XLPE | 810 | 36 | 486 | Central | TM1AH
132907 | 2015-12-02 | Scheduled Outage | Maintenance | At 8:44am section of SB05 from S14343 to end of line was isolated to allow crew to remove a section of parrallel conductor. Bronson (SB05) ID# 132907 | None | None | 77 | 131 | 168 | Central | SB05
132908 | 2015-12-02 | Scheduled Outage | Vegetation Management | A section of Beechwood UB07 from S22505B to EOL was isolated for storm hardening at the rear of 22 Birch. ID#132908. | None | None | 63 | 393 | 413 | East | UB07
132909 | 2015-12-02 | Scheduled Outage | Construction | At 11:30am TH06 was isolated from S16011 to allow crew to replace switches . Hinchey (TH06) ID# 132909 | None | None | 49 | 210 | 172 | Central | TH06
132910 | 2015-12-02 | Human Element | Improper Construction/installation | While crew restoring VT547 after planned work, S23025 W & B opened. S23025 R opened after line cleared & load restored via alternate supply. Hinchey TH06. ID#132910. | Pole Attachement | Arrester | 552 | 25 | 230 | Central | TH06
132910 | 2015-12-02 | Human Element | Improper Construction/installation | While crew restoring VT547 after planned work, S23025 W & B opened. S23025 R opened after line cleared & load restored via alternate supply. Hinchey TH06. ID#132910. | Pole Attachement | Arrester | 792 | 18 | 238 | Central | TH06
132911 | 2015-12-02 | Scheduled Outage | Construction | A section of Woodroffe UW01 was isolated for voltage conversion & plant upgrade. ID#132911. | None | None | 195 | 305 | 991 | Central | UW01
132913 | 2015-12-03 | Scheduled Outage | Maintenance | Routine maintennace on customer owned vault. Clean and torque | None | None | 1 | 198 | 3 | East | UT07
132914 | 2015-12-03 | Scheduled Outage | Maintenance | Vault isolated by Sproule to prove spare ducts available for new cables. | None | None | 1 | 169 | 3 | Central | SA23
132915 | 2015-12-03 | Defective Equipment | Electrical Failure | 77M6 circuit opened due to suspected cable fault at SC2449. 77M2 circuit interrupted during restoration switching due to cold load pick up. | U/G Cable | XLPE | 158 | 61 | 161 | East | 77M6
132915 | 2015-12-03 | Defective Equipment | Electrical Failure | 77M6 circuit opened due to suspected cable fault at SC2449. 77M2 circuit interrupted during restoration switching due to cold load pick up. | U/G Cable | XLPE | 241 | 18 | 72 | East | 77M6
132915 | 2015-12-03 | Defective Equipment | Electrical Failure | 77M6 circuit opened due to suspected cable fault at SC2449. 77M2 circuit interrupted during restoration switching due to cold load pick up. | U/G Cable | XLPE | 794 | 10 | 132 | East | 77M6
132915 | 2015-12-03 | Defective Equipment | Electrical Failure | 77M6 circuit opened due to suspected cable fault at SC2449. 77M2 circuit interrupted during restoration switching due to cold load pick up. | U/G Cable | XLPE | 3410 | 4 | 227 | East | 77M2
132915 | 2015-12-03 | Defective Equipment | Electrical Failure | 77M6 circuit opened due to suspected cable fault at SC2449. 77M2 circuit interrupted during restoration switching due to cold load pick up. | U/G Cable | XLPE | 4665 | 2 | 156 | East | 77M6
132915 | 2015-12-03 | Defective Equipment | Electrical Failure | 77M6 circuit opened due to suspected cable fault at SC2449. 77M2 circuit interrupted during restoration switching due to cold load pick up. | U/G Cable | XLPE | 5032 | 67 | 5619 | East | 77M6
132916 | 2015-12-03 | Scheduled Outage | Construction | Transformer X33574 at 1539 Arnhem St. isolated by crew for pole change | None | None | 13 | 360 | 78 | Central | AK10
132917 | 2015-12-04 | Scheduled Outage | Construction | TP6204 isolated for transfomrer and elbow replacment. Jockvale (145F4) | None | Padmount (1ph) | 6 | 117 | 12 | South | 145F4
132918 | 2015-12-04 | Foreign Interference | Wildlife (Bird/Animal) | Field Operators refused transformer X28229 at 1301 Dowler Ave. | O/H Switchgear | Fused Cutout | 10 | 104 | 17 | Central | 505
132919 | 2015-12-04 | Scheduled Outage | Construction | Transformer X23734 at 377 Iberville St. isolated by crew for pole replacement | None | None | 9 | 35 | 5 | East | AA03
132920 | 2015-12-04 | Scheduled Outage | Maintenance | Transformer X24612 at 2068 Beaverhill Dr isolated by crew to repair corroded connections at the transformer and change the switch assembly | None | None | 12 | 61 | 12 | East | BCHF1
132921 | 2015-12-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | Not yet known. | None | None | 30 | 99 | 50 | West | 624F6
132922 | 2015-12-06 | Scheduled Outage | Construction | install new switch SC19616. | None | None | 1 | 202 | 3 | East | 5310
132923 | 2015-12-06 | Scheduled Outage | Construction | convert UW07 4kv customers to TW18 13kv. | None | None | 355 | 318 | 1882 | Central | UW07
132924 | 2015-12-06 | Defective Equipment | Defective Equipment/ Material | defective fuse cutout | O/H Switchgear | Fused Cutout | 2 | 90 | 3 | West | 624F6
132925 | 2015-12-06 | Defective Equipment | Defective Equipment/ Material | Replace defective transformer. | U/G Transformer | Padmount (1ph) | 30 | 110 | 55 | East | 8F1
132926 | 2015-12-06 | Scheduled Outage | Maintenance | 13KV transformer busses only at VT367. Isolated to allow contractor to replace 600 volt breaker. | None | Breaker \ Relay | 1 | 720 | 12 | Central | TK5TS
132927 | 2015-12-07 | Scheduled Outage | Construction | VOLTAGE CONVERSION FROM 4KV TO 13KV | None | None | 31 | 96 | 50 | Central | UW01
132928 | 2015-12-07 | Scheduled Outage | Construction | Transfer plant to new pole | None | None | 12 | 180 | 36 | Central | TH01
132929 | 2015-12-07 | Scheduled Outage | Construction | 4kv to 13KV voltage conversion | None | None | 108 | 31 | 56 | Central | UW01
132930 | 2015-12-07 | Scheduled Outage | Construction | Replace inserts and elbows to vented model. | None | None | 19 | 82 | 26 | West | 44F3
132931 | 2015-12-07 | Scheduled Outage | Construction | 4kv to 13kv voltage conversion | None | None | 1 | 40 | 1 | Central | UW07
132932 | 2015-12-08 | Scheduled Outage | Construction | TP9760 isolated for soil remediation. | None | Padmount (1ph) | 1 | 557 | 9 | East | CYRF4
132933 | 2015-12-08 | Scheduled Outage | Construction | S14296 to EOL was isolated to allow crew to replace the porcelain switch | None | None | 22 | 10 | 4 | Central | TH06
132934 | 2015-12-08 | Scheduled Outage | Construction | UW00 line coplete was isolated to allow cew to convert line to 13 KV | None | None | 4 | 97 | 6 | Central | UW00
132935 | 2015-12-08 | Defective Equipment | Defective Equipment/ Material | Switch S22505 B phase opened due to undersize fuse. Crew replace 80 Amp fuse with 140 Amp fuse. | O/H Switchgear | Fused Cutout | 63 | 126 | 132 | East | UB07
132936 | 2015-12-08 | Scheduled Outage | Construction | Transformer KT548 at 2950 Penny was isolated to allow crew to replace transformer. | None | None | 15 | 398 | 100 | Central | TD12
132938 | 2015-12-08 | Scheduled Outage | Construction | Transformer X15192 at 3852 Leitrim Rd isolated by crew for transformer replacement for upgrading | None | None | 7 | 75 | 9 | East | LTM04
132939 | 2015-12-08 | Foreign Interference | Wildlife (Bird/Animal) | Field Operators refused transformer X48654 at 1133 Agincourt Rd - cause was animal interference, squirrel | O/H Switchgear | Fused Cutout | 17 | 148 | 42 | Central | UW07
132940 | 2015-12-08 | Scheduled Outage | Maintenance | To clean and torque VT560 and bucket crew to change porcelain cutouts. | None | None | 1 | 202 | 3 | Central | TH06
132941 | 2015-12-08 | Scheduled Outage | Construction | Transformer 2654R was isolated to allow crew reconfigure U/G cable | None | None | 11 | 410 | 75 | West | 24F1
132942 | 2015-12-08 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X45153 isolated by crew due to squirrel contact | O/H Switchgear | Fused Cutout | 16 | 99 | 26 | Central | UW07
132943 | 2015-12-09 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to transfer cables to a new pole | None | None | 4 | 250 | 17 | East | TB07
132944 | 2015-12-09 | Scheduled Outage | Maintenance | Temp 90 to EOL was isoalted to allow crew to repalce insulators. Langs (AP02) | None | None | 1 | 431 | 7 | East | AP02
132946 | 2015-12-09 | Adverse Environment | Flood | VE27 isolated due to flooding. | None | None | 1 | 434 | 7 | East | BLKF8
132947 | 2015-12-09 | Scheduled Outage | Construction | Transformer X11343 at 7211 Franktown Rd isolated by crew for transformer replacement | None | None | 2 | 113 | 4 | West | 43F3
132948 | 2015-12-10 | Scheduled Outage | Vegetation Management | At 8:34am UG07 was isolated from Pole 65A3B-0350 to end of line for tree removal. Vaughan (UG07) ID# 132948 | None | None | 15 | 371 | 93 | East | UG07
132949 | 2015-12-10 | Scheduled Outage | Maintenance | At 8:02am crews isolated the AP02 from Temp90 to end of line to allow crew to replace insulators. Langs Road (AP02) ID# 132949 | None | None | 1 | 183 | 3 | East | AP02
132950 | 2015-12-10 | Scheduled Outage | Maintenance | Replace a leaking transformer and oil clean up by Drain-All. | None | Kiosk (1ph) | 5 | 397 | 33 | East | 77M2
132951 | 2015-12-10 | Scheduled Outage | Construction | Change broken insulator on live front transformer 2655. 2654 isolated for remediation and transformer change, | None | None | 7 | 517 | 60 | West | 24F1
132951 | 2015-12-10 | Scheduled Outage | Construction | Change broken insulator on live front transformer 2655. 2654 isolated for remediation and transformer change, | None | None | 18 | 91 | 27 | West | 24F1
132952 | 2015-12-10 | Scheduled Outage | Maintenance | Isolated Transformer X33686 to replace cut out and arrestor. | None | None | 4 | 53 | 4 | Central | TH01
132953 | 2015-12-10 | Scheduled Outage | Construction | At 9:36am Sproule isolated V341 to install new cables. Slater (SA23) ID# 132953 | None | None | 1 | 195 | 3 | Central | SA23
132955 | 2015-12-10 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X34142 TO REPLACE SWITCH AND ARRESTER | None | None | 9 | 25 | 4 | Central | TH01
132957 | 2015-12-10 | Unknown/Other | Unknown | 24/7 refused transformer X31926 at 369 Zephyr Ave | O/H Transformer | O/H Transformer (1ph) | 16 | 46 | 12 | Central | TD14
132958 | 2015-12-11 | Scheduled Outage | Construction | planned outage to pull in new secondary services. | None | None | 13 | 271 | 59 | South | FAL02
132959 | 2015-12-11 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact. (crow) Replaced blown fuse at transformer X35321. | O/H Transformer | O/H Transformer (1ph) | 6 | 84 | 8 | Central | TW22
132961 | 2015-12-11 | Scheduled Outage | Maintenance | outage to replace 3 broken switches. | None | None | 14 | 29 | 7 | East | UT12
132962 | 2015-12-11 | Defective Equipment | Electrical Failure | S1160 opened due to defective elbow at TP11035 Oncall crew made repirs to defective elbow | U/G Cable Attachement | Elbow \ Insert | 8 | 221 | 29 | South | 130F2
132963 | 2015-12-12 | Unknown/Other | Unknown | Fuse at G696 found open, refused and closed. No cause found. Upland (4801F8) ID# | Unknown \ Other | Unknown \ Other | 30 | 85 | 42 | East | 4801F8
132964 | 2015-12-12 | Scheduled Outage | Construction | Transfomrer 5624 and 5625 isolated for removale and to energize new TP7241. South March (39F2) ID# | None | None | 6 | 456 | 46 | West | 39F2
132965 | 2015-12-12 | Scheduled Outage | Maintenance | Customer owned vault shut down for routine maintenance by Eaton. | None | None | 1 | 315 | 5 | Central | TL2TS
132967 | 2015-12-12 | Foreign Interference | Wildlife (Bird/Animal) | Transformer fuse blown due to squirrel contact. | None | None | 14 | 65 | 15 | East | TB14
132968 | 2015-12-12 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X1562 fuse blown due to squirrel contact | None | None | 2 | 45 | 2 | East | 56F1
132969 | 2015-12-13 | Defective Equipment | Electrical Failure | Suspected cable fault between SB05 and PPH Switches. Circuit transferred to SB00 | U/G Cable | PILC | 726 | 142 | 1718 | Central | SB05
132970 | 2015-12-13 | Scheduled Outage | Maintenance | 13kv Vault TV3060 isolated to allow contractor to clean vault and torque connections. | None | None | 1 | 170 | 3 | Central | 618
132971 | 2015-12-14 | Adverse Environment | Fire | TR09 was forced open to allow crew to extinguish pole fire | Pole | Pole | 10 | 2 | 0 | Central | TR09
132971 | 2015-12-14 | Adverse Environment | Fire | TR09 was forced open to allow crew to extinguish pole fire | Pole | Pole | 10 | 180 | 30 | Central | TR09
132971 | 2015-12-14 | Adverse Environment | Fire | TR09 was forced open to allow crew to extinguish pole fire | Pole | Pole | 469 | 144 | 1126 | Central | TR09
132971 | 2015-12-14 | Adverse Environment | Fire | TR09 was forced open to allow crew to extinguish pole fire | Pole | Pole | 1527 | 8 | 204 | Central | TR09
132972 | 2015-12-14 | Scheduled Outage | Construction | Isolation to replace switches and arresters. | None | None | 58 | 31 | 30 | Central | TH06
132973 | 2015-12-14 | Scheduled Outage | Construction | TP2853 isolated for transfomer upgrade. Lincoln Heights (TD05) ID#132973 | None | Padmount (3ph) | 1 | 4387 | 73 | Central | TD05
132974 | 2015-12-14 | Scheduled Outage | Construction | Switch S14696 RWB isolated for SMD replacement. Kanata (624F6) ID#132974 | None | None | 32 | 120 | 64 | West | 624F6
132975 | 2015-12-14 | Scheduled Outage | Construction | Isolation from S15221 ro replace porcelian switch | None | None | 102 | 87 | 148 | Central | TH06
132976 | 2015-12-14 | Scheduled Outage | Construction | Transformer #X40033 isolated by crew to replace pole | None | None | 2 | 105 | 4 | South | 145F3
132977 | 2015-12-14 | Scheduled Outage | Construction | TXFF1 isolated from RX2013 to EOL for SMD replacment aty S25248B | None | None | 74 | 27 | 33 | West | TFXF1
132978 | 2015-12-14 | Scheduled Outage | Construction | Transformer #X34117 isolated by crew to replace a rotten pole | None | None | 12 | 305 | 61 | Central | TH01
132979 | 2015-12-14 | Scheduled Outage | Construction | Transformer #X29231 isolated by crew to transfer plant | None | None | 2 | 315 | 10 | East | UG09
132980 | 2015-12-14 | Scheduled Outage | Maintenance | AP02 from TEMP 90 to EOL for insulator replacement. | None | None | 1 | 472 | 8 | East | AP02
132981 | 2015-12-14 | Scheduled Outage | Maintenance | Owner install new cable to building. Outage to cut over from generator to new cable. | None | None | 1 | 36 | 1 | Central | UC08
132982 | 2015-12-14 | Scheduled Outage | Construction | To install new cable and terminations on S57-4 and completing the loop to TP8974. | None | None | 18 | 236 | 71 | West | 39F2
132983 | 2015-12-15 | Scheduled Outage | Vegetation Management | S28766 to EOL isolate for tree trimming. Munster (43F3) ID #132983 | None | None | 1 | 358 | 6 | West | 43F3
132987 | 2015-12-15 | Scheduled Outage | Construction | TP2810 was isolated to allow crews to replace elbows and inserts. Kanata (624F1) ID #132 | None | None | 1 | 50 | 1 | West | 624F1
132988 | 2015-12-15 | Scheduled Outage | Construction | Overhead section isolated from TEMP 90 to end of line to complete tree trimming and insulator changes. Langs AP02, ID # 132988 | None | None | 1 | 480 | 8 | East | AP02
132989 | 2015-12-16 | Scheduled Outage | Vegetation Management | Overhead section from TEMP 90 to end of line isolated to allow for tree clearance and insulator replacement, Langs AP02, ID# 132989 | None | None | 1 | 490 | 8 | East | AP02
132990 | 2015-12-16 | Scheduled Outage | Vegetation Management | Overhead section from S13037 to end of line isolated to allow for tree trimming, Lincoln TD01, ID # 132990 | None | None | 15 | 292 | 73 | Central | TD01
132992 | 2015-12-16 | Scheduled Outage | Construction | MWDF3 blue phase OH from switch 128 to EOL was isolated for SMD upgrade. Marchwood (MWDF3) ID #132992 | None | None | 20 | 133 | 44 | West | MWDF3
132993 | 2015-12-16 | Defective Equipment | Electrical Failure | Cable sections fed from AQ09 blue phase dip to K130 opened interupting K130, K129, K128 and K125, blown lightening arrestor in K130. McCarthy AQ09, ID # 132993 | U/G Cable Attachement | Arrester | 10 | 7 | 1 | East | AQ09
132993 | 2015-12-16 | Defective Equipment | Electrical Failure | Cable sections fed from AQ09 blue phase dip to K130 opened interupting K130, K129, K128 and K125, blown lightening arrestor in K130. McCarthy AQ09, ID # 132993 | U/G Cable Attachement | Arrester | 20 | 13 | 4 | East | AQ09
132993 | 2015-12-16 | Defective Equipment | Electrical Failure | Cable sections fed from AQ09 blue phase dip to K130 opened interupting K130, K129, K128 and K125, blown lightening arrestor in K130. McCarthy AQ09, ID # 132993 | U/G Cable Attachement | Arrester | 29 | 17 | 8 | East | AQ09
132993 | 2015-12-16 | Defective Equipment | Electrical Failure | Cable sections fed from AQ09 blue phase dip to K130 opened interupting K130, K129, K128 and K125, blown lightening arrestor in K130. McCarthy AQ09, ID # 132993 | U/G Cable Attachement | Arrester | 41 | 86 | 59 | East | AQ09
132994 | 2015-12-17 | Scheduled Outage | Construction | Transformer X34467 at 1 Noel St. isolated by crew to rearange plant | None | None | 15 | 127 | 32 | East | UG03
132995 | 2015-12-17 | Foreign Interference | Vehicle | MVA damged pole X45946 and primary cable into V238. Carling (SM01) ID#132995 | U/G Cable | PILC | 1 | 26924 | 449 | Central | SM01
132996 | 2015-12-18 | Scheduled Outage | Maintenance | Transformer TP4146 was isolated to allow crew to perform transformer soil remediation. Moulton (8F1) | None | None | 30 | 515 | 258 | East | 8F1
132998 | 2015-12-19 | Scheduled Outage | Maintenance | VT318 was isolated for contractor to perform routine vault maintenance affecting 1 customer at 2100 Walkley Road. | None | None | 1 | 343 | 6 | East | ELW13
132999 | 2015-12-19 | Defective Equipment | Mechanical Failure | Urbandale AE02 B phase lead at rear of 2144 Carnegie burned off. Lead replaced & power restored. ID#132999. | O/H Conductor | Hot-Line Clamp | 16 | 113 | 30 | East | AE02
133001 | 2015-12-21 | Scheduled Outage | Maintenance | Service upgrade. | None | None | 6 | 61 | 6 | Central | TH01
133003 | 2015-12-22 | Scheduled Outage | Vegetation Management | storm Hardening | None | None | 24 | 205 | 82 | East | UZ05
133031 | 2015-12-25 | Foreign Interference | Vehicle | Vehicle accident broke off a pole tripping the breaker at the station, Blackburn BLKF5, ID # 133 | Pole | Pole | 45 | 360 | 270 | East | BLKF5
133032 | 2015-12-26 | Scheduled Outage | Vegetation Management | tree on primary and secondary | None | None | 14 | 75 | 18 | Central | AH02
133033 | 2015-12-27 | Defective Equipment | Electrical Failure | defective red phase rabbit WX2052 | O/H Transformer | Step Transformer (Rabbit) | 79 | 165 | 217 | South | FAL03
133034 | 2015-12-27 | Tree Contacts | Falling Tree | TD05 o/h line isolated to allow Davey Tree to remove a large tree off the primary in the rear of 987 Farrell. | O/H Conductor | O/H Conductor | 289 | 34 | 164 | Central | TD05
133035 | 2015-12-27 | Defective Equipment | Defective Equipment/ Material | Defective cable between transformer 2529W and switch 299W cause the switch 299 to blow. | U/G Cable | XLPE | 59 | 134 | 132 | West | BRDF5
133038 | 2015-12-28 | Adverse Weather | Extreme Wind | Auto Reclose on station breaker blue phase flag, 3 phase inline recloser RX2060 tripped also blue phase flags, Janet King JKGF4, ID # 133038 | None | None | 200 | 81 | 270 | West | JKGF4
133039 | 2015-12-29 | Adverse Weather | Extreme Wind | Auto Reclose on station breaker, 3 phase inline recloser RX2060 tripped Janet King JKGF4, ID # 13303 | None | None | 18 | 98 | 29 | West | JKGF4
133039 | 2015-12-29 | Adverse Weather | Extreme Wind | Auto Reclose on station breaker, 3 phase inline recloser RX2060 tripped Janet King JKGF4, ID # 13303 | None | None | 183 | 14 | 43 | West | JKGF4
133039 | 2015-12-29 | Adverse Weather | Extreme Wind | Auto Reclose on station breaker, 3 phase inline recloser RX2060 tripped Janet King JKGF4, ID # 13303 | None | None | 200 | 16 | 53 | West | JKGF4
133040 | 2015-12-29 | Adverse Weather | Extreme Wind | Phases contacted each other on trunk at Flewelyn and Munster caused auto Reclose on station breaker, 3 phase inline recloser RX2060 tripped, Janet King JKGF4, ID # 133040 | None | None | 200 | 21 | 70 | West | JKGF4
133041 | 2015-12-29 | Scheduled Outage | Maintenance | to allow Hydro Ottawa crews to repair aburnt off transformer lead | None | None | 2 | 38 | 1 | West | 43F3
133042 | 2015-12-29 | Defective Equipment | Mechanical Failure | Damaged customer secondary equipment casued a fuse in the switch gear to blow | Customer Owned | Customer-Owned | 1 | 24842 | 414 | Central | 5201
133043 | 2015-12-29 | Tree Contacts | Broken Branch | New S12316 install at 1319 Southwood to allow removal of large tree limb resting on 3 phase at 2422 Thorson. | None | None | 60 | 84 | 84 | Central | UV03
133044 | 2015-12-30 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X33991 TO REPLACE CONNECTIONS ON SECONDARY SERVICE | None | None | 6 | 30 | 3 | Central | UV05
133046 | 2015-12-30 | Defective Equipment | Mechanical Failure | To allow Hydro Ottawa crews to investigate, make repairs and re-fuse a live front transformer after the internal fuse tripped. | U/G Cable Attachement | Unknown \ Other | 1 | 34 | 1 | South | 47F6
133048 | 2015-12-31 | Scheduled Outage | Construction | Transformer 38 at 260 Hearst Way was isolated to allow the crew to replace the elbows and inserts | None | None | 1 | 92 | 2 | West | MWDF2
133049 | 2016-01-03 | Foreign Interference | Wildlife (Bird/Animal) | Crews found S24241 and OH transformer cutout blown due to animal contact. Hinchey (TH01) ID #133049 | O/H Switchgear | Inline Switch | 28 | 89 | 42 | Central | TH01
133051 | 2016-01-03 | Scheduled Outage | Forced Switching | Defective transformer X20263 | None | O/H Transformer (1ph) | 12 | 87 | 17 | East | 249F2
133052 | 2016-01-04 | Scheduled Outage | Construction | CONNECT NEW SERVICE | None | None | 16 | 54 | 14 | Central | SB05
133054 | 2016-01-05 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X36420 TO REPLACE SWITCH AND ARRESTER. | None | None | 4 | 28 | 2 | West | BECKF2
133055 | 2016-01-05 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X17710 TO REPLACE SWITCH AND ARRESTER | None | None | 5 | 60 | 5 | West | BECKF2
133056 | 2016-01-05 | Scheduled Outage | Construction | Trx X17708 opened to replace switch and arrestor. | None | None | 7 | 60 | 7 | West | BECKF2
133057 | 2016-01-05 | Tree Contacts | Broken Branch | Tree branch contacted O/H line & caused S17705 to open. Munster 43F3. ID#133057. | None | None | 2 | 98 | 3 | West | 43F3
133058 | 2016-01-05 | Defective Equipment | Mechanical Failure | defective transformer switch | O/H Transformer | Fused Cutout | 12 | 247 | 49 | East | AQ07
133059 | 2016-01-06 | Scheduled Outage | Maintenance | To allow Hydro Ottawa U/G crews to replace a damaged transformer TE2824 with new TP11236. Uplands 4801 F8. ID#133059. | None | Padmount (1ph) | 16 | 166 | 44 | East | 4801F7
133060 | 2016-01-06 | Scheduled Outage | Construction | A section of Beck F2 between S15910 & S16095 was isolated to install new pole & transfer plant. Beckwith F2. ID#133060. | None | None | 2 | 260 | 9 | West | BECKF2
133061 | 2016-01-06 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at X32648 caused fuse to open as well as S27708 B to open. Lincoln TD12. ID#133061. | O/H Switchgear | Fused Cutout | 20 | 116 | 39 | Central | TD12
133064 | 2016-01-06 | Defective Equipment | Defective Equipment/ Material | Transformer KT53 primary fuse insulator was tracking. Caused fuse to open. Affecting 15 customers. Russell 5310. | U/G Cable Attachement | Termination \ Stress Cone | 15 | 89 | 22 | East | 5310
133067 | 2016-01-06 | Defective Equipment | Electrical Failure | BCHF1 white phase cable fault between TP4259 and TE374. | U/G Cable | XLPE | 8 | 60 | 8 | East | BCHF1
133067 | 2016-01-06 | Defective Equipment | Electrical Failure | BCHF1 white phase cable fault between TP4259 and TE374. | U/G Cable | XLPE | 10 | 10 | 2 | East | BCHF1
133067 | 2016-01-06 | Defective Equipment | Electrical Failure | BCHF1 white phase cable fault between TP4259 and TE374. | U/G Cable | XLPE | 12 | 15 | 3 | East | BCHF1
133067 | 2016-01-06 | Defective Equipment | Electrical Failure | BCHF1 white phase cable fault between TP4259 and TE374. | U/G Cable | XLPE | 14 | 145 | 34 | East | BCHF1
133068 | 2016-01-07 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to replace a pole and transfer O/H conductor to new poles | None | None | 2 | 266 | 9 | West | BECKF2
133069 | 2016-01-07 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change a switch and install a pole | None | None | 14 | 252 | 59 | West | BECKF2
133070 | 2016-01-07 | Scheduled Outage | Maintenance | To allow a contractor to replace customer secondary risers | None | None | 14 | 313 | 73 | South | 200F2
133071 | 2016-01-07 | Tree Contacts | Tree Growth/ Untrimmed Tree | REPLACED BLOWN FUSE AT THE ROAD FEEDING CUSTOMER OWNED OVERHEAD LINE TO TRANSFORMER X24101 (TREE CONTACT) | O/H Switchgear | Fused Cutout | 1 | 84 | 1 | East | LMBF5
133072 | 2016-01-07 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X26015 TO REPLACE SECONDARY SERVICE | None | None | 7 | 25 | 3 | Central | AH13
133073 | 2016-01-07 | Defective Equipment | Electrical Failure | REPLACED DEFECTIVE TRANSFORMER X2614 | O/H Transformer | O/H Transformer (1ph) | 1 | 256 | 4 | South | 200F1
133074 | 2016-01-07 | Defective Equipment | Mechanical Failure | REPLACED BLOWN FUSE FEEDING TRANSFORMER X29452 (SECONDARY CONDUCTOR SHORTED OUT) | O/H Transformer | O/H Transformer (1ph) | 9 | 111 | 17 | East | SO12
133076 | 2016-01-07 | Defective Equipment | Electrical Failure | Cable fault between KT101 and KT103 caused ELW07 CB to auto reclose and B phase fuse at S21789 to open. Ellwood (ELW07) ID#133076 | U/G Cable | Unknown \ Other | 46 | 17 | 13 | East | ELW07
133076 | 2016-01-07 | Defective Equipment | Electrical Failure | Cable fault between KT101 and KT103 caused ELW07 CB to auto reclose and B phase fuse at S21789 to open. Ellwood (ELW07) ID#133076 | U/G Cable | Unknown \ Other | 59 | 37 | 36 | East | ELW07
133076 | 2016-01-07 | Defective Equipment | Electrical Failure | Cable fault between KT101 and KT103 caused ELW07 CB to auto reclose and B phase fuse at S21789 to open. Ellwood (ELW07) ID#133076 | U/G Cable | Unknown \ Other | 115 | 86 | 165 | East | ELW07
133077 | 2016-01-07 | Unknown/Other | Unknown | TE374 found defective, ONCALL crews replaced transformer and energized under new nomenclature TP11241 | Unknown \ Other | Unknown \ Other | 8 | 408 | 54 | East | BCHF8
133077 | 2016-01-07 | Unknown/Other | Unknown | TE374 found defective, ONCALL crews replaced transformer and energized under new nomenclature TP11241 | Unknown \ Other | Unknown \ Other | 88 | 122 | 179 | East | BCHF8
133079 | 2016-01-07 | Defective Equipment | Electrical Failure | Overhead transformer X35990 found defective. OH isolated from S173 to EOL to replace transformer. | O/H Transformer | O/H Transformer (1ph) | 8 | 250 | 33 | South | EPWF2
133079 | 2016-01-08 | Defective Equipment | Electrical Failure | Overhead transformer X35990 found defective. OH isolated from S173 to EOL to replace transformer. | O/H Transformer | O/H Transformer (1ph) | 18 | 135 | 40 | South | EPWF2
133080 | 2016-01-08 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X17706 TO REPLACE SWITCH AND ARRESTER | None | None | 7 | 40 | 5 | West | BECKF2
133081 | 2016-01-08 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X07176 TO FAULT FIND ON A SECONDARY UNDERGROUND SERVICE | None | None | 3 | 25 | 1 | West | 624F6
133082 | 2016-01-08 | Defective Equipment | Mechanical Failure | Defective porcelain cut-out replaced at X23744. | O/H Switchgear | Fused Cutout | 1 | 90 | 2 | East | AA03
133084 | 2016-01-09 | Scheduled Outage | Maintenance | crews replaced and tightened connections at the transformer. | None | None | 2 | 55 | 2 | Central | SB11
133085 | 2016-01-09 | Scheduled Outage | Construction | Transformer #X27074 isolated by crew to replace triplex | None | None | 9 | 45 | 7 | East | TB06
133086 | 2016-01-09 | Scheduled Outage | Construction | isolation for contractor to connect new secondary cables. | None | None | 1 | 88 | 1 | West | RHNF1
133088 | 2016-01-10 | Foreign Interference | Customer Equipment | At 00:48am SCADA indicated the TL20 breaker open. Crews found the CB1 and CB15 at VT644 were also open due to a problem on the customer side. Customer isolated the fault and the line was re-energized. Lisgar (TL20) | Customer Owned | Customer-Owned | 47 | 138 | 108 | Central | 5211
133089 | 2016-01-10 | Tree Contacts | Broken Branch | Tree fell into overhead wire. | O/H Conductor | O/H Conductor | 4736 | 67 | 5289 | East | CYRF3
133090 | 2016-01-10 | Loss Of Supply | Transmission Inadvertent | At 20:30 SCADA indicates Casselman MS lost the 62M2 supply from Hydro One. | None | None | 312 | 390 | 2028 | East | V11F1
133090 | 2016-01-10 | Loss Of Supply | Transmission Inadvertent | At 20:30 SCADA indicates Casselman MS lost the 62M2 supply from Hydro One. | None | None | 399 | 390 | 2594 | East | V11F3
133090 | 2016-01-10 | Loss Of Supply | Transmission Inadvertent | At 20:30 SCADA indicates Casselman MS lost the 62M2 supply from Hydro One. | None | None | 989 | 390 | 6428 | East | V11F2
133091 | 2016-01-10 | Tree Contacts | Falling Tree | Tree in overhead circuit at this location. Primary line pulled down. On call crew required to make repairs. LMBF5 CB would not close, LMBf5F6 CB would not close, RTU at Limebank failed. LMBF5 restored from 7F4 via CS29260. | O/H Conductor | O/H Conductor | 814 | 211 | 2863 | East | LMBF5
133091 | 2016-01-10 | Tree Contacts | Falling Tree | Tree in overhead circuit at this location. Primary line pulled down. On call crew required to make repairs. LMBF5 CB would not close, LMBf5F6 CB would not close, RTU at Limebank failed. LMBF5 restored from 7F4 via CS29260. | O/H Conductor | O/H Conductor | 1400 | 180 | 4200 | East | LMBF5
133092 | 2016-01-10 | Adverse Weather | Extreme Wind | At 21:09 SCADA indicates the BRDF2 breaker is opened at the station. Ottawa Fire reported sparks at Colonnade and Prince of Wales. Crews check line and found no issues. System Office closed the breaker from SCADA to restore customers. Borden Farms (BRDF2) | None | None | 272 | 21 | 95 | West | BRDF2
133093 | 2016-01-10 | Tree Contacts | Falling Tree | At 23:14 SCADA indicates the 47F3 breaker auto-reclosed then tripped. 353 customers affected. | O/H Conductor | O/H Conductor | 27 | 527 | 237 | South | 47F3
133093 | 2016-01-10 | Tree Contacts | Falling Tree | At 23:14 SCADA indicates the 47F3 breaker auto-reclosed then tripped. 353 customers affected. | O/H Conductor | O/H Conductor | 353 | 170 | 1000 | South | 47F3
133094 | 2016-01-10 | Adverse Weather | Extreme Wind | R phase stirrup & hot line clamp burned off at pole X06121 | O/H Conductor | Stirrup | 4 | 170 | 11 | South | 180F4
133094 | 2016-01-10 | Adverse Weather | Extreme Wind | R phase stirrup & hot line clamp burned off at pole X06121 | O/H Conductor | Stirrup | 39 | 169 | 110 | South | 180F4
133095 | 2016-01-10 | Adverse Weather | Extreme Wind | Crew found G649 R open during heavy winds. Line patrolled, no issue found, G649R closed. | None | None | 1 | 466 | 8 | South | 145F3
133097 | 2016-01-11 | Scheduled Outage | Vegetation Management | Tree limb on triplex. Transformer opened to remove limb. | None | None | 7 | 63 | 7 | East | UZ12
133099 | 2016-01-11 | Scheduled Outage | Maintenance | renew connections on customer seconday service. | None | O/H Service | 17 | 96 | 27 | East | TB06
133100 | 2016-01-11 | Defective Equipment | Mechanical Failure | Repair defective switches. | O/H Switchgear | Fused Cutout | 1 | 60 | 1 | East | LMBF5
133101 | 2016-01-11 | Scheduled Outage | Construction | transformer X25567 was isolated to install new pole. | None | None | 1 | 59 | 1 | South | FAL03
133102 | 2016-01-12 | Tree Contacts | Tree Growth/ Untrimmed Tree | 24/7 to open transformer X27407. Turning off 7 customers. Dropped secondary service to 136 Kamloops. To remove tree limb from the area of secondary O/H conductor in the rear of 136 Kamloops. | None | None | 7 | 93 | 11 | East | UZ12
133104 | 2016-01-12 | Foreign Interference | Customer Equipment | TL19 breaker opened due to defective CB1 at VT166, 341 McLaren | Customer Owned | Customer-Owned | 10 | 523 | 87 | Central | TL7TS
133104 | 2016-01-12 | Foreign Interference | Customer Equipment | TL19 breaker opened due to defective CB1 at VT166, 341 McLaren | Customer Owned | Customer-Owned | 132 | 13 | 29 | Central | TL7TS
133104 | 2016-01-12 | Foreign Interference | Customer Equipment | TL19 breaker opened due to defective CB1 at VT166, 341 McLaren | Customer Owned | Customer-Owned | 153 | 29 | 74 | Central | TL7TS
133104 | 2016-01-12 | Foreign Interference | Customer Equipment | TL19 breaker opened due to defective CB1 at VT166, 341 McLaren | Customer Owned | Customer-Owned | 718 | 47 | 562 | Central | TL7TS
133105 | 2016-01-13 | Scheduled Outage | Construction | Switch S18757 to EOL at 395 Parkdale was isoalted to allow crew to replace porcelain switch. Hinchey (TH06) | None | None | 91 | 82 | 124 | Central | TH06
133106 | 2016-01-13 | Defective Equipment | Defective Equipment/ Material | The crew had to make repairs to switch S22249 that feeds TP6843 | O/H Conductor | Sleeve | 3 | 41 | 2 | East | AF03
133107 | 2016-01-14 | Scheduled Outage | Construction | To allow Ottawa Hydro crews to change hydro pole. | None | Pole | 1 | 114 | 2 | South | FAL01
133108 | 2016-01-14 | Unknown/Other | Unknown | G901R was found blown, line patrolled & no cause found. Leitrim 249F2. ID#133108. | Unknown \ Other | Unknown \ Other | 173 | 110 | 317 | East | 249F2
133109 | 2016-01-15 | Scheduled Outage | Construction | planned outage to allow contractor to pull in new secondary cables | None | None | 4 | 151 | 10 | East | TB14
133110 | 2016-01-15 | Scheduled Outage | Maintenance | To repair O/H conductor between S423, S461, S416 & S861 damaged by previous tree contacts. Bells Corners 47F3. | None | O/H Conductor | 27 | 307 | 138 | South | 47F3
133111 | 2016-01-15 | Scheduled Outage | Maintenance | VT90 @ 360 Laurier was isolated to allow the metering dept to make some repairs. | None | Unknown \ Other | 1 | 30 | 0 | Central | TL2TS
133112 | 2016-01-16 | Foreign Interference | Foreign Objects | A motor vehicle accident caused a guy wire to get tangled up into a Hydro One owned conductor that runs parallel to Hydro Ottawa owned conductor. The fault caused G180W to open. | Pole Attachement | Unknown \ Other | 9 | 128 | 19 | East | 249F2
133113 | 2016-01-16 | Scheduled Outage | Maintenance | VT184 at 2480 Walkley rd was isolated to allow the contractor to replace the vault buss duct replacement to new switchgear | None | Switch | 1 | 1043 | 17 | East | 5309
133114 | 2016-01-16 | Foreign Interference | Customer Equipment | Transformer X29518 opened due to ballons making contact with transformer. Church AA05 | O/H Transformer | O/H Transformer (1ph) | 4 | 846 | 56 | East | AA05
133116 | 2016-01-18 | Scheduled Outage | Construction | SR04 circuit from S25065 to EOL isolated to transfer plant to new poles. 117 customers affected. Riverdale (SR03) | None | O/H Conductor | 117 | 98 | 191 | Central | SR03
133117 | 2016-01-18 | Scheduled Outage | Forced Switching | To repair a neutral wire that burned down due to Asplundh trimming trees and dropping a branch on a triplex. | None | O/H Conductor | 6 | 242 | 24 | Central | TD01
133119 | 2016-01-18 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMERS X31106 AND X31104 TO REPLACE THE POLES | None | None | 6 | 240 | 24 | Central | AB04
133120 | 2016-01-18 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30582 TO REPLACE THE POLE | None | None | 5 | 130 | 11 | Central | UJ07
133121 | 2016-01-19 | Defective Equipment | Defective Equipment/ Material | Transformer #X27054 opened up due to lead in top of cut out needed to be re-installed | O/H Switchgear | Fused Cutout | 6 | 117 | 12 | East | TB06
133123 | 2016-01-19 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27106 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 12 | 37 | 7 | East | TB15
133124 | 2016-01-19 | Scheduled Outage | Construction | Transformer #X30719 isolated by crew for a transformer relocation | None | None | 8 | 110 | 15 | Central | UN10
133125 | 2016-01-19 | Scheduled Outage | Maintenance | Crews opened the cut out switch at the transformer at X31232, to replace the O/H secondary triplex to 146 Goulburn per electricians request. 21 customers were without power. Chris Trafford and Jack Morrice were the responders. | None | None | 21 | 62 | 22 | Central | UN11
133126 | 2016-01-21 | Scheduled Outage | Construction | Transformer TP9114 was isolated to allow contractor to install secondary cables | None | None | 13 | 124 | 27 | South | FAL01
133127 | 2016-01-21 | Scheduled Outage | Maintenance | Disconnect for secondary service repairs | None | None | 15 | 25 | 6 | Central | AD06
133128 | 2016-01-21 | Scheduled Outage | Construction | REPLACE SECONDARY SERVICE | None | None | 12 | 110 | 22 | Central | AD07
133129 | 2016-01-21 | Scheduled Outage | Maintenance | REPAIR SEC BUSS | None | None | 12 | 15 | 3 | Central | AB07
133130 | 2016-01-21 | Defective Equipment | Electrical Failure | B phase fuse at S20249 at 1015 Frances opened due to broken transformer cutout at the rear of 575 Wolfdale. 87 customers affected. Overbrook (SO02) | O/H Switchgear | Fused Cutout | 87 | 97 | 141 | East | SO02
133131 | 2016-01-22 | Scheduled Outage | Construction | P208 isolated to change riser switches and arrestors | None | Fused Cutout | 7 | 144 | 17 | East | AQ04
133133 | 2016-01-25 | Scheduled Outage | Maintenance | KT80 isolated to allow crews to replace termination on primary cables. | None | Termination \ Stress Cone | 14 | 145 | 34 | East | TB14
133134 | 2016-01-25 | Scheduled Outage | Maintenance | To replace TE621 after it was damaged by a snowplow. | None | None | 18 | 125 | 38 | East | 8F3
133135 | 2016-01-25 | Scheduled Outage | Construction | Primary cable reconfiguration from TP10353 to EOL | None | None | 64 | 348 | 371 | West | TFXF1
133136 | 2016-01-25 | Defective Equipment | Mechanical Failure | Switch & bracket failed at X36216, 117 James Cummings which also caused 200F1 to A/R. | O/H Switchgear | Fused Cutout | 3 | 103 | 5 | South | 200F1
133138 | 2016-01-25 | Scheduled Outage | Maintenance | K-line opened transformer number X30578 to transfer plant per Dan Crough. This outage affected 12 customers. | None | None | 12 | 120 | 24 | Central | AB05
133139 | 2016-01-25 | Defective Equipment | Mechanical Failure | Defective 44KV switch # CS23326 failed to operate correctly. | O/H Switchgear | Load Break Gang | 1 | 10 | 0 | South | 22M27
133140 | 2016-01-26 | Scheduled Outage | Vegetation Management | Transformer #X32738 isolated by crew for City of Ottawa tree removal | None | None | 6 | 74 | 7 | Central | TD05
133142 | 2016-01-26 | Scheduled Outage | Construction | Transformer #X23669 isolated by crew for switch maintenance | None | None | 5 | 24 | 2 | East | UB07
133143 | 2016-01-26 | Scheduled Outage | Construction | Transformer #X11099 isolated by crew to replace switch, bracket and arrestor | None | None | 3 | 45 | 2 | West | BECKF2
133144 | 2016-01-26 | Scheduled Outage | Construction | 2 transformers, #X31104 and X31106 isolated by crew to transfer hydro plant to new poles | None | None | 25 | 315 | 131 | Central | AB04
133145 | 2016-01-26 | Scheduled Outage | Maintenance | SERVICE UPGRADE | None | None | 6 | 55 | 6 | Central | TD05
133146 | 2016-01-27 | Scheduled Outage | Construction | isolated to re-arrange cables | None | None | 54 | 250 | 225 | West | TFXF1
133147 | 2016-01-27 | Scheduled Outage | Construction | Install new poles and reconfigure overhead conductors. | None | None | 9 | 250 | 38 | East | AA03
133148 | 2016-01-27 | Scheduled Outage | Construction | planned outage for Hydro One to string new conductor. | None | None | 2 | 229 | 8 | West | BECKF2
133149 | 2016-01-27 | Scheduled Outage | Construction | Pole and switch replacement. | None | None | 26 | 253 | 110 | Central | AB05
133150 | 2016-01-27 | Unknown/Other | Unknown | Replaced blown fuse feeding transformer X23502 cause unknown | O/H Transformer | O/H Transformer (1ph) | 112 | 60 | 112 | East | SO02
133151 | 2016-01-27 | Scheduled Outage | Construction | Transformer #X29796 isolated by crew to transfer plant | None | None | 13 | 60 | 13 | Central | SR03
133152 | 2016-01-28 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X21685 opened up due to squirrel contact | O/H Switchgear | Inline Switch | 7 | 49 | 6 | East | TB14
133153 | 2016-01-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X30466 opened up due to defective switch | O/H Switchgear | Fused Cutout | 28 | 78 | 36 | Central | SB02
133154 | 2016-01-28 | Scheduled Outage | Maintenance | Geoff Ryan and crew to open transformer number X11092 to replace the cutout switch and arrestors. Only 1 customer affected by this. | None | None | 1 | 37 | 1 | West | BECKF2
133156 | 2016-01-28 | Scheduled Outage | Construction | Brent Duncan and crew had X31408 openned to reconfigure and reinstall secondary. Installed 9 new secondary services. | None | None | 15 | 241 | 60 | Central | UJ06
133157 | 2016-01-28 | Scheduled Outage | Maintenance | Transformer X08603 openned to replace cut out switch and arrestor. This affected 1 customer. | None | None | 1 | 29 | 0 | West | BECKF2
133158 | 2016-01-31 | Defective Equipment | Defective Equipment/ Material | Animal contact. | O/H Switchgear | Fused Cutout | 7 | 42 | 5 | Central | TD07
133160 | 2016-02-01 | Foreign Interference | Foreign Objects | The BCHF5 circuit triped open due to ballon in the Overahead on Sheffield Rd North of the sation. | Station Equipment | Relay | 1255 | 50 | 1046 | East | BCHF5
133161 | 2016-02-01 | Scheduled Outage | Construction | INSTALL 2 NEW SERVICES | None | None | 9 | 42 | 6 | Central | TH01
133162 | 2016-02-01 | Scheduled Outage | Construction | REPLACE DEFECTIVE TRANS LEAD | None | None | 12 | 8 | 2 | Central | AB03
133163 | 2016-02-01 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32925 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 7 | 62 | 7 | Central | TD07
133164 | 2016-02-01 | Scheduled Outage | Maintenance | REPLACE INSULATOR AND ARRESTOR | None | None | 1 | 80 | 1 | West | BECKF2
133165 | 2016-02-02 | Scheduled Outage | Maintenance | At 9:27am K783 was isolated to allow crew to replace primary insulators and primary cable termination. 16 customers affected. McCarthy (AQ07) | None | None | 16 | 79 | 21 | East | AQ07
133166 | 2016-02-02 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X23893 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 12 | 109 | 22 | Central | TH06
133167 | 2016-02-04 | Scheduled Outage | Maintenance | Transformer TP2969 was isoalted to allow crew to repalce switch and cable. Epworth (58F4) | None | None | 1 | 1498 | 25 | South | EPWF4
133168 | 2016-02-04 | Unknown/Other | Unknown | REPLACED BLOWN FUSE FEEDING TRANSFORMER X47536 (CAUSE UNKNOWN) | O/H Transformer | O/H Transformer (1ph) | 17 | 35 | 10 | Central | TW18
133169 | 2016-02-04 | Defective Equipment | Mechanical Failure | Clyde T2 tripped on gas alarm | Station Equipment | Relay | 53 | 24 | 21 | Central | UC07
133169 | 2016-02-04 | Defective Equipment | Mechanical Failure | Clyde T2 tripped on gas alarm | Station Equipment | Relay | 139 | 24 | 56 | Central | UC06
133169 | 2016-02-04 | Defective Equipment | Mechanical Failure | Clyde T2 tripped on gas alarm | Station Equipment | Relay | 389 | 24 | 156 | Central | UC05
133170 | 2016-02-05 | Scheduled Outage | Construction | To replace terminations and insulators. | None | None | 17 | 128 | 36 | East | AQ08
133173 | 2016-02-08 | Scheduled Outage | Maintenance | 18 customers fed from KT652 affected to make meter base repairs at 3007 Dumaurier on the Lincoln Heights TD05 | None | None | 18 | 80 | 24 | Central | TD05
133174 | 2016-02-08 | Scheduled Outage | Maintenance | Burnt secondary connections on transformer X36575. Crew replaced secondary connections at the transformer. | None | None | 6 | 47 | 5 | South | EPWF3
133175 | 2016-02-08 | Scheduled Outage | Construction | Don Kelly of Black and Macdonald opened 3 transformers. Customers services on transformers X31245, X31246, and X31248 were moved to X47243. Customers were notified. | None | None | 5 | 210 | 18 | Central | SR03
133175 | 2016-02-08 | Scheduled Outage | Construction | Don Kelly of Black and Macdonald opened 3 transformers. Customers services on transformers X31245, X31246, and X31248 were moved to X47243. Customers were notified. | None | None | 14 | 210 | 49 | Central | SR01
133176 | 2016-02-08 | Scheduled Outage | Construction | Transformer #X30090 isolated by crew to replace triplex and all connections | None | None | 4 | 82 | 5 | Central | SB11
133177 | 2016-02-08 | Scheduled Outage | Maintenance | Rudy Grissel had X24500 open to perform pole maintenance. Customers notified. | None | None | 5 | 51 | 4 | East | UB07
133178 | 2016-02-08 | Scheduled Outage | Construction | Jim Yeldon had transformer X5265 open to install a new service. Customers notified. | None | None | 10 | 25 | 4 | South | 180F3
133179 | 2016-02-08 | Scheduled Outage | Construction | 3 transformer isolated, X29782, X29797 and X29799, no longer feeding, now being fed by X47223 | None | None | 22 | 240 | 88 | Central | SR04
133180 | 2016-02-09 | Scheduled Outage | Maintenance | At 9:04am K834 was isolated to allow crew to replace primary insulators and terminations. 16 customers affect. McCarthy (AQ08). | None | Elbow \ Insert | 16 | 101 | 27 | East | AQ08
133181 | 2016-02-09 | Scheduled Outage | Maintenance | X24484 openned for crews to perform load balancing. Customers notified. | None | None | 6 | 53 | 5 | East | UB07
133182 | 2016-02-09 | Scheduled Outage | Maintenance | Crews performing work in the area had X30765, X30766, and X26038 open. Customers notified. | None | None | 37 | 115 | 71 | Central | AB06
133183 | 2016-02-09 | Scheduled Outage | Maintenance | Crews have X11028 open to replace the cut out switch and lightning arrestor. Customers have been notified. | None | None | 1 | 43 | 1 | West | BECKF2
133184 | 2016-02-09 | Scheduled Outage | Maintenance | X35692 open so crews can replace cut out switch and lightning arrestor. Customers notified. | None | None | 5 | 20 | 2 | Central | TD12
133186 | 2016-02-09 | Scheduled Outage | Maintenance | X11022 openned by crews to replace cutout switch and lightning arrestor. Customers notified. | None | None | 1 | 43 | 1 | West | BECKF2
133187 | 2016-02-09 | Scheduled Outage | Construction | REPLACE SWITCH AND ARRESTOR | None | None | 5 | 70 | 6 | Central | TD14
133188 | 2016-02-09 | Scheduled Outage | Construction | REPLACE TRANS SWITCH | None | None | 8 | 40 | 5 | Central | TD12
133189 | 2016-02-09 | Scheduled Outage | Construction | REPLACE TRANS SW AND ARRESTOR | None | None | 9 | 70 | 10 | Central | TD14
133191 | 2016-02-10 | Scheduled Outage | Construction | At 8:00am S25065 was opened to allow crews to transfer line to new pole. 117 customers affected. Riverdale (SR03) | None | None | 117 | 175 | 341 | Central | SR03
133192 | 2016-02-10 | Scheduled Outage | Construction | At 09:02 am crews isolated a section of the 43F3 to install new rabbits. 95 customers affected. Munster (43F3) | None | None | 95 | 208 | 329 | West | 43F3
133193 | 2016-02-10 | Scheduled Outage | Maintenance | Crews to replace primary cable terminations and insulators on K892 | None | Kiosk (1ph) | 8 | 97 | 13 | East | AQ08
133195 | 2016-02-10 | Scheduled Outage | Construction | At 12:30pm a section of SR03 at Herridge and Main was isolated to allow crew to transfer line to new pole. 222 customers affected. Riverdale (SR03) | None | O/H Conductor | 222 | 158 | 585 | Central | SR03
133197 | 2016-02-10 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X23876 TO REPLACE DEFECTIVE SWITCH | None | None | 12 | 30 | 6 | Central | TH06
133198 | 2016-02-11 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change porcelain insulators and primary cable terminations | None | Termination \ Stress Cone | 34 | 72 | 41 | East | AQ07
133199 | 2016-02-11 | Scheduled Outage | Maintenance | Rick Barnett and crew have transformer X30768 open to replace pole. Customers notified. | None | None | 13 | 234 | 51 | Central | AB03
133200 | 2016-02-11 | Scheduled Outage | Maintenance | Rick Barnett and crew to have X30767 open to replace pole. Customers notified. | None | None | 9 | 174 | 26 | Central | AB03
133201 | 2016-02-11 | Scheduled Outage | Maintenance | Police call for MVA. Pole broken and need replacement. | None | Pole | 2 | 619 | 21 | South | 145F3
133202 | 2016-02-12 | Unknown/Other | Unknown | SCADA reported that the AA05 tripped with a 60A spike on the blue phase. No apparent cause found | None | None | 412 | 11 | 76 | East | AA05
133203 | 2016-02-13 | Defective Equipment | Mechanical Failure | Crews found a broken blue phase cutout at swtich 908. In order to perform repair they had to open all 3 phases. 160 customers affected. Janet King (44F1) | O/H Switchgear | Fused Cutout | 60 | 133 | 133 | West | 44F1
133203 | 2016-02-13 | Defective Equipment | Mechanical Failure | Crews found a broken blue phase cutout at swtich 908. In order to perform repair they had to open all 3 phases. 160 customers affected. Janet King (44F1) | O/H Switchgear | Fused Cutout | 160 | 67 | 179 | West | 44F1
133204 | 2016-02-13 | Defective Equipment | Defective Equipment/ Material | Defective switch. | O/H Switchgear | Fused Cutout | 17 | 226 | 64 | East | AN06
133205 | 2016-02-13 | Loss Of Supply | Transmission Inadvertent | At 8:34pm a loss of supply from Hydro One cause 485 customers to lose power. System Office using SCADA swtiches transferred the load to a Hydro Ottawa supplied feeder. 2 customer were left stranded until Hydro One restores power to their feeder. Beckwith | None | None | 2 | 105 | 4 | West | BECKF2
133205 | 2016-02-13 | Loss Of Supply | Transmission Inadvertent | At 8:34pm a loss of supply from Hydro One cause 485 customers to lose power. System Office using SCADA swtiches transferred the load to a Hydro Ottawa supplied feeder. 2 customer were left stranded until Hydro One restores power to their feeder. Beckwith | None | None | 485 | 15 | 121 | West | BECKF2
133206 | 2016-02-15 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | PILC | 2673 | 56 | 2495 | East | TO1AA
133207 | 2016-02-16 | Scheduled Outage | Forced Switching | Outage to section on Beckwith F2 to stablize broken pole and remove car. | None | None | 15 | 71 | 18 | West | BECKF2
133209 | 2016-02-16 | Foreign Interference | Vehicle | Crews isolated the O/H at 8917 FRANKTOWN RD to repsir a broken pole caused by MVA | Pole | Pole | 11 | 151 | 28 | West | JKGF4
133210 | 2016-02-16 | Scheduled Outage | Forced Switching | Kiosk K323 was isolated due to broken water main at 40 Appleby PVT | None | None | 8 | 552 | 74 | Central | AK03
133211 | 2016-02-17 | Scheduled Outage | Vegetation Management | G461 to EOL opened for Tamarack tree trimming. | None | None | 45 | 87 | 65 | East | 56F1
133214 | 2016-02-17 | Scheduled Outage | Forced Switching | 43F3 O/H between TEMP67R and TEMP39 was open to allow crew to perform out of phase switching. Minster (44F3) | None | None | 1 | 1 | 0 | West | 44F3
133215 | 2016-02-17 | Scheduled Outage | Maintenance | transformer 123R at 14 Dorey was isolated by the crew to allow them to replace a leaking transformer | None | Kiosk (1ph) | 10 | 120 | 20 | West | BRDF4
133216 | 2016-02-17 | Adverse Weather | Ice/Icing | Transformer #X39290 opened up due to ice in wires | O/H Switchgear | Fused Cutout | 14 | 71 | 17 | East | SO03
133217 | 2016-02-17 | Scheduled Outage | Construction | K-line had transformer open for pole replacement. Customers notified. | None | None | 6 | 161 | 16 | Central | AB07
133218 | 2016-02-18 | Scheduled Outage | Maintenance | Transformer 4471 was isolated to replace leaking transformer. 7 customers affected. Bridlewood BRDF4. | None | Padmount (1ph) | 7 | 137 | 16 | West | BRDF4
133219 | 2016-02-18 | Foreign Interference | Vehicle | Transformer #X28130 opened up due to dump truck taking down secondary conductors. | Secondary \ Service | O/H Service | 9 | 83 | 12 | East | UZ04
133220 | 2016-02-18 | Foreign Interference | Foreign Objects | Wires down due to balloons | O/H Conductor | O/H Conductor | 402 | 153 | 1025 | East | UA05
133220 | 2016-02-18 | Foreign Interference | Foreign Objects | Wires down due to balloons | O/H Conductor | O/H Conductor | 746 | 119 | 1480 | East | UA05
133220 | 2016-02-19 | Foreign Interference | Foreign Objects | Wires down due to balloons | O/H Conductor | O/H Conductor | 746 | 57 | 709 | East | UA05
133221 | 2016-02-20 | Defective Equipment | Mechanical Failure | Customer call in reported power out. Crew found broken switch and repaired and closed. | O/H Switchgear | Fused Cutout | 103 | 82 | 141 | East | BLKF1
133222 | 2016-02-20 | Foreign Interference | Wildlife (Bird/Animal) | Transformer cut-out fuse blown open. Dead squirrel found on site. Assume animal interference. | O/H Transformer | O/H Transformer (1ph) | 18 | 39 | 12 | Central | TR09
133223 | 2016-02-20 | Foreign Interference | Vehicle | Transformer hit by snowplow and had to be replaced by on call crew | U/G Transformer | Padmount (1ph) | 16 | 97 | 26 | West | 624F3
133224 | 2016-02-20 | Tree Contacts | Falling Tree | Fire department reports tree on O/H and on fire at 6157 Russell Rd. Gr6 red closed, tree rmoved and G606R closed to restore all customers. | O/H Switchgear | Fused Cutout | 161 | 27 | 72 | East | 249F2
133224 | 2016-02-20 | Tree Contacts | Falling Tree | Fire department reports tree on O/H and on fire at 6157 Russell Rd. Gr6 red closed, tree rmoved and G606R closed to restore all customers. | O/H Switchgear | Fused Cutout | 415 | 138 | 954 | East | 249F2
133225 | 2016-02-20 | Defective Equipment | Mechanical Failure | OMS rolled up calls to G435R line patrolled by on-call nothing found and fuse replaced. Next day Feb21 insualtor at pole X14575 broke conductor down belived to original problem. | Pole Attachement | Insulator | 69 | 130 | 150 | East | 4801F8
133226 | 2016-02-20 | Scheduled Outage | Maintenance | V74 @ 30 Metcafle was isolated to allow the contractor to preform vault maintenance | Vault Equipment | Breaker \ Relay | 1 | 158 | 3 | Central | SA24
133228 | 2016-02-21 | Defective Equipment | Mechanical Failure | At pole X14575 broken insulator and primary conductor down. Repairs completed G435R closed | Pole Attachement | Insulator | 69 | 126 | 145 | East | 4801F8
133229 | 2016-02-21 | Scheduled Outage | Construction | K Line crews isolated the O/H at 333 NEPEAN ST to reconfigure a pole at the corner of Nepean and Lyon | None | Pole | 15 | 316 | 79 | Central | AB03
133230 | 2016-02-22 | Scheduled Outage | Construction | Dan Crough and crew from K-Line had transformer open to transfer services. Customers restored individually as services transferred. Customers notified. | None | None | 8 | 269 | 36 | Central | AB07
133231 | 2016-02-22 | Defective Equipment | Defective Equipment/ Material | Defective cable between K651 P/P/H switch and K651 transformer at 340 Stone Quarry Pvt | U/G Cable | Unknown \ Other | 48 | 250 | 200 | East | AP05
133233 | 2016-02-22 | Defective Equipment | Electrical Failure | At 8:18pm a cable fault on the BLKF4 caused an auto-reclose on the circuit and fuse G630 blue was blown. The outage was prolonged due to FCIs not working correctly. Crews performed troubleshooting and were able to identify the cause and restore power to c | U/G Cable | Unknown \ Other | 48 | 41 | 33 | East | BLKF4
133233 | 2016-02-22 | Defective Equipment | Electrical Failure | At 8:18pm a cable fault on the BLKF4 caused an auto-reclose on the circuit and fuse G630 blue was blown. The outage was prolonged due to FCIs not working correctly. Crews performed troubleshooting and were able to identify the cause and restore power to c | U/G Cable | Unknown \ Other | 84 | 24 | 34 | East | BLKF4
133233 | 2016-02-22 | Defective Equipment | Electrical Failure | At 8:18pm a cable fault on the BLKF4 caused an auto-reclose on the circuit and fuse G630 blue was blown. The outage was prolonged due to FCIs not working correctly. Crews performed troubleshooting and were able to identify the cause and restore power to c | U/G Cable | Unknown \ Other | 84 | 121 | 169 | East | BLKF4
133233 | 2016-02-22 | Defective Equipment | Electrical Failure | At 8:18pm a cable fault on the BLKF4 caused an auto-reclose on the circuit and fuse G630 blue was blown. The outage was prolonged due to FCIs not working correctly. Crews performed troubleshooting and were able to identify the cause and restore power to c | U/G Cable | Unknown \ Other | 84 | 218 | 305 | East | BLKF4
133233 | 2016-02-22 | Defective Equipment | Electrical Failure | At 8:18pm a cable fault on the BLKF4 caused an auto-reclose on the circuit and fuse G630 blue was blown. The outage was prolonged due to FCIs not working correctly. Crews performed troubleshooting and were able to identify the cause and restore power to c | U/G Cable | Unknown \ Other | 801 | 1 | 13 | East | BLKF4
133233 | 2016-02-22 | Defective Equipment | Electrical Failure | At 8:18pm a cable fault on the BLKF4 caused an auto-reclose on the circuit and fuse G630 blue was blown. The outage was prolonged due to FCIs not working correctly. Crews performed troubleshooting and were able to identify the cause and restore power to c | U/G Cable | Unknown \ Other | 801 | 3 | 40 | East | BLKF4
133234 | 2016-02-23 | Scheduled Outage | Construction | Overhead section isolated to allow for re-arrangment of primary, affecting 85 customers, Bayswater UJ07 | None | None | 85 | 139 | 197 | Central | UJ07
133235 | 2016-02-23 | Scheduled Outage | Maintenance | P129 isolated to change defective insulator and padmount | None | Kiosk (3ph) | 1 | 60 | 1 | East | SO05
133236 | 2016-02-23 | Scheduled Outage | Maintenance | ISOLATED SWITCH P129 FEEDING TRANSFORMER P0129 TO REPLACE CRACKED INSULATOR | None | None | 65 | 45 | 49 | East | SO05
133237 | 2016-02-23 | Scheduled Outage | Maintenance | To replace single white phase switch and make run off a true 3 phases. All 3 phase us to be connected through single white phase switch. New switch # 22964 | None | Unknown \ Other | 49 | 171 | 140 | Central | SB05
133239 | 2016-02-24 | Scheduled Outage | Maintenance | To allow customer to repair CB1 breaker in vault. | None | Breaker \ Relay | 1 | 17 | 0 | East | TO3UT
133240 | 2016-02-24 | Scheduled Outage | Construction | Overhead section isolated to replace insulators and upgrade plant affecting 4 customers, Terry Fox TFXF1 | None | None | 4 | 174 | 12 | West | TFXF1
133241 | 2016-02-24 | Defective Equipment | Mechanical Failure | S20249 blue phase inline fuse found defective and fuse open. 87 customers affected. Overbrook DS (SO02) | O/H Switchgear | Inline Switch | 87 | 175 | 254 | East | SO02
133242 | 2016-02-24 | Scheduled Outage | Maintenance | Transformer TE2287 at 36 Greynam was isolated to allow crew to replace swollen insert. Transformer change will be required at a later date. Merivale (72F1) | None | None | 17 | 70 | 20 | South | 72F1
133243 | 2016-02-24 | Scheduled Outage | Maintenance | Transformer was isolated to allow for clearance to fault find a secondary cable affecting 17 customers, Queensway Carleton 160F2 | None | U/G Service | 17 | 84 | 24 | South | 160F2
133244 | 2016-02-24 | Adverse Weather | Freezing Rain | NOT KNOWN | O/H Transformer | O/H Transformer (1ph) | 4 | 79 | 5 | Central | TD01
133246 | 2016-02-24 | Adverse Weather | Wind | S961 RB phases opened during adverse weather, no direct cause found. | Unknown \ Other | Unknown \ Other | 331 | 72 | 397 | South | 49F6
133247 | 2016-02-25 | Tree Contacts | Falling Tree | Tree on primary one phase down at Grenfell and Burnbank called in by fire department. S20599 opened for isolation. | O/H Conductor | O/H Conductor | 114 | 158 | 300 | South | 72F7
133248 | 2016-02-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact caused fuse at transformer X39609 to open. 1 customer affected. Fallowfield (FAL01) | O/H Transformer | O/H Transformer (1ph) | 1 | 69 | 1 | South | FAL01
133249 | 2016-02-25 | Tree Contacts | Falling Tree | RX2054 auto reclosed. G739 W opened. Crew patrolled circuit and found a tree on the line at X17762. S27210 opened, and G739W closed. Tree removed by forestry crew and power restored. | O/H Conductor | Unknown \ Other | 17 | 134 | 38 | East | 4801F8
133249 | 2016-02-25 | Tree Contacts | Falling Tree | RX2054 auto reclosed. G739 W opened. Crew patrolled circuit and found a tree on the line at X17762. S27210 opened, and G739W closed. Tree removed by forestry crew and power restored. | O/H Conductor | Unknown \ Other | 110 | 174 | 319 | East | 4801F8
133251 | 2016-02-25 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35382 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 5 | 37 | 3 | Central | TD12
133253 | 2016-02-25 | Scheduled Outage | Construction | Transformer #X31468 isolated by crew to replace service by the drop | None | None | 5 | 69 | 6 | Central | TH01
133255 | 2016-02-26 | Scheduled Outage | Construction | Transformer #KT0155 isolated by crew to repair secondary | None | None | 18 | 56 | 17 | East | ELW07
133256 | 2016-02-26 | Scheduled Outage | Construction | Transformer #X32099 isolated by crew to do disconnects around the drop | None | None | 10 | 255 | 42 | Central | AH04
133257 | 2016-02-27 | Unknown/Other | Unknown | Trip on UJK1Y1 breaker carrying caused UJT2-1 breaker to open as well. Manual reset required to allow operation of UJT2-1 breaker. Bayswater UJ05, UJ06 and UJ07 | None | None | 269 | 67 | 300 | Central | UJ05
133257 | 2016-02-27 | Unknown/Other | Unknown | Trip on UJK1Y1 breaker carrying caused UJT2-1 breaker to open as well. Manual reset required to allow operation of UJT2-1 breaker. Bayswater UJ05, UJ06 and UJ07 | None | None | 286 | 68 | 324 | Central | UJ06
133257 | 2016-02-27 | Unknown/Other | Unknown | Trip on UJK1Y1 breaker carrying caused UJT2-1 breaker to open as well. Manual reset required to allow operation of UJT2-1 breaker. Bayswater UJ05, UJ06 and UJ07 | None | None | 786 | 67 | 878 | Central | UJ07
133258 | 2016-02-27 | Scheduled Outage | Maintenance | To allow metering department to repair metering problem. | Customer Owned | Customer-Owned | 1 | 32 | 1 | East | 2204
133259 | 2016-02-27 | Adverse Weather | Extreme Wind | At 8:55am, 9:22am and 9:47am customers on the BeckF2 were momentarily interrupted due to wind gust causing the white and blue phases of the conductor to make contact. Beckwith (BeckF2) | None | None | 0 | 25 | 0 | West | BECKF2
133259 | 2016-02-27 | Adverse Weather | Extreme Wind | At 8:55am, 9:22am and 9:47am customers on the BeckF2 were momentarily interrupted due to wind gust causing the white and blue phases of the conductor to make contact. Beckwith (BeckF2) | None | None | 0 | 27 | 0 | West | BECKF2
133262 | 2016-02-28 | Scheduled Outage | Forced Switching | AF03, TA1UZ and TA3AF all dumped at the request of Ottawa Fire. Brookfield (AF03) / Albion (TA1UZ, TA3AF) | None | None | 240 | 93 | 372 | East | TA3AF
133262 | 2016-02-28 | Scheduled Outage | Forced Switching | AF03, TA1UZ and TA3AF all dumped at the request of Ottawa Fire. Brookfield (AF03) / Albion (TA1UZ, TA3AF) | None | None | 313 | 107 | 558 | East | AF03
133262 | 2016-02-28 | Scheduled Outage | Forced Switching | AF03, TA1UZ and TA3AF all dumped at the request of Ottawa Fire. Brookfield (AF03) / Albion (TA1UZ, TA3AF) | None | None | 418 | 40 | 279 | East | TA3AF
133262 | 2016-02-28 | Scheduled Outage | Forced Switching | AF03, TA1UZ and TA3AF all dumped at the request of Ottawa Fire. Brookfield (AF03) / Albion (TA1UZ, TA3AF) | None | None | 2140 | 45 | 1605 | East | TA1UZ
133263 | 2016-02-28 | Foreign Interference | Foreign Objects | At 11:20am System Office had to dump the AD07 circuit due to a down primary conductor caused by balloons. Shillington (AD07) | O/H Conductor | O/H Conductor | 660 | 277 | 3047 | Central | AD07
133264 | 2016-02-28 | Scheduled Outage | Forced Switching | At 12:35pm crews opened transformer X15228 to allow Ottawa Fire to put out fire at 4100 Leitrim. 7 customers affected. Leitrim (249F4) | None | None | 7 | 397 | 46 | East | LTM04
133266 | 2016-02-29 | Scheduled Outage | Vegetation Management | Transformer X5006 was isolated to permit tree trimming on customer line. 1 customer affected. Jockvale 145F3. | None | None | 1 | 42 | 1 | South | 145F3
133267 | 2016-02-29 | Unknown/Other | Unknown | REPLACED BLOWN FUSE IN PADMOUNT TRANSFORMER TP6067 (CAUSE UNKNOWN) | U/G Transformer | Padmount (1ph) | 12 | 59 | 12 | South | 145F1
133269 | 2016-02-29 | Adverse Weather | Extreme Wind | High Winds cause the AM04/ AM00 circuit to slap toghether. | O/H Conductor | O/H Conductor | 446 | 30 | 223 | Central | AM04
133270 | 2016-02-29 | Defective Equipment | Defective Equipment/ Material | Transformer #X36175 opened up due to broken transformer switch | O/H Switchgear | Fused Cutout | 7 | 71 | 8 | South | 170F1
133271 | 2016-02-29 | Adverse Weather | Extreme Wind | 22M24 circuit auto reclosed three serperate times during heavy wind gusts. Direct cause not found. | Unknown \ Other | Unknown \ Other | 0 | 1 | 0 | South | 22M24
133271 | 2016-02-29 | Adverse Weather | Extreme Wind | 22M24 circuit auto reclosed three serperate times during heavy wind gusts. Direct cause not found. | Unknown \ Other | Unknown \ Other | 0 | 5 | 0 | South | 22M24
133272 | 2016-02-29 | Defective Equipment | Defective Equipment/ Material | Transformer #X23722 opened up due to broken top lead | O/H Switchgear | Fused Cutout | 6 | 40 | 4 | East | SO02
133273 | 2016-02-29 | Scheduled Outage | Maintenance | Transformer #X29475 isolated by crew to kink the wires for more separation | None | None | 24 | 15 | 6 | East | UT02
133274 | 2016-03-01 | Scheduled Outage | Construction | Rick Barnett had transformer X30770 open for construction purposes. Customers notified. | None | None | 13 | 72 | 16 | Central | AB03
133275 | 2016-03-01 | Scheduled Outage | Construction | X29475 openned to replace defective services. Customers notified. | None | None | 24 | 101 | 40 | East | UT02
133276 | 2016-03-01 | Scheduled Outage | Construction | Transformer #P298 isolated by crew to reconnect 55 lebreton | None | None | 10 | 9 | 2 | Central | UJ06
133277 | 2016-03-01 | Scheduled Outage | Forced Switching | VT425 at 410 Laurier was de-energized to allow crew to perfrom off potential switching at VT325 due to manufacturer restriction. | None | None | 1 | 27 | 0 | Central | TL3TS
133279 | 2016-03-03 | Scheduled Outage | Maintenance | K1136 at 21 Forestlane was isolated to make repairs to defective transformer affecting 20 customers on the SO05 out of Overbrook Sub. | None | None | 20 | 49 | 16 | East | SO05
133280 | 2016-03-03 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER K1136 TO REPLACE DEFECTIVE PRIMARY ELBOW | None | Elbow \ Insert | 20 | 40 | 13 | East | SO05
133281 | 2016-03-03 | Scheduled Outage | Maintenance | ISOLATED AND REPLACED DEFECTIVE OVERHEAD TRANSFORMER X35653 | None | O/H Transformer (1ph) | 1 | 80 | 1 | Central | SM02
133283 | 2016-03-04 | Scheduled Outage | Maintenance | Remove Asbestos , and vault maintenance. | None | None | 1 | 244 | 4 | Central | 604
133284 | 2016-03-04 | Scheduled Outage | Maintenance | TE372 was isolated on the BCHF1 out of Beacon Hill MS to change broken insulators and to renew the primary connections affecting 12 customers | None | None | 12 | 128 | 26 | East | BCHF1
133285 | 2016-03-04 | Defective Equipment | Defective Equipment/ Material | Broken bushing on X24444. Temporary repairs were made until On-call arrived. On-Call replaced transformer X24444. | O/H Transformer | O/H Transformer (1ph) | 8 | 101 | 13 | East | LMBF5
133287 | 2016-03-06 | Scheduled Outage | Maintenance | repair oil leak on T2A transformer bank | None | Transformer | 2 | 140 | 5 | East | TB2JP
133288 | 2016-03-06 | Scheduled Outage | Maintenance | customer vault maintenance | None | None | 1 | 143 | 2 | Central | SB02
133289 | 2016-03-07 | Scheduled Outage | Construction | S13913 to EOL was isolated to allow crew to relocate SR03 O/H circuit. | None | None | 1 | 37 | 1 | Central | SR03
133290 | 2016-03-07 | Scheduled Outage | Construction | Rick Barnett and crew had transformer X30773 open in order to re-arrange primary. Customers notified. | None | None | 4 | 100 | 7 | Central | AB05
133291 | 2016-03-08 | Scheduled Outage | Maintenance | Overhead transformer was opened to change porceline transformer switch, affecting 20 customers. | None | None | 20 | 35 | 12 | Central | TH01
133292 | 2016-03-09 | Scheduled Outage | Vegetation Management | 56F1 from G318 to EOL isolated for tree trimming and to remove GR3 from service. 10 customers affected. South Gloucester (56F1) | None | O/H Conductor | 10 | 401 | 67 | East | 56F1
133293 | 2016-03-09 | Scheduled Outage | Construction | Shaun Evans of K-line and crew to replace leaning pole with transformer X31012 on it. | None | None | 27 | 142 | 64 | Central | AB07
133296 | 2016-03-09 | Scheduled Outage | Maintenance | Forced outge to straighen pole that was considered a hazard in parking lot. | None | Pole | 27 | 98 | 44 | Central | AB07
133297 | 2016-03-09 | Scheduled Outage | Construction | Scott Barkley to have X29908 open to run new secondary service. Customers notified. | None | None | 12 | 108 | 22 | Central | SB12
133298 | 2016-03-09 | Defective Equipment | Mechanical Failure | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X34840 | O/H Transformer | O/H Transformer (1ph) | 4 | 92 | 6 | Central | AK06
133299 | 2016-03-09 | Defective Equipment | Mechanical Failure | TK 20 breaker tripped (411/TK6TS breaker) due to suspected cable fault between on 411 between VT684 and TK, and TK6TS and VT84. | U/G Cable | PILC | 682 | 52 | 591 | Central | TK6TS
133300 | 2016-03-09 | Defective Equipment | Electrical Failure | Defective 3 phase transformer | Customer Owned | Customer-Owned | 1 | 11070 | 184 | East | 7F4
133301 | 2016-03-10 | Scheduled Outage | Maintenance | 336 and 319 Rideau was isolated from VT852-161 to allow the contractor to install a fire pump at 319 Rideau | None | Unknown \ Other | 2 | 329 | 11 | Central | 413
133302 | 2016-03-10 | Scheduled Outage | Construction | Rearrange overhead for future work | None | None | 2 | 221 | 7 | South | FAL03
133303 | 2016-03-10 | Scheduled Outage | Construction | Scott Barkley and crew to have X34246 open to install new U/G service. Customers notified. | None | None | 7 | 67 | 8 | Central | SM03
133304 | 2016-03-10 | Defective Equipment | Mechanical Failure | 4 KV vaults V731, V732 and V732 were isolated to allow crew to fault find cable fault between V732 and S16452. | U/G Cable | PILC | 343 | 132 | 755 | East | UZ06
133305 | 2016-03-10 | Scheduled Outage | Construction | Rick Barnett to have transformer X30771 open for pole replacement. Customers notified. | None | None | 19 | 251 | 79 | Central | AB05
133306 | 2016-03-10 | Scheduled Outage | Construction | Rick Barnett to have transformer X30770 open for pole replacement. Customers notified. | None | None | 13 | 251 | 54 | Central | AB03
133307 | 2016-03-11 | Scheduled Outage | Construction | Jeff Magee to have transformer X30572 to re-arrange secondaries. Customers notified. | None | None | 14 | 35 | 8 | Central | SA23
133308 | 2016-03-11 | Scheduled Outage | Construction | Jeff Magee to have transformer X30574 open to re-arrange secondaries. | None | None | 1 | 35 | 1 | Central | SA23
133309 | 2016-03-11 | Scheduled Outage | Construction | Jeff Magee to have transformer X30575 open to re-arrange secondaries. Customers notified. | None | None | 17 | 12 | 3 | Central | SA23
133310 | 2016-03-11 | Scheduled Outage | Construction | Planned outage to switch between out of phase systems. | None | None | 5 | 66 | 6 | South | FAL03
133311 | 2016-03-11 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X39190 open to upgrade a secondary service. Customers have been notified. | None | None | 7 | 127 | 15 | Central | SM02
133312 | 2016-03-11 | Scheduled Outage | Construction | Brent Duncan and crew to have transformer X31016 open to reposition transformer. Customers notified. | None | None | 15 | 161 | 40 | Central | AB06
133313 | 2016-03-11 | Scheduled Outage | Vegetation Management | Mike Anderson to have transformer X35189 open for tree trimming. Customers notified. | None | None | 7 | 206 | 24 | Central | TW22
133314 | 2016-03-11 | Scheduled Outage | Vegetation Management | Mike Anderson to have transformer X35199 open for tree trimming. Customers notified. | None | None | 8 | 206 | 27 | Central | TW22
133315 | 2016-03-11 | Scheduled Outage | Vegetation Management | Mike Anderson to have transformer X35188 open for tree trimming. Customers notified. Issue occurred with open bus secondary. 24/7 called to make repairs. | None | None | 10 | 271 | 45 | Central | TW22
133316 | 2016-03-11 | Foreign Interference | Vehicle | 190F2 overhead between S633, S28980 and S1498 isolated to repair broken pole caused by MVA. AK03 circuit also isolated during repairs for working clearance to remove cables to TE1891. 698 customers affected. Parkwood Hills (190F2) | Pole | Pole | 2 | 221 | 7 | South | 190F2
133316 | 2016-03-11 | Foreign Interference | Vehicle | 190F2 overhead between S633, S28980 and S1498 isolated to repair broken pole caused by MVA. AK03 circuit also isolated during repairs for working clearance to remove cables to TE1891. 698 customers affected. Parkwood Hills (190F2) | Pole | Pole | 75 | 241 | 301 | South | 190F2
133316 | 2016-03-11 | Foreign Interference | Vehicle | 190F2 overhead between S633, S28980 and S1498 isolated to repair broken pole caused by MVA. AK03 circuit also isolated during repairs for working clearance to remove cables to TE1891. 698 customers affected. Parkwood Hills (190F2) | Pole | Pole | 439 | 29 | 212 | South | 190F2
133316 | 2016-03-12 | Foreign Interference | Vehicle | 190F2 overhead between S633, S28980 and S1498 isolated to repair broken pole caused by MVA. AK03 circuit also isolated during repairs for working clearance to remove cables to TE1891. 698 customers affected. Parkwood Hills (190F2) | Pole | Pole | 1 | 595 | 10 | South | 190F2
133316 | 2016-03-12 | Foreign Interference | Vehicle | 190F2 overhead between S633, S28980 and S1498 isolated to repair broken pole caused by MVA. AK03 circuit also isolated during repairs for working clearance to remove cables to TE1891. 698 customers affected. Parkwood Hills (190F2) | Pole | Pole | 75 | 217 | 271 | South | 190F2
133316 | 2016-03-12 | Foreign Interference | Vehicle | 190F2 overhead between S633, S28980 and S1498 isolated to repair broken pole caused by MVA. AK03 circuit also isolated during repairs for working clearance to remove cables to TE1891. 698 customers affected. Parkwood Hills (190F2) | Pole | Pole | 260 | 34 | 147 | Central | AK03
133318 | 2016-03-13 | Scheduled Outage | Maintenance | TP3877 @ 1605 Orleans was isolated to allow the crew to replace a defective transformer | None | Kiosk (3ph) | 5 | 81 | 7 | East | 77M2
133319 | 2016-03-13 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X25689 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 15 | 36 | 9 | Central | TH11-NIU
133321 | 2016-03-14 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X34687 TO REPLACE SWITCH AND ARRESTER | None | None | 12 | 43 | 9 | Central | TH01
133324 | 2016-03-15 | Scheduled Outage | Construction | Isolation of TE2287 at 36 Greynam. To replace defective transformer # TE2287. | None | Padmount (1ph) | 17 | 58 | 16 | South | 72F1
133325 | 2016-03-15 | Scheduled Outage | Construction | 2 transformers, X29602 and X29603 isolated by crew for a pole change | None | None | 7 | 60 | 7 | East | SO10
133326 | 2016-03-15 | Scheduled Outage | Construction | 2 transformers, X31026 and X31025 isolated by crew to transfer plant | None | None | 10 | 10 | 2 | Central | UF10
133327 | 2016-03-15 | Scheduled Outage | Construction | At 13:00 crews isolated FAL03 from switch at X4497 affecting 1 customer to allow crew to rearrange overhead plant. Fallowfield (FAL03) | None | None | 1 | 40 | 1 | South | FAL03
133328 | 2016-03-15 | Scheduled Outage | Maintenance | Transformer needs to be relocated on base. | None | Padmount (3ph) | 1 | 94 | 2 | East | 8F1
133329 | 2016-03-16 | Scheduled Outage | Construction | To allow crews to string new circuit. | None | O/H Transformer (1ph) | 1 | 312 | 5 | South | FAL03
133331 | 2016-03-17 | Tree Contacts | Other Vegetation | An overhead transformer fused cutout opened when vines that had grown up the pole got into the secondaries affecting 25 customers. Lincoln TD14 | O/H Switchgear | Fused Cutout | 25 | 71 | 30 | Central | TD14
133332 | 2016-03-17 | Scheduled Outage | Construction | Transformer X4497 isolated to allow crew to string new primary conductor. 1 customer affected. Fallowfield (FAL03) | None | O/H Conductor | 1 | 330 | 6 | South | FAL03
133334 | 2016-03-17 | Lightning | Lightning | Lightning strike caused FAL01 circuit to auto reclose and FAL03 circuit to open under hold off protection. FAL03 restored remotely by system office. 8846 customers affected. Fallowfield (FAL01, FAL03) | O/H Conductor | O/H Conductor | 5872 | 6 | 587 | South | FAL03
133335 | 2016-03-17 | Scheduled Outage | Construction | INSTALL NEW SERVICE | None | None | 20 | 69 | 23 | Central | AH02
133336 | 2016-03-18 | Scheduled Outage | Construction | Transformer X30772 at 487 Cooper St. isolated to allow crew to connect new secondary bus. 7 cusomters affected. Nepean (AB05) | None | O/H Service | 7 | 162 | 19 | Central | AB05
133337 | 2016-03-18 | Scheduled Outage | Construction | Transformer TP11122 at Meadowlands Mall isolated to connect secondary services. 6 customers affected. Epworht (58F4) | None | Padmount (3ph) | 6 | 2716 | 272 | South | EPWF4
133338 | 2016-03-18 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to upgrade transformer TP2278 | None | None | 6 | 79 | 8 | West | MWDF3
133339 | 2016-03-18 | Scheduled Outage | Construction | REMOVE SERVICE FROM APT BUILDING FOR CONTRACTOR | None | None | 15 | 292 | 73 | Central | AB06
133340 | 2016-03-18 | Defective Equipment | Defective Equipment/ Material | Transformer #X32889 opened up due to broken transformer switch | O/H Switchgear | Fused Cutout | 2 | 95 | 3 | South | 145F2
133341 | 2016-03-19 | Defective Equipment | Defective Equipment/ Material | Suspected cable fault. | U/G Cable | XLPE | 217 | 86 | 311 | West | 24F5
133342 | 2016-03-20 | Scheduled Outage | Construction | To decommission TE2091 and transfer secondary service to new transformer TP11122. | None | Padmount (3ph) | 1 | 315 | 5 | South | EPWF4
133343 | 2016-03-20 | Scheduled Outage | Construction | Rick Barnett to have transformers open for pole replacement. X30531. Customers notified. | None | None | 17 | 340 | 96 | Central | AB05
133344 | 2016-03-20 | Scheduled Outage | Construction | Rick Barnett to have transofrmer X30774 open for pole replacement. Customers notified. | None | None | 1 | 340 | 6 | Central | AB05
133345 | 2016-03-20 | Scheduled Outage | Construction | Rick Barnett to have transofrmer X30550-1666005 open for pole replacement. Customers notified. | None | None | 3 | 435 | 22 | Central | AB05
133346 | 2016-03-21 | Scheduled Outage | Maintenance | Micro-fit and vault maintenance | None | Connector | 1 | 338 | 6 | South | 140F1
133347 | 2016-03-21 | Scheduled Outage | Construction | Install new overhead conductors. | None | None | 1 | 78 | 1 | South | FAL03
133348 | 2016-03-21 | Scheduled Outage | Construction | Transformer #X34163 isolated by crew to install 2 new services | None | None | 4 | 65 | 4 | Central | SM15
133349 | 2016-03-21 | Scheduled Outage | Construction | Black and Macdonald have X23563 open for pole replacement. Customers notified. | None | None | 10 | 180 | 30 | East | SO10
133350 | 2016-03-21 | Scheduled Outage | Construction | Black and Macdonald have X23561 open for pole replacement. Customers notified. | None | None | 12 | 180 | 36 | East | SO10
133352 | 2016-03-21 | Scheduled Outage | Construction | Scott Barkley to have X29925 open to instal new service @ 51 Elliot. Customers notified. | None | None | 9 | 69 | 10 | Central | SR02
133353 | 2016-03-21 | Scheduled Outage | Construction | Transformer #X26095 isolated by crew to transfer plant | None | None | 17 | 1 | 0 | East | SO10
133354 | 2016-03-21 | Adverse Environment | Contamination (Dirt, pollution, other external particles) | OFD reports pole fire at 1550 Michael | Pole | Insulation Failure (Pole Fire) | 2 | 346 | 12 | East | TB07
133354 | 2016-03-21 | Adverse Environment | Contamination (Dirt, pollution, other external particles) | OFD reports pole fire at 1550 Michael | Pole | Insulation Failure (Pole Fire) | 108 | 388 | 698 | East | TB07
133354 | 2016-03-21 | Adverse Environment | Contamination (Dirt, pollution, other external particles) | OFD reports pole fire at 1550 Michael | Pole | Insulation Failure (Pole Fire) | 329 | 1 | 5 | East | TB07
133354 | 2016-03-21 | Adverse Environment | Contamination (Dirt, pollution, other external particles) | OFD reports pole fire at 1550 Michael | Pole | Insulation Failure (Pole Fire) | 329 | 45 | 247 | East | TB07
133355 | 2016-03-21 | Scheduled Outage | Construction | Joe Mckenna to have X11074 open to replace a cut-out switch. Customers notified. | None | None | 5 | 55 | 5 | West | BECKF2
133356 | 2016-03-21 | Scheduled Outage | Maintenance | Doug Featherstone to have TP3108 open to replace hot connections on U/G secondary. Customers notified. | U/G Transformer | Padmount (1ph) | 13 | 67 | 15 | East | BCHF5
133357 | 2016-03-21 | Scheduled Outage | Construction | disconnect temporary service, and connect permanent service. | None | None | 1 | 105 | 2 | South | 84F4
133358 | 2016-03-21 | Human Element | Improper Construction/installation | Contractor pulled secondary neutral bushing out of TP10276. | U/G Transformer | Padmount (1ph) | 114 | 118 | 224 | West | TFXF1
133359 | 2016-03-22 | Scheduled Outage | Construction | Overhead transformer at 2347 Sheldon was opened to allow for upgrades, affecting 5 customers, Edwin UV03 | None | None | 5 | 54 | 4 | Central | UV03
133360 | 2016-03-22 | Scheduled Outage | Maintenance | Transformer TE1443 at 1404 Foxwell was isolated to allow crew to make repairs to transformer elbows, H1A and H1B. | None | None | 22 | 184 | 67 | East | 6F1
133361 | 2016-03-22 | Scheduled Outage | Construction | Transformer #X29276 isolated by crew for a service upgrade | None | None | 12 | 30 | 6 | East | UG05
133362 | 2016-03-22 | Scheduled Outage | Construction | Transformer #X34116 isolated by crew for service removal and relocation | None | None | 10 | 63 | 10 | Central | TH01
133363 | 2016-03-22 | Scheduled Outage | Maintenance | Customer vault isolation to allow contractor to repair CB1 breaker. | None | Customer-Owned | 1 | 138 | 2 | East | TO3UT
133364 | 2016-03-23 | Scheduled Outage | Maintenance | Transformer #2520 isolated by crew to make repairs to defective secondary service | None | None | 7 | 40 | 5 | West | BRDF5
133365 | 2016-03-23 | Scheduled Outage | Construction | 2 transformers, X23563 and X23561 isolated by crew to transfer to new transformer #X49756 | None | None | 17 | 10 | 3 | East | SO10
133366 | 2016-03-23 | Scheduled Outage | Construction | Transformer #X30773 isolated by crew to transfer plant | None | None | 4 | 105 | 7 | Central | AB05
133367 | 2016-03-23 | Scheduled Outage | Construction | Transformer #X30654 isolated by crew to transfer plant | None | None | 21 | 140 | 49 | Central | AB06
133368 | 2016-03-23 | Scheduled Outage | Construction | Transformer #X38339 isolated by crew to replace defective transformer | None | None | 18 | 90 | 27 | Central | TR3UY
133369 | 2016-03-23 | Scheduled Outage | Maintenance | S28161CHZ Switch isolated at 2244 Innes affecting 1 customer on the 48M3 out of Hawthorne for contractor to perform substation and switch maintenance | None | None | 1 | 519 | 9 | East | 48M3
133370 | 2016-03-24 | Scheduled Outage | Maintenance | Doug Featherstone to have transformer 65C1B-0122 open to remove a piece of tin from secondary and repair neutral. Customers notified. | None | None | 13 | 41 | 9 | East | UT02
133371 | 2016-03-24 | Foreign Interference | Vehicle | MVA at pole feeding 4kv transformer K340 caused damage to pole and switch to break. | O/H Switchgear | Fused Cutout | 11 | 96 | 18 | East | AL02
133372 | 2016-03-25 | Defective Equipment | Defective Equipment/ Material | Defective Cut-out switch @ transformer X31022. Replaced by 24/7. | O/H Transformer | O/H Transformer (1ph) | 27 | 85 | 38 | Central | AB06
133373 | 2016-03-26 | Defective Equipment | Defective Equipment/ Material | Transformer X45601 opened due to defective hot line clamp. | O/H Switchgear | Fused Cutout | 25 | 92 | 38 | East | UT04
133376 | 2016-03-26 | Scheduled Outage | Maintenance | VT432 Rideau Center, isoalted for customer maintenance, and to install new 1200 amp switch. | None | None | 1 | 630 | 10 | Central | 411
133377 | 2016-03-27 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X20853 opened due to animal contact. | O/H Switchgear | Fused Cutout | 12 | 80 | 16 | East | BCHF3
133379 | 2016-03-28 | Defective Equipment | Electrical Failure | S944 W phase opened due to transformer failure at TE1103. Stafford (200F6) | U/G Transformer | Padmount (3ph) | 9 | 276 | 41 | South | 200F6
133379 | 2016-03-28 | Defective Equipment | Electrical Failure | S944 W phase opened due to transformer failure at TE1103. Stafford (200F6) | U/G Transformer | Padmount (3ph) | 64 | 45 | 48 | South | 200F6
133379 | 2016-03-28 | Defective Equipment | Electrical Failure | S944 W phase opened due to transformer failure at TE1103. Stafford (200F6) | U/G Transformer | Padmount (3ph) | 132 | 34 | 75 | South | 200F6
133379 | 2016-03-28 | Defective Equipment | Electrical Failure | S944 W phase opened due to transformer failure at TE1103. Stafford (200F6) | U/G Transformer | Padmount (3ph) | 142 | 28 | 66 | South | 200F6
133380 | 2016-03-29 | Foreign Interference | Customer Equipment | Defective 3 phase bank of transformers. | Customer Owned | Customer-Owned | 1 | 1178 | 20 | East | 6F1
133380 | 2016-03-29 | Foreign Interference | Customer Equipment | Defective 3 phase bank of transformers. | Customer Owned | Customer-Owned | 27 | 818 | 368 | East | 6F1
133381 | 2016-03-29 | Tree Contacts | Falling Tree | Tree contact brought down primary line. On call crew required to make repairs. Albion 2207. | O/H Conductor | O/H Conductor | 72 | 175 | 210 | East | 2207
133382 | 2016-03-29 | Scheduled Outage | Vegetation Management | Overhead transformer X42421 interrupted for vegetation management at 1890 Sixth Line affecting 1 customer on the 624F6 out of Kanata MTS | None | None | 1 | 210 | 4 | West | 624F6
133383 | 2016-03-29 | Scheduled Outage | Maintenance | Yannick to have transformer X35687 open for maintenance. Customers notified. | None | None | 7 | 62 | 7 | Central | TD14
133384 | 2016-03-29 | Scheduled Outage | Maintenance | switching on out of phase condition | None | None | 143 | 10 | 24 | South | 140F4
133386 | 2016-03-29 | Human Element | Improper Construction/installation | Pole slid into hole while contractor was digging to prepare for new pole. Crews stablized pole and re-tensioned the overhead. Janet King DS (44F3). | Pole | Pole | 83 | 60 | 83 | West | 44F3
133387 | 2016-03-30 | Scheduled Outage | Forced Switching | Switching interruption was required to TP8915 and TP8918 transformers to perform an isolation of cable section on the MWDF3 out of Marchwood affecting 15 customers for 2 minutes. | None | None | 15 | 2 | 0 | West | MWDF3
133388 | 2016-03-30 | Scheduled Outage | Construction | Scott Barkley to have X29785 open to install a new secondary service at 22 Hazel. Customers notified. | None | None | 7 | 52 | 6 | Central | SR03
133389 | 2016-03-30 | Scheduled Outage | Construction | Overhead section on Avenue N isolated to transfer plant to new poles, affecting 17 customers. Overbrook sub SO10 | None | None | 17 | 240 | 68 | East | SO10
133390 | 2016-03-30 | Scheduled Outage | Construction | Overhead section on Avenue O isolated to transfer plant to new poles, affecting 3 customers. Overbrook sub SO10 | None | None | 3 | 146 | 7 | East | SO10
133391 | 2016-03-30 | Scheduled Outage | Construction | Brent Duncan had transformer X30670 open to install new pole. Customers notified. | None | None | 11 | 121 | 22 | Central | AB06
133392 | 2016-03-30 | Scheduled Outage | Maintenance | To restore 140F4 and and due out of phase condition with WX2052, 145 customer were interupted. Barrhaven DS | None | None | 145 | 3 | 7 | South | 140F4
133393 | 2016-03-31 | Defective Equipment | Defective Equipment/ Material | S17175 W phase blew due to defective switch G560. | O/H Switchgear | Fused Cutout | 129 | 146 | 314 | East | 8F3
133394 | 2016-03-31 | Defective Equipment | Defective Equipment/ Material | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X38286 | O/H Transformer | O/H Transformer (1ph) | 1 | 81 | 1 | West | MWDF3
133395 | 2016-03-31 | Defective Equipment | Defective Equipment/ Material | A broken switch S26818 @ 1757 HAIG DR | O/H Switchgear | Fused Cutout | 41 | 61 | 42 | East | TB15
133396 | 2016-03-31 | Defective Equipment | Mechanical Failure | The Bronson SB05 CB tripped on instantaneous WB. Circuit was patrolled and nothing was found | U/G Cable | PILC | 729 | 27 | 328 | Central | SB05
133397 | 2016-04-01 | Scheduled Outage | Maintenance | Transformer TP7063 was isolated to allow crew to change leaking transformer. Billberry (77M6) | None | None | 14 | 98 | 23 | East | 77M6
133398 | 2016-04-01 | Scheduled Outage | Construction | The O/H from switch S427 @ 4230 VIEWBANK RD was isolated to allow the crews to transfer the load from Red phase to Blue phase | None | O/H Conductor | 17 | 34 | 10 | South | FAL03
133399 | 2016-04-01 | Scheduled Outage | Forced Switching | Switching interruption was required to TP8915 and TP8918 transformers to perform the restoration of cable section on the MWDF3 out of Marchwood affecting 15 customers for 2 minutes. | None | Padmount (1ph) | 15 | 2 | 0 | West | MWDF3
133400 | 2016-04-01 | Scheduled Outage | Construction | Patrick Brisson to have X35497 open to cut blown arrestor clear. Customers notified. | None | None | 2 | 14 | 0 | Central | UC07
133401 | 2016-04-01 | Scheduled Outage | Construction | Patrick Brisson to have X35690 open to replace a switch. Customers notified. | None | None | 11 | 35 | 6 | Central | TD14
133402 | 2016-04-01 | Scheduled Outage | Maintenance | Metering Repairs by HOL Crew at 1419 Carling isolating VT901W1 transformer bus affecting 1 customer for 15 minutes on the Carling 301 circuit. | None | None | 1 | 15 | 0 | Central | 301
133405 | 2016-04-02 | Defective Equipment | Defective Equipment/ Material | Janet King T2 trip due to gas alarm. Faulty wire on oil gas relay caused trip. | Station Equipment | Transformer | 1082 | 45 | 812 | West | JKGF5
133405 | 2016-04-02 | Defective Equipment | Defective Equipment/ Material | Janet King T2 trip due to gas alarm. Faulty wire on oil gas relay caused trip. | Station Equipment | Transformer | 3713 | 50 | 3094 | West | JKGF4
133406 | 2016-04-03 | Defective Equipment | Mechanical Failure | Suspected cable fault between SW1600 and SC27912, caused the Station breaker to trip affecting 342 customers, Carling TM2SB | U/G Cable | PILC | 32 | 7 | 4 | Central | TM2SB
133406 | 2016-04-03 | Defective Equipment | Mechanical Failure | Suspected cable fault between SW1600 and SC27912, caused the Station breaker to trip affecting 342 customers, Carling TM2SB | U/G Cable | PILC | 122 | 43 | 87 | Central | TM2SB
133406 | 2016-04-03 | Defective Equipment | Mechanical Failure | Suspected cable fault between SW1600 and SC27912, caused the Station breaker to trip affecting 342 customers, Carling TM2SB | U/G Cable | PILC | 342 | 67 | 382 | Central | TM2SB
133408 | 2016-04-03 | Scheduled Outage | Maintenance | VT53 was isolated to allow stations crew to top up oil in transformers & customer to replace defective switchgear handle. Overbrook 1807. | None | Transformer | 2 | 69 | 2 | East | 1807
133409 | 2016-04-03 | Scheduled Outage | Maintenance | Transformer #NPTE0005 isolated by crew to disconnect other leg during repairs to a defective U/G service | None | None | 12 | 15 | 3 | South | 160F2
133410 | 2016-04-03 | Scheduled Outage | Maintenance | Transformer #NPTE0005 isolated by crew due to repairs made to defective U/G sec cable from TE05 to ped. | None | None | 12 | 13 | 3 | South | 160F2
133412 | 2016-04-04 | Scheduled Outage | Construction | Transformer #K00431 isolated by crew to disconnect 2 services for the contractor to make repairs | None | None | 14 | 15 | 4 | East | AN05
133413 | 2016-04-04 | Scheduled Outage | Construction | Transformer #X30766 isolated by crew for a service upgrade | None | None | 6 | 155 | 16 | Central | AB06
133414 | 2016-04-04 | Scheduled Outage | Construction | Transformer #X31995 isolated by crew to run a new service | None | None | 7 | 50 | 6 | Central | SM12
133415 | 2016-04-04 | Scheduled Outage | Construction | Transformer #X31146 isolated by crew to transfer plant | None | None | 18 | 35 | 10 | Central | SA23
133417 | 2016-04-05 | Scheduled Outage | Construction | Scott Barkley and crew to have X31632 open to run a new service to 11 Bellwood Ave. Customers notified. | None | None | 8 | 49 | 7 | Central | SR06
133418 | 2016-04-05 | Scheduled Outage | Maintenance | V423 @ 50 James St was isolated to allow the contractor to preform vault maintenance. | None | Transformer | 24 | 201 | 80 | Central | UF04
133419 | 2016-04-05 | Scheduled Outage | Construction | The Overhead at 1327 Avenu T was isolated by the contractor to allow them transfer the plant to new poles and remove primary runoffs on the SO10 circuit | None | O/H Conductor | 25 | 350 | 146 | East | SO10
133420 | 2016-04-05 | Scheduled Outage | Maintenance | KT385 @ 24 Rideauview Terrace was isolated by the crew to allow them to replace the secondary UG conductor. | None | Unknown \ Other | 10 | 122 | 20 | Central | 303
133422 | 2016-04-06 | Scheduled Outage | Maintenance | V840 @ 515 MacLaren on the UF05 curcuit was isolated to allow the contractor to perform vault maintenance | Vault Equipment | Breaker \ Relay | 1 | 149 | 2 | Central | UF05
133423 | 2016-04-06 | Scheduled Outage | Construction | The overhead on Avenue T was isolated to allow the contractor to transfer the plant to new poles and remove primary runoffs on Avenue S/T | None | O/H Conductor | 25 | 325 | 135 | East | SO10
133424 | 2016-04-08 | Scheduled Outage | Construction | Transfomrer 36W at 67 McIntosh isolated to replace transfomer. 6 customers affected. Brildewood (BRDF4) | None | Padmount (1ph) | 6 | 242 | 24 | West | BRDF4
133425 | 2016-04-08 | Scheduled Outage | Construction | Robin Blair to have X44323 open to run a new service and transfer load. Customers notified. | None | None | 2 | 62 | 2 | South | FAL03
133426 | 2016-04-08 | Scheduled Outage | Construction | Geoff Ryan to have X10636 open to replace glass insulators. Customers notified. | None | None | 16 | 63 | 17 | West | 28F2
133427 | 2016-04-08 | Scheduled Outage | Construction | Patrick Brisson to have X30653 open to transfer conductor. Customers notified. | None | None | 9 | 180 | 27 | Central | AB06
133428 | 2016-04-08 | Scheduled Outage | Construction | Chris Williams to have X27559 open for pole replacement. Customers notified. | None | None | 24 | 150 | 60 | Central | UF07
133429 | 2016-04-08 | Defective Equipment | Defective Equipment/ Material | Burned hot-line clamp on the SB07 blue phase that feeds Young St. Two transformers effected X25678 and X25687. | O/H Conductor | Hot-Line Clamp | 8 | 136 | 18 | Central | SB07
133430 | 2016-04-09 | Scheduled Outage | Maintenance | replace main OCB at VE076G at CSIS | None | None | 1 | 632 | 11 | East | 8F1
133433 | 2016-04-12 | Scheduled Outage | Construction | P256 at 300 Sommerset isolated to allow crews to rearrange overhead conductor. 1 customer affected. Slater (SA23) | None | O/H Conductor | 1 | 95 | 2 | Central | SA23
133434 | 2016-04-12 | Scheduled Outage | Construction | SO10 isolated between TEMP 55 and TEMP 64 on Avenue R and S to allow crews to transfer plant to new poles. 27 customers affected. Overbrook (SO10) | None | O/H Conductor | 27 | 385 | 173 | East | SO10
133435 | 2016-04-12 | Scheduled Outage | Construction | UF07 overhead from Gilmore and Percy to EOL isolated for conductor replacement. 89 customers affected. Florence (UF07) | None | O/H Conductor | 89 | 230 | 341 | Central | UF07
133436 | 2016-04-12 | Scheduled Outage | Construction | Transformer TE1951 was isolated to allow crew to transfer riser to new pole | None | None | 1 | 159 | 3 | South | EPWF4
133438 | 2016-04-12 | Scheduled Outage | Construction | TP6869 at 5925 Shea Rd. isolated to allow crew to move the primary cables to a different circuit. 2 customers affected. Richmond South (28F3) | None | Pothead | 2 | 5 | 0 | West | 28F3
133439 | 2016-04-13 | Scheduled Outage | Construction | SO10 overheadbetween TEMP 55 and TEMP 40 isolated to change poles and transfer plant. 24 customers affected. Overbrook (SO10) | None | O/H Conductor | 24 | 340 | 136 | East | SO10
133441 | 2016-04-13 | Scheduled Outage | Construction | Install new sec service | None | None | 21 | 270 | 94 | Central | AB06
133442 | 2016-04-13 | Scheduled Outage | Construction | Jordan Foote of K-line to have X31029 open to move transformer. Customers notified. | None | None | 1 | 36 | 1 | Central | UX08
133443 | 2016-04-14 | Scheduled Outage | Maintenance | To allow contractor to make repairs to main switch. | None | Padmount (3ph) | 1 | 60 | 1 | West | JKGF4
133444 | 2016-04-14 | Scheduled Outage | Maintenance | replace defective insulators | None | None | 1 | 60 | 1 | East | UG09
133445 | 2016-04-14 | Scheduled Outage | Construction | Transfer Plant to new pole | None | None | 30 | 180 | 90 | Central | AB06
133446 | 2016-04-14 | Scheduled Outage | Vegetation Management | Transformer #X32281 isolated by crew for Davey Tree to do trimming | None | None | 8 | 93 | 12 | Central | TD01
133447 | 2016-04-14 | Human Element | Switching Error | Human Element | U/G Transformer | Padmount (1ph) | 18 | 154 | 46 | East | 77M6
133448 | 2016-04-15 | Scheduled Outage | Maintenance | repair elbow connection | None | None | 1 | 120 | 2 | East | 5309
133449 | 2016-04-15 | Scheduled Outage | Construction | temporary outage due to out of phase condition to switch in a rabbit. | None | None | 510 | 2 | 17 | West | RHNF1
133450 | 2016-04-17 | Unknown/Other | Unknown | Line fues blue phase opened, no appatrent cause found affecting 231 customers. Moulton 8F1 | None | None | 231 | 81 | 312 | East | 8F1
133451 | 2016-04-17 | Scheduled Outage | Construction | HOL crews transferring plant to new poles on the Bells Corners 47F6 overhead at Moodie and Dilblee affecting power to 10 customers. | None | None | 10 | 449 | 75 | South | 47F6
133452 | 2016-04-17 | Defective Equipment | Electrical Failure | 200F1 overhead circuit from S515 to EOL isolated due to pole fire at 34 Solva Dr. 260 customers affected. Stafford (200F1) | Pole | Insulation Failure (Pole Fire) | 260 | 187 | 810 | South | 200F1
133454 | 2016-04-18 | Unknown/Other | Unknown | G649 R phase at 6541 Old Richmond found open. No cause found. 2 customers affected. Jockvale (145F3) | Unknown \ Other | Unknown \ Other | 2 | 53 | 2 | South | 145F3
133455 | 2016-04-18 | Scheduled Outage | Construction | Glen Carswell and crew to have transformer X256654 open to install a new pole. Customers notified. | None | None | 15 | 77 | 19 | Central | TH11-NIU
133456 | 2016-04-18 | Scheduled Outage | Construction | Transformer #X30670 isolated by crew to transfer plant | None | None | 11 | 155 | 28 | Central | AB06
133457 | 2016-04-18 | Scheduled Outage | Maintenance | Transformer #X25584 isolated by crew to replace broken insulator | None | None | 15 | 40 | 10 | Central | SB14
133458 | 2016-04-18 | Scheduled Outage | Construction | Robin Blair and crew to have transformer X3371 open to transfer plant to a new pole. Customers notified. | None | None | 4 | 173 | 12 | South | 200F3
133459 | 2016-04-18 | Scheduled Outage | Maintenance | VT78 @ 158B McArthur was isolated to allow the contractor to preform secondary main breaker maintenance and top up the oil in the main OCB | None | Breaker \ Relay | 174 | 230 | 667 | East | TO3UT
133460 | 2016-04-18 | Scheduled Outage | Construction | The Overhead on Avenue P/Q was isolated to allow the contractor to transfer the plant to new poles and remove the primary runoffs | None | O/H Conductor | 59 | 361 | 355 | East | SO10
133462 | 2016-04-19 | Unknown/Other | Unknown | Not yet known. | None | None | 162 | 72 | 194 | East | 2203
133463 | 2016-04-19 | Defective Equipment | Mechanical Failure | Cable fault between TP5408 & TP5409 caused 302 B to open. | U/G Cable | Unknown \ Other | 10 | 35 | 6 | West | BRDF5
133463 | 2016-04-19 | Defective Equipment | Mechanical Failure | Cable fault between TP5408 & TP5409 caused 302 B to open. | U/G Cable | Unknown \ Other | 42 | 153 | 107 | West | BRDF5
133464 | 2016-04-19 | Scheduled Outage | Vegetation Management | At 9:28 section of TD12 was isolated to allow crews to perform tree trimming. 19 customers affected. Lincoln Heights (TD12) ID#133464 | None | None | 19 | 125 | 40 | Central | TD12
133465 | 2016-04-19 | Scheduled Outage | Construction | At 8:30 am SO10 from S15919 to end of line was isolated to allow crew to reconfigure overhead lines. 46 customers affected. Overbrook (SO10) ID#133465 | None | None | 46 | 311 | 238 | East | SO10
133467 | 2016-04-19 | Scheduled Outage | Construction | Transformer #X3371 isolated by crew to transfer plant | None | None | 4 | 125 | 8 | South | 200F3
133468 | 2016-04-19 | Scheduled Outage | Construction | Transformer #X31016 isolated by crew to transfer plant to install new pole | None | None | 15 | 155 | 39 | Central | AB06
133469 | 2016-04-19 | Scheduled Outage | Construction | Transformer #X31025 isolated by crew to transfer plant | None | None | 1 | 20 | 0 | Central | UF10
133470 | 2016-04-19 | Scheduled Outage | Construction | Transformer #X29030 isolated by crew to re-sag a secondary service | None | None | 7 | 20 | 2 | East | SO04
133472 | 2016-04-19 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree limb brought Sec/Primary neutral | O/H Conductor | O/H Conductor | 19 | 286 | 91 | East | AF04
133473 | 2016-04-20 | Defective Equipment | Defective Equipment/ Material | Red phase cable fault between TE349 and TE350. | U/G Cable | XLPE | 26 | 20 | 9 | East | BCHF8
133473 | 2016-04-20 | Defective Equipment | Defective Equipment/ Material | Red phase cable fault between TE349 and TE350. | U/G Cable | XLPE | 36 | 53 | 32 | East | BCHF8
133473 | 2016-04-20 | Defective Equipment | Defective Equipment/ Material | Red phase cable fault between TE349 and TE350. | U/G Cable | XLPE | 238 | 66 | 262 | East | BCHF8
133473 | 2016-04-20 | Defective Equipment | Defective Equipment/ Material | Red phase cable fault between TE349 and TE350. | U/G Cable | XLPE | 820 | 86 | 1175 | East | BCHF8
133474 | 2016-04-20 | Scheduled Outage | Maintenance | A section of Jockvale 145F3 between S649 & S1510 was isolated to make repairs caused by a recurring issue on the o/h line. | None | Unknown \ Other | 26 | 85 | 37 | South | 145F3
133475 | 2016-04-20 | Defective Equipment | Defective Equipment/ Material | Fuse at 2660 Marchurst Rd opened up (TBD) due to defective fuse | O/H Switchgear | Inline Switch | 2 | 108 | 4 | West | MWDF3
133476 | 2016-04-20 | Scheduled Outage | Vegetation Management | Transformer #X26976 isolated by crew due to tree trimming and transformer maintenance | None | None | 14 | 195 | 46 | East | AJ05
133477 | 2016-04-20 | Scheduled Outage | Construction | Transformer #X30651 isolated by crew to transfer plant | None | None | 30 | 150 | 75 | Central | AB06
133478 | 2016-04-20 | Foreign Interference | Agricultural Equipment | Suspect farm equipment contacted Hydro 1 road crossing switch pole (transfer customer) and neutral wrapped around Primary. Leitrim (249F2 - RX2041) | O/H Conductor | O/H Conductor | 141 | 108 | 254 | East | 249F2
133479 | 2016-04-21 | Defective Equipment | Mechanical Failure | Riser switch at Kent and Cooper isolated to repair termination at the switch affecting 26 customers. Nepean sub AB05 | O/H Switchgear | Vega Switch | 26 | 194 | 84 | Central | AB05
133481 | 2016-04-21 | Scheduled Outage | Construction | Brian Brooks from Black and Macdonald to have X29600 open to replace the pole. Customers notified. | None | None | 12 | 82 | 16 | East | SO10
133482 | 2016-04-21 | Scheduled Outage | Maintenance | Sam Gibson to have X32951 open to replace O/H secondary conductor after burn damage. Customers notified. | None | None | 7 | 86 | 10 | Central | TD07
133483 | 2016-04-21 | Scheduled Outage | Construction | Jim Yeldon and crew to have X31597 open to replace the cut-out switch and install new secondary service. Customers notified. | None | None | 9 | 119 | 18 | Central | UC06
133484 | 2016-04-21 | Scheduled Outage | Maintenance | Sam Gibson to have X36739 open to replace burnt O/H secondary conductor. Customers notified. | None | None | 5 | 45 | 4 | South | 160F1
133486 | 2016-04-22 | Scheduled Outage | Construction | SC19919 at 491 Richmond Rd. isolated to connect new TV10887. 3 customers affected. Carling (TM1AH) | None | None | 3 | 132 | 7 | Central | TM1AH
133487 | 2016-04-22 | Scheduled Outage | Maintenance | Bill Edwards to have K01158 open to perform load balancing. Customers notified. | None | None | 2 | 8 | 0 | East | UB07
133488 | 2016-04-22 | Scheduled Outage | Vegetation Management | Joe Mckenna to have X35275 open for tree removal. Customers notified. | None | None | 11 | 9 | 2 | West | 44F1
133489 | 2016-04-22 | Defective Equipment | Mechanical Failure | A pole fire caused S565 to slip down the pole. The switch stayed closed, however had to be opened to allow line crews to make the area safe and establish permitry for repairs. | O/H Switchgear | Fused Cutout | 27 | 133 | 60 | South | 190F5
133489 | 2016-04-22 | Defective Equipment | Mechanical Failure | A pole fire caused S565 to slip down the pole. The switch stayed closed, however had to be opened to allow line crews to make the area safe and establish permitry for repairs. | O/H Switchgear | Fused Cutout | 34 | 44 | 25 | South | 190F5
133489 | 2016-04-22 | Defective Equipment | Mechanical Failure | A pole fire caused S565 to slip down the pole. The switch stayed closed, however had to be opened to allow line crews to make the area safe and establish permitry for repairs. | O/H Switchgear | Fused Cutout | 61 | 30 | 30 | South | 190F5
133490 | 2016-04-22 | Scheduled Outage | Vegetation Management | Mike Anderson and crew to have X27048 open for tree trimming. Customers notified. | None | None | 6 | 190 | 19 | East | TB06
133491 | 2016-04-22 | Scheduled Outage | Construction | Brent Duncan and crew to have transformer X30670 open to rearrange secondaries. Customers notified. | None | None | 11 | 52 | 10 | Central | AB06
133492 | 2016-04-22 | Scheduled Outage | Building/ High Load Move | Bill Edwards to have transformer 65A4A-0386 open for load balancing purposes. Customer notified. | None | None | 1 | 22 | 0 | East | UB07
133493 | 2016-04-22 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER 2520 TO DISCONNECT DEFECTIVE SECODARY UNDERGROUND SERVICE | None | None | 7 | 57 | 7 | West | BRDF5
133494 | 2016-04-22 | Scheduled Outage | Maintenance | Transformer 2520 at 104 Sherwood opened to re-connect service. 7 customers affected. Bridlewood BRDF5. | None | U/G Service | 7 | 20 | 2 | West | BRDF5
133496 | 2016-04-23 | Scheduled Outage | Maintenance | contractor performing maintenance on secondary. | None | None | 1 | 400 | 7 | South | 180F3
133497 | 2016-04-24 | Scheduled Outage | Maintenance | REPLACE STREET LIGHT FUSE | None | None | 10 | 13 | 2 | Central | UV03
133498 | 2016-04-24 | Scheduled Outage | Maintenance | REPLACE STREETLIGHT FUSE | None | None | 8 | 20 | 3 | Central | TD01
133499 | 2016-04-24 | Unknown/Other | Unknown | Not yet known. | None | None | 408 | 12 | 82 | Central | AD02
133500 | 2016-04-25 | Scheduled Outage | Maintenance | planned outage to balance load | None | None | 12 | 47 | 9 | East | UB07
133501 | 2016-04-25 | Scheduled Outage | Construction | planned outage to re-arrange SA23 overhead conductor | None | None | 1 | 240 | 4 | Central | SA23
133503 | 2016-04-25 | Scheduled Outage | Maintenance | change leaking transformer TP7914 | None | Padmount (1ph) | 8 | 116 | 15 | East | 77M2
133504 | 2016-04-25 | Scheduled Outage | Construction | Elbow, insert and switch replacement. | None | None | 39 | 222 | 144 | East | 8F3
133505 | 2016-04-25 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30670 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 11 | 225 | 41 | Central | AB06
133506 | 2016-04-25 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30673 TO INSTALL NEW POLE | None | None | 31 | 265 | 137 | Central | UF07
133508 | 2016-04-26 | Scheduled Outage | Maintenance | Jordan Foote of K-Line had transformer X31148 open to transfer plant. Customers notified. | None | None | 13 | 109 | 24 | Central | UX08
133509 | 2016-04-26 | Scheduled Outage | Construction | Transformer TP9594 at 408 Country Glen Way was isolated to allow crew to up^grade transformer from75 KVA to 100 KVA. | None | None | 13 | 104 | 23 | West | 624F1
133510 | 2016-04-26 | Scheduled Outage | Maintenance | Glenn Carswell to have transformer X26064 open to replace broken cut-out switch. Customers notified. | None | None | 11 | 18 | 3 | Central | SM15
133511 | 2016-04-26 | Scheduled Outage | Maintenance | Chris Costello to have transformer X28028 open to re-deadhead secondary services. Customers notified. | None | None | 12 | 121 | 24 | East | AF05
133512 | 2016-04-26 | Scheduled Outage | Maintenance | Geoff Ryan to have transformer 002660 open to splice U/G secondary service. Customers notified. | None | None | 16 | 42 | 11 | West | BRDF6
133513 | 2016-04-26 | Scheduled Outage | Construction | Dolton Henry to have transformer X27558 open for pole replacement. Customers notified. | None | None | 16 | 240 | 64 | Central | UF07
133514 | 2016-04-26 | Scheduled Outage | Construction | Dan Crough from K-Line to have X48936 open to transfer plant. Customers notified. | None | None | 6 | 175 | 18 | Central | UF10
133515 | 2016-04-26 | Scheduled Outage | Construction | Transformer #X46349 isolated by crew to replace transformer | None | None | 10 | 120 | 20 | East | SO11
133516 | 2016-04-27 | Scheduled Outage | Forced Switching | Transformers X25007 and X30275 isolated due to fire at 24 Spadina. 46 customers affected. Bayswater (UJ05) Customers at 22, 24, and 26 will remain without power due to fire damage. | None | O/H Transformer (1ph) | 46 | 223 | 171 | Central | UJ05
133517 | 2016-04-27 | Scheduled Outage | Construction | Bryan Brooks from Black and Macdonald to have X49783 open for pole replacement. Customers notified. | None | None | 25 | 150 | 62 | East | SO10
133518 | 2016-04-27 | Scheduled Outage | Maintenance | Shaun Evans of K-Line to have transformer X31149 open for the transfer of plant. Customers notified. | None | None | 5 | 77 | 6 | Central | SA22
133519 | 2016-04-27 | Scheduled Outage | Construction | Dan Crough to have transformer X31143 open to transfer plant. Customers notified. | None | None | 3 | 90 | 4 | Central | SA22
133520 | 2016-04-27 | Scheduled Outage | Maintenance | Shaun Evans (K-Line) to have transformer X31147 open to transfer plant. Customers notified. | None | None | 30 | 125 | 62 | Central | SA22
133521 | 2016-04-27 | Scheduled Outage | Construction | Brian Brooks from Black and Macdonald to have transformer X49738 open for pole replacement. Customes notified. | None | None | 10 | 150 | 25 | East | SO10
133522 | 2016-04-27 | Scheduled Outage | Maintenance | Contractor isolated V808 at 420 Lewis to allow them to transfer the riser to the new pole. | None | Unknown \ Other | 27 | 178 | 80 | Central | UX08
133523 | 2016-04-28 | Defective Equipment | Mechanical Failure | G530 was opened to isolate runoff to Tx 5940. Defective cut out caused pole fire at runoff to Tx 5940. Limebank LMBF5. | O/H Switchgear | Fused Cutout | 1 | 145 | 2 | East | LMBF5
133523 | 2016-04-28 | Defective Equipment | Mechanical Failure | G530 was opened to isolate runoff to Tx 5940. Defective cut out caused pole fire at runoff to Tx 5940. Limebank LMBF5. | O/H Switchgear | Fused Cutout | 2 | 5 | 0 | East | LMBF5
133525 | 2016-04-30 | Scheduled Outage | Maintenance | Carleton Univ vault VT8 @ 1125 Colonel By was isolated for the contractor to allow him install barrier board for future work. | None | Unknown \ Other | 1 | 176 | 3 | Central | TR2UY
133526 | 2016-04-30 | Scheduled Outage | Maintenance | Vault VT108 @ 320 Sparks St was isolated to allow the contractor to perform vault maintenance, 1 customer affected | None | Breaker \ Relay | 1 | 482 | 8 | Central | 611
133527 | 2016-04-30 | Defective Equipment | Mechanical Failure | Cable fault between G331 & TP9362, blown elbow & insert at TE506 and a broken elbow & insert at TE505 | U/G Cable | XLPE | 78 | 21 | 27 | East | BCHF8
133527 | 2016-04-30 | Defective Equipment | Mechanical Failure | Cable fault between G331 & TP9362, blown elbow & insert at TE506 and a broken elbow & insert at TE505 | U/G Cable | XLPE | 78 | 315 | 410 | East | BCHF8
133527 | 2016-04-30 | Defective Equipment | Mechanical Failure | Cable fault between G331 & TP9362, blown elbow & insert at TE506 and a broken elbow & insert at TE505 | U/G Cable | XLPE | 91 | 53 | 80 | East | BCHF8
133527 | 2016-04-30 | Defective Equipment | Mechanical Failure | Cable fault between G331 & TP9362, blown elbow & insert at TE506 and a broken elbow & insert at TE505 | U/G Cable | XLPE | 91 | 81 | 123 | East | BCHF8
133528 | 2016-05-01 | Scheduled Outage | Construction | Decommisioning preparation of V161 by contractor on the AB02 out of Nepean affecting 2 customers | None | None | 2 | 237 | 8 | Central | AB02
133529 | 2016-05-01 | Unknown/Other | Unknown | Transformer #X35936 opened up, crew could not find cause | O/H Switchgear | Fused Cutout | 11 | 79 | 14 | South | 190F5
133530 | 2016-05-01 | Scheduled Outage | Forced Switching | Section of 302 and TM1DK overhead on Fisher Ave isolated to allow crews to remove a truck from against a broken pole after an MVA. 2 customers affected. Carling (303, TM1DK) | None | None | 2 | 135 | 4 | Central | 303
133531 | 2016-05-02 | Scheduled Outage | Construction | SO10 circuit between M40 and X49749 isolated for pole change. 16 customers affected. Overbrook (SO10) | None | O/H Conductor | 16 | 158 | 42 | East | SO10
133533 | 2016-05-02 | Scheduled Outage | Construction | Carl Donaldson and crew to have transformer X27616 open to upgrade cut-out switch. Customers notified. | None | None | 8 | 48 | 6 | Central | UN04
133534 | 2016-05-02 | Scheduled Outage | Maintenance | Rudy Grisel and crew to have transformer X24762 open to replace a defective cut out switch. Customers notified. | None | None | 5 | 49 | 4 | East | 8F1
133535 | 2016-05-02 | Scheduled Outage | Construction | Transformer #X27615 isolated by crew to replace primary switch | None | None | 8 | 27 | 4 | Central | UN04
133536 | 2016-05-02 | Scheduled Outage | Construction | Dolton Henry and crew to have transformer X30661 open for pole replacement. Customers notified. | None | None | 10 | 228 | 38 | Central | UF05
133537 | 2016-05-02 | Scheduled Outage | Construction | Transformer #X49746 isolated by crew for a pole replacement | None | None | 27 | 150 | 68 | East | SO10
133538 | 2016-05-03 | Scheduled Outage | Construction | Clearance to reconfigure secodary conductors | None | None | 26 | 167 | 72 | East | SO10
133540 | 2016-05-03 | Scheduled Outage | Maintenance | repair a broken insrt | None | None | 14 | 76 | 18 | South | 145F1
133541 | 2016-05-03 | Scheduled Outage | Construction | Jim Yeldon and crew replacing TP6020. Customers notified. | None | None | 14 | 64 | 15 | South | 145F1
133542 | 2016-05-03 | Scheduled Outage | Construction | INSTALL NEW SECONDARY SERVICE | None | None | 21 | 60 | 21 | East | UT06
133543 | 2016-05-03 | Scheduled Outage | Construction | Secondary reconfiguration on the SO10 overhead affecting 25 customers out of Overbrook Sub. | None | None | 25 | 155 | 65 | East | SO10
133544 | 2016-05-03 | Scheduled Outage | Maintenance | Vault Maintenance at VT684 on the 411 out of King Edward Terminal by contractor affecting 1 customer. | None | None | 1 | 126 | 2 | Central | 411
133545 | 2016-05-03 | Scheduled Outage | Maintenance | Vault Maintenance | None | None | 1 | 171 | 3 | East | UA04
133546 | 2016-05-03 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35230 TO INSTALL A NEW POLE | None | None | 2 | 45 | 2 | West | JKGF5
133547 | 2016-05-04 | Scheduled Outage | Maintenance | Transformer 2661B isolated to replace a leaking transformer affecting 13 customers. Bridlewood BRDF6 | None | Padmount (1ph) | 13 | 195 | 42 | West | BRDF6
133548 | 2016-05-04 | Scheduled Outage | Construction | 3 transformers TP10730, TP10731 and TP10732 isolated for elbow and insert replacement affecting 30 customers. Moulton 8F3 | None | None | 30 | 186 | 93 | East | 8F3
133549 | 2016-05-04 | Scheduled Outage | Maintenance | VT52 isolated from HOL Sources on the 504 feeder out of Riverside Terminal for contractor to perform vault maintenance at 1801 Riverside Drive | None | None | 1 | 343 | 6 | Central | 504
133550 | 2016-05-04 | Scheduled Outage | Maintenance | Transformers TP10733 and TP10734 were isolated for elbow and insert replacement and to replace TP10733 affecting25 customers. Moulton 8F3 | None | None | 25 | 130 | 54 | East | 8F3
133552 | 2016-05-05 | Scheduled Outage | Construction | Transformers TP10735 and TP10736 were isolated to allow crew to replace elbows and inserts. | None | None | 32 | 181 | 97 | East | 8F3
133553 | 2016-05-05 | Scheduled Outage | Maintenance | Joe Mckenna to have transformer 03259 open to disconnect a service. Customers notified. | None | None | 4 | 8 | 1 | West | 39F3
133554 | 2016-05-05 | Defective Equipment | Defective Equipment/ Material | The TFXF4 CB A/R/A due to defective transformer X43446 at Cope and Terry Fox. The TFXF3 circuit also A/R | Pole Attachement | Insulator | 2062 | 36 | 1237 | West | TFXF4
133555 | 2016-05-05 | Scheduled Outage | Construction | Transformers TP10739 and TP10740 were isolated for elbow and insert replacement. Moulton DS (8F3) | None | None | 29 | 164 | 79 | East | 8F3
133556 | 2016-05-05 | Scheduled Outage | Construction | Rick Barnett and crew to have transformers X31018, X30664, and X30671 open for pole replacement. Customers notified. | None | None | 21 | 225 | 79 | Central | UF04
133557 | 2016-05-05 | Scheduled Outage | Construction | Shaun Evans (K-Line) to have transformer X31142 open for the transfer of plant. Customers notified. | None | None | 3 | 81 | 4 | Central | SA22
133558 | 2016-05-05 | Scheduled Outage | Maintenance | Mark Brown to have transformer X29977 open to replace connections to a secondary service. Customers notified. | None | None | 5 | 30 | 2 | Central | SB12
133559 | 2016-05-06 | Scheduled Outage | Construction | TP6197 was isolated from all Hydro Ottawa Sources to all crew to replace leaking transformer | None | None | 12 | 83 | 17 | South | 145F4
133560 | 2016-05-06 | Defective Equipment | Defective Equipment/ Material | TB1AL circuit rtipped due to suspected cable fault between TB and VT701. | U/G Cable | PILC | 368 | 55 | 337 | East | TB1AL
133561 | 2016-05-06 | Scheduled Outage | Forced Switching | Switch 881 to EOL was isolated to allow crew to make repairs to defective primary lead to transformer X33275. | None | Fused Cutout | 1 | 70 | 1 | West | BECKF2
133562 | 2016-05-08 | Unknown/Other | Unknown | Overhead section from Hazeldean and Jinkinson Rd interupted when inline sectionalizer tripped after the Station breaker auto reclosed, affecting 3512 customers. Janet King JKGF4 | None | None | 3311 | 14 | 773 | West | JKGF4
133562 | 2016-05-08 | Unknown/Other | Unknown | Overhead section from Hazeldean and Jinkinson Rd interupted when inline sectionalizer tripped after the Station breaker auto reclosed, affecting 3512 customers. Janet King JKGF4 | None | None | 3512 | 25 | 1463 | West | JKGF4
133563 | 2016-05-08 | Adverse Environment | Fire | Pole fire at Carling and Corkstown caused the pole to break off and trip the breaker at the station. The problem area was isolated and part of the load restored until repairs could be completed. Affecting 940 customers. Bayshore 49F6 | Pole | Insulation Failure (Pole Fire) | 224 | 437 | 1631 | South | 49F6
133563 | 2016-05-08 | Adverse Environment | Fire | Pole fire at Carling and Corkstown caused the pole to break off and trip the breaker at the station. The problem area was isolated and part of the load restored until repairs could be completed. Affecting 940 customers. Bayshore 49F6 | Pole | Insulation Failure (Pole Fire) | 940 | 90 | 1410 | South | 49F6
133564 | 2016-05-08 | Scheduled Outage | Maintenance | VT475 at 45 Clarence was isolated for contractor to perform vault maintenance affecting 1 customer on the 415 out of King Edward Terminal | None | None | 1 | 180 | 3 | Central | 415
133565 | 2016-05-08 | Defective Equipment | Moisture Ingress | Defective overhead insulators at VT282-L1 Dips | Pole | Insulation Failure (Pole Fire) | 1349 | 87 | 1956 | Central | 504
133566 | 2016-05-09 | Scheduled Outage | Maintenance | Transformers TP10741 & TP10742 isolated to upgrade elbows & inserts. 28 customers affected. Moulton 8F3. | None | None | 28 | 107 | 50 | East | 8F3
133567 | 2016-05-09 | Scheduled Outage | Construction | A section of o/h line on Basswod Ave isolated to replace poles. 11 customers affected. Janet King 44F3. | None | None | 11 | 381 | 70 | West | 44F3
133568 | 2016-05-09 | Scheduled Outage | Maintenance | Planned outage to allow crews to replace elbows and inserts. | None | None | 19 | 94 | 30 | East | 8F3
133569 | 2016-05-09 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31031 TO TRANSFER HYDRO PLANTE TO NEW POLE | None | None | 30 | 85 | 42 | Central | UX08
133570 | 2016-05-09 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X31581 TO REPLACE SECONDARY CONNECTIONS AT THE TRANSFORMER | None | None | 29 | 60 | 29 | Central | UF07
133572 | 2016-05-10 | Scheduled Outage | Construction | planned outage to replace leaker | None | None | 8 | 99 | 13 | East | 77M2
133573 | 2016-05-10 | Scheduled Outage | Maintenance | planned outage for elbow and insert replacment | None | None | 56 | 301 | 281 | East | 8F3
133575 | 2016-05-10 | Scheduled Outage | Construction | TRANSFER PRIMARY CONDUCTOR | None | None | 8 | 45 | 6 | Central | UN04
133576 | 2016-05-10 | Scheduled Outage | Maintenance | Jordan Foote (K-Line) and crew to have transformer X31030 open for the transfer of plant. Customers notified. | None | None | 1 | 90 | 2 | Central | UX08
133577 | 2016-05-11 | Scheduled Outage | Construction | replace leaker | None | None | 9 | 99 | 15 | East | CYRF3
133578 | 2016-05-11 | Scheduled Outage | Vegetation Management | S 23847 opened to isolate overhead for tree removal by Asplundt TB2JP | None | None | 21 | 223 | 78 | East | TB2JP
133580 | 2016-05-11 | Scheduled Outage | Construction | transfer plant | None | None | 14 | 6 | 1 | Central | SA22
133581 | 2016-05-11 | Scheduled Outage | Maintenance | Shaun Cunningham to have transformer X39693 open to re-arrange services to reconnect 47 Larkspur. | None | None | 6 | 78 | 8 | South | 200F3
133582 | 2016-05-12 | Scheduled Outage | Construction | Overhead section at Avalon and Belena isolated to intall a new pole and transfer plant affecting 24 customers. Russell TB14 | None | None | 24 | 176 | 70 | East | TB14
133583 | 2016-05-12 | Scheduled Outage | Maintenance | 3 transformers isolated on Ridgebrook for elbow and insert replacement affecting 34 customers. Moulton 8F3 | None | None | 31 | 144 | 74 | East | 8F3
133584 | 2016-05-12 | Scheduled Outage | Maintenance | Vault Maintenance at TV5695 by contractor, interruption of 1 customer on the TL5TS out of Lisgar at 235 Kent Street for 2.9 hours. | None | None | 1 | 137 | 2 | Central | TL5TS
133585 | 2016-05-12 | Scheduled Outage | Maintenance | 3 transformers on Ridgebrook were isolated | None | None | 42 | 179 | 125 | East | 8F3
133587 | 2016-05-12 | Scheduled Outage | Construction | Transformer #X31024 isolated by crew to replace poles | None | None | 10 | 170 | 28 | Central | UF04
133588 | 2016-05-12 | Human Element | Improper Equipment/Tool/ Maintenance | A tool tray fell into the live underbuild | None | None | 10304 | 7 | 1202 | South | 22M24
133589 | 2016-05-12 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to transfer plant to newly strung conductor | None | None | 2 | 115 | 4 | South | FAL03
133590 | 2016-05-12 | Scheduled Outage | Construction | Hydro Ottawa crews required the secondaries open at transformer 2529 in order to connect new secondary cables. | None | None | 16 | 14 | 4 | West | BRDF5
133591 | 2016-05-12 | Defective Equipment | Defective Equipment/ Material | Ottawa Fire reports smoke coming out of K728 @ 1640 Kilborn Ave. 24/7 reports defective insulator caused transformer fuse to blow. | U/G Transformer | Kiosk (1ph) | 35 | 70 | 41 | East | AJ06
133593 | 2016-05-13 | Scheduled Outage | Vegetation Management | Overhead section on Analdea was isolated to allow for tree removal affecting 21 customers. Lietrim 249F1 | None | None | 21 | 112 | 39 | East | LTM01
133594 | 2016-05-13 | Scheduled Outage | Maintenance | VT871 isolated from Hydro Ottawa Sources for contractor to perform vault maintenance on the TO3AC out of Overbrook at 525 Cote for 2.2 hours | None | None | 1 | 135 | 2 | East | TO3AC
133595 | 2016-05-14 | Adverse Weather | Extreme Wind | POSSIBLE PHASE TO PHASE CONTACT THAT CAUSED BOTH RED AND WHITE PHASE FUSES TO OPEN. | O/H Conductor | Unknown \ Other | 91 | 87 | 132 | Central | SB06
133596 | 2016-05-14 | Scheduled Outage | Construction | Transformer TP7736 was isoalted to allow crew to set and frame pole on Maple Grove and Huntmar. | None | None | 6 | 580 | 58 | West | BRDF3
133598 | 2016-05-15 | Tree Contacts | Falling Tree | Downed primary F due to fallen tree at 4120 Riverside caused the RX2001 A/R and caused the G806W and S12839W to blow. | O/H Conductor | O/H Conductor | 22 | 402 | 147 | East | 7F2
133599 | 2016-05-15 | Defective Equipment | Mechanical Failure | secondary bus down in rear of 186 latchford. | O/H Conductor | O/H Conductor | 6 | 90 | 9 | Central | UL02
133600 | 2016-05-16 | Scheduled Outage | Maintenance | Transformers TP10769, TP10770, TP10771 and TP10772 were isolated to allow crew to replace elbows and inserts. Moulton (8F3) | None | None | 46 | 241 | 185 | East | 8F3
133601 | 2016-05-16 | Scheduled Outage | Maintenance | Transformer X33038 was isoalted to allow crew to perfrom secondary work. Rideau Hieghts (180F4) | None | None | 7 | 318 | 37 | South | 180F4
133602 | 2016-05-16 | Scheduled Outage | Maintenance | Brent Duncan to have transformer X30089 open to drop services. Customers notified. | None | None | 12 | 38 | 8 | Central | SB11
133603 | 2016-05-16 | Scheduled Outage | Construction | Transformer #65C3C-0168 isolated by crew to install new cable on pole | None | None | 5 | 185 | 15 | East | UQ03
133604 | 2016-05-16 | Scheduled Outage | Forced Switching | S1627 was opened to allow crew to replace defective switch. | None | None | 4 | 10 | 1 | South | 180F2
133605 | 2016-05-17 | Scheduled Outage | Construction | V584 isolated to replace primary cables to the vault. 1 customers affected. Gladestone (UX08) | None | PILC | 1 | 425 | 7 | Central | UX08
133606 | 2016-05-17 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER 550-4B-0005 TO DISCONNECT TWO SECONDARY SERVICES FOR TREE REMOVEL | None | None | 11 | 45 | 8 | Central | SB05
133607 | 2016-05-17 | Scheduled Outage | Maintenance | ISOLATED TRANSFORNER X33580 TO REPLACE CONNECTION ON THE STREELIGHT FEED | None | None | 7 | 15 | 2 | Central | AK03
133608 | 2016-05-17 | Scheduled Outage | Construction | RHNF1 overhead section between TMEP35 and TMEP50 on Shea Rd. isolated to install new poles. 4 customers affected. Richmond North (RHNF1) | None | Pole | 4 | 263 | 18 | West | RHNF1
133609 | 2016-05-17 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X34021 TO INSTALL NEW POLE AND TRANSFER HYDRO PLANT | None | None | 8 | 253 | 34 | Central | UL04
133610 | 2016-05-17 | Scheduled Outage | Maintenance | TP10760, TP10768, TP10774, TP10775 isolated for elbow and insert replacement. | None | None | 58 | 261 | 252 | East | 8F3
133611 | 2016-05-17 | Scheduled Outage | Forced Switching | FORCED OUTAGE FOR FIRE DEPT DUE TO HOUSE FIRE AT 306 BRITANNIA RD | None | None | 12 | 70 | 14 | Central | TD14
133612 | 2016-05-17 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to change a leaking tranformer, install a new base & new grounding. | None | Padmount (1ph) | 10 | 394 | 66 | South | 140F3
133613 | 2016-05-18 | Scheduled Outage | Vegetation Management | UC03 from TEMP60 to EOL on Kerr Ave isolated for tree removal. 100 customers affected. Clyde (UC03) | None | None | 100 | 380 | 633 | Central | UC03
133614 | 2016-05-18 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32571 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 15 | 37 | 9 | Central | TD06
133615 | 2016-05-18 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X29712 TO REPLACE STREETLIGHT CONNECTION | None | None | 8 | 18 | 2 | East | AE07
133616 | 2016-05-18 | Scheduled Outage | Construction | Transformer #X31158 isolated by crew to transfer plant | None | None | 29 | 173 | 84 | Central | UF07
133617 | 2016-05-18 | Scheduled Outage | Construction | Transformer #X45116 isolated by crew to run a new service | None | None | 23 | 70 | 27 | Central | TW17
133618 | 2016-05-18 | Scheduled Outage | Maintenance | Transformers TP10831, TP6081 and TP10832 isolated by Sproule for insert elbow replacement. | None | None | 26 | 173 | 75 | East | CYRF1
133619 | 2016-05-18 | Scheduled Outage | Maintenance | TP10828, TP10829, TP10830 isolated by Sproule for insert elbow replacement. | None | None | 36 | 153 | 92 | East | CYRF1
133620 | 2016-05-19 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 36 | 308 | 185 | Central | TW22
133621 | 2016-05-19 | Scheduled Outage | Maintenance | planned outage to replace leaker | None | None | 11 | 104 | 19 | East | 77M6
133622 | 2016-05-19 | Scheduled Outage | Maintenance | 4 transformers on Beaverpond were isolated to allow crew to replace elbows and inserts. | None | None | 29 | 205 | 99 | East | CYRF1
133623 | 2016-05-19 | Scheduled Outage | Construction | Transformer #TE0039 isolated by crew to install new service | None | None | 15 | 40 | 10 | South | 190F5
133626 | 2016-05-19 | Scheduled Outage | Construction | Transformer #X34237 isolated by crew to drop a service | None | None | 3 | 15 | 1 | Central | UL03
133627 | 2016-05-19 | Scheduled Outage | Maintenance | elbow and insert replacement | None | None | 23 | 187 | 72 | East | CYRF1
133628 | 2016-05-19 | Loss Of Supply | Transmission Inadvertent | Hydro One relayting issues. | None | None | 1 | 6 | 0 | Central | 4304
133628 | 2016-05-19 | Loss Of Supply | Transmission Inadvertent | Hydro One relayting issues. | None | None | 37 | 6 | 4 | Central | TH1SH
133628 | 2016-05-19 | Loss Of Supply | Transmission Inadvertent | Hydro One relayting issues. | None | None | 50 | 6 | 5 | Central | 4301
133628 | 2016-05-19 | Loss Of Supply | Transmission Inadvertent | Hydro One relayting issues. | None | None | 1039 | 6 | 104 | Central | TH1UL
133628 | 2016-05-19 | Loss Of Supply | Transmission Inadvertent | Hydro One relayting issues. | None | None | 1379 | 6 | 138 | Central | TH2UJ
133628 | 2016-05-19 | Loss Of Supply | Transmission Inadvertent | Hydro One relayting issues. | None | None | 1526 | 6 | 153 | Central | TH06
133630 | 2016-05-20 | Scheduled Outage | Vegetation Management | Tree removal. | None | None | 47 | 230 | 180 | Central | TW22
133631 | 2016-05-20 | Scheduled Outage | Vegetation Management | Tree removal. | None | None | 41 | 312 | 213 | Central | TW22
133632 | 2016-05-20 | Scheduled Outage | Construction | planned outage to replace a leaker. | None | None | 1 | 503 | 8 | East | LMBF7
133633 | 2016-05-20 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X30922 opened up due to squirrels nest | O/H Switchgear | Fused Cutout | 11 | 119 | 22 | Central | SK16
133634 | 2016-05-20 | Defective Equipment | Electrical Failure | defective transformer | O/H Transformer | O/H Transformer (1ph) | 1 | 228 | 4 | West | 43F2
133636 | 2016-05-20 | Loss Of Supply | Transmission Inadvertent | Hydro one loss of H9A. They don’t know the cause at this time. | None | None | 977 | 6 | 98 | East | 77M2
133637 | 2016-05-20 | Foreign Interference | Vehicle | ISOLATED TRANSFORMER X31131 TO RECONNECT TWO TRIPLEX SERVICES | None | None | 12 | 16 | 3 | Central | UF06
133638 | 2016-05-20 | Tree Contacts | Broken Branch | A tree branch fell onto X29111 causing the transformer fuse to blow and S12168 W fuse to blow. | O/H Switchgear | Fused Cutout | 14 | 24 | 6 | East | TB15
133638 | 2016-05-20 | Tree Contacts | Broken Branch | A tree branch fell onto X29111 causing the transformer fuse to blow and S12168 W fuse to blow. | O/H Switchgear | Fused Cutout | 32 | 93 | 50 | East | TB15
133640 | 2016-05-20 | Defective Equipment | Electrical Failure | Transformer X17472 opened due to defective transformer and switch. Oncall crew replced transformer and switch | O/H Transformer | O/H Transformer (3ph) | 5 | 647 | 54 | East | 77M6
133641 | 2016-05-21 | Foreign Interference | Wildlife (Bird/Animal) | Field Ops report a squirrel carcas found at S21970 | None | None | 26 | 47 | 20 | South | 160F3
133642 | 2016-05-21 | Defective Equipment | Mechanical Failure | A Suspected cable fault between VT496-2 & VT220 | U/G Cable | Unknown \ Other | 25 | 83 | 35 | Central | TR1UX
133642 | 2016-05-21 | Defective Equipment | Mechanical Failure | A Suspected cable fault between VT496-2 & VT220 | U/G Cable | Unknown \ Other | 1410 | 36 | 846 | Central | TR1UX
133643 | 2016-05-21 | Foreign Interference | Wildlife (Bird/Animal) | Blown fuse S7090 due to dead crow. New fuse installed and closed | O/H Switchgear | Fused Cutout | 97 | 48 | 78 | East | 7F1
133645 | 2016-05-22 | Scheduled Outage | Forced Switching | To allow Hydro Ottawa line crews to repair a defective 44kV switch, S25382 | None | None | 2 | 168 | 6 | West | A9M4
133646 | 2016-05-22 | Unknown/Other | Unknown | 2700 customers out. Police and fire called all cclear and breaker closed. Circuit to be patrol latter today. | None | None | 2700 | 22 | 990 | South | LGFF1
133647 | 2016-05-23 | Foreign Interference | Wildlife (Bird/Animal) | Replaced blown fuse feeding transformer X35637 (Bird contact) | O/H Transformer | O/H Transformer (1ph) | 16 | 97 | 26 | Central | TD12
133648 | 2016-05-23 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEDING TRANSFORMER X35533 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 19 | 116 | 37 | Central | TD05
133649 | 2016-05-23 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused transformer fuse at KT212 to blow which also blew red phase of S21789 affecting 118 customers for 2 hours and 44 minutes. ELW07 (Ellwood) | None | None | 11 | 5 | 1 | East | ELW07
133649 | 2016-05-23 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused transformer fuse at KT212 to blow which also blew red phase of S21789 affecting 118 customers for 2 hours and 44 minutes. ELW07 (Ellwood) | None | None | 21 | 15 | 5 | East | ELW07
133649 | 2016-05-23 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused transformer fuse at KT212 to blow which also blew red phase of S21789 affecting 118 customers for 2 hours and 44 minutes. ELW07 (Ellwood) | None | None | 31 | 28 | 14 | East | ELW07
133649 | 2016-05-23 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused transformer fuse at KT212 to blow which also blew red phase of S21789 affecting 118 customers for 2 hours and 44 minutes. ELW07 (Ellwood) | None | None | 42 | 36 | 25 | East | ELW07
133649 | 2016-05-23 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused transformer fuse at KT212 to blow which also blew red phase of S21789 affecting 118 customers for 2 hours and 44 minutes. ELW07 (Ellwood) | None | None | 118 | 75 | 148 | East | ELW07
133650 | 2016-05-23 | Scheduled Outage | Maintenance | 3 phase fused dip to TP3379 opened to replace defective switches affecting 1 customer. Riverdale SR03 | None | Fused Cutout | 1 | 76 | 1 | Central | SR03
133651 | 2016-05-23 | Defective Equipment | Electrical Failure | Termination failed at 3800 Leitrim Road. | U/G Cable Attachement | Termination \ Stress Cone | 1437 | 45 | 1078 | East | LTM04
133652 | 2016-05-24 | Foreign Interference | Wildlife (Bird/Animal) | Not yet known. | Pole Attachement | Insulator | 2 | 42 | 1 | Central | 302
133653 | 2016-05-24 | Scheduled Outage | Vegetation Management | To allow tree crews to trim trees. | None | O/H Conductor | 50 | 360 | 300 | East | UZ12
133654 | 2016-05-24 | Scheduled Outage | Maintenance | To allow contractor to clear and service customer owned vault @ VT150 | None | Breaker \ Relay | 1 | 283 | 5 | Central | 5404
133655 | 2016-05-24 | Foreign Interference | Wildlife (Bird/Animal) | REFUSED SWITCH FEEDING TRANSFORMER X48569 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 19 | 78 | 25 | Central | TW18
133656 | 2016-05-24 | Scheduled Outage | Maintenance | At 9:45am V672 was isolated to allow contractor to perform maintenance. 1 customer affected. Queens (UQ03) | None | None | 1 | 147 | 2 | East | UQ03
133657 | 2016-05-24 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMER X37961, X30762 AND X30763 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 67 | 285 | 318 | Central | AB06
133659 | 2016-05-24 | Scheduled Outage | Maintenance | Yannick Fortin and crew to have transformer X34181 open to replace the cut-out switch. Customers notified. | None | None | 6 | 47 | 5 | Central | UL14
133661 | 2016-05-24 | Scheduled Outage | Construction | At 9:00am switch 5582R was open to allow crew to repair a broken pole. 1 customer affected. Marchwood (MWDF3) | None | None | 1 | 375 | 6 | West | MWDF3
133662 | 2016-05-24 | Foreign Interference | Vehicle | Car hit a hydro pole on Robertson Rd. tripping the 200F1 circuit affecting 695 customers. Stafford Rd (200F1) | Pole | Pole | 10 | 300 | 50 | South | 200F1
133663 | 2016-05-24 | Scheduled Outage | Construction | Transformer #X21231 isolated by crew to replace pole and transformer | None | None | 17 | 380 | 108 | East | V11F2
133667 | 2016-05-25 | Defective Equipment | Electrical Failure | SUSPECTED CABLE FAULT | U/G Cable | PILC | 1 | 58 | 1 | Central | 501
133668 | 2016-05-25 | Defective Equipment | Electrical Failure | cable fault | U/G Cable | Unknown \ Other | 372 | 20 | 124 | East | ELW04
133668 | 2016-05-25 | Defective Equipment | Electrical Failure | cable fault | U/G Cable | Unknown \ Other | 611 | 45 | 458 | East | ELW04
133668 | 2016-05-25 | Defective Equipment | Electrical Failure | cable fault | U/G Cable | Unknown \ Other | 1016 | 44 | 745 | East | ELW04
133669 | 2016-05-25 | Scheduled Outage | Vegetation Management | Tree trimming in the rear of 625 Southmore. | None | O/H Conductor | 24 | 155 | 62 | East | UZ05
133670 | 2016-05-25 | Scheduled Outage | Maintenance | TP10808, TP10813 & TP10817 isolated for elbow & insert upgrade.Cyrville CYRF1. | None | None | 42 | 157 | 110 | East | CYRF1
133671 | 2016-05-25 | Scheduled Outage | Maintenance | To clean the vault and sevice breaker in customer owned equipment | None | Breaker \ Relay | 1 | 199 | 3 | Central | 5404
133672 | 2016-05-25 | Defective Equipment | Imminent Equipment Failure Detected | At 10:04am crews isolated TP7588 to replace leaking transformer. 9 customers affected. Bilberry (77M6) | None | None | 9 | 116 | 17 | East | 77M6
133673 | 2016-05-25 | Scheduled Outage | Maintenance | At 12:40am crews have isolated 3 transformers to replace elbow and insert. Cyrville (CYRF1) | None | None | 42 | 151 | 106 | East | CYRF1
133674 | 2016-05-25 | Foreign Interference | Foreign Objects | Suspected contractor bumped pole blew fuse at S29352. | O/H Switchgear | Fused Cutout | 14 | 92 | 21 | South | EPWF3
133675 | 2016-05-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | crews found S1059R blown. They patrolled and trimmed trees before closing fuse. 64 customers affected. Stafford (200F3) | O/H Conductor | O/H Conductor | 64 | 69 | 74 | South | 200F3
133676 | 2016-05-25 | Unknown/Other | Unknown | At 2:42pm customers reported an outage on Spring Garden. Crews patrolled but found no cause. 14 customers affected. Epworth (EPWF3) | None | None | 14 | 95 | 22 | South | EPWF3
133678 | 2016-05-26 | Scheduled Outage | Vegetation Management | To Allow Hydro Ottawa forestry to trim trees in the area | None | None | 60 | 330 | 330 | East | UZ12
133680 | 2016-05-26 | Scheduled Outage | Construction | ISOALTED TRANSFORMER X37961 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 41 | 119 | 81 | Central | AB06
133681 | 2016-05-26 | Scheduled Outage | Construction | Rick Barnett to have three transformers open (X30762, X30763, X30764) to transfer Hydro plant. Customers notified. | None | None | 38 | 290 | 184 | Central | AB06
133682 | 2016-05-26 | Human Element | Switching Error | Non-system controlled switch at transformer pad MT1739 was inadvertently left open when restoring a transformer loop on the ELW04 line out of Ellwood affecting 65 cusrtomers for 10 minutes. | None | None | 65 | 10 | 11 | East | ELW04
133683 | 2016-05-27 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X48505 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 13 | 41 | 9 | Central | TW18
133684 | 2016-05-27 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X29872 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 10 | 129 | 22 | Central | TR09
133685 | 2016-05-27 | Scheduled Outage | Maintenance | Old leaking transformer replace with new transformer. | None | Padmount (1ph) | 11 | 101 | 19 | West | TFXF1
133686 | 2016-05-27 | Scheduled Outage | Maintenance | Ool leaking transformer replaced with new. | None | Padmount (1ph) | 7 | 106 | 12 | East | 77M2
133687 | 2016-05-27 | Scheduled Outage | Maintenance | ISOLATED AND REPLACED PAD MOUNT TRANSFORMER TP7916 (LEAKING OIL) | None | Padmount (1ph) | 7 | 123 | 14 | East | 77M2
133688 | 2016-05-27 | Foreign Interference | Vehicle | REPLACED BLOWN FUSE FEEDING TRANSFORMER X41478 (OPEN WIRE BUSS SLAPPED TOGETHER WHEN CONTRACTOR HIT THE BELL WIRE) | O/H Transformer | O/H Transformer (1ph) | 4 | 72 | 5 | South | EPWF1
133689 | 2016-05-27 | Scheduled Outage | Maintenance | Scott Barkley to have transformer X32413 open to transfer hydro plant. Customers notified. | None | None | 16 | 210 | 56 | Central | TD01
133690 | 2016-05-27 | Tree Contacts | Broken Branch | R and B fuses at G739 opened due to fallen tree limb on overhead conductor. W phase opened to create safe work area to remove limb. 539 customers affected. Uplands (4801F8) | O/H Conductor | O/H Conductor | 381 | 90 | 572 | East | 4801F8
133690 | 2016-05-27 | Tree Contacts | Broken Branch | R and B fuses at G739 opened due to fallen tree limb on overhead conductor. W phase opened to create safe work area to remove limb. 539 customers affected. Uplands (4801F8) | O/H Conductor | O/H Conductor | 539 | 13 | 117 | East | 4801F8
133691 | 2016-05-27 | Scheduled Outage | Vegetation Management | S26512 opened to allow for tree removal at YMCA camp Kanata. | None | None | 2 | 384 | 13 | West | 624F6
133692 | 2016-05-28 | Scheduled Outage | Maintenance | Customer vault maintenace | None | Breaker \ Relay | 1 | 207 | 3 | Central | TL4TS
133693 | 2016-05-28 | Scheduled Outage | Vegetation Management | Transformer #X31941 isolated by crew to trim vines | None | None | 25 | 16 | 7 | Central | TD14
133697 | 2016-05-29 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact | Pole Attachement | Unknown \ Other | 178 | 65 | 193 | South | 49F4
133698 | 2016-05-29 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact on the B2 bus, broke insulators and caused a power fuse to blow on the 84T2 at Manordale. | Station Equipment | Unknown \ Other | 397 | 50 | 331 | South | 84F4
133698 | 2016-05-29 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact on the B2 bus, broke insulators and caused a power fuse to blow on the 84T2 at Manordale. | Station Equipment | Unknown \ Other | 443 | 50 | 369 | South | 84F6
133698 | 2016-05-29 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact on the B2 bus, broke insulators and caused a power fuse to blow on the 84T2 at Manordale. | Station Equipment | Unknown \ Other | 939 | 36 | 563 | South | 84F5
133699 | 2016-05-29 | Scheduled Outage | Maintenance | change leaking transformer TP4264 | None | Padmount (3ph) | 1 | 224 | 4 | West | TFXF2
133702 | 2016-05-29 | Defective Equipment | Defective Equipment/ Material | Transformer #X33440 opened up due to broken transformer switch | O/H Switchgear | Fused Cutout | 17 | 45 | 13 | Central | UC06
133703 | 2016-05-29 | Scheduled Outage | Maintenance | planned outage for elbow and insert replacment. | None | None | 1 | 123 | 2 | East | CYRF4
133704 | 2016-05-29 | Scheduled Outage | Maintenance | At 9:02pm crews isolated TP10862 and TP10863 for elbow and insert replacement. 15 customers affected. Cyrville (CYRF1) | None | None | 15 | 138 | 34 | East | CYRF1
133705 | 2016-05-30 | Scheduled Outage | Construction | To change leaking transformer. | None | Padmount (3ph) | 2 | 506 | 17 | East | AN06
133706 | 2016-05-30 | Scheduled Outage | Forced Switching | Kevin Mckenna to have transformer X31426 open to replace service. Customers notified. | None | None | 7 | 40 | 5 | Central | AM05
133707 | 2016-05-30 | Scheduled Outage | Construction | Jeff Magee to have transformers X27785, and X27783 open for installation of new poles. Customers notified. | None | None | 12 | 148 | 30 | East | UQ03
133708 | 2016-05-30 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X36091 opened up due to tree contact | O/H Switchgear | Fused Cutout | 16 | 114 | 30 | Central | TD05
133709 | 2016-05-30 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 43 | 247 | 177 | East | 8F1
133710 | 2016-05-30 | Foreign Interference | Dig-In | s18266 feeding P123 was siolated due to a primary cable dig in | U/G Cable | Unknown \ Other | 1 | 207 | 3 | East | UZ11
133711 | 2016-05-30 | Foreign Interference | Agricultural Equipment | ISOLATED TRANSFORMER X23506 TO REMOVE TREE ON SECONDARY SERVICE | O/H Transformer | O/H Transformer (1ph) | 12 | 199 | 40 | East | SO03
133712 | 2016-05-30 | Defective Equipment | Electrical Failure | REPLACED SWITCH AND BLOWN ARRESTER AT TRANSFORMER X07433 | O/H Transformer | O/H Transformer (1ph) | 1 | 156 | 3 | West | 624F6
133713 | 2016-05-30 | Scheduled Outage | Maintenance | 27KV insert elbow replacement preformed by Sproule after hours for a school. | None | None | 1 | 180 | 3 | East | CYRF1
133714 | 2016-05-31 | Scheduled Outage | Vegetation Management | S24150 to Eol was isolated to allow tree trimming crew to remove large tree limbs | None | None | 12 | 108 | 22 | Central | TW22
133715 | 2016-05-31 | Scheduled Outage | Maintenance | Transformer K676 was isolated to allow crew to repalce kiosk to a padmount. | None | None | 1 | 281 | 5 | East | AJ06
133717 | 2016-05-31 | Scheduled Outage | Construction | Jordan Foote from K-Line to have transformer X36927 open to transfer plant. Customers notified. | None | None | 12 | 85 | 17 | West | 44F1
133718 | 2016-05-31 | Scheduled Outage | Construction | Transformer P257 was isolated to allow crew to transfer plant and install new switches. | None | None | 11 | 358 | 66 | Central | UF04
133720 | 2016-06-01 | Scheduled Outage | Vegetation Management | S21976 to EOL was isolated to allow tree trimming crew to trim tree at rear of 931 Kingsmere | None | None | 87 | 347 | 503 | Central | TW22
133723 | 2016-06-01 | Scheduled Outage | Maintenance | S24717 to Eol was isolated to allow crew to re insulate pole | None | None | 1 | 61 | 1 | West | RHNF1
133724 | 2016-06-01 | Scheduled Outage | Construction | Transformer 8500 @ 3 WHITE CEDAR ST STITTSVILLE was isolated to allow the contractor to transfer cables to new pole | None | Unknown \ Other | 7 | 132 | 15 | West | 44F3
133725 | 2016-06-01 | Foreign Interference | Vehicle | Vehicle accident | U/G Transformer | Padmount (1ph) | 10 | 244 | 41 | East | 77M5
133725 | 2016-06-01 | Foreign Interference | Vehicle | Vehicle accident | U/G Transformer | Padmount (1ph) | 95 | 87 | 138 | East | 77M5
133726 | 2016-06-01 | Defective Equipment | Electrical Failure | Isolated transformer x30211 to jumper secondary buss to restore power to customers fed from defective transformer 55D3A-0257 | O/H Transformer | O/H Transformer (1ph) | 10 | 43 | 7 | Central | AD03
133727 | 2016-06-02 | Scheduled Outage | Construction | Elbow and insert replacement | None | None | 35 | 212 | 124 | East | CYRF1
133729 | 2016-06-02 | Scheduled Outage | Maintenance | TE760 isolated to replace leaking transformer. 12 customers affected. Bilberry 77M1. | None | Padmount (1ph) | 12 | 94 | 19 | East | 77M1
133731 | 2016-06-02 | Scheduled Outage | Maintenance | Gary Colburn and crew to have transformer X40026 open to transfer equipment. Customers notified. | None | None | 1 | 120 | 2 | South | 145F3
133732 | 2016-06-02 | Scheduled Outage | Construction | At 9:53am section of FAL03 from S749 to EOL was isolated to allow crew to re-conductor overhead for voltage conversion. 1 customer affected. Fallowfield (FAL03) | None | None | 1 | 93 | 2 | South | FAL03
133733 | 2016-06-02 | Scheduled Outage | Construction | Gary Coburn to have transformer X43701 open to replace transformer and hardware on pole. Customers notified. | None | None | 1 | 76 | 1 | South | FAL01
133734 | 2016-06-02 | Tree Contacts | Falling Tree | S14621 was opened to allow crews to remove a broken tree from overhead circuit. | O/H Conductor | O/H Conductor | 98 | 129 | 211 | Central | TW22
133735 | 2016-06-02 | Tree Contacts | Tree Growth/ Untrimmed Tree | tree contact cause xfmr fuse X39577 to blow | O/H Transformer | O/H Transformer (1ph) | 2 | 150 | 5 | West | 624F6
133737 | 2016-06-03 | Scheduled Outage | Vegetation Management | Tree trimmig in the rear at 1137 Checkers. | None | O/H Conductor | 37 | 211 | 130 | Central | TW18
133738 | 2016-06-03 | Scheduled Outage | Maintenance | To replace leaking transformer # MT1535. | None | Kiosk (1ph) | 15 | 142 | 36 | Central | 307
133739 | 2016-06-03 | Scheduled Outage | Maintenance | Warren Kelly to have transformer X32496 open to replace O/H open secondary bus with triplex. Customers notified. | None | None | 3 | 87 | 4 | Central | TD06
133743 | 2016-06-04 | Defective Equipment | Mechanical Failure | Red phase cabel fault between TP10849 and S11410R | U/G Cable | Unknown \ Other | 79 | 88 | 116 | East | 8F3
133744 | 2016-06-05 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree limbs sagged into the UC06 circuit and caused to phases to burn down | O/H Conductor | O/H Conductor | 54 | 44 | 40 | Central | UC06
133744 | 2016-06-05 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree limbs sagged into the UC06 circuit and caused to phases to burn down | O/H Conductor | O/H Conductor | 93 | 261 | 405 | Central | UC06
133744 | 2016-06-05 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree limbs sagged into the UC06 circuit and caused to phases to burn down | O/H Conductor | O/H Conductor | 122 | 17 | 35 | Central | UC06
133745 | 2016-06-05 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | PILC | 52 | 28 | 24 | East | 6F10
133745 | 2016-06-05 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | PILC | 105 | 134 | 234 | East | 6F10
133745 | 2016-06-05 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | PILC | 1195 | 51 | 1016 | East | 6F10
133746 | 2016-06-05 | Tree Contacts | Tree Growth/ Untrimmed Tree | Fuse at X28190 at 2364 Orlando opened due to tree contact. 8 customers affected. Russell (TB2JP) | O/H Transformer | O/H Transformer (1ph) | 8 | 45 | 6 | East | TB2JP
133747 | 2016-06-05 | Foreign Interference | Wildlife (Bird/Animal) | Fuse at transformer X32533 opened due to animal contact. 10 customers affected. Lincoln Heights (TD06) | O/H Transformer | O/H Transformer (1ph) | 10 | 100 | 17 | Central | TD06
133748 | 2016-06-05 | Scheduled Outage | Maintenance | TP10884 t 1900 Cyrville isolated for elbow and insert replacment. 1 customer affected. Cyrville (CYRF4) | None | None | 1 | 120 | 2 | East | CYRF4
133749 | 2016-06-05 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X48523 fuse opened due to animal contact. Woodroffe (TW18) | O/H Switchgear | Fused Cutout | 6 | 111 | 11 | Central | TW18
133751 | 2016-06-06 | Defective Equipment | Electrical Failure | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27515 CAUSE UNKNOWN | O/H Transformer | O/H Transformer (1ph) | 12 | 123 | 25 | East | ELW06
133753 | 2016-06-06 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X28212 TO RE-ARRANGE HYDRO PLANT | None | None | 20 | 151 | 50 | Central | 505
133754 | 2016-06-06 | Defective Equipment | Defective Equipment/ Material | Defective white phase lightning arrestor. | Pole Attachement | Arrester | 797 | 45 | 598 | East | ELW14
133755 | 2016-06-06 | Scheduled Outage | Construction | Replace pole | None | None | 11 | 326 | 60 | Central | UL04
133756 | 2016-06-06 | Scheduled Outage | Construction | S880 to EOL isolated to allow transfer of plant to new poles and conductor. | None | None | 4 | 397 | 26 | South | FAL03
133757 | 2016-06-07 | Scheduled Outage | Construction | Install new poles | None | None | 7 | 210 | 24 | East | UQ08
133758 | 2016-06-07 | Scheduled Outage | Construction | Transfer plant to new poles. | None | None | 12 | 300 | 60 | Central | TW22
133760 | 2016-06-07 | Scheduled Outage | Construction | DISCONNECT SERVICE | None | None | 7 | 16 | 2 | West | BRDF5
133761 | 2016-06-07 | Scheduled Outage | Vegetation Management | TREE REMOVAL | None | None | 6 | 90 | 9 | Central | TD05
133762 | 2016-06-07 | Scheduled Outage | Construction | DISONNECT SERVICE | None | None | 7 | 40 | 5 | Central | UC03
133763 | 2016-06-07 | Scheduled Outage | Maintenance | Leaking Transformer 1731 was replace on the BRDF3 out of Bridlewood affecting 53 customers for 2 hours | None | None | 53 | 126 | 111 | West | BRDF3
133766 | 2016-06-07 | Scheduled Outage | Maintenance | TE1215 was isolated by HOL crews to change leaking transformer Padmount on the 4801F8 out of Uplands affecting 13 customers for 7.5 hours. | None | None | 13 | 424 | 92 | East | 4801F8
133767 | 2016-06-07 | Scheduled Outage | Construction | At 9:34am crews isolated FAL03 from S749 to end of line for construction work. 1 customer affected. Fallowfield (FAL03). | None | None | 1 | 121 | 2 | South | FAL03
133769 | 2016-06-08 | Scheduled Outage | Maintenance | At 9:10am TP8084 was isolated to replace leaking transformer. 7 customers affected. Bilberry (77M6) | None | None | 7 | 107 | 12 | East | 77M6
133770 | 2016-06-08 | Scheduled Outage | Vegetation Management | Adrian Henry to have transformer X39895 open for tree trimming. Customers Notified. | None | None | 2 | 191 | 6 | West | 43F2
133772 | 2016-06-08 | Defective Equipment | Electrical Failure | At 10:25am SCADA indicated that the TH05 breaker tripped. Crews isolated faulted cable and restored load. 650 customers affected. Hinchey (TH05) | U/G Cable | PILC | 112 | 24 | 45 | Central | TH3SH
133772 | 2016-06-08 | Defective Equipment | Electrical Failure | At 10:25am SCADA indicated that the TH05 breaker tripped. Crews isolated faulted cable and restored load. 650 customers affected. Hinchey (TH05) | U/G Cable | PILC | 650 | 63 | 682 | Central | TH3SH
133773 | 2016-06-08 | Adverse Environment | Unstable Earth | TK20 (TK6TS) tripped due to sink hole | U/G Cable | PILC | 2 | 751 | 25 | Central | TK6TS
133773 | 2016-06-08 | Adverse Environment | Unstable Earth | TK20 (TK6TS) tripped due to sink hole | U/G Cable | PILC | 7 | 655 | 76 | Central | TK6TS
133773 | 2016-06-08 | Adverse Environment | Unstable Earth | TK20 (TK6TS) tripped due to sink hole | U/G Cable | PILC | 650 | 94 | 1018 | Central | TK6TS
133773 | 2016-06-08 | Adverse Environment | Unstable Earth | TK20 (TK6TS) tripped due to sink hole | U/G Cable | PILC | 655 | 15 | 164 | Central | TK6TS
133775 | 2016-06-08 | Scheduled Outage | Vegetation Management | Customer power was interrupted at Glencairn on the SR09 out of Riverdale for crews to perform tree trimming from S29864 to End Of Line for 166 minutes. | None | None | 85 | 166 | 235 | Central | SR09
133777 | 2016-06-09 | Scheduled Outage | Vegetation Management | Switch S21316 to end of line was isoalted to allow crew to perfrom tree trimming at rear of 20 Belgrave. | None | None | 19 | 74 | 23 | Central | SR02
133779 | 2016-06-09 | Scheduled Outage | Maintenance | Transformer bus at TV9689 was isolated to allow crew to repair transformer. Slater (616) | None | None | 1 | 98 | 2 | Central | 616
133780 | 2016-06-09 | Scheduled Outage | Construction | SECONDARY SERVICE UPGRADE X28170 | None | None | 9 | 30 | 4 | Central | 505
133781 | 2016-06-09 | Scheduled Outage | Construction | SECONDARY SERVICE UPGRADE | None | None | 9 | 45 | 7 | Central | 505
133782 | 2016-06-09 | Defective Equipment | Mechanical Failure | S1223 isolated due to switch burning up. Switch replaced and all load restored. | O/H Switchgear | Fused Cutout | 2 | 32 | 1 | South | 200F2
133785 | 2016-06-09 | Scheduled Outage | Maintenance | Transformer X32578 at 567 Redwood was isolated to change a defective service. 8 customers affected. Linclon Hieghts (TD01) | Secondary \ Service | O/H Service | 8 | 38 | 5 | Central | TD01
133786 | 2016-06-10 | Scheduled Outage | Vegetation Management | S12146 to EOL was isolated to allow crew to perfrom tree trimming at rear of 187 Breezehill. | None | None | 23 | 97 | 37 | Central | UJ04
133787 | 2016-06-10 | Scheduled Outage | Construction | Transformer MT1555 at 51 grenwicj has been isolated to allow crew to replace leaking mini pad | None | None | 10 | 218 | 36 | Central | 307
133788 | 2016-06-10 | Scheduled Outage | Maintenance | Transformer X39746 isolated for transformer replacement. | None | O/H Transformer (1ph) | 1 | 160 | 3 | East | LMBF7
133789 | 2016-06-10 | Scheduled Outage | Maintenance | Transformer #X35455 isolated by crew to replace connections at the stack and pole | None | None | 10 | 60 | 10 | Central | TW22
133790 | 2016-06-11 | Scheduled Outage | Maintenance | Secondary maintenance and building main breaker uprade by contractor affecting 1 customer on the MWDF4 out of Marchwood | None | None | 1 | 817 | 14 | West | MWDF4
133791 | 2016-06-11 | Scheduled Outage | Maintenance | To allow contractor to replace secondary feeder. | None | Customer-Owned | 1 | 499 | 8 | Central | 618
133792 | 2016-06-11 | Tree Contacts | Falling Tree | Ottawa Fire reports sparking wires at this location. Field Operators found guy wire wrapped into open bus at this location. 24/7 reports guy wire is fine and is shielded and not the problem. Circuit closed via scada and holding. Later found tree contact & | O/H Conductor | O/H Conductor | 467 | 54 | 420 | East | AP06
133793 | 2016-06-11 | Tree Contacts | Broken Branch | Tree branch and conductor down in the rear of 695 Carson Rd. | O/H Conductor | O/H Conductor | 134 | 346 | 773 | East | AP06
133793 | 2016-06-11 | Tree Contacts | Broken Branch | Tree branch and conductor down in the rear of 695 Carson Rd. | O/H Conductor | O/H Conductor | 466 | 34 | 264 | East | AP06
133794 | 2016-06-11 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel found at the base of X12889. Crew refused S14076 feeding transformer X12899. Power restored. | O/H Switchgear | Fused Cutout | 4 | 73 | 5 | East | 7F2
133795 | 2016-06-11 | Foreign Interference | Wildlife (Bird/Animal) | At 16:44 a squirrel caused a transformer fuse at the rear of 9 Walgate to open and also cause S624 to blow. 57 customers affected. Parkwood Hills (190F6) | O/H Switchgear | Fused Cutout | 16 | 27 | 7 | South | 190F6
133795 | 2016-06-11 | Foreign Interference | Wildlife (Bird/Animal) | At 16:44 a squirrel caused a transformer fuse at the rear of 9 Walgate to open and also cause S624 to blow. 57 customers affected. Parkwood Hills (190F6) | O/H Switchgear | Fused Cutout | 57 | 31 | 29 | South | 190F6
133796 | 2016-06-11 | Defective Equipment | Defective Equipment/ Material | Blue Phase cable fault between TP7046 and S21557. Bilberry 77M6 | U/G Cable | Unknown \ Other | 94 | 143 | 224 | East | 77M6
133798 | 2016-06-12 | Tree Contacts | Broken Branch | Outage due to tree branch falling on overhead conductor and damaging conductor. | O/H Conductor | O/H Conductor | 74 | 98 | 121 | Central | TR09
133799 | 2016-06-12 | Tree Contacts | Falling Tree | Tree fallen in the backyard has pulled primary down. | O/H Conductor | O/H Conductor | 245 | 182 | 743 | Central | SM02
133801 | 2016-06-12 | Scheduled Outage | Forced Switching | Transformer opened at 32 Arundel to allow crew to replace service affecting 11 customers for 15 minutes. Beechwood UB04 | None | None | 11 | 38 | 7 | East | UB04
133802 | 2016-06-12 | Defective Equipment | Mechanical Failure | Line clamp found burnt off supplying radial line between Holland & Hinton | O/H Conductor | Hot-Line Clamp | 28 | 67 | 31 | Central | SH02
133803 | 2016-06-12 | Scheduled Outage | Forced Switching | 39F2 and 39F3 interrupted to prevent partial phasing with the South March transformer high side red phase loss. Load recovered using Beaverbrook 24F5 as back-up. 874 customers affected for 1 hour. | None | None | 0 | 254880 | 0 | West | 39F3
133803 | 2016-06-12 | Scheduled Outage | Forced Switching | 39F2 and 39F3 interrupted to prevent partial phasing with the South March transformer high side red phase loss. Load recovered using Beaverbrook 24F5 as back-up. 874 customers affected for 1 hour. | None | None | 874 | 55 | 801 | West | 39F2
133804 | 2016-06-12 | Tree Contacts | Tree Growth/ Untrimmed Tree | trees coming in contact with OH and sparking | None | None | 1 | 355 | 6 | South | 180F4
133805 | 2016-06-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer GB002694 openned due to animal contact. 24/7 to refuse. | O/H Switchgear | Fused Cutout | 10 | 126 | 21 | West | TFXF1
133806 | 2016-06-13 | Scheduled Outage | Vegetation Management | AH07 from TEMP 40 to EOL at 473 Hillcrest was isolated for tree trimming. 8 customers affected. Hillcrest (AH07) | None | O/H Conductor | 8 | 229 | 31 | Central | AH07
133807 | 2016-06-13 | Scheduled Outage | Construction | At 9:40am FAL03 from X4774 to end of line was isolated to allow crew to reconfigure overhead lines. 1 customer affected. Fallowfield (FAL03) | None | None | 1 | 330 | 6 | South | FAL03
133808 | 2016-06-13 | Scheduled Outage | Maintenance | Jeremy Walker and crew to have transformers X30002, and X30088 open to transfer plant. Customers notified Friday. | None | None | 6 | 52 | 5 | Central | SB03
133809 | 2016-06-13 | Foreign Interference | Foreign Objects | G60R blew due to tree branch falling on the overhead primary circuit. | O/H Conductor | Hot-Line Clamp | 6 | 195 | 20 | East | BLKF5
133810 | 2016-06-14 | Scheduled Outage | Construction | planned outage to replace pole and transfer plant | None | None | 15 | 220 | 55 | West | 44F1
133811 | 2016-06-14 | Scheduled Outage | Construction | replace leaker | None | None | 6 | 454 | 45 | East | 77M2
133812 | 2016-06-14 | Unknown/Other | Unknown | REPLACED SWITCH AND ARRESTER FEEDING TRANSFORMER X11145 (FUSE FOUND BLOWN) | O/H Transformer | O/H Transformer (1ph) | 1 | 131 | 2 | West | BECKF2
133813 | 2016-06-14 | Scheduled Outage | Maintenance | isolated to replace a burnt termination | None | None | 7 | 208 | 24 | South | 84F5
133814 | 2016-06-14 | Scheduled Outage | Maintenance | change leaking transformer MT1553 | None | None | 8 | 195 | 26 | Central | 307
133815 | 2016-06-14 | Scheduled Outage | Maintenance | REPLACED TRANSFORMER X35891 (PCB OIL) | None | None | 3 | 160 | 8 | West | 43F2
133816 | 2016-06-14 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 28 | 301 | 140 | Central | TW22
133818 | 2016-06-14 | Defective Equipment | Defective Equipment/ Material | Blowwn cable at SC13 MH | U/G Cable | PILC | 33 | 21 | 12 | East | ELW04
133818 | 2016-06-14 | Defective Equipment | Defective Equipment/ Material | Blowwn cable at SC13 MH | U/G Cable | PILC | 65 | 4 | 4 | East | ELW04
133818 | 2016-06-14 | Defective Equipment | Defective Equipment/ Material | Blowwn cable at SC13 MH | U/G Cable | PILC | 103 | 28 | 48 | East | ELW04
133818 | 2016-06-14 | Defective Equipment | Defective Equipment/ Material | Blowwn cable at SC13 MH | U/G Cable | PILC | 2856 | 26 | 1238 | East | ELW04
133818 | 2016-06-14 | Defective Equipment | Defective Equipment/ Material | Blowwn cable at SC13 MH | U/G Cable | PILC | 3095 | 69 | 3559 | East | ELW04
133819 | 2016-06-14 | Defective Equipment | Defective Equipment/ Material | Defective Transformer X26828 had to be replaced. | O/H Transformer | O/H Transformer (1ph) | 11 | 430 | 79 | East | AE03
133820 | 2016-06-15 | Defective Equipment | Defective Equipment/ Material | B phase cable fault between TP7590 and TP7582 caused the S13785 to open. | U/G Cable | XLPE | 90 | 114 | 171 | East | 77M6
133821 | 2016-06-15 | Scheduled Outage | Construction | planned outage to allow crews to perform voltage conversions. | None | None | 4 | 59 | 4 | South | FAL03
133821 | 2016-06-15 | Scheduled Outage | Construction | planned outage to allow crews to perform voltage conversions. | None | None | 5 | 145 | 12 | South | FAL03
133822 | 2016-06-15 | Scheduled Outage | Maintenance | planned outgae to replace a leaker and elbows and inserts. | None | None | 21 | 179 | 63 | East | BCHF1
133823 | 2016-06-15 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35688 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 5 | 85 | 7 | Central | TD14
133824 | 2016-06-15 | Scheduled Outage | Construction | Transformer #X29124 isolated by crew for a service upgrade | None | None | 7 | 87 | 10 | East | TB15
133825 | 2016-06-15 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 12 | 177 | 35 | Central | AH13
133826 | 2016-06-15 | Tree Contacts | Falling Tree | CUST CUT TREE AND TOOK DOWN PRIM NEUT AND S/P /SERVICE ETC | O/H Conductor | O/H Conductor | 12 | 201 | 40 | East | SO02
133827 | 2016-06-16 | Scheduled Outage | Maintenance | To remove a fibre board, transformer TE1259 was isolated by HOL crew on the BLKF8 out of Blackburn for 46 minutes. | None | None | 19 | 46 | 15 | East | BLKF8
133828 | 2016-06-16 | Scheduled Outage | Vegetation Management | Tree Trimming and vegetation management by HOL crew, TE1571 isolated from S25281 on the 145F2 out of Jockvale DS affecting 1 customer for 5.5 hours. | None | None | 1 | 332 | 6 | South | 145F2
133829 | 2016-06-16 | Scheduled Outage | Maintenance | Leaking transformer change by HOL Crew on 381B50 affecting 12 customers on the Bridlewood BRDF3 | None | None | 12 | 511 | 102 | West | BRDF3
133830 | 2016-06-16 | Scheduled Outage | Construction | Circuit reconfiguration on Shea Road interrupting 30 customers on the Richmond North RHNF1 | None | None | 30 | 181 | 90 | West | RHNF1
133831 | 2016-06-16 | Unknown/Other | Unknown | TW18 breaker tripped, line patrolled but cause unknown | None | None | 1378 | 47 | 1079 | Central | TW18
133832 | 2016-06-16 | Foreign Interference | Customer Equipment | SC20 failed and tripped 403/404 circuits | Customer Owned | Customer-Owned | 1 | 1071 | 18 | Central | TK13
133832 | 2016-06-16 | Foreign Interference | Customer Equipment | SC20 failed and tripped 403/404 circuits | Customer Owned | Customer-Owned | 4 | 55 | 4 | Central | TK13
133832 | 2016-06-16 | Foreign Interference | Customer Equipment | SC20 failed and tripped 403/404 circuits | Customer Owned | Customer-Owned | 284 | 39 | 185 | Central | 404
133835 | 2016-06-16 | Scheduled Outage | Maintenance | Rearrange of Overhead on Yvon St Casselman on the Casselman V11F2 circuit affecting 15 customers for 3 hours 50 minutes | None | None | 15 | 230 | 58 | East | V11F2
133836 | 2016-06-16 | Defective Equipment | Defective Equipment/ Material | TP5060 lost supply when cable fault tripped S14263 Blue Phase affecting 8 customers on the Fallowfield FAL02 for 2 hours. | Pole Attachement | Arrester | 8 | 115 | 15 | South | FAL02
133839 | 2016-06-17 | Scheduled Outage | Construction | 12 customers affected on Farmers Way for HOL crew to transfer conductor to new poles on the Leitrim 249F2 | None | None | 12 | 262 | 52 | East | 249F2
133840 | 2016-06-17 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to clean inside the transformer enclosure and base | None | None | 8 | 112 | 15 | Central | AK03
133841 | 2016-06-17 | Scheduled Outage | Maintenance | Jim Yeldon to have transformer NPTE0410 open for emergnecy repairs. Customers notified. | None | None | 13 | 38 | 8 | South | 84F5
133844 | 2016-06-17 | Scheduled Outage | Maintenance | TP2739 secondary isolation by HOL crew for customer to perform secondary maintenance on the TFXF6 out of Terry Fox Station. 1 Customer affected for 1 hour. | None | None | 1 | 65 | 1 | West | TFXF6
133845 | 2016-06-18 | Scheduled Outage | Construction | BRDF3 overhead isolation on Maplegrove, between SC7965-L2 and SC29984-L2, and the 789, to allow crew to remove old 28kv line on Maple Grove, as well as the 44kv W of S23857 to the road crossing on Maple Grove. No customer outage on the 44kv. | None | O/H Conductor | 14 | 409 | 95 | West | BRDF3
133846 | 2016-06-18 | Defective Equipment | Electrical Failure | Not yet known. | O/H Switchgear | Fused Cutout | 32 | 82 | 44 | Central | AK07
133847 | 2016-06-19 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change switches & insulators inside transformer P126 | None | Unknown \ Other | 8 | 77 | 10 | East | SO07
133848 | 2016-06-19 | Foreign Interference | Wildlife (Bird/Animal) | SQUIRREL CONTACT | O/H Transformer | O/H Transformer (1ph) | 41 | 104 | 71 | East | TB15
133849 | 2016-06-19 | Foreign Interference | Wildlife (Bird/Animal) | SQUIRREL CONTACT | O/H Transformer | O/H Transformer (1ph) | 7 | 24 | 3 | Central | TD14
133850 | 2016-06-19 | Defective Equipment | Mechanical Failure | Broken cutout | O/H Switchgear | Fused Cutout | 12 | 73 | 15 | Central | TW22
133851 | 2016-06-19 | Foreign Interference | Wildlife (Bird/Animal) | Crow made contact | O/H Transformer | O/H Transformer (1ph) | 28 | 42 | 20 | West | JKGF5
133852 | 2016-06-19 | Defective Equipment | Defective Equipment/ Material | Cable fault between TE1509 and TE1510. | U/G Cable | XLPE | 73 | 130 | 158 | East | 4801F8
133854 | 2016-06-20 | Unknown/Other | Unknown | Not yet known. | None | None | 5199 | 13 | 1126 | East | 4801F8
133856 | 2016-06-20 | Scheduled Outage | Maintenance | Transformer TP11433 isolated to replace leaking transformer. | None | Padmount (1ph) | 13 | 64 | 14 | East | 4801F8
133857 | 2016-06-20 | Scheduled Outage | Construction | Transformer X57465 to EOL, was isolated to allow crew to install new wire. | None | None | 5 | 58 | 5 | West | 44F1
133858 | 2016-06-20 | Defective Equipment | Mechanical Failure | The TL05 CB tripped due tosuspected cable fault between VT384 and TV9880. Cable was sectionalized at 14:28 and all load was restored, no fault found. Cable tripped again at 14:54 pm and fault was found between VT384 and TV9880. | Vault Equipment | Switch | 607 | 68 | 688 | East | TB1AL
133858 | 2016-06-20 | Defective Equipment | Mechanical Failure | The TL05 CB tripped due tosuspected cable fault between VT384 and TV9880. Cable was sectionalized at 14:28 and all load was restored, no fault found. Cable tripped again at 14:54 pm and fault was found between VT384 and TV9880. | Vault Equipment | Switch | 725 | 97 | 1172 | Central | 5202
133858 | 2016-06-20 | Defective Equipment | Mechanical Failure | The TL05 CB tripped due tosuspected cable fault between VT384 and TV9880. Cable was sectionalized at 14:28 and all load was restored, no fault found. Cable tripped again at 14:54 pm and fault was found between VT384 and TV9880. | Vault Equipment | Switch | 752 | 71 | 890 | East | TB1AL
133860 | 2016-06-20 | Adverse Weather | Extreme Wind | The UZ06 Overhead wires wrap around each other because of the high winds | O/H Conductor | O/H Conductor | 654 | 84 | 916 | East | UZ06
133861 | 2016-06-20 | Adverse Weather | Extreme Wind | AE05 breaker tripped. S24351 found open at 2050 WALKLEY RD, crews found nothing but there was high winds | O/H Conductor | O/H Conductor | 217 | 118 | 427 | East | AE05
133863 | 2016-06-20 | Adverse Weather | Extreme Wind | TB1AL circuit tripped at the same time as AL02 circuit. TB1AL circuit closed in, and AL02 circuit to be patrolled. Trip was caused by phases wrapped around each other east of switch S24448 on Gladwin | O/H Conductor | Unknown \ Other | 226 | 23 | 87 | East | TB1AL
133863 | 2016-06-20 | Adverse Weather | Extreme Wind | TB1AL circuit tripped at the same time as AL02 circuit. TB1AL circuit closed in, and AL02 circuit to be patrolled. Trip was caused by phases wrapped around each other east of switch S24448 on Gladwin | O/H Conductor | Unknown \ Other | 909 | 19 | 288 | East | TB1AL
133864 | 2016-06-20 | Tree Contacts | Falling Tree | Tree fell on the O/H at Coronation and took down the B phase primary and broke pole top at X39346 | O/H Conductor | O/H Conductor | 33 | 404 | 222 | East | TB14
133866 | 2016-06-20 | Tree Contacts | Broken Branch | TR04 circuit tripped. TR1UQ and TR2TS circuits. Queens UQT2 and UQT3 transformers also affected. Vegetation contact found at TB1UQ riser S24133 RWB Abbey Rd South of Balfour Ave at the right of way. | None | None | 2 | 43 | 1 | Central | TR1UQ
133866 | 2016-06-20 | Tree Contacts | Broken Branch | TR04 circuit tripped. TR1UQ and TR2TS circuits. Queens UQT2 and UQT3 transformers also affected. Vegetation contact found at TB1UQ riser S24133 RWB Abbey Rd South of Balfour Ave at the right of way. | None | None | 4 | 26 | 2 | Central | TR1UQ
133866 | 2016-06-20 | Tree Contacts | Broken Branch | TR04 circuit tripped. TR1UQ and TR2TS circuits. Queens UQT2 and UQT3 transformers also affected. Vegetation contact found at TB1UQ riser S24133 RWB Abbey Rd South of Balfour Ave at the right of way. | None | None | 964 | 28 | 450 | Central | TR1UQ
133867 | 2016-06-20 | Tree Contacts | Falling Tree | Tree came down behind 31 Evergreen and caused the braces to break on the pole, the crossarm is twisted, and the centre phase came down, on the pole 1 span south. A section on the 47F3 overhead was isoalted to make repairs. | O/H Conductor | Unknown \ Other | 79 | 53 | 70 | South | 47F3
133868 | 2016-06-20 | Tree Contacts | Tree Growth/ Untrimmed Tree | Trees in the Overhead cause the line to slap together | O/H Conductor | O/H Conductor | 654 | 194 | 2115 | East | UZ06
133869 | 2016-06-20 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact on overhead 4kv circuit caused a trip and a flash that tripped 2 adjacent 13kv circuits. The circuits where restored separatly after each was cleared of vegitation, Affecting 3160 customers. Russell TB3LE & TB1AL, Bantree AL02 | None | None | 220 | 139 | 510 | East | AL02
133869 | 2016-06-20 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact on overhead 4kv circuit caused a trip and a flash that tripped 2 adjacent 13kv circuits. The circuits where restored separatly after each was cleared of vegitation, Affecting 3160 customers. Russell TB3LE & TB1AL, Bantree AL02 | None | None | 683 | 3 | 34 | East | TB1AL
133869 | 2016-06-20 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact on overhead 4kv circuit caused a trip and a flash that tripped 2 adjacent 13kv circuits. The circuits where restored separatly after each was cleared of vegitation, Affecting 3160 customers. Russell TB3LE & TB1AL, Bantree AL02 | None | None | 2197 | 4 | 146 | East | TB3LE
133870 | 2016-06-20 | Scheduled Outage | Vegetation Management | Tree limbs on customer secondary. Transformer X31325 openned to cut down secondaries. 125 and 127 will remain off until repairs are made. Layout required. | None | O/H Conductor | 18 | 12 | 4 | Central | SB05
133871 | 2016-06-20 | Scheduled Outage | Vegetation Management | Large Willow Tree in the secondary of X33912 at 1155 Maitland. Crews interrupted power to the transformer to clear the pole affecting 16 customers on the Clyde UC05. | None | None | 16 | 61 | 16 | Central | UC05
133872 | 2016-06-20 | Scheduled Outage | Maintenance | Transformer #X26846 isolated by crew due to burnt neutral | None | None | 10 | 52 | 9 | East | TB15
133873 | 2016-06-20 | Scheduled Outage | Vegetation Management | Outage to transformer X23673 so that tree crews could clear vegetation from 2 spans of secondary bus on Placel Road affecting 10 customers on the Beechwood UB07. | None | None | 10 | 1125 | 188 | East | UB07
133874 | 2016-06-20 | Defective Equipment | Mechanical Failure | Defective reyrolle fuse in customer vault at 340 Gloucester required to be opened to change affecting 75 customers. Lisgar 5202 | Vault Equipment | Switch | 75 | 20 | 25 | Central | 5202
133875 | 2016-06-21 | Tree Contacts | Falling Tree | Tree on the secondary overhead at 883 Dunlevie required isolation to remove affecting 12 customers.Woodroffe TW22 | O/H Conductor | O/H Conductor | 12 | 109 | 22 | Central | TW22
133876 | 2016-06-20 | Scheduled Outage | Vegetation Management | X45289 transformer interrupted by crew to remove trees from the overhead at 296 Ducharme Blvd on the Church AA03 feeder affecting 14 customers for 1 hr and 45 minutes. | None | None | 14 | 105 | 24 | East | AA03
133877 | 2016-06-21 | Foreign Interference | Wildlife (Bird/Animal) | Not yet known. | None | None | 110 | 80 | 147 | East | 8F3
133879 | 2016-06-21 | Scheduled Outage | Maintenance | TP10804, TP10805, TP10806 & TP10807 isolated for elbow and insert replacement | None | Padmount (1ph) | 41 | 210 | 144 | East | CYRF1
133880 | 2016-06-21 | Scheduled Outage | Construction | Glen Carswell to have transformer X32211 open to instal a new service. Customers notified. | None | None | 2 | 60 | 2 | Central | SM02
133881 | 2016-06-21 | Scheduled Outage | Vegetation Management | S17138 opened to allow tree contractor to remove trees. | None | None | 18 | 313 | 94 | Central | SR09
133882 | 2016-06-21 | Scheduled Outage | Construction | Transformer #X31330 isolated by crew to reconnect service | None | None | 8 | 80 | 11 | Central | SB05
133885 | 2016-06-22 | Tree Contacts | Tree Growth/ Untrimmed Tree | 7 customers affected when X36404 transformer fuse blew on the Barrhaven 140F5 feeder. | None | None | 7 | 102 | 12 | South | 140F5
133886 | 2016-06-22 | Scheduled Outage | Maintenance | TP10870, TP10874 & TP10881 iso9lated for elbow & insert replacement | None | Padmount (1ph) | 43 | 223 | 160 | East | 8F3
133887 | 2016-06-22 | Scheduled Outage | Vegetation Management | UZ05 OH isolated from TEMP124 to EOL for tree trimming | None | None | 20 | 187 | 62 | East | UZ05
133888 | 2016-06-22 | Scheduled Outage | Maintenance | Oil Remediation at TP3925 | None | None | 20 | 335 | 112 | South | 87F6
133889 | 2016-06-22 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X29918 TO INSTALL A NEW TRIPLEX SERVICE | None | None | 12 | 20 | 4 | Central | SB12
133890 | 2016-06-22 | Scheduled Outage | Maintenance | Leaking PT141 replaced with TP11452 | None | Padmount (3ph) | 25 | 316 | 132 | Central | TH11-NIU
133894 | 2016-06-23 | Scheduled Outage | Construction | Elebow and inserts | None | None | 65 | 169 | 183 | East | 8F3
133895 | 2016-06-23 | Scheduled Outage | Vegetation Management | planned outage for tree crews | None | None | 32 | 227 | 121 | East | AN04
133898 | 2016-06-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31645 TO INSTALL A NEW POLE | None | None | 9 | 150 | 22 | Central | SR08
133899 | 2016-06-23 | Scheduled Outage | Construction | Elbows and inserts | None | None | 29 | 74 | 36 | East | 8F3
133900 | 2016-06-23 | Scheduled Outage | Maintenance | Vault Maintenance | None | None | 1 | 362 | 6 | Central | SK11
133901 | 2016-06-21 | Scheduled Outage | Maintenance | Transformer TN9576-T1CZZ was isolated for customer owned equipment maintenance. | Vault Equipment | Transformer | 1 | 2865 | 48 | East | 48M4
133903 | 2016-06-24 | Defective Equipment | Defective Equipment/ Material | Transformer X32394 opened due to defective switch. Woodroffe 170F1 | O/H Switchgear | Fused Cutout | 8 | 69 | 9 | South | 170F1
133904 | 2016-06-24 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X25241 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 5 | 54 | 4 | East | TB06
133905 | 2016-06-24 | Scheduled Outage | Construction | change hydro pole damaged by woodpecker. | None | Pole | 1 | 316 | 5 | Central | 4301
133906 | 2016-06-24 | Scheduled Outage | Construction | Place transformer back onto base. | None | None | 12 | 32 | 6 | East | BCHF5
133907 | 2016-06-24 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X36544 TO CHECK PRIMARY CONNECTIONS ON THE SWITCH AND TRANSFORMER | None | None | 6 | 15 | 2 | South | EPWF4
133908 | 2016-06-24 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X26951 TO REPLACE TRIPLEX SERVICE | None | None | 10 | 55 | 9 | East | AJ05
133909 | 2016-06-24 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 35 | 238 | 139 | Central | TD06
133915 | 2016-06-25 | Foreign Interference | Wildlife (Bird/Animal) | Customer reported outage, crews found fused cutout blown due to animal contact, switch replaced due to being damaged. Riverdale (TR3UY) | O/H Switchgear | Fused Cutout | 30 | 164 | 82 | Central | TR3UY
133916 | 2016-06-25 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35790 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 14 | 108 | 25 | Central | TD06
133917 | 2016-06-25 | Defective Equipment | Mechanical Failure | Switch Barrel at S224 went defective at 31 Tiverton originally affecting 45 customers on the 190F5 out of Parkwood Hills. Outage expanded to create safe work to jumper out the switch. | O/H Switchgear | Inline Switch | 45 | 224 | 168 | South | 190F5
133917 | 2016-06-25 | Defective Equipment | Mechanical Failure | Switch Barrel at S224 went defective at 31 Tiverton originally affecting 45 customers on the 190F5 out of Parkwood Hills. Outage expanded to create safe work to jumper out the switch. | O/H Switchgear | Inline Switch | 110 | 48 | 88 | South | 190F5
133918 | 2016-06-25 | Defective Equipment | Mechanical Failure | White phase was in contact with grounded new construction overhead conductor at 3688 McBean Street Richmond. Overhead was sectionalized to pinpoint location. Crew had to be in the air to spot the problem. | O/H Conductor | O/H Conductor | 44 | 309 | 227 | West | 28F3
133919 | 2016-06-25 | Scheduled Outage | Maintenance | Hydro Ottawa FOPS & 24/7 crew isolated Hazeldean Mall-44kV vault/mini sub to allow Kroon Electric to take oils samples from the customer owned transformers. (T1 & T2) | None | None | 46 | 39 | 30 | West | A9M1
133921 | 2016-06-25 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 2 | 415 | 14 | West | 28F3
133924 | 2016-06-26 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35229 opened up due to animal contact | O/H Switchgear | Fused Cutout | 10 | 129 | 22 | West | JKGF5
133926 | 2016-06-26 | Scheduled Outage | Maintenance | TP10882 at 1486 Innes isolated by contractor for elbow, insert and switch replacement on the CYRF4 out of Cyrville MTS affecting 1 customer for 1 hour 45 minutes. | None | None | 1 | 101 | 2 | East | CYRF4
133927 | 2016-06-26 | Foreign Interference | Wildlife (Bird/Animal) | Transformer cut out opened at 2357 Georgina caused by a squirrel affecting 8 customers. Woodroffe TW22 | O/H Switchgear | Fused Cutout | 8 | 58 | 8 | Central | TW22
133928 | 2016-06-26 | Defective Equipment | Mechanical Failure | Cable fault on the 303 circuit between VT365 & VT240 | U/G Cable | PILC | 15 | 197 | 49 | Central | 303
133928 | 2016-06-26 | Defective Equipment | Mechanical Failure | Cable fault on the 303 circuit between VT365 & VT240 | U/G Cable | PILC | 275 | 7 | 32 | Central | 303
133928 | 2016-06-26 | Defective Equipment | Mechanical Failure | Cable fault on the 303 circuit between VT365 & VT240 | U/G Cable | PILC | 1011 | 65 | 1095 | Central | 303
133929 | 2016-06-24 | Scheduled Outage | Maintenance | To amalgamate service to new 800A 347/600v service. | None | None | 1 | 3015 | 50 | East | TB2AL
133930 | 2016-06-26 | Defective Equipment | Mechanical Failure | The fused cut-out at transformer X39589 was found broken and blown. Switch repaired and power restored. | O/H Switchgear | Fused Cutout | 1 | 120 | 2 | West | 624F6
133931 | 2016-06-27 | Defective Equipment | Electrical Failure | TP8250 was found to be defective | U/G Transformer | Padmount (1ph) | 14 | 376 | 88 | East | 77M2
133932 | 2016-06-27 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree branches caused the transformer fuse to open at transformer X4062 to open | O/H Switchgear | Fused Cutout | 15 | 46 | 12 | South | 170F1
133933 | 2016-06-27 | Scheduled Outage | Vegetation Management | Brent Ducan and crew to have transformer x35183 open to remove tree from service. Customer has been notified | None | None | 8 | 35 | 5 | Central | UC03
133937 | 2016-06-27 | Scheduled Outage | Construction | Dan Crough (K-Line) and crew to have transformer X57465 open to transfer plant to new poles. Customers notified. | None | None | 16 | 140 | 37 | West | 44F1
133938 | 2016-06-27 | Scheduled Outage | Construction | Dan Crough (K-Line) to have transformer X57469 open to transfer plant to new poles. Customers notified. | None | None | 3 | 170 | 8 | West | 44F1
133939 | 2016-06-27 | Scheduled Outage | Maintenance | Brent Duncan to have transformer X35183 open to install a new service. Customers notified. | None | None | 8 | 88 | 12 | Central | UC03
133941 | 2016-06-27 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contacted primary at RX2058 causing trip on station breaker and inline recloser RX2020 to trip affecting 7409 customers. Bilberry Creek 77M2 | None | None | 1207 | 10 | 201 | East | 77M2
133941 | 2016-06-27 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contacted primary at RX2058 causing trip on station breaker and inline recloser RX2020 to trip affecting 7409 customers. Bilberry Creek 77M2 | None | None | 3020 | 33 | 1661 | East | 77M2
133942 | 2016-06-27 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X35736 | O/H Transformer | O/H Transformer (1ph) | 1 | 98 | 2 | West | BECKF2
133943 | 2016-06-27 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X57458 AND X57448 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 10 | 240 | 40 | West | 44F1
133944 | 2016-06-27 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X29963 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 9 | 71 | 11 | Central | UC08
133945 | 2016-06-27 | Scheduled Outage | Construction | Replace defective elbow. | None | None | 21 | 113 | 40 | East | 77M6
133946 | 2016-06-28 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel caused transformer X32741 fuse to open. | O/H Switchgear | Fused Cutout | 8 | 60 | 8 | Central | TD05
133947 | 2016-06-28 | Scheduled Outage | Vegetation Management | Tree trimming at the rear of 20 Foothills. | None | None | 65 | 305 | 330 | South | 200F3
133948 | 2016-06-28 | Scheduled Outage | Maintenance | Elbow and insert replacements | None | Padmount (1ph) | 68 | 230 | 261 | East | 8F3
133950 | 2016-06-28 | Scheduled Outage | Construction | Don Kelly opened transformer x49783 to change connection on back yard bus. Customers notified. | None | None | 10 | 54 | 9 | East | SO10
133951 | 2016-06-28 | Scheduled Outage | Construction | Dan Crough transfering plant | None | None | 12 | 120 | 24 | West | 44F1
133952 | 2016-06-28 | Scheduled Outage | Construction | Don Kelly (Black and Macdonald) to have transformer X49775 open to transfer plant. Customers notified. | None | None | 10 | 36 | 6 | East | SO10
133953 | 2016-06-28 | Defective Equipment | Defective Equipment/ Material | Customer issue in customer owned vault. | Customer Owned | Customer-Owned | 1562 | 1 | 26 | East | 48M4
133954 | 2016-06-28 | Scheduled Outage | Construction | Brent Duncan to have transformer X33741 open to run a service by the drop. Customers notified. | None | None | 6 | 79 | 8 | Central | TH01
133955 | 2016-06-28 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact in customer vault VT577 caused fuse to blow on R3-F switch. 3 customers affected. Woodroffe TW2UV. | O/H Switchgear | Fused Cutout | 3 | 276 | 14 | Central | TW2UV
133956 | 2016-06-28 | Foreign Interference | Wildlife (Bird/Animal) | Transformer fuse at X15547 opened due to animal contact (Crow) | O/H Switchgear | Fused Cutout | 2 | 63 | 2 | East | LTM01
133957 | 2016-06-28 | Tree Contacts | Falling Tree | Tree took down overhead conductor and neutral. | O/H Conductor | O/H Conductor | 1 | 213 | 4 | East | LTM01
133957 | 2016-06-28 | Tree Contacts | Falling Tree | Tree took down overhead conductor and neutral. | O/H Conductor | O/H Conductor | 28 | 103 | 48 | East | LTM01
133958 | 2016-06-29 | Scheduled Outage | Maintenance | Replace leaking transformer | None | Kiosk (1ph) | 10 | 138 | 23 | East | 77M6
133959 | 2016-06-29 | Scheduled Outage | Maintenance | At 9:00 crews isolated TP11435 to do soil remediation. 53 customers affected. Bridlewood (BRDF3) | None | None | 53 | 387 | 342 | West | BRDF3
133962 | 2016-06-29 | Scheduled Outage | Construction | Transfer of plant | None | None | 10 | 110 | 18 | West | 44F1
133963 | 2016-06-29 | Scheduled Outage | Construction | To remove 5991 from service and energize new TP11034. | None | Padmount (3ph) | 1 | 67 | 1 | West | 39F2
133964 | 2016-06-29 | Scheduled Outage | Maintenance | At 8:39am crews isolated 4 transforms for elbow and insert replacement. 53 customers affected. Moulton (8F3) | None | None | 53 | 282 | 249 | East | 8F3
133966 | 2016-06-29 | Scheduled Outage | Construction | At 9:00am S427 was open to transfer plant from 8Kv to 27Kv. 14 customers affected. Fallowfield (FAL03) | None | None | 14 | 191 | 45 | South | FAL03
133967 | 2016-06-29 | Defective Equipment | Mechanical Failure | REPLACED BLOWN FUSE FEEDING TRANSFORMER X48460 (CAUSE UNKNOWN) | O/H Transformer | O/H Transformer (1ph) | 16 | 96 | 26 | Central | TW18
133969 | 2016-06-29 | Scheduled Outage | Maintenance | Interruption to Overhead transformer X5609 to replace the connections on service. Rideau Heights 180F6. 4 Customers affected at 70 Bently Ave. | None | None | 4 | 99 | 7 | South | 180F6
133970 | 2016-06-30 | Scheduled Outage | Maintenance | 4 transformers on Beaverpond Dr. isolated for elbow and insert replacment. Cyrville (CYRF1) | None | Elbow \ Insert | 49 | 227 | 185 | East | CYRF1
133971 | 2016-06-30 | Scheduled Outage | Maintenance | Customer owned overhead circuit at 5925 Old Richmond isolate to replace primary switch and trim trees. 1 customer affected. Jockvale (145F3) | None | O/H Conductor | 1 | 145 | 2 | South | 145F3
133972 | 2016-06-30 | Scheduled Outage | Maintenance | Customer vault shut down for routine maintenance. | None | None | 1 | 401 | 7 | East | TO3UT
133995 | 2016-07-02 | Lightning | Lightning | REPLACED DEFECTIVE TRANSFORMER X36338 | O/H Transformer | O/H Transformer (1ph) | 1 | 340 | 6 | West | JKGF5
133996 | 2016-07-02 | Tree Contacts | Broken Branch | crew opened a transformer to replace an open bus service. | Secondary \ Service | O/H Service | 10 | 57 | 10 | East | SO02
133997 | 2016-07-02 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X31993 TO DISCONNECT TRIPLEX SERVICE DAMGED BY WIND STORM | None | None | 6 | 28 | 3 | Central | SM12
133999 | 2016-07-02 | Scheduled Outage | Maintenance | Transformer at 3275 McCarthy was re-isolated to allow crew to find defective service. 17 customers affected. McCarthy (AQ02) | None | None | 17 | 22 | 6 | East | AQ02
134000 | 2016-07-03 | Scheduled Outage | Maintenance | To replace a defective transformer TP2972. | None | Padmount (1ph) | 10 | 64 | 11 | South | FAL02
134001 | 2016-07-03 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE AT SWITCH 5975 FEEDING TRANSFORMER X26631 (BIRD CONTACT) | O/H Switchgear | Fused Cutout | 1 | 80 | 1 | West | MWDF3
134002 | 2016-07-03 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33531 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 5 | 351 | 29 | Central | 303
134003 | 2016-07-03 | Defective Equipment | Electrical Failure | crew open transformer X23762 to jump out secondary bus, because of defective transformer at 466 wolfdale, that will be replaced. | O/H Transformer | O/H Transformer (1ph) | 4 | 7 | 0 | East | SO07
134004 | 2016-07-03 | Defective Equipment | Electrical Failure | defective transformer x23763 at 466 wolfdale | O/H Transformer | O/H Transformer (1ph) | 7 | 459 | 54 | East | SO07
134005 | 2016-07-04 | Scheduled Outage | Construction | Elbow and insert replacement and transfromers replacement. | None | None | 36 | 220 | 132 | East | CYRF1
134006 | 2016-07-04 | Scheduled Outage | Vegetation Management | tree across 3 phase overhead of UZ05 | None | None | 121 | 71 | 143 | East | UZ05
134007 | 2016-07-04 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X36461 TO TRANSFER HYDRO PLANT TO NEW TRANSFORMER | None | None | 6 | 158 | 16 | West | 44F1
134008 | 2016-07-04 | Scheduled Outage | Construction | New pole line. | None | None | 70 | 191 | 223 | West | 28F2
134009 | 2016-07-04 | Scheduled Outage | Construction | Rick Barnett to have trasnformer X31993 open to change secondary connections. Customers notified. | None | None | 6 | 9 | 1 | Central | SM12
134010 | 2016-07-05 | Foreign Interference | Vehicle | A car struck pole X34719, shearing it off at the base. Transformer X34719 was ripped off the pole and fell on the road. | Pole | Pole | 15 | 204 | 51 | Central | TD05
134010 | 2016-07-05 | Foreign Interference | Vehicle | A car struck pole X34719, shearing it off at the base. Transformer X34719 was ripped off the pole and fell on the road. | Pole | Pole | 24 | 10 | 4 | Central | TD05
134012 | 2016-07-05 | Scheduled Outage | Vegetation Management | S20121 to Eol was isolated to allow crew to perfrom tree trimming. Woodroffe TW18 | None | None | 12 | 194 | 39 | Central | TW18
134013 | 2016-07-05 | Scheduled Outage | Construction | Temp 76 to EOL on Codds an Via Venus was isolated to allow crew to remove O/H line on Codds st. Langs (AP02) | None | None | 3 | 421 | 21 | East | AP02
134014 | 2016-07-05 | Foreign Interference | Wildlife (Bird/Animal) | X41017 opened up due to animal contact | O/H Switchgear | Fused Cutout | 3 | 127 | 6 | West | 624F6
134015 | 2016-07-05 | Scheduled Outage | Maintenance | Old leaker replaced with new transformer. | U/G Transformer | Padmount (1ph) | 14 | 118 | 28 | West | TFXF1
134016 | 2016-07-05 | Scheduled Outage | Construction | Switch S29287 opened to isolate X39746 to allow overhead reconfigure, | None | None | 1 | 197 | 3 | South | FAL03
134017 | 2016-07-05 | Scheduled Outage | Maintenance | Repairs made to burnt terminations at S23944 | None | None | 1 | 173 | 3 | South | 180F6
134018 | 2016-07-05 | Scheduled Outage | Construction | Transformer #X34237 isolated by crew to install new U/G service | None | None | 3 | 90 | 4 | Central | UL03
134019 | 2016-07-05 | Scheduled Outage | Maintenance | Transformers TP10838, TP10839 and TP10837 were isoalted to allow crwe to replace elbows and inserts. Cyrville (CYRF1) | None | None | 44 | 250 | 183 | East | CYRF1
134020 | 2016-07-05 | Scheduled Outage | Construction | transfer plant | None | None | 10 | 215 | 36 | West | 44F1
134021 | 2016-07-05 | Scheduled Outage | Construction | X57496 Transfer Plant | None | None | 10 | 215 | 36 | West | 44F1
134022 | 2016-07-05 | Scheduled Outage | Maintenance | Line crew replaced broken crossarm at 90 Withrow | None | None | 71 | 177 | 209 | South | EPWF1
134023 | 2016-07-05 | Scheduled Outage | Maintenance | Transformer isolated to change damaged transfomer bus bar. | None | None | 9 | 79 | 12 | West | TFXF1
134024 | 2016-07-05 | Scheduled Outage | Construction | x29997 Transfer plant | None | None | 10 | 260 | 43 | Central | TR09
134025 | 2016-07-05 | Scheduled Outage | Maintenance | MVA Pepsi truck struck pole. Transformer X27571 openned to make repairs. | None | None | 5 | 96 | 8 | Central | SR01
134026 | 2016-07-05 | Scheduled Outage | Maintenance | Scott Dixon and crew to have transformers X32636 and X32618 open to make repairs. Customers notified. | None | None | 17 | 198 | 56 | Central | TD05
134027 | 2016-07-06 | Scheduled Outage | Vegetation Management | S15042 to EOL was isolated to allow crew to perfrom tree trimming at rear of 1802 Paisley | None | None | 29 | 297 | 144 | Central | TW18
134028 | 2016-07-06 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27632 opened up due to animal contact | O/H Switchgear | Fused Cutout | 7 | 108 | 13 | Central | TH11-NIU
134029 | 2016-07-06 | Foreign Interference | Vehicle | Service pulled down ,opened and removed service to create safe area | None | None | 12 | 27 | 5 | East | AC06
134030 | 2016-07-06 | Scheduled Outage | Maintenance | Transformer TP3663 at 2019 Garfield was isolated to alow cre to remove transformer base to allow contractor to seal secondary ducts | None | None | 1 | 124 | 2 | Central | TW18
134031 | 2016-07-06 | Scheduled Outage | Maintenance | Vault VT205 at 1081 Ambleside was isolated to allow crew to perfrom customer vault maintenance. Lincoln Heights (5401) | None | None | 1 | 379 | 6 | Central | 5401
134032 | 2016-07-06 | Scheduled Outage | Construction | V113, V108 and V108 at 1505 baseline were isoalted to allow crew to install new cables to V107 from pole X48204. Fisher (AK06). | None | None | 1 | 189 | 3 | Central | AK06
134034 | 2016-07-06 | Scheduled Outage | Construction | Service upgrades | None | None | 14 | 57 | 13 | Central | SB11
134035 | 2016-07-06 | Scheduled Outage | Maintenance | S28488 opened to allow for reconfigure of new 27 KV overhead conductor | None | None | 1 | 105 | 2 | South | FAL03
134036 | 2016-07-06 | Scheduled Outage | Construction | Vault V731, V732, V733 were isoalted to allow crew to remove failed cable from vault to O/H riser S16452. Walkley (UZ06) | None | None | 561 | 143 | 1337 | East | UZ06
134037 | 2016-07-06 | Scheduled Outage | Maintenance | 5 27 kv transformers isolated by Sproule for elbow, insert replacement. | None | None | 56 | 278 | 259 | East | 8F3
134038 | 2016-07-06 | Scheduled Outage | Vegetation Management | S21447 to Eol was isolated to allow contractor to transfer connect additional services to private line. Jockvale (145F3) | None | None | 1 | 200 | 3 | South | 145F3
134039 | 2016-07-07 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact | O/H Transformer | O/H Transformer (1ph) | 7 | 52 | 6 | South | 47F3
134040 | 2016-07-07 | Tree Contacts | Tree Growth/ Untrimmed Tree | REPLACED BLOWN FUSE FEEDING TRANSFORMER X37233 | O/H Transformer | O/H Transformer (1ph) | 10 | 127 | 21 | South | EPWF3
134041 | 2016-07-07 | Scheduled Outage | Construction | At 8:30 FAL03 from X4488 to End of Line was isolated for voltage conversion. 2 customers affected. Fallowfield (FAL03) | None | None | 2 | 390 | 13 | South | FAL03
134042 | 2016-07-07 | Scheduled Outage | Maintenance | Change leaking transformer #6316. | None | Padmount (1ph) | 10 | 116 | 19 | West | JKGF5
134042 | 2016-07-07 | Scheduled Outage | Maintenance | Change leaking transformer #6316. | None | Padmount (1ph) | 10 | 170 | 28 | West | JKGF5
134042 | 2016-07-07 | Scheduled Outage | Maintenance | Change leaking transformer #6316. | None | Padmount (1ph) | 30 | 10 | 5 | West | JKGF5
134043 | 2016-07-07 | Scheduled Outage | Maintenance | Replace leaking transformer # TE307. | None | Padmount (1ph) | 8 | 146 | 19 | East | BCHF5
134044 | 2016-07-07 | Scheduled Outage | Maintenance | At 8:36am, 4 transformers were isolated for elbow and insert replacement. 45 customers affected. Moulton (8F3) | None | None | 45 | 301 | 226 | East | 8F3
134045 | 2016-07-07 | Scheduled Outage | Maintenance | At 9:20am VT116 was isolated to all contractor to perform vault maintenance and Hydro crew to do metering work. 1 customers affected. Overbrook (TO3AC) | None | None | 1 | 372 | 6 | East | TO3AC
134046 | 2016-07-07 | Scheduled Outage | Vegetation Management | At 8:26am UC10 from Temp55 to end of line was isolated for tree trimming. 13 customers affected. Clyde (UC10) | None | None | 13 | 176 | 38 | Central | UC10
134047 | 2016-07-07 | Defective Equipment | Mechanical Failure | At 12:14pm UT07 was dumped from SCADA due to a live conductor on the ground. 394 customers affected. Eastview (UT07) | O/H Conductor | Unknown \ Other | 394 | 121 | 795 | East | UT07
134049 | 2016-07-07 | Scheduled Outage | Vegetation Management | At 4:30pm crews had isolate a section of UF07 to remove a tree on the primary. 97 customers affected. Florence (UF07) | None | None | 97 | 60 | 97 | Central | UF07
134050 | 2016-07-08 | Scheduled Outage | Vegetation Management | At 08:30am UC05 from Temp 74 to end of line was isolated for tree trimming. 36 customers affected. Clyde (UC05) | None | None | 36 | 266 | 160 | Central | UC05
134051 | 2016-07-08 | Foreign Interference | Wildlife (Bird/Animal) | REFUSE TRANSFORMER X13776 DUE TO (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 1 | 75 | 1 | East | 4801F8
134053 | 2016-07-08 | Unknown/Other | Unknown | Overhead cirucit patrolled no fault found and under ground cables Hi-potted. | O/H Conductor | Unknown \ Other | 282 | 138 | 649 | West | TFXF1
134054 | 2016-07-08 | Scheduled Outage | Maintenance | Removal of lead | None | None | 30 | 60 | 30 | Central | AB04
134055 | 2016-07-08 | Scheduled Outage | Maintenance | Maintance | None | None | 7 | 97 | 11 | Central | SM13
134056 | 2016-07-08 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact (squirrel) | O/H Transformer | O/H Transformer (1ph) | 10 | 79 | 13 | West | RHNF1
134057 | 2016-07-08 | Tree Contacts | Broken Branch | Tree in backyard fell caused causing S868 blue phase to open. | O/H Conductor | O/H Conductor | 53 | 61 | 54 | South | EPWF6
134058 | 2016-07-08 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32648 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 7 | 81 | 9 | Central | TD12
134059 | 2016-07-09 | Defective Equipment | Defective Equipment/ Material | G628W and G627W found blown. Crew sectionalized, and closed G628W. Crews patrolled overhead line and found defective switch at overhead transformer, at 34 Kaymar. | O/H Transformer | O/H Transformer (1ph) | 81 | 44 | 59 | East | 8F1
134059 | 2016-07-09 | Defective Equipment | Defective Equipment/ Material | G628W and G627W found blown. Crew sectionalized, and closed G628W. Crews patrolled overhead line and found defective switch at overhead transformer, at 34 Kaymar. | O/H Transformer | O/H Transformer (1ph) | 118 | 68 | 134 | East | 8F1
134060 | 2016-07-09 | Unknown/Other | Unknown | G320 B phase at 2116 Montreal Rd. found open. Line patrolled, nothing found. 99 customers affected. Moulton (8F1) | Unknown \ Other | Unknown \ Other | 99 | 154 | 254 | East | 8F1
134061 | 2016-07-09 | Lightning | Lightning | TFXF4 circuit auto reclosed during lightning storm. Line patrolled, nothing found. Terry Fox (TFXF4) | Unknown \ Other | Unknown \ Other | 1147 | 1 | 19 | West | TFXF4
134061 | 2016-07-09 | Lightning | Lightning | TFXF4 circuit auto reclosed during lightning storm. Line patrolled, nothing found. Terry Fox (TFXF4) | Unknown \ Other | Unknown \ Other | 2113 | 37 | 1303 | West | TFXF4
134061 | 2016-07-09 | Lightning | Lightning | TFXF4 circuit auto reclosed during lightning storm. Line patrolled, nothing found. Terry Fox (TFXF4) | Unknown \ Other | Unknown \ Other | 2113 | 39 | 1373 | West | TFXF4
134062 | 2016-07-09 | Tree Contacts | Falling Tree | A tree fell into the overhead during a storm and brought down 3 phase conductor behind 9 Cherrywood. Also, single phase conductor came down between 5 & 7 Cherrywood and fell onto Cherrywood Dr itself. | O/H Conductor | O/H Conductor | 0 | 1 | 0 | South | 47F4
134062 | 2016-07-09 | Tree Contacts | Falling Tree | A tree fell into the overhead during a storm and brought down 3 phase conductor behind 9 Cherrywood. Also, single phase conductor came down between 5 & 7 Cherrywood and fell onto Cherrywood Dr itself. | O/H Conductor | O/H Conductor | 100 | 562 | 937 | South | 47F4
134062 | 2016-07-09 | Tree Contacts | Falling Tree | A tree fell into the overhead during a storm and brought down 3 phase conductor behind 9 Cherrywood. Also, single phase conductor came down between 5 & 7 Cherrywood and fell onto Cherrywood Dr itself. | O/H Conductor | O/H Conductor | 156 | 152 | 395 | South | 47F4
134062 | 2016-07-09 | Tree Contacts | Falling Tree | A tree fell into the overhead during a storm and brought down 3 phase conductor behind 9 Cherrywood. Also, single phase conductor came down between 5 & 7 Cherrywood and fell onto Cherrywood Dr itself. | O/H Conductor | O/H Conductor | 542 | 17 | 154 | South | 47F4
134062 | 2016-07-09 | Tree Contacts | Falling Tree | A tree fell into the overhead during a storm and brought down 3 phase conductor behind 9 Cherrywood. Also, single phase conductor came down between 5 & 7 Cherrywood and fell onto Cherrywood Dr itself. | O/H Conductor | O/H Conductor | 542 | 60 | 542 | South | 47F4
134063 | 2016-07-09 | Lightning | Lightning | UX06 and UX00 circuits opened due to a lightning strike that hit a pole at McLeod and Elgin. 695 customers affected. Gladestone (UX06) | Pole | Pole | 695 | 87 | 1008 | Central | UX06
134067 | 2016-07-09 | Scheduled Outage | Forced Switching | To allow Hydro Ottawa crews to replace a defective & unsafe switch. This switch was preventing crews from restoring 56 customers of 156 affected on another outage on Cherrywood Dr. | None | Fused Cutout | 44 | 57 | 42 | South | 47F6
134068 | 2016-07-09 | Scheduled Outage | Maintenance | Routine customer owned vault amintenance performed by Eaton Electric. | None | None | 1 | 309 | 5 | Central | 5213
134070 | 2016-07-09 | Foreign Interference | Wildlife (Bird/Animal) | Animal nest caused one phase of transformer X36647 to open causing outage. | O/H Switchgear | Fused Cutout | 3 | 296 | 15 | South | EPWF5
134071 | 2016-07-09 | Lightning | Lightning | S19 RB phases on Twin Elm opened due to lightning strike that damaged switches and arrestors. 15 customers affected. Jockvale (145F3) | O/H Conductor | O/H Conductor | 1 | 101 | 2 | South | 145F3
134071 | 2016-07-09 | Lightning | Lightning | S19 RB phases on Twin Elm opened due to lightning strike that damaged switches and arrestors. 15 customers affected. Jockvale (145F3) | O/H Conductor | O/H Conductor | 3 | 56 | 3 | South | 145F3
134071 | 2016-07-09 | Lightning | Lightning | S19 RB phases on Twin Elm opened due to lightning strike that damaged switches and arrestors. 15 customers affected. Jockvale (145F3) | O/H Conductor | O/H Conductor | 15 | 264 | 66 | South | 145F3
134072 | 2016-07-09 | Tree Contacts | Other Vegetation | Transformer X23755 opened up due to overgrown vines on the transformer and open bus secondary. | O/H Transformer | O/H Transformer (1ph) | 11 | 391 | 72 | East | SO02
134073 | 2016-07-09 | Defective Equipment | Defective Equipment/ Material | Transformer X40107 opened due to defective transformer switch. | O/H Switchgear | Fused Cutout | 3 | 245 | 12 | West | MWDF3
134074 | 2016-07-09 | Tree Contacts | Falling Tree | Transformer X26003 isolated to allow crew to remove tree off service and make repairs to broken guy wire. | Secondary \ Service | O/H Service | 15 | 10 | 2 | East | AP03
134075 | 2016-07-09 | Tree Contacts | Broken Branch | Overgrown tree branch and defective transformer at 2050 Kings Grove caused the BCHF3 to A/R and transformer X20814 to open. | O/H Switchgear | Fused Cutout | 11 | 825 | 151 | East | BCHF3
134077 | 2016-07-10 | Scheduled Outage | Construction | JKGF5 between TEMP131 and TEMP116 on Sweetnam Dr. isolated to string new conductor. 8 customers affected. Janet King (JKGF5) | None | O/H Conductor | 8 | 404 | 54 | West | JKGF5
134078 | 2016-07-10 | Foreign Interference | Wildlife (Bird/Animal) | Transformer fuse X35631 at 44 Kempster opened due to animal contact. 7 customers affected. Lincoln Heights (TD12) | O/H Transformer | O/H Transformer (1ph) | 7 | 65 | 8 | Central | TD12
134079 | 2016-07-10 | Defective Equipment | Mechanical Failure | A defective cable bet transformer TP7006 and TE1971 on YOUVILLE Dr | U/G Cable | Unknown \ Other | 1 | 178 | 3 | East | 77M5
134081 | 2016-07-11 | Scheduled Outage | Maintenance | To allow Hydro Ottawa line crews to change the elbows on TE1357 | None | Elbow \ Insert | 14 | 65 | 15 | East | BLKF8
134082 | 2016-07-11 | Scheduled Outage | Construction | FAL03 from X4522 to EOL at 4065 Prince of Whales isolated to transfer plant to new poles. 4 customers affected. Fallowfield (FAL03) | None | O/H Conductor | 4 | 184 | 12 | South | FAL03
134083 | 2016-07-11 | Scheduled Outage | Vegetation Management | Tree removal | None | None | 4 | 45 | 3 | Central | AD03
134086 | 2016-07-11 | Scheduled Outage | Maintenance | Four 27.6kV transformers on Northdale and Meadowbrook isolated for elbow and insert replacement. 43 customers affected. Moulton (8F3) | None | Elbow \ Insert | 43 | 225 | 161 | East | 8F3
134087 | 2016-07-11 | Scheduled Outage | Construction | TP10566 and Vault 63 at 2673 McBean isolated to transfer secondaries to TP10566. 2 customers affected. Richmond South (28F3) | None | Padmount (3ph) | 2 | 500 | 17 | West | 28F3
134088 | 2016-07-11 | Scheduled Outage | Maintenance | Transformer #X36425 isolated by crew to replace connections | None | None | 5 | 25 | 2 | West | 44F1
134090 | 2016-07-11 | Scheduled Outage | Vegetation Management | Isolation on Bonnie to allow tree contractor to remove limbs | None | None | 58 | 326 | 315 | Central | UC05
134091 | 2016-07-11 | Scheduled Outage | Vegetation Management | Transfomer X29938 isolated to allow tree crew to remove broken limb from secondary. | None | None | 18 | 177 | 53 | Central | SR02
134092 | 2016-07-12 | Foreign Interference | Wildlife (Bird/Animal) | Racoon contact caused fuse to open at 2705 Don, X31937. 11 customers affected. Lincoln TD14. | None | None | 11 | 75 | 14 | Central | TD14
134094 | 2016-07-12 | Scheduled Outage | Maintenance | Sproule Elec. Replacing Elbows and inserts on 4 transformers. Moulton (8F3) | None | Padmount (1ph) | 43 | 230 | 165 | East | 8F3
134095 | 2016-07-12 | Scheduled Outage | Maintenance | Service upgrade | None | None | 29 | 15 | 7 | East | SO03
134096 | 2016-07-12 | Scheduled Outage | Construction | Pole change | None | None | 5 | 271 | 23 | West | 28F2
134097 | 2016-07-12 | Scheduled Outage | Construction | Pole Change | None | None | 9 | 270 | 40 | West | 28F2
134098 | 2016-07-12 | Scheduled Outage | Construction | Pole Change | None | None | 13 | 270 | 58 | West | 28F2
134099 | 2016-07-12 | Scheduled Outage | Construction | Brian and Sproule to be moving transformer from pole X22780 to pole X21498. Customers notified. | None | None | 1 | 285 | 5 | East | V11F2
134100 | 2016-07-12 | Scheduled Outage | Construction | Brian Brooks and Black and Mac had transformer X10628 open for pole changes. Customers notified. | None | None | 8 | 165 | 22 | West | 28F2
134102 | 2016-07-13 | Scheduled Outage | Vegetation Management | Vegetation management at 900 Rand affecting 46 customers on the Wakley (UZ11) for 4.5 hours. | None | None | 46 | 269 | 206 | East | UZ11
134103 | 2016-07-13 | Scheduled Outage | Maintenance | Sproule isolated TP10800, TP10801 & TP108023 for elbow & insert replacement. Moulton (8F3) | None | Elbow \ Insert | 33 | 166 | 91 | East | 8F3
134104 | 2016-07-13 | Scheduled Outage | Maintenance | To allow crews to replace a leaking transformer # TP7949. | None | Padmount (1ph) | 7 | 43 | 5 | East | 77M5
134105 | 2016-07-13 | Scheduled Outage | Construction | Transformer #X33875 isolated by crew for a service upgrade | None | None | 8 | 49 | 7 | Central | UC03
134107 | 2016-07-13 | Defective Equipment | Defective Equipment/ Material | Cable fault occurred from S17096 to transformer KT25 Tapiola and Greenboro Cres. Affecting 165 customers on the Ellwood ELW07 for 90 minutes. | U/G Cable | PILC | 165 | 90 | 248 | East | ELW07
134108 | 2016-07-13 | Defective Equipment | Electrical Failure | TP2992 found defective and replaced. Terry Fox (TFXF1) | U/G Transformer | Padmount (1ph) | 12 | 384 | 77 | West | TFXF1
134110 | 2016-07-13 | Lightning | Lightning | Adverse Weather (Lightning Storm going through the city) Tripped UC05 affecting 388 customers for 6 minutes. | None | None | 388 | 6 | 39 | Central | UC05
134111 | 2016-07-13 | Tree Contacts | Falling Tree | A tree fell into the O/H during a thunderstorm causing the RHNF2 & RHNF3 to trip | None | None | 3 | 274 | 14 | West | RHNF2
134111 | 2016-07-13 | Tree Contacts | Falling Tree | A tree fell into the O/H during a thunderstorm causing the RHNF2 & RHNF3 to trip | None | None | 423 | 176 | 1241 | West | RHNF3
134112 | 2016-07-13 | Lightning | Lightning | 3 phases of OH down due to lightning storm. Affecting 90 customers. Also transformer X31660 was found to be defective, affecting an additional 10 customers. | O/H Conductor | O/H Conductor | 10 | 346 | 58 | Central | SR08
134112 | 2016-07-13 | Lightning | Lightning | 3 phases of OH down due to lightning storm. Affecting 90 customers. Also transformer X31660 was found to be defective, affecting an additional 10 customers. | O/H Conductor | O/H Conductor | 100 | 201 | 335 | Central | SR08
134112 | 2016-07-13 | Lightning | Lightning | 3 phases of OH down due to lightning storm. Affecting 90 customers. Also transformer X31660 was found to be defective, affecting an additional 10 customers. | O/H Conductor | O/H Conductor | 427 | 6 | 43 | Central | SR08
134112 | 2016-07-13 | Lightning | Lightning | 3 phases of OH down due to lightning storm. Affecting 90 customers. Also transformer X31660 was found to be defective, affecting an additional 10 customers. | O/H Conductor | O/H Conductor | 427 | 103 | 733 | Central | SR08
134113 | 2016-07-13 | Scheduled Outage | Vegetation Management | Mike Van Delst to have transformer X29842 open to remove trees from wires. Customers notified. | None | None | 6 | 58 | 6 | Central | SB05
134114 | 2016-07-13 | Scheduled Outage | Maintenance | Transformer K474 was isolated to replace insulators and barriers affecting 8 customers for 3 hrs on the Edwin (UV05) | None | None | 8 | 180 | 24 | Central | UV05
134116 | 2016-07-13 | Lightning | Lightning | TR04 breaker tripped due to storm. | None | None | 967 | 5 | 81 | Central | TR1UQ
134117 | 2016-07-13 | Lightning | Lightning | Repair damaged pole and condustor, line sectionalized to restore most customers untill repair coudutors and power restored. | O/H Conductor | O/H Conductor | 79 | 326 | 429 | Central | UC05
134117 | 2016-07-13 | Lightning | Lightning | Repair damaged pole and condustor, line sectionalized to restore most customers untill repair coudutors and power restored. | O/H Conductor | O/H Conductor | 142 | 192 | 454 | Central | UC05
134117 | 2016-07-13 | Lightning | Lightning | Repair damaged pole and condustor, line sectionalized to restore most customers untill repair coudutors and power restored. | O/H Conductor | O/H Conductor | 388 | 136 | 879 | Central | UC05
134118 | 2016-07-13 | Scheduled Outage | Forced Switching | To allow Hydro Ottawa crews to replace a transformer that was struck by a vehicle & knocked off its base. | None | Padmount (1ph) | 8 | 137 | 18 | East | CYRF3
134119 | 2016-07-13 | Lightning | Lightning | Tree on the wires do to lightnig strike. Line sectionalized to restore most customers till tree removed from overhead. | O/H Conductor | O/H Conductor | 60 | 354 | 354 | East | UB05
134119 | 2016-07-13 | Lightning | Lightning | Tree on the wires do to lightnig strike. Line sectionalized to restore most customers till tree removed from overhead. | O/H Conductor | O/H Conductor | 96 | 94 | 150 | East | UB05
134119 | 2016-07-13 | Lightning | Lightning | Tree on the wires do to lightnig strike. Line sectionalized to restore most customers till tree removed from overhead. | O/H Conductor | O/H Conductor | 378 | 94 | 592 | East | UB07
134120 | 2016-07-13 | Scheduled Outage | Maintenance | To allow Sproule Electric to replace elbows & inserts on TP10797, TP10798 & TP10799. | None | Elbow \ Insert | 36 | 115 | 69 | East | 8F3
134121 | 2016-07-13 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to repair a damaged/defective switch- S1257 | None | Fused Cutout | 1 | 24 | 0 | South | EPWF5
134122 | 2016-07-13 | Adverse Weather | Extreme Wind | S29284 red and white fuses blown do to tangled conductor. Wire untangled and fuses repalced | O/H Conductor | O/H Conductor | 12 | 508 | 102 | Central | SR03
134123 | 2016-07-14 | Foreign Interference | Wildlife (Bird/Animal) | The switch 238W on Gainsford open due to animal contact with the O/H | O/H Switchgear | Fused Cutout | 29 | 96 | 46 | West | 624F6
134124 | 2016-07-14 | Scheduled Outage | Vegetation Management | S22257 to EOL was isoalted to allow crew to perfrom tree trimming at 917, 1025 and 971 Cormwell. | None | None | 43 | 370 | 265 | East | UZ03
134125 | 2016-07-14 | Scheduled Outage | Maintenance | VT303 at 2969 Fairlea was isolated to allow contractor to perfrom customer vault maintenance. Albion (2202) | None | None | 2 | 430 | 14 | East | 2202
134126 | 2016-07-14 | Scheduled Outage | Maintenance | Transformers TP10777,TP10778,TP10786 & TP10796 were isolated to allow the contractors to perform elbow and insert replacement project | None | Elbow \ Insert | 53 | 233 | 206 | East | 8F3
134127 | 2016-07-14 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X29635 TO RECONNECT TRIPLEX SERVICE | None | None | 6 | 60 | 6 | East | SO03
134128 | 2016-07-14 | Scheduled Outage | Maintenance | Isolation of Billing Bridge Transit Station to install new fuses on customer owned sub station. | None | Breaker \ Relay | 1 | 63 | 1 | Central | 503
134129 | 2016-07-14 | Lightning | Lightning | A thunder storm caused the 190F5 to A/R then trip. | None | None | 1714 | 5 | 143 | South | 190F5
134134 | 2016-07-14 | Lightning | Lightning | A thunder storm caused the UV02 breaker to A/R and trip | None | None | 260 | 2 | 9 | Central | UV02
134135 | 2016-07-14 | Adverse Weather | Extreme Wind | A broken pole top insulator has caused the 43F2 W phase to trip | Pole Attachement | Insulator | 105 | 235 | 411 | West | 43F2
134135 | 2016-07-15 | Adverse Weather | Extreme Wind | A broken pole top insulator has caused the 43F2 W phase to trip | Pole Attachement | Insulator | 322 | 99 | 531 | West | 43F2
134136 | 2016-07-14 | Tree Contacts | Broken Branch | A thunderstorm caused the UZ07 breaker to trip | None | None | 239 | 133 | 530 | East | UZ07
134137 | 2016-07-14 | Unknown/Other | Unknown | No apparent cause found at this time | None | None | 259 | 96 | 414 | East | SO02
134138 | 2016-07-14 | Lightning | Lightning | Inclement weather | O/H Transformer | O/H Transformer (1ph) | 1 | 71 | 1 | West | BECKF2
134140 | 2016-07-14 | Adverse Weather | Extreme Wind | A thunderstorm caused a tree branch to come down onto the O/H and G166B phase to blow. Hydro Ottawa on-call crews cleared the branch & restored power. | O/H Switchgear | Fused Cutout | 112 | 169 | 315 | East | LMBF5
134141 | 2016-07-14 | Adverse Weather | Extreme Wind | A thunderstorm brought a tree branch down onto the O/H and caused S13187 to open. Hydro Ottawa 24/7 crews cleared the branch and restored power | O/H Switchgear | Fused Cutout | 64 | 165 | 176 | East | TB2JP
134142 | 2016-07-14 | Lightning | Lightning | INCLEMENT WEATHER | O/H Transformer | O/H Transformer (1ph) | 13 | 245 | 53 | Central | UV02
134143 | 2016-07-14 | Lightning | Lightning | No apparent cause found. Lightning is suspected | O/H Switchgear | Fused Cutout | 1102 | 296 | 5437 | East | TB06
134143 | 2016-07-15 | Lightning | Lightning | No apparent cause found. Lightning is suspected | O/H Switchgear | Fused Cutout | 1590 | 3 | 80 | East | TB06
134144 | 2016-07-14 | Foreign Interference | Foreign Objects | CONTACT FROM VINES | O/H Transformer | O/H Transformer (1ph) | 5 | 284 | 24 | Central | TD05
134145 | 2016-07-14 | Lightning | Lightning | A thunder stormed caused conductor to come down and G60 R phase to open. Hydro Ottawa 24/7 crews could not find what caused the condcutor to break. | O/H Switchgear | Fused Cutout | 6 | 1167 | 117 | East | BLKF5
134148 | 2016-07-15 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X34223 opened up due to animal contact | O/H Switchgear | Fused Cutout | 7 | 72 | 8 | Central | TW22
134149 | 2016-07-15 | Scheduled Outage | Vegetation Management | S27544 to EOL was isoalted to allow crew to perfrom tree trimming at rear of 512 Mansfield. | None | None | 26 | 345 | 150 | East | UZ11
134150 | 2016-07-15 | Scheduled Outage | Maintenance | FAL03 from S24280 to EOL at 4378 McKenna Casey isolated to test transformers after a suspected animal contact. 1 customer affected. Fallowfield (FAL03) | None | O/H Transformer (3ph) | 1 | 93 | 2 | South | FAL03
134151 | 2016-07-15 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32130 opened up due to animal contact | O/H Switchgear | Fused Cutout | 1 | 59 | 1 | West | BECKF2
134152 | 2016-07-15 | Scheduled Outage | Maintenance | Transformer #X26950 isolated by crew to reconnect service after storm damage | None | None | 4 | 80 | 5 | East | AJ05
134153 | 2016-07-15 | Scheduled Outage | Maintenance | Transformer 7820 at 7820 Bleeks Rd. isolated for replacment due to oil leak. 1 customer affected. Munster (43F2) | U/G Transformer | Padmount (1ph) | 1 | 231 | 4 | West | 43F2
134154 | 2016-07-15 | Defective Equipment | Defective Equipment/ Material | The UB03 circuit trip due to down phase at 411 Plum Tree. Beechwood (UB03) | O/H Conductor | O/H Conductor | 56 | 316 | 295 | East | UB03
134154 | 2016-07-15 | Defective Equipment | Defective Equipment/ Material | The UB03 circuit trip due to down phase at 411 Plum Tree. Beechwood (UB03) | O/H Conductor | O/H Conductor | 594 | 98 | 970 | East | UB03
134155 | 2016-07-15 | Tree Contacts | Other Vegetation | G11R phase opened during adverse weather due to overgrown vines at X24136 27 Dunham. 46 customers affected. Moulton (8F1) | O/H Switchgear | Fused Cutout | 10 | 33 | 6 | East | 8F1
134155 | 2016-07-15 | Tree Contacts | Other Vegetation | G11R phase opened during adverse weather due to overgrown vines at X24136 27 Dunham. 46 customers affected. Moulton (8F1) | O/H Switchgear | Fused Cutout | 46 | 274 | 210 | East | 8F1
134158 | 2016-07-16 | Scheduled Outage | Vegetation Management | Transformer X27274 was isolated to permit tree trimming on service wires. 12 customers affected. Cahill AN04. | None | None | 12 | 47 | 9 | East | AN04
134159 | 2016-07-16 | Scheduled Outage | Construction | To allow crews to transfer plante to new hydro pole. | None | O/H Transformer (1ph) | 1 | 222 | 4 | West | TFXF2
134162 | 2016-07-16 | Foreign Interference | Wildlife (Bird/Animal) | Racoon made contact with trans cutout | O/H Transformer | O/H Transformer (1ph) | 10 | 104 | 17 | East | BLKF1
134163 | 2016-07-16 | Scheduled Outage | Maintenance | Vault at 400 Cumberland isolated at customer request for vault maintenance affecting 3 customers. King Edward TK4TS | None | None | 3 | 178 | 9 | Central | TK4TS
134165 | 2016-07-17 | Defective Equipment | Defective Equipment/ Material | Crews report switch S17287 blue phase flashed across the arrester. | O/H Switchgear | Fused Cutout | 40 | 93 | 62 | East | 77M2
134166 | 2016-07-17 | Tree Contacts | Broken Branch | TREE AT 150 BASELINE FELL AND TORE DOWN SERVICE AND S/P had to disconnect service | Secondary \ Service | O/H Service | 12 | 10 | 2 | Central | AK02
134167 | 2016-07-17 | Foreign Interference | Wildlife (Bird/Animal) | CYRF3 circuit auto reclosed and RX2022 locked out. 3965 Customers experienced a momentory outage, and 463 remain out due to the outage on RX2022. | O/H Switchgear | Recloser (3ph) | 463 | 59 | 455 | East | CYRF3
134168 | 2016-07-18 | Scheduled Outage | Maintenance | Elbow and insert replacement. | None | Padmount (1ph) | 36 | 242 | 145 | East | 8F3
134169 | 2016-07-18 | Scheduled Outage | Maintenance | Secondary Maintenance | None | Kiosk (3ph) | 1 | 19 | 0 | West | BRDF3
134170 | 2016-07-18 | Foreign Interference | Crane | MVA, a crane made contact with a pole, breaking the pole. 59 customers affected. Limebank 7F4. S11479W opened to make repairs. | Pole | Pole | 59 | 217 | 213 | East | 7F4
134171 | 2016-07-18 | Scheduled Outage | Maintenance | Elbow and insert replacement. | None | Padmount (1ph) | 26 | 97 | 42 | East | 8F3
134172 | 2016-07-18 | Scheduled Outage | Vegetation Management | At 09:39am section of TW22 on Fairlawn was isolated for tree trimming at the rear of 836 Fairlawn. 30 customers affected. Woodroffe (TW22) | None | None | 30 | 265 | 132 | Central | TW22
134173 | 2016-07-18 | Scheduled Outage | Maintenance | S24150 opened to make repairs to defective switch at X32426. 20 customers affected. Woodroffe TW22. | None | None | 20 | 26 | 9 | Central | TW22
134174 | 2016-07-18 | Unknown/Other | Unknown | Crew found G308B phase opened. Overhead checked clear from G308B to EOL. | O/H Conductor | Unknown \ Other | 65 | 105 | 114 | East | 249F2
134175 | 2016-07-18 | Defective Equipment | Defective Equipment/ Material | 249f2 auto reclosed. G900B phase opened, crew patrolled from G900B to EOLand found nothing. Cause of outage remains under investigation at this time. Leitrim (249F2) | O/H Switchgear | Fused Cutout | 65 | 127 | 138 | East | 249F2
134176 | 2016-07-18 | Defective Equipment | Defective Equipment/ Material | Transformer TE1165 at 17 Tristan was isolated to allow crew to repair defective U/G cable. | U/G Cable | XLPE | 2 | 486 | 16 | South | 180F6
134177 | 2016-07-19 | Foreign Interference | Wildlife (Bird/Animal) | Not yet known. | O/H Transformer | O/H Transformer (1ph) | 5 | 65 | 5 | Central | TH11-NIU
134178 | 2016-07-19 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 20 | 344 | 115 | Central | TW18
134180 | 2016-07-19 | Scheduled Outage | Maintenance | soil remediation | None | None | 25 | 494 | 206 | Central | TH11-NIU
134181 | 2016-07-19 | Scheduled Outage | Maintenance | elbow and insert replacement on transformers TP10752, TP10753 and replace transformer TP10751 | None | None | 35 | 25 | 15 | East | 8F3
134182 | 2016-07-19 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMERS X35410, X10643 AND X10640 TO REPLACE POLES | None | None | 20 | 210 | 70 | West | 28F2
134183 | 2016-07-19 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30142 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 14 | 231 | 54 | Central | AM05
134184 | 2016-07-19 | Scheduled Outage | Construction | 2 transformers, X10648 and X10653 isolated by crew for pole replacement | None | None | 12 | 270 | 54 | West | 28F3
134185 | 2016-07-19 | Scheduled Outage | Maintenance | REPLACE DEFECTIVE TRANSFORMER | None | O/H Transformer (1ph) | 1 | 250 | 4 | East | AL03
134186 | 2016-07-19 | Scheduled Outage | Maintenance | SERVICE UPGRADE | None | None | 2 | 149 | 5 | East | UG10
134187 | 2016-07-20 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 28 | 323 | 151 | Central | TD06
134189 | 2016-07-20 | Scheduled Outage | Maintenance | planned outage to change a leaker | None | None | 12 | 95 | 19 | East | 77M6
134192 | 2016-07-20 | Scheduled Outage | Maintenance | planned outage for elbow and insert replacement | None | None | 41 | 282 | 193 | East | 8F3
134193 | 2016-07-20 | Scheduled Outage | Construction | to re-insulate, and restring private line. | None | None | 1 | 328 | 5 | South | FAL03
134195 | 2016-07-20 | Defective Equipment | Electrical Failure | At 11:55pm customers called to report an outage on X48254 affecting 20 customers. On-Call crews replaced a defective transformer. Woodroffe (TW12). | O/H Transformer | O/H Transformer (1ph) | 20 | 356 | 119 | Central | TW18
134196 | 2016-07-21 | Scheduled Outage | Maintenance | Secondary cable installation by contractor affecting 31 customers on the TO2AP out of Overbrook for 5 hours and 15 minutes. | None | None | 31 | 315 | 163 | East | TO2AP
134197 | 2016-07-21 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X47364 TO TRANSFER LOAD TO NEW TRANSFORMER DUE TO LOW VOLTAGE ISSUES | None | None | 12 | 60 | 12 | Central | UX09
134198 | 2016-07-21 | Scheduled Outage | Construction | Replace S/W and triplex service | None | None | 6 | 45 | 4 | South | EPWF1
134199 | 2016-07-21 | Scheduled Outage | Maintenance | 3 transformers isolated for elbow and insert replacement. Moulton (8F3) | U/G Transformer | Kiosk (1ph) | 28 | 156 | 73 | East | 8F3
134200 | 2016-07-21 | Scheduled Outage | Maintenance | Two transformers isolate to replace elbows and insert. Moulton (8F3) | U/G Transformer | Kiosk (1ph) | 36 | 118 | 71 | East | 8F3
134201 | 2016-07-21 | Scheduled Outage | Vegetation Management | Overhead section at 364 Holland isolated for tree trimming affecting 14 customers. Holland SH04 | None | None | 14 | 226 | 53 | Central | SH04
134202 | 2016-07-21 | Scheduled Outage | Maintenance | Disconnect damaged secondary | None | None | 19 | 30 | 10 | East | AE07
134203 | 2016-07-21 | Scheduled Outage | Maintenance | Reconnect repaired secondary service | None | None | 19 | 34 | 11 | East | AE07
134205 | 2016-07-21 | Unknown/Other | Unknown | UZ06 tripped for no apparent reason affecting 654 customers out of Walkley Sub for 12 minutes. | None | None | 654 | 13 | 142 | East | UZ06
134207 | 2016-07-22 | Scheduled Outage | Maintenance | S12137 to eol was isolated to allow crews replaced defective insulators Munster (43F2) | None | Insulator | 31 | 60 | 31 | West | 43F2
134208 | 2016-07-22 | Scheduled Outage | Vegetation Management | Opened X27198 on the TB15 to remove tree branches from open bus. | None | None | 15 | 20 | 5 | East | TB15
134211 | 2016-07-22 | Defective Equipment | Electrical Failure | Defective transformer TP8606 located at 10 Innesbrook Crt, was replaced. | U/G Transformer | Padmount (1ph) | 16 | 402 | 107 | West | JKGF5
134212 | 2016-07-22 | Lightning | Lightning | blown lighning arrestor, lighning in the area at the time of outage | Pole Attachement | Arrester | 1 | 208 | 3 | West | 43F2
134213 | 2016-07-22 | Lightning | Lightning | lightning in the area, crew refused transformer | None | None | 1 | 220 | 4 | West | 43F2
134214 | 2016-07-22 | Defective Equipment | Electrical Failure | Not yet known. | O/H Transformer | O/H Transformer (1ph) | 14 | 138 | 32 | Central | TW18
134215 | 2016-07-23 | Lightning | Lightning | lightning strike cause all three fuses at switch s16262 to open. | O/H Switchgear | Fused Cutout | 1 | 116 | 2 | West | 43F2
134216 | 2016-07-23 | Foreign Interference | Wildlife (Bird/Animal) | TA07 CB tripped due animal contact at VT896 primary incommers at 9 Lindbergh. Albion (2211) | Customer Owned | Customer-Owned | 1 | 758 | 13 | East | 2211
134216 | 2016-07-23 | Foreign Interference | Wildlife (Bird/Animal) | TA07 CB tripped due animal contact at VT896 primary incommers at 9 Lindbergh. Albion (2211) | Customer Owned | Customer-Owned | 2812 | 76 | 3562 | East | 2211
134217 | 2016-07-24 | Foreign Interference | Wildlife (Bird/Animal) | The TR09 CB A/R and transformer X29817 opened due to animal contact. | O/H Switchgear | Fused Cutout | 8 | 158 | 21 | Central | TR09
134218 | 2016-07-24 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X29817 opened up due to animal contact | O/H Switchgear | Fused Cutout | 8 | 77 | 10 | Central | TR09
134219 | 2016-07-24 | Scheduled Outage | Construction | Transformer #X56109 isolated by crew to transfer plant | None | None | 2 | 382 | 13 | West | JKGF5
134220 | 2016-07-24 | Scheduled Outage | Construction | Transformer #X56106 isolated by crew to transfer plant | None | None | 3 | 584 | 29 | West | JKGF5
134221 | 2016-07-24 | Lightning | Lightning | Lightning | Customer Owned | Customer-Owned | 1 | 179 | 3 | West | BECKF2
134222 | 2016-07-25 | Foreign Interference | Wildlife (Bird/Animal) | An animal contact with the O/H which caused G739R to open | O/H Switchgear | Fused Cutout | 168 | 64 | 179 | East | 4801F8
134223 | 2016-07-25 | Lightning | Lightning | The TB02 and TB09 tripped during the lightning storm, crew patrolled circuit and found the pot head at VT81 on the 5307-L10 switch blown. | Vault Equipment | Connector | 8 | 10 | 1 | East | 5307
134223 | 2016-07-25 | Lightning | Lightning | The TB02 and TB09 tripped during the lightning storm, crew patrolled circuit and found the pot head at VT81 on the 5307-L10 switch blown. | Vault Equipment | Connector | 9 | 7 | 1 | East | 5307
134223 | 2016-07-25 | Lightning | Lightning | The TB02 and TB09 tripped during the lightning storm, crew patrolled circuit and found the pot head at VT81 on the 5307-L10 switch blown. | Vault Equipment | Connector | 10 | 8 | 1 | East | 5307
134223 | 2016-07-25 | Lightning | Lightning | The TB02 and TB09 tripped during the lightning storm, crew patrolled circuit and found the pot head at VT81 on the 5307-L10 switch blown. | Vault Equipment | Connector | 11 | 53 | 10 | East | 5307
134223 | 2016-07-25 | Lightning | Lightning | The TB02 and TB09 tripped during the lightning storm, crew patrolled circuit and found the pot head at VT81 on the 5307-L10 switch blown. | Vault Equipment | Connector | 138 | 10 | 23 | East | 5306
134224 | 2016-07-25 | Scheduled Outage | Vegetation Management | S24227 to EOL was isolated to allow crew to perfrom tree trimming at 3385 riverside. Walkley (UZ12) | None | None | 16 | 349 | 93 | East | UZ12
134226 | 2016-07-25 | Scheduled Outage | Construction | install new cable sections from TP11144, and replace submersible xfmr TP11144 with padmount. | None | None | 30 | 310 | 155 | East | BLKF3
134227 | 2016-07-25 | Lightning | Lightning | During the lightning storm the R1-F at VT960 at 920 tripped open. Crew refused the R1-F and all power was restored. Russell (TB14) | Vault Equipment | Breaker \ Relay | 6 | 539 | 54 | East | TB14
134228 | 2016-07-25 | Scheduled Outage | Maintenance | X33921 REPLACED HOT LINE CLAMP AND SWITCH | None | None | 10 | 60 | 10 | Central | UV05
134229 | 2016-07-25 | Scheduled Outage | Construction | re-insulate, and re-string overhead line fed from from S21804. | None | None | 2 | 121 | 4 | South | FAL03
134230 | 2016-07-25 | Lightning | Lightning | VT81 at 869 Belfast was isoalted to allow contractor to make temporary repairs to the defective switch 5307-L10 and make safe. | Vault Equipment | Switch | 1 | 175 | 3 | East | 5307
134231 | 2016-07-25 | Scheduled Outage | Construction | to transfer leads to new pole X45338. | None | None | 2 | 277 | 9 | South | 140F4
134233 | 2016-07-26 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry crews to trim trees in the rear of 74 Merrit | None | None | 40 | 330 | 220 | Central | SR02
134234 | 2016-07-26 | Scheduled Outage | Maintenance | To allow Hydro Ottawa line crews to change a leaky U/G transformer. | None | Padmount (3ph) | 12 | 104 | 21 | West | TFXF1
134235 | 2016-07-26 | Scheduled Outage | Construction | 8kV transfomrers TP11141, TP11142, TP11143 and TP3176 on Glenn Park isolated for cable replacement. 71 customers affected. Blackburn (BLKF3) | None | None | 71 | 291 | 344 | East | BLKF3
134236 | 2016-07-26 | Scheduled Outage | Construction | TD01 from S12403 to EOL on Hillcrest isolated to move line tap from W phase to B phase. 17 customers affected. Lincoln Heights (TD01) | None | Hot-Line Clamp | 17 | 104 | 29 | Central | TD01
134237 | 2016-07-26 | Scheduled Outage | Construction | REPLACE PCB TRANS | None | None | 6 | 140 | 14 | South | 180F3
134238 | 2016-07-26 | Scheduled Outage | Construction | PCB TRANS REPLACEMENT | None | None | 5 | 73 | 6 | South | 180F4
134239 | 2016-07-26 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa crews to remove a tree from the O/H. | None | None | 10 | 193 | 32 | West | TFXF1
134240 | 2016-07-26 | Defective Equipment | Mechanical Failure | a blown arrestor at X14555 caused G435 R to open. | Pole Attachement | Arrester | 0 | 4 | 0 | East | 4801F8
134240 | 2016-07-26 | Defective Equipment | Mechanical Failure | a blown arrestor at X14555 caused G435 R to open. | Pole Attachement | Arrester | 7 | 53 | 6 | East | 4801F8
134240 | 2016-07-26 | Defective Equipment | Mechanical Failure | a blown arrestor at X14555 caused G435 R to open. | Pole Attachement | Arrester | 70 | 70 | 82 | East | 4801F8
134241 | 2016-07-27 | Scheduled Outage | Construction | TP10852, TP10853 and TP10854 on Stonehenge Cres. isolated for elbow and insert replacment. 29 customers affected. Moulton (8F3) | None | Elbow \ Insert | 29 | 165 | 80 | East | 8F3
134242 | 2016-07-27 | Scheduled Outage | Vegetation Management | 4kV overhead circuit from S28149 to EOL at 131 Mountbatten at isolated for tree trimming. 15 customers affected. Queens (UQ03) | None | O/H Conductor | 15 | 204 | 51 | East | UQ03
134243 | 2016-07-27 | Scheduled Outage | Construction | K108 at 3445 Uplands isolated to replace kiosk. 16 customers affected. McCarthy (AQ06) | None | Kiosk (1ph) | 16 | 251 | 67 | East | AQ06
134244 | 2016-07-27 | Scheduled Outage | Construction | TP4911 at McBean and Main isolated to re arrange cables on poles. 1 customer affected. Richmond South (28F2) | None | None | 1 | 82 | 1 | West | 28F2
134245 | 2016-07-27 | Scheduled Outage | Construction | V113, V107 and V108 at 1465 Baseline isolated to install new primary cable. 1 customer affected. Fisher (AK06) | None | PILC | 1 | 211 | 4 | Central | AK06
134246 | 2016-07-27 | Scheduled Outage | Maintenance | Changed transformer switch on X34720 | None | None | 9 | 158 | 24 | Central | UC05
134247 | 2016-07-27 | Scheduled Outage | Maintenance | REPLACE DEFECTIVE TRANS CUTOUT | None | O/H Transformer (1ph) | 3 | 70 | 4 | East | 4801F8
134248 | 2016-07-27 | Scheduled Outage | Maintenance | To allow Hydro Ottawa line crews to replace primary cables | None | PILC | 14 | 237 | 55 | East | BLKF3
134249 | 2016-07-27 | Scheduled Outage | Forced Switching | Burnt terminations at S21787 RWB & S15151 RWB | None | Termination \ Stress Cone | 268 | 47 | 210 | East | BCHF4
134250 | 2016-07-27 | Scheduled Outage | Construction | TP10850 and TP10851 on Stonehenge isolated for elbow and insert replacment. 26 customers affected. Moulton (8F3) | None | Elbow \ Insert | 26 | 148 | 64 | East | 8F3
134251 | 2016-07-27 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to commissiona new trunk extension for Trans-Canada pole line | None | None | 1 | 350 | 6 | West | TFXF5
134253 | 2016-07-27 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X31942 (ANIMAL CONTACT RACOON) | O/H Transformer | O/H Transformer (1ph) | 13 | 148 | 32 | Central | TD14
134254 | 2016-07-28 | Scheduled Outage | Maintenance | TP2302 isolated for transformer bus isolation to allow contractor to perform secondary vault mtce. | None | Padmount (1ph) | 1 | 33 | 1 | Central | SB16
134256 | 2016-07-28 | Scheduled Outage | Construction | Elbow and insert replacement. | None | None | 40 | 233 | 155 | East | 8F3
134257 | 2016-07-28 | Defective Equipment | Imminent Equipment Failure Detected | transformer 9458 will be replace and soil remediation, and cutouts replaced on switch S24423. | None | None | 1 | 547 | 9 | West | 43F2
134258 | 2016-07-28 | Scheduled Outage | Construction | planned outage to decommission TV113 and energize new TP10949 | None | None | 41 | 211 | 144 | Central | UD08
134259 | 2016-07-28 | Defective Equipment | Mechanical Failure | Cable fault between 299W and 2529W | U/G Cable | Unknown \ Other | 59 | 45 | 44 | West | BRDF5
134259 | 2016-07-28 | Defective Equipment | Mechanical Failure | Cable fault between 299W and 2529W | U/G Cable | Unknown \ Other | 812 | 44 | 595 | West | BRDF5
134259 | 2016-07-28 | Defective Equipment | Mechanical Failure | Cable fault between 299W and 2529W | U/G Cable | Unknown \ Other | 871 | 2 | 29 | West | BRDF5
134259 | 2016-07-28 | Defective Equipment | Mechanical Failure | Cable fault between 299W and 2529W | U/G Cable | Unknown \ Other | 871 | 33 | 479 | West | BRDF5
134260 | 2016-07-28 | Scheduled Outage | Construction | Replace submersible transformer with a pad mount. | None | None | 15 | 251 | 63 | East | BLKF3
134261 | 2016-07-28 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 32 | 325 | 173 | Central | 505
134262 | 2016-07-28 | Defective Equipment | Electrical Failure | CABLE FAULT | U/G Cable | Unknown \ Other | 14 | 127 | 30 | East | AN05
134262 | 2016-07-28 | Defective Equipment | Electrical Failure | CABLE FAULT | U/G Cable | Unknown \ Other | 27 | 115 | 52 | East | AN05
134263 | 2016-07-28 | Scheduled Outage | Vegetation Management | tree about to fall on overhead wires, tree crew required a crane to remove the tree. | None | None | 25 | 63 | 26 | Central | AK02
134265 | 2016-07-29 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 32 | 341 | 182 | Central | TW22
134267 | 2016-07-29 | Scheduled Outage | Maintenance | SERVICE UPGRADES OUT OF X32090 ON THE UL04 | None | None | 10 | 84 | 14 | Central | UL04
134270 | 2016-07-29 | Defective Equipment | Mechanical Failure | to replace a defective cutout on a three phase bank X21117. | O/H Switchgear | Fused Cutout | 5 | 18 | 2 | East | V11F1
134272 | 2016-07-30 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X13956 | O/H Transformer | O/H Transformer (1ph) | 13 | 109 | 24 | East | LTM04
134273 | 2016-07-31 | Defective Equipment | Electrical Failure | Secondary undergorund service feeding 49 Okanagan faulted, repaired by on-call crew. 1 customer affected. Queensway Carleton (160F4) | Secondary \ Service | U/G Service | 1 | 861 | 14 | South | 160F4
134274 | 2016-08-01 | Defective Equipment | Mechanical Failure | A cable fault on the 77M1 circuit between S23450 R and TP7028 caused S23450 R to blow, resulting in an outage to TP7028, TE1006 & TE1007, affecting 36 customers. | U/G Cable | PILC | 36 | 124 | 74 | East | 77M1
134275 | 2016-08-01 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X14029 | O/H Transformer | O/H Transformer (1ph) | 2 | 69 | 2 | East | 7F2
134276 | 2016-08-01 | Tree Contacts | Broken Branch | Branch on the overhead primary behind 1478 Orchard caused the inline recloser to auto then trip affecting 498 customers. Russell TB2JP | None | None | 498 | 40 | 332 | East | TB2JP
134277 | 2016-08-01 | Unknown/Other | Unknown | 160F3 patrolled and nothing was found that caused breaker to trip out of Queensway Carleton affecting 26 customers. | Unknown \ Other | Unknown \ Other | 26 | 16 | 7 | South | 160F3
134278 | 2016-08-01 | Foreign Interference | Wildlife (Bird/Animal) | Raccoon contact | O/H Conductor | Unknown \ Other | 7 | 70 | 8 | Central | TR1UQ
134278 | 2016-08-01 | Foreign Interference | Wildlife (Bird/Animal) | Raccoon contact | O/H Conductor | Unknown \ Other | 91 | 38 | 58 | East | UQ04
134278 | 2016-08-01 | Foreign Interference | Wildlife (Bird/Animal) | Raccoon contact | O/H Conductor | Unknown \ Other | 967 | 32 | 516 | Central | TR1UQ
134279 | 2016-08-02 | Unknown/Other | Unknown | the MWDF2 breaker tripped twice. Circuit patrolled, all devices inspected. Circuit restored to normal without finding a cause. | None | None | 281 | 38 | 178 | West | MWDF2
134279 | 2016-08-02 | Unknown/Other | Unknown | the MWDF2 breaker tripped twice. Circuit patrolled, all devices inspected. Circuit restored to normal without finding a cause. | None | None | 281 | 89 | 417 | West | MWDF2
134279 | 2016-08-02 | Unknown/Other | Unknown | the MWDF2 breaker tripped twice. Circuit patrolled, all devices inspected. Circuit restored to normal without finding a cause. | None | None | 651 | 2 | 22 | West | MWDF2
134279 | 2016-08-02 | Unknown/Other | Unknown | the MWDF2 breaker tripped twice. Circuit patrolled, all devices inspected. Circuit restored to normal without finding a cause. | None | None | 651 | 31 | 336 | West | MWDF2
134279 | 2016-08-02 | Unknown/Other | Unknown | the MWDF2 breaker tripped twice. Circuit patrolled, all devices inspected. Circuit restored to normal without finding a cause. | None | None | 1488 | 22 | 546 | West | MWDF2
134280 | 2016-08-02 | Scheduled Outage | Construction | Remove old overhead conductor. | None | None | 5 | 249 | 21 | South | FAL03
134281 | 2016-08-02 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 9 | 90 | 14 | West | BRDF3
134286 | 2016-08-03 | Scheduled Outage | Maintenance | At 9:07am TP11452 was isolated to allow for soil remediation. 25 customers affected. Hinchey (TH11) | None | None | 25 | 576 | 240 | Central | TH11-NIU
134287 | 2016-03-08 | Loss Of Supply | Transmission Inadvertent | Blown lightning arrester on Nepean T4. | None | None | 0 | 213120 | 0 | South | 22M24
134287 | 2016-08-03 | Loss Of Supply | Transmission Inadvertent | Blown lightning arrester on Nepean T4. | None | None | 2957 | 8 | 394 | South | 22M28
134287 | 2016-08-03 | Loss Of Supply | Transmission Inadvertent | Blown lightning arrester on Nepean T4. | None | None | 3346 | 8 | 446 | South | 22M25
134287 | 2016-08-03 | Loss Of Supply | Transmission Inadvertent | Blown lightning arrester on Nepean T4. | None | None | 4197 | 8 | 560 | South | 22M23
134287 | 2016-08-03 | Loss Of Supply | Transmission Inadvertent | Blown lightning arrester on Nepean T4. | None | None | 5773 | 8 | 770 | South | 22M26
134287 | 2016-08-03 | Loss Of Supply | Transmission Inadvertent | Blown lightning arrester on Nepean T4. | None | None | 9662 | 8 | 1288 | South | 22M27
134288 | 2016-08-03 | Unknown/Other | Unknown | no cause found | None | None | 18 | 76 | 23 | East | UT06
134289 | 2016-08-04 | Defective Equipment | Electrical Failure | defective transforemr in V390 | Vault Equipment | Transformer | 29 | 75 | 36 | East | AE05
134290 | 2016-08-04 | Foreign Interference | Crane | Temporary customer owned overhead on Parliament Hill contacted by construction crane caused TL23 circuit breaker to open. 9 customers affected. Lisgar (5203) | Customer Owned | Customer-Owned | 9 | 44 | 7 | Central | 5203
134291 | 2016-08-04 | Scheduled Outage | Construction | Hydro Ottawa line crews opened transformer X41776 to reconfigure secondary O/H conductor | None | None | 40 | 75 | 50 | Central | AH14
134293 | 2016-08-04 | Scheduled Outage | Vegetation Management | To allow a contractor to trim trees for the NCC | None | None | 1 | 400 | 7 | South | 180F4
134294 | 2016-08-04 | Scheduled Outage | Maintenance | Customer vault maintenance performed by contractor. | None | None | 1 | 76 | 1 | Central | 409
134295 | 2016-08-04 | Scheduled Outage | Construction | V271 at 99 Cartier isolated to allow crews to re arrange overhead for construction clearance. 67 customers affected. Gladestone (UX02) | None | O/H Conductor | 67 | 89 | 99 | Central | UX02
134297 | 2016-08-05 | Defective Equipment | Mechanical Failure | A cable fault on the 77M6 blue phase between TE912 & TE913 caused S26061 B phase fuse to blow. Also, tranformer TE994 faulted upon restoration of the cable fault. 10 customers affected by the transformer | U/G Cable | PILC | 10 | 374 | 62 | East | 77M6
134297 | 2016-08-05 | Defective Equipment | Mechanical Failure | A cable fault on the 77M6 blue phase between TE912 & TE913 caused S26061 B phase fuse to blow. Also, tranformer TE994 faulted upon restoration of the cable fault. 10 customers affected by the transformer | U/G Cable | PILC | 90 | 91 | 136 | East | 77M6
134297 | 2016-08-05 | Defective Equipment | Mechanical Failure | A cable fault on the 77M6 blue phase between TE912 & TE913 caused S26061 B phase fuse to blow. Also, tranformer TE994 faulted upon restoration of the cable fault. 10 customers affected by the transformer | U/G Cable | PILC | 101 | 44 | 74 | East | 77M6
134297 | 2016-08-05 | Defective Equipment | Mechanical Failure | A cable fault on the 77M6 blue phase between TE912 & TE913 caused S26061 B phase fuse to blow. Also, tranformer TE994 faulted upon restoration of the cable fault. 10 customers affected by the transformer | U/G Cable | PILC | 264 | 157 | 691 | East | 77M6
134298 | 2016-08-05 | Tree Contacts | Other Vegetation | VINES IN THE TRANSFORMER | O/H Transformer | O/H Transformer (1ph) | 15 | 150 | 38 | Central | TR3UY
134299 | 2016-08-05 | Foreign Interference | Wildlife (Bird/Animal) | SQUIRREL CONTACT | O/H Transformer | O/H Transformer (1ph) | 8 | 90 | 12 | Central | TD12
134300 | 2016-08-05 | Scheduled Outage | Vegetation Management | MC2069 opened at 6249 Ottawa street Richmond to allow for tree removal. | None | None | 22 | 181 | 66 | West | 28F2
134301 | 2016-08-05 | Scheduled Outage | Maintenance | To allow for soil remediation | None | None | 10 | 69 | 12 | West | TFXF1
134303 | 2016-08-05 | Tree Contacts | Broken Branch | Tree branch fell and broke 2 conductors at the rear of 2242 Quinton. Circuit interrupted to isolate the broken section. 370 customers affected. Playfair (AJ03) | O/H Conductor | O/H Conductor | 40 | 49 | 33 | East | AJ03
134303 | 2016-08-05 | Tree Contacts | Broken Branch | Tree branch fell and broke 2 conductors at the rear of 2242 Quinton. Circuit interrupted to isolate the broken section. 370 customers affected. Playfair (AJ03) | O/H Conductor | O/H Conductor | 100 | 372 | 620 | East | AJ03
134303 | 2016-08-05 | Tree Contacts | Broken Branch | Tree branch fell and broke 2 conductors at the rear of 2242 Quinton. Circuit interrupted to isolate the broken section. 370 customers affected. Playfair (AJ03) | O/H Conductor | O/H Conductor | 370 | 21 | 130 | East | AJ03
134304 | 2016-08-05 | Adverse Weather | Extreme Wind | UZ06 CB opened when strong wind gusts caused conductor along Railroad ROW on Walkey road to wrap together. 654 customers affected. Walkey (UZ06) | O/H Conductor | O/H Conductor | 654 | 77 | 839 | East | UZ06
134305 | 2016-08-05 | Tree Contacts | Tree Growth/ Untrimmed Tree | At 6:03 tree contact caused the UZ06 circuit to trip and causing conductors to wrap together. 654 customers affected. Walkley (UZ06) ID#134305 | None | None | 654 | 160 | 1744 | East | UZ06
134306 | 2016-08-05 | Tree Contacts | Tree Growth/ Untrimmed Tree | G60 opened up due to tree contact | O/H Switchgear | Inline Switch | 6 | 309 | 31 | East | BLKF5
134307 | 2016-08-05 | Defective Equipment | Mechanical Failure | Defective switch at S26621 replaced. | O/H Switchgear | Fused Cutout | 1 | 55 | 1 | East | 77M2
134308 | 2016-08-06 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact | O/H Transformer | O/H Transformer (1ph) | 196 | 82 | 268 | East | 7F2
134309 | 2016-08-06 | Defective Equipment | Mechanical Failure | Cable fault. | U/G Cable | XLPE | 13 | 57 | 12 | West | 39F3
134309 | 2016-08-06 | Defective Equipment | Mechanical Failure | Cable fault. | U/G Cable | XLPE | 61 | 212 | 216 | West | 39F3
134313 | 2016-08-07 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X24654 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 6 | 108 | 11 | East | TB14
134316 | 2016-08-08 | Scheduled Outage | Vegetation Management | TREE TRIMMING | None | None | 1 | 157 | 3 | West | RHNF3
134317 | 2016-08-08 | Foreign Interference | Vehicle | Construction worker made contact with the neutral, shook the lines and the phases slapped together. No damage to the hydro plant, but there was an unstable pole that the crews attached a down guy to. DTP WO# 200706. 1 service feeding 12 customers remains | Pole Attachement | Ground | 12 | 373 | 75 | East | UB06
134317 | 2016-08-08 | Foreign Interference | Vehicle | Construction worker made contact with the neutral, shook the lines and the phases slapped together. No damage to the hydro plant, but there was an unstable pole that the crews attached a down guy to. DTP WO# 200706. 1 service feeding 12 customers remains | Pole Attachement | Ground | 524 | 73 | 638 | East | UB06
134318 | 2016-08-08 | Defective Equipment | Corrosion | REPLACE LEAKING TRANSFORMER | O/H Transformer | O/H Transformer (1ph) | 8 | 135 | 18 | Central | SB11
134319 | 2016-08-09 | Foreign Interference | Wildlife (Bird/Animal) | GR2 W opened due to animal contact at 4233 Rideau Valley Rd. 494 customers affected. Limebank (LMBF5) | O/H Transformer | O/H Transformer (1ph) | 4 | 166 | 11 | East | LMBF5
134319 | 2016-08-09 | Foreign Interference | Wildlife (Bird/Animal) | GR2 W opened due to animal contact at 4233 Rideau Valley Rd. 494 customers affected. Limebank (LMBF5) | O/H Transformer | O/H Transformer (1ph) | 494 | 29 | 239 | East | LMBF5
134320 | 2016-08-09 | Scheduled Outage | Construction | Transformer X25746 at 87 Pamilla St. isolated to run new secondary service. 4 customers affected. Bronson (SB10) | None | O/H Service | 10 | 83 | 14 | Central | SB10
134322 | 2016-08-09 | Scheduled Outage | Construction | Transformer #X34695 isolated by crew to run a new service | None | None | 6 | 60 | 6 | Central | UL14
134323 | 2016-08-09 | Scheduled Outage | Construction | Transformer #X33371 isolated by crew to remove a service | None | None | 9 | 14 | 2 | South | EPWF3
134324 | 2016-08-09 | Foreign Interference | Vehicle | Garbage Truck has come in contact with the UG10 and UG11 O/H wires at 320 Chrichton. Restoration was delayed due to MOL restriction. | O/H Conductor | O/H Conductor | 221 | 78 | 287 | East | UG11
134324 | 2016-08-09 | Foreign Interference | Vehicle | Garbage Truck has come in contact with the UG10 and UG11 O/H wires at 320 Chrichton. Restoration was delayed due to MOL restriction. | O/H Conductor | O/H Conductor | 418 | 78 | 543 | East | UG10
134325 | 2016-08-09 | Scheduled Outage | Vegetation Management | A tree contractor trim the trees in the rear of 321 Mountbatten | None | Unknown \ Other | 27 | 97 | 44 | East | TB06
134326 | 2016-08-09 | Scheduled Outage | Maintenance | VT693 @ 379 Gilmour was isolated to allow the contractor perform vault maintenance. | Vault Equipment | Breaker \ Relay | 1 | 189 | 3 | Central | TL7TS
134327 | 2016-08-09 | Scheduled Outage | Construction | Transformer #X31848 isolated by crew to replace broken switch | None | None | 6 | 60 | 6 | Central | UL06
134328 | 2016-08-09 | Scheduled Outage | Construction | Transformer #X33371 isolated by crew to reconnect service | None | None | 9 | 29 | 4 | South | EPWF3
134329 | 2016-08-09 | Defective Equipment | Electrical Failure | Defective lighting arrestor at K833 cause WSC10 W phase fuse to open at 3344 Uplands Dr. 74 customers affected. McCarthy (AQ08) | U/G Cable Attachement | Arrester | 74 | 49 | 60 | East | AQ08
134330 | 2016-08-09 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact caused primary R phase fuse at 1530 Clementine to open. 34 customers affected. Riverdale (505) | O/H Conductor | O/H Conductor | 34 | 60 | 34 | Central | 505
134331 | 2016-08-10 | Scheduled Outage | Vegetation Management | Hydro Ottwa line crews isolated the UB04 circuit from S23864 to E.O.L to allow forestry to clear trees that are encroaching on the O/H power line. | None | None | 13 | 208 | 45 | East | UB04
134332 | 2016-08-10 | Scheduled Outage | Maintenance | Vault VT729 @ 300 Wiggins was isolated to allow the contractor perform vault maintenance | None | Breaker \ Relay | 124 | 144 | 298 | Central | TR1UN
134333 | 2016-08-10 | Scheduled Outage | Construction | Transformer #X35198 isolated by crew to hook up 2 new services | None | None | 10 | 60 | 10 | Central | AH02
134334 | 2016-08-10 | Scheduled Outage | Maintenance | Vault VT764 @ 430 Wiggins was isolated for the contractor to allow them to preform vault naintenance | None | Breaker \ Relay | 154 | 133 | 341 | Central | TR1UN
134335 | 2016-08-10 | Scheduled Outage | Maintenance | To allow Hydro Ottawa U/G crews to repair a defective customer owned primary cable | None | Unknown \ Other | 516 | 426 | 3664 | East | UZ06
134336 | 2016-08-10 | Defective Equipment | Electrical Failure | replace defective overhead transformer X29996 | O/H Transformer | O/H Transformer (1ph) | 2 | 291 | 10 | Central | TR09
134337 | 2016-08-11 | Scheduled Outage | Construction | Replace leaking transformer. | None | None | 10 | 529 | 88 | East | 8F1
134339 | 2016-08-11 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32074 opened up due to animal contact | O/H Switchgear | Fused Cutout | 17 | 58 | 16 | Central | TD06
134340 | 2016-08-11 | Scheduled Outage | Construction | Transformer #X56919 that fed MX 2082 isolated by crew to change a blown arrestor | None | None | 1 | 10 | 0 | East | 249F2
134341 | 2016-08-11 | Scheduled Outage | Construction | Transformer #X34249 isolated by crew to run a new service | None | None | 5 | 75 | 6 | Central | SM06
134342 | 2016-08-11 | Foreign Interference | Dig-In | Dig in. | U/G Cable | Unknown \ Other | 4 | 261 | 17 | West | 24F8
134342 | 2016-08-11 | Foreign Interference | Dig-In | Dig in. | U/G Cable | Unknown \ Other | 29 | 27 | 13 | West | 24F8
134342 | 2016-08-11 | Foreign Interference | Dig-In | Dig in. | U/G Cable | Unknown \ Other | 89 | 50 | 74 | West | 24F8
134344 | 2016-08-11 | Defective Equipment | Electrical Failure | Blown pothead feeding into 1804-L2 at VT192 at 456 Mcarthur | U/G Cable Attachement | Pothead | 6 | 31 | 3 | East | 1804
134344 | 2016-08-11 | Defective Equipment | Electrical Failure | Blown pothead feeding into 1804-L2 at VT192 at 456 Mcarthur | U/G Cable Attachement | Pothead | 73 | 86 | 105 | East | 1804
134345 | 2016-08-11 | Defective Equipment | Electrical Failure | Blown Pothead at 2627 Alta Vista | U/G Cable Attachement | Pothead | 1 | 9 | 0 | East | 2201
134345 | 2016-08-11 | Defective Equipment | Electrical Failure | Blown Pothead at 2627 Alta Vista | U/G Cable Attachement | Pothead | 2 | 7 | 0 | East | 2201
134345 | 2016-08-11 | Defective Equipment | Electrical Failure | Blown Pothead at 2627 Alta Vista | U/G Cable Attachement | Pothead | 3 | 9 | 0 | East | 2201
134345 | 2016-08-11 | Defective Equipment | Electrical Failure | Blown Pothead at 2627 Alta Vista | U/G Cable Attachement | Pothead | 15 | 55 | 14 | East | 2201
134348 | 2016-08-12 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 3520 | 8 | 469 | South | FAL04
134349 | 2016-08-12 | Scheduled Outage | Construction | Transformer #X35336 isolated by crew to run a new service | None | None | 12 | 30 | 6 | Central | AD07
134350 | 2016-08-12 | Scheduled Outage | Construction | Transformer #X26268 isolated by crew to run a new service | None | None | 8 | 70 | 9 | Central | SH04
134351 | 2016-08-12 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X27082 TO REMOVE A WASPS NEST | None | None | 8 | 13 | 2 | East | TB14
134352 | 2016-08-12 | Defective Equipment | Defective Equipment/ Material | Circuit patrolled no fault found. S22204 Red phase switch found defective. Switch replaced and restored. | O/H Switchgear | Inline Switch | 80 | 96 | 128 | Central | SK10
134354 | 2016-08-12 | Defective Equipment | Defective Equipment/ Material | Cable fault between transformer TP9733 and TP9732 caused the S18955W to blow | U/G Cable | PILC | 71 | 18 | 21 | East | CYRF4
134354 | 2016-08-12 | Defective Equipment | Defective Equipment/ Material | Cable fault between transformer TP9733 and TP9732 caused the S18955W to blow | U/G Cable | PILC | 87 | 83 | 120 | East | CYRF4
134355 | 2016-08-12 | Scheduled Outage | Maintenance | Vault VT408 @ 80 Rideau St was isolated to allow the contractor to inspect the cracks in the vault floor after the sink hole was repaired | None | Unknown \ Other | 1 | 40 | 1 | Central | TK6TS
134357 | 2016-08-13 | Defective Equipment | Mechanical Failure | Blown lightning arrestor found. No other apparent cause found. | Pole Attachement | Arrester | 427 | 86 | 612 | East | UT03
134358 | 2016-08-13 | Defective Equipment | Mechanical Failure | transformer 235 was found blown off it’s base. | U/G Transformer | Padmount (3ph) | 1 | 349 | 6 | West | 624F5
134358 | 2016-08-13 | Defective Equipment | Mechanical Failure | transformer 235 was found blown off it’s base. | U/G Transformer | Padmount (3ph) | 166 | 191 | 528 | West | 624F5
134359 | 2016-08-13 | Foreign Interference | Wildlife (Bird/Animal) | O/H transformer 2694 opened due to animal contact. | O/H Switchgear | Fused Cutout | 10 | 132 | 22 | West | TFXF1
134362 | 2016-08-13 | Tree Contacts | Falling Tree | UQ04 CB opened due to broken conductor at the rear of 1548 Caledoncaused by fallen tree. 91 customers affected. Queens (UQ04) | O/H Conductor | Sleeve | 13 | 136 | 29 | East | UQ04
134362 | 2016-08-13 | Tree Contacts | Falling Tree | UQ04 CB opened due to broken conductor at the rear of 1548 Caledoncaused by fallen tree. 91 customers affected. Queens (UQ04) | O/H Conductor | Sleeve | 78 | 2 | 3 | East | UQ04
134362 | 2016-08-13 | Tree Contacts | Falling Tree | UQ04 CB opened due to broken conductor at the rear of 1548 Caledoncaused by fallen tree. 91 customers affected. Queens (UQ04) | O/H Conductor | Sleeve | 91 | 152 | 231 | East | UQ04
134364 | 2016-08-13 | Scheduled Outage | Forced Switching | Transfomrer X33841 isolated due to burning hot line clamp. 6 customers affected. Woodroffe (TW22) | None | O/H Transformer (1ph) | 9 | 145 | 22 | Central | TW22
134365 | 2016-08-13 | Tree Contacts | Falling Tree | The G806W and S12839W blew due to primary down between 4120 and 4200 Riverside caused by fallen tree. Limebank (7F2) | O/H Conductor | O/H Conductor | 22 | 329 | 121 | East | 7F2
134365 | 2016-08-13 | Tree Contacts | Falling Tree | The G806W and S12839W blew due to primary down between 4120 and 4200 Riverside caused by fallen tree. Limebank (7F2) | O/H Conductor | O/H Conductor | 196 | 54 | 176 | East | 7F2
134366 | 2016-08-13 | Scheduled Outage | Vegetation Management | X35544 at 904 Dundee isolated to allow crew to remove tree branch from secondary conductor. 15 customers affected. Linclon Heights (TD05) | None | O/H Transformer (1ph) | 15 | 29 | 7 | Central | TD05
134367 | 2016-08-13 | Defective Equipment | Defective Equipment/ Material | UG cable fault between vault VT796 and VT834 caused the TL05 circuit breaker to trip. Vault loop restoration was delayed due to mechanical failure at VT281. | U/G Cable | PILC | 295 | 424 | 2085 | Central | 5202
134367 | 2016-08-13 | Defective Equipment | Defective Equipment/ Material | UG cable fault between vault VT796 and VT834 caused the TL05 circuit breaker to trip. Vault loop restoration was delayed due to mechanical failure at VT281. | U/G Cable | PILC | 359 | 26 | 156 | Central | TL3SB
134367 | 2016-08-13 | Defective Equipment | Defective Equipment/ Material | UG cable fault between vault VT796 and VT834 caused the TL05 circuit breaker to trip. Vault loop restoration was delayed due to mechanical failure at VT281. | U/G Cable | PILC | 725 | 201 | 2429 | Central | 5202
134368 | 2016-08-13 | Defective Equipment | Defective Equipment/ Material | The S13051 B at 2865 Millstream blew due to defective switch. Limebank (7F2) | O/H Switchgear | Fused Cutout | 46 | 122 | 94 | East | 7F2
134369 | 2016-08-13 | Defective Equipment | Defective Equipment/ Material | Transformer X3890 opened due to broken cut out at 62 Steeple Hill. 145F3. | O/H Switchgear | Fused Cutout | 3 | 376 | 19 | South | 145F3
134370 | 2016-08-13 | Tree Contacts | Tree Growth/ Untrimmed Tree | tree contact | O/H Conductor | O/H Conductor | 2 | 511 | 17 | West | MWDF3
134372 | 2016-08-14 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at 1320 Amesbrooke caused TW12 CB and fuse at X48319 to open. 667 customers affected. Woodroffe (TW12) | O/H Conductor | O/H Conductor | 15 | 26 | 6 | Central | TW12
134372 | 2016-08-14 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at 1320 Amesbrooke caused TW12 CB and fuse at X48319 to open. 667 customers affected. Woodroffe (TW12) | O/H Conductor | O/H Conductor | 667 | 44 | 489 | Central | TW12
134374 | 2016-08-14 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree branch contact caused S28149 R phase to blow. | O/H Switchgear | Fused Cutout | 15 | 107 | 27 | East | UQ03
134375 | 2016-08-14 | Defective Equipment | Electrical Failure | Suspected defecrtive breaker relay caused the BLKF4 CB to open. | Station Equipment | Relay | 801 | 91 | 1215 | East | BLKF4
134376 | 2016-08-15 | Scheduled Outage | Maintenance | TP7700 leaking transformer replaced. | None | None | 14 | 73 | 17 | West | BRDF2
134377 | 2016-08-15 | Scheduled Outage | Vegetation Management | Transformer #X31397 isolated by crew for tree removal | None | None | 19 | 516 | 163 | Central | SB02
134378 | 2016-08-15 | Scheduled Outage | Construction | Transformer #X33048 isolated by crew to extend some secondary | None | None | 6 | 70 | 7 | South | 180F4
134380 | 2016-08-15 | Defective Equipment | Defective Equipment/ Material | White phase primary conductor on the ground at 125 Primrose Ave. | O/H Conductor | O/H Conductor | 305 | 52 | 264 | Central | AM05
134381 | 2016-08-15 | Defective Equipment | Electrical Failure | Cable fault between TE288 & TE289 on Orient park caused S16763 to open. | U/G Cable | XLPE | 17 | 15 | 4 | East | BLKF8
134381 | 2016-08-15 | Defective Equipment | Electrical Failure | Cable fault between TE288 & TE289 on Orient park caused S16763 to open. | U/G Cable | XLPE | 29 | 42 | 20 | East | BLKF8
134381 | 2016-08-15 | Defective Equipment | Electrical Failure | Cable fault between TE288 & TE289 on Orient park caused S16763 to open. | U/G Cable | XLPE | 90 | 54 | 81 | East | BLKF8
134383 | 2016-08-16 | Scheduled Outage | Maintenance | TP6654 isolated and replaced due to leaking oil. Richmond North DS (RHNF1) | None | Padmount (1ph) | 12 | 78 | 16 | West | RHNF1
134384 | 2016-08-16 | Scheduled Outage | Maintenance | TP10750 & TP10756 isolated for elbow & insert Upgrade. Moulton (8F3) | None | Padmount (1ph) | 22 | 557 | 204 | East | 8F3
134386 | 2016-08-16 | Adverse Weather | Extreme Wind | At 5:19pm SCADA indicated UX03 and UX05 breakers opened. 549 customers affected. Gladstone (UX03, UX05) | O/H Conductor | O/H Conductor | 187 | 72 | 224 | Central | UX02
134386 | 2016-08-16 | Adverse Weather | Extreme Wind | At 5:19pm SCADA indicated UX03 and UX05 breakers opened. 549 customers affected. Gladstone (UX03, UX05) | O/H Conductor | O/H Conductor | 362 | 72 | 434 | Central | UX05
134387 | 2016-08-16 | Adverse Weather | Extreme Wind | Circuit patrolled no cause found. | O/H Conductor | O/H Conductor | 32 | 148 | 79 | Central | 505
134388 | 2016-08-16 | Scheduled Outage | Vegetation Management | Transformer #X32861 isolated by crew to trim tree | None | None | 2 | 17 | 1 | South | 170F1
134389 | 2016-08-16 | Foreign Interference | Customer Equipment | 13KV metelclad failed at VT322 @ 865 Gladstone causing outage on TL4SB (TL3SB) | Vault Equipment | Switch | 359 | 96 | 574 | Central | TL4SB
134390 | 2016-08-17 | Defective Equipment | Mechanical Failure | Wind & rain caused secondary conductor to fail & X36656 to open. 4 customers affected. Rideau Heights 180F4. | O/H Conductor | Unknown \ Other | 4 | 55 | 4 | South | 180F4
134392 | 2016-08-17 | Scheduled Outage | Vegetation Management | crews performing tree trimming. Stafford (200f1) | None | None | 81 | 253 | 342 | South | 200F1
134394 | 2016-08-17 | Scheduled Outage | Maintenance | 90 customers affected on the Riverdale SR08 to install a new pole at Brighton and Bristol by HOL crew | None | None | 10 | 90 | 15 | Central | SR08
134394 | 2016-08-17 | Scheduled Outage | Maintenance | 90 customers affected on the Riverdale SR08 to install a new pole at Brighton and Bristol by HOL crew | None | None | 90 | 217 | 326 | Central | SR08
134395 | 2016-08-17 | Scheduled Outage | Maintenance | At 9:03am K346 was isolated to allow crews to replace it with new TP11479. 38 customers affected. Urbandale (AE07) | None | None | 38 | 189 | 120 | East | AE07
134396 | 2016-08-17 | Scheduled Outage | Maintenance | At 8:43am crews isolated K1161 at 1185 merivale to replace leaking transformer. 18 customers affected. Shillington (AD04) | None | None | 18 | 464 | 139 | Central | AD04
134397 | 2016-08-17 | Scheduled Outage | Construction | Transformer #X29675 isolated by crew to disconnect service | None | None | 12 | 15 | 3 | East | SO03
134399 | 2016-08-17 | Scheduled Outage | Maintenance | Isolation of customer owned vault to replace cracked arc snuffer by contractor. | None | None | 1 | 61 | 1 | Central | 5408
134400 | 2016-08-18 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER K00586 TO REPLACE CONNECTIONS ON THE SECONDARY BUSS | None | None | 22 | 55 | 20 | East | UA11
134401 | 2016-08-18 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER TP3897 TO REPLACE DEFECTIVE PEDESTAL | None | None | 11 | 64 | 12 | East | BCHF5
134402 | 2016-08-18 | Scheduled Outage | Maintenance | Transformer K424 @ 3266 Southgate was isolated by the crew to allow them to install new cables | None | Unknown \ Other | 14 | 110 | 26 | East | AN05
134403 | 2016-08-18 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27110 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 8 | 171 | 23 | East | TB14
134405 | 2016-08-18 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31138 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 12 | 150 | 30 | Central | UF04
134406 | 2016-08-18 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X39041 TO REPLACE DEFECTIVE SWITCH | None | None | 7 | 43 | 5 | East | SO12
134407 | 2016-08-18 | Scheduled Outage | Maintenance | Vault VT118 @ 1660 Walkley Rd was isolated to allow the contractor perform vault maintenance. | None | Breaker \ Relay | 1 | 358 | 6 | East | 2201
134409 | 2016-08-19 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER BANK X5113 (PART OUT 3 PHASE SERVICE)BIRD CONTACT | O/H Transformer | O/H Transformer (3ph) | 1 | 33 | 1 | South | 72F7
134411 | 2016-08-19 | Scheduled Outage | Maintenance | Transformer TP3538 at 395 Celtic Ridge was isolated by the crew to allow them to replace leaking transformer | None | Padmount (1ph) | 12 | 88 | 18 | West | 624F6
134412 | 2016-08-19 | Scheduled Outage | Vegetation Management | The Overhead at 558 Keenan was isolated to the tree contractor perform tree trimming | None | O/H Conductor | 55 | 208 | 191 | Central | TD01
134413 | 2016-08-20 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X39334 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 24 | 113 | 45 | Central | TR3UY
134415 | 2016-08-20 | Defective Equipment | Mechanical Failure | S991 including TE749 was isolated for clearance to replace a broken cross arm. 5 customers affected. Manordale 84F3. | Pole | Crossarm | 5 | 127 | 11 | South | 84F3
134416 | 2016-08-21 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X33756 opened up due to tree contact | O/H Switchgear | Fused Cutout | 9 | 156 | 23 | Central | TW22
134417 | 2016-08-21 | Defective Equipment | Defective Equipment/ Material | Transformer #X29474 opened up due to broken transformer cut out | O/H Switchgear | Fused Cutout | 19 | 197 | 62 | East | SO12
134418 | 2016-08-21 | Tree Contacts | Tree Growth/ Untrimmed Tree | Blue phase fused switch opened at SC66 causing outage to 75 customers. | O/H Conductor | O/H Conductor | 75 | 92 | 115 | Central | TR1UN
134419 | 2016-08-21 | Defective Equipment | Electrical Failure | Blown lightning arrestor and damaged fuses cutout at 1110 Falaise affecting 2 customers. Parkwood Hills 190F2 | Pole Attachement | Arrester | 2 | 76 | 3 | South | 190F2
134420 | 2016-08-21 | Defective Equipment | Mechanical Failure | Transformer at 99 St. Claire was found to be defective and leaking required replacement affecting 6 customers. Epworth EPWF1 | O/H Transformer | O/H Transformer (1ph) | 6 | 434 | 43 | South | EPWF1
134422 | 2016-08-22 | Adverse Weather | Extreme Wind | UX02 & UX05 breakers tripped. | None | None | 187 | 366 | 1141 | Central | UX02
134422 | 2016-08-22 | Adverse Weather | Extreme Wind | UX02 & UX05 breakers tripped. | None | None | 362 | 366 | 2208 | Central | UX05
134422 | 2016-08-22 | Adverse Weather | Extreme Wind | UX02 & UX05 breakers tripped. | None | None | 878 | 133 | 1946 | Central | UX09
134424 | 2016-08-22 | Scheduled Outage | Maintenance | Elbow and Insert replacement | None | Padmount (1ph) | 60 | 279 | 279 | East | 8F3
134425 | 2016-08-22 | Scheduled Outage | Maintenance | At 10:17am TP8307 was isolated to replace leaking transformer. 18 customers affected. Marchwood (MWDF4) | None | None | 18 | 103 | 31 | West | MWDF4
134426 | 2016-08-22 | Scheduled Outage | Construction | TP7135 at 1385 Halton isolated to upgrade & relocate transformer. Work to take 5 days to complete. 1 customer affected. Marchwood MWDF3. | None | None | 1 | 5691 | 95 | West | MWDF3
134427 | 2016-08-22 | Scheduled Outage | Construction | O/H line from S22768 isolated for voltage conversion. 5 customers affected. Fallowfield FAL03. | None | None | 5 | 75 | 6 | South | FAL03
134428 | 2016-08-22 | Scheduled Outage | Construction | ISOLATED AND REMOVED 3 TRANSFORMERS X31136, X31135, X31137 AND REPLACED THEM WITH X56412 | None | None | 26 | 234 | 101 | Central | UF04
134429 | 2016-08-23 | Scheduled Outage | Construction | planned outage for soil remediation | None | None | 14 | 422 | 98 | East | 8F3
134430 | 2016-08-23 | Scheduled Outage | Construction | planned outage to replace a leaker | None | None | 15 | 195 | 49 | East | 8F3
134431 | 2016-08-23 | Scheduled Outage | Construction | To allow crew to operate a defective switch safely. | None | None | 1 | 12 | 0 | Central | TK2AC
134433 | 2016-08-23 | Scheduled Outage | Construction | Transfer of plant to new pole. | None | None | 50 | 179 | 149 | Central | UF06
134434 | 2016-08-23 | Foreign Interference | Customer Equipment | The repair the burnt secondary cables in the base of the transformer K288 @ 381 Kintrye | Customer Owned | Customer-Owned | 24 | 471 | 188 | Central | AK04
134436 | 2016-08-24 | Scheduled Outage | Construction | planned outage to replace a leaker | None | None | 9 | 176 | 26 | East | 77M1
134437 | 2016-08-24 | Scheduled Outage | Maintenance | replace leaking transformer | U/G Transformer | Padmount (1ph) | 10 | 645 | 108 | East | 77M2
134438 | 2016-08-24 | Scheduled Outage | Maintenance | planned outage to remove a wasps nest from the transformer. Custoemrs on downview and benlea affected | None | None | 109 | 42 | 76 | South | 72F1
134440 | 2016-08-24 | Scheduled Outage | Construction | INSTALL NEW SERVICE | None | None | 9 | 120 | 18 | Central | TD05
134441 | 2016-08-24 | Scheduled Outage | Construction | Replace leaking transformer. | None | None | 1 | 442 | 7 | Central | SM02
134442 | 2016-08-25 | Scheduled Outage | Vegetation Management | Tree trimming on Woodcrest on the TB2JP out of Russell affecting 12 customers. | None | None | 12 | 206 | 41 | East | TB2JP
134443 | 2016-08-25 | Scheduled Outage | Maintenance | Transformer TN6835 isolated at 755 Industrial for contractor to perform inspection for future FIT program | None | None | 1 | 101 | 2 | East | 5306
134444 | 2016-08-25 | Scheduled Outage | Maintenance | 14 customers affected for isolation of Limebank (LMBF7) section from S18686 to EOL for circuit re-configuration on Maplehill Way for 35 minutes. | None | None | 14 | 35 | 8 | East | LMBF7
134445 | 2016-08-25 | Scheduled Outage | Maintenance | 20 customers affected on Corkstown for HOL crew to transfer blue phase load to the white phase of Bayshore 49F6 feeder. | None | None | 20 | 62 | 21 | South | 49F6
134446 | 2016-08-25 | Scheduled Outage | Maintenance | Transformer isolated at 50 Sumac to change a leaking transformer affecting 5 customers. Moulton 8F1 | None | Padmount (1ph) | 5 | 378 | 32 | East | 8F1
134447 | 2016-08-25 | Scheduled Outage | Maintenance | 7 Customers affected for 76 minutes on the Bayshore (49F6) for HOL crew to transfer plant from blue to white phase on Ararat. | None | None | 7 | 76 | 9 | South | 49F6
134448 | 2016-08-25 | Scheduled Outage | Construction | Customer at 1 Elgin was isolated for contractor to install new primary cable in the transformer bay. Slater (617) | None | None | 1 | 256 | 4 | Central | 617
134449 | 2016-08-26 | Scheduled Outage | Maintenance | Hydro Ottawa line crews isolated leaking transformer X32067 at 1771 Woodward, as the transformer had to be replaced. | None | O/H Transformer (1ph) | 3 | 40 | 2 | Central | UC06
134450 | 2016-08-26 | Scheduled Outage | Vegetation Management | Tree trimming on Windemere affecting 43 customers, Lincoln Height (TD01) | None | None | 43 | 274 | 196 | Central | TD01
134451 | 2016-08-26 | Human Element | Improper Construction/installation | New transformer installed with phases crossed caused an outage and required staged outage to restore line affecting 992 customers. Marchwood MWDF4 | None | None | 381 | 19 | 121 | West | MWDF4
134451 | 2016-08-26 | Human Element | Improper Construction/installation | New transformer installed with phases crossed caused an outage and required staged outage to restore line affecting 992 customers. Marchwood MWDF4 | None | None | 992 | 14 | 231 | West | MWDF4
134452 | 2016-08-26 | Scheduled Outage | Maintenance | Transformer at 1217 Klondike was isolated to replace a leaking transformer affecting 1 customer. Marchwood MWDF4 | None | Padmount (3ph) | 1 | 108 | 2 | West | MWDF4
134453 | 2016-08-26 | Human Element | Switching Error | TK25 (414) out of King Edward tripped when 413-L12 at VT340 was earthed thus grounding the 414 due to a switching error. VT852 at 221 Nelson was affected for 4 minutes. | None | None | 1 | 4 | 0 | Central | 414
134454 | 2016-08-26 | Scheduled Outage | Forced Switching | 3 phase transformer connected out of phase had to be removed from potential to correct the out of phase condition affecting 611 customers. Warchwood MWDF4 | None | None | 611 | 3 | 31 | West | MWDF4
134455 | 2016-08-26 | Scheduled Outage | Maintenance | Transformer X34247 in the rear of 473 Piccadilly was interrupted to replace a service on the Carling SM03 affecting 6 customers | None | None | 6 | 45 | 4 | Central | SM03
134456 | 2016-08-26 | Scheduled Outage | Maintenance | 8 customers were affected at 811 Connaught when KT0137 was isolated to perform an inspection. Lincoln (TD14) | None | None | 8 | 33 | 4 | Central | TD14
134457 | 2016-08-27 | Scheduled Outage | Maintenance | Vault VT228 @ 250 Holland Ave was isolated to allow the contractor to perform vault maintenance | None | Breaker \ Relay | 1 | 243 | 4 | Central | TH3SH
134458 | 2016-08-27 | Scheduled Outage | Construction | Transformer TE2965 at 440 Longfields was isolated to allow crew to transfer transformer form switch S7030 to switch gear SC2876-CB3 | None | None | 2 | 324 | 11 | South | FAL04
134459 | 2016-08-28 | Unknown/Other | Unknown | The Cyrville CYRF2 circuit tripped on instantaneous RW phases. Ciruit was patrolled and nothing was found | None | None | 132 | 13 | 29 | East | CYRF2
134460 | 2016-08-28 | Scheduled Outage | Maintenance | Vault VT1426 @ 240 Freil was isolated to allow the contractor perform vault maintenance | None | Breaker \ Relay | 1 | 139 | 2 | Central | 413
134462 | 2016-08-28 | Defective Equipment | Defective Equipment/ Material | Transformer X44486 opened due to defective transformer. Bayswater (UJ03) | O/H Transformer | O/H Transformer (1ph) | 22 | 209 | 77 | Central | UJ03
134463 | 2016-08-28 | Scheduled Outage | Construction | The Over head on Kent bet McLeod and Arlington was isolated to allow the contractor to install a new pole and reconfigure the UF06 and UF08 circuits | None | Pole | 190 | 562 | 1780 | Central | UF06
134464 | 2016-08-28 | Scheduled Outage | Forced Switching | Transformer X31512 at 1328 Thames was open for working clearance for crew to reconnect down phase at 1332 Thames. Carling (SM01) | None | O/H Service | 13 | 48 | 10 | Central | SM01
134465 | 2016-08-28 | Tree Contacts | Broken Branch | Tree took down secondary services. | O/H Conductor | O/H Conductor | 12 | 102 | 20 | East | SO03
134466 | 2016-08-28 | Scheduled Outage | Construction | crew replaced defective cutout feeding 4kv transformer P506. | None | Fused Cutout | 1 | 72 | 1 | Central | UL06
134467 | 2016-08-28 | Lightning | Lightning | Lightning caused the lightning arrestor at X39026 to open. | Pole Attachement | Arrester | 1 | 440 | 7 | East | TB15
134468 | 2016-08-29 | Scheduled Outage | Construction | S19629 to Eol was isoalted to allow crew to convert O/H from 8KV to 28KV. | None | None | 22 | 70 | 26 | South | FAL03
134469 | 2016-08-29 | Tree Contacts | Falling Tree | S26916 to EOL was isolated allow crew to make repairs to downed conductor due to fallen tree on primary O/H. Queens (UQ04) | O/H Conductor | O/H Conductor | 2 | 170 | 6 | East | UQ04
134470 | 2016-08-29 | Scheduled Outage | Construction | SECONDARY SERVICE UPGRADE | None | None | 6 | 72 | 7 | Central | AH14
134471 | 2016-08-29 | Unknown/Other | Unknown | The 249F1 circuit tripped under hold off. Forestry crew were clear and circuit was picked up. Circuit was patrolled and nothing was found. Leitrim (249F1) | None | None | 2918 | 10 | 486 | East | LTM01
134472 | 2016-08-29 | Scheduled Outage | Vegetation Management | The O/H on Rodney St was isolated to allow the tree contractor trim trees at the rear of 172 and 184 Rodney | None | Unknown \ Other | 17 | 313 | 89 | East | UQ07
134473 | 2016-08-30 | Foreign Interference | Wildlife (Bird/Animal) | Transformer opened at 629 Gainborough when a racoon came in contact affecting 8 customers. Lincoln Heights TD01 | None | None | 8 | 82 | 11 | Central | TD01
134475 | 2016-08-30 | Scheduled Outage | Maintenance | TE2825 isolated to allow crew to replace transformer. | None | Padmount (1ph) | 13 | 506 | 110 | East | 4801F8
134476 | 2016-08-30 | Scheduled Outage | Maintenance | Crew replaced leaking transformer TP7879. | None | Padmount (1ph) | 3 | 73 | 4 | West | MWDF3
134478 | 2016-08-30 | Scheduled Outage | Construction | REPLACED SWITCH, ARRESTER AND SECONDARY PADDLE | None | None | 17 | 35 | 10 | East | LTM04
134479 | 2016-08-31 | Scheduled Outage | Construction | Switch S14375 at 4174 Rideau Valley was isolated to allow crew to convert customer equipment to 28kV. | None | None | 1 | 32 | 1 | South | FAL03
134480 | 2016-08-31 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change a leaking transformer (TP8048) | None | Padmount (1ph) | 11 | 125 | 23 | East | 77M6
134481 | 2016-08-31 | Scheduled Outage | Construction | Switch 10103 at 4082 Rideau alley was isolated to allow crew to convert customer equipment to 28kV. | None | None | 1 | 30 | 0 | South | FAL03
134482 | 2016-08-31 | Scheduled Outage | Construction | FAL03 from S12611 to EOL at 4082 Rideau Valley was isolated to allow crew to convert customer equipment to 28kV. | None | None | 2 | 48 | 2 | South | FAL03
134483 | 2016-09-01 | Scheduled Outage | Construction | REPLACE SERVICE DROP NEAR PRIMARY LEAD | None | None | 17 | 35 | 10 | Central | TH01
134484 | 2016-09-01 | Scheduled Outage | Maintenance | replace leaking transformer TP8335. | None | Padmount (1ph) | 11 | 102 | 19 | West | MWDF3
134485 | 2016-09-01 | Scheduled Outage | Construction | TP11119 isolated to install temporary secondary service. | None | None | 1 | 308 | 5 | South | 190F6
134487 | 2016-09-01 | Scheduled Outage | Maintenance | to isolate transformer P2 to replace burning overhead switch on one phase of a three phase. | None | Fused Cutout | 3 | 53 | 3 | Central | UC02
134488 | 2016-09-01 | Scheduled Outage | Construction | Transformer #X25859 isolated by crew to cover load and transfer plant from X25858 that was isolated at 13:50 but is being removed. | None | None | 12 | 55 | 11 | Central | SB10
134489 | 2016-09-01 | Scheduled Outage | Construction | convert customer to 28KV | None | None | 1 | 39 | 1 | South | FAL03
134490 | 2016-09-01 | Scheduled Outage | Construction | convert customer to 28KV | None | None | 1 | 57 | 1 | South | FAL03
134492 | 2016-09-02 | Loss Of Supply | Transmission Inadvertent | BECKF2 cirucit was dumped by Hydro One due burning switch on the 44KV M28 circuit feeding the Beckwith DS. | None | None | 2 | 18 | 1 | West | BECKF2
134493 | 2016-09-02 | Scheduled Outage | Construction | SERVICE UPGRADE | None | None | 5 | 130 | 11 | Central | UC02
134495 | 2016-09-03 | Defective Equipment | Defective Equipment/ Material | Bad white phase termination at S21510 caused fuse to open affecting 118 customers on the CYRF3 out of Cyrville for 102 minutes. | O/H Switchgear | Fused Cutout | 118 | 102 | 201 | East | CYRF3
134497 | 2016-09-03 | Unknown/Other | Unknown | G537 RB phases found blown, patroled OH and TX padmount on the red and blue phases, no cause found. Billberry (77M6) | None | None | 136 | 144 | 326 | East | 77M6
134501 | 2016-09-06 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X33083 fuse blew due to squirrel contact. | O/H Transformer | O/H Transformer (1ph) | 3 | 58 | 3 | Central | TD07
134502 | 2016-09-06 | Scheduled Outage | Construction | A section of overhead line from S29963 was isolated for voltage conversion. 1 customer affected. Fallowfield FAL03. | None | None | 1 | 110 | 2 | South | FAL03
134503 | 2016-09-06 | Scheduled Outage | Construction | A section of overhead line from S10422 was isolated for voltage conversion. 6 customer affected. Fallowfield FAL03. | None | None | 6 | 110 | 11 | South | FAL03
134504 | 2016-09-06 | Scheduled Outage | Construction | At 8:31am TP11041 was isolated to allow crew to replace transformer and a red phase cable between TP11041 and TP11042. 13 customers affected. Merivale DS (72F1) | None | None | 13 | 374 | 81 | South | 72F1
134506 | 2016-09-07 | Scheduled Outage | Vegetation Management | Planned outage for tree removal. | None | O/H Conductor | 12 | 143 | 29 | East | TB2JP
134508 | 2016-09-07 | Scheduled Outage | Vegetation Management | Transformer #55D2D-0655 isolated by crew for tree trimming | None | None | 6 | 79 | 8 | Central | SB02
134509 | 2016-09-07 | Scheduled Outage | Construction | At 8:32am TP11049 was isolated to allow crew to replace transformer and primary cables. 29 customers affected. Merivale (72F1) | None | None | 29 | 326 | 158 | South | 72F1
134510 | 2016-09-07 | Scheduled Outage | Construction | Transformer #X12744 isolated by crew to re-arrange plant | None | None | 20 | 55 | 18 | West | TFXF1
134512 | 2016-09-07 | Scheduled Outage | Forced Switching | At 10:20am crews transferred load for planned work and due to an out of phase condition, 44 customers were affected during the duration of the switching. Richmond North (RHNF3) | None | None | 44 | 23 | 17 | West | RHNF3
134513 | 2016-09-07 | Scheduled Outage | Construction | At 6:09pm FAL03 from S15373 to EOL was isolated to allow crews to convert line from 8kv to 28kv. 1 customer affected. Fallowfield (FAL03) | None | None | 1 | 149 | 2 | South | FAL03
134514 | 2016-09-07 | Scheduled Outage | Construction | FAL03 from S27578 to EOL was isolated to allow crews to convert line from 8kv to 28kv. 1 customer affected. Fallowfield (FAL03) | None | None | 1 | 71 | 1 | South | FAL03
134515 | 2016-09-08 | Scheduled Outage | Construction | Transformer at 110 Didsbury isolated to change transformer and connect new service affecting 3 customers. Kanata 624F1 | None | None | 3 | 276 | 14 | West | 624F1
134517 | 2016-09-08 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry to clear over grown trees from the overhead lines | None | None | 12 | 176 | 35 | East | TB2JP
134518 | 2016-09-08 | Scheduled Outage | Construction | Transformer #X31471 isolated by crew to replace a service | None | None | 5 | 70 | 6 | Central | TH01
134519 | 2016-09-08 | Defective Equipment | Defective Equipment/ Material | TH04 Circuit tripped due to …. While fault finding on the 4301 circuit the TH03 also tripped when the TH04 CB was closed in. Hinchey (4301, 4303). | Customer Owned | Customer-Owned | 1 | 9 | 0 | Central | 4303
134519 | 2016-09-08 | Defective Equipment | Defective Equipment/ Material | TH04 Circuit tripped due to …. While fault finding on the 4301 circuit the TH03 also tripped when the TH04 CB was closed in. Hinchey (4301, 4303). | Customer Owned | Customer-Owned | 48 | 23 | 18 | Central | 4301
134519 | 2016-09-08 | Defective Equipment | Defective Equipment/ Material | TH04 Circuit tripped due to …. While fault finding on the 4301 circuit the TH03 also tripped when the TH04 CB was closed in. Hinchey (4301, 4303). | Customer Owned | Customer-Owned | 51 | 85 | 72 | Central | 4301
134519 | 2016-09-08 | Defective Equipment | Defective Equipment/ Material | TH04 Circuit tripped due to …. While fault finding on the 4301 circuit the TH03 also tripped when the TH04 CB was closed in. Hinchey (4301, 4303). | Customer Owned | Customer-Owned | 229 | 36 | 137 | Central | 4303
134520 | 2016-09-08 | Tree Contacts | Tree Growth/ Untrimmed Tree | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32648 AFTER REMOVING A TREE BRANCH | O/H Transformer | O/H Transformer (1ph) | 7 | 141 | 16 | Central | TD12
134521 | 2016-09-08 | Tree Contacts | Other Vegetation | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27694 (VINES AROUND THE SWITCH) | O/H Transformer | O/H Transformer (1ph) | 10 | 77 | 13 | Central | 505
134522 | 2016-09-09 | Scheduled Outage | Forced Switching | Hydro Ottawa Field Operator crews isolated the transformer bus at V185 after the Ottawa Fire Dept. reported smoke coming from the electrical room. Field Operators found two blown fuses feeding the transformer bank and burnt fire pump connections | None | Customer-Owned | 2 | 208 | 7 | Central | UL02
134523 | 2016-09-09 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry crews to clear overgrown trees from the TB06 O/H line downstream of S18618 | None | None | 16 | 295 | 79 | East | TB06
134525 | 2016-09-09 | Scheduled Outage | Construction | At 6:22pm FAL03 from S29543 to EOL was isolated to allow crew to convert customer from 8Kv to 28Kv supply. 1 customer affected. Fallowfield (FAL03) | None | None | 1 | 128 | 2 | South | FAL03
134526 | 2016-09-10 | Scheduled Outage | Maintenance | To allow cable crew to repair both incomming cables in VT154. | None | PILC | 1 | 158 | 3 | Central | TL4TS
134528 | 2016-09-10 | Scheduled Outage | Construction | Install new hydro poles. | None | None | 1 | 385 | 6 | Central | UV07
134529 | 2016-09-10 | Lightning | Lightning | Customer report hearing K329 fuse blow at 1991 Tawney Rd. 24/7 crew reports blown lightning arrestor and fuse cutout. 01:23 24/7 reports both cables to K329 are bad and on-call crew required to fault find and repair faulted cables. | O/H Switchgear | Fused Cutout | 7 | 737 | 86 | East | AE06
134530 | 2016-09-11 | Tree Contacts | Falling Tree | wire down | O/H Conductor | O/H Conductor | 22 | 485 | 178 | East | 7F2
134531 | 2016-09-11 | Lightning | Lightning | Pole fire. | Pole | Insulation Failure (Pole Fire) | 1 | 380 | 6 | Central | TD12
134533 | 2016-09-11 | Tree Contacts | Broken Branch | tree contact | O/H Conductor | O/H Conductor | 169 | 133 | 375 | South | EPWF2
134533 | 2016-09-11 | Tree Contacts | Broken Branch | tree contact | O/H Conductor | O/H Conductor | 204 | 18 | 61 | South | EPWF5
134535 | 2016-09-11 | Adverse Weather | Extreme Wind | High winds tree fell into secondary bus. | Secondary \ Service | O/H Service | 12 | 362 | 72 | Central | AD07
134536 | 2016-09-12 | Scheduled Outage | Construction | At 5:00am FAL03 from S26645 to end of line was isolated to allow crew to convert customer to 27Kv. 1 customer affected. Fallowfield. (FAL03) | None | None | 1 | 207 | 3 | South | FAL03
134537 | 2016-09-12 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X29914 FOR CONTRACTOR TO REMOVE A TREE | None | None | 16 | 30 | 8 | Central | SR02
134538 | 2016-09-12 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER GLTE0371 TO DISCONNECT SECONDARY SERVICE FOR REPAIRS | None | None | 12 | 5 | 1 | East | BCHF1
134539 | 2016-09-12 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 21 | 160 | 56 | East | UB07
134540 | 2016-09-12 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X29914 TO RECONNECT SECONDARY SERVICE THAT WAS DROPPED FOR TREE REMOVAL | None | None | 16 | 40 | 11 | Central | SR02
134541 | 2016-09-12 | Scheduled Outage | Construction | 2 transformers, X27614 and X 27613 isolated by crew for a pole replacement | None | None | 7 | 370 | 43 | Central | UN04
134542 | 2016-09-13 | Scheduled Outage | Construction | Switch S22430 R to EOL was isolated to allow crew to convert line section to 28KV. Fallowfield FAL03 | None | None | 34 | 123 | 70 | South | FAL03
134543 | 2016-09-13 | Defective Equipment | Imminent Equipment Failure Detected | Transformer 6487 at 11 Hartin Street, was isolated to allow crew to replace leaking transformer and small base. | None | Oil Filled - Submersible | 5 | 521 | 43 | West | TFXF1
134545 | 2016-09-13 | Scheduled Outage | Forced Switching | Vault V291 was isolated to allow crew to repalce 3 phase transformer bank and replce box switch at pole. Clifton (UL02) | None | None | 2 | 231 | 8 | Central | UL02
134546 | 2016-09-13 | Scheduled Outage | Vegetation Management | S13166 to Eol was isolated to allow forestry crwe to trim tree at rear of 107 Acacia. (Vaughan (UG07) | None | None | 16 | 225 | 60 | East | UG07
134549 | 2016-09-13 | Scheduled Outage | Construction | Temp 145 RWB to EOL were isolated to allow crew to replace pole and conductor. Jockvale (145F3) | None | None | 5 | 438 | 36 | South | 145F3
134550 | 2016-09-13 | Defective Equipment | Defective Equipment/ Material | Transformer #X22543 opened up due to defective cut out | O/H Switchgear | Fused Cutout | 20 | 142 | 47 | East | V11F3
134551 | 2016-09-14 | Scheduled Outage | Vegetation Management | UA07 O/H from pole 54B4B-0146BHH to EOL at 2000 cochrane was isolated to allow tree trimming crew to trim tree at rear of 1320 Paardeburgh. (Albion UA07) | None | None | 10 | 156 | 26 | East | UA07
134554 | 2016-09-14 | Adverse Weather | Extreme Wind | The UX02 and UX05 circuit tripped during the wind storm in the Ottawa Area. Crew patrolled circuit and suspect wires slapped toghether at Carier and Maclaren. (Gladstone UX02, UX05) | Station Equipment | Relay | 187 | 20 | 62 | Central | UX02
134554 | 2016-09-14 | Adverse Weather | Extreme Wind | The UX02 and UX05 circuit tripped during the wind storm in the Ottawa Area. Crew patrolled circuit and suspect wires slapped toghether at Carier and Maclaren. (Gladstone UX02, UX05) | Station Equipment | Relay | 363 | 75 | 454 | Central | UX05
134555 | 2016-09-14 | Adverse Weather | Extreme Wind | The TA21 circuit tripped and the UA04 circuit A/R during the wind storm in the Ottawa Area. | Station Equipment | Relay | 180 | 16 | 48 | East | 2203
134556 | 2016-09-14 | Scheduled Outage | Construction | TE2977 was isolated due to out of phase condition to remove the rabbits WX2051 from service. | None | None | 5 | 59 | 5 | South | 140F4
134557 | 2016-09-14 | Adverse Weather | Extreme Wind | The TB1UQ circuit tripped during the wind storm in the Ottawa area. Circuit was under hold Off at the time of the trip. Crew was cleared and circuit was picked up. Russell (TB1UQ) | None | None | 94 | 19 | 30 | East | TB1UQ
134559 | 2016-09-14 | Foreign Interference | Wildlife (Bird/Animal) | The TW12 circuit breaker tripped and transforme S48319 opened due to due to animal contact. Woodroffe (TW12) | Station Equipment | Relay | 667 | 8 | 89 | Central | TW12
134560 | 2016-09-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X45102 opened up due to animal contact | O/H Switchgear | Fused Cutout | 11 | 81 | 15 | Central | TW17
134561 | 2016-09-14 | Defective Equipment | Mechanical Failure | V371 tripped due to defective vault equipment. Gladstone (UX02) | Customer Owned | Customer-Owned | 7 | 605 | 71 | Central | UX02
134563 | 2016-09-15 | Scheduled Outage | Maintenance | To inspect vault issues and replace step-up transformer in secondary room. | None | Transformer | 2 | 198 | 7 | Central | UL02
134564 | 2016-09-15 | Scheduled Outage | Maintenance | At 11:40am TP5454 was isolated to replace it due to a leak. 16 customers affected. Bridlewood (BRDF7) | None | None | 16 | 138 | 37 | West | BRDF7
134567 | 2016-09-16 | Scheduled Outage | Vegetation Management | To allow Davey Tree to remove tree at the rear of 410 Huron. | None | O/H Conductor | 27 | 331 | 149 | Central | SM10
134568 | 2016-09-16 | Scheduled Outage | Construction | To allow crews to upgrade sidewalk vault to include submersible transformer. | None | Oil Filled - Submersible | 47 | 225 | 176 | Central | UD01
134570 | 2016-09-16 | Tree Contacts | Broken Branch | To remove tree on UC10 circuit at the rear of 1008 Castle Hill | O/H Conductor | O/H Conductor | 110 | 93 | 170 | Central | UC10
134571 | 2016-09-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35335 TO INSTALL A NEW POLE | None | None | 7 | 240 | 28 | Central | AD05
134572 | 2016-09-16 | Foreign Interference | Wildlife (Bird/Animal) | At 11:20am a bird flew into the overhead causing all three phases on S14263 to blow causing an outage to 39 customers. Fallowfield (FAL02). | Unknown \ Other | Unknown \ Other | 39 | 37 | 24 | South | FAL02
134573 | 2016-09-16 | Scheduled Outage | Maintenance | 600V RECONFIGURATION | None | None | 4 | 156 | 10 | South | 72F4
134578 | 2016-09-17 | Scheduled Outage | Maintenance | Old leaking tx 672 replaced with TP11550 | None | None | 1 | 449 | 7 | West | 39F2
134579 | 2016-09-17 | Tree Contacts | Broken Branch | Transformer #X35912 opened up due to branch on primary | O/H Switchgear | Fused Cutout | 8 | 94 | 13 | Central | TD06
134580 | 2016-09-17 | Scheduled Outage | Vegetation Management | Transformer #X35912 isolated by crew to remove a branch from the primary, they thought the cause of the outage at 14:04 at this location was due to vines but found out after they closed back in that there was a branch on primary so they isolated it again | None | None | 8 | 11 | 1 | Central | TD06
134581 | 2016-09-17 | Scheduled Outage | Forced Switching | Transformer TP11293 had to be isolated immediately after being connected & energize because the secondary phase rotation was incorrect. | None | None | 1 | 43 | 1 | East | LMBF7
134582 | 2016-09-17 | Scheduled Outage | Forced Switching | Transformer X29975 was isolated to allow crew to replace defective service to 31 Fifth Ave. Bronson (SB05). | None | O/H Service | 5 | 68 | 6 | Central | SB12
134583 | 2016-09-17 | Scheduled Outage | Forced Switching | Transformer X33597 at 1634 Ortona was isolated to allow crew to make repairs to make repairs to burning secondary service. 9 customers were affected. Fisher (AK02) | Secondary \ Service | O/H Service | 9 | 8 | 1 | Central | AK02
134585 | 2016-09-18 | Defective Equipment | Defective Equipment/ Material | A burnt terminaion at switch S168 @ 21 Richer Circle casselman, 1 customer affected | O/H Switchgear | Unknown \ Other | 1 | 98 | 2 | East | V11F1
134586 | 2016-09-18 | Unknown/Other | Unknown | Transformer #X35736 opened up, crew could not find cause | O/H Switchgear | Fused Cutout | 1 | 150 | 2 | West | BECKF2
134587 | 2016-09-18 | Scheduled Outage | Maintenance | Routine customer owned vault maintenance. | None | None | 1 | 420 | 7 | West | A9M1
134588 | 2016-09-18 | Unknown/Other | Unknown | S29852 failed to close properly when the Field Operator crew attempted to operate it. This caused A9M3 to auto-reclose, & JKGF5 and TFXF1 to trip. 2416 customers on JKGF5 and 2760 customers on TFXF1 remained out until a 24/7 line crew cut the defective sw | O/H Switchgear | Load Break Gang | 2416 | 34 | 1369 | West | JKGF5
134588 | 2016-09-18 | Unknown/Other | Unknown | S29852 failed to close properly when the Field Operator crew attempted to operate it. This caused A9M3 to auto-reclose, & JKGF5 and TFXF1 to trip. 2416 customers on JKGF5 and 2760 customers on TFXF1 remained out until a 24/7 line crew cut the defective sw | O/H Switchgear | Load Break Gang | 2760 | 34 | 1564 | West | TFXF1
134590 | 2016-09-18 | Defective Equipment | Defective Equipment/ Material | Defective B phase U/G cable between TP7056-HB and TE2016 caused the SC5398-CB3 RWB to trip | U/G Cable | XLPE | 37 | 98 | 60 | East | 77M1
134590 | 2016-09-18 | Defective Equipment | Defective Equipment/ Material | Defective B phase U/G cable between TP7056-HB and TE2016 caused the SC5398-CB3 RWB to trip | U/G Cable | XLPE | 324 | 183 | 988 | East | 77M1
134592 | 2016-09-18 | Scheduled Outage | Construction | Transformer TE3514 at 800 Stonehaven was isolated to allow the crew transfer cables from old riser to new pole, 2 customers were affected | None | Unknown \ Other | 2 | 367 | 12 | South | 145F3
134593 | 2016-09-19 | Scheduled Outage | Forced Switching | LMBF7 section between S20094 and S5588 was isolated for emergency crew to clear MOV and Hydro crew to repair broken Hydro pole caused by MOV accident. | None | Pole | 44 | 250 | 183 | East | LMBF7
134594 | 2016-09-19 | Scheduled Outage | Construction | Transfomer #X23699 isolated by crew for a service upgrade | None | None | 9 | 35 | 5 | East | UB07
134595 | 2016-09-19 | Scheduled Outage | Maintenance | A Hydro Ottawa 24/7 line crew isolated the 13kV transformer bus at VT112 the allow the Hydro Ottawa metering Dept. to repair a metering problem inside the vault | None | Meter | 1 | 25 | 0 | East | TO3UB
134597 | 2016-09-19 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to install new services | None | None | 25 | 130 | 54 | Central | UX04
134597 | 2016-09-19 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to install new services | None | None | 49 | 37 | 30 | Central | UX04
134598 | 2016-09-19 | Scheduled Outage | Construction | Bill Armstrong reports that he has transformer X35940 open so that he can change a triplex service and replace the fused cut-out feeding the transformer | None | O/H Conductor | 8 | 68 | 9 | South | 190F5
134599 | 2016-09-19 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry crews to clear over grown trees from the O/H lines | None | None | 5 | 193 | 16 | East | TB06
134600 | 2016-09-19 | Scheduled Outage | Construction | FAL03 from S29287 to EOL at 4278 Greenbank isolated to allow crews to transfer plant to new poles. 1 customer affected. Fallwofield (FAL03) | None | O/H Conductor | 1 | 22 | 0 | South | FAL03
134601 | 2016-09-19 | Scheduled Outage | Construction | Transfomrer 2672 at 124 Abbeyhill was isolated for permanent removal. 12 customers affected. Bridlewood (BRDF6) | None | Padmount (1ph) | 12 | 325 | 65 | West | BRDF6
134602 | 2016-09-19 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X23124 TO REPLACE TRANSFORMER AND TRANSFER SERVICES TO NEW POLE | None | None | 2 | 65 | 2 | East | 77M1
134603 | 2016-09-20 | Scheduled Outage | Vegetation Management | Overhead section of primary isolated at Cavendish and Alta Vista for tree trimming affecting 33 customers. Russell TB06 | None | None | 33 | 155 | 85 | East | TB06
134604 | 2016-09-20 | Defective Equipment | Electrical Failure | REPAIRS TO DAMAGED SEC CABLES | U/G Cable | XLPE | 24 | 270 | 108 | Central | AK04
134605 | 2016-09-20 | Scheduled Outage | Maintenance | S1000 opened to re-set transformer Pad TE765 on its base affecting one customer on the Rideau Heights 180F2. | None | None | 1 | 20 | 0 | South | 180F2
134607 | 2016-09-21 | Scheduled Outage | Vegetation Management | Overhead section of primary at 1387 Cavendish isolated for tree trimming affecting 32 customers. Russell TB06 | None | None | 32 | 200 | 107 | East | TB06
134608 | 2016-09-21 | Scheduled Outage | Construction | Transformer opened at 10 West Presland Rd crew replacing a pole affecting 11 customers. Overbrook sub SO05 | None | None | 11 | 276 | 51 | East | SO05
134609 | 2016-09-21 | Scheduled Outage | Construction | SECONDARY SERVICE WORK | None | None | 13 | 40 | 9 | East | AE06
134610 | 2016-09-21 | Scheduled Outage | Maintenance | REPLACE SEC SERVICE | None | None | 1 | 50 | 1 | Central | SB05
134611 | 2016-09-21 | Scheduled Outage | Maintenance | TV143 isolated for transformer upgrade. Augusta (UD01) | None | Transformer | 41 | 181 | 124 | Central | UD01
134613 | 2016-09-21 | Scheduled Outage | Maintenance | K690 isolated to relocate tx onto base. Vaughan (UG10) | None | Padmount (1ph) | 10 | 206 | 34 | East | UG10
134614 | 2016-09-21 | Scheduled Outage | Maintenance | Padmount 2616R was isolated in order to remove the transformer from the system and transfer 32 affected customers to other sources on the Bridlewood BRDF6 | None | None | 32 | 358 | 191 | West | BRDF6
134615 | 2016-09-21 | Scheduled Outage | Vegetation Management | QT127 was isolated affecting 1 customer on the 22M24 out of Nepean TS to allow customer to remove vegetation and repair a fence | None | None | 1 | 309 | 5 | South | 22M24
134616 | 2016-09-21 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X33036 TO REPLACE BROKEN SWITCH S185 | None | None | 5 | 35 | 3 | South | 180F4
134617 | 2016-09-22 | Scheduled Outage | Vegetation Management | Switch S19733 to Eol was isoalted to allow forestry crew to perfrom tree trimming at rear of 171 Fanshaw. Riverdale (505) | None | None | 55 | 160 | 147 | Central | 505
134618 | 2016-09-22 | Scheduled Outage | Construction | Overhead line from S13609 opened to allow crew to relocate transformer. | None | None | 10 | 157 | 26 | West | 44F1
134619 | 2016-09-22 | Scheduled Outage | Construction | INSTALLING TWO POLES | None | None | 17 | 425 | 120 | Central | TW17
134620 | 2016-09-22 | Tree Contacts | Other Vegetation | VINES ON THE TRANS POLE | O/H Transformer | O/H Transformer (1ph) | 12 | 101 | 20 | East | BCHF3
134621 | 2016-09-23 | Scheduled Outage | Construction | Transformer TV181 at 317 Murray was isolated to allow crew to repalce transformer vault with new transformer TP10965. Augusat (UD05. | None | None | 36 | 237 | 142 | Central | UD05
134622 | 2016-09-23 | Defective Equipment | Defective Equipment/ Material | The 190F5 circuit tripped due to pole Fire and defective switch S554 at 1197 Deer Park. At the same time that the 190F5 circuit tripped the 190F2 circuit A/R and went out again at 12:57 pm due when the 22M26 circuit tripped due defective CS185851 circuit | O/H Switchgear | Fused Cutout | 41 | 51 | 35 | South | 190F5
134622 | 2016-09-23 | Defective Equipment | Defective Equipment/ Material | The 190F5 circuit tripped due to pole Fire and defective switch S554 at 1197 Deer Park. At the same time that the 190F5 circuit tripped the 190F2 circuit A/R and went out again at 12:57 pm due when the 22M26 circuit tripped due defective CS185851 circuit | O/H Switchgear | Fused Cutout | 128 | 112 | 239 | South | 190F5
134622 | 2016-09-23 | Defective Equipment | Defective Equipment/ Material | The 190F5 circuit tripped due to pole Fire and defective switch S554 at 1197 Deer Park. At the same time that the 190F5 circuit tripped the 190F2 circuit A/R and went out again at 12:57 pm due when the 22M26 circuit tripped due defective CS185851 circuit | O/H Switchgear | Fused Cutout | 1201 | 110 | 2202 | South | 190F2
134622 | 2016-09-23 | Defective Equipment | Defective Equipment/ Material | The 190F5 circuit tripped due to pole Fire and defective switch S554 at 1197 Deer Park. At the same time that the 190F5 circuit tripped the 190F2 circuit A/R and went out again at 12:57 pm due when the 22M26 circuit tripped due defective CS185851 circuit | O/H Switchgear | Fused Cutout | 1224 | 10 | 204 | South | 190F5
134622 | 2016-09-23 | Defective Equipment | Defective Equipment/ Material | The 190F5 circuit tripped due to pole Fire and defective switch S554 at 1197 Deer Park. At the same time that the 190F5 circuit tripped the 190F2 circuit A/R and went out again at 12:57 pm due when the 22M26 circuit tripped due defective CS185851 circuit | O/H Switchgear | Fused Cutout | 1801 | 101 | 3032 | South | 190F5
134623 | 2016-09-23 | Defective Equipment | Defective Equipment/ Material | Defective circuit switcher CS18851 caused the 22M26 circuit to auto reclose three times and lock out. Nepean TS (22M26) | O/H Switchgear | Load Break Gang | 767 | 22 | 281 | South | 22M26
134623 | 2016-09-23 | Defective Equipment | Defective Equipment/ Material | Defective circuit switcher CS18851 caused the 22M26 circuit to auto reclose three times and lock out. Nepean TS (22M26) | O/H Switchgear | Load Break Gang | 1730 | 1 | 29 | South | 22M26
134623 | 2016-09-23 | Defective Equipment | Defective Equipment/ Material | Defective circuit switcher CS18851 caused the 22M26 circuit to auto reclose three times and lock out. Nepean TS (22M26) | O/H Switchgear | Load Break Gang | 7833 | 81 | 10575 | South | 22M26
134624 | 2016-09-23 | Scheduled Outage | Maintenance | Hazeldean Mall was isolated for contractor to receive transformer oil samples affecting 1 customer on the South March A9M1 | None | None | 1 | 56 | 1 | West | A9M1
134625 | 2016-09-24 | Defective Equipment | Electrical Failure | At 8:45am crews were dispatch to the South March area and after troubleshooting found a defective underground cable between S10 and tranformer 3085 red phase. 63 customers affected. South March (39F3) | U/G Cable | Unknown \ Other | 63 | 97 | 102 | West | 39F3
134628 | 2016-09-24 | Scheduled Outage | Maintenance | Transformer 235 isolated for soil remediation affecting 1 customer on the Kanata 624F5 | None | None | 1 | 943 | 16 | West | 624F5
134630 | 2016-09-25 | Scheduled Outage | Construction | At 08:32am TE3141 was isolated to allow crews to disconnect it from S7069 and connect it to new SC2876-CB4. 2 customers affected. Longfields DS (210F1) | None | None | 2 | 146 | 5 | South | LGFF1
134631 | 2016-09-26 | Scheduled Outage | Maintenance | To allow crews to replace hydro pole at the rear of 1266 Wesmar Dr.Tra | None | Pole | 13 | 338 | 73 | East | TA3AF
134632 | 2016-09-26 | Scheduled Outage | Vegetation Management | Tree triming at 1367 Kilborn. | None | O/H Conductor | 10 | 243 | 40 | Central | 505
134633 | 2016-09-26 | Scheduled Outage | Maintenance | Transformer 1233 at 99 Castle Glen was isolated to repace leaking transformer. 13 customers affected. Terry Fox TFXF1. | None | Padmount (1ph) | 13 | 197 | 43 | West | TFXF1
134634 | 2016-09-26 | Foreign Interference | Wildlife (Bird/Animal) | X32509 fuse blown due to animal interference. Kevin Mckenna dispatched. | O/H Transformer | O/H Transformer (1ph) | 13 | 42 | 9 | Central | TD01
134635 | 2016-09-26 | Loss Of Supply | Transmission Inadvertent | At 4:21pm SCADA incidated that all the breakers on the J bus and TR10 on the Y bus tripped. Hydro One reported a differential trip on the J Bus. All load was transferred to the Y bus through the transfer breaker so Hydro One can investigate. 1271 customer | None | None | 1 | 61 | 1 | Central | TR2UY
134635 | 2016-09-26 | Loss Of Supply | Transmission Inadvertent | At 4:21pm SCADA incidated that all the breakers on the J bus and TR10 on the Y bus tripped. Hydro One reported a differential trip on the J Bus. All load was transferred to the Y bus through the transfer breaker so Hydro One can investigate. 1271 customer | None | None | 5 | 61 | 5 | Central | TR1FB
134635 | 2016-09-26 | Loss Of Supply | Transmission Inadvertent | At 4:21pm SCADA incidated that all the breakers on the J bus and TR10 on the Y bus tripped. Hydro One reported a differential trip on the J Bus. All load was transferred to the Y bus through the transfer breaker so Hydro One can investigate. 1271 customer | None | None | 304 | 61 | 309 | Central | 502
134635 | 2016-09-26 | Loss Of Supply | Transmission Inadvertent | At 4:21pm SCADA incidated that all the breakers on the J bus and TR10 on the Y bus tripped. Hydro One reported a differential trip on the J Bus. All load was transferred to the Y bus through the transfer breaker so Hydro One can investigate. 1271 customer | None | None | 727 | 61 | 739 | Central | TR02UQTR
134635 | 2016-09-26 | Loss Of Supply | Transmission Inadvertent | At 4:21pm SCADA incidated that all the breakers on the J bus and TR10 on the Y bus tripped. Hydro One reported a differential trip on the J Bus. All load was transferred to the Y bus through the transfer breaker so Hydro One can investigate. 1271 customer | None | None | 1534 | 61 | 1560 | Central | TR09
134637 | 2016-09-26 | Unknown/Other | Unknown | The TA21 circuit breaker opened, crew patrolled circuit and did not find anything. Cause remains under investigation. Albion (2203) | None | None | 198 | 47 | 155 | East | 2203
134638 | 2016-09-27 | Scheduled Outage | Construction | Cable replacement. | None | None | 14 | 350 | 82 | South | 72F2
134639 | 2016-09-27 | Scheduled Outage | Construction | planned outage to allow crew to replace a padmount an move the other transformer back on its base after being hit by a snowplow | None | None | 20 | 123 | 41 | East | ELW07
134640 | 2016-09-27 | Scheduled Outage | Vegetation Management | tree trimming at rear of 1049 and 1069 apolydor | None | None | 29 | 247 | 119 | Central | 505
134641 | 2016-09-27 | Scheduled Outage | Construction | pole installation | None | None | 13 | 352 | 76 | East | TA3AF
134642 | 2016-09-27 | Scheduled Outage | Construction | replacing TV179 and replacing with new transformer TP11477. | None | None | 20 | 402 | 134 | Central | UD05
134643 | 2016-09-27 | Scheduled Outage | Forced Switching | Doug Featherstone to have S20370 open under PC10A # 11266. Broken Bell pole. Require isolation to remove span guy. | None | None | 5 | 18 | 2 | East | LTM01
134644 | 2016-09-28 | Scheduled Outage | Construction | Transformer P482 was isolated to allow crew to replace transformer with new TP11568. Overbrook (SO04) | None | None | 1 | 99 | 2 | East | SO04
134645 | 2016-09-28 | Scheduled Outage | Construction | Transformer #X36445 isolated by crew to install a new service | None | None | 7 | 25 | 3 | West | RHNF3
134646 | 2016-09-28 | Scheduled Outage | Construction | Transformer #X23516 isolated by crew for a service disconnect/reconnect | None | None | 5 | 45 | 4 | East | SO02
134647 | 2016-09-28 | Scheduled Outage | Construction | Transformer #X20216 isolated by crew to replace arrestor | None | None | 1 | 47 | 1 | East | 249F2
134648 | 2016-09-28 | Scheduled Outage | Construction | Transfomrer X40896 at 1266 Wesmar isolated to transfer plant. 20 customers affected. Albion (TA3AF) | None | O/H Transformer (1ph) | 20 | 162 | 54 | East | TA3AF
134649 | 2016-09-28 | Scheduled Outage | Construction | Transformer #X29709 isolated by crew to re-arrange plant | None | None | 13 | 75 | 16 | East | AE07
134651 | 2016-09-28 | Scheduled Outage | Construction | Transformer X31759 at 43 Kinnear St. isolated to replace a service. 7 customers affected. Carling (SM13) | None | O/H Transformer (1ph) | 7 | 84 | 10 | Central | SM13
134652 | 2016-09-28 | Scheduled Outage | Construction | Shaun Evans from K-Line and crew to have transformer X31140 open to transfer plant. Customers notified. | None | None | 14 | 167 | 39 | Central | AB05
134653 | 2016-09-28 | Scheduled Outage | Maintenance | Rick Barnett to have transformer X23516 open for service disc/reconnect. Customers notified. | None | None | 5 | 413 | 34 | East | SO02
134654 | 2016-09-29 | Scheduled Outage | Maintenance | Cable replacement at TP11044 on the Merivale 72F2 affecting 13 customers. | None | None | 13 | 469 | 102 | South | 72F2
134655 | 2016-09-29 | Scheduled Outage | Maintenance | 4kv vault, TV139, isolated for vault & transformer upgrade. 51 customers affected. Agusta (UD01) | None | Transformer | 51 | 254 | 216 | Central | UD01
134657 | 2016-09-29 | Scheduled Outage | Vegetation Management | 505 OH sectio from X28162 to EOL isolated to allow forestry to trim. 21 customers affected. Riverdale (505) | None | O/H Conductor | 21 | 315 | 110 | Central | 505
134658 | 2016-09-29 | Scheduled Outage | Maintenance | AE01 OH from pole X56887 to EOL isolated to installpoes. 16 customers affected. Urban Dale (AE01) | None | O/H Conductor | 16 | 275 | 73 | East | AE01
134659 | 2016-09-29 | Scheduled Outage | Construction | Transformer #X26003 isolated by crew to install new service | None | None | 15 | 70 | 18 | East | AP03
134660 | 2016-09-29 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35763 opened up due to animal contact | O/H Switchgear | Fused Cutout | 1 | 89 | 1 | West | RHNF3
134662 | 2016-09-30 | Scheduled Outage | Maintenance | 7 customers were affected when 44F1 blue phase overhead was isolated on Andrew Alexander for HOL crew to transfer them to a new supply. | None | None | 7 | 81 | 9 | West | 44F1
134663 | 2016-09-30 | Foreign Interference | Wildlife (Bird/Animal) | SUSPECT ANIMAL CONTACT | O/H Transformer | O/H Transformer (1ph) | 27 | 107 | 48 | East | 4801F8
134664 | 2016-09-30 | Foreign Interference | Wildlife (Bird/Animal) | SUSPECT ANIMAL CONTACT AT TRANS X13821 | O/H Switchgear | Fused Cutout | 107 | 46 | 82 | East | 4801F8
134665 | 2016-09-30 | Scheduled Outage | Construction | Transformer #X26098 isolated by crew to install a new service | None | None | 11 | 35 | 6 | East | AC05
134667 | 2016-10-01 | Scheduled Outage | Vegetation Management | Doug Featherstone to have transformer X36078 open to remove a limb from a secondary service. Customers notified. | None | None | 6 | 10 | 1 | South | 190F5
134669 | 2016-10-03 | Scheduled Outage | Construction | crew pulling in new cable to PT1440 and splicing and energize from new S29688. | None | None | 1 | 153 | 3 | East | TB07
134670 | 2016-10-03 | Scheduled Outage | Vegetation Management | S14998 at Revelstoke to EOL was isoalted to allow forestry crew to perfrom tree trimming. (Walkley (UZ11)) | None | None | 17 | 326 | 92 | East | UZ11
134671 | 2016-10-03 | Scheduled Outage | Maintenance | Transformer TP11050 isolated to allow crew to replace primary cables. | None | Padmount (1ph) | 20 | 470 | 157 | South | 72F2
134672 | 2016-10-03 | Human Element | Switching Error | GR6 recloser was opened by accidently while setting a hold off by K-Line. | O/H Switchgear | Recloser (3ph) | 708 | 9 | 106 | East | 249F2
134674 | 2016-10-03 | Scheduled Outage | Maintenance | Scott Barkley to have transformer X31770 open to transfer plant. Customers notified. | None | None | 29 | 180 | 87 | Central | AK04
134676 | 2016-10-03 | Scheduled Outage | Construction | TV141 at 30 Desjardin was isolated to allow crew to upgrade the sidewalk vault and replace the submersible transforme. Augusta (UD01) | None | None | 57 | 224 | 213 | Central | UD01
134677 | 2016-10-03 | Defective Equipment | Defective Equipment/ Material | Defective arrester at X32421 caused the S21495 to blow. Crew repalced arrester and refused the S21495. All power was restored. Lincoln (TD01) | Pole Attachement | Arrester | 280 | 53 | 247 | Central | TD01
134678 | 2016-10-03 | Scheduled Outage | Maintenance | Adrian Henry and crew to have transformer X32421 open to transfer plant. Customers notified. | None | None | 7 | 390 | 46 | Central | TD01
134679 | 2016-10-03 | Scheduled Outage | Maintenance | MAKE REPAIRS TO NEUTRAL CONDUCTOR | O/H Conductor | O/H Conductor | 2 | 78 | 3 | East | UZ12
134680 | 2016-10-03 | Defective Equipment | Defective Equipment/ Material | Blown arrester at K99 at 825 Cahill caused the WSC6 W phase to blow. Crew cleared arrester and refused the WCS6 W and all power was restored. 30 customers were affected. McCarthy (AQ06). | U/G Cable Attachement | Arrester | 30 | 50 | 25 | East | AQ06
134682 | 2016-10-04 | Scheduled Outage | Construction | TP11051 at 19Ancroft isolated for cable replacement. 14 customers affected. Merivale (72F2) | None | XLPE | 14 | 403 | 94 | South | 72F1
134683 | 2016-10-04 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X24451 TO REPLACE SECONDARY CONNECTIONS | None | None | 20 | 30 | 10 | East | 77M6
134684 | 2016-10-04 | Scheduled Outage | Vegetation Management | 4kV overhead circuit from S17953 to EOL on Blanchard isolated for tree trimming. 50 customers affected. Walkley (UZ02) | None | O/H Conductor | 50 | 249 | 208 | East | UZ02
134685 | 2016-10-04 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X24195 TO REPLACE PRIMARY LINE INSULATORS | None | None | 13 | 60 | 13 | East | 8F3
134686 | 2016-10-04 | Scheduled Outage | Maintenance | K1120 replaced and contaminated soil removed. | None | None | 9 | 150 | 22 | Central | UN06
134687 | 2016-10-04 | Scheduled Outage | Construction | Transformer @X35340 isolatedby crew to transfer plant | None | None | 7 | 295 | 34 | Central | AD05
134688 | 2016-10-04 | Scheduled Outage | Maintenance | Customer owned vault maintenance. | None | None | 1 | 244 | 4 | East | 5303
134689 | 2016-10-04 | Scheduled Outage | Construction | REPLACE BROKEN STUB POLE | Pole | Pole | 9 | 309 | 46 | Central | TH01
134691 | 2016-10-05 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry to clear large trees away from the O/H line. | None | None | 19 | 213 | 67 | East | UZ12
134692 | 2016-10-05 | Scheduled Outage | Construction | TP11052 at 87 Downsview isolated for cable replacement. 50 customers affected. Merivale (72F2) | None | Padmount (1ph) | 14 | 363 | 85 | South | 72F2
134692 | 2016-10-05 | Scheduled Outage | Construction | TP11052 at 87 Downsview isolated for cable replacement. 50 customers affected. Merivale (72F2) | None | Padmount (1ph) | 50 | 4 | 3 | South | 72F2
134693 | 2016-10-05 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to re-route cables and install a new O/H switch | None | None | 1 | 301 | 5 | Central | UN07
134694 | 2016-10-05 | Scheduled Outage | Maintenance | Vault VT262 at 400 Slater isolated for customer vault maintenance. 1 customer affected. Lisgar (TC2TL) | None | None | 1 | 365 | 6 | Central | TC2TL
134696 | 2016-10-05 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry crews to clear large overgrown trees away from the O/H line | None | None | 102 | 103 | 175 | East | UA07
134697 | 2016-10-05 | Scheduled Outage | Construction | Transformer #X20517 isolated by crew (Jordan Foote from K-Line) to transfer Hydro plant | None | None | 2 | 126 | 4 | East | 249F2
134698 | 2016-10-05 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to replace poles | None | Pole | 35 | 376 | 219 | East | AE07
134699 | 2016-10-05 | Scheduled Outage | Construction | Transformer #X33948 isolated by crew to install new service | None | None | 7 | 67 | 8 | Central | UL04
134701 | 2016-10-05 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X20515 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 1 | 120 | 2 | East | 249F2
134702 | 2016-10-06 | Scheduled Outage | Construction | Kiosk K685 at 1177 S. Laurent was isolated to allow crew to install new secondary. 9 customers were affected. Overbrook (SO04) | None | None | 9 | 340 | 51 | East | SO04
134703 | 2016-10-06 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32421 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 7 | 87 | 10 | Central | TD01
134704 | 2016-10-06 | Scheduled Outage | Construction | Transfer plant to new gear. | None | None | 1 | 70 | 1 | South | LGFF1
134705 | 2016-10-06 | Scheduled Outage | Construction | Transformer #X21511 isolated by crew to work on a fly tap service on open buss | None | None | 14 | 59 | 14 | Central | UC05
134706 | 2016-10-06 | Scheduled Outage | Construction | Transformer #K00376 isolated by crew for a pedestal re-build | None | None | 19 | 75 | 24 | East | AE07
134707 | 2016-10-06 | Scheduled Outage | Construction | Transformer #X32628 isolated by crew for a transformer upgrade | None | None | 3 | 260 | 13 | Central | TD12
134710 | 2016-10-07 | Defective Equipment | Defective Equipment/ Material | Transformer X27054 opened due to defective transformer switch. Russell (TB06) | O/H Switchgear | Fused Cutout | 9 | 126 | 19 | East | TB06
134713 | 2016-10-07 | Scheduled Outage | Maintenance | Rick Barnett and crew to have transformer X23219 open to make room for Rogers plant. Customers notitifed. | None | None | 1 | 45 | 1 | East | UT06
134714 | 2016-10-07 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X48683 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 17 | 124 | 35 | Central | TW18
134715 | 2016-10-07 | Defective Equipment | Electrical Failure | Transformer X31044 at 469 Catherine found to be defective, replaced by on-call crew. 17 customers affected. Florence (UF08) | O/H Transformer | O/H Transformer (1ph) | 17 | 443 | 126 | Central | UF08
134716 | 2016-10-08 | Adverse Environment | Fire | Ottawa Fire reports Pole fire at 11 Cleto on the Epworth DS EPWF5 which auto reclosed at 12:23pm affecting 201 customers. 11 premises remained out while repairs to downed overhead were made. | Pole | Insulation Failure (Pole Fire) | 11 | 409 | 75 | South | EPWF5
134717 | 2016-10-08 | Unknown/Other | Unknown | TW07 (2806) Tripped at 5:23pm. No flags and no transient spike on RWB to indicate phase. TW07 closed and holding at 5:36pm. Crew dispatched to perform patrol of overhead equipment. | None | None | 450 | 13 | 98 | Central | 2806
134718 | 2016-10-08 | Scheduled Outage | Maintenance | VT702 amd VT769 shut down for contractor to install power monitoring equipment in secondary room | None | None | 1 | 165 | 3 | East | TO2UB
134718 | 2016-10-08 | Scheduled Outage | Maintenance | VT702 amd VT769 shut down for contractor to install power monitoring equipment in secondary room | None | None | 1 | 165 | 3 | East | TO3AP
134719 | 2016-10-09 | Defective Equipment | Defective Equipment/ Material | UNKNOWN | O/H Transformer | O/H Transformer (1ph) | 2 | 41 | 1 | Central | TW22
134721 | 2016-10-11 | Scheduled Outage | Maintenance | To replace cables to TP11053 and transformer. TP11054 had to be unloaded while switching was completed due to live front transformer. | None | Padmount (1ph) | 20 | 375 | 125 | South | 72F2
134721 | 2016-10-11 | Scheduled Outage | Maintenance | To replace cables to TP11053 and transformer. TP11054 had to be unloaded while switching was completed due to live front transformer. | None | Padmount (1ph) | 40 | 1 | 1 | South | 72F2
134723 | 2016-10-11 | Scheduled Outage | Maintenance | Replace leaking transformer | None | Padmount (1ph) | 25 | 90 | 38 | West | TFXF4
134724 | 2016-10-11 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X20521 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 1 | 107 | 2 | East | 249F2
134725 | 2016-10-11 | Scheduled Outage | Building/ High Load Move | At 9:15 TP9665 was isolated to transfer customer to blue phase. 1 customer affected. Eastview (UT04) | None | None | 1 | 50 | 1 | East | UT04
134726 | 2016-10-11 | Scheduled Outage | Construction | At 9:00am crews isolated a section of AE06 on Martha Ave to replace poles. 22 customers affected. Urbandale (AE06) | None | None | 22 | 345 | 126 | East | AE06
134727 | 2016-10-11 | Scheduled Outage | Construction | Transformer #X33139 isolated by crew to install new service | None | None | 13 | 68 | 15 | Central | UV07
134728 | 2016-10-11 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35798 opened up pdue to squirrel contact | O/H Switchgear | Fused Cutout | 8 | 74 | 10 | Central | TD06
134729 | 2016-10-12 | Scheduled Outage | Maintenance | Replace transformer cable going to TP11053 and transformer. | None | Padmount (1ph) | 16 | 368 | 98 | South | 72F2
134730 | 2016-10-12 | Scheduled Outage | Maintenance | Replace leaking transformer #1215. Due to a mapping error TP10124 was also de-energized when transformer 1216-1 was opened. Causing outage to both TP101124 and 1215. Crews notified System Office and TP101124 was energized and transformer # 1215 was isol | None | Padmount (1ph) | 10 | 10 | 2 | West | TFXF1
134730 | 2016-10-12 | Scheduled Outage | Maintenance | Replace leaking transformer #1215. Due to a mapping error TP10124 was also de-energized when transformer 1216-1 was opened. Causing outage to both TP101124 and 1215. Crews notified System Office and TP101124 was energized and transformer # 1215 was isol | None | Padmount (1ph) | 10 | 147 | 24 | West | TFXF1
134730 | 2016-10-12 | Scheduled Outage | Maintenance | Replace leaking transformer #1215. Due to a mapping error TP10124 was also de-energized when transformer 1216-1 was opened. Causing outage to both TP101124 and 1215. Crews notified System Office and TP101124 was energized and transformer # 1215 was isol | None | Padmount (1ph) | 30 | 43 | 22 | West | TFXF1
134732 | 2016-10-12 | Scheduled Outage | Maintenance | At 9:18am transformer 5517R was isolated to allow crew to replace transformer and base. 7 customers affected. Bridlewood (BRDF5) | None | None | 7 | 472 | 55 | West | BRDF5
134733 | 2016-10-12 | Human Element | Incorrect Records/ labelling | Incorrect mapping at SC67 caused an outage to 67 customers in the Nelson st / Murray st area. King Edward SK12. | None | None | 67 | 45 | 50 | Central | SK12
134734 | 2016-10-12 | Scheduled Outage | Maintenance | To allow crews to replace leaking transformer. | None | Padmount (1ph) | 10 | 121 | 20 | West | TFXF1
134736 | 2016-10-12 | Scheduled Outage | Construction | V664 at 80 Rideau Terrace was de-commissioned & new TP11416 energized. 71 customers affected. Vaughn UG05. | None | None | 71 | 50 | 59 | East | UG05
134737 | 2016-10-12 | Scheduled Outage | Vegetation Management | Transformer #X27951 isolated by crew for Forestry | None | None | 6 | 340 | 34 | East | UZ07
134738 | 2016-10-12 | Scheduled Outage | Maintenance | At 9:26am KT64 was isolate to replace terminations in Kiosk. 11 customers affected. Ellwood (ELW07) | None | None | 11 | 94 | 17 | East | ELW07
134739 | 2016-10-12 | Scheduled Outage | Maintenance | At 12:51 K61 was isolated to allow crew to replace terminations in Kiosk. 20 customers affected. Ellwood (ELW07) | None | None | 20 | 67 | 22 | East | ELW07
134740 | 2016-10-12 | Foreign Interference | Vehicle | At 4:48pm a car hit a pole at Clyde and Woodward causing the UC05 and UC06 to trip. UC00 was openned via SCADA because it was also on the pole but did not trip. A total of 527 customers were affected. Clyde (UC05,UC06) | Pole | Pole | 139 | 417 | 966 | Central | UC06
134740 | 2016-10-12 | Foreign Interference | Vehicle | At 4:48pm a car hit a pole at Clyde and Woodward causing the UC05 and UC06 to trip. UC00 was openned via SCADA because it was also on the pole but did not trip. A total of 527 customers were affected. Clyde (UC05,UC06) | Pole | Pole | 388 | 417 | 2697 | Central | UC05
134741 | 2016-10-12 | Scheduled Outage | Forced Switching | A defective blue phase primary cable at 2543 St Joseph required all 3 phases isolated for repair affecting 1 customer. Bilberry Creek 77M6 | None | XLPE | 1 | 628 | 10 | East | 77M6
134743 | 2016-10-13 | Scheduled Outage | Construction | TP10409 at 320 Jatoba isolated to allow contractor to install new secondary service. 13 customers affected. Terry Fox (TFXF4) | None | Padmount (1ph) | 13 | 271 | 59 | West | TFXF4
134744 | 2016-10-13 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X18512 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 4 | 98 | 7 | East | 249F2
134745 | 2016-10-13 | Scheduled Outage | Maintenance | Customer owned vault maintenance | None | None | 1 | 102 | 2 | Central | 505
134746 | 2016-10-13 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X31915 (BIRD CONTACT) | O/H Transformer | O/H Transformer (1ph) | 5 | 121 | 10 | Central | 503
134747 | 2016-10-13 | Scheduled Outage | Construction | TP2535 at 56 Chickasaw isolated for replacement due to oil leak. 9 customers affected, Bridlewood (BRDF1) | None | Padmount (1ph) | 9 | 128 | 19 | West | BRDF1
134748 | 2016-10-13 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X16964 TO RE-ARRANGE SECONDARY HYDRO PLANT | None | None | 18 | 110 | 33 | East | BCHF5
134750 | 2016-10-13 | Foreign Interference | Vehicle | RX2001 opened under hold off protection due to broken pole at River Rd. and Balmoral. Suspected vehicle contact with the overhead. 196 customers affected. Limebank (7F2) | O/H Conductor | O/H Conductor | 196 | 296 | 967 | East | 7F2
134751 | 2016-10-13 | Scheduled Outage | Maintenance | Shaun Evans from K-Line to hace transformer X18502 open to transfer plant. Customers notified. | None | None | 3 | 180 | 9 | East | 249F2
134752 | 2016-10-13 | Human Element | Switching Error | Switching Error | None | None | 418 | 1 | 7 | East | TA3AF
134753 | 2016-10-14 | Scheduled Outage | Construction | Transformer K1126 and X23626 at 90 West Presland isolated for a pole change and the transfer of plant. 15 customers affected. Overbrook (SO05) | None | None | 15 | 193 | 48 | East | SO05
134754 | 2016-10-14 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to upgrade the sidewalk vault & replace the submersible transformer in the vault | None | None | 69 | 158 | 182 | Central | UD08
134755 | 2016-10-14 | Scheduled Outage | Construction | TP2722 and TP2723 on Yoho Dr. isolate for replacement due to oil leaks. 20 customers affected. Bridlewood (BRDF1) | None | Padmount (1ph) | 20 | 217 | 72 | West | BRDF1
134757 | 2016-10-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X48535 openned due to animal contact. 24/7 (Chris Trafford & Jack Morrice) responded and refused the cut out. | O/H Switchgear | Fused Cutout | 15 | 44 | 11 | Central | TW18
134758 | 2016-10-15 | Scheduled Outage | Construction | To replace defective elbows and inserts and soil remediation and replace leaking transformer (1573). | None | None | 1 | 280 | 5 | West | TFXF6
134758 | 2016-10-15 | Scheduled Outage | Construction | To replace defective elbows and inserts and soil remediation and replace leaking transformer (1573). | None | None | 2 | 183 | 6 | West | TFXF6
134759 | 2016-10-15 | Scheduled Outage | Construction | Upgrade transformer. | None | None | 1 | 1665 | 28 | East | 4801F7
134762 | 2016-10-16 | Foreign Interference | Wildlife (Bird/Animal) | Switch S19459 opened up due to squirrel contact | O/H Switchgear | Inline Switch | 169 | 101 | 284 | Central | TR1UN
134763 | 2016-10-16 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32438 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 11 | 101 | 19 | Central | TW22
134764 | 2016-10-16 | Scheduled Outage | Construction | reconductor o/h line and transfer transformer bank to new pole. | None | None | 1 | 273 | 5 | Central | AK05
134765 | 2016-10-16 | Scheduled Outage | Maintenance | contractor repairing and replacing relays | None | None | 1 | 543 | 9 | Central | 507
134766 | 2016-10-16 | Scheduled Outage | Vegetation Management | Transformer X32430 at 895 Iroquois was opened to trim trees & repair a damaged service. 6 customers affected. Woodroffe TW22. | Secondary \ Service | O/H Service | 6 | 80 | 8 | Central | TW22
134767 | 2016-10-16 | Scheduled Outage | Maintenance | SW1756 at 2056 Bank was isolated to replace pressure gauge & top up SF6 gas. 1 customer affected. Elwood ELW09. | None | None | 1 | 220 | 4 | East | ELW09
134768 | 2016-10-17 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 27 | 213 | 96 | East | TB06
134769 | 2016-10-17 | Scheduled Outage | Construction | Cable and transformer replacement. | None | None | 6 | 380 | 38 | South | 72F2
134770 | 2016-10-17 | Scheduled Outage | Maintenance | Jim Yeldon to have transformer X36533 open to remove a service. Customers notified. | None | None | 7 | 30 | 4 | South | EPWF3
134771 | 2016-10-17 | Scheduled Outage | Maintenance | Gary Coburn to have transformer X29710 open to transfer secondary bus. Customers notified. | None | None | 9 | 116 | 17 | East | AE07
134772 | 2016-10-17 | Scheduled Outage | Construction | 2 transformers #X30900 and X27983 isolated by crew to install new triplex and remove transformer | None | None | 8 | 320 | 43 | Central | SK16
134776 | 2016-10-18 | Lightning | Lightning | Thunderstorm | None | None | 3718 | 5 | 310 | West | TFXF5
134778 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | HONI circuit A3RM tripped during a lightning storm. | None | None | 103 | 64 | 110 | South | 72F6
134778 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | HONI circuit A3RM tripped during a lightning storm. | None | None | 214 | 65 | 232 | South | 72F7
134780 | 2016-10-18 | Lightning | Lightning | No apparent cause found. Active thunderstorms at the time of this outage | O/H Switchgear | Fused Cutout | 30 | 157 | 78 | East | 8F1
134781 | 2016-10-18 | Lightning | Lightning | Thunderstorms | None | None | 1 | 821 | 14 | East | 7F4
134784 | 2016-10-18 | Defective Equipment | Defective Equipment/ Material | The Walkley UZ06 tripped due tangled primary O/H wires and to defective primary riser U/G cable. Walkley (UZ06) | U/G Cable | PILC | 654 | 162 | 1766 | East | UZ06
134785 | 2016-10-18 | Scheduled Outage | Construction | The Overhead on Abbot st was isolated to allow the crew to tranfer load to the new overhead under the voltage conversion program | None | Unknown \ Other | 21 | 254 | 89 | West | 44F1
134786 | 2016-10-18 | Adverse Weather | Broken Branch | The AE05 circuit tripped during the Wind storm due to branch on the O/H on Harding St. Urbandlae (AE05). | O/H Switchgear | Fused Cutout | 98 | 158 | 258 | East | AE05
134786 | 2016-10-18 | Adverse Weather | Broken Branch | The AE05 circuit tripped during the Wind storm due to branch on the O/H on Harding St. Urbandlae (AE05). | O/H Switchgear | Fused Cutout | 218 | 8 | 29 | East | AE05
134787 | 2016-10-18 | Tree Contacts | Falling Tree | A large tree fell on to the 22M24 O/H at Vann and Slack | O/H Conductor | O/H Conductor | 5461 | 70 | 6371 | South | 22M24
134788 | 2016-10-18 | Scheduled Outage | Maintenance | 7 W phase transformers were isolated on Eastvale Dr to allow crew to verify cable tagging and reaplce the base at TP3101. Beaconhill (BCHF5) | None | None | 78 | 379 | 493 | East | BCHF5
134789 | 2016-10-18 | Adverse Weather | Extreme Wind | With high winds the white and blue phase wrapped around each other | O/H Conductor | O/H Conductor | 654 | 43 | 469 | East | UZ06
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 213 | 6 | 21 | South | 87F6
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 390 | 6 | 39 | South | 84F1
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 397 | 6 | 40 | South | 84F4
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 476 | 6 | 48 | South | 87F7
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 478 | 6 | 48 | South | 84F2
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 547 | 6 | 55 | South | 87F5
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 570 | 6 | 57 | South | 84F3
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 1001 | 6 | 100 | South | 87F4
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 1102 | 6 | 110 | South | 84F5
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 1305 | 6 | 130 | South | 87F1
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 1354 | 6 | 135 | South | 87F3
134791 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | C7BM/W6CS 115kV line tripped off. An Osprey nest at Chats Falls GS (Hydro One) was determined to be the cause | None | None | 2447 | 6 | 245 | South | 84F6
134793 | 2016-10-18 | Tree Contacts | Tree Growth/ Untrimmed Tree | REFUSED SWITCH FEEDING TRANSFORMER X33047 (TREE CONTACT) | O/H Transformer | O/H Transformer (1ph) | 4 | 105 | 7 | South | 180F4
134794 | 2016-10-18 | Defective Equipment | Mechanical Failure | REPAIRED BROKEN PRIMARY DROP LEAD FEEDING TRANSFORMER X29866 | O/H Transformer | O/H Transformer (1ph) | 19 | 162 | 51 | Central | TR09
134795 | 2016-10-18 | Scheduled Outage | Maintenance | Routine vault maintenance by contractor on customer owned vault. | None | None | 2 | 301 | 10 | Central | TM3UC
134796 | 2016-10-18 | Defective Equipment | Mechanical Failure | Defective secondary service | Secondary \ Service | O/H Service | 9 | 74 | 11 | South | 160F2
134797 | 2016-10-19 | Scheduled Outage | Construction | Transformer TP11047 at 54 Downsview was isoalted to allow crew to replace TP11047 and prepare new cable between TP11046 and TP11047. TP11048 was place off potential to isolate TP11047 due to live front transformer. Mervivale (72F2). ID# 134797 | None | Padmount (1ph) | 32 | 401 | 214 | South | 72F2
134797 | 2016-10-19 | Scheduled Outage | Construction | Transformer TP11047 at 54 Downsview was isoalted to allow crew to replace TP11047 and prepare new cable between TP11046 and TP11047. TP11048 was place off potential to isolate TP11047 due to live front transformer. Mervivale (72F2). ID# 134797 | None | Padmount (1ph) | 62 | 2 | 2 | South | 72F2
134798 | 2016-10-19 | Scheduled Outage | Maintenance | K130 isolated to allow crew to remove asbestos install new lightning arrestor and redo termination. | None | Kiosk (1ph) | 10 | 119 | 20 | East | AQ09
134799 | 2016-10-19 | Scheduled Outage | Maintenance | Transformer TP11418 at 181 Abbotsford was isolated to allow crew to perfrom soil remediation. Bridlewood (BRDF6) | None | None | 13 | 457 | 99 | West | BRDF6
134800 | 2016-10-19 | Scheduled Outage | Vegetation Management | X20411 to EOL isolated to allow tree trimming and replace pole X20411. | None | O/H Conductor | 4 | 248 | 17 | East | 249F2
134801 | 2016-10-19 | Scheduled Outage | Maintenance | Transformer KT171 at 41 Esterlawn was isolated to allow crew to remove transformer and base for soil remediation. Woodroffe (TW22) | None | None | 20 | 527 | 176 | Central | TW22
134802 | 2016-10-20 | Scheduled Outage | Construction | Planned outage to replace transfore and re-arrange cables | None | None | 30 | 404 | 202 | South | 72F2
134804 | 2016-10-20 | Scheduled Outage | Maintenance | planned outage to move SE-8 back on its base | None | None | 66 | 7 | 8 | South | 190F5
134806 | 2016-10-20 | Scheduled Outage | Vegetation Management | planned outage for G Schwartz to trim trees | None | None | 2 | 231 | 8 | West | BECKF2
134807 | 2016-10-20 | Defective Equipment | Electrical Failure | Blown egress riser pothead at Merivale DS | U/G Cable Attachement | Pothead | 214 | 49 | 175 | South | 72F7
134808 | 2016-10-20 | Loss Of Supply | Transmission Inadvertent | A loss of supply from Hydro One on the C7BM caused a loss of power to customers at Centrepoint and Manordale stations. Due to planned work at our Queensway Carleton station customers on the 160F2 and 160F4 were also being feed from Manordale. Hydro One pr | None | None | 4626 | 21 | 1619 | South | C7BM (Centrepointe MS - T1/T2)
134808 | 2016-10-20 | Loss Of Supply | Transmission Inadvertent | A loss of supply from Hydro One on the C7BM caused a loss of power to customers at Centrepoint and Manordale stations. Due to planned work at our Queensway Carleton station customers on the 160F2 and 160F4 were also being feed from Manordale. Hydro One pr | None | None | 5384 | 21 | 1884 | South | C7BM (Manordale MS - T1/T2)
134809 | 2016-10-20 | Scheduled Outage | Maintenance | Gary Coburn to have X29862 open to move primary conductor and replace the transformer. Customers notified | None | None | 8 | 90 | 12 | Central | TR09
134810 | 2016-10-20 | Scheduled Outage | Maintenance | Transformers K99 & K100 at 825 Cahill were isolated to remove asbestos & upgrade insulators. 20 customers affected. McCarthy AQ06. | None | None | 20 | 117 | 39 | East | AQ06
134811 | 2016-10-20 | Scheduled Outage | Maintenance | Robin Blair and crew to have transformer X36202 open to rearrange plant. Customers notified. | None | None | 3 | 136 | 7 | South | 200F1
134812 | 2016-10-20 | Scheduled Outage | Forced Switching | At 9:19am crews were restoring the TFXF4 but due to an out of phase condition 169 customers were interrupted while crews were switching. Terry Fox (TFXF4) | None | None | 169 | 24 | 68 | West | TFXF4
134813 | 2016-10-20 | Foreign Interference | Crane | A crane made contact with overhead lines at Kenwood at Brierwood. This caused Carling TM3UC & TM1AH to trip & Hillcrest AH14 to auto reclose. AH14 was then opened to clear crane from lines. 732 customers affected. | O/H Conductor | O/H Conductor | 0 | 34 | 0 | Central | AH14
134813 | 2016-10-20 | Foreign Interference | Crane | A crane made contact with overhead lines at Kenwood at Brierwood. This caused Carling TM3UC & TM1AH to trip & Hillcrest AH14 to auto reclose. AH14 was then opened to clear crane from lines. 732 customers affected. | O/H Conductor | O/H Conductor | 23 | 58 | 22 | Central | TM3UC
134813 | 2016-10-20 | Foreign Interference | Crane | A crane made contact with overhead lines at Kenwood at Brierwood. This caused Carling TM3UC & TM1AH to trip & Hillcrest AH14 to auto reclose. AH14 was then opened to clear crane from lines. 732 customers affected. | O/H Conductor | O/H Conductor | 250 | 43 | 179 | Central | TM1AH
134813 | 2016-10-20 | Foreign Interference | Crane | A crane made contact with overhead lines at Kenwood at Brierwood. This caused Carling TM3UC & TM1AH to trip & Hillcrest AH14 to auto reclose. AH14 was then opened to clear crane from lines. 732 customers affected. | O/H Conductor | O/H Conductor | 454 | 6 | 45 | Central | AH14
134815 | 2016-10-20 | Scheduled Outage | Construction | prep work for future co-gen installation. | None | None | 1 | 618 | 10 | Central | 305
134816 | 2016-10-21 | Scheduled Outage | Maintenance | customer to add load to CB3 and HOL stations group to re-test vista gear. | None | None | 1 | 159 | 3 | Central | 617
134817 | 2016-10-21 | Scheduled Outage | Construction | Replace defective transformers. | None | None | 6 | 229 | 23 | West | 624F2
134818 | 2016-10-21 | Foreign Interference | Wildlife (Bird/Animal) | Fuse at transformer X24093 openned due to animal contact. 24/7 to re-fuse. | O/H Switchgear | Fused Cutout | 5 | 224 | 19 | East | LMBF5
134822 | 2016-10-22 | Tree Contacts | Tree Growth/ Untrimmed Tree | REPLACED BLOWN FUSE AT SWITCH 2161B FEEDING CUSTOMER OWNED LINE (TREE CONTACT) | O/H Switchgear | Fused Cutout | 1 | 218 | 4 | West | 624F6
134823 | 2016-10-22 | Scheduled Outage | Maintenance | Customer owned sub station maintenance. Rogers Cable | None | None | 1 | 152 | 3 | Central | TM1AH
134826 | 2016-10-23 | Scheduled Outage | Maintenance | 13kv vault VT126 isolated for customer vault mtce. | None | None | 1 | 591 | 10 | Central | 605
134828 | 2016-10-23 | Scheduled Outage | Construction | V53 at 109 Bank isolated for decommisioning. 1 customer affected. Slater (SA19) | None | None | 1 | 160 | 3 | Central | SA19
134829 | 2016-10-23 | Defective Equipment | Mechanical Failure | REPLACED BROKEN SWICH FEEDING 3 PHASE PAD MOUNT TRANSFORMER PT0228 | O/H Transformer | O/H Transformer (3ph) | 1 | 50 | 1 | East | TB07
134830 | 2016-10-23 | Defective Equipment | Mechanical Failure | REPLACED BROKEN PRIMARY LEAD FEEDING TRANSFORMER X40058 | O/H Transformer | O/H Transformer (1ph) | 4 | 166 | 11 | South | 200F2
134831 | 2016-10-23 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING PRIVATE PRIMARY LINE AND TRANSFORMER X24101 (SQUIRREL CONTACT) | O/H Switchgear | Fused Cutout | 1 | 112 | 2 | East | LMBF5
134832 | 2016-10-23 | Adverse Weather | Extreme Wind | Transformer X30291 fue blew due to triplex tails dangling in the wind made contact with H1 bushing on the transformer. Hinchey (TH11) | O/H Switchgear | Fused Cutout | 22 | 54 | 20 | Central | TH11-NIU
134833 | 2016-10-24 | Defective Equipment | Electrical Failure | Transformer X34043 opened by crew to make repairs to broken neutral and tighten triplex. | O/H Conductor | O/H Conductor | 8 | 24 | 3 | Central | TD01
134834 | 2016-10-24 | Scheduled Outage | Maintenance | To replace transformer & cables | None | None | 18 | 358 | 107 | South | 72F2
134835 | 2016-10-24 | Scheduled Outage | Maintenance | Permit on TH01 to brace broken pole that was hit by car. | None | None | 1426 | 27 | 642 | Central | TH01
134836 | 2016-10-24 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X29711 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 8 | 262 | 35 | East | AE07
134837 | 2016-10-24 | Defective Equipment | Electrical Failure | Cable fault cause S20063 fuse to open. 1 customer affected. Blackburn (BLKF8) | U/G Cable | Unknown \ Other | 1 | 656 | 11 | East | BLKF8
134838 | 2016-10-24 | Scheduled Outage | Forced Switching | Overhead circuit from S1400 to EOL isolated to repair broken primary lead. 6 customers affected. Stafford (200F1) | None | O/H Conductor | 6 | 57 | 6 | South | 200F1
134839 | 2016-10-24 | Defective Equipment | Corrosion | Broken primary lead made contact with neutral. Transformer X39698 openned due to fault. 24/7 dispatched to make repairs. | O/H Conductor | O/H Conductor | 8 | 147 | 20 | South | 200F2
134840 | 2016-10-24 | Scheduled Outage | Maintenance | 24/7 required to isolate from S1400 in order to remove broken lead. Customers notified. | None | None | 6 | 59 | 6 | South | 200F2
134842 | 2016-10-25 | Scheduled Outage | Construction | Section of overhead primary at 2219 Audrey was isolated for pole replacement affecting 47 customers. Urbandale AE07 | None | None | 47 | 408 | 320 | East | AE07
134844 | 2016-10-25 | Scheduled Outage | Vegetation Management | A section of primary overhead at Clover and Gregg was isolated for tree trimming affecting 91 customers. Brookfield AF06 | None | None | 91 | 275 | 417 | East | AF06
134846 | 2016-10-25 | Scheduled Outage | Construction | Transformer #X36084 isolated by crew to replace hot line clamp | None | None | 6 | 35 | 4 | Central | TD05
134848 | 2016-10-25 | Scheduled Outage | Maintenance | Gary Coburn to have transformer X26851 open to transfer secondary bus. Customers notified. | None | None | 5 | 367 | 31 | East | AE07
134851 | 2016-10-25 | Scheduled Outage | Construction | At 7:35pm TP11550 was isolated to allow cable crew to splice cables into new SC15983. 1 customer affected. South March (39F2) | None | None | 1 | 168 | 3 | West | 39F2
134852 | 2016-10-26 | Scheduled Outage | Construction | TP5581 was isolated to transfer supply to SC19185. 4 customers affected. Janet KinG (JKGF5) | None | Padmount (3ph) | 4 | 45 | 3 | West | JKGF5
134853 | 2016-10-26 | Scheduled Outage | Construction | A section of primary overhead at Hickson and Morrison was isolated for pole replacement and tree trimming affecting 92 customers. Edwin UV07 | None | None | 8 | 31 | 4 | Central | UV07
134853 | 2016-10-26 | Scheduled Outage | Construction | A section of primary overhead at Hickson and Morrison was isolated for pole replacement and tree trimming affecting 92 customers. Edwin UV07 | None | None | 18 | 26 | 8 | Central | UV07
134853 | 2016-10-26 | Scheduled Outage | Construction | A section of primary overhead at Hickson and Morrison was isolated for pole replacement and tree trimming affecting 92 customers. Edwin UV07 | None | None | 92 | 398 | 610 | Central | UV07
134854 | 2016-10-26 | Scheduled Outage | Vegetation Management | S20246 to EOL isolated for tree trimming affecting 8 customers. Albion (UA07) | None | None | 8 | 335 | 45 | East | UA07
134855 | 2016-10-26 | Scheduled Outage | Construction | TP10330 at 460 St. Laurent isolated on the TO5UB out of Overbrook Terminal for HOL crew to oversee contractor pulling in new secondaries affecting 1 customer for 6 hours. | None | None | 1 | 378 | 6 | East | TO5UB
134856 | 2016-10-26 | Scheduled Outage | Construction | Transformer #X27155 isolated by crew for a service upgrade | None | None | 7 | 40 | 5 | East | TB15
134858 | 2016-10-26 | Scheduled Outage | Construction | Transformer #X32952 isolated by crew for a service upgrade | None | None | 3 | 78 | 4 | Central | TD07
134860 | 2016-10-27 | Defective Equipment | Defective Equipment/ Material | The 140F5 CB A/R and caused the S1118 to blow due to cable fault between transformer TP6459 and TP6460 at 53 Fieldgate. | U/G Cable | XLPE | 31 | 50 | 26 | South | 140F5
134860 | 2016-10-27 | Defective Equipment | Defective Equipment/ Material | The 140F5 CB A/R and caused the S1118 to blow due to cable fault between transformer TP6459 and TP6460 at 53 Fieldgate. | U/G Cable | XLPE | 63 | 184 | 193 | South | 140F5
134862 | 2016-10-27 | Scheduled Outage | Maintenance | S12137 to EOL was isolated to allow crew to replace rotten pole in backyard of 7702 Bleeks | None | None | 33 | 135 | 74 | West | 43F2
134865 | 2016-10-27 | Scheduled Outage | Construction | Transformer #X30033 isolated by crew to re-attach 2 guy wires | None | None | 6 | 9 | 1 | Central | SB02
134866 | 2016-10-27 | Adverse Weather | Wet Snow | No apparent cause found. Mixed precipitation (snow/rain) and windy conditions are suspected | None | None | 187 | 66 | 206 | Central | UX02
134866 | 2016-10-27 | Adverse Weather | Wet Snow | No apparent cause found. Mixed precipitation (snow/rain) and windy conditions are suspected | None | None | 334 | 66 | 367 | Central | UX05
134867 | 2016-10-27 | Scheduled Outage | Maintenance | Customer owned vault maintenance to install flexible connections between pothead and busbar. | None | None | 1 | 109 | 2 | Central | 4303
134868 | 2016-10-27 | Scheduled Outage | Maintenance | Contractor replacing customers high voltage breaker | None | None | 1 | 1125 | 19 | East | TO3UT
134869 | 2016-10-27 | Defective Equipment | Electrical Failure | Switch at transformer X35458 broke and shorted out to cross arm eventually causing S19995 to open as well. 23 customers affected. Lincoln Heights (TD01) | O/H Switchgear | Fused Cutout | 10 | 179 | 30 | Central | TD01
134869 | 2016-10-28 | Defective Equipment | Electrical Failure | Switch at transformer X35458 broke and shorted out to cross arm eventually causing S19995 to open as well. 23 customers affected. Lincoln Heights (TD01) | O/H Switchgear | Fused Cutout | 23 | 165 | 63 | Central | TD01
134870 | 2016-10-28 | Scheduled Outage | Maintenance | Replace transformer 2094. | None | Padmount (1ph) | 11 | 166 | 30 | West | BRDF2
134872 | 2016-10-29 | Scheduled Outage | Maintenance | James Leader and crew to have transformer X20476 open to move secondary services. Customers notified. | None | None | 5 | 44 | 4 | East | 249F2
134874 | 2016-10-29 | Defective Equipment | Mechanical Failure | Transformer X4172 opened do to broken bushing. On-Call called in to make repairs. Upon inspection it was determined that secondary contact caused the outage but neither the fuse at the transformer nor the upstream switch (S1352) blew. This caused the prim | O/H Transformer | O/H Transformer (1ph) | 4 | 11 | 1 | South | 170F1
134874 | 2016-10-29 | Defective Equipment | Mechanical Failure | Transformer X4172 opened do to broken bushing. On-Call called in to make repairs. Upon inspection it was determined that secondary contact caused the outage but neither the fuse at the transformer nor the upstream switch (S1352) blew. This caused the prim | O/H Transformer | O/H Transformer (1ph) | 4 | 514 | 34 | South | 170F1
134874 | 2016-10-29 | Defective Equipment | Mechanical Failure | Transformer X4172 opened do to broken bushing. On-Call called in to make repairs. Upon inspection it was determined that secondary contact caused the outage but neither the fuse at the transformer nor the upstream switch (S1352) blew. This caused the prim | O/H Transformer | O/H Transformer (1ph) | 38 | 58 | 37 | South | 170F1
134875 | 2016-10-30 | Scheduled Outage | Maintenance | Planned outage for secondary maintenance. | None | Unknown \ Other | 1 | 385 | 6 | West | 624F5
134876 | 2016-10-30 | Scheduled Outage | Maintenance | Sam Gibson to have transformer X29443 open to replace O/H triplex to 95 St. Ambrose. | None | None | 14 | 68 | 16 | East | AC05
134877 | 2016-10-31 | Foreign Interference | Customer Equipment | sparking & humming from switch, & arching, disconnect power asap, at Brookfield Global co. | Customer Owned | Customer-Owned | 1 | 237 | 4 | East | 77M5
134878 | 2016-10-31 | Scheduled Outage | Construction | A section of O/H line from S16744 to EOL was isolated to replace poles & trim trees. Customers restored in stages. 143 customers affected. Edwin UV03. | None | None | 43 | 268 | 192 | Central | UV03
134878 | 2016-10-31 | Scheduled Outage | Construction | A section of O/H line from S16744 to EOL was isolated to replace poles & trim trees. Customers restored in stages. 143 customers affected. Edwin UV03. | None | None | 143 | 220 | 524 | Central | UV03
134879 | 2016-10-31 | Scheduled Outage | Construction | Transformer #X34415 isolated by crew to re-arrange plant for new 600v service | None | None | 19 | 200 | 63 | Central | UJ06
134880 | 2016-10-31 | Scheduled Outage | Construction | Gary Coburn to have transformer X27004 open to transfer secondary bus. Customers notified. | None | None | 9 | 406 | 61 | East | AE01
134883 | 2016-11-01 | Scheduled Outage | Maintenance | planned outage to replace insulators and blown arrestors | None | None | 18 | 198 | 59 | East | AQ03
134884 | 2016-11-01 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 21 | 425 | 149 | East | SO03
134885 | 2016-11-01 | Human Element | Improper Equipment/Tool/ Maintenance | Davey tree crews dropped a branch onto the 624F5 O/H. The circuit was under hold off and tripped. Hydro Ottawa line crews had to remove the branch safely before the circuit could be re energized | None | None | 166 | 47 | 130 | West | 624F5
134886 | 2016-11-01 | Scheduled Outage | Maintenance | Hydro Ottawa line crews isolated TP2723 at 163 Yoho Dr., To allow for soil remediation | None | None | 18 | 431 | 129 | West | BRDF1
134888 | 2016-11-01 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X23424 TO REPAIR BROKEN SECONDARY NEUTRAL | None | None | 9 | 37 | 6 | East | UB04
134890 | 2016-11-01 | Scheduled Outage | Construction | Transformer #X33126 isolated by crew to transfer plant | None | None | 14 | 270 | 63 | Central | UV07
134891 | 2016-11-01 | Scheduled Outage | Forced Switching | Transformer TP9673 at 100 Woodhurst was isolated to allow crew to straighten secondary bus and place transformer back on its base. Janet king (JKGF4) | None | None | 8 | 140 | 19 | West | JKGF4
134891 | 2016-11-01 | Scheduled Outage | Forced Switching | Transformer TP9673 at 100 Woodhurst was isolated to allow crew to straighten secondary bus and place transformer back on its base. Janet king (JKGF4) | None | None | 52 | 14 | 12 | West | JKGF4
134893 | 2016-11-02 | Defective Equipment | Defective Equipment/ Material | CS19942CHZ opened by crew due to fused switch burning up. | Customer Owned | Customer-Owned | 1 | 1162 | 19 | South | 22M26
134894 | 2016-11-02 | Scheduled Outage | Construction | Transformer #X47281 isolated by crew to transfer plant | None | None | 1 | 25 | 0 | South | 72F6
134895 | 2016-11-02 | Scheduled Outage | Construction | install new pole | None | None | 22 | 319 | 117 | Central | TD01
134896 | 2016-11-02 | Scheduled Outage | Maintenance | ISOLATED TRANSFOMER X33768 TO REPLACE OPEN WIRE SECONDARY SERVICE | None | None | 10 | 40 | 7 | Central | TW22
134897 | 2016-11-02 | Scheduled Outage | Construction | pole replacement and transfer plant | None | None | 30 | 360 | 180 | East | AE07
134898 | 2016-11-02 | Scheduled Outage | Construction | Transformer #X49235 isolated by crew to transfer plant | None | None | 5 | 205 | 17 | East | AE06
134899 | 2016-11-02 | Scheduled Outage | Construction | install new pole and transfer plant | None | None | 16 | 195 | 52 | Central | TD05
134900 | 2016-11-03 | Scheduled Outage | Maintenance | 2 transformers at 1325 and 1320 Alloway were isolated for insulator and lightning arrestor replacement affecting 24 customers. Langs AP05 | None | Arrester | 24 | 113 | 45 | East | AP05
134902 | 2016-11-03 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X28106 TO INSTALL A SECONDARY TRIIPLEX SERVICE MID SPAN CONNECTED | None | None | 18 | 67 | 20 | East | AF06
134904 | 2016-11-04 | Scheduled Outage | Maintenance | TP2722 isolation for oil remediation. 11 customers affected. Bridlewood (BRDF1) | None | None | 11 | 455 | 83 | West | BRDF1
134905 | 2016-11-04 | Scheduled Outage | Construction | A section of primary overhead at Howland and Magnus was isolated for pole replacement affecting 16 CUSTOMERS. Urbandale AE07 | None | None | 16 | 320 | 85 | East | AE07
134906 | 2016-11-04 | Scheduled Outage | Maintenance | Adam McNulty and crew to have transformer X34116 open to install new triplex to 203 Northwestern Ave. Customers notified. | None | None | 9 | 66 | 10 | Central | TH01
134907 | 2016-11-04 | Scheduled Outage | Maintenance | Adrian Henry and crew to have transformer 002922 isolated to replace leaking transformer. Customers notified. | None | None | 9 | 72 | 11 | West | TFXF5
134908 | 2016-11-04 | Scheduled Outage | Construction | TX 2922 isolated to be replaced and TX 2923 was dumped due to equipment configuration. 16 customers affected. Terry Fox TS (TFXF5) | None | None | 16 | 90 | 24 | West | TFXF5
134909 | 2016-10-18 | Defective Equipment | Electrical Failure | Underground cable fault. | U/G Cable | Unknown \ Other | 724 | 74 | 893 | East | 2204
134909 | 2016-10-18 | Defective Equipment | Electrical Failure | Underground cable fault. | U/G Cable | Unknown \ Other | 1987 | 157 | 5199 | East | 2204
134910 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | Over-tripping due to incorrect feeder protection settings. | None | None | 15 | 94 | 24 | East | TA1UZ
134910 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | Over-tripping due to incorrect feeder protection settings. | None | None | 2127 | 1 | 35 | East | 2201
134910 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | Over-tripping due to incorrect feeder protection settings. | None | None | 2142 | 2 | 71 | East | 2201
134910 | 2016-10-18 | Loss Of Supply | Transmission Inadvertent | Over-tripping due to incorrect feeder protection settings. | None | None | 2142 | 91 | 3249 | East | 2201
134911 | 2016-11-04 | Defective Equipment | Electrical Failure | Suspected cable fault | U/G Cable | Unknown \ Other | 96 | 12 | 19 | East | 1802
134911 | 2016-11-04 | Defective Equipment | Electrical Failure | Suspected cable fault | U/G Cable | Unknown \ Other | 98 | 7 | 11 | East | 1802
134911 | 2016-11-04 | Defective Equipment | Electrical Failure | Suspected cable fault | U/G Cable | Unknown \ Other | 99 | 56 | 92 | East | 1802
134912 | 2016-11-05 | Scheduled Outage | Maintenance | clean and torque vauilt | None | None | 1 | 181 | 3 | East | 7F2
134914 | 2016-11-07 | Scheduled Outage | Forced Switching | X24270 interrupted for HOL crew to reconnect a service | None | None | 2 | 45 | 2 | East | 8F3
134916 | 2016-11-08 | Scheduled Outage | Vegetation Management | 13kV overhead circuit between TEMP 61 and TEMP74 in the Bromley Rd and Lauder Rd. area was isolated for tree trimming. 180 customers affected. Lincoln Heights (TD06) | None | O/H Conductor | 180 | 314 | 942 | Central | TD06
134917 | 2016-11-08 | Scheduled Outage | Maintenance | K833 at 3325 isolated for insulator and arrestor replacement. 25 customers affected. McCarthy (AQ08) | None | Kiosk (1ph) | 25 | 174 | 72 | East | AQ08
134919 | 2016-11-08 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X31695 FOR A SERVICE UP-GRADE | None | None | 8 | 153 | 20 | Central | SR09
134920 | 2016-11-08 | Scheduled Outage | Maintenance | K482 at 3322 Uplands was isolated for insulator replacment. 18 customers affected. McCarthy (AQ08) | None | Kiosk (1ph) | 18 | 158 | 47 | East | AQ08
134922 | 2016-11-09 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to complete a voltage upgrade on transformer 8267. Transformer 8267 will become TP11189 and move from, the 8kV voltage level on 44F1 to the 27.6kV voltage level on JKGF4 | None | None | 9 | 71 | 11 | West | 44F1
134923 | 2016-11-09 | Scheduled Outage | Vegetation Management | 13kV overhead circuit between TEMP11 and TEMP86 in the Keenan Ave and Dovercourt Ave area was isolated for tree trimming at multiple addressess. 395 customers affected. Lincoln Heights (TD01) | None | O/H Conductor | 395 | 451 | 2969 | Central | TD01
134924 | 2016-11-09 | Scheduled Outage | Maintenance | At 9:33am crews red phase transformer and cables section to verify and correct cable tagging. 54 customers affected. Beacon Hill (BCHF5) | None | None | 54 | 190 | 171 | East | BCHF5
134926 | 2016-11-09 | Scheduled Outage | Maintenance | To allow Sproule Power Lines to verify cable tagging | None | None | 56 | 127 | 119 | East | BCHF5
134927 | 2016-11-09 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to cut over transformer TP9148from the 8kV voltage level to the 27.6kV voltage level | None | None | 6 | 51 | 5 | West | 44F1
134928 | 2016-11-09 | Scheduled Outage | Construction | Transformer #X14348 isolated by crew to replace burning hot line clamp | None | None | 5 | 15 | 1 | East | LMBF5
134929 | 2016-11-09 | Scheduled Outage | Construction | Transformer #X23262 isolated by crew to transfer hydro plant | None | None | 8 | 360 | 48 | East | AE07
134930 | 2016-11-10 | Scheduled Outage | Maintenance | to verify cable tagging. | None | None | 42 | 157 | 110 | East | BCHF5
134931 | 2016-11-10 | Scheduled Outage | Maintenance | to verify cable tagging | None | None | 24 | 75 | 30 | East | BCHF5
134932 | 2016-11-11 | Adverse Weather | Extreme Wind | During the win storm in the Ottawa area the AE01 CB tripped open. The breaker did not a/r. System closed breaker via SCADA and all load was restored. Urbandale (AE01) | Station Equipment | Relay | 439 | 7 | 51 | East | AE01
134935 | 2016-11-11 | Tree Contacts | Falling Tree | tree on overhead. Winds were prevalent. | O/H Switchgear | Inline Switch | 6 | 131 | 13 | East | BLKF5
134936 | 2016-11-11 | Adverse Weather | Extreme Wind | High winds caused phases to slap together. | O/H Conductor | O/H Conductor | 187 | 41 | 128 | Central | UX02
134936 | 2016-11-11 | Adverse Weather | Extreme Wind | High winds caused phases to slap together. | O/H Conductor | O/H Conductor | 334 | 41 | 228 | Central | UX05
134937 | 2016-11-11 | Defective Equipment | Electrical Failure | Broken overhead conductor at 99 Cartier caused UX02, UX05 and UX09 circuits to open. SA23 from X45277 was also isolated for working clearance. 1205 customers affected. Gladestone (UX02, UX05, UX09) Slater (SA23) | O/H Conductor | O/H Conductor | 98 | 219 | 358 | Central | SA23
134937 | 2016-11-11 | Defective Equipment | Electrical Failure | Broken overhead conductor at 99 Cartier caused UX02, UX05 and UX09 circuits to open. SA23 from X45277 was also isolated for working clearance. 1205 customers affected. Gladestone (UX02, UX05, UX09) Slater (SA23) | O/H Conductor | O/H Conductor | 187 | 436 | 1359 | Central | UX02
134937 | 2016-11-11 | Defective Equipment | Electrical Failure | Broken overhead conductor at 99 Cartier caused UX02, UX05 and UX09 circuits to open. SA23 from X45277 was also isolated for working clearance. 1205 customers affected. Gladestone (UX02, UX05, UX09) Slater (SA23) | O/H Conductor | O/H Conductor | 334 | 436 | 2427 | Central | UX05
134937 | 2016-11-11 | Defective Equipment | Electrical Failure | Broken overhead conductor at 99 Cartier caused UX02, UX05 and UX09 circuits to open. SA23 from X45277 was also isolated for working clearance. 1205 customers affected. Gladestone (UX02, UX05, UX09) Slater (SA23) | O/H Conductor | O/H Conductor | 586 | 436 | 4258 | Central | UX09
134938 | 2016-11-11 | Tree Contacts | Falling Tree | tree on overhead circuit. | O/H Switchgear | Inline Switch | 6 | 148 | 15 | East | BLKF5
134939 | 2016-11-12 | Scheduled Outage | Maintenance | Vault TV9451 isolated to replace switchgear due to SF6 gas leak. 1 customer affected. Slater (606) | None | Switch | 1 | 192 | 3 | Central | 606
134940 | 2016-11-12 | Scheduled Outage | Construction | Transformer #X33084 isolated by crew to run a new service, the old one was taken down by a tree | None | None | 8 | 30 | 4 | Central | TD07
134941 | 2016-11-12 | Tree Contacts | Broken Branch | A transformer at 2401 Dwight was opened to remove a tree limb from the secondary affecting 7 customers. Bantree AL02 | None | None | 7 | 13 | 2 | East | AL02
134943 | 2016-11-13 | Scheduled Outage | Construction | VT71 at 1725 St. Laurent isolated to replace TB3LE cable. 32 customers affected. Russell 5303 | None | None | 32 | 386 | 206 | East | 5303
134944 | 2016-11-13 | Scheduled Outage | Maintenance | A transformer at 2300 Bank was isolated to replace a leaking transformer affecting 1 customer. Cahill AN05 | None | Padmount (3ph) | 1 | 412 | 7 | East | AN05
134945 | 2016-11-13 | Unknown/Other | Unknown | Noise reported at Gainsford and Dunrobin. No evidence found of what caused a primary inline fuse to open affecting 29 customers. Kanata 624F6 | None | None | 29 | 81 | 39 | West | 624F6
134946 | 2016-11-14 | Scheduled Outage | Maintenance | To replace leaking transformer on the Terry Fox TFXF5 affecting 25 customers. | None | None | 25 | 91 | 38 | West | TFXF5
134948 | 2016-11-14 | Scheduled Outage | Construction | Transformer #X31194 isolated by crew to run a new service | None | None | 11 | 98 | 18 | Central | UF08
134949 | 2016-11-14 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X14789 TO RE-ARRANGE HYDRO PLANT | None | None | 1 | 58 | 1 | East | LMBF5
134950 | 2016-11-14 | Defective Equipment | Defective Equipment/ Material | White phase transformer loop outage due to cable fault. | U/G Cable | Unknown \ Other | 15 | 143 | 36 | East | 77M1
134950 | 2016-11-14 | Defective Equipment | Defective Equipment/ Material | White phase transformer loop outage due to cable fault. | U/G Cable | Unknown \ Other | 69 | 69 | 79 | East | 77M1
134950 | 2016-11-14 | Defective Equipment | Defective Equipment/ Material | White phase transformer loop outage due to cable fault. | U/G Cable | Unknown \ Other | 77 | 93 | 119 | East | 77M1
134952 | 2016-11-14 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32524 TO REPLACE HOT LINE CLAMP | None | None | 10 | 10 | 2 | Central | TD01
134953 | 2016-11-15 | Scheduled Outage | Construction | At 8:18am section of AP02 from Temp29 to EOL was isolated to allow crew to replace pole and transfer plant. 2 customers affected. LANGS (AP02). | None | None | 2 | 309 | 10 | East | AP02
134954 | 2016-11-15 | Scheduled Outage | Maintenance | At 09:02am PC10A#011384 was established on switch 841 to allow crew to upgrade customer secondary. 1 customer affected. Marchwood (MWDF3) | None | None | 1 | 68 | 1 | West | MWDF3
134955 | 2016-11-15 | Scheduled Outage | Construction | At 1:25pm a section of the 145F3 was isolated to allow crew to transfer plant. 5 customers affected. JOCKVALE (145F3) | None | None | 5 | 240 | 20 | South | 145F3
134956 | 2016-11-15 | Scheduled Outage | Construction | A section of the 145F3 on Old Richmond rd was isolated to allow crew to transfer plant to new pole line. 3 customers affected. JOCKVALE (145F3) | None | None | 3 | 108 | 5 | South | 145F3
134957 | 2016-11-15 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused fuse feeding transformer X24101 at 938 River rd to open. Squirrel guards installed & power restored. Limebank LMBF5. | None | None | 1 | 107 | 2 | East | LMBF5
134958 | 2016-11-16 | Scheduled Outage | Construction | At 11:56am section of the 145F3 was isolated to allow crew to transfer customer to new line. 1 customer affected. Jockvale (145F3) | None | None | 1 | 109 | 2 | South | 145F3
134960 | 2016-11-16 | Scheduled Outage | Construction | A section of the 145F3 on Old Richmond rd was isolated to allow crew to transfer customer to new line. 1 customer affected. Jockvale (145F3) | None | None | 1 | 194 | 3 | South | 145F3
134961 | 2016-11-16 | Scheduled Outage | Construction | At 9:34am section of AE07 was isolated to allow crew to install new poles and transfer plant. 56 customers affected. Urbandale (AE07) | None | None | 56 | 342 | 319 | East | AE07
134962 | 2016-11-16 | Scheduled Outage | Construction | At 6:38pm P458 was isolated to allow crew to transfer plan. 1 customer affected. Florence (UF06) | None | None | 1 | 167 | 3 | Central | UF06
134963 | 2016-11-16 | Scheduled Outage | Construction | Primary cable at 4 Booth was isolated to move plant to new pole affecting 2 customers. Lisgar TC2TL | None | None | 2 | 564 | 19 | Central | TC2TL
134964 | 2016-11-17 | Scheduled Outage | Maintenance | TV4867 isolated from all Hydro Sources for customer vault maintenance | None | None | 1 | 134 | 2 | Central | TK6TS
134965 | 2016-11-17 | Scheduled Outage | Construction | AE07 from TEMP 73 to EOL on Magnus Ave. was isolated to intstall new poles. 21 customers affected. Urbandale (AE07) | None | Pole | 21 | 366 | 128 | East | AE07
134966 | 2016-11-17 | Scheduled Outage | Construction | P311 at 205 Catherine St. was isolated to replace dip switches. 21 customer affected. Florence UF06 | None | Fused Cutout | 21 | 55 | 19 | Central | UF06
134968 | 2016-11-18 | Scheduled Outage | Construction | James Leader and crew to have transformer X24082 open to install a new service. Customers notified. | None | None | 10 | 43 | 7 | East | SO02
134969 | 2016-11-18 | Unknown/Other | Unknown | TW18 CB opened, closed via SCADA. Circuit was patrolled no cause found. 1367 customers affected. Woodroffe (TW18) | Unknown \ Other | Unknown \ Other | 1367 | 8 | 182 | Central | TW18
134972 | 2016-11-19 | Scheduled Outage | Construction | transferring plant to new overhead line. | None | None | 2 | 127 | 4 | South | 145F3
134973 | 2016-11-19 | Scheduled Outage | Construction | transfer plant to new overhead circuit. | None | None | 2 | 207 | 7 | South | 145F3
134974 | 2016-11-19 | Defective Equipment | Mechanical Failure | broken xfmr switch at 637 southmore | O/H Transformer | O/H Transformer (1ph) | 24 | 90 | 36 | Central | UX05
134976 | 2016-11-19 | Foreign Interference | Wildlife (Bird/Animal) | animal contact | O/H Transformer | O/H Transformer (1ph) | 16 | 89 | 24 | Central | TW18
134978 | 2016-11-20 | Tree Contacts | Broken Branch | tree on wires | O/H Conductor | O/H Conductor | 763 | 112 | 1424 | West | RHNF3
134980 | 2016-11-20 | Scheduled Outage | Construction | planned outage to replace cables into Vault | None | None | 4 | 525 | 35 | Central | UF06
134982 | 2016-11-20 | Defective Equipment | Mechanical Failure | Defective barrier board at TE176 caused S14316 open. | U/G Transformer | Padmount (1ph) | 41 | 154 | 105 | East | BCHF5
134984 | 2016-11-21 | Scheduled Outage | Construction | Reconfigure transformer loop. | None | None | 177 | 200 | 590 | West | BRDF2
134985 | 2016-11-21 | Scheduled Outage | Vegetation Management | REMOVE TREES FROM OVERHEAD LINE | None | None | 4 | 45 | 3 | East | UQ07
134987 | 2016-11-21 | Human Element | Protection Setting | while unloading UJ05 circuit to UJ04, UJ05 breaker tripped after the crew closed 2 phases, just the red phase of UJ05 was interupted. UJ04 auto reclosed at the same time. | None | None | 99 | 1 | 2 | Central | UJ05
134989 | 2016-11-22 | Scheduled Outage | Maintenance | Transformer TP6443 at 13 Kadeer Way, isolated to allow crew to replace transformer. | None | Padmount (1ph) | 14 | 526 | 123 | South | 140F4
134990 | 2016-11-22 | Scheduled Outage | Maintenance | Transformer 774 isolated to replace leaking transformer. | U/G Transformer | Padmount (1ph) | 10 | 94 | 16 | West | TFXF2
134991 | 2016-11-22 | Scheduled Outage | Construction | The internal fuse at KT562 @ 14 JESSICA PV was pulled to allow the crew to pull the meter at 2 JESSICA PV affecting 12 customers | None | None | 12 | 25 | 5 | East | 2206
134993 | 2016-11-22 | Scheduled Outage | Construction | Transformer #X23888 isolated by crew to re-arrange plant to install new pole on TH15 circuit | None | None | 10 | 150 | 25 | Central | TH11-NIU
134994 | 2016-11-22 | Scheduled Outage | Maintenance | Vault VT185 at 2850 Cedarwood was isolated to allow crw to repair metring problem. Albion (2208) | None | None | 1 | 122 | 2 | East | 2208
134995 | 2016-11-22 | Defective Equipment | Electrical Failure | G950 RWB opened by crew to isolate and repair downed conductor. | O/H Conductor | O/H Conductor | 4 | 18 | 1 | East | 4801F8
134996 | 2016-11-22 | Scheduled Outage | Construction | TRANSFER PLANT TO NEW POLE | None | None | 14 | 61 | 14 | Central | UC01
134997 | 2016-11-22 | Scheduled Outage | Vegetation Management | The overhead at the rear of 1090 Wiseman was isolated to allow the tree contractors to trimm the trees | O/H Conductor | O/H Conductor | 46 | 330 | 253 | East | UZ03
134998 | 2016-11-22 | Adverse Weather | Extreme Wind | RX2042 R and B phase tripped open during high wind in the Ottawa Area. Recloser was underhold off when it tripped. Circuit was patrolled and nothing was found. Cause of outage remains under investigation. | O/H Switchgear | Recloser (1ph) | 416 | 68 | 471 | West | MWDF3
134999 | 2016-11-22 | Scheduled Outage | Construction | Shaun Evans from K-Line and crew to have transformer X33204 open to change pole and transfer plant. Customers notified. | None | None | 7 | 120 | 14 | Central | TD05
135000 | 2016-11-22 | Scheduled Outage | Construction | 145F3 W phase between TEMP133 W and EOL was isolated to allow crew to to transfer plant to new pole. Jockvale (145F3) | None | None | 3 | 200 | 10 | South | 145F3
135001 | 2016-11-23 | Defective Equipment | Defective Equipment/ Material | Transformer TE1356 isolated to replace leaking transformer. | U/G Transformer | Padmount (1ph) | 9 | 128 | 19 | East | LTM04
135003 | 2016-11-23 | Defective Equipment | Mechanical Failure | While isolating the 53F3 W phase between S305 and S708 the switch S305W broke in two places and for safety reason the 58F3 Cb was open to allow crew to safely remove the leads from the S305. Section between S305 and S708 was then isolated to allow crew to | O/H Switchgear | Fused Cutout | 161 | 316 | 848 | South | EPWF3
135003 | 2016-11-23 | Defective Equipment | Mechanical Failure | While isolating the 53F3 W phase between S305 and S708 the switch S305W broke in two places and for safety reason the 58F3 Cb was open to allow crew to safely remove the leads from the S305. Section between S305 and S708 was then isolated to allow crew to | O/H Switchgear | Fused Cutout | 805 | 3 | 40 | South | EPWF3
135004 | 2016-11-23 | Scheduled Outage | Construction | Transformer #X35381 isolated by crew to install new service | None | None | 11 | 58 | 11 | Central | TD12
135005 | 2016-11-23 | Scheduled Outage | Construction | Transformer #X33999 isolated by crew to transfer plant | None | None | 5 | 205 | 17 | Central | UV03
135007 | 2016-11-23 | Scheduled Outage | Construction | Transformer #X36093 isolated by crew to run a new service | None | None | 20 | 45 | 15 | Central | TD05
135008 | 2016-11-23 | Scheduled Outage | Construction | Planned outage to allow crew to prove the ducts for future cable replacement. | None | None | 1 | 177 | 3 | Central | UF04
135009 | 2016-11-23 | Defective Equipment | Electrical Failure | defective transformer TE1041 | U/G Transformer | Padmount (1ph) | 15 | 550 | 138 | East | 77M1
135010 | 2016-11-24 | Scheduled Outage | Vegetation Management | At 8:49am section of TD01 was isolated for tree trimming. 33 customers affected. Lincoln Heights (TD01) | None | None | 33 | 256 | 141 | Central | TD01
135011 | 2016-11-24 | Scheduled Outage | Construction | At 9:25am a section of AE07 was isolated to allow crew to install new poles and transfer plant. 61 customers affected. Urbandale (AE07) | None | None | 61 | 425 | 432 | East | AE07
135012 | 2016-11-24 | Scheduled Outage | Maintenance | TP8860 isolated for oil remediation affecting 8 customers. Terry Fox (TFXF6) | None | Kiosk (1ph) | 8 | 444 | 59 | West | TFXF6
135013 | 2016-11-24 | Scheduled Outage | Maintenance | 4kv Kiosks K634, K635 & K637 and riser S12286 isolated for insulator repairs, affected 34 customers. Langs (AP05) | None | Kiosk (1ph) | 34 | 165 | 94 | East | AP05
135014 | 2016-11-24 | Scheduled Outage | Maintenance | A section of overhead line on Goth Ave was isolated to replace poles. 148 customers affected. Uplands 4801F8. Transformers X13785 & X13780 remained off to complete secondary connections. | None | None | 31 | 38 | 20 | East | 4801F8
135014 | 2016-11-24 | Scheduled Outage | Maintenance | A section of overhead line on Goth Ave was isolated to replace poles. 148 customers affected. Uplands 4801F8. Transformers X13785 & X13780 remained off to complete secondary connections. | None | None | 148 | 191 | 471 | East | 4801F8
135015 | 2016-11-24 | Scheduled Outage | Construction | TE2341 replaced due to damage from MVC, affecting 10 customers. Upland (4801F8) | None | Padmount (1ph) | 10 | 81 | 14 | East | 4801F8
135016 | 2016-11-24 | Scheduled Outage | Construction | At 5:30pm crews isolated P131 to transfer plant. 1 customer affected. Florence (UF06) | None | None | 1 | 285 | 5 | Central | UF06
135017 | 2016-11-25 | Defective Equipment | Electrical Failure | A defective underground cable caused S2-2 red to open. 87 customers affected. Beaverbrook 24F1. | U/G Cable | Unknown \ Other | 1 | 10 | 0 | West | 24F1
135017 | 2016-11-25 | Defective Equipment | Electrical Failure | A defective underground cable caused S2-2 red to open. 87 customers affected. Beaverbrook 24F1. | U/G Cable | Unknown \ Other | 87 | 108 | 157 | West | 24F1
135018 | 2016-11-25 | Scheduled Outage | Maintenance | At 9:18am section of AE07 was isolated to allow crews to install new pole. 48 customers affected. Urbandale (AE07) | None | None | 48 | 173 | 138 | East | AE07
135019 | 2016-11-25 | Scheduled Outage | Vegetation Management | At 8:49am section of UQ04 was isolated to allow crew to trim trees. 5 customers affected. Queens (UQ04) | None | None | 5 | 171 | 14 | East | UQ04
135020 | 2016-11-25 | Defective Equipment | Electrical Failure | A defective underground cable caused S21908 to open. Bridlewood BRDF5. 59 customers affected. | U/G Cable | Unknown \ Other | 59 | 57 | 56 | West | BRDF5
135021 | 2016-11-25 | Defective Equipment | Mechanical Failure | During inspection of TE1505, lid hinge came apart & lid made contact with secondary bus causing internal fuse to open. Bilberry 77M1. 11 customers affected. | U/G Transformer | Padmount (1ph) | 11 | 305 | 56 | East | 77M1
135022 | 2016-11-25 | Scheduled Outage | Maintenance | VT40 @ 116 Albert was isolated to allow the metering dept to repair metering problem | None | Unknown \ Other | 1 | 60 | 1 | Central | 601
135023 | 2016-11-25 | Scheduled Outage | Maintenance | VT367 @ 90 Spark was isolated to allow the contractor to replace the bus ducts in the vault | None | Unknown \ Other | 1 | 1189 | 20 | Central | TK5TS
135025 | 2016-11-26 | Scheduled Outage | Construction | Customer outage to add new conductor around corner lot. | None | None | 1 | 309 | 5 | East | V11F2
135026 | 2016-11-26 | Scheduled Outage | Maintenance | Customer high voltage maintenance | None | None | 1 | 211 | 4 | West | 39F2
135027 | 2016-11-26 | Scheduled Outage | Maintenance | Customer transferred to new conductor on Old Richmond Rd. | None | None | 1 | 128 | 2 | South | 145F3
135029 | 2016-11-27 | Scheduled Outage | Maintenance | To allow Hydro Ottawa meterning crews to replace a metering center that was damaged due to a fault. | None | None | 13 | 480 | 104 | Central | TD06
135031 | 2016-11-27 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to change poles and re-route secondary conductor | None | None | 8 | 190 | 25 | West | JKGF4
135032 | 2016-11-27 | Scheduled Outage | Construction | Vault V434 at 359 Kent isolated to replace primary cables. 1 customer affected. Florence (UF04) | U/G Cable | PILC | 1 | 387 | 6 | Central | UF04
135033 | 2016-11-27 | Scheduled Outage | Construction | Vault V236 at 1269 Carling isolated to repair defective cable and change switches. 1 customer affected. Carling (SM01) | Vault Equipment | Cable | 1 | 461 | 8 | Central | SM01
135034 | 2016-11-28 | Scheduled Outage | Construction | Glen Carswell and crew to have transformer X30921 open to change a secondary service. Customers notified. | None | None | 6 | 72 | 7 | Central | SK16
135035 | 2016-11-28 | Human Element | Improper Construction/installation | Conductor slapped together due to pole being bumped. | O/H Conductor | O/H Conductor | 214 | 8 | 29 | South | 180F5
135035 | 2016-11-28 | Human Element | Improper Construction/installation | Conductor slapped together due to pole being bumped. | O/H Conductor | O/H Conductor | 993 | 9 | 149 | South | 180F4
135036 | 2016-11-28 | Scheduled Outage | Construction | 2 transformers, X31081 and X31080 isolated by crew to re-arrange plant | None | None | 41 | 200 | 137 | Central | UN07
135037 | 2016-11-28 | Human Element | Incorrect Records/ labelling | VT1585 at 1870 Alta Vista interrupted during planned switching due to a mapping error. 1 customer affected. Russell (TB1UQ) | Vault Equipment | Unknown \ Other | 1 | 14 | 0 | East | TB1UQ
135038 | 2016-11-28 | Scheduled Outage | Maintenance | Shaun Cunninghamto have transformer X26003 open to perform a service disconnect. Customers notified. | None | None | 15 | 45 | 11 | East | AP03
135039 | 2016-11-28 | Scheduled Outage | Vegetation Management | UZ11 from S16135 to EOL on Marcel St. isolated for tree trimming. 26 customers affected. Walkley (UZ11) | None | O/H Conductor | 26 | 245 | 106 | East | UZ11
135040 | 2016-11-28 | Human Element | Incorrect Records/ labelling | Hydro Ottawa crews accidentally spiked a live cable, causing an outage to transformer 4573 (1 customer). A mapping issue is the suspected cause | U/G Cable | PILC | 1 | 81 | 1 | West | BRDF4
135042 | 2016-11-29 | Defective Equipment | Mechanical Failure | Broken cut out lead fell into overhead primary. | O/H Switchgear | Fused Cutout | 78 | 130 | 169 | East | TB06
135045 | 2016-11-30 | Scheduled Outage | Construction | A transformer was isolated at 1670 Heron to allow contractor to pull in new secondary affecting 1 customers. Ellwood ELW06 | None | None | 1 | 110 | 2 | East | ELW06
135046 | 2016-11-30 | Scheduled Outage | Maintenance | A transformer at 4 Stursberg was isolated to replace a transformer affecting 7 customers. Bridlwood BRDF3. | None | Padmount (1ph) | 7 | 112 | 13 | West | BRDF3
135047 | 2016-11-30 | Scheduled Outage | Construction | Transformer #X26893 isolated by crew to install fly tap | None | None | 13 | 45 | 10 | East | TB06
135048 | 2016-11-30 | Scheduled Outage | Construction | Transformer #55D2D-0762 isolated by crew to work on fly tap | None | None | 15 | 80 | 20 | Central | SB03
135050 | 2016-11-30 | Scheduled Outage | Construction | Transformer #X32314 isolated by crew to install new triplex at 390 Greenwood Ave | None | None | 13 | 110 | 24 | Central | UC03
135051 | 2016-11-30 | Scheduled Outage | Construction | Transformer #X36473 isolated by crew to hook up a new service | None | None | 3 | 104 | 5 | West | 44F1
135052 | 2016-11-30 | Scheduled Outage | Construction | Transformer #X49453 isolted by crew for secondary buss work | None | None | 26 | 300 | 130 | East | AE07
135053 | 2016-11-30 | Foreign Interference | Wildlife (Bird/Animal) | S25720 found blown suspected due to animal contact. Affecting 836 customers. Billberry (77M2) | O/H Switchgear | Fused Cutout | 63 | 49 | 51 | East | 77M2
135053 | 2016-11-30 | Foreign Interference | Wildlife (Bird/Animal) | S25720 found blown suspected due to animal contact. Affecting 836 customers. Billberry (77M2) | O/H Switchgear | Fused Cutout | 836 | 43 | 599 | East | 77M2
135054 | 2016-11-30 | Scheduled Outage | Maintenance | Pole replacement at Brighton and Riverside by HOL Crew affecting 90 customers on the SR08 out of Riverdale | None | None | 10 | 110 | 18 | Central | SR08
135054 | 2016-11-30 | Scheduled Outage | Maintenance | Pole replacement at Brighton and Riverside by HOL Crew affecting 90 customers on the SR08 out of Riverdale | None | None | 90 | 240 | 360 | Central | SR08
135055 | 2016-11-30 | Human Element | Improper Equipment/Tool/ Maintenance | 43F3 W phase breaker at Munster DS opened under hold off after live line tool contacted an arrestor while attempting to block a field recloser. 116 customers affected. | Pole Attachement | Arrester | 116 | 75 | 145 | West | 43F3
135057 | 2016-12-01 | Scheduled Outage | Construction | Jim Yeldon to have transformers X33539 and X33545 open to install new services. | None | None | 15 | 90 | 22 | Central | AK02
135058 | 2016-12-01 | Scheduled Outage | Maintenance | The overhead line on Silver was isolated to allow the crews to reconfigure the overhead | None | O/H Conductor | 229 | 155 | 592 | Central | AD07
135059 | 2016-12-01 | Defective Equipment | Mechanical Failure | The primary O/H at 289 Queen Mary was isolated to allow the crew make repairs to burnt connection | O/H Conductor | Ampact | 1 | 171 | 3 | East | SO03
135060 | 2016-12-01 | Scheduled Outage | Construction | Gary Coburn and crew to have transformer X43096 open to transfer secondary bus. | None | None | 10 | 267 | 44 | East | AE07
135061 | 2016-12-01 | Scheduled Outage | Construction | S15728 to EOL was isolated to allow crew to re insulate O/H pole at 5140 Limebank due insulator failure. Limebank (7F4) | None | Insulator | 28 | 37 | 17 | East | 7F4
135062 | 2016-12-01 | Scheduled Outage | Maintenance | Switch S613 at 6 Corvus was isoalted to allow crew to perfrom switch maintenance. Rideau Heights (180F5) | None | None | 1 | 120 | 2 | South | 180F5
135063 | 2016-12-01 | Scheduled Outage | Forced Switching | 145F3 O/H section from Temp 37 W phase to EOL was open to allow crew to perfrom out of phase swiching. Jockvale (145F3) | None | None | 4 | 1 | 0 | South | 145F3
135066 | 2016-12-02 | Scheduled Outage | Vegetation Management | Transformer #X23460 isolated by crew due to tree contact and to straighten out buss | None | None | 19 | 30 | 10 | East | UG04
135067 | 2016-12-02 | Scheduled Outage | Construction | VT520 isolated by crew to replace three phase switch bracket, switches, hot line clams, drop wire and lightning arrestors | None | None | 122 | 63 | 128 | Central | TD07
135068 | 2016-12-02 | Scheduled Outage | Maintenance | Transformer #X23460 isolated by crew after repairs to standpipe made, and triplex replaced | None | None | 19 | 21 | 7 | East | UG04
135069 | 2016-12-02 | Defective Equipment | Mechanical Failure | The 347/600 cables feeding 62 WILLIAM ST from VT463 was isolated to allow the crew repair a defectuve cable | Secondary \ Service | U/G Service | 5 | 17 | 1 | Central | TK6TS
135070 | 2016-12-02 | Scheduled Outage | Maintenance | Transformer TP8335 @ 47 Beacon Way was isolated to allow the crew to preform soil remediation | None | Unknown \ Other | 11 | 270 | 50 | West | MWDF3
135071 | 2016-12-04 | Foreign Interference | Wildlife (Bird/Animal) | Animal found at the base of RX2022. Customer reported seeing a fireball at this location. Field Operators report finding a squirel at base of pole. | O/H Conductor | O/H Conductor | 4000 | 1 | 67 | East | CYRF3
135072 | 2016-12-04 | Scheduled Outage | Maintenance | Transformer TP8856 isolated on Fernbank for replacement and soil remediation | None | None | 15 | 125 | 31 | West | TFXF4
135073 | 2016-12-04 | Defective Equipment | Defective Equipment/ Material | Defective transformer located on pole X34697 @887 Roseview. 6 Customers effected in power outage. | O/H Transformer | O/H Transformer (1ph) | 6 | 310 | 31 | Central | TD12
135074 | 2016-12-05 | Scheduled Outage | Maintenance | S14 to EOL isolated for Trafford Pole Line to perform customer upgrades | None | None | 15 | 332 | 83 | South | 47F2
135075 | 2016-12-05 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30338 TO TRANSFER SERVICES TO NEW POLE | None | None | 5 | 95 | 8 | Central | UF08
135076 | 2016-12-05 | Scheduled Outage | Construction | At 9:58am section of UC02 was isolated to allow crew to install new pole. 25 customers affected. Clyde (UC02) | None | None | 25 | 222 | 92 | Central | UC02
135077 | 2016-12-05 | Defective Equipment | Defective Equipment/ Material | S21908W opened due to suspected cable fault between S21908W and transformer 2529W on Coutnry Lane. Bridlewood (BRDF5). | U/G Cable | XLPE | 59 | 97 | 95 | West | BRDF5
135078 | 2016-12-05 | Defective Equipment | Electrical Failure | SM 10 breaker tripped, due to egress cable fault | U/G Cable | PILC | 205 | 73 | 249 | Central | SM10
135080 | 2016-12-06 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 46 | 320 | 245 | Central | TD01
135081 | 2016-12-06 | Scheduled Outage | Construction | Pole replacement. | None | None | 25 | 467 | 195 | Central | UC03
135081 | 2016-12-06 | Scheduled Outage | Construction | Pole replacement. | None | None | 55 | 467 | 428 | Central | UC02
135082 | 2016-12-06 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 12 | 133 | 27 | East | ELW04
135085 | 2016-12-06 | Defective Equipment | Electrical Failure | Outage on transformer X27100. Cause unknown. Rudy Grisel refused and restored power. | O/H Switchgear | Fused Cutout | 10 | 138 | 23 | East | TB14
135086 | 2016-12-07 | Scheduled Outage | Maintenance | The 4Kv vault V774 @ 1161 Wellington was isolated to allow the crews to transfer the vault to the new cables | None | Cable | 141 | 283 | 665 | Central | UJ05
135088 | 2016-12-07 | Scheduled Outage | Vegetation Management | UZ05 OH isolted from S17729 to EOIL for forestry affecting 19 customers. Walkley (UZ05) | None | None | 19 | 129 | 41 | East | UZ05
135090 | 2016-12-07 | Scheduled Outage | Maintenance | Crews isolated OH transformer at pole X33373 tio transfer secondary bus affecting 7 customers. Epworth (EPWF3) | O/H Transformer | O/H Transformer (1ph) | 7 | 256 | 30 | South | EPWF3
135091 | 2016-12-07 | Scheduled Outage | Maintenance | Crews isolated OH transformer at pole X36530 tio transfer secondary bus affecting 5 customers. Epworth (EPWF3) | O/H Transformer | O/H Transformer (1ph) | 5 | 250 | 21 | South | EPWF3
135092 | 2016-12-07 | Scheduled Outage | Construction | Pole replacement. | None | None | 156 | 371 | 965 | East | AE07
135096 | 2016-12-07 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X31506 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 8 | 63 | 8 | Central | TW22
135097 | 2016-12-07 | Scheduled Outage | Construction | 3 transformers, #X32316, X32358 and X35510 isolated by crew to transfer plant | None | None | 17 | 275 | 78 | Central | UC03
135098 | 2016-12-08 | Scheduled Outage | Construction | Transformer 2922 at 177 Grassy Plains isolated for replacmenet due to oil leak. 9 customers affected. Terry Fox (TFXF5) | None | Padmount (1ph) | 9 | 177 | 27 | West | TFXF5
135099 | 2016-12-08 | Scheduled Outage | Maintenance | Vault Maintenance at 275 Charlotte affecting 1 customer on the 405 out of King Edward Terminal | None | None | 1 | 105 | 2 | Central | 405
135101 | 2016-12-08 | Scheduled Outage | Vegetation Management | Tree trimming on Linton affecting 37 customers on the Walkley UZ11 | None | None | 37 | 248 | 153 | East | UZ11
135102 | 2016-12-08 | Defective Equipment | Defective Equipment/ Material | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X29677 | O/H Switchgear | Fused Cutout | 19 | 67 | 21 | East | SO03
135103 | 2016-12-08 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35515 TO TRANSFER HYDRO PLANT FOR TRANSFORMER UP-GRADE | None | None | 6 | 125 | 12 | Central | AH14
135104 | 2016-12-08 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35509 FOR TRANSFORMER UP-GRADE | None | None | 2 | 234 | 8 | Central | AH14
135105 | 2016-12-09 | Scheduled Outage | Vegetation Management | Overhead circuit from S10518 to EOL on Elmhurst isolated for tree trimming. 17 customers affected. Lincoln Heights (TD05) | None | None | 17 | 331 | 94 | Central | TD05
135106 | 2016-12-09 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X27313 TO RE-ARRANGE HYDRO PLANT | None | None | 10 | 215 | 36 | East | UZ05
135107 | 2016-12-09 | Scheduled Outage | Maintenance | ISOLATED K0393 TO REPLACE DAMAGED PEDESTAL | None | None | 21 | 255 | 89 | East | UA02
135108 | 2016-12-10 | Scheduled Outage | Construction | Transformer #X31713 isolated by crew to replace triplex and connections | None | None | 10 | 43 | 7 | Central | UF07
135109 | 2016-12-10 | Defective Equipment | Electrical Failure | secondary short caused X36404 transformer fuse blew | Secondary \ Service | O/H Service | 7 | 143 | 17 | South | 140F5
135111 | 2016-12-11 | Scheduled Outage | Construction | Transformer #X21656 isolated by crew to upgrade transformer | None | None | 1 | 120 | 2 | East | AC14
135112 | 2016-12-11 | Scheduled Outage | Construction | Transformer #X16686 isolated by crew for a pole replacement | None | None | 9 | 157 | 24 | East | 249F2
135113 | 2016-12-12 | Foreign Interference | Vehicle | outage to replace pole hit by car | Pole | Pole | 194 | 36 | 116 | West | 624F6
135114 | 2016-12-12 | Defective Equipment | Defective Equipment/ Material | Barrier Board fell on to bushing in KT24 at 22 Fox Hunt Ave. | U/G Transformer | Kiosk (1ph) | 222 | 52 | 192 | East | 2211
135115 | 2016-12-13 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry crews to clear trees from the overhead conductor at the rear of 2407 Cabot St | None | None | 14 | 175 | 41 | East | AF02
135117 | 2016-12-13 | Scheduled Outage | Maintenance | To allow Hydro Ottawa line crews to ID underground cables for future re-configuration | None | None | 65 | 46 | 50 | West | JKGF4
135118 | 2016-12-13 | Scheduled Outage | Maintenance | Transformer 301 at 1 Shearer isolated to replace elbow and insert. 10 customers affected. Bridlewood (BRDF4) | None | Padmount (1ph) | 10 | 114 | 19 | West | BRDF4
135119 | 2016-12-13 | Scheduled Outage | Maintenance | TP3726 isolated for soil remediation by Drainall and Antrim | None | None | 10 | 109 | 18 | West | TFXF5
135120 | 2016-12-13 | Scheduled Outage | Construction | Adrian Henry and crew to have transformer X49453 open to transfer secondary bus. | None | None | 26 | 253 | 110 | East | AE07
135122 | 2016-12-14 | Scheduled Outage | Maintenance | To re-tolerance 15kV Oil Circuit Breaker at VT475 affecting 1 customer on the 415 out of King Edward Terminal | None | None | 1 | 64 | 1 | Central | 415
135123 | 2016-12-14 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry to clear trees from the O/H conductor in the rear of 688 & 691 Farmington and at 722 Fielding | None | None | 89 | 257 | 381 | East | UZ05
135124 | 2016-12-14 | Scheduled Outage | Construction | TP8330 at 1386 Halton isolated for replacement due to oil leak. 6 customers affected. Marchwood (MWDF3) | None | None | 6 | 72 | 7 | West | MWDF3
135125 | 2016-12-14 | Scheduled Outage | Maintenance | Isolation to allow contractor to connect new secondary cables. | None | None | 1 | 239 | 4 | South | EPWF4
135126 | 2016-12-14 | Defective Equipment | Defective Equipment/ Material | ISOLATED AND REPLACED BROKEN SWITCH FEEDING TRANSFORMER X25681 | O/H Switchgear | Fused Cutout | 9 | 45 | 7 | Central | SB07
135127 | 2016-12-15 | Adverse Weather | Extreme Wind | secondary wrapped together fed from o/h transformer X33539 | Secondary \ Service | O/H Service | 8 | 142 | 19 | Central | AK02
135128 | 2016-12-15 | Scheduled Outage | Maintenance | planned outage to re-arrange cables and transformers | None | None | 169 | 428 | 1206 | West | JKGF4
135129 | 2016-12-15 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 152 | 132 | 334 | East | UZ05
135130 | 2016-12-15 | Foreign Interference | Vehicle | Commerciale vehicle caught guy wire and broke pole X18231, insulators and span guy. | Pole | Pole | 0 | 22 | 0 | East | LTM04
135130 | 2016-12-15 | Foreign Interference | Vehicle | Commerciale vehicle caught guy wire and broke pole X18231, insulators and span guy. | Pole | Pole | 7 | 43 | 5 | East | LTM04
135130 | 2016-12-16 | Foreign Interference | Vehicle | Commerciale vehicle caught guy wire and broke pole X18231, insulators and span guy. | Pole | Pole | 44 | 271 | 199 | East | LTM04
135131 | 2016-12-16 | Defective Equipment | Defective Equipment/ Material | to make emergency repairs to a broken pole on Belgreen | Pole | Pole | 12 | 211 | 42 | East | LTM04
135135 | 2016-12-19 | Defective Equipment | Electrical Failure | Transformer had a failure on the insert causing an auto reclose on the circuit and a fused dip to open affecting 1875 customers. Load was restored in sections. QCH 160F1 | U/G Cable Attachement | Elbow \ Insert | 6 | 321 | 32 | South | 145F1
135135 | 2016-12-19 | Defective Equipment | Electrical Failure | Transformer had a failure on the insert causing an auto reclose on the circuit and a fused dip to open affecting 1875 customers. Load was restored in sections. QCH 160F1 | U/G Cable Attachement | Elbow \ Insert | 30 | 109 | 54 | South | 145F1
135135 | 2016-12-19 | Defective Equipment | Electrical Failure | Transformer had a failure on the insert causing an auto reclose on the circuit and a fused dip to open affecting 1875 customers. Load was restored in sections. QCH 160F1 | U/G Cable Attachement | Elbow \ Insert | 103 | 25 | 43 | South | 145F1
135135 | 2016-12-19 | Defective Equipment | Electrical Failure | Transformer had a failure on the insert causing an auto reclose on the circuit and a fused dip to open affecting 1875 customers. Load was restored in sections. QCH 160F1 | U/G Cable Attachement | Elbow \ Insert | 103 | 57 | 98 | South | 145F1
135135 | 2016-12-19 | Defective Equipment | Electrical Failure | Transformer had a failure on the insert causing an auto reclose on the circuit and a fused dip to open affecting 1875 customers. Load was restored in sections. QCH 160F1 | U/G Cable Attachement | Elbow \ Insert | 103 | 80 | 137 | South | 145F1
135137 | 2016-12-19 | Defective Equipment | Mechanical Failure | UJ02 OH phase down, radial section isolated from Line clamps at Laurel. 118 customers affected | O/H Conductor | O/H Conductor | 118 | 95 | 187 | Central | UJ02
135138 | 2016-12-19 | Scheduled Outage | Maintenance | K184 isolated to replace fiber boards and insulators affecting 13 customers on the Walkley UZ04 | None | None | 13 | 161 | 35 | East | UZ04
135139 | 2016-12-20 | Scheduled Outage | Maintenance | At 8:57am transformer 3720 at 11 Dunn was isolated for full remediation. 10 customers affected. Marchwood (MWDF2) | None | None | 10 | 276 | 46 | West | MWDF2
135140 | 2016-12-20 | Scheduled Outage | Construction | At 9:28am transformer X5006 was isolated for work. 1 customer affected. Jockvale (145F3) | None | None | 1 | 267 | 4 | South | 145F3
135141 | 2016-12-21 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 46 | 71 | 54 | Central | TW22
135142 | 2016-12-21 | Scheduled Outage | Construction | At 8:57am damaged transformer 302 was isolated for replacement. 10 customers affected. Bridlewood (BRDF3) | None | None | 10 | 78 | 13 | West | BRDF3
135143 | 2016-12-21 | Defective Equipment | Electrical Failure | crew to investigate why transformer fuse in V120 is blown. | Vault Equipment | Switch | 71 | 60 | 71 | Central | AB03
135145 | 2016-12-22 | Scheduled Outage | Maintenance | New elbow termination installed on new cable. | None | None | 16 | 14 | 4 | West | BRDF5
135146 | 2016-12-23 | Scheduled Outage | Maintenance | V707 at 50 Selkirk isolated to change transformers. 1 customer affected. Eastview (UT03) | None | Transformer | 1 | 234 | 4 | East | UT03
135147 | 2016-12-24 | Defective Equipment | Defective Equipment/ Material | TL18 breaker opened due to a possible cable fault on TL2SB cable. Outage cause loss of supply to SBT4 bank at Bronson Substation and 1268 customers. | U/G Cable | PILC | 1268 | 49 | 1036 | Central | TL2SB
135148 | 2016-12-25 | Defective Equipment | Mechanical Failure | Broken porcelin cut out. | O/H Switchgear | Fused Cutout | 3 | 87 | 4 | Central | AD02
135149 | 2016-12-27 | Defective Equipment | Mechanical Failure | MWDF3 CB auto-reclosed and fuse S25456 white phase blew due to broken insulator at March Rd E of Huntmar. | Pole Attachement | Insulator | 196 | 311 | 1016 | West | MWDF3
135150 | 2016-12-27 | Defective Equipment | Electrical Failure | 24F8 circuit auto reclosed and 539 R opened due to cable fault between TP5424 and 3833R. The elbow and insert at 4136R was also found blown off and broken, as well as blown fuse in transformer 3833. 713 customers affected. Beaverbrook (24F8) | U/G Cable | Unknown \ Other | 13 | 112 | 24 | West | 24F8
135150 | 2016-12-27 | Defective Equipment | Electrical Failure | 24F8 circuit auto reclosed and 539 R opened due to cable fault between TP5424 and 3833R. The elbow and insert at 4136R was also found blown off and broken, as well as blown fuse in transformer 3833. 713 customers affected. Beaverbrook (24F8) | U/G Cable | Unknown \ Other | 19 | 371 | 117 | West | 24F8
135150 | 2016-12-27 | Defective Equipment | Electrical Failure | 24F8 circuit auto reclosed and 539 R opened due to cable fault between TP5424 and 3833R. The elbow and insert at 4136R was also found blown off and broken, as well as blown fuse in transformer 3833. 713 customers affected. Beaverbrook (24F8) | U/G Cable | Unknown \ Other | 53 | 136 | 120 | West | 24F8
135151 | 2016-12-27 | Foreign Interference | Customer Equipment | VTS644-2CZZ-CB15 tripped and caused the VTM644-CB1 breaker to trip, customer suspect water leak on their secondary equipment. Customer isolated the CB15 breaker to investigate . | Customer Owned | Customer-Owned | 1 | 126 | 2 | Central | 5211
135152 | 2016-12-27 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27694 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 10 | 122 | 20 | Central | 505
135153 | 2016-12-27 | Defective Equipment | Electrical Failure | TM18 CB opened, suspected cable fault. Load transferred to alternate supply. 712 customers affected. Carling (TM2AK) | U/G Cable | PILC | 712 | 46 | 546 | Central | TM2AK
135154 | 2016-12-28 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X23886 TO DISCONNECT TWO OVERHEAD SERVICES | None | None | 11 | 20 | 4 | Central | TH06
135156 | 2017-01-03 | Foreign Interference | Vehicle | ISOLATED TRANSFORMER X28130 TO REPAIR OPEN BUSS THAT HAD BEEN DAMAGED BY DUMP TRUCK HITTING OVERHEAD TRIPLEX SERVICE TO 770 BROOKFIELD | None | None | 9 | 105 | 16 | East | UZ04
135157 | 2017-01-03 | Tree Contacts | Falling Tree | Primary line down caused buy broken tee covered in ice. | O/H Conductor | O/H Conductor | 57 | 323 | 307 | Central | UC02
135158 | 2017-01-03 | Tree Contacts | Falling Tree | RX2063 auto reclosed when large tree fell across 3 phase line at the rear of 1465 Farmsworth | O/H Conductor | O/H Conductor | 98 | 194 | 317 | East | TB2JP
135158 | 2017-01-03 | Tree Contacts | Falling Tree | RX2063 auto reclosed when large tree fell across 3 phase line at the rear of 1465 Farmsworth | O/H Conductor | O/H Conductor | 416 | 350 | 2427 | East | TB2JP
135160 | 2017-01-03 | Tree Contacts | Falling Tree | CS22203 was opened to clear tree limbs from overhead. | O/H Conductor | O/H Conductor | 78 | 70 | 91 | East | 7F4
135161 | 2017-01-03 | Tree Contacts | Falling Tree | G606 found open @ 6490 Russell Rd. Crews found trees down across the road on Farmers Way and trees in primary at the end of line. G493 is opened and tagged C/T at this time. Crews also found trees in primary at G240 fuse is opened and tagged C/T | O/H Conductor | O/H Conductor | 10 | 653 | 109 | East | 249F2
135161 | 2017-01-03 | Tree Contacts | Falling Tree | G606 found open @ 6490 Russell Rd. Crews found trees down across the road on Farmers Way and trees in primary at the end of line. G493 is opened and tagged C/T at this time. Crews also found trees in primary at G240 fuse is opened and tagged C/T | O/H Conductor | O/H Conductor | 161 | 377 | 1012 | East | 249F2
135162 | 2017-01-03 | Tree Contacts | Broken Branch | Crews removed a large pine branch off the overhead | O/H Conductor | O/H Conductor | 122 | 268 | 545 | South | 200F2
135164 | 2017-01-03 | Tree Contacts | Broken Branch | S407 White Phase fuse found opened. | O/H Conductor | O/H Conductor | 63 | 13 | 14 | South | 72F4
135164 | 2017-01-03 | Tree Contacts | Broken Branch | S407 White Phase fuse found opened. | O/H Conductor | O/H Conductor | 285 | 187 | 888 | South | 72F4
135165 | 2017-01-03 | Tree Contacts | Broken Branch | Not yet known. | O/H Conductor | O/H Conductor | 79 | 219 | 288 | South | 170F3
135166 | 2017-01-03 | Scheduled Outage | Maintenance | To make repairs to secondary Bus of X25873 on Chamberlain | None | None | 3 | 26 | 1 | Central | SB11
135167 | 2017-01-03 | Defective Equipment | Mechanical Failure | Downed conductor at 439 Brennan on the UL04 White phase. | O/H Conductor | O/H Conductor | 51 | 95 | 81 | Central | UL04
135169 | 2017-01-03 | Tree Contacts | Broken Branch | Trees in overhead caused power outage. | O/H Conductor | O/H Conductor | 570 | 160 | 1520 | South | 84F3
135171 | 2017-01-03 | Scheduled Outage | Maintenance | To clear tree from the overhead | None | None | 50 | 780 | 650 | East | UZ12
135172 | 2017-01-03 | Tree Contacts | Falling Tree | Tree on the single phase primary overhead at 17 Dorland Cres | None | None | 42 | 198 | 139 | South | 47F3
135194 | 2017-01-03 | Tree Contacts | Falling Tree | Tree in wires required primary overhead isolation to repair affecting 2 customers. Lietrim 249F2 | O/H Conductor | O/H Conductor | 2 | 1073 | 36 | East | 249F2
135213 | 2017-01-05 | Tree Contacts | Broken Branch | S23301 to EOL to allow crews to remove branches from OH and make necessary repairs, affecting 40 customers. Hinchey (TH01) | O/H Conductor | O/H Conductor | 40 | 93 | 62 | Central | TH01
135214 | 2017-01-05 | Scheduled Outage | Vegetation Management | S12414 opened to allow removal of tree from overhead line. | None | None | 17 | 124 | 35 | Central | TW22
135216 | 2017-01-05 | Adverse Weather | Freezing Rain | UV03 from the rear of 1307 Southwood to EOL isolated to allow crew to repair broken conductor. 500 customers affected. Edwin (UV03) | O/H Conductor | O/H Conductor | 10 | 75 | 12 | Central | UV03
135216 | 2017-01-05 | Adverse Weather | Freezing Rain | UV03 from the rear of 1307 Southwood to EOL isolated to allow crew to repair broken conductor. 500 customers affected. Edwin (UV03) | O/H Conductor | O/H Conductor | 500 | 32 | 267 | Central | UV03
135216 | 2017-01-16 | Adverse Weather | Freezing Rain | UV03 from the rear of 1307 Southwood to EOL isolated to allow crew to repair broken conductor. 500 customers affected. Edwin (UV03) | O/H Conductor | O/H Conductor | 95 | 12 | 19 | South | FAL03
135219 | 2017-01-05 | Tree Contacts | Tree Growth/ Untrimmed Tree | TB 10 breaker opened, (5303 cct) under hold off. Circuit patrolled, no direct cause found. Possible tree contact. | O/H Conductor | O/H Conductor | 173 | 52 | 150 | East | 5303
135220 | 2017-01-05 | Scheduled Outage | Vegetation Management | S27382 opened to allow crew to trim trees. | None | O/H Conductor | 25 | 67 | 28 | Central | TH01
135221 | 2017-01-05 | Scheduled Outage | Maintenance | S23681 to EOL isolated To allow crew to make repairs to primary and pole. | None | O/H Conductor | 5 | 61 | 5 | South | 145F3
135222 | 2017-01-06 | Scheduled Outage | Vegetation Management | To install new secondaries and tree trimming. | None | None | 7 | 120 | 14 | Central | UN05
135223 | 2017-01-05 | Tree Contacts | Broken Branch | OH transformer X45480 was interupted to allow cres to remove branch from Down guy and secondary bus affecting 12 customers. Woodroffe (TW17) | O/H Transformer | O/H Transformer (1ph) | 12 | 62 | 12 | Central | TW17
135224 | 2017-01-06 | Scheduled Outage | Maintenance | S102 opened at 1159 Moodie to change burning live line clamp. 1 customer affected. Bells Corners (47F6) | None | Hot-Line Clamp | 1 | 35 | 1 | South | 47F6
135225 | 2017-01-06 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X27229 TO REPLACE BROKEN TRIPLEX SERVICE | None | None | 15 | 40 | 10 | East | UQ07
135226 | 2017-01-06 | Scheduled Outage | Construction | Travis Rowe to have transformer X44295 open to reconnect an overhead service. Customers notified. | None | None | 10 | 45 | 8 | East | TB2JP
135227 | 2017-01-06 | Scheduled Outage | Construction | Kevin McKenna to have transformer X33763 open to install a new service. Customers notified. | None | None | 11 | 72 | 13 | Central | TW22
135228 | 2017-01-06 | Defective Equipment | Defective Equipment/ Material | G207W phase opened, Crew patrolled line and did not find anything. G207W was refused and all custoemrs were restored. Lmebank (LMBF5) | O/H Switchgear | Fused Cutout | 5 | 114 | 10 | East | LMBF5
135230 | 2017-01-07 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer X21626 open due to tree hedge contact with secondary open bus at 80 Pineglen. Rideau Heights (180F4) | O/H Transformer | O/H Transformer (1ph) | 8 | 67 | 9 | South | 180F4
135231 | 2017-01-08 | Defective Equipment | Mechanical Failure | V199 primary dip fuses at pole 55D2A-0223 opened due to defective fuses. Crew replaced procelain box switches and refused switch. | O/H Switchgear | Fused Cutout | 53 | 65 | 57 | Central | AM04
135232 | 2017-01-08 | Scheduled Outage | Maintenance | Transformer X21626 was open to allow crew to replace defective secondary lead. Richmond North (RHNF3) | Secondary \ Service | Unknown \ Other | 12 | 32 | 6 | West | RHNF3
135233 | 2017-01-09 | Scheduled Outage | Construction | Patrick Brisson to have transformer 55D1a-0775 open to install new spun bus and run new services. Customers notified. | None | None | 6 | 124 | 12 | Central | UL05
135234 | 2017-01-10 | Defective Equipment | Electrical Failure | At 9:06am transformer 3833 was isolated for replacement. 13 customers affected. Beaverbrook (24F8) | U/G Transformer | Padmount (1ph) | 13 | 157 | 34 | West | 24F8
135235 | 2017-01-10 | Scheduled Outage | Forced Switching | ISOLATED TRANSFOMER X29938 TO REMOVE BROKEN BRANCH OFF THE OPEN WIRE BUSS | None | None | 18 | 30 | 9 | Central | SR02
135236 | 2017-01-11 | Loss Of Supply | Transmission Inadvertent | Hydro One reports the 62M2 A/R/A tripping off Casselman DS and advised high winds were suspected. | None | None | 2710 | 1 | 45 | East | 62M2 (Casselman MS)
135237 | 2017-01-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer fuse X39753 at 21 Bedale Dr. opened due to tree contact on primary transofrmer lead. 15 customers affected. Bayshore (49F6)also required new switch for transformer. | O/H Transformer | O/H Transformer (1ph) | 15 | 335 | 84 | South | 49F6
135238 | 2017-01-11 | Loss Of Supply | Transmission Inadvertent | Hydro One reports 62M2 A/R/A High Winds Suspected. | None | None | 2710 | 2 | 90 | East | 62M2 (Casselman MS)
135239 | 2017-01-11 | Loss Of Supply | Transmission Inadvertent | Hydro One loss of supply from 62M2, A/R/A high winds suspected. | None | None | 2710 | 1 | 45 | East | 62M2 (Casselman MS)
135241 | 2017-01-11 | Adverse Environment | Contamination (Salt) | TD12 RB phases from S12240 to EOL isolated due to pole fire on Penny Dr. 161 customers affected. Lincoln Heights (TD12) | None | Pole | 13 | 426 | 92 | Central | TD12
135241 | 2017-01-11 | Adverse Environment | Contamination (Salt) | TD12 RB phases from S12240 to EOL isolated due to pole fire on Penny Dr. 161 customers affected. Lincoln Heights (TD12) | None | Pole | 31 | 8 | 4 | Central | TD12
135241 | 2017-01-11 | Adverse Environment | Contamination (Salt) | TD12 RB phases from S12240 to EOL isolated due to pole fire on Penny Dr. 161 customers affected. Lincoln Heights (TD12) | None | Pole | 69 | 40 | 46 | Central | TD12
135241 | 2017-01-11 | Adverse Environment | Contamination (Salt) | TD12 RB phases from S12240 to EOL isolated due to pole fire on Penny Dr. 161 customers affected. Lincoln Heights (TD12) | None | Pole | 161 | 44 | 118 | Central | TD12
135242 | 2017-01-11 | Defective Equipment | Electrical Failure | R & W phase of S17474 at 2625 Queensview opened during wind storm. 434 customers affected. Lincoln TD05.burnt lead to K656 was burnt off. | O/H Switchgear | Inline Switch | 434 | 320 | 2315 | Central | TD05
135243 | 2017-01-11 | Adverse Weather | Extreme Wind | RX2024 tripped during wind storm. Recloser was blocked for tree trimmers. | None | None | 281 | 115 | 539 | West | BECKF2
135244 | 2017-01-11 | Defective Equipment | Electrical Failure | line side clamp burnt of switch S478 | O/H Switchgear | Inline Switch | 54 | 165 | 148 | South | 47F3
135245 | 2017-01-11 | Defective Equipment | Electrical Failure | At 6:45am RX2024 Red phase reclosed and locked out due to an issue on a customer owned primary. The customer primary 2980 Dywer Hill was fuse at was blown but it the RX2024 also tripped. 169 customers affected. Beckwith (BeckF2) | Pole | Insulation Failure (Pole Fire) | 169 | 135 | 380 | West | BECKF2
135247 | 2017-01-11 | Tree Contacts | Broken Branch | At 10:02am transformer at X26852 was isolated to remove tree limbs on secondary. 6 customers affected. Urbandale (AE01) | None | None | 6 | 16 | 2 | East | AE01
135248 | 2017-01-11 | Scheduled Outage | Construction | At 09:26am crew isolated TP9784 to install new secondary. 13 customers affected. Moulton (8F4) | None | None | 13 | 18 | 4 | East | 8F4
135249 | 2017-01-11 | Scheduled Outage | Vegetation Management | tree trimming at rea of 505 Brennan | None | None | 8 | 199 | 27 | Central | UL04
135250 | 2017-01-11 | Loss Of Supply | Transmission Inadvertent | At 10:41am a loss of supply from Hydro One due to a pole fire on their lines caused all the load at our Casselman station to be interrupted. 1724 customers affected. St-Isiodore (62M2) | None | None | 1724 | 299 | 8591 | East | 62M2 (Casselman MS)
135252 | 2017-01-12 | Defective Equipment | Mechanical Failure | TB10 (5303) Tripped due to the 5303 dips to VT264 going defective at Russell and Southvale | U/G Cable Attachement | Pothead | 89 | 8 | 12 | East | 5303
135252 | 2017-01-12 | Defective Equipment | Mechanical Failure | TB10 (5303) Tripped due to the 5303 dips to VT264 going defective at Russell and Southvale | U/G Cable Attachement | Pothead | 90 | 6 | 9 | East | 5303
135252 | 2017-01-12 | Defective Equipment | Mechanical Failure | TB10 (5303) Tripped due to the 5303 dips to VT264 going defective at Russell and Southvale | U/G Cable Attachement | Pothead | 173 | 75 | 216 | East | 5303
135253 | 2017-01-12 | Defective Equipment | Imminent Failure | To replace leaking transformer. | U/G Transformer | Padmount (3ph) | 3 | 185 | 9 | West | BRDF6
135254 | 2017-01-12 | Scheduled Outage | Construction | Transformer #X23497 isolated by crew to install new pole | None | None | 10 | 270 | 45 | East | AA02
135255 | 2017-01-12 | Tree Contacts | Broken Branch | suspected fallen tree branch on secondary | O/H Transformer | O/H Transformer (1ph) | 9 | 54 | 8 | Central | 505
135256 | 2017-01-12 | Tree Contacts | Broken Branch | tree on primary | O/H Conductor | O/H Conductor | 21 | 61 | 21 | Central | SH04
135257 | 2017-01-13 | Scheduled Outage | Vegetation Management | S11625 to end of line was isoalted to allow crew to perfrom tree trimming at 31 Higwood and 30 Beaverton. 99 customers were affected. Parkwoodhills (190F5) | None | None | 99 | 245 | 404 | South | 190F5
135258 | 2017-01-13 | Scheduled Outage | Forced Switching | S457 at 162 Viewmount to EOL was isoalted to allow crew to replace a defective transformer cut outs on transformer X37248 and X37249. 46 customers were affected . Borden Farms. BDFF1 | None | Fused Cutout | 46 | 51 | 39 | South | 130F1
135259 | 2017-01-13 | Scheduled Outage | Construction | Bill Armstrong to have transformer X23843 open to install a new service. Customers notified. | None | None | 2 | 37 | 1 | East | AP04
135260 | 2017-01-13 | Scheduled Outage | Construction | Warren Kelly and crew to have transformer X31191 open to plant a new pole. Customers notified. | None | None | 10 | 117 | 20 | Central | UF08
135261 | 2017-01-14 | Defective Equipment | Electrical Failure |  | U/G Cable Attachement | Pothead | 258 | 51 | 219 | East | 5310
135264 | 2017-01-16 | Scheduled Outage | Forced Switching | 12 trabsfirners were interruped due to out of phase condition which was restored back to normal. | None | Padmount (1ph) | 95 | 12 | 19 | South | FAL03
135265 | 2017-01-15 | Unknown/Other | Unknown | S16879 R at 2635 Hickerson Cres. opened. Line was patrolled, no cause found. 41 customers affected. Edwin (UV07) | Unknown \ Other | Unknown \ Other | 41 | 93 | 64 | Central | UV07
135266 | 2017-01-16 | Scheduled Outage | Maintenance | 4kV transformer bus at V724 was isolated to change a defective transformer. 1 customer affected. Urbandale (AE07) | None | Transformer | 1 | 121 | 2 | East | AE07
135267 | 2017-01-16 | Defective Equipment | Electrical Failure | S1401 R phase at 53 Maple View Cres. opened due to defectvie insulator at TE1824. 105 customers affected. Centrepointe (87F4) | U/G Transformer | Padmount (1ph) | 12 | 300 | 60 | South | 87F4
135267 | 2017-01-16 | Defective Equipment | Electrical Failure | S1401 R phase at 53 Maple View Cres. opened due to defectvie insulator at TE1824. 105 customers affected. Centrepointe (87F4) | U/G Transformer | Padmount (1ph) | 88 | 55 | 81 | South | 87F4
135267 | 2017-01-16 | Defective Equipment | Electrical Failure | S1401 R phase at 53 Maple View Cres. opened due to defectvie insulator at TE1824. 105 customers affected. Centrepointe (87F4) | U/G Transformer | Padmount (1ph) | 105 | 82 | 144 | South | 87F4
135268 | 2017-01-16 | Scheduled Outage | Maintenance | Dalton Henry and crew to have transformer X35805 isolated to make repairs to a burned secondary padel. | None | None | 8 | 75 | 10 | South | 190F5
135270 | 2017-01-17 | Scheduled Outage | Construction | Transformer #K00418 isolated by crew to set up to replace damaged pedestal | None | None | 17 | 5 | 1 | East | AN05
135271 | 2017-01-17 | Scheduled Outage | Construction | Transformer #X35508 isolated by crew to install new pole. | None | None | 4 | 199 | 13 | Central | AH14
135273 | 2017-01-18 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X25692 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 16 | 46 | 12 | Central | TH11-NIU
135274 | 2017-01-18 | Scheduled Outage | Maintenance | Transformer #X20170 isolated by crew to repair secondary connection on the transformer | None | None | 4 | 38 | 3 | East | 249F2
135276 | 2017-01-19 | Defective Equipment | Electrical Failure | At 10:28am TE1254 was isolated to allow crew to replace transformer. 11 customers affected. Bilberry (77M1) | U/G Transformer | Padmount (1ph) | 11 | 144 | 26 | East | 77M1
135277 | 2017-01-20 | Scheduled Outage | Maintenance | seal up duct openings to prevent potential water issues. | None | None | 1 | 69 | 1 | Central | AB07
135278 | 2017-01-21 | Defective Equipment | Electrical Failure | Blown cable pothead at S29252 VT270 2421 Lancaster Road | U/G Cable Attachement | Pothead | 2 | 10 | 0 | East | 5310
135278 | 2017-01-21 | Defective Equipment | Electrical Failure | Blown cable pothead at S29252 VT270 2421 Lancaster Road | U/G Cable Attachement | Pothead | 4 | 12 | 1 | East | 5310
135278 | 2017-01-21 | Defective Equipment | Electrical Failure | Blown cable pothead at S29252 VT270 2421 Lancaster Road | U/G Cable Attachement | Pothead | 5 | 11 | 1 | East | 5310
135278 | 2017-01-21 | Defective Equipment | Electrical Failure | Blown cable pothead at S29252 VT270 2421 Lancaster Road | U/G Cable Attachement | Pothead | 230 | 19 | 73 | East | 5310
135278 | 2017-01-21 | Defective Equipment | Electrical Failure | Blown cable pothead at S29252 VT270 2421 Lancaster Road | U/G Cable Attachement | Pothead | 248 | 11 | 45 | East | 5310
135278 | 2017-01-21 | Defective Equipment | Electrical Failure | Blown cable pothead at S29252 VT270 2421 Lancaster Road | U/G Cable Attachement | Pothead | 258 | 68 | 292 | East | 5310
135279 | 2017-01-21 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X43886 at 6 Galt opened due to squirrel contact. 1 customer was affected. Riverdale (TR3UY) | O/H Transformer | O/H Transformer (1ph) | 1 | 60 | 1 | Central | TR3UY
135280 | 2017-01-21 | Unknown/Other | Unknown | Red phase fuse found blown at SW136-F1, WB fuses open to test cable. 2 customers afftected. Russell TS (5310). | U/G Switchgear | Unknown \ Other | 2 | 45 | 2 | East | 5310
135283 | 2017-01-22 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused transformer X34478 and swicht G508 W phase to blow.52 customers were affected. Uplands (4801F8) | O/H Switchgear | Fused Cutout | 52 | 103 | 89 | East | 4801F8
135284 | 2017-01-22 | Scheduled Outage | Construction | Rudy Grisel and crew to have transformer X16478 open to and isolated to replace with padmount TP11555 and install switch S21195. Customers notified. | None | None | 3 | 299 | 15 | East | 7F4
135285 | 2017-01-23 | Defective Equipment | Electrical Failure | Transformer TP1319 at 7 Windfield Cres was isoalted to allow crew to replace elbows and inserts. 9 customers were affected. Terry Fox (TFXF5) | U/G Cable Attachement | Elbow \ Insert | 9 | 163 | 24 | West | TFXF5
135286 | 2017-01-23 | Scheduled Outage | Vegetation Management | G997 to EOL was isoalted to allow forestry crew to perform tree trimming at 3780 Louiseize. Leitrim (249F2) | None | None | 1 | 359 | 6 | East | 249F2
135287 | 2017-01-23 | Scheduled Outage | Maintenance | Carl Donaldson and crew to have transformer X12978 open to install new services. Customers notified. | None | None | 7 | 75 | 9 | East | 7F2
135288 | 2017-01-23 | Scheduled Outage | Construction | 2 transformers (X31196 and X31197, located at 502 and 508 Mcleod), isolated by crew to re-arrange plant | None | None | 18 | 25 | 8 | Central | UF08
135289 | 2017-01-23 | Scheduled Outage | Construction | Transformer #X10382 isolated by crew to install new switch, cross arm etc | None | None | 1 | 103 | 2 | West | RHNF1
135290 | 2017-01-23 | Scheduled Outage | Construction | Dave Burns and crew to have transformer X31198 open to re-arrange plant for pole replacement. Customers notified. | None | None | 9 | 60 | 9 | Central | UF08
135291 | 2017-01-24 | Defective Equipment | Mechanical Failure | One phase of G771 was burning up. Controlled outage to 55 customers was required to isolate. Further work was required to repair broken insert pin. | U/G Cable Attachement | Elbow \ Insert | 1 | 241 | 4 | East | BCHF4
135291 | 2017-01-24 | Defective Equipment | Mechanical Failure | One phase of G771 was burning up. Controlled outage to 55 customers was required to isolate. Further work was required to repair broken insert pin. | U/G Cable Attachement | Elbow \ Insert | 55 | 109 | 100 | East | BCHF4
135292 | 2017-01-25 | Scheduled Outage | Maintenance | To allow Hydro Ottawa metering to repair a metering problem | None | Meter | 1 | 14 | 0 | East | 5303
135293 | 2017-01-25 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUCE FEEDING TRANSFORMER X39861 | O/H Transformer | O/H Transformer (1ph) | 9 | 52 | 8 | South | 47F6
135294 | 2017-01-25 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35515 TO RE-SAG SECONDARY BUSS | None | None | 6 | 100 | 10 | Central | AH14
135295 | 2017-01-25 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35509 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 2 | 180 | 6 | Central | AH14
135296 | 2017-01-25 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X39149 TO TRANSFER HYDRO PLANT | None | None | 10 | 201 | 34 | East | UZ05
135297 | 2017-01-25 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31854 TO INSTALL A NEW POLE | None | None | 12 | 30 | 6 | Central | UF08
135298 | 2017-01-26 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X48257 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 14 | 62 | 14 | Central | TW12
135299 | 2017-01-26 | Scheduled Outage | Construction | Transformer #X34909 isolated by crew to put up a new service | None | None | 5 | 80 | 7 | Central | UL04
135300 | 2017-01-26 | Scheduled Outage | Vegetation Management | SO03 OH from S17261 to EOL isolated by Forestry to trimm tree, affecting 21 customers. Overbrook (SO03) | None | None | 21 | 250 | 88 | East | SO03
135301 | 2017-01-26 | Scheduled Outage | Maintenance | Overhead transformer at pole X43095 isolated to re-arrange plant. Urbandale (AE07) | None | O/H Transformer (1ph) | 2 | 240 | 8 | East | AE07
135303 | 2017-01-26 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X06249 TO REPAIR SECODARY SERVICE | None | None | 1 | 63 | 1 | South | 180F4
135304 | 2017-01-27 | Scheduled Outage | Construction | Transformer #K00237 isolated by crew for a service upgrade | None | None | 23 | 68 | 26 | Central | UV07
135305 | 2017-01-27 | Scheduled Outage | Construction | Transformer #X23329 isolated by crew to install a new service | None | None | 9 | 120 | 18 | East | AA04
135306 | 2017-01-27 | Scheduled Outage | Construction | Transformer #X35078 isolated by crew to replace cutout and arrestor | None | None | 7 | 25 | 3 | Central | TD06
135307 | 2017-01-27 | Scheduled Outage | Construction | Transformer #X35083 isolated by crew to replace cut out and arrestor | None | None | 11 | 45 | 8 | Central | TD06
135308 | 2017-01-28 | Scheduled Outage | Forced Switching | To isolate cable fault between S17859 and 791 | None | None | 4 | 15 | 1 | West | 624F6
135312 | 2017-01-30 | Scheduled Outage | Maintenance | Transformer #X34780 isolated by crew for a service repair | None | None | 1 | 25 | 0 | South | 145F3
135313 | 2017-01-31 | Scheduled Outage | Vegetation Management | A section of overhead line from pole X23775 was isolated to trim trees at rear of 789 Dunloe. 14 customers affected. Beechwood UB07. | None | None | 14 | 226 | 53 | East | UB07
135314 | 2017-01-31 | Defective Equipment | Electrical Failure | Planned outage to replace overheating elbows and inserts | U/G Cable Attachement | Elbow \ Insert | 10 | 116 | 19 | West | TFXF6
135315 | 2017-01-31 | Scheduled Outage | Building/ High Load Move | ISOLATED TRANSFORMER X32927 TO TRANSFER LOAD FROM ONE ONE PHASE TO ANOTHER PHASE | None | None | 10 | 15 | 2 | Central | TD07
135316 | 2017-01-31 | Defective Equipment | Electrical Failure | Defective padmount transformer | U/G Transformer | Padmount (1ph) | 9 | 365 | 55 | East | LTM04
135317 | 2017-01-31 | Scheduled Outage | Building/ High Load Move | ISOLATED TRANSFORMER X32937 TO TRANSFER FROM ONE PHASE TO ANOTHER PHASE | None | None | 12 | 15 | 3 | Central | TD07
135318 | 2017-01-31 | Defective Equipment | Electrical Failure | defective transformer | U/G Transformer | Padmount (1ph) | 12 | 444 | 89 | East | LMBF7
135319 | 2017-01-31 | Scheduled Outage | Building/ High Load Move | ISOLATED TRANSFORMER X32936 TO TRANSFER FROM ONE PHASE TO ANOTHER | None | None | 4 | 15 | 1 | Central | TD07
135320 | 2017-01-31 | Scheduled Outage | Construction | Transformer #X33825 isolated by crew to replace insulator and switch | None | None | 8 | 60 | 8 | Central | TD06
135321 | 2017-01-31 | Scheduled Outage | Construction | Transformer #X36087 isolated by crew to replace triplex service | None | None | 8 | 58 | 8 | Central | TD05
135322 | 2017-02-01 | Scheduled Outage | Vegetation Management | A section of overhead line from S26818 was isolated to trim trees on Hutton Ave. 41 customers affected. Russell TB15. | None | None | 41 | 312 | 213 | East | TB15
135323 | 2017-02-01 | Defective Equipment | Electrical Failure | A section of overhead line on Nulligan & Shirley was isolated to replace dead end insulators & switch at X12995. 48 customers affected. Limebank 7F2. | Pole Attachement | Insulator | 48 | 160 | 128 | East | 7F2
135324 | 2017-02-01 | Scheduled Outage | Maintenance | S20894 at 3224 Huntly isolated to change primary switch. 1 cusomter affected. Richmond South (28F1) | None | Fused Cutout | 1 | 49 | 1 | West | 28F2
135325 | 2017-02-01 | Scheduled Outage | Construction | Dave Burns and crew to have transformer X31195 open to remove and install new transformer X55213. Customers notified. | None | None | 13 | 160 | 35 | Central | UF08
135326 | 2017-02-01 | Scheduled Outage | Construction | Dave Burns and crew to have transformer X31194 open to remove and install new transformer X55213. Customers notified. | None | None | 11 | 130 | 24 | Central | UF08
135327 | 2017-02-01 | Scheduled Outage | Construction | Dave Burns and crew to have transformer X31193 open to remove and install new transformer X55213. Customers notified. | None | None | 14 | 29 | 7 | Central | UF08
135328 | 2017-02-01 | Foreign Interference | Other Utilities | Transformer #X14734 opened up::reports of bell working in the area may have hit our secondary buss. broke secondary lug at transformer. we cleaned up connection and tightened back down. closed in transformer and it held. | O/H Switchgear | Fused Cutout | 5 | 122 | 10 | East | LTM04
135329 | 2017-02-02 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry to perform tree trimming work in the rear 293, 301 & 305 Summit | None | None | 52 | 232 | 201 | East | TB06
135330 | 2017-02-02 | Scheduled Outage | Maintenance | To replace 7 poles and transfer overhead conductor. | None | None | 1 | 262 | 4 | East | UZ12
135331 | 2017-02-02 | Scheduled Outage | Maintenance | To allow Hydro Ottawa line crews to move S10091 from the W phase to the B phase | None | None | 17 | 65 | 18 | Central | TD07
135332 | 2017-02-02 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33203 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 9 | 160 | 24 | Central | TD05
135333 | 2017-02-02 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32513 (squirrel) | O/H Transformer | O/H Transformer (1ph) | 8 | 44 | 6 | Central | TD01
135335 | 2017-02-02 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X23402 TO REMOVE TREE BRANCH FROM THE SECONDARY BUSS | None | None | 15 | 7 | 2 | East | UB04
135336 | 2017-02-02 | Foreign Interference | Dig-In | Transformer TP11199 at 173 Helen was isolated to allow crew to replace damaged transformer. | U/G Transformer | Kiosk (1ph) | 6 | 107 | 11 | East | 7F2
135337 | 2017-02-02 | Scheduled Outage | Maintenance | Doug Featherstone to have transformer X32316 open to replace a faulting porcelin cut out. Customers notified. | None | None | 6 | 46 | 5 | Central | UC03
135339 | 2017-02-03 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to change poles | None | Pole | 1 | 240 | 4 | East | UZ12
135340 | 2017-02-03 | Defective Equipment | Mechanical Failure | First trip of 43F2 Red and White, no cause was found yet. | Pole Attachement | Insulator | 215 | 30 | 108 | West | 43F2
135341 | 2017-02-03 | Defective Equipment | Mechanical Failure | 43F2 Red and White tripped for a second time. Insulator found detached from the cross arm at X12195 West of Munster Hamlet on Bleeks. | Pole Attachement | Insulator | 215 | 63 | 226 | West | 43F2
135342 | 2017-02-03 | Unknown/Other | Unknown | Line downstream of S18845 patrolled and no cause found. S18845 closed and holding | Unknown \ Other | Unknown \ Other | 1 | 97 | 2 | South | 145F3
135346 | 2017-02-06 | Scheduled Outage | Construction | Transformer #X34290 isolated by crew to replace cut out and arrestor | None | None | 10 | 52 | 9 | Central | TD06
135347 | 2017-02-06 | Scheduled Outage | Construction | Transformer #X35087 isolated by crew to replace cut out and arrestor | None | None | 11 | 40 | 7 | Central | TD06
135348 | 2017-02-06 | Scheduled Outage | Construction | Transformer #TP3895 isolated by crew to make repairs to secondary U/G service | None | None | 11 | 210 | 38 | East | BCHF5
135349 | 2017-02-06 | Scheduled Outage | Construction | Transformer #X31525 isolated by crew to transfer plant | None | None | 36 | 40 | 24 | Central | UF07
135350 | 2017-02-06 | Scheduled Outage | Construction | Transformer #X32494 isolated by crew to replace cut out and arrestor | None | None | 9 | 54 | 8 | Central | TD06
135351 | 2017-02-07 | Scheduled Outage | Vegetation Management | A section of primary oeverhead was isolated at 1041 Du pere Charlebois for tree trimming affecting 34 customers. Overbrook SO12 | None | None | 34 | 154 | 87 | East | SO12
135352 | 2017-02-07 | Defective Equipment | Electrical Failure | outage to investigate blown fuse | U/G Transformer | Padmount (3ph) | 1 | 350 | 6 | South | 180F3
135353 | 2017-02-07 | Scheduled Outage | Construction | A section of primary overhead on Sadler was isolated for pole replacement affecting 28 customers. Lincoln TD07 | None | None | 28 | 246 | 115 | Central | TD07
135354 | 2017-02-07 | Scheduled Outage | Vegetation Management | planned outage for tree trimming | None | None | 1 | 198 | 3 | West | BECKF2
135355 | 2017-02-07 | Defective Equipment | Mechanical Failure | REPLACED BROKEN PRIMARY LEAD AT THE SWITCH FEEDING TRANSFORMER X27750 | O/H Transformer | O/H Transformer (1ph) | 6 | 229 | 23 | East | UZ07
135356 | 2017-02-08 | Scheduled Outage | Construction | planned outag to allow crews to plant new poles | None | None | 1 | 267 | 4 | East | UZ12
135358 | 2017-02-08 | Scheduled Outage | Maintenance | Brent Duncan and crew to have transformer X29915 open to replace secondary connections at the transformer. Customers notified. | None | None | 11 | 24 | 4 | Central | SR02
135359 | 2017-02-08 | Scheduled Outage | Vegetation Management | Section of primary overhead at 324 Fullertonwas isolated for tree trimming affecting 76 customers. Overbrook SO12 | None | None | 76 | 227 | 288 | East | SO12
135360 | 2017-02-09 | Scheduled Outage | Maintenance | UZ12 OH fromTEMP47 to EOL isolated to replace poles, affecting 1 customer. Walkley (UZ12) | None | None | 1 | 322 | 5 | East | UZ12
135361 | 2017-02-09 | Scheduled Outage | Vegetation Management | A section of SO12 from S14842 was isolated for tree trimming at the rar of 455 Queen Mary. 39 customers affected. Overbrook SO12. | None | None | 39 | 168 | 109 | East | SO12
135362 | 2017-02-10 | Defective Equipment | Electrical Failure | TP11199 at 173 Helen Rapp isolated for transformer replacement. 6 customers affected. Lietrim (249F1) | U/G Transformer | Padmount (1ph) | 6 | 528 | 53 | East | LTM01
135363 | 2017-02-13 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry to perform tree trimming at the rear of 1836 & 1847 Edgecombe St. | None | None | 66 | 255 | 280 | East | TB15
135364 | 2017-02-13 | Scheduled Outage | Maintenance | To allow Hydro Ottawa line crews to transfer S11281 and all cutomers fed by this switch from the W phase to the B phase | None | None | 96 | 20 | 32 | Central | TW12
135365 | 2017-02-13 | Scheduled Outage | Maintenance | To allow Hydro Ottawa line crews to transfer S24930 to E.O.L from the W phase to the B phase | None | None | 60 | 18 | 18 | Central | TW12
135366 | 2017-02-13 | Scheduled Outage | Maintenance | Damaged transformer TP10579 changed on the Leitrim 249F1 affecting 9 customers | None | None | 9 | 55 | 8 | East | LTM01
135367 | 2017-02-14 | Loss Of Supply | Third Party | CB1 at VT140, 2181 Navaho tripped causing TW04 breaker to trip. Suspected defective main breaker. | None | None | 1 | 963 | 16 | Central | 2802
135367 | 2017-02-14 | Loss Of Supply | Third Party | CB1 at VT140, 2181 Navaho tripped causing TW04 breaker to trip. Suspected defective main breaker. | None | None | 358 | 53 | 316 | Central | 2802
135368 | 2017-02-14 | Scheduled Outage | Vegetation Management | AT 8:36am S14967 was opened to allow crew to perform tree trimming. 26 customers affected. Russell (TB14) | None | None | 26 | 354 | 153 | East | TB14
135369 | 2017-02-14 | Scheduled Outage | Construction | At 09:07am section of TD07 was isolated to allow crews to perform pole replacement. 70 customers affected. Lincoln Heights. (TD07) | None | None | 60 | 273 | 273 | Central | TD07
135370 | 2017-02-14 | Scheduled Outage | Construction | Andy McNulty and crew to have transformer X31862 to transfer plant to a new pole. Customers notified. | None | None | 6 | 80 | 8 | Central | UF07
135371 | 2017-02-14 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel found by 24/7 crew. Openned fused cut-out for transformer X32438. Crew inspected and refused. | None | None | 11 | 84 | 15 | Central | TW22
135373 | 2017-02-15 | Scheduled Outage | Vegetation Management | At 8:50am S19632 was opened to allow crews to perform tree trimming. 43 customers affected. Russell (TB14) | None | None | 43 | 130 | 93 | East | TB14
135374 | 2017-02-15 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry crews to remove a large tree that had fallen onto the O/H line. | None | None | 34 | 89 | 50 | East | SO12
135375 | 2017-02-16 | Scheduled Outage | Vegetation Management | Section of primary overhead at 500 Avalon was isolated for tree trimming affecting 24 customers. Russell TB14 | None | None | 24 | 168 | 67 | East | TB14
135376 | 2017-02-16 | Defective Equipment | Defective Equipment/ Material | Inline trunk phase fuse blew on Kent Street feeding all Blue phase load South of Florence on the Florence UF06. | O/H Switchgear | Inline Switch | 142 | 139 | 329 | Central | UF06
135377 | 2017-02-18 | Foreign Interference | Foreign Objects | Balloon in o/h wires. | None | None | 0 | 3 | 0 | East | AF03
135377 | 2017-02-18 | Foreign Interference | Foreign Objects | Balloon in o/h wires. | None | None | 380 | 17 | 108 | East | AF03
135377 | 2017-02-18 | Foreign Interference | Foreign Objects | Balloon in o/h wires. | None | None | 380 | 72 | 456 | East | AF03
135379 | 2017-02-19 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at pole X25082, caused TB15 breaker (5401) to trip and burn up pole and switches. Overhead line isolated to allow crew to replace burnt pole at a later date. | Pole | Pole | 1 | 5 | 0 | Central | 5401
135379 | 2017-02-19 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at pole X25082, caused TB15 breaker (5401) to trip and burn up pole and switches. Overhead line isolated to allow crew to replace burnt pole at a later date. | Pole | Pole | 3 | 11 | 1 | Central | 5401
135379 | 2017-02-19 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at pole X25082, caused TB15 breaker (5401) to trip and burn up pole and switches. Overhead line isolated to allow crew to replace burnt pole at a later date. | Pole | Pole | 6 | 15 | 2 | Central | 5401
135379 | 2017-02-19 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at pole X25082, caused TB15 breaker (5401) to trip and burn up pole and switches. Overhead line isolated to allow crew to replace burnt pole at a later date. | Pole | Pole | 262 | 69 | 301 | Central | 5401
135380 | 2017-02-19 | Defective Equipment | Defective Equipment/ Material | Transformer TP8098 at 1546 Burningtree was isolated to allow the crew replace defective transformer, 10 customers affected | U/G Transformer | Kiosk (1ph) | 10 | 111 | 18 | East | 77M6
135382 | 2017-02-20 | Defective Equipment | Electrical Failure | Primary conductor down in the rear of 875 Denison. S27829 opened by on call crew to isolate line and repair conductor. | O/H Conductor | O/H Conductor | 22 | 232 | 85 | Central | UC03
135382 | 2017-02-20 | Defective Equipment | Electrical Failure | Primary conductor down in the rear of 875 Denison. S27829 opened by on call crew to isolate line and repair conductor. | O/H Conductor | O/H Conductor | 52 | 108 | 94 | Central | UC03
135383 | 2017-02-21 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 31 | 102 | 53 | East | SO02
135384 | 2017-02-21 | Scheduled Outage | Construction | Transformer #X33989 isolated by crew to install new pole with a crane | None | None | 4 | 215 | 14 | Central | UV03
135385 | 2017-02-21 | Defective Equipment | Electrical Failure | S2-2 red phase fuse found blown | U/G Cable | XLPE | 57 | 37 | 35 | West | 24F1
135385 | 2017-02-21 | Defective Equipment | Electrical Failure | S2-2 red phase fuse found blown | U/G Cable | XLPE | 86 | 155 | 222 | West | 24F1
135387 | 2017-02-22 | Defective Equipment | Defective Equipment/ Material | Blown lightening arrester in the transformer at 1383 Ambridge way caused a primary fused switch to open affecting 23 customers. Fisher AK04 | U/G Cable Attachement | Arrester | 11 | 10 | 2 | Central | AK04
135387 | 2017-02-22 | Defective Equipment | Defective Equipment/ Material | Blown lightening arrester in the transformer at 1383 Ambridge way caused a primary fused switch to open affecting 23 customers. Fisher AK04 | U/G Cable Attachement | Arrester | 23 | 126 | 48 | Central | AK04
135388 | 2017-02-22 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 29 | 235 | 114 | East | UQ05
135390 | 2017-02-22 | Scheduled Outage | Construction | 2 transformers, #X27376 and X27381 isolated by crew to transfer plant | None | None | 8 | 180 | 24 | East | UZ05
135391 | 2017-02-23 | Unknown/Other | Unknown | G441 B phase found open at 1499 Star Top Rd. Circuit patrolled, no cause found. 20 customers affected. Startop (6F1) | Unknown \ Other | Unknown \ Other | 10 | 76 | 13 | East | 6F1
135392 | 2017-02-23 | Scheduled Outage | Vegetation Management | At 8:30am crews isolated section of the TW22 for tree trimming. 37 customers affected. Woodroffe (TW22). | None | None | 37 | 138 | 85 | Central | TW22
135393 | 2017-02-23 | Defective Equipment | Mechanical Failure | The switch that feeds transformer KT682 @ 4 Marielle was defective causinhg the outage to 15 customers on TD12 | O/H Switchgear | Fused Cutout | 15 | 110 | 28 | Central | TD12
135394 | 2017-02-24 | Defective Equipment | Electrical Failure | At 06:02am SCADA indicated the TO46 breaker opened affecting 450 customers. Crews transferred customers and isolated circuit with the fault. Overbrook (TO2UB) | U/G Cable | PILC | 450 | 152 | 1140 | East | TO2UB
135395 | 2017-02-24 | Scheduled Outage | Vegetation Management | The O/H in the rear of 1471 Woodward was isolated to allow the tree contractor to preform tree trimming | None | O/H Conductor | 50 | 241 | 201 | Central | UC08
135396 | 2017-02-24 | Scheduled Outage | Vegetation Management | The O/H in the rear 1352 Woodward was isolated to allow the tree contractor to perform tree trimming, affecting 29 customers | None | O/H Conductor | 29 | 336 | 162 | Central | AD05
135397 | 2017-02-24 | Defective Equipment | Mechanical Failure | ISOLATED TRANSFORMER X24108 DUE TO SECONDARY OPEN BUSS BURNT DOWN | O/H Conductor | O/H Conductor | 12 | 399 | 80 | East | LMBF5
135398 | 2017-02-24 | Defective Equipment | Electrical Failure | Defective transformer bus red phase cable. | Vault Equipment | Cable | 1 | 530 | 9 | East | TO2UT
135399 | 2017-02-24 | Lightning | Lightning | Unknown lighting in the area the time of outage. | O/H Switchgear | Inline Switch | 54 | 160 | 144 | East | UB07
135400 | 2017-02-25 | Human Element | Switching Error | While switching at the station a breaker was not closed in error affecting 1 customer at 145 Richmond. Carling 308 | None | None | 1 | 5 | 0 | Central | TM1DK
135403 | 2017-02-26 | Scheduled Outage | Vegetation Management | Tree removal due to split in trunk. | None | None | 77 | 64 | 82 | Central | SB05
135404 | 2017-02-27 | Scheduled Outage | Vegetation Management | S13838 to Eol was isolated to allow tree trimming crew to trim trees at rear of 1309 and 1313 Erindale. | None | None | 46 | 168 | 129 | Central | TW12
135406 | 2017-02-28 | Scheduled Outage | Construction | New pole installed at 913 Dresden affecting 67 customers on the Lincoln TD07 | None | None | 67 | 113 | 126 | Central | TD07
135407 | 2017-02-28 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X09575 | O/H Transformer | O/H Transformer (1ph) | 1 | 143 | 2 | West | JKGF4
135408 | 2017-02-28 | Scheduled Outage | Construction | Transformer removal by crane at 2351 Rembrandt on the Lincoln TD07 affecting 28 customers | None | None | 11 | 80 | 15 | Central | TD07
135408 | 2017-02-28 | Scheduled Outage | Construction | Transformer removal by crane at 2351 Rembrandt on the Lincoln TD07 affecting 28 customers | None | None | 28 | 193 | 90 | Central | TD07
135409 | 2017-02-28 | Scheduled Outage | Construction | To remove unused primary wire in backyard. | None | None | 6 | 113 | 11 | East | 7F2
135410 | 2017-02-28 | Scheduled Outage | Maintenance | Bill Armstrong and crew to have transformer X39533 open to repair damaged neutral at rear of 16 Kimberley. Customers notified. | None | None | 3 | 47 | 2 | South | 47F3
135412 | 2017-02-28 | Scheduled Outage | Construction | Shawn Ryan and crew to have transformer X36354 open to transfer Hydro Ottawa plant. Customers notified. | None | None | 5 | 300 | 25 | South | 140F5
135413 | 2017-02-28 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X06500 opened up due to squirrel interference | O/H Switchgear | Fused Cutout | 4 | 139 | 9 | West | BRDF5
135415 | 2017-03-01 | Scheduled Outage | Maintenance | Transformer #X29626 isolated by crew to replace connections at the transformer | None | None | 8 | 24 | 3 | East | SO05
135416 | 2017-03-01 | Defective Equipment | Defective Equipment/ Material | Transformer #X4638 opened up due to defective switch | O/H Switchgear | Fused Cutout | 1 | 50 | 1 | South | 145F4
135417 | 2017-03-02 | Defective Equipment | Electrical Failure | Blue phase cable fault between TE3144 and TE340 | U/G Cable | XLPE | 44 | 64 | 47 | East | 6F10
135417 | 2017-03-02 | Defective Equipment | Electrical Failure | Blue phase cable fault between TE3144 and TE340 | U/G Cable | XLPE | 83 | 165 | 228 | East | 6F10
135418 | 2017-03-02 | Scheduled Outage | Vegetation Management | Tree trimming | None | None | 79 | 236 | 311 | Central | TW22
135419 | 2017-03-02 | Defective Equipment | Electrical Failure | ISOLATED TRANSFORMER X35811 TO REPLACE SECONDARY SERVICE | Secondary \ Service | O/H Service | 14 | 80 | 19 | South | 190F5
135420 | 2017-03-02 | Scheduled Outage | Construction | Repair conductor laying on a cross arm. | None | None | 34 | 44 | 25 | Central | SM10
135421 | 2017-03-02 | Defective Equipment | Mechanical Failure | Outage to replace backyard dead end pole on Majestic Millford. | Pole | Pole | 29 | 304 | 147 | South | 170F1
135422 | 2017-03-02 | Scheduled Outage | Maintenance | Field crew reported G324B heating up and needs to be replaced. | None | Fused Cutout | 8 | 80 | 11 | East | 7F2
135423 | 2017-03-03 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33989 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 4 | 120 | 8 | Central | UV03
135424 | 2017-03-03 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27064 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 4 | 124 | 8 | East | TB06
135425 | 2017-03-03 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 380 | 46 | 291 | East | AF03
135426 | 2017-03-03 | Unknown/Other | Unknown | AF03 circuit re-opened causing outage to 380 customers. Circuit was split and energized restoring all customer load. Circuit was patrolled by crews and no problem found. | O/H Conductor | Unknown \ Other | 380 | 50 | 317 | East | AF03
135427 | 2017-03-03 | Scheduled Outage | Maintenance | Jonathon Parker and crew to have T103 open to repair underground conductor. | None | None | 12 | 60 | 12 | East | BCHF5
135428 | 2017-03-03 | Defective Equipment | Electrical Failure | To make repairs to a defective connection at S596W, Outage was expanded so that switch connection to overhead could be safely cut clear to make repairs | O/H Switchgear | Fused Cutout | 40 | 43 | 29 | South | 190F5
135428 | 2017-03-03 | Defective Equipment | Electrical Failure | To make repairs to a defective connection at S596W, Outage was expanded so that switch connection to overhead could be safely cut clear to make repairs | O/H Switchgear | Fused Cutout | 40 | 108 | 72 | South | 190F5
135428 | 2017-03-03 | Defective Equipment | Electrical Failure | To make repairs to a defective connection at S596W, Outage was expanded so that switch connection to overhead could be safely cut clear to make repairs | O/H Switchgear | Fused Cutout | 1735 | 2 | 58 | South | 190F5
135429 | 2017-03-04 | Unknown/Other | Unknown | Overhead circuit was patrolled still no fault was found | None | None | 172 | 89 | 255 | East | AF03
135430 | 2017-03-04 | Scheduled Outage | Forced Switching | The vault at V442 was flooded in 3 feet of water and circuit was dumped for safety. 410 customers affected. Florence (UF10) | None | None | 410 | 10 | 68 | Central | UF04
135431 | 2017-03-04 | Adverse Environment | Flood | 4KV vault was isolated due to flooding. | Vault Equipment | Unknown \ Other | 1 | 516 | 9 | Central | UF04
135432 | 2017-03-04 | Defective Equipment | Electrical Failure | Blown switch and arrester at X12843, crew re-fused and customers restored. Followup pole-top insulator replacement required | Pole Attachement | Insulator | 5 | 69 | 6 | East | 7F2
135433 | 2017-03-05 | Defective Equipment | Defective Equipment/ Material | A BLKF8 R phase cable fault between transformer TP4836 and S16763 in the Innes Rd and Orient Park Dr area, affecting 110 customers | U/G Cable | XLPE | 110 | 96 | 176 | East | BLKF8
135434 | 2017-03-06 | Defective Equipment | Defective Equipment/ Material | Defective cut | O/H Switchgear | Fused Cutout | 9 | 104 | 16 | East | UB04
135435 | 2017-03-06 | Scheduled Outage | Construction | Transformer #X31526 isolated by crew for secondary transfers | None | None | 30 | 160 | 80 | Central | UF07
135436 | 2017-03-06 | Scheduled Outage | Vegetation Management | The O/H at 102 Martin was isolated to allow the tree contractors trim trees, 14 customers were affected on the 28F2 circuit | None | O/H Conductor | 14 | 259 | 60 | West | 28F2
135437 | 2017-03-06 | Scheduled Outage | Maintenance | Rudy Grisel and crew to have transformer X12843 open to replace pole top insulator, switch bracket, switch, and arrester. Customers Notified. | None | None | 4 | 35 | 2 | East | 7F2
135438 | 2017-03-06 | Defective Equipment | Defective Equipment/ Material | Not yet known. | U/G Cable | XLPE | 25 | 35 | 15 | East | 77M6
135438 | 2017-03-06 | Defective Equipment | Defective Equipment/ Material | Not yet known. | U/G Cable | XLPE | 37 | 20 | 12 | East | 77M6
135438 | 2017-03-06 | Defective Equipment | Defective Equipment/ Material | Not yet known. | U/G Cable | XLPE | 79 | 161 | 212 | East | 77M6
135439 | 2017-03-07 | Scheduled Outage | Vegetation Management | Forestry crew to trim in the rear of 1290 Tara Cres. | None | O/H Conductor | 55 | 81 | 74 | Central | TW18
135440 | 2017-03-07 | Scheduled Outage | Construction | TP8808 at 350 Cresthaven isolated to installl new secondary. 1 customer affected. Limebank 7F1. | None | None | 1 | 451 | 8 | East | 7F1
135441 | 2017-03-08 | Defective Equipment | Defective Equipment/ Material | Defective secondary burnt to the ground. | Secondary \ Service | O/H Service | 5 | 95 | 8 | South | 170F1
135442 | 2017-03-08 | Scheduled Outage | Vegetation Management | Isolation of TW18 Red phase o/h line at X48719 to allow crew to trim tree in rear of 1149 Tara. | None | O/H Conductor | 86 | 211 | 302 | Central | TW18
135443 | 2017-03-08 | Scheduled Outage | Construction | TD06 overhead line from S26469W, TEMP 60 RB to EOL to install pole with a crane in the rear of 1902 Wembley. | None | Pole | 32 | 184 | 98 | Central | TD06
135444 | 2017-03-08 | Scheduled Outage | Maintenance | Stuart Maclaren and crew to have transformer X48105 open to change a broken switch and transfer plant. Customers notified. | None | None | 10 | 34 | 6 | East | TB15
135445 | 2017-03-08 | Scheduled Outage | Maintenance | Shawn Ryan and Crew to open transformer X4172 and X4163 to make repairs to secondary services. Customers notified. | None | None | 9 | 132 | 20 | South | 170F1
135447 | 2017-03-08 | Foreign Interference | Dig-In | Customer dig in on secondary conductor from TE3154 caused G674 to open. TE3154 isolated, defective secondary disconnected & remaining customer restored. 2 customers affected. Bilberry 77M2. | Secondary \ Service | U/G Service | 2 | 232 | 8 | East | 77M2
135448 | 2017-03-08 | Unknown/Other | Unknown | S1400 found open, line patrolled & no problem found. 8 customers affected. Stafford 200F2. | None | None | 8 | 71 | 9 | South | 200F2
135449 | 2017-03-08 | Defective Equipment | Electrical Failure | Outage on TB15 o/h line due to broken lead at S22538 | Pole Attachement | Unknown \ Other | 40 | 40 | 27 | East | TB15
135450 | 2017-03-09 | Scheduled Outage | Maintenance | checking for blown metering fuseon the A bus. | None | None | 1 | 90 | 2 | Central | 415
135451 | 2017-03-09 | Scheduled Outage | Vegetation Management | Planned outage to remove a large tree limbs from overhead conductor. | None | O/H Conductor | 34 | 213 | 121 | Central | TW22
135452 | 2017-03-09 | Defective Equipment | Corrosion | Replace rusted transformer 4081 at 30 Turret affecting 10 customers on the BRDF6 out of Bridlewood | U/G Transformer | Padmount (1ph) | 10 | 191 | 32 | West | BRDF6
135454 | 2017-03-09 | Scheduled Outage | Maintenance | Rudy Grisel and crew to have transformer GLTE103 open to repair a pedestal. Customers notified. | None | None | 12 | 184 | 37 | East | BCHF5
135455 | 2017-03-09 | Scheduled Outage | Construction | Mike Byers and crew to have transformers X31527 and X31526 open to transfer plant. Customers notified. | None | None | 49 | 207 | 169 | Central | UF07
135456 | 2017-03-09 | Scheduled Outage | Construction | Scott Barkley to have transformers X38561 and X33415 open to transfer plant. Customers notified. | None | None | 17 | 239 | 68 | Central | TD07
135457 | 2017-03-09 | Defective Equipment | Electrical Failure | A cable fault on the 77M6 W phase between TP8072 & TP8073 caused S19837 W phase to blow, affecting 166 customers | U/G Cable | XLPE | 12 | 47 | 9 | East | 77M6
135457 | 2017-03-09 | Defective Equipment | Electrical Failure | A cable fault on the 77M6 W phase between TP8072 & TP8073 caused S19837 W phase to blow, affecting 166 customers | U/G Cable | XLPE | 64 | 29 | 31 | East | 77M6
135457 | 2017-03-09 | Defective Equipment | Electrical Failure | A cable fault on the 77M6 W phase between TP8072 & TP8073 caused S19837 W phase to blow, affecting 166 customers | U/G Cable | XLPE | 166 | 135 | 374 | East | 77M6
135458 | 2017-03-10 | Defective Equipment | Corrosion | Rusted transformer change by HOL crew affecting 11 customers on the BRDF3 out of Bridlewood | U/G Transformer | Padmount (1ph) | 11 | 170 | 31 | West | BRDF3
135459 | 2017-03-10 | Scheduled Outage | Construction | Brent Duncan and crew to have transformer X29817 open to transfer plant. Customers notified. | None | None | 8 | 131 | 17 | Central | TR09
135461 | 2017-03-10 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X32937 open to trasnfer plant. Customers notified. | None | None | 12 | 202 | 40 | Central | TD07
135462 | 2017-03-10 | Scheduled Outage | Maintenance | Mano Delavadova to have transformer X07129 open to replace the cut out and lightning arrestor. Customers notified. | None | None | 2 | 45 | 2 | West | MWDF3
135464 | 2017-03-11 | Defective Equipment | Electrical Failure | Cable fault in TP9342 at 23 Erskine caused fuse S989 to open. 8 customers affected. Bayshore (49F6) | U/G Cable Attachement | Elbow \ Insert | 8 | 372 | 50 | South | 49F6
135466 | 2017-03-13 | Defective Equipment | Electrical Failure | G435R at 1603 Athans opened, cause not yet determined. 70 customers affected. Uplands (4801F8). Blown arrester found and removed. | O/H Conductor | Unknown \ Other | 41 | 88 | 60 | East | 4801F8
135466 | 2017-03-13 | Defective Equipment | Electrical Failure | G435R at 1603 Athans opened, cause not yet determined. 70 customers affected. Uplands (4801F8). Blown arrester found and removed. | O/H Conductor | Unknown \ Other | 70 | 234 | 273 | East | 4801F8
135467 | 2017-03-13 | Defective Equipment | Electrical Failure | TK14 CB opened at King Edward due to suspected cable fault. 283 customers affected. King Edward (407/417) | U/G Cable | PILC | 2 | 37 | 1 | Central | 417
135467 | 2017-03-13 | Defective Equipment | Electrical Failure | TK14 CB opened at King Edward due to suspected cable fault. 283 customers affected. King Edward (407/417) | U/G Cable | PILC | 283 | 60 | 283 | Central | 417
135468 | 2017-03-13 | Scheduled Outage | Vegetation Management | S19171 open to allow for tree removal at 2660 Claenda | None | None | 131 | 283 | 618 | Central | TD05
135469 | 2017-03-13 | Defective Equipment | Mechanical Failure | Burnt off switch lead on S16331 | O/H Conductor | Stirrup | 33 | 129 | 71 | East | 77M1
135474 | 2017-03-14 | Defective Equipment | Defective Equipment/ Material | Cable fault between VT566@ 70 Clarence St & VT833 @ 119 Clarence St | U/G Cable | PILC | 338 | 69 | 389 | Central | TK5TS
135474 | 2017-03-14 | Defective Equipment | Defective Equipment/ Material | Cable fault between VT566@ 70 Clarence St & VT833 @ 119 Clarence St | U/G Cable | PILC | 752 | 78 | 978 | Central | TK5TS
135475 | 2017-03-14 | Scheduled Outage | Vegetation Management | S12775 to end of line was isolated to allow Davey Tree crew to trim tree at rear of 1246 Stanton. | None | None | 88 | 337 | 494 | Central | UV05
135476 | 2017-03-14 | Scheduled Outage | Maintenance | Transformer #X07037 isolated by crew to replace switch | None | None | 5 | 38 | 3 | West | MWDF3
135477 | 2017-03-14 | Scheduled Outage | Maintenance | Transformer #X40234 isolated by crew to replace switch | None | None | 4 | 20 | 1 | West | MWDF3
135478 | 2017-03-14 | Scheduled Outage | Construction | Transformer #X32730 isolated by crew to transfer plant | None | None | 10 | 159 | 26 | Central | TD05
135479 | 2017-03-14 | Scheduled Outage | Maintenance | Transformer #X40172 isolated by crew to replace switch | None | None | 2 | 30 | 1 | West | MWDF3
135481 | 2017-03-14 | Adverse Weather | Extreme Wind | UC05 and UC06 same time trip | O/H Conductor | Unknown \ Other | 140 | 32 | 75 | Central | UC06
135481 | 2017-03-14 | Adverse Weather | Extreme Wind | UC05 and UC06 same time trip | O/H Conductor | Unknown \ Other | 388 | 32 | 207 | Central | UC05
135483 | 2017-03-15 | Scheduled Outage | Maintenance | Transformer P432 at 2787 Sheffield was isolated to allow crew to straighten padmount on base. Bantree (AL03) | None | None | 1 | 49 | 1 | East | AL03
135484 | 2017-03-15 | Defective Equipment | Defective Equipment/ Material | Defective insulator at K758, affecting 12 customers. Mcarthy (AQ07) | U/G Transformer | Kiosk (1ph) | 12 | 152 | 30 | East | AQ07
135485 | 2017-03-15 | Defective Equipment | Mechanical Failure | Transformer X35384 open due to a broken cut-out switch. | O/H Switchgear | Fused Cutout | 5 | 97 | 8 | Central | TD14
135486 | 2017-03-16 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 10 | 90 | 15 | East | AQ07
135487 | 2017-03-16 | Scheduled Outage | Maintenance | TP6430 at 16 Scova was isolated to replace defective elbows & inserts. 7 customers affected. Barhaven 140F4. | None | None | 7 | 56 | 7 | South | 140F4
135489 | 2017-03-16 | Scheduled Outage | Construction | Relocate primary cables. | None | None | 2 | 458 | 15 | Central | TC2TL
135490 | 2017-03-17 | Scheduled Outage | Construction | Replace blown arrestor | None | None | 10 | 52 | 9 | East | AQ06
135491 | 2017-03-17 | Scheduled Outage | Construction | Transformer #X07799 isolated by crew for a switch replacement | None | None | 1 | 37 | 1 | West | MWDF3
135492 | 2017-03-17 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X28173 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 19 | 49 | 16 | Central | 505
135493 | 2017-03-17 | Scheduled Outage | Maintenance | TV9989 at 85 Sparks was isoalted to allow contractor to perform vault Clean up. Salter (615) | None | None | 4 | 132 | 9 | Central | 615
135495 | 2017-03-18 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 333 | 43 | 239 | East | UZ03
135496 | 2017-03-20 | Scheduled Outage | Maintenance | Replace blown arrestor in kiosk and change insulators. | None | Kiosk (1ph) | 2 | 63 | 2 | East | UG05
135497 | 2017-03-20 | Scheduled Outage | Maintenance | To fix fallen transformer barrier board and inspect for any damage the board may have caused. 8 Customers | None | None | 8 | 11 | 1 | East | 6F10
135498 | 2017-03-20 | Scheduled Outage | Maintenance | Scott Barkley and crew to have transformer X32493 open to replace secondary spools. This was a semi emergency as it was noticed during the installation of the primary line. Customers were notified if possible. | None | None | 9 | 75 | 11 | Central | TD06
135499 | 2017-03-21 | Scheduled Outage | Construction | Transformer #X30695 isolated by crew for an upgrade | None | None | 16 | 65 | 17 | Central | UF05
135500 | 2017-03-21 | Scheduled Outage | Construction | Transformer #X27141 isolated by crew for a service upgrade | None | None | 6 | 18 | 2 | East | TB06
135501 | 2017-03-21 | Scheduled Outage | Maintenance | crew isolted transformer to free up cable so that switching could occur. 10 customers affected. Merivale (72F1) | None | None | 10 | 84 | 14 | South | 72F1
135502 | 2017-03-21 | Defective Equipment | Imminent Failure | At 9:54am crews isolated TE1884 to replace leaking transformer. 15 customers affected. Uplands( 4801F8) | U/G Transformer | Padmount (1ph) | 15 | 262 | 66 | East | 4801F8
135503 | 2017-03-21 | Scheduled Outage | Vegetation Management | At 8:54am a section of AD05 was isolated to allow tree trimming at the rear of 1153 and 1157 Emperor. 25 customers affected. Shillington (AD05) | None | None | 25 | 280 | 117 | Central | AD05
135504 | 2017-03-21 | Scheduled Outage | Maintenance | crew isolated overhead transformer X30458 to renew connections at transformer. 14 customers were affected. Bronson. (SB02) | None | None | 14 | 50 | 12 | Central | SB02
135505 | 2017-03-21 | Scheduled Outage | Construction | SERVICE UPGRADES | None | None | 18 | 188 | 56 | Central | UF05
135507 | 2017-03-21 | Defective Equipment | Defective Equipment/ Material | Defective Trans Cutout | O/H Transformer | O/H Transformer (1ph) | 8 | 77 | 10 | Central | AD07
135508 | 2017-03-22 | Adverse Weather | Extreme Wind | Transformer fuse X31969 at 15 Riverdale opened during high winds, direct cause not found. 12 cstomers affected. Riverdale (SR09) | O/H Conductor | O/H Conductor | 12 | 97 | 19 | Central | SR09
135510 | 2017-03-22 | Scheduled Outage | Construction | At 9:17am TP6058 was isolate to replace a defective insert. 10 customers affected. Jockvale (145F4) | None | None | 10 | 42 | 7 | South | 145F4
135511 | 2017-03-22 | Scheduled Outage | Maintenance | Transformer #X28179 isolated by crew to replace streetlight fuse | None | None | 10 | 5 | 1 | East | TB2JP
135512 | 2017-03-22 | Tree Contacts | Broken Branch | Transformer #945 opened up due to branch contact | O/H Switchgear | Fused Cutout | 1 | 177 | 3 | West | 624F6
135513 | 2017-03-22 | Scheduled Outage | Construction | Transformer #X38564 isolated by crew to replace cutout and arrestor | None | None | 13 | 55 | 12 | Central | TD06
135514 | 2017-03-22 | Scheduled Outage | Construction | Transformer K576 at 2844 Sandalwood was isolated to allow the crews remove the NIU cable | None | Padmount (1ph) | 1 | 20 | 0 | East | UA05
135515 | 2017-03-22 | Foreign Interference | Foreign Objects | Balloons made contact with the overhead at 1023 MERIVALE RD causing the AD04 circuit to trip | O/H Conductor | O/H Conductor | 446 | 9 | 67 | Central | AD04
135516 | 2017-03-22 | Scheduled Outage | Maintenance | Transformer #X31726 isolated by crew to replace cut out and arrestor | None | None | 13 | 55 | 12 | Central | TD06
135517 | 2017-03-22 | Scheduled Outage | Construction | 3 transformers (X30804, X30850 and X31871) isolated by crew to transfer plant | None | None | 48 | 295 | 236 | Central | UF06
135518 | 2017-03-22 | Scheduled Outage | Construction | Transformer #X34786 isolated by crew to replace cutout and arrestor | None | None | 24 | 63 | 25 | Central | TD06
135519 | 2017-03-23 | Scheduled Outage | Vegetation Management | S18422 to Eol was isoalted to allow Davey Tree to trim tree at rear of 1443 Raven. (Shillington AD03) | None | None | 16 | 214 | 57 | Central | AD03
135521 | 2017-03-23 | Scheduled Outage | Construction | Transformer #X40174 isolated by crew to replace defective primary insulator | None | None | 2 | 20 | 1 | West | MWDF3
135522 | 2017-03-23 | Scheduled Outage | Construction | Transformer #40156 isolated by crew to replace insulator | None | None | 2 | 67 | 2 | West | MWDF3
135523 | 2017-03-23 | Scheduled Outage | Construction | Transformer #40156 isolated by crew to replace insulator | None | None | 7 | 30 | 4 | South | 130F1
135524 | 2017-03-23 | Scheduled Outage | Construction | Transformer #X39187 isolated by crew to reposition service | None | None | 11 | 33 | 6 | Central | SM01
135525 | 2017-03-23 | Scheduled Outage | Construction | Transformer #X40159 isolated by crew to replace insulator | None | None | 3 | 60 | 3 | West | MWDF3
135526 | 2017-03-23 | Defective Equipment | Mechanical Failure | broken insulator | Pole Attachement | Insulator | 54 | 22 | 20 | South | 200F2
135528 | 2017-03-23 | Defective Equipment | Defective Equipment/ Material | Defective fuse cutout on transformer X23036. | O/H Switchgear | Fused Cutout | 4 | 291 | 19 | Central | TK2AC
135529 | 2017-03-23 | Defective Equipment | Mechanical Failure | Blown secondary transformer fuse at TP8173- unknown cause. This transformer is on the 325M8 (Orleans TS) Not 77M6. 325M8 is not in the listing in the outage report program | U/G Cable Attachement | Unknown \ Other | 7 | 130 | 15 | East | 325M8
135530 | 2017-03-24 | Defective Equipment | Mechanical Failure | Broken H1 bushing on transformer X37034 | O/H Transformer | O/H Transformer (1ph) | 10 | 335 | 56 | South | 49F6
135530 | 2017-03-24 | Defective Equipment | Mechanical Failure | Broken H1 bushing on transformer X37034 | O/H Transformer | O/H Transformer (1ph) | 17 | 20 | 6 | South | 49F6
135531 | 2017-03-24 | Scheduled Outage | Forced Switching | Transformer K555 was open to allow crew to perfrom emergency disconnect to 2084 Banff from primary pedastal due to meter not reading. Crew did not find anyhting wrong with U/G secondary cable to meter base. Suspect loose connection. | None | None | 20 | 58 | 19 | East | AF03
135532 | 2017-03-24 | Scheduled Outage | Construction | Transformer #X31460 isolated by crew to set a new pole | None | None | 12 | 80 | 16 | Central | TH01
135533 | 2017-03-25 | Defective Equipment | Electrical Failure | TO43 CB opened, blown arrestor found at Vanier and Presland. 1877 customers affected. Overbrook (TO3UT) | Pole Attachement | Arrester | 187 | 16 | 50 | East | TO2UT
135535 | 2017-03-25 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact | O/H Transformer | O/H Transformer (1ph) | 11 | 111 | 20 | Central | TW22
135536 | 2017-03-25 | Foreign Interference | Wildlife (Bird/Animal) | S478 found blown | O/H Conductor | O/H Conductor | 54 | 34 | 31 | South | 47F3
135538 | 2017-03-25 | Foreign Interference | Vehicle | At 7:06pm a car hit a pole on Georgina West of Woodroffe causing a white phase fuse to blow and affecting 753 customers. On-Call crews were brought in to replace a pole. Woodroffe (TW22) | Pole | Pole | 9 | 317 | 48 | Central | TW22
135538 | 2017-03-25 | Foreign Interference | Vehicle | At 7:06pm a car hit a pole on Georgina West of Woodroffe causing a white phase fuse to blow and affecting 753 customers. On-Call crews were brought in to replace a pole. Woodroffe (TW22) | Pole | Pole | 273 | 291 | 1324 | Central | TW22
135538 | 2017-03-25 | Foreign Interference | Vehicle | At 7:06pm a car hit a pole on Georgina West of Woodroffe causing a white phase fuse to blow and affecting 753 customers. On-Call crews were brought in to replace a pole. Woodroffe (TW22) | Pole | Pole | 753 | 61 | 766 | Central | TW22
135538 | 2017-03-25 | Foreign Interference | Vehicle | At 7:06pm a car hit a pole on Georgina West of Woodroffe causing a white phase fuse to blow and affecting 753 customers. On-Call crews were brought in to replace a pole. Woodroffe (TW22) | Pole | Pole | 1026 | 32 | 547 | Central | TW22
135540 | 2017-03-27 | Scheduled Outage | Vegetation Management | A section of overhead line on Joys rd was isolated for tree trimming. 7 customers affected. Richmond South 28F1. | None | None | 7 | 165 | 19 | West | 28F1
135541 | 2017-03-27 | Defective Equipment | Defective Equipment/ Material | Transformer #X33382 opened up due to defective equipment | O/H Switchgear | Fused Cutout | 4 | 49 | 3 | South | 190F2
135542 | 2017-03-27 | Scheduled Outage | Construction | 3 transformers isolated, X31859, X31857 and X31863 isolated by crew to transfer plant | None | None | 36 | 320 | 192 | Central | UF06
135543 | 2017-03-28 | Defective Equipment | Imminent Failure | TE1093 replaced due to leaking oil. Startop (6F10) | U/G Transformer | Padmount (1ph) | 11 | 594 | 109 | East | 6F10
135544 | 2017-03-28 | Scheduled Outage | Construction | Chris Costello and crew to have transformer X35088 open to replace cut-out switch. Customers notified. | None | None | 10 | 27 | 4 | Central | TD06
135545 | 2017-03-28 | Scheduled Outage | Maintenance | Chris Costello and crew to have transformer X26065 open to perform scheduled maintenance. Customers notified. | None | None | 14 | 15 | 4 | Central | TD06
135546 | 2017-03-28 | Scheduled Outage | Maintenance | Isolation for metering depairment to repair metering problem. | None | None | 1 | 23 | 0 | Central | 504
135547 | 2017-03-28 | Foreign Interference | Wildlife (Bird/Animal) | S10111 openned unexpectedly due to animal contact. 24/7 crews found a dead crow upon inspection. Refused and closed. | O/H Switchgear | Fused Cutout | 29 | 35 | 17 | East | UQ05
135548 | 2017-03-28 | Defective Equipment | Defective Equipment/ Material | Transformer #X39783 opened up due to neutral and 110 made contact | O/H Switchgear | Fused Cutout | 5 | 75 | 6 | South | 47F6
135550 | 2017-03-29 | Scheduled Outage | Maintenance | KT134 at 2312 Walsh was isolated to repair riser switches and kiosk barrier boards. Lincon heights (TD07) | None | None | 3 | 154 | 8 | Central | TD07
135551 | 2017-03-29 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32485 TO REPLACE SWITCH AND ARRESTER | None | None | 15 | 36 | 9 | Central | TD06
135552 | 2017-03-29 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32487 TO REPLACE THE SWITCH AND ARRESTER | None | None | 3 | 19 | 1 | Central | TD06
135553 | 2017-03-29 | Scheduled Outage | Maintenance | Chris Costello and crew to have transformer X32486 open to replaced fused cut out switch. Customers notified. | None | None | 13 | 25 | 5 | Central | TD06
135554 | 2017-03-29 | Scheduled Outage | Maintenance | Chris Costello and crew to have transformer X32385 open to replace fused cut out switch. Customers notified. | None | None | 9 | 33 | 5 | Central | TD06
135556 | 2017-03-29 | Foreign Interference | Vehicle | S22177 to EOL to repair fallen neutral. Barrhaven (140F4) crews reported neutral struck by construction shovel. | O/H Conductor | O/H Conductor | 3 | 75 | 4 | South | 140F4
135557 | 2017-03-29 | Scheduled Outage | Construction | Dave Burns and crew to have transformer X30803 open to transfer plant to a new pole. Customers notified. | None | None | 5 | 55 | 5 | Central | UF07
135558 | 2017-03-30 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X31881 FOR TREE TRIMMING AROUND SECONDARY | None | None | 34 | 60 | 34 | Central | AD07
135559 | 2017-03-30 | Defective Equipment | Corrosion | faulty arrestors at sectionalizer SE33 caused two fuses to open. 83 customers were interrupted. Limebank (LMBF7) | U/G Switchgear | Unknown \ Other | 61 | 24 | 24 | East | LMBF7
135559 | 2017-03-30 | Defective Equipment | Corrosion | faulty arrestors at sectionalizer SE33 caused two fuses to open. 83 customers were interrupted. Limebank (LMBF7) | U/G Switchgear | Unknown \ Other | 83 | 83 | 115 | East | LMBF7
135561 | 2017-03-30 | Scheduled Outage | Maintenance | Shaun Cunningham to have transformer X35163 open to repair customer secondary. | None | None | 7 | 28 | 3 | Central | SH04
135562 | 2017-03-31 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X35964 FOR FORESTRY WORK AROUND SECONDAY | None | None | 29 | 135 | 65 | Central | AD07
135563 | 2017-03-31 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X40164 TO REPLACE THE SWITCH AND ARRESTER | None | None | 4 | 53 | 4 | West | MWDF3
135564 | 2017-03-31 | Scheduled Outage | Maintenance | underground transformer TP8098 at 1544 burningtree was isolated for soil remediation. 10 customers were interrupted. Billberry (77M6) | None | None | 10 | 319 | 53 | East | 77M6
135567 | 2017-04-01 | Defective Equipment | Defective Equipment/ Material | Defective white phase cable between at 55 Beechmont caused an outage starting with an auto reclose of the breaker at the station load was restored in sections. Affecting 1129 customers Blackburn BLKF3 | U/G Cable | XLPE | 11 | 23 | 4 | East | BLKF3
135567 | 2017-04-01 | Defective Equipment | Defective Equipment/ Material | Defective white phase cable between at 55 Beechmont caused an outage starting with an auto reclose of the breaker at the station load was restored in sections. Affecting 1129 customers Blackburn BLKF3 | U/G Cable | XLPE | 11 | 142 | 26 | East | BLKF3
135567 | 2017-04-01 | Defective Equipment | Defective Equipment/ Material | Defective white phase cable between at 55 Beechmont caused an outage starting with an auto reclose of the breaker at the station load was restored in sections. Affecting 1129 customers Blackburn BLKF3 | U/G Cable | XLPE | 23 | 89 | 34 | East | BLKF3
135567 | 2017-04-01 | Defective Equipment | Defective Equipment/ Material | Defective white phase cable between at 55 Beechmont caused an outage starting with an auto reclose of the breaker at the station load was restored in sections. Affecting 1129 customers Blackburn BLKF3 | U/G Cable | XLPE | 29 | 12 | 6 | East | BLKF3
135567 | 2017-04-01 | Defective Equipment | Defective Equipment/ Material | Defective white phase cable between at 55 Beechmont caused an outage starting with an auto reclose of the breaker at the station load was restored in sections. Affecting 1129 customers Blackburn BLKF3 | U/G Cable | XLPE | 29 | 17 | 8 | East | BLKF3
135567 | 2017-04-01 | Defective Equipment | Defective Equipment/ Material | Defective white phase cable between at 55 Beechmont caused an outage starting with an auto reclose of the breaker at the station load was restored in sections. Affecting 1129 customers Blackburn BLKF3 | U/G Cable | XLPE | 126 | 38 | 80 | East | BLKF3
135567 | 2017-04-01 | Defective Equipment | Defective Equipment/ Material | Defective white phase cable between at 55 Beechmont caused an outage starting with an auto reclose of the breaker at the station load was restored in sections. Affecting 1129 customers Blackburn BLKF3 | U/G Cable | XLPE | 126 | 157 | 330 | East | BLKF3
135568 | 2017-04-02 | Foreign Interference | Foreign Objects | Breaker tripped open did not attempt to auto reclose. Crew found helium ballon made contact with O/H at Kent and Maclaren causing the S28407 Wb to blow. | O/H Conductor | O/H Conductor | 44 | 238 | 175 | Central | UF04
135568 | 2017-04-02 | Foreign Interference | Foreign Objects | Breaker tripped open did not attempt to auto reclose. Crew found helium ballon made contact with O/H at Kent and Maclaren causing the S28407 Wb to blow. | O/H Conductor | O/H Conductor | 410 | 10 | 68 | Central | UF04
135569 | 2017-04-02 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X45650 opened up due to bird contact | O/H Switchgear | Fused Cutout | 1 | 156 | 3 | East | 249F2
135570 | 2017-04-02 | Defective Equipment | Mechanical Failure | switch 525 found defective at 61 Beaufort, affecting 17 customers. Beaver Brook (24F8) | O/H Switchgear | Fused Cutout | 11 | 31 | 6 | West | 24F8
135570 | 2017-04-02 | Defective Equipment | Mechanical Failure | switch 525 found defective at 61 Beaufort, affecting 17 customers. Beaver Brook (24F8) | O/H Switchgear | Fused Cutout | 17 | 99 | 28 | West | 24F8
135572 | 2017-04-03 | Defective Equipment | Electrical Failure | Brent Duncan and crew to have transformer X31557 open to replace cut-out and lightning arrestor. Customers notified. | O/H Switchgear | Fused Cutout | 14 | 80 | 19 | Central | TD06
135573 | 2017-04-03 | Defective Equipment | Electrical Failure | Brent Duncan and crew to have transformer X32481 open to replace the cut out and lightning arrestor. Customers notified. | O/H Switchgear | Fused Cutout | 19 | 61 | 19 | Central | TD06
135574 | 2017-04-03 | Scheduled Outage | Maintenance | Mano Della Vadova and crew to have transformer X40157 open to replace cut out and lightning arrestor. Customers notified. | None | None | 3 | 60 | 3 | West | MWDF3
135575 | 2017-04-03 | Scheduled Outage | Construction | Patrick Brisson and crew to have transformers X26239 and X31463 open to transfer plant. Customers notified. | None | None | 33 | 204 | 112 | Central | TH01
135576 | 2017-04-03 | Scheduled Outage | Maintenance | Brent Duncan and crew to have transformer X32568 open to change cut-out and lightning arrester. Customers notified. | None | None | 13 | 55 | 12 | Central | TD06
135577 | 2017-04-03 | Scheduled Outage | Construction | Patrick Brisson and crew to have transformer X33552 open to remove a service. Customers notified. | None | None | 4 | 74 | 5 | Central | 303
135578 | 2017-04-03 | Scheduled Outage | Maintenance | Mano Della Vedova and crew to have transformer X40170 open to replace the cut out and lightning arrester. Customers notified. | None | None | 2 | 130 | 4 | West | MWDF3
135579 | 2017-04-03 | Scheduled Outage | Maintenance | 3 transformers on Pheasant Run were isolated to perform various repairs to elbows and inserts affecting 24 customers. Jockvale 145F1 | None | Elbow \ Insert | 24 | 165 | 66 | South | 145F1
135580 | 2017-04-04 | Defective Equipment | Defective Equipment/ Material | Defective fuse in cutout. | O/H Switchgear | Fused Cutout | 37 | 61 | 38 | West | 28F2
135581 | 2017-04-05 | Defective Equipment | Mechanical Failure | A lead on the UT04 B phase O/h at Eastwood & Brebeuf burnt off. The suspected cause was a birds nest on transformer X29319 is the suspected cause | O/H Conductor | Stirrup | 48 | 134 | 107 | East | UT04
135582 | 2017-04-05 | Scheduled Outage | Maintenance | Transformer X35123 at the rear of 2365 Ryan Dr. was opened to allow Hydro Ottawa line crews to change the cut out feeding the transformer | None | Fused Cutout | 3 | 42 | 2 | Central | UV03
135583 | 2017-04-05 | Scheduled Outage | Vegetation Management | Rick Barnett to have transformer X36154 open for tree trimming. Customers notified. | None | None | 6 | 98 | 10 | West | 28F2
135584 | 2017-04-05 | Defective Equipment | Electrical Failure | Brent Duncan and crew to have transformer X32402 open to replace cut out switch and arrestor. Customers notified. | O/H Switchgear | Fused Cutout | 28 | 45 | 21 | Central | TD06
135586 | 2017-04-06 | Scheduled Outage | Forced Switching | repaired 6F4 single phase O/H that was hanging down. Startop DS | None | O/H Conductor | 3 | 37 | 2 | East | 6F4
135587 | 2017-04-06 | Defective Equipment | Electrical Failure | DEFECTIVE TRANS | O/H Transformer | O/H Transformer (1ph) | 2 | 201 | 7 | East | 249F2
135588 | 2017-04-06 | Loss Of Supply | Transmission Inadvertent | The Russell B Bus tripped due to defective Hydro One Cap bank. | None | None | 1 | 57 | 1 | East | 5304
135588 | 2017-04-06 | Loss Of Supply | Transmission Inadvertent | The Russell B Bus tripped due to defective Hydro One Cap bank. | None | None | 39 | 79 | 51 | East | 5306
135588 | 2017-04-06 | Loss Of Supply | Transmission Inadvertent | The Russell B Bus tripped due to defective Hydro One Cap bank. | None | None | 259 | 78 | 337 | East | 5310
135588 | 2017-04-06 | Loss Of Supply | Transmission Inadvertent | The Russell B Bus tripped due to defective Hydro One Cap bank. | None | None | 334 | 79 | 440 | East | TB07
135588 | 2017-04-06 | Loss Of Supply | Transmission Inadvertent | The Russell B Bus tripped due to defective Hydro One Cap bank. | None | None | 2168 | 70 | 2529 | East | TB3LE
135590 | 2017-04-07 | Scheduled Outage | Maintenance | Bill Edwards to have transformer X17608 to upgrade a service. Customers notified. | None | None | 2 | 60 | 2 | East | 6F1
135591 | 2017-04-07 | Adverse Weather | Extreme Wind | High winds at time of outage, otherwise cause of trip is unknown | O/H Conductor | O/H Conductor | 752 | 192 | 2406 | Central | UF07
135592 | 2017-04-08 | Scheduled Outage | Maintenance | crew isolated swithgear S584 at 349 terry fox to replace switch with new vista gear. One customer was interrupted. Kanata (624F5) | None | None | 1 | 537 | 9 | West | 624F5
135593 | 2017-04-08 | Defective Equipment | Defective Equipment/ Material | To change connections at transformer X33458. | O/H Conductor | Ampact | 8 | 270 | 36 | South | 190F5
135594 | 2017-04-09 | Defective Equipment | Mechanical Failure | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X32100 | O/H Transformer | O/H Transformer (1ph) | 2 | 100 | 3 | Central | AH04
135595 | 2017-04-10 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30863 TO INSTALL NEW POLE | None | None | 32 | 182 | 97 | Central | UF07
135596 | 2017-04-10 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31869 TO INSTALL NEW POLE | None | None | 6 | 182 | 18 | Central | UF07
135597 | 2017-04-10 | Scheduled Outage | Vegetation Management | The O/h in the rear of 1138 Sherman was isolated to allow tree contractor to trim trees | None | O/H Conductor | 56 | 307 | 287 | Central | TW18
135598 | 2017-04-10 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31464 TO INSTALL A NEW POLE | None | None | 5 | 374 | 31 | Central | TH01
135599 | 2017-04-10 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X31397 TO REPAIR DOWNED SECONDAY NAUTRAL AT THE REAR OF 12 COBALT | None | None | 19 | 82 | 26 | Central | SB02
135600 | 2017-04-10 | Scheduled Outage | Construction | Steve Rutherford and crew to have transformer X31850 open to transfer plant. Customers notified. | None | None | 7 | 197 | 23 | Central | UF07
135601 | 2017-04-10 | Defective Equipment | Electrical Failure | At 9:04am TE291 was isolated for repairs to a faulted cable. 7 customers affected. Blackburn (BLKF3). | U/G Cable | XLPE | 6 | 146 | 15 | East | BLKF3
135602 | 2017-04-10 | Adverse Weather | Extreme Wind | Not yet known. Scada showed the 6F4 breaker opened. Very high winds were present. Fire, and police called, circuit closed back in and held. 163 customers interrupted. Startop (6F4) | O/H Conductor | O/H Conductor | 163 | 13 | 35 | East | 6F4
135603 | 2017-04-10 | Defective Equipment | Electrical Failure | Broken blue phase lead at switch S15922. 101 customers affected. Janet King (JKGF5) | O/H Switchgear | Inline Switch | 101 | 77 | 130 | West | JKGF5
135605 | 2017-04-10 | Adverse Weather | Extreme Wind | At 17:41 SCADA indicates and auto recloses due to high winds, circuit tripped at 17:53 and locked-out. 163 customers affect. Startop (6F4) | O/H Conductor | O/H Conductor | 0 | 12 | 0 | East | 6F4
135605 | 2017-04-10 | Adverse Weather | Extreme Wind | At 17:41 SCADA indicates and auto recloses due to high winds, circuit tripped at 17:53 and locked-out. 163 customers affect. Startop (6F4) | O/H Conductor | O/H Conductor | 163 | 126 | 342 | East | 6F4
135606 | 2017-04-10 | Lightning | Lightning | Suspected lightning in the area. | O/H Switchgear | Inline Switch | 126 | 107 | 225 | West | 28F3
135607 | 2017-04-10 | Adverse Weather | Extreme Wind | Primary wires tangled together. | O/H Conductor | O/H Conductor | 12 | 234 | 47 | Central | SR03
135607 | 2017-04-10 | Adverse Weather | Extreme Wind | Primary wires tangled together. | O/H Conductor | O/H Conductor | 18 | 44 | 13 | Central | SR03
135608 | 2017-04-10 | Tree Contacts | Falling Tree | High winds caused tree to fall into overhead. | O/H Switchgear | Inline Switch | 62 | 225 | 232 | East | 7F4
135609 | 2017-04-10 | Tree Contacts | Falling Tree | Tree fell into overhead | O/H Switchgear | Inline Switch | 43 | 79 | 57 | South | 22M27
135610 | 2017-04-11 | Defective Equipment | Imminent Failure | VT134 at 810 Pincrest isolated to repair 13kV main breaker and replace leaking transformer. 1 customer affected. Lincoln Heighs (5408) | Vault Equipment | Breaker \ Relay | 1 | 270 | 4 | Central | 5408
135611 | 2017-04-11 | Scheduled Outage | Maintenance | Transformer #X39838 isolated by crew to replace transformer switch | None | None | 2 | 44 | 1 | West | MWDF3
135612 | 2017-04-11 | Scheduled Outage | Maintenance | Transformer #X40230 isolated by crew to replace transformer switch | None | None | 2 | 30 | 1 | West | MWDF3
135613 | 2017-04-11 | Scheduled Outage | Construction | Transformer #X26884 isolated by crew to take a transformer out of service and installed a new one | None | None | 16 | 65 | 17 | East | TB15
135614 | 2017-04-12 | Scheduled Outage | Vegetation Management | TD05 overhead section on Henley isolated for tree trimming. 18 customers affected. Lincoln Heights (TD05) | None | O/H Conductor | 18 | 118 | 35 | Central | TD05
135615 | 2017-04-12 | Defective Equipment | Imminent Failure | Replace Leaking Transformer TE1898 | U/G Transformer | Padmount (1ph) | 9 | 114 | 17 | East | 4801F8
135616 | 2017-04-12 | Scheduled Outage | Maintenance | TP11199 isolated for soil remediation | None | Padmount (1ph) | 7 | 562 | 66 | East | LTM01
135617 | 2017-04-12 | Scheduled Outage | Construction | Transformer #X34465 isolated by crew to replace transformer | None | None | 15 | 58 | 14 | East | TB15
135619 | 2017-04-12 | Scheduled Outage | Construction | Transformer #X39849 isolated by crew to replace transformer switch | None | None | 2 | 18 | 1 | West | MWDF3
135620 | 2017-04-12 | Scheduled Outage | Maintenance | Colin Portt and Oakley McCoy to have transformer X23074 open to replace O/H secondary conductor to 454 Queen Mary St. | None | None | 8 | 81 | 11 | East | SO12
135621 | 2017-04-13 | Scheduled Outage | Vegetation Management | P71 at 181 Donald St was isolated by the crew to allow them replace the switches and put the padmount back onto its base. | None | Fused Cutout | 1 | 60 | 1 | East | UT07
135622 | 2017-04-13 | Defective Equipment | Mechanical Failure | Wires down at Bank St North of Findlay creek. W phase tap feeding G798 | O/H Conductor | O/H Conductor | 1 | 53 | 1 | East | LTM01
135622 | 2017-04-13 | Defective Equipment | Mechanical Failure | Wires down at Bank St North of Findlay creek. W phase tap feeding G798 | O/H Conductor | O/H Conductor | 3027 | 45 | 2270 | East | LTM01
135623 | 2017-04-13 | Scheduled Outage | Maintenance | Soil remediation and re-location of transformer | None | Padmount (1ph) | 7 | 373 | 44 | East | LTM01
135625 | 2017-04-13 | Scheduled Outage | Vegetation Management | Forestry work on Thorson Ave affecting 60 customers on the Edwin UV03 | None | None | 60 | 136 | 136 | Central | UV03
135628 | 2017-04-15 | Scheduled Outage | Maintenance | Chris Donnelly and on-call crew to have transformer X33657 open to replace overhread secondary service to 2032 Killarney Drive. Customers notified. | None | None | 6 | 28 | 3 | Central | TW22
135629 | 2017-04-15 | Defective Equipment | Defective Equipment/ Material | Defective transformer X32398 was replaced by on call crew. | O/H Transformer | O/H Transformer (1ph) | 8 | 242 | 32 | South | 170F1
135630 | 2017-04-16 | Defective Equipment | Mechanical Failure | Customer called in part power. 24/7 found one phase blown at S22902. Under ground came in to make repairs to terminated at base of switch gear. | U/G Cable Attachement | Termination \ Stress Cone | 31 | 247 | 128 | Central | TR3UY
135631 | 2017-04-16 | Defective Equipment | Mechanical Failure | Not yet known. | O/H Switchgear | Fused Cutout | 47 | 85 | 67 | South | 87F3
135633 | 2017-04-16 | Defective Equipment | Electrical Failure | Underground cable fault between K552 & K553 caused S20710W to open. 35 customers restored in stages. Playfair AJ06. | U/G Cable | XLPE | 7 | 37 | 4 | East | AJ06
135633 | 2017-04-16 | Defective Equipment | Electrical Failure | Underground cable fault between K552 & K553 caused S20710W to open. 35 customers restored in stages. Playfair AJ06. | U/G Cable | XLPE | 17 | 22 | 6 | East | AJ06
135633 | 2017-04-16 | Defective Equipment | Electrical Failure | Underground cable fault between K552 & K553 caused S20710W to open. 35 customers restored in stages. Playfair AJ06. | U/G Cable | XLPE | 35 | 134 | 78 | East | AJ06
135636 | 2017-04-17 | Defective Equipment | Mechanical Failure | Crews reports TE1699 might be defective and TP7385-H1A elbow is defective and possible cable fault. Cable isolation between TE1695WB, TE1698R & TE1704BR & TE1702W.(transformers isolated TE1699RWB,TE1700W,TP7069RWB & TP7385B) | U/G Cable | XLPE | 42 | 208 | 146 | East | 77M6
135636 | 2017-04-17 | Defective Equipment | Mechanical Failure | Crews reports TE1699 might be defective and TP7385-H1A elbow is defective and possible cable fault. Cable isolation between TE1695WB, TE1698R & TE1704BR & TE1702W.(transformers isolated TE1699RWB,TE1700W,TP7069RWB & TP7385B) | U/G Cable | XLPE | 63 | 15 | 16 | East | 77M6
135636 | 2017-04-17 | Defective Equipment | Mechanical Failure | Crews reports TE1699 might be defective and TP7385-H1A elbow is defective and possible cable fault. Cable isolation between TE1695WB, TE1698R & TE1704BR & TE1702W.(transformers isolated TE1699RWB,TE1700W,TP7069RWB & TP7385B) | U/G Cable | XLPE | 73 | 33 | 40 | East | 77M6
135636 | 2017-04-17 | Defective Equipment | Mechanical Failure | Crews reports TE1699 might be defective and TP7385-H1A elbow is defective and possible cable fault. Cable isolation between TE1695WB, TE1698R & TE1704BR & TE1702W.(transformers isolated TE1699RWB,TE1700W,TP7069RWB & TP7385B) | U/G Cable | XLPE | 109 | 1 | 2 | East | 77M6
135636 | 2017-04-17 | Defective Equipment | Mechanical Failure | Crews reports TE1699 might be defective and TP7385-H1A elbow is defective and possible cable fault. Cable isolation between TE1695WB, TE1698R & TE1704BR & TE1702W.(transformers isolated TE1699RWB,TE1700W,TP7069RWB & TP7385B) | U/G Cable | XLPE | 151 | 268 | 674 | East | 77M6
135636 | 2017-04-17 | Defective Equipment | Mechanical Failure | Crews reports TE1699 might be defective and TP7385-H1A elbow is defective and possible cable fault. Cable isolation between TE1695WB, TE1698R & TE1704BR & TE1702W.(transformers isolated TE1699RWB,TE1700W,TP7069RWB & TP7385B) | U/G Cable | XLPE | 213 | 14 | 50 | East | 77M6
135636 | 2017-04-17 | Defective Equipment | Mechanical Failure | Crews reports TE1699 might be defective and TP7385-H1A elbow is defective and possible cable fault. Cable isolation between TE1695WB, TE1698R & TE1704BR & TE1702W.(transformers isolated TE1699RWB,TE1700W,TP7069RWB & TP7385B) | U/G Cable | XLPE | 213 | 28 | 99 | East | 77M6
135636 | 2017-04-17 | Defective Equipment | Mechanical Failure | Crews reports TE1699 might be defective and TP7385-H1A elbow is defective and possible cable fault. Cable isolation between TE1695WB, TE1698R & TE1704BR & TE1702W.(transformers isolated TE1699RWB,TE1700W,TP7069RWB & TP7385B) | U/G Cable | XLPE | 213 | 54 | 192 | East | 77M6
135636 | 2017-04-17 | Defective Equipment | Mechanical Failure | Crews reports TE1699 might be defective and TP7385-H1A elbow is defective and possible cable fault. Cable isolation between TE1695WB, TE1698R & TE1704BR & TE1702W.(transformers isolated TE1699RWB,TE1700W,TP7069RWB & TP7385B) | U/G Cable | XLPE | 264 | 138 | 607 | East | 77M6
135636 | 2017-04-17 | Defective Equipment | Mechanical Failure | Crews reports TE1699 might be defective and TP7385-H1A elbow is defective and possible cable fault. Cable isolation between TE1695WB, TE1698R & TE1704BR & TE1702W.(transformers isolated TE1699RWB,TE1700W,TP7069RWB & TP7385B) | U/G Cable | XLPE | 1477 | 1 | 25 | East | 77M6
135637 | 2017-04-18 | Scheduled Outage | Maintenance | Transformer TP11199 at 173 Helen Rapp was isolated to allow crew to perfrom transformer soil remediation. Limebank (7F2). | None | None | 7 | 570 | 66 | East | 7F2
135638 | 2017-04-18 | Scheduled Outage | Maintenance | Transformer #X32370 isolated by crew to replace porcelain switch | None | None | 18 | 48 | 14 | Central | TD06
135639 | 2017-04-18 | Scheduled Outage | Maintenance | Transformer #X32368 isolated by crew to replace porcelain switch | None | None | 4 | 48 | 3 | Central | TD06
135640 | 2017-04-18 | Scheduled Outage | Construction | Transformer #X23308 isolated by crew for a service upgrade | None | None | 5 | 70 | 6 | East | UB03
135642 | 2017-04-18 | Defective Equipment | Electrical Failure | Transformer #X32355 isolated by crew to replace porcelain switch | O/H Switchgear | Fused Cutout | 41 | 25 | 17 | Central | TD06
135643 | 2017-04-18 | Scheduled Outage | Maintenance | Transformer #X32356 isolated by crew to replace porcelain switch | None | None | 13 | 35 | 8 | Central | TD06
135644 | 2017-04-18 | Scheduled Outage | Construction | Transformer #X35146 isolated by crew to replace cut out | None | None | 10 | 44 | 7 | South | 190F5
135645 | 2017-04-18 | Scheduled Outage | Maintenance | Transformer #X32354 isolated by crew to replace porcelain switch | None | None | 28 | 21 | 10 | Central | TD06
135646 | 2017-04-19 | Scheduled Outage | Vegetation Management | Overhead circuit from S13339 to EOL on Mansfield isolated for tree trimming. 14 customers affected. Lincoln Heights (TD01) | None | O/H Conductor | 14 | 276 | 64 | Central | TD01
135648 | 2017-04-19 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X27014 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 13 | 140 | 30 | East | AE06
135649 | 2017-04-19 | Scheduled Outage | Maintenance | OUTAGE TO MAKE REPAIRS TO DEFTV SWITCHES | None | Fused Cutout | 9 | 110 | 16 | South | 200F2
135650 | 2017-04-20 | Scheduled Outage | Construction | TB15 ovehread on Tweed Ave. isolated to set poles with a crane. 51 customers affected. Russell (TB15) | None | Pole | 51 | 495 | 421 | East | TB15
135651 | 2017-04-20 | Defective Equipment | Electrical Failure | Transformers K765, K766, K767 and K768 on Walklley and Flannery were isolated for insulator and arresstor replacement. 28 customers affected. Walklye (UZ02) | U/G Transformer | Kiosk (1ph) | 28 | 194 | 91 | East | UZ02
135653 | 2017-04-20 | Scheduled Outage | Construction | Transformer #X36265 isolated by crew to replace a service | None | None | 9 | 75 | 11 | South | EPWF4
135654 | 2017-04-20 | Scheduled Outage | Vegetation Management | Overhead at 61 Burke isolated for tree trimming. 8 cutomers affected. Richmond South (28F2) | None | O/H Conductor | 8 | 236 | 31 | West | 28F2
135655 | 2017-04-20 | Scheduled Outage | Construction | Transformer #X30695 isolated by crew for a transformer upgrade | None | None | 16 | 190 | 51 | Central | UF05
135656 | 2017-04-21 | Defective Equipment | Electrical Failure | defective transformer | U/G Transformer | Padmount (3ph) | 1 | 334 | 6 | Central | UC03
135659 | 2017-04-22 | Defective Equipment | Electrical Failure | Red phase cable fault between K40 and K41 | U/G Cable | XLPE | 35 | 112 | 65 | East | AQ09
135660 | 2017-04-23 | Foreign Interference | Vehicle | Motor Vehicle accident at 2244 Russell Rd, car hit pole X25011 and caused the S10681 to open and road side / field side phases to disconnect from insulator. Russell (5310) | O/H Switchgear | Fused Cutout | 75 | 130 | 162 | East | 5310
135663 | 2017-04-23 | Scheduled Outage | Construction | To replace transformer TP11134. | None | Padmount (3ph) | 2 | 160 | 5 | South | FAL01
135664 | 2017-04-23 | Defective Equipment | Defective Equipment/ Material | To check secondary connections at transformer. | Secondary \ Service | O/H Service | 8 | 35 | 5 | South | 49F6
135665 | 2017-04-23 | Defective Equipment | Mechanical Failure | Loose/sagging open wire secondary buss caused S312 to open, affecting 160 customers on the 190F2 B phase. | Secondary \ Service | O/H Service | 160 | 63 | 168 | South | 190F2
135666 | 2017-04-23 | Defective Equipment | Defective Equipment/ Material | Transformer X21134 open due to defective fuse barrel and arrestor. CASSELMAN (CAS-F1). | O/H Switchgear | Fused Cutout | 8 | 139 | 19 | East | V11F2
135669 | 2017-04-24 | Scheduled Outage | Vegetation Management | Tree Trimming on Stevenson affecting 55 customers on the Shillington AD06 | None | None | 55 | 325 | 298 | Central | AD06
135670 | 2017-04-24 | Defective Equipment | Electrical Failure | Outage to 3 Kiosks on Sandhurst to replace blown arresters, porcelain insulators and to remove asbestos boards. Walkley UZ04 | U/G Cable Attachement | Arrester | 18 | 224 | 67 | East | UZ04
135671 | 2017-04-24 | Scheduled Outage | Maintenance | To change ou old copper conductor on the UF04 Red phase run-off at James and Kent affecting 16 customers out of Florence | None | None | 16 | 24 | 6 | Central | UF04
135672 | 2017-04-24 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to repair open wire secondary bus that had become twisted. | None | O/H Conductor | 8 | 60 | 8 | South | 190F5
135673 | 2017-04-24 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35309 TO REPLACE SWITCH AND ARRESTER | None | None | 21 | 40 | 14 | Central | TD06
135674 | 2017-04-25 | Scheduled Outage | Maintenance | Vault V473 at 258 lisgar was isolated for vault maintence. One customer was affected. Gladstone. (UX10) | None | None | 1 | 187 | 3 | Central | UX10
135675 | 2017-04-25 | Defective Equipment | Imminent Failure | At 9:30 Transformers 8680 and 8679 were isolated to allow crews to replace leaking transformers. 30 customers affected. Terry Fox (TFXF1) | U/G Transformer | Padmount (1ph) | 30 | 292 | 146 | West | TFXF1
135676 | 2017-04-25 | Scheduled Outage | Vegetation Management | At 9:02am a section of 43F3 was isolated to allow crews to trim trees. 1 customer affected. Munster (43F3) | None | None | 1 | 281 | 5 | West | 43F3
135677 | 2017-04-25 | Scheduled Outage | Maintenance | vault VT709 at 520 bronson was isolated to allow contractor to replace main disconnect on solar array. One customer was affected. Hinchey. (TH1SB) | None | None | 1 | 170 | 3 | Central | TH01
135678 | 2017-04-25 | Scheduled Outage | Construction | Marc Branchaud and crew to have transformer X34054 open to upgrade a service. Customer notiifed. | None | None | 6 | 45 | 4 | East | AA06
135679 | 2017-04-25 | Scheduled Outage | Construction | Transformer #X30519 isolated by crew to transfer services | None | None | 14 | 465 | 108 | Central | UF05
135681 | 2017-04-26 | Defective Equipment | Electrical Failure | 4kv circuit section was isolated including V840 to replace deadend of circuit at Maclaren and lyon. 21 customers were affected. Florence (UF05) | Pole Attachement | Insulator | 21 | 143 | 50 | Central | UF05
135682 | 2017-04-26 | Scheduled Outage | Construction | Stuart Maclaren and crew to have a transformer open at this address for pole replacement affecting 14 customers. Customers notified. | None | None | 14 | 340 | 79 | East | TB15
135683 | 2017-04-26 | Scheduled Outage | Construction | overhead transformer X27361 was isolated to allow crew to reconfigure UQ07 overhead. 13 customers were interrupted. Queens (UQ07) | None | None | 13 | 510 | 110 | East | UQ07
135684 | 2017-04-27 | Scheduled Outage | Maintenance | 3 transformers were isolated on Red Fox Cres to clear sand from the bases affecting 40 customers. Bridlewood BRDF2 | None | None | 40 | 231 | 154 | West | BRDF2
135685 | 2017-04-27 | Defective Equipment | Electrical Failure | planned outage to repair blown arrestor, remove asbestos barrier board. | U/G Cable Attachement | Arrester | 47 | 167 | 131 | East | AL02
135687 | 2017-04-27 | Scheduled Outage | Vegetation Management | planned outage for vegetation management | None | None | 38 | 206 | 130 | Central | SM02
135688 | 2017-04-27 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X27045 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 10 | 300 | 50 | East | TB06
135689 | 2017-04-27 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33716 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 13 | 170 | 37 | Central | UJ07
135690 | 2017-04-27 | Scheduled Outage | Forced Switching | Switch S1634 at 3147 Carling was open to allow crew to Brace pole due to woodpecker dammage. Bayshore (49F1) | None | None | 1 | 61 | 1 | South | 49F1
135698 | 2017-04-28 | Defective Equipment | Defective Equipment/ Material | While perfroming switching to restore the TW22 circuit to normal, crew close the TW22 PPH switches and S14621 B phase blew. Suspect defective TW22 B phase egress cable. | U/G Cable | XLPE | 495 | 28 | 231 | Central | TW00
135699 | 2017-04-28 | Defective Equipment | Defective Equipment/ Material | REPLACED BROKEN SWICH FEEDING TRANSFOMER X35881 | O/H Transformer | O/H Transformer (1ph) | 7 | 140 | 16 | West | 28F1
135700 | 2017-04-28 | Scheduled Outage | Forced Switching | Transformer TP7469 at 432 was isoated to allow crew to replace transformer that was dammaged by garbage truck. To during the isolation and restoration of TP7469, 133 customers were interrupted due to out of phase switching. Limebank (LMBF5) | None | Padmount (1ph) | 0 | 8 | 0 | East | LMBF5
135700 | 2017-04-28 | Scheduled Outage | Forced Switching | Transformer TP7469 at 432 was isoated to allow crew to replace transformer that was dammaged by garbage truck. To during the isolation and restoration of TP7469, 133 customers were interrupted due to out of phase switching. Limebank (LMBF5) | None | Padmount (1ph) | 0 | 10 | 0 | East | LMBF5
135700 | 2017-04-28 | Scheduled Outage | Forced Switching | Transformer TP7469 at 432 was isoated to allow crew to replace transformer that was dammaged by garbage truck. To during the isolation and restoration of TP7469, 133 customers were interrupted due to out of phase switching. Limebank (LMBF5) | None | Padmount (1ph) | 7 | 51 | 6 | East | LMBF5
135700 | 2017-04-28 | Scheduled Outage | Forced Switching | Transformer TP7469 at 432 was isoated to allow crew to replace transformer that was dammaged by garbage truck. To during the isolation and restoration of TP7469, 133 customers were interrupted due to out of phase switching. Limebank (LMBF5) | None | Padmount (1ph) | 133 | 1 | 2 | East | LMBF5
135700 | 2017-04-28 | Scheduled Outage | Forced Switching | Transformer TP7469 at 432 was isoated to allow crew to replace transformer that was dammaged by garbage truck. To during the isolation and restoration of TP7469, 133 customers were interrupted due to out of phase switching. Limebank (LMBF5) | None | Padmount (1ph) | 133 | 2 | 4 | East | LMBF5
135701 | 2017-04-28 | Defective Equipment | Defective Equipment/ Material | Transformer TE2133 at 2 Stonebank was isolated to allow crew to replace leaking transformer. Stafford (200F6) | U/G Transformer | Padmount (1ph) | 13 | 96 | 21 | South | 200F6
135703 | 2017-04-29 | Loss Of Supply | Third Party | Transformer TN9550CZZ isolated from S10043 RWB to allow contractor to disconnect defective customer owned equipment. | None | None | 1 | 355 | 6 | West | BECKF2
135707 | 2017-04-30 | Scheduled Outage | Maintenance | X28143 opened to allow crew to replace blown streetlight fuse. | O/H Transformer | O/H Transformer (1ph) | 6 | 8 | 1 | East | AF06
135708 | 2017-05-01 | Scheduled Outage | Construction | Transformer #X32505 isolated by crew to drop a service | None | None | 13 | 20 | 4 | Central | TD01
135709 | 2017-05-01 | Defective Equipment | Defective Equipment/ Material | The 77M5 A/R/A and the RX2040 A/R/A due to defective arrestor at S28442. Billberry (77M5) | Pole Attachement | Arrester | 54 | 36 | 32 | East | 77M5
135709 | 2017-05-01 | Defective Equipment | Defective Equipment/ Material | The 77M5 A/R/A and the RX2040 A/R/A due to defective arrestor at S28442. Billberry (77M5) | Pole Attachement | Arrester | 1371 | 7 | 160 | East | 77M5
135710 | 2017-05-01 | Loss Of Supply | Third Party | The Uplands 4801F8 CB A/R during the heavy rain fall and W phase flagged on instantaneous trip. Crew to patrol circuit during day time. Crew found S16332 W to be open due to tree branch on customer owned line. | None | None | 1 | 1047 | 17 | East | 4801F8
135711 | 2017-05-02 | Scheduled Outage | Vegetation Management | OH from S28196 to EOL isolated for tree trimmimh. 17 customers affected. Edwin DS (UV05) | None | None | 17 | 100 | 28 | Central | UV05
135712 | 2017-05-02 | Scheduled Outage | Maintenance | transfer plant | None | O/H Service | 5 | 250 | 21 | Central | TH01
135713 | 2017-05-03 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 13 | 158 | 34 | East | LMBF5
135714 | 2017-05-03 | Defective Equipment | Defective Equipment/ Material | K41 transformer isolated to repair defective cable. Affected 9 customers. McCarthy (AQ09) | Secondary \ Service | U/G Service | 9 | 165 | 25 | East | AQ09
135717 | 2017-05-03 | Defective Equipment | Defective Equipment/ Material | SO07 overhead isolated to repaired down wires at 542 Donald, affecting 18 customners. Overbrook (SO07). | O/H Conductor | Unknown \ Other | 18 | 92 | 28 | East | SO07
135719 | 2017-05-03 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X37173 TO REPLACE SECONDARY CONNECTIONS | None | None | 5 | 48 | 4 | Central | SH04
135720 | 2017-05-04 | Scheduled Outage | Vegetation Management | crew isolated overhead line to trim trees on Oakdale. 25 customers affected. Hinchey (TH01) | None | None | 25 | 285 | 119 | Central | TH01
135721 | 2017-05-04 | Defective Equipment | Electrical Failure | Not yet known.crew isolated four transformers on southvale cres. To replace blown arrestors, and asbestos removal. 64 customers affected. Bantree (AL02) | U/G Cable Attachement | Arrester | 64 | 198 | 211 | East | AL02
135722 | 2017-05-04 | Defective Equipment | Imminent Failure | At 10:17, leaking transformer TP6241 was isolated to allow crew to replace it. 12 customers affected. Jockvale (145F4) | U/G Transformer | Padmount (1ph) | 12 | 116 | 23 | South | 145F4
135723 | 2017-05-04 | Scheduled Outage | Construction | crew isolated K1004 at 438 Bay st. to re-arrange overhead. 6 customers were affected. Florence (UF07) | None | None | 6 | 34 | 3 | Central | UF07
135724 | 2017-05-04 | Scheduled Outage | Construction | crew isolated UF07 overhead section on James between Percy and Bay to change customers to white phase. 53 customers were affected. Florence (UF07) | None | None | 53 | 305 | 269 | Central | UF07
135725 | 2017-05-04 | Scheduled Outage | Vegetation Management | At 09:10am X26261 on the UN04 circuit was isolated to allow crew to perform vegetation management. 12 customers affected. Henderson (UN04). | None | None | 12 | 129 | 26 | Central | UN04
135726 | 2017-05-04 | Foreign Interference | Vehicle | PRIMARY CONDUCTOR CAME DOWN ON SEC SERVICE | O/H Conductor | O/H Conductor | 16 | 350 | 93 | Central | UF07
135727 | 2017-05-05 | Defective Equipment | Mechanical Failure | A broken switch at S371 cause the outage to the overhead on Todd dr affecting 18 customers RFNF1 | O/H Switchgear | Fused Cutout | 18 | 167 | 50 | West | RHNF1
135733 | 2017-05-06 | Foreign Interference | Foreign Objects | Balloon | Station Equipment | Relay | 246 | 17 | 70 | Central | UX04
135735 | 2017-05-07 | Scheduled Outage | Maintenance | planned outage to replace overheating elbows | None | None | 1 | 279 | 5 | West | MWDF4
135736 | 2017-05-07 | Scheduled Outage | Construction | planned outage to connect riser cables to a new pole. | None | None | 1 | 410 | 7 | Central | AM06
135738 | 2017-05-07 | Scheduled Outage | Construction | ISOLATED TRANSFORMER 55D-2A-0386 TO INSTALL NEW POLE | None | None | 3 | 70 | 4 | Central | AM06
135740 | 2017-05-07 | Scheduled Outage | Construction | ISOLATED TRANSFORMER 55D2A-0386 TO INSTALL NEW POLE | None | None | 3 | 39 | 2 | Central | AM06
135741 | 2017-05-07 | Defective Equipment | Electrical Failure | 2202 egress cable fault | U/G Cable | PILC | 62 | 34 | 35 | East | 2202
135743 | 2017-05-08 | Defective Equipment | Electrical Failure | planned outage to replace blown arrestors and replace porceiln switches | Pole Attachement | Arrester | 93 | 214 | 332 | East | AL02
135744 | 2017-05-08 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X29494 TO REPLACE POLE | None | None | 15 | 153 | 38 | East | SO03
135745 | 2017-05-08 | Scheduled Outage | Maintenance | Oakley McCoy and crew to have transformer X31926 open to upgrade the service at 368 Brittannia. Emergency outage customers notified if possible. | None | None | 16 | 69 | 18 | Central | TD14
135746 | 2017-05-09 | Scheduled Outage | Construction | To transfer riser to new pole. | None | None | 1 | 301 | 5 | Central | UF07
135747 | 2017-05-09 | Scheduled Outage | Construction | Transformer #X24923 isolated by crew for a service upgrade | None | None | 3 | 35 | 2 | East | UZ03
135750 | 2017-05-10 | Defective Equipment | Corrosion | To allow Hydro Ottawa line crews to replace transformer 5194 and Drain-All to perform soil remediation | U/G Transformer | Padmount (1ph) | 12 | 671 | 134 | West | BRDF5
135751 | 2017-05-10 | Scheduled Outage | Construction | 2 transformers, X31460 and X31468 isolated by crew to transfer plant | None | None | 17 | 235 | 67 | Central | TH01
135752 | 2017-05-10 | Scheduled Outage | Construction | Transformer #X08020 isolated by crew to replace cut out | None | None | 1 | 120 | 2 | West | MWDF3
135753 | 2017-05-10 | Scheduled Outage | Construction | Doug Featherstone and crew to have transformer X33890 open to reconnect an overhead service. | None | None | 7 | 45 | 5 | Central | SM06
135754 | 2017-05-11 | Defective Equipment | Mechanical Failure | K9 isolated to repair defective insulator and disconnect secondary pedestle, affecting 10 customers. McCarthy (AQ11) | Pole Attachement | Insulator | 10 | 127 | 21 | East | AQ11
135755 | 2017-05-11 | Scheduled Outage | Maintenance | K9 fused disconnect open to reconnect secondary pedastle, affecting 10 customers. Mccarthy (AQ11) | None | Kiosk (1ph) | 10 | 8 | 1 | East | AQ11
135756 | 2017-05-12 | Scheduled Outage | Maintenance | P382 isolated to test equipotential grounding, affecting 1 customer. Hilcrest (AH14) | None | Padmount (3ph) | 1 | 37 | 1 | Central | AH14
135758 | 2017-05-13 | Foreign Interference | Wildlife (Bird/Animal) | Crew reports outage at transformer X27645 due to animal contact. | O/H Switchgear | Fused Cutout | 12 | 95 | 19 | East | TB15
135759 | 2017-05-13 | Scheduled Outage | Construction | 4kv Vault V306 at 331 cooper was isolated to allow crew to prove spare duct, and install new secondary conductor. One customer was affected. Gladstone (UX03) | None | None | 1 | 154 | 3 | Central | UX03
135761 | 2017-05-15 | Defective Equipment | Electrical Failure | four 4KV kiosks on Montfort st. were isolated to allow crew to replace blown arrestors,porcelin insulators, and porcelin cutouts. 90 customers were affected. Church (AA03) | U/G Cable Attachement | Arrester | 90 | 198 | 297 | East | AA03
135762 | 2017-05-15 | Scheduled Outage | Vegetation Management | section of UV05 overhead circuit was isolated to allow crews to trim trees at rear of 2400 Malone. 42 customers were affected. Edwin (UV05) | None | None | 42 | 376 | 263 | Central | UV05
135763 | 2017-05-15 | Scheduled Outage | Construction | section of TB15 overhead circuit at 1909 Tweed ave. was isolated to allow crews to set poles wit crane. 20 customers affected. Russell. (TB15) | None | None | 20 | 378 | 126 | East | TB15
135764 | 2017-05-15 | Defective Equipment | Mechanical Failure | Defective lightning arrestor. | Pole Attachement | Arrester | 43 | 165 | 118 | East | 77M1
135765 | 2017-05-16 | Scheduled Outage | Maintenance | P313 at 411 Dovercourt was isolated for soil remediation. Customer is on generator while work being performed. 1 customer affected. Clyde UC03. | None | Padmount (3ph) | 1 | 10 | 0 | Central | UC03
135766 | 2017-05-16 | Scheduled Outage | Vegetation Management | A section of overhead line on Viscount Ave was isolated to trim trees. 93 customers affected. Carling SM01. | None | None | 93 | 230 | 356 | Central | SM01
135769 | 2017-05-16 | Defective Equipment | Imminent Failure | TE1096 at 5 Cheryl Rd. isolated for replacement due to oil leak. 13 customers affected. Merivale (72F1) | U/G Transformer | Padmount (1ph) | 13 | 83 | 18 | South | 72F1
135770 | 2017-05-16 | Scheduled Outage | Construction | Transformer #X28140 isolated by crew for a service upgrade | None | None | 9 | 60 | 9 | East | UZ04
135771 | 2017-05-16 | Scheduled Outage | Construction | POLE REPLACEMENT | None | None | 13 | 558 | 121 | Central | TH01
135772 | 2017-05-17 | Defective Equipment | Electrical Failure | Defective cutout at X35928 caused to S11625R to blow. | O/H Transformer | O/H Transformer (1ph) | 38 | 110 | 70 | South | 190F5
135773 | 2017-05-17 | Scheduled Outage | Construction | 140F4 W overhead line isolated from S18702 to allow crew to transfer plant to new line. | None | Customer-Owned | 2 | 196 | 7 | South | 140F4
135775 | 2017-05-17 | Scheduled Outage | Vegetation Management | Transformer #X26985 isolated by crew for tree trimming | None | None | 15 | 180 | 45 | East | AJ03
135777 | 2017-05-17 | Scheduled Outage | Construction | 3 transformers (TP7268, 7267 and 7263) isolated by crew to re-arrange plant | None | None | 36 | 20 | 12 | South | FAL03
135778 | 2017-05-17 | Scheduled Outage | Construction | Outage to 36 customers during switching due to an out of phase condition. Fallowfield FAL03. | None | None | 36 | 5 | 3 | South | FAL03
135781 | 2017-05-17 | Adverse Weather | Extreme Wind | 6F4 auto reclosed, to be patrolled by 24/7. | Station Equipment | Relay | 0 | 67 | 0 | East | 6F4
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 1 | 9 | 0 | East | TB07
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 1 | 204 | 3 | East | 5306
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 2 | 1 | 0 | East | TB07
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 3 | 5 | 0 | East | TB07
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 4 | 3 | 0 | East | TB07
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 5 | 2 | 0 | East | TB07
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 6 | 5 | 0 | East | TB07
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 22 | 5 | 2 | East | 5306
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 25 | 3 | 1 | East | 5306
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 26 | 14 | 6 | East | 5306
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 36 | 38 | 23 | East | TB07
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 36 | 75 | 45 | East | TB07
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 37 | 24 | 15 | East | 5306
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 39 | 159 | 103 | East | 5306
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 46 | 60 | 46 | East | TB07
135783 | 2017-05-18 | Defective Equipment | Mechanical Failure | A blown pothead at S28992 feeding VT244 at 1411 Triole caused the 5306 O/H line to failand fall into TB07 causing outages to both circuits. | U/G Cable Attachement | Pothead | 333 | 175 | 971 | East | TB07
135784 | 2017-05-18 | Scheduled Outage | Vegetation Management | Forrestry management on Traverse affecting 65 customers on the Brookfield AF07 Red phase | None | None | 65 | 301 | 326 | East | AF07
135785 | 2017-05-18 | Defective Equipment | Imminent Failure | Leaking transformer TP7979 changeout by HOL Crew affecting 10 customers on the Terry Fox TFXF1 | U/G Transformer | Padmount (3ph) | 10 | 68 | 11 | West | TFXF1
135786 | 2017-05-18 | Defective Equipment | Corrosion | Pedastal changeout at 17 Okenagan Drive on the QCH 160F4 affecting 6 customers | Secondary \ Service | Secondary Pedestal | 6 | 166 | 17 | South | 160F1
135787 | 2017-05-18 | Defective Equipment | Electrical Failure | Replacing blown arresters, removing asbestos boards and changing porcelain insulators at K79, K80, and K81 at 770 Huntclub Road affecting 24 AQ10 customers out of McCarthy Sub | U/G Cable Attachement | Arrester | 24 | 182 | 73 | East | AQ10
135789 | 2017-05-18 | Foreign Interference | Agricultural Equipment | Hydro Pole broken by farm equipment. | Pole Attachement | Unknown \ Other | 7 | 350 | 41 | West | 28F3
135789 | 2017-05-18 | Foreign Interference | Agricultural Equipment | Hydro Pole broken by farm equipment. | Pole Attachement | Unknown \ Other | 2281 | 67 | 2547 | West | 28F3
135790 | 2017-05-18 | Scheduled Outage | Construction | Transformer #K00930 isolated by crew to install new service | None | None | 7 | 35 | 4 | East | UB05
135791 | 2017-05-18 | Defective Equipment | Corrosion | Mark Brown and crew to have transformer NPTE0103 open to change a pedestal. Customers notified. | Secondary \ Service | Secondary Pedestal | 6 | 223 | 22 | South | 160F4
135792 | 2017-05-18 | Scheduled Outage | Construction | Scott Barkely to have X30126 and transformer X30136 open to replace both transformers with a single transformer. Customers notified. | None | None | 32 | 295 | 157 | Central | AM05
135793 | 2017-05-18 | Adverse Weather | Extreme Wind | Not yet known. | O/H Conductor | O/H Conductor | 165 | 314 | 864 | East | 6F4
135797 | 2017-05-18 | Adverse Weather | Extreme Wind | High winds suspected | None | None | 654 | 13 | 142 | East | UZ06
135798 | 2017-05-18 | Defective Equipment | Electrical Failure | Crew isolated 4Kv transformer K288 at 211 Twyford to replace decfective transformer, and faulted secondary. 16 customers were affected. Elwood (ELW04) | U/G Transformer | Kiosk (1ph) | 16 | 596 | 159 | East | ELW04
135799 | 2017-05-18 | Scheduled Outage | Maintenance | The switch gear S183 at the Canadian Tire centre was isolated to allow the crew inspect and repair load side elbows | None | Padmount (3ph) | 1 | 112 | 2 | West | 624F1
135800 | 2017-05-18 | Tree Contacts | Broken Branch | The W phase at switch S28321 open due to a limb on the overhead on the AP04 affecting 12 customers | O/H Conductor | O/H Conductor | 12 | 176 | 35 | East | AP04
135801 | 2017-05-18 | Defective Equipment | Electrical Failure | crew made repairs to the 4Kv white phase overhead that burnt clear at 2205 St. Laurent. The circuit was opened to make final connection due to proximatey of adjacent circuit. 117 customer were affected by the burnt connection. 323 were affected to make c | O/H Conductor | O/H Conductor | 117 | 318 | 620 | East | AE01
135801 | 2017-05-18 | Defective Equipment | Electrical Failure | crew made repairs to the 4Kv white phase overhead that burnt clear at 2205 St. Laurent. The circuit was opened to make final connection due to proximatey of adjacent circuit. 117 customer were affected by the burnt connection. 323 were affected to make c | O/H Conductor | O/H Conductor | 323 | 27 | 145 | East | AE01
135804 | 2017-05-20 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at RX2063 caused TB13 to open. 2251 customers affected. Russell TB2JP. | None | None | 674 | 6 | 67 | East | TB2JP
135804 | 2017-05-20 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at RX2063 caused TB13 to open. 2251 customers affected. Russell TB2JP. | None | None | 2251 | 55 | 2063 | East | TB2JP
135805 | 2017-05-20 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused fuse to open at transformer X33390 at 867 Norton. 12 customers affected. Lincoln TD05. | None | None | 12 | 280 | 56 | Central | TD05
135806 | 2017-05-20 | Defective Equipment | Electrical Failure | Cable fault between TE702 and TE703 caused the 180F1 to auto reclose and S975 B to open. Restoration delayed due to equipment failure at TE703. 640 customers affected. Rideau Heights (180F4) | U/G Cable | XLPE | 7 | 282 | 33 | South | 180F4
135806 | 2017-05-20 | Defective Equipment | Electrical Failure | Cable fault between TE702 and TE703 caused the 180F1 to auto reclose and S975 B to open. Restoration delayed due to equipment failure at TE703. 640 customers affected. Rideau Heights (180F4) | U/G Cable | XLPE | 30 | 2 | 1 | South | 180F4
135806 | 2017-05-20 | Defective Equipment | Electrical Failure | Cable fault between TE702 and TE703 caused the 180F1 to auto reclose and S975 B to open. Restoration delayed due to equipment failure at TE703. 640 customers affected. Rideau Heights (180F4) | U/G Cable | XLPE | 48 | 49 | 39 | South | 180F4
135806 | 2017-05-20 | Defective Equipment | Electrical Failure | Cable fault between TE702 and TE703 caused the 180F1 to auto reclose and S975 B to open. Restoration delayed due to equipment failure at TE703. 640 customers affected. Rideau Heights (180F4) | U/G Cable | XLPE | 71 | 23 | 27 | South | 180F4
135806 | 2017-05-20 | Defective Equipment | Electrical Failure | Cable fault between TE702 and TE703 caused the 180F1 to auto reclose and S975 B to open. Restoration delayed due to equipment failure at TE703. 640 customers affected. Rideau Heights (180F4) | U/G Cable | XLPE | 71 | 24 | 28 | South | 180F4
135806 | 2017-05-20 | Defective Equipment | Electrical Failure | Cable fault between TE702 and TE703 caused the 180F1 to auto reclose and S975 B to open. Restoration delayed due to equipment failure at TE703. 640 customers affected. Rideau Heights (180F4) | U/G Cable | XLPE | 71 | 71 | 84 | South | 180F4
135806 | 2017-05-21 | Defective Equipment | Electrical Failure | Cable fault between TE702 and TE703 caused the 180F1 to auto reclose and S975 B to open. Restoration delayed due to equipment failure at TE703. 640 customers affected. Rideau Heights (180F4) | U/G Cable | XLPE | 16 | 4 | 1 | South | 180F4
135807 | 2017-05-21 | Defective Equipment | Defective Equipment/ Material | Defective AH14 egress cable at Hillcrest DS, affecting 460 customers. | U/G Cable | PILC | 460 | 49 | 376 | Central | AH14
135808 | 2017-05-21 | Tree Contacts | Tree Growth/ Untrimmed Tree | Fuse X27694 at 275 Corcus opened due to vines wrapped around transformer. 10 customers affected. Riverdale (505) | O/H Transformer | O/H Transformer (1ph) | 10 | 93 | 16 | Central | 505
135809 | 2017-05-22 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDINF TRANSFORMER X29974 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 7 | 117 | 14 | Central | TD14
135810 | 2017-05-22 | Defective Equipment | Defective Equipment/ Material | Fuse found blown at S0-2 red phase due to defective cable, affecting 51 customers. South march DS (39F2) | U/G Cable | XLPE | 22 | 73 | 27 | West | 39F2
135810 | 2017-05-22 | Defective Equipment | Defective Equipment/ Material | Fuse found blown at S0-2 red phase due to defective cable, affecting 51 customers. South march DS (39F2) | U/G Cable | XLPE | 51 | 70 | 60 | West | 39F2
135812 | 2017-05-22 | Defective Equipment | Defective Equipment/ Material | Transformer #X5627 opened up due to defective transformer switch | O/H Switchgear | Fused Cutout | 9 | 87 | 13 | South | 180F2
135814 | 2017-05-22 | Scheduled Outage | Maintenance | Transformer isolated by crew due to 2 spans of 1/0 that burnt down | None | None | 19 | 43 | 14 | Central | SB02
135815 | 2017-05-23 | Scheduled Outage | Maintenance | Overhead transformer X31397 interrupted to make a service repair affecting 19 customers on the Bronson SB02 | None | None | 19 | 191 | 60 | Central | SB02
135816 | 2017-05-22 | Defective Equipment | Mechanical Failure | Faulted transformer 1578 | U/G Transformer | Padmount (3ph) | 1 | 407 | 7 | West | MWDF4
135816 | 2017-05-22 | Defective Equipment | Mechanical Failure | Faulted transformer 1578 | U/G Transformer | Padmount (3ph) | 3 | 90 | 4 | West | MWDF4
135817 | 2017-05-23 | Defective Equipment | Imminent Failure | Transformer 8425 at 8 Forest Creek was isolated to allow crew to replace leaking transformer. Janet King (JKGF5) | U/G Transformer | Padmount (1ph) | 12 | 117 | 23 | West | JKGF5
135822 | 2017-05-24 | Scheduled Outage | Vegetation Management | MC2087 to EOL at 4042 McBean was isolated to allow crew to perfrom tree trimming. Richmond South (28F3) | None | None | 4 | 345 | 23 | West | 28F3
135823 | 2017-05-24 | Defective Equipment | Electrical Failure | Transformers K76, K77, K78 and K327 were isolated to allow crew to replace blown arrestors, porcelain unsulators and remove asbestos. McCarthy (AQ10) | U/G Cable Attachement | Arrester | 44 | 173 | 127 | East | AQ10
135824 | 2017-05-24 | Defective Equipment | Imminent Failure | A transformer at 2361 Raintree was isolated to replace a leaking transformer affecting 9 customers. Cyrville CYRF3 | U/G Transformer | Padmount (1ph) | 9 | 358 | 54 | East | CYRF3
135827 | 2017-05-24 | Foreign Interference | Vehicle | SB06 CB A/R/A due MVA accident. Truck backed into the Hydro pole X31313 at Bank and Fourth and caused the SB06 O/H conduector to come in contact with each other. No dammage to Hydro Pole | O/H Conductor | O/H Conductor | 621 | 34 | 352 | Central | SB06
135828 | 2017-05-24 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X31459 open to replace poles. Customers notified. | None | None | 9 | 300 | 45 | Central | TH01
135829 | 2017-05-24 | Foreign Interference | Agricultural Equipment | Tractor hit dead end pole. | Pole | Pole | 23 | 129 | 49 | West | RHNF1
135830 | 2017-05-24 | Defective Equipment | Mechanical Failure | Not yet known. | O/H Transformer | O/H Transformer (1ph) | 1 | 376 | 6 | South | 145F1
135831 | 2017-05-25 | Scheduled Outage | Vegetation Management | Overhead circuit from S24582 to EOL at 865 Bronson isolated for tree removal. 64 customers affected. Rivedale (TR09) | None | None | 64 | 264 | 282 | Central | TR09
135832 | 2017-05-25 | Defective Equipment | Imminent Failure | TP7105 isolated to allow crew to replace leaking transformer. | U/G Transformer | Padmount (3ph) | 3 | 60 | 3 | West | MWDF3
135834 | 2017-05-25 | Scheduled Outage | Maintenance | ISOLATED AND REPLACED OVERHEAD 3 PHASE TRANSFORMER X2505 | None | None | 2 | 270 | 9 | South | 200F5
135835 | 2017-05-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | Not yet known. | O/H Conductor | O/H Conductor | 334 | 370 | 2060 | Central | UX05
135835 | 2017-05-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | Not yet known. | O/H Conductor | O/H Conductor | 879 | 415 | 6080 | Central | UX09
135837 | 2017-05-26 | Scheduled Outage | Sectionalizing | Over transformer X30880 isolated to reapir services, affecting 14 customers. Henderson (UN04). | None | None | 14 | 30 | 7 | Central | UN04
135838 | 2017-05-26 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30969 TO UP-GRADE EQUIPMENT (REPLACE SWITCH AND ARRESTER) | None | None | 17 | 72 | 20 | Central | UN05
135839 | 2017-05-26 | Defective Equipment | Imminent Failure | Transformers TE156, TE174 and TE175 on Woodridge were isolated for replacement due to oil leaks. 90 customers affected. Bayshore (49F1) | U/G Transformer | Padmount (1ph) | 55 | 240 | 220 | South | 49F1
135839 | 2017-05-26 | Defective Equipment | Imminent Failure | Transformers TE156, TE174 and TE175 on Woodridge were isolated for replacement due to oil leaks. 90 customers affected. Bayshore (49F1) | U/G Transformer | Padmount (1ph) | 90 | 3 | 4 | South | 49F1
135841 | 2017-05-26 | Scheduled Outage | Maintenance | Glen Carswell and crew to have transformer X30628 open to replace the transformer. Customers notified. | None | None | 9 | 95 | 14 | Central | SK10
135842 | 2017-05-26 | Adverse Environment | Fire | The 84F5 and 84F6 CB were forced open due to pole fire at request of crew due to safety hazard. | Pole | Insulation Failure (Pole Fire) | 39 | 284 | 185 | South | 84F6
135842 | 2017-05-26 | Adverse Environment | Fire | The 84F5 and 84F6 CB were forced open due to pole fire at request of crew due to safety hazard. | Pole | Insulation Failure (Pole Fire) | 261 | 66 | 287 | South | 84F6
135842 | 2017-05-26 | Adverse Environment | Fire | The 84F5 and 84F6 CB were forced open due to pole fire at request of crew due to safety hazard. | Pole | Insulation Failure (Pole Fire) | 480 | 203 | 1624 | South | 84F6
135842 | 2017-05-26 | Adverse Environment | Fire | The 84F5 and 84F6 CB were forced open due to pole fire at request of crew due to safety hazard. | Pole | Insulation Failure (Pole Fire) | 1102 | 202 | 3710 | South | 84F5
135843 | 2017-05-26 | Scheduled Outage | Construction | Bill Armstrong and crew to have transformer X30880 open to reinstall triplex to 219 Goulburn Ave. Customers not notified due to time of night. | None | None | 14 | 101 | 24 | Central | UN04
135847 | 2017-05-27 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact in overhead line feeding transformer X24678 | None | None | 3 | 154 | 8 | East | LMBF5
135851 | 2017-05-28 | Scheduled Outage | Maintenance | Hydro Ottawa 24/7 line crew had to open X32927 to change a defective triplex service. | None | O/H Conductor | 10 | 69 | 12 | Central | TD07
135852 | 2017-05-28 | Unknown/Other | Unknown | Transformer #X35108 opened up, crew could not find cause | O/H Switchgear | Fused Cutout | 12 | 99 | 20 | Central | UV03
135853 | 2017-05-28 | Tree Contacts | Tree Growth/ Untrimmed Tree | tree and vine contact at transformer and primary lateral fuse interrrupted 47 customers on the Russell TB14 | None | None | 47 | 93 | 73 | East | TB14
135854 | 2017-05-29 | Foreign Interference | Wildlife (Bird/Animal) | Switch 243R at 1176 Old Carp Rd opened due to squirrel contact. | O/H Switchgear | Fused Cutout | 14 | 76 | 18 | West | 624F6
135855 | 2017-05-29 | Scheduled Outage | Vegetation Management | Transformer outage at X33660 due to vegetation. Crews removed vines and closed transformer. | None | O/H Transformer (1ph) | 7 | 124 | 14 | Central | TW22
135856 | 2017-05-29 | Foreign Interference | Vehicle | Badger truck boom pulled down Bell messenger and broke the hydro pole in half on Manotick Island (LIMEBANK LMBF5) | Pole | Pole | 8 | 335 | 45 | East | LMBF5
135856 | 2017-05-29 | Foreign Interference | Vehicle | Badger truck boom pulled down Bell messenger and broke the hydro pole in half on Manotick Island (LIMEBANK LMBF5) | Pole | Pole | 89 | 51 | 76 | East | LMBF5
135856 | 2017-05-29 | Foreign Interference | Vehicle | Badger truck boom pulled down Bell messenger and broke the hydro pole in half on Manotick Island (LIMEBANK LMBF5) | Pole | Pole | 111 | 92 | 170 | East | LMBF5
135857 | 2017-05-29 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X27348 open due to squirrel contact. Crews refused. | O/H Transformer | O/H Transformer (1ph) | 11 | 151 | 28 | East | TB06
135858 | 2017-05-29 | Tree Contacts | Broken Branch | Tree on the line. Crew cleared tree and refused the transformer. | O/H Transformer | O/H Transformer (1ph) | 2 | 92 | 3 | West | 624F6
135859 | 2017-05-29 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #65C1B-0122 opened up due to vines on primary lead | O/H Switchgear | Fused Cutout | 13 | 215 | 47 | East | UT02
135860 | 2017-05-29 | Scheduled Outage | Maintenance | Service repair to X44467 by 24/7 interrupting 12 customers on the Startop 6F4 | None | None | 12 | 35 | 7 | East | 6F4
135861 | 2017-05-29 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33394 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 9 | 205 | 31 | Central | TD05
135862 | 2017-05-29 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X21685 | O/H Transformer | O/H Transformer (1ph) | 6 | 82 | 8 | East | TB14
135865 | 2017-05-30 | Scheduled Outage | Construction | Rick Barnett and crew to have transformer X27361 open to perform a service upgrade. Customers notified. | None | None | 13 | 158 | 34 | East | UQ07
135867 | 2017-05-30 | Scheduled Outage | Maintenance | transformer TP2620 at 53 Westpark was isolated to repair sagging fibre board, and transformers TP2619, TP2621, TP2622, and TP2623 were interrupted due to live front transformers. 43 customers were affected. Blackburn. (BLKF4) | None | None | 43 | 125 | 90 | East | BLKF4
135868 | 2017-05-30 | Scheduled Outage | Vegetation Management | At 8:32am crews isolated TD01 from S12446 to EOL for tree trimming. 14 customers affected. Lincoln Heights (TD01) | None | None | 14 | 80 | 19 | Central | TD01
135869 | 2017-05-30 | Defective Equipment | Electrical Failure | At 18:17 SCADA indicates the UQ08 breaker tripped open. Crew found blown pothead at riser S19309, 250 Smyth Rd. 155 customers affected. Queens (UQ08) | U/G Cable Attachement | Pothead | 153 | 18 | 46 | East | UQ08
135869 | 2017-05-30 | Defective Equipment | Electrical Failure | At 18:17 SCADA indicates the UQ08 breaker tripped open. Crew found blown pothead at riser S19309, 250 Smyth Rd. 155 customers affected. Queens (UQ08) | U/G Cable Attachement | Pothead | 155 | 107 | 276 | East | UQ08
135870 | 2017-05-30 | Defective Equipment | Electrical Failure | Defective transformer at VT415at 245 Rideau caused a fuse and the R1-F to open. 1 customer affected. King Edward (409) | Vault Equipment | Transformer | 1 | 636 | 11 | Central | 409
135871 | 2017-05-31 | Defective Equipment | Mechanical Failure | Fuse at transformer X24785 at 18 Kaymar opened due to a defective cut out. 10 customers affected. Moulton (8F1) | O/H Switchgear | Fused Cutout | 10 | 93 | 16 | East | 8F1
135872 | 2017-05-31 | Scheduled Outage | Construction | overhead section of TB15 circuit on tweed was isolated to allow crews to install new poles. 20 customers were affected. Russell. (TB15) | None | None | 20 | 420 | 140 | East | TB15
135873 | 2017-05-31 | Adverse Weather | Extreme Wind | The UZ06 circuit trip do to high winds which caused the conductor to wrap together in two separate location affectting 654 customers | O/H Conductor | O/H Conductor | 654 | 69 | 752 | East | UZ06
135874 | 2017-05-31 | Scheduled Outage | Maintenance | Transformer TP5954 at 17 Berkshire was isolated to allow the crew make secondary repairs, 19 customers wer affect on the 145F1 | None | Kiosk (1ph) | 19 | 292 | 92 | South | 145F1
135878 | 2017-06-01 | Scheduled Outage | Construction | Patrick Brisson and crew to have transformer X30435 open to rearrange equipment. Customers notified. | None | None | 10 | 113 | 19 | Central | SB11
135879 | 2017-06-01 | Scheduled Outage | Construction | Rick Barnett and crew to have transformer X24141 open to perform a service upgrade. Customers Notified. | None | None | 14 | 114 | 27 | East | 8F1
135881 | 2017-06-01 | Scheduled Outage | Vegetation Management | planned outage for tree trimming | None | None | 75 | 315 | 394 | South | 200F1
135882 | 2017-06-01 | Defective Equipment | Imminent Failure | Transformer TE1150 at 66 Collonade was isolated to allow crew to replace leaking transformer. Borden Farms (BDFF3) | U/G Transformer | Padmount (3ph) | 9 | 124 | 19 | South | 130F3
135883 | 2017-06-02 | Defective Equipment | Defective Equipment/ Material | Transformer TE0013 secondary was isolated to allow crew to replace pedastal. 19 customers were affected. (160F1) | Secondary \ Service | Secondary Pedestal | 19 | 216 | 68 | South | 160F1
135884 | 2017-06-02 | Scheduled Outage | Construction | planned outage to re-arrange the conductors on the pole. | None | None | 18 | 146 | 44 | East | 8F1
135885 | 2017-06-02 | Foreign Interference | Wildlife (Bird/Animal) | 713 customers were interrupted momentarily when the 72F7 auto reclosed and 9 customers affected for 113 mins due to squirrel contact at transformer NP002983 located at 18 GERVIN ST . Merivale (72F7) | Station Equipment | Relay | 9 | 113 | 17 | South | 72F7
135886 | 2017-06-03 | Scheduled Outage | Maintenance | Transformer 1526 at 310 Legget isolated for elbow and insert change. 2 customers affected. Kanata (624F5) | U/G Cable Attachement | Elbow \ Insert | 2 | 165 | 6 | West | 624F5
135887 | 2017-06-03 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X31773 | O/H Transformer | O/H Transformer (1ph) | 8 | 50 | 7 | Central | TW22
135889 | 2017-06-03 | Scheduled Outage | Construction | Overhead circuit from S25760 to EOL was isolated to reloacte a transformer and remove a span of overhead conductor. 47 customers affected. Russell (TB15) | None | O/H Conductor | 47 | 113 | 89 | East | TB15
135890 | 2017-06-03 | Foreign Interference | Wildlife (Bird/Animal) | An animal made contact with transformer X27518 at 1509 Grace St affecting 8 customers on the TB2JP circuit | O/H Transformer | O/H Transformer (1ph) | 8 | 71 | 9 | East | TB2JP
135893 | 2017-06-05 | Scheduled Outage | Construction | TP11439 and 4573 at 110 McCurdy isolated to remove 4573 from service. 1 customer affected. Bridlewood (BRDF4) | None | None | 1 | 337 | 6 | West | BRDF4
135895 | 2017-06-05 | Scheduled Outage | Vegetation Management | A section of overhead line from S12835 was isolated to trim trees at the rear of 902 Charleswood. 52 customers affected. Langs AP06. | None | None | 52 | 115 | 100 | East | AP06
135897 | 2017-06-05 | Scheduled Outage | Construction | VT838 at 221 Wiggins to be de-commisioned & replaced by new TV11696. Customer will be on generator until Friday when new service is energized. 171 cutomers affected, Riverdale TR1UN. | None | None | 171 | 383 | 1092 | Central | TR1UN
135898 | 2017-06-06 | Defective Equipment | Electrical Failure | Defective cable fault between transformers TE2011W and TP7056 caused the SC5398-CB3 to trip open. Billberry (77M1) | U/G Cable | XLPE | 337 | 131 | 736 | East | 77M1
135899 | 2017-06-06 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27189 opened up due to squirrel contact | None | None | 6 | 101 | 10 | East | TB06
135900 | 2017-06-06 | Defective Equipment | Electrical Failure | X24564 WHICH WAS DEFECTIVE // G677W OPENED UP ,, CREW CLOSED G677 POWER RESTORED TRANS TO BE REPLACED | O/H Transformer | O/H Transformer (1ph) | 67 | 13 | 15 | East | LMBF5
135901 | 2017-06-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer X18899 opened up due to tree contact | None | None | 1 | 111 | 2 | East | BLKF5
135902 | 2017-06-06 | Defective Equipment | Electrical Failure | Transformer was defective. Shaun Ryan and crew to replace transformer X24564. | O/H Transformer | O/H Transformer (1ph) | 7 | 309 | 36 | East | LMBF5
135904 | 2017-06-06 | Unknown/Other | Unknown | A transformer fused switch at 1476 Farnsworth opened, no cause was found, affecting 10 customers. Playfair AJ03 | Unknown \ Other | Unknown \ Other | 10 | 103 | 17 | East | AJ03
135905 | 2017-06-07 | Defective Equipment | Imminent Failure | TP7983 replaced due to leaking oil, affecting 10 customers. Cyrville MTS (CYRF3). | U/G Transformer | Padmount (3ph) | 10 | 487 | 81 | East | CYRF3
135908 | 2017-06-07 | Scheduled Outage | Construction | Transformer #X36478 isolated by crew for a service removal for a demolition | None | None | 8 | 15 | 2 | South | 72F4
135909 | 2017-06-07 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at transformer X49890 caused S28921 to open. 24 customers affected. Woodroffe TW18. | None | None | 14 | 27 | 6 | Central | TW18
135909 | 2017-06-07 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at transformer X49890 caused S28921 to open. 24 customers affected. Woodroffe TW18. | None | None | 24 | 145 | 58 | Central | TW18
135910 | 2017-06-07 | Defective Equipment | Mechanical Failure | Defective transformer X35108 at 2355 Riley was replaced by on - call crew. 11 customers affected. Edwin UV03. | O/H Transformer | O/H Transformer (1ph) | 11 | 550 | 101 | Central | UV03
135911 | 2017-06-08 | Unknown/Other | Unknown | Recloser RX2063 auto reclosed causing TB13 breaker to trip. Circuit to be patrolled in daylight. Field Operators patrolled the circuit June 8th am and found nothing. | Unknown \ Other | Unknown \ Other | 2241 | 11 | 411 | East | TB2JP
135912 | 2017-06-08 | Scheduled Outage | Maintenance | due to live front transformers crew opened switch to enable isolation of cable section. 204 customers were affected. Epworth (EPWF6) | None | None | 204 | 4 | 14 | South | EPWF6
135914 | 2017-06-08 | Scheduled Outage | Construction | At 8:55am isolated a section of TB15 to replace poles affecting 38 customers. Russell (TB15) | None | None | 38 | 371 | 235 | East | TB15
135916 | 2017-06-08 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30075 FOR A SERVICE UP-GRADE | None | None | 5 | 45 | 4 | Central | SB11
135917 | 2017-05-23 | Foreign Interference | Vehicle | MVA - truck hit SL wires, TH06 conductor broken & down @ Scott & Parkdale | None | None | 679 | 81 | 917 | Central | TH06
135917 | 2017-05-23 | Foreign Interference | Vehicle | MVA - truck hit SL wires, TH06 conductor broken & down @ Scott & Parkdale | None | None | 1502 | 136 | 3405 | Central | TH06
135918 | 2017-05-23 | Human Element | Protection Setting | MVA @ Scott & Parkdale, TH06 circuit down. TH06 relay malfunction caused multiple reclose operations. Hydro One transformer protection operated to trip both Hinchey transformers. | None | None | 1026 | 9 | 154 | Central | F10MV (Hinchey - T4)
135918 | 2017-05-23 | Human Element | Protection Setting | MVA @ Scott & Parkdale, TH06 circuit down. TH06 relay malfunction caused multiple reclose operations. Hydro One transformer protection operated to trip both Hinchey transformers. | None | None | 1143 | 4 | 76 | Central | F10MV (Hinchey - T4)
135918 | 2017-05-23 | Human Element | Protection Setting | MVA @ Scott & Parkdale, TH06 circuit down. TH06 relay malfunction caused multiple reclose operations. Hydro One transformer protection operated to trip both Hinchey transformers. | None | None | 1180 | 5 | 98 | Central | F10MV (Hinchey - T4)
135918 | 2017-05-23 | Human Element | Protection Setting | MVA @ Scott & Parkdale, TH06 circuit down. TH06 relay malfunction caused multiple reclose operations. Hydro One transformer protection operated to trip both Hinchey transformers. | None | None | 2330 | 14 | 544 | Central | F10MV (Hinchey - T4)
135918 | 2017-05-23 | Human Element | Protection Setting | MVA @ Scott & Parkdale, TH06 circuit down. TH06 relay malfunction caused multiple reclose operations. Hydro One transformer protection operated to trip both Hinchey transformers. | None | None | 2433 | 5 | 203 | Central | V12M (Hinchey - T3)
135918 | 2017-05-23 | Human Element | Protection Setting | MVA @ Scott & Parkdale, TH06 circuit down. TH06 relay malfunction caused multiple reclose operations. Hydro One transformer protection operated to trip both Hinchey transformers. | None | None | 3844 | 27 | 1730 | Central | V12M (Hinchey - T3)
135918 | 2017-05-23 | Human Element | Protection Setting | MVA @ Scott & Parkdale, TH06 circuit down. TH06 relay malfunction caused multiple reclose operations. Hydro One transformer protection operated to trip both Hinchey transformers. | None | None | 4632 | 72 | 5558 | Central | F10MV (Hinchey - T4)
135918 | 2017-05-23 | Human Element | Protection Setting | MVA @ Scott & Parkdale, TH06 circuit down. TH06 relay malfunction caused multiple reclose operations. Hydro One transformer protection operated to trip both Hinchey transformers. | None | None | 4633 | 104 | 8031 | Central | V12M (Hinchey - T3)
135919 | 2017-06-08 | Defective Equipment | Electrical Failure | A cable fault on the 77M2 B phase in the Laurelwood area causing an outage to 56 customers | U/G Cable | XLPE | 56 | 129 | 120 | East | 77M2
135922 | 2017-06-09 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at transformer X48304 at 1204 Amesbrooke caused fuse to open.18 customer affected. Woodroffe TW12. | None | None | 18 | 60 | 18 | Central | TW12
135923 | 2017-06-09 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35318 opened up due to squirrel contact | None | None | 1 | 139 | 2 | Central | TD01
135924 | 2017-06-10 | Defective Equipment | Mechanical Failure | Broken transformer cut out. | O/H Switchgear | Fused Cutout | 0 | 311 | 0 | South | 130F2
135924 | 2017-06-10 | Defective Equipment | Mechanical Failure | Broken transformer cut out. | O/H Switchgear | Fused Cutout | 1 | 116 | 2 | South | 130F2
135926 | 2017-06-10 | Defective Equipment | Imminent Failure | Transformer TP7984 at 1856 Thornecrest was isolated to allow crew to replace leaking transforemr. 8 customers were affected. Billberry (77M2) | U/G Transformer | Padmount (3ph) | 8 | 80 | 11 | East | 77M2
135927 | 2017-06-10 | Unknown/Other | Unknown | Unexpected transformer outage at X17648. Shaun Cunningham and Matt Stuytt refused and restored. | Unknown \ Other | Unknown \ Other | 17 | 98 | 28 | East | 4801F8
135931 | 2017-06-11 | Scheduled Outage | Construction | A vault at 85 Plymouth was isolated to install a new feed to the vault affecting 1 customer. Bronson SB15 | None | None | 1 | 202 | 3 | Central | SB15
135932 | 2017-06-11 | Foreign Interference | Foreign Objects | S29284 RWB to EOL was isolated due to down primary at 69 Springhurst caused by construcion trap that blew onto O/H and took one phase down and dammaged two other phases affecting 16 customers. Riverdale (SR03) | None | None | 16 | 202 | 54 | Central | SR03
135933 | 2017-06-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | trees in the wires | None | None | 9 | 284 | 43 | South | EPWF3
135933 | 2017-06-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | trees in the wires | None | None | 34 | 192 | 109 | South | EPWF3
135934 | 2017-06-11 | Defective Equipment | Electrical Failure | Defective transformer. | U/G Transformer | Padmount (1ph) | 12 | 358 | 72 | West | TFXF2
135936 | 2017-06-11 | Human Element | Incorrect Records/ labelling | Incorrect nomenclature. | None | None | 10 | 109 | 18 | West | TFXF2
135937 | 2017-06-11 | Scheduled Outage | Construction | Relocate plant overhead transformer. | None | None | 8 | 945 | 126 | Central | SA22
135938 | 2017-06-11 | Defective Equipment | Electrical Failure | defective transformer TE645 repalced, affecting 16 customers. Beachon Hill DS BCHF7 | U/G Transformer | Padmount (1ph) | 16 | 953 | 254 | East | BCHF5
135939 | 2017-06-12 | Defective Equipment | Defective Equipment/ Material | Defective transformer | U/G Transformer | Padmount (1ph) | 8 | 226 | 30 | Central | 307
135940 | 2017-06-12 | Scheduled Outage | Vegetation Management | S21643 to Eol was isolated to allow tree trimming crew to trim trees at rear of 815 Edgeworth and 2361 Whitehaven. Lincoln Heights (TD07) | None | None | 14 | 180 | 42 | Central | TD07
135941 | 2017-06-12 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X31658 opened up due to animal contact | O/H Switchgear | Fused Cutout | 13 | 179 | 39 | Central | SR08
135942 | 2017-06-12 | Scheduled Outage | Construction | Dave Macdonald and crew to have transformer X35803 open to replace an existing overhead service. Customers notified. | None | None | 14 | 60 | 14 | South | 190F5
135943 | 2017-06-12 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact caused an in line fused switch to open on Hart affecting 4 customers. Bilberry Creek 77M5 | None | None | 4 | 346 | 23 | East | 77M5
135944 | 2017-06-12 | Defective Equipment | Mechanical Failure | A transfomer at 1021 Plante caught fire and had to be opened to allow for fire to be extiguished and transformer replaced affecting 10 customers. McCarthy AQ09 | U/G Transformer | Padmount (1ph) | 10 | 574 | 96 | East | AQ09
135945 | 2017-06-12 | Human Element | Switching Error | The Fallowfield station trip due to overloading | None | None | 15398 | 53 | 13602 | South | S7M (Fallowfield - T1/T2)
135946 | 2017-06-12 | Defective Equipment | Electrical Failure | DEFECTIVE TRANS | U/G Transformer | Kiosk (1ph) | 10 | 559 | 93 | East | AQ09
135947 | 2017-06-13 | Foreign Interference | Wildlife (Bird/Animal) | A crow made contact to switch S7055 @ 3050 WOODROFFE AVE causing the RX2056 to auto reclosed and also it blew the fuse S7055 causing and outage to 164 on the LMBF7 ciruit | None | None | 164 | 101 | 276 | East | LMBF7
135948 | 2017-06-13 | Scheduled Outage | Vegetation Management | To allow Davey Tree to clear overgrown tree limbs from the O/H circuit | None | None | 33 | 233 | 128 | West | 43F2
135949 | 2017-06-13 | Scheduled Outage | Construction | Crew replacing broken crossarm affecting 6 customers on the 145F3 | None | None | 6 | 169 | 17 | South | 145F3
135950 | 2017-06-13 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35983 FOR A SERVICE UP-GRADE | None | None | 7 | 70 | 8 | South | EPWF1
135952 | 2017-06-13 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X11413 FOR TREE CONTRACTOR | None | None | 6 | 133 | 13 | West | 43F3
135953 | 2017-06-13 | Scheduled Outage | Construction | To replace P237 @ 400 Catherine St. | None | None | 1 | 139 | 2 | Central | UF08
135954 | 2017-06-13 | Tree Contacts | Falling Tree | A tree on a customer owned O/H line caused S19826 to open. | None | None | 6 | 580 | 58 | West | 624F6
135955 | 2017-06-14 | Scheduled Outage | Construction | 600 volt upgrade. | None | O/H Transformer (3ph) | 6 | 69 | 7 | Central | SM03
135956 | 2017-06-14 | Scheduled Outage | Vegetation Management | 81 customers affected with S679 opened to End Of Line for forestry work on the Stafford Road 200F1 | None | None | 81 | 351 | 474 | South | 200F1
135957 | 2017-06-14 | Defective Equipment | Electrical Failure | TE2637 isolation for defective transformer change on the Uplands Q4801F8 affecting 8 customers | U/G Transformer | Padmount (1ph) | 8 | 123 | 16 | East | 4801F8
135958 | 2017-06-14 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to replace poles | None | Pole | 38 | 443 | 281 | East | TB15
135959 | 2017-06-14 | Defective Equipment | Imminent Failure | To allow Hydro Ottawa crews to change leaking transformer TP6614 | U/G Transformer | Padmount (1ph) | 1 | 56 | 1 | South | 190F5
135960 | 2017-06-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32181 opened up due to squirrel interference | O/H Switchgear | Fused Cutout | 7 | 58 | 7 | Central | TD01
135963 | 2017-06-14 | Defective Equipment | Mechanical Failure | 77M6 cable fault between TE912 & TE913 | U/G Cable | XLPE | 10 | 27 | 4 | East | 77M6
135963 | 2017-06-14 | Defective Equipment | Mechanical Failure | 77M6 cable fault between TE912 & TE913 | U/G Cable | XLPE | 80 | 54 | 72 | East | 77M6
135963 | 2017-06-14 | Defective Equipment | Mechanical Failure | 77M6 cable fault between TE912 & TE913 | U/G Cable | XLPE | 110 | 29 | 53 | East | 77M6
135963 | 2017-06-14 | Defective Equipment | Mechanical Failure | 77M6 cable fault between TE912 & TE913 | U/G Cable | XLPE | 129 | 30 | 64 | East | 77M6
135963 | 2017-06-14 | Defective Equipment | Mechanical Failure | 77M6 cable fault between TE912 & TE913 | U/G Cable | XLPE | 158 | 62 | 163 | East | 77M6
135964 | 2017-06-14 | Scheduled Outage | Forced Switching | VT325 interupted to allow switching on defective gear. | Vault Equipment | Switch | 1 | 12 | 0 | Central | TL3TS
135965 | 2017-06-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer fuse at X33224 blew due to squirel contact. | O/H Switchgear | Fused Cutout | 17 | 58 | 16 | South | 190F2
135966 | 2017-06-15 | Scheduled Outage | Vegetation Management | Tree trimming | None | None | 77 | 345 | 443 | South | 190F5
135968 | 2017-06-15 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X31478 opened up due to squirrel interference | O/H Switchgear | Fused Cutout | 18 | 125 | 38 | Central | TH11-NIU
135969 | 2017-06-15 | Scheduled Outage | Construction | Install insulators and re-sag conductors. | None | None | 333 | 156 | 866 | East | UZ03
135969 | 2017-06-15 | Scheduled Outage | Construction | Install insulators and re-sag conductors. | None | None | 654 | 161 | 1755 | East | UZ06
135970 | 2017-06-15 | Defective Equipment | Imminent Failure | TE103 was repalced due to leaking oil, affecting 6 customers. QCH DS (160F4) | U/G Transformer | Padmount (1ph) | 6 | 512 | 51 | South | 160F4
135972 | 2017-06-15 | Unknown/Other | Unknown | REFUSED SITCH S14656 FEEDING TRANSFORMER X36340 | O/H Switchgear | Fused Cutout | 4 | 51 | 3 | West | JKGF5
135973 | 2017-06-15 | Unknown/Other | Unknown | The 8LKF4 CB A/A/R, cause is currently under investigation. Area crew to patrol during day time. Circuit was patrolled on June 19th by area crew. No cause was found. Crews installed 3 sets of FCIs incase of further outages. | None | None | 801 | 27 | 360 | East | BLKF4
135974 | 2017-06-16 | Scheduled Outage | Maintenance | replaced defective transformer TE470 and riser switches G273, affecting 1 customer. Cyrville (CYRF1) | None | Kiosk (3ph) | 1 | 150 | 2 | East | CYRF1
135975 | 2017-06-16 | Foreign Interference | Wildlife (Bird/Animal) | Not yet known. | Unknown \ Other | Unknown \ Other | 2960 | 12 | 592 | South | 22M28
135977 | 2017-06-16 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X33030 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 6 | 103 | 10 | South | 180F4
135978 | 2017-06-16 | Loss Of Supply | Transmission Inadvertent | H1 loss of 115KV supply to Orleans TS affected 1451 customers. (325M8). Hydro One reports foreign object in overhead wires on 115kV. Did not elaborate. | None | None | 474 | 25 | 198 | East | 325M8
135978 | 2017-06-16 | Loss Of Supply | Transmission Inadvertent | H1 loss of 115KV supply to Orleans TS affected 1451 customers. (325M8). Hydro One reports foreign object in overhead wires on 115kV. Did not elaborate. | None | None | 1451 | 12 | 290 | East | 325M8
135979 | 2017-06-16 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact causing transformer fuse to blow at X46293 | O/H Transformer | O/H Transformer (1ph) | 37 | 75 | 46 | Central | TW05
135979 | 2017-06-16 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact causing transformer fuse to blow at X46293 | O/H Transformer | O/H Transformer (1ph) | 412 | 5 | 34 | Central | TW05
135982 | 2017-06-17 | Scheduled Outage | Construction | crew isolated Hazeldean Mall to replace pole. 1 customer was affected. South March (A9M1) | None | None | 1 | 249 | 4 | West | A9M1
135983 | 2017-06-18 | Defective Equipment | Defective Equipment/ Material | Conflicting reports from Ottawa Fire and Police to the cause of the outage. 24/7 reports Blown arresters found on overhead at Lewis and Elgin st. | Pole Attachement | Arrester | 246 | 89 | 365 | Central | UX04
135983 | 2017-06-18 | Defective Equipment | Defective Equipment/ Material | Conflicting reports from Ottawa Fire and Police to the cause of the outage. 24/7 reports Blown arresters found on overhead at Lewis and Elgin st. | Pole Attachement | Arrester | 714 | 89 | 1059 | Central | UX06
135984 | 2017-06-18 | Foreign Interference | Wildlife (Bird/Animal) | A squirrel made contact with an O/H transformer X15173 @ 4066 Ramsayville Rd which caused the G902R to open affecting 52 cuustomers on the 249F2 circuit | O/H Switchgear | Fused Cutout | 52 | 81 | 70 | East | 249F2
135985 | 2017-06-18 | Foreign Interference | Wildlife (Bird/Animal) | At 8:06am SCADA indicated that the TB01 breaker opened. Crews found a cat as the cause of the outage Russel (TB3LE) | None | None | 1261 | 20 | 420 | East | TB3LE
135986 | 2017-06-18 | Adverse Weather | Extreme Wind | circuit was patrolled and no cause was found. There was storm activity in the area at the time the circuit tripped. Enviroment canada had posted tornado warnings. | None | None | 801 | 85 | 1135 | East | BLKF4
135987 | 2017-06-18 | Adverse Weather | Extreme Wind | At 2:37pm SCADA indicated the UZ06 breaker opened due to high winds. 654 customers affected. Walkley (UZ06) | O/H Conductor | O/H Conductor | 654 | 69 | 752 | East | UZ06
135988 | 2017-06-18 | Tree Contacts | Broken Branch | The 200 F1 auto reclosed in the Moodie, Corkstown Rd area affecting 643 customers, extreme wind caused a branch at 3728 CARLING AVE to fall on the primary which caused the R phase to fall to the ground, the other two phase are about to fall, isolated the | O/H Conductor | O/H Conductor | 5 | 158 | 13 | South | 200F1
135988 | 2017-06-18 | Tree Contacts | Broken Branch | The 200 F1 auto reclosed in the Moodie, Corkstown Rd area affecting 643 customers, extreme wind caused a branch at 3728 CARLING AVE to fall on the primary which caused the R phase to fall to the ground, the other two phase are about to fall, isolated the | O/H Conductor | O/H Conductor | 30 | 211 | 106 | South | 200F1
135989 | 2017-06-18 | Adverse Weather | Extreme Wind | At 4:14pm UZ06 breaker tripped again due to high winds. System Office closed the circuit back in via SCADA to restore 654 customers. Walkley (UZ06) | O/H Conductor | O/H Conductor | 654 | 5 | 54 | East | UZ06
135990 | 2017-06-18 | Adverse Weather | Extreme Wind | At 4:33pm the UZ06 tripped for a third time due to wind. System Office closed the breaker via SCADA to restore all 654 customers. Walkley (UZ06) | O/H Conductor | O/H Conductor | 654 | 5 | 54 | East | UZ06
135992 | 2017-06-18 | Defective Equipment | Mechanical Failure | At 5:31pm SCADA indicated and auto-reclose on the 145F3 breaker due to a pole fire. At 6:10pm the circuit was dumped for safety affecting 365 customers. Jockvale (145F3) Cause of fire: Insulator broke and conductor fell on bracket energizing it and causin | Pole | Insulation Failure (Pole Fire) | 0 | 39 | 0 | South | 145F3
135992 | 2017-06-18 | Defective Equipment | Mechanical Failure | At 5:31pm SCADA indicated and auto-reclose on the 145F3 breaker due to a pole fire. At 6:10pm the circuit was dumped for safety affecting 365 customers. Jockvale (145F3) Cause of fire: Insulator broke and conductor fell on bracket energizing it and causin | Pole | Insulation Failure (Pole Fire) | 9 | 173 | 26 | South | 145F3
135992 | 2017-06-18 | Defective Equipment | Mechanical Failure | At 5:31pm SCADA indicated and auto-reclose on the 145F3 breaker due to a pole fire. At 6:10pm the circuit was dumped for safety affecting 365 customers. Jockvale (145F3) Cause of fire: Insulator broke and conductor fell on bracket energizing it and causin | Pole | Insulation Failure (Pole Fire) | 365 | 68 | 414 | South | 145F3
135993 | 2017-06-18 | Adverse Weather | Extreme Wind | At 6:15pm SCADA indicated the UZ06 breaker tripped open for a fourth time today. 654 customers affected. Walkley (UZ06) | O/H Conductor | O/H Conductor | 654 | 5 | 54 | East | UZ06
135994 | 2017-06-19 | Tree Contacts | Falling Tree | To allow crews to remove tree off secondary services. | O/H Conductor | O/H Conductor | 12 | 35 | 7 | Central | TD06
135995 | 2017-06-19 | Defective Equipment | Defective Equipment/ Material | Defective transformer. | O/H Transformer | O/H Transformer (1ph) | 10 | 440 | 73 | Central | SM16
135996 | 2017-06-19 | Defective Equipment | Imminent Failure | TE2329 at 299 Greenbank was isolated by the crew to allow the crew to replace leaking transformer, 1 customer was affected | U/G Transformer | Kiosk (3ph) | 1 | 102 | 2 | South | 84F2
135997 | 2017-06-19 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X35287 (BIRD CONTACT) | O/H Transformer | O/H Transformer (1ph) | 7 | 66 | 8 | West | TFXF4
135998 | 2017-06-19 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X26869 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 12 | 115 | 23 | East | TB15
135999 | 2017-06-19 | Scheduled Outage | Maintenance | The O/H on Thomas Dolan was isolated to allow the crew replace a pole, 3 customers were affected on the MWDF3 | None | Pole | 3 | 253 | 13 | West | MWDF3
136000 | 2017-06-19 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X33354 TO REPAIR OPEN WIRE SECONDARY BUSS | None | None | 2 | 63 | 2 | South | EPWF4
136001 | 2017-06-19 | Scheduled Outage | Vegetation Management | At 9:07am a section of TD12 from TEMP98 to end of line was isolated for tree trimming. 31 customers affected. Lincoln Heights (TD12) | None | None | 31 | 323 | 167 | Central | TD12
136002 | 2017-06-19 | Scheduled Outage | Construction | Transformer #X30099 isolated by crew to re-arrange plant | None | None | 4 | 319 | 21 | Central | SB03
136004 | 2017-06-20 | Tree Contacts | Tree Growth/ Untrimmed Tree | Possible tree contacts on Bearbrook rd & in wooded area caused Blackburn BLKF4 to trip. New switches also cut in on overhead line to aid in future sectionalizing. | None | None | 2 | 626 | 21 | East | BLKF4
136004 | 2017-06-20 | Tree Contacts | Tree Growth/ Untrimmed Tree | Possible tree contacts on Bearbrook rd & in wooded area caused Blackburn BLKF4 to trip. New switches also cut in on overhead line to aid in future sectionalizing. | None | None | 166 | 62 | 172 | East | BLKF4
136004 | 2017-06-20 | Tree Contacts | Tree Growth/ Untrimmed Tree | Possible tree contacts on Bearbrook rd & in wooded area caused Blackburn BLKF4 to trip. New switches also cut in on overhead line to aid in future sectionalizing. | None | None | 801 | 70 | 934 | East | BLKF4
136005 | 2017-06-20 | Defective Equipment | Imminent Failure | TP2897 at 261 Flodden was isolated for replacement due to oil leak. 8 customers affected. Limebank (7F1) | U/G Transformer | Padmount (1ph) | 8 | 134 | 18 | East | 7F1
136006 | 2017-06-20 | Scheduled Outage | Maintenance | Removing esisting lead cable and replacing with 1/0 CU XLPE, reframe riser pole and install new switch. | None | XLPE | 2 | 301 | 10 | Central | SR01
136007 | 2017-06-20 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE AT SWITCH S22794 FEEDING TWO OVERHEAD TRANSFORMERS ON ELM ST | O/H Switchgear | Fused Cutout | 28 | 129 | 60 | Central | TH15
136008 | 2017-06-20 | Scheduled Outage | Maintenance | TP5029 at 609 Rosehill isolated for soil remediation. 12 customers affected. Terry Fox TFXF2. | None | None | 12 | 468 | 94 | West | TFXF2
136009 | 2017-06-20 | Scheduled Outage | Vegetation Management | A section of overhead line from G465B was isolated for tree trimming at 2 Meadowlark. 8 customers affected. Moulton 8F1. | None | None | 8 | 289 | 39 | East | 8F1
136010 | 2017-06-20 | Scheduled Outage | Construction | Evan Cowell and crew to have transformer X33626 open to install a new service. Customers notified. | None | None | 14 | 90 | 21 | Central | SM16
136012 | 2017-06-20 | Scheduled Outage | Maintenance | Oakley McCoy and 24/7 to have transformer X34201 open to fix a broken Cut-out switch. Customers notified. | None | None | 8 | 28 | 4 | Central | UL14
136014 | 2017-06-20 | Tree Contacts | Broken Branch | Tree contact took down secondary bus. | O/H Conductor | O/H Conductor | 16 | 73 | 19 | Central | TW17
136014 | 2017-06-20 | Tree Contacts | Broken Branch | Tree contact took down secondary bus. | O/H Conductor | O/H Conductor | 16 | 165 | 44 | Central | TW17
136014 | 2017-06-20 | Tree Contacts | Broken Branch | Tree contact took down secondary bus. | O/H Conductor | O/H Conductor | 127 | 150 | 318 | Central | TW17
136015 | 2017-06-21 | Scheduled Outage | Vegetation Management | Davey Tree trimming trees in the rear of 1437, 1445, 1457 on Edgecliffe. | None | None | 69 | 307 | 353 | Central | AD03
136018 | 2017-06-21 | Scheduled Outage | Maintenance | Evan Cowell and crew to have transformer X32672 open to drop a service. Customers notified. | None | None | 10 | 54 | 9 | Central | TW22
136019 | 2017-06-21 | Defective Equipment | Imminent Failure | TE2741 at 1999 Silver Pines was isolated to replace leaking transfomer. 14 customers affected. Cyrville CYRF3. | U/G Transformer | Padmount (1ph) | 14 | 547 | 128 | East | CYRF3
136020 | 2017-06-21 | Scheduled Outage | Construction | 49F1 overhead from X47200 to EOL at 3147 Carling isolated for pole change. 1 customer affected. Bayshore (49F1) | None | Pole | 1 | 624 | 10 | South | 49F1
136021 | 2017-06-21 | Scheduled Outage | Maintenance | Transformer #X32672 isolated by crew to reconnect service after tree trimming (replaced triplex) | None | None | 10 | 47 | 8 | Central | TW22
136022 | 2017-06-21 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27631 opened up due to squirrel contact | O/H Transformer | O/H Transformer (1ph) | 12 | 94 | 19 | Central | TH15
136023 | 2017-06-22 | Unknown/Other | Unknown | Unknown, no cause found | Unknown \ Other | Unknown \ Other | 4507 | 4 | 300 | West | JKGF4
136024 | 2017-06-22 | Defective Equipment | Imminent Failure | Transformer replace on the Kanata 624F5 affecting 1 customer for leaker changeout | U/G Transformer | Padmount (1ph) | 1 | 106 | 2 | West | 624F5
136025 | 2017-06-22 | Defective Equipment | Imminent Failure | Leaking transformer TE767 replacement on the Merivale 72F1 affecting 18 customers | U/G Transformer | Padmount (1ph) | 18 | 532 | 160 | South | 72F1
136026 | 2017-06-22 | Defective Equipment | Corrosion | To remove transformer and cleanup oil spill. | U/G Transformer | Kiosk (3ph) | 12 | 301 | 60 | Central | SK16
136027 | 2017-06-22 | Scheduled Outage | Maintenance | Asbestos removal from incoming cable | None | None | 65 | 325 | 352 | East | UT03
136028 | 2017-06-22 | Defective Equipment | Imminent Failure | Leaking transformer replacement on the 145F4 affecting 11 customers | U/G Transformer | Padmount (1ph) | 11 | 226 | 41 | South | 145F4
136029 | 2017-06-22 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32648 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 7 | 152 | 18 | Central | TD12
136030 | 2017-06-22 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32647 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 10 | 57 | 10 | Central | TD12
136031 | 2017-06-22 | Scheduled Outage | Vegetation Management | Tree Trimming on Cleadon affecting 47 customers on the Bayshore 49F6 | None | None | 47 | 322 | 252 | South | 49F6
136032 | 2017-06-22 | Scheduled Outage | Construction | Jeff Magee and crew to have transformers X24040 and X24041 open to transfer plant. Customers notified. | None | None | 18 | 295 | 88 | East | UT05
136033 | 2017-06-22 | Loss Of Supply | Third Party | To replace a defective transformer Customer is on generator | None | None | 1 | 9562 | 159 | West | 624F1
136034 | 2017-06-23 | Loss Of Supply | Third Party | At 00:12, the main breaker at 200 Rideau Terrace tripped, Schneider electric was called to check customers equipement, Schneider has just installed a new equipment in the vault and they suspect the issue was improper protection settings on their equipment | None | None | 1 | 356 | 6 | East | AC06
136035 | 2017-06-23 | Foreign Interference | Wildlife (Bird/Animal) | A crow was found a the base of the pole where X13949 is. This also caused G953 R phase to blow. | O/H Switchgear | Fused Cutout | 47 | 116 | 91 | East | LTM04
136037 | 2017-06-23 | Tree Contacts | Broken Branch | A branch that had fallen onto the neutral at 5845 Thunder Ridge Rd caused G308 B phase to open | O/H Switchgear | Fused Cutout | 65 | 123 | 133 | East | 249F2
136038 | 2017-06-23 | Scheduled Outage | Maintenance | Bill Armstong and crew to have transformer X07291 open to replaced broken cut out switch. Customers notified. | None | None | 4 | 29 | 2 | West | 624F6
136039 | 2017-06-23 | Adverse Environment | Contamination (Salt) | S29199 RWB was opened due to pole top fire at S20037. On call crew made temporary repairs. 21 customers affected. Carling TS (303) | None | Insulator | 21 | 241 | 84 | Central | 303
136041 | 2017-06-24 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X48723 opened up due to bird contact | O/H Switchgear | Fused Cutout | 15 | 127 | 32 | Central | TW18
136042 | 2017-06-24 | Scheduled Outage | Maintenance | TP1118 cable supply cut over from S27856 to new S11673 cable splice in MH#4755. | None | None | 1 | 368 | 6 | South | FAL03
136043 | 2017-06-24 | Defective Equipment | Defective Equipment/ Material | Secondary bus down. | O/H Conductor | O/H Conductor | 8 | 249 | 33 | East | UB03
136044 | 2017-06-24 | Tree Contacts | Tree Growth/ Untrimmed Tree | Vines in the cut out. | O/H Switchgear | Fused Cutout | 7 | 218 | 25 | East | CYRF3
136045 | 2017-06-24 | Scheduled Outage | Construction | Transformer at 164 Rachael was isolated to allow crew to re-install secondary service. 16 customers were affected. Riverdale (505) | None | None | 16 | 45 | 12 | Central | 505
136048 | 2017-06-24 | Unknown/Other | Unknown | Fuse at transformer X36346 opened, cause undetermined. 6 customers affected. Janet king JKGF5. | None | None | 6 | 80 | 8 | West | JKGF5
136050 | 2017-06-25 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X47850 opened up due to animal contact | O/H Switchgear | Fused Cutout | 6 | 69 | 7 | Central | TW18
136053 | 2017-06-25 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32418 opened up due to bird contact | O/H Switchgear | Fused Cutout | 6 | 70 | 7 | Central | TD01
136054 | 2017-06-25 | Lightning | Lightning | Transformer #X35202 opened up due to lightning strike | O/H Switchgear | Fused Cutout | 20 | 62 | 21 | Central | UC08
136055 | 2017-06-25 | Lightning | Lightning | Lightning Line patrolled and nothing found. | Station Equipment | Relay | 359 | 88 | 527 | South | 72F4
136056 | 2017-06-25 | Defective Equipment | Defective Equipment/ Material | Transformer #P108 opened up due to blown lightning arrestor | O/H Switchgear | Inline Switch | 7 | 90 | 10 | Central | SM12
136058 | 2017-06-25 | Tree Contacts | Broken Branch | Tree on overhead white phase. | None | None | 50 | 71 | 59 | East | TB06
136060 | 2017-06-25 | Lightning | Lightning | G59R opened during severe weather. Line patrolled & no cause found. G59R closed. 16 customers affected. Blackburn BLKF5. | None | None | 16 | 293 | 78 | East | BLKF5
136062 | 2017-06-25 | Tree Contacts | Broken Branch | Tree branch took down primary line at 6545 Fernbank during thunderstorm causing RX2013 to open. 118 customers affected. Terry Fox TFXF4. | O/H Conductor | O/H Conductor | 118 | 293 | 576 | West | TFXF4
136063 | 2017-06-25 | Defective Equipment | Defective Equipment/ Material | A suspected cable fault between G712W and TE210 on McLean caused a power outage to 3 transformers. | U/G Cable | XLPE | 22 | 387 | 142 | East | LMBF5
136064 | 2017-06-25 | Tree Contacts | Broken Branch | Tree contacts at rear of 139 Rachel caused S25781 to open. 15 customers affected. Russell TB06. | None | None | 15 | 120 | 30 | East | TB06
136065 | 2017-06-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contacts on customer line at 8707 Flewellyn caused fuse to open at X35735. 1 customer affected. Beckwith BECKF2. | None | None | 1 | 515 | 9 | West | BECKF2
136066 | 2017-06-25 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X23945 opened due to bird contact. | O/H Switchgear | Fused Cutout | 2 | 379 | 13 | East | 77M6
136067 | 2017-06-25 | Unknown/Other | Unknown | Transformer X33348 was blown. Cause unknown. Suspected Lightning. | O/H Transformer | O/H Transformer (1ph) | 1 | 145 | 2 | West | BECKF2
136068 | 2017-06-25 | Lightning | Lightning |  | O/H Transformer | O/H Transformer (1ph) | 20 | 567 | 189 | Central | TR09
136069 | 2017-06-26 | Foreign Interference | Wildlife (Bird/Animal) | TRANSFORMER X44691 OPENED DUE to ANIMAL CONTACT. | O/H Switchgear | Fused Cutout | 7 | 77 | 9 | Central | 505
136070 | 2017-06-26 | Scheduled Outage | Vegetation Management | Tree trimming | None | None | 32 | 155 | 83 | Central | AH13
136071 | 2017-06-26 | Scheduled Outage | Construction | Transformer #X28066 isolated by crew for a service upgrade | None | None | 8 | 65 | 9 | East | AF03
136072 | 2017-06-26 | Scheduled Outage | Construction | G909B to EOL isolated to allow crews to upgrade a sectio of overhead and install 2 new overhead transformers. South Gloucester (56F1) | None | None | 8 | 380 | 51 | East | 56F1
136073 | 2017-06-26 | Scheduled Outage | Construction | Re-frame pole. | None | None | 89 | 245 | 363 | East | UQ05
136075 | 2017-06-26 | Scheduled Outage | Vegetation Management | Transformer #X26245 isolated by crew for Forestry Dept to trim | None | None | 3 | 70 | 4 | Central | TH01
136076 | 2017-06-26 | Scheduled Outage | Construction | To relocate cables in manhole for future new transformer install | None | None | 3 | 349 | 17 | West | TFXF4
136077 | 2017-06-26 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X2014 opened up due to animal contact | O/H Switchgear | Fused Cutout | 2 | 113 | 4 | South | 130F3
136078 | 2017-06-26 | Scheduled Outage | Forced Switching | Operating restrictions on switch gear in Hydro vault. | Vault Equipment | Switch | 1 | 3 | 0 | Central | TL3TS
136079 | 2017-06-27 | Scheduled Outage | Maintenance | planned outage to allow crew to re-insulate primary and remove a quick sleeve. | None | None | 2 | 94 | 3 | South | 180F1
136080 | 2017-06-27 | Scheduled Outage | Vegetation Management | planned outage to allow crews to trim trees on Horner | None | None | 37 | 335 | 207 | South | 49F6
136081 | 2017-06-27 | Scheduled Outage | Maintenance | Bill Armstrong and crew to have transformer X16477 open to replace lightning arrestors and fused cut-outs. Customers notified. | None | None | 7 | 88 | 10 | East | 7F4
136082 | 2017-06-27 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One. Hydro One loss their Band Y bus at the St. Isidore station. Cause remains under investigation. | None | None | 1711 | 10 | 285 | East | 62M2 (Casselman MS)
136083 | 2017-06-27 | Unknown/Other | Unknown | The AP02 circuit A/R/A and locked out. No reports from fire and police, circuit was closed in after 10 mintues and locked out again. Circuit was patrolled by Field Operators and crew could not find anything. Customer at reported lighting strike at pole X2 | None | None | 5 | 115 | 10 | East | AP02
136084 | 2017-06-27 | Defective Equipment | Imminent Failure | Leaking transformer TE579 changed out with new TP12004 at 21 Hogan affecting 18 customers on the 190F5 Parrkwood Hills DS | U/G Transformer | Padmount (1ph) | 18 | 30 | 9 | South | 190F5
136085 | 2017-06-27 | Tree Contacts | Broken Branch | Tree Branch on the O/H caused the wires to come in contact with each other at Dundee and Elmhurst and caused S21516 to blow. Lincoln Heights (TD05) | O/H Switchgear | Fused Cutout | 338 | 69 | 389 | Central | TD05
136087 | 2017-06-27 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33411 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 9 | 57 | 9 | Central | TW22
136088 | 2017-06-27 | Tree Contacts | Tree Growth/ Untrimmed Tree | REMOVED VINES FROM THE AROUND THE TRANSFORMER (X27481) SWITCH FEFUSED SWITCH | O/H Transformer | O/H Transformer (1ph) | 8 | 104 | 14 | Central | 505
136089 | 2017-06-27 | Unknown/Other | Unknown | REFUSED SWITCH S29287 FEEDING TRANSFORMER X39746 | O/H Switchgear | Fused Cutout | 1 | 150 | 2 | South | FAL03
136090 | 2017-06-28 | Scheduled Outage | Construction | Transformer TV195 at 292 St. Andrew was isoalted to allow crew to upgrade sidewalk vault and replace submersible transformers. King Edward (SK12) | None | None | 37 | 444 | 274 | Central | SK12
136091 | 2017-06-28 | Defective Equipment | Imminent Failure | Leaking transformer change at 1708 Laurelwood affecting 7 customers on the 77M2 out of Bilberry Creek | U/G Transformer | Padmount (1ph) | 7 | 87 | 10 | East | 77M2
136092 | 2017-06-28 | Scheduled Outage | Construction | TB15 from pole X48071 to end of line was isolated to allow crew to change Hydro pole at 955 Hamlet. Russell (TB15). | None | None | 82 | 430 | 588 | East | TB15
136093 | 2017-06-28 | Defective Equipment | Imminent Failure | TE1883 and TE1884 transformer leaker change outs on Medhurst affecting 28 customers on the Merivale 72F1 | U/G Transformer | Padmount (1ph) | 28 | 69 | 32 | South | 72F1
136094 | 2017-06-28 | Defective Equipment | Defective Equipment/ Material | The Kanata 624F3 tripped due to defective riser switch termination at switch 72 at March Rd and Salter Rd. | U/G Cable Attachement | Termination \ Stress Cone | 13 | 23 | 5 | West | 624F3
136094 | 2017-06-28 | Defective Equipment | Defective Equipment/ Material | The Kanata 624F3 tripped due to defective riser switch termination at switch 72 at March Rd and Salter Rd. | U/G Cable Attachement | Termination \ Stress Cone | 572 | 41 | 391 | West | 624F3
136095 | 2017-06-28 | Defective Equipment | Electrical Failure | defective transformer | O/H Transformer | O/H Transformer (1ph) | 1 | 93 | 2 | South | FAL03
136096 | 2017-06-28 | Tree Contacts | Other Vegetation | REMOVED VINES FROM AROUND THE TRANSFORMER AND REFUSED SWITCH FEEDING X34299 | O/H Transformer | O/H Transformer (1ph) | 8 | 90 | 12 | Central | TD06
136098 | 2017-06-28 | Tree Contacts | Broken Branch | Tree limb on red phase at 15 Bradleyremoved by 24/7 | O/H Conductor | Unknown \ Other | 125 | 28 | 58 | West | 44F1
136099 | 2017-06-28 | Defective Equipment | Defective Equipment/ Material | Defective transformer replaced by oncall crew | O/H Transformer | O/H Transformer (1ph) | 14 | 150 | 35 | South | 200F2
136100 | 2017-06-29 | Scheduled Outage | Maintenance | new secondary cables installed, generator removed | None | U/G Service | 1 | 50 | 1 | West | 624F1
136101 | 2017-06-29 | Defective Equipment | Imminent Failure | TP5980 replaced due to leaking oil, affecting 23 customers. Barrhaven (140F3) | U/G Transformer | Padmount (1ph) | 23 | 78 | 30 | South | 140F3
136103 | 2017-06-29 | Scheduled Outage | Maintenance | TE1096 isolated to replaced defective transformer., affecting 13 customers. Merivale DS (72F1) | None | Padmount (1ph) | 13 | 32 | 7 | South | 72F1
136104 | 2017-06-29 | Foreign Interference | Wildlife (Bird/Animal) | A crow was found at transformer X10961. The crow caused the transformer fuse to blow and the primary line fuse S11736 to blow. Restoration was delayed due to trouble finding the proper transformer fuse in stock. | O/H Switchgear | Fused Cutout | 1 | 169 | 3 | West | BECKF2
136105 | 2017-06-29 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X25762 open to transfer plant to a new pole. Customers notified. | None | None | 18 | 90 | 27 | Central | SB13
136106 | 2017-06-29 | Unknown/Other | Unknown | SC23215-CB3 found tripped, crews placed PC10c #006280 and issued ti to Sean best (Bradley Kelly), affecting 1 customer. Carling TS (TM06) | Customer Owned | Customer-Owned | 1 | 254 | 4 | Central | TM4SB
136107 | 2017-06-29 | Tree Contacts | Broken Branch | Tree limb on wires. | Station Equipment | Relay | 884 | 51 | 751 | Central | TW17
136108 | 2017-06-30 | Lightning | Lightning | S1739R found blown, crew replaced fuse. Possible lightning strike | Unknown \ Other | Unknown \ Other | 28 | 75 | 35 | West | MWDF3
136109 | 2017-06-30 | Foreign Interference | Wildlife (Bird/Animal) | Blown fuse at transformer X30296, caused by squirrel. Refused and closed. All power restored. As per Field Operators. | O/H Switchgear | Fused Cutout | 17 | 141 | 40 | Central | TH15
136110 | 2017-06-30 | Defective Equipment | Mechanical Failure | To allow Hydro Ottawa line crews to change elbows & inserst on transformer 3717B. | U/G Cable Attachement | Elbow \ Insert | 12 | 137 | 27 | West | 24F8
136111 | 2017-06-30 | Scheduled Outage | Construction | Evan Cowell and crew to have transformer X33410 open to install two overhead secondary services. Customers notified. | None | None | 7 | 49 | 6 | Central | TW22
136112 | 2017-06-30 | Loss Of Supply | Third Party | A-B switch and S-207 in VT432 flashed over. | None | None | 1 | 409 | 7 | Central | 412
136112 | 2017-06-30 | Loss Of Supply | Third Party | A-B switch and S-207 in VT432 flashed over. | None | None | 13 | 82 | 18 | Central | 630
136112 | 2017-06-30 | Loss Of Supply | Third Party | A-B switch and S-207 in VT432 flashed over. | None | None | 41 | 121 | 83 | Central | 412
136112 | 2017-06-30 | Loss Of Supply | Third Party | A-B switch and S-207 in VT432 flashed over. | None | None | 682 | 105 | 1194 | Central | 411
136114 | 2017-07-01 | Tree Contacts | Broken Branch | Transformer X26772 open due to defective switch and burnt primary leads caused by tree branch fallen on the O/H primary. | None | None | 4 | 424 | 28 | East | AJ06
136115 | 2017-07-01 | Lightning | Lightning | S15456 blew due to lightning strike on customer primary. Beckwith (BECKF2) | O/H Switchgear | Fused Cutout | 1 | 213 | 4 | West | BECKF2
136116 | 2017-07-01 | Lightning | Lightning | A transformer at 7974 Bleeks was interupted when the fused switch was opened by lightning strike affecting 1 customer. Beckwith BECKF2 | None | None | 1 | 227 | 4 | West | BECKF2
136117 | 2017-07-02 | Human Element | Protection Setting | LMBT3 tripped on differential and multiple equipment relays have activated. Transformer tripped due to B protection not blocking the harmonic protection when L2M circuit auto-reclosed. | Unknown \ Other | Unknown \ Other | 1505 | 3 | 75 | East | LMBF5
136117 | 2017-07-02 | Human Element | Protection Setting | LMBT3 tripped on differential and multiple equipment relays have activated. Transformer tripped due to B protection not blocking the harmonic protection when L2M circuit auto-reclosed. | Unknown \ Other | Unknown \ Other | 7218 | 68 | 8180 | East | LMBF7
136120 | 2017-07-02 | Defective Equipment | Defective Equipment/ Material | Sustpected cable fault between SC24464 and VT633 | U/G Cable | PILC | 3 | 9 | 0 | East | TO5UB
136120 | 2017-07-02 | Defective Equipment | Defective Equipment/ Material | Sustpected cable fault between SC24464 and VT633 | U/G Cable | PILC | 101 | 24 | 40 | East | TO5UB
136120 | 2017-07-02 | Defective Equipment | Defective Equipment/ Material | Sustpected cable fault between SC24464 and VT633 | U/G Cable | PILC | 278 | 27 | 125 | East | TO5UB
136120 | 2017-07-02 | Defective Equipment | Defective Equipment/ Material | Sustpected cable fault between SC24464 and VT633 | U/G Cable | PILC | 520 | 84 | 728 | East | TO5UB
136120 | 2017-07-02 | Defective Equipment | Defective Equipment/ Material | Sustpected cable fault between SC24464 and VT633 | U/G Cable | PILC | 1526 | 5 | 127 | East | TO5UB
136121 | 2017-07-03 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27696 (SQUIRREL CONTACT) | None | None | 9 | 66 | 10 | East | TB06
136122 | 2017-07-03 | Loss Of Supply | Third Party | Blown fuse in Reyrolle switchgear. | None | None | 1 | 112 | 2 | Central | TH01
136123 | 2017-07-04 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X36381 openned due to animal contact. Crews re-fused and re-energized. | None | None | 4 | 129 | 9 | South | 72F4
136126 | 2017-07-04 | Human Element | Switching Error | At 10:35am while performing a switching order to isolate a cable section, JW leslie inadvertenly dumped off 73 customers. Fallowfield (FAL03) | U/G Transformer | Padmount (1ph) | 73 | 33 | 40 | South | FAL03
136128 | 2017-07-04 | Scheduled Outage | Construction | At 09:17am TE481 was isolated for replacement. 8 customers affected. Cyrville (CYRF3) | None | None | 8 | 408 | 54 | East | CYRF3
136129 | 2017-07-04 | Scheduled Outage | Construction | Mike Byers and crew to have transformer X5348 open to transfer plant. Customers notified. | None | None | 1 | 19 | 0 | South | 180F4
136131 | 2017-07-04 | Foreign Interference | Wildlife (Bird/Animal) | Fuse at transformer X32805 opened due to animal contact. 12 customers affected. Woodroffe (TW22) | None | None | 12 | 82 | 16 | Central | TW22
136132 | 2017-07-05 | Scheduled Outage | Vegetation Management | At 08:30am a section of the 170F1 from S26344 to EOL was isolated to allow tree trimming. 39 customers affected. Woodroffe DS (170F1) | None | None | 39 | 349 | 227 | South | 170F1
136133 | 2017-07-05 | Scheduled Outage | Construction | At 8:34am K349 was isolated to replace transformer and switch, 24 customers affected. Urbandale (AE07) | None | None | 24 | 418 | 167 | East | AE07
136134 | 2017-07-05 | Scheduled Outage | Construction | section of TB15 overhead circuit was isolated to change poles with crane. 170 customers were affected. Russell (TB15) | None | None | 170 | 462 | 1309 | East | TB15
136135 | 2017-07-05 | Scheduled Outage | Vegetation Management | 24/7 isolated overhead circuit between Garfield and Savoy to remove tree on primary at 1912 Savoy. 40 customers were affected. Clyde (UC05) | None | None | 40 | 42 | 28 | Central | UC05
136136 | 2017-07-06 | Scheduled Outage | Construction | Transformer K347 at 2322 Russell was isolated to allow crew to replace transformer. Urbandale (AE07) | None | None | 18 | 352 | 106 | East | AE07
136137 | 2017-07-06 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X48450 (SQUIRREL CONTACT) | None | None | 8 | 94 | 13 | Central | TW18
136138 | 2017-07-06 | Defective Equipment | Imminent Failure | replace leaking transformer | U/G Transformer | Padmount (1ph) | 9 | 98 | 15 | South | 145F4
136139 | 2017-07-06 | Defective Equipment | Imminent Failure | replace leaker | U/G Transformer | Padmount (1ph) | 6 | 140 | 14 | South | 140F5
136140 | 2017-07-06 | Defective Equipment | Moisture Ingress | S17513 open due to defective fuse switch. Manordale 84F2 | O/H Switchgear | Fused Cutout | 57 | 39 | 37 | South | 84F2
136142 | 2017-07-07 | Scheduled Outage | Construction | A section of primary overhead on Prince of Wales was isolated to replace a pole and transformer affecting 2 customers. Rideau Heights 180F4 | None | None | 2 | 215 | 7 | South | 180F4
136143 | 2017-07-07 | Defective Equipment | Imminent Failure | A transformer at Cedarhill and Royal Berkdale was isolated to replace a leaking transformer affecting 7 customers. Jockvale 145F2 | U/G Transformer | Padmount (1ph) | 7 | 100 | 12 | South | 145F2
136144 | 2017-07-07 | Defective Equipment | Electrical Failure | S-507 fuses to PT198 open due to defective transformer PT198 at 3201 Conroy Albion (2206 ) | U/G Transformer | Padmount (3ph) | 1 | 414 | 7 | East | 2206
136145 | 2017-07-07 | Lightning | Lightning | During the lightning storm the RX2005 WB phases tripped open. Crew patrolled circuit from RX2005 to EOL and suspect lightning caused the RX2005 to trip open. Beckwith (BECKF2) | None | None | 45 | 7 | 5 | West | BECKF2
136145 | 2017-07-07 | Lightning | Lightning | During the lightning storm the RX2005 WB phases tripped open. Crew patrolled circuit from RX2005 to EOL and suspect lightning caused the RX2005 to trip open. Beckwith (BECKF2) | None | None | 180 | 66 | 198 | West | BECKF2
136146 | 2017-07-07 | Defective Equipment | Defective Equipment/ Material | Transformer #X17707 opened up due to defective fuse | O/H Switchgear | Fused Cutout | 7 | 180 | 21 | West | BECKF2
136149 | 2017-07-08 | Lightning | Lightning | At 2:39am and 2:45am lighting caused an auto-reclose on the Beckwith F2 affecting 600 customers. 1 customer remained out due to a blown transformer fuse. Beckwith (BECKF2) | None | None | 1 | 165 | 3 | West | BECKF2
136152 | 2017-07-08 | Lightning | Lightning | Lightning in area caused S23526 at 4334 Cedarview to open. 1 customer affected. Fallowfield FAL01. | None | None | 1 | 155 | 3 | South | FAL01
136153 | 2017-07-08 | Lightning | Lightning | Lightning in area caused S10110 at 4282 Cedarview to open. 1 customer affected. Fallowfield FAL01. | None | None | 1 | 170 | 3 | South | FAL01
136154 | 2017-07-08 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X36011 opened up due to tree contact | None | None | 4 | 148 | 10 | South | EPWF1
136155 | 2017-07-08 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32605 opened up due to squirrel contact | None | None | 4 | 151 | 10 | Central | TD05
136156 | 2017-07-08 | Defective Equipment | Defective Equipment/ Material | Transformer #X40601 opened up due to defective transformer. On call came in to replace it. | O/H Transformer | O/H Transformer (1ph) | 2 | 281 | 9 | South | 140F4
136157 | 2017-07-08 | Adverse Weather | Extreme Wind | Suspected storm caused 1 phase of G497 at 4897 Albion to open, other 2 phases opened to replace switches. 1 customer affected. Limebank 7F4. | None | None | 1 | 45 | 1 | East | 7F4
136158 | 2017-07-08 | Defective Equipment | Electrical Failure | Cable fault between TE1530 and TE1531 caused SE24-4 to blow. | U/G Cable | XLPE | 75 | 124 | 155 | East | 77M1
136161 | 2017-07-09 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X40062 opened up due to animal contact | None | None | 7 | 50 | 6 | South | 200F3
136162 | 2017-07-09 | Scheduled Outage | Construction | P1571 at 166 Montreal rd was isolated to install new primary cable. 9 customers affected. Eastview UT05. | None | None | 1 | 297 | 5 | East | UT05
136163 | 2017-07-09 | Defective Equipment | Corrosion | TP11930 at 66 Colonade was isolated for soil remediation & to replace transformer base. 9 ustomers affected. Borden Farm BDFF3. | U/G Transformer | Padmount (1ph) | 9 | 732 | 110 | South | 130F3
136164 | 2017-07-09 | Scheduled Outage | Construction | Transformer K1195 isolated to transfer riser to new pole. | None | None | 6 | 64 | 6 | East | UT05
136165 | 2017-07-09 | Tree Contacts | Broken Branch | UG07 overhead line from S13156 was isoalted to allow forestry crew to remove large limb of primary. | None | None | 16 | 103 | 27 | East | UG07
136166 | 2017-07-09 | Tree Contacts | Other Vegetation | Transformer #X33265 opened up due to vines contact | None | None | 1 | 106 | 2 | West | 43F3
136167 | 2017-07-10 | Foreign Interference | Wildlife (Bird/Animal) | Cut out fuse at transformer X47523 openned due to contact with a squirrel. Crews re-fused and re-energized. | None | None | 13 | 44 | 10 | Central | TW18
136168 | 2017-07-10 | Scheduled Outage | Vegetation Management | 24/7 crew to isolate privately owned section of LMBF7 to remove trees from the line. Crew had to expand the outage inorder to restore the line safely. | None | None | 6 | 22 | 2 | East | LMBF7
136169 | 2017-07-10 | Scheduled Outage | Vegetation Management | S15366 was opened to trim trees at rear of 3430 Carling. 12 customers affected. Stafford 200F1. | None | None | 12 | 234 | 47 | South | 200F1
136170 | 2017-07-10 | Scheduled Outage | Maintenance | TP10630 at 34 Vanstone was isolated to move transformer for better access. 11 customers affected. Bridlwood BRDF4. | None | None | 11 | 165 | 30 | West | BRDF4
136171 | 2017-07-10 | Scheduled Outage | Maintenance | S23441 at 5686 Fernbank opened to repair primary neutral connections. 1 customer affected. Terry Fox TFXF5. | None | None | 1 | 125 | 2 | West | TFXF5
136172 | 2017-07-10 | Scheduled Outage | Construction | TP10637 at 12 Oakview isolated to replace broken insert. 7 customers affected. Bridlewood BRDF4. | None | None | 7 | 73 | 9 | West | BRDF4
136173 | 2017-07-11 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X36738 open due to animal contact. Q.C.H(160F1) | None | None | 10 | 51 | 8 | South | 160F1
136175 | 2017-07-11 | Scheduled Outage | Vegetation Management | Tree trimming | None | None | 24 | 243 | 97 | South | 200F1
136176 | 2017-07-11 | Scheduled Outage | Maintenance | Repairs to heating secondary connection. | None | None | 4 | 79 | 5 | South | 72F1
136177 | 2017-07-11 | Scheduled Outage | Maintenance | Transformer isolated to turn transformer for better access | None | None | 9 | 171 | 26 | West | BRDF4
136178 | 2017-07-12 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 42 | 311 | 218 | South | 47F3
136179 | 2017-07-12 | Scheduled Outage | Construction | TB15 OH section isolated for crews to replace poles, affecting 197 customers. Russell TS (TB15). | None | None | 197 | 520 | 1707 | East | TB15
136180 | 2017-07-12 | Scheduled Outage | Construction | K537 isolated for secondary excavation clearance, asbestos removal and switch upgrade, affecting 19 customers. Carling DS (SM15) | None | None | 19 | 100 | 32 | Central | SM15
136181 | 2017-07-12 | Scheduled Outage | Construction | Pole and cable replacement. | None | None | 149 | 405 | 1006 | Central | UF04
136182 | 2017-07-12 | Scheduled Outage | Construction | Soil remediation. | None | None | 18 | 517 | 155 | South | 190F5
136183 | 2017-07-12 | Scheduled Outage | Construction | Install secondaries. | None | None | 23 | 280 | 107 | East | CYRF4
136184 | 2017-07-12 | Foreign Interference | Dig-In | Defective equipment. | None | None | 1 | 1521 | 25 | West | 624F1
136185 | 2017-07-12 | Defective Equipment | Electrical Failure | Fuse at S666 opened at 43 Harrison due to a defectvie lightning arrestor. 35 customers affected. Manordale (84F6) | Pole Attachement | Arrester | 35 | 75 | 44 | South | 84F6
136186 | 2017-07-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X27078 blew due to squirrel contact. | O/H Transformer | O/H Transformer (1ph) | 13 | 75 | 16 | East | TB14
136187 | 2017-07-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer fuse at 1002 Alpine opened due to animal contact. 4 customers affected. Lincoln Heights (TD05) | None | None | 4 | 54 | 4 | Central | TD05
136188 | 2017-07-13 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #1170 opened up due to tree contact | O/H Switchgear | Fused Cutout | 2 | 102 | 3 | South | EPWF1
136189 | 2017-07-13 | Defective Equipment | Imminent Failure | Transformer TP8471 at 5946 Meadowglen was isolated to allow the crew to replace a leaking transformer, affecting 8 customers on the 77M5 circuit for 93 minutes | U/G Transformer | Padmount (1ph) | 8 | 93 | 12 | East | 77M5
136190 | 2017-07-13 | Scheduled Outage | Construction | Transformer #X30075 isolated by crew to relocate plant | None | None | 4 | 140 | 9 | Central | SB11
136191 | 2017-07-13 | Scheduled Outage | Construction | At 9:15am transformers 346W and 347W were isolated for repairs. 18 customers affected. Bridlewood (BRDF4) | None | None | 18 | 112 | 34 | West | BRDF4
136193 | 2017-07-13 | Scheduled Outage | Maintenance | Transformer #X31981 isolated by crew to replace blown arrestor and switch | None | None | 8 | 45 | 6 | Central | SM12
136194 | 2017-07-13 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X38568 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 5 | 83 | 7 | Central | TD06
136195 | 2017-07-13 | Scheduled Outage | Construction | At 9:27am transformer 11387 was isolated to allow crew to replace transformer base. 2 customers affected. Munster (43F3) | None | None | 2 | 293 | 10 | West | 43F3
136196 | 2017-07-13 | Defective Equipment | Electrical Failure | At 2:14pm 180F1 tripped under hold-off and was carrying the 180F4 also. It was closed and tripped again 10mins later under hold-off. At 3:00pm it was closed a third time and reclosed 14mins later. Crews found a defective arrestor at transformer 2983 on Ge | Pole Attachement | Arrester | 9 | 120 | 18 | South | 180F1
136196 | 2017-07-13 | Defective Equipment | Electrical Failure | At 2:14pm 180F1 tripped under hold-off and was carrying the 180F4 also. It was closed and tripped again 10mins later under hold-off. At 3:00pm it was closed a third time and reclosed 14mins later. Crews found a defective arrestor at transformer 2983 on Ge | Pole Attachement | Arrester | 1041 | 14 | 243 | South | 180F1
136196 | 2017-07-13 | Defective Equipment | Electrical Failure | At 2:14pm 180F1 tripped under hold-off and was carrying the 180F4 also. It was closed and tripped again 10mins later under hold-off. At 3:00pm it was closed a third time and reclosed 14mins later. Crews found a defective arrestor at transformer 2983 on Ge | Pole Attachement | Arrester | 2082 | 22 | 763 | South | 180F1
136196 | 2017-07-13 | Defective Equipment | Electrical Failure | At 2:14pm 180F1 tripped under hold-off and was carrying the 180F4 also. It was closed and tripped again 10mins later under hold-off. At 3:00pm it was closed a third time and reclosed 14mins later. Crews found a defective arrestor at transformer 2983 on Ge | Pole Attachement | Arrester | 3123 | 24 | 1249 | South | 180F1
136197 | 2017-07-14 | Scheduled Outage | Construction | Transformer #X35483 isolated by crew to transfer load | None | None | 21 | 60 | 21 | Central | UC08
136198 | 2017-07-14 | Scheduled Outage | Construction | Transformer #X34739 isolated by crew to transfer load | None | None | 23 | 60 | 23 | Central | UC08
136199 | 2017-07-14 | Scheduled Outage | Construction | Transformer #X33203 isolated by crew to remove animal from hydro plant | None | None | 9 | 3 | 0 | Central | TD05
136200 | 2017-07-14 | Scheduled Outage | Construction | transformer P247 at 135 Preston was isolated to replace same. One customer was affected. Bayswater (UJ06) | None | None | 1 | 95 | 2 | Central | UJ06
136201 | 2017-07-14 | Scheduled Outage | Construction | At 9:21am a section of the Epworth F1 was isolated to allow crew to install a new pole. 59 customers affected. Epworth (EPWF1) | None | None | 59 | 251 | 247 | South | EPWF1
136202 | 2017-07-14 | Defective Equipment | Imminent Failure | Crew isolated transformer TE1759 at 15 Piety Hill Way to replace leaking transformer. 7 customers were affected. Jockvale (145F3) | U/G Transformer | Padmount (1ph) | 7 | 143 | 17 | South | 145F3
136203 | 2017-07-14 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X38568 opened up due to tree contact | O/H Switchgear | Fused Cutout | 5 | 68 | 6 | Central | TD06
136204 | 2017-07-14 | Scheduled Outage | Construction | transformer K612, and K613 at 37 Belvedere were isolated to replace blown arrestors, remove asbestos, and replace porcelin insulators. 16 customers were affected. Vaughan (UG09) | None | None | 16 | 165 | 44 | East | UG09
136205 | 2017-07-14 | Scheduled Outage | Construction | Transformer #X35923 isolated by crew to replace switch | None | None | 6 | 60 | 6 | Central | TD06
136206 | 2017-07-14 | Scheduled Outage | Construction | REPLACED TRANSFORMER X5348 AND TRANSFERRED CUSTOMERS TO NEW HYDRO PLANT | None | None | 1 | 31 | 1 | South | 180F4
136207 | 2017-07-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #55C2D-0402 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 1 | 50 | 1 | Central | TD06
136208 | 2017-07-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X15234 TO INSTALL NEW POLE | None | None | 2 | 30 | 1 | East | LTM04
136209 | 2017-07-14 | Tree Contacts | Tree Growth/ Untrimmed Tree | TRIMMED TREES AROUND TRANSFORMER NP001170 REFUSED SWITCH AND RESTORED POWER | O/H Transformer | O/H Transformer (1ph) | 3 | 92 | 5 | South | EPWF1
136210 | 2017-07-14 | Lightning | Lightning | Rideau Heights 180F3 breaker tripped and locked out due to thunder storm, affecting 350 customers | Unknown \ Other | Unknown \ Other | 350 | 2 | 12 | South | 180F3
136213 | 2017-07-14 | Defective Equipment | Electrical Failure | AQ03 white phase defective cable, affecting 28 customers. | U/G Cable | XLPE | 28 | 138 | 64 | East | AQ03
136215 | 2017-07-15 | Defective Equipment | Electrical Failure | G120 B phase was found blown, crew patrolled circuit and did not find anything. G120 was refused and all load was restored | O/H Switchgear | Fused Cutout | 365 | 94 | 572 | East | 77M1
136216 | 2017-07-15 | Scheduled Outage | Construction | planned outage to allow crew to change some neutal connections and investigate farm stray voltage issues. | None | None | 1 | 80 | 1 | West | BECKF2
136217 | 2017-07-14 | Tree Contacts | Broken Branch | Tree contact | O/H Transformer | O/H Transformer (1ph) | 7 | 195 | 23 | South | EPWF3
136218 | 2017-07-15 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact | O/H Switchgear | Fused Cutout | 6 | 122 | 12 | South | 200F2
136221 | 2017-07-17 | Scheduled Outage | Construction | A transformer at 18 Sunridge was isolated to install new primary cable affecting 12 customers. Barrhaven 140F4 | None | None | 12 | 262 | 52 | South | 140F4
136222 | 2017-07-17 | Scheduled Outage | Vegetation Management | Switch S18599 to EOL was isolated to allow Davey tree to perfrom tree trimming at rear of 9 and 25 Donnington. Edwin (UV04) | None | None | 67 | 341 | 381 | Central | UV04
136223 | 2017-07-17 | Scheduled Outage | Construction | Transformer 341W was isolated to allow crew to turn the transformer on its base to allow for easier access. Bridlewood (BRRDF4) | None | None | 10 | 106 | 18 | West | BRDF4
136224 | 2017-07-17 | Human Element | Improper Design | Under sized fuse blew when circuit was transferred to alternate source. | O/H Switchgear | Fused Cutout | 526 | 78 | 684 | West | 28F3
136225 | 2017-07-17 | Lightning | Lightning | After restoring load from an undersized fuse (outage ID# 136224) a wire burned down on Eagleson, G Ryan reports, it looks like a lightning strike weakend the conductor. | O/H Conductor | O/H Conductor | 526 | 102 | 894 | West | 28F3
136226 | 2017-07-17 | Defective Equipment | Electrical Failure | ISOLATED TRANSFORMER X35911 TO REPLACE SWITCH AND ARRESTER | O/H Switchgear | Fused Cutout | 12 | 86 | 17 | Central | TD06
136227 | 2017-07-17 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X48613 opened up due to animal contact | O/H Switchgear | Fused Cutout | 14 | 50 | 12 | Central | TW18
136228 | 2017-07-18 | Scheduled Outage | Construction | planned outage to replace blown arrestors and insulators. | None | None | 13 | 78 | 17 | Central | SM15
136230 | 2017-07-18 | Scheduled Outage | Construction | planned outage to upgrade sidewalk vault TV187 | None | None | 38 | 180 | 114 | Central | SK12
136231 | 2017-07-18 | Scheduled Outage | Construction | Transformer TP5911 replacement and cable replacement affecting 15 customers on the Barrhaven 140F4 | None | None | 15 | 340 | 85 | South | 140F4
136232 | 2017-07-18 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35910 TO REPLACE SWITCH AND ARRESTER | None | None | 10 | 65 | 11 | Central | TD06
136233 | 2017-07-18 | Scheduled Outage | Construction | ISOLATED TRANSFORMER TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 71 | 7 | South | 180F4
136234 | 2017-07-18 | Scheduled Outage | Construction | 6 customers affecting for HOL crew to transfer services to other supply for removal of overhead conductor. Rideau Heights 180F4 | None | None | 6 | 150 | 15 | South | 180F4
136235 | 2017-07-18 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 reports transformer infront of 11 Appleford St found opened. G490R was refused and closed. Restoring 31 customers on Appleford St. 24/7 reports a bird was found on top of the transformer. | O/H Transformer | O/H Transformer (1ph) | 9 | 13 | 2 | East | 8F1
136235 | 2017-07-18 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 reports transformer infront of 11 Appleford St found opened. G490R was refused and closed. Restoring 31 customers on Appleford St. 24/7 reports a bird was found on top of the transformer. | O/H Transformer | O/H Transformer (1ph) | 40 | 61 | 41 | East | 8F1
136236 | 2017-07-19 | Scheduled Outage | Construction | TB15 overhead from TEMP 47 to EOL isolated to set new poles with crane, affecting 65 customers. Russell TS (TB15) | None | None | 65 | 397 | 430 | East | TB15
136237 | 2017-07-19 | Scheduled Outage | Maintenance | Padmount 340 was isolated to re-position the transformer for better access on the Bridlewood BRDF3 affecting 9 customers | None | None | 9 | 149 | 22 | West | BRDF3
136239 | 2017-07-19 | Defective Equipment | Imminent Failure | Overhead transformer X23139, replaced due to leaking oil. Vaughan DS (UG05) | O/H Transformer | O/H Transformer (1ph) | 3 | 135 | 7 | East | UG05
136240 | 2017-07-19 | Defective Equipment | Electrical Failure | AD06 OH to EOL isolated to allow crews to replace transformer and remove 2 transformers, affecting 46 customers. Shillington DS (AD06) | O/H Transformer | O/H Transformer (1ph) | 46 | 252 | 193 | Central | AD06
136242 | 2017-07-19 | Scheduled Outage | Construction | Chris Costello and crew to have transformer X41936 open to transfer plant. Customers notified. | None | None | 8 | 245 | 33 | Central | UF06
136243 | 2017-07-19 | Scheduled Outage | Construction | Transformer TP5905 replacement and new cable put into service affecting 9 customers on the Barrhaven 140F4 | None | None | 9 | 317 | 48 | South | 140F4
136243 | 2017-07-19 | Scheduled Outage | Construction | Transformer TP5905 replacement and new cable put into service affecting 9 customers on the Barrhaven 140F4 | None | None | 19 | 52 | 16 | South | 140F4
136244 | 2017-07-19 | Scheduled Outage | Vegetation Management | Tree removal on the Woodroffe 170F1 affecting 86 customers | None | None | 86 | 315 | 452 | South | 170F1
136246 | 2017-07-20 | Defective Equipment | Electrical Failure | K383 & K386 isolated to replace arresters and Insulators, affecting 19 customers. Albion DS (UA11). | U/G Cable Attachement | Arrester | 19 | 150 | 48 | East | UA11
136247 | 2017-07-20 | Scheduled Outage | Construction | Transformer replacement and soil remediation. | None | None | 8 | 418 | 56 | South | 190F5
136248 | 2017-07-20 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32148 TO INSTALL NEW POLE | None | None | 8 | 330 | 44 | West | RHNF3
136249 | 2017-07-20 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 46 | 348 | 267 | South | 130F1
136250 | 2017-07-20 | Scheduled Outage | Construction | V523 isolated to transfer rise cables, affecting 49 customers. Slater DS (SA22) | None | None | 49 | 317 | 259 | Central | SA22
136251 | 2017-07-20 | Human Element | Incorrect Records/ labelling | A section of primary overhead on Lenester was opened to allow for installing jumpers on a burning switch. The phase markins turned out to be wrong and the phase opened was not the one with the burning switch affecting 91 customers. Woodroffe TW22 | None | None | 91 | 40 | 61 | Central | TW22
136252 | 2017-07-20 | Scheduled Outage | Forced Switching | TW22 circuit carried by the TW00 was opened to allow crew to safley install jumpers on a burning switch S29439. 1355 customers were affected. Woodroffe (TW22) | None | Inline Switch | 1355 | 3 | 68 | Central | TW22
136253 | 2017-07-21 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27679 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 12 | 56 | 11 | East | TB06
136254 | 2017-07-21 | Scheduled Outage | Construction | Raise transformer base. | None | None | 16 | 367 | 98 | West | MWDF3
136255 | 2017-07-21 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 47 | 315 | 247 | South | 130F1
136256 | 2017-07-21 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33589 AND X33597 TO INSTALL NEW POLE | None | None | 16 | 150 | 40 | Central | AK12
136257 | 2017-07-21 | Scheduled Outage | Maintenance | IR scan shoowed TE409 red phase at 102 degress C. Due to live front transformers on amp reading at 22 amps load had to be dropped to safly open switch. | None | Padmount (1ph) | 48 | 35 | 28 | South | 160F2
136257 | 2017-07-21 | Scheduled Outage | Maintenance | IR scan shoowed TE409 red phase at 102 degress C. Due to live front transformers on amp reading at 22 amps load had to be dropped to safly open switch. | None | Padmount (1ph) | 80 | 23 | 31 | South | 84F5
136258 | 2017-07-21 | Defective Equipment | Mechanical Failure | A cable fault on the TO2UT U/G dip at pole X34753 caused TO43 breaker to open. | U/G Cable | PILC | 187 | 52 | 162 | East | TO2UT
136259 | 2017-07-23 | Scheduled Outage | Maintenance | To allow Hydro Ottawa 24/7 to change defective transformer switch at X27299 | None | Fused Cutout | 6 | 45 | 4 | East | UA07
136260 | 2017-07-23 | Defective Equipment | Electrical Failure | To allow Hydro Ottawa on-call crews to change a defective transformer | O/H Transformer | O/H Transformer (1ph) | 6 | 230 | 23 | Central | SM10
136262 | 2017-07-23 | Defective Equipment | Electrical Failure | Gary Coburn and crew to have transformer X32580 open to replace defective arrestor. | O/H Transformer | Arrester | 11 | 87 | 16 | Central | TD01
136263 | 2017-07-23 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact determined by the Field Operators. Re-fused and closed. | O/H Switchgear | Fused Cutout | 9 | 63 | 9 | Central | TW22
136264 | 2017-07-23 | Foreign Interference | Wildlife (Bird/Animal) | animal contact caused overhead transformer X29872 at 65 Findlay creek to open. 10 customers were interrupted. Riverdale (TR09) | None | None | 10 | 22 | 4 | Central | TR09
136265 | 2017-07-23 | Defective Equipment | Imminent Failure | At 7:57am leaking transformers 5878 and 4746 at 103 and 101 Schneider Rd were isolated to allow crew to replace them 3 customers affected. Kanata MTS (624F6) | U/G Transformer | Padmount (3ph) | 3 | 408 | 20 | West | 624F6
136267 | 2017-07-24 | Defective Equipment | Electrical Failure | Blown fuse on UG Primary switch. Affected transformer NPTE1820. | U/G Switchgear | Unknown \ Other | 10 | 325 | 54 | South | 49F6
136268 | 2017-07-24 | Scheduled Outage | Forced Switching | At 2:16pm an outage was requried while switching due to an out of phase condition. 44 customers affected. Terry Fox (TFXF4) | None | None | 44 | 9 | 7 | West | TFXF4
136269 | 2017-07-24 | Tree Contacts | Tree Growth/ Untrimmed Tree | Refused transformer x36130 crew removed vines and a squirrel | O/H Transformer | O/H Transformer (1ph) | 8 | 151 | 20 | South | 190F2
136271 | 2017-07-24 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32580 | O/H Transformer | O/H Transformer (1ph) | 11 | 198 | 36 | Central | TD01
136272 | 2017-07-25 | Scheduled Outage | Construction | Bill Edwards and crew to have transformer X28107 open for a service upgrade. Customers notified. | None | None | 14 | 20 | 5 | East | AF06
136274 | 2017-07-25 | Scheduled Outage | Maintenance | K93 at 3415 Uplands was isolated to change insulators. 10 customers affected. McCarthy (AQ06) | None | Padmount (1ph) | 10 | 75 | 12 | East | AQ06
136275 | 2017-07-25 | Scheduled Outage | Vegetation Management | To allow Davey Tree to trim trees around the primary at the rear of 81 & 85 Cote des Neiges | None | None | 14 | 384 | 90 | South | EPWF1
136276 | 2017-07-25 | Scheduled Outage | Construction | Relocate dip cables and install new hydro pole | None | None | 2 | 180 | 6 | South | 180F4
136277 | 2017-07-25 | Scheduled Outage | Construction | Patrick Brisson and crew to have transformer X35504 open for construction purposes. Customers notified. | None | None | 10 | 179 | 30 | Central | AH14
136278 | 2017-07-25 | Scheduled Outage | Maintenance | Jeremy Walker and crew to have transformer X32223 open to drop a service. Customers notified. | None | None | 10 | 10 | 2 | Central | AD06
136279 | 2017-07-25 | Scheduled Outage | Construction | Patrick Brisson and crew to have transformer X35503 open for construction purposes. Customers notified. | None | None | 7 | 218 | 25 | Central | AH14
136283 | 2017-07-26 | Scheduled Outage | Vegetation Management | To allow Davey Tree to trim trees along the EPWF1 O/H from S22290 to EOL | None | None | 13 | 331 | 72 | South | EPWF1
136284 | 2017-07-26 | Scheduled Outage | Construction | Geoff Ryan and crew to have transformer X32996 open to re-arrange plant on the pole. Customers notified. | None | None | 4 | 40 | 3 | West | 28F2
136285 | 2017-07-26 | Scheduled Outage | Construction | Scott Barkley and crew to have 4 transformers (X31409, X17745, X31410, X31411) open to install prespun bus. Customer notified. | None | None | 38 | 135 | 86 | Central | AM03
136286 | 2017-07-26 | Defective Equipment | Imminent Failure | To allow Hydro Ottawa crews to replace the elbows on TE644 and replace TE649 (leaking transformer) | U/G Cable Attachement | Elbow \ Insert | 11 | 247 | 45 | East | BCHF7
136286 | 2017-07-26 | Defective Equipment | Imminent Failure | To allow Hydro Ottawa crews to replace the elbows on TE644 and replace TE649 (leaking transformer) | U/G Cable Attachement | Elbow \ Insert | 20 | 179 | 60 | East | BCHF7
136287 | 2017-07-26 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 7 | 531 | 62 | South | 180F4
136288 | 2017-07-26 | Human Element | Improper Construction/installation | S14880 RWB was found tapped to the wrong circuit. It was supposed to be tapped to MWDF4 but was actuall tapped to MWDF3. When MWDF4 was opened under PC17A 17-147421, it caused an outage to 1466 customers | U/G Cable Attachement | Pothead | 1466 | 45 | 1100 | West | MWDF4
136289 | 2017-07-26 | Defective Equipment | Mechanical Failure | Cable fault. | U/G Cable | XLPE | 152 | 10 | 25 | East | 77M6
136289 | 2017-07-26 | Defective Equipment | Mechanical Failure | Cable fault. | U/G Cable | XLPE | 225 | 20 | 75 | East | 77M6
136289 | 2017-07-26 | Defective Equipment | Mechanical Failure | Cable fault. | U/G Cable | XLPE | 269 | 64 | 287 | East | 77M6
136289 | 2017-07-26 | Defective Equipment | Mechanical Failure | Cable fault. | U/G Cable | XLPE | 279 | 13 | 60 | East | 77M6
136289 | 2017-07-26 | Defective Equipment | Mechanical Failure | Cable fault. | U/G Cable | XLPE | 285 | 93 | 442 | East | 77M6
136290 | 2017-07-26 | Foreign Interference | Wildlife (Bird/Animal) | A crow made contact at X32127 and caused the transformer fuse to open as well as S15712 B phase to open, affecting 49 customers | O/H Switchgear | Fused Cutout | 4 | 19 | 1 | West | BECKF2
136290 | 2017-07-26 | Foreign Interference | Wildlife (Bird/Animal) | A crow made contact at X32127 and caused the transformer fuse to open as well as S15712 B phase to open, affecting 49 customers | O/H Switchgear | Fused Cutout | 29 | 1 | 0 | West | BECKF2
136290 | 2017-07-26 | Foreign Interference | Wildlife (Bird/Animal) | A crow made contact at X32127 and caused the transformer fuse to open as well as S15712 B phase to open, affecting 49 customers | O/H Switchgear | Fused Cutout | 49 | 95 | 78 | West | BECKF2
136291 | 2017-07-26 | Scheduled Outage | Construction | Replace hydro poles and transfer plant. | None | None | 2 | 357 | 12 | South | 145F3
136292 | 2017-07-26 | Tree Contacts | Falling Tree | ISOLATED TRANSFORMER X23477 TO REMOVE TREE FROM THE SECONDARY OPEN WIRE BUSS. | None | None | 19 | 143 | 45 | East | AA04
136293 | 2017-07-27 | Scheduled Outage | Vegetation Management | Forrestry trimming at rear of 9 Tower and 9 Cote des Neiges affecting 43 customers on the Epworth EPWF1 | None | None | 43 | 347 | 249 | South | EPWF1
136294 | 2017-07-27 | Scheduled Outage | Construction | Soil Remediation of TP6614 on the Parkwood Hills 190F5 affecting 1 customer | None | None | 1 | 362 | 6 | South | 190F5
136295 | 2017-07-27 | Scheduled Outage | Construction | To allow Hydro Ottawa crews to upgrade the sidewalk vault and replace the submersible transformer | None | Transformer | 46 | 280 | 215 | Central | SK12
136298 | 2017-07-27 | Scheduled Outage | Construction | New service to X36094 at 902 Alpine affecting 8 customers on the Lincoln TD05 | None | None | 8 | 42 | 6 | Central | TD05
136299 | 2017-07-27 | Unknown/Other | Unknown | No apparent cause found | None | None | 16 | 9 | 2 | East | AL04
136299 | 2017-07-27 | Unknown/Other | Unknown | No apparent cause found | None | None | 108 | 9 | 16 | East | AL03
136299 | 2017-07-27 | Unknown/Other | Unknown | No apparent cause found | None | None | 139 | 9 | 21 | East | TB1AL
136299 | 2017-07-27 | Unknown/Other | Unknown | No apparent cause found | None | None | 226 | 11 | 41 | East | AL02
136300 | 2017-07-27 | Unknown/Other | Unknown | At 7:42pm S27153 Blue phase blew open affecting 447 customers. The RHNF1 was also feeding most the the 28F2 circuit due to planned work on Huntley Rd. The circuit was patrolled and restored in two stages. No cause was found. Richmond North (RHNF1) | None | None | 127 | 26 | 55 | West | RHNF1
136300 | 2017-07-27 | Unknown/Other | Unknown | At 7:42pm S27153 Blue phase blew open affecting 447 customers. The RHNF1 was also feeding most the the 28F2 circuit due to planned work on Huntley Rd. The circuit was patrolled and restored in two stages. No cause was found. Richmond North (RHNF1) | None | None | 447 | 118 | 879 | West | RHNF1
136302 | 2017-07-28 | Scheduled Outage | Construction | Evan Cowell and crew to have transformer X32350 open to run a new service. Customers notified. | None | None | 6 | 36 | 4 | Central | TD01
136303 | 2017-07-28 | Scheduled Outage | Construction | Corey Nixon and crew to have transformers X26978 and X26942 to transfer secondaries. Customers notified. | None | None | 18 | 180 | 54 | East | AJ04
136304 | 2017-07-28 | Defective Equipment | Electrical Failure | Cable fault between Xfmr 240 and 1727 caused SC3769-CB4 to blow. | U/G Cable | XLPE | 4 | 5 | 0 | West | TFXF6
136304 | 2017-07-28 | Defective Equipment | Electrical Failure | Cable fault between Xfmr 240 and 1727 caused SC3769-CB4 to blow. | U/G Cable | XLPE | 76 | 110 | 139 | West | TFXF6
136309 | 2017-07-30 | Foreign Interference | Wildlife (Bird/Animal) | Transfomer X20818 blew due to animal contact | O/H Transformer | O/H Transformer (1ph) | 20 | 60 | 20 | East | BCHF5
136311 | 2017-07-30 | Foreign Interference | Wildlife (Bird/Animal) | Not yet known. | O/H Switchgear | Fused Cutout | 49 | 161 | 131 | South | 47F4
136313 | 2017-07-31 | Defective Equipment | Mechanical Failure | Red phase cable fault between SW167 and SW167. | U/G Cable | XLPE | 35 | 18 | 10 | Central | TH1SH
136313 | 2017-07-31 | Defective Equipment | Mechanical Failure | Red phase cable fault between SW167 and SW167. | U/G Cable | XLPE | 36 | 59 | 35 | Central | TH1SH
136314 | 2017-07-31 | Scheduled Outage | Construction | ISOLATED 5 TRANSFORMERS AND TRANSFERRED THE LOAD TO ONE TRANSFORMER X17745 | None | None | 32 | 320 | 171 | Central | AM03
136315 | 2017-07-31 | Scheduled Outage | Vegetation Management | Isolation of overhead for tree removal at rear of 33 and 37 Lotta | None | None | 14 | 359 | 84 | South | EPWF1
136317 | 2017-07-31 | Scheduled Outage | Construction | To relocate Hydro pole. | None | None | 25 | 183 | 76 | South | 180F4
136318 | 2017-08-01 | Scheduled Outage | Construction | Hydro Ottawa line crew had to open X25862 to change a service | None | None | 2 | 69 | 2 | Central | SB11
136320 | 2017-08-01 | Scheduled Outage | Vegetation Management | A section of backyard primary overhead between Lotta and Cote de Neiges was isolated for tree trimming affecting 17 customers. Epworth EPWF1 | None | None | 17 | 334 | 95 | South | EPWF1
136324 | 2017-08-01 | Defective Equipment | Imminent Failure | A transformer at 9 Sheldrake was isolated to change a leaking transformer affecting 9 customers. Bridlewood BRDF6 | U/G Transformer | Padmount (1ph) | 9 | 541 | 81 | West | BRDF6
136325 | 2017-08-02 | Scheduled Outage | Vegetation Management | Forrestry work on Epworth EPWF3 overhead at 117 Fieldrow affecting 54 customers | None | None | 54 | 320 | 288 | South | EPWF3
136326 | 2017-08-02 | Scheduled Outage | Construction | S11832 to EOL was isolated to allow crew to set pole with crane. Russell (TB15) | None | None | 14 | 337 | 79 | East | TB15
136327 | 2017-08-02 | Scheduled Outage | Construction | S11832 to EOL was isolated to allow crew to set pole with crane. Russell (TB15) | None | None | 36 | 281 | 169 | East | TB15
136330 | 2017-08-02 | Scheduled Outage | Construction | A transformer at 216 Hudson was opened to replace a service affecting 5 customers. Fisher AK02 | None | None | 5 | 19 | 2 | Central | AK02
136332 | 2017-08-02 | Lightning | Lightning | A lightning stike caused a stion breaker to auto relose and an inline interupter to open affecting 2438 customers. Bilberry 77M2 | None | None | 2017 | 5 | 168 | East | 77M2
136335 | 2017-08-02 | Lightning | Lightning | 249F2 breaker auto reclosed due to lightning storm passing through the city, affecting 4046 customers. Leitrim DS | None | None | 1 | 44 | 1 | East | 249F2
136335 | 2017-08-02 | Lightning | Lightning | 249F2 breaker auto reclosed due to lightning storm passing through the city, affecting 4046 customers. Leitrim DS | None | None | 28 | 223 | 104 | East | 249F2
136336 | 2017-08-02 | Defective Equipment | Mechanical Failure | Crews found defective riser switch to K1037, opened K1036 riser and replaced both switches that feed the loop. 43 customers affected. Henderson DS (UN04) | O/H Switchgear | Inline Switch | 27 | 65 | 29 | Central | UN04
136336 | 2017-08-02 | Defective Equipment | Mechanical Failure | Crews found defective riser switch to K1037, opened K1036 riser and replaced both switches that feed the loop. 43 customers affected. Henderson DS (UN04) | O/H Switchgear | Inline Switch | 43 | 18 | 13 | Central | UN04
136337 | 2017-08-02 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X17120 openned unexpectedly. Possibly animal interference but no animal was found on site. Crews restored. | O/H Switchgear | Fused Cutout | 12 | 93 | 19 | East | BLKF1
136339 | 2017-08-02 | Scheduled Outage | Vegetation Management | Primary down due to tre on th eoH lines, affecting 17 customers. Carling DS (SM12) | None | O/H Conductor | 17 | 200 | 57 | Central | SM12
136340 | 2017-08-03 | Scheduled Outage | Construction | Replace defective transformer. | None | None | 1 | 54 | 1 | South | 87F7
136341 | 2017-08-03 | Scheduled Outage | Construction | Overhead circuits on Olympia was isolated to replace poles. 40 customers affected. Russell (TB15) | None | Pole | 40 | 321 | 214 | East | TB15
136342 | 2017-08-03 | Scheduled Outage | Vegetation Management | Tree trimming on Stanwood affecting 112 customers on the Epworth EPWF3 | None | None | 112 | 340 | 635 | South | EPWF3
136345 | 2017-08-03 | Human Element | Improper Construction/installation | Contractor was excavating and pole fell into two phases on the 28F2. Switching was done to minimize outage. A second pole beside this pole started to lean and it had to be removed as well. | Pole | Pole | 3 | 188 | 9 | West | 28F2
136345 | 2017-08-03 | Human Element | Improper Construction/installation | Contractor was excavating and pole fell into two phases on the 28F2. Switching was done to minimize outage. A second pole beside this pole started to lean and it had to be removed as well. | Pole | Pole | 1282 | 72 | 1538 | West | 28F2
136346 | 2017-08-03 | Scheduled Outage | Forced Switching | Terra flex was digging and caused pole to fall on two phases on the 28F2. The 28F1 was isolated for clearnce. A second pole had to be removed as it was leaning as well. | None | Pole | 118 | 148 | 291 | West | 28F1
136347 | 2017-08-03 | Scheduled Outage | Construction | Transformer TP2191 at 32 Friendly was isolated to install temporary primary feed to new TP11875 using double feed thru at TP2191. | None | None | 1 | 181 | 3 | West | TFXF1
136348 | 2017-08-04 | Foreign Interference | Wildlife (Bird/Animal) | Crews report animal contact openned transformer X35249. Crews on site re-fused and restored. | O/H Switchgear | Fused Cutout | 9 | 117 | 18 | West | JKGF5
136349 | 2017-08-04 | Scheduled Outage | Maintenance | Service truck to have transformer X34105 open for service repair. Customers notified. | None | None | 12 | 21 | 4 | Central | TH01
136350 | 2017-08-04 | Defective Equipment | Imminent Failure | To allow Hydro Ottawa line crews to change leaking transformer TP8143. | U/G Transformer | Padmount (1ph) | 10 | 109 | 18 | East | 325M8
136351 | 2017-08-04 | Defective Equipment | Defective Equipment/ Material | Top of Pole broke at S21176 South East Corner of St. Laurent and Innes causing the TB2AL (TB24) and 5301(TB21) to trip. | Pole | Pole | 28 | 162 | 76 | East | TB2AL
136351 | 2017-08-04 | Defective Equipment | Defective Equipment/ Material | Top of Pole broke at S21176 South East Corner of St. Laurent and Innes causing the TB2AL (TB24) and 5301(TB21) to trip. | Pole | Pole | 190 | 43 | 136 | East | 5301
136351 | 2017-08-04 | Defective Equipment | Defective Equipment/ Material | Top of Pole broke at S21176 South East Corner of St. Laurent and Innes causing the TB2AL (TB24) and 5301(TB21) to trip. | Pole | Pole | 215 | 32 | 115 | East | 5301
136351 | 2017-08-04 | Defective Equipment | Defective Equipment/ Material | Top of Pole broke at S21176 South East Corner of St. Laurent and Innes causing the TB2AL (TB24) and 5301(TB21) to trip. | Pole | Pole | 508 | 29 | 246 | East | 5301
136352 | 2017-08-04 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X32593 opened up due to tree contact | O/H Switchgear | Fused Cutout | 7 | 83 | 10 | Central | TD06
136353 | 2017-08-04 | Foreign Interference | Wildlife (Bird/Animal) | A transformer's primary fused cutout at 635 Westminster opened caused by animal contact. Lincoln Heights TD01 | O/H Switchgear | Fused Cutout | 10 | 42 | 7 | Central | TD01
136354 | 2017-08-04 | Foreign Interference | Vehicle | A power fuse opened after a pole near-by was struck by a vehicle affecting 11 customers. King Edward TK2AC | O/H Switchgear | Fused Cutout | 11 | 76 | 14 | Central | TK2AC
136355 | 2017-08-05 | Loss Of Supply | Transmission Inadvertent | Hydro One's 22M28 breaker tripped. A blown power fuse on the closing coil was the cause | None | None | 4 | 68 | 5 | South | 22M28
136355 | 2017-08-05 | Loss Of Supply | Transmission Inadvertent | Hydro One's 22M28 breaker tripped. A blown power fuse on the closing coil was the cause | None | None | 1195 | 33 | 657 | South | 22M28
136355 | 2017-08-05 | Loss Of Supply | Transmission Inadvertent | Hydro One's 22M28 breaker tripped. A blown power fuse on the closing coil was the cause | None | None | 2962 | 14 | 691 | South | 22M28
136356 | 2017-08-05 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact at transformer pole causing transformer switch and 1410B at road to blow, crew replaced old porcelain switch at transformer X06959 and re-fused at both locations. | O/H Switchgear | Fused Cutout | 2 | 121 | 4 | West | MWDF3
136357 | 2017-08-06 | Scheduled Outage | Vegetation Management | SC3770-CB4 to EOL was isolated to allow City of Ottawa to clear tree that fell onto secondary at 273 Stewart and in close proximity of primary conductors. Augusta (UD04) | None | None | 678 | 57 | 644 | Central | UD04
136358 | 2017-08-06 | Unknown/Other | Unknown | Unknown cause for G613 W phase blowing & GR5 W phase tripping. Power restored in stages | O/H Switchgear | Recloser (1ph) | 40 | 36 | 24 | East | 8F1
136358 | 2017-08-06 | Unknown/Other | Unknown | Unknown cause for G613 W phase blowing & GR5 W phase tripping. Power restored in stages | O/H Switchgear | Recloser (1ph) | 188 | 77 | 241 | East | 8F1
136359 | 2017-08-06 | Foreign Interference | Foreign Objects | O/H transformer 4518 at the rear of 12 Briarcliffe was found to be smoking after power was restored from the previous outage. Outage# 136358. 24/7 line crews cleared some dense vegetation around the cutout | O/H Switchgear | Fused Cutout | 3 | 19 | 1 | East | 8F1
136363 | 2017-08-07 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact caused transformer X35249 cut-out fuse to blow, crew re-fused and re-energized. | O/H Switchgear | Fused Cutout | 9 | 76 | 11 | West | JKGF5
136364 | 2017-08-07 | Scheduled Outage | Forced Switching | Tranformer X44489 tested bad and had to be replaced. | None | O/H Transformer (1ph) | 15 | 335 | 84 | Central | UJ03
136365 | 2017-08-08 | Defective Equipment | Imminent Failure | transformer 129B at 82 McLellan was isolated for crew to replace leaking transformer. 11 customers were affected. Bridlewood (BRDF3) | U/G Transformer | Padmount (1ph) | 11 | 78 | -14 | West | BRDF3
136366 | 2017-08-08 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30947 TO TRANSFER HYDRO PLANT | None | None | 19 | 60 | 19 | Central | UD04
136368 | 2017-08-08 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X41423 FOR SERVICE UPGRADE | None | None | 27 | 30 | 14 | Central | SR01
136369 | 2017-08-08 | Scheduled Outage | Construction | Transformer #X29059 isolated by crew to replace pole | None | None | 8 | 315 | 42 | East | UA05
136371 | 2017-08-09 | Scheduled Outage | Forced Switching | Forced outage to allow crews to perform out of phase switching in preperation of unplanned outage on Mitch Owens. 70 customers affected. Lietrim (249F2) | None | O/H Conductor | 70 | 18 | 21 | East | LTM01
136372 | 2017-08-09 | Scheduled Outage | Forced Switching | 249F2 overhead on Mitch Owens at John Quinn isolated for Hydro One to replace a broken pole. 121 customers affected. Leitrim (249F2) | None | Pole | 121 | 250 | 504 | East | 249F2
136373 | 2017-08-09 | Scheduled Outage | Forced Switching | Forced outage to allow crew to perform out of phase switching to restore circuit to normal after a pole replacement on Mitch Owens. 70 customers affected. Leitrim (249F2) | None | O/H Conductor | 70 | 15 | 18 | East | 249F2
136374 | 2017-08-09 | Scheduled Outage | Vegetation Management | section of overhead was isolated for crew to remove tree in the rear of 2 Indian. 18 customers were affected. Epworth (EPWF1) | None | None | 18 | 343 | 103 | South | EPWF1
136375 | 2017-08-09 | Defective Equipment | Imminent Failure | crew isolated transformer TE2133 at 1 Stonebank to relocate and replace leaking transformer. Stafford (200F6) | U/G Transformer | Padmount (1ph) | 13 | 444 | 96 | South | 200F6
136376 | 2017-08-09 | Scheduled Outage | Construction | At 9:14 am Transformer KT556 at 21 Preston Street was isolated to replace transformer. 16 Customers affected. Hinchey TS (TH15) | None | None | 16 | 169 | 45 | Central | TH15
136378 | 2017-08-09 | Scheduled Outage | Maintenance | Transformer #X31435 isolated by crew to drop a span of quad | None | None | 2 | 15 | 0 | Central | AM02
136380 | 2017-08-09 | Scheduled Outage | Construction | Transformers K382 and K385 @ 2939 fairlea was isolated by the crew to allow them to replace blown arrestor ad porcelain insulators and replace cutouts affecting 20 customers on the UA06 circuit | None | None | 20 | 194 | 65 | East | UA06
136381 | 2017-08-09 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31362 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 311 | 31 | Central | AK05
136382 | 2017-08-09 | Scheduled Outage | Construction | Transformer #X29059 isolated by crew for a pole change | None | None | 8 | 175 | 23 | East | UA05
136383 | 2017-08-09 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X23722 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 220 | 22 | East | SO02
136384 | 2017-08-09 | Scheduled Outage | Construction | Transformer PT11 @ 2740 Queensview was isolated to allow the crew replace arrestors and install current limiting fuse, 1 customer affected on the 5408 circuit | None | None | 1 | 79 | 1 | Central | 5408
136385 | 2017-08-09 | Scheduled Outage | Construction | A bad vault transformer was causing the customer some voltage issues. The vault had to be islated and the affected transformer changed | Vault Equipment | Transformer | 1 | 343 | 6 | Central | TH01
136386 | 2017-08-10 | Scheduled Outage | Vegetation Management | EPWF3 W phase was isolated to allow Davey Tree to trim trees at rear of 73 and 83 Palsen. Epworth (EPWF3) | None | None | 34 | 349 | 198 | South | EPWF3
136387 | 2017-08-10 | Scheduled Outage | Construction | 303 R phase from pole 54B1B-0154 to Eol was isolated to allow crew to transfer plant to new pole. Carling (303) | None | None | 22 | 128 | 47 | Central | 303
136388 | 2017-08-10 | Scheduled Outage | Construction | Chris Costello and crew to have transformer X35775 open to work on a service. Customers notified. | None | None | 5 | 39 | 3 | Central | TD06
136390 | 2017-08-10 | Loss Of Supply | Transmission Inadvertent | The Hydro One Overbrook TS 31T2Q1 CB tripped open and caused an outage to the Q1 and Q2 busses. Hydro One currently under investigation | None | None | 9543 | 9 | 1431 | East | A4K (Overbrook - T2)
136391 | 2017-08-10 | Scheduled Outage | Construction | To allow crew to rearrange plante on pole. | None | Pole | 1 | 138 | 2 | West | RHNF1
136392 | 2017-08-10 | Defective Equipment | Defective Equipment/ Material | G425R phase blew do to defective cable between G425R and TE1069. | U/G Cable | XLPE | 53 | 79 | 70 | East | 4801F8
136394 | 2017-08-11 | Defective Equipment | Mechanical Failure | A cable fault on the ELW04 egress cable caused the ELW04 breaker to trip. All load was transferred to ELW09 | U/G Cable | PILC | 1029 | 49 | 840 | East | ELW04
136395 | 2017-08-11 | Scheduled Outage | Vegetation Management | To allow crews to tree trimming in the rear of 15 Parkside. | None | None | 35 | 328 | 191 | South | EPWF3
136397 | 2017-08-11 | Defective Equipment | Imminent Failure | Change leaking transformer. | U/G Transformer | Padmount (1ph) | 9 | 118 | 18 | West | TFXF5
136399 | 2017-08-11 | Scheduled Outage | Construction | Vault TV90 at 135 Beausoleil was isolated to allow crew to upgrade sidewalk vault and replace submersible transformers. Augusta (UD08) | None | None | 47 | 225 | 176 | Central | UD08
136400 | 2017-08-11 | Defective Equipment | Mechanical Failure | S1806 to EOL was isolated to allow crew to repalce transformer cut outs to transformers X35777, X35799, X35784, X35783, X35782. Lincoln Heights (TD06) | O/H Switchgear | Fused Cutout | 35 | 100 | 58 | Central | TD06
136401 | 2017-08-11 | Scheduled Outage | Construction | S15728 W phase to EOL was isolated to allow crew to replace defective insulator at 5199 Limebank. Limebank (7F4) | None | Insulator | 28 | 51 | 24 | East | 7F4
136402 | 2017-08-11 | Scheduled Outage | Construction | crew isolated padmount transformer at 2555 st. Joseph to reposition transformer on base. 1 customer was interrupted. Billberry (77M6) | None | None | 1 | 5 | 0 | East | 77M6
136403 | 2017-08-12 | Foreign Interference | Wildlife (Bird/Animal) | A squirrel made contact with transformer X48732 at 2124 Westbury causing the transformer fuse to blow. 48 customers were affect for 33 min on the TW17 circuit | O/H Switchgear | Fused Cutout | 48 | 33 | 26 | Central | TW17
136405 | 2017-08-12 | Lightning | Lightning | Lightning storm caused the 624F6 to auto reclosed and transformer X34876 opened. X34876 was hit by lightning and needed to be replaced. Kanata (624F6) | None | None | 17 | 486 | 138 | West | 624F6
136408 | 2017-08-12 | Tree Contacts | Falling Tree | TREE ON LINE IN THE REAR OF 2221 ST. LAURENT CREW OPENED S24534 TO REMOVE TREE. | O/H Conductor | O/H Conductor | 16 | 35 | 9 | East | AE01
136409 | 2017-08-12 | Lightning | Lightning | Severe storm in the area caused the TM1UC circuit (TM32 breaker) to trip causing and outage to 1848 customers | O/H Conductor | O/H Conductor | 1848 | 1 | 31 | Central | TM1UC
136411 | 2017-08-12 | Tree Contacts | Falling Tree | A severe storm went through caused a tree to fall into primary and the secondary bus that caused S16738 to blow causing and outage to 54 customers on the TD05 circuit | O/H Conductor | O/H Conductor | 54 | 133 | 120 | Central | TD05
136412 | 2017-08-12 | Scheduled Outage | Maintenance | 13KV transformer bus isolated to allow contractor repair secondary breakers. | None | Breaker \ Relay | 1 | 692 | 12 | Central | TD3AHTD
136413 | 2017-08-12 | Tree Contacts | Falling Tree | two phases of switch S19554 opened due to tree on overhead at 2088 Arch st. 576 customers were affected. Russell (TB06) | O/H Conductor | O/H Conductor | 576 | 321 | 3082 | East | TB06
136414 | 2017-08-12 | Adverse Weather | Extreme Wind | switch G960R on Leitrim rd. opened during storm activity, no cause was found. 14 customers were affected. Leitrim (249F2) | None | None | 14 | 175 | 41 | East | 249F2
136415 | 2017-08-12 | Lightning | Lightning | Circuit patrolled no problem found . | O/H Conductor | O/H Conductor | 232 | 376 | 1454 | East | TA3AF
136416 | 2017-08-12 | Tree Contacts | Broken Branch | Wires down in the rear of 840 Claude st. | O/H Conductor | O/H Conductor | 4 | 405 | 27 | East | AA06
136417 | 2017-08-12 | Defective Equipment | Electrical Failure | At 5:09pm customers reported no power to K628. 12 customers affected. Langs (AP05) | U/G Cable | PILC | 12 | 366 | 73 | East | AP05
136418 | 2017-08-12 | Tree Contacts | Broken Branch | Tansformer # X31333 opened to allow tree trimmers to trim tree in secondary services. | Secondary \ Service | O/H Service | 4 | 62 | 4 | Central | SB05
136419 | 2017-08-12 | Defective Equipment | Electrical Failure | At 5:45pm customers started to call in about TP5112. On-Call crew found the transformer to be defective. 10 customers affected. Kanata (624F6) | U/G Transformer | Padmount (1ph) | 10 | 503 | 84 | West | 624F6
136420 | 2017-08-12 | Lightning | Lightning | At 4:39pm G349R blew open due to lightning affecting 2 customers. Crews patrolled, refused and closed. Blackburn (BLKF5) | None | None | 2 | 519 | 17 | East | BLKF5
136421 | 2017-08-12 | Lightning | Lightning | Blown arrestor and fuse cutout on pole X56135. | O/H Transformer | O/H Transformer (1ph) | 6 | 650 | 65 | West | 28F3
136422 | 2017-08-12 | Adverse Weather | Extreme Wind | possible storm activity caused overhead transformer X38566 at 887 Richmond rd. to open. One customer was affected. Lincoln. (TD06) | O/H Switchgear | Fused Cutout | 1 | 270 | 4 | Central | TD06
136423 | 2017-08-13 | Scheduled Outage | Construction | Vehicle hit hydro pole at bank and park st. crew isolated and replaced pole. 18 customers were affected. Leitrim (249F4) | None | None | 18 | 312 | 94 | East | LTM04
136425 | 2017-08-12 | Tree Contacts | Falling Tree | At 3:00pm 2 phases of the AA06 fell in the rear of 840 Claude causing an outage to 21 customers. 2 hours of tree trimming was required and conductor was repaired. Church (AA06) | O/H Conductor | O/H Conductor | 21 | 780 | 273 | East | AA06
136426 | 2017-08-12 | Defective Equipment | Electrical Failure | At 19:28 an issued with transformer X20004 affected 1 customer. On-Call crew replaced the defective transformer. Leitrim (249F2) | O/H Transformer | O/H Transformer (1ph) | 1 | 407 | 7 | East | 249F2
136427 | 2017-08-13 | Unknown/Other | Unknown | TA15 Breaker, TA2AF tripped. Suspected cable fault. | Unknown \ Other | Unknown \ Other | 1120 | 29 | 541 | East | TA2AF
136428 | 2017-08-13 | Scheduled Outage | Construction | To string in and connect new 28F2 O/H section on Nixon Farm from Perth Street. | None | None | 3 | 519 | 26 | West | 28F2
136429 | 2017-08-13 | Tree Contacts | Broken Branch | X26938 opened to replace service to 1869 Kilborn damaged by fallen tree branch. Transformer switch also replaced. 11 customers affected. Playfair AJ04. | None | None | 11 | 90 | 16 | East | AJ04
136430 | 2017-08-13 | Scheduled Outage | Vegetation Management | Crew isolated o/h line from S24297 to allow Forestry Crew to remove large limb off secondary. | None | None | 44 | 53 | 39 | Central | TR3UY
136431 | 2017-08-13 | Scheduled Outage | Maintenance | X49235 at St Laurent & Susan opened to repair secondary damaged by tree branch. 5 customers affected. Urbandale AE05. | None | None | 5 | 10 | 1 | East | AE05
136432 | 2017-08-13 | Scheduled Outage | Vegetation Management | TR3UY overhead circuit opened at S21583, to allow Forestry Crew to remove large tree off secondary bus. | None | None | 16 | 30 | 8 | Central | TR3UY
136433 | 2017-08-13 | Scheduled Outage | Maintenance | X32331 at 1355 Raven opened to replace defective switch & lead. 10 customera affected. Shillington AD05. | None | Fused Cutout | 10 | 45 | 8 | Central | AD05
136435 | 2017-08-13 | Scheduled Outage | Maintenance | X31652 at 133 Fentiman opened to replace secondary connections. 5 customers affected. Riverdale SR07. | Secondary \ Service | O/H Service | 5 | 23 | 2 | Central | SR07
136436 | 2017-08-13 | Defective Equipment | Electrical Failure | At 7:39 SCADA indicates a Auto-Reclose on the ELW05 affecting 1139 momentarily and 58 customers remained out. Crews found flash marks at SC29 and blown fuses on Darlington Pvt and isolated a defective cable. Elwood (ELW05) | U/G Switchgear | Unknown \ Other | 58 | 180 | 174 | East | ELW05
136438 | 2017-08-13 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact caused overhead transformer X35632 at 111 Scrivens to open. 16 customers affected. Lincoln. TD12 | O/H Switchgear | Fused Cutout | 16 | 53 | 14 | Central | TD12
136439 | 2017-08-14 | Scheduled Outage | Vegetation Management | Davey Tree trimming in the rear of 19, 35, 41, 43, 45 Oakridge. | None | None | 50 | 356 | 297 | East | ELW03
136440 | 2017-08-14 | Scheduled Outage | Maintenance | isolated transformer x32548 to replace switch and arrester | None | None | 8 | 56 | 7 | Central | TD06
136441 | 2017-08-14 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMERS X38568 AND X32593 TO TRANSFER HYDRO PLANT | None | None | 12 | 95 | 19 | Central | TD06
136442 | 2017-08-14 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32534 TO REPLACE SWITCH AND ARRESTER | None | None | 6 | 25 | 2 | Central | TD06
136444 | 2017-08-14 | Scheduled Outage | Maintenance | Transformer TP11032 isolated to allow contractor to terminate and connect new secondary cables. | None | None | 1 | 302 | 5 | South | FAL01
136445 | 2017-08-14 | Scheduled Outage | Construction | Transformer #X14728 isolated by crew to make area safe for Bell to work | None | None | 7 | 15 | 2 | East | LTM04
136446 | 2017-08-14 | Scheduled Outage | Construction | P53 isolated to allow crew to plant new pole and move phases. | None | None | 1 | 149 | 2 | Central | AK05
136447 | 2017-08-14 | Scheduled Outage | Vegetation Management | S28321 to EOL was isolated to allow contractor to remove tree off the primary and crew to repair downed primary phase at 17 Fairhaven. Langs (AP04) | None | O/H Conductor | 36 | 140 | 84 | East | AP04
136448 | 2017-08-15 | Scheduled Outage | Vegetation Management | S14963 to EOL isolated for tree trimminga affecting 19 customers. Epworth DS (EPWF1). | None | None | 19 | 333 | 105 | South | EPWF1
136449 | 2017-08-15 | Scheduled Outage | Construction | Replace kiosk with minipad transformer. KT613 removed and new TP11933 installed. | None | None | 17 | 163 | 46 | Central | TH15
136450 | 2017-08-15 | Scheduled Outage | Construction | KT393 removed and replaced with TP12080 75 mva transformer. | None | None | 18 | 146 | 44 | East | 2204
136451 | 2017-08-15 | Scheduled Outage | Construction | TX 3691 replaced, affecting 12 customers. Beaverbrook DS (24F8) | None | Padmount (1ph) | 12 | 127 | 25 | West | 24F8
136452 | 2017-08-15 | Scheduled Outage | Construction | Scott Barkley and crew to install S26379. In doing so will have transformers X32549 and X32074 open. Customers notified. | None | None | 28 | 116 | 54 | Central | TD06
136454 | 2017-08-15 | Scheduled Outage | Construction | Scott Barkley and crew to have switch S27798 open to replace porcelin insulators. Customers notified. | None | None | 14 | 78 | 18 | Central | TD06
136455 | 2017-08-15 | Scheduled Outage | Vegetation Management | S19799W phase to EOL was isolated to allow forestry crew to remove fallen tree on O/H primary at rear of 45 Bullock. Riverdale (SR04) | None | None | 38 | 77 | 49 | Central | SR04
136456 | 2017-08-16 | Scheduled Outage | Construction | Replace transformer. | None | None | 9 | 73 | 11 | East | 77M6
136457 | 2017-08-16 | Scheduled Outage | Construction | Adam Mcnulty and crew to have transformer X32538 open to replace the fused cut out switch. Customers notified. | None | None | 7 | 28 | 3 | Central | TD06
136459 | 2017-08-16 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 22 | 12 | 4 | Central | UV05
136460 | 2017-08-16 | Scheduled Outage | Construction | Radial section from X3969 isolated yo replace pole, affecting 2 customers. Jockvale DS (145F3). | None | None | 2 | 65 | 2 | South | 145F3
136461 | 2017-08-16 | Scheduled Outage | Construction | Transformer #X35475 isolated by crew to reconnect service. Evan Cowell was the crew | None | None | 7 | 60 | 7 | Central | UL06
136463 | 2017-08-17 | Unknown/Other | Unknown | Transformer fuse X30041 at 98 Paterson opened, no cause found. 8 customers affected. Bronson (SB02) | O/H Switchgear | Fused Cutout | 8 | 82 | 11 | Central | SB02
136464 | 2017-08-17 | Scheduled Outage | Construction | At 7:58am crew isolated a section of AP02 to reconfigure overhead. 2 customers affected. Langs Road (AP02) | None | None | 1 | 92 | 2 | East | AP02
136464 | 2017-08-17 | Scheduled Outage | Construction | At 7:58am crew isolated a section of AP02 to reconfigure overhead. 2 customers affected. Langs Road (AP02) | None | None | 2 | 240 | 8 | East | AP02
136465 | 2017-08-17 | Scheduled Outage | Construction | crew opened overhead switch S25943 feeding two customers to install new temporary switch to replace rotten pole with switch S25943. 2 customers affected. Beckwith (BECKF2) | None | None | 2 | 126 | 4 | West | BECKF2
136466 | 2017-08-17 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32547 TO REPLACE SWITCH AND ARRESTER | None | None | 7 | 46 | 5 | Central | TD06
136467 | 2017-08-17 | Scheduled Outage | Construction | Transformer KT466 at 1001 QUEEN ELIZABETH DRIVEWAY was isolated by the crew to allow them to replace the transformer affecting 1 customer on the 303 circuit for 167 min. | None | None | 1 | 167 | 3 | Central | 303
136469 | 2017-08-17 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32535 TO REPLACE SWICH AND ARRESTER | None | None | 4 | 50 | 3 | Central | TD06
136470 | 2017-08-17 | Scheduled Outage | Vegetation Management | crew isolated overhead section from switch S369 to end of line to trim trees. 40 customers were affected. Stafford. 200F1 | None | None | 40 | 274 | 183 | South | 200F1
136471 | 2017-08-17 | Defective Equipment | Electrical Failure | G223 B opened due to a cable fault. 250 customers affected. Startop (6F10) | U/G Cable | XLPE | 60 | 18 | 18 | East | 6F10
136471 | 2017-08-17 | Defective Equipment | Electrical Failure | G223 B opened due to a cable fault. 250 customers affected. Startop (6F10) | U/G Cable | XLPE | 68 | 40 | 45 | East | 6F10
136471 | 2017-08-17 | Defective Equipment | Electrical Failure | G223 B opened due to a cable fault. 250 customers affected. Startop (6F10) | U/G Cable | XLPE | 83 | 121 | 167 | East | 6F10
136472 | 2017-08-17 | Defective Equipment | Defective Equipment/ Material | Defective transformer. On-Call crew called in to replace transformer X24104. | O/H Transformer | O/H Transformer (1ph) | 7 | 467 | 54 | East | LMBF5
136473 | 2017-08-18 | Defective Equipment | Imminent Failure | ISOLATED AND REPLACED TRANSFORMER NPTE823 DUE TO OIL LEAK | U/G Transformer | Padmount (1ph) | 9 | 120 | 18 | South | 84F5
136474 | 2017-08-19 | Foreign Interference | Wildlife (Bird/Animal) | The TW12 and TW18 CB circuit breakers tripped due to animal contact at S11651 at 2161 Navaho. Woodroffe (TW12, TW18) | O/H Switchgear | Load Break Gang | 562 | 17 | 159 | Central | TW12
136474 | 2017-08-19 | Foreign Interference | Wildlife (Bird/Animal) | The TW12 and TW18 CB circuit breakers tripped due to animal contact at S11651 at 2161 Navaho. Woodroffe (TW12, TW18) | O/H Switchgear | Load Break Gang | 1333 | 19 | 422 | Central | TW18
136475 | 2017-08-19 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact at 969 Bronson caused the S19847 R phase to ope. Crew also found the box switch to be defective and had to be replaced. Riverdale (TR09) | O/H Switchgear | Fused Cutout | 29 | 271 | 131 | Central | TR09
136478 | 2017-08-19 | Tree Contacts | Broken Branch | Tree limb feel on O/H primary and broke pole insulator causing the S23042 to open. | Pole Attachement | Insulator | 15 | 254 | 64 | South | EPWF3
136480 | 2017-08-20 | Scheduled Outage | Construction | A section of primary overhead on Hawthorne Rd was isolated to replace poles and transfer plant affecting 3 customers. Leitrim 249F4 | None | None | 3 | 600 | 30 | East | LTM04
136481 | 2017-08-20 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One when the breaker tripped at the station when the 48M1-M4 switch was closed the 48M1 and 48M4 both tripped affecting 1507 customers. Hawthorn 48M4 | None | None | 1507 | 4 | 100 | East | 48M4
136482 | 2017-08-21 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 38 | 347 | 220 | South | EPWF6
136483 | 2017-08-21 | Defective Equipment | Corrosion | Transformer K406 secondary was isolated to allow crew to replace pedastal. Albion (UA04) | Secondary \ Service | Secondary Pedestal | 20 | 186 | 62 | East | UA04
136484 | 2017-08-21 | Defective Equipment | Mechanical Failure | UC05 O/H section from S22991 to Clyde substation was isolated to allow crew to repair defective O/H conductor at Garfield and Ridell. Clyde (UC05) | O/H Conductor | O/H Conductor | 167 | 34 | 95 | Central | UC05
136485 | 2017-08-21 | Scheduled Outage | Construction | Evan Cowell and crew to have transformer X33097 open to install a new service. Customers notified. | None | None | 9 | 78 | 12 | Central | TD07
136486 | 2017-08-21 | Scheduled Outage | Construction | Dave Burns and crew to have transformer X31362 open to rearrange secondaries and plant. Customers notified. | None | None | 6 | 144 | 14 | Central | AK05
136487 | 2017-08-22 | Scheduled Outage | Vegetation Management | Large limb removal. | None | None | 14 | 75 | 18 | South | EPWF1
136489 | 2017-08-22 | Defective Equipment | Mechanical Failure | S15922 Blue Phase lead broke lose from the overhead | O/H Conductor | O/H Conductor | 607 | 89 | 900 | West | JKGF4
136491 | 2017-08-22 | Lightning | Lightning | Adverse weather- Lightning storm and hail storm | None | None | 1 | 10 | 0 | South | FAL04
136494 | 2017-08-22 | Loss Of Supply | Transmission Inadvertent | Adverse weather- Lightning storm and hail storm caused A3RM to auto reclose & trip. Due to this circuit being in abnormal configuration, Hydro One was forced to restore the circuit and the resulting Hydro Ottawa load in sections. | None | None | 6822 | 5 | 568 | South | A3RM (Merivale MTS - T1)
136494 | 2017-08-22 | Loss Of Supply | Transmission Inadvertent | Adverse weather- Lightning storm and hail storm caused A3RM to auto reclose & trip. Due to this circuit being in abnormal configuration, Hydro One was forced to restore the circuit and the resulting Hydro Ottawa load in sections. | None | None | 7141 | 2 | 238 | South | A3RM (Merivale MTS - T1)
136494 | 2017-08-22 | Loss Of Supply | Transmission Inadvertent | Adverse weather- Lightning storm and hail storm caused A3RM to auto reclose & trip. Due to this circuit being in abnormal configuration, Hydro One was forced to restore the circuit and the resulting Hydro Ottawa load in sections. | None | None | 29952 | 2 | 998 | South | A3RM (Merivale MTS - T1)
136495 | 2017-08-22 | Lightning | Lightning | Thunder Storm and lightening | O/H Switchgear | Inline Switch | 11 | 152 | 28 | West | RHNF1
136497 | 2017-08-22 | Lightning | Lightning | Adverse weather-lightning and hail storm | None | None | 4052 | 3 | 203 | East | 249F2
136498 | 2017-08-22 | Scheduled Outage | Vegetation Management | Mark Brown and Dave MacDonald to have transformer X37115 open to replace and triplex taken down by trees. Customers notified. | None | None | 4 | 21 | 1 | South | EPWF6
136499 | 2017-08-22 | Scheduled Outage | Maintenance | To allow Hydro Ottawa line crews to replace a damaged transformer | None | Padmount (1ph) | 3 | 46 | 2 | East | 249F2
136501 | 2017-08-22 | Lightning | Lightning | Thunder storm caused a loss of supply to Casselman MS | O/H Conductor | O/H Conductor | 506 | 2 | 17 | East | V11F1
136501 | 2017-08-22 | Lightning | Lightning | Thunder storm caused a loss of supply to Casselman MS | O/H Conductor | O/H Conductor | 600 | 2 | 20 | East | V11F2
136501 | 2017-08-22 | Lightning | Lightning | Thunder storm caused a loss of supply to Casselman MS | O/H Conductor | O/H Conductor | 600 | 2 | 20 | East | V11F3
136502 | 2017-08-22 | Scheduled Outage | Maintenance | To allow Hydro Ottawa and Drain-All crews to clean up a leaking transformer | None | Padmount (1ph) | 13 | 224 | 49 | Central | TD12
136503 | 2017-08-22 | Adverse Weather | Extreme Wind | crew replaced broken hydro pole at switch S23347 on Deniverville pvt.. One customer was affected. Uplands (4801F8) | Pole | Pole | 1 | 571 | 10 | East | 4801F8
136504 | 2017-08-22 | Scheduled Outage | Vegetation Management | Crew isolated JKGF4 section from switch S22270 to end of line to remove tree from overhead circuit at 107 Brae. 83 customers were affected. Janet King (44F3) | None | None | 83 | 55 | 76 | West | 44F3
136505 | 2017-08-23 | Scheduled Outage | Vegetation Management | Tree Trimming at the rear of 24 Lynhar affecting 62 customers on the Stafford Road 200F2 | None | None | 62 | 366 | 378 | South | 200F2
136506 | 2017-08-23 | Scheduled Outage | Construction | Setting Poles on Wingate affecting 13 customers on the Russell TB06 | None | None | 13 | 211 | 46 | East | TB06
136508 | 2017-08-23 | Scheduled Outage | Construction | Changeout livefront transformers and install new cables. | None | Kiosk (1ph) | 38 | 491 | 311 | South | 170F1
136510 | 2017-08-23 | Scheduled Outage | Construction | Rotten pole change | None | None | 1 | 376 | 6 | West | 28F3
136511 | 2017-08-23 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33107 (RACOON CONTACFT) | O/H Transformer | O/H Transformer (1ph) | 12 | 72 | 14 | Central | TD05
136512 | 2017-08-24 | Tree Contacts | Falling Tree | Broken span guy cause by fallen tree at Finlay and Torrington caused switch S10936 to open. Riverdale (TR09) | O/H Switchgear | Inline Switch | 74 | 84 | 104 | Central | TR09
136513 | 2017-08-24 | Scheduled Outage | Construction | Install poles with crane. | None | None | 14 | 366 | 85 | East | TB15
136514 | 2017-08-24 | Scheduled Outage | Construction | TP12005 isolated for soil remendiation, affecting 6 customers. Merivale DS (72F1) | None | None | 6 | 355 | 36 | South | 72F1
136515 | 2017-08-24 | Scheduled Outage | Construction | Evan Cowell and crew to have transformer X30496 open for a service upgrade. Because this was an emergency as many customers as possible were notified. | None | None | 11 | 32 | 6 | Central | TH01
136516 | 2017-08-24 | Tree Contacts | Broken Branch | Switch at pole X14946 open for isolation to allow crew to replace down neutral conductor. Conductor broken earlier in week due to tree branch | O/H Conductor | O/H Conductor | 17 | 88 | 25 | East | UB04
136517 | 2017-08-24 | Human Element | Switching Error | power interupted to TP11049, TP11050 & TP11051 due to switching error at TP11049, crews closed elbow as per OTO 17-148548 but internal switch position was not verified, affecting 64 customers. Merivale (72F1) | None | None | 64 | 15 | 16 | South | 72F1
136521 | 2017-08-25 | Scheduled Outage | Vegetation Management | EPWF6 OH section from S10955 to EOL isolated for tree trimming, affecting 29 customers. Epworth DS | None | None | 29 | 320 | 155 | South | EPWF6
136522 | 2017-08-25 | Scheduled Outage | Construction | RHNF1 OH on Shea rd isolated for pole replacemment, affecting 6 customers. Richmond North DS (RHNF1). | None | None | 6 | 140 | 14 | West | RHNF1
136523 | 2017-08-25 | Defective Equipment | Mechanical Failure | Switch opened to allow crew to replace old and broken insulators. | Pole Attachement | Insulator | 34 | 102 | 58 | Central | TD06
136524 | 2017-08-25 | Scheduled Outage | Construction | TE2529 isolated and replaced defective transformer, affecting 11. Longfields DS (LGFF2) | None | None | 11 | 150 | 28 | South | LGFF2
136526 | 2017-08-27 | Defective Equipment | Mechanical Failure | A cable fault caused S23439 W phase to open. Power was restored in stages | U/G Cable | XLPE | 12 | 38 | 8 | West | MWDF2
136526 | 2017-08-27 | Defective Equipment | Mechanical Failure | A cable fault caused S23439 W phase to open. Power was restored in stages | U/G Cable | XLPE | 81 | 39 | 53 | West | MWDF2
136526 | 2017-08-27 | Defective Equipment | Mechanical Failure | A cable fault caused S23439 W phase to open. Power was restored in stages | U/G Cable | XLPE | 123 | 83 | 170 | West | MWDF2
136528 | 2017-08-27 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X35229 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 11 | 110 | 20 | West | JKGF5
136530 | 2017-08-28 | Scheduled Outage | Vegetation Management | At 08:30am EPWF1 between S205, S1487 and S301 was isolated for Tree Trimming. 62 customers affected. Epworth (EPWF1) | None | None | 62 | 357 | 369 | South | EPWF1
136531 | 2017-08-28 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE AT SWITCH S22324 FEEDING TRANSFORMER X36279 | O/H Switchgear | Fused Cutout | 1 | 173 | 3 | West | TFXF4
136532 | 2017-08-29 | Scheduled Outage | Maintenance | Isolation of 3 transformer in VT74 toallow station crew to adjust tap setting. | None | None | 1 | 115 | 2 | East | TO1UB
136534 | 2017-08-29 | Scheduled Outage | Construction | Transformer TP9007 @ 42 Brae Cre was isolated to allow the crew to replace badly rusted transformer and replace the base affecting 9 customers on the JKGF4 circuit for 293 minutes | None | None | 9 | 293 | 44 | West | JKGF4
136536 | 2017-08-29 | Scheduled Outage | Vegetation Management | Crew to have transformer GL004390 open to remove vines and fix burning switch. Unable to notify customers. | None | None | 2 | 27 | 1 | East | 56F1
136537 | 2017-08-30 | Defective Equipment | Electrical Failure | 77M2 defective underground cable cable, affecting 167 customers. Billberry MTS. | U/G Cable | XLPE | 167 | 170 | 473 | East | 77M2
136538 | 2017-08-30 | Scheduled Outage | Vegetation Management | A section of overhead line at 384 Halldon was isolated to trim trees. 17 customers affected. Lincoln TD06. | None | None | 17 | 286 | 81 | Central | TD06
136539 | 2017-08-30 | Defective Equipment | Mechanical Failure | While Hydro Ottawa line crews were taking down vines from the O/H, S751 broke & fell open | O/H Switchgear | Fused Cutout | 6 | 112 | 11 | South | 170F1
136540 | 2017-08-30 | Defective Equipment | Imminent Failure | To allow Hydro Ottawa line crews to change leaking transformers TP4980, TP4981 & TP4982 | U/G Transformer | Padmount (1ph) | 27 | 109 | 49 | East | LTM01
136541 | 2017-08-30 | Scheduled Outage | Construction | At 8:11pm TP2968 was isolated to change the supply. 1 customer affected. Janet King (JKGF4) | None | None | 1 | 143 | 2 | West | JKGF4
136542 | 2017-08-31 | Defective Equipment | Electrical Failure | At 4:12am a cable fault on a white phase cable section between TP7570 and TP7571 caused S13601 white phase to blow affecting 148 customers. Billberry (77M6) | U/G Cable | XLPE | 148 | 138 | 340 | East | 77M6
136543 | 2017-08-31 | Scheduled Outage | Maintenance | To allow Hydro Ottawa U/G crew to replace switches, arrestors & remove asbestos | None | None | 14 | 129 | 30 | East | AQ10
136544 | 2017-08-31 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry to clear trees from the O/H line | None | None | 4 | 264 | 18 | Central | TD06
136545 | 2017-08-31 | Scheduled Outage | Maintenance | Soil Remediation on TE1261 affecting 6 customers on the Barrhaven 140F5 | None | None | 6 | 437 | 44 | South | 140F5
136546 | 2017-08-31 | Scheduled Outage | Maintenance | Soil remediation at TP12099 on the Bridlewood BRDF3 affecting 11 customers | None | None | 11 | 577 | 106 | West | BRDF3
136547 | 2017-08-31 | Foreign Interference | Vehicle | MVA caused overhead line to slap together and blowing G739RW fuses. Crews open G739B to isolate overhead line to remove transport truck from hydro pole. | O/H Conductor | O/H Conductor | 170 | 66 | 187 | East | 4801F8
136547 | 2017-08-31 | Foreign Interference | Vehicle | MVA caused overhead line to slap together and blowing G739RW fuses. Crews open G739B to isolate overhead line to remove transport truck from hydro pole. | O/H Conductor | O/H Conductor | 259 | 62 | 268 | East | 4801F8
136548 | 2017-09-01 | Scheduled Outage | Construction | Transformer change at 890 Dynes affecting 3 customers on the AK07 out of Fisher | None | None | 3 | 80 | 4 | Central | AK07
136551 | 2017-09-02 | Foreign Interference | Wildlife (Bird/Animal) | Outage on transformer X32580 due to squirrel contact. Crews refused and closed. | O/H Switchgear | Fused Cutout | 11 | 78 | 14 | Central | TD01
136552 | 2017-09-03 | Defective Equipment | Mechanical Failure | S232299 found deteriated and broken apart, affecting 8 customers. Fisher DS (AK07) | O/H Switchgear | Inline Switch | 8 | 68 | 9 | Central | AK07
136553 | 2017-09-03 | Tree Contacts | Falling Tree | RX2007 blue phase tripped, cause unknown but suspect due to rainy weather, affecting 227 customers. Kanata DS (624F6) | O/H Conductor | O/H Conductor | 197 | 215 | 706 | West | 624F6
136553 | 2017-09-03 | Tree Contacts | Falling Tree | RX2007 blue phase tripped, cause unknown but suspect due to rainy weather, affecting 227 customers. Kanata DS (624F6) | O/H Conductor | O/H Conductor | 227 | 54 | 204 | West | 624F6
136554 | 2017-09-04 | Tree Contacts | Falling Tree | Fallen tree on the overhead, | None | None | 129 | 82 | 176 | South | 180F3
136554 | 2017-09-04 | Tree Contacts | Falling Tree | Fallen tree on the overhead, | None | None | 349 | 83 | 483 | South | 180F3
136554 | 2017-09-04 | Tree Contacts | Falling Tree | Fallen tree on the overhead, | None | None | 1031 | 4 | 69 | South | 180F1
136555 | 2017-09-04 | Foreign Interference | Wildlife (Bird/Animal) | Animal interference (squirrel) caused transformer X31497 to open. Crews refused and restored. | O/H Switchgear | Fused Cutout | 9 | 79 | 12 | Central | TH15
136557 | 2017-09-04 | Defective Equipment | Mechanical Failure | A hotline clamp that burned up caused the primary conductor to come down. | O/H Conductor | O/H Conductor | 54 | 104 | 94 | Central | TD05
136558 | 2017-09-05 | Scheduled Outage | Construction | A transformer at Echo and Evelyn was isolated to replace a transformer affecting 1 customer. Riverdale SR01 | None | None | 1 | 180 | 3 | Central | SR01
136559 | 2017-09-04 | Foreign Interference | Wildlife (Bird/Animal) | animal contact to X48613 | O/H Transformer | O/H Transformer (1ph) | 14 | 147 | 34 | Central | TW18
136560 | 2017-09-05 | Loss Of Supply | Transmission Inadvertent | The South March A9T1 transformer tripped under diferential due to defective W phase insulator on the A9M3-L at South March TS and caused the A9M2, M3 and M5 circuits to trip. | None | None | 930 | 78 | 1209 | West | M32S (South March TS - T1)
136560 | 2017-09-05 | Loss Of Supply | Transmission Inadvertent | The South March A9T1 transformer tripped under diferential due to defective W phase insulator on the A9M3-L at South March TS and caused the A9M2, M3 and M5 circuits to trip. | None | None | 936 | 1 | 16 | West | M32S (South March TS - T1)
136560 | 2017-09-05 | Loss Of Supply | Transmission Inadvertent | The South March A9T1 transformer tripped under diferential due to defective W phase insulator on the A9M3-L at South March TS and caused the A9M2, M3 and M5 circuits to trip. | None | None | 3129 | 6 | 313 | West | M32S (South March TS - T1)
136561 | 2017-09-05 | Scheduled Outage | Maintenance | Asbestos removal and insulator replacement at K761 affecting 11 customers on the McCarthy AQ07 red phase | None | None | 11 | 124 | 23 | East | AQ07
136562 | 2017-09-05 | Scheduled Outage | Construction | BRDF5 O/H from S16789 to S12675 was isolated to allow crew to replace riser S21626 on Rothesay Dr. Brildewood (BRDF5) | None | None | 62 | 312 | 322 | West | BRDF5
136563 | 2017-09-05 | Scheduled Outage | Construction | A section of primary overhead on Highgate was isolated for pole replacement in backyards affecting 82 customers. Woodroffe TW17 | None | None | 28 | 71 | 33 | Central | TW17
136563 | 2017-09-05 | Scheduled Outage | Construction | A section of primary overhead on Highgate was isolated for pole replacement in backyards affecting 82 customers. Woodroffe TW17 | None | None | 82 | 194 | 265 | Central | TW17
136564 | 2017-09-05 | Scheduled Outage | Construction | Transformer #X29550 isolated by crew to install new U/G service | None | None | 12 | 30 | 6 | East | UG02
136565 | 2017-09-05 | Defective Equipment | Electrical Failure | S153 at 1 Laser St was isolated to allow crew to make repairs to defective switch termination. Rideau Heights (180F3) | O/H Switchgear | Inline Switch | 9 | 110 | 16 | South | 180F3
136566 | 2017-09-05 | Foreign Interference | Other Utilities | Truck pull the Bell communcation wire at 139 Cutris and caused overhead line to slap together and blowing G739RB fuses. Uplands (4801F8) | None | None | 460 | 104 | 797 | East | 4801F8
136568 | 2017-09-06 | Scheduled Outage | Vegetation Management | A section of primary overhead on Skuce Prvt was isolated for tree trimming affecting 17 customers. Lincoln Heights TD14 | None | None | 17 | 277 | 78 | Central | TD14
136569 | 2017-09-06 | Scheduled Outage | Construction | A transformer at 3225 Uplands was isolated to replace the transformer affecting 22 customers McCartthy AQ07 | None | None | 22 | 296 | 109 | East | AQ07
136570 | 2017-09-06 | Scheduled Outage | Construction | A section of primary overhead at Prince of Wales at Maryland was isolated to transfer plant to new poles affecting 43 customers. Fisher AK05 | None | None | 43 | 307 | 220 | Central | AK05
136571 | 2017-09-06 | Scheduled Outage | Maintenance | Transformer TP8143 at 6565 Morningview was isolated to allow crew to perfrom soil remediation. Billberry (77M2) | None | None | 10 | 399 | 66 | East | 77M2
136572 | 2017-09-06 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X33397 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 8 | 104 | 14 | South | 190F2
136573 | 2017-09-06 | Foreign Interference | Wildlife (Bird/Animal) | The 7F1 CB auto reclosed due to animal contact at 556 River Rd. Crew found blown cut out at transformer 2688 caused by animal contact. Limebank (7F1) | O/H Switchgear | Fused Cutout | 1 | 136 | 2 | East | 7F1
136574 | 2017-09-06 | Scheduled Outage | Construction | Transformer #X37108 isolated by crew to remove the service. Bobby from Sproule | None | None | 5 | 15 | 1 | South | EPWF2
136576 | 2017-09-06 | Scheduled Outage | Maintenance | Transformer #x3626 isolated by crew to replace connections in the transformer | None | None | 1 | 55 | 1 | South | 200F1
136577 | 2017-09-07 | Scheduled Outage | Maintenance | K724, K725, K726 & K727 at 3225 Uplands isolated to remove asbestos, replace insulators & arrestors. 21 customers affected. McCarthy AQ07. | None | None | 21 | 113 | 40 | East | AQ07
136578 | 2017-09-07 | Defective Equipment | Mechanical Failure | TRANSFORMER TP5551 ISOLATED TO ALLOW CREW TO REPLACE LEAKING TRANSFORMER. | U/G Transformer | Padmount (1ph) | 12 | 91 | 18 | East | LTM01
136579 | 2017-09-07 | Defective Equipment | Mechanical Failure | TP5557 at 711 White Alder was isolated to allow crews to replace it due to an oil leak. 14 customers affected. Leitrim (249F1) | U/G Transformer | Padmount (1ph) | 14 | 53 | 12 | East | LTM01
136580 | 2017-09-07 | Tree Contacts | Falling Tree | Merivale 72F4 auto reclosed. S501 blew causing outage to customers on Vaan Drive/Rongail area. Tree on Line at Vaan Drive S of Pineland. | O/H Conductor | O/H Conductor | 77 | 85 | 109 | South | 72F4
136581 | 2017-09-07 | Lightning | Lightning | Crew found blown arrestors at Walkley and Anand Road causing ELW09 to auto reclose and UZ11, UZ00 and TA10 breakers to trip. | None | None | 635 | 39 | 413 | East | UZ11
136581 | 2017-09-07 | Lightning | Lightning | Crew found blown arrestors at Walkley and Anand Road causing ELW09 to auto reclose and UZ11, UZ00 and TA10 breakers to trip. | None | None | 2142 | 3 | 107 | East | TA1UZ
136583 | 2017-09-07 | Lightning | Lightning | 145F3 circuit opened under hold off protection during adverse weather. 362 customers affected. Jockvale (145F3) | O/H Conductor | O/H Conductor | 362 | 11 | 66 | South | 145F3
136586 | 2017-09-07 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X29521 FOR A SERVICE UP-GRADE | None | None | 6 | 63 | 6 | East | AA05
136588 | 2017-09-07 | Lightning | Lightning | REPLACED TRANSFORMER X33656 HIT BY LIGHTNING | O/H Transformer | O/H Transformer (1ph) | 11 | 343 | 63 | Central | TD01
136590 | 2017-09-08 | Scheduled Outage | Vegetation Management | A section of overhead line on Lepage west of Cavan was isolated for tree trimming. 40 customers affected. Shillington AD03. | None | None | 40 | 120 | 80 | Central | AD03
136591 | 2017-09-08 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X47957 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 20 | 61 | 20 | Central | TW18
136592 | 2017-09-08 | Defective Equipment | Electrical Failure | BRDF5 tripped under hold off. Line restored after hold off cleared, S21647 found open. Cable fault was found | U/G Cable | XLPE | 116 | 19 | 37 | West | BRDF5
136592 | 2017-09-08 | Defective Equipment | Electrical Failure | BRDF5 tripped under hold off. Line restored after hold off cleared, S21647 found open. Cable fault was found | U/G Cable | XLPE | 129 | 156 | 335 | West | BRDF5
136592 | 2017-09-08 | Defective Equipment | Electrical Failure | BRDF5 tripped under hold off. Line restored after hold off cleared, S21647 found open. Cable fault was found | U/G Cable | XLPE | 887 | 21 | 310 | West | BRDF5
136593 | 2017-09-08 | Tree Contacts | Tree Growth/ Untrimmed Tree | S14325 at 5957 Fernbank opened due to tree contact on customer owned primary. 1 customer affected. Terry Fox (TFXF4) | O/H Conductor | O/H Conductor | 1 | 95 | 2 | West | TFXF4
136597 | 2017-09-10 | Scheduled Outage | Construction | To transfer riser to new hydro pole. | None | Termination \ Stress Cone | 1 | 397 | 7 | South | 200F6
136598 | 2017-09-11 | Defective Equipment | Mechanical Failure | A transformer at 26 Wigan was opened to repair a sparking secondary connections affecting 10 customers. Parkwood Hills 190F5 | Secondary \ Service | O/H Service | 10 | 51 | 8 | South | 190F5
136599 | 2017-09-11 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X34081 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 9 | 180 | 27 | Central | SH07
136600 | 2017-09-11 | Scheduled Outage | Construction | ISOLATED 4 TRANSFORMERS X30312 X30311 X30310 AND X30309 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 45 | 240 | 180 | Central | UF08
136601 | 2017-09-11 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X26657 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 20 | 300 | 100 | Central | SH07
136602 | 2017-09-11 | Scheduled Outage | Vegetation Management | Tree trimming. | None | None | 20 | 312 | 104 | South | EPWF1
136603 | 2017-09-12 | Defective Equipment | Mechanical Failure | padmount transformer TP8948 at 112 rothesay was isolated for soil remediation. 9 customers were affected. Terry fox (TFXF5) | U/G Transformer | Padmount (1ph) | 9 | 649 | 97 | West | TFXF5
136604 | 2017-09-12 | Defective Equipment | Mechanical Failure | Transformer TE1702 @ 6 Conover was isolated to allow the crew make repairs to heated secondaries and bare cables affecting 11 customers on the 84F2 circuit for 163 minutes. | Secondary \ Service | U/G Service | 11 | 163 | 30 | South | 84F2
136605 | 2017-09-12 | Scheduled Outage | Maintenance | Transformer TE2528 @ 8 Shannon was isolated to allow the crew to replace the elbows and inspect the bushing on the LGFF2 circuit affecting 10 customers for 125 min | None | None | 10 | 125 | 21 | South | LGFF2
136607 | 2017-09-12 | Scheduled Outage | Maintenance | At 9:08am K729 and K730 were isolated to allow crew to replace insulators. 53 customers affected. McCarthy (AQ07) | None | None | 53 | 79 | 70 | East | AQ07
136608 | 2017-09-12 | Scheduled Outage | Construction | At 9:16am KT632 was isolated to allow crew to replace it. 5 customers affected. Lincoln Heights (TD01) | None | None | 5 | 270 | 22 | Central | TD01
136609 | 2017-09-12 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X36408 opened up due to tree contact | O/H Switchgear | Fused Cutout | 1 | 105 | 2 | South | 72F4
136610 | 2017-09-12 | Defective Equipment | Electrical Failure | TH04 CB opened due to, blown pothead on SH3UJ-L1 at VT310 51 customers affected. Hincehy (4301) | U/G Cable Attachement | Pothead | 51 | 58 | 49 | Central | 4301
136611 | 2017-09-12 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X38062 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 8 | 97 | 13 | Central | 503
136612 | 2017-09-13 | Scheduled Outage | Construction | Bobby McNab from Sproule powerlines to have transformer X33591 open to remove a service. Customers notified. | None | None | 6 | 8 | 1 | Central | AK03
136613 | 2017-09-13 | Scheduled Outage | Vegetation Management | switch S24249 was opened to isolate overhead line to remove dead tree with crane at the rear of 405 donald. 52 customers were affected. Overbrook (SO12) | None | None | 52 | 208 | 180 | East | SO12
136614 | 2017-09-13 | Foreign Interference | Wildlife (Bird/Animal) | Field Operators on site believe outage due to overgrown vines or animal contact. Refused and restored transformer X33411. | O/H Switchgear | Fused Cutout | 9 | 70 | 10 | Central | TW22
136615 | 2017-09-13 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X3711 TO TRANSFER SECONDARY SERVICE TO MID SPAN CONNECTION | None | None | 1 | 120 | 2 | South | 145F3
136616 | 2017-09-13 | Scheduled Outage | Construction | Sproule powerlines to have transformers X30315, X30314, and X30315 open to move customers to new equipment on new poles. Customers notified. Transformers have been replaced with two new transformers X56373 and X56371. | None | None | 29 | 206 | 100 | Central | UF08
136617 | 2017-09-13 | Defective Equipment | Mechanical Failure | Transformer TE917 @ 1374 Bethamy was isolated by the crew to allow them to replace a leaking transformer on the 8F1 circuit affecting 14 customers for 96 minutes | U/G Transformer | Padmount (1ph) | 14 | 96 | 22 | East | 8F1
136618 | 2017-09-13 | Tree Contacts | Broken Branch | ISOLATED TRANSFORMER X23576 TO REMOVE A BRORKEN TREE BRANCH FROM THE PRIMARY AND SECONDARY BUSS | None | None | 5 | 39 | 3 | East | UG07
136621 | 2017-09-14 | Scheduled Outage | Construction | Transformer X3969 at 4750 Fallowfield was isolated to allow crew to replace transformer and reframe pole. Jockvale (145F3) | None | None | 2 | 363 | 12 | South | 145F3
136622 | 2017-09-14 | Defective Equipment | Mechanical Failure | Transformer TE823 at 1 banner was isolated to allow crew to replace transformer and remediate soil. Manordale (84F5) | U/G Transformer | Padmount (1ph) | 9 | 340 | 51 | South | 84F5
136623 | 2017-09-14 | Scheduled Outage | Maintenance | planned outage to remove asbestos barrier boards and change insulators | None | None | 14 | 100 | 23 | East | AQ07
136624 | 2017-09-14 | Scheduled Outage | Construction | S666 to EOL was isolated to allow crew to transfer plant to new pole and tree trimming on Harrison St. Manordale (84F5) | None | None | 35 | 7 | 4 | South | 84F5
136626 | 2017-09-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30305 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 18 | 93 | 28 | Central | UF07
136627 | 2017-09-14 | Scheduled Outage | Construction | Transformer 5945B at 6 Amundsen was isolated to allow crew to replace transformer. Beaverbrook (24F8) | None | None | 4 | 396 | 26 | West | 24F8
136628 | 2017-09-14 | Scheduled Outage | Construction | S666 to EOL was isolated to allow crew to transfer plant to new pole and tree trimming on Harrison St. Manordale (84F5) | None | None | 35 | 238 | 139 | South | 84F5
136629 | 2017-09-14 | Defective Equipment | Defective Equipment/ Material | S1538 B phase blew to defective lightning arrestor. 145F4 CB was open for crew's safety to allow crew to safley remove the defective lighning arrestor. Jockvale (145F4) | Pole Attachement | Arrester | 45 | 60 | 45 | South | 145F4
136629 | 2017-09-14 | Defective Equipment | Defective Equipment/ Material | S1538 B phase blew to defective lightning arrestor. 145F4 CB was open for crew's safety to allow crew to safley remove the defective lighning arrestor. Jockvale (145F4) | Pole Attachement | Arrester | 1168 | 3 | 58 | South | 145F4
136631 | 2017-09-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32802 FOR A SERVICE UP-GRADE | None | None | 9 | 20 | 3 | Central | TW22
136632 | 2017-09-14 | Scheduled Outage | Vegetation Management | planned outage for tree trimming | None | None | 46 | 339 | 260 | Central | TW22
136633 | 2017-09-15 | Scheduled Outage | Vegetation Management | planned outage for tree trimming | None | None | 54 | 319 | 287 | Central | TW22
136634 | 2017-09-15 | Unknown/Other | Unknown | The 22M28 circuit tripped while under hold off. Circuit was patrolled and nothing was found, cause remains under investigation | None | None | 1 | 27 | 0 | South | 22M28
136634 | 2017-09-15 | Unknown/Other | Unknown | The 22M28 circuit tripped while under hold off. Circuit was patrolled and nothing was found, cause remains under investigation | None | None | 2 | 28 | 1 | South | 22M28
136634 | 2017-09-15 | Unknown/Other | Unknown | The 22M28 circuit tripped while under hold off. Circuit was patrolled and nothing was found, cause remains under investigation | None | None | 1193 | 34 | 676 | South | 22M28
136634 | 2017-09-15 | Unknown/Other | Unknown | The 22M28 circuit tripped while under hold off. Circuit was patrolled and nothing was found, cause remains under investigation | None | None | 2960 | 8 | 395 | South | 22M28
136636 | 2017-09-15 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33699 TO INSTALL NEW SECONDARY SERVICE | None | None | 8 | 56 | 7 | Central | UL04
136637 | 2017-09-15 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X39534 TO INSATLL A NEW SECONDARY SERVICE | None | None | 4 | 29 | 2 | South | 47F3
136640 | 2017-09-17 | Scheduled Outage | Construction | At 6:40am K1196 and K1197 were isolated for and upgrade. 13 customers affected. Eastview (UT06) | None | None | 13 | 210 | 46 | East | UT06
136641 | 2017-09-18 | Foreign Interference | Wildlife (Bird/Animal) | Fields Ops responded to transformer outage call. Found a dead squirrel to have caused outage on transformer X48687. Refused and restored. | O/H Switchgear | Fused Cutout | 17 | 40 | 11 | Central | TW18
136642 | 2017-09-18 | Scheduled Outage | Vegetation Management | S936 to EOL isolated to allow forestry crew to trim trees in the rear of 24 Pritchard. | None | None | 37 | 257 | 158 | South | 170F1
136643 | 2017-09-18 | Defective Equipment | Mechanical Failure | G986 to EOL opened to repair downed phase. 1 customer affected. | O/H Conductor | O/H Conductor | 1 | 31 | 1 | East | 77M5
136644 | 2017-09-18 | Defective Equipment | Mechanical Failure | Crew replaced leaking transformer TE3448. | U/G Transformer | Padmount (1ph) | 11 | 138 | 25 | East | LMBF7
136645 | 2017-09-18 | Scheduled Outage | Construction | 3 transformers, X30316, X30317 and X30318 isolated by crew to upgrade plant | None | None | 41 | 365 | 249 | Central | UF08
136646 | 2017-09-18 | Foreign Interference | Wildlife (Bird/Animal) | REFUSED SWITCH FEEDING TRANSFORMER X35817 | None | None | 8 | 126 | 17 | South | 190F5
136647 | 2017-09-19 | Scheduled Outage | Construction | 4kv kiosk K277 at 960 Debra upgraded to padmount transformer, affecting 20 customers. Fisher (AK04) | None | Kiosk (1ph) | 20 | 218 | 73 | Central | AK04
136648 | 2017-09-19 | Scheduled Outage | Construction | TX 20114R at 48 Harry Douglas upgraded to ne TX, affecting 9 customers. Janet king DS (JKGF4). | None | None | 9 | 132 | 20 | West | JKGF4
136649 | 2017-09-19 | Scheduled Outage | Maintenance | Replace porcelin insulators, arrestors and remove asbestos. | None | None | 47 | 100 | 78 | East | AQ05
136651 | 2017-09-19 | Scheduled Outage | Vegetation Management | S28196 to EOL isolated for tree trimming at 2428 Rector, affecting 17 customers. Edwin (UV05). | None | None | 17 | 320 | 91 | Central | UV05
136653 | 2017-09-19 | Scheduled Outage | Construction | Sproule powerlines to have transformer X36023 open to install a new secondary triplex. Customers notified. | None | None | 15 | 20 | 5 | South | EPWF1
136654 | 2017-09-19 | Defective Equipment | Mechanical Failure | Replaced leaking transformer, TP8116, affecting 11 customers. Bilberry TS (77M6) | U/G Transformer | Padmount (1ph) | 11 | 384 | 70 | East | 77M6
136655 | 2017-09-20 | Tree Contacts | Broken Branch | Not yet known. | O/H Switchgear | Fused Cutout | 108 | 99 | 178 | Central | TD05
136656 | 2017-09-20 | Scheduled Outage | Construction | Pole replacement. | None | None | 51 | 505 | 429 | East | TB06
136657 | 2017-09-20 | Scheduled Outage | Vegetation Management | UV03 OH from S16744 to EOL was isolated to removes trees at 1200, 12024 and 1272 Placid, affecting 144 customers. Edwin DS (UV03). | None | None | 144 | 290 | 696 | Central | UV03
136658 | 2017-09-20 | Scheduled Outage | Construction | Replace transformer and base | None | None | 0 | 52 | 0 | East | TO2UB
136658 | 2017-09-20 | Scheduled Outage | Construction | Replace transformer and base | None | None | 26 | 10 | 4 | East | TO2UB
136658 | 2017-09-20 | Scheduled Outage | Construction | Replace transformer and base | None | None | 26 | 126 | 55 | East | TO2UB
136660 | 2017-09-20 | Scheduled Outage | Construction | Sproule powerlines to have transformer X36016 open to install a new secondary service. Customers notified. | None | None | 4 | 30 | 2 | South | EPWF1
136661 | 2017-09-20 | Scheduled Outage | Construction | Reframe pole from single circuit to double circuit. | None | None | 1 | 311 | 5 | South | 145F3
136662 | 2017-09-20 | Defective Equipment | Mechanical Failure | Transformer replacement and soil remediation. | U/G Transformer | Padmount (1ph) | 12 | 464 | 93 | South | 84F3
136663 | 2017-09-21 | Scheduled Outage | Construction | Sproule crew to have transformer X31849 open to install a new secondary service. Customers notified. | None | None | 17 | 17 | 5 | Central | UL06
136664 | 2017-09-21 | Scheduled Outage | Construction | Transformer 20133 at 49 Granite Ridge was isolated by the crew to allow them to replace the rusted out u/g transformer affecting 7 customers on the JKGF4 circuit for 129 min. | None | None | 7 | 129 | 15 | West | JKGF4
136665 | 2017-09-21 | Scheduled Outage | Maintenance | At 9:00am K90 and K107 were isolated to allow crew to replace blown arrestors, remove asbestos. 33 customers affected. McCarthy (AQ05) | None | None | 33 | 83 | 46 | East | AQ05
136666 | 2017-09-21 | Scheduled Outage | Construction | Sproule crew to have transformer X30307 open to rearrange secondaries. Customers notified. | None | None | 11 | 90 | 16 | Central | UF07
136667 | 2017-09-21 | Scheduled Outage | Vegetation Management | section of overhead circuit fed from switch S1120 was isolated for crews to trim trees at rear of 3 and 7 sherry. 14 customers were affected. Woodroffe D.S (170F3) | None | None | 14 | 325 | 76 | South | 170F3
136669 | 2017-09-21 | Defective Equipment | Mechanical Failure | transformer TP4007 at cedarhill and doral park was isolated for soil remediation. 7 customers were affected. Jockvale (145F2) | U/G Transformer | Padmount (1ph) | 7 | 474 | 55 | South | 145F2
136671 | 2017-09-21 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contacts on primary line on Park Lane & Conroy caused G570W & G370W to open. 22 customers affected. Leitrim 249F4. | None | None | 15 | 17 | 4 | East | LTM04
136671 | 2017-09-21 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contacts on primary line on Park Lane & Conroy caused G570W & G370W to open. 22 customers affected. Leitrim 249F4. | None | None | 22 | 111 | 41 | East | LTM04
136672 | 2017-09-21 | Defective Equipment | Mechanical Failure | 44kV overhead circuit isolated on Colonade Rd. to replace defective in-line switches. 2 customers affected. Nepean TS (22M24) | O/H Switchgear | Inline Switch | 2 | 212 | 7 | South | 22M24
136673 | 2017-09-22 | Scheduled Outage | Construction | Patrick Brisson and crew to have transformer X34019 open to move overhead triplexes to new attachment points. Customers notified. | None | None | 13 | 54 | 12 | Central | SM15
136678 | 2017-09-24 | Defective Equipment | Electrical Failure | Defective white phase switch at S15970 | O/H Switchgear | Fused Cutout | 17 | 7 | 2 | East | UA04
136678 | 2017-09-24 | Defective Equipment | Electrical Failure | Defective white phase switch at S15970 | O/H Switchgear | Fused Cutout | 34 | 131 | 74 | East | UA04
136679 | 2017-09-24 | Defective Equipment | Defective Equipment/ Material | S15996 W opened, due to defective transformer. Fallowfield (FAL01) | O/H Transformer | O/H Transformer (1ph) | 1 | 415 | 7 | South | FAL01
136680 | 2017-09-24 | Defective Equipment | Mechanical Failure | Downed red phase conductor | O/H Conductor | O/H Conductor | 49 | 170 | 139 | South | 180F4
136680 | 2017-09-24 | Defective Equipment | Mechanical Failure | Downed red phase conductor | O/H Conductor | O/H Conductor | 88 | 74 | 109 | South | 180F4
136680 | 2017-09-24 | Defective Equipment | Mechanical Failure | Downed red phase conductor | O/H Conductor | O/H Conductor | 145 | 760 | 1837 | South | 180F4
136681 | 2017-09-25 | Foreign Interference | Wildlife (Bird/Animal) | An apparent animal contact at a switchgear at 1950 Walkley caused a flash which tripped the sectionalizer affecting 23 customers. Albion 2203 | None | None | 2 | 15 | 0 | East | 2203
136681 | 2017-09-25 | Foreign Interference | Wildlife (Bird/Animal) | An apparent animal contact at a switchgear at 1950 Walkley caused a flash which tripped the sectionalizer affecting 23 customers. Albion 2203 | None | None | 3 | 21 | 1 | East | 2203
136681 | 2017-09-25 | Foreign Interference | Wildlife (Bird/Animal) | An apparent animal contact at a switchgear at 1950 Walkley caused a flash which tripped the sectionalizer affecting 23 customers. Albion 2203 | None | None | 5 | 37 | 3 | East | 2203
136681 | 2017-09-25 | Foreign Interference | Wildlife (Bird/Animal) | An apparent animal contact at a switchgear at 1950 Walkley caused a flash which tripped the sectionalizer affecting 23 customers. Albion 2203 | None | None | 9 | 61 | 9 | East | 2203
136681 | 2017-09-25 | Foreign Interference | Wildlife (Bird/Animal) | An apparent animal contact at a switchgear at 1950 Walkley caused a flash which tripped the sectionalizer affecting 23 customers. Albion 2203 | None | None | 23 | 79 | 30 | East | 2203
136682 | 2017-09-25 | Foreign Interference | Wildlife (Bird/Animal) | Switch SW782 B phase opened due to animal contact with the O/H. Crew refused transformer X32129 and SW782 and all load was restored. Beckwith (BECKF2) | O/H Switchgear | Fused Cutout | 29 | 89 | 43 | West | BECKF2
136683 | 2017-09-25 | Scheduled Outage | Vegetation Management | Planned outage for tree trimming | None | None | 36 | 253 | 152 | Central | SB02
136686 | 2017-09-25 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree branch contact at 3080 Queen Anne caused the 180F1 circuit to Auto reclosed and lock out. Rideau Heights (180F1) | None | None | 1031 | 45 | 773 | South | 180F1
136687 | 2017-09-25 | Scheduled Outage | Construction | Kevin Mckenna and crew to have transformer X31466 open to re-energize customer service. | None | None | 7 | 33 | 4 | Central | TH01
136689 | 2017-09-26 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry crews clear over grown trees from the primary O/H line | None | None | 38 | 148 | 94 | Central | UV02
136690 | 2017-09-26 | Scheduled Outage | Construction | A transformer at 939 Dynes was isolated to replace a kiosk transformer with a mini pad transformer affecting 28 customers. Fisher AK04 | None | None | 28 | 258 | 120 | Central | AK04
136691 | 2017-09-26 | Defective Equipment | Mechanical Failure | To allow Hydro Ottawa line crews to change a leaking transformer | O/H Transformer | O/H Transformer (1ph) | 8 | 125 | 17 | West | BRDF3
136693 | 2017-09-26 | Scheduled Outage | Construction | Not yet known.A transformer at 1301 Prince of Wales was isolated for duct work affecting 1 customer. Fisher AK05 | None | None | 1 | 114 | 2 | Central | AK05
136694 | 2017-09-26 | Defective Equipment | Mechanical Failure | At 8:23 pm a phase from the TA2AF circuit came down at the rear of 1980 Bank causing the TA2AF and ELW11 circuits to trip. ELW11 was on the transfer breaker along with ELW05, 07, 09 and 13. TA2AF was carrying the TA3AF and the 505 circuit. A total of 8 ci | O/H Conductor | O/H Conductor | 2 | 197 | 7 | Central | 507
136694 | 2017-09-26 | Defective Equipment | Mechanical Failure | At 8:23 pm a phase from the TA2AF circuit came down at the rear of 1980 Bank causing the TA2AF and ELW11 circuits to trip. ELW11 was on the transfer breaker along with ELW05, 07, 09 and 13. TA2AF was carrying the TA3AF and the 505 circuit. A total of 8 ci | O/H Conductor | O/H Conductor | 89 | 40 | 59 | East | ELW13
136694 | 2017-09-26 | Defective Equipment | Mechanical Failure | At 8:23 pm a phase from the TA2AF circuit came down at the rear of 1980 Bank causing the TA2AF and ELW11 circuits to trip. ELW11 was on the transfer breaker along with ELW05, 07, 09 and 13. TA2AF was carrying the TA3AF and the 505 circuit. A total of 8 ci | O/H Conductor | O/H Conductor | 136 | 196 | 444 | East | ELW11
136694 | 2017-09-26 | Defective Equipment | Mechanical Failure | At 8:23 pm a phase from the TA2AF circuit came down at the rear of 1980 Bank causing the TA2AF and ELW11 circuits to trip. ELW11 was on the transfer breaker along with ELW05, 07, 09 and 13. TA2AF was carrying the TA3AF and the 505 circuit. A total of 8 ci | O/H Conductor | O/H Conductor | 161 | 197 | 529 | East | ELW11
136694 | 2017-09-26 | Defective Equipment | Mechanical Failure | At 8:23 pm a phase from the TA2AF circuit came down at the rear of 1980 Bank causing the TA2AF and ELW11 circuits to trip. ELW11 was on the transfer breaker along with ELW05, 07, 09 and 13. TA2AF was carrying the TA3AF and the 505 circuit. A total of 8 ci | O/H Conductor | O/H Conductor | 1024 | 40 | 683 | East | ELW09
136694 | 2017-09-26 | Defective Equipment | Mechanical Failure | At 8:23 pm a phase from the TA2AF circuit came down at the rear of 1980 Bank causing the TA2AF and ELW11 circuits to trip. ELW11 was on the transfer breaker along with ELW05, 07, 09 and 13. TA2AF was carrying the TA3AF and the 505 circuit. A total of 8 ci | O/H Conductor | O/H Conductor | 1092 | 103 | 1875 | East | TA3AF
136694 | 2017-09-26 | Defective Equipment | Mechanical Failure | At 8:23 pm a phase from the TA2AF circuit came down at the rear of 1980 Bank causing the TA2AF and ELW11 circuits to trip. ELW11 was on the transfer breaker along with ELW05, 07, 09 and 13. TA2AF was carrying the TA3AF and the 505 circuit. A total of 8 ci | O/H Conductor | O/H Conductor | 1122 | 103 | 1926 | East | TA2AF
136694 | 2017-09-26 | Defective Equipment | Mechanical Failure | At 8:23 pm a phase from the TA2AF circuit came down at the rear of 1980 Bank causing the TA2AF and ELW11 circuits to trip. ELW11 was on the transfer breaker along with ELW05, 07, 09 and 13. TA2AF was carrying the TA3AF and the 505 circuit. A total of 8 ci | O/H Conductor | O/H Conductor | 1139 | 40 | 759 | East | ELW05
136694 | 2017-09-26 | Defective Equipment | Mechanical Failure | At 8:23 pm a phase from the TA2AF circuit came down at the rear of 1980 Bank causing the TA2AF and ELW11 circuits to trip. ELW11 was on the transfer breaker along with ELW05, 07, 09 and 13. TA2AF was carrying the TA3AF and the 505 circuit. A total of 8 ci | O/H Conductor | O/H Conductor | 1762 | 40 | 1175 | East | ELW07
136694 | 2017-09-26 | Defective Equipment | Mechanical Failure | At 8:23 pm a phase from the TA2AF circuit came down at the rear of 1980 Bank causing the TA2AF and ELW11 circuits to trip. ELW11 was on the transfer breaker along with ELW05, 07, 09 and 13. TA2AF was carrying the TA3AF and the 505 circuit. A total of 8 ci | O/H Conductor | O/H Conductor | 1898 | 103 | 3258 | Central | 505
136718 | 2017-09-28 | Tree Contacts | Falling Tree | AD06 circuit dummped to allow crew to cut a primary tap clear that was dangerously low and close to the secondary | None | None | 676 | 12 | 135 | Central | AD06
136719 | 2017-09-28 | Tree Contacts | Falling Tree | S20308 was isolated to allow crew to safely remove tree on the overhead primary on Parkhurst. 28 customers were affected. Woodroffe (TW22) | None | None | 28 | 32 | 15 | Central | TW22
136720 | 2017-09-28 | Tree Contacts | Falling Tree | trees on wires in 2 different locations 1- 609 Fraser. 2-683 Mansfield | O/H Conductor | O/H Conductor | 1169 | 273 | 5319 | Central | TD01
136729 | 2017-09-28 | Tree Contacts | Broken Branch | Hydro Ottawa 24/7 line crews had to open tranformer X14728 to repair damaged open wire secondary bus. Damaged was caused by a storm | None | None | 8 | 18 | 2 | East | LTM04
136734 | 2017-09-28 | Tree Contacts | Broken Branch | Tree on wires and defective cut out. | O/H Conductor | Unknown \ Other | 14 | 60 | 14 | Central | SH04
136742 | 2017-09-28 | Tree Contacts | Broken Branch | Tree took down primary | O/H Conductor | Unknown \ Other | 14 | 63 | 15 | Central | TD01
136746 | 2017-09-28 | Tree Contacts | Broken Branch | Wires down due to trees | O/H Conductor | Unknown \ Other | 22 | 84 | 31 | Central | TD01
136748 | 2017-09-28 | Tree Contacts | Falling Tree | Large tree took down transforme and broke pole at 1149 Shillington. 7 customers were affected. Shillington AD06 | O/H Transformer | O/H Transformer (1ph) | 7 | 588 | 69 | Central | AD06
136751 | 2017-09-29 | Tree Contacts | Falling Tree | Tree in the wires at 669 Mansfield caused sparking and a fire requiring isolation to clear the branches affecting 33 customers. Lincoln Heights TD01 | None | None | 33 | 68 | 37 | Central | TD01
136752 | 2017-09-29 | Scheduled Outage | Vegetation Management | Remove tree with a crane. | None | None | 27 | 121 | 54 | Central | TD01
136754 | 2017-09-29 | Defective Equipment | Electrical Failure | Reapair defective switches | O/H Switchgear | Unknown \ Other | 1 | 69 | 1 | Central | 505
136755 | 2017-09-29 | Scheduled Outage | Construction | Transformer isolated by Sproule to install 2 new services | None | None | 11 | 20 | 4 | Central | SB16
136756 | 2017-09-29 | Tree Contacts | Broken Branch | A tree branch was found across the 3 phases of AH14 circuit. | O/H Conductor | O/H Conductor | 454 | 2 | 15 | Central | AH14
136757 | 2017-09-29 | Tree Contacts | Broken Branch | Branch in secondary sercice service cause wires to spark. | O/H Conductor | O/H Conductor | 276 | 20 | 92 | East | UZ12
136758 | 2017-09-30 | Tree Contacts | Broken Branch | To repair secondary triplex crews opened transformer X29974 on TD14 circuit. | O/H Conductor | O/H Conductor | 7 | 58 | 7 | Central | TD14
136759 | 2017-09-30 | Scheduled Outage | Construction | Brian from Sproule Powerlines to have transformer X28078 open to install a new service. | None | None | 9 | 53 | 8 | Central | 505
136760 | 2017-09-30 | Scheduled Outage | Construction | Pete Barr and crew to have transformer X32601 open to install a new secondary service. | None | None | 15 | 60 | 15 | Central | TD14
136761 | 2017-09-30 | Scheduled Outage | Construction | Rick Barnett and crew to have transformer X21543 open to install a new secondary service. | None | None | 10 | 63 | 10 | Central | TD01
136762 | 2017-09-30 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X27237 open to install new customer service. | None | None | 9 | 95 | 14 | East | UZ12
136763 | 2017-09-30 | Scheduled Outage | Construction | Pete Barr and crew to have transformer X31929 open to install a new secondary service. | None | None | 11 | 106 | 19 | Central | TD14
136764 | 2017-09-30 | Scheduled Outage | Construction | Mike Lamoureux and crew to have transformer X27633 open to install a secondary service. | None | None | 15 | 44 | 11 | Central | 505
136765 | 2017-09-30 | Tree Contacts | Broken Branch | At 2:16pm AF02 was isolated to allow crew to remove a limb on the primary. 57 customers affected. Brookfield (AF02) | None | None | 14 | 56 | 13 | East | AF02
136765 | 2017-09-30 | Tree Contacts | Broken Branch | At 2:16pm AF02 was isolated to allow crew to remove a limb on the primary. 57 customers affected. Brookfield (AF02) | None | None | 57 | 63 | 60 | East | AF02
136766 | 2017-09-30 | Defective Equipment | Mechanical Failure | Crews isolated SW1563 @ 1950 Walkley Rd to replace defective barrier boards in S-592 compatment. | U/G Switchgear | Unknown \ Other | 1 | 170 | 3 | East | 2203
136768 | 2017-10-01 | Tree Contacts | Broken Branch | Oakley McCoy and Collin Port to have tranformer X35789 open to remove a tree branch from a secondary service. | None | None | 10 | 20 | 3 | Central | TD06
136769 | 2017-10-01 | Tree Contacts | Broken Branch | Red and Blue phase overhead burnt down behind Bromley due to branch falling into conductors | O/H Conductor | O/H Conductor | 20 | 363 | 121 | Central | TD06
136769 | 2017-10-01 | Tree Contacts | Broken Branch | Red and Blue phase overhead burnt down behind Bromley due to branch falling into conductors | O/H Conductor | O/H Conductor | 1054 | 112 | 1967 | Central | TD06
136771 | 2017-10-02 | Defective Equipment | Defective Equipment/ Material | The transformer TP5603 at 172 Burnetts had defective elbows which caused the blue phase to blow at S1104 on the 140F3 affecting 11 customers for 602 minutes | U/G Cable Attachement | Elbow \ Insert | 11 | 426 | 78 | South | 140F3
136771 | 2017-10-02 | Defective Equipment | Defective Equipment/ Material | The transformer TP5603 at 172 Burnetts had defective elbows which caused the blue phase to blow at S1104 on the 140F3 affecting 11 customers for 602 minutes | U/G Cable Attachement | Elbow \ Insert | 20 | 13 | 4 | South | 140F3
136771 | 2017-10-02 | Defective Equipment | Defective Equipment/ Material | The transformer TP5603 at 172 Burnetts had defective elbows which caused the blue phase to blow at S1104 on the 140F3 affecting 11 customers for 602 minutes | U/G Cable Attachement | Elbow \ Insert | 32 | 30 | 16 | South | 140F3
136771 | 2017-10-02 | Defective Equipment | Defective Equipment/ Material | The transformer TP5603 at 172 Burnetts had defective elbows which caused the blue phase to blow at S1104 on the 140F3 affecting 11 customers for 602 minutes | U/G Cable Attachement | Elbow \ Insert | 44 | 17 | 12 | South | 140F3
136771 | 2017-10-02 | Defective Equipment | Defective Equipment/ Material | The transformer TP5603 at 172 Burnetts had defective elbows which caused the blue phase to blow at S1104 on the 140F3 affecting 11 customers for 602 minutes | U/G Cable Attachement | Elbow \ Insert | 68 | 116 | 131 | South | 140F3
136772 | 2017-10-02 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X16002 opened up due to animal contact (current limiting fuse blown on OH transformer) | None | None | 2 | 273 | 9 | East | LTM01
136773 | 2017-10-02 | Scheduled Outage | Construction | crew isolated overhead section from switch S28391 at corner of Fallowfield and Steeple hill, to relocate switches for future work. 30 customers affected. Jockvale (145F3) | None | None | 30 | 130 | 65 | South | 145F3
136774 | 2017-10-02 | Defective Equipment | Mechanical Failure | Jeff Magee and crew to open transformer X18597 to replace defective cut out. | O/H Transformer | O/H Transformer (1ph) | 2 | 8 | 0 | East | CYRF1
136775 | 2017-10-02 | Scheduled Outage | Construction | Transformer #X34008 isolated by crew due to a service upgrade, Evan Cowell | None | None | 6 | 85 | 8 | Central | SM03
136776 | 2017-10-02 | Defective Equipment | Mechanical Failure | Transformer TP11521 at 6 Rothwell was isolated to allow the crew to replace the transformer and repair the elbows affecting 13 on BCHF1 circuit for 272 min | U/G Transformer | Padmount (1ph) | 13 | 272 | 59 | East | BCHF1
136777 | 2017-10-02 | Defective Equipment | Mechanical Failure | transformer TP8628 at 7 eagle rock was isolated to replace same. 11 customers were affected. Terry fox. (TFXF1) | U/G Transformer | Padmount (1ph) | 11 | 349 | 64 | West | TFXF1
136778 | 2017-10-02 | Defective Equipment | Mechanical Failure | Transformer TP11520 was isolated to access repairs of broken bushing. 9 customers were affected. Beaconhill. (BCHF8) | U/G Transformer | Padmount (1ph) | 9 | 24 | 4 | East | BCHF8
136779 | 2017-10-02 | Defective Equipment | Mechanical Failure | Repairs at S21086 cable dip required feeding TP10112 | O/H Switchgear | Fused Cutout | 1 | 296 | 5 | South | FAL01
136780 | 2017-10-02 | Loss Of Supply | Third Party | Customer secondary breaker burnt up and ttripped the VT732 R1-F and Blew 2 Rayrolle Fuses | None | None | 1 | 686 | 11 | East | TR02UQ
136781 | 2017-10-03 | Scheduled Outage | Construction | Transformers K814 and K813 including S24903 and S11373 at 1565 Heron Road were isolated to replace switches, arrestors and remove asbestos. 30 customers affected. Albion DS (UA05) | None | None | 30 | 93 | 46 | East | UA05
136783 | 2017-10-03 | Defective Equipment | Mechanical Failure | Transformer 355 at 49 Drainie was isolated to replace defective transformer. 10 customers affected. Bridlewood BRDF3. | U/G Transformer | Padmount (1ph) | 10 | 100 | 17 | West | BRDF3
136784 | 2017-10-03 | Tree Contacts | Falling Tree | Large maple wrapped in 3 phase primary line. TD00 (TD19) breaker opened to allow crew to safely open mid span switches on glass insulators. Temp 11 RWB remained opened to allow crew to remove tree. (TD01 line is transferred to the TD00) | None | None | 776 | 44 | 569 | Central | TD01
136784 | 2017-10-03 | Tree Contacts | Falling Tree | Large maple wrapped in 3 phase primary line. TD00 (TD19) breaker opened to allow crew to safely open mid span switches on glass insulators. Temp 11 RWB remained opened to allow crew to remove tree. (TD01 line is transferred to the TD00) | None | None | 1380 | 1 | 23 | Central | TD01
136784 | 2017-10-03 | Tree Contacts | Falling Tree | Large maple wrapped in 3 phase primary line. TD00 (TD19) breaker opened to allow crew to safely open mid span switches on glass insulators. Temp 11 RWB remained opened to allow crew to remove tree. (TD01 line is transferred to the TD00) | None | None | 1380 | 2 | 46 | Central | TD01
136787 | 2017-10-04 | Scheduled Outage | Construction | K1117 isolated to upgrade transformer to new mini pad and change out porcelain switch and arresstor at pole. | None | Padmount (1ph) | 11 | 78 | 14 | East | SO05
136788 | 2017-10-04 | Defective Equipment | Mechanical Failure | Transformer K237 at the rear of 1045 Morrison was isolated to replace defective transformer. | U/G Transformer | Kiosk (1ph) | 23 | 213 | 82 | Central | UV07
136790 | 2017-10-04 | Defective Equipment | Mechanical Failure | Transformer #X33859 isolated by crew to reconnect service at 54 Holland and make repairs, Evan Cowell | Secondary \ Service | O/H Service | 4 | 25 | 2 | Central | TH01
136793 | 2017-10-04 | Tree Contacts | Broken Branch | tree on an arrestor on overhead transformer caused switch G324B to open, causing the RX2001 to auto-reclose. 108 customers were affected. G324 was closed and power restored. Limebank. (7F2) | None | None | 8 | 134 | 18 | East | 7F2
136796 | 2017-10-04 | Adverse Weather | Extreme Wind | A storm with high wind andrain throuh the area which caused the RX2019 to auto reclose affecting 2036 customers | O/H Conductor | Unknown \ Other | 2036 | 13 | 441 | East | 77M6
136798 | 2017-10-04 | Tree Contacts | Tree Growth/ Untrimmed Tree | High winds and rain blew through the area causing a tree to come in contact with the O/H and a blown arrestor caused the fuse to blow at the rabbit WX2015 W phase affecting 9 customers on the 624F6 for 633 min | O/H Conductor | Unknown \ Other | 9 | 633 | 95 | West | 624F6
136799 | 2017-10-05 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to transfer plant to new poles | None | None | 14 | 240 | 56 | East | TB15
136801 | 2017-10-05 | Scheduled Outage | Maintenance | To allow underground crews to do maintenance on transformers K816 & 820. | None | Arrester | 20 | 131 | 44 | East | AQ10
136803 | 2017-10-05 | Defective Equipment | Mechanical Failure | Replacing defective transformer at 1946 Naskap1 on the BDHF8 out of Beacon Hill | U/G Transformer | Padmount (1ph) | 9 | 170 | 26 | East | BCHF8
136804 | 2017-10-05 | Defective Equipment | Mechanical Failure | To allow Hydro Ottawa line crews to replace transformer 241R due to a broken insert | O/H Transformer | O/H Transformer (1ph) | 10 | 90 | 15 | West | BRDF3
136805 | 2017-10-05 | Defective Equipment | Mechanical Failure | Transformer replacement and plant transfer of TE824 on the Manordale 84F5 | U/G Transformer | Padmount (1ph) | 12 | 348 | 70 | South | 84F5
136806 | 2017-10-05 | Defective Equipment | Mechanical Failure | Leaking transformer replacement at 1647 Boyer on the Billberry 77M2 | U/G Transformer | Padmount (1ph) | 9 | 431 | 65 | East | 77M2
136808 | 2017-10-05 | Tree Contacts | Broken Branch | To allow Hydro Ottawa forestry crews to safely remove a large branch from an O/H service | None | None | 50 | 57 | 48 | East | UZ02
136809 | 2017-10-05 | Scheduled Outage | Construction | To upgrade customer service. | None | None | 6 | 73 | 7 | Central | SB03
136811 | 2017-10-06 | Scheduled Outage | Construction | To install new service to TP11548 at 2628 St Joseph on the 77M6 out of Bilberry MS | None | None | 1 | 80 | 1 | East | 77M6
136812 | 2017-10-06 | Defective Equipment | Electrical Failure | The secondaruy cables fed out of K250 were isolated to allow Hydro Ottawa cable crews to make repairs to damaged/faulty secondary conductor | Secondary \ Service | U/G Service | 21 | 105 | 37 | East | UA04
136813 | 2017-10-06 | Foreign Interference | Wildlife (Bird/Animal) | As per Brad Fraser squirrel caused outage at transformer X31942. Field operators refused and closed. | None | None | 13 | 49 | 11 | Central | TD14
136814 | 2017-10-06 | Defective Equipment | Electrical Failure | Cable fault between TP5410 and TP11115 | U/G Cable | XLPE | 38 | 11 | 7 | West | BRDF5
136814 | 2017-10-06 | Defective Equipment | Electrical Failure | Cable fault between TP5410 and TP11115 | U/G Cable | XLPE | 129 | 79 | 170 | West | BRDF5
136816 | 2017-10-06 | Foreign Interference | Vehicle | ISOLATED TRANSFORMER X20926 TO UN-WRAP OPEN SECONDARY BUSS CAUSED BY BELL WIRE BEING HIT AND POLE PULLED ON | Secondary \ Service | O/H Service | 7 | 25 | 3 | East | 249F2
136818 | 2017-10-07 | Defective Equipment | Defective Equipment/ Material | ISOLATE TE245 IN ORDER TO OPEN HYDRO / BELL JOINT USE PEDESTAL TO INSPECT DUE TO FIRE DEPT CALL REPORTING LOUD NOISE. WILL REQUIRE REPLACEMENT. | Secondary \ Service | Secondary Pedestal | 11 | 13 | 2 | South | 84F2
136819 | 2017-10-07 | Defective Equipment | Defective Equipment/ Material | RX2019 opened due to defective dead end insulator | Pole Attachement | Insulator | 0 | 5 | 0 | East | 77M6
136819 | 2017-10-07 | Defective Equipment | Defective Equipment/ Material | RX2019 opened due to defective dead end insulator | Pole Attachement | Insulator | 127 | 79 | 167 | East | 77M6
136819 | 2017-10-07 | Defective Equipment | Defective Equipment/ Material | RX2019 opened due to defective dead end insulator | Pole Attachement | Insulator | 185 | 35 | 108 | East | 77M6
136819 | 2017-10-07 | Defective Equipment | Defective Equipment/ Material | RX2019 opened due to defective dead end insulator | Pole Attachement | Insulator | 1848 | 3 | 92 | East | 77M6
136819 | 2017-10-07 | Defective Equipment | Defective Equipment/ Material | RX2019 opened due to defective dead end insulator | Pole Attachement | Insulator | 2036 | 60 | 2036 | East | 77M6
136819 | 2017-10-07 | Defective Equipment | Defective Equipment/ Material | RX2019 opened due to defective dead end insulator | Pole Attachement | Insulator | 2036 | 72 | 2443 | East | 77M6
136821 | 2017-10-07 | Unknown/Other | Unknown | AE05 breaker tripped open. Ottawa Fire reported a pole fire at 2140 Walkley, but nothing found. System closed AE05 breaker and A/R/A. S24351 WB fuses found blown. Crew patrolled nothing found. | None | None | 51 | 114 | 97 | East | AE05
136821 | 2017-10-07 | Unknown/Other | Unknown | AE05 breaker tripped open. Ottawa Fire reported a pole fire at 2140 Walkley, but nothing found. System closed AE05 breaker and A/R/A. S24351 WB fuses found blown. Crew patrolled nothing found. | None | None | 219 | 45 | 164 | East | AE05
136823 | 2017-10-08 | Unknown/Other | Unknown | TW05 breaker tripped. NO CAUSE FOUND | None | None | 1296 | 28 | 605 | Central | TW05
136824 | 2017-10-08 | Defective Equipment | Mechanical Failure | Defective line clamp | O/H Conductor | Hot-Line Clamp | 43 | 35 | 25 | Central | TD06
136826 | 2017-10-08 | Tree Contacts | Broken Branch | Tree on lines | None | None | 13 | 178 | 39 | East | LTM04
136827 | 2017-10-08 | Tree Contacts | Broken Branch | Tree branch on overhead | None | None | 153 | 182 | 464 | West | MWDF3
136828 | 2017-10-08 | Tree Contacts | Broken Branch | Tree limb on wires | None | None | 28 | 168 | 78 | East | 249F2
136829 | 2017-10-08 | Defective Equipment | Mechanical Failure | Defective transformer lead | O/H Conductor | Stirrup | 5 | 264 | 22 | East | UZ03
136830 | 2017-10-08 | Defective Equipment | Mechanical Failure | Defective equipment | Pole | Crossarm | 1012 | 3 | 51 | East | BLKF8
136831 | 2017-10-09 | Tree Contacts | Other Vegetation | Replaced blown fuse feeding transformer X27168 (vines) | O/H Transformer | O/H Transformer (1ph) | 12 | 79 | 16 | East | TB15
136833 | 2017-10-09 | Defective Equipment | Mechanical Failure | Defective switch | U/G Cable Attachement | Termination \ Stress Cone | 2 | 96 | 3 | Central | UC07
136834 | 2017-10-09 | Scheduled Outage | Construction | Transfer riser to new pole | None | None | 1 | 280 | 5 | East | CYRF1
136836 | 2017-10-10 | Scheduled Outage | Construction | A section of primary overhead on Huntley Rd was isolated to replace poles and transfer plant affecting 3 customers. Richmond South 28F2 | None | None | 3 | 331 | 17 | West | 28F2
136837 | 2017-10-10 | Defective Equipment | Mechanical Failure | planned outage to transfer the Munster load to Beckwith through the rabbits to offload Muster STN due to gas accumulation. | Station Equipment | Transformer | 321 | 1 | 5 | West | 43F2
136838 | 2017-10-10 | Defective Equipment | Mechanical Failure | planned outage to transfer the Munster load to Beckwith through the rabbits to offload Muster STN due to gas accumulation. | Station Equipment | Transformer | 347 | 2 | 12 | West | 43F3
136840 | 2017-10-10 | Defective Equipment | Electrical Failure | flashed insulator blew line fuse S11164 on Genest St | Pole Attachement | Insulator | 29 | 104 | 50 | East | AC05
136842 | 2017-10-11 | Scheduled Outage | Construction | TB06 O/H line from TEMP41 and TEMP34 on Haig Dr was isoalted to allow crew to set new poles with crane. Russell (TB06) | None | None | 29 | 495 | 239 | East | TB00
136843 | 2017-10-11 | Scheduled Outage | Construction | Bobby Mcnab from Sproule Powerlines to have transformer TP7232 open to instal a new service. Customers notified. | None | None | 11 | 15 | 3 | East | BLKF8
136844 | 2017-10-11 | Scheduled Outage | Vegetation Management | S23090 to EOL was isolated to allow tree trimming crew to remove tree at rear of 1347 Coldrey. Clyde (UC08) | None | None | 117 | 305 | 595 | Central | UC08
136845 | 2017-10-11 | Defective Equipment | Mechanical Failure | A transformer at 53 Knoxdale was isolated to replace a leaking transformer affecting 8 customers. Woodroffe 170F1 | U/G Transformer | Padmount (1ph) | 8 | 450 | 60 | South | 170F1
136847 | 2017-10-11 | Scheduled Outage | Vegetation Management | planned outage for tree trimming | None | None | 41 | 65 | 44 | East | LTM01
136848 | 2017-10-11 | Scheduled Outage | Vegetation Management | S13367 to EOL was isolated to allow tree trimming crew to remove tree in proximity of O/H line at 186 Baseline. (Fisher AK02) | None | None | 46 | 94 | 72 | Central | AK02
136849 | 2017-10-11 | Defective Equipment | Mechanical Failure | leaking transformer | U/G Transformer | Padmount (1ph) | 17 | 86 | 24 | West | MWDF2
136851 | 2017-10-12 | Scheduled Outage | Construction | Bob Mcnab from Sproule to have transformer X35027 open to install a new service. Customers notified. | None | None | 7 | 68 | 8 | Central | UL04
136852 | 2017-10-12 | Scheduled Outage | Vegetation Management | Sproule to have transformer X34232 open for tree trimming. Customers notified. Outage extended due to extensive trimming. | None | None | 11 | 391 | 72 | Central | TH01
136853 | 2017-10-12 | Foreign Interference | Wildlife (Bird/Animal) | 24/7 reports that a dead crow was found at the base of transformer 001505. Crew refused and closed. | O/H Switchgear | Fused Cutout | 1 | 320 | 5 | West | MWDF3
136854 | 2017-10-12 | Scheduled Outage | Construction | Change feed to V607 | None | None | 1 | 308 | 5 | Central | SB15
136855 | 2017-10-13 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30085 TO TRANSFER SECONDARY HYDRO PLANT | None | None | 10 | 75 | 12 | Central | SB11
136856 | 2017-10-13 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X30075 TO WORK ON SECONDARY SERVICES | None | None | 4 | 255 | 17 | Central | SB11
136857 | 2017-10-13 | Scheduled Outage | Vegetation Management | A section of oveerhead line from S34 to EOL was isolated to perform tree trimming on Savuto Way. 74 customers affected. Epworth EPWF3. | None | None | 74 | 288 | 355 | South | EPWF3
136858 | 2017-10-13 | Defective Equipment | Mechanical Failure | TE827 at 9 Banner was isolated to replace transformer. 13 customers affected. Manordale 84F4. | U/G Transformer | Padmount (1ph) | 13 | 267 | 58 | South | 84F4
136861 | 2017-10-14 | Scheduled Outage | Construction | 2 transformers isolated by Steve Rutherford from Sproule to transfer plant (X30319 and X30320) | None | None | 16 | 190 | 51 | Central | UF06
136863 | 2017-10-14 | Scheduled Outage | Construction | Overhead circuit transfer to a new pole at Racine and Principale on the Casselman CASF2 | None | None | 1 | 157 | 3 | East | V11F1
136865 | 2017-10-15 | Defective Equipment | Defective Equipment/ Material | Switch S27153 B phase opened due to defctive fuse barrel. Richmond North (RHNF1) | O/H Switchgear | Fused Cutout | 239 | 135 | 538 | West | RHNF1
136867 | 2017-10-15 | Defective Equipment | Mechanical Failure | Broken ampact at Iber and Hazeldean caused the A9M3 circuit to trip. | O/H Conductor | Ampact | 3558 | 269 | 15952 | West | A9M3
136867 | 2017-10-15 | Defective Equipment | Mechanical Failure | Broken ampact at Iber and Hazeldean caused the A9M3 circuit to trip. | O/H Conductor | Ampact | 10962 | 74 | 13520 | West | A9M3
136869 | 2017-10-15 | Adverse Weather | Extreme Wind | Severe weather caused the MWDF3 to auto-reclose, no apparent reason found | None | None | 416 | 320 | 2219 | West | MWDF3
136871 | 2017-10-15 | Adverse Weather | Extreme Wind | Severe weather caused the 47F6 breaker to trip | None | None | 1197 | 49 | 978 | South | 47F6
136872 | 2017-10-15 | Adverse Weather | Extreme Wind | Severe weather caused the UX04 & UX06 breakers to trip | None | None | 246 | 10 | 41 | Central | UX04
136872 | 2017-10-15 | Adverse Weather | Extreme Wind | Severe weather caused the UX04 & UX06 breakers to trip | None | None | 714 | 11 | 131 | Central | UX06
136873 | 2017-10-15 | Adverse Weather | Extreme Wind | Severe weather caused the UF04 breaker to trip | None | None | 370 | 17 | 105 | Central | UF04
136874 | 2017-10-15 | Tree Contacts | Falling Tree | Fallen tree on the O/H cause SM16 W phase insulator to break and W phase tap to break clear on the primary at 262 Avondale affecting 16 customers . Carling (SM16). | None | None | 16 | 140 | 37 | Central | SM16
136875 | 2017-10-15 | Tree Contacts | Falling Tree | Severe weather caused a large tree to come down. The tree brought down AM02 3 phases radial circuit at Gladstone Ave & Cambridge Ave . | O/H Conductor | O/H Conductor | 42 | 24 | 17 | Central | AM02
136875 | 2017-10-15 | Tree Contacts | Falling Tree | Severe weather caused a large tree to come down. The tree brought down AM02 3 phases radial circuit at Gladstone Ave & Cambridge Ave . | O/H Conductor | O/H Conductor | 42 | 131 | 92 | Central | AM02
136875 | 2017-10-15 | Tree Contacts | Falling Tree | Severe weather caused a large tree to come down. The tree brought down AM02 3 phases radial circuit at Gladstone Ave & Cambridge Ave . | O/H Conductor | O/H Conductor | 434 | 13 | 94 | Central | AM02
136875 | 2017-10-15 | Tree Contacts | Falling Tree | Severe weather caused a large tree to come down. The tree brought down AM02 3 phases radial circuit at Gladstone Ave & Cambridge Ave . | O/H Conductor | O/H Conductor | 476 | 8 | 63 | Central | AM02
136875 | 2017-10-15 | Tree Contacts | Falling Tree | Severe weather caused a large tree to come down. The tree brought down AM02 3 phases radial circuit at Gladstone Ave & Cambridge Ave . | O/H Conductor | O/H Conductor | 476 | 99 | 785 | Central | AM02
136876 | 2017-10-15 | Adverse Weather | Extreme Wind | 2 phases of Primary on AK05 down in the rear of 1453 Lexington, and burning three phase transformer P406. No cause found for downed wires other than wind. | O/H Conductor | O/H Conductor | 124 | 322 | 665 | Central | AK05
136876 | 2017-10-15 | Adverse Weather | Extreme Wind | 2 phases of Primary on AK05 down in the rear of 1453 Lexington, and burning three phase transformer P406. No cause found for downed wires other than wind. | O/H Conductor | O/H Conductor | 209 | 400 | 1393 | Central | AK05
136876 | 2017-10-16 | Adverse Weather | Extreme Wind | 2 phases of Primary on AK05 down in the rear of 1453 Lexington, and burning three phase transformer P406. No cause found for downed wires other than wind. | O/H Conductor | O/H Conductor | 146 | 250 | 608 | Central | 303
136876 | 2017-10-16 | Adverse Weather | Extreme Wind | 2 phases of Primary on AK05 down in the rear of 1453 Lexington, and burning three phase transformer P406. No cause found for downed wires other than wind. | O/H Conductor | O/H Conductor | 227 | 261 | 987 | Central | AK02
136878 | 2017-10-15 | Tree Contacts | Falling Tree | tree on wires | None | None | 27 | 65 | 29 | South | 130F2
136878 | 2017-10-15 | Tree Contacts | Falling Tree | tree on wires | None | None | 320 | 327 | 1744 | South | 130F2
136879 | 2017-10-15 | Tree Contacts | Falling Tree | Large tree took down primary and neutral conductor at 1035 Bakervale affecting 56 customers. Shillington (AD05) | O/H Conductor | O/H Conductor | 56 | 290 | 271 | Central | AD05
136880 | 2017-10-15 | Tree Contacts | Falling Tree | Switch G739 at 15 De Niverville open due to tree on the O/H at 15 De Niverville. Uplands (4801F8) | None | None | 549 | 242 | 2214 | East | 4801F8
136881 | 2017-10-15 | Tree Contacts | Broken Branch | S898 open due to tree limb on the O/H at 10 Lytle. 13 customers were affected. Jockvale (145F2) | O/H Conductor | Unknown \ Other | 13 | 527 | 114 | South | 145F2
136882 | 2017-10-16 | Defective Equipment | Defective Equipment/ Material | Transformer X27923 was open to allow crew to repair down span guy. Queen (UQ08) | Pole Attachement | Unknown \ Other | 11 | 76 | 14 | East | UQ08
136883 | 2017-10-15 | Tree Contacts | Falling Tree | A tree at 35 Evergreen came down on the primary causing a fused switch to open affecting 42 customers. Bells Corners 47F3 | O/H Conductor | O/H Conductor | 42 | 743 | 520 | South | 47F3
136884 | 2017-10-15 | Tree Contacts | Broken Branch | Tree branch pulled down UN04 B phase radial primary at 172 Malborough. 14 customers were affeceted (UN04). | O/H Conductor | O/H Conductor | 14 | 570 | 133 | Central | UN04
136885 | 2017-10-15 | Tree Contacts | Tree Growth/ Untrimmed Tree | vines into the overhead transformer | None | None | 58 | 629 | 608 | East | 4801F8
136886 | 2017-10-16 | Tree Contacts | Broken Branch | A tree in contact with the primary overhead was burning and Hydro 1 crews requested we take the primary off potential while they cleared theire plant and allowed the tree to fall clear, affecting 148 customers. Terry Fox TFXF1 | None | None | 148 | 7 | 17 | West | TFXF1
136887 | 2017-10-15 | Tree Contacts | Falling Tree | Pine tree on the Primary O/H at 670 Cedarview caused the S25281 to open affecting 3 customers. (145F2) | None | None | 3 | 593 | 30 | South | 145F2
136889 | 2017-10-15 | Tree Contacts | Falling Tree | trees | None | None | 64 | 457 | 487 | South | 200F3
136892 | 2017-10-16 | Tree Contacts | Broken Branch | S27812 opened due to tree contact | O/H Conductor | O/H Conductor | 20 | 108 | 36 | Central | TK2AC
136893 | 2017-10-16 | Tree Contacts | Broken Branch | To allow crews to repair primary conductor. | O/H Conductor | O/H Conductor | 8 | 80 | 11 | Central | TD01
136894 | 2017-10-16 | Scheduled Outage | Vegetation Management | To allow Hydro Ottawa forestry crews to trim trees at the rear of 10 Largo Cres. | None | None | 61 | 344 | 350 | South | EPWF3
136895 | 2017-10-16 | Scheduled Outage | Maintenance | Transformer X4201 at 28 Millford was openedTo allow Hydro Ottawa line crews to re-sag secondary conductor | None | None | 8 | 30 | 4 | South | 170F1
136896 | 2017-10-17 | Scheduled Outage | Vegetation Management | EPWF4 OH from S831 to EOL for tree trimming at 15 & 22 Harris, affecting 49 customers. Epworth DS (EPWF4) | None | None | 49 | 332 | 271 | South | EPWF4
136897 | 2017-10-17 | Foreign Interference | Wildlife (Bird/Animal) | Field Operators report animal contact caused transformer X36098 to open. Refused and closed. | None | None | 4 | 67 | 4 | Central | TD05
136898 | 2017-10-17 | Scheduled Outage | Construction | RHNF1 OH isolated for crews to install new overhead lines, affecting 3 customers. Richmo0nd North DS (RHNF1) | None | None | 3 | 439 | 22 | West | RHNF1
136899 | 2017-10-17 | Unknown/Other | Unknown | Woodroffe TW12 breaker opened that was also carrying TW18 circuit. crew sectionalized and restored power. No apparent cause was found. 2020 customers were affected. Woodroffe. (TW12) | Unknown \ Other | Unknown \ Other | 106 | 96 | 170 | Central | TW12
136899 | 2017-10-17 | Unknown/Other | Unknown | Woodroffe TW12 breaker opened that was also carrying TW18 circuit. crew sectionalized and restored power. No apparent cause was found. 2020 customers were affected. Woodroffe. (TW12) | Unknown \ Other | Unknown \ Other | 473 | 15 | 118 | Central | TW12
136899 | 2017-10-17 | Unknown/Other | Unknown | Woodroffe TW12 breaker opened that was also carrying TW18 circuit. crew sectionalized and restored power. No apparent cause was found. 2020 customers were affected. Woodroffe. (TW12) | Unknown \ Other | Unknown \ Other | 2020 | 114 | 3838 | Central | TW12
136900 | 2017-10-17 | Scheduled Outage | Construction | Transformer TP11522 at 1952 MARQUIS AVE was isolated to allow the crew to replace the transformer and energize new cables affecting 13 on the BCHF8 circuit for 349 min | None | None | 13 | 349 | 76 | East | BCHF8
136901 | 2017-10-17 | Tree Contacts | Broken Branch | A tree limb on Kerwin Rd made contact with the O/H causing the RX2009 and the RX2007 B phase to trip which were both block under hold offs affecting 227 customer for 97 min on the 624F6 circuit | O/H Conductor | O/H Conductor | 227 | 97 | 367 | West | 624F6
136902 | 2017-10-17 | Scheduled Outage | Construction | Transformer K368 at 2704 Baseline was isolated to allow th crew to upgrade the transformer affecting 16 customers on UV04 circuit for 331 min | None | None | 16 | 331 | 88 | Central | UV04
136903 | 2017-10-17 | Defective Equipment | Corrosion | PRIMARY LEAD BURNT OFF HOT LINE CLAMP FEEDING TRANSFORMER X19730 THAT FEEDS THE RAILWAY CROSSING | Pole Attachement | Unknown \ Other | 1 | 172 | 3 | East | BLKF5
136904 | 2017-10-17 | Defective Equipment | Mechanical Failure | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X24946 | O/H Transformer | O/H Transformer (1ph) | 10 | 277 | 46 | East | UB04
136905 | 2017-10-18 | Scheduled Outage | Construction | 624F6 OH from S14033 to EOL isolatd to extend the pole line for a new house., affecting 5 customers Kanata (624F6) | None | None | 5 | 275 | 23 | West | 624F6
136906 | 2017-10-18 | Scheduled Outage | Construction | UC08 OH from taps at pole X31524 to EOL isolated to rearrange Primary and secondary, affecting 47 customers. Clyde DS (UC08) | None | None | 8 | 179 | 24 | Central | UC08
136908 | 2017-10-18 | Scheduled Outage | Construction | Section of overhead was isolated affecting customers on Haig dr., colson ave., and Hanmlet rd., to allow crews to install new poles. 34 customers were affected. Russell (TB06) | None | None | 34 | 474 | 269 | East | TB06
136909 | 2017-10-18 | Scheduled Outage | Construction | The Richmond N F1 O/H on Fallowfield Rd was isolated to allow the crews to replace poles, affecting 5 customers for 152 min. | None | None | 5 | 152 | 13 | West | RHNF1
136910 | 2017-10-18 | Scheduled Outage | Construction | Transforme K372 at 2632 Baseline Rd was isolated to allow the crew to upgrdae the transformer and swithes on the UV04 circuit affecting 9 customers for 249 min | None | None | 9 | 249 | 37 | Central | UV04
136911 | 2017-10-18 | Scheduled Outage | Construction | Transformer TP11525 and TP11528 @ 1970 Marquis was isolated by the crew to allow them install and energize new cables on the BCHF8 affecting 24 customers for 355 min. | None | None | 24 | 355 | 142 | East | BCHF8
136912 | 2017-10-18 | Defective Equipment | Mechanical Failure | A defective transformer TP10782 @ 1482 BORTOLOTTI CRES | U/G Transformer | Padmount (1ph) | 9 | 367 | 55 | East | 8F3
136912 | 2017-10-18 | Defective Equipment | Mechanical Failure | A defective transformer TP10782 @ 1482 BORTOLOTTI CRES | U/G Transformer | Padmount (1ph) | 64 | 14 | 15 | East | 8F3
136912 | 2017-10-18 | Defective Equipment | Mechanical Failure | A defective transformer TP10782 @ 1482 BORTOLOTTI CRES | U/G Transformer | Padmount (1ph) | 96 | 154 | 246 | East | 8F3
136916 | 2017-10-19 | Defective Equipment | Mechanical Failure | planned outage to replace xfmr, base, pad and ground grid | U/G Transformer | Padmount (1ph) | 7 | 359 | 42 | South | 145F2
136918 | 2017-10-19 | Scheduled Outage | Construction | Glenn Carswell and crew to have transformer X25651 open to upgrade a service. Customers notified. | None | None | 22 | 106 | 39 | Central | TH15
136919 | 2017-10-19 | Scheduled Outage | Construction | Bobby McNabb from Sproule powerlines to have transformer X35198 open to remove a service. Customers notified. | None | None | 11 | 13 | 2 | Central | AH02
136920 | 2017-10-16 | Defective Equipment | Electrical Failure | Transformer P53 was isolated to allow crew to install new primary from X58261 to P53, replace switch and defective transformer. Fisher AK05 | U/G Transformer | Padmount (3ph) | 1 | 4220 | 70 | Central | AK05
136921 | 2017-10-19 | Tree Contacts | Falling Tree | S27031 to EOL at 1261 Agincourt was isoalted to allow tree trimming crew to remove dead tree off the primary line. Woodroffe (TW22) | None | None | 55 | 125 | 115 | Central | TW22
136924 | 2017-10-19 | Loss Of Supply | Third Party | SW1850 CB tripped for unknown reason while switching. Still under investigation. | None | None | 2 | 169 | 6 | East | TO2UB
136925 | 2017-10-20 | Scheduled Outage | Construction | planned outage to extend primary line | None | None | 5 | 271 | 23 | West | 624F6
136926 | 2017-10-20 | Defective Equipment | Defective Equipment/ Material | planned outage to replace an end of life transformer | U/G Transformer | Padmount (1ph) | 12 | 324 | 65 | South | 84F5
136927 | 2017-10-20 | Foreign Interference | Foreign Objects | planned outage to replace a dammaged xfmr | None | None | 12 | 86 | 17 | West | MWDF4
136928 | 2017-10-20 | Scheduled Outage | Construction | Glen Carswell and crew to have transformer X23891 open to upgrade a secondary service. Customers notified. | None | None | 9 | 95 | 14 | Central | TH06
136929 | 2017-10-20 | Scheduled Outage | Forced Switching | Not yet known.A section of primary overhead on Barnsdale at the 416 was isolated to remove tree down on lines affecting 6 customers. Fallowfield FAL01 | None | None | 6 | 41 | 4 | South | FAL01
136930 | 2017-10-20 | Tree Contacts | Tree Growth/ Untrimmed Tree | Terry Dans to have transformer X32580 open so forestry crews can remove tree limbs from secondary bus. Customers notified. | None | None | 11 | 185 | 34 | Central | TD01
136931 | 2017-10-21 | Scheduled Outage | Construction | TB06 overhead line from TEMP 109 to EOL was isolated to allow crew to string in new conductor and transfer plant. | None | None | 13 | 265 | 57 | East | TB06
136933 | 2017-10-21 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BROKEN SWITCH BARREL AND FUSE FEEDING TRANSFORMER X24763 | O/H Transformer | O/H Transformer (1ph) | 4 | 143 | 10 | East | 8F1
136935 | 2017-10-21 | Defective Equipment | Mechanical Failure | TP6747 at 5000 Riverside isolated to replace defective transformer. 1 customer affected. Limebank 7F2. | U/G Transformer | Padmount (1ph) | 1 | 41 | 1 | East | 7F2
136938 | 2017-10-22 | Scheduled Outage | Construction | V422 at 21 James St. was isolated to replace primary cables and pole. 1 customer affected. Florence (UF04) | None | XLPE | 1 | 391 | 7 | Central | UF04
136942 | 2017-10-23 | Scheduled Outage | Construction | TP11530 & TP11527 at 1900 Marquis were isolated for primary cable replacement. 22 customrs affected. Beacon Hill BCHF8. | None | None | 22 | 373 | 137 | East | BCHF8
136943 | 2017-10-23 | Scheduled Outage | Construction | Overhead circuit on Fallowfield Rd. from TEMP 94 to EOL was isolated to string new conductor. 1 customer affected. Richmond North (RHNF1) | None | None | 1 | 435 | 7 | West | RHNF1
136944 | 2017-10-23 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER TE0762 TO REPLACE SECONDARY CONNECTIONS | None | None | 8 | 120 | 16 | East | 77M1
136945 | 2017-10-23 | Defective Equipment | Defective Equipment/ Material | AK02 breaker tripped due to Blown Pothead on AK02. | U/G Cable Attachement | Pothead | 228 | 42 | 160 | Central | AK02
136946 | 2017-10-23 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X40267 TO REPLACE SECONDARY CONNECTIONS | None | None | 10 | 65 | 11 | East | TB06
136948 | 2017-10-24 | Scheduled Outage | Construction | Cable replacement | None | None | 26 | 543 | 235 | East | BCHF8
136949 | 2017-10-24 | Unknown/Other | Unknown | Transformer #X31506 opened up, cause unknown | O/H Switchgear | Fused Cutout | 8 | 54 | 7 | Central | TW22
136950 | 2017-10-24 | Scheduled Outage | Vegetation Management | Cut in switch to allow customer to perform tree trimming | None | None | 1 | 377 | 6 | West | BECKF2
136950 | 2017-10-24 | Scheduled Outage | Vegetation Management | Cut in switch to allow customer to perform tree trimming | None | None | 32 | 75 | 40 | West | BECKF2
136951 | 2017-10-24 | Scheduled Outage | Construction | Sproule to have transformer X31095 open to install a new secondary service. Customers notified. | None | None | 10 | 15 | 2 | Central | UD04
136952 | 2017-10-24 | Tree Contacts | Tree Growth/ Untrimmed Tree | trees into primary line | O/H Conductor | O/H Conductor | 1 | 494 | 8 | West | RHNF1
136953 | 2017-10-24 | Unknown/Other | Unknown | Transformer X20249 at 5950 Piperville opened up. Crew could not any cause.3 customers were affected. Leitrim (249F2) | O/H Switchgear | Fused Cutout | 3 | 100 | 5 | East | 249F2
136954 | 2017-10-24 | Foreign Interference | Wildlife (Bird/Animal) | As per crew raccoon caused outage on transformer X36098. Crew replaced cut out switch and refused to restore power. | O/H Switchgear | Fused Cutout | 4 | 240 | 16 | Central | TD05
136955 | 2017-10-25 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X11605 open due to animal contact affecting 1 customer. Beckwith (BECKF2) | O/H Switchgear | Fused Cutout | 1 | 83 | 1 | West | BECKF2
136956 | 2017-10-25 | Defective Equipment | Mechanical Failure | Replace transformer, base and overhead switch. | U/G Transformer | Padmount (1ph) | 8 | 365 | 49 | South | 145F2
136957 | 2017-10-25 | Scheduled Outage | Construction | 2 transformers at 1900 Marquis were isolated for cable replacement affecting 27 customers. Beacon Hill BCHF8 | None | None | 27 | 350 | 158 | East | BCHF8
136958 | 2017-10-25 | Unknown/Other | Unknown | Transformer #X36611 opened up, cause unknown | O/H Switchgear | Fused Cutout | 1 | 227 | 4 | West | 624F6
136959 | 2017-10-25 | Scheduled Outage | Vegetation Management | Tree trimming | None | None | 5 | 228 | 19 | West | 624F6
136960 | 2017-10-25 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X48723 opened up due to animal contact | O/H Switchgear | Fused Cutout | 15 | 95 | 24 | Central | TW18
136961 | 2017-10-25 | Foreign Interference | Wildlife (Bird/Animal) | Blue phase voltage dip on bus. Police and fire clear breaker closed and holding. 24/7 to patrol. Transformer fuse blown on blue phase at 1293 Erindale X48316. | None | None | 2043 | 22 | 749 | Central | TW12
136962 | 2017-10-25 | Defective Equipment | Mechanical Failure | Primary lead came unattached from live linecausing loss of power to transformer X25755. No apparent cause. 24/7 crews reattached and restored power. | O/H Switchgear | Fused Cutout | 13 | 96 | 21 | Central | SB10
136963 | 2017-10-26 | Scheduled Outage | Construction | REPLACE SECONDARY SERVICE | None | O/H Service | 9 | 30 | 4 | South | EPWF3
136964 | 2017-10-26 | Scheduled Outage | Construction | Transformer #X27633 isolated by crew to install a service | None | None | 15 | 36 | 9 | Central | 505
136965 | 2017-10-26 | Defective Equipment | Mechanical Failure | Transformer #X24487 isolated by Bobby from Sproule to replace a defective trans switch | O/H Switchgear | Fused Cutout | 8 | 76 | 10 | East | UB07
136966 | 2017-10-26 | Scheduled Outage | Forced Switching | At 15:00 crews isolated a section of TD06 due to a branch on the overhead.29 customers affected. Lincoln Heights (TD06) | None | None | 29 | 62 | 30 | Central | TD06
136967 | 2017-10-27 | Scheduled Outage | Construction | A section of the 28F2 from Temp 145 to Temp 118 was isolated to allow crew to install new poles. 3 customers affected. Richmond South (28F2) | None | None | 3 | 167 | 8 | West | 28F2
136968 | 2017-10-27 | Defective Equipment | Imminent Failure | TE922 was isolated to replace leaking transformers | U/G Transformer | Padmount (1ph) | 14 | 466 | 109 | East | 77M1
136969 | 2017-10-27 | Scheduled Outage | Construction | K936 was isolated to replace K935 and riser. 16 customers affected. Langs Road (AP05) | None | None | 16 | 106 | 28 | East | AP05
136970 | 2017-10-27 | Defective Equipment | Mechanical Failure | defective white phase switch of three phase switches at Kent and McLeod opened. 8f customers affected. Florence (UF06) | O/H Switchgear | Inline Switch | 85 | 60 | 85 | Central | UF06
136971 | 2017-10-27 | Foreign Interference | Dig-In | Leaking transformer and dig in. | Secondary \ Service | U/G Service | 8 | 96 | 13 | East | 77M6
136975 | 2017-10-28 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X29836 open to transfer plant. Customers notified. | None | None | 12 | 433 | 87 | Central | TR09
136977 | 2017-10-27 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact | O/H Switchgear | Fused Cutout | 2 | 175 | 6 | West | 624F6
136983 | 2017-10-29 | Defective Equipment | Mechanical Failure | Suspected cable fault. | U/G Cable | XLPE | 24 | 659 | 264 | East | CYRF4
136983 | 2017-10-29 | Defective Equipment | Mechanical Failure | Suspected cable fault. | U/G Cable | XLPE | 59 | 89 | 88 | East | CYRF4
136985 | 2017-10-30 | Adverse Weather | Extreme Wind | High winds. | Station Equipment | Relay | 219 | 4 | 15 | East | AE05
136986 | 2017-10-30 | Tree Contacts | Falling Tree | S24351 blew when dead tree fell and contacted primary overhead | None | None | 98 | 206 | 336 | East | AE05
136989 | 2017-10-30 | Loss Of Supply | Transmission Inadvertent | The Hydro One 62M2 circuit A/R three times during the rain storm in the Ottawa areadue to defective cross arm on Hydro One pole. St. Isisdore (62M2) | None | None | 0 | 7 | 0 | East | 62M2 (Casselman MS)
136989 | 2017-10-30 | Loss Of Supply | Transmission Inadvertent | The Hydro One 62M2 circuit A/R three times during the rain storm in the Ottawa areadue to defective cross arm on Hydro One pole. St. Isisdore (62M2) | None | None | 0 | 16 | 0 | East | 62M2 (Casselman MS)
136990 | 2017-10-30 | Adverse Weather | Extreme Wind | Not yet known. | None | None | 2884 | 62 | 2980 | West | TFXF1
136993 | 2017-10-30 | Adverse Weather | Extreme Wind | Station breaker auto reclosed | None | None | 406 | 118 | 798 | East | UA02
136995 | 2017-10-30 | Tree Contacts | Falling Tree | Station breaker auto reclosed and locked out due to tree on the line at 2858 Prince of Whales. (180F4) | None | None | 44 | 78 | 57 | South | 180F4
136995 | 2017-10-30 | Tree Contacts | Falling Tree | Station breaker auto reclosed and locked out due to tree on the line at 2858 Prince of Whales. (180F4) | None | None | 983 | 195 | 3195 | South | 180F4
136996 | 2017-10-30 | Tree Contacts | Falling Tree | The SK10 circuit tripped due to tree on the O/H at 44 Besserer. King Edward (SK10) | O/H Conductor | O/H Conductor | 886 | 396 | 5848 | Central | SK10
136999 | 2017-10-30 | Tree Contacts | Falling Tree | During the wind and rain storm a tree came down on primary overhead causing the RHNF1 breaker to auto reclose and inline recloser RX2061 stayed open, affecting 1252 customers, load was restored in stages Richmond North RHNF1 | None | None | 98 | 87 | 142 | West | RHNF1
136999 | 2017-10-30 | Tree Contacts | Falling Tree | During the wind and rain storm a tree came down on primary overhead causing the RHNF1 breaker to auto reclose and inline recloser RX2061 stayed open, affecting 1252 customers, load was restored in stages Richmond North RHNF1 | None | None | 1252 | 225 | 4695 | West | RHNF1
137001 | 2017-10-30 | Adverse Weather | Extreme Wind | The UL03 CB tripped during the wind and rain storm. Circuit did not A/R. | None | None | 248 | 64 | 265 | Central | UL03
137002 | 2017-10-30 | Tree Contacts | Falling Tree | Tree on the primary line at 220 Harcourt caused the S10691 to blow. Lincoln Heights (TD06) | None | None | 29 | 327 | 158 | Central | TD06
137003 | 2017-10-30 | Defective Equipment | Electrical Failure | SE11 flashed, crews will replace | U/G Switchgear | Live-Front | 24 | 163 | 65 | East | 8F4
137003 | 2017-10-30 | Defective Equipment | Electrical Failure | SE11 flashed, crews will replace | U/G Switchgear | Live-Front | 220 | 23 | 84 | East | 8F4
137004 | 2017-10-30 | Adverse Weather | Extreme Wind | pole down | None | None | 2 | 570 | 19 | West | RHNF3
137004 | 2017-10-30 | Adverse Weather | Extreme Wind | pole down | None | None | 8 | 119 | 16 | West | RHNF3
137006 | 2017-10-30 | Adverse Weather | Extreme Wind | Two phases of primary overhead on Old Secondline came down opening the RX2042 inline recloser affecting 791 customers. Marchwood MWDF3 | O/H Conductor | O/H Conductor | 325 | 130 | 704 | West | MWDF3
137006 | 2017-10-30 | Adverse Weather | Extreme Wind | Two phases of primary overhead on Old Secondline came down opening the RX2042 inline recloser affecting 791 customers. Marchwood MWDF3 | O/H Conductor | O/H Conductor | 791 | 170 | 2241 | West | MWDF3
137007 | 2017-10-30 | Tree Contacts | Falling Tree | tree on wires | O/H Conductor | O/H Conductor | 69 | 42 | 48 | East | 7F4
137008 | 2017-10-30 | Adverse Weather | Extreme Wind | During the wind and ain storm the UG05 CB A/R and locked out due to tangled O/H wires at S16386. | None | None | 231 | 163 | 628 | East | UG05
137009 | 2017-10-30 | Tree Contacts | Falling Tree | tree pulled down conductor | O/H Conductor | O/H Conductor | 14 | 87 | 20 | East | 249F2
137009 | 2017-10-30 | Tree Contacts | Falling Tree | tree pulled down conductor | O/H Conductor | O/H Conductor | 161 | 66 | 177 | East | 249F2
137010 | 2017-10-30 | Tree Contacts | Falling Tree | Tree took down primary LMBF5 O/H line at 5504 Spratt RD. Crew isolated the O/H to make repairs to down primary. Limebank (LMBF5) | O/H Conductor | O/H Conductor | 30 | 8 | 4 | East | LMBF5
137011 | 2017-10-30 | Scheduled Outage | Forced Switching | S20585 to EOL was isolated to allow crew to remove tree on the O/H line at 609 Mansfield. | None | None | 46 | 394 | 302 | Central | TD01
137012 | 2017-10-30 | Tree Contacts | Falling Tree | tree on wires on Vann dr | O/H Conductor | O/H Conductor | 80 | 265 | 353 | South | 170F3
137013 | 2017-10-30 | Tree Contacts | Falling Tree | Tree contact on primary overhead caused in line fused switch to open at 2320 Lester affecting 7 customers. Uplands 4801F7 | O/H Conductor | O/H Conductor | 7 | 676 | 79 | East | 4801F7
137014 | 2017-10-30 | Adverse Weather | Extreme Wind | wire down | O/H Conductor | O/H Conductor | 53 | 105 | 93 | West | 624F6
137014 | 2017-10-30 | Adverse Weather | Extreme Wind | wire down | O/H Conductor | O/H Conductor | 135 | 256 | 576 | West | 624F6
137015 | 2017-10-30 | Tree Contacts | Falling Tree | Tree came down on primary casing fused switch at Royal York and Fortune to open affecting 51 customers. Richmond South 28F2 | O/H Conductor | O/H Conductor | 51 | 391 | 332 | West | 28F2
137016 | 2017-10-30 | Adverse Weather | Extreme Wind | pole down | O/H Conductor | O/H Conductor | 3 | 606 | 30 | East | 249F2
137017 | 2017-10-30 | Tree Contacts | Falling Tree | tree on primary | O/H Conductor | O/H Conductor | 3 | 483 | 24 | West | 624F6
137018 | 2017-10-30 | Adverse Weather | Extreme Wind | A section of conductor on the 49F6 came down at 4 Horner due to heavy wind and rain. 109 customers were affected. Bayshore (49F6) | O/H Conductor | Unknown \ Other | 109 | 148 | 269 | South | 49F6
137019 | 2017-10-31 | Scheduled Outage | Maintenance | Transformer 1502 at 8 Shaughnessey was isolated for maintenance, hydro vac inside & outside of base. 13 customers affected. Marchwood MWDF2. | None | None | 13 | 104 | 23 | West | MWDF2
137020 | 2017-10-31 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact on RX2022 ligtning arrestors caused RX2022 to open & CYRF3 CB to open. CYRF3 was carrying 77M2 load at the time | Pole Attachement | Arrester | 2231 | 37 | 1376 | East | CYRF3
137020 | 2017-10-31 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact on RX2022 ligtning arrestors caused RX2022 to open & CYRF3 CB to open. CYRF3 was carrying 77M2 load at the time | Pole Attachement | Arrester | 8585 | 13 | 1860 | East | CYRF3
137022 | 2017-10-31 | Scheduled Outage | Vegetation Management | Tree Trimming on Forest Drive affecting 54 TD05 customers out of Lincoln Heights Terminal | None | None | 54 | 29 | 26 | Central | TD05
137023 | 2017-11-01 | Scheduled Outage | Construction | To allow Sproule Power Lines to complete cable replacement work | None | None | 27 | 409 | 184 | East | BCHF8
137025 | 2017-11-02 | Defective Equipment | Mechanical Failure | A defective transformer at 380 Hunt Club caused the station breaker to auto reclose and a switchgear fuse to open affecting 989 customers. Load was restored in stages. Elwood ELW04 | U/G Transformer | Padmount (3ph) | 1 | 290 | 5 | East | ELW04
137025 | 2017-11-02 | Defective Equipment | Mechanical Failure | A defective transformer at 380 Hunt Club caused the station breaker to auto reclose and a switchgear fuse to open affecting 989 customers. Load was restored in stages. Elwood ELW04 | U/G Transformer | Padmount (3ph) | 40 | 170 | 113 | East | ELW04
137026 | 2017-11-02 | Scheduled Outage | Construction | Bobby McNabb from Sproule to have transformer X29996 open to install a new service. Customers notified. | None | None | 1 | 14 | 0 | Central | TR09
137027 | 2017-11-02 | Scheduled Outage | Construction | Bobby McNabb from Sproule Powerlines to have transformer X33133 open to install a new service. Customers notified. | None | None | 6 | 44 | 4 | Central | TD05
137028 | 2017-11-02 | Scheduled Outage | Construction | Bobby McNabb and crew to have transformer X32942 open to install a new service. Customers notified. | None | None | 7 | 39 | 5 | Central | TD05
137029 | 2017-11-02 | Tree Contacts | Broken Branch | A branch on the overhead caused an in line fused switch at Conroy and Park to open affecting 13 customers. Lietrim 249F4 | None | None | 13 | 62 | 13 | East | LTM04
137030 | 2017-11-03 | Defective Equipment | Mechanical Failure | Transformer X31397 open due to open wire bus wrapped toghether | O/H Switchgear | Fused Cutout | 19 | 106 | 34 | Central | SB02
137031 | 2017-11-03 | Tree Contacts | Broken Branch | Transformer X28199 open due to branch on the secondary | Secondary \ Service | O/H Service | 13 | 127 | 28 | Central | 505
137033 | 2017-11-03 | Defective Equipment | Defective Equipment/ Material | S15970 W phase open due to defective cable between K404 and K403 | U/G Cable | XLPE | 17 | 16 | 5 | East | UA04
137033 | 2017-11-03 | Defective Equipment | Defective Equipment/ Material | S15970 W phase open due to defective cable between K404 and K403 | U/G Cable | XLPE | 34 | 109 | 62 | East | UA04
137034 | 2017-11-03 | Scheduled Outage | Construction | Soil Remnediation | None | None | 17 | 505 | 143 | West | MWDF2
137035 | 2017-11-03 | Scheduled Outage | Construction | Install new riser and install new transformer NOT completed due to back hoe getting stuck. | None | None | 36 | 75 | 45 | South | 190F5
137036 | 2017-11-03 | Scheduled Outage | Construction | Transformer #X33401 isolated by crew to install new streetlight feed, Evan Cowell | None | None | 4 | 60 | 4 | Central | UV03
137037 | 2017-11-03 | Defective Equipment | Defective Equipment/ Material | Replaceingold P382 with new TP11736 from new riser S11080 | U/G Transformer | Padmount (3ph) | 1 | 300 | 5 | Central | AH14
137038 | 2017-11-03 | Foreign Interference | Wildlife (Bird/Animal) | City called to report seeing a squirrel make contact at S11085 which caused CB3 to trip | None | None | 689 | 110 | 1263 | Central | 505
137041 | 2017-11-03 | Scheduled Outage | Forced Switching | Hydro Ottawa line crews isolated TP11710 from S18881 due to a burst water main leaking into the school | None | None | 1 | 482 | 8 | South | 84F6
137044 | 2017-11-04 | Defective Equipment | Mechanical Failure | Hydro Ottawa line crews isolated transformer TE475 & switch S892 so that both devices could be replaced. | U/G Transformer | Padmount (3ph) | 1 | 423 | 7 | South | 200F2
137046 | 2017-11-03 | Loss Of Supply | Transmission Inadvertent | Due to the failure of Hydro One’s Q1Q2 CT’s at Overbrook TS, Hydro One dumped off the Q2 buss load as a safety precaution. Hydro Ottawa Field Operators & System Office recovered the load via the Q1 buss at Overbrook TS. | None | None | 17 | 27 | 8 | East | 1808
137046 | 2017-11-03 | Loss Of Supply | Transmission Inadvertent | Due to the failure of Hydro One’s Q1Q2 CT’s at Overbrook TS, Hydro One dumped off the Q2 buss load as a safety precaution. Hydro Ottawa Field Operators & System Office recovered the load via the Q1 buss at Overbrook TS. | None | None | 187 | 27 | 84 | East | TO2UT
137046 | 2017-11-03 | Loss Of Supply | Transmission Inadvertent | Due to the failure of Hydro One’s Q1Q2 CT’s at Overbrook TS, Hydro One dumped off the Q2 buss load as a safety precaution. Hydro Ottawa Field Operators & System Office recovered the load via the Q1 buss at Overbrook TS. | None | None | 680 | 27 | 306 | East | TO3UB
137046 | 2017-11-03 | Loss Of Supply | Transmission Inadvertent | Due to the failure of Hydro One’s Q1Q2 CT’s at Overbrook TS, Hydro One dumped off the Q2 buss load as a safety precaution. Hydro Ottawa Field Operators & System Office recovered the load via the Q1 buss at Overbrook TS. | None | None | 884 | 27 | 398 | East | 1806
137047 | 2017-11-05 | Scheduled Outage | Construction | TRANSFER PLANT TO NEW POLE INSTALLATION FROM STORM | Pole | Pole | 5 | 113 | 9 | East | AF06
137049 | 2017-11-06 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32089 TO INSTALL A NEW SERVICE | None | None | 7 | 73 | 9 | Central | UL04
137050 | 2017-11-06 | Scheduled Outage | Maintenance | At 8:26am S20708 R was opened to allow crews to cut in a new transformers. 4 customers affected. Terry Fox (TFXF4) | None | None | 4 | 443 | 30 | West | TFXF4
137051 | 2017-11-06 | Scheduled Outage | Maintenance | Transformer #X11782 isolated by crew to transfer plant, was done by Boyd Knox from Thirau | None | None | 13 | 222 | 48 | West | JKGF4
137053 | 2017-11-07 | Defective Equipment | Imminent Failure | Transformer 2378 at 59 Windcrest was isolated to replace leaking transformer. 20 customers affected. Marchwood MWDF1. | U/G Transformer | Padmount (1ph) | 20 | 91 | 30 | West | MWDF1
137054 | 2017-11-07 | Scheduled Outage | Maintenance | TP11236 isolated to temorarilty remove transformer to allow crew to install 12: spacer on existing base. | None | None | 16 | 73 | 19 | East | 4801F8
137055 | 2017-11-07 | Scheduled Outage | Construction | Replacing transformer TP3106 and install and energize new cables. | None | None | 13 | 390 | 84 | East | BCHF8
137056 | 2017-11-07 | Scheduled Outage | Construction | Transformer TP11968 at 411 Dovercourt was isolated to allow crew to install new cables to transformer. Clyde (UC03) | None | None | 1 | 357 | 6 | Central | UC03
137057 | 2017-11-07 | Defective Equipment | Defective Equipment/ Material | S17096 B open due flashed insulators at KT64 at 13 Gentle Way | U/G Cable Attachement | Insulator | 11 | 157 | 29 | East | ELW07
137057 | 2017-11-07 | Defective Equipment | Defective Equipment/ Material | S17096 B open due flashed insulators at KT64 at 13 Gentle Way | U/G Cable Attachement | Insulator | 27 | 35 | 16 | East | ELW07
137057 | 2017-11-07 | Defective Equipment | Defective Equipment/ Material | S17096 B open due flashed insulators at KT64 at 13 Gentle Way | U/G Cable Attachement | Insulator | 57 | 2 | 2 | East | ELW07
137057 | 2017-11-07 | Defective Equipment | Defective Equipment/ Material | S17096 B open due flashed insulators at KT64 at 13 Gentle Way | U/G Cable Attachement | Insulator | 193 | 145 | 466 | East | ELW07
137058 | 2017-11-07 | Defective Equipment | Electrical Failure | S13474 RWB to EOL was isolated to allow crew to make repairs to burnt cross arm at 587 Bathurst | Pole | Insulation Failure (Pole Fire) | 165 | 175 | 481 | East | TB14
137059 | 2017-11-07 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X26444 TO INSTALL NEW SERVICE | None | None | 1 | 173 | 3 | Central | AH02
137061 | 2017-11-07 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X32648 open due to susoected animal contact as per field crew. Crews refused and restored. | O/H Switchgear | Fused Cutout | 6 | 71 | 7 | Central | TD12
137062 | 2017-11-07 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X23895 openned due to animal contact. Crew found dead squirrel at the base of the pole. Refused and restored. | O/H Switchgear | Fused Cutout | 20 | 77 | 26 | Central | TH15
137064 | 2017-11-07 | Scheduled Outage | Construction | 2 transformers, X34025 and x34039 isolated by crew to transfer plant | None | None | 7 | 290 | 34 | Central | UC03
137065 | 2017-11-08 | Scheduled Outage | Construction | To move taps to new overhead line. | None | None | 1 | 74 | 1 | South | 145F3
137066 | 2017-11-08 | Scheduled Outage | Construction | Transformers TP11532 and TP11533 isolated to replace transformers base and install and energize new cables. | None | None | 16 | 447 | 119 | East | BCHF8
137068 | 2017-11-08 | Scheduled Outage | Construction | S14033 at 2450 Sixth Line opened to transfer plant to new conductor. 5 customers affected. Kanata 624F6. | None | None | 5 | 305 | 25 | West | 624F6
137069 | 2017-11-08 | Scheduled Outage | Construction | Transformer TP11546 was isolated to allow crew to relocate cable into new ductbank. Queens (UQ08) | None | None | 2 | 91 | 3 | East | UQ08
137070 | 2017-11-08 | Scheduled Outage | Construction | To allow crew to install pulling ropes. | None | None | 64 | 296 | 316 | South | LGFF1
137072 | 2017-11-08 | Scheduled Outage | Construction | Transformer #X32236 isolated by crew to transfer plant | None | None | 15 | 286 | 72 | Central | AD04
137073 | 2017-11-08 | Scheduled Outage | Construction | Transformer #X31930 isolated by crew to replace triplex to 2652 Regina St | None | None | 28 | 30 | 14 | Central | TD14
137074 | 2017-11-09 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to move the primary line tap to a new conductor | None | None | 35 | 10 | 6 | South | 145F3
137075 | 2017-11-09 | Scheduled Outage | Maintenance | 20 customers on the BRDF3 out of Bridlewood for transformer elbow and inset repair on Hewitt Way | None | None | 20 | 165 | 55 | West | BRDF3
137076 | 2017-11-09 | Scheduled Outage | Maintenance | Kevin Ennis to have transformer GLTE0382 open for maintenance purposes. Customers notified. | None | None | 2 | 335 | 11 | East | 8F1
137077 | 2017-11-09 | Scheduled Outage | Maintenance | Transformer and civil upgrade to TE382 on the Moulton 8F1 affecting 2 customers | None | None | 2 | 392 | 13 | East | 8F1
137078 | 2017-11-09 | Human Element | Switching Error | While Hydro Ottawa line crews were switching, Dane O'relly reports that on sequence 10 of PC17A 17-151898, that at S27-D B phase didn't seat properly, and when Dane went to close the fuse, it fell out of the holder and made contact with the concentric neu | None | None | 55 | 39 | 36 | East | 77M5
137080 | 2017-11-09 | Adverse Weather | Extreme Wind | With high winds caused the UG05 conductor to rap together causing the UG05 breaker to trip affecting 230 customers for 197 min | O/H Conductor | O/H Conductor | 231 | 197 | 758 | East | UG05
137082 | 2017-11-09 | Tree Contacts | Falling Tree | Overhead wires were brought down by a large tree on Mariposa west of Springfield. 231 customers were interrupted. King edward. (TK2AC- SCV66901) | O/H Conductor | O/H Conductor | 75 | 155 | 194 | Central | TK2AC
137082 | 2017-11-09 | Tree Contacts | Falling Tree | Overhead wires were brought down by a large tree on Mariposa west of Springfield. 231 customers were interrupted. King edward. (TK2AC- SCV66901) | O/H Conductor | O/H Conductor | 231 | 210 | 808 | Central | TK2AC
137083 | 2017-11-10 | Defective Equipment | Mechanical Failure | REPLACED PRIMARY LEAD FROM THE SWITCH TO THE LINE FEEDING TRANSFORMER X28241 | O/H Transformer | O/H Transformer (1ph) | 8 | 310 | 41 | Central | 505
137084 | 2017-11-10 | Defective Equipment | Imminent Failure | To allow Hydro Ottawa line crews to change leaking transformer TE2925 | U/G Transformer | Padmount (1ph) | 11 | 427 | 78 | East | LMBF7
137085 | 2017-11-10 | Scheduled Outage | Maintenance | To allow Hydro Ottawa line crews to make repairs to the transformer grounding and the base of TP6241 | None | None | 11 | 60 | 11 | South | 145F4
137087 | 2017-11-10 | Scheduled Outage | Construction | 4kV overhead reconfiguration affeting 49 customers on the Henderson UN04 | None | None | 49 | 180 | 147 | Central | UN04
137088 | 2017-11-10 | Scheduled Outage | Construction | VT469 at 360 Albert was isolated for de-commisioning. 1 customer affected. Lisgar (5201) | None | Transformer | 1 | 1495 | 25 | Central | 5201
137089 | 2017-11-10 | Unknown/Other | Unknown | Fuse S16879 W at 2635 Hickson opened, cause not determined. 23 customers affected. Edwin (UV07) | Unknown \ Other | Unknown \ Other | 23 | 171 | 66 | Central | UV07
137090 | 2017-11-10 | Scheduled Outage | Maintenance | Goulbourn Rec Center isolated for 44kv maintenance. | None | None | 2 | 325 | 11 | West | A9M3
137092 | 2017-11-11 | Tree Contacts | Tree Growth/ Untrimmed Tree | tree contact | O/H Conductor | O/H Conductor | 48 | 84 | 67 | South | 180F4
137094 | 2017-11-11 | Loss Of Supply | Third Party | Customer issue at DND Franktown issue on secondary equipment. | None | None | 0 | 12 | 0 | West | BECKF2
137094 | 2017-11-11 | Loss Of Supply | Third Party | Customer issue at DND Franktown issue on secondary equipment. | None | None | 0 | 42 | 0 | West | BECKF2
137094 | 2017-11-11 | Loss Of Supply | Third Party | Customer issue at DND Franktown issue on secondary equipment. | None | None | 1 | 393 | 7 | West | BECKF2
137095 | 2017-11-11 | Scheduled Outage | Construction | Transformer #X27698 isolated by crew for a service upgrade | None | None | 8 | 70 | 9 | East | TB06
137098 | 2017-11-11 | Defective Equipment | Mechanical Failure | emergncy repairs to damaged conductor | O/H Conductor | O/H Conductor | 5 | 53 | 4 | East | 249F2
137099 | 2017-11-11 | Defective Equipment | Electrical Failure | SC76 at 1236 Merivale isolated for replacement. 9 customers affected. Carling (307) | U/G Switchgear | Unknown \ Other | 9 | 257 | 39 | Central | 307
137100 | 2017-11-12 | Defective Equipment | Electrical Failure | During Switching at SE15, crew opened live front switch and drew an arc causing the 140F1 to trip. | U/G Switchgear | Unknown \ Other | 402 | 3 | 20 | South | 140F1
137101 | 2017-11-12 | Scheduled Outage | Construction | To disconnect and remove services from TE1212 and TE1213 and install new 3 phase transformer. | None | None | 27 | 249 | 112 | South | 140F1
137103 | 2017-11-12 | Defective Equipment | Defective Equipment/ Material | S21789 B phase blown. Customer reported to crew steam from KT99. Ached bushing and small oil leak. Kt 99 to be replaed by on-call. | U/G Transformer | Kiosk (1ph) | 8 | 182 | 24 | East | ELW07
137103 | 2017-11-12 | Defective Equipment | Defective Equipment/ Material | S21789 B phase blown. Customer reported to crew steam from KT99. Ached bushing and small oil leak. Kt 99 to be replaed by on-call. | U/G Transformer | Kiosk (1ph) | 115 | 74 | 142 | East | ELW07
137105 | 2017-11-13 | Defective Equipment | Imminent Failure | Outage to change leaking transformer. | U/G Transformer | Padmount (1ph) | 10 | 402 | 67 | East | 7F1
137106 | 2017-11-13 | Scheduled Outage | Vegetation Management | 49F6 OH isolated for clearance for tree trimmers, affecting 109 customers. Bayshore DS. | None | None | 109 | 285 | 518 | South | 49F6
137107 | 2017-11-13 | Scheduled Outage | Construction | Cable replacement | None | None | 9 | 440 | 66 | East | BCHF8
137108 | 2017-11-13 | Scheduled Outage | Construction | Booby Mcnab from Sproule powerlines to have transformer X44786 open to install a new service. | None | None | 16 | 59 | 16 | East | UZ11
137110 | 2017-11-13 | Scheduled Outage | Construction | String new lines | None | None | 3 | 387 | 19 | West | 28F2
137111 | 2017-11-13 | Scheduled Outage | Maintenance | S17578 open to allow crew to relocate primary conductor | None | None | 10 | 94 | 16 | East | TA3AF
137112 | 2017-11-13 | Scheduled Outage | Construction | Bobby McNabb of Sproule Powerlines to have transformer X24234 open to install a new service. | None | None | 9 | 58 | 9 | East | AF06
137113 | 2017-11-14 | Scheduled Outage | Vegetation Management | planned outage to allow crew to trim trees | None | None | 54 | 286 | 257 | Central | TD05
137114 | 2017-11-14 | Scheduled Outage | Construction | A transformer at 1945 Naskapi was isolated as part of the cable replacement program affecting 10 customers. Beacon Hill BCHF8 | None | None | 10 | 210 | 35 | East | BCHF8
137115 | 2017-11-14 | Defective Equipment | Electrical Failure | Transformer 378B was isolated to allow crew to replace transformer due to defective inserts. Bridlewood (BRDF3) | U/G Cable Attachement | Elbow \ Insert | 11 | 124 | 23 | West | BRDF3
137116 | 2017-11-14 | Scheduled Outage | Maintenance | A transformer at 415 Michael Cowpland was isolated at customer request for secondary switch Maintenance affecting 1 customer. Terry Fox TFXF5 | None | None | 1 | 268 | 4 | West | TFXF5
137117 | 2017-11-14 | Foreign Interference | Wildlife (Bird/Animal) | 77M6 circuit tripped due to squirel contact S19210. Circuit was under hold off when 77M6 tripped. Load was restored in stages due to cold load pickup. Billberry (77M6) | O/H Switchgear | Fused Cutout | 88 | 11 | 16 | East | 77M6
137117 | 2017-11-14 | Foreign Interference | Wildlife (Bird/Animal) | 77M6 circuit tripped due to squirel contact S19210. Circuit was under hold off when 77M6 tripped. Load was restored in stages due to cold load pickup. Billberry (77M6) | O/H Switchgear | Fused Cutout | 2310 | 62 | 2387 | East | 77M6
137117 | 2017-11-14 | Foreign Interference | Wildlife (Bird/Animal) | 77M6 circuit tripped due to squirel contact S19210. Circuit was under hold off when 77M6 tripped. Load was restored in stages due to cold load pickup. Billberry (77M6) | O/H Switchgear | Fused Cutout | 2323 | 36 | 1394 | East | 77M6
137117 | 2017-11-14 | Foreign Interference | Wildlife (Bird/Animal) | 77M6 circuit tripped due to squirel contact S19210. Circuit was under hold off when 77M6 tripped. Load was restored in stages due to cold load pickup. Billberry (77M6) | O/H Switchgear | Fused Cutout | 3205 | 5 | 267 | East | 77M6
137117 | 2017-11-14 | Foreign Interference | Wildlife (Bird/Animal) | 77M6 circuit tripped due to squirel contact S19210. Circuit was under hold off when 77M6 tripped. Load was restored in stages due to cold load pickup. Billberry (77M6) | O/H Switchgear | Fused Cutout | 3369 | 16 | 898 | East | 77M6
137117 | 2017-11-14 | Foreign Interference | Wildlife (Bird/Animal) | 77M6 circuit tripped due to squirel contact S19210. Circuit was under hold off when 77M6 tripped. Load was restored in stages due to cold load pickup. Billberry (77M6) | O/H Switchgear | Fused Cutout | 3478 | 10 | 580 | East | 77M6
137118 | 2017-11-14 | Scheduled Outage | Construction | TRANSFERING CONDUCTOR | None | O/H Transformer (1ph) | 14 | 124 | 29 | East | AE07
137119 | 2017-11-15 | Defective Equipment | Electrical Failure | Suspected cable fault | U/G Cable | PILC | 62 | 6 | 6 | Central | TM2SB
137119 | 2017-11-15 | Defective Equipment | Electrical Failure | Suspected cable fault | U/G Cable | PILC | 219 | 26 | 95 | Central | TM2SB
137119 | 2017-11-15 | Defective Equipment | Electrical Failure | Suspected cable fault | U/G Cable | PILC | 342 | 70 | 399 | Central | TM2SB
137120 | 2017-11-15 | Scheduled Outage | Construction | A transformer at 731 Ludgate was isolated as part of the cable replacement program affecting 9 customers. Beacon Hill BCHF8 | None | None | 9 | 285 | 43 | East | BCHF8
137121 | 2017-11-15 | Scheduled Outage | Construction | A transformer at 20 Hogan was isolated to replace pole and cable and remediate soil from leak affecting 36 customers. Parkwood Hills 190F5 | None | None | 36 | 359 | 215 | South | 190F5
137123 | 2017-11-15 | Scheduled Outage | Construction | A section of primary overhead on Kaymar was isolated for pole changes affecting 15 customers. Moulton 8F1 | None | None | 15 | 361 | 90 | East | 8F1
137124 | 2017-11-15 | Scheduled Outage | Construction | A section of primary overhead on Huntley Rd was isolated toi string new overhead affecting 11 customers. Richmond South 28F2 | None | None | 11 | 319 | 58 | West | 28F2
137125 | 2017-11-16 | Scheduled Outage | Construction | Ttransformers at TP11517 and TP3105 isolated to splice in new cable. | None | None | 22 | 397 | 146 | East | BLKF8
137126 | 2017-11-16 | Scheduled Outage | Construction | TP5877 isolated to allow crew to install new cable and riser switch. | None | None | 30 | 239 | 120 | South | 190F5
137127 | 2017-11-16 | Scheduled Outage | Vegetation Management | S25881 opened for forestry to trim on Connecticut Ave. 18 customers affected. Playfair AJ07. | None | None | 18 | 180 | 54 | East | AJ07
137128 | 2017-11-16 | Scheduled Outage | Construction | Transformer #X26886 isolated by crew for a pole replacement | None | None | 14 | 122 | 28 | East | TB06
137129 | 2017-11-16 | Scheduled Outage | Construction | Transformer #X35351 isolated by crew to transfer plant | None | None | 5 | 105 | 9 | Central | AD05
137130 | 2017-11-16 | Scheduled Outage | Maintenance | TE1023 was isolated for transformer replacement and cable insptection. | None | None | 11 | 90 | 16 | East | 77M6
137131 | 2017-11-16 | Defective Equipment | Defective Equipment/ Material | Transformer #X39750 opened up due to defective switch | O/H Switchgear | Fused Cutout | 1 | 61 | 1 | South | 49F6
137132 | 2017-11-16 | Scheduled Outage | Construction | Transformer #X33804 isolated by crew for a service upgrade | None | None | 8 | 45 | 6 | Central | SM15
137135 | 2017-11-17 | Defective Equipment | Electrical Failure | TP3791 at 71 Huntsman was isolated to replace defective transformer. 9 customers affected. Terry Fox TFXF5. | U/G Transformer | Padmount (1ph) | 9 | 138 | 21 | West | TFXF5
137136 | 2017-11-17 | Defective Equipment | Mechanical Failure | Leaking Transformer replaced at TP2888. | U/G Transformer | Padmount (1ph) | 18 | 69 | 21 | East | 7F1
137138 | 2017-11-17 | Defective Equipment | Mechanical Failure | To isolate transformers TP4951 and TP4952 for transformer replacement. | U/G Transformer | Padmount (1ph) | 18 | 114 | 34 | South | FAL03
137139 | 2017-11-17 | Defective Equipment | Electrical Failure | Cable fault between VT863 and VT70 caused TS73 to open. 224 customers affected. Slater (622) | U/G Cable | PILC | 19 | 4 | 1 | Central | 622
137139 | 2017-11-17 | Defective Equipment | Electrical Failure | Cable fault between VT863 and VT70 caused TS73 to open. 224 customers affected. Slater (622) | U/G Cable | PILC | 224 | 118 | 441 | Central | 622
137141 | 2017-11-18 | Foreign Interference | Vehicle | To allow Hydro Ottawa line crews to change damaged transformer TP11512 | None | None | 21 | 95 | 33 | East | LTM01
137142 | 2017-11-18 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X15674 FOR SERVICE MAINTENANCE | None | None | 14 | 60 | 14 | East | LTM01
137143 | 2017-11-19 | Tree Contacts | Broken Branch | Transformer X35005 open due to broken branch on the secondary transformer bushing. Bronson (SB04) | O/H Switchgear | Fused Cutout | 7 | 141 | 16 | Central | SB04
137144 | 2017-11-19 | Scheduled Outage | Construction | Decommisioning of P498 on the Bronson SB10 | None | None | 1 | 435 | 7 | Central | SB10
137146 | 2017-11-19 | Unknown/Other | Unknown | S27153 W phase found blown. No apparent cause found. | O/H Switchgear | Fused Cutout | 245 | 71 | 290 | West | RHNF1
137149 | 2017-11-20 | Defective Equipment | Defective Equipment/ Material | Kevin McKenna reports line taps have been removed at pole # 55D1B-0539. To isolate downed O/H conductor in the rear of 56 Spadina Ave. | O/H Conductor | O/H Conductor | 78 | 173 | 225 | Central | UJ07
137149 | 2017-11-20 | Defective Equipment | Defective Equipment/ Material | Kevin McKenna reports line taps have been removed at pole # 55D1B-0539. To isolate downed O/H conductor in the rear of 56 Spadina Ave. | O/H Conductor | O/H Conductor | 582 | 30 | 291 | Central | UJ02
137149 | 2017-11-20 | Defective Equipment | Defective Equipment/ Material | Kevin McKenna reports line taps have been removed at pole # 55D1B-0539. To isolate downed O/H conductor in the rear of 56 Spadina Ave. | O/H Conductor | O/H Conductor | 836 | 30 | 418 | Central | UJ07
137152 | 2017-11-20 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X32648 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 6 | 43 | 4 | Central | TD12
137153 | 2017-11-20 | Scheduled Outage | Construction | Stuart Maclaren and crew to have transformer X26891 open to transfer plant to a new pole. Customers notified. | None | None | 5 | 420 | 35 | East | TB06
137155 | 2017-11-21 | Scheduled Outage | Construction | Transformer #X33996 isolated by crew to install new triplex | None | None | 6 | 65 | 6 | Central | UV07
137156 | 2017-11-21 | Scheduled Outage | Vegetation Management | At 9:12am crews isolated 49F6 from S598 to end of line for tree trimming. 84 customers affected. Bayshore (49F6) | None | None | 84 | 218 | 305 | South | 49F6
137157 | 2017-11-21 | Scheduled Outage | Maintenance | At 09:03am Transformer 258 was isolated to replace the transformer. 10 customers affected. Bridlewood (BRDF4) | None | Padmount (1ph) | 10 | 137 | 23 | West | BRDF4
137158 | 2017-11-21 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X18294 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 5 | 116 | 10 | East | LTM04
137161 | 2017-11-22 | Tree Contacts | Broken Branch | Tree branches caused fuse to blow at transformer X33047, 29 Pineglen. | O/H Transformer | O/H Transformer (1ph) | 4 | 45 | 3 | South | 180F4
137162 | 2017-11-22 | Defective Equipment | Electrical Failure | Suspected cable fault between TP7050 & TE1575 caused S19551 B to open. FCI's gave false indication delaying restoration & isolation of defective cable. | U/G Cable | XLPE | 8 | 22 | 3 | East | 77M6
137162 | 2017-11-22 | Defective Equipment | Electrical Failure | Suspected cable fault between TP7050 & TE1575 caused S19551 B to open. FCI's gave false indication delaying restoration & isolation of defective cable. | U/G Cable | XLPE | 42 | 23 | 16 | East | 77M6
137162 | 2017-11-22 | Defective Equipment | Electrical Failure | Suspected cable fault between TP7050 & TE1575 caused S19551 B to open. FCI's gave false indication delaying restoration & isolation of defective cable. | U/G Cable | XLPE | 57 | 67 | 64 | East | 77M6
137162 | 2017-11-22 | Defective Equipment | Electrical Failure | Suspected cable fault between TP7050 & TE1575 caused S19551 B to open. FCI's gave false indication delaying restoration & isolation of defective cable. | U/G Cable | XLPE | 99 | 8 | 13 | East | 77M6
137162 | 2017-11-22 | Defective Equipment | Electrical Failure | Suspected cable fault between TP7050 & TE1575 caused S19551 B to open. FCI's gave false indication delaying restoration & isolation of defective cable. | U/G Cable | XLPE | 190 | 49 | 155 | East | 77M6
137162 | 2017-11-22 | Defective Equipment | Electrical Failure | Suspected cable fault between TP7050 & TE1575 caused S19551 B to open. FCI's gave false indication delaying restoration & isolation of defective cable. | U/G Cable | XLPE | 199 | 109 | 362 | East | 77M6
137163 | 2017-11-22 | Scheduled Outage | Construction | overhead section fed from switch 238 white was isolated to switch feed to the blue phase. 29 customers were affected. Kanata (624F6) | None | None | 29 | 22 | 11 | West | 624F6
137165 | 2017-11-22 | Scheduled Outage | Construction | Transformer #X18246 isolated by crew to replace connections at the transformer | None | None | 2 | 15 | 0 | East | LTM04
137166 | 2017-11-22 | Scheduled Outage | Construction | Transformer #X48221 isolated by crew for a pole replacement | None | None | 15 | 266 | 66 | East | TB06
137167 | 2017-11-22 | Scheduled Outage | Construction | Brian from Sproule Powerlines to have transformer X30306 and X30307 open to transfer plant. Customers notified. | None | None | 23 | 231 | 89 | Central | UF07
137168 | 2017-11-23 | Defective Equipment | Electrical Failure | Transformer 377B at 82 Lightfoot was isolated to allow crew to replace defective transformer and inserts. Bridlewood (BRDF3) | U/G Transformer | Padmount (1ph) | 13 | 49 | 11 | West | BRDF3
137169 | 2017-11-23 | Scheduled Outage | Vegetation Management | At 9:09am a section of the 47F6 was isolated to allow Davey Tree to perform tree trimming. 82 customers affected. Bells Corners (47F6) | None | None | 82 | 334 | 456 | South | 47F6
137170 | 2017-11-23 | Scheduled Outage | Vegetation Management | Transformer #X29382 isolated by crew due to tree trimming | None | None | 11 | 55 | 10 | East | AE01
137171 | 2017-11-23 | Tree Contacts | Falling Tree | tree on primary | None | None | 46 | 13 | 10 | Central | AK02
137172 | 2017-11-23 | Scheduled Outage | Construction | Transformer #X14813 isolated by Chris from Sproule to energize new service | None | None | 10 | 23 | 4 | East | 4801F8
137174 | 2017-11-24 | Scheduled Outage | Maintenance | Replaing dip switches and installing new nomenclature at transformer PT33 | None | None | 1 | 83 | 1 | Central | TD06
137176 | 2017-11-24 | Foreign Interference | Wildlife (Bird/Animal) | The 7F4 CB A/R and cause the G30R to blow due to squirel contact at 4925 Bowesville. Limebank (7F4) | O/H Switchgear | Fused Cutout | 49 | 96 | 78 | East | 7F4
137177 | 2017-11-24 | Scheduled Outage | Vegetation Management | Switch S15005 to EOL was isolated to allow tree trimming crew to remove tree at rear of 10 Quinpool. Bellscorner (47F6). | None | None | 30 | 171 | 86 | South | 47F6
137178 | 2017-11-24 | Scheduled Outage | Construction | Transformers TP6664, TP663, TP6662, TP6666, TP6667, TP6668 and TP669 on Highbury Park was isolated to allow crew to remove S27494 and splice cables to connect 4 transformers between TP6664 and TP6663. Longfield (LGFF1) | None | None | 53 | 47 | 42 | South | LGFF1
137179 | 2017-11-24 | Scheduled Outage | Maintenance | PLANNED OUTAGE TO RE-DO TERMINATIONS, REMOVE ASBESTOS AND REPLACE INSULATORS | None | None | 17 | 83 | 24 | East | UA04
137180 | 2017-11-24 | Defective Equipment | Mechanical Failure | planned outage to allow crew to replace defective switch. | O/H Switchgear | Fused Cutout | 1 | 302 | 5 | East | AN05
137181 | 2017-11-24 | Scheduled Outage | Construction | OUTAGE REQUIRED TO TRANSFER PLANT | None | O/H Transformer (1ph) | 25 | 62 | 26 | Central | UL04
137182 | 2017-11-24 | Tree Contacts | Other Vegetation | Transformer #X23269 opened up due to vine contact | O/H Switchgear | Fused Cutout | 1 | 104 | 2 | Central | TK2AC
137183 | 2017-11-25 | Scheduled Outage | Construction | Mark Brown and crew to have transformer X5732 open to install a new pole. Customers notified. | None | None | 4 | 480 | 32 | South | 180F6
137184 | 2017-11-25 | Foreign Interference | Wildlife (Bird/Animal) | Jordan Grant reports that transformer X46734 openned due to animal contact. Crew refused and restored. | O/H Switchgear | Fused Cutout | 48 | 42 | 34 | Central | TW17
137185 | 2017-11-26 | Scheduled Outage | Construction | To convert a section of the BRDF7 from 8kv to 27kv. | None | None | 1 | 145 | 2 | West | BRDF7
137186 | 2017-11-26 | Scheduled Outage | Maintenance | Transformer 4550 isolated to allow crew to straighten transformer on base and replace elbow/inserts and rebuild riser. | None | None | 1 | 439 | 7 | West | 624F5
137187 | 2017-11-27 | Scheduled Outage | Construction | TB15 overhead from S20629 to EOL on Hamlet St. isolated to allow crew to tranfer overhead to new poles. 24 customers affected. Russell (TB15) | None | None | 24 | 284 | 114 | East | TB15
137188 | 2017-11-27 | Scheduled Outage | Vegetation Management | S604 opened to isolated overhead line for tree trimming. | None | None | 78 | 325 | 422 | South | 49F6
137189 | 2017-11-27 | Scheduled Outage | Construction | Transformer #X30196 isolated by crew for a service upgrade, Chris Trafford and Evan Cowell | None | None | 16 | 20 | 5 | Central | UJ02
137190 | 2017-11-27 | Scheduled Outage | Construction | Glen Carswell and crew to have transformer X30656 open to install a new service. Customers notified. | None | None | 44 | 137 | 100 | Central | AB05
137191 | 2017-11-27 | Scheduled Outage | Construction | Glen Carswell and crew to have transformer X30652 open to rearrange secondary services. Customers notified. | None | None | 22 | 33 | 12 | Central | AB05
137192 | 2017-11-27 | Defective Equipment | Electrical Failure | S21557 R 77M6. | U/G Cable | XLPE | 123 | 101 | 207 | East | 77M6
137193 | 2017-11-28 | Scheduled Outage | Maintenance | Transformer PT167 was isolated to allow crew to replace switches feeding PT167. Lincoln Hieghts (TD01) | None | None | 1 | 70 | 1 | Central | TD01
137194 | 2017-11-28 | Scheduled Outage | Vegetation Management | planned outage for tree trimming | None | None | 68 | 117 | 133 | South | 190F5
137195 | 2017-11-28 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X32378 TO REPLACE SWITCH | None | None | 16 | 50 | 13 | Central | TD06
137197 | 2017-11-28 | Scheduled Outage | Maintenance | Cable injection on 4 cable sections. Outage to customers due to non-vented elbows. | None | None | 30 | 163 | 82 | East | 77M5
137198 | 2017-11-28 | Scheduled Outage | Maintenance | Cable injection to 4 cable section. Outage due to non-vented elbows. | None | None | 29 | 163 | 79 | East | 77M5
137199 | 2017-11-28 | Defective Equipment | Defective Equipment/ Material | SC11-CB3 tripped open on the B phase due to KT367 blown elbow | U/G Transformer | Kiosk (1ph) | 17 | 240 | 68 | East | 2204
137199 | 2017-11-28 | Defective Equipment | Defective Equipment/ Material | SC11-CB3 tripped open on the B phase due to KT367 blown elbow | U/G Transformer | Kiosk (1ph) | 37 | 27 | 17 | East | 2204
137199 | 2017-11-28 | Defective Equipment | Defective Equipment/ Material | SC11-CB3 tripped open on the B phase due to KT367 blown elbow | U/G Transformer | Kiosk (1ph) | 57 | 20 | 19 | East | 2204
137199 | 2017-11-28 | Defective Equipment | Defective Equipment/ Material | SC11-CB3 tripped open on the B phase due to KT367 blown elbow | U/G Transformer | Kiosk (1ph) | 74 | 63 | 78 | East | 2204
137199 | 2017-11-28 | Defective Equipment | Defective Equipment/ Material | SC11-CB3 tripped open on the B phase due to KT367 blown elbow | U/G Transformer | Kiosk (1ph) | 143 | 75 | 179 | East | 2204
137199 | 2017-11-28 | Defective Equipment | Defective Equipment/ Material | SC11-CB3 tripped open on the B phase due to KT367 blown elbow | U/G Transformer | Kiosk (1ph) | 150 | 79 | 198 | East | 2204
137201 | 2017-11-29 | Defective Equipment | Defective Equipment/ Material | A suspected cabl;e fault at 1486 Innes caused a inline fused switch to open affecting 17 customers. Load was restored in stages. Cyrville CYRF4 | U/G Cable | XLPE | 2 | 62 | 2 | East | CYRF4
137201 | 2017-11-29 | Defective Equipment | Defective Equipment/ Material | A suspected cabl;e fault at 1486 Innes caused a inline fused switch to open affecting 17 customers. Load was restored in stages. Cyrville CYRF4 | U/G Cable | XLPE | 17 | 75 | 21 | East | CYRF4
137202 | 2017-11-28 | Defective Equipment | Electrical Failure | A suspected cable fault caused a switchgear fuse to open at Chantenay and Bilberry affecting 221 customers. Load was restored in stages. Bilberry Creek 77M6 | U/G Cable | XLPE | 72 | 13 | 16 | East | 77M6
137202 | 2017-11-28 | Defective Equipment | Electrical Failure | A suspected cable fault caused a switchgear fuse to open at Chantenay and Bilberry affecting 221 customers. Load was restored in stages. Bilberry Creek 77M6 | U/G Cable | XLPE | 193 | 95 | 306 | East | 77M6
137202 | 2017-11-28 | Defective Equipment | Electrical Failure | A suspected cable fault caused a switchgear fuse to open at Chantenay and Bilberry affecting 221 customers. Load was restored in stages. Bilberry Creek 77M6 | U/G Cable | XLPE | 221 | 89 | 328 | East | 77M6
137203 | 2017-11-29 | Scheduled Outage | Construction | Planned outage for J Lewandousky to remove temp service and install permanent service | None | None | 1 | 2954 | 49 | West | 624F1
137204 | 2017-11-29 | Scheduled Outage | Construction | Planned outage to replace Bell Canada owned poles. | None | None | 15 | 218 | 54 | East | 8F1
137206 | 2017-11-29 | Scheduled Outage | Construction | To replace insulators and switches. | None | None | 43 | 75 | 54 | Central | TD06
137207 | 2017-11-29 | Scheduled Outage | Construction | Transformer #X33278 isolated by crew to energize streetlight service, Bobby Mcnabb | None | None | 12 | 60 | 12 | Central | UV03
137208 | 2017-11-29 | Defective Equipment | Mechanical Failure | REPLACED BLOWN FUSE FEEDING TRANSFORMER X12814 (CAUSED BY OPEN WIRE BUSS MAKING CONTACT WITH NEUTRAL) | O/H Transformer | O/H Transformer (1ph) | 7 | 92 | 11 | East | 7F2
137210 | 2017-11-29 | Scheduled Outage | Construction | Transformer #X48214 isolated by crew to install new secondary | None | None | 5 | 242 | 20 | East | TB06
137211 | 2017-11-29 | Scheduled Outage | Vegetation Management | planned outage for tree trimmimng | None | None | 64 | 271 | 289 | South | 200F3
137212 | 2017-11-29 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact caused Transformer infront of 34 Ohara to blow and Switch 111B to blow | O/H Transformer | O/H Transformer (1ph) | 30 | 58 | 29 | West | 624F6
137213 | 2017-11-30 | Scheduled Outage | Construction | Transformer #X30016 isolated by crew to install new service, Chris Trafford | None | None | 12 | 50 | 10 | Central | SB09
137214 | 2017-11-30 | Scheduled Outage | Maintenance | transformer TP12188 at 105 Schneider was isolated to replace leaking transformer. One customer was affected. Kanata (624F5) | None | Padmount (3ph) | 1 | 66 | 1 | West | 624F5
137215 | 2017-11-30 | Scheduled Outage | Construction | Chris from Sproule Powerlines to have transformer X32440 open to install a new service. Customers notified. | None | None | 8 | 56 | 7 | Central | TW22
137216 | 2017-11-30 | Scheduled Outage | Construction | Overhead line section was isolated to allow crew to replace hydro pole at 53 Quinpool. 18 customers were affected. Bells corners (47F6) | None | None | 18 | 228 | 68 | South | 47F6
137217 | 2017-11-30 | Defective Equipment | Defective Equipment/ Material | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X34231 | O/H Transformer | O/H Transformer (1ph) | 10 | 178 | 30 | Central | UL04
137218 | 2017-12-01 | Scheduled Outage | Maintenance | Secondary Maintenance on TP2082 | None | None | 1 | 52 | 1 | East | 5303
137219 | 2017-12-01 | Scheduled Outage | Construction | Transformer #X32504 isolated by crew for a service upgrade, Evan Cowell | None | None | 11 | 60 | 11 | Central | TD01
137220 | 2017-12-01 | Scheduled Outage | Maintenance | transformers TE991, TE990, and TP7088 were isolated to allow crew to perform cable injection tests. 31 customers were interrupted. Billberry (77M6) | None | None | 31 | 158 | 82 | East | 77M6
137221 | 2017-12-01 | Scheduled Outage | Construction | Transformer #X23887 isolated by crew to transfer plant | None | None | 4 | 105 | 7 | Central | TH06
137222 | 2017-12-01 | Scheduled Outage | Maintenance | transformers were isolated on Decaire and Genoble to all crew to perform cable injection testing. 26 customers were affected. | None | None | 26 | 93 | 40 | East | 77M6
137225 | 2017-12-02 | Scheduled Outage | Construction | A section of primary overhead at 5854 Fallowfield was isolated for reconfiguration affecting 1 customer. Richmond North RHNF1 | None | None | 1 | 348 | 6 | West | RHNF1
137226 | 2017-12-02 | Defective Equipment | Mechanical Failure | A transformer at 395 Beatrice was isolated to change a leaking transformer affecting 13 customers. Limebank LMBF7 | U/G Transformer | Padmount (1ph) | 13 | 54 | 12 | East | LMBF7
137227 | 2017-12-02 | Defective Equipment | Mechanical Failure | A transformer at 123 Markland was isolated to change a leaking transformer affecting 14 customers. Limebank LMBF7 | U/G Transformer | Padmount (1ph) | 14 | 59 | 14 | East | LMBF7
137228 | 2017-12-02 | Defective Equipment | Mechanical Failure | A transformer at 11 Redpath was isolated to replace a leaking transformer affecting 13 customers. Limebank LMBF7 | U/G Transformer | Padmount (1ph) | 13 | 59 | 13 | East | LMBF7
137229 | 2017-12-02 | Defective Equipment | Mechanical Failure | A transformer at 59 Roblyn was isolated to change a leaking transformer affecting 9 customers. Limebank LMBF7 | U/G Transformer | Padmount (1ph) | 9 | 40 | 6 | East | LMBF7
137230 | 2017-12-02 | Defective Equipment | Mechanical Failure | A transformer at 242 Redpath was isolated to replace a leaking transformer affecting 11 customers. Limebank LMBF7 | U/G Transformer | Padmount (1ph) | 11 | 53 | 10 | East | LMBF7
137231 | 2017-12-03 | Scheduled Outage | Maintenance | 4 KV vault V673 at 2211 Riverside was isolated to allow contractor to perfrom vault maintenance, remove asbestos and crew to reaplce overhead switches. Brookfield (AF02) | None | None | 1 | 304 | 5 | East | AF02
137232 | 2017-12-03 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X45112 open due to squirrel contact. Woodroffe (TW17) | O/H Switchgear | Fused Cutout | 28 | 85 | 40 | Central | TW17
137233 | 2017-12-03 | Scheduled Outage | Construction | A transformer at 3804 Carling was opened to clear a service from stringing new primary affecting 1 customer. Stafford 200F1 | None | None | 1 | 11 | 0 | South | 200F1
137234 | 2017-12-03 | Scheduled Outage | Construction | A customer substation at 3701 Carling was isolated to reconfigure 44kv overhead feeding the substation affecting 1 customer. South March A9M2 | None | None | 1 | 253 | 4 | West | A9M2
137235 | 2017-12-04 | Scheduled Outage | Maintenance | Transformers TE996, TE995 and TP11500 were isolated to allow crew to perfrom cable injection. Bilbery (77M6) | None | None | 30 | 122 | 61 | East | 77M6
137236 | 2017-12-04 | Scheduled Outage | Construction | isolISOLATED TRANSFORMER X26899 TO TRANSFER HYDRO PLANT TO THE NEW POLE | None | None | 14 | 240 | 56 | East | TB15
137237 | 2017-12-04 | Scheduled Outage | Construction | ISOLTAED TRANSFORMER X48062 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 30 | 3 | East | TB15
137238 | 2017-12-04 | Scheduled Outage | Construction | ISOLTAED TRANSFORMER X48065 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 9 | 30 | 4 | East | TB15
137239 | 2017-12-04 | Scheduled Outage | Construction | A section of primary overhead at 3700 Carling was isolated to remove old overhead and transfer customers to new affecting 3 customers. Stafford 200F1 | None | None | 3 | 284 | 14 | South | 200F1
137240 | 2017-12-05 | Scheduled Outage | Vegetation Management | Tree removal by crane | None | None | 37 | 265 | 163 | Central | TR09
137241 | 2017-12-05 | Scheduled Outage | Construction | To transfer plant and remove old overhead conductor. | None | O/H Conductor | 4 | 120 | 8 | South | 200F1
137242 | 2017-12-05 | Scheduled Outage | Construction | To relocate VT552 supply | None | None | 1 | 336 | 6 | Central | TH06
137243 | 2017-12-05 | Scheduled Outage | Maintenance | Metering inspection | None | None | 1 | 73 | 1 | Central | 5405
137244 | 2017-12-05 | Tree Contacts | Falling Tree | Tree on overhead conductor affecting 4 customers. BLKF5 | None | None | 4 | 87 | 6 | East | BLKF5
137245 | 2017-12-05 | Scheduled Outage | Construction | Chris from Sproule to have transformer X35872 open to energize a new service. Customers notified. | None | None | 4 | 65 | 4 | South | EPWF1
137246 | 2017-12-05 | Scheduled Outage | Maintenance | Shaun Cunningham and crew to have transformer X29154 open to replace live line clamp. | None | None | 10 | 12 | 2 | East | UT02
137247 | 2017-12-05 | Scheduled Outage | Maintenance | Jeremy Tufts and crew to have transformer X15366 open to change connections on the service to 10 Kemp Dr. | None | None | 9 | 23 | 3 | East | LTM01
137248 | 2017-12-05 | Scheduled Outage | Construction | Jeremy Tufts to have transformer X33370 open install a new service. | None | None | 13 | 40 | 9 | South | EPWF3
137250 | 2017-12-05 | Tree Contacts | Tree Growth/ Untrimmed Tree | The UG05 circuit trip due to high winds which caused a tree contact at 80 Rideau Tres affecting 231 customers, crews patrol the rest of the circuit and found nothing | O/H Conductor | Unknown \ Other | 231 | 48 | 185 | East | UG05
137251 | 2017-12-06 | Tree Contacts | Falling Tree | tree contact caused overhead tansformer X19125at 2491 cleroux to open. 11 customers were affected. Blackburn (BLKF3) | O/H Transformer | O/H Transformer (1ph) | 11 | 71 | 13 | East | BLKF5
137252 | 2017-12-06 | Scheduled Outage | Maintenance | Switch upgrade and service repair at X36090 | None | None | 17 | 51 | 14 | Central | TD05
137254 | 2017-12-06 | Scheduled Outage | Construction | Chris from Sproule Powerlines to have transformer X06222 open to install a new service. | None | None | 1 | 75 | 1 | South | 180F4
137255 | 2017-12-06 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32493 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 9 | 170 | 26 | Central | TD06
137256 | 2017-12-06 | Scheduled Outage | Construction | Stuart Maclaren and crew to have transformer X48062 open to transfer plant. Customers notified. | None | None | 6 | 235 | 24 | East | TB15
137257 | 2017-12-06 | Defective Equipment | Mechanical Failure | change out leaking and rusting transformer | U/G Transformer | Padmount (1ph) | 10 | 307 | 51 | West | 39F2
137258 | 2017-12-06 | Defective Equipment | Mechanical Failure | As per Jeremy Tufts transformer X39615 openned due to a defective transformer switch. Crew repaired and restored power. | O/H Switchgear | Fused Cutout | 2 | 70 | 2 | South | FAL03
137260 | 2017-12-07 | Scheduled Outage | Construction | Switch S28391 to Eol was isolated to allow crew to relocate switch from pole X3981 to X45579. Jockvale (145F3) | None | None | 30 | 70 | 35 | South | 145F3
137263 | 2017-12-07 | Scheduled Outage | Construction | 8F1 W O/H section between G494 and TEMP44 on Quincy and Kaymar was isolated to allow crew to install secondary and transfer services. Moulton (8F1) | None | None | 25 | 286 | 119 | East | 8F1
137264 | 2017-12-07 | Scheduled Outage | Maintenance | VE8N avult maintenance by Carleton Electric. | None | None | 1 | 208 | 3 | South | 190F2
137265 | 2017-12-07 | Scheduled Outage | Construction | Chris from Sproule Powerlines and crew to have transformer X35088 open to install a new service. Customers notified. | None | None | 10 | 15 | 2 | Central | TD06
137266 | 2017-12-08 | Scheduled Outage | Construction | Transfering dip switches to new pole. | None | None | 1 | 114 | 2 | East | AN05
137267 | 2017-12-08 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35110 TO REPAIR SECONDARY SERVICE | None | None | 7 | 47 | 5 | Central | UV03
137268 | 2017-12-08 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X30074 TO REPLACE OPEN WIRE SECONDARY BUSS WITH TRIPLEX | None | None | 15 | 210 | 52 | Central | SB06
137269 | 2017-12-08 | Scheduled Outage | Vegetation Management | ISOLATED TRANSFORMER X28202 FOR FORESTRY TO TRIM TREES AROUND SECONDAY BUSS | None | None | 12 | 190 | 38 | East | UQ03
137270 | 2017-12-08 | Foreign Interference | Wildlife (Bird/Animal) | Matt Gabriel reports that possible animal contact mau have openned transformer X32848. Crew refused and restored power. | O/H Switchgear | Fused Cutout | 8 | 87 | 12 | Central | TD05
137272 | 2017-12-10 | Defective Equipment | Mechanical Failure | Suspected cable fault on th ELW05 cuased the ELW05 breaker to trip | U/G Cable | XLPE | 109 | 10 | 18 | East | ELW05
137272 | 2017-12-10 | Defective Equipment | Mechanical Failure | Suspected cable fault on th ELW05 cuased the ELW05 breaker to trip | U/G Cable | XLPE | 163 | 3 | 8 | East | ELW05
137272 | 2017-12-10 | Defective Equipment | Mechanical Failure | Suspected cable fault on th ELW05 cuased the ELW05 breaker to trip | U/G Cable | XLPE | 163 | 22 | 60 | East | ELW05
137273 | 2017-12-11 | Scheduled Outage | Construction | Kevin Mckenna and crew to have transformer X06249 open to instal fusing for streetlights. | None | None | 1 | 65 | 1 | South | 180F4
137274 | 2017-12-11 | Foreign Interference | Wildlife (Bird/Animal) | David Gill reports that squirrel contact caused the fuse at transformer X32950 to open. Crew refused and restored. | O/H Switchgear | Fused Cutout | 14 | 66 | 15 | Central | TD07
137275 | 2017-12-11 | Scheduled Outage | Construction | Greg Forbes from J.W. Leslie to have transformer K339 open to replace the pedestal. Customers notified. | None | None | 8 | 157 | 21 | East | AL02
137276 | 2017-12-11 | Scheduled Outage | Construction | Transformer #X27414 isolated by crew to relocate primary | None | None | 1 | 155 | 3 | East | AN05
137277 | 2017-12-11 | Scheduled Outage | Construction | Kevin Mckenna to have transformer X33911 open to install the triplex to 2044 Neepawa. | None | None | 12 | 55 | 11 | Central | TD06
137278 | 2017-12-11 | Scheduled Outage | Construction | Stuart Maclaren to have transformer X48071 open to move secondary and install a new transformer. Customers notified. | None | None | 16 | 300 | 80 | East | TB15
137279 | 2017-12-11 | Scheduled Outage | Construction | richmond south circuits were isolated to allow crews to install poles and transfer plant. 132 customers were affected. Richmond south (28F1, 28F2) | None | None | 11 | 319 | 58 | West | 28F2
137279 | 2017-12-11 | Scheduled Outage | Construction | richmond south circuits were isolated to allow crews to install poles and transfer plant. 132 customers were affected. Richmond south (28F1, 28F2) | None | None | 121 | 319 | 643 | West | 28F1
137281 | 2017-12-11 | Tree Contacts | Other Vegetation | Vegetation caused switch S803 at 94 queensline to flash over, which opened the breaker at QCH station. 519 customers were affected. QCH (160F1) | O/H Switchgear | Fused Cutout | 146 | 35 | 85 | South | 160F1
137281 | 2017-12-11 | Tree Contacts | Other Vegetation | Vegetation caused switch S803 at 94 queensline to flash over, which opened the breaker at QCH station. 519 customers were affected. QCH (160F1) | O/H Switchgear | Fused Cutout | 519 | 88 | 761 | South | 160F1
137282 | 2017-12-11 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X3600 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 1 | 427 | 7 | South | 200F1
137283 | 2017-12-12 | Scheduled Outage | Construction | Transformer 2529W at 34 Country Lane isolated to install new primary cable. 16 customers affected. Bridelwood (BRDF5) | None | XLPE | 16 | 661 | 176 | West | BRDF5
137284 | 2017-12-12 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X23715 TO REPAIR SECONDARY SERVICE | None | None | 9 | 124 | 19 | East | AA05
137285 | 2017-12-13 | Defective Equipment | Defective Equipment/ Material | Not yet known. | O/H Transformer | O/H Transformer (1ph) | 25 | 55 | 23 | Central | SR07
137287 | 2017-12-13 | Scheduled Outage | Maintenance | K774 at 2610 Draper including new S11632 & S16388 isolated to replace switches, insulators & arrestors. 16 customers affected. Edwin UV02 | None | None | 16 | 70 | 19 | Central | UV02
137288 | 2017-12-13 | Scheduled Outage | Maintenance | V423 at 50 James St. isolated to allow crew to re-insulate riser pole, replace switches and arrestors. | None | None | 24 | 94 | 38 | Central | UF04
137289 | 2017-12-13 | Scheduled Outage | Maintenance | VT260 at 370 Dominion was isolated to allow HOL crew to make metering repairs. | None | None | 1 | 200 | 3 | Central | TM1AH
137290 | 2017-12-13 | Scheduled Outage | Construction | Mark Brown and crew to have transformer X36232 open to re-arrange secondary plant. Customer notified. | None | None | 10 | 155 | 26 | South | 190F5
137291 | 2017-12-14 | Scheduled Outage | Construction | To allow Hydro Ottawa cable & line crews change transformer K736 | None | Kiosk (1ph) | 3 | 218 | 11 | East | UZ07
137292 | 2017-12-14 | Scheduled Outage | Maintenance | TP10782 was isolated for soil remendition. | None | Kiosk (1ph) | 7 | 490 | 57 | East | 8F3
137293 | 2017-12-14 | Defective Equipment | Electrical Failure | White phase arrester at X17697 went defective and caused BECKF2 to open under hold-off. | O/H Conductor | O/H Conductor | 1282 | 171 | 3654 | West | BECKF2
137294 | 2017-12-14 | Scheduled Outage | Maintenance | Defective switch at S692 on the center phase! | None | Inline Switch | 105 | 18 | 32 | South | 170F3
137295 | 2017-12-15 | Defective Equipment | Mechanical Failure | To replace transformer. | U/G Transformer | Kiosk (1ph) | 1 | 166 | 3 | South | 200F1
137298 | 2017-12-15 | Scheduled Outage | Construction | Evan Cowell and crew to have transformer X33661 open to install a new service. Customers notified. | None | None | 7 | 45 | 5 | Central | TW22
137299 | 2017-12-15 | Scheduled Outage | Construction | Stuart Maclaren and crew to have transformer X48080 open to rearrange the secondary services. Customers notified. | None | None | 8 | 285 | 38 | East | TB15
137302 | 2017-12-16 | Human Element | Switching Error | Incorrect switching order. | None | None | 855 | 5 | 71 | West | 624F2
137303 | 2017-12-17 | Foreign Interference | Wildlife (Bird/Animal) | tansformer X33397 fuse blew due to animal contact | O/H Transformer | O/H Transformer (1ph) | 8 | 81 | 11 | South | 190F2
137304 | 2017-12-17 | Defective Equipment | Defective Equipment/ Material | Defective elbow at TP9342 affecting 8 customers. Bayshore DS (49F6). | U/G Cable Attachement | Elbow \ Insert | 8 | 730 | 97 | South | 49F6
137305 | 2017-12-17 | Defective Equipment | Mechanical Failure | Not yet known. | O/H Transformer | O/H Transformer (1ph) | 10 | 465 | 78 | East | TB07
137308 | 2017-12-18 | Scheduled Outage | Construction | isolated transformer X29114 to transfer hydro plant to new pole | None | None | 8 | 241 | 32 | East | TB15
137309 | 2017-12-18 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X36457 TO REPLACE SWITCH AND ARRESTER | None | None | 4 | 39 | 3 | West | 44F1
137310 | 2017-12-19 | Scheduled Outage | Construction | planned outage to allow for voltage conversion | None | None | 133 | 217 | 481 | West | 44F1
137311 | 2017-12-19 | Scheduled Outage | Vegetation Management | S25769 to Eol was isolated to allow tree trimming crew to perfrom tree trimming. 42 customers were affected. Lincoln Heights (TD01) | None | None | 42 | 243 | 170 | Central | TD01
137312 | 2017-12-19 | Scheduled Outage | Maintenance | Vault at 1365 bank was isolated to repair a malfunctioning switch affecting 1 customer. Riverdale 503 | None | None | 1 | 42 | 1 | Central | 503
137313 | 2017-12-19 | Scheduled Outage | Vegetation Management | A transformer at 3089 Otterson was opened to disconnect secondadies for tree removal affecting 3 customers. Walkley UZ12 | None | None | 3 | 50 | 2 | East | UZ12
137314 | 2017-12-19 | Scheduled Outage | Construction | A transformner at 19 Ellbry was opened to install a new service affecting 4 customers. Stafford 200F2 | None | None | 4 | 80 | 5 | South | 200F2
137316 | 2017-12-19 | Tree Contacts | Falling Tree | S28321 RW found blown at 755 Montreal, crew patrolled line and found a tree on the line. Langs (AP04). 25 customers were affected. | O/H Switchgear | Fused Cutout | 25 | 294 | 122 | East | AP04
137317 | 2017-12-19 | Adverse Environment | Fire | A pole fire at Bantree DS caused TB1AL, TB3LE, AL02 & AL04 to trip | Pole | Pole | 16 | 4 | 1 | East | TB1AL
137317 | 2017-12-19 | Adverse Environment | Fire | A pole fire at Bantree DS caused TB1AL, TB3LE, AL02 & AL04 to trip | Pole | Pole | 258 | 446 | 1918 | East | TB1AL
137317 | 2017-12-19 | Adverse Environment | Fire | A pole fire at Bantree DS caused TB1AL, TB3LE, AL02 & AL04 to trip | Pole | Pole | 366 | 116 | 708 | East | TB1AL
137317 | 2017-12-19 | Adverse Environment | Fire | A pole fire at Bantree DS caused TB1AL, TB3LE, AL02 & AL04 to trip | Pole | Pole | 2202 | 90 | 3303 | East | TB3LE
137318 | 2017-12-19 | Adverse Environment | Contamination (Salt) | Pole fire at X06688 Beaverbrook DS | None | None | 2062 | 55 | 1890 | West | A9M3
137318 | 2017-12-19 | Adverse Environment | Contamination (Salt) | Pole fire at X06688 Beaverbrook DS | None | None | 3232 | 49 | 2639 | West | A9M3
137318 | 2017-12-19 | Adverse Environment | Contamination (Salt) | Pole fire at X06688 Beaverbrook DS | None | None | 8966 | 7 | 1046 | West | A9M3
137319 | 2017-12-20 | Adverse Environment | Contamination (Salt) | S1171 failed due to pole fire. 3 Customers were affected. Rideau Heights 180F6 | O/H Switchgear | Fused Cutout | 3 | 365 | 18 | South | 180F6
137320 | 2017-12-20 | Defective Equipment | Mechanical Failure | planned outage to replace defective transformer | U/G Transformer | Padmount (1ph) | 23 | 61 | 23 | West | BRDF3
137321 | 2017-12-20 | Scheduled Outage | Construction | S28144 to EOL was isolated to allow crew to transformer supply from R phase to W phase. Janet king (JKGF4). 38 customers were affected | None | None | 38 | 64 | 41 | West | JKGF4
137322 | 2017-12-20 | Scheduled Outage | Construction | Transformer #X27248 isolated by crew to reconnect a service | None | None | 3 | 62 | 3 | East | UZ12
137323 | 2017-12-20 | Scheduled Outage | Forced Switching | S767 to EOL was isolated to allow crew to reaplce defective switch and replace borken insulator. Barrhaven (140F3). 1 customer was affected | None | Fused Cutout | 1 | 174 | 3 | South | 140F3
137324 | 2017-12-20 | Scheduled Outage | Maintenance | Transformer TP10782 at 1482 Bortolotti was isolated to allow crew to perfrom soil remediation. Moulton (8F3). 9 customers were affected | None | Padmount (1ph) | 9 | 137 | 21 | East | 8F3
137325 | 2017-12-20 | Scheduled Outage | Construction | Transformer #X3962 isolated by crew to transfer plant | None | None | 4 | 40 | 3 | South | 145F3
137326 | 2017-12-20 | Scheduled Outage | Construction | Transformer #X36474 isolated by crew to replace switch | None | None | 4 | 27 | 2 | West | 44F1
137327 | 2017-12-20 | Scheduled Outage | Construction | Transformer #X3966 isolated by crew to transfer plant | None | None | 3 | 50 | 2 | South | 145F3
137328 | 2017-12-20 | Scheduled Outage | Construction | Transformer #X37108 isolated by crew to install new service, Bobby from Sproule | None | None | 5 | 65 | 5 | South | EPWF2
137329 | 2017-12-20 | Foreign Interference | Wildlife (Bird/Animal) | Collin Port and Oakley McCoy report transformer X48717 open due to animal contact. Crew refused and restored. | O/H Switchgear | Fused Cutout | 22 | 176 | 65 | Central | TW18
137330 | 2017-12-20 | Scheduled Outage | Maintenance | VE10 off loaded to allow SE1-F to be repaired. | None | None | 1 | 229 | 4 | East | BCHF1
137333 | 2017-12-21 | Scheduled Outage | Construction | INSTALL A NEW SEC SERVICE | None | None | 10 | 24 | 4 | Central | AH13
137334 | 2017-12-21 | Tree Contacts | Broken Branch | Tree took down primary neutral. | None | None | 9 | 182 | 27 | East | UZ12
137334 | 2017-12-22 | Tree Contacts | Broken Branch | Tree took down primary neutral. | None | None | 20 | 88 | 29 | East | UZ12
137335 | 2017-12-25 | Unknown/Other | Unknown | Not yet known, possible cable fault to be investigated. TR03 (TR2UY) supplying part of Carleton U tripped , load transferred to alternate source. 1 customer affected, Riverdale TR2UY. | Unknown \ Other | Unknown \ Other | 1 | 51 | 1 | Central | TR2UY
137336 | 2017-12-27 | Defective Equipment | Defective Equipment/ Material | A defective fuse at a three phase TP3455 cause a part out at 330 McArthur, crews isolated TP3455 to replace fuse affecting 4 customers on the 1802 circuit for 14 min | U/G Transformer | Padmount (3ph) | 4 | 14 | 1 | East | 1802
137340 | 2017-12-29 | Defective Equipment | Mechanical Failure | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X31887 | O/H Transformer | O/H Transformer (1ph) | 13 | 65 | 14 | Central | AD06
137341 | 2017-12-30 | Defective Equipment | Electrical Failure | Customers reported sparking wires at the rear of 651 Morin. A broken swtich at X23160 (651 Morin St) caused and outage to 10 customer. Church (AA06) | O/H Switchgear | Fused Cutout | 10 | 108 | 18 | East | AA06
137342 | 2017-12-31 | Foreign Interference | Vehicle | At vehicle hit a pole causing fuse S18753 to blow. 12 customers affected. Blackburn (BLKF5) | Pole | Pole | 12 | 101 | 20 | East | BLKF5
137344 | 2018-01-02 | Defective Equipment | Electrical Failure | Customer reported partial outage, fed from PT1566, Underground crew was called to investigate and through testing determined there was a defective transformer. Transformer was isolated and replaced 1 customer affected, Lincoln Heights (TD07) | U/G Transformer | Padmount (3ph) | 1 | 440 | 7 | Central | TD07
137345 | 2018-01-03 | Scheduled Outage | Construction | Jim Lewandowsky and crew to have transformers X36471, X36457, and X36473 open to convert to 16kV. Customers notified. | None | None | 12 | 39 | 8 | West | 44F1
137346 | 2018-01-03 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X25741 TO REPLACE SECONDARY CONNECTIONS | None | None | 11 | 39 | 7 | Central | SM12
137347 | 2018-01-03 | Defective Equipment | Mechanical Failure | Defective transformer cut out | O/H Switchgear | Fused Cutout | 4 | 75 | 5 | West | JKGF4
137348 | 2018-01-04 | Defective Equipment | Imminent Failure | At 09:31am TP6677 was isolated to allow crew to replace transformer. 11 customers affected. Bridlewood (BRDF7) | U/G Transformer | Padmount (1ph) | 11 | 82 | 15 | West | BRDF7
137349 | 2018-01-04 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X55981 TO MOVE HYDRO PLANT TO MAKE ROOM FOR NEW POLE | None | None | 4 | 32 | 2 | Central | UV03
137350 | 2018-01-04 | Scheduled Outage | Construction | Shaun Evans from K-Line to have transformers X30770 and X30768 open to move load. Customers notified. | None | None | 45 | 50 | 38 | Central | AB03
137351 | 2018-01-06 | Foreign Interference | Foreign Objects | TW06-B2 CB tripped due to milar balloon contact on the Overhead at (TW2UC). | None | None | 669 | 81 | 903 | Central | TW2UC
137352 | 2018-01-06 | Loss Of Supply | Transmission Inadvertent | Customer fed from RX2048 were interrupted due to loss of supply from Hydro One BECKF2. 1278 customers were affected. Beckwith (BECKF2) | None | None | 1278 | 17 | 362 | West | BECKF2
137353 | 2018-01-06 | Human Element | Protection Setting | Human Ellement incorrect protection settings at Beckwith. RX2048 opeened and CS14830 closed restoring all customers from Janet King | None | None | 1278 | 27 | 575 | West | BECKF2
137354 | 2018-01-06 | Human Element | Protection Setting | RX2048 tripped during extremely cold weather due to suspected high load. Line was patrolled & no problem found. Load restored using alternate supply. Load restored in stages. 1238 customers affected. Beckwith F2. | None | None | 341 | 22 | 125 | West | BECKF2
137354 | 2018-01-06 | Human Element | Protection Setting | RX2048 tripped during extremely cold weather due to suspected high load. Line was patrolled & no problem found. Load restored using alternate supply. Load restored in stages. 1238 customers affected. Beckwith F2. | None | None | 688 | 16 | 183 | West | BECKF2
137354 | 2018-01-06 | Human Element | Protection Setting | RX2048 tripped during extremely cold weather due to suspected high load. Line was patrolled & no problem found. Load restored using alternate supply. Load restored in stages. 1238 customers affected. Beckwith F2. | None | None | 973 | 56 | 908 | West | BECKF2
137354 | 2018-01-06 | Human Element | Protection Setting | RX2048 tripped during extremely cold weather due to suspected high load. Line was patrolled & no problem found. Load restored using alternate supply. Load restored in stages. 1238 customers affected. Beckwith F2. | None | None | 1278 | 29 | 618 | West | BECKF2
137355 | 2018-01-08 | Defective Equipment | Mechanical Failure | Transformer TE105 at 638 Glenhurst was isolated to allow crew to repalce broken insulators in transformer. Beaconhill (BCHF1) | U/G Transformer | Kiosk (1ph) | 6 | 85 | 8 | East | BCHF1
137356 | 2018-01-08 | Scheduled Outage | Construction | A transformer at 2343 Briarhill was opened to install a new secondary affecting 14 customers. Albion UA05 | None | None | 14 | 75 | 18 | East | UA05
137357 | 2018-01-08 | Scheduled Outage | Construction | A transformer at Nepean and Lyon was opened to transfer primary feed to another cicuit affecting 14 customers. Nepean AB03 | None | None | 14 | 9 | 2 | Central | AB03
137358 | 2018-01-08 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32709 TO TRANSFER HYDRO PLANT TO MAKE ROOM FOR NEW POLE | None | None | 12 | 33 | 7 | Central | UV03
137360 | 2018-01-09 | Scheduled Outage | Maintenance | Mark Brown and crew to have transformer NPTE0142 open to splice a secondary cable. | None | None | 9 | 67 | 10 | South | 84F3
137361 | 2018-01-09 | Scheduled Outage | Construction | To allow crews to remove a sevice. | None | Unknown \ Other | 10 | 22 | 4 | East | UB04
137362 | 2018-01-10 | Scheduled Outage | Construction | Dave Burns and crew to have transformer open to re-arrange equipment. Customers notified. | None | None | 5 | 54 | 4 | Central | UV03
137364 | 2018-01-11 | Defective Equipment | Electrical Failure | Underground cable fault between G76B & TE128 caused G76B to open. 56 customers affected. Blackburn BLKF4. | U/G Cable | Unknown \ Other | 56 | 200 | 187 | East | BLKF4
137365 | 2018-01-11 | Loss Of Supply | Third Party | Defective switchgear at VT345 cause TR07 breaker to trip, affecting 378 customers. Riverdale TS | None | None | 1 | 3259 | 54 | Central | 502
137365 | 2018-01-11 | Loss Of Supply | Third Party | Defective switchgear at VT345 cause TR07 breaker to trip, affecting 378 customers. Riverdale TS | None | None | 51 | 19 | 16 | Central | 502
137365 | 2018-01-11 | Loss Of Supply | Third Party | Defective switchgear at VT345 cause TR07 breaker to trip, affecting 378 customers. Riverdale TS | None | None | 328 | 2 | 11 | Central | 502
137365 | 2018-01-11 | Loss Of Supply | Third Party | Defective switchgear at VT345 cause TR07 breaker to trip, affecting 378 customers. Riverdale TS | None | None | 378 | 19 | 120 | Central | 502
137365 | 2018-01-11 | Loss Of Supply | Third Party | Defective switchgear at VT345 cause TR07 breaker to trip, affecting 378 customers. Riverdale TS | None | None | 378 | 67 | 422 | Central | 502
137366 | 2018-01-11 | Scheduled Outage | Construction | Jeff Nicholas and crew to have transformer TP5295 open to re-arrange secondaries. Customer notified. | None | None | 1 | 48 | 1 | West | 28F2
137367 | 2018-01-11 | Defective Equipment | Mechanical Failure | Shaun Cunningham and Doug Featherstone report that tranformer NPTE3243 lost power due to a defective dip switch. Replaced switch and refused to restore. | O/H Switchgear | Fused Cutout | 8 | 158 | 21 | South | 49F6
137368 | 2018-01-11 | Defective Equipment | Electrical Failure | Chris Peasley reports that transformer switch is faulty and requires replacing. Crew isolated transformer X20245 to replace. | U/G Transformer | Padmount (1ph) | 9 | 30 | 4 | East | LTM02
137369 | 2018-01-11 | Loss Of Supply | Third Party | Dump truck pulled down customer own neutral at 3545 Leitrim Rd (DND). Repairs made by contractor and power restored ESA# 1570070 | None | None | 1 | 601 | 10 | East | LTM01
137370 | 2018-01-12 | Tree Contacts | Broken Branch | Transformer X10774 open due to brach contact with transformer bushing . 2 customers were affected. Janet King (JKGF4) | O/H Transformer | O/H Transformer (1ph) | 2 | 64 | 2 | West | JKGF4
137371 | 2018-01-12 | Defective Equipment | Electrical Failure | Underground cable fault caused S21557B to open. 94 customers affected. Bilberry 77M6. | U/G Cable | Unknown \ Other | 25 | 38 | 16 | East | 77M6
137371 | 2018-01-12 | Defective Equipment | Electrical Failure | Underground cable fault caused S21557B to open. 94 customers affected. Bilberry 77M6. | U/G Cable | Unknown \ Other | 94 | 109 | 171 | East | 77M6
137372 | 2018-01-12 | Scheduled Outage | Construction | Mark Brown and crew to isolate tranformer X31620 to re-arrange secondary connections. Customers notified. | None | None | 12 | 60 | 12 | Central | AK04
137374 | 2018-01-12 | Loss Of Supply | Third Party | Defective customer owned equipment supplied by VT13 affected one customer. Carling TM (TM3SH) | None | None | 1 | 459 | 8 | Central | TM3SH
137375 | 2018-01-12 | Defective Equipment | Defective Equipment/ Material | Transformer #X32079 opened up due to the lead that pulled out of the switch | O/H Switchgear | Fused Cutout | 14 | 91 | 21 | Central | SM16
137376 | 2018-01-13 | Tree Contacts | Tree Growth/ Untrimmed Tree | trees in wires | O/H Conductor | O/H Conductor | 1 | 104 | 2 | West | 624F6
137378 | 2018-01-14 | Defective Equipment | Electrical Failure | A defective elbow at transformer 5795W on the 39F2 caused and outage to 570 customers. South March (39F2) | U/G Transformer | Padmount (1ph) | 5 | 524 | 44 | West | 39F2
137378 | 2018-01-14 | Defective Equipment | Electrical Failure | A defective elbow at transformer 5795W on the 39F2 caused and outage to 570 customers. South March (39F2) | U/G Transformer | Padmount (1ph) | 261 | 146 | 635 | West | 39F2
137378 | 2018-01-14 | Defective Equipment | Electrical Failure | A defective elbow at transformer 5795W on the 39F2 caused and outage to 570 customers. South March (39F2) | U/G Transformer | Padmount (1ph) | 338 | 4 | 23 | West | 39F2
137378 | 2018-01-14 | Defective Equipment | Electrical Failure | A defective elbow at transformer 5795W on the 39F2 caused and outage to 570 customers. South March (39F2) | U/G Transformer | Padmount (1ph) | 493 | 7 | 58 | West | 39F2
137378 | 2018-01-14 | Defective Equipment | Electrical Failure | A defective elbow at transformer 5795W on the 39F2 caused and outage to 570 customers. South March (39F2) | U/G Transformer | Padmount (1ph) | 570 | 59 | 560 | West | 39F2
137379 | 2018-01-15 | Scheduled Outage | Construction | Steve Rutherford from Sproule Powerlines to have transformers TP11596, TP11597, and TP11601 open to install new secondary services. Customers notified. | None | None | 3 | 355 | 18 | West | BRDF5
137380 | 2018-01-16 | Loss Of Supply | Transmission Inadvertent | Loss of supply | None | None | 1279 | 28 | 597 | West | BECKF2
137381 | 2018-01-17 | Scheduled Outage | Construction | Transformer #X33202 isolated by crew to remove a service | None | None | 13 | 23 | 5 | Central | TD05
137382 | 2018-01-17 | Defective Equipment | Electrical Failure | Replace defective transformer. | U/G Transformer | Padmount (1ph) | 14 | 120 | 28 | East | AN05
137383 | 2018-01-17 | Scheduled Outage | Construction | Voltage conversion. | None | None | 2 | 87 | 3 | South | FAL02
137384 | 2018-01-17 | Tree Contacts | Broken Branch | Transformer #X36381 opened up due to tree contact | O/H Switchgear | Fused Cutout | 4 | 48 | 3 | South | 72F4
137385 | 2018-01-17 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X29998 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 8 | 162 | 22 | Central | TR09
137386 | 2018-01-17 | Scheduled Outage | Construction | Steve Rutherford and crew from Sproule to have transformers 002528 and 003118 open to remove services. Services are being re fed from new plant in the front of properties. Customers notified. | None | None | 20 | 60 | 20 | West | BRDF5
137387 | 2018-01-17 | Defective Equipment | Electrical Failure | Defective secondary conductor | Secondary \ Service | O/H Service | 8 | 46 | 6 | East | TB07
137389 | 2018-01-18 | Scheduled Outage | Construction | Underground circuit re-configuration on the BRDF5 out of Bridlewood affecting 5 customers | None | None | 5 | 356 | 30 | West | BRDF5
137390 | 2018-01-18 | Scheduled Outage | Construction | planned outage to crane in new poles | None | None | 30 | 156 | 78 | East | TB06
137391 | 2018-01-18 | Defective Equipment | Electrical Failure | DEFECTIVE SEC BUSHING ON THE TRANS | O/H Transformer | O/H Transformer (1ph) | 8 | 110 | 15 | Central | AK07
137394 | 2018-01-19 | Scheduled Outage | Construction | Replace Transformer | None | O/H Transformer (1ph) | 5 | 312 | 26 | West | 28F2
137398 | 2018-01-20 | Scheduled Outage | Construction | A section of Uplands 4801F7 from Temp152 on Lester rd was isolated to install new pole & primary conductor, 2 customers affected. | None | None | 2 | 473 | 16 | East | 4801F7
137399 | 2018-01-20 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused fuse to open at X41262, 4210 Boundary. 4 customers affected. Leitrim 249F2. | None | None | 4 | 112 | 7 | East | LTM02
137400 | 2018-01-21 | Foreign Interference | Wildlife (Bird/Animal) | Brad Fraser and crew to investigate customer outage. Crew reported finding a squirrel at the base of the transformer at 320 John Aselford Way. Crew refused and restored power. | O/H Switchgear | Fused Cutout | 2 | 104 | 3 | West | MWDF3
137401 | 2018-01-21 | Scheduled Outage | Construction | A section of Uplands 4801F7 from Temp137 on Lester was isolated to install new pole and primary conductor. 5 customers were affected. Uplands (4801F7) | None | None | 5 | 375 | 31 | East | 4801F7
137402 | 2018-01-21 | Scheduled Outage | Construction | Bad connections. | None | None | 13 | 40 | 9 | Central | AD06
137404 | 2018-01-22 | Scheduled Outage | Construction | Transformer #TP5027 isolated by crew to transfer plant | None | None | 16 | 20 | 5 | Central | SM12
137405 | 2018-01-22 | Scheduled Outage | Construction | TP9991 at 3328 Huntley was isolated to replace primary cables. 1 customer affected. Richmond South 28F1. | None | None | 1 | 280 | 5 | West | 28F1
137406 | 2018-01-22 | Scheduled Outage | Construction | A brief outage took place to customers on Shea & Flewellyn during planned switching due to an out of phase condition, 30 customers affected. Richmond North RHNF1. | None | None | 30 | 2 | 1 | West | RHNF1
137407 | 2018-01-22 | Scheduled Outage | Construction | Bobby McNabb and crew from Sproule Powerlines to have transformer X33515 open to install a new service. Customers notified. | None | None | 4 | 45 | 3 | Central | AK02
137408 | 2018-01-22 | Scheduled Outage | Construction | Jordan Foote from K-Line to have transformers X30768 and X30770 open to rearrange secondaries. Customers Notified. | None | None | 45 | 71 | 53 | Central | AB03
137409 | 2018-01-22 | Adverse Weather | Extreme Wind | Customer reported seeinga flash at at Rideau Terrace and Springfield. Possible conductor slap at this location. | O/H Conductor | O/H Conductor | 230 | 16 | 61 | East | UG05
137410 | 2018-01-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X3122 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 10 | 276 | 46 | Central | AB03
137411 | 2018-01-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMERS X31045 TO TRANSFER HYDRO PLANT | None | None | 10 | 10 | 2 | Central | UF05
137412 | 2018-01-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31150 TO TRANSFER HYDRO PLANT | None | None | 35 | 15 | 9 | Central | AB06
137413 | 2018-01-23 | Defective Equipment | Electrical Failure | Faulty transformer at 305 Stoneway affecting 15 customers. Limebank LMBF7 | U/G Transformer | Padmount (1ph) | 15 | 456 | 114 | East | LMBF7
137414 | 2018-01-24 | Scheduled Outage | Construction | A section of overhead line was isolated on Weston and Dorval St to allow crew to replace poles. 57 customers were affected. Russell (TB06) | None | None | 57 | 411 | 390 | East | TB06
137415 | 2018-01-24 | Scheduled Outage | Construction | TP3375 isolated for riser cable upgrade, affecting 1 customer. Richmond South DS (28F2) | None | None | 1 | 146 | 2 | West | 28F2
137416 | 2018-01-24 | Scheduled Outage | Construction | A transformer at 91 Country Lane was isolated for primary cable re-configuration affecting 7 customers. Bridlewood BRDF5 | None | None | 7 | 392 | 46 | West | BRDF5
137417 | 2018-01-24 | Defective Equipment | Imminent Failure | A transformer at 5 Henry Goulbourn was isolated to replace a leaking transformer affecting 6 customers. Janet King JKGF4 | U/G Transformer | Padmount (1ph) | 6 | 257 | 26 | West | JKGF4
137418 | 2018-01-24 | Scheduled Outage | Construction | SOLATED FOUR TRANSFORMERS X33974, X33975, X33976, AND X33977 TO INSTALL NEW POLES | None | None | 63 | 160 | 168 | Central | UV03
137419 | 2018-01-24 | Foreign Interference | Foreign Objects | Transformer #X32623 opened up due to foreign interference (balloons) | O/H Switchgear | Fused Cutout | 16 | 81 | 22 | Central | TD14
137420 | 2018-01-24 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X24653 DUE TO SQUIRREL CONTACT | O/H Transformer | O/H Transformer (1ph) | 13 | 80 | 17 | East | TB14
137421 | 2018-01-25 | Defective Equipment | Electrical Failure | Suspected cable fault between S24757 & TE122 caused S24757 to open. 58 customers affected. Balckburn BLKF4. | U/G Cable | Unknown \ Other | 58 | 125 | 121 | East | BLKF4
137422 | 2018-01-24 | Scheduled Outage | Construction | Dan Crough from K-Line to have transformers X31150, X31123, and X31124 open to transfer plant to new poles. Customers notified. | None | None | 69 | 360 | 414 | Central | AB03
137424 | 2018-01-25 | Defective Equipment | Mechanical Failure | Insert and elbow replacement. | U/G Cable Attachement | Elbow \ Insert | 8 | 110 | 15 | South | 87F4
137425 | 2018-01-25 | Scheduled Outage | Construction | UV03 OH from pole X50112 to EOL isolated to set in new poles, affected 15 customers. Edwin (UV03). | None | None | 15 | 305 | 76 | Central | UV03
137426 | 2018-01-25 | Scheduled Outage | Construction | Patrick Brisson and crew to have transformer X25702 and X25703 open to install new poles. Customers notified. | None | None | 8 | 240 | 32 | Central | SM12
137427 | 2018-01-26 | Scheduled Outage | Construction | TP9991 at 3338 Huntley Rd. was isolated to allow crews to transfer plant. 1 customer affected. Richmond South (28F2) | None | Padmount (1ph) | 1 | 195 | 3 | West | 28F2
137428 | 2018-01-26 | Human Element | Switching Error | Human element | None | None | 146 | 36 | 88 | South | EPWF3
137430 | 2018-01-28 | Defective Equipment | Defective Equipment/ Material | Crews found defective dry core transformer D1 at VT783 312 Cumberland St. | Vault Equipment | Transformer | 28 | 512 | 239 | Central | 415
137432 | 2018-01-29 | Scheduled Outage | Construction | Transformer #X35390 isolated by crew for a service upgrade | None | None | 7 | 75 | 9 | Central | TD14
137433 | 2018-01-29 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X36685 opened up due to animal contact | O/H Switchgear | Fused Cutout | 5 | 142 | 12 | West | 43F2
137436 | 2018-01-30 | Scheduled Outage | Maintenance | At 09:00am transformer TP5259 was isolated to allow crew to perform transformer upgrade. 2 customers affected. Bells Corners (47F2) | None | None | 2 | 390 | 13 | South | 47F2
137437 | 2018-01-29 | Loss Of Supply | Third Party | Customer defective equipment | None | None | 60 | 66 | 66 | South | 49F3
137437 | 2018-01-29 | Loss Of Supply | Third Party | Customer defective equipment | None | None | 133 | 141 | 313 | South | 49F3
137439 | 2018-01-31 | Foreign Interference | Wildlife (Bird/Animal) | Oms indicates that the transformer X36517 openned in the rear of 40 Canter. Brad Fraser reports that a squirrel body was found at the base of the pole. Crews refused and restored power. | O/H Switchgear | Fused Cutout | 8 | 69 | 9 | South | EPWF3
137440 | 2018-01-31 | Scheduled Outage | Construction | At 08:40am S14299 was opened to allow crew to replace poles. 30 customers affected. Russell (TB06) | None | None | 30 | 324 | 162 | East | TB06
137441 | 2018-01-31 | Foreign Interference | Wildlife (Bird/Animal) | OMS indicates that transformer X47957 openned. Adam Donaldson reports a squirrel found at the base of the pole caused the outage. Crew refused and restored power. | O/H Switchgear | Fused Cutout | 37 | 33 | 20 | Central | TW18
137442 | 2018-01-31 | Scheduled Outage | Construction | K1226 at 155 Lebrun was isolated for padmount transformer conversion. 8 customers were affected. Dagmar (AC07) | None | None | 8 | 116 | 15 | East | AC07
137444 | 2018-01-31 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X21045 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 30 | 5 | Central | UF05
137446 | 2018-01-31 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X31046 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 8 | 30 | 4 | Central | UF05
137447 | 2018-01-31 | Scheduled Outage | Construction | Shaun Evans form K-Line to have transformer X31047 open to transfer load to new equipment. Customers notified. | None | None | 6 | 15 | 2 | Central | UF05
137448 | 2018-01-31 | Scheduled Outage | Construction | Shaun Evans from K-Line to have transformer X31049 open to transfer load to new equipment. Customers notified. | None | None | 22 | 2 | 1 | Central | UF05
137449 | 2018-01-31 | Scheduled Outage | Construction | Shaun Evans of K-Line to have transformers X30659 and X56349 open to transfer load to new equipment. Customers notified. | None | None | 63 | 10 | 10 | Central | UF05
137450 | 2018-01-31 | Scheduled Outage | Construction | Evan Cowell to have transformer X33690 open to remove a service. Customers notified. | None | None | 4 | 22 | 1 | Central | TH01
137451 | 2018-01-31 | Foreign Interference | Vehicle | The SO13 breaker auto reclosed due to a vehicle hitting a pole at 380 Industrial ave. and knocking it down. 10 customers were affected. Overbrook (SO13) | Pole | Pole | 2 | 637 | 21 | East | SO13
137451 | 2018-01-31 | Foreign Interference | Vehicle | The SO13 breaker auto reclosed due to a vehicle hitting a pole at 380 Industrial ave. and knocking it down. 10 customers were affected. Overbrook (SO13) | Pole | Pole | 10 | 84 | 14 | East | SO13
137452 | 2018-01-31 | Scheduled Outage | Construction | Shaun Evans from K-Line to have transformers X57965 and X57970 open to move load to new equipment. Customers notified. | None | None | 82 | 10 | 14 | Central | UF05
137453 | 2018-01-31 | Defective Equipment | Defective Equipment/ Material | Transformer #X31121 opened up due to broken switch | O/H Switchgear | Fused Cutout | 7 | 178 | 21 | Central | AB04
137454 | 2018-01-31 | Scheduled Outage | Construction | Transformer #X14199 isolated by crew to make repairs to pole | None | None | 1 | 85 | 1 | East | 7F4
137455 | 2018-02-01 | Scheduled Outage | Vegetation Management | A section of primary overhead at 6461 Flewelynn was isolated for tree triming affecting 1 customer. Richmond North RHNF3 | None | None | 1 | 323 | 5 | West | RHNF3
137456 | 2018-02-01 | Scheduled Outage | Construction | Not yet known.S11074 to EOL was isolated to allow crew to install spun bus abd energize new O/H transformer. Edwin (UV03) | None | None | 15 | 186 | 46 | Central | UV03
137457 | 2018-02-01 | Defective Equipment | Imminent Failure | A transformer at 4 Lynhurst was isolated to replace broken insulators, live front transformers required an outage to additional customers to perform switching safely, affecting 22 customers. Manordale 84F5 | O/H Switchgear | Unknown \ Other | 7 | 136 | 16 | South | 84F5
137457 | 2018-02-01 | Defective Equipment | Imminent Failure | A transformer at 4 Lynhurst was isolated to replace broken insulators, live front transformers required an outage to additional customers to perform switching safely, affecting 22 customers. Manordale 84F5 | O/H Switchgear | Unknown \ Other | 22 | 5 | 2 | South | 84F5
137458 | 2018-02-01 | Defective Equipment | Electrical Failure | Transformer P1433 at 99 River Lane was isolated to allow crew to replace burnt cable from transformer to switch. 1 customer was affected. Vaughn (UG10) | U/G Cable | Unknown \ Other | 1 | 287 | 5 | East | UG10
137459 | 2018-02-01 | Scheduled Outage | Construction | Scott Barkley and crews to have transformers X25703, X45577, and X25704 open to transfer plant to new poles. Customers notified. | None | None | 28 | 269 | 126 | Central | SM12
137460 | 2018-02-01 | Scheduled Outage | Construction | Adrian Henry to have transformer X29261 open to transfer plant. Customers notified. | None | None | 15 | 272 | 68 | East | UG10
137464 | 2018-02-02 | Tree Contacts | Falling Tree | A tree came down on primary overhead at Ridge Rd at Anderson requiring isolation to safely remove affecting 16 customers. Blackburn BLKF5 | None | None | 16 | 35 | 9 | East | BLKF5
137465 | 2018-02-03 | Scheduled Outage | Construction | Reconfigure overhead lines | None | None | 1 | 579 | 10 | West | A9M3
137466 | 2018-02-03 | Scheduled Outage | Construction | Transfer plant to new line | None | None | 5 | 453 | 38 | East | 4801F7
137467 | 2018-02-03 | Defective Equipment | Electrical Failure | Transformer #X24124 opened up due to blown fuse at line switch | O/H Switchgear | Inline Switch | 2 | 116 | 4 | East | LTM04
137468 | 2018-02-03 | Human Element | Improper Construction/installation | While transfering plant to new pole primary cable made contact with live overhead. | O/H Conductor | O/H Conductor | 502 | 6 | 50 | Central | UC03
137469 | 2018-02-03 | Defective Equipment | Electrical Failure | Replace defective old switch gear | U/G Switchgear | Live-Front | 1 | 490 | 8 | West | 624F4
137470 | 2018-02-03 | Scheduled Outage | Maintenance | Transformer #X36084 isolated by crew to replace transformer leeds and connections | None | None | 6 | 70 | 7 | Central | TD05
137471 | 2018-02-03 | Scheduled Outage | Construction | TP10146 at 1804 Carling isolated to transfer plant to new poles. 3 customers affected. Clyde (UC03) | U/G Cable | PILC | 3 | 513 | 26 | Central | UC03
137472 | 2018-02-03 | Foreign Interference | Foreign Objects | At 8:05pm the SA23 circuit tripped due to balloons in the overhead. 473 customers affected. Slater (SA23) | None | None | 473 | 49 | 386 | Central | SA23
137473 | 2018-02-04 | Scheduled Outage | Construction | Transfer plant to new poles. | None | None | 2 | 139 | 5 | East | 4801F7
137474 | 2018-02-04 | Defective Equipment | Electrical Failure | Transformer #X29818 opened up due to broken switch | O/H Switchgear | Fused Cutout | 6 | 103 | 10 | Central | TR09
137475 | 2018-02-04 | Scheduled Outage | Maintenance | Overhead transformer X33289 was opened to allow crew to change all connections on tranformer. 12 customers were affected. Edwin (UV05) | None | None | 12 | 44 | 9 | Central | UV05
137476 | 2018-02-05 | Scheduled Outage | Construction | Transformer replacement. | None | None | 11 | 136 | 25 | East | 7F1
137477 | 2018-02-05 | Defective Equipment | Corrosion | Transformer KT106 @ 1771 Russell Rd was isolated by the crew to allow them to replace the Kiosk to padmount on the TB15 circuits affecting 17 customers for 226 minutes | U/G Transformer | Kiosk (3ph) | 17 | 226 | 64 | East | TB15
137478 | 2018-02-05 | Scheduled Outage | Construction | Jordan Foote and crew from K-Line to have transformer X31067 open to transfer plant to a different phase. Customers notified. | None | None | 24 | 11 | 4 | Central | UF08
137479 | 2018-02-06 | Scheduled Outage | Construction | PLANNED OUTAGE TO TRANSFER V840 TO THE BLUE PHASE FOR FUTUR CONSTRUCTION | None | None | 1 | 12 | 0 | Central | UF08
137480 | 2018-02-06 | Scheduled Outage | Construction | planned outage to transfer customers from UF08 to UF07 circuit | None | None | 55 | 43 | 39 | Central | UF08
137481 | 2018-02-06 | Scheduled Outage | Construction | PLANNED OUTAGE TO RE-ARRANGE CIRCUITS AND TRANSFER PHASES | None | None | 57 | 31 | 29 | Central | UF08
137482 | 2018-02-06 | Human Element | Improper Equipment/Tool/ Maintenance | 180F1 breaker tripped while crews (mark brown) were working on overhead line, crews reported a piece of coverup moved while transfering plant and conductor made contact with down guy. 120 customers affected. Rideau Heights DS | None | None | 120 | 6 | 12 | South | 180F1
137483 | 2018-02-06 | Scheduled Outage | Construction | Dave Burns and crew to have transformer X33974 open to replace. Customers notified. | None | None | 24 | 65 | 26 | Central | UV03
137484 | 2018-02-06 | Scheduled Outage | Construction | transformeer 2531R isolated, secondaries transferred and made NIU. Affected 13 customers, Briddlewood (BRDF5) | None | None | 13 | 540 | 117 | West | BRDF5
137485 | 2018-02-06 | Defective Equipment | Corrosion | K386 replaced with newTP12252 | U/G Transformer | Kiosk (3ph) | 9 | 258 | 39 | East | UA11
137486 | 2018-02-07 | Scheduled Outage | Construction | TRANSFER PLANT TO NEW POLE | None | O/H Transformer (1ph) | 19 | 70 | 22 | Central | UF08
137487 | 2018-02-07 | Defective Equipment | Imminent Failure | TE148 at 45 Canfield isolated to repair defective insulators. 10 customers affected. Manordale 84F5. | O/H Switchgear | Unknown \ Other | 10 | 182 | 30 | South | 84F5
137488 | 2018-02-07 | Scheduled Outage | Maintenance | VE15 was isolated for metering repairs, affecting 1 customer. Parkwood Hills (190F5) | None | Meter | 1 | 37 | 1 | South | 190F5
137489 | 2018-02-07 | Defective Equipment | Defective Equipment/ Material | TP8938 found to be defective, transformeer isolated and replaced. Kanata (624F1) | U/G Transformer | Padmount (1ph) | 8 | 242 | 32 | West | 624F1
137490 | 2018-02-07 | Scheduled Outage | Construction | Dave Burns and crew to have transformer X33976 open to replace transformer. Customers notified. | None | None | 14 | 120 | 28 | Central | UV03
137491 | 2018-02-07 | Scheduled Outage | Construction | Section TEMP109 to S19554 to TEMP 131 isolated to allow crew to install poles. | None | None | 73 | 335 | 408 | East | TB06
137492 | 2018-02-07 | Defective Equipment | Electrical Failure | Transfomer 6317 at 61 Woodwind isolated to replace broken insert. 11 customers affected. Janet King JKGF4. | U/G Cable Attachement | Elbow \ Insert | 11 | 31 | 6 | West | JKGF4
137493 | 2018-02-08 | Scheduled Outage | Construction | crew isolated padmount transformer P451 at 403 Richmond rd. to rearrange conduactor and prove spare duct. One customer was affected. Hillcrest (AH02) | None | None | 1 | 107 | 2 | Central | AH02
137494 | 2018-02-08 | Scheduled Outage | Construction | At 8:00am transformer 2530R was isolate to allow crew to make it NIU. 13 customers affected. Bridlewood (BRDF5) | None | None | 13 | 480 | 104 | West | BRDF5
137495 | 2018-02-08 | Foreign Interference | Foreign Objects | City plow struck guying and caused transformer X29868 to open. Central crews made repairs, refused and closed. | O/H Switchgear | Fused Cutout | 4 | 159 | 11 | Central | TR09
137496 | 2018-02-08 | Scheduled Outage | Construction | Scott Grace and crew to have transformer X25603 open to replace jumper to switch with a lead. Customers notified. | None | None | 7 | 18 | 2 | South | EPWF3
137497 | 2018-02-08 | Defective Equipment | Mechanical Failure | Cable fault | U/G Cable | PILC Splice | 59 | 172 | 169 | East | BLKF4
137498 | 2018-02-09 | Tree Contacts | Broken Branch | REMOVE LIMB FROM SEC SERVICE | None | None | 8 | 10 | 1 | Central | AH13
137500 | 2018-02-10 | Defective Equipment | Defective Equipment/ Material | Customer reported outage, crews report transformer fire at X17221. OH circuit dumped from RX2040 to allow OFS and crews to extinguish fire. Billberry (77M5) | O/H Transformer | O/H Transformer (1ph) | 3 | 61 | 3 | East | 77M5
137500 | 2018-02-10 | Defective Equipment | Defective Equipment/ Material | Customer reported outage, crews report transformer fire at X17221. OH circuit dumped from RX2040 to allow OFS and crews to extinguish fire. Billberry (77M5) | O/H Transformer | O/H Transformer (1ph) | 3 | 200 | 10 | East | 77M5
137500 | 2018-02-10 | Defective Equipment | Defective Equipment/ Material | Customer reported outage, crews report transformer fire at X17221. OH circuit dumped from RX2040 to allow OFS and crews to extinguish fire. Billberry (77M5) | O/H Transformer | O/H Transformer (1ph) | 55 | 30 | 28 | East | 77M5
137503 | 2018-02-12 | Foreign Interference | Vehicle | Dump truck made contact with the Bell and knocked two phases down at 455 Coventry causing an outage on the SO11 circuit. Overbrook (SO11). 1 customer was affected. | Pole Attachement | Unknown \ Other | 25 | 148 | 62 | East | SO11
137505 | 2018-02-12 | Unknown/Other | Unknown | The Albion UA11 circuit tripped and did not auto reclosed due to hold off for Forestry. Forestry crew were cleared from the hold and circuit was restored. Circuit was patrolled and nothing was found. Albion (UA11) | None | None | 387 | 7 | 45 | East | UA11
137507 | 2018-02-12 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X27031 TO RE-SAG SECONDARY OPEN BUSS | None | None | 14 | 10 | 2 | East | TB06
137509 | 2018-02-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35391 opened up due to animal contact | O/H Switchgear | Fused Cutout | 7 | 82 | 10 | Central | TD14
137510 | 2018-02-13 | Scheduled Outage | Maintenance | Jeremy Tufts and crew to have transformer X23565 open to replace a streetlight fuse. | None | None | 8 | 23 | 3 | East | SO02
137513 | 2018-02-13 | Human Element | Incorrect Records/ labelling | S27153 White phase fuse found opened. | O/H Switchgear | Fused Cutout | 425 | 60 | 425 | West | RHNF1
137514 | 2018-02-14 | Defective Equipment | Defective Equipment/ Material | V504 was isolated to investigate and replace blown fuse. 63 customers were affected. Eastview (UT03) | Vault Equipment | Unknown \ Other | 63 | 24 | 25 | East | UT03
137515 | 2018-02-14 | Scheduled Outage | Construction | HOL crews performing pole replacement on the TB06 out of Russell affecting 109 customers for the duration of work | None | None | 109 | 370 | 672 | East | TB06
137516 | 2018-02-14 | Scheduled Outage | Construction | Transformer #X29000 isolated by crew to replace cut out, Chris from Sproule | None | None | 9 | 82 | 12 | East | UQ04
137518 | 2018-02-14 | Tree Contacts | Tree Growth/ Untrimmed Tree | overgrown trees on Ramseyville caused G59R to blow | None | None | 16 | 83 | 22 | East | BLKF4
137519 | 2018-02-14 | Unknown/Other | Unknown | R00242813 Customer reports outage at 1161 Murphy Side Rd. Crew on scene reports blown fuse at switch 1190. Crew replaced fuse and closed. No cause reported. | O/H Switchgear | Fused Cutout | 1 | 90 | 2 | West | MWDF3
137520 | 2018-02-15 | Adverse Weather | Freezing Rain | G256B found blown, crew patrolled line found nothing. Freezing rain at the time. | None | None | 43 | 122 | 87 | East | 8F1
137521 | 2018-02-15 | Scheduled Outage | Construction | Pole replacement, also 2 new switches installed. | None | None | 35 | 93 | 54 | Central | UV02
137521 | 2018-02-15 | Scheduled Outage | Construction | Pole replacement, also 2 new switches installed. | None | None | 52 | 259 | 224 | Central | UV02
137522 | 2018-02-15 | Defective Equipment | Defective Equipment/ Material | Transformer #X35457 opened up due to a broken switch | O/H Switchgear | Fused Cutout | 14 | 133 | 31 | Central | TD01
137523 | 2018-02-15 | Unknown/Other | Unknown | S28149 found blown, line patrol found no obvious cause of outage, affecting 15 customers. Queens (UQ03) | None | None | 15 | 56 | 14 | East | UQ03
137524 | 2018-02-15 | Scheduled Outage | Vegetation Management | Transformer #X27371 isolated by crew to reconnect 2 services that were dropped for Forestry | None | None | 7 | 100 | 12 | East | UQ03
137525 | 2018-02-16 | Scheduled Outage | Construction | SERVICE UPGRADE | None | None | 11 | 130 | 24 | Central | SB16
137526 | 2018-02-17 | Scheduled Outage | Construction | Scott Barkley and crew to have transformers X45577, X25704, and X25703 open to transfer plant to new transformers. Two new transformers to replace the three old ones. Customers notified. | None | None | 28 | 447 | 209 | Central | SM12
137527 | 2018-02-17 | Scheduled Outage | Maintenance | Vault VT263 isolation for stations crew to make repairs to broken primary bushings | None | None | 1 | 187 | 3 | Central | 628
137528 | 2018-02-18 | Foreign Interference | Wildlife (Bird/Animal) | Bill Armstrong and crew found dead squirrel on site. Crew refused and restored transformer X35318. | O/H Switchgear | Fused Cutout | 1 | 93 | 2 | Central | TD01
137530 | 2018-02-19 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact on transformer in vault VT1565 caused the main vault supply to trip. One customer was affected. Ellwood(ELW14) | Vault Equipment | Transformer | 1 | 151 | 3 | East | ELW14
137531 | 2018-02-19 | Foreign Interference | Wildlife (Bird/Animal) | Mike Vandelst and crew on site found dead squirrel on site. Refused and restored power to transformer X49862. | O/H Switchgear | Fused Cutout | 1 | 40 | 1 | West | TFXF4
137532 | 2018-02-20 | Scheduled Outage | Construction | Transformer #X11321 isolated by Bobby from Sproule to install a new service | None | None | 2 | 40 | 1 | West | 43F3
137533 | 2018-02-20 | Scheduled Outage | Construction | Transformer #X31047 isolated by Jordan Foote from Kline to transfer plant | None | None | 6 | 56 | 6 | Central | UF05
137535 | 2018-02-20 | Adverse Environment | Flood | W phase fuse S2-2W at 52 Tiffany opened due to flooded transformer 2644W. 154 customers affected. Beaverbrook (24F1) | U/G Transformer | Kiosk (1ph) | 154 | 130 | 334 | West | 24F1
137536 | 2018-02-20 | Adverse Environment | Flood | Transformer 2644 at 5 Tiffany was isolated for crew to pump flooding water and test cable sections for damage | None | None | 13 | 201 | 44 | West | 24F1
137537 | 2018-02-21 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X48468 opened up due to animal contact | O/H Switchgear | Fused Cutout | 14 | 49 | 11 | Central | TW18
137540 | 2018-02-21 | Tree Contacts | Tree Growth/ Untrimmed Tree | REPLACED BLOWN FUSE FOR SWITCH FEEDING TRANSFORMER X36235 (VINES AROUND SWITCH) | O/H Transformer | O/H Transformer (1ph) | 14 | 85 | 20 | South | 190F5
137541 | 2018-02-21 | Scheduled Outage | Forced Switching | At 8:50pm G263 was opened to allow on-call crew to make repairs to a burn pole. 8 customers affected. Limebank (7F4) | None | Insulation Failure (Pole Fire) | 8 | 136 | 18 | East | 7F4
137542 | 2018-02-22 | Scheduled Outage | Construction | S17078 isolation to EOL for Pole Change by HOL crew affecting 21 customers | None | None | 21 | 385 | 135 | East | TB06
137543 | 2018-02-22 | Scheduled Outage | Construction | Marc Branchaud and crew to have transformer X23251 open to upgrade a customer service at 7 Rock Ave. Customers notified. | None | None | 4 | 60 | 4 | East | UG09
137544 | 2018-02-22 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32533 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 10 | 59 | 10 | Central | TD06
137546 | 2018-02-24 | Defective Equipment | Defective Equipment/ Material | Transformer X30600 isolated to allow crew to change defective cut-out. 38 customers affected. King Edward (SK16) | Unknown \ Other | Unknown \ Other | 38 | 20 | 13 | Central | SK09
137549 | 2018-02-25 | Defective Equipment | Electrical Failure | TO38 breaker tripped due to defective cable, affecting 1 customer. Overbrook TS (TO38) | U/G Cable | PILC | 1 | 45 | 1 | Central | TB1TOTO
137550 | 2018-02-25 | Scheduled Outage | Construction | AD06 from S23377 to EOL isolated to change line side lead at S23377. 48 customers affected. Shillington (AD06) | None | Fused Cutout | 48 | 9 | 7 | Central | AD06
137553 | 2018-02-26 | Scheduled Outage | Construction | Isolated transformer x26816 to replace pole | None | None | 4 | 240 | 16 | East | AE06
137554 | 2018-02-26 | Scheduled Outage | Maintenance | Crew replaced cables and switches | None | None | 1 | 363 | 6 | Central | AH02
137555 | 2018-02-26 | Scheduled Outage | Construction | Brief outage to 30 customers during planned switching due to out of phase condition. Richmond North RHNF1. | None | None | 30 | 5 | 2 | West | RHNF1
137557 | 2018-02-27 | Scheduled Outage | Construction | Patrick Brisson and crew to have transformer X25692 open to transfer plant. Customers notified. | None | None | 17 | 236 | 67 | Central | TH15
137558 | 2018-02-27 | Scheduled Outage | Construction | Glen Carswell and crew to have transformer X35198 open to install new secondary services. Customers notified. | None | None | 10 | 190 | 32 | Central | AH02
137559 | 2018-02-27 | Unknown/Other | Unknown | Per Shaun Cunningham transformer X36451 openned with no apparent cause. Crew refused and restored. R00243106 | O/H Switchgear | Fused Cutout | 6 | 99 | 10 | West | JKGF4
137561 | 2018-02-28 | Scheduled Outage | Vegetation Management | S28899 to Eol was isolated to allow crew to perfrom tree trimming. 17 customers were affected. Albion (UA07). | None | None | 17 | 263 | 75 | East | UA07
137562 | 2018-02-28 | Scheduled Outage | Construction | Dan Crough and crew from K-Line to have transformer X31051 open to transfer plant to the new transformer X31067. Customers notified. R00243113 | None | None | 10 | 60 | 10 | Central | UF08
137563 | 2018-02-28 | Defective Equipment | Mechanical Failure | Defective equipment | Unknown \ Other | Unknown \ Other | 34 | 29 | 16 | West | MWDF3
137564 | 2018-02-28 | Scheduled Outage | Construction | Transformer #X28140 isolated by crew due to replacing a pole | None | None | 9 | 254 | 38 | East | UZ04
137565 | 2018-02-28 | Scheduled Outage | Construction | Transformer #X39275 isolated by crew to replace a pole | None | None | 7 | 254 | 30 | East | UZ04
137566 | 2018-03-01 | Scheduled Outage | Construction | TB06 from S23555 to EOL on Weston Dr. isolated to allow crews to change a pole. 53 customers affected. Russel (TB06) | None | Pole | 53 | 540 | 477 | East | TB06
137567 | 2018-03-01 | Defective Equipment | Defective Equipment/ Material | PT256 at 2475 Regina was isolated for transformer and switch replacement. 1 customer affected. Lincoln Heigths (TD14) | Vault Equipment | Transformer | 1 | 235 | 4 | Central | TD14
137568 | 2018-03-01 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X28050 TO INSTALL A NEW POLE | None | None | 8 | 130 | 17 | East | AF03
137570 | 2018-03-01 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X33813 to transfer plant. Customers notified. | None | None | 16 | 270 | 72 | Central | UL14
137571 | 2018-03-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact caused W & B phases of S360 to open & brought down primary line. S360R opened for isolation to complete repairs. On call crew required. 29 customers afected. Parkwood Hills 190F5. | O/H Conductor | O/H Conductor | 28 | 49 | 23 | South | 190F5
137571 | 2018-03-02 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact caused W & B phases of S360 to open & brought down primary line. S360R opened for isolation to complete repairs. On call crew required. 29 customers afected. Parkwood Hills 190F5. | O/H Conductor | O/H Conductor | 29 | 270 | 130 | South | 190F5
137572 | 2018-03-02 | Scheduled Outage | Construction | Replace PP2179 | None | None | 181 | 8 | 24 | West | TFXF4
137573 | 2018-03-02 | Defective Equipment | Mechanical Failure | TP5482 isolated to allow crew to replace bushings and elbow. | U/G Cable Attachement | Elbow \ Insert | 10 | 85 | 14 | East | LMBF7
137574 | 2018-03-02 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35179 TO RE-ARRANGE HYDRO PLANT | None | None | 6 | 110 | 11 | Central | UL14
137575 | 2018-03-03 | Scheduled Outage | Maintenance | A vault at 131 Queen was isolated to adjust the settings on the CB3 and CB4 affecting 1 customer. Slater TL2TS | None | None | 1 | 228 | 4 | Central | TL2TSTS
137576 | 2018-03-03 | Defective Equipment | Mechanical Failure | Transformer #X14858 isolated by crew to replace transformer bushings | U/G Cable Attachement | Elbow \ Insert | 12 | 133 | 27 | East | AN06
137577 | 2018-03-03 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X39544 open due to animal contact. Crew refuse transformer and all power was restored. 7 customers were affected. Bells Corner (47F3) | O/H Transformer | O/H Transformer (1ph) | 7 | 47 | 5 | South | 47F3
137579 | 2018-03-04 | Defective Equipment | Defective Equipment/ Material | planned outage to allow crew to install new switche and transformer | U/G Transformer | Padmount (1ph) | 5 | 320 | 27 | South | EPWF4
137580 | 2018-03-04 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #X34557 opened up due to tree contact | O/H Switchgear | Fused Cutout | 1 | 136 | 2 | South | FAL01
137581 | 2018-03-05 | Scheduled Outage | Construction | Mike Irven and crew to have transformer X33889 open to upgrade a service. Customers notified. | None | None | 5 | 47 | 4 | Central | UL14
137582 | 2018-03-05 | Unknown/Other | Unknown | blown fuse at DND on Franktown, unknown cause | None | None | 1 | 190 | 3 | West | BECKF2
137583 | 2018-03-05 | Scheduled Outage | Construction | Transformer #X38372 isolated by crew to remove transformer | None | None | 8 | 20 | 3 | East | UB03
137584 | 2018-03-05 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X34738 open to transfer plant. Customers notified. | None | None | 10 | 174 | 29 | Central | TH06
137585 | 2018-03-06 | Scheduled Outage | Maintenance | transformer loop was isolated to allow crew to rearrange primary cables at transformer at 4312 Sunwood cres. 87 customers were affected. (cyrville(CYRF4) | None | None | 87 | 100 | 145 | East | CYRF4
137586 | 2018-03-06 | Defective Equipment | Defective Equipment/ Material | transformer was isolated at 15 North Harrow to replace same. 12 customers were affected. Fallowfield (FAL02) | U/G Transformer | Padmount (1ph) | 12 | 161 | 32 | South | FAL02
137587 | 2018-03-06 | Scheduled Outage | Construction | The overhead in the rear of 853 Chapman was issolated to allow the crews to replace poles. 10 customers were affected on the TB06 circuit for 409 minutes | None | Pole | 10 | 409 | 68 | East | TB06
137588 | 2018-03-06 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27102 | O/H Transformer | O/H Transformer (1ph) | 8 | 83 | 11 | East | TB14
137589 | 2018-03-06 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X29154 TO REPLACE THE SECONDARY CONNECTIONS FEEDING THE OPEN BUSS | None | None | 10 | 41 | 7 | East | UT02
137590 | 2018-03-07 | Defective Equipment | Defective Equipment/ Material | transformer at 2611 Baynes way was isolated to reeplace same. 30 customers affected. Fallowfield (FAL03. | None | None | 30 | 99 | 50 | South | FAL03
137592 | 2018-03-07 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X35603 open to upgrade customer service. Customers supposed to be notified but two customers claim they were not. | None | None | 9 | 48 | 7 | Central | UC03
137593 | 2018-03-07 | Scheduled Outage | Construction | Bob Wills to have transformer X29571 open to replace the transformer. Customers notified. | None | None | 1 | 229 | 4 | East | UG02
137594 | 2018-03-07 | Scheduled Outage | Construction | Jordan Foote and crew from K-Line to have transformers X31046 and X31045 open to transfer equipment to new transformer. Customers notified. | None | None | 18 | 240 | 72 | Central | UF05
137596 | 2018-03-07 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X30696 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 4 | 150 | 10 | Central | UF05
137597 | 2018-03-07 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X33377 TO REPLACED SECONDARY CONNECTIONS FEEDING THE OPEN BUSS | None | None | 11 | 66 | 12 | Central | TD05
137598 | 2018-03-08 | Scheduled Outage | Maintenance | To allow Hydro Ottawa line crews to change a bayonet gasket inside TP5164 | None | Unknown \ Other | 136 | 119 | 270 | South | FAL02
137599 | 2018-03-08 | Defective Equipment | Mechanical Failure | crews isolated a 3 phase transformer to replace a broken switch. | O/H Switchgear | Fused Cutout | 1 | 45 | 1 | Central | TD06
137600 | 2018-03-09 | Scheduled Outage | Construction | Mike Irven and crew to have transformer X32681 open to install a new service. Customers notified. | None | None | 19 | 65 | 21 | Central | UC06
137601 | 2018-03-09 | Scheduled Outage | Construction | Glen Carswell and crew to have transformer X57499 open to perform secondary service work. | None | None | 27 | 197 | 89 | Central | AB07
137602 | 2018-03-09 | Scheduled Outage | Construction | A section of overhead line on Weston St from S12029 to end of line was isolated to allow crew to perfrom pole replacement. Russell (TB06) | None | None | 43 | 316 | 226 | East | TB06
137603 | 2018-03-09 | Tree Contacts | Off Right of Way Tree | Gary Coburn and crew to have transformer X35502 open to repair secondary service to 431 Ravennhill. | Secondary \ Service | O/H Service | 9 | 59 | 9 | Central | AH14
137605 | 2018-03-11 | Foreign Interference | Wildlife (Bird/Animal) | R1-F at 2431 Bank St. opened due animal contact in VT1565. 1 customer affected. Ellwood (ELW14) | None | None | 1 | 57 | 1 | East | ELW14
137607 | 2018-03-11 | Foreign Interference | Wildlife (Bird/Animal) | An animal made contact with the overhead transformer X32634 at the rear of 2692 Marie St causing the fuse to blow and also caused the fuse upstream S19308 to also blow interupting 17 customers on the TD14 circuit for 84 minutes. | O/H Transformer | O/H Transformer (1ph) | 17 | 84 | 24 | Central | TD14
137610 | 2018-03-12 | Scheduled Outage | Maintenance | S12129 to eol isolated to allow crew to perform air brake maintenance. | None | None | 1 | 176 | 3 | East | 7F4
137611 | 2018-03-12 | Scheduled Outage | Construction | V42 at 88 Albert was isolated to complete civil work to prepare for de-commisioning. 2 customers affected. Slater (SA24) | None | Unknown \ Other | 2 | 224 | 7 | Central | SA24
137613 | 2018-03-12 | Defective Equipment | Corrosion | Replace defective lid. | U/G Transformer | Kiosk (1ph) | 23 | 31 | 12 | Central | AK04
137615 | 2018-03-12 | Scheduled Outage | Construction | Jordan Foote from K-Line to have transformers X31048 and X31047 open to transfer plant. Customers notified. | None | None | 4 | 445 | 30 | Central | UF05
137616 | 2018-03-13 | Scheduled Outage | Construction | Transformer #X55095 isolated by crew to transfer plant, Dan from Kline | None | None | 44 | 168 | 123 | Central | UF08
137618 | 2018-03-13 | Scheduled Outage | Construction | Transformer #X31067 isolated by crew to transfer plant | None | None | 24 | 3 | 1 | Central | UF08
137619 | 2018-03-13 | Defective Equipment | Mechanical Failure | Old end of life TE175 replaced with new TP11907 | U/G Transformer | Padmount (1ph) | 11 | 243 | 45 | South | 49F2
137620 | 2018-03-13 | Scheduled Outage | Construction | Jordan Foote (K-Line) and crew to have transformer X31068 open to transfer plant. R00243423 | None | None | 41 | 255 | 174 | Central | UF08
137621 | 2018-03-14 | Scheduled Outage | Construction | Transformer #X31066 isolated by crew to transfer plant | None | None | 19 | 57 | 18 | Central | UF08
137622 | 2018-03-14 | Scheduled Outage | Construction | A section of primary line from S27580 on Chapman Dr was isolated for pole replacement. 10 customers affected. Russell TB06. | None | None | 10 | 167 | 28 | East | TB06
137624 | 2018-03-14 | Defective Equipment | Corrosion | TP2771 was replaced due to leaking oil, affecting 21 customers. Limebank DS (LMBF7). | U/G Transformer | Padmount (1ph) | 21 | 98 | 34 | East | LMBF7
137625 | 2018-03-14 | Scheduled Outage | Construction | transformer #X24747 isolated by crew for a service disconnect | None | None | 12 | 5 | 1 | East | AC05
137627 | 2018-03-14 | Scheduled Outage | Construction | S19112 W open to EOL to allow contractor move run off to new conductor. Boyd Knox | None | None | 58 | 109 | 105 | West | RHNF1
137628 | 2018-03-14 | Scheduled Outage | Construction | A section of overhead line from S23555 at Weston Dr at Arch was isolated for pole replacement work. 53 customers affected. Russell TB06. | None | None | 53 | 132 | 117 | East | TB06
137629 | 2018-03-14 | Scheduled Outage | Construction | two transformers, X31050 & X31051 isolated by crew to transfer plant | None | None | 28 | 235 | 110 | Central | UF08
137630 | 2018-03-14 | Scheduled Outage | Construction | Transformer #X55521 isolated by crew to transfer plant | None | None | 15 | 23 | 6 | Central | UV02
137631 | 2018-03-14 | Scheduled Outage | Construction | Jordan Foote from K-Line and crew to have transformers X55213 and X55209 open to transfer plant. | None | None | 74 | 47 | 58 | Central | UF07
137632 | 2018-03-14 | Scheduled Outage | Construction | 3 transformers, X56373, X56371 and X55279 isolated by crew to transfer plant | None | None | 56 | 45 | 42 | Central | UF06
137633 | 2018-03-15 | Scheduled Outage | Construction | Stu Patterson and crew to have transformer X23067 open to transfer plant. Customers notified. | None | None | 12 | 47 | 9 | East | UB06
137634 | 2018-03-15 | Scheduled Outage | Construction | Mike Beyers and crew to have transformers X32716 and X34677 open to tranfer plant. Customers notified. | None | None | 26 | 340 | 147 | Central | UV02
137635 | 2018-03-15 | Defective Equipment | Mechanical Failure | customer owned substation QT125 was isolated to allow crew to repair broken switch on 44kV overhead. One customer was affected. Nepean (22M28) | O/H Switchgear | Inline Switch | 1 | 149 | 2 | South | 22M28
137636 | 2018-03-15 | Defective Equipment | Mechanical Failure | overhead section of 8kv was isolated affecting transformer TE1472 to allow crew to repair broken switch on overhead 44kv circuit. Stafford (200F3) | O/H Switchgear | Inline Switch | 1 | 155 | 3 | South | 200F3
137637 | 2018-03-15 | Defective Equipment | Corrosion | At 09:34am TP3247 at 318 Quetico Pvt was isolated to allow the crew to replace leaking transformer. 21 customers affected. Fallowfield (FAL03) | U/G Transformer | Padmount (1ph) | 21 | 93 | 33 | South | FAL03
137640 | 2018-03-16 | Scheduled Outage | Construction | padmount transformer at 314 Maberly was isolated to allow crew to replace transformer. Four customers were affected. Leitrim (LTM01) | None | None | 4 | 78 | 5 | East | LTM01
137641 | 2018-03-16 | Scheduled Outage | Construction | Chris Costello and crew to have transformer X45116 to upgrade the transformer. Customers notified. | None | None | 25 | 77 | 32 | Central | TW17
137642 | 2018-03-16 | Scheduled Outage | Construction | Transformer #X27087 isolated by crew to replace fuse holder for streetlighting | None | None | 10 | 55 | 9 | East | TB14
137643 | 2018-03-16 | Defective Equipment | Electrical Failure | Defective transformer X31226 at 14 Range rd isolated & replaced. 1 customer affected. Henderson UN06. | O/H Transformer | O/H Transformer (1ph) | 1 | 365 | 6 | Central | UN06
137644 | 2018-03-17 | Tree Contacts | Broken Branch | Branches on the O/H primary line caused G60 R phase to blow on the BLKF5. A 24/7 Line crew patrolled the circuit, cleared branches that had fallen onto the O/H and re-fused G60. 6 customers affected. | None | None | 6 | 111 | 11 | East | BLKF5
137645 | 2018-03-19 | Scheduled Outage | Construction | A section of primary overhead from 2267 Elmira to the end of line was isolated to transfer plant and install a new fused switch affecting 65 customers. Edwin UV03 | None | None | 65 | 207 | 224 | Central | UV03
137646 | 2018-03-19 | Defective Equipment | Corrosion | Transformer TE3660 was isolated to allow crew to replace leaking transformer. 9 customers were affected. Limebank (LBF7) | U/G Transformer | Padmount (1ph) | 9 | 123 | 18 | East | LMBF7
137647 | 2018-03-19 | Defective Equipment | Mechanical Failure | To allow Hydro Ottawa line crews to make repairs to the quad cable feeding 1156 Ogilvie Rd. | Secondary \ Service | U/G Service | 1 | 37 | 1 | East | 6F10
137648 | 2018-03-19 | Scheduled Outage | Construction | Mike Irven and crew to have transformer X 34207 open to instal a new service. Customrs notified. | None | None | 24 | 82 | 33 | Central | AH02
137649 | 2018-03-19 | Scheduled Outage | Construction | Dan Crough and crew (K-Line) to have transformer X31067 open to transfer plant. Customers notified. | None | None | 24 | 264 | 106 | Central | UF08
137650 | 2018-03-19 | Foreign Interference | Wildlife (Bird/Animal) | Gary Corburn and crew report that dead squirrel found at the base of pole caused X36817 to open. Crew refused and closed. | O/H Switchgear | Fused Cutout | 1 | 162 | 3 | West | 624F6
137652 | 2018-03-21 | Defective Equipment | Corrosion | transformer at 18 James long crt. Was isolated to allow crew to replace leaking transformer. 12 customers were affected. Longfields (LGFF) | U/G Transformer | Padmount (1ph) | 12 | 125 | 25 | South | LGFF2
137653 | 2018-03-21 | Scheduled Outage | Construction | isolated transformer x37217 to transfer hydro plant | None | None | 12 | 184 | 37 | Central | UV02
137654 | 2018-03-21 | Scheduled Outage | Construction | planned outage to V840 to allow crew to transfer feed to another phase. | None | None | 1 | 11 | 0 | Central | UF05
137655 | 2018-03-21 | Scheduled Outage | Construction | ISOLATED PRIMARY LINE AT TEMP SWITCH AT TEMP 115 TO REPLACE SECONDARY BUSS | None | None | 30 | 269 | 134 | East | TB06
137656 | 2018-03-21 | Scheduled Outage | Construction | Transformer #X11738 isolated by crew due to a conversion, Boyd Knox from Thirau | None | None | 1 | 39 | 1 | West | TFXF4
137657 | 2018-03-21 | Human Element | Improper Construction/installation | Construction by Hydro caused the service to pull away from the house at 540 Lyon affecting 1 customer. Lyon UF08 | Secondary \ Service | O/H Service | 1 | 317 | 5 | Central | UF08
137658 | 2018-03-21 | Scheduled Outage | Maintenance | Transformer #K00253 isolated by crew to make repairs to neutral | None | None | 18 | 110 | 33 | Central | AK12
137659 | 2018-03-22 | Scheduled Outage | Construction | TWO TRANSFORMERS X32715 & X32714 ISOLATED BY CREW TO TRANFER PLANT | None | None | 16 | 160 | 43 | Central | UV02
137660 | 2018-03-22 | Scheduled Outage | Construction | Bobby McNabb from Sproule Powerlines to have transformer X39476 open to install a new service. Customers notified. | None | None | 3 | 85 | 4 | Central | TR09
137662 | 2018-03-23 | Scheduled Outage | Construction | Transformer #X40267 isolated by crew to transfer plant to new pole | None | None | 9 | 225 | 34 | East | TB06
137664 | 2018-03-23 | Defective Equipment | Defective Equipment/ Material | Defective xlpe cable | U/G Cable | XLPE | 50 | 135 | 112 | East | BLKF1
137665 | 2018-03-24 | Scheduled Outage | Construction | TRANSFER PLANT TO NEW POLES | None | None | 15 | 270 | 68 | Central | TD05
137666 | 2018-03-24 | Scheduled Outage | Construction | Section of 27KV overhead was isolated on Lester rd. to allow crew to install equipment on hydro pole for future padmount transformer. Four customers were affected. Uplands (4801F7) | None | None | 4 | 443 | 30 | East | 4801F7
137667 | 2018-03-25 | Scheduled Outage | Construction | section of overhead on Perth st, and McBean was isolated to allow crews to reconfigure overhead and transfer customers to new overhead. 5 customers affected. Richmond south (28F2) | None | None | 5 | 513 | 43 | West | 28F2
137668 | 2018-03-26 | Unknown/Other | Unknown | Refused switch feeding transformer X42832 (no apparent cause) | O/H Transformer | O/H Transformer (1ph) | 2 | 154 | 5 | South | FAL03
137669 | 2018-03-26 | Scheduled Outage | Construction | At 08:09am UV03 from S29842 to end of line was isolated to allow crew to install new poles with crane. 35 customers affected. Edwin (UV03) | None | None | 35 | 234 | 136 | Central | UV03
137670 | 2018-03-26 | Scheduled Outage | Construction | Transformer #X11741 isolated by crew to transfer plant by Boyd Knox from Thirau | None | None | 4 | 70 | 5 | West | TFXF4
137671 | 2018-03-26 | Defective Equipment | Defective Equipment/ Material | Transformer #X28138 opened up due to defective switch | O/H Switchgear | Fused Cutout | 5 | 323 | 27 | East | UZ04
137672 | 2018-03-26 | Defective Equipment | Electrical Failure | AF03 breaker tripped due to suspected defective egress cable, affecting 382 customers. Brookfield DS | U/G Cable | PILC | 382 | 90 | 573 | East | AF03
137673 | 2018-03-27 | Scheduled Outage | Construction | Pole replacement. | None | None | 17 | 369 | 105 | East | TB06
137674 | 2018-03-27 | Scheduled Outage | Maintenance | To transfer plant | None | None | 6 | 60 | 6 | East | 77M2
137675 | 2018-03-27 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X26098 AND X23597 TO TRANSFER LOAD TO NEW TRANSFORMER | None | None | 26 | 227 | 98 | East | AC05
137676 | 2018-03-27 | Scheduled Outage | Construction | Transformer #X24791 isolated by crew to replace switch | None | None | 7 | 29 | 3 | East | 8F1
137677 | 2018-03-27 | Scheduled Outage | Construction | Transformer #X33934 isolated by crew to replace transformer | None | None | 4 | 440 | 29 | Central | UL14
137678 | 2018-03-27 | Scheduled Outage | Construction | Transformer #X32661 isolated by crew to transfer plant | None | None | 8 | 65 | 9 | Central | UV05
137680 | 2018-03-28 | Scheduled Outage | Construction | Reconfigure overhead | None | None | 53 | 110 | 97 | Central | TH06
137682 | 2018-03-28 | Defective Equipment | Defective Equipment/ Material | TRANSFORMER X 31999 OPENED UP DUE TO DEFECTIVE SWITCH. | O/H Switchgear | Fused Cutout | 3 | 93 | 5 | Central | SH04
137683 | 2018-03-28 | Defective Equipment | Defective Equipment/ Material | Transformer replacement TE2639 | U/G Transformer | Padmount (1ph) | 10 | 104 | 17 | South | 87F4
137684 | 2018-03-28 | Scheduled Outage | Construction | TO TRANSFER PLANT | None | None | 5 | 222 | 18 | Central | UV03
137685 | 2018-03-28 | Defective Equipment | Mechanical Failure | Transformer TE1199 was isolated by crew to change defective bushing and elbow. Crew advised they will have to cancel shut down, because they will have to change the transformer. | U/G Transformer | Padmount (1ph) | 14 | 37 | 9 | South | 87F3
137686 | 2018-03-28 | Defective Equipment | Imminent Failure | Patrick Brisson and crew to have transformer X37957 open to replace defective transformer. Customers notified. | O/H Transformer | O/H Transformer (1ph) | 16 | 165 | 44 | Central | SR01
137687 | 2018-03-28 | Scheduled Outage | Maintenance | Bill Edwards and crew to have primary swich open to repair O/H secondary neutral in the rear of 679 Denbury. | None | O/H Conductor | 14 | 76 | 18 | Central | TD01
137688 | 2018-03-29 | Scheduled Outage | Construction | planned outage to replace poles in the backyard on Weston | None | None | 14 | 315 | 74 | East | TB06
137689 | 2018-03-29 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X31670 | None | None | 10 | 131 | 22 | Central | SR08
137690 | 2018-03-29 | Scheduled Outage | Construction | At 09:06am crews isolated K351 to replace Kiosk and cables affecting 9 customers. Urbandale (AE07) | None | None | 9 | 249 | 37 | East | AE07
137691 | 2018-03-29 | Tree Contacts | Other Vegetation | Crew reports excessive vegetation caused transformer to open. Crew refused and restored. | O/H Switchgear | Fused Cutout | 3 | 60 | 3 | Central | SH04
137694 | 2018-03-30 | Human Element | Switching Error | switching incident, incorrect switch was operated. | None | None | 7815 | 4 | 521 | South | 22M26
137697 | 2018-03-31 | Tree Contacts | Other Vegetation | Transformer #X33436 opened up due to vine interference | O/H Switchgear | Fused Cutout | 12 | 96 | 19 | Central | UC05
137699 | 2018-04-01 | Adverse Weather | Extreme Wind | SCADA indicates UG07 tripped, and at the same time UG05 auto reclosed. High Winds in effect. Circuit patrolled. | None | None | 188 | 44 | 138 | East | UG07
137702 | 2018-04-01 | Tree Contacts | Falling Tree | 24/7 located tree on primary 1 span south of switch 53. Tree on abandon 44kv dropped into 27 kv. | O/H Conductor | O/H Conductor | 94 | 22 | 34 | West | TFXF1
137702 | 2018-04-01 | Tree Contacts | Falling Tree | 24/7 located tree on primary 1 span south of switch 53. Tree on abandon 44kv dropped into 27 kv. | O/H Conductor | O/H Conductor | 2235 | 50 | 1862 | West | TFXF1
137702 | 2018-04-01 | Tree Contacts | Falling Tree | 24/7 located tree on primary 1 span south of switch 53. Tree on abandon 44kv dropped into 27 kv. | O/H Conductor | O/H Conductor | 2776 | 27 | 1249 | West | TFXF1
137703 | 2018-04-01 | Adverse Weather | Extreme Wind | G216W opened during high winds. Line was patrolled & no problems found. 21 customers affected. Uplands 4801F8. | None | None | 21 | 133 | 47 | East | 4801F8
137704 | 2018-04-01 | Defective Equipment | Electrical Failure | 75 kv transformer X34684 defective and replaced with new by on-call | O/H Transformer | O/H Transformer (1ph) | 13 | 163 | 35 | Central | TD07
137705 | 2018-04-01 | Defective Equipment | Electrical Failure | Defective cable from S12254 to TP7065, affecting 109 customers. Bilberry MTS (77M6) | U/G Cable | XLPE | 109 | 180 | 327 | East | 77M6
137706 | 2018-04-03 | Scheduled Outage | Construction | To allow Thirau Pole lines to remove an old switch, install a new switch and complete a volatge conversion | None | None | 8 | 138 | 18 | West | JKGF4
137708 | 2018-04-03 | Scheduled Outage | Maintenance | 249F4 radial O/H from pole X18215 N to EOL at 3818 Russell was isolate to allow crew to make repairs to overhead conductor. Leitrim (249F4) | None | O/H Conductor | 1 | 40 | 1 | East | LTM04
137709 | 2018-04-03 | Foreign Interference | Vehicle | A vehicle struck a pole at Merivale and Viewmount and damaged the pole and a cable dip to a transformer. Pole and dip had to be replaced affecting 2 customers. Borden Farm BDFF4 | Pole | Pole | 2 | 681 | 23 | South | 130F4
137710 | 2018-04-04 | Adverse Weather | Extreme Wind | Suspect wind slap on Red and Blue Phases causing S961 R & B to clear. Crews patrolled and re-fused the 961 RB | O/H Switchgear | Fused Cutout | 202 | 153 | 515 | South | 49F6
137711 | 2018-04-04 | Human Element | Improper Construction/installation | Adrian Henry installed wire spacers at Rideau and Springfield earlier during the day as a suspect of wire slapping toghether at this location. | O/H Conductor | O/H Conductor | 231 | 218 | 839 | East | UG05
137713 | 2018-04-04 | Human Element | Improper Construction/installation | Slack wire and wind conditions caused primary conductor to contact which caused two phases of a primary fused switch to open affecting 202 customers. Bayshore 49F6 | O/H Switchgear | Inline Switch | 202 | 190 | 640 | South | 49F6
137714 | 2018-04-04 | Tree Contacts | Broken Branch | Crew determined tree branch damaged switch. Crew refused and power restored | None | None | 3 | 49 | 2 | South | 200F3
137715 | 2018-04-04 | Defective Equipment | Defective Equipment/ Material | The ELW12 and EWL14 circuit tripped due to defective arrestor and arrestor lead at Albion Rd S of Huntclub. | Pole Attachement | Arrester | 664 | 42 | 465 | East | ELW12
137715 | 2018-04-04 | Defective Equipment | Defective Equipment/ Material | The ELW12 and EWL14 circuit tripped due to defective arrestor and arrestor lead at Albion Rd S of Huntclub. | Pole Attachement | Arrester | 2797 | 41 | 1911 | East | ELW14
137716 | 2018-04-04 | Defective Equipment | Mechanical Failure | Faulty connections on a primary fused switch at 401 Corkstown required the fuses be opened for repair affecting 2 customers. Stafford 200F1 | O/H Switchgear | Fused Cutout | 2 | 13 | 0 | South | 200F1
137717 | 2018-04-04 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X11721 TO TRANSFER CUSTOMERS TO NEW SECONDARY BUSS | None | None | 3 | 23 | 1 | West | JKGF4
137718 | 2018-04-04 | Tree Contacts | Falling Tree | Not yet known. REPORT OF A TREE ON THE WIRES AT 2050 OLD SECOND LINE RD; also had to change insulators | O/H Conductor | O/H Conductor | 415 | 9 | 62 | West | MWDF3
137718 | 2018-04-04 | Tree Contacts | Falling Tree | Not yet known. REPORT OF A TREE ON THE WIRES AT 2050 OLD SECOND LINE RD; also had to change insulators | O/H Conductor | O/H Conductor | 785 | 625 | 8177 | West | MWDF3
137719 | 2018-04-04 | Human Element | Improper Construction/installation | During the wind storm the UGK1Y1 which was carrying the UG05 load tripped open for the second time. Cause remains under investigation. Circuit to be patrolled. Vaughn (UG05) Adrian Henry installed wire spacers at Rideau and Springfield earlier during the | None | None | 231 | 11 | 42 | East | UG05
137720 | 2018-04-04 | Human Element | Improper Construction/installation | 3 phase conductor at 350 Springfield came down after heavy winds caused wires to slap together. Section of UG12 islated to make repairs. UG12 & UG05 opened to re-connect wires after repair complete. Vaughn UG12 & UG05. 463 customers affected. | O/H Conductor | O/H Conductor | 0 | 122 | 0 | East | UG05
137720 | 2018-04-04 | Human Element | Improper Construction/installation | 3 phase conductor at 350 Springfield came down after heavy winds caused wires to slap together. Section of UG12 islated to make repairs. UG12 & UG05 opened to re-connect wires after repair complete. Vaughn UG12 & UG05. 463 customers affected. | O/H Conductor | O/H Conductor | 174 | 142 | 412 | East | UG12
137720 | 2018-04-04 | Human Element | Improper Construction/installation | 3 phase conductor at 350 Springfield came down after heavy winds caused wires to slap together. Section of UG12 islated to make repairs. UG12 & UG05 opened to re-connect wires after repair complete. Vaughn UG12 & UG05. 463 customers affected. | O/H Conductor | O/H Conductor | 229 | 108 | 412 | East | UG05
137720 | 2018-04-04 | Human Element | Improper Construction/installation | 3 phase conductor at 350 Springfield came down after heavy winds caused wires to slap together. Section of UG12 islated to make repairs. UG12 & UG05 opened to re-connect wires after repair complete. Vaughn UG12 & UG05. 463 customers affected. | O/H Conductor | O/H Conductor | 231 | 13 | 50 | East | UG05
137720 | 2018-04-04 | Human Element | Improper Construction/installation | 3 phase conductor at 350 Springfield came down after heavy winds caused wires to slap together. Section of UG12 islated to make repairs. UG12 & UG05 opened to re-connect wires after repair complete. Vaughn UG12 & UG05. 463 customers affected. | O/H Conductor | O/H Conductor | 232 | 13 | 50 | East | UG12
137720 | 2018-04-04 | Human Element | Improper Construction/installation | 3 phase conductor at 350 Springfield came down after heavy winds caused wires to slap together. Section of UG12 islated to make repairs. UG12 & UG05 opened to re-connect wires after repair complete. Vaughn UG12 & UG05. 463 customers affected. | O/H Conductor | O/H Conductor | 232 | 88 | 340 | East | UG12
137721 | 2018-04-04 | Scheduled Outage | Construction | S10852 to EOL at 641 Principale was isolated to allow contractor to install new pole and new transformer. Casselman (CAS-F2) | None | None | 1 | 106 | 2 | East | CAS-F2
137723 | 2018-04-04 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One, All power restored by H1. High gusting winds. | None | None | 1715 | 6 | 172 | East | 62M2 (Casselman MS)
137724 | 2018-04-04 | Tree Contacts | Falling Tree | S15333 opened to clear large tree off line. 53 customers affected. Woodroffe TW18. | None | None | 53 | 203 | 179 | Central | TW18
137725 | 2018-04-04 | Tree Contacts | Falling Tree | Large tree on line at 3 Farnham caused Beechwood UB04 to open. Line section isolated to restore 280 customers. 13 customers remained off until repairs completed. Beechwood UB04. | None | None | 13 | 348 | 75 | East | UB04
137725 | 2018-04-04 | Tree Contacts | Falling Tree | Large tree on line at 3 Farnham caused Beechwood UB04 to open. Line section isolated to restore 280 customers. 13 customers remained off until repairs completed. Beechwood UB04. | None | None | 293 | 14 | 68 | East | UB04
137726 | 2018-04-04 | Tree Contacts | Falling Tree | Tree removed from overhead and power restored to customer | None | None | 1 | 221 | 4 | East | LTM02
137727 | 2018-04-05 | Scheduled Outage | Construction | Patrick Brisson and crew to have transformer X30014 open to remove a service. Customers notified. | None | None | 8 | 29 | 4 | Central | SB09
137728 | 2018-04-05 | Tree Contacts | Falling Tree | Fuse G476 opened after tree fell and broke conductor on Conroy S of Huntclub. 2 customers affected. Lietrim (249F4) | O/H Conductor | O/H Conductor | 2 | 146 | 5 | East | LTM04
137729 | 2018-04-05 | Scheduled Outage | Maintenance | Glen Carswell and crew to have transformer X34207 open to make repairs to overhead lines. Customers not notified. | None | None | 24 | 108 | 43 | Central | AH02
137730 | 2018-04-05 | Defective Equipment | Mechanical Failure | Replace dective PPH swiches to P393. | O/H Switchgear | Simple Solid Blade Switch | 1 | 125 | 2 | East | UT03
137731 | 2018-04-05 | Scheduled Outage | Construction | Transfer plant. | None | None | 12 | 321 | 64 | Central | UV05
137732 | 2018-04-05 | Scheduled Outage | Construction | Bill Nynekamp and crew to have transformer X24228 open to replace the pole and transformer. Customers notified. | None | None | 11 | 143 | 26 | East | AF06
137734 | 2018-04-05 | Defective Equipment | Mechanical Failure | Crew reports lead came out of hot line clamp. Crew repaired and restored. | None | None | 5 | 339 | 28 | East | 77M6
137735 | 2018-04-05 | Scheduled Outage | Construction | Transformer #X31394 isolated by crew to reconnect service | None | None | 8 | 31 | 4 | Central | SB16
137736 | 2018-04-05 | Tree Contacts | Falling Tree | TFXF4 OH section isolated to remove tree on the condutor at pole X09364, affecting 84 customers. | None | None | 84 | 24 | 34 | West | TFXF4
137737 | 2018-04-05 | Foreign Interference | Customer-Cut Trees | Transformer #X39297 isolated by crew to make repairs to wires | None | None | 18 | 25 | 8 | East | AC14
137738 | 2018-04-06 | Defective Equipment | Electrical Failure | Defective triplex repalced by 24/7 | O/H Conductor | O/H Conductor | 9 | 44 | 7 | East | 6F1
137739 | 2018-04-06 | Tree Contacts | Falling Tree | Fallen tree broke primary causing fuse 239B to open at 2145 Fifth Line Rd. 18 customers affected. Kanata (624F6) | O/H Conductor | O/H Conductor | 18 | 277 | 83 | West | 624F6
137740 | 2018-04-06 | Scheduled Outage | Construction | Replace dead end arms. | None | None | 1 | 248 | 4 | West | RHNF1
137741 | 2018-04-06 | Scheduled Outage | Construction | Secondary upgrade | None | None | 5 | 142 | 12 | Central | UV05
137742 | 2018-04-06 | Scheduled Outage | Construction | MIKE IRVEN INSTALLING 2 NEW SERVICES | None | None | 23 | 58 | 22 | Central | TW17
137743 | 2018-04-06 | Tree Contacts | Falling Tree | S1351 on Rifle Rd. opened due to fallen tree on overhead. 1 customer affected. Stafford (200F1) | O/H Conductor | O/H Conductor | 1 | 117 | 2 | South | 200F1
137744 | 2018-04-06 | Scheduled Outage | Construction | Transformer #X27088 isolated by crew to pull up several services | None | None | 33 | 67 | 37 | East | TB14
137745 | 2018-04-07 | Defective Equipment | Mechanical Failure | A faulty hot line clamp failed, 1 phase of primary came down which caused the primary fused switch to open. The other 2 phases had to be isolated to perform repairs affecting 278 customers. Lincoln Heights TD01 | O/H Conductor | Hot-Line Clamp | 97 | 247 | 399 | Central | TD01
137745 | 2018-04-07 | Defective Equipment | Mechanical Failure | A faulty hot line clamp failed, 1 phase of primary came down which caused the primary fused switch to open. The other 2 phases had to be isolated to perform repairs affecting 278 customers. Lincoln Heights TD01 | O/H Conductor | Hot-Line Clamp | 278 | 79 | 366 | Central | TD01
137747 | 2018-04-07 | Scheduled Outage | Construction | Transformer 1441 at 135 Michael Cowpland was isolated to allow crew to replace three phase transformer. Terry Fox (TFXF6) | None | None | 1 | 199 | 3 | West | TFXF6
137748 | 2018-04-07 | Defective Equipment | Mechanical Failure | REPLACED BROKEN SWITCH FEEDING TRANSFORMER X36401 | O/H Transformer | O/H Transformer (1ph) | 1 | 95 | 2 | South | 140F5
137749 | 2018-04-07 | Defective Equipment | Corrosion | Transformer PT58 at 2190 Thurston was isolated to allow crew to replace leaking transformer and remediate the soil. 8 customers were affected. Albion (2202) | U/G Transformer | Padmount (1ph) | 8 | 239 | 32 | East | 2202
137750 | 2018-04-08 | Foreign Interference | Wildlife (Bird/Animal) | ANIMAL CONTACT BLEW TRANSFORMER | O/H Transformer | O/H Transformer (1ph) | 10 | 51 | 8 | East | TB06
137751 | 2018-04-08 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X39041 TO REPLACE SECONDARY SERVICE AND TRIM TREE,S | None | None | 7 | 54 | 6 | East | SO12
137752 | 2018-04-09 | Scheduled Outage | Construction | planned outage to cut over 600V secondary | None | None | 1 | 58 | 1 | Central | SA24
137753 | 2018-04-09 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32664 TO TRANSFER HYDRO PLANT | None | None | 12 | 180 | 36 | Central | UV05
137754 | 2018-04-09 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X27345 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 11 | 220 | 40 | East | TB06
137755 | 2018-04-09 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X18834 TO REPLACE SECONDARY SERVICE | None | None | 2 | 56 | 2 | East | BLKF5
137756 | 2018-04-09 | Defective Equipment | Moisture Ingress | At 17:07 the FALT2Q and FALT2S7M breakers tripped open interrupting the load on the FAL02 and FAL04 circuit. Cause of trip remains under investigation. Fallowfield (FAL02, FAL04) | Station Equipment | Transformer | 1 | 44 | 1 | South | FAL04
137756 | 2018-04-09 | Defective Equipment | Moisture Ingress | At 17:07 the FALT2Q and FALT2S7M breakers tripped open interrupting the load on the FAL02 and FAL04 circuit. Cause of trip remains under investigation. Fallowfield (FAL02, FAL04) | Station Equipment | Transformer | 7391 | 6 | 739 | South | FAL02
137757 | 2018-04-10 | Defective Equipment | Electrical Failure | A B phase cable fault bet S19386 and TP7034 casued the outage | U/G Cable | Unknown \ Other | 62 | 173 | 179 | East | 77M1
137758 | 2018-04-10 | Scheduled Outage | Construction | Transformer #X56686 isolated by crew to transfer plant | None | None | 5 | 15 | 1 | Central | UL14
137759 | 2018-04-10 | Scheduled Outage | Construction | Transformer #X60000 isolated by crew to transfer plant | None | None | 5 | 335 | 28 | East | TB06
137762 | 2018-04-11 | Defective Equipment | Electrical Failure | Cable fault on TH1SB cable section between SC8673 and VT66 caused TL08 breaker (TL4SB) to trip. TL08 breaker was backfeeding TH1SB. | U/G Cable | PILC | 2 | 115 | 4 | Central | TL4SB
137762 | 2018-04-11 | Defective Equipment | Electrical Failure | Cable fault on TH1SB cable section between SC8673 and VT66 caused TL08 breaker (TL4SB) to trip. TL08 breaker was backfeeding TH1SB. | U/G Cable | PILC | 191 | 54 | 172 | Central | TL4SB
137763 | 2018-04-11 | Scheduled Outage | Construction | At 08:37am S22209 to end of line was isolated to allow crews to replace poles. 24 customers affected. Russell (TB06) | None | None | 24 | 327 | 131 | East | TB06
137764 | 2018-04-11 | Defective Equipment | Imminent Failure | transformer at 5 willBriar was isolated for crew to replace defective insert and elbow. 8 customers were affected. Centrepointe (87F4) | U/G Cable Attachement | Elbow \ Insert | 8 | 229 | 31 | South | 87F4
137765 | 2018-04-11 | Defective Equipment | Imminent Failure | Transformer #X32663 isolated by crew due to broken secondary ties | Secondary \ Service | O/H Service | 12 | 45 | 9 | Central | UV05
137767 | 2018-04-11 | Defective Equipment | Corrosion | An 8Kv transformer TE191 at 45 Silver Aspen was isolated to allow the crew to replace damaged secondary pedestal affecting 12 customer for 168 minutes on the BLKF1 circuit. | Secondary \ Service | Secondary Pedestal | 12 | 168 | 34 | East | BLKF1
137769 | 2018-04-11 | Scheduled Outage | Construction | 2 transformers, X32775 and X35082 isolated by crew to remove a transformer and re-arrange plant | None | None | 11 | 185 | 34 | Central | UC05
137770 | 2018-04-11 | Scheduled Outage | Construction | 2 transformers, X33778 and X33776 isolated by crew to remove a transformer and re-arrange plant | None | None | 10 | 90 | 15 | Central | UC05
137771 | 2018-04-11 | Scheduled Outage | Construction | 2 transformers, X30721 and X30722 isolated by crew to re-arrange plant for a new pole install | None | None | 28 | 140 | 65 | Central | UN06
137772 | 2018-04-11 | Defective Equipment | Electrical Failure | Transformer X36538 defective | O/H Transformer | O/H Transformer (1ph) | 5 | 199 | 17 | South | EPWF4
137773 | 2018-04-11 | Scheduled Outage | Construction | Opened transformer X36539 to feed customers from X36539 | None | None | 4 | 52 | 3 | South | EPWF4
137777 | 2018-04-12 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to replace TE1687 | None | Padmount (1ph) | 18 | 284 | 85 | South | 87F3
137779 | 2018-04-12 | Tree Contacts | Falling Tree | A tree in the primary on Piperville Rd caused the inline recloser white phase to open affecting 101 customers. Leitrim LTM02 | O/H Conductor | O/H Conductor | 101 | 137 | 231 | East | LTM02
137780 | 2018-04-12 | Tree Contacts | Falling Tree | Tree on the Jockvale 145F2 line fed from S898, tree was removed and power restored | O/H Switchgear | Fused Cutout | 13 | 47 | 10 | South | 145F2
137782 | 2018-04-13 | Scheduled Outage | Construction | Transformer X23885 at 690 Champman Blvd was isolated to allow crew to transfer plant to new pole affecting 14 customers. Russell (TB06) | None | None | 14 | 276 | 64 | East | TB06
137783 | 2018-04-13 | Defective Equipment | Electrical Failure | Transformer KT105 was isolated to allow crew to replace defective transformer affecting 16 customers. Russell (TB15) | U/G Transformer | Kiosk (3ph) | 16 | 182 | 49 | East | TB15
137784 | 2018-04-13 | Foreign Interference | Wildlife (Bird/Animal) | Switch S12843 opened due to animal contact at 1137 Checkers. Woodroffe (TW18) 30 customers were affected. | None | None | 30 | 68 | 34 | Central | TW18
137785 | 2018-04-14 | Unknown/Other | Unknown | Two 4KV circuits along elgin st. opened. Cause yet to be determined. 248 customers affected. Gladstone (UX04, UX00) | None | None | 248 | 47 | 194 | Central | UX04
137789 | 2018-04-15 | Defective Equipment | Mechanical Failure | Defective LLC at P357 | O/H Switchgear | Unknown \ Other | 28 | 18 | 8 | East | AF04
137791 | 2018-04-15 | Adverse Weather | Freezing Rain | S961 R & B phases blew, due to wires galloping/slapping together at 80 Crystal Beach. | O/H Conductor | O/H Conductor | 212 | 91 | 322 | South | 49F6
137794 | 2018-04-15 | Adverse Weather | Freezing Rain | With extreme weather the AC02 breaker trip,waited 10 minutes and closed breaker and holding | O/H Conductor | Unknown \ Other | 302 | 10 | 50 | East | AC02
137795 | 2018-04-15 | Scheduled Outage | Forced Switching | Two 13KV circuits the TM1AK and TM2AK and a 4Kv circuit AD06 was open for safety clearance to allow the crew to put a truck on a broken pole affecting 4167 customers for 15 minutes. | None | None | 691 | 15 | 173 | Central | AD06
137795 | 2018-04-15 | Scheduled Outage | Forced Switching | Two 13KV circuits the TM1AK and TM2AK and a 4Kv circuit AD06 was open for safety clearance to allow the crew to put a truck on a broken pole affecting 4167 customers for 15 minutes. | None | None | 719 | 15 | 180 | Central | TM2AK
137795 | 2018-04-15 | Scheduled Outage | Forced Switching | Two 13KV circuits the TM1AK and TM2AK and a 4Kv circuit AD06 was open for safety clearance to allow the crew to put a truck on a broken pole affecting 4167 customers for 15 minutes. | None | None | 2757 | 15 | 689 | Central | TM1AK
137796 | 2018-04-15 | Adverse Weather | Freezing Rain | TH05 breaker at hinchey opened, possibly to freezing rain and wind conditions. To be patrolled. 119 customers affected. Hinchey TH3SH, TL1TH | None | None | 119 | 54 | 107 | Central | TH3SH
137797 | 2018-04-15 | Adverse Weather | Freezing Rain | With extreme weather high winds and freezing rain the UC03 circuit trip affecting 508 customers for 7 minutes | O/H Conductor | Unknown \ Other | 508 | 7 | 59 | Central | UC03
137798 | 2018-04-15 | Adverse Weather | Freezing Rain | TB13 breaker at russell opened possibly due to freezing rain and wind. 2319 customers were affected. Russell (TB2JP) | None | None | 2319 | 19 | 734 | East | TB2JP
137799 | 2018-04-15 | Adverse Weather | Freezing Rain | opened a scadamate to allow crew to refuse at switch on hawthorne road that opened due to broken hydro pole also on Hawthorne. 1469 customers were affected. Uplands (Q4801F8) | Pole | Pole | 1469 | 16 | 392 | East | 4801F8
137801 | 2018-04-15 | Tree Contacts | Falling Tree | A tree took the secondary down at the rear of 15 Kingbury which caused the fuse to blow at 457 on the BDFF1 circuit affecting 46 customers for 144 minutes | Secondary \ Service | O/H Service | 46 | 144 | 110 | South | 130F1
137802 | 2018-04-15 | Adverse Weather | Freezing Rain | Two broken insulators caused the R and W phase to trip on the RX2042 affecting 587 customers for 329 minutes | Pole Attachement | Insulator | 587 | 329 | 3219 | West | MWDF3
137807 | 2018-04-15 | Adverse Weather | Freezing Rain | Hydro One O/H at switch S29583 on Russell Rd fell into Hydro Ottawa R phase primary which caused switch S29583 R phase and G901 R phase to blow, waiting for Hydro One to respond 10 customers remain out on the LTM02 | O/H Conductor | O/H Conductor | 10 | 2197 | 366 | East | LTM01
137807 | 2018-04-15 | Adverse Weather | Freezing Rain | Hydro One O/H at switch S29583 on Russell Rd fell into Hydro Ottawa R phase primary which caused switch S29583 R phase and G901 R phase to blow, waiting for Hydro One to respond 10 customers remain out on the LTM02 | O/H Conductor | O/H Conductor | 175 | 237 | 691 | East | LTM01
137808 | 2018-04-15 | Tree Contacts | Broken Branch | Trees in the wires caused the G60R fuse at 5081 RIDGE RD to blow affecting 6 customers on the BLKF5 circuit | O/H Conductor | O/H Conductor | 6 | 373 | 37 | East | BLKF5
137880 | 2018-04-17 | Adverse Weather | Freezing Rain | A section of Leitrim 249F4 on Hawthorne rd was isolated to replace broken pole. 92 customers affected. | Pole | Pole | 92 | 183 | 281 | East | LTM04
137881 | 2018-04-17 | Tree Contacts | Broken Branch | A section of Woodroffe 170F3 from S1120 was isolated to remove tree from wires. 14 customers affected. | None | None | 14 | 40 | 9 | South | 170F3
137882 | 2018-04-17 | Tree Contacts | Broken Branch | WX2071 opened to remove tree from line. 22 customers affected. Limebank LMBF7. | None | None | 22 | 20 | 7 | East | LMBF7
137883 | 2018-04-17 | Tree Contacts | Falling Tree | S27708 RB opened due to down neutral at 2896 High field, forestry crew required to clear tree, affecting 70 customers. Lincoln Heights (TD12) | None | None | 70 | 447 | 522 | Central | TD12
137884 | 2018-04-17 | Adverse Weather | Freezing Rain | White phase OH down at 2373 Urbandale, S24351 openned affecting 13 customers. Urbandale DS (AE07) | None | None | 13 | 205 | 44 | East | AE05
137884 | 2018-04-17 | Adverse Weather | Freezing Rain | White phase OH down at 2373 Urbandale, S24351 openned affecting 13 customers. Urbandale DS (AE07) | None | None | 98 | 80 | 131 | East | AE05
137885 | 2018-04-17 | Adverse Weather | Freezing Rain | Wires down at 1929 Highridge, Temp 143 at 1928 Highridge to EOL to make repairs, affecting 52 customers. Queens DS (UQ07) | None | None | 10 | 115 | 19 | East | UQ07
137885 | 2018-04-17 | Adverse Weather | Freezing Rain | Wires down at 1929 Highridge, Temp 143 at 1928 Highridge to EOL to make repairs, affecting 52 customers. Queens DS (UQ07) | None | None | 52 | 135 | 117 | East | UQ07
137886 | 2018-04-17 | Tree Contacts | Broken Branch | S14313 opend to repair services damaged by fallen tree. 10 customers affected. Limebank LMBF5. | Secondary \ Service | O/H Service | 10 | 205 | 34 | East | LMBF5
137887 | 2018-04-17 | Tree Contacts | Broken Branch | A section of EPWF1 from line taps at pole X36008 was isolated to remove tree branch from line. 21 customers affected. Epworth EPWF1. | None | None | 21 | 30 | 10 | South | EPWF1
137888 | 2018-04-17 | Adverse Weather | Freezing Rain | GR2 was opened to clear downed conductor from O/H lines at Spratt & Rideau rd. 1526 customers affected. Limebank LMBF5. | O/H Conductor | O/H Conductor | 1526 | 7 | 178 | East | LMBF5
137889 | 2018-04-17 | Unknown/Other | Unknown | S12814 white phase found blown, line patrolled and no cause found, affecting 50 customers. Riverdale DS (SR04) | None | None | 50 | 671 | 559 | Central | SR04
137890 | 2018-04-17 | Scheduled Outage | Maintenance | V616 at1405 prince of wales was isolated for maint, affecting 1 customer. Fisher DS (AK05) | None | None | 1 | 358 | 6 | Central | AK05
137891 | 2018-04-17 | Tree Contacts | Falling Tree | S25743 RWB opened to remove trees from line. 26 customers affected. Kanata 624F6. | None | None | 26 | 282 | 122 | West | 624F6
137892 | 2018-04-17 | Defective Equipment | Mechanical Failure | G657 opened to repair floating conductor. 6 customers qaffected. Limebank 7F2. | Pole Attachement | Insulator | 6 | 56 | 6 | East | 7F2
137893 | 2018-04-17 | Tree Contacts | Broken Branch | G555 RWB opened to remove trees from line. 1 customer affected. Blackburn BLKF4. | None | None | 1 | 92 | 2 | East | BLKF4
137894 | 2018-04-17 | Adverse Weather | Freezing Rain | Transformer #X31430 isolated by crew to make repairs | None | None | 1 | 57 | 1 | Central | TH15
137895 | 2018-04-17 | Scheduled Outage | Forced Switching | Transformer at 1075 Bridge was isolated to replace blown secondary transformer fuses affecting 1 customer. Limebank LMBF5 | None | Padmount (3ph) | 1 | 22 | 0 | East | LMBF5
137896 | 2018-04-17 | Tree Contacts | Falling Tree | A 3 phase run off at 5185 Dolman Ridge was isolated to remove a tree from the primary affecting 1 customer. Blackburn BLKF5 | O/H Conductor | O/H Conductor | 1 | 81 | 1 | East | BLKF5
137897 | 2018-04-17 | Defective Equipment | Electrical Failure | A broken Lightning arrestor at Rotaryway and Bank required isolation for repair affecting 1 customer. Leitrim LTM01 | Pole Attachement | Arrester | 1 | 549 | 9 | East | LTM01
137899 | 2018-04-17 | Defective Equipment | Electrical Failure | Cable to TE1671 FROM G660 is faulted affecting 1 customer. (City of Ottawa) Bilberry Creek 77M2 | U/G Cable | XLPE | 1 | 5027 | 84 | East | 77M2
137900 | 2018-04-17 | Tree Contacts | Broken Branch | Switch S27539 open due to branch on primary at 2 Reidhaven. 26 customers were affected. Queensway Carelton (160F1) | O/H Switchgear | Fused Cutout | 26 | 124 | 54 | South | 160F1
137902 | 2018-04-17 | Scheduled Outage | Forced Switching | An out of phase condition caused the secondary fuse in the transformer at 5219 Mitch Owens to open affecting 1 customer. Limebank LMBF5 | None | Padmount (3ph) | 1 | 65 | 1 | East | LMBF5
137903 | 2018-04-18 | Adverse Weather | Freezing Rain | To allow Hydro Ottawa line crew to change a damaged secondary service. Service was damaged in the ice storm. | Secondary \ Service | O/H Service | 6 | 40 | 4 | Central | TH01
137904 | 2018-04-18 | Defective Equipment | Imminent Failure | SH04 circuit was isolated to repair defective cross arm on Parkdale Ave, affecting 332 customers, Holland DS (SH04). | Pole | Crossarm | 332 | 46 | 255 | Central | SH04
137905 | 2018-04-18 | Tree Contacts | Broken Branch | Tree on the primary on Montreal Rd near pole 65A4D-0248 | O/H Conductor | Unknown \ Other | 10 | 94 | 16 | East | AP02
137905 | 2018-04-18 | Tree Contacts | Broken Branch | Tree on the primary on Montreal Rd near pole 65A4D-0248 | O/H Conductor | Unknown \ Other | 34 | 99 | 56 | East | AP04
137907 | 2018-04-18 | Tree Contacts | Falling Tree | S17088 open to allow forestry crew to remove tree from overhead. | O/H Conductor | O/H Conductor | 33 | 53 | 29 | Central | SR09
137908 | 2018-04-18 | Adverse Weather | Freezing Rain | SB09 OH to eol was isolated to repair damage insulators, affecting 25 customers. Bronson DS (SB09) | Pole Attachement | Insulator | 25 | 75 | 31 | Central | SB09
137910 | 2018-04-18 | Defective Equipment | Defective Equipment/ Material | 1 tx blown on 347 tx bank. 16kv 75 kva 347 tx required for road side of tx bank. leads have been removed from defective tx. all three fuses open and leads removed | O/H Transformer | O/H Transformer (1ph) | 1 | 256 | 4 | East | 7F2
137911 | 2018-04-19 | Scheduled Outage | Construction | VT485 at 947 Richmond Rd. isolated to replace cutouts and arrestors. 2 customers affected. Lincoln Heights (TD06) | None | Arrester | 2 | 45 | 2 | Central | TD06
137912 | 2018-04-19 | Scheduled Outage | Maintenance | Adam Donaldson and Chris Peasley to have transformer 54B2D-0464 open to make secondary repairs. At 10:39 they opebbed X26259 to expand the outage. | None | None | 8 | 27 | 4 | East | TB2JP
137912 | 2018-04-19 | Scheduled Outage | Maintenance | Adam Donaldson and Chris Peasley to have transformer 54B2D-0464 open to make secondary repairs. At 10:39 they opebbed X26259 to expand the outage. | None | None | 19 | 35 | 11 | East | TB2JP
137913 | 2018-04-19 | Scheduled Outage | Vegetation Management | Adam McNulty and crew to have transformer X30789 open for tree contractors to work. | None | None | 7 | 43 | 5 | Central | SR01
137914 | 2018-04-19 | Defective Equipment | Imminent Failure | Dave MacDonald and crew to have transformer X5787 open to replace a broken cut out and arrestor. | O/H Switchgear | Fused Cutout | 1 | 23 | 0 | South | 145F3
137915 | 2018-04-19 | Scheduled Outage | Maintenance | Bill Nyenkamp and crew to have transformers X23420 and X23416 open to repair secondary neutral bus and disconnect damaged services. | None | None | 24 | 65 | 26 | East | AP03
137916 | 2018-04-19 | Scheduled Outage | Maintenance | Cory Nixon and crew to have transformer X27489 open to isolate a service. | None | None | 7 | 40 | 5 | Central | 505
137918 | 2018-04-19 | Tree Contacts | Broken Branch | 4801F8 overhead line from S16332 isolated to allow crew to remove branches off the overhead. | None | None | 1 | 41 | 1 | East | 4801F8
137919 | 2018-04-20 | Scheduled Outage | Construction | Bill Nyenkamp and crew to have transformers X25483 and X25484 open to remove and replace. Customers notified. | None | None | 17 | 155 | 44 | Central | UJ07
137924 | 2018-04-21 | Defective Equipment | Mechanical Failure | X24016 opened due to a broken switch. 15 customers affected. Bilberry 77M2. | O/H Switchgear | Fused Cutout | 15 | 176 | 44 | East | 77M2
137925 | 2018-04-21 | Scheduled Outage | Construction | Vault V225 at 830 Campbell was isolated to allow crew to rearange the dipswitch to make clearance to stand new pole affecting 1 customer. Clyde (UC03) | None | None | 1 | 341 | 6 | Central | UC03
137926 | 2018-04-21 | Scheduled Outage | Construction | Set new pole | None | None | 8 | 35 | 5 | Central | UC02
137927 | 2018-04-21 | Defective Equipment | Defective Equipment/ Material | Isolate transformer pole, replace old box switch, replace 25m of #2 triplex, service is burnt in the tree | O/H Transformer | Unknown \ Other | 6 | 72 | 7 | Central | SM06
137930 | 2018-04-22 | Defective Equipment | Defective Equipment/ Material | Defective secondary line need to be repaired | O/H Transformer | O/H Transformer (1ph) | 8 | 95 | 13 | South | 190F2
137931 | 2018-04-22 | Defective Equipment | Electrical Failure | Defective lightning arrestor caused S519 to open. 47 customers affected. Bayshors 49F6 | Pole Attachement | Arrester | 47 | 159 | 125 | South | 49F6
137932 | 2018-04-22 | Scheduled Outage | Construction | TV5850 isolated to transfer plant to new pole, affecting 1 customer. (Richmond South DS (28F2) | None | None | 1 | 310 | 5 | West | 28F2
137933 | 2018-04-23 | Scheduled Outage | Construction | TB06 ovehead circuit on Weston was isolated to allow crew to perfrom pole replacement. 65 customers were affected. Russell (TB06) | None | None | 65 | 432 | 468 | East | TB06
137934 | 2018-04-23 | Defective Equipment | Electrical Failure | TO REPLACE CONNECTIONS ON TRANSFORMER POLE | Secondary \ Service | O/H Service | 14 | 65 | 15 | South | 84F2
137935 | 2018-04-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33975 TO REPLACE OPEN WIRE SECONDARY BUSS | None | None | 14 | 45 | 10 | Central | UV03
137936 | 2018-04-23 | Scheduled Outage | Construction | REPLACING TRANSFORMER | None | None | 3 | 180 | 9 | East | UQ07
137937 | 2018-04-23 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X58935 TO TO REPLACE CONNECTIONS ON THE SECONDARY BUSS | None | None | 9 | 35 | 5 | Central | UV05
137938 | 2018-04-23 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X27215 | None | None | 3 | 120 | 6 | East | UQ07
137939 | 2018-04-23 | Adverse Weather | Ice/Icing | Reconnectiion of service | None | None | 12 | 30 | 6 | Central | SM16
137940 | 2018-04-23 | Scheduled Outage | Maintenance | Transformer #X28227 isolated by crew to make temporary repairs to reconnect a service after the storm | None | None | 5 | 20 | 2 | East | TA3AF
137941 | 2018-04-24 | Scheduled Outage | Construction | Rick Barnett and crew to have transformer X17368 open for construction purposes. Customers notified. | None | None | 13 | 80 | 17 | East | 77M2
137942 | 2018-04-24 | Scheduled Outage | Construction | The 4Kv overhead in the rear of 2416 Malone was isolated to allow the crews transfer plant to new poles and remove the old plant, affecting 54 customers on the UV05 circuit for 228 minutes. | O/H Conductor | O/H Conductor | 54 | 228 | 205 | Central | UV05
137943 | 2018-04-24 | Defective Equipment | Defective Equipment/ Material | defective transformer | U/G Transformer | Padmount (1ph) | 10 | 271 | 45 | West | TFXF1
137944 | 2018-04-24 | Scheduled Outage | Maintenance | Shaun Cunningham and crew to have transformer X20170 open to replace cut out switch and leed. | None | None | 4 | 37 | 2 | East | LTM01
137946 | 2018-04-24 | Scheduled Outage | Construction | The 13kv overhead at the rear of 2046 Haig was isolated to allow the crew to replace poles affecting 24 customers on the TB06 circuit for 390 minutes. | None | None | 24 | 390 | 156 | East | TB06
137947 | 2018-04-24 | Scheduled Outage | Construction | Transformer #X30797 isolated by crew to reconnect service at 77 Delaware | None | None | 14 | 13 | 3 | Central | UX05
137948 | 2018-04-24 | Defective Equipment | Defective Equipment/ Material | Transformer #X33371 opened up due to open buss sagging | O/H Switchgear | Fused Cutout | 9 | 152 | 23 | South | EPWF3
137951 | 2018-04-25 | Scheduled Outage | Maintenance | At 06:39am PT7 was isolate to replace old cutouts and arrestors. Lincoln Heights (TD01) | None | None | 1 | 56 | 1 | Central | TD01
137952 | 2018-04-25 | Unknown/Other | Unknown | Mike VanDelst and crew report no visible cause of outage. Refused transformer X35229 and closed. | O/H Switchgear | Fused Cutout | 10 | 49 | 8 | West | JKGF5
137953 | 2018-04-25 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X32378 open to replace the transformer. Customers notified. | None | None | 16 | 60 | 16 | Central | TD06
137954 | 2018-04-25 | Tree Contacts | Broken Branch | Oakley McCoy and crew to have transformer X28061 open to remove a limb from the secondary bus. | None | None | 19 | 60 | 19 | East | AF04
137955 | 2018-04-25 | Scheduled Outage | Construction | Mike Irven to have transformer X24495 open to install a new service. Customers notified via phone system. | None | None | 4 | 55 | 4 | East | UB07
137956 | 2018-04-25 | Tree Contacts | Broken Branch | A large tree limb on the primary 2197 Saunderson required the circuit off potential to safely remove the limb affecting 266 customers. Urbandale AE02 | None | None | 266 | 10 | 44 | East | AE02
137957 | 2018-04-25 | Defective Equipment | Electrical Failure | 2 station breakers tripped affecting 1626 customers, customer reports of a flash on Enfield south of McArthur investigated, no apparent cause found. Load was restored in stages. Overbrook TO3UT, Eastview UT05 Crew patrolled the circuit and found a Blo | U/G Cable Attachement | Pothead | 232 | 114 | 441 | East | UT05
137957 | 2018-04-25 | Defective Equipment | Electrical Failure | 2 station breakers tripped affecting 1626 customers, customer reports of a flash on Enfield south of McArthur investigated, no apparent cause found. Load was restored in stages. Overbrook TO3UT, Eastview UT05 Crew patrolled the circuit and found a Blo | U/G Cable Attachement | Pothead | 590 | 18 | 177 | East | TO3UT
137957 | 2018-04-25 | Defective Equipment | Electrical Failure | 2 station breakers tripped affecting 1626 customers, customer reports of a flash on Enfield south of McArthur investigated, no apparent cause found. Load was restored in stages. Overbrook TO3UT, Eastview UT05 Crew patrolled the circuit and found a Blo | U/G Cable Attachement | Pothead | 944 | 12 | 189 | East | TO3UT
137957 | 2018-04-25 | Defective Equipment | Electrical Failure | 2 station breakers tripped affecting 1626 customers, customer reports of a flash on Enfield south of McArthur investigated, no apparent cause found. Load was restored in stages. Overbrook TO3UT, Eastview UT05 Crew patrolled the circuit and found a Blo | U/G Cable Attachement | Pothead | 1394 | 74 | 1719 | East | TO3UT
137958 | 2018-04-26 | Tree Contacts | Falling Tree | A Hydro Ottawa line crew had to open X33377 to allow a removal of a tree from the O/H conductor. The tree was causing the customer at 1055 Roman to have partial power | None | O/H Conductor | 11 | 123 | 23 | Central | TD05
137959 | 2018-04-26 | Loss Of Supply | Transmission Inadvertent | Loss of supply from Hydro One. 325M8 , 1532 customers affected. | None | None | 1532 | 2 | 51 | East | 325M8
137960 | 2018-04-26 | Scheduled Outage | Construction | Scott Barkley and crew to have transformer X45309 open for construction purposes. Customers notified. | None | None | 5 | 111 | 9 | Central | UN07
137961 | 2018-04-28 | Tree Contacts | Broken Branch | Transformer #2003 opened up due to tree contact | O/H Switchgear | Fused Cutout | 1 | 272 | 5 | West | 624F6
137964 | 2018-04-28 | Tree Contacts | Broken Branch | At 4:48pm G605B and G604B downstream both blew due to a branche on the line. 17 customers affected. Limebank (7F4) | None | None | 2 | 24 | 1 | East | 7F4
137964 | 2018-04-28 | Tree Contacts | Broken Branch | At 4:48pm G605B and G604B downstream both blew due to a branche on the line. 17 customers affected. Limebank (7F4) | None | None | 17 | 82 | 23 | East | 7F4
137965 | 2018-04-29 | Scheduled Outage | Construction | Transformer #TP9148 isolated by crew to replace fuse in transformer | None | None | 10 | 6 | 1 | West | JKGF4
137968 | 2018-05-01 | Defective Equipment | Moisture Ingress | ELWT1 low side outdoor bus duct bus is blown reason unknown at this time. | Station Equipment | Unknown \ Other | 4857 | 46 | 3724 | East | ELW01
137969 | 2018-05-01 | Scheduled Outage | Construction | Sam Gibson and crew to have transformer X33509 open to remove from service for pole replacement. Customers being moved to new transformer. Customers notified. | None | None | 5 | 240 | 20 | Central | AK12
137970 | 2018-05-01 | Scheduled Outage | Construction | Replace overhead conductor. | None | None | 1 | 278 | 5 | South | 200F1
137971 | 2018-05-01 | Scheduled Outage | Construction | Overhead circuit from S29237 to EOL on Osgood isolated to replace 5 spans of primary conductor. 29 customers affected. Henderson (UN06) | None | O/H Conductor | 29 | 222 | 107 | Central | UN06
137972 | 2018-05-01 | Defective Equipment | Mechanical Failure | Fuse S12814 on Clegg St. opened due guy wire wraped in primary. 186 customers affected. Riverdale (SR04) | Pole Attachement | Unknown \ Other | 127 | 143 | 303 | Central | SR04
137972 | 2018-05-01 | Defective Equipment | Mechanical Failure | Fuse S12814 on Clegg St. opened due guy wire wraped in primary. 186 customers affected. Riverdale (SR04) | Pole Attachement | Unknown \ Other | 186 | 81 | 251 | Central | SR04
137974 | 2018-05-02 | Scheduled Outage | Construction | KT617 at Woodroffe and Halldon isolated to replace primary siwthces. 6 customers affected. Lincoln Heights (TD06) | None | Fused Cutout | 6 | 20 | 2 | Central | TD06
137975 | 2018-05-02 | Scheduled Outage | Construction | MT1691 at Woodroffe and Flower isolated to replace primary switches. 6 cusomters affected. Lincoln Heights (TD06) | None | Fused Cutout | 6 | 21 | 2 | Central | TD06
137976 | 2018-05-02 | Scheduled Outage | Construction | Replace switch and transformer. | None | None | 1 | 89 | 1 | West | JKGF4
137977 | 2018-05-02 | Scheduled Outage | Vegetation Management | Tree trimming | None | None | 21 | 245 | 86 | Central | TD05
137978 | 2018-05-02 | Defective Equipment | Mechanical Failure | Overhead circuit from G461W to EOL isolated due to broken pole. 45 customers affected. South Glouster (56F1) | Pole | Pole | 13 | 388 | 84 | East | 56F1
137978 | 2018-05-02 | Defective Equipment | Mechanical Failure | Overhead circuit from G461W to EOL isolated due to broken pole. 45 customers affected. South Glouster (56F1) | Pole | Pole | 45 | 182 | 136 | East | 56F1
137979 | 2018-05-02 | Scheduled Outage | Construction | TE1163 at 6 Bexley was isolated to allow crews to transfer plant to new poles. 8 customers affected. Stafford (200F3) | None | Pole | 8 | 233 | 31 | South | 200F3
137980 | 2018-05-02 | Defective Equipment | Mechanical Failure | Defective CS17894 | O/H Switchgear | Load Break Gang | 2396 | 3 | 120 | South | 22M26
137981 | 2018-05-03 | Scheduled Outage | Construction | planned outage to lower duct structure | None | None | 1 | 340 | 6 | Central | AK05
137983 | 2018-05-03 | Scheduled Outage | Vegetation Management | Mike Van Delst and crew to have transformer X27796 open for forestry crew to remove tree limb. Customers notified. | None | None | 12 | 44 | 9 | East | UQ07
137984 | 2018-05-03 | Tree Contacts | Falling Tree | Tree on the line at Renaud and Saddleridge required isolation of radial overhead for removal of tree | None | None | 6 | 35 | 4 | East | CYRF3
137985 | 2018-05-03 | Scheduled Outage | Construction | Mike Irven and crew to have transformer X32644 open to remove a service. Customers notified. | None | None | 6 | 15 | 2 | Central | TD05
137986 | 2018-05-03 | Loss Of Supply | Transmission Inadvertent | Woodroffe T4 tripped on Differential, with Lincoln Heghts abnormal the bbus pair lost load when the tripp occurred | None | None | 7119 | 3 | 356 | Central | TD01
138017 | 2018-05-05 | Tree Contacts | Falling Tree | To allow crew to remove trees off overhead lines. | None | None | 7 | 1193 | 139 | South | 200F1
138019 | 2018-05-05 | Adverse Weather | Extreme Wind | Primary down in the rear of 1269 Fellows. | None | None | 11 | 210 | 38 | Central | TW17
138037 | 2018-05-05 | Tree Contacts | Falling Tree | tree in the overhead at X20119 affecting 162 cust. Lietrim DS (LTM02) | None | None | 162 | 258 | 697 | East | LTM02
138040 | 2018-05-05 | Tree Contacts | Falling Tree | S12921 found blown due to fallen tree, affecting 26 customers. Russell TS (TB2JP) | None | None | 26 | 502 | 218 | East | TB2JP
138042 | 2018-05-05 | Tree Contacts | Falling Tree | Tree took down a section of primary on Aldercest from pole X36765 on the EPW3. | O/H Conductor | O/H Conductor | 20 | 494 | 165 | South | EPWF3
138044 | 2018-05-05 | Scheduled Outage | Construction | V832 at 969 River isolated to replace primary cut outs. 55 customers affected. Eastview (UT12) | None | Fused Cutout | 55 | 26 | 24 | East | UT12
138046 | 2018-05-05 | Tree Contacts | Falling Tree | Tree on overhead line | O/H Conductor | Unknown \ Other | 3 | 829 | 41 | West | RHNF3
138047 | 2018-05-05 | Tree Contacts | Falling Tree | Tree on line | O/H Conductor | Unknown \ Other | 1 | 245 | 4 | South | 200F1
138050 | 2018-05-05 | Tree Contacts | Falling Tree | Tree on overhead line. | None | None | 31 | 98 | 51 | West | 43F3
138051 | 2018-05-05 | Tree Contacts | Falling Tree | Tree on primary caused S20643 to open. 14 customers affected. Leitrim (LTM02) | O/H Conductor | O/H Conductor | 14 | 521 | 122 | East | LTM02
138054 | 2018-05-05 | Adverse Weather | Extreme Wind | Broken Pole | O/H Conductor | Unknown \ Other | 12 | 979 | 196 | East | 7F2
138054 | 2018-05-05 | Adverse Weather | Extreme Wind | Broken Pole | O/H Conductor | Unknown \ Other | 22 | 458 | 168 | East | 7F2
138055 | 2018-05-06 | Tree Contacts | Falling Tree | Tree on the primary at 960 Winnington. | None | None | 36 | 170 | 102 | Central | TW22
138056 | 2018-05-06 | Tree Contacts | Falling Tree | Downed tree leaning on overhead | O/H Conductor | Unknown \ Other | 60 | 65 | 65 | East | LTM01
138057 | 2018-05-06 | Defective Equipment | Mechanical Failure | 28F3 radial section isolated at 5909 Ottawa to replace damaged pole, affecting 1 customer. Richmond South DS. | Pole | Pole | 1 | 138 | 2 | West | 28F3
138058 | 2018-05-06 | Foreign Interference | Wildlife (Bird/Animal) | G11R opened due to squirrel contact. 46 customers affected. Moulton 8F1. | None | None | 46 | 120 | 92 | East | 8F1
138059 | 2018-05-06 | Tree Contacts | Falling Tree | S18599 opened to remove tree from primary line. 67 customers affected. Edwin UV04. | None | None | 67 | 135 | 151 | Central | UV04
138060 | 2018-05-06 | Tree Contacts | Falling Tree | AP05 line isolated to remove tree from Primary at 920 Bathgate. | None | None | 546 | 8 | 73 | East | AP05
138061 | 2018-05-06 | Tree Contacts | Falling Tree | ISOLATED TRANSFORMER X26876 TO REMOVE TREE BRANCH FROM THE OPEN WIRE SECONDARY | None | None | 9 | 50 | 8 | East | TB3LE
138062 | 2018-05-06 | Tree Contacts | Falling Tree | SM06 line complete was isolated to remove tree at 517 Island park, affecting 261 customers. Carling DS | None | None | 261 | 85 | 370 | Central | SM06
138063 | 2018-05-06 | Tree Contacts | Falling Tree | X35959 at 965 Sheridan opeed to remove tree fromm secondary . 7 customers affected. Shillington AD06. | None | None | 7 | 86 | 10 | Central | AD06
138064 | 2018-05-06 | Tree Contacts | Falling Tree | 47F6 from S25142 to EOL isolated to remove tree from overhead. 4 customers affected. Bells Corners (47F6) | None | None | 4 | 94 | 6 | South | 47F6
138065 | 2018-05-07 | Tree Contacts | Falling Tree | UD04 overhead section at 551 besserer was isolated to remove tree on the overhead, 10 customers affected. Augusta DS (UD04). | None | None | 10 | 154 | 26 | Central | UD04
138066 | 2018-05-07 | Defective Equipment | Mechanical Failure | S395 opened to replace broken switch. 1 customer affected. Jockvale 145F3. | O/H Switchgear | Fused Cutout | 1 | 25 | 0 | South | 145F3
138067 | 2018-05-07 | Defective Equipment | Mechanical Failure | S17180 to EOL isolated to repair damaged pole, affecting 2 customers. Uplands DS (UPLF8) | None | None | 2 | 278 | 9 | East | 4801F8
138068 | 2018-05-07 | Tree Contacts | Falling Tree | G30R opened to remove tree from line. 49 customers affected. Limebank 7F4. | None | None | 49 | 140 | 114 | East | 7F4
138069 | 2018-05-07 | Tree Contacts | Falling Tree | outage to remove tree on wires | None | None | 4 | 37 | 2 | East | LMBF7
138070 | 2018-05-08 | Defective Equipment | Mechanical Failure | To allow Hydro Ottawa line crews to change a defective elbow in transformer TP6064 | U/G Cable Attachement | Elbow \ Insert | 9 | 114 | 17 | South | 145F1
138072 | 2018-05-08 | Unknown/Other | Unknown | The RX2038 tripped open, crew patrol R phase radial line and did not find anything. Beckwith (BECKF2) | O/H Switchgear | Recloser (1ph) | 24 | 139 | 56 | West | BECKF2
138073 | 2018-05-08 | Defective Equipment | Mechanical Failure | To allow Hydro Ottawa line crews to change a broken bushing in TP6063 | U/G Cable Attachement | Termination \ Stress Cone | 12 | 90 | 18 | South | 145F1
138074 | 2018-05-08 | Tree Contacts | Falling Tree | To allow Hydro Ottawa lne crew remove a tree off the O/H conductor | None | None | 54 | 32 | 29 | South | 47F3
138075 | 2018-05-08 | Scheduled Outage | Construction | To allow Thirau line crews to install new switches | None | None | 28 | 212 | 99 | West | RHNF3
138076 | 2018-05-08 | Defective Equipment | Electrical Failure | crew replaced defective transformer | O/H Transformer | O/H Transformer (1ph) | 4 | 175 | 12 | West | MWDF3
138077 | 2018-05-09 | Defective Equipment | Defective Equipment/ Material | Replace defective transformer | O/H Transformer | O/H Transformer (1ph) | 4 | 134 | 9 | South | EPWF4
138078 | 2018-05-09 | Scheduled Outage | Construction | Vault V745 was isolated to allow crew to decomisson vault and reservice customer with secondary conductor. 33 customers were affeted. King Edward (SK10) | None | None | 33 | 396 | 218 | Central | SK10
138079 | 2018-05-09 | Scheduled Outage | Construction | A Hydro Ottawa line crew opened transformer X33374 to allow for a service to be disconnected | None | None | 6 | 22 | 2 | South | EPWF3
138080 | 2018-05-09 | Scheduled Outage | Construction | Hydro Ottawa crews isolated transformers TP5586 & transformer 153 to allow for plant to be transferred from an old pole to a new pole | None | None | 26 | 257 | 111 | West | 28F2
138081 | 2018-05-09 | Scheduled Outage | Construction | TRNSFR PLANT | None | None | 5 | 55 | 5 | Central | UN05
138082 | 2018-05-09 | Defective Equipment | Mechanical Failure | 180F4 W conductor down on Brookdale Ave East of Merivale, due to a failed quick sleeve. | O/H Conductor | Sleeve | 10 | 120 | 20 | South | 180F4
138082 | 2018-05-09 | Defective Equipment | Mechanical Failure | 180F4 W conductor down on Brookdale Ave East of Merivale, due to a failed quick sleeve. | O/H Conductor | Sleeve | 88 | 59 | 87 | South | 180F4
138083 | 2018-05-09 | Defective Equipment | Defective Equipment/ Material | 13KV padmount transformer at 2910 Carling was isolated to repair defective arrester, affecting 2 customers. Lincoln Heights (TD12) | Pole Attachement | Arrester | 2 | 273 | 9 | Central | TD12
138084 | 2018-05-09 | Tree Contacts | Broken Branch | RHNF2 tripped while restoring S23466W. A tree branch was found on the line 676 customers affected. Richmond North RHNF2. | None | None | 20 | 42 | 14 | West | RHNF2
138084 | 2018-05-09 | Tree Contacts | Broken Branch | RHNF2 tripped while restoring S23466W. A tree branch was found on the line 676 customers affected. Richmond North RHNF2. | None | None | 20 | 114 | 38 | West | RHNF2
138084 | 2018-05-09 | Tree Contacts | Broken Branch | RHNF2 tripped while restoring S23466W. A tree branch was found on the line 676 customers affected. Richmond North RHNF2. | None | None | 676 | 2 | 23 | West | RHNF2
138085 | 2018-05-10 | Defective Equipment | Mechanical Failure | planned outage to replace a damaged secondary pedistal | Secondary \ Service | Secondary Pedestal | 10 | 159 | 26 | East | BCHF3
138086 | 2018-05-10 | Scheduled Outage | Construction | Replace 4 trnasformers | None | None | 28 | 197 | 92 | West | BRDF3
138087 | 2018-05-10 | Tree Contacts | Broken Branch | Tree contact | O/H Switchgear | Unknown \ Other | 8 | 103 | 14 | West | 28F3
138088 | 2018-05-10 | Tree Contacts | Falling Tree | S20148 at 2022 Bel-Air opened to remove tree from line. 20 customers affected. Woodroffe TW18. | None | None | 20 | 101 | 34 | Central | TW18
138089 | 2018-05-11 | Scheduled Outage | Maintenance | 13kv overhead transformer x33897 was isolted to make repairs to defective secondary bus neutral, affecting 11 customers. Woodroffe TS (TW22) | None | None | 11 | 190 | 35 | Central | TW22
138091 | 2018-05-11 | Scheduled Outage | Forced Switching | Out of phase conditions. | None | None | 73 | 13 | 16 | West | TFXF4
138092 | 2018-05-11 | Scheduled Outage | Forced Switching | Out of phase conditions. | None | None | 73 | 6 | 7 | West | TFXF4
138093 | 2018-05-11 | Unknown/Other | Unknown | Unknow possible animal contact. | Unknown \ Other | Unknown \ Other | 26 | 131 | 57 | South | 47F4
138094 | 2018-05-11 | Foreign Interference | Vehicle | S2078 to EOL at Sheffield and Leeds was isolated to allow crew to replace dammaged cause by MOV. 36 customers were affected. Bantree AL06 | None | None | 36 | 148 | 89 | East | AL06
138096 | 2018-05-12 | Scheduled Outage | Construction | TO RELOCATE PRIMARY SWITCH S17741 ON THE SB05 OUT OF BRONSON | None | None | 20 | 81 | 27 | Central | SB05
138098 | 2018-05-12 | Scheduled Outage | Construction | Hydro Ottawa crews had an outage on transformer X48148 to allow for the transfer of plant to a new pole | None | None | 12 | 165 | 33 | Central | TR09
138099 | 2018-05-12 | Defective Equipment | Electrical Failure | Switch S26067 B phase termination burnt off causing ans outage to down stream B phase transformers. 53 Customers were affected. Tery Fox (TFXF4) | U/G Cable Attachement | Termination \ Stress Cone | 53 | 89 | 79 | West | TFXF4
138104 | 2018-05-13 | Scheduled Outage | Construction | Johnathon Parker and Brad Todd to have transformer X33231 open to replace an Overhead triplex to 14 Bowmoor Ave. due to a fire. | None | None | 8 | 46 | 6 | South | 190F5
138105 | 2018-05-13 | Scheduled Outage | Maintenance | A transformer at 12 Bowmoor was opened to repair an open wire bus neutral affecting 8 customers. Parkwood Hills 190F5 | None | O/H Service | 8 | 39 | 5 | South | 190F5
138106 | 2018-05-14 | Scheduled Outage | Construction | voltage conversion | None | None | 20 | 274 | 91 | West | JKGF4
138107 | 2018-05-14 | Scheduled Outage | Construction | Transformer #X33202 isolated by crew to install new service | None | None | 14 | 83 | 19 | Central | TD05
138109 | 2018-05-14 | Defective Equipment | Mechanical Failure | TO make repairs to broken insert pin at transformer 683 | None | None | 1 | 48 | 1 | West | BRDF3
138110 | 2018-05-14 | Scheduled Outage | Vegetation Management | Transformer #X32577 isolated by crew to drop 2 services for tree removal. | None | None | 9 | 25 | 4 | Central | TD01
138111 | 2018-05-14 | Scheduled Outage | Construction | 3 transformers (X33231, X33232 and X33229) isolated by crew to replace neutral | None | None | 28 | 85 | 40 | South | 190F5
138112 | 2018-05-14 | Scheduled Outage | Construction | Transformer #X24492 isolated by crew to replace damaged service | None | None | 5 | 30 | 2 | East | UB07
138113 | 2018-05-14 | Scheduled Outage | Construction | planned outage to transfer plant | None | None | 1 | 261 | 4 | West | 28F2
138114 | 2018-05-14 | Scheduled Outage | Construction | 2 transformers, X29757 and X29758, isolated by crew for a pole replacement | None | None | 10 | 300 | 50 | Central | SR02
138115 | 2018-05-14 | Scheduled Outage | Construction | Transformer #X32577 isolated by crew to hang 2 services back up | None | None | 9 | 40 | 6 | Central | TD01
138117 | 2018-05-15 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 1466 | 12 | 293 | East | 77M2
138118 | 2018-05-15 | Foreign Interference | Wildlife (Bird/Animal) | An animal made contact with switch S17287 at 1710 Boyer causing the W & B phase to blow on the 77M2 circuit affecting 95 customers for 107 min. | O/H Switchgear | Fused Cutout | 95 | 107 | 169 | East | 77M2
138119 | 2018-05-15 | Scheduled Outage | Construction | At 09:15am a section of EPWF1 was isolated to allow crews to replace poles. 14 customers affected. Epworth (EPWF1) | None | None | 14 | 106 | 25 | South | EPWF1
138120 | 2018-05-15 | Scheduled Outage | Construction | crew isolated transformer feeding 2140 walkley to transfer overhead switch to new pole. One customer was affected. Urbandale (AE04) | None | None | 1 | 465 | 8 | East | AE04
138121 | 2018-05-15 | Defective Equipment | Defective Equipment/ Material | crew isolated transformer at 936 dynes to replace defective secondary pedestal. 23 customers affected. Fisher (AK04) | U/G Switchgear | Primary Pedestal | 23 | 170 | 65 | Central | AK04
138122 | 2018-05-15 | Scheduled Outage | Construction | crew isolated section of overhead for pole replacement on alton and Pleasant park. 25 customers affected. Russell (TB06) | None | None | 25 | 376 | 157 | East | TB06
138124 | 2018-05-15 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32378 TO TRANSFER HYDRO PLANT TO NEW POLE AND TRANSFORMER | None | None | 15 | 248 | 62 | Central | TD06
138125 | 2018-05-15 | Scheduled Outage | Construction | VT639 was isoalted to replace the vault transformers and fusing. | None | None | 1 | 194 | 3 | Central | TH01
138128 | 2018-05-16 | Scheduled Outage | Construction | ISOLATED 3 TRANSFORMERS X58908, X58909 AND X33918 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 22 | 158 | 58 | Central | UV07
138129 | 2018-05-16 | Defective Equipment | Imminent Failure | At 10:37am TE2411 was isolated to allow crew to replace leaking transformer. 1 customer affected. Beaconhill (BCHF8) | None | Padmount (3ph) | 1 | 270 | 4 | East | BCHF8
138130 | 2018-05-16 | Scheduled Outage | Maintenance | A 4Kv O/H in the rear of 341 Osgood St was isolated to allow the crews to replace 5 spans of O/H primary conductor and to trim trees affecting 29 customers on the UN06 for 216 minutes | None | O/H Conductor | 29 | 216 | 104 | Central | UN06
138131 | 2018-05-16 | Scheduled Outage | Construction | Transformer #X24911 isolated by crew to replace service | None | None | 8 | 35 | 5 | East | UZ03
138132 | 2018-05-16 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMER X29756 AND X33997 TO INSTALL NEW POLES | None | None | 15 | 317 | 79 | Central | UV05
138133 | 2018-05-16 | Defective Equipment | Imminent Failure | At 5:00pm transformer 153 was isolated to allow crew to replace leaking transforme. 10 customers affected. Bridlewood (BRDF4) | None | Padmount (1ph) | 9 | 139 | 21 | West | BRDF4
138133 | 2018-05-16 | Defective Equipment | Imminent Failure | At 5:00pm transformer 153 was isolated to allow crew to replace leaking transforme. 10 customers affected. Bridlewood (BRDF4) | None | Padmount (1ph) | 10 | 175 | 29 | West | BRDF4
138134 | 2018-05-16 | Loss Of Supply | Transmission Inadvertent | At 6:05pm SCADA indicates a loss of supply from Hawthorne 48M1 and 48M2. 13458 customers affected. Hydro One reports 48T10 transformer tripped out on gas. Hawthorne (48M2 and 48M1) | None | None | 13458 | 13 | 2916 | East | 48M2
138136 | 2018-05-17 | Scheduled Outage | Construction | Transformer #X33213 isolated by crew to change triplex for 8 Millbrook | None | None | 8 | 55 | 7 | South | 190F2
138137 | 2018-05-17 | Scheduled Outage | Construction | Transformer S27071 at 816 Champan was isolated to allow crew to transfer secondary to new spun bus. 8 customers were affected. Russell TB06 | None | None | 8 | 347 | 46 | East | TB06
138138 | 2018-05-17 | Scheduled Outage | Construction | Transformer #X29758 isolated by crew for a pole upgrade | None | None | 10 | 320 | 53 | Central | SR02
138140 | 2018-05-17 | Scheduled Outage | Construction | Transformer KT526 including Riser cable was isolated to allow crew to move switch to new pole. 7 customers were affected. Lincoln Heights (TD12) | None | None | 7 | 372 | 43 | Central | TD12
138142 | 2018-05-17 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X27228 TO INSTALL NEW POLES | None | None | 10 | 301 | 50 | East | UQ07
138143 | 2018-05-18 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X43860 opened up due to animal contact | O/H Switchgear | Fused Cutout | 12 | 95 | 19 | Central | TR3UY
138144 | 2018-05-18 | Scheduled Outage | Construction | TRNAS #X33889 isolated by crew to install new service | None | None | 5 | 44 | 4 | Central | UL14
138145 | 2018-05-18 | Scheduled Outage | Construction | 2 transformers, X58553 and X58557 isolated by crew for a pole replacement | None | None | 22 | 260 | 95 | Central | SR02
138148 | 2018-05-19 | Foreign Interference | Wildlife (Bird/Animal) | At 06:30am SCADA indicates the RX2048 tripped open. 77M6 breaker also auto reclosed. | O/H Switchgear | Recloser (3ph) | 119 | 65 | 129 | East | 77M6
138148 | 2018-05-19 | Foreign Interference | Wildlife (Bird/Animal) | At 06:30am SCADA indicates the RX2048 tripped open. 77M6 breaker also auto reclosed. | O/H Switchgear | Recloser (3ph) | 1942 | 12 | 388 | East | 77M6
138149 | 2018-05-19 | Defective Equipment | Mechanical Failure | Not yet known. | U/G Cable | XLPE | 150 | 55 | 138 | South | 180F2
138150 | 2018-05-20 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel. Placed hold off on tr09 and refused all power restored | None | None | 10 | 20 | 3 | Central | TR09
138152 | 2018-05-20 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel. Hold off on tw11 and refused all power restored | None | None | 6 | 25 | 2 | Central | TW18
138153 | 2018-05-20 | Foreign Interference | Vehicle | Neutral conductor wrapped into primary overhead. | O/H Switchgear | Recloser (1ph) | 5 | 24 | 2 | West | RHNF3
138153 | 2018-05-20 | Foreign Interference | Vehicle | Neutral conductor wrapped into primary overhead. | O/H Switchgear | Recloser (1ph) | 38 | 265 | 168 | West | RHNF3
138155 | 2018-05-21 | Foreign Interference | Wildlife (Bird/Animal) | Replaced blown fuse feeding X10786 (bird contact) | O/H Transformer | O/H Transformer (1ph) | 1 | 60 | 1 | West | JKGF4
138158 | 2018-05-22 | Scheduled Outage | Construction | SW17651 switches and arresters replaced | None | None | 218 | 42 | 153 | Central | TD06
138159 | 2018-05-22 | Scheduled Outage | Construction | S10762 switches and arresrters replaced | None | None | 108 | 68 | 122 | Central | TD06
138160 | 2018-05-22 | Defective Equipment | Defective Equipment/ Material | TV121 outage to replace damaged turtle transformer | U/G Transformer | SIDT - Submersible (Turtle) | 55 | 242 | 222 | Central | UD08
138162 | 2018-05-22 | Defective Equipment | Electrical Failure | Burnt Secondary | U/G Transformer | Kiosk (1ph) | 11 | 146 | 27 | East | UA04
138162 | 2018-05-22 | Defective Equipment | Electrical Failure | Burnt Secondary | U/G Transformer | Kiosk (1ph) | 15 | 521 | 130 | East | UA04
138162 | 2018-05-22 | Defective Equipment | Electrical Failure | Burnt Secondary | U/G Transformer | Kiosk (1ph) | 21 | 327 | 114 | East | UA04
138163 | 2018-05-23 | Scheduled Outage | Construction | 28F1 overhead at Joys road and Franktown Rd was isolated to complete connection at new overhead, affecting 80 customers. Richmond South DS (28F1) | None | None | 80 | 178 | 237 | West | 28F1
138166 | 2018-05-23 | Scheduled Outage | Construction | Pole Replacement. | None | None | 26 | 403 | 175 | East | TB06
138167 | 2018-05-23 | Foreign Interference | Foreign Objects | crews found millar ballon at 14 Newark, affecting 48 customers. Manordale DS (84F2) | None | None | 48 | 116 | 93 | South | 84F2
138168 | 2018-05-24 | Scheduled Outage | Construction | At 9:12am TP12373 was isolated to allow crew to perform soil remediation. 12 customers affected. Fallowfield (FAL02) | None | None | 12 | 454 | 91 | South | FAL02
138169 | 2018-05-24 | Scheduled Outage | Construction | At 06:30am S17158 at 1501 Innes Rd was opened to allow crew to install new services. 9 customers affected. Cyrville (CYRF4) | None | None | 9 | 127 | 19 | East | CYRF4
138173 | 2018-05-24 | Scheduled Outage | Construction | Install new pole and transfer plant. X23086 | Pole | Pole | 22 | 135 | 50 | East | AP06
138174 | 2018-05-24 | Scheduled Outage | Construction | crew isolated section of overhead on roosevelt to install new hydro pole. 90 customers were affected. Hillcrest (AH02) | None | None | 90 | 197 | 296 | Central | AH02
138175 | 2018-05-24 | Scheduled Outage | Construction | Ugrading service. Pole replacement. X33976 | None | None | 14 | 285 | 66 | Central | UV03
138177 | 2018-05-24 | Loss Of Supply | Third Party | At 5:28pm Hydro One dumped the A9M3 for safety after a dump truck got stuck in Bell wire in proximity to the overhead conductor. 1018 customers affected. South March (A9M3) | None | None | 1018 | 28 | 475 | West | A9M3
138180 | 2018-05-25 | Defective Equipment | Electrical Failure | crew isolated outside switchgear SW117 at 2 Lorry greenberg, to repair faulted switches. 26 customers were affected. Albion (2206) | U/G Switchgear | Primary Pedestal | 26 | 576 | 250 | East | 2206
138182 | 2018-05-26 | Foreign Interference | Wildlife (Bird/Animal) | Squirel contact at 1968 Neepawa caused the transformer 55C2C-0411 to open. 5 customers were affected. Lincoln Heights (TD06) | O/H Switchgear | Fused Cutout | 5 | 55 | 5 | Central | TD06
138183 | 2018-05-26 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X09910 at 45 Vanier Rd open due to squirel contact. 6 customers were affected. Stafford (200F2) | O/H Switchgear | Fused Cutout | 6 | 130 | 13 | South | 200F2
138184 | 2018-05-27 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change switches, arrestors & quicksleeves in this area | None | None | 161 | 361 | 969 | West | 44F1
138184 | 2018-05-27 | Scheduled Outage | Maintenance | To allow Hydro Ottawa crews to change switches, arrestors & quicksleeves in this area | None | None | 163 | 189 | 513 | West | 44F1
138186 | 2018-05-27 | Foreign Interference | Wildlife (Bird/Animal) | fused switch S320 at 2090 Innes Rd. was found open due to animal contact. 1 customer was affected. Blackburn DS (BLKF4) | O/H Switchgear | Fused Cutout | 1 | 62 | 1 | East | BLKF4
138187 | 2018-05-27 | Scheduled Outage | Construction | Transformer T335 isolated by crew to disc def u/g service in transformer | None | None | 9 | 12 | 2 | East | 6F10
138189 | 2018-05-27 | Scheduled Outage | Construction | 28KV transformer TP9784 at 2300 City Park was isolated for upgrade, affecting 13 customers. Moulton DS (8F4) | None | None | 13 | 320 | 69 | East | 8F4
138190 | 2018-05-27 | Defective Equipment | Electrical Failure | TM28 breaker tripped ue to pole fire at 55C4B-0118 (900 Clyde), affecting 5 customers. Carling TS | Pole | Insulation Failure (Pole Fire) | 4 | 36 | 2 | Central | TM3UC
138190 | 2018-05-27 | Defective Equipment | Electrical Failure | TM28 breaker tripped ue to pole fire at 55C4B-0118 (900 Clyde), affecting 5 customers. Carling TS | Pole | Insulation Failure (Pole Fire) | 5 | 70 | 6 | Central | TM3UC
138190 | 2018-05-27 | Defective Equipment | Electrical Failure | TM28 breaker tripped ue to pole fire at 55C4B-0118 (900 Clyde), affecting 5 customers. Carling TS | Pole | Insulation Failure (Pole Fire) | 29 | 13 | 6 | Central | TM2UC
138191 | 2018-05-28 | Defective Equipment | Electrical Failure | Defective under ground section at Don Reid & St. Laurent from SW139 to SW1593, affecting 23 customers. Albion TS (2203) | U/G Cable | PILC | 4 | 30 | 2 | East | 2203
138191 | 2018-05-28 | Defective Equipment | Electrical Failure | Defective under ground section at Don Reid & St. Laurent from SW139 to SW1593, affecting 23 customers. Albion TS (2203) | U/G Cable | PILC | 23 | 83 | 32 | East | 2203
138192 | 2018-05-28 | Scheduled Outage | Construction | Transformer X33597 was opened to allow Hydro Ottawa line crews to complete secondary work 1 span south ofthis transformer at 1645 Ortona. 9 customers were affected. Fisher DS (AK12) | None | None | 9 | 187 | 28 | Central | AK12
138193 | 2018-05-28 | Defective Equipment | Electrical Failure | Transformer #X28049 opened up due to broken switch | O/H Switchgear | Fused Cutout | 7 | 91 | 11 | East | AF05
138194 | 2018-05-28 | Scheduled Outage | Construction | A transformer at 340 Queen Mary was opened to upograde the transformer affecting 17 people. Overbrook SO03 | None | None | 17 | 105 | 30 | East | SO03
138195 | 2018-05-28 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X56457 opened up due to animal contact | O/H Switchgear | Fused Cutout | 1 | 63 | 1 | West | TFXF2
138196 | 2018-05-28 | Unknown/Other | Unknown | Refused switch S21249 feeding transformer X33270 cause of blown fuse unknown | O/H Switchgear | Fused Cutout | 1 | 201 | 3 | West | BECKF2
138197 | 2018-05-29 | Scheduled Outage | Construction | X39476 Crews dropping triplex. | None | O/H Transformer (1ph) | 4 | 30 | 2 | Central | TR09
138198 | 2018-05-29 | Foreign Interference | Wildlife (Bird/Animal) | At 10:23 the 7F4 breaker tripped under hold-off. 637 customers affected.Crew found S18742 blown and a dead Raven at the base of the pole. Limebank (7F4) | None | None | 637 | 13 | 138 | East | 7F4
138199 | 2018-05-29 | Scheduled Outage | Construction | At 09:02am TP12376 was isolated for soil remediation. 12 customers affected. Longfield (LGFF2) | None | None | 12 | 462 | 92 | South | LGFF2
138201 | 2018-05-30 | Scheduled Outage | Construction | planned outage to install new poles | None | None | 65 | 470 | 509 | East | TB06
138202 | 2018-05-30 | Scheduled Outage | Maintenance | planned outage for remediation | None | Padmount (1ph) | 18 | 480 | 144 | East | 7F1
138203 | 2018-05-31 | Scheduled Outage | Maintenance | 28kv transformers 157R & TP12519 at Liston Cres. Were isolated for repairs and oil remediation, 19 customers affected. Bridlewood MS (BRDF4) | None | None | 9 | 230 | 34 | West | BRDF4
138203 | 2018-05-31 | Scheduled Outage | Maintenance | 28kv transformers 157R & TP12519 at Liston Cres. Were isolated for repairs and oil remediation, 19 customers affected. Bridlewood MS (BRDF4) | None | None | 19 | 105 | 33 | West | BRDF4
138204 | 2018-05-31 | Tree Contacts | Tree Growth/ Untrimmed Tree | Kevin McKenna reports that dense foliage and trees growing within proximity of transformer caused outage on transformer X39532. Crew trimmed the branches back, refused the transformer and restored power. | O/H Switchgear | Fused Cutout | 4 | 96 | 6 | South | 47F3
138206 | 2018-05-31 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H1 due to bus differential trip at South March TS (A9M2, M3 & M5), affecting 3759 customers. | None | None | 5 | 4 | 0 | West | A9M5
138206 | 2018-05-31 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H1 due to bus differential trip at South March TS (A9M2, M3 & M5), affecting 3759 customers. | None | None | 1013 | 4 | 68 | West | A9M2
138206 | 2018-05-31 | Loss Of Supply | Transmission Inadvertent | Loss of supply from H1 due to bus differential trip at South March TS (A9M2, M3 & M5), affecting 3759 customers. | None | None | 2741 | 4 | 183 | West | A9M3
138208 | 2018-05-31 | Defective Equipment | Defective Equipment/ Material | Opened X33409. resagged and sleeved open wire bus to appropriate sag spacing so wire wont slap together again | O/H Transformer | O/H Transformer (1ph) | 8 | 70 | 9 | Central | TW22
138211 | 2018-05-31 | Scheduled Outage | Forced Switching | 4KV kiosk, K435 at 3310 Southgate was isolated at the fused cutout to make repairs to the secondaries, affecting 15 customers. Cahill DS (AN05) | None | None | 15 | 149 | 37 | East | AN05
138212 | 2018-05-31 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to transfer plant from old poles to new poles | None | None | 22 | 303 | 111 | West | 28F2
138213 | 2018-06-01 | Unknown/Other | Unknown | TA09 circuit breaker tripped open and did not auto reclose. Cause remains under investigation. Albion (2206) | Station Equipment | Relay | 3519 | 22 | 1290 | East | 2206
138214 | 2018-06-01 | Defective Equipment | Defective Equipment/ Material | Transformer 11384 at 7 Cone Terrace was isolated to replace elbows & inserts. 2 customers affected. Munster 43F3. Broken Insert | None | None | 2 | 77 | 3 | West | 43F3
138215 | 2018-06-01 | Defective Equipment | Electrical Failure | 77M1 suspected cable fault at TP6975, affecting | U/G Cable | XLPE | 8 | 30 | 4 | East | 77M1
138215 | 2018-06-01 | Defective Equipment | Electrical Failure | 77M1 suspected cable fault at TP6975, affecting | U/G Cable | XLPE | 8 | 106 | 14 | East | 77M1
138215 | 2018-06-01 | Defective Equipment | Electrical Failure | 77M1 suspected cable fault at TP6975, affecting | U/G Cable | XLPE | 43 | 118 | 85 | East | 77M1
138215 | 2018-06-01 | Defective Equipment | Electrical Failure | 77M1 suspected cable fault at TP6975, affecting | U/G Cable | XLPE | 70 | 104 | 121 | East | 77M1
138216 | 2018-06-01 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree on line, removed , closed in S21249 | O/H Transformer | O/H Transformer (1ph) | 1 | 42 | 1 | West | BECKF2
138218 | 2018-06-02 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X49984 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 8 | 46 | 6 | South | 200F1
138219 | 2018-06-02 | Foreign Interference | Wildlife (Bird/Animal) | TW18 circuit opened due to an animal contact on an normally open overhead switch. 1388 customers affected. Woodroffe (TW18) | Station Equipment | Primary Switchgear | 1388 | 16 | 370 | Central | TW18
138222 | 2018-06-02 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X33290 TO REPLACE TRIPLEX SERVICE | None | None | 6 | 60 | 6 | Central | UV05
138223 | 2018-06-03 | Defective Equipment | Electrical Failure | suspected cable fault | U/G Cable | EPR | 1 | 18 | 0 | Central | 510
138223 | 2018-06-03 | Defective Equipment | Electrical Failure | suspected cable fault | U/G Cable | EPR | 1467 | 37 | 905 | Central | 510
138224 | 2018-06-03 | Tree Contacts | Tree Growth/ Untrimmed Tree | REPLACED BLOWN FUSE FEEDING TRANSFORMER X38569 (TREE CONTACT) | O/H Transformer | O/H Transformer (1ph) | 5 | 87 | 7 | Central | TD06
138225 | 2018-06-03 | Defective Equipment | Mechanical Failure | REPLACED BROKEN FUSE FEEDING TRANSFORMER X39186 | O/H Switchgear | Fused Cutout | 1 | 155 | 3 | Central | SM12
138226 | 2018-06-03 | Defective Equipment | Imminent Failure | At 08:34am TE945 was isolated to allow crew to replace it due to a leak. 1 customer affected. Rideau Heights (180F1) | None | None | 1 | 451 | 8 | South | 180F1
138227 | 2018-06-03 | Foreign Interference | Wildlife (Bird/Animal) | animal contact caused transformer to open | O/H Transformer | O/H Transformer (1ph) | 8 | 100 | 13 | Central | 503
138232 | 2018-06-04 | Human Element | Switching Error | RX2009 inadvertantly opened while setting H/O. 194 customers affected. Kanata 624F6. | None | None | 0 | 2 | 0 | West | 624F6
138232 | 2018-06-04 | Human Element | Switching Error | RX2009 inadvertantly opened while setting H/O. 194 customers affected. Kanata 624F6. | None | None | 194 | 2 | 6 | West | 624F6
138232 | 2018-06-04 | Human Element | Switching Error | RX2009 inadvertantly opened while setting H/O. 194 customers affected. Kanata 624F6. | None | None | 194 | 6 | 19 | West | 624F6
138234 | 2018-06-05 | Foreign Interference | Wildlife (Bird/Animal) | suspected animal contact | O/H Conductor | O/H Conductor | 67 | 70 | 78 | South | LGFF2
138234 | 2018-06-05 | Foreign Interference | Wildlife (Bird/Animal) | suspected animal contact | O/H Conductor | O/H Conductor | 927 | 14 | 216 | South | LGFF2
138235 | 2018-06-05 | Scheduled Outage | Maintenance | 2 28KV transformers on Liston Ave. were isolated to reapir elbows and perform oil remediation, affecting 19 customers. Bridlewood MTS (BRDF4) | None | None | 10 | 182 | 30 | West | BRDF4
138235 | 2018-06-05 | Scheduled Outage | Maintenance | 2 28KV transformers on Liston Ave. were isolated to reapir elbows and perform oil remediation, affecting 19 customers. Bridlewood MTS (BRDF4) | None | None | 19 | 188 | 60 | West | BRDF4
138237 | 2018-06-05 | Scheduled Outage | Construction | UV05 OH section isolated to replace pole and transfer plant, affecting 78 customers. Edwin DS (UV05) | None | None | 78 | 132 | 172 | Central | UV05
138239 | 2018-06-05 | Scheduled Outage | Maintenance | P185 at 73 First was isolated to pump water out of the base. 1 customer affected. Bronson (SB06) | None | None | 1 | 119 | 2 | Central | SB06
138241 | 2018-06-06 | Scheduled Outage | Maintenance | Transformer Replacement TE1732. | None | None | 16 | 292 | 78 | South | EPWF4
138242 | 2018-06-06 | Scheduled Outage | Maintenance | Reparing secondary on x23847 | None | None | 6 | 30 | 3 | East | AP04
138243 | 2018-06-06 | Defective Equipment | Electrical Failure | An ampact came off of the overhead in front of Clyde DS resualting in loss of R phase load on UC01 and UC03. 234 customers affected. Clyde (UC00, UC01, UC03) | O/H Conductor | Ampact | 100 | 61 | 102 | Central | UC01
138243 | 2018-06-06 | Defective Equipment | Electrical Failure | An ampact came off of the overhead in front of Clyde DS resualting in loss of R phase load on UC01 and UC03. 234 customers affected. Clyde (UC00, UC01, UC03) | O/H Conductor | Ampact | 134 | 61 | 136 | Central | UC03
138244 | 2018-06-06 | Scheduled Outage | Maintenance | Crew reports damaged triplex needs to be replaced. Requires outage on transformer X30029. | None | None | 7 | 27 | 3 | Central | SB05
138245 | 2018-06-06 | Defective Equipment | Mechanical Failure | Crew to have transformer X30711 open to replace broken pole. Customers notified. | None | None | 14 | 180 | 42 | Central | UN04
138247 | 2018-06-07 | Scheduled Outage | Construction | Transformer #X23847 isolated by crew to install new pole | None | None | 6 | 413 | 41 | East | AP04
138251 | 2018-06-08 | Scheduled Outage | Construction | Outage due to out of phase switch . JW Leslie crew was energizing more new transformers | None | None | 30 | 15 | 8 | West | JKGF4
138252 | 2018-06-08 | Scheduled Outage | Construction | Planned switching on an out of phase loop. Energizing new transformers in the loop | None | Padmount (1ph) | 30 | 7 | 4 | West | JKGF4
138253 | 2018-06-08 | Scheduled Outage | Maintenance | Secondary maintenance for X34844. | None | None | 18 | 120 | 36 | Central | SH02
138254 | 2018-06-08 | Scheduled Outage | Maintenance | Isolated to allow contractor to replace secondary services | None | U/G Service | 40 | 216 | 144 | South | 87F1
138255 | 2018-06-08 | Loss Of Supply | Transmission Inadvertent | Loss of supply to J buss at Hawthrone. Hydro One 48T8J breaker opened. 48M1 breaker failed to open causing 48T8J breaker to trip. | None | None | 2396 | 13 | 519 | East | 48M2
138255 | 2018-06-08 | Loss Of Supply | Transmission Inadvertent | Loss of supply to J buss at Hawthrone. Hydro One 48T8J breaker opened. 48M1 breaker failed to open causing 48T8J breaker to trip. | None | None | 8045 | 12 | 1609 | East | 48M2
138256 | 2018-06-08 | Scheduled Outage | Construction | Transformer #X34394 isolated by crew to replace transformer | None | None | 12 | 95 | 19 | Central | UC03
138257 | 2018-06-08 | Defective Equipment | Electrical Failure | Cable fault caused interruption to KT531 at 878 Grenon. 8 customers affected. Linclon Heights (TD12) | U/G Cable | XLPE | 8 | 191 | 25 | Central | TD12
138259 | 2018-06-09 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused S14967 fuse to blow. | O/H Switchgear | Fused Cutout | 27 | 165 | 74 | East | TB14
138260 | 2018-06-09 | Defective Equipment | Defective Equipment/ Material | 28KV transformer loop isolated to replace leaking transformer, repair elbows and iserts and upgrade riser swaithes, affecting 29 customers. Richmond North (RHNF3). | U/G Transformer | Kiosk (1ph) | 29 | 300 | 145 | West | RHNF3
138262 | 2018-06-09 | Scheduled Outage | Construction | 28KV vault, V4592 at 10 katimavik was isolated to decommsion vault & transfer secondaries to new TP 12334, affecting 1 customer. Marchwood MTS (MWDF2) | None | None | 1 | 465 | 8 | West | MWDF2
138263 | 2018-06-09 | Foreign Interference | Vehicle | Dump truck contacted bell wire and caused pole top insulator to break, S460R opened for isolation point. | Pole Attachement | Insulator | 48 | 77 | 62 | East | 7F2
138264 | 2018-06-09 | Scheduled Outage | Maintenance | Vault maintenance and repair UL1AH-L5 | None | None | 1 | 241 | 4 | Central | TH2UL
138266 | 2018-06-10 | Foreign Interference | Wildlife (Bird/Animal) | Customer called in on the outage line. Crew discovered transformer X58491 had openned due to animal contact. Crew refused and restored. | O/H Switchgear | Fused Cutout | 6 | 102 | 10 | East | 77M6
138268 | 2018-06-10 | Foreign Interference | Wildlife (Bird/Animal) | Probable animal contact caused X48612 to open. 14 customers affected. Woodroffe TW18 | O/H Transformer | O/H Transformer (1ph) | 14 | 70 | 16 | Central | TW18
138269 | 2018-06-10 | Scheduled Outage | Maintenance | Tunneys Pasture vault supply rearrangement | None | None | 1 | 492 | 8 | Central | 4304
138270 | 2018-06-10 | Defective Equipment | Mechanical Failure | Transformer X24922 at 1010 Harkness found to be defective. X24921 also isolated to allow crew to jumper the seocndary. 13 customers affected. Walkley (UZ03) | O/H Transformer | O/H Transformer (1ph) | 4 | 384 | 26 | East | UZ03
138270 | 2018-06-10 | Defective Equipment | Mechanical Failure | Transformer X24922 at 1010 Harkness found to be defective. X24921 also isolated to allow crew to jumper the seocndary. 13 customers affected. Walkley (UZ03) | O/H Transformer | O/H Transformer (1ph) | 13 | 53 | 11 | East | UZ03
138271 | 2018-06-10 | Scheduled Outage | Construction | Transfomrers X31490 and X31491 isolated for pole replacement at 930 Gladestone. 13 customers affected. Bayswater (UJ04) | None | Pole | 13 | 425 | 92 | Central | UJ04
138272 | 2018-06-10 | Scheduled Outage | Construction | Transfomrer X31489 at 930 Gladestone was isolated for pole replacement. 1 customer affected. Bayswater (UJ04) | None | Pole | 1 | 330 | 6 | Central | UJ04
138274 | 2018-06-11 | Scheduled Outage | Construction | 84F4 overhead section on Greenbank isolated for for pole replacement project, affecting 1 customer. Manordale DS (84F4) | None | None | 1 | 435 | 7 | South | 84F4
138275 | 2018-06-11 | Tree Contacts | Other Vegetation | Transformer #X26288 opened up due to vines interference | O/H Switchgear | Fused Cutout | 6 | 248 | 25 | East | TB06
138277 | 2018-06-11 | Foreign Interference | Wildlife (Bird/Animal) | AJ05 circuit isolated to allow crew to repair copper conductor that had burnt through due to racoon contact. | O/H Conductor | O/H Conductor | 291 | 93 | 451 | East | AJ05
138278 | 2018-06-11 | Defective Equipment | Electrical Failure | 8kv pad mount transformer TP5317 at 162 Paseo was isolated to repair defective seconday to 128 Paseo, affecting 40 customers. Centre Point DS (87F1) | Secondary \ Service | U/G Service | 40 | 265 | 177 | South | 87F1
138280 | 2018-06-11 | Scheduled Outage | Construction | Transformer #X27954 isolated by crew for a service upgrade | None | None | 7 | 45 | 5 | East | UZ06
138281 | 2018-06-12 | Foreign Interference | Wildlife (Bird/Animal) | animal contact | O/H Transformer | O/H Transformer (1ph) | 8 | 58 | 8 | Central | TD05
138282 | 2018-06-12 | Unknown/Other | Unknown | Not yet known. Crew patrolled line, no apparent reason or cause, crew re-fused and closed switch | Unknown \ Other | Unknown \ Other | 136 | 129 | 292 | Central | TD12
138283 | 2018-06-12 | Scheduled Outage | Maintenance | Transformer TP3247 at 318 Quetico was isolated to allow crew to perfrom oil remeditation. Fallowfield (FAL03) | None | None | 21 | 433 | 152 | South | FAL03
138284 | 2018-06-12 | Scheduled Outage | Construction | Transformers TP8661 and TP8660 were isolated to allow crew to remove the S2 from service. 15 customers were affected. Terry Fox (TFXF1). | None | None | 15 | 214 | 54 | West | TFXF1
138285 | 2018-06-12 | Scheduled Outage | Construction | Customer at Fallowfield and Greenbank was isolated to allow crew to repalce pole on Greenbank RD. Manordale (84F4) | None | None | 1 | 490 | 8 | South | 84F4
138286 | 2018-06-12 | Scheduled Outage | Maintenance | 28KV padmount Transformer TP3247 at 318 Quetico was isolated to allow crew to perfrom oil remeditation. Fallowfield (FAL03) | None | None | 14 | 312 | 73 | West | BRDF4
138288 | 2018-06-12 | Scheduled Outage | Construction | A section of primary overhead at Claude St and Dora Cres was isolated to upgrade Hydro Plant affecting 6 customers. Church AA06 | None | None | 6 | 277 | 28 | East | AA06
138290 | 2018-06-12 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel Contact, blew transformer fuse. | O/H Switchgear | Fused Cutout | 9 | 154 | 23 | Central | 505
138291 | 2018-06-12 | Scheduled Outage | Construction | Pulling in new secondary cable. | None | O/H Transformer (1ph) | 10 | 56 | 9 | East | TB06
138293 | 2018-06-12 | Defective Equipment | Imminent Failure | crew to replace rotten crossarms | Pole | Crossarm | 362 | 204 | 1231 | East | AA04
138294 | 2018-06-13 | Defective Equipment | Electrical Failure | Possible Blue phase cable fault | U/G Cable | XLPE | 263 | 105 | 460 | East | CYRF3
138296 | 2018-06-13 | Defective Equipment | Electrical Failure | suspected cable faulkt between TR and SC4169 | U/G Cable | PILC | 1848 | 53 | 1632 | Central | TR1UN
138296 | 2018-06-13 | Defective Equipment | Electrical Failure | suspected cable faulkt between TR and SC4169 | U/G Cable | PILC | 3472 | 39 | 2257 | Central | TR1UN
138297 | 2018-06-13 | Scheduled Outage | Construction | To allow Hydro Ottawa constuction line crews set poles with a crane and change a transformer | None | None | 10 | 374 | 62 | South | 170F4
138298 | 2018-06-13 | Defective Equipment | Imminent Failure | Transformer TE1336 at 2704 Farriers Lane was isolated to allow crew to replace leaking transformer. Uplands (4801F8) | U/G Transformer | Padmount (1ph) | 18 | 392 | 118 | East | 4801F8
138299 | 2018-06-13 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact. | O/H Switchgear | Fused Cutout | 6 | 177 | 18 | Central | TH01
138301 | 2018-06-13 | Scheduled Outage | Construction | To allow Hydro Ottawa line crews to complete secondary work out of transformer X38170 | None | None | 5 | 110 | 9 | Central | 503
138303 | 2018-06-13 | Foreign Interference | Wildlife (Bird/Animal) | Switch S27515 open due to animal contact. 1 customer was affected. Limebank (LMBF5) | O/H Switchgear | Fused Cutout | 1 | 71 | 1 | East | LMBF5
138304 | 2018-06-13 | Foreign Interference | Wildlife (Bird/Animal) | S27515 opened up due to animal contact | O/H Switchgear | Inline Switch | 5 | 84 | 7 | East | LMBF5
138305 | 2018-06-13 | Human Element | Switching Error | While switching to restore 84F2 cable section between TE1688 and TP12402 the 84F2 CB A/R grounds left on at TE1688. Crew also found defective bushing at TE1381. 58 customers were affected. | U/G Transformer | Padmount (1ph) | 18 | 190 | 57 | South | 84F2
138305 | 2018-06-13 | Human Element | Switching Error | While switching to restore 84F2 cable section between TE1688 and TP12402 the 84F2 CB A/R grounds left on at TE1688. Crew also found defective bushing at TE1381. 58 customers were affected. | U/G Transformer | Padmount (1ph) | 108 | 82 | 148 | South | 84F2
138306 | 2018-06-13 | Defective Equipment | Defective Equipment/ Material | Defective transformer at 1196 Old Carp Rd caused the S24972 to open. Kanata (624F6) | O/H Transformer | O/H Transformer (1ph) | 3 | 187 | 9 | West | 624F6
138306 | 2018-06-13 | Defective Equipment | Defective Equipment/ Material | Defective transformer at 1196 Old Carp Rd caused the S24972 to open. Kanata (624F6) | O/H Transformer | O/H Transformer (1ph) | 58 | 168 | 162 | West | 624F6
138308 | 2018-06-13 | Scheduled Outage | Construction | Transformer #X24108 isolated by crew to make repairs to sec buss | None | None | 12 | 30 | 6 | East | LMBF5
138309 | 2018-06-13 | Tree Contacts | Falling Tree | outage on X35333 Repairs for fallen tree on lines | O/H Transformer | O/H Transformer (1ph) | 11 | 65 | 12 | Central | AD06
138310 | 2018-06-13 | Defective Equipment | Electrical Failure | S16390 Red and blue fuses found blown at 54 Marble Arch due to defective riser cable, affecting 150 customers. Centre Pointe DS (87F5) | U/G Cable | XLPE | 150 | 123 | 308 | South | 87F5
138312 | 2018-06-14 | Defective Equipment | Imminent Failure | Transformer K625 at 1390 Plumber was replaced due to an oil leak. 11 customer affected. Langs (AP05) | None | None | 11 | 452 | 83 | East | AP05
138313 | 2018-06-14 | Defective Equipment | Defective Equipment/ Material | To replace leaking transformer at TP2512 | None | None | 10 | 71 | 12 | West | BRDF1
138314 | 2018-06-14 | Scheduled Outage | Construction | TB14 from S17114 to EOL isolated for pole replacement. 24 customers affected. Russell (TB14) | None | Pole | 24 | 81 | 32 | East | TB14
138316 | 2018-06-14 | Scheduled Outage | Maintenance | Panned outage to install lightning arrestor. | None | O/H Transformer (1ph) | 3 | 52 | 3 | West | 624F6
138317 | 2018-06-14 | Scheduled Outage | Construction | Transformer #X43575 isolated by crew to connect a new service | None | None | 8 | 22 | 3 | Central | TR3UY
138318 | 2018-06-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X27284 TO INSTALL NEW POLE | None | None | 4 | 208 | 14 | East | UA07
138319 | 2018-06-15 | Scheduled Outage | Maintenance | Transformer TE3080 was isolated for remediation. | None | None | 11 | 420 | 77 | South | FAL02
138320 | 2018-06-15 | Scheduled Outage | Maintenance | Transformer 11383 at 7 Cone Terrace isolated to replace elbows & inserts. 3 customers affected. Munster 43F3. | None | Padmount (1ph) | 3 | 64 | 3 | West | 43F3
138321 | 2018-06-15 | Scheduled Outage | Construction | S18502 at 7555 Soldiers Line opened to install new guy wires. 1 customer affected. Munster 43F3. | None | None | 1 | 65 | 1 | West | 43F3
138322 | 2018-06-15 | Scheduled Outage | Construction | TP3504 at 2140 Walkley isolated to transfer overhead switch to new pole. 1 customer affected. Urbandale (AE04) | None | Fused Cutout | 1 | 257 | 4 | East | AE04
138323 | 2018-06-15 | Scheduled Outage | Construction | Temp 196 to EOL was isoalted to allow crew to install a pole | None | None | 1 | 32 | 1 | West | RHNF1
138331 | 2018-06-18 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X33575 open due squirel contact. | O/H Switchgear | Fused Cutout | 18 | 30 | 9 | Central | TR3UY
138332 | 2018-06-18 | Lightning | Lightning | lightning storm in area at time of the trip | Unknown \ Other | Unknown \ Other | 999 | 7 | 117 | East | LTM02
138336 | 2018-06-18 | Scheduled Outage | Construction | Planned outage for switching on an out of phase condition | U/G Transformer | Kiosk (1ph) | 15 | 8 | 2 | West | JKGF4
138337 | 2018-06-18 | Unknown/Other | Unknown | Replaced blown fuse on transformer x29995. Cause unknown. | O/H Transformer | O/H Transformer (1ph) | 4 | 64 | 4 | Central | TR09
138338 | 2018-06-18 | Defective Equipment | Mechanical Failure | Floating insulator | Pole Attachement | Insulator | 301 | 58 | 291 | East | UA06
138339 | 2018-06-18 | Scheduled Outage | Construction | Transformer #X33997 isolated by crew to string in new secondary services | None | None | 10 | 315 | 52 | Central | UV05
138340 | 2018-06-18 | Defective Equipment | Electrical Failure | S26669 opened due to cable fault at 6400 Jeanne D'Arc. 192 custmers affected. Bilberry (77M1) | U/G Cable | XLPE | 122 | 59 | 120 | East | 77M1
138340 | 2018-06-18 | Defective Equipment | Electrical Failure | S26669 opened due to cable fault at 6400 Jeanne D'Arc. 192 custmers affected. Bilberry (77M1) | U/G Cable | XLPE | 192 | 136 | 435 | East | 77M1
138341 | 2018-06-18 | Foreign Interference | Foreign Objects | A piece of plastic construction debris contacted the overhead at 2221 Gladwin causing TB17 and AL02 breakers to open. 592 customers affected. Russel, Bantree (TB1AL, AL02) | O/H Conductor | O/H Conductor | 227 | 65 | 246 | East | AL02
138341 | 2018-06-18 | Foreign Interference | Foreign Objects | A piece of plastic construction debris contacted the overhead at 2221 Gladwin causing TB17 and AL02 breakers to open. 592 customers affected. Russel, Bantree (TB1AL, AL02) | O/H Conductor | O/H Conductor | 365 | 65 | 395 | East | TB1AL
138344 | 2018-06-19 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact blew transformer fuse. | O/H Transformer | O/H Transformer (1ph) | 6 | 122 | 12 | Central | TD12
138345 | 2018-06-19 | Defective Equipment | Imminent Failure | A 4Kv transformer K53 at 150 Pidgeon was isolated to allow the crews to replace broken primary insulators and remove asbestos boards affecting 6 customers for 108 minutes on the AQ04 circuit | None | Padmount (1ph) | 6 | 108 | 11 | East | AQ04
138346 | 2018-06-19 | Scheduled Outage | Maintenance | transformer at 35 castl glen was isolated to replace badly rusted transformer, 10 customers were affected. Terry fox (TFXF1) | None | None | 10 | 69 | 12 | West | TFXF1
138347 | 2018-06-19 | Scheduled Outage | Construction | Removing and installing new pole. | None | None | 32 | 74 | 39 | Central | TH01
138348 | 2018-06-19 | Scheduled Outage | Maintenance | A 27Kv transformer TE2830 at 2939 Millstream was isolated by the crew to allow them to put the transformer back onto its base affecting 6 customers for 24 minutes on the 4801F8 circuit. | U/G Transformer | Kiosk (1ph) | 6 | 24 | 2 | East | 4801F8
138350 | 2018-06-19 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X32710 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 13 | 75 | 16 | Central | UV03
138351 | 2018-06-19 | Defective Equipment | Imminent Failure | Transformer at 2636 Equus was was isolated to allow crew to replace leaking transformer. 10 customers were affected. Uplands (4801F8) | None | None | 10 | 262 | 44 | East | 4801F8
138352 | 2018-06-20 | Unknown/Other | Unknown | Not yet known. | None | None | 3152 | 21 | 1103 | East | TB2JP
138354 | 2018-06-20 | Scheduled Outage | Construction | Transferring plant to new pole. | None | None | 8 | 20 | 3 | South | 170F1
138356 | 2018-06-20 | Scheduled Outage | Maintenance | crew isolated six transformers on Majestic dr, to trasfer the feed to another phase for future work. 6 customers were affected. Woodroffe (170F1) | None | None | 6 | 15 | 2 | South | 170F1
138357 | 2018-06-20 | Scheduled Outage | Maintenance | crew isolated verhead section on Pritchard dr., to transfer the feed to another phase for future work. 20 customers were affected. Woodroffe (170F1) | None | None | 20 | 5 | 2 | South | 170F1
138358 | 2018-06-20 | Unknown/Other | Unknown | Transformer #X27206 opened up, no apparent cause found | O/H Switchgear | Fused Cutout | 6 | 171 | 17 | East | UQ07
138359 | 2018-06-20 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X29926 opened up due to animal contact | O/H Switchgear | Fused Cutout | 6 | 79 | 8 | Central | SR09
138360 | 2018-06-20 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X29993 opened up due to animal contact | O/H Switchgear | Fused Cutout | 5 | 91 | 8 | Central | TR09
138362 | 2018-06-21 | Scheduled Outage | Maintenance | Transformer TP4952 at 535 Sandgate was isolated to allow crew to perfrom soil remediation. Falllowfield (FAL03) | None | None | 9 | 463 | 69 | South | FAL03
138363 | 2018-06-21 | Scheduled Outage | Construction | Transformer TP10077 was isolated to allow crew to install new poles on Innes at 417 HWY. Cyrville (CYRF4) | None | None | 1 | 213 | 4 | East | CYRF4
138364 | 2018-06-21 | Scheduled Outage | Construction | SC4528 including the W and B phase transformers between S1-2 were isolated to allow crew to re-arrange cables and remove SC4528. Janet King (JKGF4). 112 customers were affected. | None | None | 112 | 238 | 444 | West | JKGF4
138365 | 2018-06-21 | Defective Equipment | Defective Equipment/ Material | Replaced blown fuse feeding transformer x27206 (Secodary service made contact with primary drop lead from switch to transformer) | Secondary \ Service | O/H Service | 6 | 164 | 16 | East | UQ07
138366 | 2018-06-21 | Scheduled Outage | Construction | planned outage to re-configure the overhead circuits and replace damaged poles | None | None | 332 | 325 | 1798 | Central | SH04
138368 | 2018-06-22 | Defective Equipment | Imminent Failure | Transformer TP7664 at 1420 Forest Valley was isolated for replacement due to an oil leak. 10 customers affected. Bilberry (77M5) | None | Padmount (1ph) | 10 | 167 | 28 | East | 77M5
138372 | 2018-06-22 | Defective Equipment | Electrical Failure | A blown pothead at Gladstone and Tyndale caused the station breaker to trip causing an outage to Civic Hospital Heart institute. Hinchey TH2SH | U/G Cable Attachement | Pothead | 1 | 233 | 4 | Central | TH2SH
138374 | 2018-06-23 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X49309 opened up due to animal contact | O/H Switchgear | Fused Cutout | 8 | 66 | 9 | South | 200F1
138375 | 2018-06-23 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X31915 opened up due to animal contact | O/H Switchgear | Fused Cutout | 5 | 120 | 10 | Central | 503
138377 | 2018-06-23 | Unknown/Other | Unknown | Transformer #Ott22275 opened up, cause unknown | O/H Switchgear | Fused Cutout | 10 | 151 | 25 | East | 77M6
138378 | 2018-06-23 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact caused overhead transformer at 505 Mansfield to open. 9 customers affected. Lincoln (TD01) | O/H Transformer | O/H Transformer (1ph) | 9 | 114 | 17 | Central | TD01
138379 | 2018-06-23 | Foreign Interference | Wildlife (Bird/Animal) | At 11:03pm the fuse feeding transformer X32848 blew causing an outage to 8 customers due to racoons. Lincoln Heights (TD05) | O/H Transformer | O/H Transformer (1ph) | 8 | 55 | 7 | Central | TD05
138381 | 2018-06-24 | Unknown/Other | Unknown | At 6:18am SCADA indicated an auto-reclose on the 8F1 and the RX2017 reclosed and locked out. The RX2017 was closed from SCADA restoring power. Moulton (8F1) | None | None | 2072 | 11 | 380 | East | 8F1
138381 | 2018-06-24 | Unknown/Other | Unknown | At 6:18am SCADA indicated an auto-reclose on the 8F1 and the RX2017 reclosed and locked out. The RX2017 was closed from SCADA restoring power. Moulton (8F1) | None | None | 2222 | 2 | 74 | East | 8F1
138382 | 2018-06-24 | Scheduled Outage | Construction | Transformer 409 RWB including 408W on Hazeldeen rd were isolated to replace leaking transformer. 12 customers were affected. Bridlewood (BRDF3) | None | None | 12 | 213 | 43 | West | BRDF3
138383 | 2018-06-24 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X23911 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 21 | 115 | 40 | East | 77M6
138384 | 2018-06-24 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35137 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 12 | 79 | 16 | South | 190F5
138385 | 2018-06-24 | Foreign Interference | Wildlife (Bird/Animal) | animal contact caused overhead transformer at 9 starwood to open. 4 customers were affected. Epworth (EPWF1) | O/H Transformer | O/H Transformer (1ph) | 4 | 58 | 4 | South | EPWF1
138386 | 2018-06-25 | Foreign Interference | Wildlife (Bird/Animal) | LGF2 breaker opened under hold off protection, cause unknown. Line to be patrolled. 927 customers affected. Longfields (LGFF2). Line patrolled muliple times, nothing found, crews also did some tree trimming just to make sure that it wasn't being caused | None | None | 927 | 11 | 170 | South | LGFF2
138388 | 2018-06-25 | Defective Equipment | Imminent Failure | To replace leaking transformer TE3027 | None | None | 1 | 527 | 9 | East | 4801F8
138389 | 2018-06-25 | Scheduled Outage | Construction | Planned outage to replace KT29 transformer. ELW07. 12 Customers. | None | Kiosk (1ph) | 12 | 114 | 23 | East | ELW07
138390 | 2018-06-25 | Scheduled Outage | Construction | A transformer at 190 Richmond Rd was isolated to pull in a new secondary cable affecting 1 customer. Carling UL1AH | None | None | 1 | 335 | 6 | Central | UL1AH
138391 | 2018-06-26 | Foreign Interference | Wildlife (Bird/Animal) | Not yet known. Line patrolled muliple times, nothing found, crews also did some tree trimming just to make sure that it wasn't being caused by tree branches. | Unknown \ Other | Unknown \ Other | 927 | 6 | 93 | South | LGFF2
138392 | 2018-06-26 | Defective Equipment | Electrical Failure | 4kV padmount transformer at 2970 Fairlea cres. Secondary isolation to replace defective pedestal, affecting 21 customers. Albion (UA04) | Secondary \ Service | Secondary Pedestal | 21 | 279 | 98 | East | UA04
138393 | 2018-06-26 | Foreign Interference | Vehicle | MVC at Smyth and Freedom PVT damage two poles and wires own, Queens DS (UQ7) | Pole | Pole | 24 | 303 | 121 | East | UQ07
138393 | 2018-06-26 | Foreign Interference | Vehicle | MVC at Smyth and Freedom PVT damage two poles and wires own, Queens DS (UQ7) | Pole | Pole | 380 | 209 | 1324 | East | UQ07
138394 | 2018-06-26 | Defective Equipment | Imminent Failure | Replace leaking transformer and soil remediation | None | None | 8 | 437 | 58 | South | FAL03
138397 | 2018-06-26 | Scheduled Outage | Construction | Planned outage on x28275 for crew to install recorder on secondary | None | None | 14 | 35 | 8 | Central | AH14
138398 | 2018-06-26 | Human Element | Improper Equipment/Tool/ Maintenance | Tree trimmer dropped limb on conductor causing breaker to open under holdoff | O/H Conductor | O/H Conductor | 660 | 32 | 352 | South | EPWF1
138399 | 2018-06-26 | Scheduled Outage | Maintenance | Planned outage on X24973, to install new insulators. | None | O/H Transformer (1ph) | 5 | 18 | 2 | East | AA04
138400 | 2018-06-27 | Scheduled Outage | Maintenance | 27kv padmount transformer at 46 Golders Green was isolated for oil remediation, affecting 11 customers. Limebank DS (LMBF7) | None | None | 11 | 450 | 82 | East | LMBF7
138401 | 2018-06-27 | Defective Equipment | Imminent Failure | 28kv padmount transformer at 3123 Quail Dr was isolated and replaced due to oil leak, also included an outage to transforemr at 3153 Quail to allow for clearance to operate elbows safely. affecting 30 customers in total then down to 14 customers. | None | Padmount (1ph) | 14 | 482 | 112 | East | 4801F8
138401 | 2018-06-27 | Defective Equipment | Imminent Failure | 28kv padmount transformer at 3123 Quail Dr was isolated and replaced due to oil leak, also included an outage to transforemr at 3153 Quail to allow for clearance to operate elbows safely. affecting 30 customers in total then down to 14 customers. | None | Padmount (1ph) | 30 | 5 | 2 | East | 4801F8
138401 | 2018-06-27 | Defective Equipment | Imminent Failure | 28kv padmount transformer at 3123 Quail Dr was isolated and replaced due to oil leak, also included an outage to transforemr at 3153 Quail to allow for clearance to operate elbows safely. affecting 30 customers in total then down to 14 customers. | None | Padmount (1ph) | 30 | 10 | 5 | East | 4801F8
138403 | 2018-06-27 | Scheduled Outage | Maintenance | KT39 at 16 Fireside was isolated to remove insulation board. 1 customers affected. Ellwood ELW07. | None | None | 13 | 81 | 18 | East | ELW07
138406 | 2018-06-27 | Scheduled Outage | Construction | S936 opened to transfer plant to new pole line. 37 customers affected. Woodroffe 170F1. | None | None | 37 | 55 | 34 | South | 170F1
138407 | 2018-06-27 | Foreign Interference | Wildlife (Bird/Animal) | S18919 at 2287 Iris found blown due to animal conact at overhead transformer, affecting 21 customers. Woodroffe TS (TW17) | O/H Transformer | O/H Transformer (1ph) | 21 | 115 | 40 | Central | TW17
138408 | 2018-06-27 | Scheduled Outage | Maintenance | TRANSFERRING CUST FROM X58931 TO NEW BUS | None | None | 16 | 360 | 96 | Central | UV07
138409 | 2018-06-27 | Scheduled Outage | Construction | Reroute of white and blue cable sections with the removal of SC4528 | None | None | 187 | 172 | 536 | West | TFXF1
138410 | 2018-06-27 | Defective Equipment | Electrical Failure | Lead burnt off and bushing cracked at 3 phase overhead transformer. | O/H Transformer | O/H Transformer (3ph) | 7 | 338 | 39 | East | 6F1
138412 | 2018-06-28 | Unknown/Other | Unknown | The TFXF2 trip the circuit was sectionalize and was patrol in the area where the Fci indicated where the fault was and nothing was found affecting 847 customers. | O/H Conductor | Unknown \ Other | 389 | 28 | 182 | West | TFXF2
138412 | 2018-06-28 | Unknown/Other | Unknown | The TFXF2 trip the circuit was sectionalize and was patrol in the area where the Fci indicated where the fault was and nothing was found affecting 847 customers. | O/H Conductor | Unknown \ Other | 392 | 8 | 52 | West | TFXF2
138412 | 2018-06-28 | Unknown/Other | Unknown | The TFXF2 trip the circuit was sectionalize and was patrol in the area where the Fci indicated where the fault was and nothing was found affecting 847 customers. | O/H Conductor | Unknown \ Other | 804 | 10 | 134 | West | TFXF2
138412 | 2018-06-28 | Unknown/Other | Unknown | The TFXF2 trip the circuit was sectionalize and was patrol in the area where the Fci indicated where the fault was and nothing was found affecting 847 customers. | O/H Conductor | Unknown \ Other | 847 | 11 | 155 | West | TFXF2
138414 | 2018-06-28 | Scheduled Outage | Maintenance | Planned outage by Mike Irven to perform service upgrade. | None | None | 4 | 114 | 8 | Central | TR09
138415 | 2018-06-28 | Defective Equipment | Imminent Failure | underground transformer at 3103 Timbermill was isolated to allow crew ro change leaking transformer. 8 customers were affected. Uplands (4801F8) | None | None | 8 | 195 | 26 | East | 4801F8
138416 | 2018-06-28 | Scheduled Outage | Construction | The O/H at 9 HARWICK CRES was isolated to allow the crew to install new poles and hardware affecting 1 customer for 298 minutes on the 47F3 circuit | None | None | 1 | 298 | 5 | South | 47F3
138417 | 2018-06-28 | Defective Equipment | Electrical Failure | The 77M1 and 77M6 circuits tripped due to the RX2043 recloser blowing up on the 77M6 and S17817 blue phase blade missing on the 77M1. Crews isolated the RX2043, restoring most power, and later found the blue phase missing load from S17817. The 77M2 brea | O/H Switchgear | Recloser (3ph) | 119 | 285 | 565 | East | 77M6
138417 | 2018-06-28 | Defective Equipment | Electrical Failure | The 77M1 and 77M6 circuits tripped due to the RX2043 recloser blowing up on the 77M6 and S17817 blue phase blade missing on the 77M1. Crews isolated the RX2043, restoring most power, and later found the blue phase missing load from S17817. The 77M2 brea | O/H Switchgear | Recloser (3ph) | 462 | 213 | 1640 | East | 77M1
138417 | 2018-06-28 | Defective Equipment | Electrical Failure | The 77M1 and 77M6 circuits tripped due to the RX2043 recloser blowing up on the 77M6 and S17817 blue phase blade missing on the 77M1. Crews isolated the RX2043, restoring most power, and later found the blue phase missing load from S17817. The 77M2 brea | O/H Switchgear | Recloser (3ph) | 1822 | 17 | 516 | East | 77M1
138417 | 2018-06-28 | Defective Equipment | Electrical Failure | The 77M1 and 77M6 circuits tripped due to the RX2043 recloser blowing up on the 77M6 and S17817 blue phase blade missing on the 77M1. Crews isolated the RX2043, restoring most power, and later found the blue phase missing load from S17817. The 77M2 brea | O/H Switchgear | Recloser (3ph) | 2174 | 39 | 1413 | East | 77M6
138417 | 2018-06-28 | Defective Equipment | Electrical Failure | The 77M1 and 77M6 circuits tripped due to the RX2043 recloser blowing up on the 77M6 and S17817 blue phase blade missing on the 77M1. Crews isolated the RX2043, restoring most power, and later found the blue phase missing load from S17817. The 77M2 brea | O/H Switchgear | Recloser (3ph) | 2454 | 126 | 5153 | East | 77M6
138417 | 2018-06-28 | Defective Equipment | Electrical Failure | The 77M1 and 77M6 circuits tripped due to the RX2043 recloser blowing up on the 77M6 and S17817 blue phase blade missing on the 77M1. Crews isolated the RX2043, restoring most power, and later found the blue phase missing load from S17817. The 77M2 brea | O/H Switchgear | Recloser (3ph) | 3097 | 17 | 877 | East | 77M6
138417 | 2018-06-28 | Defective Equipment | Electrical Failure | The 77M1 and 77M6 circuits tripped due to the RX2043 recloser blowing up on the 77M6 and S17817 blue phase blade missing on the 77M1. Crews isolated the RX2043, restoring most power, and later found the blue phase missing load from S17817. The 77M2 brea | O/H Switchgear | Recloser (3ph) | 5465 | 14 | 1275 | East | 77M1
138418 | 2018-06-29 | Defective Equipment | Electrical Failure | S11410 B phase switch blew due to suspected cable fault between TP10858 and TP10859 on Saxony Cres. 30 customers affected. | U/G Cable | XLPE | 30 | 86 | 43 | East | 8F3
138419 | 2018-06-29 | Foreign Interference | Wildlife (Bird/Animal) | LGFF2 CB opened under hold off protection. Closed via SCADA and held. To be patrolled. 927 customers affected. Longfields (LGFF2), Circuit to be patrolled. FC2273 indicated Fault indication, which is located on the 44kv. Line patrolled muliple times, | None | None | 927 | 4 | 62 | South | LGFF2
138420 | 2018-06-29 | Scheduled Outage | Construction | Scott Barkley to have transformer X47529 open to replace. Customers notified. | None | None | 16 | 121 | 32 | Central | TW18
138421 | 2018-06-29 | Human Element | Protection Setting | After breaking parrellal while isolating switch S17817 a R & W phase at G242 blew due to loading.Billberry Creek (77M2) | O/H Switchgear | Inline Switch | 1544 | 86 | 2213 | East | 77M2
138421 | 2018-06-29 | Human Element | Protection Setting | After breaking parrellal while isolating switch S17817 a R & W phase at G242 blew due to loading.Billberry Creek (77M2) | O/H Switchgear | Inline Switch | 3733 | 35 | 2178 | East | 77M2
138422 | 2018-06-30 | Foreign Interference | Wildlife (Bird/Animal) | 13KV overhead transformer (x33471) at 2543 Hopkins was interupted due to animal contact, affecting 8 customers. Lincoln Heights (TD05) | O/H Transformer | O/H Transformer (1ph) | 8 | 130 | 17 | Central | TD05
138423 | 2018-06-30 | Unknown/Other | Unknown | A station breaker tripped, no apparent cause found affecting 664 customers. Elwood ELW12 | Unknown \ Other | Unknown \ Other | 664 | 9 | 100 | East | ELW12
138424 | 2018-06-30 | Tree Contacts | Tree Growth/ Untrimmed Tree | replaced blown fuse feeding transformer 1562-25 (tree contact) | O/H Transformer | O/H Transformer (1ph) | 2 | 80 | 3 | East | 56F1
138432 | 2018-06-30 | Lightning | Lightning | S18318 WB found blown with damage at TP5168 7 TP5169, suspect due to lightning, affecting 39 customers. Fallowfield DS (FAL02) | U/G Transformer | Padmount (1ph) | 39 | 492 | 320 | South | FAL02
138434 | 2018-06-30 | Lightning | Lightning | Transformer TP3243 at 228 Wabiska blew due to lighthning strike. FAL03 | U/G Transformer | Padmount (1ph) | 10 | 530 | 88 | South | FAL03
138435 | 2018-06-30 | Lightning | Lightning | Transformer X47457 at 4495 McKenna Casey blew due to lightning strike. 1 customer was affected. Fallowfield (FAL03) | O/H Transformer | O/H Transformer (1ph) | 1 | 1325 | 22 | South | FAL03
138436 | 2018-07-01 | Defective Equipment | Electrical Failure | A suspected cable fault between 180 Cooper and 20 Driveway caused the station breaker to trip affecting 202 customers. The power was restored in stages. Slater 626 (TS76) | U/G Cable | PILC | 3 | 16 | 1 | Central | 626
138436 | 2018-07-01 | Defective Equipment | Electrical Failure | A suspected cable fault between 180 Cooper and 20 Driveway caused the station breaker to trip affecting 202 customers. The power was restored in stages. Slater 626 (TS76) | U/G Cable | PILC | 202 | 135 | 454 | Central | 626
138437 | 2018-07-01 | Defective Equipment | Mechanical Failure | A live front transformer cable connection between transformer switches and the transformer faulted causing the fused switch to open at 854 Rob Roy affecting 12 customers. Lincoln Heights TD05 | U/G Cable | XLPE | 12 | 354 | 71 | Central | TD05
138439 | 2018-07-01 | Defective Equipment | Defective Equipment/ Material | Transfomer TE654 blew due to defective equipment. 10 customers were affected. Uplands 4801F8 | U/G Transformer | Padmount (1ph) | 10 | 380 | 63 | East | 4801F8
138440 | 2018-07-01 | Defective Equipment | Electrical Failure | TE1273 defective and replaced by on-call | U/G Transformer | Padmount (1ph) | 9 | 247 | 37 | East | 8F1
138441 | 2018-07-02 | Foreign Interference | Vehicle | 180F4 overhead section between S483, S23559 and TEMP100 was isolated at 2176 Prince Of Whales to allow crew to replace pole damaged by MVA. 2 customers were affected. Rideau Heights (180F4) | Pole | Pole | 2 | 314 | 10 | South | 180F4
138443 | 2018-07-02 | Tree Contacts | Falling Tree | During the lightning storm the 190F6 Tripped with W and B phase flagged. 529 customers | O/H Conductor | O/H Conductor | 29 | 65 | 31 | South | 190F6
138443 | 2018-07-02 | Tree Contacts | Falling Tree | During the lightning storm the 190F6 Tripped with W and B phase flagged. 529 customers | O/H Conductor | O/H Conductor | 516 | 6 | 52 | South | 190F6
138443 | 2018-07-02 | Tree Contacts | Falling Tree | During the lightning storm the 190F6 Tripped with W and B phase flagged. 529 customers | O/H Conductor | O/H Conductor | 529 | 111 | 979 | South | 190F6
138445 | 2018-07-02 | Adverse Weather | Extreme Wind | Thunder storm with high winds caused the two circuits to slap together and two phases of the one circuit to wrap together causing both station breakers to trip affecting 759 customers. Power was restored in stages. Riverdale SR07 and SR08 | None | None | 321 | 134 | 717 | Central | SR07
138445 | 2018-07-02 | Adverse Weather | Extreme Wind | Thunder storm with high winds caused the two circuits to slap together and two phases of the one circuit to wrap together causing both station breakers to trip affecting 759 customers. Power was restored in stages. Riverdale SR07 and SR08 | None | None | 438 | 59 | 431 | Central | SR08
138447 | 2018-07-02 | Lightning | Lightning | During the lightning storm the AA04 CB tripped. Circuit to be patrolled. 618 customers were affected for 16 min in the De Leglise St and Guy St area Chruch (AA04) | Station Equipment | Relay | 618 | 16 | 165 | East | AA04
138449 | 2018-07-02 | Tree Contacts | Broken Branch | Tree bach on the O/H line at 4660 Farmers Way cause the GR6 B phase to open. 252 customers were affected. Leitrim 249F2 | O/H Switchgear | Recloser (1ph) | 257 | 83 | 356 | East | LTM02
138450 | 2018-07-02 | Lightning | Lightning | A lightning storm caused the SB16 breaker and the SBK2Y2 breaker (carrying SB05) to open at the same time. | Unknown \ Other | Unknown \ Other | 415 | 115 | 795 | Central | SB16
138450 | 2018-07-02 | Lightning | Lightning | A lightning storm caused the SB16 breaker and the SBK2Y2 breaker (carrying SB05) to open at the same time. | Unknown \ Other | Unknown \ Other | 745 | 116 | 1440 | Central | SB00
138451 | 2018-07-02 | Defective Equipment | Electrical Failure | Marty Link reports transformer X33647 openned due to a broken porcelin switch. Switch replaced and power restored. 10 customers. | O/H Switchgear | Fused Cutout | 10 | 146 | 24 | Central | UL03
138453 | 2018-07-02 | Tree Contacts | Broken Branch | Tree on the O/H at 1610 Sixth Line caused the WX2015 RWB to open. 37 customers were affected for 297 minutes on the Kanata (624F6) | O/H Switchgear | Fused Cutout | 37 | 297 | 183 | West | 624F6
138454 | 2018-07-02 | Lightning | Lightning | S15728 at 5410 Limebank open during the lightning storm. Crew patrolled circuit and did not find anything. Limebank (7F4) | O/H Switchgear | Fused Cutout | 28 | 195 | 91 | East | 7F4
138456 | 2018-07-03 | Defective Equipment | Defective Equipment/ Material | A 13Kv defective switch S26221 at 831 High St that feeds KT527 caused the outage affecting 17 customers for 122 minutes on the TD12 circuit | O/H Switchgear | Fused Cutout | 17 | 122 | 35 | Central | TD12
138457 | 2018-07-03 | Scheduled Outage | Construction | planned outage to replace transformer | O/H Transformer | O/H Transformer (1ph) | 9 | 86 | 13 | West | BRDF4
138458 | 2018-07-03 | Foreign Interference | Vehicle | Opened transformer bank to disconnect 347/600v commercial service for electrician to make repairs on standpipe | Secondary \ Service | O/H Service | 5 | 60 | 5 | East | AL07
138459 | 2018-07-03 | Defective Equipment | Imminent Failure | Transformer overheating and leaking. Had to be replaced. | U/G Transformer | Padmount (1ph) | 21 | 150 | 52 | Central | SR03
138461 | 2018-07-03 | Defective Equipment | Electrical Failure | At 11:01pm the Fallowfield FAL01 breaker auto-reclosed causing all of Trail road to trip. S28089 white phase and S14389 white and blue phase fuses were found blown. TP6875 was found smoking. Crews found TP6875 defective. Fallowfield (FAL01) | U/G Transformer | Padmount (3ph) | 3 | 3105 | 155 | South | FAL01
138463 | 2018-07-04 | Foreign Interference | Wildlife (Bird/Animal) | bird contact | None | None | 43 | 187 | 134 | East | LTM02
138464 | 2018-07-04 | Scheduled Outage | Maintenance | Adam Donaldson and crew to have transformer X35492 open to remove damaged customer service. 4 customers. | None | None | 4 | 37 | 2 | Central | UC07
138465 | 2018-07-04 | Unknown/Other | Unknown | A fused switch at 12 Marielle opened causing Affecting 95 customers. No apparent cause was found. Lincoln Heights TD12 | Unknown \ Other | Unknown \ Other | 95 | 51 | 81 | Central | TD12
138466 | 2018-07-05 | Defective Equipment | Imminent Failure | Transformer TP3703 at 778 Bowcrest was isolated to allow crew to replace leaking transformer. 8 customers were affected. Limebank (LMBF7) | U/G Transformer | Padmount (1ph) | 8 | 180 | 24 | East | LMBF7
138467 | 2018-07-05 | Unknown/Other | Unknown | Switch S26624 at 3700 Prince of Whales open. Crew patrolled O/H line and did not find anything. 1 customer was affected. Limebank (LMBF7) | O/H Switchgear | Fused Cutout | 1 | 30 | 0 | East | LMBF7
138468 | 2018-07-05 | Defective Equipment | Defective Equipment/ Material | Transformer #X36590 opened up due to defective transformer that had to be replaced | O/H Switchgear | Fused Cutout | 21 | 564 | 197 | South | EPWF3
138469 | 2018-07-06 | Scheduled Outage | Construction | Transformer P259 at 361 Cambridge was isolated to alow crew to upgrade to new TP12635 and replace pole switches. Cambridge (AM02). | None | None | 1 | 168 | 3 | Central | AM02
138470 | 2018-07-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | The TB17 tripped due Wire coming in contact and branches making contact with the O/H on the AL02 wich is fed from the TB1AL circuit. Russell (TB17) | Station Equipment | Relay | 227 | 31 | 117 | East | TB1AL
138470 | 2018-07-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | The TB17 tripped due Wire coming in contact and branches making contact with the O/H on the AL02 wich is fed from the TB1AL circuit. Russell (TB17) | Station Equipment | Relay | 243 | 1 | 4 | East | TB1AL
138470 | 2018-07-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | The TB17 tripped due Wire coming in contact and branches making contact with the O/H on the AL02 wich is fed from the TB1AL circuit. Russell (TB17) | Station Equipment | Relay | 350 | 10 | 58 | East | TB1AL
138470 | 2018-07-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | The TB17 tripped due Wire coming in contact and branches making contact with the O/H on the AL02 wich is fed from the TB1AL circuit. Russell (TB17) | Station Equipment | Relay | 365 | 18 | 110 | East | TB1AL
138471 | 2018-07-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree brach contact on the O/H caused the TB1AL & TB3LE to trip open. 2564 customers were affected. Russell (TB1AL / TB3LE) | O/H Conductor | O/H Conductor | 365 | 4 | 24 | East | TB1AL
138471 | 2018-07-06 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree brach contact on the O/H caused the TB1AL & TB3LE to trip open. 2564 customers were affected. Russell (TB1AL / TB3LE) | O/H Conductor | O/H Conductor | 2208 | 5 | 184 | East | TB3LE
138472 | 2018-06-28 | Human Element | Protection Setting | Blown fuse on 77M2 G242 while restoring 77M1 & 77M6 from RX2043 recloser failure. Fuse was found to be undersized at 100A | None | None | 1894 | 3 | 95 | East | 77M2
138473 | 2018-07-06 | Foreign Interference | Wildlife (Bird/Animal) | LGFF2 breaker tripped, cause unknown, affecting 3581 customers. Longfields DS. Crews found SE26 flashed due to chipmunks inside gear Circuit was patrolled and several dead squirels found in SE26. Switch was isolated, cleaned up and is now back in serv | U/G Switchgear | Live-Front | 3581 | 18 | 1074 | South | LGFF2
138474 | 2018-07-06 | Scheduled Outage | Maintenance | 28KV padmount transformer secondary bus isolated to repair damaged secondary pedastal, affecting 11 customers. Moulton DS (8F1) | None | None | 11 | 152 | 28 | East | 8F1
138475 | 2018-07-06 | Tree Contacts | Other Vegetation | Vines growing into dip switch 232 burnt off lead and damaged arresters | U/G Cable Attachement | Termination \ Stress Cone | 837 | 133 | 1855 | West | 624F4
138475 | 2018-07-06 | Tree Contacts | Other Vegetation | Vines growing into dip switch 232 burnt off lead and damaged arresters | U/G Cable Attachement | Termination \ Stress Cone | 1487 | 11 | 273 | West | 624F4
138477 | 2018-07-06 | Loss Of Supply | Third Party | Vault V316 was isolated due to defective primary cable on customer side. 1 customer was affected (SO11) | None | None | 1 | 526 | 9 | East | SO11
138478 | 2018-07-06 | Scheduled Outage | Construction | 28KV padmount transformer at 66 Stonepath was isolated and relocate transformer and base, affecting 15 customers. Janet King DS (JKGF4) | U/G Transformer | Padmount (1ph) | 15 | 398 | 100 | West | JKGF4
138479 | 2018-07-06 | Scheduled Outage | Construction | 27KV switchgear at 73 Leikin was isolated and replaced, affecting 2 customers. Longfields (LGFF2) | None | Live-Front | 2 | 204 | 7 | South | LGFF2
138480 | 2018-07-06 | Defective Equipment | Defective Equipment/ Material | defective Red and Blue phase switches at S10247 and Red phase tap brunt of at Holland and Scott | O/H Switchgear | Inline Switch | 524 | 155 | 1354 | Central | TH01
138481 | 2018-07-07 | Scheduled Outage | Construction | crew isolated overhead transformer at 477 parkdale to renew conections. 11 customers were affected. Holland (SH07) | None | None | 11 | 62 | 11 | Central | UJ07
138484 | 2018-07-08 | Tree Contacts | Tree Growth/ Untrimmed Tree | At 2:53pm SCADA indicated a trip on the TH05 breaker, crew found trees burnt on the TL1TH at 801 Albert. 119 customers affected. Hinchey (TH05) | None | None | 119 | 27 | 54 | Central | TH3SH
138485 | 2018-07-08 | Unknown/Other | Unknown | circuit opened. 520 customers affected. Beaconhill (BCHF3) | Unknown \ Other | Unknown \ Other | 78 | 4 | 5 | East | BCHF3
138485 | 2018-07-08 | Unknown/Other | Unknown | circuit opened. 520 customers affected. Beaconhill (BCHF3) | Unknown \ Other | Unknown \ Other | 116 | 2 | 4 | East | BCHF3
138485 | 2018-07-08 | Unknown/Other | Unknown | circuit opened. 520 customers affected. Beaconhill (BCHF3) | Unknown \ Other | Unknown \ Other | 133 | 8 | 18 | East | BCHF3
138485 | 2018-07-08 | Unknown/Other | Unknown | circuit opened. 520 customers affected. Beaconhill (BCHF3) | Unknown \ Other | Unknown \ Other | 249 | 3 | 12 | East | BCHF3
138485 | 2018-07-08 | Unknown/Other | Unknown | circuit opened. 520 customers affected. Beaconhill (BCHF3) | Unknown \ Other | Unknown \ Other | 265 | 3 | 13 | East | BCHF3
138485 | 2018-07-08 | Unknown/Other | Unknown | circuit opened. 520 customers affected. Beaconhill (BCHF3) | Unknown \ Other | Unknown \ Other | 287 | 10 | 48 | East | BCHF3
138485 | 2018-07-08 | Unknown/Other | Unknown | circuit opened. 520 customers affected. Beaconhill (BCHF3) | Unknown \ Other | Unknown \ Other | 349 | 84 | 489 | East | BCHF3
138485 | 2018-07-08 | Unknown/Other | Unknown | circuit opened. 520 customers affected. Beaconhill (BCHF3) | Unknown \ Other | Unknown \ Other | 520 | 1 | 9 | East | BCHF3
138485 | 2018-07-08 | Unknown/Other | Unknown | circuit opened. 520 customers affected. Beaconhill (BCHF3) | Unknown \ Other | Unknown \ Other | 520 | 2 | 17 | East | BCHF3
138485 | 2018-07-08 | Unknown/Other | Unknown | circuit opened. 520 customers affected. Beaconhill (BCHF3) | Unknown \ Other | Unknown \ Other | 520 | 115 | 997 | East | BCHF3
138486 | 2018-07-08 | Tree Contacts | Broken Branch | tree on wires | None | None | 767 | 105 | 1342 | West | BRDF5
138487 | 2018-07-09 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X23898 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 18 | 112 | 34 | Central | TH15
138490 | 2018-07-09 | Scheduled Outage | Construction | 2 Transformers, X26696 and X32174 isolated by crew to transfer plant | None | None | 23 | 262 | 100 | Central | UL06
138492 | 2018-07-09 | Scheduled Outage | Construction | crew isolated a section of overhead line for pole replacement, and tree trimming. 84 customers were affected. Woddroffe (170F1) | None | None | 84 | 458 | 641 | South | 170F1
138493 | 2018-07-09 | Foreign Interference | Vehicle | MVC broke pole and dmaged OH wires at Dunrobin Rd and Murphey side road. 908 customers affected. Kanata MTS (624F6) | Pole | Pole | 303 | 4 | 20 | West | 624F6
138493 | 2018-07-09 | Foreign Interference | Vehicle | MVC broke pole and dmaged OH wires at Dunrobin Rd and Murphey side road. 908 customers affected. Kanata MTS (624F6) | Pole | Pole | 904 | 48 | 723 | West | 624F6
138493 | 2018-07-10 | Foreign Interference | Vehicle | MVC broke pole and dmaged OH wires at Dunrobin Rd and Murphey side road. 908 customers affected. Kanata MTS (624F6) | Pole | Pole | 85 | 209 | 296 | West | 624F6
138493 | 2018-07-10 | Foreign Interference | Vehicle | MVC broke pole and dmaged OH wires at Dunrobin Rd and Murphey side road. 908 customers affected. Kanata MTS (624F6) | Pole | Pole | 1122 | 209 | 3908 | West | 624F6
138494 | 2018-07-10 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact. X38719 | O/H Transformer | O/H Transformer (1ph) | 10 | 146 | 24 | Central | TH15
138495 | 2018-07-10 | Defective Equipment | Imminent Failure | TP2911 at 228 Stedman was isolated for replacement due to an oil leak. 15 customers affected. Uplands (4801F8) | U/G Transformer | Padmount (1ph) | 15 | 157 | 39 | East | 4801F8
138496 | 2018-07-10 | Adverse Weather | Extreme Wind | Transformer #X32328 opened up due to open wire secondary bus hit together and fused causing an outage. PER JESSE PLUNKET, SECONDARY TWISTED IN NEUTRAL | O/H Switchgear | Fused Cutout | 10 | 177 | 30 | Central | AD06
138499 | 2018-07-10 | Foreign Interference | Dig-In | TH24 breaker tripped due to cable fault between TN12368 and TV12354 | U/G Cable | PILC | 1 | 181 | 3 | Central | 4302
138499 | 2018-07-10 | Foreign Interference | Dig-In | TH24 breaker tripped due to cable fault between TN12368 and TV12354 | U/G Cable | PILC | 2 | 125 | 4 | Central | 4302
138500 | 2018-07-10 | Scheduled Outage | Construction | Shawn Evans (K-Line) to have transformer X4222 open to install a new pole. 13 customers notified. | None | None | 13 | 238 | 52 | South | 170F1
138501 | 2018-07-10 | Scheduled Outage | Construction | Paul Bortoletti (K-Line) to have transformer X23166 open to transfer plant. 18 customers notified. | None | None | 18 | 56 | 17 | East | AA06
138502 | 2018-07-10 | Scheduled Outage | Maintenance | 13KV vault at 200 Cedarview was isolated to investigate metering issues, affecting 1 customer. Hinchey TS (TH2UL) | None | None | 1 | 183 | 3 | Central | TH2UL
138503 | 2018-07-11 | Scheduled Outage | Maintenance | Mark Brown and crew to have transformer TE309 isolated to replace board. | None | None | 9 | 180 | 27 | South | 160F2
138504 | 2018-07-11 | Scheduled Outage | Construction | Transformer #X23317 isolated by crew to transfer plant, Paul from K-Line | None | None | 4 | 125 | 8 | East | UB03
138505 | 2018-07-11 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32261 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 1 | 186 | 3 | West | BECKF2
138506 | 2018-07-11 | Human Element | Commissioning Error | TP9751 interrupted during planned switching. 9 customers affected. Cyrville (CYRF4) | U/G Transformer | Padmount (1ph) | 9 | 2 | 0 | East | CYRF4
138507 | 2018-07-11 | Scheduled Outage | Construction | Transformer #X4355 isolated by crew to transfer plant, Sean Evans from Kline | None | None | 8 | 195 | 26 | South | 170F1
138508 | 2018-07-11 | Foreign Interference | Dig-In | Transformer #TP4873 isolated by crew due to U/G cable dig in, secondary | None | None | 12 | 12 | 2 | East | BCHF1
138509 | 2018-07-11 | Scheduled Outage | Maintenance | Transformer #X32009 isolated by crew to replace pole and transformer | None | None | 14 | 290 | 68 | Central | UL06
138510 | 2018-07-11 | Human Element | Improper Construction/installation | While construction crew was removing old conductor wire dropped into live underbuild causing TEMP 183 red phase to blow. | None | None | 180 | 20 | 60 | Central | UV07
138511 | 2018-07-11 | Scheduled Outage | Construction | To transfer plant. X23314 | O/H Transformer | O/H Transformer (1ph) | 7 | 90 | 10 | East | UB03
138513 | 2018-07-12 | Scheduled Outage | Construction | 2 transformers, X22541 and X22543 isolated by crew, Jordan Foote from K-Line, for a service upgrade | None | None | 25 | 30 | 12 | East | CAS-F4
138514 | 2018-07-12 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X9696 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 9 | 200 | 30 | West | JKGF4
138515 | 2018-07-12 | Scheduled Outage | Construction | Transformer 3204 at 5 Charmichael was isolated to allow crew to replace transfomer. 13 customers were affected. South March (39F2) | U/G Transformer | Padmount (1ph) | 13 | 571 | 124 | West | 39F2
138517 | 2018-07-12 | Scheduled Outage | Construction | planned outage to replace a pole and transfer plant | None | None | 66 | 347 | 382 | South | 47F3
138518 | 2018-07-12 | Scheduled Outage | Construction | Transformer #X32168 isolated by crew to transfer plant | None | None | 16 | 233 | 62 | Central | SM16
138519 | 2018-07-12 | Scheduled Outage | Construction | Transformer #X36083 isolated by crew to replace connections | None | None | 14 | 35 | 8 | Central | TD05
138521 | 2018-07-12 | Foreign Interference | Wildlife (Bird/Animal) | Squirel contact on the O/H cuased the switch W1265 to blow. Billberry (77M6). 54 customers were affected | O/H Switchgear | Fused Cutout | 54 | 150 | 135 | East | 77M6
138522 | 2018-07-12 | Defective Equipment | Mechanical Failure | At 9:51pm SH02 and SH04 circuits were isolated to allow crew to replace a broken pole at Holland and Ruskin. 342 customers affected. Holland (SH04,SH02) | Pole | Pole | 28 | 282 | 132 | Central | SH04
138522 | 2018-07-12 | Defective Equipment | Mechanical Failure | At 9:51pm SH02 and SH04 circuits were isolated to allow crew to replace a broken pole at Holland and Ruskin. 342 customers affected. Holland (SH04,SH02) | Pole | Pole | 314 | 282 | 1476 | Central | SH02
138523 | 2018-07-12 | Scheduled Outage | Forced Switching | crew isolated overhead feeding customers on Larch and juniper to allow crane to assist in changing defective overhead transformer. 54 customers were affected. Billberry (77M6) | None | None | 54 | 154 | 139 | East | 77M6
138524 | 2018-07-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X48651 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 19 | 99 | 31 | Central | TW18
138525 | 2018-07-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32609 opened up due to animal contact | O/H Switchgear | Fused Cutout | 19 | 183 | 58 | Central | TD05
138526 | 2018-07-13 | Scheduled Outage | Construction | To remove 4 cables from the main splitter to satisfy hydro spec. | None | Customer-Owned | 1 | 122 | 2 | East | UZ04
138527 | 2018-07-13 | Scheduled Outage | Construction | Transformer #X32309 isolated by crew to transfer plant | None | None | 5 | 98 | 8 | Central | UC03
138530 | 2018-07-14 | Foreign Interference | Vehicle | Motor vehicle accident at Bronson and Fifth caused damage to hydro pole and caused the S24582 to blow. 20 customers were affected. Riverdale (TR09) | Pole | Pole | 20 | 80 | 27 | Central | TR09
138534 | 2018-07-15 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel blew transformer X32925 fuse, replaced switch, arrester, and primary lead. Removed vines. Re-Fused, power restored. | O/H Transformer | O/H Transformer (1ph) | 7 | 75 | 9 | Central | TD07
138535 | 2018-07-16 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X39328 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 3 | 141 | 7 | Central | TH15
138536 | 2018-07-16 | Foreign Interference | Wildlife (Bird/Animal) | Critter caused transformer X34386 to open. Re fused and closed back in. | O/H Transformer | O/H Transformer (1ph) | 9 | 30 | 4 | East | TB15
138538 | 2018-07-16 | Foreign Interference | Wildlife (Bird/Animal) | Recloser tripped open under hold off to tree trimmers. Report from line crew of crow making contact on Prince of Wales at Woodroffe | Unknown \ Other | Unknown \ Other | 4637 | 14 | 1082 | East | LMBF7
138539 | 2018-07-16 | Scheduled Outage | Maintenance | VT103 at 30 Mcewen was isolated to investigate equipment failure in vault. A Blown PT was found. 1 customer affected. Lincoln 5401. | None | Unknown \ Other | 1 | 27 | 0 | Central | 5401
138541 | 2018-07-16 | Unknown/Other | Unknown | Not yet known. | None | None | 16 | 157 | 42 | West | 624F6
138542 | 2018-07-16 | Unknown/Other | Unknown | Not yet known. | None | None | 257 | 170 | 728 | South | 190F5
138544 | 2018-07-16 | Defective Equipment | Imminent Failure | replace leaking transformer | O/H Transformer | O/H Transformer (1ph) | 1 | 78 | 1 | South | 145F3
138546 | 2018-07-17 | Tree Contacts | Broken Branch | Not yet known. | O/H Conductor | O/H Conductor | 469 | 15 | 117 | West | 624F6
138546 | 2018-07-17 | Tree Contacts | Broken Branch | Not yet known. | O/H Conductor | O/H Conductor | 787 | 4 | 52 | West | 624F6
138546 | 2018-07-17 | Tree Contacts | Broken Branch | Not yet known. | O/H Conductor | O/H Conductor | 787 | 32 | 420 | West | 624F6
138546 | 2018-07-17 | Tree Contacts | Broken Branch | Not yet known. | O/H Conductor | O/H Conductor | 1251 | 5 | 104 | West | 624F6
138546 | 2018-07-17 | Tree Contacts | Broken Branch | Not yet known. | O/H Conductor | O/H Conductor | 1251 | 96 | 2002 | West | 624F6
138547 | 2018-07-17 | Unknown/Other | Unknown | The 22M24 Cb tripped open while under hold off. System cleared hold off and closed the circuit back in and circuit held. Circuit patrolled and nothing was found. | Station Equipment | Relay | 5839 | 4 | 389 | South | 22M24
138548 | 2018-07-17 | Defective Equipment | Imminent Failure | Transformer TE1344 at 3058 Olympic Way was isolated to allow crew to replace leaking transformer. 15 customer was affected. Leitrim (249F4) | U/G Transformer | Padmount (1ph) | 15 | 325 | 81 | East | LTM04
138552 | 2018-07-17 | Tree Contacts | Tree Growth/ Untrimmed Tree | REPLACED BLOWN FUSE FEEDING TRANSFORMER X36608 ON CUSTOMER OWNED LINE (TREE CONTACT) CUSTOMER ADVISED TO HAVE TREES TRIMMED | Customer Owned | Customer-Owned | 1 | 133 | 2 | West | 624F6
138553 | 2018-07-17 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X27329 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 13 | 240 | 52 | East | TB06
138554 | 2018-07-18 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X31478 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 17 | 57 | 16 | Central | TH15
138557 | 2018-07-18 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact. | O/H Transformer | O/H Transformer (1ph) | 10 | 2 | 0 | Central | TW18
138558 | 2018-07-18 | Scheduled Outage | Construction | Transformer #X31406 isolated by crew to rearrange plant | None | None | 11 | 105 | 19 | Central | AM03
138559 | 2018-07-18 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X36458 opened up due to bird contact | O/H Switchgear | Fused Cutout | 12 | 147 | 29 | West | JKGF4
138560 | 2018-07-19 | Foreign Interference | Wildlife (Bird/Animal) | G260 W fuse at 4210 Albion opened due to an animal contact at X16003. 44 customers affected. Lietrim (LTM01) | O/H Conductor | O/H Conductor | 44 | 95 | 70 | East | LTM01
138561 | 2018-07-19 | Foreign Interference | Wildlife (Bird/Animal) | TO30 CB opened, suspected animal contact. 1393 customers affected. Overbrook (TO3UT) | Unknown \ Other | Unknown \ Other | 944 | 43 | 677 | East | TO3UT
138561 | 2018-07-19 | Foreign Interference | Wildlife (Bird/Animal) | TO30 CB opened, suspected animal contact. 1393 customers affected. Overbrook (TO3UT) | Unknown \ Other | Unknown \ Other | 1393 | 4 | 93 | East | TO3UT
138563 | 2018-07-19 | Defective Equipment | Imminent Failure | TP8192 at 1752 Bromont was isolated for replacement due to an oil leak. 12 customers affected. Orleans (325M8) | U/G Transformer | Padmount (1ph) | 12 | 314 | 63 | East | 77M6
138565 | 2018-07-19 | Scheduled Outage | Construction | Planned outage to transfer hydro plant to new pole. | None | None | 12 | 456 | 91 | Central | AM03
138566 | 2018-07-20 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X27511 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 6 | 137 | 14 | East | TB06
138567 | 2018-07-20 | Defective Equipment | Imminent Failure | TP7907 at 1744 Teakdale was isolated for replacement due to an oil leak. 9 customers affected. Bilberry (77M2) | U/G Transformer | Padmount (1ph) | 9 | 216 | 32 | East | 77M2
138568 | 2018-07-20 | Scheduled Outage | Construction | To transfer plant from UL06 feed to SM16 and remove overhead line from S18273. | None | None | 16 | 188 | 50 | Central | UL06
138569 | 2018-07-20 | Scheduled Outage | Construction | To transfer plant from UL06 to SM16 from S20743 on SM16. | None | None | 16 | 150 | 40 | Central | SM16
138570 | 2018-07-20 | Unknown/Other | Unknown | UQ05 breaker tripped under holdoff. Outage closed as per log entry | None | None | 427 | 7 | 50 | East | UQ05
138571 | 2018-07-20 | Scheduled Outage | Forced Switching | Isolation from TEMP1506 RWB on UQ05 cct, to repair White phase conductor in the rear of 499 Neighbourhood way | None | None | 9 | 155 | 23 | East | UQ05
138573 | 2018-07-21 | Defective Equipment | Mechanical Failure | The switch S25733 R phase at Meadowlands and Inverness blew due to defective switch. Parkwoodhills (190F5) 253 customers were affected. | O/H Switchgear | Fused Cutout | 253 | 130 | 548 | South | 190F5
138574 | 2018-07-21 | Tree Contacts | Tree Growth/ Untrimmed Tree | Transformer #2110 opened up due to tree contact | O/H Switchgear | Fused Cutout | 4 | 88 | 6 | East | 56F1
138575 | 2018-07-22 | Foreign Interference | Wildlife (Bird/Animal) | Switch G289R phase blew due to animal contact on the O/H 4251 Whyte Side Rd. 25 customers were affected. Leitrim (LTM04) | O/H Switchgear | Fused Cutout | 1 | 32 | 1 | East | LTM04
138575 | 2018-07-22 | Foreign Interference | Wildlife (Bird/Animal) | Switch G289R phase blew due to animal contact on the O/H 4251 Whyte Side Rd. 25 customers were affected. Leitrim (LTM04) | O/H Switchgear | Fused Cutout | 25 | 185 | 77 | East | LTM04
138576 | 2018-07-22 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X58083 open due to animal contact at 2066 Westbury. 49 Customer were affected. Woodroffe (TW17) | O/H Switchgear | Fused Cutout | 49 | 61 | 50 | Central | TW17
138580 | 2018-07-22 | Foreign Interference | Foreign Objects | The UT03 circuit auto reclosed and locked due to a lunch bag wrapped on the center phase making contact with the road side phase at the Station. 439 customers were affected. Eastview (UT03) | Station Equipment | Relay | 439 | 48 | 351 | East | UT03
138581 | 2018-07-22 | Tree Contacts | Broken Branch | Transformer #X23699 opened up due to tree contact | O/H Switchgear | Fused Cutout | 9 | 98 | 15 | East | UB07
138582 | 2018-07-22 | Tree Contacts | Falling Tree | The TW03 CB (TW22) circuit tripped due to a tree on the O/H line at 908 Fairlawn. 1327 customers were affected. Woodroffe (TW22) | O/H Switchgear | Fused Cutout | 1327 | 107 | 2366 | Central | TW22
138583 | 2018-07-22 | Scheduled Outage | Construction | Transformer #X35633 isolated by crew due streetlight pole down | None | None | 3 | 6 | 0 | Central | TD12
138584 | 2018-07-22 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35542 opened up due to animal contact | O/H Switchgear | Fused Cutout | 20 | 81 | 27 | Central | TD05
138585 | 2018-07-22 | Tree Contacts | Tree Growth/ Untrimmed Tree | AA04 CB tripped due to braches on the O/H at 864 Forthwick | O/H Switchgear | Fused Cutout | 242 | 91 | 367 | East | AA04
138585 | 2018-07-22 | Tree Contacts | Tree Growth/ Untrimmed Tree | AA04 CB tripped due to braches on the O/H at 864 Forthwick | O/H Switchgear | Fused Cutout | 618 | 45 | 464 | East | AA04
138586 | 2018-07-22 | Tree Contacts | Tree Growth/ Untrimmed Tree | Overgrown trees cause the transformer at 5262 Pipperville to open. 1 customer was affected. Leitrim (LTM02) | O/H Switchgear | Fused Cutout | 1 | 247 | 4 | East | LTM02
138588 | 2018-07-23 | Human Element | Improper Design | While operating overhead switches, switchstick made contact with live primary tripping the UVK1Y1, interrupting UV03 load. Crew reports switches being operated were too close to live primary. | None | None | 498 | 3 | 25 | Central | UV03
138589 | 2018-07-23 | Scheduled Outage | Maintenance | Transformer #X31746 isolated by crew TO MAKE REPAIRS, BROKEN NEUTRAL AT SECONDARY BUSS | None | None | 9 | 82 | 12 | Central | UL14
138590 | 2018-07-23 | Defective Equipment | Imminent Failure | Transformer #X06047 opened up due to defective equipment, crew had to replace switch and bracket | O/H Switchgear | Fused Cutout | 8 | 260 | 35 | South | 140F4
138591 | 2018-07-23 | Scheduled Outage | Maintenance | X28160 at 1232 Cheverton isolated to replace burning secondary connections. 14 customers affected. Riverdale (505) | None | O/H Service | 14 | 72 | 17 | Central | 505
138592 | 2018-07-24 | Tree Contacts | Broken Branch | Tree fell on prrimary at Prince of Whales and Fallowfield and caused the 180F4 breaker to open. 988 customers affected. Rideau Heights (180F4) | O/H Conductor | O/H Conductor | 45 | 581 | 436 | South | 180F4
138592 | 2018-07-24 | Tree Contacts | Broken Branch | Tree fell on prrimary at Prince of Whales and Fallowfield and caused the 180F4 breaker to open. 988 customers affected. Rideau Heights (180F4) | O/H Conductor | O/H Conductor | 988 | 60 | 988 | South | 180F4
138593 | 2018-07-23 | Foreign Interference | Wildlife (Bird/Animal) | S417 at 6 Stinson opened due to an animal contact. 27 customers affected. Stafford (200F2) | O/H Switchgear | Fused Cutout | 27 | 319 | 144 | South | 200F2
138594 | 2018-07-23 | Foreign Interference | Wildlife (Bird/Animal) | Fuse at X34033 at 1763 Kerr Ave. opened due to an animal contact. 2 customers affected. Clyde (UC03) | O/H Switchgear | Fused Cutout | 2 | 350 | 12 | Central | UC03
138595 | 2018-07-24 | Defective Equipment | Defective Equipment/ Material | Crew reports that defective elbow at transformer TP6203 resulted in a loss of load. Crew reports that elbow was slightly swollen and backed off from the insert after switching. 36 customers were affected. Jockvale D.S. (145F4) | U/G Cable Attachement | Elbow \ Insert | 36 | 58 | 35 | South | 145F4
138598 | 2018-07-24 | Defective Equipment | Imminent Failure | Transformer at 1261 Famlit was isolated to replace transformer and perform soil remediation. 9 customers affected. Moulton (8F1) | None | None | 9 | 461 | 69 | East | 8F1
138599 | 2018-07-24 | Defective Equipment | Mechanical Failure | 56F1 from S26200 to EOL isolated due to fallen conductor at Mitch Owens and Sale Barn. 42 customers affected. South Gloucester (56F1) | O/H Conductor | Unknown \ Other | 42 | 421 | 295 | East | 56F1
138600 | 2018-07-25 | Unknown/Other | Unknown | Transformer fuse blown, cause uknown. | O/H Transformer | O/H Transformer (1ph) | 13 | 103 | 22 | East | 77M2
138601 | 2018-07-25 | Scheduled Outage | Maintenance | PAUL FROM K-LINE TO TRANSFER PLANT ON X23479 | None | O/H Transformer (1ph) | 6 | 55 | 6 | East | AA04
138602 | 2018-07-25 | Scheduled Outage | Maintenance | PAUL FROM K-LINE TO TRANSFER PLANT ON X23484 | None | O/H Transformer (1ph) | 2 | 55 | 2 | East | AA04
138608 | 2018-07-25 | Unknown/Other | Unknown | Scada indicates TM30 CB has opened and G2 at Chaudiere is offline. | O/H Conductor | Unknown \ Other | 1 | 55 | 1 | Central | TC3TM
138610 | 2018-07-25 | Defective Equipment | Defective Equipment/ Material | Blue phase cable fault between K580 and K583 on UA05 circuit. | U/G Cable | XLPE | 1 | 2 | 0 | East | UA11
138610 | 2018-07-25 | Defective Equipment | Defective Equipment/ Material | Blue phase cable fault between K580 and K583 on UA05 circuit. | U/G Cable | XLPE | 15 | 24 | 6 | East | UA05
138610 | 2018-07-25 | Defective Equipment | Defective Equipment/ Material | Blue phase cable fault between K580 and K583 on UA05 circuit. | U/G Cable | XLPE | 68 | 273 | 309 | East | UA05
138612 | 2018-07-26 | Scheduled Outage | Construction | Two transformers at 1501 Innes Rd where isolated to transfer primary feed cable to a new pole affecting 9 customers. Cyrville CYRF4 | None | None | 9 | 260 | 39 | East | CYRF4
138613 | 2018-07-26 | Defective Equipment | Imminent Failure | Transformer TE1715 at 1296 Famlit Crt was isolated to allow crew to replace leaking transformer. 9 customers were affected. Moulton (8F1) | U/G Transformer | Padmount (1ph) | 9 | 373 | 56 | East | 8F1
138614 | 2018-07-26 | Defective Equipment | Imminent Failure | Transformer TP6351 at 699 Des Cedres was iolated to allow crew to replace leaking transformer. 7 customers were affected. Casselman (CASF2) | U/G Transformer | Padmount (1ph) | 7 | 170 | 20 | East | CAS-F2
138615 | 2018-07-26 | Scheduled Outage | Construction | A Hydro Ottawa U/G crew isolated K779 to alow for new secondary wire to be installed and connected | None | None | 16 | 159 | 42 | East | AQ07
138617 | 2018-07-26 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact blew transformer fuse. | O/H Transformer | O/H Transformer (1ph) | 10 | 266 | 44 | Central | TD01
138618 | 2018-07-26 | Defective Equipment | Imminent Failure | Crew changing leaking transformer TP2687 on the BRDF1 cicruit. 8 customers affected. | U/G Transformer | Padmount (1ph) | 8 | 103 | 14 | West | BRDF1
138619 | 2018-07-26 | Human Element | Switching Error | A switching error occurred while isolating TP2687 resulting in an outage on the TP2686. 8 customers affected on the BRDF1. | U/G Transformer | Padmount (1ph) | 8 | 103 | 14 | West | BRDF1
138620 | 2018-07-26 | Scheduled Outage | Construction | Hydro Ottawa line crews isolated TD07 from S29572 to E.O.L to allow S29572 to be removed from the system and a new S17060 installed 1 span north. | None | Fused Cutout | 27 | 67 | 30 | Central | TD07
138622 | 2018-07-26 | Tree Contacts | Broken Branch | UQ04 circuit opened and locked out. Field Operators found a tree branch in the overhead at the rear of 1634 Abbey. Branch was removed and UQ04 breaker closed and holding. | None | None | 92 | 105 | 161 | East | UQ04
138623 | 2018-07-27 | Foreign Interference | Wildlife (Bird/Animal) | Blown transformer fuse | O/H Transformer | O/H Transformer (1ph) | 20 | 61 | 20 | East | 4801F8
138624 | 2018-07-27 | Unknown/Other | Unknown | The Janet King JKGF4 trip while under hold off. Crew were clear of the line at the time of circuit trip. Circuit was resotred, cause of ciruit trip remains under investigation. Janet King (JKGF4) | None | None | 7217 | 7 | 842 | West | JKGF4
138625 | 2018-07-27 | Defective Equipment | Imminent Failure | Transformer MT1309 at 110 Artista Crt was isolated to allow crew to replace leaking transformer. 10 customers were affected. Albion (2206) | None | None | 10 | 159 | 26 | East | 2206
138626 | 2018-07-27 | Scheduled Outage | Construction | Transformers TP7377 an TP7378 on Derbeyshire were isolated to allow crew to replace transformer inserts. 11 customers were affected. Marchwood (MWDF3) | U/G Cable Attachement | Elbow \ Insert | 11 | 89 | 16 | West | MWDF3
138627 | 2018-07-27 | Scheduled Outage | Construction | Travis Baker and crew isolated TP2007 to replace transformer because of excessive rust. This affected 11 customers on the JKGF4 circuit. | U/G Transformer | Padmount (1ph) | 11 | 62 | 11 | West | JKGF4
138630 | 2018-07-27 | Defective Equipment | Electrical Failure | red phase cable fault on billberry drive caused overhead switch on Champlain to blow. 262 customers were affected. Billberry 77M6 | U/G Cable | XLPE | 262 | 258 | 1127 | East | 77M6
138631 | 2018-07-27 | Defective Equipment | Defective Equipment/ Material | A 27Kv cable fault in the Hunters Run Dr and Boyer area cause the outage to 102 customers for 228 minutes on the 77M2 ciruit. | U/G Cable | XLPE | 102 | 228 | 388 | East | 77M6
138634 | 2018-07-28 | Tree Contacts | Broken Branch | At 6:14am SCADA indicated an auto-reclose on the RX2001 on the 7F2 circuit affecting 188 customers. While patrolling crews found a blown fuse at 1425 Mulligan and branches on the secondary fed from X24554. Limebank (7F2) | None | None | 1 | 226 | 4 | East | 7F2
138635 | 2018-07-28 | Defective Equipment | Electrical Failure | faulted cable caused fuse to blow feeding underground transformer at 1208 Meadowlands. 42 customers affected, Parkwood hills 190F5 | U/G Cable | XLPE | 42 | 485 | 340 | South | 190F5
138636 | 2018-07-29 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X22031 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 5 | 80 | 7 | East | LTM02
138640 | 2018-07-29 | Foreign Interference | Foreign Objects | A balloon in the O/H at the corner of ROWATT ST AND BRITANNIA caused the W and B phases at S16327 to open affecting 500 customers for 117 minutes on the TD14 circuit. | O/H Conductor | O/H Conductor | 500 | 117 | 975 | Central | TD14
138641 | 2018-07-29 | Foreign Interference | Wildlife (Bird/Animal) | animal contact caused overhead transformer at 25 Bonner to open. 8 customers were affected. Bells corners 47F2. | None | None | 8 | 60 | 8 | South | 47F2
138643 | 2018-07-29 | Foreign Interference | Wildlife (Bird/Animal) | An animal made contact with the fuse the feeds transformer X28223 at the rear of 152 Begonia Ave causing an outage for 10 customers for 37 minutes on the 505 circuit | O/H Transformer | O/H Transformer (1ph) | 10 | 37 | 6 | Central | 505
138645 | 2018-07-30 | Defective Equipment | Mechanical Failure | crew isolated the transformer at 1584 walkley to replace defective primary insulators, and switches at pole. 10 customers affected. Albion UA06. | Pole Attachement | Insulator | 10 | 187 | 31 | East | UA06
138646 | 2018-07-29 | Defective Equipment | Electrical Failure | defective overhead transformer at 463 Richardson ave. opened. 10 customers were affected. Lincoln TD07 | O/H Transformer | O/H Transformer (1ph) | 10 | 427 | 71 | Central | TD07
138647 | 2018-07-30 | Scheduled Outage | Maintenance | At 07:05am P105 was isolated to allow crew to make repairs. 1 customer affected. Overbrook (SOO4) | None | None | 1 | 18 | 0 | East | SO04
138649 | 2018-07-30 | Unknown/Other | Unknown | At 06:15am G88 blue phase blew. Crews patrolled line but found not issue. 4 customers affected. Limebank (7F4) | None | None | 4 | 127 | 8 | East | 7F4
138652 | 2018-07-30 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35012 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 8 | 175 | 23 | Central | SH04
138653 | 2018-07-30 | Scheduled Outage | Maintenance | K-Line to transfer plant X39572 | None | Kiosk (1ph) | 1 | 255 | 4 | South | 170F1
138654 | 2018-07-30 | Defective Equipment | Electrical Failure | Transformer TP5268 at 49 Queensline Dr was isolated to allow crew to make repairs to defective secondary cable at 43 Queensline. 14 customers were affected. QCH (160F1) | Secondary \ Service | U/G Service | 14 | 282 | 66 | South | 160F1
138655 | 2018-07-30 | Scheduled Outage | Construction | A transformer at 166 Craig was isolated to replace a badly rusted transformer affecting 17 customers. Centerpoint 87F3 | None | Padmount (1ph) | 17 | 713 | 202 | South | 87F3
138659 | 2018-07-31 | Scheduled Outage | Construction | 4KV transformer kiosk, K586, at 1555 Walkley was islated to repair secondary connections, affecting 22 customers. Albion DS (UA11) | None | Kiosk (1ph) | 22 | 45 | 16 | East | UA11
138660 | 2018-07-31 | Defective Equipment | Imminent Failure | Transformer TE3523 isolated to replace due to leaking by Mark Brown and crew. 10 Customers on the FAL02 cicruit affected. | None | None | 10 | 180 | 30 | South | FAL02
138661 | 2018-07-31 | Scheduled Outage | Construction | Old transformer and base replaced with new TP12755 | U/G Transformer | Padmount (1ph) | 9 | 426 | 64 | West | 24F1
138662 | 2018-08-01 | Scheduled Outage | Construction | 2 4 kv kiosk transformers, K580 & K5934, isolated for clearance to pull in new primary cables and remove asbestos, affecting 34 customers. Albion DS (UA05) | None | Kiosk (1ph) | 34 | 175 | 99 | East | UA05
138663 | 2018-08-01 | Scheduled Outage | Maintenance | VT814 at 84 Wiggins isolated for customer vault maintenance. 117 customers on the TR1UN circuit affected. | None | None | 117 | 148 | 289 | Central | TR1UN
138664 | 2018-08-01 | Scheduled Outage | Construction | Paul from K-Line to have transformer X29683 open to transfer plant. Customers notified. | None | None | 6 | 32 | 3 | East | SO03
138665 | 2018-08-01 | Scheduled Outage | Construction | New pole being installed. Outage on X35321 | None | Pole | 2 | 120 | 4 | Central | TW22
138667 | 2018-08-01 | Scheduled Outage | Construction | New pole being installed. Outage on X35321 | None | Pole | 7 | 120 | 14 | Central | TW22
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 0 | 95 | 0 | Central | AH13
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 0 | 146 | 0 | Central | AH13
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 5 | 161 | 13 | Central | UL1AH
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 8 | 70 | 9 | Central | AH07
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 136 | 254 | 576 | Central | AH04
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 181 | 20 | 60 | Central | AH13
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 181 | 254 | 766 | Central | AH13
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 241 | 70 | 281 | Central | AH05
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 294 | 9 | 44 | Central | TM1AH
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 443 | 254 | 1875 | Central | AH14
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 555 | 70 | 648 | Central | TM1AH
138669 | 2018-08-01 | Lightning | Lightning | Suspect lightnight strike at Kenwood & Broad view damaged insulators and broke span guys caused breaker trips on TM1AH, TM3UC and AH13 circuits and loss of supply to AH05 & AH07 circuit, affecting 2180 customers. Carling TS & HillCrest DS | Pole Attachement | Insulator | 804 | 70 | 938 | Central | TM1AH
138670 | 2018-08-01 | Loss Of Supply | Third Party | defective equipment in V590, Vault was decommissioned. Slater (SA23) | Customer Owned | Customer-Owned | 1 | 1265 | 21 | Central | SA23
138671 | 2018-08-02 | Scheduled Outage | Forced Switching | Transformer X37372 was isolated to allow crew to investigate part power issues. 8 customers were affected. Carling (SM12) | O/H Transformer | O/H Transformer (1ph) | 8 | 28 | 4 | Central | SM12
138672 | 2018-08-01 | Defective Equipment | Defective Equipment/ Material | Transformer X32729 was open due to defective transformer.Transformer X32614 was also open to allow crew to transfer secondary load from X32729 to X32614. 13 customers were affected. Lincoln Heights (TD05) | O/H Transformer | O/H Transformer (1ph) | 13 | 625 | 135 | Central | TD05
138672 | 2018-08-02 | Defective Equipment | Defective Equipment/ Material | Transformer X32729 was open due to defective transformer.Transformer X32614 was also open to allow crew to transfer secondary load from X32729 to X32614. 13 customers were affected. Lincoln Heights (TD05) | O/H Transformer | O/H Transformer (1ph) | 21 | 132 | 46 | Central | TD05
138673 | 2018-08-02 | Scheduled Outage | Construction | Tansformer TE316 isolated by Mark Brown to replace due to leaking. 21 customer affected on the 84F5 circuit out of Manordale. | None | None | 21 | 635 | 222 | South | 84F5
138674 | 2018-08-02 | Scheduled Outage | Maintenance | Transformer K584 secondary isolated by Bob Cooper to repair a hot secodnary connection. 21 customers on the UA05 circuit affected. | None | None | 21 | 36 | 13 | East | UA05
138676 | 2018-08-02 | Scheduled Outage | Construction | Pole replacement X35322 | None | Pole | 5 | 200 | 17 | Central | TW22
138677 | 2018-08-02 | Scheduled Outage | Construction | Pole replacement. X35324 removed and to be replaced at a later date | None | Pole | 5 | 200 | 17 | Central | TW22
138678 | 2018-08-02 | Scheduled Outage | Maintenance | At 10:00am vault VT607 was isolated to for scheduled work. 21 customers affected. Lincoln Heights (TD06) | None | None | 21 | 55 | 19 | Central | TD06
138681 | 2018-08-03 | Foreign Interference | Wildlife (Bird/Animal) | An animal made contact with transformer X29729 at 485 Penhill Ave wich the caused the fuse to blow affecting 7 customer for 43 minutes on the TB14 circuit | O/H Transformer | O/H Transformer (1ph) | 7 | 43 | 5 | East | TB14
138682 | 2018-08-03 | Scheduled Outage | Construction | Matt Ruppel and crew to have transformer X21929 open to install new services. Customers notified. | None | None | 17 | 101 | 29 | East | AC04
138683 | 2018-08-03 | Foreign Interference | Wildlife (Bird/Animal) | OMS has predicted based on calls an outage from the G316R. Roch Groulx in the field confirmed an outage caused by animal contact. 81 customers on the LTM04 affected. | None | None | 81 | 171 | 231 | East | LTM04
138684 | 2018-08-03 | Scheduled Outage | Maintenance | At 9:10am K580 and K583 were isolated to allow crew to replace cables and remove asbestos. 34 customers affected. Albion (UA05) | None | None | 34 | 123 | 70 | East | UA05
138685 | 2018-08-04 | Defective Equipment | Defective Equipment/ Material | Defective transformer. | O/H Transformer | O/H Transformer (1ph) | 15 | 294 | 74 | East | 4801F8
138687 | 2018-08-05 | Foreign Interference | Wildlife (Bird/Animal) | 27KV overhaed transformer, X24166, at 9 sumac was with blown fuse due to animal contact, affecting 12 customers. Moulton (8F1). | O/H Transformer | O/H Transformer (1ph) | 12 | 179 | 36 | East | 8F1
138688 | 2018-08-06 | Defective Equipment | Electrical Failure | A blown lightning arrestor at Avonlea and Beth caused a primary fused switch at 228 Grenfell to open affecting 172 customers. Barhaven 140F5 | Pole Attachement | Arrester | 172 | 116 | 333 | South | 140F5
138689 | 2018-08-06 | Scheduled Outage | Construction | Transformer #X29692 isolated by crew to repair damaged streetlight wire | None | None | 16 | 20 | 5 | East | SO12
138700 | 2018-08-06 | Defective Equipment | Electrical Failure | TW03 (TW22) breaker auto-reclosed then locked out during a thunderstorm. Crews found the TW22 egress cable was faulted. 1326 customers affected. Woodroffe (TW22(TW03)) | U/G Cable | Unknown \ Other | 1326 | 238 | 5260 | Central | TW22
138707 | 2018-08-06 | Lightning | Lightning | The 22M25 auto-reclosed 3 times but lock out on the third time. 2638 customers affected. Nepean (22M25) | None | None | 0 | 3 | 0 | South | 22M25
138707 | 2018-08-06 | Lightning | Lightning | The 22M25 auto-reclosed 3 times but lock out on the third time. 2638 customers affected. Nepean (22M25) | None | None | 0 | 5 | 0 | South | 22M25
138707 | 2018-08-06 | Lightning | Lightning | The 22M25 auto-reclosed 3 times but lock out on the third time. 2638 customers affected. Nepean (22M25) | None | None | 2638 | 3 | 132 | South | 22M25
138708 | 2018-08-06 | Lightning | Lightning | Bells corners 47F6 opened during storm activity. Crew found blown fuses feeding three phase transformer TE759 at 3955 richmond rd. crew opened fuses to transformer. Circuit was closed and tripped. Circuit was patrolled no cause was found, closed and tripp | None | None | 210 | 109 | 382 | South | 47F6
138708 | 2018-08-06 | Lightning | Lightning | Bells corners 47F6 opened during storm activity. Crew found blown fuses feeding three phase transformer TE759 at 3955 richmond rd. crew opened fuses to transformer. Circuit was closed and tripped. Circuit was patrolled no cause was found, closed and tripp | None | None | 883 | 184 | 2708 | South | 47F6
138709 | 2018-08-06 | Lightning | Lightning | S315R blew during a thunderstorm, crew patrolled the line but did not find a problem.122 customers affected. Epworth (EPWF3) | None | None | 122 | 223 | 453 | South | EPWF3
138710 | 2018-08-06 | Lightning | Lightning | Lightning strike caused elbow at transformer TP5374 at 111 Oakbriar to catch on fire and also cause a possible cable fault between transformers on Heathercrest and Islay and a defective transformer TP5336 at 6 KNOTWOOD CRT affecting 84 customers on the F | None | None | 38 | 715 | 453 | South | FAL02
138710 | 2018-08-06 | Lightning | Lightning | Lightning strike caused elbow at transformer TP5374 at 111 Oakbriar to catch on fire and also cause a possible cable fault between transformers on Heathercrest and Islay and a defective transformer TP5336 at 6 KNOTWOOD CRT affecting 84 customers on the F | None | None | 52 | 46 | 40 | South | FAL02
138710 | 2018-08-06 | Lightning | Lightning | Lightning strike caused elbow at transformer TP5374 at 111 Oakbriar to catch on fire and also cause a possible cable fault between transformers on Heathercrest and Islay and a defective transformer TP5336 at 6 KNOTWOOD CRT affecting 84 customers on the F | None | None | 84 | 333 | 466 | South | FAL02
138713 | 2018-08-07 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32533 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 10 | 79 | 13 | Central | TD06
138714 | 2018-08-07 | Scheduled Outage | Construction | Transformer #X35311 isolated by crew to replace switch | None | None | 16 | 15 | 4 | Central | TD06
138715 | 2018-08-07 | Scheduled Outage | Construction | Transformer #X23666 isolated by crew to replace a service, Mike from Kline | None | None | 6 | 68 | 7 | East | UB07
138716 | 2018-08-07 | Scheduled Outage | Construction | Transformer #X27299 isolated by crew to replace service | None | None | 6 | 48 | 5 | East | UA07
138718 | 2018-08-07 | Lightning | Lightning | a 27Kv transformer TP5374 at 39 OAKBRIAR CRES was isolated to allow the crews replace leaking transformer affecting 1 customer. Fallowfield FAL02 | U/G Transformer | Kiosk (3ph) | 1 | 455 | 8 | South | FAL02
138719 | 2018-08-08 | Scheduled Outage | Maintenance | PLANNED OUTAGE FOR B COOPER TO REPLACE HOT PRIMARY CONNECTIONS, REMOVE ASBESTOS AND PORCELAIN INSULATORS | None | None | 4 | 181 | 12 | East | 2211
138722 | 2018-08-08 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35893 opened up due to animal contact | O/H Switchgear | Fused Cutout | 5 | 191 | 16 | West | 43F2
138723 | 2018-08-08 | Scheduled Outage | Maintenance | To replace TE245 and base and repair TE248 | None | Kiosk (1ph) | 21 | 542 | 190 | South | 84F2
138724 | 2018-08-08 | Scheduled Outage | Construction | Transformer #X32955 isolated by Mike from Kline to disconnect a service | None | None | 5 | 30 | 2 | Central | TD06
138725 | 2018-08-09 | Scheduled Outage | Construction | To allow a line crew to install a new switch, transformer and O/H conductor. | None | None | 1 | 475 | 8 | West | RHNF1
138726 | 2018-08-09 | Scheduled Outage | Maintenance | To allow a Hydro Ottawa U/G crew to replace a cracked insulator in TE362 | None | Unknown \ Other | 10 | 106 | 18 | East | BCHF8
138728 | 2018-08-09 | Scheduled Outage | Construction | Transformer #X29832 isolated by Mike from Kline to transfer plant | None | None | 22 | 35 | 13 | Central | SB05
138729 | 2018-08-09 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X14991 opened up due to bird contact | O/H Switchgear | Fused Cutout | 1 | 80 | 1 | East | LTM04
138732 | 2018-08-09 | Defective Equipment | Defective Equipment/ Material | REPLACED SWITCH AND ARRESTER FEEDING TRANSFORMER X37209 | O/H Transformer | O/H Transformer (1ph) | 4 | 156 | 10 | South | 180F4
138734 | 2018-08-10 | Scheduled Outage | Construction | 4KV kiosk, K339 at 9 Elderfield was isolated to replay secondary pedestal, affecting 16 customers. Bantree DS (AL02). | None | Secondary Pedestal | 16 | 184 | 49 | East | AL02
138735 | 2018-08-10 | Scheduled Outage | Construction | Transformer #X25717 isolated by crew for a service upgrade by Evan Houle | None | None | 4 | 75 | 5 | Central | SM10
138736 | 2018-08-10 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X31773 opened up due to animal contact | O/H Switchgear | Fused Cutout | 8 | 72 | 10 | Central | TW22
138737 | 2018-08-10 | Scheduled Outage | Construction | Transformer #X29451 isolated by crew to replace triplex, and all connections to 9 services at the transformer pole | None | None | 9 | 187 | 28 | East | SO12
138738 | 2018-08-10 | Foreign Interference | Vehicle | TE1436 isolated to allow crews to set transformer back on it base. | Unknown \ Other | Unknown \ Other | 15 | 24 | 6 | East | BLKF4
138740 | 2018-08-11 | Foreign Interference | Vehicle | crew dumped section of the Beckwith F2 circuit from recloser RX2024 to brace hydro pole that was hit from MVA. 308 customers were affected. Beckwith BECKF2. | Pole | Pole | 308 | 29 | 149 | West | BECKF2
138741 | 2018-08-11 | Foreign Interference | Wildlife (Bird/Animal) | At 08:01am SCADA indicated an Auto-Reclose on the A9M1 and the 624F6. Crews found a raccoon and two blown fuses at 48 Richardson Side Rd. South March (A9M1) Kanata (624F6) | O/H Switchgear | Fused Cutout | 1 | 389 | 6 | West | 624F6
138743 | 2018-08-12 | Scheduled Outage | Construction | To tansfer plant. X33683 | None | O/H Transformer (1ph) | 9 | 44 | 7 | Central | SH05
138744 | 2018-08-12 | Scheduled Outage | Construction | To tansfer plant. X33706 | None | O/H Transformer (1ph) | 1 | 44 | 1 | Central | SH05
138745 | 2018-08-12 | Scheduled Outage | Construction | To tansfer plant. X33702 | None | O/H Transformer (1ph) | 1 | 44 | 1 | Central | SH05
138749 | 2018-08-13 | Foreign Interference | Wildlife (Bird/Animal) | An animal made contact with the fuse at X48411 at 1207 Major St causing the S21248 to also to blow affecting 67 customer for 57 minutes on the TW18 circuit | O/H Transformer | O/H Transformer (1ph) | 67 | 57 | 64 | Central | TW18
138750 | 2018-08-13 | Defective Equipment | Mechanical Failure | A 27 Kv transformer TP7903 at 1694 Des Sapins was isolated by the crew for replacement affecting 7 customer for | U/G Transformer | Padmount (1ph) | 7 | 112 | 13 | East | 77M2
138751 | 2018-08-13 | Scheduled Outage | Maintenance | crew isolated transformer at 6 Cremona to repair defective elbow. 9 customers were affected. Woodroffe 170F1. | None | None | 9 | 121 | 18 | South | 170F1
138752 | 2018-08-13 | Defective Equipment | Electrical Failure | At 09:26am SCADA indicates the TH05 breaker tripped. Crews found the SC6137-L4 was flashed. 116 customers affected. Hinchey (TH3SH/TL1TH) | U/G Switchgear | Unknown \ Other | 116 | 38 | 73 | Central | TH3SH
138753 | 2018-08-13 | Scheduled Outage | Vegetation Management | overhead transformer at 2130 strathmore was isolated to allow for tree trimming. 11 customers were affected. Woodroffe TW22 | None | None | 11 | 235 | 43 | Central | TW22
138754 | 2018-08-13 | Scheduled Outage | Construction | Transformer #X32714 isolated by crew to transfer hydro plant | None | None | 9 | 26 | 4 | Central | UV02
138756 | 2018-08-13 | Defective Equipment | Defective Equipment/ Material | Transformer #X36382 opened up due to defective equipment | O/H Switchgear | Fused Cutout | 2 | 142 | 5 | South | 170F3
138757 | 2018-08-14 | Scheduled Outage | Maintenance | planned outage to repair hot connection and replace blown arrestor | None | None | 12 | 122 | 24 | East | AQ09
138759 | 2018-08-14 | Defective Equipment | Imminent Failure | planned outage to change leaking transformer | U/G Transformer | Padmount (1ph) | 15 | 266 | 66 | East | UQ02
138761 | 2018-08-14 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35170 TO REPLACE BROKEN SWITCH | None | O/H Transformer (1ph) | 12 | 64 | 13 | Central | SM10
138764 | 2018-08-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27481 opened up due to bird and vines contact | O/H Switchgear | Fused Cutout | 8 | 67 | 9 | Central | 505
138765 | 2018-08-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X23120 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 1 | 214 | 4 | East | 77M1
138766 | 2018-08-14 | Scheduled Outage | Maintenance | 13KV transformer kiosk, KT109 at 1797 Russell Rd. was interupted to disconnect secondary pedestal for repairs, affecting 19 customers. Russell TS (TB15). | None | Secondary Pedestal | 19 | 50 | 16 | East | TB15
138767 | 2018-08-15 | Foreign Interference | Wildlife (Bird/Animal) | replaced blown fuse feeding transformer X49984 (squirrel contact) | O/H Transformer | O/H Transformer (1ph) | 8 | 80 | 11 | South | 200F1
138769 | 2018-08-15 | Defective Equipment | Imminent Failure | KT90 at 114 renova was isolated for replacement due to an oil leak. KT86 also interrupted during switching due to incorrect cable nomenclature. 22 customers affected. Russell (TB14) | U/G Transformer | Padmount (1ph) | 9 | 315 | 47 | East | TB14
138769 | 2018-08-15 | Defective Equipment | Imminent Failure | KT90 at 114 renova was isolated for replacement due to an oil leak. KT86 also interrupted during switching due to incorrect cable nomenclature. 22 customers affected. Russell (TB14) | U/G Transformer | Padmount (1ph) | 22 | 18 | 7 | East | TB14
138770 | 2018-08-15 | Tree Contacts | Broken Branch | Broken Branch on secondary and primary in the backyard at 356 Second Ave. | O/H Conductor | O/H Conductor | 79 | 46 | 61 | Central | SB09
138772 | 2018-08-15 | Lightning | Lightning | GR6 recloser and S23796 at Piperville and Anderson opened a during thunder storm. No direct cause found, lightning reported in the area. 261 customers affected. Lietrim (LTM02) | O/H Conductor | O/H Conductor | 261 | 34 | 148 | East | LTM02
138773 | 2018-08-15 | Scheduled Outage | Construction | TO check ducts in manohole for future upgrade. | None | Duct | 1 | 91 | 2 | Central | UV03
138775 | 2018-08-16 | Tree Contacts | Broken Branch | tree limb fell into customer owned primary causing switch to open at 2975 shea rd. two customers were affected. Richmond north. RHNF1. | O/H Switchgear | Fused Cutout | 2 | 177 | 6 | West | RHNF1
138776 | 2018-08-16 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X48343 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 15 | 36 | 9 | Central | TW12
138777 | 2018-08-16 | Defective Equipment | Imminent Failure | Hydro Ottawa line crews had to force leaking transformer TE182 out of service so that it could be replaced | U/G Transformer | Padmount (1ph) | 7 | 659 | 77 | South | 145F2
138778 | 2018-08-16 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X38559 TO REMOVE SPAN GUY | O/H Transformer | O/H Transformer (1ph) | 5 | 15 | 1 | Central | TD07
138780 | 2018-08-16 | Foreign Interference | Wildlife (Bird/Animal) | A squirrel made contact with the transformer fuse at X20419. This fault went past G901W & G283W and tripped GR6 W which was under holdoff. Hydro Ottawa FOPS crew re-fused the transformer and a Hydro Ottawa 24/7 line crew patrolled and restored all load. | O/H Switchgear | Recloser (1ph) | 100 | 98 | 163 | East | LTM02
138781 | 2018-08-16 | Scheduled Outage | Construction | TD07 overhead from S17060 to EOL was isolated to transfer plant to new poles. 27 customers affected. Lincoln Heights (TD07) | None | O/H Conductor | 27 | 138 | 62 | Central | TD07
138782 | 2018-08-16 | Defective Equipment | Corrosion | To allow Hydro Ottawa 24/7 line crews to repair a defective live line clamp | Pole Attachement | Unknown \ Other | 38 | 36 | 23 | Central | TW22
138783 | 2018-08-16 | Scheduled Outage | Maintenance | planned outage to replace lightning arrestor. | Pole Attachement | Arrester | 10 | 29 | 5 | Central | SR08
138785 | 2018-08-17 | Foreign Interference | Wildlife (Bird/Animal) | A bird made contact with S11651, which is a N/O tie point for TW11 (old TW18) & TW12 circuits. This caused both circuits to trip as they were under hold off. | None | None | 663 | 61 | 674 | Central | TW12
138785 | 2018-08-17 | Foreign Interference | Wildlife (Bird/Animal) | A bird made contact with S11651, which is a N/O tie point for TW11 (old TW18) & TW12 circuits. This caused both circuits to trip as they were under hold off. | None | None | 1342 | 62 | 1387 | Central | TW18
138786 | 2018-08-17 | Scheduled Outage | Maintenance | Remove asbestos clean and torque Russian Embassy | None | None | 1 | 203 | 3 | Central | UD01
138787 | 2018-08-17 | Scheduled Outage | Construction | Transferring Hydro plant to new pole. | None | None | 11 | 242 | 44 | Central | TD07
138788 | 2018-08-18 | Defective Equipment | Imminent Failure | 13KV transformer, PT45 at 2212 Gladwin was isolated and replaced due to leaking oil, 12 customers affected. Russell TS (TB2AL) | U/G Transformer | Padmount (1ph) | 12 | 95 | 19 | East | TB2AL
138789 | 2018-08-18 | Scheduled Outage | Construction | 4KV transformer, P324 at 1665 Apeldoom was isolated to replace pole and transfer plant, affecting 1 customer. Fisher DS (AK10). | None | Pole | 1 | 491 | 8 | Central | AK10
138790 | 2018-08-18 | Scheduled Outage | Construction | Transformer #X33599 isolated by crew to replace a pole | None | None | 5 | 490 | 41 | Central | AK10
138791 | 2018-08-18 | Defective Equipment | Electrical Failure | Fuse opened at X33306 6643 Fallowfield due to a defective transformer. 1 customer affected. Richmond Norht (RHNF3) | O/H Transformer | O/H Transformer (1ph) | 1 | 509 | 8 | West | RHNF3
138792 | 2018-08-19 | Scheduled Outage | Maintenance | Transformer 3193 at 254 Herzberg was isolated to perform soil remediation. 1 customer affected. Kanata 624F5. | None | None | 1 | 325 | 5 | West | 624F5
138794 | 2018-08-19 | Tree Contacts | Other Vegetation | 13KV fuse, S10518 and fused cutout to X34274 were found blown due to vines on equipment, affecting 18 customers. Lincoln Heights TS (TD05) | O/H Switchgear | Fused Cutout | 18 | 50 | 15 | Central | TD05
138795 | 2018-08-20 | Tree Contacts | Broken Branch | S29462 at 199 Lynda Lane opened due to tree contact. 11 cust. Affected. Russell (TB06) | O/H Conductor | O/H Conductor | 11 | 71 | 13 | East | TB06
138796 | 2018-08-20 | Foreign Interference | Wildlife (Bird/Animal) | TW11 & TW12 breakers tripped at Woodroffe TS due to animal contact at S11651, affecting 2019 customers. | None | None | 663 | 11 | 122 | Central | TW12
138796 | 2018-08-20 | Foreign Interference | Wildlife (Bird/Animal) | TW11 & TW12 breakers tripped at Woodroffe TS due to animal contact at S11651, affecting 2019 customers. | None | None | 1356 | 10 | 226 | Central | TW18
138797 | 2018-08-20 | Defective Equipment | Imminent Failure | 13KV transformeer, KT239 at 44 Bramble was isolated and replaced due leaking oil, affecting 9 customers. Albion TS (2204) | U/G Transformer | Kiosk (1ph) | 9 | 475 | 71 | East | 2204
138798 | 2018-08-20 | Human Element | Switching Error | 32 customers on Shea & Fallowfield were interrupted due to an out of phase condition during switching to isolate a section of overhead line. | None | None | 33 | 5 | 3 | West | RHNF1
138800 | 2018-08-20 | Scheduled Outage | Construction | Planned outage to install new service. | None | O/H Service | 22 | 63 | 23 | Central | TW18
138801 | 2018-08-20 | Scheduled Outage | Construction | Planned outage to transfer plant to new pole. | None | Pole | 9 | 83 | 12 | Central | TD07
138802 | 2018-08-20 | Foreign Interference | Wildlife (Bird/Animal) | Blown transformer fuse. | O/H Transformer | O/H Transformer (1ph) | 7 | 72 | 8 | Central | TD06
138804 | 2018-08-20 | Unknown/Other | Unknown | replaced blown fuse feeding transformer x49309 | O/H Transformer | O/H Transformer (1ph) | 8 | 99 | 13 | South | 200F1
138805 | 2018-08-20 | Loss Of Supply | Third Party | 13KV vault, VT1443 at 525 Terminal has failed and oil all over the ground, affecting 1 customer. Overbrook TS (1802) | Vault Equipment | Transformer | 1 | 684 | 11 | East | 1802
138806 | 2018-08-21 | Scheduled Outage | Construction | Temp 41 to end of line on Elmira was isolated to allow crew to replace riser and cable to V359 and transfer plant to new pole. 24 customers were affected. Edwin (UV03) | None | None | 24 | 420 | 168 | Central | UV03
138807 | 2018-08-21 | Scheduled Outage | Construction | Transformer at pole X55540 was isolated at 2291 Edwin Cres to allwo crew to transfer plant to new pole. 12 customers were affected. Edwin (UV02) | None | None | 12 | 211 | 42 | Central | UV02
138808 | 2018-08-21 | Scheduled Outage | Maintenance | Planned outage with Mike from K-Line to disconnect a service and change a switch. | None | O/H Transformer (1ph) | 14 | 31 | 7 | East | AA02
138809 | 2018-08-21 | Scheduled Outage | Construction | Marc Branchaud planned outage for service upgrade. | None | O/H Transformer (1ph) | 13 | 53 | 11 | East | TB06
138810 | 2018-08-21 | Scheduled Outage | Maintenance | Dave Burns planned outage to remove NIU line clamps. | None | O/H Transformer (1ph) | 9 | 210 | 32 | Central | UV02
138811 | 2018-08-21 | Scheduled Outage | Maintenance | Planned outage for transformer replacement. | None | O/H Transformer (1ph) | 11 | 63 | 12 | Central | UL05
138812 | 2018-08-21 | Foreign Interference | Wildlife (Bird/Animal) | REPLACE BLOWN FUSE FEEDING TRANSFORMER X27485 (RACCOON CONTACT) | O/H Transformer | O/H Transformer (1ph) | 10 | 58 | 10 | Central | 505
138813 | 2018-08-21 | Lightning | Lightning | Customer owned pole line at the rear of 15 Steeple Hill was hit by lightning at S1656. | Customer Owned | Customer-Owned | 40 | 120 | 80 | South | 145F3
138814 | 2018-08-21 | Defective Equipment | Defective Equipment/ Material | Cable fault between S10 and transformer # 3085 red phase. | U/G Cable | XLPE | 61 | 110 | 112 | West | 39F3
138815 | 2018-08-22 | Scheduled Outage | Vegetation Management | Blown transformer fuse at X33204 Crew reports transformer is covered in vines. | O/H Transformer | O/H Transformer (1ph) | 7 | 73 | 9 | Central | TD05
138816 | 2018-08-22 | Defective Equipment | Mechanical Failure | To allow a Hydro Ottawa line crew to change a leaking transformer and perform soil remediation. | U/G Transformer | Padmount (1ph) | 9 | 626 | 94 | South | 84F5
138817 | 2018-08-22 | Scheduled Outage | Construction | Switch S12092 to EOL was isolated to allow crew to install new 3 phase primary conductor on Caroline. Hinchey (TH01). 50 customers were affected. | None | None | 50 | 213 | 178 | Central | TH01
138819 | 2018-08-22 | Foreign Interference | Wildlife (Bird/Animal) | blown transformer fuse due to squirrel contact. | O/H Transformer | O/H Transformer (1ph) | 17 | 167 | 47 | Central | TW17
138820 | 2018-08-22 | Foreign Interference | Wildlife (Bird/Animal) | Switch S29290 R phase blew due to squirrel contact at 333 River Rd. 1 customer was affected. Limebank (7F2) | O/H Switchgear | Fused Cutout | 1 | 180 | 3 | East | 7F2
138821 | 2018-08-21 | Loss Of Supply | Third Party | 8KV customer owned Overhead and switch, S1656 at 5 Steeple hill was damaged due to lightning strike, affecting 2 customers. Jockvale DS (145F3) | O/H Switchgear | Fused Cutout | 2 | 914 | 30 | South | 145F3
138822 | 2018-08-22 | Scheduled Outage | Construction | Crews replacing a pole. | None | Pole | 11 | 278 | 51 | Central | UL05
138823 | 2018-08-22 | Defective Equipment | Mechanical Failure | Defective switch gear SC27 at Johnston and Baslaw caused the TA09 (2206) circuit to trip. 3522 customers were affected. Albion (2206) | U/G Switchgear | Live-Front | 158 | 87 | 229 | East | 2206
138823 | 2018-08-22 | Defective Equipment | Mechanical Failure | Defective switch gear SC27 at Johnston and Baslaw caused the TA09 (2206) circuit to trip. 3522 customers were affected. Albion (2206) | U/G Switchgear | Live-Front | 545 | 54 | 490 | East | 2206
138823 | 2018-08-22 | Defective Equipment | Mechanical Failure | Defective switch gear SC27 at Johnston and Baslaw caused the TA09 (2206) circuit to trip. 3522 customers were affected. Albion (2206) | U/G Switchgear | Live-Front | 3522 | 94 | 5518 | East | 2206
138825 | 2018-08-22 | Defective Equipment | Electrical Failure | EPWF4 breaker tripped due to defective cable at 15 Kidgrove , affecting 1310 customers. Epworth DS | U/G Cable | XLPE | 10 | 47 | 8 | South | EPWF4
138825 | 2018-08-22 | Defective Equipment | Electrical Failure | EPWF4 breaker tripped due to defective cable at 15 Kidgrove , affecting 1310 customers. Epworth DS | U/G Cable | XLPE | 20 | 130 | 43 | South | EPWF4
138825 | 2018-08-22 | Defective Equipment | Electrical Failure | EPWF4 breaker tripped due to defective cable at 15 Kidgrove , affecting 1310 customers. Epworth DS | U/G Cable | XLPE | 32 | 238 | 127 | South | EPWF4
138825 | 2018-08-22 | Defective Equipment | Electrical Failure | EPWF4 breaker tripped due to defective cable at 15 Kidgrove , affecting 1310 customers. Epworth DS | U/G Cable | XLPE | 1310 | 25 | 546 | South | EPWF4
138827 | 2018-08-22 | Foreign Interference | Foreign Objects | Metallic balloon removed from overhead and switch S15700 W closed. | Unknown \ Other | Unknown \ Other | 213 | 44 | 156 | Central | TW22
138828 | 2018-08-22 | Unknown/Other | Unknown | S26669W & B found open. Fault indicators were clear, no obvious cause at S26669. Fuses replaced & closed restoring all load. 206 customers affected. Bilberry 77M1. | None | None | 206 | 80 | 275 | East | 77M1
138832 | 2018-08-23 | Scheduled Outage | Vegetation Management | Overhead circuit from X31395 to EOL at R of 1 Cobalt Ave. was isolated for tree trimming. 14 customers affected. Bronson (SB02) | None | O/H Conductor | 14 | 241 | 56 | Central | SB02
138833 | 2018-08-24 | Defective Equipment | Electrical Failure | SW1563 inspected and CB3 at SC23 closed to restore power, 24/7 report switch gear has black marks inside. | U/G Switchgear | Gas-Insulated Dead Front | 4 | 99 | 7 | East | 2203
138836 | 2018-08-24 | Defective Equipment | Defective Equipment/ Material | Crew had to open X35808 to resag wires on open bus | O/H Transformer | O/H Transformer (1ph) | 10 | 10 | 2 | South | 190F5
138838 | 2018-08-25 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X27796 TO TRANSFER HYDRO PLANTE | None | O/H Transformer (1ph) | 12 | 150 | 30 | East | UQ07
138839 | 2018-08-25 | Defective Equipment | Electrical Failure | A cable fault caused G242 W phase to open. Hydro Ottawa 24/7 line crews sectionalized the circuit and restored power in stages. | U/G Cable | XLPE | 25 | 30 | 12 | East | 77M1
138839 | 2018-08-25 | Defective Equipment | Electrical Failure | A cable fault caused G242 W phase to open. Hydro Ottawa 24/7 line crews sectionalized the circuit and restored power in stages. | U/G Cable | XLPE | 62 | 61 | 63 | East | 77M1
138839 | 2018-08-25 | Defective Equipment | Electrical Failure | A cable fault caused G242 W phase to open. Hydro Ottawa 24/7 line crews sectionalized the circuit and restored power in stages. | U/G Cable | XLPE | 189 | 76 | 239 | East | 77M1
138840 | 2018-08-25 | Unknown/Other | Unknown | REPLACED BLOWN FUSE FEEDING TRANSFORMER X34086 (NO APPARENT CAUSE) | O/H Transformer | O/H Transformer (1ph) | 8 | 91 | 12 | Central | TH01
138841 | 2018-08-25 | Scheduled Outage | Maintenance | Transformer X24456 at 2470 St. Joseph was isolated to allow crew to replace defective hot line clamp. 16 customers were affected. Billberry (77M2) | None | Hot-Line Clamp | 16 | 17 | 5 | East | 77M2
138842 | 2018-08-26 | Loss Of Supply | Transmission Planned | To allow Hydro One to safely switch Orleans TS from 230Kv supply to 115Kv supply. 3616 Hydro Ottawa customers affected for 4 minutes on the 325M8 feeder. | None | None | 3616 | 4 | 241 | East | 325M8
138843 | 2018-08-26 | Defective Equipment | Electrical Failure | Mechanical catastrophic failure of X17218 caused the transformer fuse to open. The transformer oil leaked due to failure. | O/H Transformer | O/H Transformer (1ph) | 3 | 231 | 12 | East | 77M5
138844 | 2018-08-27 | Defective Equipment | Imminent Failure | To replace defective transformer. | U/G Transformer | Padmount (1ph) | 8 | 485 | 65 | East | 6F10
138846 | 2018-08-27 | Scheduled Outage | Maintenance | Truck 1108 To transfer plant on X29846 | None | O/H Transformer (1ph) | 18 | 205 | 62 | Central | TR09
138847 | 2018-08-27 | Scheduled Outage | Construction | Truck 1108 To transfer plant on X29846, X29879, X29880 | O/H Transformer | O/H Transformer (1ph) | 30 | 90 | 45 | Central | TR09
138849 | 2018-08-27 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X37198 TO REPLACE ARRESTER | None | O/H Transformer (1ph) | 4 | 57 | 4 | West | JKGF5
138850 | 2018-08-27 | Tree Contacts | Tree Growth/ Untrimmed Tree | Tree contact. | O/H Transformer | O/H Transformer (1ph) | 9 | 109 | 16 | South | 200F3
138851 | 2018-08-28 | Scheduled Outage | Maintenance | transformer at 22 the Masters drive was isolated for crew to make repairs to secondary pedestal. 9 customers were affected. Albion 2211 | None | None | 9 | 122 | 18 | East | 2211
138852 | 2018-08-28 | Defective Equipment | Imminent Failure | Leaking transformer TP8510 was forced out of service to allow a Hydro Ottawa line crew to replace it. 9 customers were affected. | U/G Transformer | Padmount (1ph) | 9 | 339 | 51 | East | 77M5
138853 | 2018-08-28 | Foreign Interference | Wildlife (Bird/Animal) | Blown transformer fuse due to squirrel contact. | O/H Transformer | O/H Transformer (1ph) | 8 | 146 | 19 | East | TB06
138854 | 2018-08-28 | Unknown/Other | Unknown | Cause unknown. | O/H Switchgear | Inline Switch | 3 | 118 | 6 | West | BECKF2
138855 | 2018-08-28 | Scheduled Outage | Maintenance | Planned outage to transfer new plant. | O/H Conductor | O/H Conductor | 14 | 175 | 41 | Central | TW18
138858 | 2018-08-28 | Defective Equipment | Defective Equipment/ Material | Defective line clamp. | None | None | 64 | 19 | 20 | East | 4801F8
138860 | 2018-08-29 | Unknown/Other | Unknown | Not yet known. | O/H Switchgear | Recloser (1ph) | 261 | 64 | 278 | East | LTM02
138861 | 2018-08-29 | Defective Equipment | Imminent Failure | Leaking transformer TP9762 was forced out of service to allow a Hydro Ottawa line crew to replace the transformer. | U/G Transformer | Padmount (1ph) | 19 | 274 | 87 | East | CYRF4
138863 | 2018-08-29 | Loss Of Supply | Transmission Inadvertent | A server lightning storm went through the area which caused the S7M to trip affecting Marchwood,Fallowfield,Richmond S and the Bridlewood station affecting 25670 customers for 15 minutes | None | None | 1448 | 15 | 362 | West | S7M (Richmond MTS)
138863 | 2018-08-29 | Loss Of Supply | Transmission Inadvertent | A server lightning storm went through the area which caused the S7M to trip affecting Marchwood,Fallowfield,Richmond S and the Bridlewood station affecting 25670 customers for 15 minutes | None | None | 2256 | 15 | 564 | West | S7M (Bridlewood MTS - T1/T2)
138863 | 2018-08-29 | Loss Of Supply | Transmission Inadvertent | A server lightning storm went through the area which caused the S7M to trip affecting Marchwood,Fallowfield,Richmond S and the Bridlewood station affecting 25670 customers for 15 minutes | None | None | 5975 | 15 | 1494 | West | S7M (Marchwood MTS)
138863 | 2018-08-29 | Loss Of Supply | Transmission Inadvertent | A server lightning storm went through the area which caused the S7M to trip affecting Marchwood,Fallowfield,Richmond S and the Bridlewood station affecting 25670 customers for 15 minutes | None | None | 15993 | 15 | 3998 | South | S7M (Fallowfield - T1/T2)
138864 | 2018-08-29 | Lightning | Lightning | heavy lightning and rain were present when the 140F4 breaker opened. 1316 customers were affected. Barrhaven 140F4 | None | None | 1316 | 10 | 219 | South | 140F4
138865 | 2018-08-29 | Lightning | Lightning | heavy lightning and rain were present when the FAL01 breaker opened. Circuit to be patrolled. 2764 customers were affected. Fallowfield FAL01 | None | None | 2764 | 10 | 461 | South | FAL01
138866 | 2018-08-29 | Lightning | Lightning | heavy lightning and rain were present when the FAL02 circuit opened. Circuit to be patrolled. 7830 customers were affected. Fallowfield FAL02 | None | None | 7830 | 10 | 1305 | South | FAL02
138868 | 2018-08-29 | Defective Equipment | Electrical Failure | A suspect cable fault bet transformers TP2955 to SC2000 in the Kelly Farm Dr/Creston Valley area affecting 83 customers for 100 minutes on the LTM01 circuit | U/G Cable | XLPE | 83 | 100 | 138 | East | LTM01
138869 | 2018-08-29 | Tree Contacts | Falling Tree | A K-line line crew had to isolate a section of O/H line on the CASF2 from S19877 to E.O.L, so a tree could be safely removed from the O/H. | None | None | 26 | 42 | 18 | East | CAS-F2
138870 | 2018-08-29 | Lightning | Lightning | A lightning storm caused JKGF4 to auto-reclose, damaged RX2060 and caused it to trip. A line crew inspected the recloser and patrolled the line. Load was picked up through RX2060-L1 | O/H Switchgear | Recloser (3ph) | 215 | 197 | 706 | West | JKGF4
138871 | 2018-08-29 | Lightning | Lightning | No apparent cause found. Lightning storm is suspected | O/H Switchgear | Fused Cutout | 1 | 82 | 1 | West | RHNF3
138872 | 2018-08-29 | Human Element | Improper Equipment/Tool/ Maintenance | To make repairs in Metering CT. | Customer Owned | Customer-Owned | 1 | 291 | 5 | South | 84F5
138873 | 2018-08-29 | Foreign Interference | Vehicle | MVA broke sky wire and wrapped it into 5408 circuit | O/H Conductor | Unknown \ Other | 0 | 143 | 0 | Central | 5407
138873 | 2018-08-29 | Foreign Interference | Vehicle | MVA broke sky wire and wrapped it into 5408 circuit | O/H Conductor | Unknown \ Other | 417 | 305 | 2120 | Central | 5408
138873 | 2018-08-30 | Foreign Interference | Vehicle | MVA broke sky wire and wrapped it into 5408 circuit | O/H Conductor | Unknown \ Other | 95 | 96 | 152 | Central | TD12
138873 | 2018-08-30 | Foreign Interference | Vehicle | MVA broke sky wire and wrapped it into 5408 circuit | O/H Conductor | Unknown \ Other | 385 | 162 | 1040 | Central | TD12
138873 | 2018-08-30 | Foreign Interference | Vehicle | MVA broke sky wire and wrapped it into 5408 circuit | O/H Conductor | Unknown \ Other | 462 | 162 | 1247 | Central | 5407
138874 | 2018-08-30 | Defective Equipment | Electrical Failure | White phase fuse was found open at S11752. OnCall crews check under ground cable and refused RWB and closed switch. Switch opened during the T-storm. Crews reports 2 phases blown when TP6862 was energized. Transformer is now smoking. | U/G Transformer | Kiosk (3ph) | 1 | 923 | 15 | South | FAL02
138875 | 2018-08-30 | Scheduled Outage | Forced Switching | Transformer KT109 at 1797 Russell was isolated to allow crew to replace defective pedastal. 20 customers were affected. Russell (TB15) | None | None | 20 | 165 | 55 | East | TB15
138877 | 2018-08-30 | Scheduled Outage | Construction | To allow a Hydro Ottawa line crew to decommission K994 & install a new 75Kva mini-pad, TP127780. | None | None | 16 | 173 | 46 | East | SO06
138878 | 2018-08-30 | Scheduled Outage | Construction | TRANSFER TO PLANT X46648 AND X33636 | None | Pole | 20 | 315 | 105 | Central | UL05
138879 | 2018-08-30 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X 27348 opened due to animal contact | O/H Transformer | O/H Transformer (1ph) | 10 | 44 | 7 | East | TB06
138880 | 2018-08-31 | Defective Equipment | Electrical Failure | Red phase cable fault between TP10772 and TP10773 on Ridgebrook | U/G Cable | XLPE | 38 | 74 | 47 | East | 8F3
138881 | 2018-08-31 | Scheduled Outage | Construction | Dave burns scheduled outage to transfer to plant X33990 | O/H Transformer | O/H Transformer (1ph) | 4 | 180 | 12 | Central | UV04
138882 | 2018-09-01 | Scheduled Outage | Maintenance | Planned outage to replace defective switch. | None | Fused Cutout | 8 | 61 | 8 | South | 84F2
138883 | 2018-09-01 | Defective Equipment | Electrical Failure | Suspected cable fault. | U/G Cable | XLPE | 13 | 30 | 6 | West | JKGF5
138883 | 2018-09-01 | Defective Equipment | Electrical Failure | Suspected cable fault. | U/G Cable | XLPE | 19 | 125 | 40 | West | JKGF5
138884 | 2018-09-02 | Loss Of Supply | Transmission Inadvertent | Animal contact caused Y bus to trip on differential. | Station Equipment | Primary Switchgear | 2 | 6 | 0 | West | A9M4
138884 | 2018-09-02 | Loss Of Supply | Transmission Inadvertent | Animal contact caused Y bus to trip on differential. | Station Equipment | Primary Switchgear | 5892 | 6 | 589 | West | A9M1
138885 | 2018-09-02 | Tree Contacts | Other Vegetation | Vine growth. Replaced cutout. | O/H Switchgear | Fused Cutout | 8 | 100 | 13 | South | 49F6
138886 | 2018-09-02 | Scheduled Outage | Maintenance | Planned outage to replace switch and hot line clamp. | None | Fused Cutout | 9 | 140 | 21 | Central | TW22
138889 | 2018-09-04 | Scheduled Outage | Construction | 8kv transformer TE0300 ay 1 Haanel was isolated for pole replacement, affecting 1 customer. Stafford DS (200F1) | None | None | 1 | 507 | 8 | South | 200F1
138890 | 2018-09-04 | Unknown/Other | Unknown | Bilberry 77M6 tripped. Investigated customer report of flash & loud bang, no problem found. Load restored in stages. 4826 customers affected. | None | None | 2287 | 29 | 1105 | East | 77M6
138890 | 2018-09-04 | Unknown/Other | Unknown | Bilberry 77M6 tripped. Investigated customer report of flash & loud bang, no problem found. Load restored in stages. 4826 customers affected. | None | None | 4303 | 13 | 932 | East | 77M6
138890 | 2018-09-04 | Unknown/Other | Unknown | Bilberry 77M6 tripped. Investigated customer report of flash & loud bang, no problem found. Load restored in stages. 4826 customers affected. | None | None | 4826 | 18 | 1448 | East | 77M6
138891 | 2018-09-04 | Defective Equipment | Electrical Failure | A cable fault on 8F1 R phase caused S26248 R to open. Power was restored in stages. 75 customers were affected | U/G Cable | XLPE | 9 | 29 | 4 | East | 8F1
138891 | 2018-09-04 | Defective Equipment | Electrical Failure | A cable fault on 8F1 R phase caused S26248 R to open. Power was restored in stages. 75 customers were affected | U/G Cable | XLPE | 37 | 40 | 25 | East | 8F1
138891 | 2018-09-04 | Defective Equipment | Electrical Failure | A cable fault on 8F1 R phase caused S26248 R to open. Power was restored in stages. 75 customers were affected | U/G Cable | XLPE | 75 | 226 | 282 | East | 8F1
138892 | 2018-09-05 | Tree Contacts | Tree Growth/ Untrimmed Tree | A 24/7 line crew found S16751 R blown. The circuit was patrolled to end of line. No apparent cause found. The crew reports that the radial circuit is heavily treed. 4 customers affected. | O/H Switchgear | Fused Cutout | 4 | 78 | 5 | East | BLKF5
138894 | 2018-09-05 | Scheduled Outage | Construction | TE119 & TE120 on Woodhill were isolated for transformer & cable replacement. 21 customers affected. Balckburn BLKF4. | None | None | 21 | 492 | 172 | East | BLKF4
138896 | 2018-09-05 | Scheduled Outage | Maintenance | Outage to replace barrier board and change cut outs at S26074 | None | None | 15 | 126 | 32 | East | AQ04
138897 | 2018-09-05 | Scheduled Outage | Maintenance | Isolation for customer owned vault maintenance. | None | None | 1 | 171 | 3 | Central | SB16
138898 | 2018-09-05 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33404 TO TRANSFER HYDRO PLANT TO NEW TRANSFORMER X58914 | O/H Transformer | O/H Transformer (1ph) | 11 | 240 | 44 | Central | UV05
138899 | 2018-09-05 | Scheduled Outage | Construction | Sam Gibson and crew to have transformer TP6012 isolated to replace. 10 customers on the 145F1 affected. | None | None | 10 | 466 | 78 | South | 145F1
138900 | 2018-09-05 | Adverse Weather | Extreme Wind | SR07 (321cust.) and SR08 (438 cust.) circuit breakers tripped during storm conditions. Fire and police were called and nothing had been reported. | Unknown \ Other | Unknown \ Other | 321 | 8 | 43 | Central | SR07
138900 | 2018-09-05 | Adverse Weather | Extreme Wind | SR07 (321cust.) and SR08 (438 cust.) circuit breakers tripped during storm conditions. Fire and police were called and nothing had been reported. | Unknown \ Other | Unknown \ Other | 438 | 8 | 58 | Central | SR08
138901 | 2018-09-05 | Tree Contacts | Broken Branch | 77M6 circuit breaker tripped due to inclement weather conditions. 3,874 customers were affected. | Unknown \ Other | Unknown \ Other | 0 | 5 | 0 | East | 77M6
138901 | 2018-09-05 | Tree Contacts | Broken Branch | 77M6 circuit breaker tripped due to inclement weather conditions. 3,874 customers were affected. | Unknown \ Other | Unknown \ Other | 2048 | 1 | 34 | East | 77M6
138901 | 2018-09-05 | Tree Contacts | Broken Branch | 77M6 circuit breaker tripped due to inclement weather conditions. 3,874 customers were affected. | Unknown \ Other | Unknown \ Other | 3874 | 23 | 1485 | East | 77M6
138901 | 2018-09-05 | Tree Contacts | Broken Branch | 77M6 circuit breaker tripped due to inclement weather conditions. 3,874 customers were affected. | Unknown \ Other | Unknown \ Other | 3874 | 108 | 6973 | East | 77M6
138903 | 2018-09-05 | Lightning | Lightning | Adverse weather | None | None | 174 | 45 | 130 | West | 28F2
138904 | 2018-09-05 | Lightning | Lightning | Adverse weather | None | None | 215 | 40 | 143 | West | 28F2
138904 | 2018-09-05 | Lightning | Lightning | Adverse weather | None | None | 268 | 15 | 67 | West | 28F2
138904 | 2018-09-05 | Lightning | Lightning | Adverse weather | None | None | 290 | 93 | 450 | West | 28F2
138904 | 2018-09-05 | Lightning | Lightning | Adverse weather | None | None | 323 | 62 | 334 | West | 28F2
138904 | 2018-09-05 | Lightning | Lightning | Adverse weather | None | None | 444 | 17 | 126 | West | 28F2
138904 | 2018-09-05 | Lightning | Lightning | Adverse weather | None | None | 444 | 265 | 1961 | West | 28F2
138904 | 2018-09-06 | Lightning | Lightning | Adverse weather | None | None | 444 | 3 | 22 | West | 28F2
138905 | 2018-09-05 | Loss Of Supply | Transmission Inadvertent | Lightning | Unknown \ Other | Unknown \ Other | 1556 | 5 | 130 | East | 325M8
138906 | 2018-09-05 | Tree Contacts | Broken Branch | Part of 77M6 overhead circuit on St. Joseph isolated to remove branch from overhead. 524 customers affected. Bilberry (77M6) | O/H Conductor | O/H Conductor | 524 | 2 | 17 | East | 77M6
138907 | 2018-09-05 | Scheduled Outage | Forced Switching | AC07 circuit isolated due to a wire down at 135 Jolliet. 800 customers affected. Dagmar (AC07) | None | None | 180 | 394 | 1182 | East | AC07
138907 | 2018-09-05 | Scheduled Outage | Forced Switching | AC07 circuit isolated due to a wire down at 135 Jolliet. 800 customers affected. Dagmar (AC07) | None | None | 800 | 72 | 960 | East | AC07
138908 | 2018-09-05 | Lightning | Lightning | S20193 at 181 Allison crew found 2 fuses opened due to broken conductor at 464 Ancaster. 334 customers affected. Lincoln Heights (TD06) | O/H Conductor | O/H Conductor | 334 | 509 | 2833 | Central | TD06
138909 | 2018-09-05 | Lightning | Lightning | S13521 opened during adverse weather. No direct cause found. 28 customers affected. Lincoln Heights (TD06) | O/H Conductor | O/H Conductor | 28 | 605 | 282 | Central | TD06
138911 | 2018-09-05 | Lightning | Lightning | Lightning | O/H Transformer | O/H Transformer (1ph) | 12 | 554 | 111 | West | 624F6
138912 | 2018-09-05 | Tree Contacts | Falling Tree | Tree on overhead line. | O/H Switchgear | Fused Cutout | 1 | 530 | 9 | West | 624F6
138914 | 2018-09-05 | Adverse Weather | Extreme Wind | Fuse at X23699 at 30 Bedford opened when the secondary bus wrapped together. X23614 on Kilarney isolated to make repairs. 17 customers affected. Beechwood (UB07) | Secondary \ Service | O/H Service | 17 | 429 | 122 | East | UB07
138915 | 2018-09-05 | Lightning | Lightning | Lightning | O/H Transformer | O/H Transformer (1ph) | 1 | 885 | 15 | South | 49F6
138916 | 2018-09-05 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X29959 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 6 | 970 | 97 | Central | TD14
138917 | 2018-09-05 | Defective Equipment | Defective Equipment/ Material | Transformer #X32669 opened up due to defective switch | O/H Switchgear | Fused Cutout | 12 | 1036 | 207 | Central | UV03
138918 | 2018-09-06 | Scheduled Outage | Maintenance | A 13Kv transformer KT42 at 62 Fireside Cres was isolated by the crew to allow them remove damage barrier boards and change primary insulators affecting 15 customer of the ELW07 circuit for 127 minutes | None | Kiosk (1ph) | 15 | 127 | 32 | East | ELW07
138919 | 2018-09-06 | Scheduled Outage | Maintenance | A 27Kv transformer TP5815 at 3589 Cambrian was isolated by the crew to allow them to replace a leaking transformer affecting 12 customers for 134 minutes on the Fal03 circuit | U/G Transformer | Padmount (1ph) | 12 | 134 | 27 | South | FAL03
138920 | 2018-09-06 | Defective Equipment | Defective Equipment/ Material | Transformer #44541 opened up due to defective transformer, has been replaced | O/H Transformer | O/H Transformer (1ph) | 41 | 319 | 218 | East | AC07
138921 | 2018-09-06 | Scheduled Outage | Construction | At 09:25am TE121 was isolated for transformer and cable replacement. 12 customers affected. Blackburn. (BLKF4) | None | None | 12 | 414 | 83 | East | BLKF4
138922 | 2018-09-05 | Defective Equipment | Mechanical Failure | Transformer #X35808 opened up due to found secondary lead at transformer X35808 burned off and had fallen onto bottom wire blowing fuse | Secondary \ Service | O/H Service | 10 | 889 | 148 | South | 190F5
138923 | 2018-09-06 | Scheduled Outage | Maintenance | At 09:41am transformer 1946 was isolated for soil remediation. 11 customers affected. Terry Fox (TFXF1) | None | None | 11 | 450 | 82 | West | TFXF1
138924 | 2018-09-06 | Scheduled Outage | Vegetation Management | The O/H on Tower rd was isolated to allow the tree contractor do some tree trimming affecting 19 customers for 345 minutes on the EPWF1 circuit | O/H Conductor | O/H Conductor | 19 | 345 | 109 | South | EPWF1
138925 | 2018-09-06 | Defective Equipment | Imminent Failure | transformers at 196, and 241 Provender were isolated to allow crew to replace both leaking transformers. 40 customers were affected. Overbrook TO2UB | None | None | 40 | 200 | 133 | East | TO2UB
138926 | 2018-09-06 | Scheduled Outage | Maintenance | Due to flickering lights crew isolated transformer X33657 to replaced sec paddle at trans and did a big haircut on trees | O/H Transformer | O/H Transformer (1ph) | 6 | 45 | 4 | Central | TW22
138927 | 2018-09-06 | Lightning | Lightning | REPLACED 3 PHASE TRANSFORMER BANK X33150 (HIT BY LIGHTNING) | O/H Transformer | O/H Transformer (3ph) | 1 | 826 | 14 | West | 28F2
138930 | 2018-09-07 | Scheduled Outage | Maintenance | A 4Kv transformer K770 at 2829 Springland was isolated to allow the crew repair hot primary connection affecting 8 customers for 82 minutes on the UZ02 circuit. | None | Kiosk (1ph) | 8 | 82 | 11 | East | UZ02
138931 | 2018-09-07 | Scheduled Outage | Vegetation Management | crew isolated overhead section affecting customers on Spartan, and fullerton, and Brant, to remove tree from overhead. 51 customers were affected. Church AA05. No outage Notifications given. | None | None | 51 | 89 | 76 | East | AA05
138932 | 2018-09-07 | Defective Equipment | Imminent Failure | crew isolated transformer at 24 Springfield to replace leaking transformer. 13 customers wwere affected. Vaughan UG05. | None | None | 13 | 159 | 34 | East | UG05
138933 | 2018-09-07 | Defective Equipment | Imminent Failure | At 08:56am transformer 2166 was isolated to replace it due to a leak. 12 customers affected. Kanata (624F5) | None | None | 12 | 162 | 32 | West | 624F5
138935 | 2018-09-07 | Defective Equipment | Electrical Failure | Cable fault located between SC6915-L2 and SC6698-L1 | U/G Cable | Unknown \ Other | 1 | 222 | 4 | Central | 305
138936 | 2018-09-08 | Defective Equipment | Mechanical Failure | Fire Department reported sparking wires. S18381 hot line clamp replaced. | O/H Switchgear | Fused Cutout | 22 | 16 | 6 | Central | TD01
138937 | 2018-09-10 | Defective Equipment | Imminent Failure | 27KV transformer, TE1989 was replaced due to leaking oil, affecting 5 customers. Bilberry (77M6) | U/G Transformer | Padmount (1ph) | 5 | 90 | 8 | East | 77M6
138938 | 2018-09-10 | Foreign Interference | Wildlife (Bird/Animal) | X16011 R phase & G260 R phase was found blown. A 24/7 line crew patrolled the radial O/H and found a dead bird at X16011. | O/H Switchgear | Fused Cutout | 10 | 241 | 40 | East | LTM01
138939 | 2018-09-10 | Scheduled Outage | Maintenance | REPLACE TRANSFORMER FROM A 50KVA TO A 75. X28275 | O/H Transformer | O/H Transformer (1ph) | 14 | 90 | 21 | Central | AH14
138941 | 2018-09-10 | Defective Equipment | Mechanical Failure | Transformer #X24054 isolated by crew due to primary wires on ground (failed dead end insulator) | None | None | 6 | 90 | 9 | East | AA06
138942 | 2018-09-11 | Scheduled Outage | Maintenance | Isolated to allow crew to repair a secondary connection in the transformer. | None | Kiosk (1ph) | 12 | 36 | 7 | East | AE03
138943 | 2018-09-11 | Defective Equipment | Imminent Failure | planned outage to allow crew to replace leaking transformer | None | None | 9 | 243 | 36 | East | 77M5
138945 | 2018-09-11 | Scheduled Outage | Construction | planned outage to repair transformer base | None | None | 13 | 72 | 16 | East | 4801F8
138946 | 2018-09-11 | Scheduled Outage | Maintenance | Planned outage to transfer HOL plant. | None | None | 11 | 20 | 4 | Central | UV07
138947 | 2018-09-11 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35920 TO REPLACE SWITCH AND ARRESTER | O/H Transformer | O/H Transformer (1ph) | 13 | 60 | 13 | Central | TD06
138948 | 2018-09-11 | Scheduled Outage | Maintenance | Planned outage with Mike Byers to transfer plant to new pole. | None | None | 11 | 32 | 6 | Central | UV05
138949 | 2018-09-11 | Scheduled Outage | Maintenance | REPLACED SWITCH AND ARRESTER FEEDING TRANSFORMER X35908 | O/H Transformer | O/H Transformer (1ph) | 8 | 25 | 3 | Central | TD06
138950 | 2018-09-11 | Scheduled Outage | Maintenance | Planned outage with Mike Byers to transfer plant to new pole. | None | None | 6 | 31 | 3 | Central | UV05
138952 | 2018-09-11 | Scheduled Outage | Maintenance | Transferring hydro plant to new pole. | None | None | 12 | 50 | 10 | Central | UV07
138953 | 2018-09-11 | Scheduled Outage | Maintenance | Planned outage for Mike Byers to transfer hydro plant. | None | None | 9 | 53 | 8 | Central | UV03
138955 | 2018-09-11 | Scheduled Outage | Construction | Transformer #X23096 isolated by Paul from K-Line to transfer plant | None | None | 13 | 40 | 9 | East | BCHF5
138956 | 2018-09-11 | Defective Equipment | Electrical Failure | SO12 breaker auto reclosed. Blown arrestor at 388 Donald | Pole Attachement | Arrester | 568 | 1 | 9 | East | SO12
138957 | 2018-09-11 | Scheduled Outage | Vegetation Management | Transformer #X32852 isolated by crew to remove vines | None | None | 8 | 33 | 4 | South | 170F1
138958 | 2018-09-11 | Scheduled Outage | Construction | Transformer #X24833 isolated by crew to replace triplex and connections | None | None | 10 | 49 | 8 | East | UQ05
138959 | 2018-09-12 | Unknown/Other | Unknown | Not yet known. | None | None | 850 | 9 | 128 | East | 77M2
138960 | 2018-09-10 | Loss Of Supply | Transmission Inadvertent | Hydro One reported an outage on South Gloucester 56F1 due to equipment failure on their system. No further details were provided. | None | None | 157 | 88 | 230 | East | 56F1
138964 | 2018-09-12 | Scheduled Outage | Vegetation Management | Planned outage for Paul Bortolotti with K-line for tree trimmers. | None | None | 19 | 45 | 14 | East | AA04
138965 | 2018-09-12 | Scheduled Outage | Construction | To allow crews to move plant to new poles. | None | O/H Conductor | 18 | 96 | 29 | Central | UV02
138966 | 2018-09-12 | Scheduled Outage | Construction | Sam Gibson and crew to have transformer NPTE1267 at 71 Holitman out of service to replace because of leaking. 8 customers on the 140F5 will be affected. | None | None | 8 | 496 | 66 | South | 140F5
138967 | 2018-09-12 | Scheduled Outage | Construction | Planned outage with Dave Burns to transfer HOL plant. | None | None | 15 | 97 | 24 | Central | UV02
138969 | 2018-09-12 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X35779 TO REPLACE SWITCH AND ARRESTER | None | O/H Transformer (1ph) | 12 | 75 | 15 | Central | TD06
138971 | 2018-09-12 | Scheduled Outage | Vegetation Management | Planned outage to transfer plant for tree trimmers. | None | O/H Service | 19 | 44 | 14 | East | AA04
138972 | 2018-09-12 | Scheduled Outage | Construction | Transformer #X20170 isolated by Shawn Evans from Kline to transfer plant | None | None | 4 | 15 | 1 | East | LTM02
138974 | 2018-09-12 | Defective Equipment | Electrical Failure | The 39F3 R phase between S10 & 3085R faulted. | U/G Cable | XLPE | 61 | 314 | 319 | West | 39F3
138975 | 2018-09-13 | Scheduled Outage | Construction | Kyle Baker and crew to have Transformer TE334 isolated to replace as per Job# 6499. 14 customers on the 200F5 to be affected. | None | None | 14 | 573 | 134 | South | 200F5
138976 | 2018-09-13 | Defective Equipment | Imminent Failure | 13KV transformer kiosk, K520 replaced due to leakking oil, affecting 18 customers. Overbrook TS (TO3UB) | None | Kiosk (1ph) | 18 | 298 | 89 | East | TO3UB
138977 | 2018-09-13 | Scheduled Outage | Vegetation Management | 8KV overhead section on Starwood was isolated to remove large limbs from tree, affecting 16 customers. Epworth DS (EWPF1) | None | None | 16 | 305 | 81 | South | EPWF1
138979 | 2018-09-13 | Scheduled Outage | Maintenance | Customer owned vault maintenance. | None | None | 1 | 155 | 3 | Central | 5401
138981 | 2018-09-13 | Scheduled Outage | Maintenance | Planned outage to replace switch and arrestor. | O/H Switchgear | Fused Cutout | 9 | 70 | 10 | Central | TD06
138982 | 2018-09-14 | Defective Equipment | Defective Equipment/ Material | X36144 three phase bank transformers was isolated to allow crew to replace a defective transfomer on the three phase bank. Epworth (EPWF4). 1 customer was affected. | O/H Transformer | O/H Transformer (3ph) | 1 | 917 | 15 | South | EPWF4
138983 | 2018-09-14 | Scheduled Outage | Construction | Transformer PT112 at 1862 Bromley was isolated to allow crew to repalce porcelain switches and arrestors. 6 customers were affected. Lincoln (TD06) | None | None | 6 | 69 | 7 | Central | TD06
138984 | 2018-09-14 | Foreign Interference | Wildlife (Bird/Animal) | Racoon contact. Animal guard needs to be installed due to dumpster at base of pole | Unknown \ Other | Unknown \ Other | 24 | 105 | 42 | East | LTM01
138986 | 2018-09-14 | Defective Equipment | Imminent Failure | Replace defective transformer. | None | None | 11 | 520 | 95 | East | BCHF8
138988 | 2018-09-14 | Scheduled Outage | Maintenance | Transformers isolated to repair hot secondary connection | None | Unknown \ Other | 7 | 43 | 5 | East | UZ06
138989 | 2018-09-14 | Defective Equipment | Imminent Failure | 28kv transformer , TP11563 at 10C Jaguar PVT replaced due to leaking oil, affecting 26 customers. Initially 64 customers were affected dure the switching process. Terry Fox MTS (TFXF4) | None | Padmount (1ph) | 26 | 87 | 38 | West | TFXF4
138989 | 2018-09-14 | Defective Equipment | Imminent Failure | 28kv transformer , TP11563 at 10C Jaguar PVT replaced due to leaking oil, affecting 26 customers. Initially 64 customers were affected dure the switching process. Terry Fox MTS (TFXF4) | None | Padmount (1ph) | 64 | 2 | 2 | West | TFXF4
138989 | 2018-09-14 | Defective Equipment | Imminent Failure | 28kv transformer , TP11563 at 10C Jaguar PVT replaced due to leaking oil, affecting 26 customers. Initially 64 customers were affected dure the switching process. Terry Fox MTS (TFXF4) | None | Padmount (1ph) | 64 | 3 | 3 | West | TFXF4
138990 | 2018-09-14 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X40313 TO TRANSFER HYDRO PLANT | None | O/H Transformer (1ph) | 11 | 203 | 37 | Central | UL04
138991 | 2018-09-14 | Scheduled Outage | Maintenance | Isolation to allow metering department to make repairs. | None | None | 1 | 263 | 4 | Central | 5401
138992 | 2018-09-14 | Scheduled Outage | Maintenance | Transformer isolated to straighten transformer lid on base. | None | None | 5 | 35 | 3 | East | LMBF7
138994 | 2018-09-14 | Scheduled Outage | Maintenance | Crew opened transformer in order to replace defective hotline clamp. | None | Hot-Line Clamp | 12 | 8 | 2 | East | BCHF3
138995 | 2018-09-15 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X56432 opened up due to animal contact | O/H Switchgear | Fused Cutout | 1 | 87 | 1 | South | FAL03
138996 | 2018-09-15 | Defective Equipment | Mechanical Failure | At 10:49am a defective switch 129W caused an outage to 43 customers. K-Line was called in to repair defective equipment. Casselman CASF2 | O/H Switchgear | Fused Cutout | 43 | 254 | 182 | East | CAS-F2
138997 | 2018-09-16 | Loss Of Supply | Transmission Inadvertent | loss of supply from Hydro One at Orleans TS | None | None | 1560 | 4 | 104 | East | 325M8
138998 | 2018-09-16 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | Unknown \ Other | 87 | 81 | 117 | West | 24F1
138999 | 2018-09-16 | Scheduled Outage | Construction | Transformer #X33658 isolated by crew to transfer secondary to new pole | None | None | 8 | 178 | 24 | Central | UC02
139001 | 2018-09-17 | Defective Equipment | Electrical Failure | Fuse S2-2 red phase on 24F1 blew due to underground fault. | U/G Cable | Unknown \ Other | 87 | 96 | 139 | West | 24F1
139002 | 2018-09-17 | Scheduled Outage | Maintenance | Planned outage with Dave Burns to transfer plant. | None | None | 14 | 100 | 23 | Central | UV02
139003 | 2018-09-17 | Scheduled Outage | Construction | Planned outage with K-Line to remove a service. | None | None | 6 | 18 | 2 | South | EPWF2
139004 | 2018-09-17 | Defective Equipment | Electrical Failure | At 08:30am while trying to restore a cable section S2-2 red phase fuse blew due to a faulted cable. 87 customers affected. Beaverbrook (24F1) | U/G Cable | Unknown \ Other | 87 | 96 | 139 | West | 24F1
139005 | 2018-09-17 | Scheduled Outage | Maintenance | A 8Kv transformer TP10479 at @ 55 Ariel was isolated to allow the crew to remove soil from the base affecting 18 customers for 248 minutes on the 200 F5 circuit | None | Unknown \ Other | 18 | 248 | 74 | South | 200F5
139006 | 2018-09-17 | Scheduled Outage | Construction | RHNF1 B phase between TEMP170B and TEMP177 RWB was isolated to allow crew to replace poles and transfer plant to new poles. 3 customers were affected. Richmond North (RHNF1). | None | None | 3 | 519 | 26 | West | RHNF1
139008 | 2018-09-18 | Scheduled Outage | Maintenance | Transfomrer TP3082 at 737 Stiles was isolated for secondary conductor repair. 13 customers affected. Beacon Hill (BCHF5) | None | U/G Service | 13 | 36 | 8 | East | BCHF5
139009 | 2018-09-18 | Scheduled Outage | Maintenance | TE3469 at 31 Upmnister way was isolated for soil remediation. 12 customers affected. Longfields (LGFF1) | None | Padmount (1ph) | 12 | 180 | 36 | South | LGFF1
139010 | 2018-09-18 | Scheduled Outage | Maintenance | Planned outage with Marc Branchaud to replace a service. | None | O/H Service | 9 | 60 | 9 | East | TB14
139011 | 2018-09-18 | Scheduled Outage | Construction | Pleanned outage with Mike from K-Line to transfer plant. | None | O/H Service | 7 | 103 | 12 | East | LTM02
139012 | 2018-09-18 | Scheduled Outage | Construction | TE499 at Woodhill Cres. Was isolated for cable and transformer replacement. 4 customers affected. Blackburn (BLKF4) | None | Padmount (1ph) | 4 | 390 | 26 | East | BLKF4
139013 | 2018-09-18 | Scheduled Outage | Construction | TE608 at 32 Allison Korn Pvt. Was isolated for cable replacement. 14 customers affected. Stafford (200F5) | None | None | 14 | 446 | 104 | South | 200F5
139014 | 2018-09-18 | Scheduled Outage | Construction | Replace transformer and reconfigure line. | None | None | 23 | 260 | 100 | Central | UV03
139015 | 2018-09-18 | Defective Equipment | Imminent Failure | TE347 at 1375 Leigh Cres. Was isolated for replacement due to an oil leak. 15 customers affected. Beacon Hill (BCHF8) | U/G Transformer | Padmount (1ph) | 15 | 600 | 150 | East | BCHF8
139017 | 2018-09-19 | Scheduled Outage | Construction | Mike Irvin - scheduled outage on X35098 to install new service. | O/H Transformer | O/H Transformer (1ph) | 12 | 90 | 18 | Central | UC05
139018 | 2018-09-19 | Scheduled Outage | Maintenance | Planned outage with Marc Branchaud to cut a service. | Secondary \ Service | O/H Service | 7 | 13 | 2 | Central | 505
139019 | 2018-09-19 | Defective Equipment | Corrosion | TE310 at 52 Moorecroft was isolated for replacement due to an oil leak. 8 customers affected. Manordale (84F5) | U/G Transformer | Padmount (1ph) | 8 | 389 | 52 | South | 84F5
139020 | 2018-09-19 | Scheduled Outage | Construction | TE451 at 27 Tauvette will was isolated for transformer and cable replacement. 9 customers affected. Blackburn (BLKF4) | None | Padmount (1ph) | 9 | 432 | 65 | East | BLKF4
139021 | 2018-09-19 | Scheduled Outage | Construction | Replace porcelain switches. | None | None | 1 | 95 | 2 | Central | TD06
139023 | 2018-09-19 | Scheduled Outage | Construction | Planned outage with Mike Byers to transfer services to new plant. | O/H Transformer | O/H Transformer (1ph) | 9 | 210 | 32 | Central | UV03
139024 | 2018-09-19 | Scheduled Outage | Construction | Planned outage with Paul from K-line to hook up a temporary service. | None | None | 7 | 93 | 11 | South | EPWF3
139027 | 2018-09-19 | Scheduled Outage | Construction | Marc Branchaud - scheduled outage for service upgarde. K600 | O/H Transformer | O/H Transformer (1ph) | 7 | 45 | 5 | East | AJ06
139028 | 2018-09-20 | Scheduled Outage | Construction | planned outage for TE607 to replace transformer and cable replacement | None | None | 14 | 454 | 106 | South | 200F5
139029 | 2018-09-20 | Scheduled Outage | Construction | Transformer #X20278 isolated by Shawn Evans from Kline to remove transformer and transfer plant | None | None | 1 | 25 | 0 | East | LTM02
139031 | 2018-09-20 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27190 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 11 | 217 | 40 | East | TB06
139032 | 2018-09-20 | Defective Equipment | Imminent Failure | planned outage to replace leaking transformer | None | None | 16 | 440 | 117 | East | 6F10
139033 | 2018-09-20 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27108 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 16 | 96 | 26 | East | TB14
139077 | 2018-09-22 | Tree Contacts | Falling Tree | Tree on line. | None | None | 17 | 67 | 19 | East | 7F4
139079 | 2018-09-22 | Defective Equipment | Electrical Failure | A cable fault caused the S13785 to blow and the 77M6 breaker to trip. A Hydro Ottawa line crew sectionalized to find the fault and restored power in steps | U/G Cable | XLPE | 82 | 43 | 59 | East | 77M6
139079 | 2018-09-22 | Defective Equipment | Electrical Failure | A cable fault caused the S13785 to blow and the 77M6 breaker to trip. A Hydro Ottawa line crew sectionalized to find the fault and restored power in steps | U/G Cable | XLPE | 90 | 18 | 27 | East | 77M6
139079 | 2018-09-22 | Defective Equipment | Electrical Failure | A cable fault caused the S13785 to blow and the 77M6 breaker to trip. A Hydro Ottawa line crew sectionalized to find the fault and restored power in steps | U/G Cable | XLPE | 90 | 153 | 230 | East | 77M6
139079 | 2018-09-22 | Defective Equipment | Electrical Failure | A cable fault caused the S13785 to blow and the 77M6 breaker to trip. A Hydro Ottawa line crew sectionalized to find the fault and restored power in steps | U/G Cable | XLPE | 5253 | 5 | 438 | East | 77M6
139080 | 2018-09-22 | Tree Contacts | Broken Branch | Tree branch on overhead. | Station Equipment | Relay | 24 | 132 | 53 | Central | TK2AC
139085 | 2018-09-23 | Tree Contacts | Broken Branch | Broken conductor at 1836 Playfair required isolation of entire circuit for repair affecting 238 customers. Playfair AJ04 | O/H Conductor | O/H Conductor | 238 | 168 | 666 | East | AJ04
139099 | 2018-09-24 | Scheduled Outage | Forced Switching | CS17894 opened to partially repair storm damage. 2054 customers affected. Hawthorne 48M6. | None | Unknown \ Other | 2054 | 4 | 137 | East | 48M2
139101 | 2018-09-24 | Scheduled Outage | Construction | 8KV transformer, TP9975 at 300 bank was isolated for FIT installtion, affecting 1 customer. Manordale DS (84F4) | None | None | 1 | 487 | 8 | South | 84F4
139102 | 2018-09-24 | Scheduled Outage | Construction | Not yet known. | None | None | 2 | 7 | 0 | South | EPWF1
139103 | 2018-09-24 | Loss Of Supply | Third Party | 4kv vault, V432 at 2487 Kaladar Main OCB found tripped, cuase under investigation. Affecting 6 customers. Brookfield DS (AF04) | Customer Owned | Customer-Owned | 6 | 477 | 48 | East | AF04
139104 | 2018-09-24 | Defective Equipment | Defective Equipment/ Material | 8KV switch S1565 and lightning arrester at 1651 Merivale found defective, affecting 12 customers. | Pole Attachement | Arrester | 12 | 68 | 14 | South | 130F4
139105 | 2018-09-24 | Scheduled Outage | Construction | Planned outage with Adam Donaldson to run a new service. | None | O/H Service | 5 | 120 | 10 | East | UG09
139108 | 2018-09-25 | Defective Equipment | Defective Equipment/ Material | x5312 broken insulator | Pole Attachement | Insulator | 27 | 401 | 180 | South | 130F2
139108 | 2018-09-25 | Defective Equipment | Defective Equipment/ Material | x5312 broken insulator | Pole Attachement | Insulator | 274 | 56 | 256 | South | 130F2
139109 | 2018-09-25 | Foreign Interference | Foreign Objects | Not yet known. Crew patrolled the O/H and found some insulation lying on the O/H wires | None | None | 6 | 94 | 9 | Central | TH2UL
139110 | 2018-09-25 | Scheduled Outage | Forced Switching | 2 broken poles at 82 Byron required the breaker at the station opened for safety affecting 189 customers. Carling SM05 | None | Pole | 7 | 354 | 41 | Central | SM05
139110 | 2018-09-25 | Scheduled Outage | Forced Switching | 2 broken poles at 82 Byron required the breaker at the station opened for safety affecting 189 customers. Carling SM05 | None | Pole | 14 | 181 | 42 | Central | SM05
139110 | 2018-09-25 | Scheduled Outage | Forced Switching | 2 broken poles at 82 Byron required the breaker at the station opened for safety affecting 189 customers. Carling SM05 | None | Pole | 17 | 28 | 8 | Central | SM05
139110 | 2018-09-25 | Scheduled Outage | Forced Switching | 2 broken poles at 82 Byron required the breaker at the station opened for safety affecting 189 customers. Carling SM05 | None | Pole | 24 | 1 | 0 | Central | SM05
139110 | 2018-09-25 | Scheduled Outage | Forced Switching | 2 broken poles at 82 Byron required the breaker at the station opened for safety affecting 189 customers. Carling SM05 | None | Pole | 24 | 3 | 1 | Central | SM05
139110 | 2018-09-25 | Scheduled Outage | Forced Switching | 2 broken poles at 82 Byron required the breaker at the station opened for safety affecting 189 customers. Carling SM05 | None | Pole | 189 | 20 | 63 | Central | SM05
139112 | 2018-09-25 | Scheduled Outage | Maintenance | Planned outage to run a new service. | None | O/H Service | 5 | 62 | 5 | Central | SB13
139113 | 2018-09-25 | Scheduled Outage | Vegetation Management | Transformer #X24584 isolated by crew due to tree trimming required | None | None | 4 | 35 | 2 | East | 8F1
139114 | 2018-09-25 | Scheduled Outage | Maintenance | Planned outage to reconnect a service. | Secondary \ Service | O/H Service | 8 | 129 | 17 | East | AN04
139115 | 2018-09-25 | Scheduled Outage | Maintenance | Planned outage with Travis Rowe to disconnect a service. | None | O/H Service | 14 | 25 | 6 | Central | SB05
139116 | 2018-09-26 | Unknown/Other | Unknown | Not yet known. | None | None | 5506 | 39 | 3579 | South | FAL03
139117 | 2018-09-26 | Defective Equipment | Mechanical Failure | Customer equipment failed at 200 Elgin tripping the station breaker affecting 204 customers. Power was restored in stages. Slater 626 | Vault Equipment | Breaker \ Relay | 188 | 25 | 78 | Central | 626
139117 | 2018-09-26 | Defective Equipment | Mechanical Failure | Customer equipment failed at 200 Elgin tripping the station breaker affecting 204 customers. Power was restored in stages. Slater 626 | Vault Equipment | Breaker \ Relay | 201 | 80 | 268 | Central | 626
139117 | 2018-09-26 | Defective Equipment | Mechanical Failure | Customer equipment failed at 200 Elgin tripping the station breaker affecting 204 customers. Power was restored in stages. Slater 626 | Vault Equipment | Breaker \ Relay | 204 | 57 | 194 | Central | 626
139118 | 2018-09-26 | Tree Contacts | Falling Tree | SCADA indicates the BDFF2 CB A/R and blew fusenat S1513 due to tree on the line at 28 Concourse. 274 customers were affected. Borden Farms (BDFF2) | O/H Switchgear | Fused Cutout | 1 | 101 | 2 | South | 130F2
139119 | 2018-09-26 | Adverse Weather | Extreme Wind | To isolate TP5600 for repairs and reconnect | Customer Owned | Customer-Owned | 5 | 20 | 2 | South | 130F3
139121 | 2018-09-26 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X30179 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 6 | 52 | 5 | Central | TH15
139124 | 2018-09-26 | Scheduled Outage | Construction | Transformer #X24894 isolated by crew to cut old buss clear | None | None | 8 | 24 | 3 | Central | TK2AC
139125 | 2018-09-26 | Tree Contacts | Falling Tree | S5307 at 2009 Prince of Whales open due to down primary on customer property caused by fallen tree branches. 1 customer was affected. Broden Farms (BDFF2) | O/H Conductor | O/H Conductor | 1 | 142 | 2 | South | 130F2
139126 | 2018-09-26 | Scheduled Outage | Vegetation Management | Transformer #X24660 isolated by crew to trim trees and re-sag open wire buss | None | None | 4 | 95 | 6 | East | UQ05
139127 | 2018-09-26 | Scheduled Outage | Maintenance | Planned outage to run new secondary services. | None | O/H Service | 17 | 153 | 43 | Central | SR07
139128 | 2018-09-27 | Defective Equipment | Electrical Failure | 77M1 circuit auto reclosed.The crews found a blown arrestor at switch G130 which cause the circuit at auto reclose and trip affecting 3645 customers affected98 minutes Bilberry (77M1) | Pole Attachement | Arrester | 3645 | 98 | 5954 | East | 77M1
139129 | 2018-09-27 | Scheduled Outage | Vegetation Management | Overhead circuit at 80 Stinson isolated to remove tree at 80 Stinson. 27 customers affected. Bells Corners (47F3) | None | O/H Conductor | 27 | 249 | 112 | South | 47F3
139130 | 2018-09-27 | Defective Equipment | Electrical Failure | TP7035 at 1213 Saint Moritz was found to be defective and replaced. 14 customers affected. Bilberry (77M1) | U/G Transformer | Padmount (1ph) | 14 | 215 | 50 | East | 77M1
139132 | 2018-09-28 | Defective Equipment | Electrical Failure | SCADA indicates a reclose and a trip on the FAL03 circuit breaker at Fallowfield MTS affecting 5514 customers. | Pole Attachement | Arrester | 5514 | 85 | 7812 | South | FAL03
139133 | 2018-09-28 | Scheduled Outage | Construction | Replace broken poles | None | None | 45 | 323 | 242 | South | 180F6
139134 | 2018-09-28 | Loss Of Supply | Third Party | A switchgear fault in a vault at 99 Metcalfe caused the station breaker to trip affecting 369 customers. Slater TL4TS VT477 | Vault Equipment | Breaker \ Relay | 1 | 1458 | 24 | Central | TL4TS
139134 | 2018-09-28 | Loss Of Supply | Third Party | A switchgear fault in a vault at 99 Metcalfe caused the station breaker to trip affecting 369 customers. Slater TL4TS VT477 | Vault Equipment | Breaker \ Relay | 369 | 67 | 412 | Central | TL4TS
139136 | 2018-09-29 | Scheduled Outage | Maintenance | To allow crews to change rotten hydro pole. | None | Pole | 1 | 432 | 7 | Central | TD07
139139 | 2018-09-29 | Scheduled Outage | Construction | OUTAGE ON X32925 TO REPLACE A POLE | None | Pole | 7 | 195 | 23 | Central | TD07
139140 | 2018-09-30 | Foreign Interference | Vehicle | A motor vehicle accident brok pole X50586, caused UZ02 to auto-reclose and UZ12 to trip. UZ02 was later forced out of service to allow for the safe replacement of the broken pole. | Pole | Pole | 0 | 145 | 0 | East | UZ02
139140 | 2018-09-30 | Foreign Interference | Vehicle | A motor vehicle accident brok pole X50586, caused UZ02 to auto-reclose and UZ12 to trip. UZ02 was later forced out of service to allow for the safe replacement of the broken pole. | Pole | Pole | 225 | 384 | 1440 | East | UZ02
139140 | 2018-09-30 | Foreign Interference | Vehicle | A motor vehicle accident brok pole X50586, caused UZ02 to auto-reclose and UZ12 to trip. UZ02 was later forced out of service to allow for the safe replacement of the broken pole. | Pole | Pole | 272 | 536 | 2430 | East | UZ12
139141 | 2018-09-30 | Foreign Interference | Dig-In | field crews report someone has been digging at this address, no crews on site, but plywood over the hole, locates are there, but it looks like someone dug too deep and damaged the cable. | U/G Cable | XLPE | 20 | 47 | 16 | East | 77M2
139141 | 2018-09-30 | Foreign Interference | Dig-In | field crews report someone has been digging at this address, no crews on site, but plywood over the hole, locates are there, but it looks like someone dug too deep and damaged the cable. | U/G Cable | XLPE | 82 | 260 | 355 | East | 77M6
139141 | 2018-09-30 | Foreign Interference | Dig-In | field crews report someone has been digging at this address, no crews on site, but plywood over the hole, locates are there, but it looks like someone dug too deep and damaged the cable. | U/G Cable | XLPE | 90 | 102 | 153 | East | 77M6
139142 | 2018-09-30 | Scheduled Outage | Construction | X33684 to transfer plant | None | O/H Transformer (3ph) | 10 | 180 | 30 | Central | SH05
139143 | 2018-09-30 | Foreign Interference | Vehicle | MVA hit TP2704 on Steeple Chase and knocked transformer off its pad and punctured the side. | U/G Transformer | Padmount (1ph) | 10 | 318 | 53 | West | TFXF6
139146 | 2018-10-01 | Scheduled Outage | Construction | Transformer #X35180 isolated by crew to remove service | None | None | 8 | 13 | 2 | Central | UL14
139147 | 2018-10-01 | Scheduled Outage | Construction | Transformer #X30722 isolated by crew to remove a service | None | None | 25 | 25 | 10 | Central | UN06
139148 | 2018-10-01 | Scheduled Outage | Construction | K-LINE TRANSFER TO PLANT X42052 | None | O/H Transformer (1ph) | 6 | 40 | 4 | East | LTM02
139149 | 2018-10-01 | Foreign Interference | Wildlife (Bird/Animal) | Fuse S11832 at 1932 Hall St. opened due to an animal contact. 14 customers affected. Russell (TB15) | None | None | 14 | 621 | 145 | East | TB15
139150 | 2018-10-02 | Loss Of Supply | Third Party | While performing switching to restore the 502 cable section apon closing VT220-L2 the TR07 breaker trip affecting 722 customers for 15 minutes,possible cable fault. | U/G Cable | PILC | 722 | 15 | 180 | Central | 502
139153 | 2018-10-03 | Scheduled Outage | Construction | A section of a 4Kv overhead line in the rear of 2361 Ryan Dr was isolated to allow the crews replace poles affecting 51 customers on the UV03 circuit for 98 minutes | None | Pole | 51 | 98 | 83 | Central | UV03
139154 | 2018-10-03 | Scheduled Outage | Construction | Transformer #X35322 isolated by crew to transfer plant | None | None | 5 | 105 | 9 | Central | TW22
139155 | 2018-10-03 | Defective Equipment | Imminent Failure | Transformer #TE0135 isolated by crew to replace transformer | None | None | 7 | 120 | 14 | East | BLKF3
139157 | 2018-10-03 | Defective Equipment | Electrical Failure | 24/7 crew responding to trouble call reports a cut out open at the road feeding PT251. Remaining switches were open so repairs can be made. Outage affects 1 customer on the 5408. | U/G Transformer | Padmount (3ph) | 1 | 399 | 7 | Central | 5408
139158 | 2018-10-03 | Scheduled Outage | Maintenance | A 8Kv transformer TE333 at 29 Hadley Cir was isolated to allow the crews to replace the transformer and cables affecting 12 customers for 328 minutes on the 200f5 | None | Kiosk (1ph) | 12 | 328 | 66 | South | 47F1
139160 | 2018-10-03 | Scheduled Outage | Maintenance | transformer at 2044 Gatneau View was isolated to replace transformer. 12 customers were affected. Beaconhill BCHF1 | None | None | 12 | 485 | 97 | East | BCHF1
139161 | 2018-10-03 | Foreign Interference | Crane | backhoe contacted overhead circuit on river road and broke hydro pole, causing switch G1 to open all three phases. 1055 customers were affected. Limebank LMBF5 | Pole | Pole | 609 | 122 | 1238 | East | LMBF5
139161 | 2018-10-03 | Foreign Interference | Crane | backhoe contacted overhead circuit on river road and broke hydro pole, causing switch G1 to open all three phases. 1055 customers were affected. Limebank LMBF5 | Pole | Pole | 1055 | 151 | 2655 | East | LMBF5
139162 | 2018-10-03 | Defective Equipment | Imminent Failure | planned outage to replace leaker | None | None | 13 | 619 | 134 | South | 140F1
139163 | 2018-10-04 | Scheduled Outage | Construction | Transformer TE332 at 12 Hadley was isolated to allow crew to replace transformer. 5 customers were affected. Stafford (200F5) | None | None | 5 | 183 | 15 | South | 200F5
139164 | 2018-10-04 | Scheduled Outage | Construction | Transformer #X33755 isolated by crew to install new service | None | None | 5 | 49 | 4 | Central | TW22
139165 | 2018-10-04 | Scheduled Outage | Construction | Transformer TE364 at 2021 Gatineau was isolated to allow crew to replace cables and transformer. 24 customers were affected. Beaconhill (BCHF1). | None | None | 24 | 396 | 158 | East | BCHF1
139167 | 2018-10-04 | Scheduled Outage | Construction | Transformer #X37168 isolated by crew to plant a pole | None | None | 9 | 59 | 9 | Central | UV07
139168 | 2018-10-04 | Defective Equipment | Electrical Failure | SC1447 insulator flahsed. Riverdale (TR1UN) | U/G Switchgear | Live-Front | 4 | 39 | 3 | Central | TR1UN
139168 | 2018-10-04 | Defective Equipment | Electrical Failure | SC1447 insulator flahsed. Riverdale (TR1UN) | U/G Switchgear | Live-Front | 60 | 88 | 88 | Central | TR1UN
139168 | 2018-10-04 | Defective Equipment | Electrical Failure | SC1447 insulator flahsed. Riverdale (TR1UN) | U/G Switchgear | Live-Front | 1847 | 88 | 2709 | Central | TR1UN
139169 | 2018-10-04 | Scheduled Outage | Construction | Section of the RHNF1 B phase between TEMP163 and TEMP110 was isolasted on Shea Rd to allow crew to replace pole and transfer plant. 1 customer was affected. Richmond North (RHNF1) | None | None | 1 | 190 | 3 | West | RHNF1
139169 | 2018-10-04 | Scheduled Outage | Construction | Section of the RHNF1 B phase between TEMP163 and TEMP110 was isolasted on Shea Rd to allow crew to replace pole and transfer plant. 1 customer was affected. Richmond North (RHNF1) | None | None | 2 | 140 | 5 | West | RHNF1
139170 | 2018-10-04 | Foreign Interference | Vehicle | Transformer #X27832 isolated by crew due to 2 services pulled down by a truck | None | None | 12 | 63 | 13 | Central | TH06
139172 | 2018-10-04 | Scheduled Outage | Construction | Transformer #X35502 isolated by crew to transfer plant | None | None | 15 | 35 | 9 | Central | AH14
139174 | 2018-10-04 | Scheduled Outage | Construction | To allow Hydro Ottaw cable crews to remove K364 from the system | None | None | 57 | 201 | 191 | Central | UV02
139176 | 2018-10-04 | Foreign Interference | Wildlife (Bird/Animal) | replaced blown fuse feeding transformer X27515 due to squirrel contact | O/H Transformer | O/H Transformer (1ph) | 12 | 375 | 75 | East | TB2JP
139178 | 2018-10-04 | Loss Of Supply | Third Party | Moisture in vault caused switchgear to fail at VT586 & VT705 | Customer Owned | Customer-Owned | 230 | 709 | 2718 | Central | 501
139178 | 2018-10-04 | Loss Of Supply | Third Party | Moisture in vault caused switchgear to fail at VT586 & VT705 | Customer Owned | Customer-Owned | 326 | 76 | 413 | Central | 501
139178 | 2018-10-04 | Loss Of Supply | Third Party | Moisture in vault caused switchgear to fail at VT586 & VT705 | Customer Owned | Customer-Owned | 746 | 40 | 497 | Central | 501
139179 | 2018-10-04 | Scheduled Outage | Maintenance | To repair primary connections at P117. | U/G Transformer | Kiosk (3ph) | 1 | 116 | 2 | East | AP03
139183 | 2018-10-05 | Defective Equipment | Imminent Failure | Transfromer TE2776 at 1177 Foxborough was isolated to allow crew to replace leaking transformer. 18 customers were affected. Beaconhill (BCHF8) | U/G Transformer | Padmount (1ph) | 18 | 230 | 69 | East | BCHF8
139185 | 2018-10-07 | Foreign Interference | Wildlife (Bird/Animal) | S103 B on Brebeuf St. in Casselman opened due to an animal contact. 14 customers affected. Casselman (CASF4) | O/H Switchgear | Fused Cutout | 14 | 131 | 31 | East | CAS-F4
139186 | 2018-10-08 | Defective Equipment | Mechanical Failure | TP11930 at 66 Colonade was isolated to replace a broken pole. 9 customers affected. Borden Farms (BDFF2) | Pole | Pole | 9 | 437 | 66 | South | 130F2
139190 | 2018-10-09 | Defective Equipment | Imminent Failure | 13kv pad mount transformer, MT1348 at 117 Meadowcroft was replaced due to leaking oil, affecting 7 customers. Overbrook TS (TO3AP) | U/G Transformer | Padmount (1ph) | 7 | 266 | 31 | East | TO3AP
139192 | 2018-10-09 | Scheduled Outage | Maintenance | Isolated transformer x32573 to replace switch and arrerster | None | O/H Transformer (1ph) | 4 | 50 | 3 | Central | TD06
139193 | 2018-10-09 | Foreign Interference | Wildlife (Bird/Animal) | 28F3 trip due to squirrel contact, | Unknown \ Other | Unknown \ Other | 330 | 9 | 50 | West | 28F3
139194 | 2018-10-09 | Scheduled Outage | Construction | TE369 transformer and cable replacement. | None | None | 12 | 422 | 84 | East | BCHF1
139195 | 2018-10-09 | Tree Contacts | Falling Tree | A large tree on the primary at Acacia and Thorold required the circuit isolated to cut it clear affecting 241 cusomers. Vaughan UG05 | None | None | 241 | 51 | 205 | East | UG05
139196 | 2018-10-10 | Scheduled Outage | Construction | 8kv transformer, TE314 at 14 Hadley was isolated for upgrade, affecting 20 customers. Stafford DS (200F5). | None | None | 20 | 469 | 156 | South | 200F5
139197 | 2018-10-10 | Scheduled Outage | Construction | VT533 at 525 Wentworth was isolated to replace riser pole. 1 customer affected. Lincoln TD07 | None | Pole | 1 | 319 | 5 | Central | TD07
139200 | 2018-10-10 | Scheduled Outage | Construction | Transformer #X34685 isolated by crew to transfer plant | None | None | 17 | 263 | 75 | Central | TD07
139201 | 2018-10-10 | Defective Equipment | Imminent Failure | TP9758 isolated to replace leaking transformer. | None | None | 46 | 388 | 297 | East | CYRF4
139202 | 2018-10-10 | Scheduled Outage | Construction | P491 at 1175 Soderlind was isolated to transfer plant to new pole. 1 customer affected. Edwin UV07. | None | None | 1 | 194 | 3 | Central | UV07
139203 | 2018-10-10 | Scheduled Outage | Maintenance | Outage for soil remediation | None | None | 21 | 429 | 150 | East | LMBF7
139204 | 2018-10-10 | Scheduled Outage | Construction | TE370 replace withTP11805 part of transformer cable replacement. | None | None | 16 | 485 | 129 | East | BLKF1
139205 | 2018-10-10 | Foreign Interference | Vehicle | As per OMS call # R00259232 a truck struck a pole and broke it. Isolated from S996 under PC10A # 14494 to make repairs. Darcy Provost on site with On-Call crews. The outage will affect 8 customers on the 140F4 circuit out of Barrhaven DS. | Pole | Pole | 8 | 351 | 47 | South | 140F4
139206 | 2018-10-11 | Defective Equipment | Electrical Failure | RX2056 auto reclosed and S7044 opened due to defective transformer TE3030 at 491 Beatrice. 4649 customers affected. Limebank (LMB7) | U/G Transformer | Padmount (1ph) | 111 | 507 | 938 | East | LMBF7
139208 | 2018-10-11 | Defective Equipment | Imminent Failure | defective leaking transformer TE3030 at 491 Beatrice caused switch S7044 to open affecting 111 customers. Limebank, LMBF7. | U/G Transformer | Padmount (1ph) | 7 | 285 | 33 | East | LMBF7
139208 | 2018-10-11 | Defective Equipment | Imminent Failure | defective leaking transformer TE3030 at 491 Beatrice caused switch S7044 to open affecting 111 customers. Limebank, LMBF7. | U/G Transformer | Padmount (1ph) | 15 | 4 | 1 | East | LMBF7
139208 | 2018-10-11 | Defective Equipment | Imminent Failure | defective leaking transformer TE3030 at 491 Beatrice caused switch S7044 to open affecting 111 customers. Limebank, LMBF7. | U/G Transformer | Padmount (1ph) | 111 | 210 | 388 | East | LMBF7
139210 | 2018-10-11 | Defective Equipment | Imminent Failure | crew isolated transformer TE555 at 2008 Beaconwood to replace leaking transformer. 17 customers affected. Beaconhill BCHF8 | U/G Transformer | Padmount (1ph) | 17 | 131 | 37 | East | BCHF8
139212 | 2018-10-11 | Defective Equipment | Imminent Failure | crew isolated transformer at 2152 Beaconwood to replace transformer. 30 customers were affected. Beaconhill. BCHF8 | U/G Transformer | Padmount (1ph) | 30 | 92 | 46 | East | BCHF8
139213 | 2018-10-11 | Foreign Interference | Vehicle | crew isolated section of overhead circuit to replace hydro pole that was broken on Old richmond rd. due to vehicle contact. 68 customers were affected. Bells corners, 47F6 | Pole | Pole | 68 | 260 | 295 | South | 47F6
139214 | 2018-10-11 | Defective Equipment | Mechanical Failure | A 4Kv padmount transformer P76 at 2 Paddington was isolated to allow the crews broken cut outs, affecting 2 customers for 45 minutes on the UA04 circuit | O/H Switchgear | Fused Cutout | 2 | 45 | 2 | East | UA04
139215 | 2018-10-11 | Scheduled Outage | Maintenance | Planned outage to reconnect secondary service. | None | O/H Service | 15 | 34 | 8 | South | 170F1
139216 | 2018-10-12 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact | O/H Switchgear | Fused Cutout | 3 | 70 | 4 | South | FAL01
139217 | 2018-10-12 | Scheduled Outage | Construction | Transformer TP11241 was isolated to allow crew to reaplce cables. 8 customers were affected. Beaconhill (BCHF1) | None | None | 8 | 210 | 28 | East | BCHF1
139218 | 2018-10-12 | Defective Equipment | Electrical Failure | At 10:56am TV2099-CB6 tripped while switching affecting 87 customers. Slater (602) | U/G Switchgear | Gas-Insulated Dead Front | 87 | 12 | 17 | Central | 602
139219 | 2018-10-12 | Scheduled Outage | Construction | ISOLATED TRANSFORMER 4610 TO TRANSFER HYDRO PLANT TO NEW POLE | None | O/H Transformer (1ph) | 10 | 225 | 38 | South | 200F3
139220 | 2018-10-12 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X32210 | None | O/H Transformer (1ph) | 9 | 150 | 22 | Central | SM02
139221 | 2018-10-12 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X27181 TO TRANSFER HYDRO PLANT TO NEW POLE | None | O/H Transformer (1ph) | 11 | 145 | 27 | East | TB06
139222 | 2018-10-12 | Defective Equipment | Imminent Failure | crew isolated transformer at 1670 sunview to replace leaking transformer. 12 customers were affected. Billberry 77M6. | None | None | 12 | 94 | 19 | East | 77M6
139224 | 2018-10-12 | Scheduled Outage | Construction | Planned outage to replace damaged secondaries. | None | O/H Service | 9 | 69 | 10 | East | AA06
139225 | 2018-10-12 | Defective Equipment | Electrical Failure | Blue phase cable fault between TP8028 and TP7595. During switching 77M6 tripped under hold off. | U/G Cable | XLPE | 249 | 96 | 398 | East | 77M6
139225 | 2018-10-12 | Defective Equipment | Electrical Failure | Blue phase cable fault between TP8028 and TP7595. During switching 77M6 tripped under hold off. | U/G Cable | XLPE | 249 | 246 | 1021 | East | 77M6
139225 | 2018-10-12 | Defective Equipment | Electrical Failure | Blue phase cable fault between TP8028 and TP7595. During switching 77M6 tripped under hold off. | U/G Cable | XLPE | 7550 | 2 | 252 | East | 77M6
139227 | 2018-10-13 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X47884 opened up due to animal contact | O/H Switchgear | Fused Cutout | 14 | 149 | 35 | Central | TW18
139229 | 2018-10-14 | Loss Of Supply | Transmission Planned | Hydro One forced outage to the Almonte 20M28 circuit for Hydro One to make repairs to there transmission. Outage affected Hydro Ottawa customers fed from the Hydro One Beckwith (BECKF2) circuit. 636 customers were affected. | None | None | 636 | 63 | 668 | West | BECKF2
139230 | 2018-10-14 | Scheduled Outage | Construction | A transformer at 57 Clarey was opened to transfer plant affecting 5 customers. Bronson SB05 | None | None | 5 | 197 | 16 | Central | SB05
139233 | 2018-10-14 | Defective Equipment | Defective Equipment/ Material | The S1150 R phase blew due to burnt connections in TE1201 and TE1202 at 2 Seyton causing the 200F5 circuit to auto reclose. Stafford (200F5) | U/G Transformer | Padmount (1ph) | 41 | 190 | 130 | South | 200F5
139233 | 2018-10-14 | Defective Equipment | Defective Equipment/ Material | The S1150 R phase blew due to burnt connections in TE1201 and TE1202 at 2 Seyton causing the 200F5 circuit to auto reclose. Stafford (200F5) | U/G Transformer | Padmount (1ph) | 60 | 201 | 201 | South | 200F5
139234 | 2018-10-14 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X27190 opened up due to animal contact | O/H Switchgear | Fused Cutout | 11 | 122 | 22 | East | TB06
139235 | 2018-10-14 | Foreign Interference | Wildlife (Bird/Animal) | 13KV overhead transformer (X28223) at 157 Crocus was interupted due to animal contact, affected 10 cutomers. Riverside TS (505). | O/H Transformer | O/H Transformer (1ph) | 10 | 62 | 10 | Central | 505
139236 | 2018-10-15 | Defective Equipment | Imminent Failure | Transformer TP9715 was isolated to allow crew to replace leaking transformer. 13 customers were affected. Cyrville CYRF4 | U/G Transformer | Padmount (1ph) | 13 | 437 | 95 | East | CYRF4
139238 | 2018-10-15 | Defective Equipment | Imminent Failure | A transformer at Cathrine and Bank was isolated to replace a leaking transformer and remediate the soil affecting 21 customers. Florence UF06 | None | None | 21 | 715 | 250 | Central | UF06
139239 | 2018-10-15 | Defective Equipment | Mechanical Failure | S1531 to EOL was isolated to allow crew to replace defective hot line clamp. 3 customers were affected. Centrepointe (87F6) | O/H Conductor | Hot-Line Clamp | 3 | 19 | 1 | South | 87F6
139240 | 2018-10-15 | Unknown/Other | Unknown | High winds may have caused the 190F5 breaker to trip affecting 1097 customers for 50 minutes | O/H Conductor | O/H Conductor | 1097 | 50 | 914 | South | 190F5
139241 | 2018-10-16 | Tree Contacts | Tree Growth/ Untrimmed Tree | At 00:30am S24252 was opened to allow crew to untangle primary conductor. 11 people affected. Woodroffe (TW17) | None | None | 11 | 133 | 24 | Central | TW17
139242 | 2018-10-16 | Scheduled Outage | Maintenance | replace old switches and arrestors | None | None | 1 | 46 | 1 | Central | TD06
139243 | 2018-10-16 | Scheduled Outage | Maintenance | replace old switches and arrestors | None | None | 5 | 28 | 2 | Central | TD06
139244 | 2018-10-16 | Scheduled Outage | Vegetation Management | tree trimming | None | None | 4 | 325 | 22 | East | AF02
139245 | 2018-10-16 | Defective Equipment | Imminent Failure | TE2324 at 809 Curlew was isolated for repacement due to an oil leak. 3 customers affected. Moulton (8F1). | U/G Transformer | Padmount (1ph) | 3 | 298 | 15 | East | 8F1
139246 | 2018-10-16 | Scheduled Outage | Maintenance | crew isolated transformer at 13 Wareham for the cable replacement program. 14 customers were affected. Stafford 200F5. | None | None | 14 | 374 | 87 | South | 200F5
139248 | 2018-10-16 | Scheduled Outage | Construction | crew isolated transformer at 662 Laverendrye to replace transformer and cables. 16 customers affected. Beaconhill BCHF1. | None | None | 16 | 423 | 113 | East | BCHF1
139249 | 2018-10-16 | Scheduled Outage | Construction | crew isolated transformer at 51 woodburn to replace transformer. 12 customers interrupted. Blackburn BLKF4. | None | None | 12 | 487 | 97 | East | BLKF4
139250 | 2018-10-16 | Scheduled Outage | Maintenance | Planned outage for a service upgrade. | Secondary \ Service | O/H Service | 13 | 58 | 13 | Central | SM10
139251 | 2018-10-16 | Scheduled Outage | Construction | Planned outage to upgrade a service. | None | O/H Service | 5 | 67 | 6 | East | TB06
139253 | 2018-10-17 | Scheduled Outage | Maintenance | planned outage to replace switches and arrestors | None | None | 4 | 55 | 4 | Central | TD06
139254 | 2018-10-17 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact blew transformer fuse. | O/H Transformer | O/H Transformer (1ph) | 6 | 103 | 10 | West | 28F3
139256 | 2018-10-17 | Scheduled Outage | Maintenance | Planned outage for service upgrades. | None | O/H Service | 14 | 81 | 19 | Central | TD14
139257 | 2018-10-17 | Scheduled Outage | Construction | Planned outage for service upgrades. | None | O/H Service | 9 | 106 | 16 | East | UA04
139258 | 2018-10-17 | Scheduled Outage | Maintenance | transformer at 198 woodridge cres was isolared for soil remediation. 27 customers were affected. Bayshore 49F2. | None | None | 27 | 403 | 181 | South | 49F2
139259 | 2018-10-17 | Scheduled Outage | Construction | Planned outage for service upgrades. | None | O/H Service | 5 | 104 | 9 | East | UA04
139261 | 2018-10-17 | Scheduled Outage | Maintenance | Planned outage to change a switch. | None | Fused Cutout | 5 | 60 | 5 | Central | TD06
139262 | 2018-10-17 | Adverse Weather | Extreme Wind | phases wrapped together from high winds on Akins rd. caused red and blue phase to open on rabbits WX2087 on shea rd. 37 customers were interrupted. Terry fox, TFXF4 | None | None | 9 | 99 | 15 | West | TFXF4
139262 | 2018-10-17 | Adverse Weather | Extreme Wind | phases wrapped together from high winds on Akins rd. caused red and blue phase to open on rabbits WX2087 on shea rd. 37 customers were interrupted. Terry fox, TFXF4 | None | None | 37 | 94 | 58 | West | TFXF4
139264 | 2018-10-17 | Defective Equipment | Defective Equipment/ Material | Blown arrestor | Pole Attachement | Arrester | 396 | 45 | 297 | East | AN05
139265 | 2018-10-17 | Scheduled Outage | Construction | crew isolated transformer at 651 Laverendrye to replace transformers and cables. 10 customers were affected. Beaconhill BCHF1 | None | None | 10 | 434 | 72 | East | BCHF1
139266 | 2018-10-17 | Scheduled Outage | Construction | crew isolated transformer at 10 wareham to replace transformer and cables. 21 customers were affected. Stafford 200F1 | None | None | 21 | 545 | 191 | South | 200F5
139267 | 2018-10-17 | Defective Equipment | Mechanical Failure | A faulted secondary cable feeding a gang meter base caused an outage to 17 customers fed out TP6891 at 871 Schooner. Limebank DS (LMBF7) | Secondary \ Service | U/G Service | 17 | 840 | 238 | East | LMBF7
139269 | 2018-10-18 | Scheduled Outage | Construction | Planned outage to run a new service. | None | O/H Service | 4 | 95 | 6 | East | UA07
139270 | 2018-10-18 | Defective Equipment | Electrical Failure | K731 at 3230 Uplands was isolated to replace defective transformer. 34 customers affected. McCarthy AQ07. | U/G Transformer | Kiosk (1ph) | 34 | 236 | 134 | East | AQ07
139271 | 2018-10-18 | Scheduled Outage | Construction | TE367 replaced with TP11798 as part of transformer and cable replacement. | None | None | 10 | 452 | 75 | East | BLKF1
139272 | 2018-10-18 | Scheduled Outage | Construction | TE124 replace with TP11818 as part of transformer and cable replacement. | None | None | 10 | 475 | 79 | East | BLKF4
139273 | 2018-10-19 | Scheduled Outage | Construction | Planned outage to transfer HOL plant. | None | None | 2 | 192 | 6 | East | UZ07
139274 | 2018-10-19 | Scheduled Outage | Maintenance | Planned outage for service upgrades. | None | O/H Service | 4 | 142 | 9 | Central | TW22
139276 | 2018-10-19 | Tree Contacts | Broken Branch | Ottawa Fire reports sparking wires at 113 Queen Charlotte St. OMS indicates S24029 Blue phase fuse is opened. Crews report branch on overhead infront of 113 Queen Charlotte St. Switch 924 found open and defective switch at S24929. | O/H Conductor | O/H Conductor | 75 | 143 | 179 | West | 28F2
139279 | 2018-10-20 | Scheduled Outage | Maintenance | crew isolated transformer at 303 Terry fox to upgrade transformer. 2 customers were affected. Kanata, 624F5. | None | None | 2 | 315 | 10 | West | 624F5
139280 | 2018-10-20 | Defective Equipment | Imminent Failure | A 13Kv transformer PT182 at 1455 Michael St was isolated to allow the crews to replace a leaking transformers and the switches on the pole affecting 6 customers for 276 minutes on the TB07 circuit. | None | Kiosk (3ph) | 6 | 276 | 28 | East | TB07
139281 | 2018-10-20 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X35322 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 349 | 35 | Central | TW22
139282 | 2018-10-20 | Scheduled Outage | Construction | ISOLATED 3 PHASE BANK X35323 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 1 | 351 | 6 | Central | TW22
139283 | 2018-10-20 | Defective Equipment | Imminent Failure | At 08:39am TP4291 was isolated to allow crew to replace leaking transformer. 1 customer affected. Startop (6F4) | None | None | 1 | 287 | 5 | East | 6F4
139284 | 2018-10-21 | Defective Equipment | Imminent Failure | planned outage to replace leaker | None | None | 1 | 70 | 1 | East | AP02
139287 | 2018-10-21 | Defective Equipment | Imminent Failure | A 13 Kv transformer at 850 Industrial was isolated to allow the crew to replace leaking transformer affecting 1 customers for 231 minutes on the TB14 circuit | U/G Transformer | Padmount (1ph) | 1 | 231 | 4 | East | TB14
139290 | 2018-10-22 | Defective Equipment | Mechanical Failure | crews isolated X26698 to safely work on the dip feeding V827 | O/H Conductor | Pigtail | 50 | 116 | 97 | Central | AD03
139292 | 2018-10-22 | Human Element | Switching Error | At 07:44am while switching there was an outage on the SK13 breaker affecting 359 customers. King Edward (SK13) | None | None | 359 | 1 | 6 | Central | SK13
139293 | 2018-10-22 | Scheduled Outage | Forced Switching | The 4Kv O/H line in the rear of 2629 Iris was isolated to allow the crews to transfer load back to UV05 W phase affecting 54 customers for 29 minutes on the UV07 circuiot | None | None | 54 | 29 | 26 | Central | UV07
139294 | 2018-10-22 | Foreign Interference | Wildlife (Bird/Animal) | Replaced blown fuse feeding transformer X43873 (squirrel contact) | O/H Transformer | O/H Transformer (1ph) | 7 | 74 | 9 | Central | TR3UY
139295 | 2018-10-22 | Defective Equipment | Imminent Failure | crew isolated transformer at 1508 beaverpond to perform leaking transformer, and soil remediation. 10 customers were affected. Cyrville CYRF1. | None | None | 10 | 420 | 70 | East | CYRF3
139296 | 2018-10-22 | Scheduled Outage | Construction | Isolated two transformers X32005 and X32021 to transfer secondary to new poles | None | None | 19 | 105 | 33 | Central | UC02
139297 | 2018-10-22 | Scheduled Outage | Building/ High Load Move | crew isolated overhead line feeding overhead transformer at 1742 bank to remove sign that was swinging with possiblity of contacting overhead line. . 4 customers were interrupted. Brookfield AF03 | None | None | 4 | 77 | 5 | East | AF03
139298 | 2018-10-22 | Foreign Interference | Wildlife (Bird/Animal) | 13KV vault, TN12363 at 70 Colombine was found with TN12363-L3 fuses blown due to animal conatct at TN12363-L5, affecting 1 customer. Hinchey TS (43005) | None | None | 1 | 380 | 6 | Central | 4305
139299 | 2018-10-23 | Scheduled Outage | Construction | 13KV overhead transformer, ST33, at 1047 New Orchard was isolated to replace switches and arresters, affecting 1 person. Lincoln Heights TS (TD06) | None | None | 1 | 47 | 1 | Central | TD06
139301 | 2018-10-23 | Defective Equipment | Imminent Failure | Replace leaking transfomer | None | None | 1 | 503 | 8 | East | BLKF3
139302 | 2018-10-23 | Scheduled Outage | Construction | Replace cables and transformer. | None | None | 12 | 413 | 83 | East | BCHF1
139303 | 2018-10-23 | Scheduled Outage | Maintenance | Vault VT254 at 415 Greenview was isolated for a meter repair. 1 customer affected. Lincoln Heights (5408) | None | None | 1 | 93 | 2 | Central | 5408
139304 | 2018-10-23 | Scheduled Outage | Maintenance | KT158 on Wooland Ave. was isolated to replace switches and arrestors. 5 customers affected. Lincoln Heights (TD06) | None | Padmount (1ph) | 5 | 35 | 3 | Central | TD06
139305 | 2018-10-23 | Scheduled Outage | Construction | X3168 Transfer to plant | None | O/H Transformer (1ph) | 7 | 210 | 24 | South | 200F2
139306 | 2018-10-23 | Scheduled Outage | Construction | 2 transformers, X30055 and X30065 isolated by crew to upgrade secondary buss and transfer plant | None | None | 20 | 297 | 99 | Central | SB06
139308 | 2018-10-23 | Scheduled Outage | Maintenance | Planned outage for oil leak remediation. | None | Padmount (1ph) | 12 | 521 | 104 | East | BLKF3
139310 | 2018-10-24 | Scheduled Outage | Construction | Remediation | None | None | 17 | 420 | 119 | South | 49F2
139311 | 2018-10-24 | Foreign Interference | Wildlife (Bird/Animal) | An animal contact caused TR03 breaker to open at Riverdale affecting the Y bus at VT8 (Carleton University) 1 customer affected. Riverdale (TR3UY) | Pole Attachement | Arrester | 1 | 138 | 2 | Central | TR3UY
139313 | 2018-10-24 | Defective Equipment | Imminent Failure | Replace leaking transformer. | None | None | 5 | 367 | 31 | East | BLKF4
139314 | 2018-10-24 | Scheduled Outage | Construction | Cable and transfromer replacement | None | None | 12 | 474 | 95 | East | BLKF4
139315 | 2018-10-24 | Scheduled Outage | Construction | Transformer replacement | None | None | 7 | 459 | 54 | East | BCHF1
139316 | 2018-10-24 | Defective Equipment | Imminent Failure | Replace damaged transformer. | U/G Transformer | Padmount (1ph) | 15 | 145 | 36 | East | LTM01
139317 | 2018-10-24 | Scheduled Outage | Maintenance | PT216 on New Orchard was isolated to replace switches and arrestors. 27 customers affected. Lincoln Heights (TD06) | U/G Transformer | Kiosk (3ph) | 27 | 60 | 27 | Central | TD06
139318 | 2018-10-24 | Scheduled Outage | Maintenance | KT489 on New Orchard was isolated to replace switches and arrestors. 7 customers affected. Lincoln Heights (TD06) | U/G Transformer | Kiosk (3ph) | 7 | 43 | 5 | Central | TD06
139320 | 2018-10-24 | Scheduled Outage | Maintenance | P73 on Sheffield Rd isolated to repair hot connection. 36 customers affected. Bantree (AL06) | None | Padmount (1ph) | 36 | 79 | 47 | East | AL06
139321 | 2018-10-25 | Scheduled Outage | Construction | Cable and transformer replacement | None | None | 11 | 445 | 82 | East | BLKF4
139322 | 2018-10-25 | Scheduled Outage | Construction | Cable and transformer replacement. | None | Unknown \ Other | 12 | 440 | 88 | East | BCHF1
139323 | 2018-10-25 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X32648 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 6 | 43 | 4 | Central | TD12
139324 | 2018-10-25 | Scheduled Outage | Construction | Cable and transformer replacement | None | Padmount (1ph) | 2 | 221 | 7 | East | BCHF1
139326 | 2018-10-26 | Scheduled Outage | Maintenance | A transformer on Smugglers Court was isolated to repair primary cables affecting 15 customers. Manordale 84F3 | None | XLPE | 15 | 309 | 77 | South | 84F3
139331 | 2018-10-27 | Scheduled Outage | Maintenance | Scheduled shutdown of VT238 to repair a metering problem. This will affect 1 customer on the 626 circuit out of Slater TS. | None | None | 1 | 165 | 3 | Central | 626
139334 | 2018-10-27 | Defective Equipment | Electrical Failure | Blue phase cable fault between TP8028 and S13785 | U/G Cable | XLPE | 8 | 238 | 32 | East | 77M6
139335 | 2018-10-27 | Scheduled Outage | Maintenance | Transformer X38374 at 466 Tillbury was isolated to reconnect a service. 7 customers affected. Hillcrest (AH04) | Secondary \ Service | O/H Service | 7 | 60 | 7 | Central | AH04
139336 | 2018-10-28 | Defective Equipment | Electrical Failure | Cable fault | U/G Cable | XLPE | 102 | 333 | 566 | East | 77M6
139339 | 2018-10-28 | Foreign Interference | Foreign Objects | OMS indicates an outage on the 190F5 affecting 532 customers. 24/7 found a plastic bag in the overhead. | O/H Switchgear | Fused Cutout | 347 | 38 | 220 | South | 190F5
139339 | 2018-10-28 | Foreign Interference | Foreign Objects | OMS indicates an outage on the 190F5 affecting 532 customers. 24/7 found a plastic bag in the overhead. | O/H Switchgear | Fused Cutout | 532 | 159 | 1410 | South | 190F5
139340 | 2018-10-28 | Defective Equipment | Mechanical Failure | 24/7 reported that the S25733 blue phase switch openned again. This affected 183 customers out of Parkwood Hills (190F5). | O/H Switchgear | Fused Cutout | 57 | 18 | 17 | South | 190F5
139340 | 2018-10-28 | Defective Equipment | Mechanical Failure | 24/7 reported that the S25733 blue phase switch openned again. This affected 183 customers out of Parkwood Hills (190F5). | O/H Switchgear | Fused Cutout | 183 | 122 | 372 | South | 190F5
139343 | 2018-10-29 | Defective Equipment | Imminent Failure | Leaking transformer replaced | None | None | 5 | 467 | 39 | East | BCHF5
139344 | 2018-10-29 | Scheduled Outage | Maintenance | Soil redediation | None | None | 6 | 553 | 55 | East | 77M6
139345 | 2018-10-29 | Defective Equipment | Defective Equipment/ Material | crew isolated overhead in the rear of 998 Gold to make the work area safe | O/H Switchgear | Fused Cutout | 120 | 55 | 110 | Central | TD05
139347 | 2018-10-30 | Scheduled Outage | Construction | Transformer TE1706 at 9 Cullen was isolated to allow crew to transformer and base. Transformers TE249, TE1707 and TE247 were also interrupted momentarly toa low crew to perfrom switching due to Hydro One switching restrictions. 37 customers were affected. | None | None | 0 | 1 | 0 | South | 84F2
139347 | 2018-10-30 | Scheduled Outage | Construction | Transformer TE1706 at 9 Cullen was isolated to allow crew to transformer and base. Transformers TE249, TE1707 and TE247 were also interrupted momentarly toa low crew to perfrom switching due to Hydro One switching restrictions. 37 customers were affected. | None | None | 8 | 394 | 53 | South | 84F2
139347 | 2018-10-30 | Scheduled Outage | Construction | Transformer TE1706 at 9 Cullen was isolated to allow crew to transformer and base. Transformers TE249, TE1707 and TE247 were also interrupted momentarly toa low crew to perfrom switching due to Hydro One switching restrictions. 37 customers were affected. | None | None | 29 | 1 | 0 | South | 84F2
139347 | 2018-10-30 | Scheduled Outage | Construction | Transformer TE1706 at 9 Cullen was isolated to allow crew to transformer and base. Transformers TE249, TE1707 and TE247 were also interrupted momentarly toa low crew to perfrom switching due to Hydro One switching restrictions. 37 customers were affected. | None | None | 37 | 1 | 1 | South | 84F2
139348 | 2018-10-30 | Scheduled Outage | Construction | Transformer TP4873 at 687 Laverendrye was isoalted to allow crew to repalce transformer and cables. 12 customers were affected. Beaconhill (BCHF1) | None | None | 12 | 477 | 95 | East | BCHF1
139350 | 2018-10-30 | Defective Equipment | Electrical Failure | S23774 W phase open due to cable fault between TP8190 and TP8191. 164 customers affected. Orleans (325M8) | U/G Cable | XLPE | 34 | 17 | 10 | East | 325M8
139350 | 2018-10-30 | Defective Equipment | Electrical Failure | S23774 W phase open due to cable fault between TP8190 and TP8191. 164 customers affected. Orleans (325M8) | U/G Cable | XLPE | 164 | 60 | 164 | East | 325M8
139351 | 2018-10-30 | Defective Equipment | Electrical Failure | 1 phase of S19209 was found burned up. To prevent damage to transformers and to saf, a Hydro Ottawa line crew opened the other two phases resulting in an outage to 42 customers | O/H Switchgear | Inline Switch | 42 | 272 | 190 | East | AL06
139352 | 2018-10-30 | Defective Equipment | Imminent Failure | A Hydro Ottawa line crew isolated KT754 so it could be replaced with TP12812 | None | Kiosk (1ph) | 12 | 124 | 25 | East | ELW04
139353 | 2018-10-30 | Scheduled Outage | Construction | TRANSFORMER BTTRQ8 UP-GRADE FROM 25KV TO 75KV | None | None | 1 | 82 | 1 | East | 77M6
139354 | 2018-10-30 | Human Element | Incorrect Records/ labelling | Transformer 664W at 1214 Tanguay was interrupted due incorrect nomenclature in the field. 9 customers were affected. Bridlewood (BRDF3) | None | None | 9 | 23 | 3 | West | BRDF3
139356 | 2018-10-31 | Unknown/Other | Unknown | Transformer #X36265 opened up, crew could not find cause | O/H Switchgear | Fused Cutout | 9 | 68 | 10 | South | EPWF4
139357 | 2018-10-31 | Tree Contacts | Tree Growth/ Untrimmed Tree | Not yet known. | None | None | 14 | 210 | 49 | Central | TK2AC
139359 | 2018-10-31 | Scheduled Outage | Construction | Three transformers were isolated on Pickford to reconfigure primary cables affecting 12 customers. Bridlewood BRDF3 | None | None | 12 | 311 | 62 | West | BRDF3
139360 | 2018-10-31 | Defective Equipment | Electrical Failure | Suspected cable fault between VT61 & TV10428 caused Lisgar TL21 (TL3TS/ TL5TS) to open. 638 customers in the Elgin / Laurier / Kent area affected. Customers restored in stages. | U/G Cable | PILC | 1 | 29 | 0 | Central | TL3TS
139360 | 2018-10-31 | Defective Equipment | Electrical Failure | Suspected cable fault between VT61 & TV10428 caused Lisgar TL21 (TL3TS/ TL5TS) to open. 638 customers in the Elgin / Laurier / Kent area affected. Customers restored in stages. | U/G Cable | PILC | 303 | 21 | 106 | Central | TL3TS
139360 | 2018-10-31 | Defective Equipment | Electrical Failure | Suspected cable fault between VT61 & TV10428 caused Lisgar TL21 (TL3TS/ TL5TS) to open. 638 customers in the Elgin / Laurier / Kent area affected. Customers restored in stages. | U/G Cable | PILC | 638 | 160 | 1701 | Central | TL3TS
139362 | 2018-11-01 | Scheduled Outage | Construction | Planned outage to install new secondary services. | None | O/H Service | 16 | 87 | 23 | Central | TD05
139363 | 2018-11-01 | Scheduled Outage | Construction | Cable and transformer replacement | None | None | 2 | 320 | 11 | East | BCHF1
139364 | 2018-11-01 | Scheduled Outage | Construction | Cable and transformer replacement | None | None | 2 | 370 | 12 | East | BCHF1
139366 | 2018-11-01 | Scheduled Outage | Construction | Transformer #X58914 isolated by crew to transfer plant | None | None | 14 | 270 | 63 | Central | UV03
139367 | 2018-11-01 | Scheduled Outage | Construction | Isolated TP12829 for the addition of a base. This outage will affect 14 customers on the 84F3. | None | None | 14 | 463 | 108 | South | 84F3
139369 | 2018-11-01 | Defective Equipment | Imminent Failure | Replace defective transformer leaker | U/G Transformer | Kiosk (1ph) | 9 | 337 | 51 | East | 77M2
139370 | 2018-11-01 | Loss Of Supply | Third Party | 13KV vault, VT25 at 410 Laurier was interrupted during switching due to defective customer owned equipment, affecting 1 customer. Lisgar TS (TL3TS) | None | None | 1 | 14 | 0 | Central | TL3TS
139372 | 2018-11-02 | Scheduled Outage | Construction | Overhead cirucit on Breamar from S23864 to EOL isolated to remove span of overhead. 12 customers affected. Beechwood (UB04) | None | O/H Conductor | 12 | 79 | 16 | East | UB04
139374 | 2018-11-03 | Defective Equipment | Mechanical Failure | Switch S20048 at 7298 Mitch Owens Dr hot line clamp was arcing. Crews opened switch to make repairs. | O/H Conductor | Hot-Line Clamp | 9 | 30 | 4 | East | 56F1
139375 | 2018-11-03 | Defective Equipment | Electrical Failure | The 6F10 circuit auto reclosed and caused the G223 R phase to open due to flashed insulator at TE330. Startop 6F10. 1196 customers were affected. | U/G Transformer | Padmount (1ph) | 12 | 203 | 41 | East | 6F10
139375 | 2018-11-03 | Defective Equipment | Electrical Failure | The 6F10 circuit auto reclosed and caused the G223 R phase to open due to flashed insulator at TE330. Startop 6F10. 1196 customers were affected. | U/G Transformer | Padmount (1ph) | 54 | 97 | 87 | East | 6F10
139377 | 2018-11-04 | Scheduled Outage | Construction | planned outage to transfer plant | None | None | 1 | 234 | 4 | Central | TD07
139379 | 2018-11-05 | Foreign Interference | Wildlife (Bird/Animal) | Transformer X27486 at 194 Crocus open due to squirrel contact. 5 customers were affected. Riverdale (505) | O/H Switchgear | Fused Cutout | 5 | 87 | 7 | Central | 505
139380 | 2018-11-05 | Defective Equipment | Imminent Failure | Replace leaking transformer TP8430. | None | None | 10 | 58 | 10 | East | 77M5
139382 | 2018-11-05 | Defective Equipment | Imminent Failure | Replace defective transformer. | U/G Transformer | Padmount (1ph) | 14 | 125 | 29 | South | FAL02
139383 | 2018-11-06 | Tree Contacts | Broken Branch | Tree bracnch | Station Equipment | Relay | 2355 | 23 | 903 | West | JKGF4
139384 | 2018-11-06 | Tree Contacts | Other Vegetation | CUT AND REMOVED VINES FROM THE POLE AND REFUSED SWITCH FEEDING TRANSFORMER X39690 | O/H Transformer | O/H Transformer (1ph) | 9 | 115 | 17 | South | 200F3
139386 | 2018-11-06 | Tree Contacts | Broken Branch | OMS indicates the G52 openned in the field. Field crews discovered the G613 had in fact openned due to tree contact. This affected 40 customers on the 8F1. | O/H Switchgear | Fused Cutout | 40 | 69 | 46 | East | 8F1
139389 | 2018-11-06 | Defective Equipment | Mechanical Failure | OMS indicates that the S28822 blue phase switch has openned. This outage is affecting 87 customers on the BRDF4 circuit. | U/G Cable | XLPE | 87 | 132 | 191 | West | BRDF4
139390 | 2018-11-06 | Human Element | Improper Design | Overloading caused transformer internal fuse to blow. | U/G Transformer | Padmount (1ph) | 14 | 1445 | 337 | South | FAL02
139391 | 2018-11-06 | Defective Equipment | Mechanical Failure | Defective Live line clamp | O/H Conductor | Hot-Line Clamp | 3 | 30 | 2 | South | 145F3
139392 | 2018-11-07 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 248 | 27 | 112 | Central | UX04
139392 | 2018-11-07 | Unknown/Other | Unknown | Not yet known. | Unknown \ Other | Unknown \ Other | 1334 | 27 | 600 | Central | UX06
139393 | 2018-11-07 | Defective Equipment | Imminent Failure | Crew isolated transformer at 1941 Innes to replace leaking transformer. One customer was affected. Cyrville CYRF1. | U/G Transformer | Padmount (3ph) | 1 | 98 | 2 | East | CYRF1
139394 | 2018-11-07 | Defective Equipment | Imminent Failure | crew isolated transformer at 15 Ridgeview for soil remediation. Five customers were affected. Richmond north RHNF3. | U/G Transformer | Padmount (1ph) | 5 | 373 | 31 | West | RHNF3
139395 | 2018-11-07 | Scheduled Outage | Construction | Planned outage for service upgrade. | None | O/H Service | 14 | 105 | 24 | East | AN04
139396 | 2018-11-07 | Scheduled Outage | Construction | Planned outage to install a new service. | None | O/H Service | 24 | 113 | 45 | Central | TR3UY
139397 | 2018-11-07 | Scheduled Outage | Construction | Crew isolated transformer at 5225 Boundry rd. to transfer to new overhead. Two customers were affected. Leitrim LTM02. | None | None | 2 | 82 | 3 | East | LTM02
139399 | 2018-11-07 | Scheduled Outage | Construction | At 09:00am P416 was isolated to allow crews to replace P416 with new TP12081. 1 customer affected. Queens (UQ03) | None | None | 1 | 317 | 5 | East | UQ03
139400 | 2018-11-07 | Scheduled Outage | Construction | Planned outage to transfer HOL plant to new poles. | None | Pole | 11 | 275 | 50 | Central | UC01
139401 | 2018-11-07 | Scheduled Outage | Construction | crew isolated two transformers at 709 Laverendrye to replace cable and transformer. Four customers were affected. Beaconhill BCHF1 | None | None | 4 | 448 | 30 | East | BCHF1
139402 | 2018-11-07 | Scheduled Outage | Construction | Planned outage to transfer HOL plant to new poles. | None | Pole | 8 | 275 | 37 | Central | UC01
139403 | 2018-11-07 | Defective Equipment | Imminent Failure | crew isolated transformer at 6066 Vineyard to replace leaking transformer. Ten customers were interrupted. Billberry 77M6. | U/G Transformer | Padmount (1ph) | 10 | 232 | 39 | East | 77M6
139404 | 2018-11-07 | Defective Equipment | Imminent Failure | Planned outage to replace leaking transformer. | U/G Transformer | Padmount (1ph) | 10 | 280 | 47 | East | 77M6
139405 | 2018-11-07 | Scheduled Outage | Construction | crew isolated transformer at 17 woodview for transformer and cable replacement. Eleven customers were affected. Blackburn BLKF4 | None | None | 4 | 412 | 27 | East | BLKF4
139406 | 2018-11-07 | Defective Equipment | Imminent Failure | Crew isolated transformer at 491 Beatrice for soil remediation. Seven customers were affected. Limebank LMBF7 | U/G Transformer | Padmount (1ph) | 7 | 545 | 64 | East | LMBF7
139407 | 2018-11-08 | Defective Equipment | Imminent Failure | Transformer TP6894 at 6412 Glen Knolls was isolated to allow crew to repalce leaking transformer. 12 customers were affected. Billberry (77M1) | U/G Transformer | Padmount (1ph) | 12 | 382 | 76 | East | 77M1
139408 | 2018-11-08 | Scheduled Outage | Construction | Transformers TP4256 and TP4257 at 2371 Ogilvie were isolated to allow crew to reaplce cable and transformers. 5 customers were affected. Beaconhill (BCHF1) | None | None | 5 | 412 | 34 | East | BCHF1
139410 | 2018-11-08 | Scheduled Outage | Construction | Transformer TE125 at 27 Woodburn was isolated to allow crew to repalce cables and transformer. 8 customers were affected. Blackburn (BLKF4) | None | None | 8 | 461 | 61 | East | BLKF4
139411 | 2018-11-08 | Defective Equipment | Imminent Failure | A Hydro Ottawa line crew isolated leaking transformer TE1408 so that it could be replaced. | U/G Transformer | Padmount (1ph) | 6 | 277 | 28 | East | 77M1
139412 | 2018-11-08 | Scheduled Outage | Construction | 180F4 R phase from Taps at 50 Holborn Ave to EOL was isolated to allow crew to transfer plant to new pole. 5 customers were affected. Rideau Heights (180F4) | None | None | 5 | 219 | 18 | South | 180F4
139413 | 2018-11-08 | Foreign Interference | Wildlife (Bird/Animal) | Replaced blown fuse feeding transformer X48651 (Bird contact) | O/H Transformer | O/H Transformer (1ph) | 19 | 45 | 14 | Central | TW18
139416 | 2018-11-08 | Foreign Interference | Wildlife (Bird/Animal) | Replaced blown fuse feeding transformer X40097 (Squirrel contact) | O/H Transformer | O/H Transformer (1ph) | 2 | 61 | 2 | West | MWDF3
139418 | 2018-11-08 | Scheduled Outage | Maintenance | Disconnected secondary Service. | Secondary \ Service | Secondary Pedestal | 8 | 28 | 4 | Central | TW22
139419 | 2018-11-08 | Scheduled Outage | Construction | Planned outage to transfer HOL plant to new pole. | Pole | Pole | 5 | 214 | 18 | South | 180F4
139420 | 2018-11-08 | Scheduled Outage | Construction | Planned outage to transfer HOL plant to new pole. | Pole | Pole | 4 | 215 | 14 | South | 180F4
139421 | 2018-11-08 | Scheduled Outage | Construction | Planned outage to transfer HOL plant to new pole. | Pole | Pole | 19 | 348 | 110 | Central | SB02
139422 | 2018-11-08 | Unknown/Other | Unknown | Primary fuse X4034 at 21 Kirkstall opened, cause not found. 25 customers affected. Woodroffe (170F1) | None | None | 12 | 73 | 15 | South | 170F1
139423 | 2018-11-09 | Defective Equipment | Imminent Failure | Transformer TE2609 at 6032 Pineglade was isolated to allow crew to repalce dammaged transformer. 10 customers were affected. Billberry (77M1) | None | None | 10 | 110 | 18 | East | 77M1
139424 | 2018-11-09 | Defective Equipment | Imminent Failure | Transformer TE1746 at 758 St. Andre was isolated to allow crew to replace leaking transformer. 17 customers were affected. Billerry (77M1) | U/G Transformer | Padmount (1ph) | 17 | 453 | 128 | East | 77M1
139425 | 2018-11-09 | Defective Equipment | Imminent Failure | Transformer TE1739 was isolated to allow crew to replace leaking transformer. 13 customers were affected. Billberry (77M1) | U/G Transformer | Padmount (1ph) | 13 | 277 | 60 | East | 77M1
139427 | 2018-11-10 | Scheduled Outage | Construction | P470 on Cecil Ave. wa isolates to transfer plant ot new poles. 1 customer affected. Brookfield (AF05) | None | None | 1 | 314 | 5 | East | AF05
139429 | 2018-11-10 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35632 opened up due to squirrel contact | O/H Switchgear | Fused Cutout | 15 | 34 | 8 | Central | TD12
139430 | 2018-11-10 | Scheduled Outage | Maintenance | Transformer #X33149 isolated by crew to make repairs to secondary damaged by slapping together in wind | None | None | 2 | 10 | 0 | Central | UV05
139431 | 2018-11-10 | Scheduled Outage | Maintenance | Transformer #X23418 isolated by crew to re-sag open buss secondary | None | None | 18 | 33 | 10 | East | AP03
139432 | 2018-11-10 | Human Element | Improper Design | High winds | None | None | 396 | 12 | 79 | East | AN05
139433 | 2018-11-10 | Scheduled Outage | Maintenance | At 9:37pm transformer X26939 was isolated to allow crews to repair loose triplex connection. 12 customers affected. Playfair (AJ04) | None | None | 12 | 73 | 15 | East | AJ04
139434 | 2018-11-11 | Foreign Interference | Vehicle | At 01:23am a pole was hit due to a car accident and tripped the circuit. 581 customers affected. Church (AA02) | None | None | 581 | 60 | 581 | East | AA02
139436 | 2018-11-11 | Scheduled Outage | Construction | VT510 at 180 Elgin was isolated to cut customer over to generator supply for vault replacment. 1 customer affected. Slater (626) | None | None | 1 | 218 | 4 | Central | 626
139437 | 2018-11-11 | Defective Equipment | Electrical Failure | Defective transformer | U/G Transformer | Kiosk (3ph) | 2 | 180 | 6 | West | TFXF2
139438 | 2018-11-11 | Scheduled Outage | Construction | At 10:54pm SB05 from X42936 to end of line was isolated to allow crew to replace section of overhead conductor. 72 customers affected. Bronson (SB05) | None | None | 72 | 291 | 349 | Central | SB05
139439 | 2018-11-12 | Foreign Interference | Other Utilities | ELW12 CB opened due to an MVA at Bank and Huntclub that caused a street light pole to fall and contact the overhead. 651 customers affected. Ellwood (ELW12) | Pole | Pole | 249 | 51 | 212 | East | ELW12
139439 | 2018-11-12 | Foreign Interference | Other Utilities | ELW12 CB opened due to an MVA at Bank and Huntclub that caused a street light pole to fall and contact the overhead. 651 customers affected. Ellwood (ELW12) | Pole | Pole | 651 | 37 | 401 | East | ELW12
139441 | 2018-11-12 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused transformer fuse to blow. | O/H Transformer | O/H Transformer (1ph) | 12 | 112 | 22 | Central | TW18
139443 | 2018-11-12 | Defective Equipment | Imminent Failure | Replace defective transformer. | U/G Transformer | Padmount (1ph) | 16 | 415 | 111 | East | 77M2
139444 | 2018-11-12 | Defective Equipment | Imminent Failure | Replace defective transformer | U/G Transformer | Padmount (1ph) | 12 | 383 | 77 | East | 77M1
139445 | 2018-11-12 | Loss Of Supply | Third Party | TB02 CB opened and SW187 at 1500 St. Laurent was found to be defective. 22 customers affected. Russell (5307) | U/G Switchgear | Live-Front | 2 | 778 | 26 | East | 5307
139445 | 2018-11-12 | Loss Of Supply | Third Party | TB02 CB opened and SW187 at 1500 St. Laurent was found to be defective. 22 customers affected. Russell (5307) | U/G Switchgear | Live-Front | 22 | 71 | 26 | East | 5307
139446 | 2018-11-13 | Scheduled Outage | Construction | GLTE0126 at 14 Woodburn was isolated to replace transformer & primary cables. 10 customers affeced. Blackburn BLKF4 | None | None | 10 | 458 | 76 | East | BLKF4
139447 | 2018-11-13 | Unknown/Other | Unknown | Leitrim LTM01 auto reclosed & LTM02 tripped open under hold off. Line patrolled & customer fuse at 5000 Hawthorne found open. No cause found for fuse to open. 4429 customers affected. | None | None | 936 | 59 | 920 | East | LTM02
139448 | 2018-11-13 | Defective Equipment | Imminent Failure | Leaking transformer replaced. | U/G Transformer | Padmount (1ph) | 12 | 258 | 52 | East | 77M2
139449 | 2018-11-13 | Defective Equipment | Imminent Failure | Leaking transformers TP9431 replaced | U/G Transformer | Padmount (1ph) | 9 | 322 | 48 | East | 77M1
139451 | 2018-11-13 | Scheduled Outage | Maintenance | 13KV vault, VT119 at 1909 Russell Rd. was isolated to repair metering, affecting 1 customer. Russell TS (5303) | Secondary \ Service | Meter | 1 | 82 | 1 | East | 5303
139453 | 2018-11-13 | Scheduled Outage | Vegetation Management | Outage requitred to move large tree from overhead line | None | None | 195 | 84 | 273 | West | 624F6
139454 | 2018-11-14 | Defective Equipment | Imminent Failure | TP12293 at 13 Coronet was isolated for soil remediation. 11 customers affected. Limebank 7F1. | U/G Transformer | Padmount (1ph) | 11 | 435 | 80 | East | 7F1
139455 | 2018-11-14 | Defective Equipment | Imminent Failure | TE1434 at 715 Dondale isolated to replace leaking transformer. 12 customers affected. Startop 6F1. | U/G Transformer | Padmount (1ph) | 12 | 162 | 32 | East | 6F1
139456 | 2018-11-14 | Scheduled Outage | Maintenance | Planned outage with Chris Costello to remove a service. | None | O/H Service | 4 | 54 | 4 | Central | AD03
139457 | 2018-11-14 | Defective Equipment | Imminent Failure | TE2967 at 2145 Appleleaf was isolated to replace leaking transformer. 9 customers affected. Cyrville CYRF3. | U/G Transformer | Padmount (1ph) | 9 | 89 | 13 | East | CYRF3
139458 | 2018-11-14 | Scheduled Outage | Construction | Planned outage with Marc Branchaud for service upgrade. | None | O/H Service | 7 | 78 | 9 | Central | 505
139459 | 2018-11-14 | Scheduled Outage | Construction | TE131 at 17 Woodburn isolated to replace transformer & primary cables. 11 customers affected. Blackburn BLKF4. | None | Padmount (1ph) | 11 | 446 | 82 | East | BLKF4
139460 | 2018-11-14 | Scheduled Outage | Maintenance | 4kv kiosk transformer, K798 at 3333 McCarthy was isolated to repair secondary pedestal, affecting 16 customers. McCarthy DS (AQ04) | None | Secondary Pedestal | 16 | 140 | 37 | East | AQ04
139462 | 2018-11-15 | Scheduled Outage | Construction | crew isolated the transformer at 34 Southpark to replace transformer and cables. Nine customers were affected. Blackburn BLKF4 | None | None | 9 | 465 | 70 | East | BLKF4
139464 | 2018-11-15 | Scheduled Outage | Maintenance | Transformer TE2189 at 5459 Canotek Dr was isolated to allow crew to reset transformer on pad. 7 Customers affected. Beaconhill (BCHF4) | None | None | 7 | 189 | 22 | East | BCHF4
139465 | 2018-11-15 | Scheduled Outage | Construction | Planned outage with Adam McNulty to transfer HOL plant to new poles. | None | Pole | 10 | 231 | 38 | Central | UL05
139466 | 2018-11-15 | Scheduled Outage | Construction | Planned outage with Mike Buyers for service upgrades. | None | O/H Service | 13 | 266 | 58 | Central | UV03
139467 | 2018-11-16 | Scheduled Outage | Forced Switching | VT86 at 100 Metcalfe interrupted to close a primary switch that cannot be operated on potential. 1 customer affected. Slater (602) | Vault Equipment | Switch | 1 | 10 | 0 | Central | 602
139468 | 2018-11-16 | Human Element | Switching Error | While isolating TP7575 crews failed to close TP3877-HA transformer switch to complete secondary parallel between 77m2 & 77M6 circuit. | U/G Transformer | Padmount (3ph) | 102 | 31 | 53 | East | 77M6
139469 | 2018-11-16 | Defective Equipment | Imminent Failure | crew isolated transformer at 1901 Rosewind to replace leaking transformer. Nine customers afftected. Cyrville CYRF3. | U/G Transformer | Padmount (1ph) | 9 | 242 | 36 | East | CYRF3
139470 | 2018-11-16 | Defective Equipment | Electrical Failure | defective transformer KT455 at 29 Oakley caused transformer KT456 at 45 Oakley to also open. 10 customers were intterupted. Lincoln TD12 | U/G Transformer | Kiosk (1ph) | 5 | 68 | 6 | Central | TD12
139470 | 2018-11-16 | Defective Equipment | Electrical Failure | defective transformer KT455 at 29 Oakley caused transformer KT456 at 45 Oakley to also open. 10 customers were intterupted. Lincoln TD12 | U/G Transformer | Kiosk (1ph) | 10 | 205 | 34 | Central | TD12
139471 | 2018-11-16 | Foreign Interference | Vehicle | S25487 at 2800 Huntley was opened to replace pole damaged by MVA. 1 customer affected. Richmond North RHNF3. | Pole | Pole | 1 | 405 | 7 | West | RHNF3
139472 | 2018-11-18 | Scheduled Outage | Construction | A section of primary was isolated on Clarkson to replace quick sleeves affecting 1 customer. Bridlewood BRDF4 | None | None | 1 | 206 | 3 | West | BRDF4
139473 | 2018-11-18 | Scheduled Outage | Maintenance | A transformer at 7 Carbrooke was isolated to replace Hydro Plant affecting 1 customer. Bridlewood BRDF3 | None | None | 1 | 217 | 4 | West | BRDF3
139474 | 2018-11-18 | Foreign Interference | Wildlife (Bird/Animal) | REFUSED BLOWN SWITCH THAT FEEDS TRANSFORMER X32634 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 17 | 89 | 25 | Central | TD14
139475 | 2018-11-18 | Foreign Interference | Wildlife (Bird/Animal) | REFUSED SWITCH FEEDING TRANSFORMER X13365 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 8 | 161 | 21 | East | LMBF5
139476 | 2018-11-19 | Defective Equipment | Imminent Failure | K1195 was isolated to allow a Hydro Ottawa U/G crew to replace K1195 with new TP12855 | None | None | 6 | 125 | 12 | East | UT05
139477 | 2018-11-19 | Scheduled Outage | Maintenance | S624 to EOL was isolated to allow crew to replace insulators. 57 customers were affected. Parkwoodhills (190F6) | None | None | 57 | 94 | 89 | South | 190F6
139478 | 2018-11-19 | Scheduled Outage | Construction | A K-line line crew opened X34320 at 549 Hilson to transfer secondary plant from X34320 to X57201. X34230 is to be removed from the system. 6 customers affected. Carling DS (SM15) | None | None | 6 | 12 | 1 | Central | SM15
139479 | 2018-11-19 | Scheduled Outage | Construction | Planned outage with K-Line to transfer HOL plant. | Pole | Pole | 13 | 30 | 6 | Central | SM15
139480 | 2018-11-19 | Unknown/Other | Unknown | Fuse S33-4R at 64 Winchester opened, no cause found. 50 customers affected. Bridlewood (BRDF7) | None | None | 50 | 130 | 108 | West | BRDF7
139481 | 2018-11-20 | Scheduled Outage | Construction | planned outage to move transformer | None | None | 1 | 257 | 4 | West | BECKF2
139483 | 2018-11-20 | Scheduled Outage | Construction | Planned outage with K-Line to run a new service. | Secondary \ Service | O/H Service | 9 | 52 | 8 | East | UG07
139484 | 2018-11-20 | Defective Equipment | Imminent Failure | To replace leaking TP7987 | U/G Transformer | Padmount (1ph) | 10 | 231 | 38 | East | CYRF3
139485 | 2018-11-20 | Defective Equipment | Imminent Failure | Replacing U/G transformer TP8014 | None | None | 13 | 79 | 17 | East | CYRF3
139486 | 2018-11-20 | Scheduled Outage | Construction | planned outage for transformer and cable replacement | None | None | 11 | 486 | 89 | East | BLKF4
139487 | 2018-11-21 | Defective Equipment | Imminent Failure | planned outage to change leakers | U/G Transformer | Padmount (1ph) | 28 | 526 | 245 | South | 170F1
139488 | 2018-11-21 | Scheduled Outage | Maintenance | To allow crews to transfer plant from White phase dip to Blue phase dip. | None | O/H Conductor | 10 | 20 | 3 | Central | SM15
139489 | 2018-11-21 | Scheduled Outage | Construction | To allow crews to transfer dip from red phase to blue phase at new pole X34235 | None | O/H Conductor | 12 | 74 | 15 | Central | SM15
139490 | 2018-11-21 | Scheduled Outage | Construction | Transformer #X58927 isolated by crew to transfer plant | None | None | 14 | 241 | 56 | Central | UV03
139491 | 2018-11-21 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35464 opened up due to animal contact | O/H Switchgear | Fused Cutout | 9 | 31 | 5 | Central | TD01
139492 | 2018-11-21 | Unknown/Other | Unknown | S126 opened up, no cause found | O/H Switchgear | Inline Switch | 7 | 171 | 20 | West | 624F6
139493 | 2018-11-21 | Scheduled Outage | Maintenance | K536 at 551 Hilson Ave was isolated to allow crews to transfer plant to new pole. | None | O/H Conductor | 10 | 29 | 5 | Central | SM15
139494 | 2018-11-21 | Scheduled Outage | Construction | K535 at 531 Hilson Ave was isolated to allow crews to prove spare duct and transfer plant to new pole. | None | None | 12 | 35 | 7 | Central | SM15
139495 | 2018-11-22 | Defective Equipment | Imminent Failure | TP8234 & TP8235 on Mary Jane cr were isolated to replace leaking transformers. 23 customers affected. Bilberry 77M2. | U/G Transformer | Padmount (1ph) | 23 | 526 | 202 | East | 77M2
139496 | 2018-11-22 | Defective Equipment | Mechanical Failure | AA05 down overhead wire at 394 Spartan, affecting 51 customers. Church DS (AA05) | O/H Conductor | O/H Conductor | 30 | 180 | 90 | East | AA05
139496 | 2018-11-22 | Defective Equipment | Mechanical Failure | AA05 down overhead wire at 394 Spartan, affecting 51 customers. Church DS (AA05) | O/H Conductor | O/H Conductor | 51 | 67 | 57 | East | AA05
139497 | 2018-11-23 | Scheduled Outage | Maintenance | 27KV padmount transforme at 1580 Telesat was isolated for realignement on cement pad, afecting 1 customer. Moulton MTS (8F3) | None | None | 1 | 148 | 2 | East | 8F3
139498 | 2018-11-23 | Scheduled Outage | Construction | Repair and reenrgize U/G service on X36194 | None | O/H Transformer (1ph) | 12 | 40 | 8 | South | EPWF3
139499 | 2018-11-23 | Foreign Interference | Wildlife (Bird/Animal) | Fuse on pole X56135 opened due to squirrel contact | O/H Transformer | O/H Transformer (1ph) | 6 | 84 | 8 | West | 28F3
139500 | 2018-11-23 | Defective Equipment | Imminent Failure | TP7091 at 1599 Grenoble was isolated to replace leaking transformer. 8 customers affected. Bilberry 77M6. | U/G Transformer | Padmount (1ph) | 8 | 421 | 56 | East | 77M6
139501 | 2018-11-24 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused overhead transformer at 21 Colonel Murray St to open. Eleven customers were affected. Richmond South (28F2) | O/H Transformer | O/H Transformer (1ph) | 11 | 138 | 25 | West | 28F2
139502 | 2018-11-24 | Scheduled Outage | Construction | crew isolated swichgear for primary reconfiguration, which also affected undergound transformer at 3000 soldant. One customer was affected. Kanata (624F4) | None | None | 1 | 251 | 4 | West | 624F4
139506 | 2018-11-26 | Scheduled Outage | Vegetation Management | Section of overhead line on Mitch owen and Bank st. was isolated for tree removal. 39 customers were affected. South gloucester (56F1) | None | None | 39 | 44 | 29 | East | 56F1
139508 | 2018-11-27 | Unknown/Other | Unknown | Richmond North RHNF3 tripped. Fire & police reported no issues, Breaker closed via scada. To be patrolled. 473 customers affected. | Unknown \ Other | Unknown \ Other | 473 | 12 | 95 | West | RHNF3
139509 | 2018-11-27 | Defective Equipment | Imminent Failure | TP8529 at 6031 Meadowglen Dr. was isolated for replacmenet due to an oil leak. 13 customers affected. Bilberry (77M5) | U/G Transformer | Padmount (1ph) | 13 | 267 | 58 | East | 77M5
139510 | 2018-11-27 | Scheduled Outage | Vegetation Management | Transformer #X23667 isolated by K-Line for tree removal | None | None | 14 | 34 | 8 | East | UB07
139511 | 2018-11-27 | Scheduled Outage | Construction | Install new secondaries. | None | None | 9 | 178 | 27 | East | AQ07
139514 | 2018-11-27 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X21473 TO INSTALL A NEW POLE | None | None | 9 | 187 | 28 | East | CAS-F2
139516 | 2018-11-27 | Scheduled Outage | Vegetation Management | K-Line isolating X23667 for forestry contractor | None | O/H Transformer (1ph) | 14 | 67 | 16 | East | UB07
139517 | 2018-11-27 | Defective Equipment | Mechanical Failure | Switch was broken, Opened up K1203, replaced broken switch | O/H Switchgear | Fused Cutout | 9 | 14 | 2 | East | UT12
139521 | 2018-11-28 | Scheduled Outage | Construction | Transfer plant to new poles. | None | None | 51 | 285 | 242 | Central | UV03
139524 | 2018-11-28 | Scheduled Outage | Maintenance | Reapair secondary conductors. | None | None | 10 | 75 | 12 | East | UA11
139525 | 2018-11-28 | Scheduled Outage | Vegetation Management | Tree trimming | None | None | 25 | 321 | 134 | Central | TD05
139528 | 2018-11-29 | Defective Equipment | Imminent Failure | planned outage to replace leaker | None | None | 12 | 75 | 15 | East | 325M8
139528 | 2018-11-29 | Defective Equipment | Imminent Failure | planned outage to replace leaker | None | None | 15 | 108 | 27 | East | 325M8
139529 | 2018-11-29 | Scheduled Outage | Maintenance | planned outage to make secondary repairs | None | None | 15 | 53 | 13 | East | BLKF4
139531 | 2018-11-29 | Scheduled Outage | Maintenance | Planned outage with K-Line to change leads on transformer. | O/H Transformer | O/H Transformer (1ph) | 36 | 10 | 6 | Central | SK09
139532 | 2018-11-29 | Scheduled Outage | Construction | Transformer #X26725 isolated by Bobby from Sproule to transfer plant to new pole | None | None | 2 | 68 | 2 | East | 4801F8
139533 | 2018-11-29 | Scheduled Outage | Maintenance | Planned outage with K-Line to remove a secondary service. | Secondary \ Service | O/H Service | 8 | 7 | 1 | Central | UN04
139534 | 2018-11-30 | Scheduled Outage | Construction | Transformer #X29267 isolated by crew to install new service, Bobby from Sproule | None | None | 8 | 32 | 4 | East | UG02
139536 | 2018-11-30 | Scheduled Outage | Construction | Transformer #X35179 isolated by crew for secondary upgrade | None | None | 6 | 190 | 19 | Central | UL14
139537 | 2018-11-30 | Scheduled Outage | Construction | Transformer #X17766 isolated by crew to replace a pole | None | None | 12 | 198 | 40 | East | 4801F8
139538 | 2018-12-01 | Scheduled Outage | Construction | TP3671 at 3877 Old Richmond rd was isolated to upgrade transformer. 1 customer affected. Bells Corners 47F3. | None | None | 1 | 203 | 3 | South | 47F3
139541 | 2018-12-03 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X34023 AND TRANSFERRED CUSTOMERS TO NEW TRANSFORMER X71441 | None | None | 18 | 292 | 88 | Central | UL04
139542 | 2018-12-03 | Defective Equipment | Imminent Failure | TP8000 at 1745 Aspenview was isolated to replace leaking transformer. 13 customers affected. Cyrville CYRF3. | U/G Transformer | Padmount (1ph) | 13 | 237 | 51 | East | CYRF3
139543 | 2018-12-04 | Defective Equipment | Imminent Failure | A transformer at 1678 Hunter's Run was isolated to replace a leaking transformer affecting 8 customers. Bilberry Creek 77M2 | U/G Transformer | Padmount (1ph) | 8 | 244 | 33 | East | 77M2
139544 | 2018-12-04 | Scheduled Outage | Construction | Transformer K692 was isolated to allow crew to prove ducts from transformer to pole riser. 1 customer was affected. Vaughan UG05 | None | None | 1 | 97 | 2 | East | UG05
139545 | 2018-12-04 | Defective Equipment | Imminent Failure | Transformer TE1435 at 1745 Dondale was isolated to allow a Hydro Ottawa U/G crew to replace a badly rusted transformer. 14 customers were affected. Startop DS (6F1) fed by Blackburn DS (BLKF4) at the time of the outage. | U/G Transformer | Padmount (1ph) | 14 | 117 | 27 | East | 6F1
139546 | 2018-12-04 | Foreign Interference | Vehicle | An excavator working in the area made contact with bell wires on Hydro Ottawa poles. This caused the O/H fuse to blow at S22186. 30 customers were affected. Bells Corners DS (47F3) | O/H Switchgear | Fused Cutout | 30 | 87 | 44 | South | 47F3
139547 | 2018-12-04 | Scheduled Outage | Construction | Transformer K537 at 121 Bruell was isolated to allow crew to transfer supply back to SM15 B phase. 19 customers were affecet. Carling (SM15)) | None | None | 19 | 181 | 57 | Central | SM15
139548 | 2018-12-04 | Scheduled Outage | Construction | Transformer #X21170 isolated by Jordan Foote from Kline to transfer plant to new pole | None | None | 11 | 420 | 77 | East | CAS-F1
139549 | 2018-12-04 | Defective Equipment | Mechanical Failure | A Hydro Ottawa on-call crew had to replace defective transformer X35764 at 8157 Bleeks Rd. 1 customer was affected. Munster DS (MUNF2) | O/H Transformer | O/H Transformer (1ph) | 1 | 226 | 4 | West | 43F3
139550 | 2018-12-05 | Scheduled Outage | Construction | A K-Line crew isolated a radial section of the CASF1 R phase and transformer X21129 so that all plant could be transferred to new poles. 4 customers were affected. Casselman DS (CASF1) | None | None | 4 | 309 | 21 | East | CAS-F1
139551 | 2018-12-05 | Scheduled Outage | Construction | Transformer K536 at 551 Hilson was isolated to allow contractor to replace cable section to transformer. 20 customers were affected. Carling SM15 | None | None | 20 | 132 | 44 | Central | SM15
139552 | 2018-12-05 | Defective Equipment | Imminent Failure | A Hydro Ottawa line crew isolated leaking TP8212 so it could be replaced. 15 customers affected. 325M8 (Orleans TS) being carried by 77M2 (Bilberry TS) at the time of this outage | U/G Transformer | Padmount (1ph) | 15 | 651 | 163 | East | 325M8
139553 | 2018-12-05 | Defective Equipment | Imminent Failure | A Hydro Ottawa U/G crew isolated TP4852 at 2220 Orient Park so that it could be replaced. The transformer was rusting badly. 10 customers were affected. Blackburn DS ( BLKF8) | U/G Transformer | Padmount (1ph) | 10 | 311 | 52 | East | BLKF8
139554 | 2018-12-05 | Scheduled Outage | Construction | ISOLATED TRANSFORMERS X26690 AND X25558 TO REPLACE SECONDARY BUSS BETWEEN TRANSFORMERS | None | None | 18 | 148 | 44 | Central | SM12
139555 | 2018-12-05 | Scheduled Outage | Construction | Transformer K535 at 531 Hilson was isolated to allow contractor to replace cable section to transformer. 13 customers were affected. Carling SM15 | None | None | 13 | 144 | 31 | Central | SM15
139556 | 2018-12-05 | Scheduled Outage | Construction | Planned outage with Jodan Foote ( K-line ) to transfer plant. | Pole | Pole | 4 | 300 | 20 | East | CAS-F1
139557 | 2018-12-05 | Scheduled Outage | Maintenance | Planned outage to run and connect street light wire. | Secondary \ Service | U/G Service | 8 | 46 | 6 | South | 47F3
139558 | 2018-12-05 | Scheduled Outage | Construction | Transformer #X26787 isolated by crew to replace secondary service | None | None | 7 | 39 | 5 | East | AE05
139559 | 2018-12-05 | Scheduled Outage | Construction | A Hydro Ottawa on-call U/G crew isolated TP10546 from S12631 so they could assist a contractor who did no have confined space training in pulling secondary cables into MH 4613CHZ at TP10546. 2 customers were affected. Epworth DS (EPWF5) | None | None | 2 | 190 | 6 | South | EPWF5
139560 | 2018-12-05 | Scheduled Outage | Construction | Transformer #X22614 isolated by Jordan Foote from Kline to transfer plant to new pole | None | None | 12 | 160 | 32 | East | CAS-F4
139563 | 2018-12-06 | Defective Equipment | Mechanical Failure | SCADA indicates the AJ04 circuit breaker is open. Outage affecting 238 customers. | U/G Cable Attachement | Pothead | 238 | 110 | 436 | East | AJ04
139565 | 2018-12-06 | Scheduled Outage | Construction | ISOLATED TWO TRANSFORMERS X25558 AND X25559 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 14 | 266 | 62 | Central | SM12
139566 | 2018-12-06 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X22667 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 3 | 235 | 12 | East | CAS-F4
139567 | 2018-12-06 | Scheduled Outage | Construction | Section of overhead on Shea Rd. was interrupted during planned switching due to an out of phase condition. 46 customers affected. Richmond North (RHNF1) | None | None | 46 | 3 | 2 | West | RHNF1
139568 | 2018-12-06 | Scheduled Outage | Construction | Planned outage with K-Line to transfer plant to new pole. | None | Pole | 2 | 180 | 6 | East | CAS-F4
139569 | 2018-12-06 | Scheduled Outage | Maintenance | S28332 opened to repair tangled conductors. 1 customer affected. Russell TB07. | None | Unknown \ Other | 1 | 93 | 2 | East | TB07
139572 | 2018-12-07 | Defective Equipment | Mechanical Failure | Defective split bolt in rear of 34 Fairhill required S411R to be opened to make repairs. | O/H Conductor | O/H Conductor | 17 | 179 | 51 | South | 84F2
139572 | 2018-12-07 | Defective Equipment | Mechanical Failure | Defective split bolt in rear of 34 Fairhill required S411R to be opened to make repairs. | O/H Conductor | O/H Conductor | 48 | 51 | 41 | South | 84F2
139573 | 2018-12-07 | Defective Equipment | Imminent Failure | TP8211 at 6372 Nugget Dr was isolated for replacement due to an oil leak. 12 customers affected. Orelans (325M8) | U/G Transformer | Padmount (1ph) | 12 | 136 | 27 | East | 325M8
139574 | 2018-12-07 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X26690 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 14 | 228 | 53 | Central | SM12
139575 | 2018-12-07 | Scheduled Outage | Construction | Planned outage with K-Line to transfer plant to new pole. | None | None | 9 | 280 | 42 | East | CAS-F2
139577 | 2018-12-07 | Defective Equipment | Imminent Failure | Repair damages overhead conductor | None | None | 1 | 74 | 1 | East | TB07
139578 | 2018-12-08 | Defective Equipment | Imminent Failure | 1 customer affected on Campeau Drive to replace a leaking transformer. Marchwood (MWDF1) | U/G Transformer | Padmount (1ph) | 1 | 233 | 4 | West | MWDF1
139581 | 2018-12-08 | Defective Equipment | Electrical Failure | Transformer X44973 was isolated to allow oncall crews to replace transformer. | O/H Transformer | O/H Transformer (1ph) | 15 | 449 | 112 | South | 49F6
139582 | 2018-12-09 | Scheduled Outage | Construction | To allow crews to replace hydro poles and transfer conductor for future SH02 & SH04 egress cables. | None | Pole | 14 | 445 | 104 | Central | SH04
139584 | 2018-12-09 | Tree Contacts | Broken Branch | branch across 2 phases | None | None | 439 | 72 | 527 | South | 47F3
139585 | 2018-12-10 | Scheduled Outage | Construction | To allow crew to transfer plant to new hydro pole at 55D 1C-0207 | None | None | 7 | 385 | 45 | Central | SM15
139587 | 2018-12-10 | Defective Equipment | Imminent Failure | planned outage to replace leaker | U/G Transformer | Padmount (1ph) | 13 | 473 | 102 | East | CYRF3
139588 | 2018-12-10 | Human Element | Improper Equipment/Tool/ Maintenance | Tree trimmer dropped branch on wire causing transformer use to open on UQ07. | None | None | 8 | 58 | 8 | East | UQ07
139589 | 2018-12-10 | Scheduled Outage | Construction | ISOLATED TRANSFORMERS X34228 AND X34229 TO TRANSFER HYDRO PLANT TO NEW POLES | None | None | 28 | 365 | 170 | Central | SM12
139590 | 2018-12-10 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33913 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 7 | 139 | 16 | Central | TW22
139593 | 2018-12-11 | Scheduled Outage | Construction | Planned outage for service upgrade. | None | None | 13 | 58 | 13 | Central | TW22
139594 | 2018-12-11 | Defective Equipment | Imminent Failure | At 09:43am TP8223 was isolated to allow crew to replace rusted out transformer. 12 customers affected. Orleans (325F8) | U/G Transformer | Padmount (1ph) | 12 | 139 | 28 | East | 325M8
139595 | 2018-12-11 | Defective Equipment | Imminent Failure | At 09:10am TE2659 was isolated to allow crews to replace leaking transformer. 8 customers affected. Cyrville (CYRF3) | U/G Transformer | Padmount (1ph) | 8 | 234 | 31 | East | CYRF3
139596 | 2018-12-11 | Defective Equipment | Imminent Failure | At 09:08am transformer TE2971 was isolated. Crews replaced leaking transformer. 13 customers affected. Cyrville (CYRF3) | U/G Transformer | Padmount (1ph) | 13 | 305 | 66 | East | CYRF3
139597 | 2018-12-11 | Scheduled Outage | Construction | At 09:05am PC10A#013985 was establied on S10181 to end of line to allow for the installation of a new pole. 38 customers affected. Stafford DS (200F2) | None | None | 38 | 73 | 46 | South | 200F2
139598 | 2018-12-11 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X21365 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 3 | 270 | 14 | East | CAS-F2
139601 | 2018-12-12 | Human Element | Switching Error | While restoring power the crews left transformer switch open at TP8034 and dumped off 44 customers during the order to restore. 44 customers affected. Billberry (77M6) | None | None | 44 | 41 | 30 | East | 77M6
139602 | 2018-12-12 | Scheduled Outage | Construction | Planned outage with Marc Branchaud for service upgrade. | None | None | 12 | 107 | 21 | East | TB15
139604 | 2018-12-12 | Tree Contacts | Tree Growth/ Untrimmed Tree | Brush was tangled up with transformer X13073 at 33 RYEBURN DR which cause the transformer fuse and G4W fuse to blow affecting 35 customers on the LMBF1 circuit for 55 minutes | O/H Switchgear | Fused Cutout | 35 | 55 | 32 | East | 7F1
139605 | 2018-12-12 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X34235 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 250 | 42 | Central | SM15
139606 | 2018-12-12 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X34230 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 6 | 250 | 25 | Central | SM15
139607 | 2018-12-12 | Foreign Interference | Wildlife (Bird/Animal) | Squirrel contact caused tranformer fuse to blow. | O/H Transformer | O/H Transformer (1ph) | 18 | 135 | 40 | Central | TW12
139609 | 2018-12-12 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X339448 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 7 | 250 | 29 | Central | UL04
139610 | 2018-12-12 | Scheduled Outage | Construction | ISOLATED TRANSFORMER X33925 TO TRANSFER HYDRO PLANT TO NEW POLE | None | None | 10 | 250 | 42 | Central | UL04
139612 | 2018-12-12 | Scheduled Outage | Construction | Planned outage with Adam McNulty to transfer plant. | None | None | 52 | 224 | 194 | Central | UF08
139613 | 2018-12-12 | Defective Equipment | Imminent Failure | A transformer at 1704 Boisbriand was isolated to replace a leaking transformer affecting 12 customers. Bilberry Creek 77M6 | U/G Transformer | Padmount (1ph) | 12 | 258 | 52 | East | 77M6
139615 | 2018-12-12 | Scheduled Outage | Maintenance | A transformer at 121 Markland was isolated to remediate soil from previous leaking transformer affecting 12 customers. Limebank 7F7 | None | None | 12 | 349 | 70 | East | LMBF7
139616 | 2018-12-13 | Scheduled Outage | Maintenance | Transformer KT33 at 3095 Uplands was isolated to allow crew to repair hot primary connection. 17 customers were affected. Albion (221) | None | None | 17 | 173 | 49 | East | 2211
139617 | 2018-12-13 | Defective Equipment | Imminent Failure | SPL line crews isolated defective TP11333 so it could be replaced. | U/G Transformer | Padmount (1ph) | 5 | 65 | 5 | West | TFXF4
139617 | 2018-12-13 | Defective Equipment | Imminent Failure | SPL line crews isolated defective TP11333 so it could be replaced. | U/G Transformer | Padmount (1ph) | 92 | 1 | 2 | West | TFXF4
139617 | 2018-12-13 | Defective Equipment | Imminent Failure | SPL line crews isolated defective TP11333 so it could be replaced. | U/G Transformer | Padmount (1ph) | 92 | 6 | 9 | West | TFXF4
139617 | 2018-12-13 | Defective Equipment | Imminent Failure | SPL line crews isolated defective TP11333 so it could be replaced. | U/G Transformer | Padmount (1ph) | 97 | 5 | 8 | West | TFXF4
139617 | 2018-12-13 | Defective Equipment | Imminent Failure | SPL line crews isolated defective TP11333 so it could be replaced. | U/G Transformer | Padmount (1ph) | 97 | 8 | 13 | West | TFXF4
139618 | 2018-12-12 | Scheduled Outage | Forced Switching | Forced outage due to switching restrictions to allow for a scheduled isolation in the area affecting 144 customers. Limebank LMBF7 | None | None | 144 | 83 | 199 | East | LMBF7
139619 | 2018-12-12 | Scheduled Outage | Forced Switching | Forced outage due to switching restrictions for scheduled restoration of an isolated transformer affecting 144 customers. Limebank LMBF7 | None | None | 144 | 1 | 2 | East | LMBF7
139620 | 2018-12-14 | Scheduled Outage | Construction | planned outage to install new customer service. | None | None | 2 | 127 | 4 | West | MWDF3
139623 | 2018-12-14 | Defective Equipment | Electrical Failure | the TB03 circuit breaker tripped while under hold off. Circuit was patrolled and nothing was found. At 17:49 pm circuit was closed in and crew reported cross arm on fire at 2700 St. Laurent. The TB03 and TB20 circuit auto reclosed at 17:50 and crew found | Pole Attachement | Arrester | 0 | 1 | 0 | East | 5310
139623 | 2018-12-14 | Defective Equipment | Electrical Failure | the TB03 circuit breaker tripped while under hold off. Circuit was patrolled and nothing was found. At 17:49 pm circuit was closed in and crew reported cross arm on fire at 2700 St. Laurent. The TB03 and TB20 circuit auto reclosed at 17:50 and crew found | Pole Attachement | Arrester | 0 | 29 | 0 | East | 5310
139623 | 2018-12-14 | Defective Equipment | Electrical Failure | the TB03 circuit breaker tripped while under hold off. Circuit was patrolled and nothing was found. At 17:49 pm circuit was closed in and crew reported cross arm on fire at 2700 St. Laurent. The TB03 and TB20 circuit auto reclosed at 17:50 and crew found | Pole Attachement | Arrester | 272 | 16 | 73 | East | 5310
139623 | 2018-12-14 | Defective Equipment | Electrical Failure | the TB03 circuit breaker tripped while under hold off. Circuit was patrolled and nothing was found. At 17:49 pm circuit was closed in and crew reported cross arm on fire at 2700 St. Laurent. The TB03 and TB20 circuit auto reclosed at 17:50 and crew found | Pole Attachement | Arrester | 272 | 63 | 286 | East | 5310
139624 | 2018-12-14 | Defective Equipment | Electrical Failure | the TB20 circuit breaker tripped while under hold off. Circuit was patrolled and nothing was found. At 17:49 pm circuit was closed in and crew reported cross arm on fire at 2700 St. Laurent. The TB03 and TB20 circuit auto reclosed at 17:50 and crew found | Pole Attachement | Arrester | 0 | 4 | 0 | East | 5309
139624 | 2018-12-14 | Defective Equipment | Electrical Failure | the TB20 circuit breaker tripped while under hold off. Circuit was patrolled and nothing was found. At 17:49 pm circuit was closed in and crew reported cross arm on fire at 2700 St. Laurent. The TB03 and TB20 circuit auto reclosed at 17:50 and crew found | Pole Attachement | Arrester | 0 | 29 | 0 | East | 5309
139624 | 2018-12-14 | Defective Equipment | Electrical Failure | the TB20 circuit breaker tripped while under hold off. Circuit was patrolled and nothing was found. At 17:49 pm circuit was closed in and crew reported cross arm on fire at 2700 St. Laurent. The TB03 and TB20 circuit auto reclosed at 17:50 and crew found | Pole Attachement | Arrester | 176 | 19 | 56 | East | 5309
139624 | 2018-12-14 | Defective Equipment | Electrical Failure | the TB20 circuit breaker tripped while under hold off. Circuit was patrolled and nothing was found. At 17:49 pm circuit was closed in and crew reported cross arm on fire at 2700 St. Laurent. The TB03 and TB20 circuit auto reclosed at 17:50 and crew found | Pole Attachement | Arrester | 176 | 60 | 176 | East | 5309
139626 | 2018-12-15 | Foreign Interference | Wildlife (Bird/Animal) | RE-FUSED SWITCH FEEDING TRANSFORMER X43901 SQUIRREL CONTACT | O/H Transformer | O/H Transformer (1ph) | 9 | 79 | 12 | Central | TR3UY
139632 | 2018-12-17 | Foreign Interference | Wildlife (Bird/Animal) | Animal contact cause fuse to blow. | O/H Transformer | O/H Transformer (1ph) | 3 | 144 | 7 | East | LTM02
139633 | 2018-12-17 | Defective Equipment | Imminent Failure | Planned outage to replace leaking transformer. | U/G Transformer | Padmount (1ph) | 24 | 175 | 70 | East | AA03
139634 | 2018-12-18 | Scheduled Outage | Construction | Transformer #X31628 isolated by crew to re-arrange plant | None | None | 10 | 42 | 7 | Central | SR06
139635 | 2018-12-18 | Scheduled Outage | Construction | Transformer #X21688 isolated by crew for a service upgrade | None | None | 8 | 73 | 10 | East | TB15
139636 | 2018-12-18 | Scheduled Outage | Construction | 2 transformers, X26665 and X34461 isolated by Mark from Kline for pole replacement, both removed and replaced with X71443 | None | None | 10 | 155 | 26 | Central | UL04
139639 | 2018-12-19 | Scheduled Outage | Maintenance | Planned outage on x30479 transfer to plant | O/H Transformer | O/H Transformer (1ph) | 13 | 135 | 29 | Central | SM03
139640 | 2018-12-19 | Scheduled Outage | Construction | Transformer #X35240 isolated by crew to install a new service, Mike from Kline | None | None | 13 | 63 | 14 | South | 84F6
139641 | 2018-12-19 | Scheduled Outage | Construction | Transformer #K560 isolated by Paul from JW Leslie to transfer plant | None | None | 11 | 20 | 4 | East | AJ06
139642 | 2018-12-19 | Scheduled Outage | Construction | Transformer #X33467 isolated by crew for a service upgrade | None | None | 16 | 47 | 13 | Central | TD05
139643 | 2018-12-20 | Defective Equipment | Imminent Failure | Transformer TP10637 at 12 marcasite Rd was isolated to allow the crew to replace leaking transformer, affecting 7 customers for 79 minutes on the BRDF4 circuit | U/G Transformer | Padmount (1ph) | 7 | 79 | 9 | West | BRDF4
139644 | 2018-12-20 | Scheduled Outage | Maintenance | Transfer to plant X31220 | O/H Transformer | O/H Transformer (1ph) | 15 | 100 | 25 | Central | SK11
139645 | 2018-12-21 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | XLPE | 76 | 15 | 19 | East | 77M6
139645 | 2018-12-21 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | XLPE | 88 | 87 | 128 | East | 77M6
139645 | 2018-12-21 | Defective Equipment | Electrical Failure | Not yet known. | U/G Cable | XLPE | 7606 | 17 | 2155 | East | 77M6
139646 | 2018-12-21 | Scheduled Outage | Maintenance | Repair metering | None | None | 1 | 60 | 1 | Central | 622
139647 | 2018-12-21 | Defective Equipment | Electrical Failure | A defective transformer TP8065 at 1464 BONNEVILLE CRES affecting 24 customers. Defective primary cable and defective secondary cables. Bilberry Creek (77M5) | U/G Transformer | Padmount (1ph) | 12 | 789 | 158 | East | 77M6
139647 | 2018-12-21 | Defective Equipment | Electrical Failure | A defective transformer TP8065 at 1464 BONNEVILLE CRES affecting 24 customers. Defective primary cable and defective secondary cables. Bilberry Creek (77M5) | U/G Transformer | Padmount (1ph) | 24 | 315 | 126 | East | 77M6
139648 | 2018-12-21 | Scheduled Outage | Construction | New service installation. Outage on X35005 was required | None | O/H Transformer (1ph) | 7 | 45 | 5 | Central | SB04
139649 | 2018-12-21 | Defective Equipment | Mechanical Failure | A transformer at 648 Chapel was interupted when a defective fused switch opened affecting 22 customers. Henderson UN04 | O/H Switchgear | Fused Cutout | 22 | 108 | 40 | Central | UN04
139650 | 2018-12-25 | Defective Equipment | Electrical Failure | At 03:57am G901R blew due to arching. 202 customers affected. Leitrim (LTM02) | O/H Switchgear | Fused Cutout | 202 | 199 | 670 | East | LTM02
139651 | 2018-12-25 | Defective Equipment | Electrical Failure | Cable fault between TP7885 and TP7886 affecting 14 customers. | U/G Cable | XLPE | 14 | 91 | 21 | West | MWDF3
139652 | 2018-12-25 | Human Element | Protection Setting | Due to a previous outage, the open point was used to carry the load, the oppen point was undersized and blew. Crew re-sized the fuse and restored all power | None | None | 202 | 152 | 512 | East | LTM02
139654 | 2018-12-26 | Defective Equipment | Electrical Failure | At 09:59am 145F2 breaker was opened via SCADA to allow crew to open switch S805B that was burning up. 757 customers affected. Jockvale (145F2) | O/H Switchgear | Fused Cutout | 61 | 36 | 37 | South | 145F2
139654 | 2018-12-26 | Defective Equipment | Electrical Failure | At 09:59am 145F2 breaker was opened via SCADA to allow crew to open switch S805B that was burning up. 757 customers affected. Jockvale (145F2) | O/H Switchgear | Fused Cutout | 757 | 1 | 13 | South | 145F2
139655 | 2018-12-26 | Defective Equipment | Defective Equipment/ Material | Cable fault between transformers TP7550 and TP7551 caused the switch S13601 R phase to open at 1652 Westport. 148 customers were affected. Billberry (77M6) | U/G Cable | XLPE | 91 | 38 | 58 | East | 77M6
139655 | 2018-12-26 | Defective Equipment | Defective Equipment/ Material | Cable fault between transformers TP7550 and TP7551 caused the switch S13601 R phase to open at 1652 Westport. 148 customers were affected. Billberry (77M6) | U/G Cable | XLPE | 148 | 120 | 296 | East | 77M6
139656 | 2018-12-27 | Scheduled Outage | Construction | Transformer #X30285 isolated by crew to reconnect services previously disconnected for tree work | None | None | 10 | 55 | 9 | Central | TH15
139657 | 2018-12-28 | Defective Equipment | Mechanical Failure | A defective switch at 717 Hemlock caused an outage affecting 97 customers. Beechwood UB07 | O/H Switchgear | Inline Switch | 97 | 197 | 318 | East | UB07
139659 | 2018-12-29 | Defective Equipment | Electrical Failure | crew refused switch S15152 at 717 Hemlock. 97 customers were affected. Beechwood UB07. | O/H Switchgear | Inline Switch | 97 | 154 | 249 | East | UB07
139660 | 2018-12-29 | Defective Equipment | Mechanical Failure | crew opened 4kv Kiosk transformer at 1328 Holmes cres to effect repairs to secondary pedestal. 14 customers were interupted. Cahill AN06 | Secondary \ Service | Secondary Pedestal | 14 | 77 | 18 | East | AN06
139661 | 2018-12-31 | Foreign Interference | Wildlife (Bird/Animal) | REPLACED BLOWN FUSE FEEDING TRANSFORMER X46708 (SQUIRREL CONTACT) | O/H Transformer | O/H Transformer (1ph) | 11 | 134 | 25 | Central | TW17
139662 | 2018-12-31 | Defective Equipment | Mechanical Failure | S12168 at 1861 Saunderson Dr opened due to defective fuse. | O/H Switchgear | Fused Cutout | 32 | 68 | 36 | East | TB15
139663 | 2019-01-01 | Defective Equipment | Electrical Failure | S16879 B at 2635 Hickson opened due to a defective fuse. 28 customers affected. Edwin (UV07) | O/H Switchgear | Fused Cutout | 28 | 114 | 53 | Central | UV07
139664 | 2019-01-02 | Scheduled Outage | Construction | Install new service. | Secondary \ Service | O/H Service | 11 | 78 | 14 | Central | TD06
139665 | 2019-01-02 | Scheduled Outage | Construction | Planned outage to install new service. | Secondary \ Service | O/H Service | 2 | 73 | 2 | Central | SH04
139666 | 2019-01-02 | Scheduled Outage | Construction | Transformer #X32071 isolated by crew due to guy wire lying across 3 phase transformer | None | None | 2 | 11 | 0 | Central | UC10
139667 | 2019-01-02 | Scheduled Outage | Construction | Transformer #TP3972 isolated by crew due to defective U/G service | None | None | 12 | 46 | 9 | East | BCHF5
139668 | 2019-01-04 | Defective Equipment | Electrical Failure | The secondary cables fed out of KT103 were isolated to allow a Hydro Ottawa U/G crew to repair a secondary cable that had faulted. 13 customers were affected. Ellwood TS (ELW07) | Secondary \ Service | U/G Service | 13 | 51 | 11 | East | ELW07
139671 | 2019-01-08 | Scheduled Outage | Vegetation Management | Planned outage with Marc Branchaud. Asplund to do secondary tree trimming. | None | None | 10 | 145 | 24 | East | SO02
139672 | 2019-01-08 | Scheduled Outage | Construction | Planned outage to rearrange HOL plant. | None | O/H Service | 2 | 147 | 5 | West | 28F2
139673 | 2019-01-08 | Defective Equipment | Electrical Failure | Defective transformer. | O/H Transformer | O/H Transformer (1ph) | 14 | 366 | 85 | South | 49F6
139674 | 2019-01-09 | Defective Equipment | Defective Equipment/ Material | damaged conductor | O/H Conductor | Ampact | 32 | 59 | 31 | South | 47F3
139674 | 2019-01-09 | Defective Equipment | Defective Equipment/ Material | damaged conductor | O/H Conductor | Ampact | 54 | 57 | 51 | South | 47F3
139675 | 2019-01-09 | Foreign Interference | Wildlife (Bird/Animal) | Outage rolled up to primary switch S22984, . Found open transformer X32095 and dead squirell. | O/H Transformer | O/H Transformer (1ph) | 9 | 63 | 9 | Central | TD01
139676 | 2019-01-09 | Scheduled Outage | Construction | Scheduled outage with Corey Brown to transfer plant X18766 | None | O/H Transformer (1ph) | 5 | 155 | 13 | East | BLKF3
139677 | 2019-01-10 | Scheduled Outage | Maintenance | switch maintenance | None | None | 2 | 181 | 6 | East | 2206
139679 | 2019-01-10 | Scheduled Outage | Construction | Planned outage with K-Line to run new secondary. | None | None | 5 | 70 | 6 | East | 8F3
139680 | 2019-01-10 | Scheduled Outage | Construction | Planned outage with Chris Costello to ionstall new secondary service. | None | O/H Service | 18 | 40 | 12 | Central | SB03
139681 | 2019-01-10 | Scheduled Outage | Construction | Install new poles and remove old pole line. | None | None | 6 | 212 | 21 | West | BECKF2
139682 | 2019-01-10 | Defective Equipment | Electrical Failure | Blown transformer fuse. | U/G Transformer | Padmount (1ph) | 12 | 34 | 7 | East | BCHF5
139684 | 2019-01-10 | Scheduled Outage | Maintenance | To allow crews to replace porcelian switches and arrestors. | None | Arrester | 1 | 38 | 1 | Central | TD06
139685 | 2019-01-11 | Scheduled Outage | Construction | Replace defective insulator. | None | None | 1 | 40 | 1 | West | RHNF1
139686 | 2019-01-12 | Scheduled Outage | Construction | planned outage to replace a pole on Cambrian rd. | None | None | 5 | 188 | 16 | South | 145F3
139687 | 2019-01-14 | Foreign Interference | Vehicle | K1289 & K1290 were hit by a snow plow. Hydro Ottawa line crews isolated both kiosks so that they could safely be placed back on their base. 30 customers affected. Nepean DS (AB07) | None | None | 30 | 60 | 30 | Central | AB07
139688 | 2019-01-14 | Defective Equipment | Electrical Failure | Defective transformer at 50 Savage TP9019 | U/G Transformer | Padmount (1ph) | 16 | 107 | 29 | West | JKGF5
139688 | 2019-01-14 | Defective Equipment | Electrical Failure | Defective transformer at 50 Savage TP9019 | U/G Transformer | Padmount (1ph) | 49 | 147 | 120 | West | JKGF5
139689 | 2019-01-14 | Scheduled Outage | Construction | Defective transformer | None | None | 1 | 145 | 2 | West | MWDF2
139690 | 2019-01-15 | Scheduled Outage | Construction | Cory from K-Line Transfer to plant | None | O/H Transformer (1ph) | 3 | 110 | 6 | East | LTM04
139691 | 2019-01-15 | Scheduled Outage | Construction | X5250 Trnsfr to plant | None | O/H Transformer (1ph) | 1 | 170 | 3 | South | 180F3
139692 | 2019-01-15 | Scheduled Outage | Construction | Transformer K692 at 541 Acacia was isolated to allow crews to replace transformer, affecting 2 customers on the UG05 circuit for 251 minutes | None | Kiosk (1ph) | 2 | 251 | 8 | East | UG05
139693 | 2019-01-15 | Scheduled Outage | Construction | 3 transformers, X31627, X316258 and X31629 isolated by crew to transfer plant | None | None | 16 | 294 | 78 | Central | SR06
139694 | 2019-01-15 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X35695 opened up due to animal contact | O/H Switchgear | Fused Cutout | 8 | 49 | 7 | Central | TD12
139695 | 2019-01-15 | Scheduled Outage | Construction | Line Crew to have switch S25784 open to install a new pole. This will affect two customers on the 44F1 circuit out of Janet King DS. | None | None | 2 | 66 | 2 | West | 44F1
139696 | 2019-01-16 | Unknown/Other | Unknown | Station breaker opened with no attempt to reclose no apparent cause found. 274 customers affected. Walkley (UZ12) | None | None | 274 | 31 | 142 | East | UZ12
139697 | 2019-01-16 | Defective Equipment | Imminent Failure | A transformer at 1319 Maxime St was opened in order to replace a tracking lightning arrester affecting 18 customers. Moulton (8F3) | Pole Attachement | Arrester | 18 | 15 | 4 | East | 8F3
139698 | 2019-01-16 | Scheduled Outage | Construction | TB06 oh from temp 34 on saunderson rd was isolated by the crew to allow them to change three poles. Affecting 45 customers for 280 minutes. | None | Pole | 45 | 280 | 210 | East | TB06
139699 | 2019-01-16 | Scheduled Outage | Construction | Isolate TD12 oh section from x35634 to eol at 58 scrivens, to install pole and transfer plant. Affecting 7 customers for 139 minutes. | None | Pole | 7 | 139 | 16 | Central | TD12
139700 | 2019-01-16 | Scheduled Outage | Construction | TO PLANT A NEW POLE X35698 | None | Pole | 7 | 155 | 18 | Central | TD12
139702 | 2019-01-17 | Scheduled Outage | Construction | MIKE IRVEN TRANSFER TO PLANT UPGRADE | None | O/H Transformer (1ph) | 13 | 55 | 12 | Central | SM10
139703 | 2019-01-17 | Scheduled Outage | Maintenance | at 10:52 am, K223 was isolated for transformer maintenance. 1 customer affected. Eastview (UT02) | None | None | 1 | 28 | 0 | East | UT02
139704 | 2019-01-17 | Scheduled Outage | Construction | Shawn from K-Line Transfer to plant | None | O/H Transformer (1ph) | 4 | 205 | 14 | Central | AK06
139705 | 2019-01-18 | Scheduled Outage | Construction | Dave Macdonald installing new service X36638 | None | O/H Transformer (1ph) | 9 | 65 | 10 | South | EPWF1
139707 | 2019-01-18 | Foreign Interference | Wildlife (Bird/Animal) | Transformer #X48071 opened up due to animal contact | O/H Switchgear | Fused Cutout | 22 | 108 | 40 | East | TB15
139709 | 2019-01-19 | Defective Equipment | Defective Equipment/ Material | Suspected cable fault between 2547R and 2548R. | U/G Cable | Unknown \ Other | 15 | 63 | 16 | West | 39F3
139709 | 2019-01-19 | Defective Equipment | Defective Equipment/ Material | Suspected cable fault between 2547R and 2548R. | U/G Cable | Unknown \ Other | 51 | 125 | 106 | West | 39F3
139710 | 2019-01-19 | Adverse Weather | Ice/Icing | Not yet known. | O/H Switchgear | Inline Switch | 42 | 9 | 6 | South | 170F1
139710 | 2019-01-19 | Adverse Weather | Ice/Icing | Not yet known. | O/H Switchgear | Inline Switch | 113 | 65 | 122 | South | 170F1
139711 | 2019-01-21 | Tree Contacts | Broken Branch | Secondary open wire bus wrapped together due to tree contact. | Secondary \ Service | O/H Service | 8 | 93 | 12 | South | 170F1
139714 | 2019-01-21 | Adverse Weather | Extreme Wind | Transformer #X13340 opened up due to secondary open wire buss wrapped together causing sparks | O/H Switchgear | Fused Cutout | 8 | 134 | 18 | East | LMBF5
139715 | 2019-01-21 | Unknown/Other | Unknown | CB1 Trip at VT178. Cause currently under investigation. Suspected loading issue. 5405 Circuit out of Lincoln Heights. 1 Customer affected. | Vault Equipment | Breaker \ Relay | 1 | 371 | 6 | Central | 5405
139717 | 2019-01-22 | Defective Equipment | Defective Equipment/ Material | suspected bad transformer | U/G Transformer | Kiosk (1ph) | 11 | 379 | 69 | East | 77M6
139718 | 2019-01-22 | Defective Equipment | Electrical Failure | Suspect cable fault on the 4305 circuit. Between TV12359 and TV12355. Ststaions crew Thomas Anderson and James Zolty on scene for troubleshooting. | U/G Cable | Unknown \ Other | 1 | 738 | 12 | Central | 4305
139719 | 2019-01-22 | Scheduled Outage | Maintenance | ISOLATED TRANSFORMER X07562 TO REPLACE SWITCH AND ARRESTER | None | None | 1 | 9 | 0 | West | MWDF3
139720 | 2019-01-22 | Human Element | Protection Setting | Customer problem with Hvac unit causing primary fuse on transformer to blow in V742. 1 customer was affected. King Edward (SK10). | Customer Owned | Customer-Owned | 1 | 537 | 9 | Central | SK10
139722 | 2019-01-23 | Scheduled Outage | Maintenance | Transformer replaced due to damaged secondary bus. | U/G Transformer | Padmount (1ph) | 3 | 126 | 6 | East | LMBF7
139723 | 2019-01-23 | Scheduled Outage | Construction | ISOLATED AND REPLACED TRANSFORMER X3181 | None | None | 18 | 143 | 43 | South | 200F2
139724 | 2019-01-23 | Scheduled Outage | Maintenance | Repair made to secondary pedaestal | Secondary \ Service | U/G Service | 11 | 193 | 35 | East | BCHF3

## Pre Jul 2012
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR EPRF-84 Attachment A ORIGINAL
List of Outage Information - Pre July 2012
ID | Year_Out | Month_Out | Day_Out | First Of time out | Last Of time in | Sum Of Duration | Sum Of CustHours | Max of Number Customers | First Of Station | First Of Voltage | First Of Circuit | FirstOfComments | First Of Office | First Of Primary Cause | First Of Secondary Cause
3936 | 2003 | 8 | 25 | 0.84028 |  | 30 | 7 | 14 |  |  |  | Transformer OTT#6050 was isolated to allow for the replacement of a defective switch. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15257 | 2009 | 10 | 14 | 0.42361 |  | 422 | 21 | 3 |  | 4.16kV |  | Three 4kV vaults on Springland were isolated at the same time to allow contractor to clean and torque the connections in all three vaults. |  | Scheduled Outage | Preventive Maintenance
4628 | 2003 | 12 | 18 | 0.55903 |  | 49 | 3 | 4 |  |  |  | Transformer at the rear of 586 Westminister, in the Westborough area of Ottawa, was isolated to allow for the installation of a new service wire. ID#4628 | Ottawa | Scheduled Outage | Construction
4630 | 2003 | 12 | 18 | 0.43472 |  | 14 | 2 | 7 |  |  |  | Transformer #4744 at 580 O'Connor, in the downtown area of Ottawa, was isolated to allow for a pole change. ID#4630 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7754 | 2005 | 12 | 23 | 0.17431 |  | 155 | 1255 | 740 | Lincoln | 13.2kV |  | Flash reported on the overhead at 2900 Carling, patrolled but nothing found | Ottawa | Unknown/Other | No Apparent Cause
7987 | 2006 | 3 | 3 | 0.61389 |  | 161 | 86 | 32 | Wonderland | 8/4.8kV | F2 | Hydro One reports blue phase floating conductor caused power outage. (32 Hydro Ottawa transfer customers) | Goulburn | Loss of Supply
8091 | 2006 | 4 | 1 | 0.7125 |  | 308 | 929 | 279 | BECKWITH | 27.6/16kV | F2 | CAR HIT A POLE ON ASHTON STATION RD. BETWEEN SW1546 RWB AND SW228 CAUSING THE BECKWITH F2 TO TRIP. METERING UNIT ON POLE NEEDS TO BE REMOVED H1 IS WORKING ON POLE UNDER HYDRO OTTAWA PROTECTION. | Goulburn | Foreign Interference | Vehicle
9553 | 2006 | 10 | 29 | 0.71875 |  | 415 | 1143 | 200 | BECKWITH | 27.6/16kV | F2 | Tree Fallen on white and blue phase run off at DwyerHill &Hwy 7 causing Beckwith F2 Reclosers to trip. Tree removed and power restored. | Goulburn | Tree Contacts | Tree Fallen
16612 | 2010 | 8 | 3 | 0.56597 |  | 40 | 12 | 18 | WOODROOFE | 4.16kV | UW14 | Transformer X32772 at 2047 Kingsley isolated to renew connections at pole | Ottawa | Scheduled Outage | Repair
11764 | 2007 | 11 | 25 | 0.26389 |  | 415 | 227 | 40 | Wonderl, Blacks Cor | 8/4.8kV | Wond, Blacks C | Planned outage to H - 1 stations Wonderland (8kv) & Blacks Corners (8kv) affected Hydro - Ottawa transfer customers on Ashton Station rd. When stations re-energized, Blacks Corners F1 tripped resulting in extended outage for transfer customers at the S. end of Ashton Station rd. Hydro -Ottawa customers on Beckwith F2 supply transferred to Alexander supply & not affected. | Goulburn | Scheduled Outage | Preventive Maintenance
12328 | 2008 | 4 | 23 | 0.40625 |  | 145 | 27 | 11 | Riverdale | 13.2kV | 09:45 | Transformer #X29764 located at 21 Burnham Rd isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
4672 | 2004 | 1 | 4 | 0.15278 |  | 90 | 16 | 11 | Borden Farm | 8/4.8kV | 130 F1 | transformer #4038 at 30 Glenmanor a 75kva, 8kv transformer fuse blown and replaced ID# 4672 | Nepean | Unknown/Other | No Apparent Cause
3862 | 2003 | 8 | 6 | 0.68403 |  | 181 | 211 | 70 | Borden Farm | 8/4.8kV | 130 F5 | New fuse installed and holding. | Nepean | Adverse Weather | Rain
4677 | 2004 | 1 | 5 | 0.40972 |  | 20 | 2 | 6 | Borden Farms | 8/4.8kV | 130F1 | Transformer 4308 at 30 Glenmanor off to replace transformer switch. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
6274 | 2005 | 3 | 13 | 0.30556 |  | 96 | 64 | 40 | Borden Farms | 8/4.8kV | 130F1 | A 44Kv insulator on the 22M24 broke and fell into the 130F1 8Kv circuit which caused it to auto reclosed and blew a fuse at switch 477 @ 16 Glenmanor, also an arrestor blew at 25 Glenmanor. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17748 | 2011 | 3 | 21 | 0.66597 |  | 45 | 14 | 18 | BORDEN FARMS | 8/4.8kV | 130F1 | Transformer X36769 at 135 Viewmount Dr isolated to replace service | Nepean | Scheduled Outage | Construction
17886 | 2011 | 4 | 11 | 0.22222 |  | 15 | 171 | 683 | Borden farm | 8/4.8kV | 130F1 | 130F1 tripped, closed & held | Nepean | Unknown/Other
17997 | 2011 | 4 | 27 | 0.45833 |  | 33 | 376 | 683 | Borden Farm | 8/4.8kV | 130F1 | 130F1 tripped (under hold off) and 130F4 auto reclosed. Crane contacted overhead circuit at the rear of 220 Viewmount. | Nepean | Foreign Interference
14342 | 2009 | 5 | 11 | 0.39236 |  | 65 | 6 | 6 | Borden Farms | 8/4.8kV | 130F1 | Transformer #X33242 located at 7 Glenridge Rd isolated to transfer plant to new pole | Nepean | Scheduled Outage | Preventive Maintenance
6725 | 2005 | 6 | 15 | 0.069444 |  | 287 | 33 | 7 | Borden Farm | 8/4.8kV | 130F1 | Crew replaced cutout that opened feeding transformer T4309. Cutout was damaged due to thunderstorm activity. | Nepean | Adverse Weather | Lightning
5465 | 2004 | 7 | 8 | 0.39931 |  | 106 | 68 | 41 | Borden Farm | 8/4.8kV | 130F1 | 2 Overhead phase failed at the rear of Merivale Mall. Both phases came down. Overhead circuit was isolate to allow crews to repair conductor at the rear of Merivale Mall. Approx 40 Customers affected in power outage which includes Merivale Mall. 130F1 breaker did not open or auto reclose. Tree at the rear of Merivale Mall caused overhead circuit to burn down. | Nepean | Tree Contacts | Tree Limb Fallen
3894 | 2003 | 8 | 12 | 0.65972 |  | 70 | 36 | 31 | Borden Farm | 8/4.8kV | 130F1 | Switch 457 opened causing an outage to 3 o/h Tx's on Kingsbury, Viewmount & Glenmanor. Tx # 1257, 4319, 4230. | Nepean | Unknown/Other
13168 | 2008 | 8 | 29 | 0.42778 |  | 64 | 15 | 14 | Borden Farm | 8/4.8kV | 130F1 | Refused switch to transformer 4306 at the rear of 1674 Merivale Rd that opened due to contact with vines | Nepean | Tree Contacts | Inadequate Trimming
11246 | 2007 | 9 | 5 | 0.33472 |  | 238 | 178 | 45 | Borden Farms | 8/4.8kV | 130F1 | PC10A# 004169 established for B phase overhead section at 166 Viewmount to allow crew for tree trimming | Nepean | Scheduled Outage | Preventive Maintenance
7434 | 2005 | 10 | 7 | 0.3375 |  | 91 | 2 | 1 | 130F1 | 8/4.8kV | 130F1 | WHITE PHASE TERMINATIONS AMPAC LET GO. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7764 | 2005 | 12 | 26 | 0.51389 |  | 140 | 5 | 2 | Borden Farms | 8/4.8kV | 130F1 | 24/7 reports secondary cable to 1691 Merivale Rd has been damaged. Cable at 1691 disconnected in secondary of transformer #TP2819. Cable to Future Shop reconnected and power restored. 1691 Merivale is still out waiting to hear form building owner. | Nepean | Foreign Interference | Dig-in
7767 | 2005 | 12 | 29 | 0.99236 |  | 396 | 13 | 2 | Borden Farms | 8/4.8kV | 130F1 | TP2819 was isolated to allow contractor to replace defective secondary underground. | Nepean | Scheduled Outage | Repair
18696 | 2011 | 7 | 18 | 0.027778 |  | 316 | 6568 | 1247 | Borden Farms | 8/4.8kV | 130F1/130F4 | Crews isolated 130F4 and 130F1 line sections to remove trees and downed conductors. | Nepean | Adverse Weather
13462 | 2008 | 10 | 29 | 0.93472 |  | 426 | 1117 | 451 | Borden Farm | 8/4.8kV | 130F1/F4 | AT 12:20AM - J Yeldon rpts S1221 & S1196 opened, S366 & S976 closed restoring most customer. AT 5:32AM - J Yeldon rpts remaining customers on 130F1 & F4 restored | Nepean | Adverse Weather
6160 | 2005 | 1 | 31 | 0.59722 |  | 53 | 2 | 2 | Borden Farm | 8/4.8kV | 130F2 | Power interruption to transformer NP000455 front of 2001 Prince of Wales Dr to repair service | Nepean | Scheduled Outage | Repair
12104 | 2008 | 3 | 5 | 0.41667 |  | 100 | 115 | 114 | Borden Farm | 8/4.8kV | 130F2 | Ottawa Police reports street light standard was hit by a City plow which fell into 130F2 overhead circuit at Fisher & Hwy 16. | Nepean | Adverse Environment | Corrosion
18011 | 2011 | 4 | 28 | 0.59028 |  | 260 | 1287 | 297 | Borden Farms | 8/4.8kV | 130F2 | 130F2 circuit breaker tripped and was under hold off. Hold off was surrendered and breaker was closed VIA scada and held. CB then auto-reclosed mulitple times and locked out. Breaker closed VIA scada and held. | Nepean | Adverse Weather | Wind
10413 | 2007 | 5 | 14 | 0.39861 |  | 94 | 8 | 5 | Borden Farm | 27.6/16kV | 130F2 | Peter Barr isolated TRF # 300 @ 10 Rideau Heights to change a switch and arrestor | Nepean | Scheduled Outage | Repair
10843 | 2007 | 7 | 10 | 0.79931 |  | 217 | 4 | 1 | Borden Farm | 8/4.8kV | 130F2 | TE1877 at 30 Concourse Gate was replaced by Oncall crew due to an oil leak. | Nepean | Defective Equipment
14694 | 2009 | 7 | 10 | 0.43403 |  | 30 | 4 | 8 | Borden Farms | 8/4.8kV | 130F2 | TE1598 on Coolsprings was isolated to allow crew to replace broken insert. 8 customers affected. | Nepean | Scheduled Outage | Repair
16459 | 2010 | 7 | 12 | 0.44375 |  | 120 | 74 | 37 | Borden Farms | 8/4.8kV | 130F2 | TP4243 isolated to allow crews to pull in new primary cables. Located on Citiplace dr. | Nepean | Scheduled Outage | Construction
14782 | 2009 | 7 | 18 | 0.82292 |  | 78 | 3 | 2 | Borden Farm | 8/4.8kV | 130F2 | possible weather conditions caused overhead transformer X5302 to open at 1981 prince of wales. | Nepean | Unknown/Other | No Apparent Cause
15118 | 2009 | 9 | 17 | 0.56597 |  | 40 | 3 | 5 | Borden Farms | 8/4.8kV | 130F2 | Transformer #X5306 located at 2001 Prince of Wales isolated to hook up new service | Nepean | Scheduled Outage | Construction
19430 | 2011 | 10 | 20 | 0.67222 |  | 43 | 169 | 236 | Borden Farms | 8/4.8kV | 130F2 | 130F2 breaker tripped. Closed VIA SCADA and holding. | Nepean | Unknown/Other | No Apparent Cause
19431 | 2011 | 10 | 20 | 0.73472 |  | 121 | 308 | 236 | Borden Farms | 8/4.8kV | 130F2 | 130F2 tripped due to tree branch fallen on two phases. Circuit was sectionalized to restore power using the breaker and overhead switches. | Nepean | Tree Contacts | Tree Limb Fallen
4536 | 2003 | 11 | 29 | 0.58958 |  | 161 | 308 | 142 | Borden Farm | 8/4.8kV | 130F2 | Tree fell on ckt at Rideau Heights Lane. | Nepean | Tree Contacts | Tree Fallen
4655 | 2003 | 12 | 25 | 0.96806 |  | 312 | 10 | 2 | Borden Farms | 8/4.8kV | 130F2 | Customer reported sparking on Stephanie. Crew found a hole in casing of xfmr 642 at #2 Stephanie and xfmr leaking. Cutout opened cuasing outage to two customers #2 & #3 Stephanie. On call crew called in to change thr xfmr. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
14082 | 2009 | 3 | 19 | 0.39583 |  | 210 | 84 | 24 | Borden Farm | 8/4.8kV | 130F3 | Transformer #TP4246 located at 290 Tivoli Pvt isolated for contractor to pull secondary in | Nepean | Scheduled Outage | Preventive Maintenance
10210 | 2007 | 4 | 3 | 0.73264 |  | 199 | 20 | 6 | Borden Farms | 8/4.8kV | 130F3 | At 17:35 trans at 80 Colonnade Rd was isolated in order to relocate primary conductor | Ottawa | Scheduled Outage | Construction
12957 | 2008 | 7 | 28 | 0.38333 |  | 38 | 15 | 24 | Borden Farm | 8/4.8kV | 130F3 | TP4246 on Tivoli Pvt was isolated to allow contractor to pull in secondary conductor. | Nepean | Scheduled Outage | Construction
7127 | 2005 | 8 | 11 | 0.57986 |  | 307 | 5 | 1 | Borden Farm | 8/4.8kV | 130F3 | TE1524 was replaced damaged in lightning storm on Aug10/05. At 120 Colonnade Rd on 130F3 circuit. | Nepean | Adverse Weather | Lightning
13352 | 2008 | 10 | 10 | 0.38542 |  | 232 | 93 | 24 | Borden Farms | 8/4.8kV | 130F3 | TP4243 was isolated to allow contractor to pull in secondary services to transformer at Citiplace. | Nepean | Scheduled Outage | Construction
19645 | 2011 | 11 | 28 | 0.37847 |  | 139 | 16 | 7 | Borden Farms | 8/4.8kV | 130F3 | TP 4247 at 290 Citiplace isolated to allow contractor to install new secondary service. | Nepean | Scheduled Outage | Construction
4638 | 2003 | 12 | 20 | 0.24861 |  | 12 | 2 | 11 | Borden Farm | 8/4.8kV | 130F3 | At 130 Collonade Snow removal vehicle has made contact with a fibre optic cable on the hydro poles and has bumped the circuits, no damage to conductors. | Nepean | Foreign Interference | Vehicle
20073 | 2012 | 2 | 28 | 0.40625 |  | 125 | 8 | 4 | Borden Farm | 120/240 | 130F4 | Isolated and replaced Ped at the rear of 3 Saginaw Cres fed from NPTE0358 at the rear of 11 Saginaw Cres | Nepean | Scheduled Outage | Repair
20135 | 2012 | 3 | 7 | 0.37847 |  | 39 | 417 | 641 | Borden Farm | 8/4.8kV | 130F4 | Pole hit by bulldozer, causing two down guys to break, and were lying across one phase. 130F4 breaker opened by System, because one phase of the 130F4 came down and hit a fence. Temporary repairs made and power restored. | Nepean | Foreign Interference
17694 | 2011 | 3 | 10 | 0.23681 |  | 75 | 680 | 544 | Borden Farm | 8/4.8kV | 130F4 | 130F4 breaker tripped during heavy snow / rain storm. Circuit was patrolled and no fault found. Outage time was extended due to DPU failure. Circuit was transferred to 72F6 circuit. | Nepean | Adverse Weather | Snow
12348 | 2008 | 4 | 25 | 0.83333 |  | 18 | 6 | 19 | Borden Farms | 8/4.8kV | 130F4 | Transformer #TE353 located at 12 Assiniboine Dr isolated to energize service (was disconnected this morning by Serv Dept for customer to replace the meter base. U/G service. | Nepean | Unknown/Other
20650 | 2012 | 5 | 29 | 0.4375 |  | 78 | 8 | 6 | Borden Farms | 8/4.8kV | 130F4 | Transformer NPTE0828 at 20 McMurdo Cart. Isolated to allow crew to replace the transformer | Nepean | Scheduled Outage | Repair
5325 | 2004 | 6 | 17 | 0.75903 |  | 17 | 0 | 1 | Borden Farm | 8/4.8kV | 130F4 | M. Lamoureux reports fuse link broken on fuse. Fuse replaced all power restored to normal. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14779 | 2009 | 7 | 18 | 0.70278 |  | 31 | 31 | 60 | Borden Farm | 8/4.8kV | 130F4 | Crew high potted bad cable between T121 and T122, and closed in at T353 to SE7 and S882 blew. T353 to SE7 opened, and S882R refused and closed. Crew to continue their fault finding on the 190F6 cct. See Record #14778, for details. | Nepean | Defective Equipment
15048 | 2009 | 9 | 2 | 0.53819 |  | 68 | 14 | 12 | Borden Farm | 8/4.8kV | 130F4 | TP5509 at 13 Bisayne was isolated to allow crew to make resistance measurements. | Nepean | Scheduled Outage
15072 | 2009 | 9 | 9 | 0.36458 |  | 45 | 14 | 19 | Borden Farms | 8/4.8kV | 130F4 | Transformer #TE353 located at 14 Assiniboine Dr isolated for ground checks | Nepean | Scheduled Outage | Construction
19214 | 2011 | 9 | 20 | 0.40208 |  | 562 | 178 | 19 | Borden Farms | 8/4.8kV | 130F4 | transformer at 12 Assiniboine was isolated to allow crew to perform soil remediation and upgrade the transformer base. | Nepean | Scheduled Outage | Preventive Maintenance
13279 | 2008 | 9 | 23 | 0.39931 |  | 276 | 46 | 10 | Borden Farm | 8/4.8kV | 130F4 | Transformer TP5509 at 23 Biscayne was isolated to replace PCB identified transformer and install base. | Nepean | Scheduled Outage
13424 | 2008 | 10 | 24 | 0.53125 |  | 45 | 10 | 14 | Borden Farm | 8/4.8kV | 130F4 | Isolated transformer TE345 at 19 Keewatin Cres to replace defective Ped | Nepean | Scheduled Outage | Repair
7679 | 2005 | 12 | 2 | 0.40625 |  | 656 | 109 | 44 | Borden Farm | 8/4.8kV | 130F4 | All six cables at transformer TE371 8 Redpine were trenched up while a portable building was being dragged to a new location at the Century Public School. All terminations at tx TE371 were damaged and had to be replaced. | Nepean | Foreign Interference | Dig-in
13716 | 2008 | 12 | 7 | 0.73889 |  | 82 | 41 | 30 | Borden Farms | 8/4.8kV | 130F4 | S861R near 230 Viewmount open. Checked S861R and the fuse was not blown, believed the wind blew it open. | Nepean | Adverse Weather | Wind
4610 | 2003 | 12 | 16 | 0.90278 |  | 30 | 2 | 4 | Borden Farm | 8/4.8kV | 130F4 | Burning hot line clamp reported at switch S828 that supplies 4 retail stores. Repairs made after stores clased and customers were notified when repairs . Interruption taken to 4 customers rather that loss complete line. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
12416 | 2008 | 5 | 7 | 0.79861 |  | 219 | 36 | 10 | Borden Farm | 8/4.8kV | 130F5 | Transformer TE1540 @ 26 valleyridge was isolated to replace leaking transformer. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
12612 | 2008 | 6 | 12 | 0.39583 |  | 521 | 87 | 10 | Borden Farm | 8/4.8kV | 130F5 | TE1540 at 26 Valleyridge was isolated to remove contaminated soil & install transformer base. | Nepean | Scheduled Outage | Repair
3868 | 2003 | 8 | 7 | 0.091667 |  | 183 | 214 | 70 | Borden Farm |  | 130F5 | Red phase of 1286 top section of the switch has burnt clear. Switch will require replacement. Pete Bishop suggests replacing all three phases. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
7381 | 2005 | 9 | 27 | 0.38542 |  | 6 | 21 | 207 | Borden Farm | 8/4.8kV | 130F5 | M. MacLellan reports fuses at S1358 RWB where stored at the pole, and may have been contaminated by water. When load was transferred to 180F5 circuit S1358 RWB phases failed. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12644 | 2008 | 6 | 15 | 0.65764 |  | 3 | 5 | 104 | Overbrooke | 13.2kV | 1317 (TO30) | TO30 Breaker tripped (1317 Line) Severe lightning storm in effect. Breaker closed via SCADA. | Ottawa | Adverse Weather | Lightning
6496 | 2005 | 5 | 3 | 0.38403 |  | 85 | 3 | 2 | Barrhaven | 8/4.8kV | 140 F4 | Switch to Transformer NP00501 at 3853 Cambrian Rd opened due to bird contact refused the switch restored the power | Nepean | Foreign Interference | Bird
9929 | 2007 | 1 | 16 | 0.0083333 |  | 188 | 19 | 6 | Barrhaven | 8/4.8kV | 140F1 | TE1870 at 35 Larkin & TE2057 at 10 Green were isolated to replace defective elbows & inserts. TE1870's white phase elbow & insert burnt up earlier causing an outage to customers on the white phase. While isolating TE1870 from TE2057, an elbow broke off in the insert at TE2057. Both problems were repaired by On-call & power restored to both. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17504 | 2011 | 1 | 21 | 0.50694 |  | 479 | 683 | 522 | Barhaven | 8/4.8kV | 140F1 | 140F1 at Barhaven DS tripped and locked out, blue phase fuse to TP6456 in SE15 found blown, problems with elbows and inserts caused TP6450 to begin leaking, which lead to transformer replacement and a suspected cable fault was found between TP6451 and TP6452 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11979 | 2008 | 1 | 24 | 0.42986 |  | 186 | 31 | 10 | Barhaven | 8/4.8kV | 140F1 | TE874 @ 118 Tripp cres was isolated to replace same. | Nepean | Scheduled Outage | Repair
19898 | 2012 | 1 | 26 | 0.39097 |  | 85 | 466 | 521 | Barrhaven |  | 140F1 | The 140F1 CB tripped due to contractor cable dig in at the Barrhaven DS on the white phase between SE-15 and TP 6442. Load restored in section | Nepean | Foreign Interference | Dig-in
19929 | 2012 | 1 | 31 | 0.3125 |  | 417 | 35 | 5 | Barrhaven | 8/4.8kV | 140F1 | TP5503 at 900 Greenbank was isolated to allow crews to replace the transformer | Nepean | Scheduled Outage | Repair
12019 | 2008 | 2 | 8 | 0.38681 |  | 203 | 64 | 19 | Barrhaven | 8/4.8kV | 140F1 | TE872 at 9 Ventnor & TE873 at 31 Ventnor were isolated to repair defective elbow inserts. 19 customers on Ventnor Way were affected. | Nepean | Scheduled Outage | Repair
20063 | 2012 | 2 | 27 | 0.51736 |  | 99 | 23 | 14 | Barrhaven | 4.16kV | 140F1 | Transformer TP4834 at 9 Barrhaven Cres. isolated to replace defective pedestal | Nepean | Scheduled Outage | Repair
17739 | 2011 | 3 | 18 | 0.65625 |  | 329 | 163 | 48 | Barhaven DS | 8/4.8kV | 140F1 | Transformer TP5961 at 123 Trapp Drive was found submerged under water. Which caused blue phase at SE15 fuse to blow. Repairs and to TP5961 by oncall crew. Replaced a bushing & insert. | Nepean | Adverse Weather | N/A
4936 | 2004 | 3 | 25 | 0.59028 |  | 332 | 21 | 8 | Barrhaven | 8/4.8kV | 140F1 | All cables were hi pot & transformers energized in sequence. Water was found in the base of TE413 @ 20 Barrhaven Cres. Pump was install and to be checked by 24/7 during the evening & night. | Nepean | Adverse Environment | Flooding
18267 | 2011 | 6 | 1 | 0.38056 |  | 400 | 80 | 12 | Barrhaven | 8/4.8kV | 140F1 | Transformer TP5961 at 123 Tripp Crs was isolated to allow crew to install new transformer base and grounding. 12 customers were affected. Barrhaven (140F1) | Nepean | Scheduled Outage
15105 | 2009 | 9 | 15 | 0.28264 |  | 48 | 4 | 5 | Barrhaven | 8/4.8kV | 140F1 | TP5503 at 58 Tripp was isolated from Hydro Ottawa Sources to gain transformer resistance readings for PCB replacement program. 5 Customers affected and power was restored at 7:35am | Nepean | Scheduled Outage
11446 | 2007 | 10 | 3 | 0.37778 |  | 471 | 196 | 25 | Barhaven | 8/4.8kV | 140F1 | TP4822 & TP4827 on Leetom cr in Barhaven were isolated for planned cable & transformer replacement. | Nepean | Scheduled Outage | Construction
11591 | 2007 | 10 | 25 | 0.39236 |  | 392 | 65 | 10 | BARHAVEN | 8/4.8kV | 140F1 | Transformer TP4821 at 46 Tripp Cres. isolated for cable replacement and transformer replacement. | Nepean | Scheduled Outage | Construction
9520 | 2006 | 10 | 26 | 0.39722 |  | 506 | 101 | 12 | Barhaven | 8/4.8kV | 140F1 | TE916 on Knollsbrook in Barhaven was isolated to allow crew to excavate new transformer well. | Nepean | Scheduled Outage | Repair
15387 | 2009 | 11 | 13 | 0.79792 |  | 164 | 776 | 522 | Barhaven | 8/4.8kV | 140F1 | Barhaven 140F1 tripped & locked out due to a blown elbow at TP5967, 11 Ventor Way. Circuit sectionalized & load restored in stages. Note: reclosing was in-service on 140F1 but breaker did not reclose when fuse blew at SE15. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11754 | 2007 | 11 | 23 | 0.40556 |  | 70 | 23 | 20 | Barrhaven | 8/4.8kV | 140F1 | TE952 at 12 Knollsbrook isolated to replace swollen elbows & clean bushings. 20 customers on Knollsbrook & Foxfield affected. | Nepean | Scheduled Outage | Repair
9800 | 2006 | 12 | 5 | 0.46875 |  | 33 | 66 | 120 | Barrhaven | 8/4.8kV | 140F1 | Load from the 140 F1 had been transferred to 145F2 through S15-3. 15 minutes latter S919 red phase failed. 140F1 breaker closed to restore red load and S919 W,B opened. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14574 | 2009 | 6 | 19 | 0.62014 |  | 72 | 6 | 5 | Jockvale | 8/4.8kV | 140F2 | Transformer #X21628 located at 28 Lytle isolated, crew had to repair bracket & close switch | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12959 | 2008 | 7 | 28 | 0.89097 |  | 47 | 2 | 2 | Barrhaven | 8/4.8kV | 140F2 | Transformer #X35564 located at 4078 Greenbank isolated due to deteriation due to age | Nepean | Defective Equipment | Equipment Deterioration Due to Age
13312 | 2008 | 10 | 2 | 0.57708 |  | 17 | 1 | 5 | Barrhaven | 8/4.8kV | 140F2 | Transformer #X39558 located at 26 Bren-Maur isolated to change blown arrestor & line clamp | Nepean | Scheduled Outage | Repair
19364 | 2011 | 10 | 12 | 0.40625 |  | 290 | 48 | 10 | Barrhaven | 8/4.8kV | 140F2 | Transformer #X33052 located at 102 Willow Creek Cir opened by crew to replace transformer | Nepean | Scheduled Outage | Construction
11601 | 2007 | 10 | 26 | 0.38819 |  | 496 | 165 | 20 | Barrhaven | 8/4.8kV | 140F2 | TP4834 & TP4831 to allow crews to replace transformers made isnstall new alive front transformers. | Nepean | Scheduled Outage | Construction
13754 | 2008 | 12 | 15 | 0.48958 |  | 20 | 1 | 2 | Barrhaven | 8/4.8kV | 140F2 | Transformer #X09829 located at 3289 Greenbank isolated to replace broken connection at linket, replaced with ampact connection. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11981 | 2008 | 1 | 25 | 0.42292 |  | 155 | 28 | 11 | Barhaven | 8/4.8kV | 140F3 | Transformer TE1969 at 28 Townsend was isolated for replacement. 11 Customers affected by outage. | Nepean | Scheduled Outage | Preventive Maintenance
6165 | 2005 | 2 | 2 | 0.010417 |  | 113 | 38 | 20 | Barrhaven | 8/4.8kV | 140F3 | Replace defective transformer at 28 Live Oak Cres | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6174 | 2005 | 2 | 3 | 0.57986 |  | 15 | 2 | 10 | Barrhaven | 27.6/16kV | 140F3 | M.Mclellan reports TE999 is now restored to normal | Nepean | Scheduled Outage | Repair
12044 | 2008 | 2 | 14 | 0.40694 |  | 84 | 14 | 10 | Barhaven | 8/4.8kV | 140F3 | Transformer TP5580 @ 28 townsend was isolated to allow contractor to clean base of oil and water. | Nepean | Scheduled Outage | Preventive Maintenance
15925 | 2010 | 4 | 12 | 0.45139 |  | 78 | 30 | 23 | Barrhaven | 8/4.8kV | 140F3 | Transformer TP5978 at 75 Thistledown. isolated to replace leaker. | Nepean | Defective Equipment
16013 | 2010 | 4 | 29 | 0.38889 |  | 414 | 159 | 23 | Barrhaven | 8/4.8kV | 140F3 | TP5978 at 75 Melvern has been isolated to allow crews to perform soil remediation. | Nepean | Scheduled Outage
20476 | 2012 | 5 | 7 | 0.57222 |  | 49 | 82 | 251 | Barrhaven | 8/4.8kV | 140F3 | While completing PC17-69424 to restore 140F3 load to normal in Barrhaven, S1469 WB and S1555 WB fuses slid open and when the parrallel was broken, created an outage on transformer loops. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20577 | 2012 | 5 | 25 | 0.59028 |  | 110 | 2912 | 1638 | Barrhaven | 8/4.8kV | 140F3 | Truck contacted and broke pole at 3330 Moodie Dr. Circuit Isolated. 145F4 load was on the 140F3 circuit. Both breakers would not close after sectionalizing. Both circuits had to be sectionalized again and picked up in stages. | Nepean | Foreign Interference | Vehicle
8369 | 2006 | 5 | 29 | 0.61875 |  | 39 | 260 | 400 | Barrhaven | 8/4.8kV | 140F3 | Isolation of 130F3 section S1107 by S1163 to remove fallen tree from overhead line. Barrhaven North of the VIA trackes between Greenbank and Jockvale | Nepean | Tree Contacts | Tree Fallen
16229 | 2010 | 6 | 9 | 0.39236 |  | 164 | 30 | 11 | Barrhaven | 8/4.8kV | 140F3 | Transformer TP5597 at 82 Sherway was isolated to allow crews to change elbows and inserts | Nepean | Scheduled Outage | Repair
12585 | 2008 | 6 | 10 | 0.40972 |  | 540 | 126 | 14 | Barrhaven | 8/4.8kV | 140F3 | TP5624 at 35 Tedwyn isolated to replace defective elbows & inserts. 14 customers on Tedwyn & Providence were affected. | Nepean | Scheduled Outage | Repair
18413 | 2011 | 6 | 15 | 0.43333 |  | 88 | 13 | 9 | Barrahven | 8/4.8kV | 140F3 | Transformer TP5987 @ 100 Burnett Grove was isolated to allow crew to replace inserts. 9 customers were affected. Barrhaven (140F3) | Nepean | Scheduled Outage
16271 | 2010 | 6 | 16 | 0.375 |  | 118 | 22 | 11 | Barrhaven | 8/4.8kV | 140F3 | Transformer TP5596 at 22 Liveoak was siaolted to allow crews to repair a defective insert | Nepean | Scheduled Outage | Repair
16308 | 2010 | 6 | 21 | 0.37986 |  | 185 | 80 | 26 | Barrhaven | 8/4.8kV | 140F3 | Tansformers TE1005 and TE1006 on Sage & Burnette were isoalted for elbow and insert replacement. | Nepean | Scheduled Outage
6996 | 2005 | 7 | 20 | 0.14931 |  | 560 | 121 | 13 | Barrhaven | 8/4.8kV | 140F3 | Transformer TE1215B has a blown bushing. | Nepean | Defective Equipment
16560 | 2010 | 7 | 25 | 0.6125 |  | 65 | 107 | 99 | Barrhaven | 8/4.8kV | 140F3 | 24/7 reports S1112 red phase switch found open. Crew reports switch is broken only and will replace same. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
18827 | 2011 | 7 | 26 | 0.41667 |  | 226 | 11 | 3 | Barrhaven | 8/4.8kV | 140F3 | Crew isolated 140F3 circuit from S379 to EOL to transfer plant to a new pole. | Nepean | Scheduled Outage | Preventive Maintenance
13155 | 2008 | 8 | 27 | 0.44444 |  | 122 | 37 | 18 | Barhaven | 8/4.8kV | 140F3 | TP6001 was isolated at 1 Sweetbriar to replace transformer due to damaged elbow which could not be repaired on site. | Nepean | Scheduled Outage
15069 | 2009 | 9 | 8 | 0.52153 |  | 107 | 9 | 5 | Barrhaven | 8/4.8kV | 140F3 | Isolation of TE2626 to repair riser cable at S379. | Nepean | Scheduled Outage
19225 | 2011 | 9 | 21 | 0.40069 |  | 194 | 39 | 12 | Barrhaven | 8/4.8kV | 140F3 | Crew isolated TP5599 at 148 Burnettes to install new transformer inserts and elbows. | Nepean | Scheduled Outage | Repair
19229 | 2011 | 9 | 21 | 0.56944 |  | 106 | 21 | 12 | Barhaven | 8/4.8kV | 140F3 | TP5615 at 39 Providence was isolated to allow crews to replace elbows and inserts. | Nepean | Scheduled Outage | Preventive Maintenance
15166 | 2009 | 9 | 25 | 0.62014 |  | 491 | 16 | 2 | Jockvale | 8/4.8kV | 140F3 | G. Bell reports customer at 2851 Steele Hill Cres has made contact with his own overhead service, while pulling a tree down his laneway. Causing 145F3 breaker to auto reclose. Customer has been notified to have contractor repair service and ESA inspectionbefore reconnection. | Nepean | Foreign Interference | Foreign Object
19522 | 2011 | 11 | 2 | 0.38194 |  | 545 | 200 | 22 | Barrhaven | 8/4.8kV | 140F3 | Transformer TP5599 at 148 Burnett's Grove was isolated to allow crew to clean transformer due to leak, install a new base a grounding. | Nepean | Scheduled Outage | Repair
17300 | 2010 | 11 | 18 | 0.40208 |  | 587 | 117 | 12 | Barrhaven | 8/4.8kV | 140F3 | TP5617 at 19 Providence isolated to allow crews to replace the transformer. 12 customers affected. | Nepean | Scheduled Outage | Construction
11742 | 2007 | 11 | 20 | 0.53125 |  | 35 | 5 | 9 | NEPEAN TS | 27.6/16kV | 140F3 | TRANSF#NPTE990 AT 56 AMHURST ISOLATED TO ALLOW FOR SMART METER UPGRADE | Nepean | Scheduled Outage | Preventive Maintenance
11755 | 2007 | 11 | 23 | 0.55139 |  | 60 | 20 | 20 | Barrhaven | 8/4.8kV | 140F3 | TE977 at 18 Antler isolated to replace swollen elbows & clean bushings. 8 customers on Antler & Tulane affected. | Nepean | Scheduled Outage | Repair
19621 | 2011 | 11 | 23 | 0.375 |  | 505 | 101 | 12 | Barhaven | 8/4.8kV | 140F3 | TP5616 at 29 Providence was isolated to allow crews to replace a leaking transformer and install a new base | Nepean | Scheduled Outage | Repair
19655 | 2011 | 12 | 1 | 0.38542 |  | 565 | 113 | 12 | Barrhaven | 8/4.8kV | 140F3 | At 9:15 crews isolated TP5616 at 29 Providence to replace a leaking transformer. 12 customers affected . Barrhaven 140F3 ID# 19655 | Nepean | Scheduled Outage
19927 | 2012 | 1 | 30 | 0.59167 |  | 65 | 1830 | 2189 | Barhaven | 8/4.8kV | 140F3, F5 | 140F3 tripped due to a fault on the egress cable from the station. Greely & K-Line crews were working at the station & had to be cleared before proceeding with restoration. Once the location of the fault was confirmed, load was restored via alternate supply. 140F5 was opened at request of crew before closing tie switches due to proximity of o/h switches to adjacent o/h plant. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19837 | 2012 | 1 | 16 | 0.40625 |  | 25 | 1 | 2 | Barrhaven | 8/4.8kV | 140F4 | Transformer #X09829 located at 3289 Greenbank Rd opened by crew to renew connections at the transformer | Nepean | Defective Equipment | Imminent Equipment Failure Detected
6142 | 2005 | 1 | 17 | 0.69375 |  | 51 | 15 | 18 | Barrhaven | 8/4.8kV | 140F4 | Blown arrester found at transformer 3702. Refused and closed S427. | Nepean | Defective Equipment
7846 | 2006 | 1 | 23 | 0.96528 |  | 39 | 58 | 89 | Barrhaven | 8/4.8kV | 140F4 | S1064 red phase switch failed at 13 Kadeer Way. Red phase switch was replaced all power restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15706 | 2010 | 2 | 7 | 0.45278 |  | 182 | 6 | 2 | Barrhaven MS | 8/4.8kV | 140F4 | 140F4 Auto Reclosed due to transformer X39726 located at 4032 Prince of Wales Dr opening up. The transformer switch was found to be defective. 24/7 crew replaced the switch, and restored power. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7902 | 2006 | 2 | 8 | 0.40972 |  | 21 | 1 | 2 | Jockvale | 8/4.8kV | 140F4 | Isolated transformer NP0819 at 3289 Greenbank Rd to repaire service | Nepean | Scheduled Outage | Repair
15752 | 2010 | 2 | 27 | 0.88542 |  | 57 | 9 | 9 | Barrhaven DS | 8/4.8kV | 140F4 | Transformers X39724 & X39574 located at 9 & 21 Goodwood Ave. Were isolated to allow crew to replace a downed neutral conductor. | Nepean | Unknown/Other
17656 | 2011 | 3 | 1 | 0.13403 |  | 100 | 982 | 915 | Barhaven | 8/4.8kV | 140F4 | Circuit breaker auto reclosed once before locking out, circuit was sectionalized and partially restored. Patrol revealed nothing so breaker was reopened to close the circuit back in and picked up successfully | Nepean | Unknown/Other
15765 | 2010 | 3 | 3 | 0.52083 |  | 85 | 156 | 110 | Barhaven | 8/4.8kV | 140F4 | A broken insulator and a phase down on a bracket at Bren-Maur and Nowlan required isolation of the overhead at S1033 to repair and replace insulators | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14032 | 2009 | 3 | 10 | 0.47014 |  | 499 | 82 | 33 | Barhaven | 8/4.8kV | 140F4 | A vehicle pulled down a single phase conductor & pole at the corner of Rideau Valley Dr. & Barnsdale rd. S175 R blew, 140F4 A/R. Work protection established at S175 to EOL to make repairs. | Nepean | Foreign Interference | Vehicle
12146 | 2008 | 3 | 15 | 0.875 |  | 120 | 2 | 1 | Barhaven | 8/4.8kV | 140F4 | Crew replaced transformer switch & fuse on transformer X33067 at 3404 Barnsdale. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
6294 | 2005 | 3 | 16 | 0.57639 |  | 53 | 4 | 5 |  | 8/4.8kV | 140F4 | K line opened transformer at 3492 Woodroffe to change arrestors | Nepean | Scheduled Outage
6295 | 2005 | 3 | 16 | 0.57639 |  | 53 | 4 | 5 | Barrhaven DS | 8/4.8kV | 140F4 | K-Line opened a transformer @ 3492 Woodroffe to change arrestors | Nepean | Scheduled Outage | Preventive Maintenance
6296 | 2005 | 3 | 16 | 0.57639 |  | 53 | 4 | 4 | BarrhavenDS | 8/4.8kV | 140F4 | K-Line opened a transformer @3522 Woodroffe to change arrestors | Nepean | Scheduled Outage | Preventive Maintenance
14079 | 2009 | 3 | 18 | 0.77083 |  | 201 | 7 | 2 | Barhaven | 8/4.8kV | 140F4 | Crew isolated damaged hydro pole @ Barnsdale and Prince of wales. Two transformers Tx 4535 and Tx 4785 were interrupted until repirs were completed. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
8088 | 2006 | 3 | 31 | 0.67153 |  | 173 | 3 | 1 | Barrhaven | 8/4.8kV | 140F4 | Transformer located at Greenbank & Barnsdale isolated due to broken cut out to be changed | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10219 | 2007 | 4 | 6 | 0.072917 |  | 24 | 443 | 1108 | Barrhaven | 8/4.8kV | 140F4 | 140F4 Breaker tripped and locked out affecting customers on Jockvale, Brenmaur, Hwy 16, Greenbank areas. Cable fault between TE892 and TE893 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10220 | 2007 | 4 | 6 | 0.34792 |  | 493 | 767 | 1100 | Barrhaven | 8/4.8kV | 140F4 | Faulty cable section between transformers TE892 & TE893 on Henfield in Nepean caused the Barhaven 140F4 breaker to open. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
14148 | 2009 | 4 | 6 | 0.34444 |  | 64 | 2 | 2 | Barrhaven | 8/4.8kV | 140F4 | Replaced broken switch feeding transformer X39746 at 4278 Greenbank Rd | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10329 | 2007 | 4 | 26 | 0.40278 |  | 6190 | 1032 | 10 | Barrhaven | 8/4.8kV | 140F4 | TE893 @ 60 Henfield was isolated to repair cable fault betwwen TE892 and TE893. | Nepean | Scheduled Outage | Repair
17998 | 2011 | 4 | 27 | 0.38889 |  | 200 | 10 | 3 | Barrhaven | 8/4.8kV | 140F4 | Transformer #X4480 located at 3690 Bankfield Rd opened by crew to do secondary work. | Nepean | Scheduled Outage | Construction
12372 | 2008 | 5 | 1 | 0.75694 |  | 76 | 1 | 1 | Barrhaven | 8/4.8kV | 140F4 | Thermal scan detected an unseated elbow at TE1874 101 Malvern (Jockvale Elementary). Elbow and insert damaged when pulled. Transformer backfed from 140F3 circuit and customer restored. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16049 | 2010 | 5 | 6 | 0.39583 |  | 143 | 10 | 4 | Barrhaven | 8/4.8kV | 140F4 | Isolated transformer 556 at 5033 NICOLLS ISLAND RD to replace the pole | Nepean | Scheduled Outage | Construction
18145 | 2011 | 5 | 13 | 0.56319 |  | 27 | 1 | 2 | Barhaven | 8/4.8kV | 140F4 | Transformer TP4870 @ 1075 Greenbank was isolated to allow crew to disconnect secondary service to Bell moility tower due to contractor dig-in customer owned secondary cable. | Nepean | Human Element | Dig-in
3437 | 2003 | 5 | 14 | 0.43333 |  | 6 | 4 | 40 | Barrhaven | 8/4.8kV | 140F4 | G. Morrice reports tree in overhead line south of switch S820. An emergency outage is required to move tree. A section of 140F4 circuit was isolated between S820 & S552. Approx 40 customers affected in outage. | Nepean | Tree Contacts | Tree Fallen
8317 | 2006 | 5 | 18 | 0.82361 |  | 282 | 1061 | 1108 | Barhaven | 8/4.8kV | 140F4 | 140F4 AUTO-RECLOSED 3 TIMES, A HOLDOFF WAS PLACED ON THE CIRCUIT. THE FEEDER OPENED AGAIN AND STAYED OPEN. CREW PATROLED LINE AND FOUND THAT LIGHTINING HAD STRUCK TRANSFORMER 294 AND CAUSED O/H LEAD TO SNAP AND FLAP INTO THE O/H. CREW CUT LEAD CLEAR AND ALL POWER RESTORED EXCEPT 2 CUSTOMERS FED FROM 294. | Nepean | Lightning | Direct Strike
10477 | 2007 | 5 | 29 | 0.76528 |  | 343 | 6 | 1 | Barhaven | 8/4.8kV | 140F4 | TE327 at 80 Larkin was isoalted to replace leaking transformer. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12498 | 2008 | 5 | 29 | 0.47083 |  | 62 | 8 | 8 | Barrhaven | 8/4.8kV | 140F4 | Transformer TP5889 at 9 Alberni in Nepean isolated to replace defective elbows. | Nepean | Scheduled Outage
8407 | 2006 | 6 | 1 | 0.64583 |  | 65 | 2 | 2 | Barhaven | 8/4.8kV | 140F4 | Found fuse broken in switch to transformer NP1356 at 3888 Prince of Wales Dr refused the switch and restored power | Nepean | Defective Equipment | Equipment Deterioration Due to Age
10527 | 2007 | 6 | 4 | 0.92292 |  | 300 | 20 | 4 | Barrhaven | 8/4.8kV | 140F4 | Tree contact with the single phase tap off at 4065 Prince of Wales caused the 140F4 circuit to auto-reclose. The single phase conductor broke mid span & had to be cut clear of the main circuit. On-call crews cleared trees & repaired the downed conductor. | Nepean | Tree Contacts | Inadequate Trimming
18324 | 2011 | 6 | 8 | 0.14375 |  | 78 | 3 | 2 | Barrhaven | 8/4.8kV | 140F4 | A car hit a pole at 3788 Princes of Whales at switch 904 causing the the circuit to auto reclosed and to blow switch 904. | Nepean | Foreign Interference | Vehicle
8493 | 2006 | 6 | 15 | 0.46528 |  | 40 | 2 | 3 | Barrhaven | 8/4.8kV | 140F4 | Transformer #NP003876 located at 9 Goodwood Dr isolated to replace triplex | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8557 | 2006 | 6 | 20 | 0.58333 |  | 50 | 18 | 22 | Barrhaven | 8/4.8kV | 140F4 | Overhead runoff from Prince of Wales at S206 to Nichols Island isolated to remove tree from overhead. | Nepean | Tree Contacts | Tree Fallen
18455 | 2011 | 6 | 21 | 0.4375 |  | 300 | 130 | 26 | Barrahven | 8/4.8kV | 140F4 | Switch S206 opened to isolate Nicolls Island to allow tree contractor to clear trees from overhead wires. | Nepean | Scheduled Outage | Preventive Maintenance
6872 | 2005 | 7 | 5 | 0.54167 |  | 30 | 2 | 5 | Barrhaven | 8/4.8kV | 140F4 | Isolated Transformer #1684 at 36 Queen Anne to repair switch | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16422 | 2010 | 7 | 7 | 0.82014 |  | 164 | 3480 | 1626 | Barrhaven | 8/4.8kV | 140F4 | 140F4 breaker tripped due to overload. Offloaded part of circuit and restored in sections. | Nepean | Adverse Weather | Extreme Ambient Temperature
12804 | 2008 | 7 | 8 | 0.25833 |  | 199 | 202 | 77 | Barrhaven | 8/4.8kV | 140F4 | Cable fault between TE895 and TE1144 on the Barrhaven 140F4. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10825 | 2007 | 7 | 9 | 0.40278 |  | 80 | 12 | 9 | BAARHAVEN | 8/4.8kV | 140F4 | Transformer # 505 at 508 Greenbank isolated to allow for customer maintenance | Nepean | Scheduled Outage | Repair
18648 | 2011 | 7 | 13 | 0.375 |  | 240 | 20 | 5 | Barhaven | 8/4.8kV | 140F4 | TE2626 at 27 Fullam was isolated to allow crews to transfer plant to new pole. | Nepean | Scheduled Outage | Construction
10949 | 2007 | 7 | 25 | 0.36875 |  | 329 | 461 | 84 | Barhaven | 8/4.8kV | 140F4 | TE955, 956, 957, 958, 959, 960, 961 on Bartley & Chester in Barhaven isolated for planned meter replacement. Outage required due to possible defective meter bases. | Nepean | Scheduled Outage | Repair
8847 | 2006 | 7 | 26 | 0.37153 |  | 257 | 43 | 10 | Barrhaven | 8/4.8kV | 140F4 | Transformer TE1143 at 9 Foxhill isolated for replacement. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
10986 | 2007 | 8 | 1 | 0.72708 |  | 351 | 351 | 60 | Barhaven | 8/4.8kV | 140F4 | Crew replaced burnt lead and line clamp on the blue phase of switch S1155 on Greenbank feeding customers between Alberni and Glacier.(because of the problems with the 140F3 customers being out on the ajacent side of the normally open point on the transformer loop. The calls for this outage may have been lost in the shuffle. When all power was restored and the ran reset for the 140F3 one customer at 77 glacier called in reporting she was still out. She of course was on the 140F4. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
7060 | 2005 | 8 | 4 | 0.45694 |  | 373 | 75 | 12 | Barrhaven | 8/4.8kV | 140F4 | Defective transformer TE899 on Foxfield was changed. Crane was called to assist crew in lifting transformer into backyard. | Nepean | Defective Equipment
7103 | 2005 | 8 | 10 | 0.60764 |  | 66 | 723 | 657 | Barrhaven | 8/4.8kV | 140F4 | Tree on circuit at Greenbank & Viewbank. | Nepean | Foreign Interference | Foreign Object
3928 | 2003 | 8 | 21 | 0.98056 |  | 248 | 45 | 11 | Barrhaven | 8/4.8kV | 140F4 | Tree contacted overhead circuit allong Jockvale Rd. feeder atuo/reclosed, S174 fused in line switch blew. Tree was removed and switch refused and closed. | Nepean | Tree Contacts
14997 | 2009 | 8 | 22 | 0.74514 |  | 521 | 9 | 1 | Barhaven | 8/4.8kV | 140F4 | On call crew replaced defective transformer @ 3293 Baseline. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
11132 | 2007 | 8 | 23 | 0.38681 |  | 205 | 75 | 22 | Barrhaven | 8/4.8kV | 140F4 | Transformers TE1236 & TE1237 on Alberni St in Nepean isolated for the installation of new smart meters. | Nepean | Scheduled Outage | Construction
19015 | 2011 | 8 | 25 | 0.44722 |  | 169 | 94 | 34 | Barrahven | 8/4.8kV | 140F4 | Faulted cable section between TP5678 and TP5679 on Bartley Cres. Caused S1113 to blow, interrupting 7 transformers. Load restored in stages. | Nepean | Defective Equipment
19116 | 2011 | 9 | 8 | 0.95347 |  | 531 | 229 | 77 | Barrhaven |  | 140F4 | inserts blew out of TP5681 at 85 Exeter, transformer replaced by On Call crew. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16939 | 2010 | 9 | 14 | 0.47569 |  | 35 | 1 | 2 | Barrhaven | 8/4.8kV | 140F4 | Transformer #X06021 located at 126 Bren Maur opened by crew to change primary feed | Nepean | Scheduled Outage | Construction
13231 | 2008 | 9 | 15 | 0.097917 |  | 130 | 2167 | 1000 | Barrhaven | 8/4.8kV | 140F4 | A tree fell on the O/H on Greenbank four spans south of the rail way tracks cause the circuit to trip. | Nepean | Tree Contacts | Tree Fallen
4119 | 2003 | 9 | 21 | 0.62431 |  | 51 | 3 | 3 | Barrhaven | 8/4.8kV | 140F4 | Cut out was found open and was reclosed successfully. | Ottawa | Unknown/Other | No Apparent Cause
9281 | 2006 | 9 | 22 | 0.19931 |  | 423 | 113 | 16 | Barrhaven | 8/4.8kV | 140F4 | TE996B and TE997B isolated to replace defective transformers. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16990 | 2010 | 9 | 24 | 0.56528 |  | 54 | 3 | 3 | Barrhaven | 8/4.8kV | 140F4 | Isolated transformer X06043 at 65 Bren-Maur Rd to install new conductor | Nepean | Scheduled Outage | Construction
17001 | 2010 | 9 | 25 | 0.875 |  | 60 | 3 | 3 | Barrhaven | 8/4.8kV | 140F4 | Transformer T556 @ 5033 Nicolls island rd was isolated because the crew had to replace the hot line clamp. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17005 | 2010 | 9 | 27 | 0.45208 |  | 63 | 2 | 2 | BARRHAVEN DS | 8/4.8kV | 140F4 | Transformer X06021 at 32 Barcham isolated to run primary | Nepean | Scheduled Outage | Construction
4246 | 2003 | 10 | 11 | 0.93056 |  | 85 | 1 | 1 | Barhaven | 8/4.8kV | 140F4 | 24/7 found fuse open @ Tx875, 4047 Viewbank, probable animal contact. Fuse replaced & power restored. | Nepean | Foreign Interference | Animal
19412 | 2011 | 10 | 19 | 0.40625 |  | 281 | 9 | 2 | Barrhaven DS |  | 140F4 | Transformer X33069 at 3404 Greenbank Rd isolated for crew | Nepean | Scheduled Outage | Construction
11589 | 2007 | 10 | 25 | 0.40625 |  | 365 | 49 | 8 | Barrhaven | 8/4.8kV | 140F4 | To transfer customer to new pole line between Cambrain Rd & Bankfield on Greenbank. | Nepean | Scheduled Outage | Construction
4350 | 2003 | 10 | 27 | 0.44236 |  | 65 | 12 | 11 | Barrhaven | 8/4.8kV | 140F4 | 140F4 A/R, fuse at switch 174 on Greenbank & Cambrian found blown, no problems found when circuit patrolled, refused and closed. | Nepean | Unknown/Other | No Apparent Cause
4381 | 2003 | 11 | 4 | 0.56111 |  | 7 | 77 | 657 | Barrhaven | 8/4.8kV | 140F4 | Circuit was tagged hold off when breaker tripped. Circuit was patrolled and no problem was found. Hold off removed circuit reclosed restoring power to 657 customers. ID#4381 | Nepean | Adverse Weather | Rain
19552 | 2011 | 11 | 10 | 0.46181 |  | 193 | 6 | 2 | Barrhaven DS | 8/4.8kV | 140F4 | Transformer X39180 at 3671 Greenbank Rd isolated for pole change | Nepean | Scheduled Outage | Construction
4481 | 2003 | 11 | 19 | 0.00069444 |  | 64 | 1 | 1 | Barrhaven | 8/4.8kV | 140F4 | M. Lamoureux reports overhead service reports at 3293 Greenbank Rd. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
13647 | 2008 | 11 | 20 | 0.47431 |  | 61 | 1 | 1 | Barrhaven | 8/4.8kV | 140F4 | The customer owned pole at 1073 Greenbank was severly leaning due to a crew excavating to close to the pole. Single phase runoff was isolated to straighten pole. | Nepean | Foreign Interference | Dig-in
17339 | 2010 | 11 | 24 | 0.55556 |  | 43 | 10 | 14 | Barrhaven | 8/4.8kV | 140F4 | Isolated transformer TP6443 at 13 Kadeer Way to connect new service | Nepean | Scheduled Outage | Emergency Services Request
19670 | 2011 | 12 | 3 | 0.7 |  | 32 | 1 | 1 | Jockvale | 8/4.8kV | 140F4 | Customer report a tree branch caused transformer fuse to open at 4263 Prince of Wales. | Nepean | Tree Contacts | Tree Limb Fallen
5977 | 2004 | 12 | 5 | 0.12361 |  | 82 | 897 | 656 | Barrhaven | 8/4.8kV | 140F4 | Broken insulator replaced on Bren Mar near Barcham Cres. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19725 | 2011 | 12 | 15 | 0.38542 |  | 40 | 35 | 103 | Barrhaven | 8/4.8kV | 140F4 | At 09:15 crews had a scheduled outage to place WX2051 at Woodroffe and Prince of Wales in service, WX2052 at Greenbank in service and transfer some load from the 140F4 to the 7F2.Barrhaven and 606F2 ID#19725 | Nepean | Scheduled Outage | Construction
4618 | 2003 | 12 | 17 | 0.36528 |  | 44 | 1 | 2 | Barrhaven | 8/4.8kV | 140F4 | Transformer #1487 at 4144 Viewbank Road in Nepean was isolated to allow for the replacement of defective connections. ID#4618 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
11972 | 2008 | 1 | 23 | 0.40417 |  | 128 | 23 | 11 | Barrhaven | 8/4.8kV | 140F5 | TE1134 at 128 Fieldgate was replaced due to oil leak. New nomenclature TP5578. | Nepean | Scheduled Outage | Preventive Maintenance
11974 | 2008 | 1 | 23 | 0.325 |  | 242 | 60 | 15 | Barrhaven | 8/4.8kV | 140F5 | At 07:48 trans at 128 Fieldgate was isolated for oil leaking replacement | Nepean | Scheduled Outage | Preventive Maintenance
17512 | 2011 | 1 | 23 | 0.99583 |  | 36 | 3 | 5 | Barrhaven | 8/4.8kV | 140F5 | Crew re-fused transformer fuse at 176 Grenfell. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11995 | 2008 | 1 | 31 | 0.38472 |  | 144 | 31 | 13 | Barrhaven | 8/4.8kV | 140F5 | TE1131 at 30 Wolfgang was replaced due to oil leak & nomenclature changed to TP5578. | Nepean | Scheduled Outage
12018 | 2008 | 2 | 7 | 0.38889 |  | 355 | 65 | 11 | Barrhaven | 8/4.8kV | 140F5 | 8Kv transformer TP5578 @ 128 fielding was isolated to replace the transformer base. | Nepean | Scheduled Outage | Repair
12063 | 2008 | 2 | 19 | 0.40556 |  | 472 | 102 | 13 | Barrhaven | 8/4.8kV | 140F5 | Transformer TP5583 at 30 Wolfgang isolated for installation of new base and splicing of secondary and primary cables. | Nepean | Scheduled Outage | Construction
3262 | 2003 | 3 | 16 | 0.72986 |  | 209 | 3 | 1 | Barrhaven DS | 8/4.8kV | 140F5 | Underground service to house has faulted. Temperary repairs made, service from house next door tied across. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
6387 | 2005 | 4 | 8 | 0.375 |  | 390 | 65 | 10 | Barrhaven | 8/4.8kV | 140F5 | Transformer TE1135 @ 148 Feildgate isolated to repair it's insert. | Nepean | Scheduled Outage | Repair
6407 | 2005 | 4 | 13 | 0.42361 |  | 26 | 5 | 12 |  | 8/4.8kV | 140F5 | Isolation of TE1248 at 55 Thare to replace defective elbow. | Nepean | Scheduled Outage
14317 | 2009 | 5 | 6 | 0.53889 |  | 99 | 8 | 5 | BARRHAVEN DS | 8/4.8kV | 140F5 | transformer at 34 Avonlea Rd isolated to allow for pcb change | Nepean | Scheduled Outage | Preventive Maintenance
6598 | 2005 | 5 | 24 | 0.38333 |  | 611 | 92 | 9 | Barhaven | 8/4.8kV | 140F5 | Transformer #1132 at 40 Horner was Isolated to do a iol spill cleanup | Ottawa | Scheduled Outage | Preventive Maintenance
18252 | 2011 | 5 | 30 | 0.47639 |  | 161 | 38 | 14 | Barrhaven | 8/4.8kV | 140F5 | At 11:26 crews isolated TE1275 at 19 Merkel to replace a transformer. 14 customers affected for 161mins. Barrhaven 140F5, ID# 18252 | Nepean | Scheduled Outage
18284 | 2011 | 6 | 3 | 0.38056 |  | 90 | 15 | 10 | Barrhaven | 8/4.8kV | 140F5 | Transformer TE1771 @ 152 Foxfield was isolated to allow crew to replace elbows and inserts. 10 customers were affected. Barrhaven (140F5). | Nepean | Scheduled Outage
18288 | 2011 | 6 | 3 | 0.39583 |  | 60 | 10 | 10 | Barrhaven | 8/4.8kV | 140F5 | Isolated transformer NPTE1771 to replace inserts and elbows | Nepean | Scheduled Outage | Preventive Maintenance
14471 | 2009 | 6 | 6 | 0.27847 |  | 49 | 3 | 4 | Barrhaven | 8/4.8kV | 140F5 | Transformer #X36374 located at 164 Grenfell isolated due to squirrel contact | Nepean | Foreign Interference | Animal
5406 | 2004 | 6 | 30 | 0.61458 |  | 68 | 34 | 30 | Barrhaven | 8/4.8kV | 140F5 | Price reports cable blown at transformer TE1271w to S1165. 30 Customers affected in power outage. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
18586 | 2011 | 7 | 5 | 0.38194 |  | 290 | 68 | 14 | Barrhaven | 8/4.8kV | 140F5 | Transformer TE1275 @ 19 Merkel Dr was isolated to allow crew to perform transformer remediation and install new transformer base and grounding. 14 customers were affected. Barrahven 140F5 | Nepean | Scheduled Outage | Repair
5463 | 2004 | 7 | 8 | 0.40278 |  | 125 | 21 | 10 | Barrhavean | 8/4.8kV | 140F5 | A. Cooney reports TE1271 isolated to all crew to repair defective cable at TE1271. Located at 51 Elke st in Barrhavean. 10 Customers affected in power outage. G. Morrice switch 1165 white phase was hit by lightening. | Nepean | Scheduled Outage | Repair
5479 | 2004 | 7 | 12 | 0.76042 |  | 437 | 190 | 50 | Barrhaven | 8/4.8kV | 140F5 | 140F5 circuit auto reclosed affecting power to 800 customers. 50 Customers remain out due to blown switch S1246. 24/7 crew reports TE1260 also blown. Power restored to 5 transformers Approx 50 customers @ 21:10. TE1260 remained out until repairs where made approx 8 customers affected. | Nepean | Adverse Weather | Lightning
7215 | 2005 | 8 | 25 | 0.37847 |  | 720 | 84 | 7 | Barrhaven | 8/4.8kV | 140F5 | Transformer NPTE1270 at 5 Elke was isolated and replaced due to oil leak clean up complete | Nepean | Scheduled Outage | Repair
7258 | 2005 | 9 | 1 | 0.38889 |  | 710 | 118 | 10 | Barrhaven | 8/4.8kV | 140F5 | Transformer TE1269 was isolated to replace leaking transformer at 15 Elke DR | Nepean | Defective Equipment | Equipment Deterioration Due to Age
7492 | 2005 | 10 | 20 | 0.38611 |  | 105 | 280 | 160 | Barrhaven | 8/4.8kV | 140F5 | Fencing contractor digging on Fallowfield between Greenbank & Wolfgang dug into B phase cable between S1119 & TE1135. | Nepean | Foreign Interference | Dig-in
7552 | 2005 | 11 | 2 | 0.48264 |  | 41 | 248 | 800 | Barrhaven | 8/4.8kV | 140F5 | When elbow at TE1135 was installed cable blew. Insert & brushing was clead up. 140F5 circuit closed at station via scada restoring load to 680 customer. S1118 fuse was replaced restoring the remained of load. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17220 | 2010 | 11 | 4 | 0.40625 |  | 110 | 18 | 10 | Barrhaven | 8/4.8kV | 140F5 | At 09:45 transformer TP6469 at 77 Fieldgate was isolated to replace defective elbow and bushing. Customers were affected for 110 minutes. Barrhaven (140F5) ID #17220 | Nepean | Scheduled Outage
7772 | 2006 | 1 | 2 | 0.66111 |  | 78 | 78 | 60 | Jockvale | 8/4.8kV | 145F1 | Defective fuse barrell at S1309R phase causing a power outage to 6 transformers. Repairs made and power restored at Flint Crt /Pheasant Run area of Barrhaven, Nepean. | Nepean | Defective Equipment
7805 | 2006 | 1 | 14 | 0.43264 |  | 197 | 33 | 10 | Jockvale | 8/4.8kV | 145F1 | Transformer TE1342 at 22 Whelan Dr isolated for replacement due to leak. | Nepean | Scheduled Outage | Repair
7876 | 2006 | 2 | 2 | 0.375 |  | 20 | 13 | 40 | Jockvale | 8/4.8kV | 145F1 | 5 live front transformers off for switching to isolate TE281 Larkin Dr, Phylis and Fable St in Barrhaven. | Nepean | Scheduled Outage | Construction
7877 | 2006 | 2 | 2 | 0.375 |  | 85 | 27 | 19 | Jockvale | 8/4.8kV | 145F1 | Cable termination to TE281 at 26 St Remy Dr in Barrhaven. | Nepean | Scheduled Outage | Construction
7878 | 2006 | 2 | 2 | 0.5 |  | 57 | 9 | 9 | Jockvale | 8/4.8kV | 145F1 | TE 280 at 4 Langholm isolated for cable replacement, Barrhaven | Nepean | Scheduled Outage | Construction
3166 | 2003 | 2 | 5 | 0.41667 |  | 3 | 0 | 4 | Jockvale | 8/4.8kV | 145F1 | Transformer TE1451 14 Blueridge Cr. required out of service to open defective elbows for isolation to repair defective cable. | Nepean | Scheduled Outage | Repair
3186 | 2003 | 2 | 13 | 0.38472 |  | 62 | 10 | 10 | Jockvale DS | 8/4.8kV | 145F1 | Planned outage to make repairs to transformer TE1452 defective bushings. | Nepean | Scheduled Outage | Repair
3187 | 2003 | 2 | 13 | 0.54236 |  | 94 | 6 | 4 | Jockvale DS | 8/4.8kV | 145F1 | Planned interuption to TE1451 to replace defective transformer. | Nepean | Scheduled Outage | Repair
20214 | 2012 | 3 | 23 | 0.65069 |  | 70 | 5 | 4 | Jockvale | 8/4.8kV | 145F1 | At 15:37 transformer TP6025 at 33 Melville was isolated to allow crew to replace defective transformer. 4 customers were affected for 70 minutes. Jockvale (145F1) ID#20214 | Nepean | Defective Equipment
6357 | 2005 | 4 | 2 | 0.97917 |  | 454 | 303 | 40 | Jockvale | 8/4.8kV | 145F1 | With the heavy rain, the cable termination at transformer 293W @ 32 Longholm had faulted causing the fuse to blow at S833W. | Nepean | Adverse Weather | Rain
17964 | 2011 | 4 | 19 | 0.39583 |  | 250 | 33 | 8 | Jockvale | 8/4.8kV | 145F1 | TP6030 @ 11 Teevens was isolated to allow crew to replace elbows and inserts. 8 customers were affected. Jockvale a145F1. | Nepean | Scheduled Outage
6449 | 2005 | 4 | 23 | 0.48958 |  | 419 | 2100 | 950 |  | 8/4.8kV | 145F1 | J. Kelly reports temp repairs have been made to hydro pole on Jockvale & Fable. Outage was caused by pole fire at this location. After all load restored S1179B switch found lead burnt off. | Nepean | Adverse Weather | Rain
16005 | 2010 | 4 | 27 | 0.35764 |  | 112 | 7 | 4 | Jockvale | 8/4.8kV | 145F1 | Transformer #X36749 located at 16 Melville opened due to a blown arrestor | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8272 | 2006 | 5 | 10 | 0.39583 |  | 610 | 102 | 10 | Jockvale | 8/4.8kV | 145F1 | Isolated transformer TE1342 @ 22 Whelan Dr to dig up oil contaminate soil. | Nepean | Scheduled Outage | Repair
8278 | 2006 | 5 | 11 | 0.38264 |  | 444 | 740 | 100 | Jockvale | 8/4.8kV | 145F1 | TP3883 isolated to remove contaminated oil at 22 Whelan Drive | Nepean | Scheduled Outage | Repair
8298 | 2006 | 5 | 15 | 0.41667 |  | 495 | 82 | 10 | Barhaven | 8/4.8kV | 145F1 | Isolated and replaced transformer TP3883 at 20 Whelan Cres due to oil leak | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5265 | 2004 | 6 | 8 | 0.8625 |  | 18 | 0 | 1 | Jockvale | 8/4.8kV | 145F1 | S367 White phase switch failed. Switch replaced all power restored. Outage to 1 Customer. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12623 | 2008 | 6 | 14 | 0.079861 |  | 192 | 326 | 102 | Jockvale | 8/4.8kV | 145F1 | Fuse barrell burnt up at S1179 White phase. Switch was isolated and power restored to customers. Switch replaced. Restoration was delayed as oncall was required. | Nepean | Defective Equipment
10649 | 2007 | 6 | 18 | 0.70139 |  | 82 | 68 | 50 | Jockvale | 8/4.8kV | 145F1 | 24/7 reports top of switch broken S1147 blue phase switch replaced & closed. All power restored to normal. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12815 | 2008 | 7 | 10 | 0.37986 |  | 346 | 69 | 12 | Jockvale | 8/4.8kV | 145F1 | TP4786W cable replacement and transformer change. 45 Otten street Barrhaven. | Nepean | Scheduled Outage | Construction
12842 | 2008 | 7 | 15 | 0.43056 |  | 149 | 60 | 24 | Jockvale | 8/4.8kV | 145F1 | TP4787 at 53 Raftus was isolated for transformer & cable replacement, isolation included transformer TP4788 at 43 Raftus due to a defective elbow/insert at TP4788. | Nepean | Scheduled Outage | Preventive Maintenance
12845 | 2008 | 7 | 16 | 0.38264 |  | 269 | 49 | 11 | Jockvale | 8/4.8kV | 145F1 | TP4788 at 43 Raftus isolated for Barhaven cable replacement program, transformer was also replaced. 11 customers on Raftus Square & Airycot Circle were affected. | Nepean | Scheduled Outage | Preventive Maintenance
12869 | 2008 | 7 | 17 | 0.41319 |  | 280 | 47 | 10 | Jockvale | 8/4.8kV | 145F1 | TP4789 at 27 Raftus isolated for planned cable & transformer replacement. | Nepean | Scheduled Outage | Construction
12922 | 2008 | 7 | 22 | 0.39583 |  | 340 | 62 | 11 | Jockvale | 8/4.8kV | 145F1 | Crews isolated TP4790W at 55 Otten for cable and transformer replacement program | Nepean | Scheduled Outage
12934 | 2008 | 7 | 24 | 0.41736 |  | 151 | 40 | 16 | Jockvale | 8/4.8kV | 145F1 | TP4779 was isolated for transformer schange and cable replacement. During switching, the insert broke at TP4780 which had to be isolated as well. | Nepean | Scheduled Outage
5582 | 2004 | 7 | 29 | 0.75278 |  | 289 | 722 | 400 | Jockvale | 8/4.8kV | 145F1 | Truck hit a guy wire and pulled a pole over on Jockvale Rd. south of Fable causing the circuit to open. Crew sectionalized the damaged area and the bulk of the customers were restored while temporary repairs were performed to restore the remaining customers. | Nepean | Foreign Interference | Vehicle
12982 | 2008 | 7 | 31 | 0.37986 |  | 360 | 66 | 11 | Jockvale | 8/4.8kV | 145F1 | TP4782 at 54 Remy isolated from Hydro Ottawa Sources for cable isolation and transformer change. | Nepean | Scheduled Outage
3847 | 2003 | 8 | 5 | 0.76597 |  | 205 | 44 | 13 | Jockvale | 8/4.8kV | 145F1 | power outage at 18 Bourne st was caused due to an 8 amp fuse install at TX2039. Transformer was isolated and fuse replaced with 15 amp. All power was restored to normal. Also crews had to dig out TX 2044 before completing oto to isolate TX2039. Customer had back filled around transformer. | Nepean | Human Element | Incorrect Installation
5619 | 2004 | 8 | 6 | 0.76111 |  | 24 | 18 | 45 | Jockevale | 8/4.8kV | 145F1 | To make emergency repairs to the hot line clamp at S1146W on Jockevale, swithing had to be done at transformer TE1182W. While switching, the elbow at TE1182W broke causing the swithing to stop. While discussing the problem with the 24/7 and Ron Roy we decided to have momentary outage while the repairs were being made. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
5644 | 2004 | 8 | 10 | 0.74583 |  | 4 | 17 | 250 | Jockvale | 8/4.8kV | 145F1 | 145F1 open ask police and Fire department of any accidents none reported Closed via manually. | Nepean | Adverse Weather | Lightning
13040 | 2008 | 8 | 12 | 0.37917 |  | 379 | 63 | 10 | Jockvale | 8/4.8kV | 145F1 | TP4783 at 14 Phylis was isolated for part of the cable and transformer replacment project | Nepean | Scheduled Outage | Preventive Maintenance
13061 | 2008 | 8 | 15 | 0.39653 |  | 341 | 45 | 8 | JOCKVALE | 8/4.8kV | 145F1 | TP4787 at 53 Raftus, Nepean, was isolated to replace transformer and base | Nepean | Scheduled Outage
13151 | 2008 | 8 | 26 | 0.38542 |  | 245 | 45 | 11 | Jockvale | 8/4.8kV | 145F1 | TP4771 at 128 Larkin was isolated for cable replacement and transformer change | Nepean | Scheduled Outage
13158 | 2008 | 8 | 27 | 0.3875 |  | 435 | 116 | 16 | Jockvale | 8/4.8kV | 145F1 | TP4772 at 42 St Remy was isolated to change out the transformer for cable/xfmr cable replacement program | Nepean | Scheduled Outage
15014 | 2009 | 8 | 27 | 0.42292 |  | 137 | 219 | 130 | Jockvale | 8/4.8kV | 145F1 | 145F1 white phase cable fault between TP5955 and TP5954 on Whelan and Fable caused the S1180 to open. While fault finding the 145F1 auto-reclosed. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11215 | 2007 | 8 | 30 | 0.24236 |  | 295 | 34 | 7 | Jockvale | 8/4.8kV | 145F1 | Transformer fuse blew at 163 Pheasant Run, in Nepean, crew re-fused transformer, all power restored at 10:44 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13179 | 2008 | 9 | 2 | 0.39583 |  | 340 | 68 | 12 | Jockvale | 27.6/16kV | 145F1 | TP4791 @ 14 Raftus was isolated to replace transformer and cable. | Nepean | Scheduled Outage | Construction
13191 | 2008 | 9 | 4 | 0.38889 |  | 310 | 62 | 12 | Jockvale | 8/4.8kV | 145F1 | TP4793 at 42 Raftus was isolated for cable and transformer replacement program. 12 customers affected an power was restored at 14:30. | Nepean | Scheduled Outage | Preventive Maintenance
13211 | 2008 | 9 | 10 | 0.37014 |  | 297 | 74 | 15 | Jockvale | 8/4.8kV | 145F1 | Transformer TP4779 @ 178 Larkin was isolated for transformer and cable replacement program. | Nepean | Scheduled Outage | Preventive Maintenance
19231 | 2011 | 9 | 21 | 0.43681 |  | 371 | 25 | 4 | Jockvale | 8/4.8kV | 145F1 | TP6025 at 33 Melville was isolated to allow crews to install a new transformer base and energize a new xfmr TP8017. | Nepean | Scheduled Outage | Construction
13334 | 2008 | 10 | 7 | 0.40556 |  | 77 | 10 | 8 | Jockvale | 8/4.8kV | 145F1 | Transformer TE844 isolated for transformer replacement. | Nepean | Scheduled Outage
19434 | 2011 | 10 | 21 | 0.39028 |  | 387 | 39 | 6 | Jockvale | 8/4.8kV | 145F1 | Crews isolated TP6024 at 39 Phylis to reconfigure cable. | Nepean | Scheduled Outage
7563 | 2005 | 11 | 3 | 0.9625 |  | 74 | 25 | 20 | Jockvale | 8/4.8kV | 145F1 | Crew found switch 1147 white phase had a burnt fuse barrel. Switch replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19597 | 2011 | 11 | 18 | 0.39236 |  | 335 | 67 | 12 | Jockvale | 8/4.8kV | 145F1 | TP6022 on Phylis was isolated to allow crews to rearrange the cables and upgrade the transformer base. | Nepean | Scheduled Outage | Construction
17319 | 2010 | 11 | 22 | 0.44444 |  | 96 | 16 | 10 | JOCKVALE DS | 8/4.8kV | 145F1 | Transformer TP6032 at 50 Fable isolated to change elbows and replacement of secondary | Nepean | Scheduled Outage | Repair
13729 | 2008 | 12 | 10 | 0.39931 |  | 188 | 38 | 12 | Jockvale | 8/4.8kV | 145F1 | Crew isolated 8Kv transformer at 28 Merner TP6197 to allow greely to remove sand from the transformer | Nepean | Scheduled Outage | Preventive Maintenance
13784 | 2008 | 12 | 20 | 0.45556 |  | 48 | 10 | 13 | Jockvale | 8/4.8kV | 145F1 | TP5935 at 210 Sherway Dr. was isolated to repair defective insert - unable to remove insert, equipment remains defective | Nepean | Scheduled Outage
13799 | 2008 | 12 | 27 | 0.38542 |  | 145 | 31 | 13 | Jockvale | 8/4.8kV | 145F1 | TP5935 at 210 Sherway has been isolated to allow crew to replace transformer. 13 customers affected | Nepean | Scheduled Outage
9913 | 2007 | 1 | 10 | 0.42361 |  | 542 | 63 | 7 | Jockvale | 8/4.8kV | 145F2 | TE1181 @ 5 Otten Dr was isolated to allow crews to replace a leaking transformer. 7 Customers affected in planned outage. | Nepean | Scheduled Outage | Repair
9925 | 2007 | 1 | 14 | 0.70833 |  | 157 | 34 | 13 | JOCKVALE | 8/4.8kV | 145F2 | Switch 898 fuse barrel found defective at Lytle & Cedearview. Switch replaced all power restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9927 | 2007 | 1 | 15 | 0.75 |  | 102 | 170 | 100 | Jockvale | 8/4.8kV | 145F2 | A burnt white phase elbow and burnt nsert at TE1870, 35 Larkin, Nepean was isolated to restore power to customers. | Nepean | Defective Equipment
9947 | 2007 | 1 | 19 | 0.38889 |  | 142 | 24 | 10 | Jockvale | 8/4.8kV | 145F2 | Transformer # 738 on Larkin Dr was isolated to all crew to repair transformer door & remove retaining wall. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
17551 | 2011 | 2 | 4 | 0.70486 |  | 35 | 2 | 4 | Jockvale | 8/4.8kV | 145F2 | While isolating RWB cable section between TE327 rwb & TE188R , TP4818W & TE1369B. Crew opened blue phase cable at TE1368 to TE1369, and causing outage at TE1369. | Nepean | Human Element | Switching Errors
19994 | 2012 | 2 | 9 | 0 |  | 161 | 54 | 20 | Jockvale | 8/4.8kV | 145F2 | At 00:00 crews isolated the 145F2 between SE20 and S471 on Cedarview to cut in Temp switches. 20 customers affected for 161 mins. Jockvale 145F2 ID# 19994 | Nepean | Scheduled Outage | Repair
12033 | 2008 | 2 | 11 | 0.3875 |  | 212 | 32 | 9 | Jockvale | 8/4.8kV | 145F2 | Livefront transformer TP4768 at 4 Langholm replaced with elbow style due to oil leak. | Nepean | Scheduled Outage | Repair
12079 | 2008 | 2 | 25 | 0.40069 |  | 433 | 79 | 11 | Jockvale | 8/4.8kV | 145F2 | TE193 @ 36 Ettrick was isolated fro crew to install transformer base and splice in secondary & primary cables. | Nepean | Scheduled Outage | Construction
12086 | 2008 | 2 | 28 | 0.38194 |  | 313 | 47 | 9 | Jockvale | 8/4.8kV | 145F2 | TP4768 was isolated, to allow crew to replace concrete transformer pad. | Nepean | Scheduled Outage | Repair
4862 | 2004 | 3 | 5 | 0.5625 |  | 335 | 281 | 60 | Jockvale | 8/4.8kV | 145F2 | Flooding at transfomer TE293 caused S833 white phase to blow . | Nepean | Adverse Weather | Rain
4874 | 2004 | 3 | 10 | 0.67014 |  | 115 | 115 | 60 | Jockvale | 8/4.8kV | 145F2 | The blue phase at switch 866 on Fallowfield fell open. The hot line clamp and jaw side requires fixing | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12124 | 2008 | 3 | 11 | 0.41944 |  | 93 | 9 | 6 | Jockvale | 8/4.8kV | 145F2 | Transformer TE1407 @ 6 Woodsia was replaced. | Nepean | Scheduled Outage | Repair
3281 | 2003 | 3 | 21 | 0.090278 |  | 435 | 109 | 15 | Jockvale DS | 8/4.8kV | 145F2 | Transformer secondary fuses found blown due to flooding around the tranformer. | Nepean | Adverse Environment | Flooding
8098 | 2006 | 4 | 3 | 0.51528 |  | 754 | 1235 | 830 | Jockvale | 8/4.8kV | 145F2 | Billy Seaman was replacing insulators at switch S923 on Cedarveiw and all the load was over to S805, when complete he transfer it back over to S923 when the isolation was complete the fuse at S923 blew, Billy found a bad hot line clamp and fixed it,Refused it and it blew and it took the 145F2 curcuit. Went to open point at TE1424 and closed in at S805, it blew taking the 145F2 out also. Found four bad transformer at TE1431(52 Cedarhill),TE1419(7 Burnt Tree) & TE1416(20 Cedarhill),TE1427(1 Glen Oaks Cir | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6431 | 2005 | 4 | 20 | 0.39097 |  | 401 | 75 | 25 | Jockvale | 8/4.8kV | 145F2 | Transformer te293 and base replaced. 14 customers out for switching at the beginning of outage. | Nepean | Scheduled Outage | Repair
5082 | 2004 | 5 | 1 | 0.3125 |  | 102 | 27 | 16 | Jockvale | 8/4.8kV | 145F2 | A car hit a pole on Cederview at Lytle Ave. To remove the car safely the 44KV and 8KV O/H line had to be isolated causing an outage to 16 customers on Lytle Ave.. See int 5085 | Nepean | Foreign Interference | Vehicle
10355 | 2007 | 5 | 2 | 0.59861 |  | 10 | 138 | 831 | Jockvale | 8/4.8kV | 145F2 | when crew was closing at transformer TP4834 on the oto to isolate the blue phase cable section between S866 and TP4833 switch stick contacted the transformer TP4834 casing which caused the Jockvale 145F2 circuit to open. | Ottawa | Human Element | Incorrect Use of Equipment
8223 | 2006 | 5 | 3 | 0.39375 |  | 433 | 58 | 8 | Jockvale | 8/4.8kV | 145F2 | Transformer TE413 isolated to replace transformer on 20 Barrhaven Street. | Nepean | Scheduled Outage
6610 | 2005 | 5 | 28 | 0.93889 |  | 208 | 102 | 30 | Jockvale | 8/4.8kV | 145F2 | Cable fault cable section S833W to TE291 Fallowfield Rd near Larkin. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8491 | 2006 | 6 | 15 | 0.44722 |  | 132 | 110 | 50 | Jockvale | 8/4.8kV | 145F2 | Cable Dig in on Fallowfield Road at Barran St, caused S761 W phase to blow. 5 Transformers were affected on Ettrick and Barrhaven Street, Nepean. | Nepean | Foreign Interference | Dig-in
16410 | 2010 | 7 | 6 | 0.77222 |  | 136 | 1141 | 712 | Jockvale | 8/4.8kV | 145F2 | Defective insulator on Fallowfield between Cedarview and Greenbank caused the 145F2 to auto reclose and lock out. Power restored in sections. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16411 | 2010 | 7 | 6 | 0.82708 |  | 57 | 204 | 283 | Jockvale | 8/4.8kV | 145F2 | defective insulator on Fallowfield rd caused 145F2 to auto reclose and lock out. Load restored in sections. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5460 | 2004 | 7 | 7 | 0.90069 |  | 130 | 1052 | 900 | Jockvale | 8/4.8kV | 145F2 | They found a blown insulator on the 145F2 on Cedarview. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12800 | 2008 | 7 | 7 | 0.39792 |  | 717 | 299 | 25 | Jockvale | 8/4.8kV | 145F2 | Transformers TP4775 & TP4776 on Langholm and St. Reamy were isolated as part of a cable replacement program. | Nepean | Scheduled Outage | Construction
12806 | 2008 | 7 | 8 | 0.37639 |  | 350 | 128 | 22 | Jockvale | 8/4.8kV | 145F2 | Transformers TP4773 & 4774 were isolated as part of the cable replacement program. | Nepean | Scheduled Outage | Construction
12808 | 2008 | 7 | 9 | 0.38194 |  | 335 | 39 | 7 | Jockvale | 8/4.8kV | 145F2 | Isolate transformer TP4785 @ 160 Larkin for cable replacement pr5oject and transformer change. | Nepean | Scheduled Outage | Preventive Maintenance
14695 | 2009 | 7 | 10 | 0.41042 |  | 102 | 15 | 9 | Jockvale | 8/4.8kV | 145F2 | Crews isolated transformer TP3996 (TE1418) at 6 timbercrest to change a leaking transformer. | Nepean | Scheduled Outage | Repair
12927 | 2008 | 7 | 23 | 0.37986 |  | 391 | 130 | 20 | Jockvale | 8/4.8kV | 145F2 | TP477B and TP4778B isolated from hydro Ottawa sources at 195 Larkin and 5 Otten for cable replacement and transformer change. | Nepean | Scheduled Outage | Preventive Maintenance
16570 | 2010 | 7 | 27 | 0.37778 |  | 346 | 38 | 10 | Jockvale | 8/4.8kV | 145F2 | transformer at 12 Feather Sound was isolated to allow crews to upgrade transformer, when isolating the broke the insert and had to expand the isolation to include transformer at 44 Cedarhill, then that transformer was restored and the the transformwer on Feather Sound was isolated to continue their work. | Nepean | Scheduled Outage | Construction
12966 | 2008 | 7 | 29 | 0.38611 |  | 346 | 46 | 8 | Jockvale | 8/4.8kV | 145F2 | TP4780 @ 166 Larkin was isolated as part of the cable replacement program. | Nepean | Scheduled Outage | Construction
12975 | 2008 | 7 | 30 | 0.38194 |  | 296 | 39 | 8 | JockVale | 8/4.8kV | 145F2 | TP4781 @ 62 remy was isolated for the cable replacement program. | Nepean | Scheduled Outage | Construction
14886 | 2009 | 7 | 31 | 0.38889 |  | 326 | 49 | 9 | Jockvale | 8/4.8kV | 145F2 | TP3996 at 6 Timbercrest isolated to soil reclamation after oil spill. | Nepean | Scheduled Outage | Repair
13049 | 2008 | 8 | 13 | 0.40556 |  | 263 | 53 | 12 | Jockvale | 8/4.8kV | 145F2 | TP4765 at 23 Langholm isolated for part of the cable and transformer replacement project | Nepean | Scheduled Outage | Preventive Maintenance
13055 | 2008 | 8 | 14 | 0.38194 |  | 252 | 38 | 9 | Jockvale | 8/4.8kV | 145F2 | Transformer TP4766 @ 16 Langholm was isolated for cable and transformer replacement. | Nepean | Scheduled Outage | Preventive Maintenance
13124 | 2008 | 8 | 19 | 0.37847 |  | 295 | 0 | 10 | Jockvale | 8/4.8kV | 145F2 | Isolation on TP4767 at 10 Jerrilynn from Hydro Ottawa Sources | Nepean | Scheduled Outage | Preventive Maintenance
13129 | 2008 | 8 | 20 | 0.40278 |  | 360 | 96 | 16 | JOCKVALE | 8/4.8kV | 145F2 | TP4768 & TP4769 on Langholm, Nepean were isolated for transformer and cable replacement. | Nepean | Scheduled Outage
13134 | 2008 | 8 | 21 | 0.38681 |  | 303 | 50 | 10 | Jockvale | 8/4.8kV | 145F2 | TP4770 at 100 Larkin was isolated as part of the cable and transformer replacement program | Nepean | Scheduled Outage | Construction
13164 | 2008 | 8 | 28 | 0.42847 |  | 317 | 53 | 10 | JOCKVALE | 8/4.8kV | 145F2 | TP4784 isolated for cable and transformer replacement at 52 Larkin Dr. | Nepean | Scheduled Outage
13185 | 2008 | 9 | 3 | 0.39792 |  | 255 | 51 | 12 | Jockvale | 8/4.8kV | 145F2 | Transformer TP4792 @ 26 Raftus was isolated for transformer and cable replacement. | Nepean | Scheduled Outage | Construction
13217 | 2008 | 9 | 11 | 0.4 |  | 354 | 59 | 10 | Jockvale | 8/4.8kV | 145F2 | transformer TE186 @ 9 Barran was isolated to replace same. Transformer was leaking oil. | Nepean | Scheduled Outage | Repair
11396 | 2007 | 9 | 27 | 0.37083 |  | 6 | 5 | 48 | Jockvale | 8/4.8kV | 145F2 | Crew interrpted power to six live front transformers to switch out cable isolation in Barhaven. | Nepean | Scheduled Outage | Repair
11438 | 2007 | 10 | 2 | 0.37639 |  | 531 | 221 | 25 | Jockvale | 8/4.8kV | 145F2 | TP4826 & TP4830 on Leetom & Larkin including cables isolated for planned cable & transformer replacement. | Nepean | Scheduled Outage | Construction
11569 | 2007 | 10 | 22 | 0.40139 |  | 400 | 113 | 17 | Jockvale | 8/4.8kV | 145F2 | TP4833 & TP3847 on Barhaven cresc. Were isolated for planned transformer & cable replacement. | Nepean | Scheduled Outage | Construction
11586 | 2007 | 10 | 24 | 0.39306 |  | 553 | 236 | 40 | Jockvale | 8/4.8kV | 145F2 | Transformers TP4834,TP4831,TP4832, and TP4828 on Tripp Ave in Nepean isolated for transformer and cable replacement. | Nepean | Scheduled Outage | Preventive Maintenance
11642 | 2007 | 11 | 1 | 0.39792 |  | 186 | 12 | 4 | Jockvale | 8/4.8kV | 145F2 | Transformer TE1422 @ 38 Cedarhill was isolated to replace the secondary services that were heating up. | Nepean | Scheduled Outage | Repair
11643 | 2007 | 11 | 1 | 0.52708 |  | 351 | 35 | 6 | Jockvale | 8/4.8kV | 145F2 | Transformer TE1415 @ 12 Cedarhill was isolated to replace the secondary services that were heating up and replace defective insert. | Nepean | Scheduled Outage
7607 | 2005 | 11 | 13 | 0.94444 |  | 464 | 237 | 250 |  | 8/4.8kV | 145F2 | Double cable fault on the 145F2 circuit on Langholm Cres/St. Remy Drive Area. Supervisor on call advised to call in 2 lineman and Randy Kerr to test cable. Cable tested good, switching performed to restore power. | Nepean | Defective Equipment
7640 | 2005 | 11 | 21 | 0.39861 |  | 20 | 0 | 1 | JOCKVALE | 8/4.8kV | 145F2 | G. MORRIS REPORTS BURNING HOT LINE CLAMP AT GUARD HOUSE @ 3851 FALLOWFEILD (XMEr 587) ON CIRCUIT 145F2. HOT LINE CLAMP REPLACED/ REPAIRED, POWER RESTORED. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7646 | 2005 | 11 | 22 | 0.57986 |  | 9 | 5 | 35 | Jockvale | 8/4.8kV | 145F2 | Switch S879 on Fallowfield Rd had to be opened to repair a burning hotline clamp, 4 txs interupted while repairs were made. | Nepean | Defective Equipment
17359 | 2010 | 11 | 30 | 0.39236 |  | 30 | 3 | 6 | Jockvale | 8/4.8kV | 145F2 | At 9:25am crews isolated transformer TP7326 at 6 Feather Sound for work on the ground grid. 6 customers were affected for 30mins. Jockvale 145F2 ID# 17359 | Nepean | Scheduled Outage | Preventive Maintenance
7678 | 2005 | 12 | 2 | 0.48958 |  | 105 | 70 | 40 | Jockvale | 8/4.8kV | 145F2 | Tap from O/H to switch S833W burnt off affectng customers on St Remy & Langholm, connection redone. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7753 | 2005 | 12 | 22 | 0.51736 |  | 21 | 45 | 960 | 145F2 | 8/4.8kV | 145F2 | When crew was resoring faulted cbl section between TE280R and TE281R, fault re-occurred causing 145F2 to trip. Crew found fuse at S876 open. 145F2 closed back in. All but 40 customers picked up. S876 re-fused and all customers picked up. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13840 | 2009 | 1 | 6 | 0.36458 |  | 47 | 5 | 6 | Jockvale | 8/4.8kV | 145F3 | Transformer #X3495 located at 5530 Richmond Rd isolated due to upgrade | Nepean | Scheduled Outage | Construction
13853 | 2009 | 1 | 10 | 0.25694 |  | 370 | 105 | 17 | Jockvale | 8/4.8kV | 145F3 | Pole broken by vehilce accident on Twin Elm south of Cambrian had to be replaced by Oncall crew. Linbe was isolated during replacement. | Nepean | Foreign Interference | Vehicle
19822 | 2012 | 1 | 12 | 0.93472 |  | 407 | 296 | 347 | Jockvale | 8/4.8kV | 145F3 | 145F3 CB A/R, then breaker tripped 5 minutes later. OFD reported MVA at Fallowfield & Eagleson. Crews reported broken pole and 2 spans of wire down, S23681 Opened and 145F3 CB closed. Power restored to all but 5 customers.. | Nepean | Foreign Interference | Vehicle
19831 | 2012 | 1 | 14 | 0.46875 |  | 3174 | 943 | 360 | Jockvale DS | 8/4.8kV | 145F3 | The 145F3 breaker opened. Hydro Ottawa crews patrolled and found damaged conductor & a broken insulator at 4554 Fallowfield Rd. Crews performed emergency switching to restore power. When parallel was made between the 145F3 & 145F4 it caused 145F4 white phase conductor to burn down at 2990 Moodie. | Nepean | Unknown/Other | No Apparent Cause
4703 | 2004 | 1 | 15 | 0.975 |  | 66 | 66 | 60 | Jockvale | 8/4.8kV | 145F3 | Floating center phase conductor at Richmond Rd & Rushmore made contact with another phase, fuse at S113 opened. The other two phases were opened to accommodate repairs. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19864 | 2012 | 1 | 19 | 0.50833 |  | 138 | 7 | 3 | Jockvale | 8/4.8kV | 145F3 | Transformer #X35907 at 1635 Fallowfield, X08808 - 1631 Fallowfield & X08806 at 1601 Fallowfield opened by crew to repair #4 acsr neutral conductor and re-sagged. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
4748 | 2004 | 1 | 24 | 0.47917 |  | 8940 | 149 | 1 | Jockvale | 8/4.8kV | 145F3 | Charterways at 1027 Moodie Dr have had their cable repaired and power restored to transformer 955. Cable was customer owned and their responsibility to replace/ repair. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11989 | 2008 | 1 | 29 | 0.53611 |  | 111 | 15 | 8 | Bells Corners Sub | 8/4.8kV | 145F3 | Transformer #X3792 located at 32 Steeple Hill Cres isolated to allow for transfer of plant. | Nepean | Scheduled Outage
13926 | 2009 | 2 | 3 | 0.52917 |  | 58 | 4 | 4 | Barhaven | 8/4.8kV | 145F3 | TE1473 @ 5 Piety Hill was isolated to repair defective elbow & insert. | Nepean | Scheduled Outage | Repair
13930 | 2009 | 2 | 3 | 0.52083 |  | 70 | 5 | 4 | Jockvale | 8/4.8kV | 145F3 | Isolated transformer TE1473 at 5 Piety Hill Way for service up-grade (duplicate of ID # 13926) | Nepean | Scheduled Outage | Preventive Maintenance
13961 | 2009 | 2 | 11 | 0.70972 |  | 73 | 1 | 1 | Jockvale | 8/4.8kV | 145F3 | Transformer #X3872 located at 3231 Steeple Hill isolated due to blown transformer fuse. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7941 | 2006 | 2 | 17 | 0.49028 |  | 237 | 1666 | 620 | Jockvale | 8/4.8kV | 145F3 | With the high winds caused the O/H to slap together and brake the insulators off causing the primary to Float in two different location and brake two phases at switch S113 on Richmond Side Rd. | Nepean | Adverse Weather | Wind
6289 | 2005 | 3 | 15 | 0.65347 |  | 15 | 0 | 1 | Jockvale | 8/4.8kV | 145F3 | Isolate Transformer #756 at 950 Moodie dr to replace a blown arrestor and refuse cutout | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3300 | 2003 | 3 | 25 | 0.69514 |  | 374 | 280 | 45 | Jockvale DS | 8/4.8kV | 145F3 | Jockvale DS 145F3 auto tripped and auto reclosed when a pole was hit by a Purolator van. A fused switch also blew because of the accident leaving a section of the feeder on Steeple Hill Cr. between Fallowfield Rd. and Richmond Rd.remained out of service. The van was removed from the pole, the fused switch repaired and the customers were restored at 8:55 pm | Nepean | Foreign Interference | Vehicle
12179 | 2008 | 3 | 27 | 0.42083 |  | 115 | 134 | 348 | Jockvale | 8/4.8kV | 145F3 | 145F3 breaker tripped under hold Off to Louie Lauzon for tree contractor ( Tamarack) Appears truck boom contacted overhead and caused breaker to open and S152 fuse to blow. Safety Department investigating. Breaker closed from SCADA. Overhead repaired and S152 closed. | Nepean | Human Element | Incorrect Use of Equipment
17809 | 2011 | 3 | 31 | 0.44444 |  | 43 | 2 | 3 | Jockvale | 8/4.8kV | 145F3 | PC10a #8154 estabklished at S1252 to allow contractors to perform tree trimming, 3 customers affected for 43 minutes | Nepean | Scheduled Outage | Preventive Maintenance
8092 | 2006 | 4 | 1 | 0.59097 |  | 185 | 234 | 352 | JOCKVALE | 8/4.8kV | 145F3 | POLE FIRE AT FALLOWFIELD/MOODIE. CREW ISOLATED POLE MADE PARTIAL REPAIRS AND RSTORED LOAD. | Nepean | Unknown/Other | No Apparent Cause
14194 | 2009 | 4 | 20 | 0.69653 |  | 117 | 2 | 1 | Jockvale | 8/4.8kV | 145F3 | Tree contact caused transformer X40027 @ 3800 Twin Elm to open from S143. Crew trimmed and refused and closed. | Nepean | Tree Contacts | Inadequate Trimming
20399 | 2012 | 4 | 26 | 0.65 |  | 44 | 1 | 1 | Jockvale | 8/4.8kV | 145F3 | Refused line switch feeding private primary line and transformer X39850 at 5271 Richmond Rd (Cause of blown fuse unkown) | Nepean | Unknown/Other | No Apparent Cause
12393 | 2008 | 5 | 5 | 0.55556 |  | 45 | 2 | 2 | Jockvale | 8/4.8kV | 145F3 | Isolated transformer X3501 at 5576 Richmond Rd to replace the lightning arrester | Nepean | Scheduled Outage | Repair
14370 | 2009 | 5 | 16 | 0.49653 |  | 129 | 11 | 5 | Jockvale | 8/4.8kV | 145F3 | S755 on Richomnd rd red phase fuse found blown due to inclement weather. | Nepean | Adverse Weather
8323 | 2006 | 5 | 19 | 0.38264 |  | 389 | 52 | 8 | Jockvale | 8/4.8kV | 145F3 | TE 1397 leaker replaced with TP2808 at 28 Spring Cres Dr, Barf-haven. | Nepean | Scheduled Outage | Preventive Maintenance
14545 | 2009 | 6 | 16 | 0.35417 |  | 230 | 8 | 2 | Jockvale | 8/4.8kV | 145F3 | Transformer #X40041 located at 5026 Rushmore isolated for contractor to replace rotten pole | Nepean | Scheduled Outage | Construction
16274 | 2010 | 6 | 17 | 0.29444 |  | 111 | 2 | 1 | Jockvale | 8/4.8kV | 145F3 | Replaced blown fuse feeding transformer X5001 at 4820 Cambrian Rd | Nepean | Adverse Weather | Rain
16292 | 2010 | 6 | 19 | 0.62222 |  | 164 | 8 | 3 | Jockvale | 8/4.8kV | 145F3 | Crew replaced a broken switch. | Nepean | Defective Equipment
8584 | 2006 | 6 | 23 | 0.75764 |  | 114 | 2 | 1 | JOCKVALE | 8/4.8kV | 145F3 | Power outage on transformer NP0160 at 4750 Fallowfield Rd due to broken switch | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8619 | 2006 | 6 | 28 | 0.66667 |  | 171 | 14 | 5 | Jockvale | 8/4.8kV | 145F3 | A burnt center phase conducter which fell to the ground. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
5409 | 2004 | 6 | 30 | 0.74097 |  | 106 | 2 | 1 | Jockvale | 8/4.8kV | 145F3 | NP1592 at 3460 Twin Elm tree on private single phase. | Nepean | Tree Contacts | Tree Limb Fallen
6861 | 2005 | 7 | 1 | 0.75 |  | 2565 | 43 | 1 | Jockvale | 8/4.8kV | 145F3 | Refused a transformer at 3862 Moodie Dr. | Nepean | Adverse Weather | Lightning
18584 | 2011 | 7 | 5 | 0.10764 |  | 388 | 39 | 6 | Jockvale | 8/4.8kV | 145F3 | A vehicle struck a pole at 6633 Richmond Road causing pole to break and wires to come down across the road. Jockvale (145F3) ID#18584 | Nepean | Foreign Interference | Vehicle
14737 | 2009 | 7 | 13 | 0.44167 |  | 64 | 6 | 6 | Jockvale | 8/4.8kV | 145F3 | TP5706 at 6 Woodsia was isolated to replace leaking transformer | Nepean | Scheduled Outage
10908 | 2007 | 7 | 18 | 0.65208 |  | 141 | 9 | 4 | Jockvale | 8/4.8kV | 145F3 | defective switch opened at S755 at 6633 Richmond rd. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
12887 | 2008 | 7 | 18 | 0.20833 |  | 265 | 75 | 17 | Jockvale | 8/4.8kV | 145F3 | Crew found S19 R & B on Twin Elm open after storm in area, O/H section patrolled & fuses replaced. | Nepean | Adverse Weather | Lightning
18810 | 2011 | 7 | 24 | 0.85625 |  | 5 | 19 | 226 | JOCKVALE | 8/4.8kV | 145F3 | While trying to restore power to a section of the 46F6 crews closed switch energizing a section of conductor in contact with a tree limb causing the breaker to trip open. Crews re-openned switch and power was restored. Jockvale 145F3 | Nepean | Tree Contacts
13007 | 2008 | 8 | 6 | 0.41875 |  | 11 | 65 | 352 | Jockvale | 8/4.8kV | 145F3 | The 145F3 trip under hold off,crews patrolled and found nothing in the Fallowfeild/Richmond Rd area | Nepean | Unknown/Other | No Apparent Cause
14937 | 2009 | 8 | 12 | 0.39931 |  | 280 | 9 | 2 | Jockvale | 8/4.8kV | 145F3 | Transformer #X3484 located at 5477 Richmond Rd isolated to upgrade transformer to 347/600 | Nepean | Scheduled Outage | Construction
5684 | 2004 | 8 | 16 | 0.27153 |  | 78 | 3 | 2 | Jockvale | 8/4.8kV | 145F3 | Squirrel got into a transformer switch at 5569 Richmond Rd. | Nepean | Foreign Interference | Animal
8980 | 2006 | 8 | 16 | 0.10764 |  | 80 | 1 | 1 | Jockvale | 8/4.8kV | 145F3 | The new switch at 3302 MOODIE DR NEPN fell open last night, crew patrolled found nothing. | Nepean | Unknown/Other | No Apparent Cause
3954 | 2003 | 8 | 21 | 0.99306 |  | 223 | 4 | 1 | Jockvale | 8/4.8kV | 145F3 | Lighning caused damage to Cutout and arrestor at 3306 Steeple hill. | Nepean | Adverse Weather | Lightning
5704 | 2004 | 8 | 23 | 0.46875 |  | 168 | 54 | 30 | Jockvale | 8/4.8kV | 145F3 | B. Armstrong reports W & B phases down on road. S1598 opened to isolate down phases. Power was partially restored after overhead was isolated. All power restored to normal as of 13:00. | Nepean | Foreign Interference | Foreign Object
11139 | 2007 | 8 | 24 | 0.056944 |  | 49 | 3 | 4 | Jockvale | 8/4.8kV | 145F3 | Transformer at 5146 Richmond Rd. opened due to Raccoon contact, crew re-fused transformer | Nepean | Foreign Interference | Animal
16810 | 2010 | 8 | 25 | 0.71667 |  | 198 | 3 | 1 | Jockvale | 8/4.8kV | 145F3 | Transfromer #X5003 located at 6515 Richmond Rd opened up, crew could not find cause | Nepean | Unknown/Other | No Apparent Cause
7221 | 2005 | 8 | 26 | 0.57292 |  | 25 | 0 | 1 | Jockvale | 8/4.8kV | 145F3 | Transformer 682 at 5100 Fallowfield Rd was isolated to replace arrester | Nepean | Defective Equipment | Imminent Equipment Failure Detected
19111 | 2011 | 9 | 7 | 0.38333 |  | 86 | 7 | 5 | Jockvale | 8/4.8kV | 145F3 | TE1758 at 16 Peace Way was isolated to level xfmr base. | Nepean | Scheduled Outage | Repair
5788 | 2004 | 9 | 9 | 0.37847 |  | 85 | 1 | 1 | Jockvale | 8/4.8kV | 145F3 | Trees in wires that feeds transformer 2760 on Moodie Dr. | Nepean | Adverse Weather | Wind
9217 | 2006 | 9 | 14 | 0.53681 |  | 222 | 22 | 6 | Jockvale | 8/4.8kV | 145F3 | A broken pole caused by a pole fire on Trail Rd from switch 163. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13239 | 2008 | 9 | 15 | 0.83333 |  | 366 | 43 | 7 | Jockvale | 8/4.8kV | 145F3 | crew isolated section of Jockvale 145F3 overhead circuit on Richmond rd. bet. S755 and S10689 to replace hydro pole hit by MVA. (multi vehicle accident) | Nepean | Foreign Interference | Vehicle
9251 | 2006 | 9 | 19 | 0.68264 |  | 255 | 19 | 50 | JOCKVALE | 8/4.8kV | 145F3 | S113 on Richmond Rd, opened to isolate 8kv line due to vehicle accident breaking pole. RBD required to bracepole. All customers restored at 16:41 except 1 customer, who was later restored at. | Nepean | Foreign Interference | Vehicle
19216 | 2011 | 9 | 20 | 0.70486 |  | 515 | 9 | 1 | Jockvale | 8/4.8kV | 145F3 | Transformer X5015 at 6568 Richmond rd was replaced by on call crew, broken bushing. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4166 | 2003 | 9 | 27 | 0.76806 |  | 99 | 45 | 27 | Jockvale | 8/4.8kV | 145F3 | Burnt off lead at S153 replaced, Steeplechase/Fallowfield | Nepean | Defective Equipment
7443 | 2005 | 10 | 10 | 0.83889 |  | 502 | 8 | 1 | Jockvale | 8/4.8kV | 145f3 | MVA broke hydro pole infront of 4799 Fallowfield. Oncall crew called to replace pole and transformer. | Nepean | Adverse Environment | Corrosion
7485 | 2005 | 10 | 19 | 0.69097 |  | 85 | 57 | 40 | Jockvale | 8/4.8kV | 145F3 | In line fused switch S113 B phase found open, same switch is defective and could not be closed. Crew jumpered out switch. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7522 | 2005 | 10 | 27 | 0.40625 |  | 105 | 10 | 6 | Jockvale DS | 8/4.8kV | 145F3 | 8 Kv O/H on Richmond Rd between S251 & S755 isolated to replace pole. | Nepean | Scheduled Outage | Repair
15317 | 2009 | 10 | 27 | 0.44097 |  | 153 | 26 | 10 | JOCKVALE | 8/4.8kV | 145F3 | Transformer X39637 at 3030 Steeple Hill Cres isolated to allow for pole change | Nepean | Scheduled Outage | Preventive Maintenance
13463 | 2008 | 10 | 28 | 0.93611 |  | 26 | 153 | 352 | Jockvale | 8/4.8kV | 145F3 | 145F3 closed & holding | Nepean | Adverse Weather
9534 | 2006 | 10 | 29 | 0.31181 |  | 136 | 2 | 1 | Jockvale | 8/4.8kV | 145F3 | Transformer #NP000143 located at 3800 Twin Elm isolated due to tree interference | Nepean | Tree Contacts | Inadequate Trimming
15333 | 2009 | 10 | 31 | 0.36944 |  | 509 | 1298 | 153 | Jockvale | 8/4.8kV | 145F3 | S153 & one phase of TEMP121 blew from a tree falling & knocking down primary & neutral conductor on Steeple Hill south of Fallowfield. Oncall crew made required repairs and restored all power. | Nepean | Tree Contacts | Tree Fallen
11670 | 2007 | 11 | 5 | 0.94375 |  | 74 | 1 | 1 | Jockvale | 8/4.8kV | 145F3 | crew replaced a broken cutout on overhead transformer at 5500 Richmond rd. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
13597 | 2008 | 11 | 12 | 0.41667 |  | 306 | 20 | 4 | Jockvale | 8/4.8kV | 145F3 | Transformer TE1761 @ 14 Wallace CRT. was isolated to install new transformer vault, pad and grounding. | Nepean | Scheduled Outage | Construction
9718 | 2006 | 11 | 23 | 0.85764 |  | 55 | 5 | 5 | Jockvale | 8/4.8kV | 145F3 | Transformer #4332 located at 2980 Moodie isolated to determine problem-was a bad connection at the X2 bushing | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6007 | 2004 | 12 | 10 | 0.65972 |  | 135 | 4 | 2 | Jocvale | 8/4.8kV | 145F3 | Replaced connection on the switch and replaced the hot line clamp 2885 Steeple Hill Cres Trnsformer # NP000901 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4593 | 2003 | 12 | 12 | 0.45486 |  | 37 | 1 | 1 | Jockvale | 8/4.8kV | 145F3 | Transformer was opened to make repairs. 1 customer effected in power outage. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
6079 | 2004 | 12 | 19 | 0.97222 |  | 100 | 367 | 220 | Jockvale | 8/4.8kV | 145F3 | Switch 145F3 B phase broke and conductor fell to ground. | Nepean | Defective Equipment
13788 | 2008 | 12 | 22 | 0.32778 |  | 62 | 2 | 2 | Jockvale | 8/4.8kV | 145F3 | Transformer #X40040 located at 6023 Richmond Rd isolated , due to defective line clamp at transformer had to be replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
9879 | 2006 | 12 | 23 | 0.66319 |  | 35 | 4 | 6 | Jockvale | 8/4.8kV | 145F3 | S251 by S755 isolated to make temporary repairs to broken pole. | Nepean | Foreign Interference | Vehicle
9882 | 2006 | 12 | 24 | 0.50278 |  | 166 | 17 | 6 | Jockvale | 8/4.8kV | 145F3 | Broken pole on Richmond Rd near Twin Elm replaced after car accident yesterday. | Nepean | Scheduled Outage | Construction
15563 | 2009 | 12 | 27 | 0.44444 |  | 62 | 27 | 26 | Jockvale | 8/4.8kV | 145F3 | A pole broke on Richmond Rd near Steeple Hill switch S1598 was opened to make repair to the pole. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4665 | 2003 | 12 | 30 | 0.51042 |  | 65 | 32 | 30 | Jockvale | 8/4.8kV | 145F3 | An insulator failed causing two phases to come together rupturing the W&B phase fuses. A patrol was completed, the repairs were made and the power was restored by re-fusing and closing S19. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
19832 | 2012 | 1 | 14 | 0.52222 |  | 110 | 4 | 2 | Jockvale | 8/4.8kV | 145F4 | Transformer #X39971 located at 3009 Moodie Dr opened by crew to make repairs to conductor that was down. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
20057 | 2012 | 2 | 27 | 0.4375 |  | 31 | 1 | 2 | Jockvale | 8/4.8kV | 145F4 | Transformer X39973 at 3151 Moodie Drive isolated to transfer plant to new pole | Nepean | Scheduled Outage | Construction
20061 | 2012 | 2 | 27 | 0.45833 |  | 20 | 1 | 2 | Jockvale | 8/4.8kV | 145F4 | Transformer X39973 at 3151 Moodie Dr. isolated to transfer plant to new pole | Nepean | Scheduled Outage | Construction
20068 | 2012 | 2 | 28 | 0.39583 |  | 20 | 1 | 2 | Jockvale | 8/4.8kV | 145F4 | Isolated transformer X39962 at 2980 Moodie Dr for a service upgrade | Nepean | Scheduled Outage | Construction
20072 | 2012 | 2 | 28 | 0.52083 |  | 80 | 3 | 2 | Jockvale | 8/4.8kV | 145F4 | Isolated transformer X33005 at 3273 Moodie Dr to transfer hydro plant | Nepean | Scheduled Outage | Construction
20127 | 2012 | 3 | 6 | 0.36319 |  | 479 | 16 | 2 | Jockvale | 8/4.8kV | 145F4 | 8Kv Overhead section in front of 3450 Moodie Dr. Was isolated to allow crews to string new conductor | Nepean | Scheduled Outage | Construction
20132 | 2012 | 3 | 6 | 0.36319 |  | 477 | 16 | 2 | Jockvale |  | 145F4 | 2 customer outage to allow contractor to string new conductor on Mooddie Drive | Nepean | Scheduled Outage | Construction
20143 | 2012 | 3 | 7 | 0.34375 |  | 438 | 15 | 2 | Jockvale | 8/4.8kV | 145F4 | A section of O/H line on Moodie was isolated to allow contractor to install new conductor. 2 customers affected. | Nepean | Scheduled Outage
14058 | 2009 | 3 | 15 | 0.58542 |  | 172 | 3 | 1 | Jockvale | 8/4.8kV | 145F4 | Transformer #X39968 located at 3010 Moodie Dr isolated due to defective lightning arrestor | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10150 | 2007 | 3 | 20 | 0.16667 |  | 359 | 138 | 45 | Jockvale | 8/4.8kV | 145F4 | Overhead blue phase conductor failed. Ottawa Fire reports wires down at Moodie & Trail Rd area. Section was isolated by 24/7 at 05:20. 24/7 reports while restoring overhead section on Moodie rd to bankfield S19 blue phase fuse opened causing an outage to customers on Twin Elms Dr.24/7 reports a second problem at S621. P. Barr reports S621 switch has now been replaced O/H section has been repaired. Load restored on Barnsdale & moodie rd at 09:10. At 09:59 P. Barr reports downed conductor has now been repaired at Moodie & Trail RD, and 5 customers power has been restored. | Nepean | Unknown/Other | No Apparent Cause
20203 | 2012 | 3 | 22 | 0.63056 |  | 326 | 2121 | 1359 | Jockvale | 8/4.8kV | 145F4 | At 3087 Moodie a contractors boom made contact with the 145F4 overhead line blue phase line. Circuit was opened to allow emergancy crews to access area. Crews performed switching to isolate area and restore most of the load. | Nepean | Foreign Interference | Vehicle
4985 | 2004 | 4 | 8 | 0.63472 |  | 403 | 54 | 8 | Jockvale | 8/4.8kV | 145F4 | Transformer TE838 replaced after MVA. Transformer had to be replaced. | Nepean | Foreign Interference | Vehicle
6439 | 2005 | 4 | 22 | 0.29861 |  | 58 | 2 | 2 | Jockvale | 8/4.8kV | 145F4 | Tranformer #NP001457 at 4475 Trail Rd, Nepean isolated, not sure of cause | Nepean | Unknown/Other
16036 | 2010 | 5 | 4 | 0.62917 |  | 59 | 1 | 1 | Jockvale | 8/4.8kV | 145F4 | Transformer #X39968 located at 3010 Moodie Dr Nepean opened up due to blown fuse and arrestor | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18094 | 2011 | 5 | 4 | 0.93056 |  | 260 | 26 | 6 | Jockvale | 8/4.8kV | 145F4 | Transformer TP6198 at 44 Merner was isolated to allow crew to repair after a veichile hit it. Jockvale (145F4) ID#18094 | Nepean | Foreign Interference | Vehicle
8236 | 2006 | 5 | 5 | 0.36458 |  | 265 | 9 | 2 | Jockvale | 8/4.8kV | 145F4 | 2 transformers located at Cedarview/Strandherd isolated due to stringing new conductor | Nepean | Scheduled Outage | Construction
8252 | 2006 | 5 | 8 | 0.42014 |  | 286 | 10 | 2 | Jockvale | 8/4.8kV | 145F4 | Isolated the O/H line on Cedarview south of Strandherd to allow clearance for tension string. | Nepean | Scheduled Outage | Preventive Maintenance
8261 | 2006 | 5 | 9 | 0.46389 |  | 232 | 8 | 2 | Jockvale | 8/4.8kV | 145F4 | Transformer located at 2831 Moodie Dr isolated due to bird contact & then the crew found about 3 feet of conductor gone. Crew made repairs then re-energized transformer. | Nepean | Foreign Interference | Bird
12425 | 2008 | 5 | 10 | 0.64444 |  | 140 | 79 | 39 | Jockvale | 8/4.8kV | 145F4 | At transformer 2171 at 44 Chatham Garden elbow has backed off and bushing flashed. 24/7 changed bushing elbow needs work. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8301 | 2006 | 5 | 16 | 0.36944 |  | 373 | 12 | 2 | Jockvale | 8/4.8kV | 145F4 | Single phase O/H line section along Cedarview at Strandherd isolated for clearance to string new line. | Nepean | Scheduled Outage | Construction
8314 | 2006 | 5 | 18 | 0.36111 |  | 190 | 6 | 2 | Jockvale | 8/4.8kV | 145F4 | Mike Gruich had transformers at 3270 Cedarview (trans # NP2524) and at 3231 Cedarview (trans # NP1439) open to do pole changes | Nepean | Scheduled Outage | Preventive Maintenance
6574 | 2005 | 5 | 19 | 0.42222 |  | 44 | 2 | 3 | Jockvale | 8/4.8kV | 145F4 | Refused Transformer # 466 at 3302 Moodie dr caused by a Animal | Ottawa | Foreign Interference | Animal
8347 | 2006 | 5 | 24 | 0.42708 |  | 276 | 18 | 4 | Jockvale | 8/4.8kV | 145F4 | Isolated the O/H line on Cedarveiw south of Strandherd to install new poles. | Nepean | Scheduled Outage | Preventive Maintenance
8355 | 2006 | 5 | 25 | 0.45208 |  | 72 | 224 | 1668 | Jockvale | 8/4.8kV | 145F4 | Crew was stringing new conductor down Cedarview along the S115 single phase runoff and while they were tensioning the new conductor it was slipping through the connectors on the insulators without them being aware. This slipping removed the sag four spans down from there location and the grounded new conductor came in contact with the existing live conductor. | Nepean | Defective Equipment
20578 | 2012 | 5 | 25 | 0.59028 |  | 294 | 2198 | 1039 | Jockvale | 8/4.8kV | 145F4 | Truck contacted and broke pole at 3330 Moodie Dr. Circuit Isolated. 145F4 load was on the 140F3 circuit. Both breakers would not close after sectionalizing, via SCADA. Both circuits had to be sectionalized again and picked up in stages. | Nepean | Foreign Interference | Vehicle
20656 | 2012 | 5 | 29 | 0.69444 |  | 4 | 69 | 1039 | Jockvale | 8/4.8kV | 145F4 | 145F4 breaker opened due to lightning strike under holdoff. | Nepean | Adverse Weather | Lightning
8433 | 2006 | 6 | 6 | 0.40278 |  | 280 | 14 | 3 | Jockvale | 8/4.8kV | 145F4 | Planned outage to string conductor -Cedarview/Strandherd. | Nepean | Scheduled Outage
3552 | 2003 | 6 | 12 | 0.375 |  | 430 | 752 | 105 | Jockvale | 8/4.8kV | 145F4 | Ten transformers in the Houlahan, Tartan and Halley Streets of Barhaven, in Nepean, were isolated to allow for their upgrading to 27kv. Taps were changed and supplied moved to the 27kv circuit. | Nepean | Scheduled Outage | Preventive Maintenance
6737 | 2005 | 6 | 15 | 0.675 |  | 378 | 47 | 20 | Jockvale | 8/4.8kV | 145F4 | Customer reports at 3892 Twin Elms large clap of lightning no power at his location. D. McKay reports trees in wires at RX864. | Ottawa | Adverse Weather | Lightning
8490 | 2006 | 6 | 15 | 0.35208 |  | 238 | 8 | 2 | Jockvale | 8/4.8kV | 145F4 | Isolation of o/h Line on Cedarview Road to tie in new conductor. | Nepean | Scheduled Outage | Construction
12674 | 2008 | 6 | 16 | 0.71042 |  | 251 | 1556 | 1210 | Jockvale | 8/4.8kV | 145F4 | Scada indicates 145F4 opened and locked out, After crew patroled they found primary conductor down on Moodie dr, and Mckenna Casey dr. Crew repaired line & restored power to remaining customers. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
20809 | 2012 | 6 | 19 | 0.75 |  | 120 | 10 | 5 | Jockvale | 8/4.8kV | 145F4 | Transformers X33005, X5498, X5499 were isolated to allow crew to transfer plant to new line. | Nepean | Scheduled Outage | Construction
5381 | 2004 | 6 | 27 | 0.072917 |  | 68 | 11 | 10 | Jockvale | 8/4.8kV | 145F4 | A vehicle knock off transformer TE2385 of it's pedestal at 40 Kenmare in Nepean. | Nepean | Foreign Interference | Vehicle
12775 | 2008 | 7 | 2 | 0.27569 |  | 83 | 1 | 1 | Jockvale | 8/4.8kV | 145F4 | Replaced blown fuse at line switch S29707 feeding transformer X43719 at 3717 Cedarview Rd | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20916 | 2012 | 7 | 3 | 0.75 |  | 135 | 4 | 2 | Jockvale | 8/4.8kV | 145F4 | Isolated transformers X39822 and X39634 at switch S1597 at 3273 Moodie Dr to transfer hydro plant | Nepean | Scheduled Outage | Construction
14692 | 2009 | 7 | 10 | 0.37569 |  | 28 | 7 | 15 | Jockvale | 8/4.8kV | 145F4 | Crew open S1033 to replace a defective switch and arrester on riser pole at the corner of Bren-Maur & Newland on the 145F4. | Nepean | Scheduled Outage | Repair
16696 | 2010 | 8 | 9 | 0.1125 |  | 137 | 99 | 45 | Jockvale | 8/4.8kV | 145F4 | S1538 blue phase fell open due to defective fuse holder, interrupting power to 5 transformers, fuse did not blow. Power was restored in stages from alternate supply. Customers on Beddington & Shiregreen affected. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11031 | 2007 | 8 | 10 | 0.95 |  | 42 | 1 | 1 | Jockvale | 8/4.8kV | 145F4 | Bell guy wire was hit by a vehicle causing it to fly up and flash the 145F4 primary at 3151 Moodie Drive. The 145F4 auto reclosed and transformer 2948 at 3151 fused open, was re-fused by 24/7 crew. | Nepean | Foreign Interference | Vehicle
3915 | 2003 | 8 | 18 | 0.92847 |  | 151 | 5 | 2 | Jockvale | 8/4.8kV | 145F4 | Excessive vegetation around the transformer at 2966 Moodie was probable cause of transformer opening. | Nepean | Tree Contacts | Inadequate Trimming
9054 | 2006 | 8 | 25 | 0.38264 |  | 78 | 10 | 8 | JOCKVALE | 8/4.8kV | 145F4 | Isolation of TE2393 on Armadale to repair leaky bushing. | Nepean | Scheduled Outage
7220 | 2005 | 8 | 26 | 0.68611 |  | 53 | 954 | 1080 | Jockvale | 8/4.8kV | 145F4 | An insulator broke on the same pole as the S1562 cutout and contacted the cutout causing a flash over and the circuit to A/R and open and lockout. Temporary repairs done and all power restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9209 | 2006 | 9 | 13 | 0.41806 |  | 286 | 29 | 6 | Jockvale | 8/4.8kV | 145F4 | TP4172 isolated to allow crew to clean oil. | Nepean | Scheduled Outage | Preventive Maintenance
15106 | 2009 | 9 | 15 | 0.37847 |  | 285 | 133 | 28 | Jockvale | 8/4.8kV | 145F4 | TP6280 at 14 Maravista was isolated to upgrade the transformer to a higher kVA rating | Nepean | Scheduled Outage
11417 | 2007 | 9 | 30 | 0.39028 |  | 103 | 5 | 3 | Jockvale | 8/4.8kV | 145F4 | Transformer #NP000466 located at 3302 Moodie Dr isolated due to bird contact | Nepean | Foreign Interference | Bird
11419 | 2007 | 10 | 1 | 0.39931 |  | 115 | 13 | 7 | Jockvale | 44kV | 145F4 | Transformer #NPTE1081 at 105 isolated to allow for repairs to leaking transformer | Kanata | Scheduled Outage | Repair
11430 | 2007 | 10 | 1 | 0.41389 |  | 58 | 8 | 8 | Jockvale | 8/4.8kV | 145F4 | TE1081 @ 84 Tartan was isolated for replacement. (Leaking transformer) | Nepean | Scheduled Outage | Preventive Maintenance
7455 | 2005 | 10 | 14 | 0.35694 |  | 216 | 7 | 2 | Jockvale | 8/4.8kV | 145F4 | Replaced defective transformer NP3915 at 2861 Moodie Dr | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15324 | 2009 | 10 | 29 | 0.41042 |  | 74 | 41 | 33 | Jockvale | 8/4.8kV | 145F4 | TP6280 at 20 Willwood was isolated from Hydro Sources to replace Ground Grid | Nepean | Scheduled Outage | Repair
4439 | 2003 | 11 | 13 | 0.40625 |  | 91 | 121 | 80 | Jockvale | 8/4.8kV | 145F4 | Hot line clamp burnt off at switch 76 on Cedarview Dr in Barrhaven | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13649 | 2008 | 11 | 21 | 0.40278 |  | 394 | 0 | 8 | Jockvale | 8/4.8kV | 145F4 | Transformer TP6198 @ 46 Merner was isolated for oil remediation. | Nepean | Scheduled Outage | Repair
5916 | 2004 | 11 | 22 | 0.39583 |  | 98 | 3 | 2 | Jockvale | 8/4.8kV | 145F4 | Tree made contact with O/H line at Cedarview at Barnsdale by Aspludh Canada | Nepean | Tree Contacts | Tree Limb Fallen
7662 | 2005 | 11 | 28 | 0.30903 |  | 358 | 48 | 8 | Jockvale | 8/4.8kV | 145F4 | SW163 was opened to make repairs to Pole that was hit and broken by a snowplow on Trail Road. | Nepean | Foreign Interference | Vehicle
11878 | 2007 | 12 | 23 | 0.95833 |  | 46 | 1 | 1 | Jockvale | 8/4.8kV | 145F4 | 2 fuses of S641 at 4378 McKenna Casey blew when 2 phases made conatct during periods of high wind gusts. Phases were spread farther apart to provide better clearance and power was restored. Only the 1 customer, CKOY Radio Station was affected, which ran on generator during the outage. | Nepean | Adverse Weather | Wind
4779 | 2004 | 2 | 11 | 0.42847 |  | 126 | 17 | 8 | Barrhaven | 8/4.8kV | 145F5 | TE1401 isolated to upgrade transformer from 50 KVA to 100 kVA. 8 Customers affected in power outage. | Nepean | Scheduled Outage | Repair
7699 | 2005 | 12 | 7 | 0.37917 |  | 339 | 56 | 10 | Jockvale | 8/4.8kV | 145F5 | TE1134 & S1119 was isolated to allow crews to replace cable section. At 160 Fieldgate Dr. | Nepean | Scheduled Outage | Repair
6504 | 2005 | 5 | 4 | 0.36806 |  | 33 | 4 | 7 | Epwoth | 8/4.8kV | 150F4 | Opened transformer NP001102 at 45 David St to disconnect a service | Nepean | Scheduled Outage | Repair
6505 | 2005 | 5 | 4 | 0.52431 |  | 70 | 8 | 7 | Epworth | 8/4.8kV | 150F4 | Opened transformer NP001102 at 45 David St to install new service | Nepean | Scheduled Outage | Repair
4765 | 2004 | 2 | 5 | 0.27778 |  | 103 | 69 | 40 | Queensway Carleton | 8/4.8kV | 160F1 | Faulted Blue phase cable section between S803B and transformer TE63. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
3282 | 2003 | 3 | 21 | 0.097917 |  | 892 | 269 | 40 | Queensway Carlton | 8/4.8kV | 160F1 | Flooding at transformer TE50 caused fused switch to blow. Cable sections sectionalized and pumping of water required at the TE50. | Nepean | Adverse Environment | Flooding
6356 | 2005 | 4 | 3 | 0.89583 |  | 456 | 232 | 40 | QWC | 8/4.8kV | 160F1 | With the heavy rain, transformer 50 @ 12 Brinton Ave was under water causing the transformer fuse to blow and the fuse at switch S803W to also blow. | Nepean | Adverse Weather | Rain
6393 | 2005 | 4 | 9 | 0.31111 |  | 227 | 116 | 40 | Queensway Carleton | 8/4.8kV | 160F1 | Faulted cable section S803B to TE63. Insulator at the base of TE63 is also possiply defective. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17917 | 2011 | 4 | 13 | 0.40694 |  | 104 | 19 | 11 | Q.C.H | 8/4.8kV | 160F1 | TE63 at 69 Beaumaris was isolated to allow crew to repair faulty secondary service. 11 customers were affected . Q.C.H 160F1 | Nepean | Scheduled Outage
6421 | 2005 | 4 | 18 | 0.47917 |  | 80 | 5 | 4 | Queensway Carleton | 8/4.8kV | 160F1 | Transformer #NP004639 located at 8 Pulford Cres, Nepean, isolated due to tracking on the pole, pole is burnt | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8156 | 2006 | 4 | 18 | 0.39931 |  | 8 | 84 | 629 | Queensway Carleton | 8/4.8kV | 160F1 | 160F1 (QCH) OPENED DUE TO INLINE SWITCHES S9'S DROPPING OPEN ON ONE PHASE AND FLASHING THE OTHER PHASES. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5041 | 2004 | 4 | 22 | 0.375 |  | 175 | 32 | 11 | Queensway Carleton | 8/4.8kV | 160F1 | TE 48 at 100 Queensline Dr 92-112 Queensline Dr out to allow repair to terminations. | Nepean | Scheduled Outage | Preventive Maintenance
17992 | 2011 | 4 | 26 | 0.40764 |  | 34 | 15 | 27 | Q.C.H | 8/4.8kV | 160F1 | Switch S626 @ 29 Firewood was open to allow tree contractor to trim tree branch. 27 Customer were affected. Q.C.H 160F1-R | Nepean | Tree Contacts | Inadequate Trimming
18075 | 2011 | 5 | 1 | 0.41667 |  | 32 | 35 | 66 | quennsway Carleton | 8/4.8kV | 160F1 | At 13 Firwood while crew was removing a limb it caused tS1359 and S626 to blow. Both fuses replaced and power restored. | Nepean | Tree Contacts | Tree Limb Fallen
6355 | 2005 | 5 | 3 | 0.89583 |  | 456 | 232 | 40 | QWC | 8/4.8kV | 160F1 | With heavy rain, transformer 50 @ 12 Brinton Ave was flooded out causing it's fuse to blow. | Nepean | Adverse Weather | Rain
20528 | 2012 | 5 | 16 | 0.40139 |  | 393 | 79 | 12 | QCH | 8/4.8kV | 160F1 | TP5267 at 59 Queensline Dr, was isolated to replace defective transformer and install new base and grounding. | Nepean | Scheduled Outage | Repair
5170 | 2004 | 5 | 18 | 0.29514 |  | 127 | 133 | 63 | Queensway Carleton | 8/4.8kV | 160F1 | Blown lightning arrester found on Bellfield. Switch 1539 re-fused and closed. | Nepean | Adverse Weather | Lightning
8318 | 2006 | 5 | 18 | 0.82569 |  | 117 | 79 | 50 | Queensway Carleton | 8/4.8kV | 160F1 | Crew found Squirrel @ 22 firwood caused transformer fuse to open and went back to laterial fuse on S1539. | Nepean | Foreign Interference | Animal
16097 | 2010 | 5 | 18 | 0.40694 |  | 289 | 34 | 7 | QCH | 8/4.8kV | 160F1 | 160F1 O/H Blue Phase Isolated at Line Taps at X37606 to allow crews to perform tree trimming | Nepean | Scheduled Outage | Preventive Maintenance
20646 | 2012 | 5 | 31 | 0.40972 |  | 295 | 103 | 21 | QCH | 8/4.8kV | 160F1 | At 09:50 transformers TE98 and TE99 on Mohawk was isolated to allow crew replace defective transformer. 21 customers were affected for 295 minutes. Queens Way Carleton (160F1) ID#20646 | Nepean | Scheduled Outage | Repair
20777 | 2012 | 6 | 14 | 0.38403 |  | 497 | 116 | 14 | QCH |  | 160F1 | At 09:13 crews isolated TE98 for transformer replacement. QCH 160F1 ID#20777 | Nepean | Scheduled Outage | Preventive Maintenance
18416 | 2011 | 6 | 15 | 0.375 |  | 120 | 24 | 12 | Bayshore | 8/4.8kV | 160F1 | Trans TE47 at 7 Brintin Ave was isolated in order to replace a defective pedestal | Nepean | Scheduled Outage | Repair
8560 | 2006 | 6 | 19 | 0.79514 |  | 460 | 153 | 20 | Queensway Carleton | 8/4.8kV | 160f1 | S626 on Firwood, Nepean found blown open. Crew patrolled circuit nothing found. Refused and Closed. Severe thunder and lightning storm in effect. | Nepean | Adverse Weather | Lightning
14613 | 2009 | 6 | 25 | 0.38889 |  | 536 | 89 | 10 | QCH | 8/4.8kV | 160F1 | TP5502 at 30 Cinook Cres was isolated under the PCB replacement program. | Nepean | Scheduled Outage | Preventive Maintenance
14614 | 2009 | 6 | 25 | 0.375 |  | 555 | 185 | 20 | Q.C.H. | 8/4.8kV | 160F1 | Isolated and replaced transformer TP5502 at the rear of 33 Aleutian Rd (PCB oil) | Nepean | Scheduled Outage | Preventive Maintenance
16347 | 2010 | 6 | 28 | 0.6875 |  | 45 | 4 | 5 | QCH | 8/4.8kV | 160F1 | Transformer #X37045 located at 5 Bellfield St opened by crew to replace triplex | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14690 | 2009 | 7 | 9 | 0.38611 |  | 609 | 142 | 14 | QCH | 8/4.8kV | 160F1 | TP5518 @ 8 Dixon was isolated by the crew to change transformer to comply with the new PCB level standards. | Nepean | Scheduled Outage | Preventive Maintenance
10911 | 2007 | 7 | 19 | 0.55208 |  | 45 | 4 | 6 | Queensway Carlton |  | 160F1 | Isolated transformer NP1100 at 4 Magwood to repair services | Nepean | Scheduled Outage | Preventive Maintenance
14797 | 2009 | 7 | 21 | 0.38819 |  | 626 | 167 | 16 | QCH | 8/4.8kV | 160F1 | At 09:19 transformer TP5517 was isolated to allow crew to replace PCB transformer. 16 customers were affected. | Nepean | Scheduled Outage | Preventive Maintenance
14813 | 2009 | 7 | 23 | 0.41736 |  | 244 | 24 | 6 | QCH DS | 8/4.8kV | 160F1 | Crew isolated TE109 to replace it as part of PCB replacement program. Nomenclature has been changed NEW TP6837, OLD TE109. | Nepean | Scheduled Outage | Preventive Maintenance
10942 | 2007 | 7 | 24 | 0.38889 |  | 46 | 14 | 18 | QCH | 8/4.8kV | 160F1 | 2 sections of o/h line from S558 & S783 at Richmond rd & Bellefield were transferred to a temporary supply source for clearance for planned pole replacement, | Nepean | Scheduled Outage | Construction
7086 | 2005 | 8 | 8 | 0.54167 |  | 60 | 11 | 20 | Queens Way Carleton | 8/4.8kV | 160F1 | M. Byers reports S1240 switch is defective. Switch was replaced all power restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7089 | 2005 | 8 | 10 | 0.42153 |  | 77 | 13 | 10 | QCH | 8/4.8kV | 160F1 | Transformer TE12 at 46 Aleution Rd in Nepean isolated to replace defective service connection at the tx. | Nepean | Scheduled Outage | Repair
5692 | 2004 | 8 | 18 | 0.44444 |  | 85 | 20 | 14 | Queensway Carleton | 8/4.8kV | 160F1 | TE115 and TE115 out to allow secondary service connection to 14 esquimault. | Nepean | Scheduled Outage | Construction
7251 | 2005 | 8 | 31 | 0.40625 |  | 175 | 90 | 31 | Queensway Carleton | 8/4.8kV | 160F1 | Found blown arrester at 33 Bellfield and vine was tangled thru primary at transformer 1290. Repairs made, refused and closed S557. | Nepean | Defective Equipment
11352 | 2007 | 9 | 20 | 0.58819 |  | 1901 | 63 | 2 | Queens Way Carleton | 8/4.8kV | 160F1 | Defective transformer #NP1262 was replaced by oncall crew @3501 Richmond Rd | Nepean | Defective Equipment | Equipment Deterioration Due to Age
11372 | 2007 | 9 | 24 | 0.47292 |  | 52 | 9 | 10 | QWCH | 8/4.8kV | 160F1 | 1 transformer, feeding 11 customers was opened to allow crew to remove temp straps at the intersection of Bellfield and Desmond. | Nepean | Scheduled Outage
19267 | 2011 | 9 | 27 | 0.41667 |  | 45 | 3 | 4 |  | 8/4.8kV | 160F1 | Trans X36740 at 21 Firwood Cres was isolated in order to replace a switch | Nepean | Scheduled Outage
11437 | 2007 | 10 | 2 | 0.43958 |  | 50 | 8 | 10 | Queensway Carlton | 8/4.8kV | 160F1 | Approx 10 customers on Bellefield @ Richmond rd were affected while switching to restore a run-off from S558 to normal feed. | Nepean | Scheduled Outage | Construction
19350 | 2011 | 10 | 10 | 0.40417 |  | 70 | 13 | 11 |  |  | 160F1 | Transformer X 36738 at 24 Firwood refused | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13379 | 2008 | 10 | 16 | 0.5 |  | 292 | 49 | 10 | QCH | 8/4.8kV | 160F1 | 160F1 blue phase fed from S783 was isolated for contractor to install a sound barrier. | Nepean | Scheduled Outage | Construction
9452 | 2006 | 10 | 17 | 0.75 |  | 120 | 10 | 5 | Queensway Carleton | 8/4.8kV | 160F1 | A connection on the B phase of switch S469 on Richmond Rd came loose, same replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7498 | 2005 | 10 | 21 | 0.71458 |  | 106 | 39 | 30 | QWC | 8/4.8kV | 160F1 | A blown fuse at S557 @ 6 Pulford and a blown arrester at transformer 746 @ 2902 Haven Reid. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15340 | 2009 | 10 | 31 | 0.65625 |  | 187 | 3 | 1 | QCH | 8/4.8kV | 160F1 | Tree branches caused tx switch at O/H tx at 3531 Richmond to open. | Nepean | Tree Contacts | Inadequate Trimming
19646 | 2011 | 11 | 28 | 0.40278 |  | 95 | 16 | 10 | Queensway Carleton | 8/4.8kV | 160F1 | Isolated transformer NPTE0060 at 54 Beaumaris Dr to insall new service | Nepean | Scheduled Outage | Construction
19703 | 2011 | 12 | 8 | 0.46875 |  | 30 | 6 | 13 | QCH | 8/4.8kV | 160F1 | At 11h15 crews isolated TE107 at 3 Mohawk cres to disconnect a bad secondary. QCH (160F1) ID#19703 | Nepean | Scheduled Outage
17450 | 2010 | 12 | 23 | 0.46181 |  | 79 | 11 | 8 | QCH | 8/4.8kV | 160F1 | transformer X36737 @ rear of 9 Firwood was opened to change same and replace broken switch. | Nepean | Scheduled Outage | Repair
17492 | 2011 | 1 | 18 | 0.79931 |  | 66 | 10 | 9 | Queensway Carleton | 8/4.8kV | 160F2 | replaced broken switch and blow arrester at transformer X2391 at the rear of 6 Shadow Court | Nepean | Defective Equipment | Equipment Deterioration Due to Age
3131 | 2003 | 1 | 21 | 0.46667 |  | 45 | 110 | 360 | Queensway Carleton | 8/4.8kV | 160F2 | TE194W phase to TE162W did not seat properly when first closed and flashed while being opened to reclose. Flashed switch caused breaker to trip.When all men clear breaker closed picking up 2/3 of the load. Blown fuses found and replaced at S762 blue and white phase restoring the last of the customers. | Nepean | Unknown/Other | No Apparent Cause
8014 | 2006 | 3 | 13 | 0.93819 |  | 101 | 2 | 1 | Queensway Carleton | 8/4.8kV | 160F2 | QCH 160F2 feeder auto/reclosed 3 times, ground hog contact caused fault and damage in sectionalizer SE11, as well as possible damage to switches F2CA at 160F2 riser pole. Vault VE34 fed from SE11 was interrupted due to fuses blowing in sectionalizer , also 1 fuse feeding sectionalizer opened. | Nepean | Foreign Interference | Animal
6411 | 2005 | 4 | 14 | 0.375 |  | 409 | 89 | 30 | Queens Way Carleton | 8/4.8kV | 160F2 | A. Cooney reports TE50 isolated to replace transformer. TE64 & TE49 were de-energized for 20 mins while alive front transformer was isolated. | Nepean | Scheduled Outage | Repair
14185 | 2009 | 4 | 17 | 0.38889 |  | 171 | 63 | 22 | QCH | 8/4.8kV | 160F2 | Job #361 to allow crew to repair overhead circuit and change PCB contaminated transformer. | Nepean | Scheduled Outage | Repair
14313 | 2009 | 5 | 6 | 0.43056 |  | 224 | 49 | 13 | QCH | 8/4.8kV | 160F2 | transformer TE564 (new TP6743) was isolated for transformer upgrade and raise transformer pad. | Nepean | Scheduled Outage | Construction
5215 | 2004 | 5 | 27 | 0.43333 |  | 218 | 36 | 10 | Queens Way Carleton | 8/4.8kV | 160F2 | Transformer TE264W to replace connection. | Nepean | Scheduled Outage | Repair
12688 | 2008 | 6 | 18 | 0.55694 |  | 184 | 144 | 47 | QCH | 8/4.8kV | 160F2 | A fuse in sectionalizer SE11 on Rockway Cr opened when it was contacted by a groundhog that had burrowed into the switch interrupting 5 txs in the loop to TE409. Cable termination at SE11 to TE339 has been damaged. | Nepean | Foreign Interference | Animal
16326 | 2010 | 6 | 24 | 0.39583 |  | 691 | 115 | 10 | Queensway Carleton |  | 160F2 | TE51 at 6 Hobbs isoalted for a transformer and base replacement. | Nepean | Scheduled Outage
6886 | 2005 | 7 | 7 | 0.47639 |  | 89 | 89 | 60 | Queensway | 8/4.8kV | 160F2 | Cable dig ig for contractor holding CIA agreement on Guthrie St Leslie Park. | Nepean | Human Element | Incorrect Records
14704 | 2009 | 7 | 11 | 0.54306 |  | 134 | 1609 | 1198 | QCH | 8/4.8kV | 160F2 | 160F2 tripped, Breaker would not operate. Closed S9 to tie circuits & 160F1 tripped open. OPEN S9 & 160F1 restored. 24/7 patrolled line, found nothing. Stations called in to investigate 160F2 Breaker. 160F1 off loaded, Closed S9 and customers restored | Nepean | Adverse Weather
14765 | 2009 | 7 | 16 | 0.39236 |  | 630 | 147 | 14 | QCH | 8/4.8kV | 160F2 | TP5566 at 25 Dickson isolated to change out transformer due to PCB change | Nepean | Scheduled Outage | Preventive Maintenance
15010 | 2009 | 8 | 26 | 0.53958 |  | 47 | 6 | 8 | QCH | 8/4.8kV | 160F2 | Transformer TE340 at 90 Meadowbank Dr isolated to allow for pcb sampling | Nepean | Scheduled Outage | Preventive Maintenance
5799 | 2004 | 9 | 10 | 0.44931 |  | 498 | 498 | 60 | Queens way Carleton | 8/4.8kV | 160F2 | To change cable mini pads and base replacement on five transformer in the Leslie Park area. | Nepean | Scheduled Outage | Preventive Maintenance
13317 | 2008 | 10 | 3 | 0.5625 |  | 70 | 16 | 14 | QCH | 8/4.8kV | 160F2 | Transformer #TE6 located at 23 Beaumaris isolated to replace pedestal | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7486 | 2005 | 10 | 19 | 0.80486 |  | 71 | 24 | 20 | QUEENSWAY CARLETON | 8/4.8kV | 160F2 | M.Brown reports leads at S675B opened switch needs to be replaced & trees trimmed. | Nepean | Tree Contacts | Inadequate Trimming
5852 | 2004 | 11 | 4 | 0.00069444 |  | 96 | 64 | 40 | Queensway Carleton | 8/4.8kV | 160F2 | Red phase elbow blown at TE169 in Leslie Park, caused an outage to 3 transformers with approx. 40 customers. Underground cable was abnormal in the area at the time of outage. Cable section between TE201 & TE163 was isolated under CIA#3935. ( No phone number on permit, also holder never surrendered permit overnight.) Norm Legault (permit holder)called at home to surrender permit after home phone number was found. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
13590 | 2008 | 11 | 11 | 0.54514 |  | 90 | 21 | 14 | QCH DS | 8/4.8kV | 160F2 | Transformer #TE6 located at 23 Beaumaris Dr isolated due to replacing a backyard pedestal. | Nepean | Scheduled Outage | Preventive Maintenance
13602 | 2008 | 11 | 13 | 0.49444 |  | 94 | 16 | 10 | Queens way Carleton | 8/4.8kV | 160F2 | Transformer TE29 at 18 Barnes cres. was disconnected at 11:52am to repair defective underground cable at 28 Barnes cres. The power was restored at 13:26 and the systen is back to normal. | Nepean | Scheduled Outage | Repair
5914 | 2004 | 11 | 22 | 0.4375 |  | 538 | 90 | 10 | Queens Way Carleton | 8/4.8kV | 160F2 | Replace transformer TP2935 in Leslie Park. | Nepean | Scheduled Outage | Repair
7667 | 2005 | 11 | 30 | 0.39722 |  | 379 | 63 | 10 | Queens Wat Carleton | 8/4.8kV | 160F2 | Transformer TE161 @ 189 Monterey Dr was isolated for transformer replacement program. | Nepean | Scheduled Outage | Preventive Maintenance
7668 | 2005 | 11 | 30 | 0.40486 |  | 386 | 64 | 10 | queensway Carleton | 8/4.8kV | 160F2 | Transformer TE162 @ 173 Monterey Dr was isolated for transformer replacement program. | Nepean | Scheduled Outage | Preventive Maintenance
7674 | 2005 | 12 | 1 | 0.39097 |  | 397 | 165 | 25 | QCH | 8/4.8kV | 160F2 | Transformers TE163 & TE166 on Monteray in Nepean isolated for transformer replacement. | Nepean | Scheduled Outage | Construction
7677 | 2005 | 12 | 2 | 0.40694 |  | 239 | 100 | 25 | Queensway Carleton | 8/4.8kV | 160F2 | M. MUCLLEAN REPORTS WORK ON XMER REPLACEMENT @ LESLIE PARK COMPLETE ON T164 & 167. POWER IS RESTORED TO ALL CUSTOMERS. | Nepean | Scheduled Outage | Construction
7685 | 2005 | 12 | 5 | 0.4 |  | 364 | 121 | 20 | Queensway Carleton | 8/4.8kV | 160F2 | Replacement of white phase TE165 and TE168 in Leslie Park. | Nepean | Scheduled Outage | Construction
6018 | 2004 | 12 | 11 | 0.40903 |  | 481 | 281 | 40 |  | 8/4.8kV | 160F2 | Isolation of 4 transformers in Leslie Park TP2472, TE202, TP2474 and TP2473 for replacement. | Nepean | Scheduled Outage
6060 | 2004 | 12 | 14 | 0.60139 |  | 33 | 4 | 7 | QUEENSWAY CARLETON | 8/4.8kV | 160F2 | TE218 @ 7 HIGHBRUN ST ISOLATED TO ALLOW CREWS TO MAKE REPAIRS TO SERVICE. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12456 | 2008 | 5 | 21 | 0.28819 |  | 85 | 6 | 4 | NepeanTS | 8/4.8kV | 160F3 | Switch to transformer X40069 at 9 Grangemill Ave was found blown due to a Squirrel contact | Nepean | Foreign Interference | Animal
3688 | 2003 | 7 | 6 | 0.45694 |  | 112 | 11 | 6 | Queens Way Carleton | 8/4.8kV | 160F3 | 24/7 found cut-out blown on transformer . Transformer was refused restoring power to all customers. | Nepean | Unknown/Other | No Apparent Cause
7365 | 2005 | 9 | 22 | 0.99792 |  | 45 | 1 | 1 | Queensway | 8/4.8kV | 160F3 | Blown fuse at Transformer 2348, 3460 Richmond Road due to suspected animal contact | Nepean | Foreign Interference | Animal
13663 | 2008 | 11 | 24 | 0.41875 |  | 66 | 4 | 4 | Q.C.H DS | 8/4.8kV | 160F3 | Transformer X40069 at 8 Dante Ave isolated to allow for repairs to service wires | Nepean | Scheduled Outage | Repair
19684 | 2011 | 12 | 5 | 0.66319 |  | 28 | 2 | 4 |  |  | 160F3 | While replacing the service at 4 Dante Ave. 24/7 broke the buss on transformer X40070. The buss was jumpered from X40070 at 5 Grangemill Ave. to X40069 at 7 Grangemill Ave. Follow-up call was created to have South group make repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19685 | 2011 | 12 | 5 | 0.62153 |  | 88 | 9 | 6 | Queensway Carleton | 8/4.8kV | 160F3 | While replacing the service at 4 Dante Ave. 24/7 broke the buss on transformer X40070. Buss was jumpered from X40070 at 5 Grangemill Ave. to X40069 at 7 Grangemill Ave. Follow-up call was created to have South group make repairs. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4707 | 2004 | 1 | 16 | 0.55069 |  | 680 | 225 | 80 | Queens Way Carleton | 8/4.8kV | 160F4 | P. Barr reports bad cable section between S1018 & TE277. 8 Transformers effected in power outage. While restoring power via 84F6 crew closed into a second fault. 84F6 breaker locked out due to circuit tagged hold off. 750 Customers affected in power outage including Queens Way Carleton Hosp. Auto transfer switch operated at Hospital restoring load on secondary sources. 84F6 closed via scada restoing load. Crews located second fault between TE203 & TE278. 20 Customers will be out of power until cable section between TE203 & TE278 can be repaired. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
3130 | 2003 | 1 | 21 | 0.39931 |  | 97 | 103 | 64 | QueenswayCarleton | 8/4.8kV | 160F4 | S1018 red phase fuse found blown.8 transformers out of power.Cable fault located in the first section S1018 by TE277. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3132 | 2003 | 1 | 22 | 0.46319 |  | 5 | 30 | 360 | Queensway Carleton | 8/4.8kV | 160F4 | On closeing TE194 W to TE162W the switch flahed causing the breaker to trip. | Nepean | Defective Equipment
4814 | 2004 | 2 | 21 | 0.60764 |  | 369 | 43 | 12 | Queensway Carleton | 8/4.8kV | 160F4 | While Rob Cameron was megering the cables between switch 1310 and transformer TE1626 they thought they detected a bad cable so they partailly isolated the cable and went and tried to pick the two transformer from VE64. Apon closing in the gang operated switch they blew the W phase at switch S1338, they refused it and closed the W phase S1338. They rechecked the transformer and found a broken bushing at TE1627. 1310 W phase was refused and picking up transformer TE1626, the TE1627 has to be changed. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12072 | 2008 | 2 | 22 | 0.38194 |  | 35 | 6 | 11 | Queensway Carleton | 8/4.8kV | 160F4 | Isolated transformer TE1910 @ 71 Gladecrest for the crew to retighten secondary bushing. | Nepean | Scheduled Outage | Preventive Maintenance
15738 | 2010 | 2 | 23 | 0.47708 |  | 167 | 36 | 13 | QCH | 8/4.8kV | 160F4 | Transformer TE102 @ 35 Chinook & TE113 @ Okanagan was isolated to allow the crew to ID the circuit. | Nepean | Scheduled Outage | Construction
12107 | 2008 | 3 | 6 | 0.41667 |  | 70 | 22 | 19 | QCH | 8/4.8kV | 160F4 | TP2319 was isolated for transformer replacement at 75 Graham Creek, Nepean. | Nepean | Scheduled Outage
4879 | 2004 | 3 | 11 | 0.55556 |  | 75 | 16 | 13 | Queensway Carleton | 8/4.8kV | 160F4 | Transformer TE1627 at 142 Valley Stream interrupted to install temporary service. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15803 | 2010 | 3 | 15 | 0.46458 |  | 178 | 3 | 1 | QCH | 8/4.8kV | 160F4 | Leaking Tx TE821 @ 2490 Baseline was isolated & replaced. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4913 | 2004 | 3 | 17 | 0.54167 |  | 50 | 11 | 13 | Queensway Carleton | 8/4.8kV | 160F4 | TE 1627 at 142 Valley Stream isolated to replace primary cable. Al Cooney. | Nepean | Scheduled Outage | Repair
15885 | 2010 | 4 | 2 | 0.34931 |  | 622 | 10 | 1 | QCH | 8/4.8kV | 160F4 | TE821 @ 2946 Baseline Rd was isolated to allow crews to do oil leak remendiation. | Nepean | Adverse Environment | Corrosion
8110 | 2006 | 4 | 5 | 0.51389 |  | 200 | 10 | 3 | Queensway Carleton | 8/4.8kV | 160F4 | Isolated Pedestal at the rear of 62 Aleutian to repair buss bar | Nepean | Defective Equipment | Equipment Deterioration Due to Age
3369 | 2003 | 4 | 23 | 0.44444 |  | 14 | 5 | 20 | QueensWay Carleton | 8/4.8kV | 160F4 | TE1669,TE1670 Isolated due to pole fire at S1338. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
8244 | 2006 | 5 | 6 | 0.5125 |  | 12 | 4 | 20 | Queensway Carleton | 8/4.8kV | 160F4 | The transformer switch at TP2462 @ 20 Trimble was opened because somebody dug into cable with an augar and resveice a shock. TP2463 was also affected @ 13 Trimble. It turn out to be secondary service. | Nepean | Foreign Interference | Dig-in
8342 | 2006 | 5 | 24 | 0.375 |  | 310 | 181 | 35 | Queensway Carleton | 8/4.8kV | 160F4 | An 8 Kv vault at VE65 @ 91 Valleystream Dr was isolated to allow the contractor to clean and torque the connections and service the disconnects. | Nepean | Scheduled Outage | Preventive Maintenance
18216 | 2011 | 5 | 25 | 0.24097 |  | 198 | 66 | 20 | QCW | 8/4.8kV | 160F4 | A broken W phase switch at S1458 @ 52 GLADECREST CRT | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12507 | 2008 | 5 | 31 | 0.44931 |  | 91 | 12 | 8 | QCH | 8/4.8kV | 160F4 | White phase cable burnt clear at S1338 on Baseline at Sandcastle causing outage to TE1669 and white phase to VE64. Circuit backfed and power restored at 12:18. 8 customers affected. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12557 | 2008 | 6 | 6 | 0.40556 |  | 36 | 7 | 12 | Queensway Carleton | 8/4.8kV | 160F4 | Transformer TE1669 & TE1670 in Brookhaven Court were isolated to make repairs to the cable and switch. | Nepean | Scheduled Outage | Repair
5327 | 2004 | 6 | 18 | 0.38194 |  | 4 | 3 | 40 | Queensway Carleton | 8/4.8kV | 160F4 | Interruption required for switching on live front transformers. | Nepean | Scheduled Outage | Construction
5328 | 2004 | 6 | 18 | 0.38125 |  | 136 | 27 | 12 | Queensway Carleton | 8/4.8kV | 160F4 | TE206 was out of service for cable locate work around transformer. This is part of the work for cable replacement in Leslie Park. | Nepean | Scheduled Outage | Construction
20802 | 2012 | 6 | 19 | 0.20486 |  | 580 | 926 | 230 | QCH | 8/4.8kV | 160F4 | W phase conductor came apart at S1243. Switching performed to restore some customers, isolation then expanded to permit repair of conductor & S1243. Gladecrest / Monterrey area. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20819 | 2012 | 6 | 20 | 0.40556 |  | 188 | 144 | 46 | QCH | 8/4.8kV | 160F4 | Hydro Ottawa crews isolated VE65N at 91 Valley Stream to allow Carleton Elelctric to perform routine vault maintenance. | Nepean | Scheduled Outage | Preventive Maintenance
12725 | 2008 | 6 | 25 | 0.48889 |  | 5 | 1 | 12 | QCH | 8/4.8kV | 160F4 | 2 transformer Brookhaven Court was isolated to allow crews to reconnect red phase in VE64 on Sandcastle after completing a cable replacement project | Nepean | Scheduled Outage | Construction
5392 | 2004 | 6 | 29 | 0.39306 |  | 160 | 83 | 31 | Queens Way Carleton | 8/4.8kV | 160F4 | transformers TE420,421,473 & 206 isolated to allow crews to relocate cable & repair cables in Leslie Park. 40 Customers effected in power outage. | Nepean | Scheduled Outage | Construction
5393 | 2004 | 6 | 29 | 0.40347 |  | 349 | 68 | 30 | Queensway Carleton | 8/4.8kV | 160F4 | R. Blair reports red phase cable section isolated from S1018 to TE278. To include TE277. 20 Customers effected in power outage due to live front transformers. 10 Customers effected for 5-6 hours to relocate cables and transformers in Leslie Park. | Nepean | Scheduled Outage | Construction
10767 | 2007 | 7 | 1 | 0.0027778 |  | 5 | 0 | 5 | Queensway | 8/4.8kV | 160F4 | Transformer TE72 was opened to disconnect secondary service at 15 Cowichan Way. | Nepean | Unknown/Other
14748 | 2009 | 7 | 14 | 0.37778 |  | 528 | 88 | 10 | QCH | 8/4.8kV | 160F4 | transformer TP5567 @ 7 Kitmat was isolated to change transformer as part of PCB replacement program. | Nepean | Scheduled Outage | Preventive Maintenance
14861 | 2009 | 7 | 28 | 0.42778 |  | 229 | 34 | 9 | QWC | 8/4.8kV | 160F4 | TE235 at 17 Sioux Cres. Was isolated to install 500mcm secondary to BUS bar | Nepean | Scheduled Outage
16583 | 2010 | 7 | 29 | 0.40208 |  | 133 | 18 | 8 | QCH | 8/4.8kV | 160F4 | TP7320 at 24 Kitimat was isolated to allow crew to change elbows and inserts. | Nepean | Scheduled Outage
7090 | 2005 | 8 | 10 | 0.44028 |  | 50 | 8 | 10 | QCH | 8/4.8kV | 160F4 | Transformer TE12 at 46 Aleution Rd isolated to replace defective inserts. | Nepean | Scheduled Outage | Repair
5695 | 2004 | 8 | 18 | 0.40417 |  | 147 | 25 | 20 | Queensway | 8/4.8kV | 160F4 | Bad underground to 37 Oakanogan. TE271 and TE346 out for switching 4 mins. Due too live front transformer at TE113. | Nepean | Scheduled Outage | Repair
5751 | 2004 | 8 | 31 | 0.38542 |  | 482 | 120 | 15 | Queensway Carleton | 8/4.8kV | 160F4 | Transformer TE263 & TE264 in Leslie Park isolated for replacement. | Nepean | Scheduled Outage | Preventive Maintenance
5786 | 2004 | 9 | 8 | 0.44444 |  | 36 | 12 | 20 | Queensway Carleton | 8/4.8kV | 160F4 | R. Blair reports TP2466 isolated to allow crew to replace inserts & elbows. Approx 20 customers affected in power outage. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
4058 | 2003 | 9 | 12 | 0.45486 |  | 195 | 102 | 48 | Queensway Carlton | 8/4.8kV | 160F4 | Transfromer TE421 on Costello isolated for installation of new service, TE420 required O/S in the morning to isolate 421. | Nepean | Scheduled Outage | Construction
11358 | 2007 | 9 | 21 | 0.67361 |  | 95 | 5 | 3 | Queens Way Carleton | 8/4.8kV | 160F4 | On-Call crew reports new connection in pedestal. | Nepean | Defective Equipment
9574 | 2006 | 11 | 1 | 0.39861 |  | 6 | 1 | 10 | Queensway Carleton | 8/4.8kV | 160F4 | TE235 off load for switching out live front TE236 for replacement. | Nepean | Scheduled Outage | Preventive Maintenance
9575 | 2006 | 11 | 1 | 0.39861 |  | 432 | 72 | 10 | Queensway Carleton | 8/4.8kV | 160F4 | TE236 transformer and base replaced at 9 Souix Cres new # TP4252 | Nepean | Scheduled Outage | Preventive Maintenance
5928 | 2004 | 11 | 26 | 0.375 |  | 360 | 107 | 18 | Queens Way Carleton | 8/4.8kV | 160F4 | Transformer TE450 isolated to disconnect secondary services to allow contractor to install new meters. | Nepean | Scheduled Outage | Construction
5932 | 2004 | 11 | 26 | 0.39514 |  | 304 | 61 | 12 | Queensway carleton | 8/4.8kV | 160F4 | TE262 isolated to allow crews to replace transformer. | Nepean | Scheduled Outage
5952 | 2004 | 11 | 29 | 0.35417 |  | 600 | 110 | 11 | QCH |  | 160F4 | 11 customers out of xfmr TE421 on Costello (44 to 52 & 54 to 64) off for meter conversion. | Nepean | Scheduled Outage | Construction
5953 | 2004 | 11 | 30 | 0.36875 |  | 425 | 170 | 24 | Queens Way carlton | 8/4.8kV | 160F4 | Transformers 420,421 & 206 isolated for replacement. | Nepean | Scheduled Outage | Construction
5963 | 2004 | 12 | 2 | 0.43264 |  | 249 | 125 | 30 |  | 8/4.8kV | 160F4 | Scheduled outage for transformer mtce. | Nepean | Scheduled Outage
5994 | 2004 | 12 | 8 | 0.37569 |  | 490 | 368 | 45 | QWC | 8/4.8kV | 160F4 | Replacing 3 transformers in the Leslie Park area. | Nepean | Scheduled Outage | Preventive Maintenance
6000 | 2004 | 12 | 9 | 0.38889 |  | 385 | 481 | 75 | Queensway | 8/4.8kV | 160F4 | TE206, 208,209 out for new cable terminations. TE206 replace with new TP2461. Leslie Park. | Nepean | Scheduled Outage | Construction
13738 | 2008 | 12 | 11 | 0.46875 |  | 430 | 136 | 19 | QWC | 8/4.8kV | 160F4 | TE1630 at 156 Valley Stream was isolated to allow crews to replace leaky transformer and base | Nepean | Scheduled Outage
6056 | 2004 | 12 | 13 | 0.42292 |  | 293 | 98 | 20 |  | 8/4.8kV | 160F4 | Scheduled outage to 2 transformers TP2463 and TP2462 in Leslie Park. | Nepean | Scheduled Outage
6069 | 2004 | 12 | 16 | 0.40833 |  | 317 | 132 | 25 | Queensway Carlton | 8/4.8kV | 160F4 | Planned outage to txs 201,202 & 163 in the Leslie Park area for tx replacement. | Nepean | Scheduled Outage | Preventive Maintenance
13890 | 2009 | 1 | 23 | 0.39097 |  | 111 | 11 | 6 | Woodroffe DS | 8/4.8kV | 170F1 | Transformer X22473 at 96 Lisgar isolated to allow for pole replacement - PC10A#3504 issued @ 9:23 by Peter Barr, PC10A#3504 surrendered at 11:42 | Nepean | Scheduled Outage | Repair
13929 | 2009 | 2 | 3 | 0.60069 |  | 40 | 5 | 8 | Woodroffe DS | 8/4.8kV | 170F1 | Replaced blown fuse on transformer X4173 at the rear of 28 Sherry Lane (caused by a squirrel contact) | Nepean | Foreign Interference | Animal
12022 | 2008 | 2 | 8 | 0.46944 |  | 27 | 5 | 12 | MANORDALE DS | 8/4.8kV | 170F1 | Transformer #TE243 at 35 Aurora isolated to allow for repairs | Ottawa | Scheduled Outage | Repair
13957 | 2009 | 2 | 11 | 0.61806 |  | 10 | 0 | 2 | Woodroffe | 8/4.8kV | 170F1 | Transformer #TE58 located at 11 Majestic Dr isolated to see if ground had stopped smoking | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17674 | 2011 | 3 | 5 | 0.78542 |  | 615 | 212 | 45 | Woodroffe | 8/4.8kV | 170F1 | At 18:51 Blue phase fuse at S776 on the 170F1 blew causing an outage to 45 customers. Crew investigated and found TE229 full of water. Crews restored power to the 4 other transformers and proceed to pump out TE229 and then repair it. Woodroffe (170F1) ID# 17674 | Nepean | Adverse Weather | Rain
6259 | 2005 | 3 | 10 | 0.5625 |  | 75 | 10 | 8 | Woodroffe |  | 170F1 | Interrruption to Transformer NP0128 at the rear of 77-75 Majestic to replace the triplex service. | Nepean | Scheduled Outage | Emergency Services Request
17697 | 2011 | 3 | 10 | 0.78472 |  | 297 | 62 | 38 | Woodroffe | 8/4.8kV | 170F1 | Transformer TE329 was isolated to allow crew to pump out flooded transformer. 2 other transformers were interrupted momentarily to allow crew to isolate live front transformer. | Nepean | Adverse Environment | Flooding
20332 | 2012 | 4 | 16 | 0.375 |  | 80 | 9 | 7 | Woodroffe | 8/4.8kV | 170F1 | Trans X36058 at 8 Donna St was isolated in order to replace a defective secondary service | Nepean | Defective Equipment | Equipment Deterioration Due to Age
20376 | 2012 | 4 | 24 | 0.39583 |  | 41 | 5 | 7 | Woodroffe DS | 8/4.8kV | 170F1 | Isolated transformer X32386 at 31 Howden Ave to disconnect defective secondary underground service feeding 29 Howden | Nepean | Scheduled Outage | Emergency Services Request
20377 | 2012 | 4 | 24 | 0.47222 |  | 30 | 4 | 7 | Woodroffe DS | 8/4.8kV | 170F1 | Isolated transformer X32386 at 31 Howden Ave to reconnect Underground secondary service | Nepean | Scheduled Outage | Emergency Services Request
10323 | 2007 | 4 | 25 | 0.39306 |  | 304 | 41 | 6 | WOODROFFE | 8/4.8kV | 170F1 | Te 200 on Majestic was isolated to allow crew to excavate around primary cable. Planned outage. | Nepean | Scheduled Outage | Construction
10341 | 2007 | 4 | 29 | 0.71875 |  | 65 | 4 | 4 | Woodroffe | 8/4.8kV | 170F1 | While replacing secondary connections at 10 Sullivan, found & replaced defective arrestor, primary insulator & hot line clamp at Tx1025. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12373 | 2008 | 5 | 1 | 0.88472 |  | 345 | 2705 | 2194 | Woodroffe | 8/4.8kV | 170F1 | Circuits 170F1 and 87F7 interupted due to a pole fire on Norice St in Nepean. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10352 | 2007 | 5 | 2 | 0.375 |  | 50 | 6 | 7 | Woodroffe | 8/4.8kV | 170F1 | Transformer NP1091 at 51 Laird St was isolated to replace broken insulator | Nepean | Scheduled Outage | Repair
14307 | 2009 | 5 | 5 | 0.44097 |  | 128 | 21 | 10 | WOODROFFE | 8/4.8kV | 170F1 | transformer at 35 Donna St. isolated to allow for pcb change | Nepean | Scheduled Outage | Preventive Maintenance
5204 | 2004 | 5 | 24 | 0.94444 |  | 50 | 12 | 14 | Woodroffe DS | 8/4.8kV | 170F1 | Crew opened transformer at rear of 45 Sherry lane to renew bad connections at pole. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
20668 | 2012 | 6 | 2 | 0.0034722 |  | 151 | 3342 | 1328 | Woodroffe | 8/4.8kV | 170F1 | 170F1 tripped for no apparent reason. Relay failure caused delays in restoring, On Call Stations was required. | Nepean | Unknown/Other | No Apparent Cause
12571 | 2008 | 6 | 7 | 0.53403 |  | 111 | 11 | 6 | Woodroffe | 8/4.8kV | 170F1 | Saggy secondary conductor made contact with tree, which caused fuse on transformer X36062 at 25 Brook Lane to blow. Crew resagged secondary conductor & restored all power to affected customers. | Nepean | Adverse Weather | Wind
10636 | 2007 | 6 | 15 | 0.45278 |  | 8 | 1 | 8 | Woodroffe | 8/4.8kV | 170F1 | Transformer #NP003866 located at 81 Meadowlands Dr isolated to allow for working clearance | Nepean | Scheduled Outage | Construction
8580 | 2006 | 6 | 22 | 0.39097 |  | 17 | 3 | 9 | Woodroffe | 8/4.8kV | 170F1 | TE195 at 15 Matestice isolated to replace doors. Doors didn't fit, will replace transformer noxt week. | Nepean | Scheduled Outage | Repair
6817 | 2005 | 6 | 27 | 0.52153 |  | 139 | 19 | 8 | Woodroffe | 8/4.8kV | 170F1 | Isolated Transformer #1495 at 26 Millford to replace leaking Transformer | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12791 | 2008 | 7 | 4 | 0.47917 |  | 105 | 14 | 8 | Woodroffe | 8/4.8kV | 170F1 | Transformer at 163 Oakridge isolated to replace a defective open wire service. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8729 | 2006 | 7 | 15 | 0.13958 |  | 74 | 92 | 75 | Woodroffe DS | 8/4.8kV | 170F1 | 170F1 breaker auto reclosed. Found S793 blown and S412 (west side phase) blown. Refused and closed. Patrolled line, and all power restored to Skipton, Kirkstall, and Headingly in Manordale. No cause found. | Nepean | Unknown/Other
8734 | 2006 | 7 | 15 | 0.64444 |  | 79 | 99 | 75 | Woodroffe | 8/4.8kV | 170F1 | A broken switch at 412 R phase @ 56 Knoxdale. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
6976 | 2005 | 7 | 17 | 0.78125 |  | 465 | 98 | 20 | Woodroffe | 8/4.8kV | 170F1 | Lightning struck the transformer secondary O/H bet two transformer at 17 Gary St causing the connection to come apart. | Nepean | Adverse Weather | Lightning
18727 | 2011 | 7 | 17 | 0.83333 |  | 1455 | 6669 | 275 | Woodroffe | 8/4.8kV | 170F1 | Switches 412 and 413 closed after tree branches removed on Corolla and Kelvin Cres in Manordale. 170F1 cct. | Nepean | Tree Contacts
10915 | 2007 | 7 | 19 | 0.88264 |  | 44 | 6 | 8 | Woodroffe | 8/4.8kV | 170F1 | Transformer #NP846 located at 14 Roundhay isolated due to possible animal contact | Nepean | Foreign Interference | Animal
14864 | 2009 | 7 | 28 | 0.40833 |  | 107 | 45 | 25 | Woodroffe | 8/4.8kV | 170F1 | S264 at Howden & Sullivan fell open interrupting power to 25 customers on Howden Ave. Defective switch was replaced & power restored. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
18863 | 2011 | 7 | 30 | 0.92569 |  | 102 | 26 | 15 | Woodroffe | 8/4.8kV | 170F1 | Animal contact caused transformer X4062 cut out to blow. Woodroffe (170F1) ID#18863 | Nepean | Foreign Interference | Animal
9060 | 2006 | 8 | 25 | 0.86319 |  | 112 | 21 | 11 | Woodroffe DS | 8/4.8kV | 170F1 | Transformer switch NP002013 at 11 Corola St opened due to contact with a Raccoon also fuse at switch also fuse on line switch 334 was found blown | Nepean | Foreign Interference | Animal
5745 | 2004 | 8 | 29 | 0.64167 |  | 86 | 19 | 13 | Woodroffe | 8/4.8kV | 170F1 | Heavy rain and Lightning in effect. 2 tx fuses and runoff sw S1120 all found open, circuit patrolled, all apeared fine, sws refused and closed. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19316 | 2011 | 10 | 3 | 0.82708 |  | 62 | 7 | 7 | Woodroffe DS | 8/4.8kV | 170F1 | Transformer X32386 at 31 Howden Ave. Isolated to make repairs - changed broken cut out arrester | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9628 | 2006 | 11 | 9 | 0.89236 |  | 55 | 2 | 2 | Woodroffe DS | 8/4.8kV | 170F1 | Transformer located at 68 Knoxdale isolated to replace LLP | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5874 | 2004 | 11 | 10 | 0.44722 |  | 14 | 14 | 60 |  | 8/4.8kV | 170f1 | Switch burning up. 24/7 replaced switch. | Nepean | Defective Equipment
7589 | 2005 | 11 | 10 | 0.083333 |  | 230 | 19 | 5 | Woodroffe D.S. | 8/4.8kV | 170F1 | Crew replaced defective hot line clamp that caused transformer to open at 20 Carola | Nepean | Defective Equipment | Imminent Equipment Failure Detected
19579 | 2011 | 11 | 15 | 0.39722 |  | 398 | 73 | 11 | Woodroffe | 8/4.8kV | 170F1 | At 09:32 crews isolated TE329 at 9 Charing to replace the transformer. 11 customers affected. Woodroffe 170F1 ID#19579 | Nepean | Scheduled Outage
11777 | 2007 | 11 | 27 | 0.58333 |  | 190 | 6 | 2 | Woodroffe D. S. | 8/4.8kV | 170F1 | crew isolated Transformer TE1727 @ Woodroffe and Medhurst to replace transformer. | Nepean | Scheduled Outage | Repair
19723 | 2011 | 12 | 15 | 0.3375 |  | 84 | 8 | 6 | Woodroffe DS | 8/4.8kV | 170F1 | Replaced broken switch feeding transformer X32390 at 14 Sullivan Ave | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11862 | 2007 | 12 | 19 | 0.87778 |  | 156 | 21 | 8 | Woodroffe | 8/4.8kV | 170F1 | Transformer TP1688 at 162 Craig Henry was hit & damaged by a snow plow and had to replaced. | Nepean | Foreign Interference | Vehicle
4699 | 2004 | 1 | 15 | 0.13056 |  | 57 | 208 | 235 | Woodroffe | 8/4.8kV | 170F1 & 170F3 | Woodroffe 170F1 & F3 load interupted due to low voltage, load transferred to Merivale 72F1 & F4. 22M26 one phase came down at greenbelt along West Hunt Club. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8399 | 2006 | 6 | 1 | 0.39583 |  | 118 | 28 | 14 | Woodroffe | 8/4.8kV | 170F2 | Isolate TE2185 @ 138 Woodfield to replace leaking transformer. | Nepean | Scheduled Outage | Repair
8480 | 2006 | 6 | 13 | 0.375 |  | 90 | 18 | 12 | Woodroffe | 8/4.8kV | 170F2 | TP 2923 at Woodfield and Strahearn isolated again to completed comtaminated soil clean up. | Nepean | Scheduled Outage | Repair
8823 | 2006 | 7 | 25 | 0.34792 |  | 21 | 2 | 6 | Woodroffe | 8/4.8kV | 170F2 | Switch to transformer NP5049 at 15 Whitehill was found blown due to an animal contact (Squirrel) | Nepean | Foreign Interference | Animal
11381 | 2007 | 9 | 25 | 0.42361 |  | 35 | 3 | 5 | Woodroffe DS | 8/4.8kV | 170F2 | Isolated transformer TE397 at 5 Parkglen Court to connect new service for the City of Ottawa park | Nepean | Scheduled Outage | Construction
10136 | 2007 | 3 | 14 | 0.83819 |  | 52 | 8 | 9 | Woodroffe | 8/4.8kV | 170F3 | Switch S1344 was arcing and had to be opened due to a pole fire interrupting transformer TE1679. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18699 | 2011 | 7 | 17 | 0.91458 |  | 698 | 931 | 80 | Woodroffe | 8/4.8kV | 170F3 | Tree on conductors during the wind storm caused S503 fuses to blow. Crews isolated and removed tree. | Nepean | Adverse Weather | Wind
9071 | 2006 | 8 | 27 | 0.44306 |  | 88 | 6 | 4 | Woodroffe DS | 8/4.8kV | 170F3 | Crew found S704W in Cheryl Dr area feeding TE16, TE17 open due to Squirrel contact. Caused damage to switch. Crew isolated S704W and made repairs. | Nepean | Foreign Interference | Animal
9164 | 2006 | 9 | 8 | 0.76875 |  | 136 | 1924 | 849 | WOODROFFE | 8/4.8kV | 170F3 | 170F3 Breaker tripped due to severe storm. No SCADA control. Breaker was closed manually. | Nepean | Adverse Weather | Wind
19282 | 2011 | 9 | 28 | 0.29375 |  | 79 | 40 | 30 | Woodroffe | 8/4.8kV | 170F3 | At 07:03 a defective switch S1345 caused and outage to two transformers. Crews made repair and restored power. Woodroffe 170F3 ID#19282 | Nepean | Defective Equipment
7554 | 2005 | 11 | 2 | 0.39722 |  | 420 | 70 | 10 | Woodroffe | 8/4.8kV | 170F3 | TE2980 was isolated to all crews to change leaking transformer. | Ottawa | Scheduled Outage | Preventive Maintenance
4397 | 2003 | 11 | 5 | 0.38542 |  | 223 | 4 | 1 | Woodroffe D.S. | 8/4.8kV | 170F3 | Nepean transformer NP003675 was opened at 3 Vaan dr to replace the pole. | Ottawa | Defective Equipment | Construction
7586 | 2005 | 11 | 9 | 0.45278 |  | 331 | 6 | 1 | WOODROFFE | 8/4.8kV | 170F3 | O/h Line isolation required at 1751 Woodroffe Ave. to change defective customer owned pole (full of woodpecker holes). 1 customer affected. | Nepean | Defective Equipment
17273 | 2010 | 11 | 15 | 0.3625 |  | 50 | 5 | 6 | Woodroffe QT | 8/4.8kV | 170F3 | Replaced blown fuse at transformer X36376 at 16 Bie St (Squirrel contact) | Nepean | Foreign Interference | Animal
4698 | 2004 | 1 | 15 | 0.12569 |  | 1 | 9 | 560 | Woodroffe | 8/4.8kV | 170F4 | Woodroffe 170F4 load interupted due to low voltage, load transferred to Merivale 72F1. 22M26 one phase came down at greenbelt along West Hunt Club. | Nepean | Defective Equipment
11945 | 2008 | 1 | 17 | 0.38542 |  | 134 | 22 | 10 | Woodroffe | 8/4.8kV | 170F4 | TE1663 at 12 Kedgewick was isolated for replacement. | Nepean | Scheduled Outage | Preventive Maintenance
12001 | 2008 | 2 | 1 | 0.38542 |  | 437 | 73 | 10 | Woodroffe | 8/4.8kV | 170F4 | TP5536 at 12 Kedgewick isolated to clean up oil contaminated soil & install new transformer base. | Nepean | Scheduled Outage
12041 | 2008 | 2 | 13 | 0.98611 |  | 263 | 18 | 4 | Woodroffe | 8/4.8kV | 170F4 | Transformer TE736 at 194 Woodfield had to be replaced due to being knocked off its pad by a snowplow. 4 blocks of 6 units each of the Carleton Condominium Corporation on Woodfield were interrupted. | Nepean | Foreign Interference | Vehicle
10051 | 2007 | 2 | 22 | 0.58333 |  | 10 | 10 | 60 | Woodroffe | 8/4.8kV | 170F4 | S987 white phase fuse opened after loop was restored to normal. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6514 | 2005 | 5 | 5 | 0.42014 |  | 110 | 26 | 14 | Woodroffe | 8/4.8kV | 170F4 | Transformer #NPTE0767 at 38 Nestow Dr isolated to identify a service & locate a fault. | Nepean | Scheduled Outage | Repair
10386 | 2007 | 5 | 8 | 0.39236 |  | 211 | 11 | 3 | Woodroffe | 8/4.8kV | 170F4 | Robin Blair isolated TRF 3719 @ 45 Meadowlands for a pole change | Nepean | Scheduled Outage | Preventive Maintenance
10395 | 2007 | 5 | 9 | 0.42708 |  | 155 | 28 | 11 | Woodroffe | 8/4.8kV | 170F4 | Greg MacMillan isolated TRF. # NP3719 @ 34 Harris pl & TRF. # NP3870 @ 40 David to transfer hydro plant to new poles | Nepean | Scheduled Outage | Preventive Maintenance
3540 | 2003 | 6 | 8 | 0.89931 |  | 460 | 77 | 10 | Woodroffe | 8/4.8kV | 170F4 | Defective transformer TE675 at 15 Fox Meadow. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6816 | 2005 | 6 | 27 | 0.44167 |  | 26 | 3 | 7 | Rideau Heights | 8/4.8kV | 180 F4 | Isolated Transformer #512 at 9 Ashdale to disconnect customer | Nepean | Scheduled Outage | Preventive Maintenance
5386 | 2004 | 6 | 27 | 0.52153 |  | 1 | 0 | 1 | TO | 13.2kV | 1801 | While switching to restore 1801 cable to normal, VT391 @ 525 Coventry rd ( TD Waterhouse ) was dumped off momentarily. A switching error was made earlier while restoring the vaults at St Laurent shopping center leaving a switch open that was a check closed item. The switch left open @ VT791 was identified & the normal open point at VT391 restored without further incident. | Ottawa | Human Element | Switching Errors
11486 | 2007 | 10 | 9 | 0.58333 |  | 90 | 2 | 1 | Overbrook | 13.2kV | 1801 | VT74D at 1200 St Laurent isolated for emergancy transformer replacement, performed by Steve Currie at Carelton Electric | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12116 | 2008 | 3 | 9 | 0.36458 |  | 5 | 0 | 1 | Overbrook | 13.2kV | 1802 | Customer at 525 Terminal ave called in reporting all-out from VT1443 supply. Due to history of problems, 24/7 isolated VT1443 to inspect incoming cables & switches. Found blown R phase fuse, cables & switches appear OK. Customer advised they will require HV electrician to inspect & repair their equip. Customer on generator supply, will arrange for repair in near future. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19203 | 2011 | 9 | 19 | 0.51528 |  | 363 | 62 | 75 | Overbrook TS | 13.2kV | 1802 | SC5599-CB3 tripped due to contractors fish tape making contact with transformer bus at VT102 at 1525 Alta Vista. Overbrook (1802) ID# 19203 | Ottawa | Foreign Interference | Foreign Object
17070 | 2010 | 10 | 7 | 0.15 |  | 59 | 1 | 1 | Overbrook | 13.2kV | 1802 | SC1329 at Alta Vista and Industrial Ave switch gear a flashed inside. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17073 | 2010 | 10 | 7 | 0.21389 |  | 16 | 12 | 45 | Overbrook | 13.2kV | 1802 | MT1331, 1332 and 1333 power off to allow crew to complete the isolation of flashed SC1329 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4812 | 2004 | 2 | 21 | 0.45486 |  | 126 | 268 | 128 | Overbrook | 13.2kV | 1804 | Pole pothead to VT192 1804-L1 at 456 McArthur blew and caused the cicuit to trip. ID #4812 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4816 | 2004 | 2 | 21 | 0.6875 |  | 90 | 75 | 50 | Overbrook | 13.2kV | 1804 | VT192 interrupted to allow for isolation to replace condemned insulators, for clearance to repair damaged pothead. At 456 McArthur. ID #4816 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15025 | 2009 | 8 | 29 | 0.20208 |  | 55 | 71 | 77 | Overbrook | 13.2kV | 1804 | Broken down ground made contact with overhead circuit at 407 McArthur. Broken down ground was secured by 24/7 & circuit re-energized from SCADA. 4 vaults on McArthur was affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20667 | 2012 | 6 | 1 | 0.86389 |  | 1149 | 19 | 1 | Overbrook | 13.2kV | 1806 | TP7288 at 175 Trainyards was isolated due to a MVA. Transformer was replaced by On Call. | Ottawa | Foreign Interference | Vehicle
3164 | 2003 | 2 | 4 | 0.85 |  | 285 | 15 | 5 | Overbrook TS | 13.2kV | 1806 & 1807 | The breakers for 1806 & 1807 lines were opened by SCADA on Line crews recommendation due to possibility of the pole top coming down in the wind. The pole was burned most of way through because of tarcking from earlier freezing rain. 5 vaults on Industrial & Tremblay were affected. The lines were sectionalized at S-274 & S-442. The breakers were closed at 20:24 to restore 2 vaults. 1806 was opened at 00:44 to close S-442 affecting VT77. 1806 was closed at 00:48 restoring VT77 & the 3 vaults that were off during repairs. 1807 was opened at 00:52 to close S-274 affecting VT53 and closed at 0059. | Ottawa | Adverse Weather | Ice Storm
4772 | 2004 | 2 | 9 | 0.35764 |  | 175 | 1095 | 574 | TO, SO | 13.2kV | 1806, 1807,SO13 | An insulator broke on 1806 cct in front of 505 Industrial. The 13kv conductor fell into the 4kv underbuild (SO13). 1806 & 1807 were picked up first but further repairs were required on SO13. All 3 cct's were equipped with auto reclosing that was in service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14089 | 2009 | 3 | 23 | 0.6125 |  | 278 | 83 | 18 | Overbrook | 13.2kV | 1807 | TP4864 @ 515 Industrial was isolated to allow customer to make repairs to defective 600V secondary conductors. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17960 | 2011 | 4 | 19 | 0.048611 |  | 20 | 0 | 1 | Overbrook | 13.2kV | 1807 | TP7288 secondary cables disconnected to 195 Trainyards due to water leaking into customer main. Electrician has connected a generator until repairs can be made. | Ottawa | Adverse Environment | Flooding
14286 | 2009 | 5 | 1 | 0.7625 |  | 50 | 8 | 10 | Overbrook | 13.2kV | 1807 | Transformer TP4864 at 505 Industrial was isolated to remove defective u/g secondary cable. | Ottawa | Defective Equipment
5280 | 2004 | 6 | 11 | 0.0625 |  | 260 | 9 | 2 | Overbrook | 13.2kV | 1808 | VT733 & VT565 isolated to allow contractor to clean & torque vaults. | Ottawa | Scheduled Outage | Preventive Maintenance
20855 | 2012 | 6 | 24 | 0.40139 |  | 162 | 51 | 19 | Overbrook |  | 1808 | At 09:38 TO50 breaker (1808 line) tripped affecting 19 customers on Coventry and St-Laurent for 162 mins. Overbrook 1808 line ID# 20855. System tried circuit again and it tripped. crew checked Vaults and cable section - no cause found. Issue may have started upstream ov breakers in VT733 St Laurent Shopping Center | Ottawa | Unknown/Other | No Apparent Cause
10771 | 2007 | 7 | 1 | 0.26736 |  | 8 | 0 | 1 | Overbrooke | 13.2kV | 1808 | VT1667 at 295 Coventry isolated for 24/7 crew to check fuses on vault supply. | Ottawa | Defective Equipment
5585 | 2004 | 7 | 31 | 0.96875 |  | 735 | 1180 | 700 | Overbrook | 13.2kV | 1808 | Cable fault between VT738 and VT718 or VT564 and VT718 caused the outage, no access to VT718, 373 Coventry, so they were isolated along with both cables until access can be arranged to megger the cables and isolate the fault.Access arranged at 10:00 am, cable fault found in recently dug fence post holes on customers property. At request of J Meek, ministry of Labour & Pro-Mark notified of cable damage (dig-in) at this location. Locate had been done July 16th. | Ottawa | Foreign Interference | Dig-in
16548 | 2010 | 7 | 23 | 0.38958 |  | 47 | 2 | 3 | Overbrook | 13.2kV | 1809 | A cable fault bet VT74 and TO38 at St. Laurent shopping centre. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3967 | 2003 | 8 | 29 | 0.64583 |  | 5 | 23 | 278 | Overbrook | 13.2kV | 1809 | TO38 GCB (1809 line) tripped on Grd Inst. Affecting St Laurent Shopping Centre & TD Waterhouse at 525 Coventry. Line was closed by SCADA. P. Lucas checked vaults and nothing found. Line is underground so lightning at the time is probably not the cause. | Ottawa | Unknown/Other | No Apparent Cause
3970 | 2003 | 8 | 29 | 0.72431 |  | 115 | 362 | 278 | Overbrook | 13.2kV | 1809 | St. Laurent Shopping Center main vault was restored at 06:20 P.M. (VT74) The other two vaults power was restored at 07:18 p.m. After T1 bank at Langs substation was transferred to TO2AP line, and J1 bus at Overbrook was restored to normal. | Ottawa | Unknown/Other | No Apparent Cause
18012 | 2011 | 4 | 28 | 0.54375 |  | 10 | 13 | 76 | Rideau Heights | 8/4.8kV | 180F1 | 180F1 circuit breaker tripped during wind/lightning storm under holdoff. Holdoff surrendered and closed VIA scada and held. | Nepean | Adverse Weather | Wind
8249 | 2006 | 5 | 7 | 0.31597 |  | 318 | 32 | 6 | Rideau Heights | 8/4.8kV | 180F1 | To isolate the O/H on Colonnade Rd S to re-insulate the 8Kv. | Nepean | Scheduled Outage | Preventive Maintenance
15661 | 2010 | 1 | 16 | 0.097222 |  | 801 | 187 | 14 | Rideau Hieghts | 8/4.8kV | 180F2 | Transformer TP2128 at 42 Antaras was Isolated due to fire at commercial building. 14 cutomers affected for 801 minutes. Rideau Heights (180F2) ID #15661 | Nepean | Adverse Environment | Fire
7869 | 2006 | 1 | 29 | 0.59097 |  | 13 | 0 | 1 | Rideau Hieghts | 8/4.8kV | 180F2 | D. Guy reports switch #901 blue phase is broken. Red & White phases opened to replace switch. Located at 6 Antares Dr. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
9996 | 2007 | 2 | 6 | 0.60069 |  | 30 | 0 | 1 | Rideau Heights | 27.6/16kV | 180F2 | Isolated 3 phase customer to replace broken switch on transformer 2404 at 6 Antares Dr | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6905 | 2005 | 7 | 11 | 0.67292 |  | 546 | 9 | 1 | Rideau Heights | 8/4.8kV | 180F2 | Dump truck hit the overhead tilted pole and twisted transformer.NP000522 located at 141Bentley. 120/240 reconnected, 600 volt to be reconnected Tuesday, electrian could not get in building to check rotation. | Nepean | Foreign Interference | Vehicle
14777 | 2009 | 7 | 18 | 0.59236 |  | 27 | 18 | 41 | Rideau Heights | 8/4.8kV | 180F2 | S901 feeding TE2402 at 6 Anteries, had a broken switch, crew opened other 2 phases to make repairs, switch replaced and power restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11009 | 2007 | 8 | 7 | 0.46528 |  | 250 | 8 | 2 | Rideau Heights | 8/4.8kV | 180F2 | 75 Bentley Dr was isolated to allow Hydro Crew to replace a broken hydro pole. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11014 | 2007 | 8 | 8 | 0.45139 |  | 30 | 2 | 5 | Rideau Heights | 8/4.8kV | 180F2 | At 10:50 trans at 74 Bentley was isolated in order to repair a switch | Nepean | Scheduled Outage | Repair
16865 | 2010 | 9 | 3 | 0.73333 |  | 358 | 90 | 15 | Rideau Heights | 8/4.8kV | 180F2 | 180F2 circuit opened due to a tree down on the three phase primary dip S50 at 6 Antares dr. | Nepean | Tree Contacts | Tree Fallen
11351 | 2007 | 9 | 20 | 0.74583 |  | 411 | 14 | 2 | Rideau Hts | 8/4.8kV | 180F2 | TE1247 @ 92 Bentley was isolated to allow the customer to pull in new secondary conductor. | Nepean | Scheduled Outage | Repair
19567 | 2011 | 11 | 13 | 0.35278 |  | 140 | 56 | 24 | Rideau Heights | 12/7.2kV | 180F2 | The 180F2 O/H line section from S522 to S985 including TE3506 on Bentely and Huntclub was isolated to allow crew to reframe riser pole at S1635 and remove NIU conductors from pole on old O/H line. | Nepean | Scheduled Outage | Preventive Maintenance
6035 | 2004 | 12 | 11 | 0.049306 |  | 4 | 17 | 260 | Rideau Heights | 8/4.8kV | 180F2 | 180F2 bkr opened to close in line switches for restoration of the 180F6 customers. | Nepean | Defective Equipment
17531 | 2011 | 1 | 27 | 0.59861 |  | 43 | 4 | 5 | Rideau Heights | 8/4.8kV | 180F3 | Isolated transformer X36774 at 17 STEPHANIE AVE for service up-grade | Nepean | Scheduled Outage | Emergency Services Request
13965 | 2009 | 2 | 12 | 0.21875 |  | 173 | 786 | 336 | Rideau Heights | 8/4.8kV | 180F3 | Rideau Heights 180F3 feeder trip. Broken insulator at S1455 caused phases to make contact. Insulator replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13990 | 2009 | 2 | 18 | 0.64236 |  | 55 | 1 | 1 | Rideau Heights | 8/4.8kV | 180F3 | Mike Byers established PC10A#4850 at 15:25. Mike need to establish PC10A a S1572 to isolate TE1069 at 9 Capella court to check transformer. Customer complaints about single phase power out of three phase bank. Mike Byers surrendered PC10A#4850 and reported no problems, Primary and secondary and transformer were ok.TE1069 at 9 Capella is back on. 180F3 Rideau Heights ID#13990. | Ottawa | Unknown/Other | No Apparent Cause
3313 | 2003 | 4 | 2 | 0.71875 |  | 50 | 2 | 2 | Rideau Heights | 8/4.8kV | 180F3 | TE1501 replaced due to oil leak in old transformer at 85 Auriga . | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12597 | 2008 | 6 | 10 | 0.91181 |  | 32 | 179 | 336 | Rideau Heights | 8/4.8kV | 180F3 | SCADA indicates 180F3 breaker A/R/A/R/A, tree made contact with the O/H. | Nepean | Tree Contacts
6724 | 2005 | 6 | 15 | 0.13542 |  | 27 | 54 | 120 | Rideau Heights | 8/4.8kV | 180F3 | 180F3 feeder opened manually to allow crew to isolate dip sws S1426, switches have to be isolated due to pole fire and to replace sws. | Nepean | Defective Equipment
6727 | 2005 | 6 | 15 | 0.125 |  | 42 | 1 | 1 | Rideau Heights | 8/4.8kV | 180F3 | Pole fire at dip sws S1426, switches also needed to be replaced due to fire, switches isolate dand replaced. | Nepean | Adverse Environment | Fire
6791 | 2005 | 6 | 24 | 0.64931 |  | 45 | 1 | 1 | Rideau Heights | 8/4.8kV | 180F3 | Transformer #2419 located at 2 Gurdwara isolated to replace a bad switch | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12785 | 2008 | 7 | 3 | 0.69097 |  | 85 | 3 | 2 | Rideau Heights | 8/4.8kV | 180F3 | Crew replaced all three switches at S1615 feeding TE3292 @ 7 Capella crt. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
12817 | 2008 | 7 | 10 | 0.86667 |  | 354 | 1189 | 344 | Rideau Heights | 8/4.8kV | 180F3 | 180F3 auto reclosed and locked out. S1454 centre phase found broken and cable down. 24/7 isolated switch and on call called to make repairs. All 3 switches replaced and conductor. 156 customers affected for duration of repairs, all load restored 02:42 am. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
10916 | 2007 | 7 | 20 | 0.34375 |  | 25 | 0 | 1 | Rideau Hights | 8/4.8kV | 180F3 | Isolated 3 phase switchers 1490 feeding TE2022 at 10 Capella Crt to replace a broken switch | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8820 | 2006 | 7 | 25 | 0.16597 |  | 2 | 4 | 120 | Rideau Heights | 8/4.8kV | 180F3 | 180F3 Breaker tripped and locked out. Heavy Rain and lightning storm in effect. | Nepean | Lightning | Direct Strike
15343 | 2009 | 11 | 1 | 0.33472 |  | 492 | 329 | 41 | Rideau Heights | 8/4.8kV | 180F3 | 180F3 line section S341 x S347 x TEMP108 on MacFarlane isolated to replace existing 1/0 conductor. 41 commercial customers on Auriga & Corvus Crt were affected including IBM. Isolation was expanded at 8:02 to include IBM and then reduced at 9:48 to minimize the outage time to IBM. | Nepean | Scheduled Outage | Preventive Maintenance
13591 | 2008 | 11 | 12 | 0.42361 |  | 40 | 2 | 3 | Rideau Heights | 8/4.8kV | 180F3 | Transformer #X5884 located at 2 Stephanie Ave isolated due to service upgrade | Nepean | Scheduled Outage | Preventive Maintenance
4473 | 2003 | 11 | 18 | 0.525 |  | 6 | 1 | 7 |  | 8/4.8kV | 180F3 | Tree fell on primary lines, Transformer 285 and switch 1577 was opened to remove tree. 25 Promenade, Nepean | Nepean | Tree Contacts | Tree Fallen
7681 | 2005 | 12 | 2 | 0.76111 |  | 1031 | 52 | 3 | Rideau Heights | 8/4.8kV | 180F3 | Tree on the wire. NCC property and overhead not trimmed. Delay in restoration till day light | Nepean | Tree Contacts | Tree Fallen
15491 | 2009 | 12 | 9 | 0.93056 |  | 112 | 2 | 1 | Rideau Heights |  | 180F3 | S1508 was opened to interrupt power to TE476 for fire at 81 Auriga. 39 unit comercial building was interrupted for a fire affecting several units. The damaged units were left open at the customer's breaskers. | Nepean | Adverse Environment | Fire
15513 | 2009 | 12 | 14 | 0.65208 |  | 61 | 10 | 10 | Rideau Heights | 8/4.8kV | 180F3 | Transformer #X5265 located at 61 Rideau Heights Dr isolated due to defective transformer switch | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11880 | 2007 | 12 | 24 | 0.44167 |  | 124 | 6 | 3 | Rideau Heights | 8/4.8kV | 180F3 | Transformer #X5091 located at 9 Corvus isolated due to broken switch | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15609 | 2010 | 1 | 5 | 0.36458 |  | 10 | 1 | 6 | Rideau Heights | 8/4.8kV | 180F4 | Transformer #X33046 located at 6 Pineglen Cres isolated for disconnect/reconnect for an upgrade | Nepean | Scheduled Outage | Construction
19851 | 2012 | 1 | 18 | 0.089583 |  | 78 | 1262 | 971 | Rideau Heights | 8/4.8kV | 180F4 | 180F4 circuit auto reclosed and crew found signs of wires slapping together circuit was closed via SCADA and all load restores. Rideau Heights (180F4) ID#19851 | Nepean | Adverse Weather | Wind
13905 | 2009 | 1 | 29 | 0.46319 |  | 63 | 68 | 65 | Rideau Heights | 8/4.8kV | 180F4 | S934 w phase opened up, dumping off 5 transformers and 65 customers. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13923 | 2009 | 2 | 2 | 0.52222 |  | 113 | 19 | 10 | Rideau Heights | 8/4.8kV | 180F4 | xfrm #315 at 1 & 3 Winding Way isolated to allow for transformer change | Nepean | Scheduled Outage | Construction
13946 | 2009 | 2 | 9 | 0.45833 |  | 200 | 7 | 2 | Rideau Heights | 8/4.8kV | 180F4 | Isolated transformer at 91 Winding way to repair service | Nepean | Scheduled Outage | Repair
13954 | 2009 | 2 | 11 | 0.39444 |  | 177 | 68 | 23 | Rideau Hiehgts | 8/4.8kV | 180F4 | Energizing of new 8kV line on Winding Way | Ottawa | Scheduled Outage | Construction
3209 | 2003 | 2 | 24 | 0.42431 |  | 372 | 584 | 1000 | Rideau Heights DS | 8/4.8kV | 180F4 | 180F4 feeder automic trip caused by fault in cable section. The fault also caused transformer bushing and elbow damage at another location. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3210 | 2003 | 2 | 24 | 0.56875 |  | 19 | 285 | 900 | Rideau Heights DS | 8/4.8kV | 180F4 | 180F4 automatic trip occurred while attempting to restore section of feeder. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3216 | 2003 | 2 | 27 | 0.52361 |  | 114 | 23 | 12 | Rideau Heights | 8/4.8kV | 180F4 | Underground Crew working on cable fault repairs required an interruption to TE560 to repair the adjacent cable. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
20093 | 2012 | 3 | 2 | 0.70833 |  | 20 | 0 | 1 | Rideau Heights | 8/4.8kV | 180F4 | Isolated transformer X06279 at 38 Queen Anne Cres to replace defective switch and arrester | Nepean | Defective Equipment | Imminent Equipment Failure Detected
10096 | 2007 | 3 | 6 | 0.75069 |  | 152 | 380 | 150 | Rideau Hieghts | 8/4.8kV | 180F4 | upstream lead on red phase of switch S1046 burnt off. Switch could not be operated. load on red phase was restored from switch S635R. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
8029 | 2006 | 3 | 15 | 0.55556 |  | 55 | 7 | 8 | Rideau Heights | 8/4.8kV | 180F4 | Mike Macllelan had transformer NP4128 off at 78 Macfarlane to do an insulator replacement | Nepean | Unknown/Other
8033 | 2006 | 3 | 15 | 0.83333 |  | 85 | 11 | 8 | Rideau Heights | 8/4.8kV | 180F4 | TE2398 @ 83 Mcfarland rd. out to change insulatore on S193. | Nepean | Scheduled Outage | Repair
8034 | 2006 | 3 | 15 | 0.88958 |  | 68 | 9 | 8 | Rideau Heights | 8/4.8kV | 180F4 | TE2910 @ 39 Auriga out to replace insulators on S654 | Nepean | Scheduled Outage | Repair
14071 | 2009 | 3 | 17 | 0.39583 |  | 140 | 14 | 12 | Rideau Hieghts | 8/4.8kV | 180F4 | Transformer at 9 Windingway was isolated to allow crews to make repairs. | Ottawa | Scheduled Outage | Repair
6319 | 2005 | 3 | 24 | 0.50139 |  | 56 | 65 | 70 | Rideau Heights | 8/4.8kV | 180F4 | Switch 1102 blown fuse. Line patrolled nothing found. New fuse installed. | Nepean | Unknown/Other | No Apparent Cause
4939 | 2004 | 3 | 26 | 0.77917 |  | 18 | 17 | 56 | Rideau Heights | 8/4.8kV | 180F4 | S1102 had a defective live line clamp and had to be replaced | Nepean | Defective Equipment | Imminent Equipment Failure Detected
10196 | 2007 | 3 | 28 | 0.38472 |  | 334 | 11 | 2 | Rideau Heights | 8/4.8kV | 180F4 | Overhead transformer at 123 Winding Way in Barrhaven isolated to transfer customers to new U/G transformer. | Nepean | Scheduled Outage | Construction
10200 | 2007 | 3 | 28 | 0.4375 |  | 218 | 7 | 2 | Rideau Heights | 8/4.8kV | 180F4 | O/H transformer 808 at 219 Winding Way in Barrhaven isolated to transfer customers to new tx. | Nepean | Scheduled Outage | Preventive Maintenance
10201 | 2007 | 3 | 28 | 0.47917 |  | 158 | 13 | 5 | Rideau Heights | 8/4.8kV | 180F4 | O/H transformer 1440 at 201 Winding Way in Barrhaven isolated to transfer customers to new tx. | Nepean | Scheduled Outage | Construction
8085 | 2006 | 3 | 30 | 0.73611 |  | 30 | 1 | 2 | Rideau Heights | 8/4.8kV | 180F4 | Transformer #NP000820 located at 2858 Prince of Wales Dr isolated to check all connections & tighten them | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17840 | 2011 | 4 | 6 | 0.56597 |  | 17 | 2 | 7 | Rideau Heights | 8/4.8kV | 180F4 | TP3444 at 33 Chesswood isolated to make temporary repairs to connection in transformer | Nepean | Scheduled Outage | Repair
17911 | 2011 | 4 | 12 | 0.40833 |  | 117 | 25 | 13 | Rideau Heights | 8/4.8kV | 180F4 | Transformer TE690 @ 19 Parmalea was opened to allow crew to replace elbows and inserts. 13 customer were affected for 117 minutes. Rideau Heights 180F4 | Nepean | Scheduled Outage | Repair
17912 | 2011 | 4 | 12 | 0.35417 |  | 170 | 37 | 13 | Rideau Heights | 8/4.8kV | 180F4 | Trans TE690 at 19 Parmalea Cres was isolated in order to replace bushings and inserts | Nepean | Scheduled Outage | Repair
17925 | 2011 | 4 | 14 | 0.39028 |  | 88 | 10 | 7 | Rideau Heights | 8/4.8kV | 180F4 | TP3444 @ 68 Amberwood was isolated to allow crew to repair secondary services. 7 customer were affected Rideau Heights 180F4 | Nepean | Scheduled Outage
10263 | 2007 | 4 | 16 | 0.25347 |  | 160 | 160 | 60 | Rideau Heights | 8/4.8kV | 180F4 | Tree limb contacted O/H circuit causing S571 fuse to open. 180F4 auto/reclosed. | Nepean | Adverse Weather | Snow
17947 | 2011 | 4 | 17 | 0.525 |  | 252 | 193 | 46 | Rideau Heights | 8/4.8kV | 180F4 | Tree came down at the intersection of Brisbane and Promenade. Affecting 46 customers on Brisbane, Promenade, Tennyson, Deerland and Mayo streets. | Nepean | Tree Contacts | Tree Limb Fallen
5021 | 2004 | 4 | 19 | 0.39028 |  | 651 | 228 | 21 | Rideau Heights | 8/4.8kV | 180F4 | Transformer TE554 on Amberwood Dr in Nepean isolated for replacement, first transformer used leaked and had to be replaced also so outage was longer then expected. | Nepean | Scheduled Outage | Repair
17975 | 2011 | 4 | 20 | 0.53819 |  | 6 | 1 | 11 | Rideau Heights | 8/4.8kV | 180F4 | Transformer #X38273 located at 3 Belledune St opened by crew to remove branch from primary | Nepean | Tree Contacts | Tree Limb Fallen
12344 | 2008 | 4 | 25 | 0.37986 |  | 82 | 14 | 10 | Rideau Heights | 8/4.8kV | 180F4 | TE693 at 22 Fifeshire isolated to repair defective secondary cable at the base of transformer. | Nepean | Scheduled Outage | Repair
5057 | 2004 | 4 | 26 | 0.43194 |  | 62 | 12 | 12 | Rideau Heights | 8/4.8kV | 180F4 | Transformer TE558W on Amberwood Cr in Nepean isolated to repair burnt switchgear. | Nepean | Scheduled Outage | Repair
5114 | 2004 | 5 | 7 | 0.58194 |  | 94 | 16 | 10 | Ridesau Heights | 8/4.8kV | 180F4 | Te699 isolated to repair swollen elbows and possible oil leak | Nepean | Scheduled Outage | Repair
5130 | 2004 | 5 | 11 | 0.44167 |  | 13 | 1 | 6 | Rideau Heights | 8/4.8kV | 180F4 | Transformer at 2882 Prince of Wales interrupted in order to disconnect service. | Nepean | Unknown/Other
18132 | 2011 | 5 | 11 | 0.40625 |  | 165 | 6 | 2 | Rideau Heights | 8/4.8kV | 180F4 | At 09:45 inline switch was isolated to allow tree contractor to remove trees. 2 customers were affected for 165 minutes. Rideau Heights (180F4) ID#18132 | Nepean | Scheduled Outage
14479 | 2009 | 6 | 6 | 0.77431 |  | 65 | 4 | 4 | Rideau Hts | 8/4.8kV | 180F4 | Squirrel contact at Transformer X33040 at 3 Leeward caused Tx fuse to blow. Fuse replaced, power restored. | Nepean | Foreign Interference | Animal
16213 | 2010 | 6 | 7 | 0.46597 |  | 37 | 6 | 10 | RIDEAU HEIGHTS DS | 8/4.8kV | 180F4 | Transformer X06249 at 2952 Prince of Wales Dr isolated to make repairs to damaged neutral to the duplex | Nepean | Foreign Interference | Vehicle
14555 | 2009 | 6 | 17 | 0.26319 |  | 138 | 16 | 7 | Rideau Heights | 8/4.8kV | 180F4 | Transformer #X36652 located at 25 Promenade isolated due to squirrel contact | Nepean | Foreign Interference | Animal
8561 | 2006 | 6 | 19 | 0.8125 |  | 495 | 248 | 30 | Rideau Heights | 8/4.8kV | 180F4 | Crew replaced a section of o/h primary conductor at 65 Pineglen. Refused and closed S190. Severe Thunder and lightning storm in effect. | Nepean | Defective Equipment
12700 | 2008 | 6 | 20 | 0.35972 |  | 358 | 3306 | 963 | Rideau Heights | 8/4.8kV | 180F4 | 180F4 tripped at same time as 180F5. Sectionalizing indicated fault was between S1461 & S1128 but when section was sectionalized & restored one section at time no permanent fault was ever determined. Cause of tripping is still under investigation. | Nepean | Unknown/Other
6767 | 2005 | 6 | 21 | 0.034722 |  | 335 | 2281 | 835 | Rideau Heights | 8/4.8kV | 180F4 | A primary O/H center phase fell into the neutral and got tangaled up on Hwy 16 at Blazer. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6785 | 2005 | 6 | 23 | 0.32222 |  | 556 | 568 | 650 |  | 8/4.8kV | 180F4 | M. McLellan reports BOTH blue phase cable section at te704 are damaged. May have been due to a dig in by Greely. | Nepean | Foreign Interference | Dig-in
10742 | 2007 | 6 | 27 | 0.41319 |  | 101 | 50 | 50 | Rideau Heights | 8/4.8kV | 180F4 | Overhead line section isolated to install new switch S16848. 5 O/H xfmrs were interrupted in the Pineglen area. Once new switch was installed, power was restored to 3 of the overhead transformers & the remaining 2 fed from S16848 stayed off to dead end wire. | Nepean | Scheduled Outage | Construction
12776 | 2008 | 7 | 2 | 0.40764 |  | 170 | 23 | 8 | Rideau Heights | 8/4.8kV | 180F4 | Transformer TE697 @ 34 Fifeshire was isolated for replacement. | Nepean | Scheduled Outage | Repair
10798 | 2007 | 7 | 5 | 0.38889 |  | 66 | 7 | 6 | Rideau Heights | 8/4.8kV | 180F4 | At 09:20 trans at 16 Briggs Ave was isolated in order to remove old sec cond | Ottawa | Scheduled Outage | Preventive Maintenance
16430 | 2010 | 7 | 8 | 0.75 |  | 195 | 28 | 65 | Rideau Heights | 8/4.8kV | 180F4 | Pedestal fed from TP3435 was burning up and emergency switching at TP3435 was required to de-energize and cut clear the damaged equipment for follow-up repair. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
14731 | 2009 | 7 | 12 | 0.37847 |  | 100 | 2 | 1 | Rideau Hts | 8/4.8kV | 180F4 | TE820 at 2259 Prince of Wales was replaced for the second time due to a defective R phase winding. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14752 | 2009 | 7 | 15 | 0.55139 |  | 3 | 48 | 963 | Rideau hieghts | 8/4.8kV | 180F4 | A red phase lead @ switch S408 at 146 McFarlane rd, burnt off. Circuit was dumped to allow crew to repair lead. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
6973 | 2005 | 7 | 16 | 0.78125 |  | 32 | 440 | 825 | Rideau Heights | 8/4.8kV | 180F4 | Lighnting in the area caused the 180F4 which was on hold off to open, Doug closed it in and holding. He patrol the circuit and found nothing. | Nepean | Adverse Weather | Lightning
18673 | 2011 | 7 | 16 | 0.63056 |  | 77 | 69 | 54 | Rideau Heights | 8/4.8kV | 180F4 | S190 at 43 Merivale found blown. Crews patrolled line, nothing found. Re-fused and closed. | Nepean | Unknown/Other | No Apparent Cause
18765 | 2011 | 7 | 18 | 0.04375 |  | 665 | 8738 | 859 | Rideau Heights | 8/4.8kV | 180F4 | 180F4 Tripped during severe wind/lightening storm. After patrolling, testing and close attempts a broken insulator was found. Damaged insulator was isolated, customers restored at 6:32am July 18th. 180F4 returned to normal 22:55 July 18th. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
3765 | 2003 | 7 | 20 | 0.34861 |  | 38 | 4 | 7 | Rideau Heights | 8/4.8kV | 180F4 | A squirrel caused the fuse to blow at a transformer on Promenade in Nepean. The crew refused and restored power | Nepean | Foreign Interference | Animal
7001 | 2005 | 7 | 21 | 0.36736 |  | 404 | 54 | 8 | Rideau Heights | 8/4.8kV | 180F4 | Isolate transformer TE1896 on Campfield Dr to allow for cable replacement. | Nepean | Scheduled Outage | Preventive Maintenance
7003 | 2005 | 7 | 21 | 0.61667 |  | 222 | 278 | 75 | Rideau Heights | 8/4.8kV | 180F4 | They replaced the broken switch 935B at Amberwood & Merivale and meger six cable section to determine if there was a bad cable since there was consturction in the area. | Nepean | Defective Equipment
18791 | 2011 | 7 | 21 | 0.53472 |  | 20 | 19 | 58 | Rideau Heights | 8/4.8kV | 180F4 | Crew isolated overhead on Pineglen at Switch S190, to remove tree from overhead circuit. | Nepean | Tree Contacts | Tree Limb Fallen
16544 | 2010 | 7 | 22 | 0.77986 |  | 332 | 6 | 1 | Rideau Heights | 8/4.8kV | 180F4 | The overhead transformer at 2606 Prince of Wales had to be replaced by Oncall. Transformer & secondary bus are believed to have been damaged during heavy rain, wind & lightning. | Nepean | Adverse Weather
16599 | 2010 | 8 | 1 | 0.98958 |  | 25 | 2 | 6 | Rideau Heights | 8/4.8kV | 180F4 | Tree contact caused an overhead transformer at 8 Grayson to open, crew refused. | Nepean | Tree Contacts | Inadequate Trimming
7059 | 2005 | 8 | 4 | 0.37639 |  | 198 | 33 | 10 |  | 8/4.8kV | 180F4 | Isolation of TE560 on 9 Lacewood Ct. for clearance for cable replacement. | Nepean | Scheduled Outage
7120 | 2005 | 8 | 10 | 0.66667 |  | 99 | 1028 | 623 | Rideau Heights | 8/4.8kV | 180F4 | Rideau Heights 180F4 auto trip, reclosing was blocked on same, thunderstorm in area, feeder restored at the station. | Nepean | Adverse Weather
7138 | 2005 | 8 | 15 | 0.39514 |  | 167 | 45 | 16 | Rideau Heights | 8/4.8kV | 180F4 | Planned isolation for TE556 (Nepean) to excavate and replace cable | Nepean | Scheduled Outage | Construction
7150 | 2005 | 8 | 17 | 0.60833 |  | 635 | 978 | 820 | Rideua Heights | 8/4.8kV | 180F4 | A bad transformer at TE695 @ 126 Amberwood and a faulted cable bet TE559W to TE558. While trying to fault find we blew the fuse at S934W and the 180F4 opened. Refused S934 and closed 180F4 to restore power bulk of the customers. Upon restoringTE695 we blew TE696 @ 51 Fifshire and anothere cable fault bet TE560W and TE653W. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7156 | 2005 | 8 | 17 | 0.88958 |  | 64 | 13 | 12 | Rideau Heights | 8/4.8kV | 180F4 | Isolation of TE560 at 9 Lacewood to repair faulted cable.. | Nepean | Defective Equipment
7160 | 2005 | 8 | 18 | 0.31736 |  | 142 | 113 | 50 | Rideau Heights | 8/4.8kV | 180F4 | Cable fault between transformers TE558 & TE559, sw S934W blew, 5 txs between S934W and TE560 on Amberwood interupted. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16781 | 2010 | 8 | 19 | 0.64722 |  | 193 | 832 | 400 | Rideau Heights | 8/4.8kV | 180F4 | branch on overhead conductor was found accross 3 phase on HWY16 south of Fallowfield & S140 one phase of switch was found brunt into crossarm. | Nepean | Tree Contacts | Tree Limb Fallen
7180 | 2005 | 8 | 22 | 0.54167 |  | 70 | 13 | 30 | Rideau Heights | 8/4.8kV | 180F4 | 20 customers out due to switching to isolate TE558 a live front transformer. Pulling in new cable | Nepean | Scheduled Outage | Construction
7196 | 2005 | 8 | 24 | 0.375 |  | 490 | 83 | 30 | Rideau Hieghts | 8/4.8kV | 180F4 | Transformer 704 in Country Place was isolated for working clearance. Te561 & TE562 opened to allow crews to isolate TE704 for 3 mins. | Nepean | Scheduled Outage | Construction
7197 | 2005 | 8 | 24 | 0.37708 |  | 357 | 95 | 30 | Parkwoodhills | 8/4.8kV | 180F4 | TE704 at Country Place isolated for cable trenching for working clearance | Nepean | Scheduled Outage | Construction
5729 | 2004 | 8 | 27 | 0.38819 |  | 141 | 35 | 15 | Rideau Heights | 8/4.8kV | 180F4 | Two transformer removed from 8 kv and transferred to 27Kv on Winding Way, plus 4 new transformers energized. | Nepean | Scheduled Outage | Construction
15041 | 2009 | 8 | 31 | 0.4 |  | 26 | 3 | 7 | Rideau Heights | 8/4.8kV | 180F4 | TP3444 at 68 Amberwood isolated to record transformer resistance readings | Nepean | Scheduled Outage
13195 | 2008 | 9 | 5 | 0.54514 |  | 70 | 9 | 8 | Rideau Heights | 8/4.8kV | 180F4 | Transformer X5097 isolated at 128 Mcfarlane to change out transformer | Nepean | Scheduled Outage
16881 | 2010 | 9 | 6 | 0.99097 |  | 13 | 0 | 2 | Rideau Heights | 8/4.8kV | 180F4 | S1081 opened, at 61 Auriga to replace line clamps which were burning up. | Nepean | Defective Equipment
7288 | 2005 | 9 | 7 | 0.38194 |  | 350 | 70 | 12 | Rideau Heights | 8/4.8kV | 180F4 | Transformer TE653 was replaced with TP3449 in Country Place. | Nepean | Scheduled Outage | Construction
7292 | 2005 | 9 | 8 | 0.39097 |  | 487 | 130 | 16 | Rideau Hts | 8/4.8kV | 180F4 | Isolation of TE1896 (7 Campfield) and TE654 (95 Amberwood) for cable and transformer replacement (scheduled) | Nepean | Scheduled Outage | Preventive Maintenance
7293 | 2005 | 9 | 8 | 0.36111 |  | 530 | 212 | 24 | Rideau Heights | 8/4.8kV | 180F4 | Isolated transformer TP3446 & TP3447 for cable and transformer replace in Country Place. | Nepean | Scheduled Outage | Preventive Maintenance
7301 | 2005 | 9 | 9 | 0.43403 |  | 275 | 73 | 16 | Rideau Hts | 8/4.8kV | 180F4 | Isolation of TE1905 and TE555 in Country Place for transformer and cable replacement. | Nepean | Scheduled Outage
9170 | 2006 | 9 | 9 | 0.75 |  | 1265 | 1057 | 55 | Rideau Heights | 8/4.8kV | 180F4 | S190 fuse opened due to tree on line. Temp switch cut in 40 customers restored by closeing S190. Tree removed wire repaired temp switch closed and sleeved out. | Nepean | Adverse Weather | Wind
7321 | 2005 | 9 | 13 | 0.38194 |  | 352 | 47 | 8 | Rideau Heights | 8/4.8kV | 180F4 | Planned outage to transformer TE552 for replacement affecting 8 customers on Weatherwood Cr. | Nepean | Scheduled Outage | Construction
7324 | 2005 | 9 | 14 | 0.38889 |  | 460 | 92 | 12 | Rideau Heights | 8/4.8kV | 180F4 | Transformer TE560 in Country Place isolated for replacement. | Nepean | Scheduled Outage | Construction
13243 | 2008 | 9 | 16 | 0.38681 |  | 338 | 45 | 8 | Rideau Heights | 8/4.8kV | 180F4 | TP6130 at 34 Fifeshire isolated for repalcement & base installation. | Nepean | Scheduled Outage | Repair
7346 | 2005 | 9 | 19 | 0.41181 |  | 276 | 46 | 10 | Rideau Heights | 8/4.8kV | 180F4 | Isolation of TE559 at 44 Amberwood in Country Place for cable and transformer replacement. | Nepean | Scheduled Outage
7349 | 2005 | 9 | 20 | 0.38542 |  | 345 | 80 | 14 | Rideau Heights | 8/4.8kV | 180F4 | Isolate TE558 @ 12 Charnwood for cable and transformer replacement. | Nepean | Scheduled Outage | Construction
11342 | 2007 | 9 | 20 | 0.40278 |  | 221 | 48 | 13 | Rideau Heights | 8/4.8kV | 180F4 | 2 transformer effected in planned outage on Briggs & Belldune st to all crews to replace 2 Hydro Poles. | Nepean | Scheduled Outage | Construction
7355 | 2005 | 9 | 21 | 0.375 |  | 380 | 63 | 10 | Rideau Heights | 8/4.8kV | 180F4 | Isolate transformer TE557 @ 15 Charnwood to connect new cable. | Nepean | Scheduled Outage | Preventive Maintenance
7384 | 2005 | 9 | 27 | 0.39583 |  | 295 | 30 | 6 | Rideau Heights | 8/4.8kV | 180F4 | TE705 was isolated to allow crews to replace transformer in Country Place | Gloucester | Scheduled Outage | Construction
11414 | 2007 | 9 | 28 | 0.40625 |  | 295 | 69 | 14 | Rideau Heights | 8/4.8kV | 180F4 | 180F4 single phase O/H section on Briggs St isolated to install new spun bus in prep for removal of primary conductor. | Nepean | Scheduled Outage | Construction
7419 | 2005 | 10 | 3 | 0.40764 |  | 293 | 63 | 13 | RIDEAU HIGHTS | 8/4.8kV | 180F4 | TRANSFORMER TE706 ISOLATED FOR REPLACEMENT | Nepean | Scheduled Outage | Construction
7424 | 2005 | 10 | 4 | 0.38472 |  | 330 | 55 | 10 | RIDEAU HIGHTS | 8/4.8kV | 180F4 | SCHEDUALED OUTAGE OF TP3441(TE704B) FOR REPLACEMENT OF TRANSFORMER AND ASSOCIATED CABLES. | Nepean | Scheduled Outage | Construction
7432 | 2005 | 10 | 6 | 0.39444 |  | 362 | 60 | 10 | Rideau Hieghts | 8/4.8kV | 180F4 | W. Ried reports transformer TE563 isolated to replace tranformer & cables. | Nepean | Scheduled Outage | Construction
15223 | 2009 | 10 | 7 | 0.010417 |  | 145 | 34 | 14 | Rideau Heights | 8/4.8kV | 180F4 | At 00:15 am crews isolated transformer TP3442 to make repairs. 14 customers were affected for a 145 mins. Rideau Heights 180F4 ID#15223. | Nepean | Defective Equipment
11493 | 2007 | 10 | 10 | 0.37639 |  | 291 | 48 | 10 | RIDEAU HEIGHTS | 8/4.8kV | 180F4 | Planned outage on Briggs and Belldune, to 10 customers to transfer customers to new spun bus. | Nepean | Scheduled Outage
11511 | 2007 | 10 | 13 | 0.5 |  | 75 | 1 | 1 |  | 8/4.8kV | 180F4 | termination burned off at S1116 feeding TE2936 required isolation to repair at 2271 Prince of Wales | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11512 | 2007 | 10 | 13 | 0.83333 |  | 45 | 2 | 2 | Rideau Heights | 120/208 | 180F4 | 11 & 13 Lacewood were interrupted for Oncall crew to make repairs to TP3438's secondary pedestal. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4256 | 2003 | 10 | 14 | 0.39236 |  | 65 | 24 | 22 | Rideau Hieghts | 8/4.8kV | 180F4 | P. Barr reports switch #358 now refused and close restoring power. Outage caused by truck contacting overhead line. | Nepean | Foreign Interference | Vehicle
4280 | 2003 | 10 | 15 | 0.61458 |  | 95 | 45 | 47 | Rideau Heights |  | 180F4 | Tree down blow fuse at switch 571. | Nepean | Adverse Weather | Wind
7472 | 2005 | 10 | 17 | 0.42708 |  | 295 | 123 | 25 | Rideau Heights | 8/4.8kV | 180F4 | TE562 in Country Place was isolated to allow crews to replace transformer & Cables. | Nepean | Scheduled Outage | Construction
7475 | 2005 | 10 | 18 | 0.47778 |  | 102 | 10 | 6 | Rideau Heights | 8/4.8kV | 180F4 | Replaced broken switch to Transformer NP000584 at 42 Silverwood Rd cause unknown | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15276 | 2009 | 10 | 18 | 0.925 |  | 68 | 3 | 3 | Rideau Heights | 8/4.8kV | 180F4 | Crew replaced defective Switch S1232, which supplied 3 customers. Repairs made and power restored. | Nepean | Defective Equipment
7494 | 2005 | 10 | 20 | 0.38681 |  | 337 | 51 | 9 | RIDEAU HGTS. | 8/4.8kV | 180F4 | W. REID COMPLETES CBL AND TRANSFORMER REPLACEMENT @ COUNTRY PLACE ON T561(TP3439) ON BLUE PHASE. | Nepean | Scheduled Outage | Construction
4332 | 2003 | 10 | 23 | 0.33333 |  | 66 | 4 | 4 | Rideau Heights | 8/4.8kV | 180F4 | Transformer opened to allow crew to restring service. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
13519 | 2008 | 10 | 29 | 0.27153 |  | 164 | 2173 | 963 | RIDEAU HIEGHTS | 8/4.8kV | 180F4 | S1461 closed by J.Lewandowski restoring CIRCUIT | Nepean | Adverse Weather
11650 | 2007 | 11 | 2 | 0.41667 |  | 210 | 0 | 13 | Rideau Hieghts | 8/4.8kV | 180F4 | Transformer TE698 @ 6 Fifeshire was isolated for crew to perform repairs on secondary in transformer. | Nepean | Scheduled Outage | Repair
4385 | 2003 | 11 | 4 | 0.53264 |  | 126 | 1728 | 823 | Rideau Heights | 8/4.8kV | 180F4 | T. Cunningham reports conductor floating on HWY 16 & Merivale rd. causing circuit breaker to lock out. Crew reports 30 mins to repair overhead conductor. Crew reports overhead connecter repaired, and circuit restored to normal @ 14:53. ID#4385 | Nepean | Adverse Weather | Wind
13601 | 2008 | 11 | 12 | 0.65833 |  | 124 | 12 | 6 | Rideau Heights | 8/4.8kV | 180F4 | Transformer TE698 @ 6 Fifeshire was isolated to make secondary repairs. | Nepean | Scheduled Outage | Repair
4433 | 2003 | 11 | 13 | 0.013194 |  | 459 | 8 | 1 | Rideau heights | 8/4.8kV | 180F4 | 3kva transformer at 2606 Prince of Wales took a lightening strike causing it to finally give up the ghost, on call brought in to replace the whole assembly. | Nepean | Lightning | Direct Strike
9672 | 2006 | 11 | 16 | 0.73611 |  | 94 | 484 | 823 | Rideau Heights | 8/4.8kV | 180F4 | A tree limb fell across the primary o/h line on Prince of Wales Dr. 180F4 Breaker opened to open in line switches to isolate o/h line. Tree limb removed and all power restored. | Nepean | Tree Contacts | Tree Limb Fallen
17287 | 2010 | 11 | 17 | 0.67431 |  | 31 | 441 | 853 | Rideau Heights | 8/4.8kV | 180F4 | 180F4 feeder opened due to tree contact at Prince of Whales and Deakin | Nepean | Tree Contacts | Tree Fallen
4489 | 2003 | 11 | 20 | 0.44097 |  | 100 | 40 | 24 | Rideau Heights | 8/4.8kV | 180F4 | Transformers 1837, 1838 & 1839 isolated to rephase section and remove transformer 1844B. | Nepean | Scheduled Outage | Repair
4490 | 2003 | 11 | 20 | 0.44097 |  | 229 | 31 | 9 | Rideau Heights | 8/4.8kV | 180F4 | Transformer 1834 on Waterford Cr isolated to replace leaking transformer. | Nepean | Scheduled Outage | Repair
7647 | 2005 | 11 | 22 | 0.85625 |  | 47 | 6 | 8 | Rideau Heights | 8/4.8kV | 180F4 | Transformer #NP003875 isolated at the front of 18 Eisenhower due to fly tap at the top of the switch broke at the hot line clamp | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9721 | 2006 | 11 | 24 | 0.14236 |  | 550 | 157 | 70 | RIDEAU HEIGHTS | 8/4.8kV | 180F4 | TE700 at 6 Yewfield had blown bushing and elbow. Transformer needs replacement | Nepean | Defective Equipment | Equipment Deterioration Due to Age
11758 | 2007 | 11 | 24 | 0.1875 |  | 56 | 93 | 100 | Rideau Heights | 8/4.8kV | 180F4 | Switch 973 red phase fuse blown on Prince of Wales at Cheridan due to the hot line clamp burning off at the riser pole. Line clamp repaired and fuse closed and holding, all customers restored. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
13664 | 2008 | 11 | 24 | 0.53125 |  | 90 | 9 | 6 | Rideau HTS | 8/4.8kV | 180F4 | Isolated transformer TP3443 at 17 Chesswood Crt for service up-grade | Nepean | Scheduled Outage | Preventive Maintenance
11790 | 2007 | 11 | 30 | 0.47014 |  | 68 | 5 | 4 | Rideau Heights | 8/4.8kV | 180F4 | Transformer #X36656 located at 30 Silverwood isolated due to squirrel contact. Crew had to replace arrestor & live line clamp & then refuse. | Nepean | Foreign Interference | Animal
19721 | 2011 | 12 | 14 | 0.86181 |  | 23 | 372 | 971 | Rideau Heights | 8/4.8kV | 180F4 | 180F4 opened by System office due to plane crash. 180F4 breaker closed, due to incorrect field verification of plane crash. 7F1 breaker opened. | Nepean | Foreign Interference | Vehicle
6080 | 2004 | 12 | 20 | 0.44722 |  | 16 | 219 | 823 | Rideau Heights | 8/4.8kV | 180F4 | Emergency repairs required to repair floating conductor at 118 MacFarlane. Due to extreme cold, -28 with a wind chill of -43. | Nepean | Adverse Weather | Extreme Ambient Temperature
15561 | 2009 | 12 | 27 | 0.022222 |  | 437 | 6183 | 849 | Rideau Heights | 8/4.8kV | 180F4 | 180F4 circuit opened. System Office was unaware due to failed relay communication. Circuit was patrolled. Breaker was closed, then OFD reported sparks Merivale at Pine Glen, After another patrol and breaker found open, attempt to close failed. Final patrol during daylight found branch on overhead section on Prince of Whales. 180F4 closed and held once interferance was removed. | Nepean | Tree Contacts | Inadequate Trimming
19764 | 2011 | 12 | 28 | 0.2125 |  | 8 | 129 | 971 | Rideau Heights | 8/4.8kV | 180F4 | 180F4 feeder auto reclose auto. Red and blue phase spike. Police and fire have no calls, breaker closed from SCADA. No calls of power out, Snow fall over night so possible snowplow. | Nepean | Unknown/Other | No Apparent Cause
4960 | 2004 | 4 | 3 | 0.28958 |  | 346 | 6 | 1 | Rideau Heights | 8/4.8kV | 180F5 | Customer owned transformer elbows & insert burnt off transformer # 2534. On call crew were called into replace elbow & insert under PO#7995. All power restored at 12:45 pm. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6454 | 2005 | 4 | 24 | 0.59167 |  | 68 | 3 | 3 | Rideau Hieghts | 8/4.8kV | 180F5 | Mano reports strap to NP4107 broken. Strap repair & fuse replaced, all power restored to normal. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6753 | 2005 | 6 | 17 | 0.39583 |  | 15 | 0 | 1 | Rideau Heights | 8/4.8kV | 180F5 | Repair a burning hot line clamp at switch 768 that feeds 1970 Merivale. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
12701 | 2008 | 6 | 20 | 0.44375 |  | 176 | 189 | 148 | Rideau Heights | 8/4.8kV | 180F5 | The 180F5 circuit is a normal open, but was carrying the 72F4 and 72F7 circuits, due to the loss of transformers at Merivale MS. The 180F5 tripped at the same time as the 180F4 trip. After patrol and sectionalizing, circuits were all restored. Cause of circuits initially tripped underfault, but cause was never determined. Cause of tripping is still under investigation. | Nepean | Unknown/Other
14761 | 2009 | 7 | 15 | 0.46181 |  | 27 | 138 | 481 | Rideau Heights | 8/4.8kV | 180F5 | 180F5 breaker auto trip. Suspect that the lead to switch S408 on the 180F4 feeder on Macfarlane burnt off and fell into the 180F5 feeder. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7128 | 2005 | 8 | 12 | 0.37708 |  | 87 | 14 | 10 | Barrhaven | 8/4.8kV | 180F5 | Isolation of TE1274 to repair burnt elbow connection. | Nepean | Scheduled Outage | Repair
11953 | 2008 | 1 | 18 | 0.40278 |  | 54 | 3 | 3 | Rideau Heights | 8/4.8kV | 180F6 | Transformer TE777 @ 1,2 Woodfield was isolated for replacement. | Nepean | Scheduled Outage | Preventive Maintenance
12049 | 2008 | 2 | 15 | 0.39028 |  | 298 | 35 | 7 | Rideau Heights | 8/4.8kV | 180F6 | TP5535 @ 3 Woodfield was isolated for crew to install new base. | Nepean | Scheduled Outage | Repair
14142 | 2009 | 4 | 3 | 0.48264 |  | 208 | 64 | 91 | Rideau Heights | 8/4.8kV | 180F6 | At 10:57am, SCADA indicated that the 180F6 breaker auto reclosed and locked out. Overhead crew reported a pole fire at 350 West Hunt Club at S1632 feeding TE3342, Shell Oil Yard. Crews restored power and isolated to allow to make repairs. All power restored to at 2:45pm. 180F6 Rideau Heights. ID#14142. | Nepean | Adverse Environment | Fire
15996 | 2010 | 4 | 26 | 0.45 |  | 37 | 4 | 7 | Rideau Heights | 8/4.8kV | 180F6 | Transformer #5604 located at 50 Bentley Ave opened by crew for a disc/rec for the electrician to repair the S/P | Nepean | Scheduled Outage | Construction
16059 | 2010 | 5 | 8 | 0.41667 |  | 30 | 4 | 7 | Rideau Heights | 8/4.8kV | 180F6 | X5604 at 44 Bentley was opened to allow crew to make new service connections. | Nepean | Scheduled Outage | Construction
5174 | 2004 | 5 | 18 | 0.34167 |  | 108 | 13 | 7 | 180 | 8/4.8kV | 180F6 | Tx NP595 at 78 Jamie was off at 08:12 & power restored to 7 customers @ 10:00 due to blown arrestor. As per dispatch. | Nepean | Adverse Weather | Lightning
12526 | 2008 | 6 | 2 | 0.33264 |  | 77 | 1 | 1 | Rideau Heights |  | 180F6 | Replaced broken switch feeding transformer X5239 at 25 Gifford St | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16507 | 2010 | 7 | 21 | 0.53819 |  | 15 | 1 | 2 | Rideau Heights | 8/4.8kV | 180F6 | Isolated transformer X5605 at 53 Bentley Ave to disconnect secondary service that was damaged by a truck | Nepean | Foreign Interference | Vehicle
18789 | 2011 | 7 | 21 | 0.64167 |  | 54 | 1 | 1 | Rideau Heights | 8/4.8kV | 180F6 | Crew isolated TE2089 to repair defective cutout. | Nepean | Defective Equipment
3805 | 2003 | 7 | 23 | 0.52778 |  | 38 | 4 | 6 | Rideau Hts | 8/4.8kV | 180F6 | Transformer 5191 @ 50 Bentley taken out of service to replace pole reported hit and leaning at 10:53 from a vehicle accident. 6 customers affected. | Nepean | Foreign Interference | Vehicle
3811 | 2003 | 7 | 28 | 0.63542 |  | 57 | 2 | 2 | Rideau Hts. | 8/4.8kV | 180F6 | Leaking transformer at 1857 Merivale, TE2095, was changed. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
7307 | 2005 | 9 | 10 | 0.49306 |  | 5 | 0 | 1 | Rideau Hieghts | 8/4.8kV | 180F6 | D. Jones reports TE2932 isolated to replace defective arrester. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17063 | 2010 | 10 | 5 | 0.86111 |  | 270 | 4 | 1 | Rideau Hts | 8/4.8kV | 180F6 | TE1448 at 1867 Merivale was isolated to replace leaking Tx & clean up contaminated soil. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15250 | 2009 | 10 | 12 | 0.38819 |  | 127 | 2 | 1 | Rideau hieghts | 8/4.8kV | 180F6 | crew replaced faulty cutout @ 11 Tristan crt. On S136 feeding transformer TE2351. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
15362 | 2009 | 11 | 8 | 0.33333 |  | 202 | 13 | 4 | Rideau Heights | 8/4.8kV | 180F6 | Crew isolated TP6924 at 350 Huntclub to relocate cable to new pole, 4 customers affected. | Nepean | Scheduled Outage
7611 | 2005 | 11 | 14 | 0.54167 |  | 60 | 1 | 1 | RIDEAU | 8/4.8kV | 180F6 | BURNT HOTLINE CLAMP @ SHELL ON HUNTCLUP @ TE2932 OFF S835 3 PHASE. D. MCKAY REPLACED HOTLINE CLAMPS ON ALL 3 PHASES POWER RESTORED. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6023 | 2004 | 12 | 10 | 0.95139 |  | 8 | 0 | 1 | Rideau Heights | 8/4.8kV | 180F6 | Transformer Tx 1811 isolated to repair defective clamp at dip pole. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
6025 | 2004 | 12 | 10 | 0.94931 |  | 4 | 10 | 150 | Rideau Hieghts | 8/4.8kV | 180F6 | Rideau Hgts 180F6 auto/trip, heavy snow fall & high winds, defective line clamp at S1382 as well as a defective switch at 180F6-CA. | Nepean | Defective Equipment
6029 | 2004 | 12 | 10 | 0.95972 |  | 133 | 332 | 150 | Rideau Hieghts | 8/4.8kV | 180F6 | 180F6 bkr opened due to single phasing after auto/reclose. | Nepean | Defective Equipment
19731 | 2011 | 12 | 17 | 0.083333 |  | 8 | 0 | 2 | Rideau Heights | 8/4.8kV | 180F6 | TP5218 at 1840 Merivale Rd (Canadian Tire) isolated to remove secondary cable supply to A&W | Nepean | Scheduled Outage | Construction
19732 | 2011 | 12 | 17 | 0.097917 |  | 134 | 4 | 2 | Rideau Heights | 8/4.8kV | 180F6 | TP 8396 at 1840 Merivale Rd (Marks Work Wear) isolated to allplt new secondary cable to A&W to be connected. | Nepean | Scheduled Outage | Construction
14330 | 2009 | 5 | 9 | 0.37986 |  | 130 | 50 | 23 | Bilberry | 27.6/16kV | 1895 | White phase switch to Transformer 973 on Carriere found blown due to animal contact, which also caused G279W to blow, and RX2019 auto reclose. Both switches refused and closed to restore power. | Gloucester | Foreign Interference | Animal
3380 | 2003 | 4 | 28 | 0.084028 |  | 444 | 44 | 6 | Parkwood Hills | 8/4.8kV | 190 F5 | S. Muldoon reports a defective cable has caused a fuse at SE8 to blow. This is the red phase feeding transformer TE573 (1208 to 1214 Meadowlands Drive). Temp repairs made te573 now being feed via TE574 blue phase. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
3234 | 2003 | 3 | 8 | 0.91667 |  | 329 | 3220 | 1000 | Parkwood Hills | 8/4.8kV | 190F1 | M.Brown (24/7) reports insulator failed primary down accrossed Tap at S420.M. Brown reports unable to close S229 due to switch not operating properly. On-call crews dispatched to repair O/H. | Nepean | Adverse Weather | Snow
10175 | 2007 | 3 | 26 | 0.40625 |  | 50 | 1 | 1 | Parkwood Hills | 8/4.8kV | 190F1 | Crew replaced broken switch 1359 feeding transformer TE1725 at 1454 Merivale Rd | Nepean | Defective Equipment | Equipment Deterioration Due to Age
10236 | 2007 | 4 | 11 | 0.37847 |  | 10 | 0 | 3 | Parkwood Hills | 8/4.8kV | 190F1 | Isolated transformer 11 at 1536 Merivale Rd and re-located to another phase | Nepean | Scheduled Outage | Load Shedding
10987 | 2007 | 8 | 1 | 0.61528 |  | 385 | 13 | 2 | Parkwood Hills | 8/4.8kV | 190F1 | A Person who was not identified, due to leaving the scene drove a metal spike(sign post) into the 8kV cable feeding transformer TE891 and TE2024 at 1493 Merivale. Cable was repaired and power restored. | Nepean | Foreign Interference | Dig-in
9340 | 2006 | 9 | 29 | 0.39583 |  | 87 | 9 | 6 | Parkwood Hills | 8/4.8kV | 190F1 | Transformer #NP180 located at 21 Hilliard Ave isolated to replace SW/Arrester. PC10A#1475 | Nepean | Scheduled Outage | Repair
19786 | 2012 | 1 | 5 | 0.43056 |  | 50 | 4 | 5 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer #X33233 located at 5 Rockfield Cres opened by crew to transfer plant | Nepean | Scheduled Outage | Construction
19795 | 2012 | 1 | 6 | 0.39583 |  | 210 | 35 | 10 | Parkwood Hills | 8/4.8kV | 190F2 | Isolated transformer X33233 at 5 Rockfield Cres to transfer hydro plant to new pole | Nepean | Scheduled Outage | Construction
13883 | 2009 | 1 | 21 | 0.40278 |  | 180 | 6 | 2 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer TE566 at 1185 Meadowlands isolated for replacement. | Nepean | Scheduled Outage | Construction
4781 | 2004 | 2 | 11 | 0.51389 |  | 70 | 7 | 6 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer 0998 at 24 Argue Dr new fuse installed after animal contact. | Nepean | Foreign Interference | Animal
7936 | 2006 | 2 | 17 | 0.40972 |  | 110 | 1192 | 650 | Parkwood Hills | 8/4.8kV | 190F2 | Wayne Reid found the O/h slapping together on Meadowlands. | Nepean | Adverse Weather | Wind
7942 | 2006 | 2 | 17 | 0.5 |  | 24 | 260 | 650 | Parkwood Hills | 8/4.8kV | 190F2 | With high winds the primary O/H slap together on Meadowlands causing the circuit to open. | Nepean | Adverse Weather | Wind
7950 | 2006 | 2 | 20 | 0.10208 |  | 349 | 52 | 9 | Parkwood Hills | 8/4.8kV | 190F2 | Customer called said he seen no power @ 51 Argue ave. Nepean. Crew to check transformer # 3465. CREW says transformer is blown and needs replacement @ 1112 51 Argue ave.. | Nepean | Foreign Interference | Foreign Object
4825 | 2004 | 2 | 25 | 0.40486 |  | 87 | 80 | 55 | Parkwood Hills | 8/4.8kV | 190F2 | VE11 at 1150 Meadowlands Rd isolated for installation of new underground cable. 55 customers. | Nepean | Scheduled Outage | Construction
7967 | 2006 | 2 | 25 | 0.2375 |  | 6 | 1 | 8 | Parkwood Hills | 8/4.8kV | 190F2 | Overhead transformer 544 was interrupted to diconnect service to 28 Phillip due to a house fire. | Nepean | Adverse Environment | Fire
17654 | 2011 | 2 | 28 | 0.63194 |  | 105 | 206 | 162 | Parkwood Hills | 8/4.8kV | 190F2 | A blown cut-out & arrestor at 66 Argue, Tx X35850 caused S312 to blow. S312 replaced restoring most customers. Arrestor & cut-out @ X35850 replaced restoring remainder of customers. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10095 | 2007 | 3 | 6 | 0.44792 |  | 1545 | 52 | 2 | Parkwood Hills | 8/4.8kV | 190F2 | TE304 supplying the Homesense & Staples stores at Merivale & Meadowlands was isolated due to flooding in the customers building. | Nepean | Adverse Environment | Flooding
14045 | 2009 | 3 | 12 | 0.36806 |  | 30 | 2 | 5 | PARKWOOD HILLS | 8/4.8kV | 190F2 | Transformer X33383 at 12 Greenwich isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
8050 | 2006 | 3 | 22 | 0.51736 |  | 55 | 6 | 6 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer NP1199 at 29 Barlyn St was isolated to replaced triplex service | Nepean | Scheduled Outage | Repair
3293 | 2003 | 3 | 23 | 0.63194 |  | 20 | 2 | 5 | Parkwood | 8/4.8kV | 190F2 | On call crew reports transformer #2504 isolated to replace defective secondary service to 38 Argue St. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
14087 | 2009 | 3 | 23 | 0.5625 |  | 90 | 12 | 8 | Parkwood Hills | 8/4.8kV | 190F2 | Isolated transformer NP4138 at 10 Attwood Cres service repair | Nepean | Scheduled Outage | Repair
17774 | 2011 | 3 | 23 | 0.40972 |  | 185 | 12 | 4 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer X33246 at 13 Phillip Dr isolated for PCB change | Nepean | Scheduled Outage | Preventive Maintenance
14108 | 2009 | 3 | 28 | 0.7 |  | 60 | 9 | 9 | Parkwood Hills | 8/4.8kV | 190F2 | At 24 Attwood transformer X33224 was isolated to allow crew to repair defective hot line clamp. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17791 | 2011 | 3 | 28 | 0.39931 |  | 117 | 10 | 5 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer #X36237 located at 86 Argue Dr opened by crew to change connections on a 3 phase transformer. | Nepean | Scheduled Outage | Construction
8077 | 2006 | 3 | 29 | 0.48611 |  | 110 | 7 | 4 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer #3233 located at 22 Lyall isolated to change a cut-out | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8078 | 2006 | 3 | 29 | 0.48611 |  | 110 | 11 | 6 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer #1288 located at 26 Lyall isolated to change a cut-out | Nepean | Defective Equipment
3334 | 2003 | 4 | 12 | 0.25694 |  | 90 | 15 | 10 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer fuse pulled apart at transformer#374 on Ashburn Drive. Fuse was replaced and closed, full power was restored. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
8139 | 2006 | 4 | 12 | 0.39583 |  | 120 | 16 | 8 | Parkwood Hills | 8/4.8kV | 190F2 | Jim Millar opened transformer NP3469 at 1120 Falaise to replace an open wire service. | Nepean | Scheduled Outage | Repair
20343 | 2012 | 4 | 18 | 0.38681 |  | 451 | 83 | 11 | Parkwood Hills | 8/4.8kV | 190F2 | At transformer TP9231 at 49 Rockfild was isolated to allow crews to perform soil remediation. 11 customers were affected for minurtes. Parkwood Hills (190F2) ID#20343 | Nepean | Scheduled Outage | Preventive Maintenance
17973 | 2011 | 4 | 20 | 0.33542 |  | 162 | 258 | 158 | Parkwoodhills | 8/4.8kV | 190F2 | 190F2-B O/H cable section @ Falaise East and Leona to switch S916 was isolated to allow crew to repair downed condutor between Falaiase East of Leona to switch S916. High winds in Ottawa area. Parkwood Hill (190F2) | Nepean | Adverse Weather | Wind
20446 | 2012 | 5 | 2 | 0.38542 |  | 405 | 54 | 8 | Parkwood Hills | 8/4.8kV | 190F2 | TP9230 at 26 Seymour soil remediation. | Nepean | Scheduled Outage | Repair
12515 | 2008 | 5 | 31 | 0.67639 |  | 178 | 6 | 2 | Parkwood Hills | 8/4.8kV | 190F2 | transformer 3047 @ fisher and Malibu opened during heavy rain and lightning avtivity. Crew refused and closed. | Nepean | Adverse Weather
3507 | 2003 | 6 | 1 | 0.89583 |  | 25 | 0 | 1 | parkwood hills | 8/4.8kV | 190F2 | S-598 white phase fuse blew feeding VE11 at 1150 Meadowlands. Crew refused after meggaring the cable and fuse held. Cause unkown. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3509 | 2003 | 6 | 2 | 0.40069 |  | 417 | 7 | 1 | Parkwood Hilss | 8/4.8kV | 190F2 | G. Morrice reports white phase cable is now repaired. Cable was blown at base of pole. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
8565 | 2006 | 6 | 21 | 0.38889 |  | 220 | 29 | 8 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer #NP003467 located at 17 Seymour isolated due to upgrading system neutral on secondary & installing customer triplex | Nepean | Scheduled Outage | Preventive Maintenance
3632 | 2003 | 6 | 29 | 0.28333 |  | 15 | 2 | 10 | Parkwood Hills | 8/4.8kV | 190F2 | Crew took xfmr out of service to repair triplex service to 7 Greenwich. 10 customers on Greenwich affected. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5520 | 2004 | 7 | 18 | 0.89583 |  | 120 | 32 | 16 | Parkwood Hills | 8/4.8kV | 190F2 | Secondary off of transformer Tx 4548 at 48 Kilmory was damaged and had to be replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18762 | 2011 | 7 | 18 | 0.05 |  | 190 | 3357 | 1060 | Parkwood Hills |  | 190F2 | The Parkwood Hills 190F2 circuit opened during the wind and lightning storm. Breaker was closed from SCADA and reopen. Crew partolled circuit and found nothing. System closed breaker and held . All load was restored | Nepean | Adverse Weather
16733 | 2010 | 8 | 13 | 0.70556 |  | 111 | 9 | 5 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer #NP2505 located at 18 Argue opened up due to defective/old fuse | Nepean | Defective Equipment | Equipment Deterioration Due to Age
14948 | 2009 | 8 | 15 | 0.35417 |  | 244 | 180 | 46 | Parkwood Hills | 8/4.8kV | 190F2 | S614 blue phase on Meadowlands near Fisher opened with no visible cause making the suspected cause a cable fault. Inspection and testing finally came to the crew refusing the S614 blue phase at which time the faulty switch was discovered and repaired. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7213 | 2005 | 8 | 25 | 0.44097 |  | 145 | 19 | 8 | Parkwood Hills | 8/4.8kV | 190F2 | Isolated Transformer # 5212 at 68 Mulvagh to do Mtce | Ottawa | Scheduled Outage | Preventive Maintenance
19181 | 2011 | 9 | 15 | 0.41667 |  | 305 | 407 | 80 | Parkwood Hills | 8/4.8kV | 190F2 | A section of 190F2 o/h line from S28980 was isolated to replace defective poles, crossarms & riser switches. Homes affected in the Shadetree , Farmgate, Viewmount Dr area | Nepean | Scheduled Outage | Repair
11339 | 2007 | 9 | 19 | 0.9375 |  | 300 | 75 | 15 | Parkwood Hills | 8/4.8kV | 190F2 | Defective O/H transformer replaced by on -call crew at 1269 Meadowlands. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4116 | 2003 | 9 | 21 | 0.8875 |  | 52 | 9 | 10 | Parkwood Hills | 8/4.8kV | 190F2 | Service burned down feeding 55 Wigan Dr. requiring isolation of Transformer # 4397 to replace the service and renew the rest of the connections. | Ottawa | Unknown/Other | No Apparent Cause
7364 | 2005 | 9 | 22 | 0.41667 |  | 28 | 6 | 12 | Parkwood Hills | 8/4.8kV | 190F2 | Isolated transformer # 1134 at 41 Hilliard to change the Service wires | Ottawa | Scheduled Outage | Preventive Maintenance
13342 | 2008 | 10 | 8 | 0.38194 |  | 325 | 32 | 6 | Parkwood hills | 4.16kV | 190F2 | 190F2 circuit was isolated from S330 to end of line to allow crews to change Hydro Pole. | Nepean | Scheduled Outage | Construction
9416 | 2006 | 10 | 12 | 0.325 |  | 57 | 7 | 7 | Parkwood Hills | 8/4.8kV | 190F2 | Fuse to transformer NP1198 at 1159 Normandy Cres was found broken Replaced the fuse restored power | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15299 | 2009 | 10 | 24 | 0.57292 |  | 125 | 15 | 7 | Parkwood Hills | 12/7.2kV | 190F2 | Transformer #X36137 located at 24 Goodwin isolated due to vines & nest on the transformer | Nepean | Tree Contacts | Inadequate Trimming
13513 | 2008 | 10 | 29 | 0.13819 |  | 206 | 5380 | 1567 | PARKWOOD HILLS | 8/4.8kV | 190F2 | Restored circuit with OTO # RHHoct29/08: Closed S645, S633 and 190F2 CB | Nepean | Adverse Weather
19527 | 2011 | 11 | 4 | 0.43958 |  | 307 | 138 | 27 | Parkwood Hills | 8/4.8kV | 190F2 | Overhead section fed from S725 on Charkay St. Was isolated to allow crews to replace a pole | Nepean | Scheduled Outage | Repair
19529 | 2011 | 11 | 4 | 0.52083 |  | 30 | 2 | 5 | Parkwood Hills | 8/4.8kV | 190F2 | Trans X36132 at 23 Argue Dr was isolated in order to do service work | Nepean | Scheduled Outage
13567 | 2008 | 11 | 5 | 0.43403 |  | 425 | 14 | 2 | Parkwood Hills | 8/4.8kV | 190F2 | TE568 at 1163 Meadowlands isolated to allow crew to replace leaking xfmr and install new base. 2 customers | Nepean | Scheduled Outage
15398 | 2009 | 11 | 17 | 0.38889 |  | 340 | 397 | 70 | Parkwood | 8/4.8kV | 190F2 | Section of line at Inverness & Charkay isolated for forestry crews to trim trees that were in close proximity to the primary conductor. | Nepean | Scheduled Outage | Preventive Maintenance
15418 | 2009 | 11 | 24 | 0.40625 |  | 126 | 6 | 3 | Parkwood Hills | 8/4.8kV | 190F2 | Isolated transformer TE89 at 51 Rockfield Cres to replace pedestal | Nepean | Scheduled Outage | Construction
15421 | 2009 | 11 | 25 | 0.37847 |  | 123 | 23 | 11 | PARKWOOD HILLS | 8/4.8kV | 190F2 | transformer NPTE0089 at 47 Rockfield isolated for pedestal change | Ottawa | Scheduled Outage | Preventive Maintenance
13668 | 2008 | 11 | 26 | 0.43056 |  | 310 | 93 | 18 | Parkwood Hills | 8/4.8kV | 190F2 | TE570 at 1155 Meadowlands was isolated to replace transformer & install new base. | Nepean | Scheduled Outage | Repair
13693 | 2008 | 12 | 2 | 0.43125 |  | 159 | 16 | 6 | Parkwood Hills | 8/4.8kV | 190F2 | Isolation of TE569 at 1171 Meadowlands Dr for transformer replacement. | Nepean | Scheduled Outage
13697 | 2008 | 12 | 3 | 0.41319 |  | 153 | 69 | 27 | Parkwood Hills | 8/4.8kV | 190F2 | TE572 at 1161 Meadowlands was replace and nomenclature was updated to TP6612 | Nepean | Scheduled Outage
19692 | 2011 | 12 | 6 | 0.38889 |  | 218 | 51 | 67 | Parkwood Hills DS | 8/4.8kV | 190F2 | TE90, TE91, TE92 & TE93 had to be turned off via S728 to allow crews to isolate TE89. These transformers are all live front transformers. TE89 was isolated to allow Hydro Ottawa crews to replace a leaking transformer. | Nepean | Scheduled Outage | Repair
19705 | 2011 | 12 | 8 | 0.4125 |  | 156 | 21 | 8 | Parkwood hills | 8/4.8kV | 190F2 | TE88 at 26 Seymour was isolated to replace leaking transformer. | Nepean | Scheduled Outage | Repair
19759 | 2011 | 12 | 22 | 0.46528 |  | 10 | 1 | 8 | Parkwood Hills | 8/4.8kV | 190F2 | Transformer #4138 located at 1130 Deer park opened by crew to check voltage | Nepean | Scheduled Outage | Construction
5055 | 2004 | 4 | 25 | 0.87708 |  | 24 | 0 | 1 | Parkwood Hills | 8/4.8kV | 190F3 | Dave guy reports hot line clamp at S895 is arcing badly. Crew required to unload VE31 to isolate S895 line clamp. To replace clamp at 20 Chesterton Towers. Raining at the time of call. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
10777 | 2007 | 7 | 3 | 0.38681 |  | 231 | 216 | 56 | Parkwood hills | 8/4.8kV | 190F3 | A section on overhead isolated to change hydro pole. On Mulvaugh st @ Charkay st. | Nepean | Scheduled Outage | Construction
3917 | 2003 | 8 | 19 | 0.37083 |  | 366 | 6 | 1 | parkwood Hills | 8/4.8kV | 190F3 | Contractor digging a pool damaged two phase supplying Sir Winstin Churchhill School | Nepean | Foreign Interference | Dig-in
7207 | 2005 | 8 | 24 | 0.375 |  | 337 | 168 | 30 | Parkwood Hills | 12/7.2kV | 190f3 | O/H circuit isolated to replace pole. | Nepean | Scheduled Outage | Construction
19061 | 2011 | 8 | 31 | 0.39583 |  | 180 | 57 | 19 | Parkwood Hills | 8/4.8kV | 190F3 | Transformer NP00353 at 12 Assiniboine Dr isolated to replace transformer - leaker | Nepean | Scheduled Outage | Repair
7325 | 2005 | 9 | 14 | 0.40972 |  | 70 | 13 | 11 | Parkwood Hills | 8/4.8kV | 190F3 | Transformer TE120 on Chesterton isolated to make tx repairs. | Nepean | Scheduled Outage | Repair
7330 | 2005 | 9 | 15 | 0.40556 |  | 110 | 18 | 10 | Parkwood | 8/4.8kV | 190F3 | TE 121 live front transformer replaced with dead front at Chesterton and Southview. | Nepean | Scheduled Outage | Construction
7933 | 2006 | 2 | 17 | 0.40278 |  | 55 | 477 | 520 | Parkwood Hills | 8/4.8kV | 190F4 | Found tree in wires on Leaver St. causing the circuit to trip. | Nepean | Adverse Weather | Wind
10255 | 2007 | 4 | 14 | 0.83333 |  | 60 | 10 | 10 | Parkwood Hills | 8/4.8kV | 190F4 | Tx # 804 at rear of 1179 Deerpark opened to replace secondary connections at pole. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
5123 | 2004 | 5 | 9 | 0.81111 |  | 47 | 47 | 60 | Parkwood Hills | 8/4.8kV | 190F4 | 26 Willeth reported sparking wires in backyard. Switch 352 opened and hot line clamp at Fisher Heights School opened for isolation to allow repairs. Corner pole connections replaced. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
5182 | 2004 | 5 | 19 | 0.53819 |  | 111 | 6 | 3 | Parkwoodhills | 8/4.8kV | 190F4 | TE546 was isolated that feeds apartment building 25,27,& 29 on Eleanor because of a leaking transformer. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
5214 | 2004 | 5 | 27 | 0.39028 |  | 243 | 142 | 35 | Parkwood Hills | 8/4.8kV | 190F4 | Isolate transformer 546 at 25 Eleanor to remove contaminated soil from a previse shut down. | Nepean | Scheduled Outage | Repair
5225 | 2004 | 5 | 30 | 0.30278 |  | 44 | 4 | 6 | Parkwood Hills | 8/4.8kV | 190F4 | Transformer fuse found blown due to an animal. Crews refused transformer restoring power. | Nepean | Foreign Interference | Animal
3810 | 2003 | 7 | 28 | 0.42014 |  | 44 | 4 | 6 | Parkwood Hills | 8/4.8kV | 190F4 | Transformer #790 behind 1149 Deer Park taken out of service to make it safe to disconnect #59 Hilliard. | Nepean | Foreign Interference
3871 | 2003 | 8 | 7 | 0.39167 |  | 74 | 49 | 40 | Parkwood Hills | 8/4.8kV | 190F4 | Overhead circuit section isolated to repair conductor. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13259 | 2008 | 9 | 18 | 0.42639 |  | 272 | 54 | 12 | Parkwood Hills | 8/4.8kV | 190F4 | TP5511 isolated to allow replacement on PCB transformer at 14 Warbonnet. | Nepean | Scheduled Outage | Construction
9333 | 2006 | 9 | 28 | 0.36806 |  | 3 | 0 | 6 | Parkwood Hills | 8/4.8kV | 190F4 | Isolated transformer NP180 at 23 Hilliard Ave to cut blown arrester clear | Nepean | Defective Equipment | Imminent Equipment Failure Detected
9691 | 2006 | 11 | 20 | 0.39583 |  | 530 | 88 | 10 | Parkwood Hills | 8/4.8kV | 190F4 | TP2609 on Briardale Cres. isolated to allow contractor to move transformer and base. | Nepean | Scheduled Outage | Preventive Maintenance
9793 | 2006 | 12 | 4 | 0.43056 |  | 25 | 2 | 4 | Parkwood Hills | 8/4.8kV | 190F4 | Isolated transformer NP3053 at 12 Oakwood Ave to repair overhead service | Nepean | Adverse Weather | Ice Storm
11841 | 2007 | 12 | 13 | 0.40625 |  | 60 | 8 | 8 | Parkwood Hills | 8/4.8kV | 190F4 | Transformer #X35990 located at 32 Gilbey isolated due to service upgrade. | Nepean | Scheduled Outage | Preventive Maintenance
9893 | 2006 | 12 | 30 | 0.7 |  | 55 | 70 | 76 | Parkwoodhills | 8/4.8kV | 190F4 | Fused switch S446 at 41 Hillard in Nepean malfunctioned and burnt up, customers restored from another location. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19778 | 2012 | 1 | 2 | 0.44583 |  | 460 | 276 | 36 | Parkwoodhill | 8/4.8kV | 190F5 | Switch S585 @ 18 Hogan / Nepean openened due to defective underground cable. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
19782 | 2012 | 1 | 4 | 0.46875 |  | 40 | 8 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer #X35814 located at 63 Inverness Ave opened by crew to replace switch | Nepean | Defective Equipment | Imminent Equipment Failure Detected
19797 | 2012 | 1 | 6 | 0.57778 |  | 461 | 353 | 46 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer TE575 at 20 Hogan Street was isolated to allow crew to repair d a defective cable. Parkwood Hills (190F5) ID# 19797 | Nepean | Defective Equipment
13845 | 2009 | 1 | 7 | 0.41528 |  | 150 | 78 | 31 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer TE581 (TP6625) @ 1160 Meadowlands was isolated for crews to upgrade from live front to dead front elbow connected. Installed new nomenclature on the switch and transformer. | Ottawa | Scheduled Outage | Preventive Maintenance
4751 | 2004 | 2 | 2 | 0.39583 |  | 39 | 8 | 12 | Parkwood hills | 8/4.8kV | 190F5 | Tx 4940 @ 43 Tiverton was opened to renew connections. 12 customers affected | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6178 | 2005 | 2 | 4 | 0.5625 |  | 80 | 133 | 100 |  | 13.2kV | 190F5 | Changed bad connector at Transformer | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4793 | 2004 | 2 | 15 | 0.85417 |  | 1444 | 24 | 1 | Parkwood Hill | 8/4.8kV | 190F5 | White phase cable section between S721 & VE23 faulted. On Call crews to repair cable. MDF comments - PVC 9kV Cable Splice Failure. Cable was dug into this summer and spliced to repair, suspect damage due to origonal dig in. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17609 | 2011 | 2 | 18 | 0.90208 |  | 21 | 288 | 824 | Parkwood Hills | 8/4.8kV | 190F5 | 190F5 breaker tripped. High winds, and snow. 190F5 closed by system and all load restored. | Nepean | Adverse Weather
17624 | 2011 | 2 | 19 | 0.73194 |  | 61 | 12 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer on back yard of 65 Ashburn open to for oncall to repalce triplex damaged from fallen tree. Tree still needs clean-up | Nepean | Tree Contacts | Tree Limb Fallen
13998 | 2009 | 2 | 22 | 0.88889 |  | 50 | 7 | 8 | PARKWOOD HILLS | 8/4.8kV | 190F5 | At 21:08 customers at 3 Sutton Place called in with complaints of sparking wires and flashing in rear of their residence. 24-7 reports secondary bushing on transformer NPOO1155 was glowing red. 24-7 repaired secondary connections and tightened bushings and all power restored to customers at 22:10. Parkwood Hills (190F)5) (RED PHASE). ID#13998. | Nepean | Unknown/Other
14005 | 2009 | 2 | 25 | 0.37222 |  | 511 | 34 | 4 | Parkwoods Hills | 8/4.8kV | 190F5 | Transformer TP6614 @ 30 Northview was isolated for contractor to relocate secondaries, and hydro crew to recompact granular under base. | Nepean | Scheduled Outage | Construction
15746 | 2010 | 2 | 25 | 0.67153 |  | 788 | 13 | 1 | Parkwood Hills | 8/4.8kV | 190F5 | on call crew replaced defective transformers at 10 coral ave in Nepean. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
17651 | 2011 | 2 | 28 | 0.46875 |  | 46 | 632 | 824 | Parkwood Hills | 8/4.8kV | 190F5 | A broken insulator on 190F5 2 spans N. of riser pole caused 190F5 & F6 cct's to trip. Temporary repairs were made & both cct's restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10100 | 2007 | 3 | 7 | 0.46667 |  | 19 | 4 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | While switching to isolate a section of primary cable, the insert at TE3150 on Briardale ave came apart. The transformer was isolated & repaired . | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17705 | 2011 | 3 | 12 | 0.27222 |  | 76 | 8 | 6 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer X33451 was isolated to allow crew to repair secondary at 11 Sunnycrest Drive. | Nepean | Defective Equipment
17715 | 2011 | 3 | 15 | 0.39583 |  | 252 | 17 | 4 | Parkwood Hills | 8/4.8kV | 190F5 | Trans at 27 Kesler was isolated for PCB change out | Nepean | Scheduled Outage | Preventive Maintenance
20166 | 2012 | 3 | 15 | 0.38194 |  | 70 | 5 | 4 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer #X33911 located at 27 Sunnycrest opened by crew to change connections | Nepean | Scheduled Outage | Construction
20169 | 2012 | 3 | 15 | 0.49306 |  | 39 | 5 | 8 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer #X33211 located at 29 Higwood opened by crew to change a service | Nepean | Scheduled Outage | Construction
17729 | 2011 | 3 | 18 | 0.38542 |  | 130 | 22 | 10 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer X33448 at 29 Barlyn Ave. Isolated to allow for PCB change | Nepean | Scheduled Outage | Preventive Maintenance
20177 | 2012 | 3 | 18 | 0.64861 |  | 100 | 20 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | BROKEN PORCELAIN CUTOUT AT REAR OF 1297 MEADOWLANDS that feeds trans X35936. ON X35936 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17759 | 2011 | 3 | 22 | 0.375 |  | 180 | 15 | 5 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer #X32690 located at 38 Hilliard Ave opened by crew due to PCB removal | Nepean | Scheduled Outage | Construction
17779 | 2011 | 3 | 24 | 0.375 |  | 260 | 56 | 13 | parkwood Hills | 8/4.8kV | 190F5 | Transformer was isolated to allow crews to remove PCB's | Nepean | Scheduled Outage
8073 | 2006 | 3 | 29 | 0.33542 |  | 321 | 155 | 29 | Parkwood Hills | 8/4.8kV | 190F5 | 190F5 auto-reclosed due to a truck contacting the over head. Fault caused S360 @ Farlane in Nepean to open on two cutouts. Power out to 29 customers. Crew replacing S360 cutouts. TE2976 three phase pad feeding seniors home affected. | Nepean | Foreign Interference | Vehicle
15880 | 2010 | 4 | 2 | 0.93403 |  | 115 | 18 | 20 | Parkwood Hills | 8/4.8kV | 190F5 | Defective transformer at 43 Hilliard, customers backfed from adjacent transformer at 49 Hilliard until equipment can be replaced first thing Friday morning. Outage expanded to make connection to other transformer bus. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
15882 | 2010 | 4 | 2 | 0.41667 |  | 180 | 33 | 20 | PARKWOOD HILLS DS | 8/4.8kV | 190F5 | Transformer X32691 at 1131 Deer Park Rd (located at rear of #43) isolated to allow for transformer change | Nepean | Scheduled Outage | Repair
8107 | 2006 | 4 | 5 | 0.42361 |  | 9 | 1 | 4 | Parkwood | 8/4.8kV | 190F5 | Isolated transformer NP802 at 4 Newbury to replace triplex service | Nepean | Scheduled Outage | Preventive Maintenance
15890 | 2010 | 4 | 5 | 0.34028 |  | 576 | 403 | 42 | Parkwood | 8/4.8kV | 190F5 | Defective red phase cable between SE8 & TE573. Customers affected at 1208 , 1210 & 1214 Meadowlands. Oncall cable crew repaired the fault as cable section was radial with no alternate feed to TE573. | Nepean | Defective Equipment
8128 | 2006 | 4 | 11 | 0.024306 |  | 6 | 1 | 8 | Parkwood Hills | 8/4.8kV | 190f5 | Transformer 4156 opened to safley remove sizzling meter at 68 Hilliard. 8 customers affected. | Nepean | Defective Equipment
14168 | 2009 | 4 | 12 | 0.15972 |  | 165 | 38 | 14 | Parkwood Hills | 8/4.8kV | 190F5 | At 3:50am customers in the area of Beaver Ridge in Nepean, called in with no power calls, crews found a broken switch cut-out. Switch was replaced and 14 customers were affected for 165min and power was restored at 6:35am. (Parkwood Hills 190F5) ID#14168. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20351 | 2012 | 4 | 18 | 0.78542 |  | 120 | 18 | 9 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer X32686 at 105 HILLIARD AVE refused after animal contact | Ottawa | Foreign Interference | Animal
3384 | 2003 | 4 | 28 | 0.59375 |  | 12 | 1 | 6 | Parkwood Hills | 8/4.8kV | 190F5 | TE573 isolated to restore out-of-phase transformer to normal. Customers notified to outage. | Nepean | Scheduled Outage | Repair
8210 | 2006 | 5 | 1 | 0.38542 |  | 43 | 3 | 4 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer #NP004273 located at 30 Barlyn isolated due to service removal for demolition | Nepean | Scheduled Outage | Construction
14273 | 2009 | 5 | 1 | 0.16042 |  | 353 | 4526 | 1330 | Parkwoodhills | 8/4.8kV | 190F5 | Pole Fire at Meadowlands and Tiverton, and S495 switch burnt up. Pole re-fastened and switch replaced. | Nepean | Adverse Environment | Fire
14282 | 2009 | 5 | 1 | 0.54583 |  | 15 | 25 | 100 | Parkwood Hills | 8/4.8kV | 190F5 | S607R phase had blown open due to earlier pole fire. SE8 to S607 opened, to verify S607 cable and cable was good. S607 RWB fuses replaced and switches closed to restore power. | Nepean | Adverse Environment | Fire
8245 | 2006 | 5 | 6 | 0.58333 |  | 340 | 210 | 37 | Parkwood Hills | 8/4.8kV | 190F5 | Pole fire at 30 Beaverton. S467R opened for isolation affecting 37 customers on Beaverton and Higwood. Top of pole cut off and bolted on new crossarm and hardware. | Nepean | Adverse Environment | Fire
20544 | 2012 | 5 | 20 | 0.38542 |  | 399 | 113 | 17 | Parkwood Hills | 8/4.8kV | 190F5 | S222 at 15 Leaver opened due to tree limb on O/H primary at rear of 15 Leaver. | Nepean | Tree Contacts | Tree Limb Fallen
12466 | 2008 | 5 | 23 | 0.41389 |  | 100 | 3 | 2 | Parkwood Hills | 8/4.8kV | 190F5 | TE576 at 28 Hogan St was isolated to allow crews to replace flashed transformer. | Nepean | Scheduled Outage | Repair
18199 | 2011 | 5 | 23 | 0.16111 |  | 58 | 8 | 8 | Parkwood Hills | 8/4.8kV | 190F5 | Animal contact at switch S607 caused one fuse to blow. | Nepean | Foreign Interference | Animal
20563 | 2012 | 5 | 23 | 0.80417 |  | 4 | 114 | 1715 | Parkwood Hills | 8/4.8kV | 190F5 | The Parkwoodhill 190F5 auto reclosed and locked out. Police and Fire depeartment had no calls in area. Circuit was closed via SCADA and held. Crew patrolled circuit and did not find any evident cause. | Nepean | Unknown/Other | No Apparent Cause
5203 | 2004 | 5 | 24 | 0.78472 |  | 110 | 13 | 7 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer 4882 at 48 Tiverton isolated to rep[lace defective switch and arrestor damaged by fire. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16157 | 2010 | 5 | 28 | 0.34792 |  | 54 | 17 | 19 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer #X35925 located at 9 Beaverton opened up due to squirrel contact | Nepean | Foreign Interference | Animal
14445 | 2009 | 6 | 2 | 0.39167 |  | 320 | 27 | 5 | Parkwood Hills | 8/4.8kV | 190F5 | TP6614 at 30 Northview was isolated to allow crews to excavate around transformer due to a previous leaker. | Nepean | Scheduled Outage | Preventive Maintenance
14449 | 2009 | 6 | 3 | 0.34375 |  | 40 | 8 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | Isolated transformer X35815 at 58 Ashburn Dr to Dis/rec service | Nepean | Scheduled Outage | Emergency Services Request
20694 | 2012 | 6 | 4 | 0.78264 |  | 51 | 10 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | Replaced blown fuse feeding transformer NP000859 at 17 Oakwood Ave (Squirrel contact) | Nepean | Foreign Interference | Animal
3562 | 2003 | 6 | 13 | 0.59306 |  | 86 | 95 | 66 | Parkwood Hills | 8/4.8kV | 190F5 | S446 was found blown crew patrolled found nothing refused and held. | Nepean | Unknown/Other | No Apparent Cause
20788 | 2012 | 6 | 18 | 0.26667 |  | 161 | 24 | 9 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer #X32686 located at 105 Hilliard Ave opened up due to animal contact | Nepean | Foreign Interference | Animal
18485 | 2011 | 6 | 24 | 0.53958 |  | 97 | 10 | 6 | Parkwood Hills | 8/4.8kV | 190F5 | Replaced blown fuse feeding transformer X36076 at 5 Vanson Ave | Nepean | Adverse Weather | Rain
20857 | 2012 | 6 | 24 | 0.53958 |  | 164 | 14 | 5 | Parkwood Hills | 8/4.8kV | 190F5 | S931 at 36 Elanor was opened to allow crew to remove tree off secondary triplex | Nepean | Tree Contacts | Preventive Maintenance
8616 | 2006 | 6 | 28 | 0.56875 |  | 20 | 443 | 1330 | Parkwood hills | 8/4.8kV | 190F5 | The 190F5 tripped under hold off, notified the crews involved and they never touched it and are clear, closed via scada and holding, John Brown to patrol. | Nepean | Unknown/Other
8618 | 2006 | 6 | 28 | 0.39375 |  | 403 | 67 | 10 | Parkwoodhills | 8/4.8kV | 190F5 | isolate TE434 @ 7 Eleanor Dr to change transformer. | Nepean | Scheduled Outage | Preventive Maintenance
14635 | 2009 | 6 | 28 | 0.61875 |  | 160 | 2692 | 1330 | Parkwood hills | 8/4.8kV | 190F5 | Parkwood Hills 190F5 circuit opened due to a Customer cutting a tree that fell into the primary @ 1201 Meadowlands. Then the circuit had to be sectionalized during restoration as the breaker would not pick up all the load. | Nepean | Foreign Interference | Tree Fallen
12772 | 2008 | 6 | 30 | 0.77153 |  | 104 | 21 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer #X33446 located at 95 Hilliard isolated due to suspected animal contact | Nepean | Foreign Interference | Animal
18668 | 2011 | 7 | 15 | 0.94722 |  | 57 | 9 | 9 | Parkwoodhills | 8/4.8kV | 190F5 | transformer X32686 at 1191 Deerpark was isolated to repair defective hotline clamp. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
5528 | 2004 | 7 | 20 | 0.010417 |  | 374 | 480 | 125 | Parkwood Hills | 8/4.8kV | 190F5 | White phase conductor let go on load side of switch S548. Crews were able to restore all but one overhead transformer & isolate switch for repairs. After repairs the one remaining transformer was restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18793 | 2011 | 7 | 21 | 0.75139 |  | 48 | 49 | 61 | Parkwood Hills | 8/4.8kV | 190F5 | 190F5 circuit auto reclosed due to over loading on breaker. Crews also found blown 30 amp fuse at 29 Lyall St. Switch was refused and holding. 80 amps of load was transferred off 190F5 circuit. | Nepean | Adverse Weather | Extreme Ambient Temperature
8830 | 2006 | 7 | 25 | 0.38542 |  | 140 | 12 | 5 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer located at 19 Fairlane isolated to transfer secondary to new ple | Nepean | Scheduled Outage | Construction
14837 | 2009 | 7 | 25 | 0.58472 |  | 19 | 38 | 120 | Parkwood Hills | 8/4.8kV | 190F5 | S547 switch was isolated to all crew to replace defective switch. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12948 | 2008 | 7 | 27 | 0.30556 |  | 145 | 24 | 10 | Parkwood Hiills | 8/4.8kV | 190F5 | At 09:45 trans at 35 Lyall St was refused and power restored, no apparent cause for failure.. | Ottawa | Unknown/Other | No Apparent Cause
12989 | 2008 | 8 | 1 | 0.66597 |  | 89 | 16 | 11 | PARKWOOD HILLS | 8/4.8kV | 190F5 | Transformer NP004272 located at 35 Lyall isolated to allow for repairs | Nepean | Foreign Interference | Bird
7052 | 2005 | 8 | 2 | 0.59236 |  | 17 | 2 | 6 | Parkwood Hills | 8/4.8kV | 190F5 | Isolated Transformer # 790 at 1147 Deer Park to remove Vines | Ottawa | Tree Contacts
16638 | 2010 | 8 | 4 | 0.38611 |  | 119 | 44 | 22 | Parkwood Hills | 8kv | 190F5 | TE 574 at 1212 Meadowlands was isolated to allow crew to replace live front transformer to dead front and install new nomenclature | Nepean | Scheduled Outage
16762 | 2010 | 8 | 17 | 0.54375 |  | 81 | 104 | 77 | ParkwoodHills | 8/4.8kV | 190F5 | A tree fell on the primary in the rear of 58 Wiggins which caused S108 to open. | Nepean | Tree Contacts | Tree Fallen
14970 | 2009 | 8 | 20 | 0.375 |  | 35 | 6 | 10 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer #X35816 located at 36 Wigan Dr isolated due to 100 amp upgrade | Nepean | Scheduled Outage | Construction
11160 | 2007 | 8 | 25 | 0.82153 |  | 77 | 12 | 9 | Parkwood Hills | 8/4.8kV | 190F5 | A broken switch at S607 caused outage, | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13150 | 2008 | 8 | 26 | 0.59167 |  | 30 | 6 | 12 | parkwood hills | 8/4.8kV | 190F5 | transformer #NPTE0032 at 68 Beaver Ridge isolated to allow for service repairs | Nepean | Scheduled Outage | Repair
15030 | 2009 | 8 | 30 | 0.45486 |  | 90 | 8 | 5 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer #X35940 located at 15 Ashburn isolated to change service | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19056 | 2011 | 8 | 30 | 0.58889 |  | 30 | 6 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | At 14:08 transformer TE529 at 1305 Meadowlands Drive was isolated to allow crew to connect secondaries. 12 customers were affected for 30 minutes. Parkwood Hills (190F6) ID#19056 | Nepean | Scheduled Outage
15045 | 2009 | 9 | 1 | 0.53403 |  | 36 | 5 | 8 | Parkwood Hills |  | 190F5 | TP5511 at 14 Warbonnet was isolated to allow crew to take transformer reading | Nepean | Scheduled Outage | Preventive Maintenance
15047 | 2009 | 9 | 2 | 0.37778 |  | 58 | 12 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | TP5510 at 86 Beaver Ridge on the 190F5 isolated to allow crew to measure resistance | Gloucester | Scheduled Outage
13253 | 2008 | 9 | 17 | 0.39167 |  | 356 | 71 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | TP5510 at 86 Beaver Ridge was isolated for planned replacement & base installation. | Nepean | Scheduled Outage | Preventive Maintenance
15153 | 2009 | 9 | 23 | 0.39444 |  | 57 | 21 | 22 | Parkwood Hills | 8/4.8kV | 190F5 | TE580 at 33 Hogan was isolated from Hydro Ottawa Sources to change out transformer. | Nepean | Scheduled Outage
9379 | 2006 | 10 | 4 | 0.85 |  | 56 | 14 | 15 | Parkwood Hills | 8/4.8kV | 190F5 | Fused Switch was found blown on overhead transformer NP4934 at 93 Beaver Ridge due to Vines on the pole | Nepean | Tree Contacts | Inadequate Trimming
19327 | 2011 | 10 | 5 | 0.375 |  | 270 | 45 | 10 | Parkwood Hills | 8/4.8kV | 190F5 | Trans X31590 was isolated at 60 Hillard Ave in order to replace the trans which was defective | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19471 | 2011 | 10 | 26 | 0.39583 |  | 150 | 48 | 19 | Parkwood Hills | 8/4.8kV | 190F5 | Trans X35925 at 9 Beaverton Ave was isolated in order to replace a defective transformer | Nepean | Scheduled Outage | Repair
13435 | 2008 | 10 | 27 | 0.39167 |  | 208 | 153 | 44 | Parkwood Hills | 8/4.8kV | 190F5 | Crew isolated section of 190F5 o/h between S539 & Temp 54 to repair Neutral and two phases. | Nepean | Scheduled Outage | Repair
4351 | 2003 | 10 | 28 | 0.15972 |  | 58 | 12 | 12 | Parkwood hills | 8/4.8kV | 190F5 | Transformer at 25 Bowmoor feeding 12 customers on Kilmory,Tiverton and Bowmoor opened. No cause was found. Crew refused transformer. | Nepean | Unknown/Other | No Apparent Cause
13525 | 2008 | 10 | 29 | 0.49722 |  | 94 | 210 | 134 | PARKWOOD HILLS | 8/4.8kV | 190F5 | PC10A #0792 established by M.Anderson at S151 to remove tree from primary on Oakdale | Nepean | Adverse Weather
19572 | 2011 | 11 | 14 | 0.40972 |  | 41 | 5 | 8 | Parkwood Hills | 8/4.8kV | 190F5 | crew opened transformer X35930 for service changeover at 18 Sunnycrest. | Nepean | Scheduled Outage | Preventive Maintenance
5944 | 2004 | 11 | 28 | 0.56389 |  | 66 | 13 | 12 | Parkwood Hills | 8/4.8kV | 190F5 | Replaced fuse to O/H xfmr at 1141 Deerpark. | Nepean | Unknown/Other | No Apparent Cause
17353 | 2010 | 11 | 28 | 0.69097 |  | 124 | 14 | 7 | Parkwood Hills | 8/4.8kV | 190F5 | crew replaced hotline clamp, and switch on overhead transformer T790 @ 1149 Deerpark. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
17416 | 2010 | 12 | 12 | 0.98333 |  | 26 | 6 | 14 | Parkwood hills | 8/4.8kV | 190F5 | Transformer X36230 at 11 Wigan opened to allow crew to replace broken cutout. | Nepean | Defective Equipment
19728 | 2011 | 12 | 16 | 0.41667 |  | 165 | 22 | 8 | Parkwood Hills |  | 190F5 | At 10h00 crews isolated transformers at the rear of 1171 Deerpark Rd to change transformer. Parkwoodhills 190F5 ID#19728 | Nepean | Scheduled Outage | Construction
9852 | 2006 | 12 | 17 | 0.69444 |  | 20 | 3 | 8 | Parkwood Hiils | 8/4.8kV | 190F5 | At 16:40 trans NP3194 at 67 Sunnycrest Dr was isolated in order to replace defective LLC | Nepean | Defective Equipment | Equipment Deterioration Due to Age
13789 | 2008 | 12 | 22 | 0.42292 |  | 469 | 63 | 16 |  | 8/4.8kV | 190F5 | TE542 at 30 Northview isolated to replace leaking transformer. TE541 (livefront) was isolated momentary to isolate TE542 | Nepean | Defective Equipment
15581 | 2009 | 12 | 28 | 0.45833 |  | 23 | 30 | 77 | Parkwood Hills | 8/4.8kV | 190F5 | Overhead section isolated to remove large tree limb @ Wigan Dr. | Nepean | Scheduled Outage | Repair
19772 | 2011 | 12 | 31 | 0.61389 |  | 41 | 15 | 22 | Parkwood Hills | 8/4.8kV | 190F5 | Transformer X36141 at 61 Tiverton Dr isolated to replace connections at s/p @ 61 and 63 Tiverton and change trans switch and stirrup @ 59 Tiverton. | Nepean | Scheduled Outage | Repair
19805 | 2012 | 1 | 10 | 0.42222 |  | 187 | 31 | 10 | Parkwood Hills | 8/4.8kV | 190F6 | NPTE127 @ 86 Chesterton was isolated to replace leaking transformer. | Nepean | Scheduled Outage | Repair
19906 | 2012 | 1 | 26 | 0.43333 |  | 203 | 54 | 16 | Parkwood Hills | 13.2kV | 190F6 | Transformer TE138 @ 102 Chesterton was isolated to allow crew to replace leaking transformer. | Ottawa | Scheduled Outage | Preventive Maintenance
20051 | 2012 | 2 | 24 | 0.39583 |  | 255 | 68 | 16 | Parkwod Hills | 8/4.8kV | 190F6 | TP9229 at 102 Chesterton was isolated to repair & extend primary cable. | Nepean | Scheduled Outage | Repair
17652 | 2011 | 2 | 28 | 0.46875 |  | 46 | 479 | 625 | Parkwood Hills | 8/4.8kV | 190F6 | A broken insulator on 190F5 2 spans N. of riser pole caused 190F5 & F6 cct's to trip. Temporary repairs were made & both cct's restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12169 | 2008 | 3 | 23 | 0.60417 |  | 30 | 5 | 10 | PARKWOOD HILLS | 8/4.8kV | 190F6 | Transformer fuse found blown at the rear of 46 Tiverton St. possibly due to a animal contact. | Nepean | Foreign Interference | Animal
20492 | 2012 | 5 | 10 | 0.40694 |  | 152 | 68 | 27 | Stratop | 8/4.8kV | 190F6 | Transformer TE265 at 61 Bowhill was isolated to allow crew to replace leaking transformer | Gloucester | Scheduled Outage | Repair
18662 | 2011 | 7 | 15 | 0.37569 |  | 11 | 113 | 616 | PARKWOOD HILLS | 8/4.8kV | 190F6 | 190F6 circuit tripped. To be patrolled. Circuit was patrolled and no issues were found | Nepean | Unknown/Other | No Apparent Cause
18748 | 2011 | 7 | 17 | 0.80833 |  | 11 | 113 | 616 | Parkwood Hills | 8/4.8kV | 190F6 | 190F6 tripped open due to storm and was closed with success 11 minutes later | Nepean | Adverse Weather | Lightning
14783 | 2009 | 7 | 18 | 0.83611 |  | 403 | 422 | 80 | Parkwood Hills | 8/4.8kV | 190F6 | A 190F6 red phase cable fault between 8KV transformers TE125 and TE126 on Hillhurst caused S736 to open. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
19008 | 2011 | 8 | 24 | 0.375 |  | 475 | 459 | 58 | Parkwood Hills |  | 190F6 | At 09:00am crew isolated a section of the 190F6 and 190F2 to allow crews to replace 2 poles in backyards. 58 customers affected for 505 mins. Parkwood Hills 190F6 ID# 19008 | Nepean | Scheduled Outage | Repair
13159 | 2008 | 8 | 27 | 0.39861 |  | 518 | 9 | 1 | Parkwood Hills | 8/4.8kV | 190F6 | Cable dip from riser S895 had a white phase cable fault at 20 Chesterton. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
15078 | 2009 | 9 | 9 | 0.38333 |  | 21 | 2 | 7 | Parkwood Hills | 8/4.8kV | 190F6 | TP5505 at 25 Assinboine isolated for Hydro Ottawa to test transformer's grounding resistance. | Nepean | Scheduled Outage | Preventive Maintenance
19215 | 2011 | 9 | 20 | 0.77083 |  | 45 | 86 | 115 | Parkwood | 8/4.8kV | 190F6 | During switching to restore cable loop after planned outage, a flash occurred at SE7 causing S736R to blow. A possible defective cable from SE7 to TP9135 will be investigated. Cable section isolated & power restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13283 | 2008 | 9 | 24 | 0.42917 |  | 274 | 32 | 7 | PARKWOOD HILLS | 8/4.8kV | 190F6 | Scheduled outage to TP5505 at 25 Assiniboine to replace PCB identified transformer and install base. | Nepean | Scheduled Outage
17340 | 2010 | 11 | 24 | 0.74583 |  | 36 | 10 | 16 | Parkwood Hills | 8/4.8kV | 190F6 | Replaced burnt hotline clamp and stirrup at transformer NP4942 at 11 Walgate Ave | Nepean | Defective Equipment | Equipment Deterioration Due to Age
13762 | 2008 | 12 | 16 | 0.39583 |  | 52 | 1 | 1 | Parkwood Hills | 8/4.8kV | 190F6 | Isolated VE47 @ 1343 Meadowlands was isolated for contractor to pull in new cable for defective secondary main breaker. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
13766 | 2008 | 12 | 16 | 0.6875 |  | 231 | 4 | 1 | Parkwood Hills | 8/4.8kV | 190F6 | V47 at 1343 Meadowlands was isolated to allow Electrician to repair defective breaker. | Nepean | Defective Equipment
7413 | 2005 | 10 | 1 | 0.33333 |  | 140 | 23 | 10 | Parkwood Hills | 8/4.8kV | 190FS | Transformer #NP004572 located at 66 Inverness isolated to reconnect service that was off from tree contact from Thursday's storm | Nepean | Tree Contacts | Tree Limb Fallen
9940 | 2007 | 1 | 17 | 0.48403 |  | 365 | 18 | 3 | Stafford | 8/4.8kV | 200 F5 | Larry K-Line isolated TRF. 258 @ 306 Moodie dr. to relocate conductor to new pole | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4673 | 2004 | 1 | 4 | 0.63819 |  | 46 | 5 | 6 | Stafford | 8/4.8kV | 200F1 | New fuse installed at 227 Grandview, no obvious cause for fuse failure. | Nepean | Defective Equipment
17474 | 2011 | 1 | 8 | 0.37847 |  | 40 | 5 | 8 | Stafford Road | 8/4.8kV | 200F1 | Transformer NP004442 isolated to change the triplex for 6 Cleadon Drive | Nepean | Scheduled Outage | Repair
19809 | 2012 | 1 | 10 | 0.56944 |  | 88 | 4 | 3 | STAFFORD | 8/4.8kV | 200F1 | Transformer X36216 for 115 James Cummings Ave. isolated for service upgrade | Nepean | Scheduled Outage | Construction
9922 | 2007 | 1 | 14 | 0.98056 |  | 633 | 6222 | 1220 | Stafford | 8/4.8kV | 200F1 | Scada indicates 200F1 circuit opened. B. Baker dispatched to Stafford Rd. to restore O/H circuit. O/h circuit was sectionized, but 200F1 circuit breaker failed to close at station via scada or manually. 200F1 circuit was transferred 200F5. 200F5 breaker closed via scada restoring load. 994 Red phase fuse found opened 90 customers in Westcliffe area still out of power. All under ground transformers in the Westciffe area checked No Apparent cause. Loop was sectionized. S994 red phase was closed, and 200F5 circuit breaker opened. 200f5 breaker closed via scada load restored. S93 red phase fuse was closed restoring 3 transformer approx 30 customer. On call crew to meggered & hi pot test cables, and found bad cable section between TE1101 & TE753 on Priam Way, and Florizel. S994 red phase fuse replaced and closed. S994 red phase fuse blow causing 200F5 breaker to open. Breaker closed via scada restoring load to 1160 customers. B. Baker reports cable section between TE1879 & TE750 is bad. S994 red phase fuse is closed and holding. Cable section betwwen TE1879 & TE750 restored, and all load restored in the Westcliffe area. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15667 | 2010 | 1 | 18 | 0.83333 |  | 65 | 6 | 6 | Stafford | 8/4.8kV | 200F1 | Replaced broken switch for transformer X40023 at 131 Grandview Rd | Nepean | Defective Equipment | Equipment Deterioration Due to Age
7850 | 2006 | 1 | 24 | 0.79444 |  | 74 | 7 | 6 | Stafford | 8/4.8kV | 200F1 | Power ouatge to transformer NP2658 at 17 Rocky Point due to broken switch | Nepean | Defective Equipment | Equipment Deterioration Due to Age
7964 | 2006 | 2 | 24 | 0.16875 |  | 110 | 6 | 3 | Stafford | 8/4.8kV | 200F1 | Broken riser fell into neutral causing fuse at switch S16 to open on Hilda. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
17642 | 2011 | 2 | 24 | 0.67639 |  | 27 | 277 | 615 | STAFFORD DS | 8/4.8kV | 200F1 | At 16:14 the Stafford DS 200F1 and 200F5 tripped and locked out. The crews on scene found a burnt squirel. 615 customers on the 200F1 and 1238 customers on the 200F5 were affected for 27 mins. STAFFORD DS 200F1, 200F5 ID# 17642 | Nepean | Foreign Interference | Animal
15770 | 2010 | 3 | 4 | 0.69792 |  | 237 | 102 | 40 | Stafford | 8/4.8kV | 200F1 | S369 at Carling & James Cummings blew when a truck caught the Bell wires at 136 James Cummings & pulled over pole X36208. The pole was braced with a line truck & all customers except those on Tx X36208 were restored before making temporary repairs to secure pole & restore remaining customers. | Nepean | Foreign Interference | Vehicle
15772 | 2010 | 3 | 4 | 0.69792 |  | 177 | 100 | 40 | Stafford | 8/4.8kV | 200F1 | A truck pulled over pole X36208 at 136 James Cummings causing 200F1 to A/R & S369 to blow. The pole was pulled straight with a line truck to allow all customers to be restored except Tx X36208. Temporay repairs were made to secure the pole & all customers restored. | Nepean | Foreign Interference | Vehicle
10099 | 2007 | 3 | 7 | 0.56944 |  | 25 | 1 | 2 | Stafford | 8/4.8kV | 200F1 | Al Cooney isolated Sw 1351 to change the fusing in it | Nepean | Scheduled Outage | Preventive Maintenance
17695 | 2011 | 3 | 10 | 0.30208 |  | 75 | 2 | 2 | Stafford | 8/4.8kV | 200F1 | replaced broken switch feeding transformer X40021 at 146 Grandview Rd | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15790 | 2010 | 3 | 11 | 0.66875 |  | 52 | 29 | 33 | Stafford | 8/4.8kV | 200F1 | A broken fused switch S876 at Carling and Crystal Beach required isolation to repair. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15792 | 2010 | 3 | 12 | 0.40486 |  | 32 | 16 | 30 | Stafford | 8/4.8kV | 200F1 | Switch S876 at 4 Carling Ave opened to repair defective connections. Interruption to transformer TE439 to complete repairs. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4922 | 2004 | 3 | 21 | 0.12639 |  | 674 | 562 | 50 | Stafford | 8/4.8kV | 200F1 | M. Brown reports S872 switch found blown, but switch is still closed. When M. Brown went to open switch 200F1 circuit auto reclosed. Causing a momentary outage to the circuit. Cable splice and termination repaired. | Nepean | Defective Equipment
10174 | 2007 | 3 | 25 | 0.67708 |  | 40 | 1 | 1 | Stafford | 8/4.8kV | 200F1 | Isolated transformer NP2222 at 139 March Rd and replaced the connection on the secondary service | Nepean | Defective Equipment | Equipment Deterioration Due to Age
6332 | 2005 | 3 | 28 | 0.36111 |  | 80 | 1 | 1 | Stafford | 8/4.8kV | 200F1 | Replaced broken switch to transformer #93 at Robertson rd and Haanel Dr feeding one house and streetlights | Nepean | Defective Equipment | Equipment Deterioration Due to Age
8105 | 2006 | 4 | 5 | 0.38542 |  | 45 | 4 | 5 | Stafford | 8/4.8kV | 200F1 | Isolated transformer NP719 at 46 Grandview to replace primary conductor insulators | Nepean | Scheduled Outage | Preventive Maintenance
8106 | 2006 | 4 | 5 | 0.42708 |  | 25 | 2 | 4 | Stafford | 8/4.8kV | 200F1 | Isolated transformer NP3107 at 48 Grandview to replace primary conductor insulators | Nepean | Scheduled Outage
15907 | 2010 | 4 | 7 | 0.77986 |  | 470 | 446 | 607 | Stafford | 8/4.8kV | 200F1 | Vehicle accident at 639 Robertson Rd broke a hydro pole & knocked down conductor and caused the circuit to A/R at 18:13, see ID #15906. 200F1 breaker was opened from SCADA until the damaged section could be isolated. Temporary repairs were made to the damaged section with 4 overhead transformers by Oncall crews. | Nepean | Foreign Interference | Vehicle
15919 | 2010 | 4 | 10 | 0.38472 |  | 5 | 64 | 766 | Stafford |  | 200F1 | Abnormal voltage at Stafford T1 after auto reclose to 22M25. 200F1,F2,F3 breakers opened from SCADA B1 bus restored from 200T2 and 3 feeder breakers closed to restore load. 24/7 found a lead burnt off the 44Kv dip to 200T1. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12282 | 2008 | 4 | 14 | 0.4625 |  | 144 | 12 | 5 | Stafford | 8/4.8kV | 200F1 | Isolaed transformer X36222 at 20 Borden St to replace service | Nepean | Scheduled Outage | Repair
8158 | 2006 | 4 | 18 | 0.46528 |  | 170 | 8 | 3 | Stafford | 8/4.8kV | 200F1 | Isolated transformer 997 at 126 Grandview Rd to replace primary conductor pole insulators | Nepean | Scheduled Outage | Preventive Maintenance
8161 | 2006 | 4 | 19 | 0.35417 |  | 116 | 2 | 1 | Stafford | 8/4.8kV | 200F1 | 3 PHASE TRANSFORMER 854 @ 3690 CARLING AVE OPENED TO ALLOW CREW TO TO CHECK FOR VOLTAVE PROBLEM. FOUND ONE BAD PALE. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8181 | 2006 | 4 | 22 | 0.8625 |  | 218 | 29 | 8 | Stafford | 8/4.8kV | 200F1 | A broken switch on the W phase at S765 on Robertson Rd. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8188 | 2006 | 4 | 25 | 0.55208 |  | 70 | 5 | 4 | Stafford | 8/4.8kV | 200F1 | Jim Ryan opened transformer NP3093 at 162 Grandview to change the transformer lead | Nepean | Unknown/Other
14224 | 2009 | 4 | 25 | 0.82222 |  | 1456 | 1941 | 80 | Stafford Road DS | 8/4.8kV | 200F1 | Tree fell on primary wires is the rear of 58 Solva Dr. | Ottawa | Adverse Weather | Wind
14245 | 2009 | 4 | 25 | 0.81111 |  | 1472 | 1963 | 80 | Stafford | 8/4.8kV | 200F1 | 200 F1 auto reclosed, S679 blew, tree fell on primary wires. Storm & high winds. Outage delayed due to not enough crews to make repairs. Tree removed and power restored. | Nepean | Adverse Weather | Tree Fallen
12389 | 2008 | 5 | 5 | 0.35417 |  | 60 | 8 | 8 | Stafford | 8/4.8kV | 200F1 | Isolated and replaced transformer NP1013 at the rear of 17 Conniston Ave | Nepean | Scheduled Outage | Preventive Maintenance
14353 | 2009 | 5 | 14 | 0.43125 |  | 57 | 2 | 2 | Stafford | 8/4.8kV | 200F1 | Crew isolated section of 200F1 overhead from switch S1351 Carling & Range rd. to remove burning tree on overhead. | Nepean | Tree Contacts | Tree Limb Fallen
6562 | 2005 | 5 | 16 | 0.58681 |  | 29 | 2 | 4 | Stafford | 8/4.8kV | 200F1 | Transformer #NP002652 at 123 James Cummings isolated due to change a lightning arrester | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18174 | 2011 | 5 | 18 | 0.34236 |  | 92 | 2 | 1 | Stafford | 8/4.8kV | 200F1 | Transformer #X37000 located at 3859 Carling Ave opened due to squirrel contact | Nepean | Foreign Interference | Animal
6650 | 2005 | 6 | 3 | 0.53403 |  | 58 | 4 | 4 | Stafford | 8/4.8kV | 200F1 | Isolated transformer # 3093 at 187 Grandview rd to install new service | Ottawa | Scheduled Outage | Preventive Maintenance
16182 | 2010 | 6 | 3 | 0.18333 |  | 77 | 4 | 3 | Stafford | 8/4.8kV | 200F1 | S1529 blue phase fuse barrell failed, cause is unknown, isolated and load restored from other end of the loop | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8424 | 2006 | 6 | 5 | 0.40278 |  | 299 | 244 | 49 | Stafford | 8/4.8kV | 200F1 | O/H section of the 200F1 on Sunny Brae isolated for pole replacement. | Nepean | Scheduled Outage | Construction
20698 | 2012 | 6 | 5 | 0.39583 |  | 120 | 20 | 10 | Stafford | 8/4.8kV | 200F1 | Transformer at 641 Corkstown Rd isolated for CT change and transfer of plant | Nepean | Scheduled Outage | Construction
8431 | 2006 | 6 | 6 | 0.41528 |  | 77 | 5 | 4 | Stafford | 8/4.8kV | 200F1 | Isolated transformer #NP671 at 5 Sunny Brae to replacment a pole. | Ottawa | Scheduled Outage | Construction
14473 | 2009 | 6 | 6 | 0.45486 |  | 108 | 70 | 39 | Stafford | 8/4.8kV | 200F1 | Sqirrel at S369 blue phase at 3421 Carling made contact and caused the fuse to open, no permament damage | Nepean | Foreign Interference | Animal
12610 | 2008 | 6 | 12 | 0.30903 |  | 64 | 9 | 8 | Stafford DS | 8/4.8kV | 200F1 | Transformer #X40017 located at 174 Grandview isolated due to squirrel interference | Nepean | Foreign Interference | Animal
12633 | 2008 | 6 | 15 | 0.72569 |  | 117 | 1388 | 712 | Stafford | 8/4.8kV | 200F1 | The 200F1 tripped, because a pole fire and a broken insulator it runs along Eagleson Rd along with the BRDF4 and A9M1, lightning strike on the pole. | Nepean | Adverse Weather | Lightning
20849 | 2012 | 6 | 23 | 0.325 |  | 302 | 35 | 7 | Stafford | 8/4.8kV | 200F1 | Transfomer X40242 at 7 Conniston opened due to squirekl contact. | Nepean | Foreign Interference | Animal
18590 | 2011 | 7 | 5 | 0.26806 |  | 124 | 1271 | 615 | Stafford | 8/4.8kV | 200F1 | 200F1 circuit was forced out of service due to a brown out condtion caused by a white phase fuse opening on the 200T1 transformer. Stations crews inspected the B1 bus and found no problems. Circuit was restored using the 200T2 transformer. | Nepean | Unknown/Other
12805 | 2008 | 7 | 8 | 0.70972 |  | 107 | 16 | 9 | Stafford | 8/4.8kV | 200F1 | Section of 200F1 o/h circuit was isolated to allow crew to repair broken crossarm on pole at 3659 Carling ave. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
6982 | 2005 | 7 | 16 | 0.78819 |  | 625 | 10 | 1 | Stafford | 8/4.8kV | 200F1 | Lightning caused all three phases to blow at switch 1451 at the rifle range. | Nepean | Adverse Weather | Lightning
5521 | 2004 | 7 | 18 | 0.87847 |  | 400 | 7 | 1 | Stafford | 8/4.8kV | 200F1 | Transformer at 200 Moodie defective and replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6988 | 2005 | 7 | 18 | 0.44861 |  | 138 | 999 | 814 | Stafford | 8/4.8kV | 200F1 | Tree in the 3 phase primary on Ullswater caused the feeder at the station to open, switching was done to isolate the area and the breaker was closed to restore the bulk of the customers. | Nepean | Tree Contacts | Tree Limb Fallen
18764 | 2011 | 7 | 18 | 0.046528 |  | 3 | 31 | 615 | Stafford | 8/4.8kV | 200F1 | The stafford 200F1 circuit opened during the wind and lighting storm. System closed the breaker via SCADA and breaker held. All load restore | Nepean | Adverse Weather
8790 | 2006 | 7 | 19 | 0.95833 |  | 112 | 28 | 15 | Stafford | 8/4.8kV | 200F1 | Isolate the O/H line that feeds Caunaght Rifle range to allow the contracter to install new air breake switch at their new sub station. | Nepean | Scheduled Outage | Preventive Maintenance
10935 | 2007 | 7 | 23 | 0.41667 |  | 719 | 12 | 1 | Stafford | 8/4.8kV | 200F1 | Call came in from Energy Mines and Resources that the 8KV feed was lost to their pumping station at 10AM this morning. Vic Schnobb was contacted and he reports the Queensway will require a shutdown in order to repair the broken neutral conductor. PC10A #002639 received from 24/7 crew. Vic Schnobb reports that MTO will not be able to shutdown the highway until tommorow evening, no specific time given. Customer has generator that was delivered to site and are currently running off of. Vic Schnobb has said that he can be onsite but with a 3 hour notice in order to have crew set-up and ready to re-string triplex to service. | Nepean | Foreign Interference | Vehicle
14814 | 2009 | 7 | 23 | 0.425 |  | 241 | 4 | 1 | Stafford | 8/4.8kV | 200F1 | Transformer #X36816 located at 200 Moodie Dr isolated possibly due to the rain & wind per Mark | Nepean | Adverse Weather | Rain
8825 | 2006 | 7 | 25 | 0.24583 |  | 82 | 1 | 1 | Stafford | 8/4.8kV | 200F1 | Low hanging tree limb suspected cuase of in line fuses blowing. | Nepean | Tree Contacts | Inadequate Trimming
3789 | 2003 | 7 | 27 | 0.77986 |  | 72 | 8 | 7 | Stafford | 8/4.8kV | 200F1 | 24/7 reports vines in open overhead bus caused transformer fuse to blow. Vines removed and SW 1584 refused and closed restoring power to 7 customers on Burke Rd. | Nepean | Foreign Interference | Foreign Object
16633 | 2010 | 8 | 3 | 0.87708 |  | 167 | 8 | 3 | Stafford |  | 200F1 | S1351 found blown. Crew patrolled line, nothing found. Lightning in the area. Switch closed to restore power. | Nepean | Unknown/Other
3887 | 2003 | 8 | 11 | 0.29375 |  | 212 | 71 | 20 | Stafford | 8/4.8kV | 200F1 | Scada indicates 200F1 circuit auto reclosed. No reports of power outages. Circuit to be patrolled. M. Brown reports primary wire down on Rifle RD & Shirley RD. S1351 opened to repair O/H line approx 20 customer affected in outage. Repairs were made to overhead line all power restored . | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5675 | 2004 | 8 | 13 | 0.60417 |  | 10 | 1 | 7 | Stratford | 8/4.8kV | 200F1 | O/H xfmr NP2649 at 15 Myrle interrupted to replace blown lightning arrestor. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11084 | 2007 | 8 | 16 | 0.64236 |  | 190 | 3 | 1 | Stafford | 8/4.8kV | 200F1 | Transformer located at 821 Corkstown isolated due to lightning & storm | Nepean | Adverse Weather | Lightning
13071 | 2008 | 8 | 18 | 0.34375 |  | 80 | 1 | 1 | Stafford Rd DS | 8/4.8kV | 200F1 | Transformer #X36803 located at 821 Corkstown Rd isolated, no apparent cause found. | Nepean | Unknown/Other | No Apparent Cause
5735 | 2004 | 8 | 28 | 0.36389 |  | 281 | 5 | 1 | 200F1 | 8/4.8kV | 200F1 | Blown arrester found on o/h line west of S70. Arrester cut clear as per P. Donelly instructions. Swtiches closed and holding. | Nepean | Defective Equipment
7255 | 2005 | 8 | 31 | 0.6875 |  | 49 | 10 | 12 | Stafford | 8/4.8kV | 200F1 | Transformer #NP004415 located at 24 Elterwater isolated due to blown arrestor. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19087 | 2011 | 9 | 4 | 0.027083 |  | 141 | 14 | 6 | Stafford | 13.2kV | 200F1 | Vines caused transformer X40194 at 7 Elterwater cut out to blow. Stafford (200F1) ID#19087 | Nepean | Tree Contacts | Inadequate Trimming
15076 | 2009 | 9 | 9 | 0.38194 |  | 70 | 6 | 5 | Stafford | 8/4.8kV | 200F1 | Transformer #X3911 located at 25 Moodie isolated for pole installation | Nepean | Scheduled Outage | Construction
15079 | 2009 | 9 | 9 | 0.38194 |  | 70 | 6 | 5 | STAFFORD | 8/4.8kV | 200F1 | transformer X3911 at 25 Moodie Dr isolated to allow for pole installation | Nepean | Scheduled Outage | Construction
19126 | 2011 | 9 | 9 | 0.39583 |  | 14 | 2 | 7 | Stafford DS | 8/4.8kV | 200F1 | At 09:30am crews isolated transformer X36218 at 20 Myrle Ave to transfers secondary services. 7 customers for 14 mins. Stafford DS 200F1 ID# 19126 | Nepean | Scheduled Outage
19130 | 2011 | 9 | 10 | 0.52361 |  | 217 | 725 | 619 |  |  | 200F1 | At 12:34 200F1 Breaker at Stafford DS tripped due to a fallen tree on the primary at 227 Grandview. Crew isolated down conductor and performed repairs. Stafford (200F1) ID# 19130 | Nepean | Tree Contacts | Tree Fallen
13218 | 2008 | 9 | 11 | 0.70347 |  | 82 | 3 | 2 | Stafford Rd DS | 8/4.8kV | 200F1 | Transformer #X40011 located at 90 Grandview Rd isolated due to defective cut out | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15127 | 2009 | 9 | 14 | 0.91319 |  | 2300 | 38 | 1 | Stafford Road | 8/4.8kV | 200F1 | Conaught Riffle range 27kV rabbits went defective and customer lost power. Customer temporarily transferred to 8kV line. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
13305 | 2008 | 9 | 29 | 0.83333 |  | 60 | 9 | 9 | Stafford | 8/4.8kV | 200F1 | Crew replaced broken cut-out at transformer X37010, 263 Grandview. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4235 | 2003 | 10 | 9 | 0.72639 |  | 114 | 4 | 2 | Stafford | 8/4.8kV | 200F1 | Tree contacted the overhead at 44 Riverdown causing an outage on Transformer # 119. | Ottawa | Tree Contacts | Tree Limb Fallen
4319 | 2003 | 10 | 21 | 0.375 |  | 60 | 6 | 6 | Stafford | 8/4.8kV | 200F1 | The lead to switch s1584 was found burnt off. Replaced by crew. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15304 | 2009 | 10 | 26 | 0.40972 |  | 55 | 9 | 10 | Stafford | 8/4.8kV | 200F1 | Transformer X3574 at 161 Herzberg isolated to allow for rearranging of hydro plant and streetlight plant | Nepean | Scheduled Outage | Construction
9551 | 2006 | 10 | 30 | 0.084722 |  | 488 | 5043 | 712 | Stafford DS | 8/4.8kV | 200F1 | 200F1 Breaker tripped due to a fallen tree on Range Road, and S1351 never blew. Breaker problems hampered restoration efforts. Carling Ave and Moodie Area. | Nepean | Tree Contacts | Tree Fallen
9606 | 2006 | 11 | 6 | 0.35972 |  | 12 | 1 | 3 | Stafford | 8/4.8kV | 200F1 | Scott Dickson had Transformer 581 open for mtce on a meter | Ottawa | Scheduled Outage | Preventive Maintenance
13624 | 2008 | 11 | 17 | 0.39931 |  | 10 | 1 | 4 | STAFFORD ROAD | 8/4.8kV | 200F1 | Isolated transformer X40178 at 26 Ullswater Dr to remove the temporary secondary buss jumpers so crew can replace transformer X40188 at 16 Ullswater Dr | Nepean | Scheduled Outage | Repair
13626 | 2008 | 11 | 17 | 0.41181 |  | 137 | 14 | 6 | Stafford | 8/4.8kV | 200F1 | Transformer 4413 at 16 Ullswater was isolated to replace transformer. | Nepean | Scheduled Outage
11740 | 2007 | 11 | 20 | 0.16458 |  | 98 | 10 | 6 | Stafford | 8/4.8kV | 200F1 | Vines grew into primary at rear of 7 Elterwater causing cut-out at Tx NP278 to blow. Vines removed & fuse replaced | Nepean | Tree Contacts | Inadequate Trimming
15415 | 2009 | 11 | 23 | 0.53472 |  | 60 | 5 | 5 | Stafford | 8/4.8kV | 200F1 | Transformer #NP3722 located at 21 Bayfield opened, with no cause found | Nepean | Unknown/Other | No Apparent Cause
19633 | 2011 | 11 | 25 | 0.35764 |  | 120 | 2 | 1 | Stafford | 8/4.8kV | 200F1 | Transformer #X36816 located at 200 Moodie Dr opened up, crew could not find the cause | Nepean | Unknown/Other | No Apparent Cause
9775 | 2006 | 12 | 1 | 0.84931 |  | 306 | 1757 | 814 | Stafford | 8/4.8kV | 200F1 | 200F1 Breaker tripped, due to tree down on primary at 5 Nesbitt. Circuit sectionalized to restore power. | Nepean | Adverse Weather | Ice Storm
7745 | 2005 | 12 | 19 | 0.4375 |  | 90 | 9 | 6 | Stafford | 8/4.8kV | 200F1 | The O/H neutral on Shirley Rd east of Range rd was down repaire were made. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15603 | 2010 | 1 | 3 | 0.60625 |  | 113 | 17 | 68 | Stafford | 8/4.8kV | 200F2 | Transformer #2060 @ the rear of 8 Ellery St switch failed and lead was close to primary netural. 24/7 reports lead was blowing in the wind, and requested the circuit to be dump. While lead was cut clear ( lineman was on the pole and clearance was required)Transformer lead was replaced, and power was restored to transformer #2060 on Ellery St. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
4679 | 2004 | 1 | 5 | 0.70139 |  | 70 | 26 | 22 | Stafford | 8/4.8kV | 200F2 | Transformer connections tightened and hot line clamps replaced. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
7806 | 2006 | 1 | 14 | 0.69583 |  | 68 | 5 | 4 | Stafford | 8/4.8kV | 200F2 | Broken switch S188 feeding transformer TE2390 at 3754 Richmand Rd, switch replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7891 | 2006 | 2 | 5 | 0.047222 |  | 267 | 107 | 24 | Stafford | 8/4.8kV | 200F2 | Switch feeding O/H transformer at 11 Vanier has broken, same switch replaced. | Nepean | Tree Contacts
17566 | 2011 | 2 | 9 | 0.39722 |  | 38 | 13 | 21 | Stafford Road | 8/4.8kV | 200F2 | Replaced broken fuse (Cause unknown) feeding transformer X3190 at the rear of 12 Redfern Ave | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14138 | 2009 | 4 | 2 | 0.52431 |  | 115 | 10 | 5 | Stafford | 8/4.8kV | 200F2 | Transformer #X39539 located at 15 Virgil Rd isolated for PCB change | Nepean | Scheduled Outage | Preventive Maintenance
4966 | 2004 | 4 | 4 | 0.44514 |  | 38 | 13 | 20 | Stafford | 8/4.8kV | 200F2 | Transformer # 256 fuse cutout found blown No Apparent Cause . Fuse replaced and closed. | Nepean | Unknown/Other | No Apparent Cause
3436 | 2003 | 5 | 13 | 0.61667 |  | 120 | 2 | 1 | Woodroffe | 13.2kV | 200F2 | Switch S893 went defective causing an outage at transformer TE2922, 55 Robertson Road in Nepean. Defective switch was isolated and repairs made. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20691 | 2012 | 6 | 4 | 0.39375 |  | 151 | 15 | 6 | Stafford | 8/4.8kV | 200F2 | Refused transformer X09910 at 37 Vanier Rd. - squirrel | Ottawa | Foreign Interference | Animal
16380 | 2010 | 7 | 1 | 0.50278 |  | 229 | 8 | 8 | Stafford Road | 8/4.8kV | 200F2 | Defective switch S1017 opened interupting 8 customers at 3700 Richmond rd. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18591 | 2011 | 7 | 5 | 0.26806 |  | 124 | 192 | 93 | Stafford | 8/4.8kV | 200F2 | 200F2 circuit was forced out of service due to a brown out condtion caused by a white phase fuse opening on the 200T1 transformer. Stations crews inspected the B1 bus and found no problems. Circuit was restored using the 200T2 transformer. | Nepean | Unknown/Other | No Apparent Cause
3706 | 2003 | 7 | 8 | 0.29514 |  | 85 | 10 | 7 | Stafford | 8/4.8kV | 200F2 | Blown fuse, refused and power restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16553 | 2010 | 7 | 24 | 0.67083 |  | 23 | 2 | 4 | Stafford | 8/4.8kV | 200F2 | Trans at :36 VIRGIL ROAD Nepean was isolated to replace a defective trans sw .. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
14891 | 2009 | 8 | 1 | 0.98958 |  | 175 | 18 | 6 | Stafford Road | 8/4.8kV | 200F2 | TE1219 at 1 Stafford on 200F2 was isolated to replace due to leaking transformer | Nepean | Scheduled Outage | Repair
14915 | 2009 | 8 | 5 | 0.41806 |  | 64 | 5 | 5 | Stafford | 8/4.8kV | 200F2 | Isolated transformer X2424 at 3775 Richmond Rd to repair pole | Nepean | Scheduled Outage | Repair
7135 | 2005 | 8 | 14 | 0.125 |  | 155 | 16 | 6 | Stafford | 8/4.8kV | 200F2 | Transformer TE1220 on Stafford Rd in Nepean isolated for replacement due to oil leak. | Nepean | Scheduled Outage | Repair
15013 | 2009 | 8 | 27 | 0.25694 |  | 50 | 8 | 9 | Stafford | 8/4.8kV | 200F2 | At 6:10am transformer TP5401 at Lynwood Shopping Centre on Richmond Rd. Bells Corners was isolated to install new switches and arrestors. 200F2 Stafford Road ID# 15013 | Nepean | Scheduled Outage
11176 | 2007 | 8 | 29 | 0.054167 |  | 26 | 6 | 15 | Stafford | 8/4.8kV | 200F2 | o/h transformer at trailer park on bonner in Nepean was opened to replace defective hot line clamp. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
16909 | 2010 | 9 | 8 | 0.92153 |  | 93 | 16 | 10 | STAFFORD | 8/4.8kV | 200F2 | Transformer X40058 at 34 Virgil refused by on-call | Nepean | Adverse Weather | Repair
5791 | 2004 | 9 | 9 | 0.39236 |  | 185 | 247 | 80 | Stafford | 8/4.8kV | 200F2 | A tree fell on the line near the switch causing the switch to flash over. One of the phases had to be replaced and the tree trim back. | Nepean | Adverse Weather | Wind
9195 | 2006 | 9 | 11 | 0.40625 |  | 105 | 33 | 19 | Bells Corners | 8/4.8kV | 200F2 | Isolated overhead section of line feeding 3 transformers on Ridgefield Cres for tree contractor to remove broken Tree limb at 14 Ridgefield Cres | Nepean | Tree Contacts | Tree Limb Fallen
7575 | 2005 | 11 | 7 | 0.87569 |  | 124 | 31 | 15 | Stafford | 8/4.8kV | 200F2 | M. byers reports lead brunt off at top of hot line clamp. | Nepean | Adverse Weather | Wind
9790 | 2006 | 12 | 3 | 0.44444 |  | 277 | 14 | 3 | Stafford | 8/4.8kV | 200F2 | Isolated a section of O/H on Stafford Rd to replace insulators | Nepean | Scheduled Outage | Preventive Maintenance
4609 | 2003 | 12 | 16 | 0.27292 |  | 207 | 276 | 80 | Stafford | 8/4.8kV | 200F2 | W phase of switch S417 at Robertson and Stinson in Bells Corners opened, same had to be replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11875 | 2007 | 12 | 23 | 0.75694 |  | 35 | 2 | 4 | Stafford | 8/4.8kV | 200F2 | A burning hot line clamp at switch 781 @ 62 Robertson Rd/Richmond Rd had to be replaced, affecting 4 customers | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7788 | 2006 | 1 | 10 | 0.39028 |  | 120 | 18 | 9 | Stafford | 8/4.8kV | 200F3 | S1203 on Northside RD. Opened to fix broken insulator 9 customers affected. | Nepean | Scheduled Outage | Repair
13933 | 2009 | 2 | 4 | 0.59028 |  | 500 | 33 | 4 | Stafford | 8/4.8kV | 200F3 | Contractor dug into primary cable between TE2917 & TE1301 at 16 Bexley Pl. causing center phase of S662 to blow. TE1301, radial feed from TE2917 was isolated to make repairs to primary cable. | Ottawa | Foreign Interference | Dig-in
7934 | 2006 | 2 | 17 | 0.33333 |  | 179 | 119 | 40 | Stafford | 8/4.8kV | 200F3 | Tree on O/H in the Foothills area causing switch 1059 to blow. | Nepean | Adverse Weather | Wind
10252 | 2007 | 4 | 13 | 0.94097 |  | 10 | 1 | 4 | Stafford Rd | 8/4.8kV | 200F3 | Tx 1382 at 4 Thorncliffe was opened to replace defective hotline clamp & stirrup. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
20478 | 2012 | 5 | 8 | 0.17153 |  | 81 | 315 | 233 | Stafford | 8/4.8kV | 200F3 | 200F3 breaker tripped when the 22M28 circuit tripped, after a patroll the circuit was re-energized by SCADA. Pole fire at QT125 on the 22M28 (44kV) | Nepean | Adverse Environment | Salt Spray
18301 | 2011 | 6 | 5 | 0.88056 |  | 34 | 4 | 7 | Stafford | 8/4.8kV | 200F3 | Fuse found open on X3371 in the rear of 17 Dumas, refused and holding | Nepean | Unknown/Other | No Apparent Cause
18589 | 2011 | 7 | 5 | 0.26736 |  | 267 | 343 | 77 | Stafford | 8/4.8kV | 200F3 | 200F3 auto reclosed and locked out. 200T1 transformer white phase fuse opened at the same time causing a brown out condition on the B1 bus. The 200F1 and 200F2 were then forced out of service. 200F3 egress cable was tested and the overhead patrolled. No causes found. | Ottawa | Unknown/Other | No Apparent Cause
18734 | 2011 | 7 | 18 | 0.94028 |  | 106 | 132 | 75 | Stafford | 8/4.8kV | 200F3 | Downed Primary and Secondary neutral caused G1059 to blow on Foothills. Repairs made, G1059 refused and closed. | Nepean | Adverse Weather | Wind
7014 | 2005 | 7 | 23 | 0.92431 |  | 69 | 9 | 8 | Stafford | 8/4.8kV | 200f3 | transformer fuse cut out failed @ 42 Lankspur St. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
10965 | 2007 | 7 | 30 | 0.0125 |  | 402 | 60 | 9 | Stafford | 8/4.8kV | 200F3 | Transformer failure caused the down ground to become energized and burned the base of the pole | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8948 | 2006 | 8 | 10 | 0.83958 |  | 513 | 9 | 7 | Stafford | 8/4.8kV | 200F3 | 200F3 opened to allow crew to isolate pole on O/H section of line Between Taps east of S662 and S705. 7 customers out for duration of isolation, one customer out (LOEB TE2919 ) after isolation. LOEB will be restored when pole replaced. | Nepean | Adverse Environment | Fire
8950 | 2006 | 8 | 11 | 0.18403 |  | 9 | 1 | 7 | Stafford | 8/4.8kV | 200F3 | 200F3 opened to allow crew to connect double dead end taps. | Nepean | Adverse Environment | Fire
11207 | 2007 | 8 | 29 | 0.76875 |  | 49 | 215 | 263 | Stafford Road | 8/4.8kV | 200F3 | Circuit opened and locked out, closed in via SCADA and circuit is holding | Nepean | Adverse Weather
19326 | 2011 | 10 | 5 | 0.45417 |  | 34 | 107 | 188 | Stafford Road | 8/4.8kV | 200F3 | A switch fell across across the 22M23 and 200F3 circuits while a crew were installing them to replace the MSO370 (Job# 1187, PC2-61569) at 4 Cassidy . Crew clear the overhead and breakers were closed back in. Queensway Carleton and Bayshore substations were affected. 47F6 load was transfered to the 160F3 and was also affected. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11500 | 2007 | 10 | 12 | 0.99097 |  | 518 | 1357 | 263 | Stafford | 8/4.8kV | 200F3 | A pole fire caused the top of 200F3 dip pole feeding switch S662 @ rear of bexley place to burn off. Wires down on ground. Damaged section isolated, cct restored. 2 transformers at 10 Stafford remained off until repairs completed | Nepean | Defective Equipment | Imminent Equipment Failure Detected
11510 | 2007 | 10 | 13 | 0.38194 |  | 650 | 65 | 6 | Stafford | 8/4.8kV | 200F3 | Isolation to allow contractor to replace privately owned pole line, PC10C to Carleton electric | Nepean | Scheduled Outage
9453 | 2006 | 10 | 17 | 0.90764 |  | 163 | 377 | 263 | Stafford | 8/4.8kV | 200F3 | A fallen tre had to removed from the feeder as well as loose connectiions on an in line switch had to be replaced | Nepean | Defective Equipment
7479 | 2005 | 10 | 18 | 0.83819 |  | 325 | 414 | 299 | Stafford Rd | 8/4.8kV | 200F3 | Pole fire at 34 Stafford Rd - required the 44kv and 8kv circuits to be interrupted for the fire department to extinguis the flames. Damaged poles were scetionalized to restore most of the power. On-call crew made temporary repairs and the rest of the customers were restored. | Nepean | Adverse Environment | Fire
9801 | 2006 | 12 | 6 | 0.43125 |  | 58 | 254 | 263 | Stafford | 8/4.8kV | 200F3 | Tree limb caused 200F3 breaker to open. Customers heard loud bang near 26 foothill in the park.Limb cleared and breaker closed. | Nepean | Tree Contacts | Tree Limb Fallen
15482 | 2009 | 12 | 7 | 0.53125 |  | 35 | 7 | 12 | Stafford | 8/4.8kV | 200F3 | Transformer #X39687 located at 15 Thorncliff isolated due to changing arrestors | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9824 | 2006 | 12 | 10 | 0.5 |  | 164 | 8 | 3 | Stafford | 8/4.8kV | 200F3 | TP1162 @ 30 Stafford was isolated to allow crew to replace leaking tranformer. | Nepean | Scheduled Outage | Repair
13948 | 2009 | 2 | 9 | 0.67708 |  | 111 | 74 | 40 | Stafford | 8/4.8kV | 200F5 | Lead came out of switch S1141 @ 420 Moodie feeding two transformers. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
17643 | 2011 | 2 | 24 | 0.67639 |  | 27 | 557 | 1238 | Stafford | 8/4.8kV | 200F5 | At 16:14 the Stafford DS 200F1 and 200F5 tripped and locked out. The crews on scene found a burnt squirel. 615 customers on the 200F1 and 1238 customers on the 200F5 were affected for 27 mins. STAFFORD DS 200F1, 200F5 ID# 17643 | Nepean | Foreign Interference
4982 | 2004 | 4 | 8 | 0.59722 |  | 21 | 6 | 16 | Stafford | 8/4.8kV | 200F5 | TE1209 isolated to change transformer bushing. # 10,12,16,18 Seyton Dr power out to make repairs. Customers notified at the door 30 minutes prior. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12309 | 2008 | 4 | 19 | 0.82292 |  | 450 | 163 | 43 | Stafford | 8/4.8kV | 200F5 | Defective elbows at transformer T1502 at 4 lovell caused fuse S1262W to open interrupting 4 transformers. Crew replaced elbows and cleaned transformer. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
14391 | 2009 | 5 | 21 | 0.54792 |  | 37 | 7 | 12 | Stafford Road | 8/4.8kV | 200F5 | TE1159 on the 8KV in Bells Corners was isolated for crews to repair a defective primary bushing. | Nepean | Scheduled Outage | Repair
14404 | 2009 | 5 | 24 | 0.32569 |  | 63 | 5 | 5 | Stafford | 8/4.8kV | 200F5 | Overhead transformer X09910 @ trailer park opened feeding customers on Vanier rd in bells corners. | Nepean | Unknown/Other | No Apparent Cause
14458 | 2009 | 6 | 4 | 0.39861 |  | 373 | 62 | 10 | Stafford | 8/4.8kV | 200F5 | TE458 at 22 Cymbeline isolated to upgrade transformer. Nomenclature changed to TP6744. | Nepean | Scheduled Outage | Construction
14464 | 2009 | 6 | 4 | 0.4375 |  | 348 | 104 | 18 | Stafford | 8/4.8kV | 200F5 | at 10:30 trans at 22 Cymbeline was isolated in ordeer to replace the trans and the base | Ottawa | Scheduled Outage | Preventive Maintenance
8456 | 2006 | 6 | 9 | 0.53472 |  | 145 | 22 | 9 | Stafford | 8/4.8kV | 200F5 | Isolated transformer NP000467 at 22 Tanglewood Dr to re-install primary neutral that had been pulled down by the box of a dump truck | Nepean | Foreign Interference | Vehicle
8499 | 2006 | 6 | 16 | 0.57292 |  | 188 | 1592 | 508 | Stafford | 8/4.8kV | 200F5 | Bell wires, cablevision and our system neutral was contacted by a Tomlinson dumptruck on Moodie Drive at Hadley Circle. The contact broke the neutral conductor, caused a nearby pole to lean over & broke switch S1012. Temporary repairs wer made to the pole, neutral and switch and power was restored to all customers. | Nepean | Foreign Interference | Vehicle
14780 | 2009 | 7 | 18 | 0.69722 |  | 84 | 102 | 73 | Stafford | 8/4.8kV | 200F5 | Defective termination at S863, caused power outage to 5 transformers. Switching performed to isolate switch and restore power. | Nepean | Defective Equipment
3943 | 2003 | 8 | 26 | 0.38194 |  | 360 | 60 | 10 | Stafford | 8/4.8kV | 200F5 | S1301 switch opened to install new transformer on Tyrell Place. 10 customers affected in power outage. | Nepean | Scheduled Outage | Construction
9231 | 2006 | 9 | 16 | 0.36181 |  | 385 | 13 | 2 | Stafford | 8/4.8kV | 200F5 | Transformer at 340 Moodie isolated for replacement. Note: customer also did work on their plant. ESA approval #11822465 received. | Nepean | Scheduled Outage | Construction
11367 | 2007 | 9 | 23 | 0.70764 |  | 78 | 390 | 300 | Stafford | 8/4.8kV | 200F5 | White phase lead burnt off at S1541 near Stafford Stn, lead was cleared from O/H & the switch, customers were restored from alternate source, 47F5. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11441 | 2007 | 10 | 2 | 0.42083 |  | 369 | 68 | 11 | Stafford rd | 8/4.8kV | 200F5 | TE509 including cable to riser isolated for cable replacement. 419 Moodie dr. | Nepean | Scheduled Outage | Construction
4456 | 2003 | 11 | 14 | 0.35486 |  | 76 | 622 | 800 | Stafford | 8/4.8kV | 200F5 | 200F5 breaker open under Hold Off, crew have been cleared breaker closed back in picking up app. 600 customers. A W Phase switch at S1012 was found open crews repair and closed back in. | Nepean | Adverse Weather | Wind
7628 | 2005 | 11 | 17 | 0.94444 |  | 121 | 95 | 50 | Stafford | 8/4.8kV | 200F5 | A blown cable bet Transformer TE509W(7 Hadley) & TE442W(4 Tanglewood). | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4560 | 2003 | 12 | 5 | 0.39583 |  | 75 | 12 | 10 | Stafford | 8/4.8kV | 200F5 | Transformer TE1204 on Seyton Drive in Nepean was isolated to allow for the replacement of elbows and bushing inserts. ID#4560 | Nepean | Scheduled Outage | Preventive Maintenance
4562 | 2003 | 12 | 5 | 0.47222 |  | 70 | 12 | 10 | Stafford | 8/4.8kV | 200F5 | Transformer TE1208 on Seyton Drive in Nepean was isolated to allow for the replacement of elbows and bushing inserts. ID#4562 | Nepean | Scheduled Outage | Preventive Maintenance
20282 | 2012 | 4 | 4 | 0.63681 |  | 148 | 114 | 517 | Stafford | 8/4.8kV | 200F6 | 200F6 breaker A/R & locked out. Crews found blown switches and arresters at S198, 145 Robertson Rd. Repaired and power restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12261 | 2008 | 4 | 9 | 0.67708 |  | 25 | 5 | 11 | Stafford | 8/4.8kV | 200F6 | Transformer #TE1888 located at 15 Fitzgerald isolated to disconnect service due to flooding | Nepean | Adverse Environment | Flooding
3364 | 2003 | 4 | 22 | 0.013889 |  | 40 | 1 | 2 | Stafford | 8/4.8kV | 200F6 | S1324 opened to repair defective hot line clamp & defective stirup. Outage affected 175 & 165 Robertson Rd. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
14430 | 2009 | 5 | 30 | 0.23958 |  | 441 | 15 | 2 | Stafford | 8/4.8kV | 200F6 | TE1888 at 17 Fitzgerald was isolated to plug ducts in transformer pit & customer to perform secondary work. | Nepean | Scheduled Outage | Preventive Maintenance
10629 | 2007 | 6 | 14 | 0.5 |  | 43 | 4 | 6 | Queensway Carleton | 8/4.8kV | 200F6 | Transformer #NP001313 located at 160 Robertson isolated to transfer secondary service | Nepean | Scheduled Outage | Construction
14728 | 2009 | 7 | 11 | 0.73611 |  | 135 | 2 | 1 | Stafford Road | 8/4.8kV | 200F6 | Transformer at 85 Robertson road was isolated to be replaced due to damage from storm. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5505 | 2004 | 7 | 16 | 0.41667 |  | 176 | 3 | 1 | Stafford | 8/4.8kV | 200F6 | Isolate transforme 2401 at 145 Robertson Rd to replace bayonette fuses. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5663 | 2004 | 8 | 10 | 0.83333 |  | 2263 | 377 | 10 | Stafford | 8/4.8kV | 200F6 | Transformer TE1119B @ 90 Florizel was hit by lightning and had a oil leak. | Nepean | Adverse Weather | Lightning
9103 | 2006 | 8 | 30 | 0.73958 |  | 128 | 15 | 7 | Stafford | 8/4.8kV | 200F6 | TE1887 isolated and changed due to leak. New transformer TP3629. | Nepean | Scheduled Outage | Repair
16929 | 2010 | 9 | 12 | 0.74306 |  | 117 | 21 | 11 | Stafford | 8/4.8kV | 200F6 | S1431 at 16 Fitzgerald opened to isolate TE1888 to change hotline clamp | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5803 | 2004 | 9 | 14 | 0.64861 |  | 26 | 1 | 2 | Stafford | 8/4.8kV | 200F6 | Customer part out at Graham Nissan. Line clamp and arrestor repaired. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7390 | 2005 | 9 | 28 | 0.39583 |  | 30 | 3 | 6 | STAFFORD | 8/4.8kV | 200F6 | HOT LINE CLAMP ARCING @ 60-72 ROBERTSON RD. TE328 ISOLATED TO MAKE REPAIRS. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
13479 | 2008 | 10 | 28 | 0.85069 |  | 5 | 4 | 42 | STAFFORD | 8/4.8kV | 200F6 | Breaker closed from SCADA and holding | Nepean | Adverse Weather
13501 | 2008 | 10 | 28 | 0.85069 |  | 246 | 172 | 42 | Stafford | 8/4.8kV | 200F6 | 200F6 opened, patrolled and found nothing closed and held via scada | Nepean | Adverse Weather
13514 | 2008 | 10 | 29 | 0.15 |  | 27 | 0 | 42 | STAFFORD | 8/4.8kV | 200F6 | 200F6 closed back in and holding | Nepean | Adverse Weather
9604 | 2006 | 11 | 5 | 0.64028 |  | 533 | 156 | 60 | Stafford | 8/4.8kV | 200F6 | A defective transformer TE470B @ 27 Westcliffe Rd. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9791 | 2006 | 12 | 3 | 0.44444 |  | 277 | 9 | 2 | Stafford | 8/4.8kV | 200F6 | Isolated a section of O/H on Stafford Rd to replace insulators | Nepean | Scheduled Outage | Preventive Maintenance
17418 | 2010 | 12 | 13 | 0.52917 |  | 58 | 4 | 4 | Stafford | 8/4.8kV | 200F6 | Switch S1631 at 320 Moodie was isolated to allow crew to repair defective terminations at S1631. 4 customers were affected for 58 minutes. Stafford (200F6) ID #17418 | Nepean | Defective Equipment
7124 | 2005 | 8 | 11 | 0.63611 |  | 7 | 236 | 2019 | Moulton | 27.6/16kV | 2019 | Auto reclose Auto on the 8F1. No reports of accidents from police or fire. Breaker closed from SCADA. 70 amps at CSIS auto transfer did not work. Done manually by CSIS. Flashed insulator at Montreal Rd and HWY174. | Gloucester | Foreign Interference | Bird
7782 | 2006 | 1 | 8 | 0.17917 |  | 2 | 7 | 200 | Longfield | 27.6/16kV | 210F1 | The 210F1 was open to allow the crew to to operate inline switches to pick up the remaining load from the 606F2. | Nepean | Scheduled Outage | Repair
10123 | 2007 | 3 | 13 | 0.75278 |  | 68 | 283 | 250 | Longfields | 27.6/16kV | 210F1 | 210F1 (also feeding station service for Longfields) opened when 2 birds came in contact with hydro plant at or near S7028 at 110 Berrigan. With no station service breaker operation is not possible, circuit did not reclose, and switching to restore station service was required before restoring load. No apparent damage to hydro plant. | Nepean | Foreign Interference | Animal
5433 | 2004 | 7 | 2 | 0.61667 |  | 772 | 1089 | 110 | Longfields | 27.6/16kV | 210F1 | Lightning strike on the overhead caused insert at TE3167 to blow, Also damaged O/H Transformer 750 at 33 DeerFox | Nepean | Adverse Weather | Lightning
16463 | 2010 | 7 | 13 | 0.50486 |  | 53 | 1 | 1 | longfield |  | 210F1 | 210F1 Auto-Reclosed, RED Phase Trip Flag caused by a crow making contact with a O/H transformer at Woodroffe. | Nepean | Foreign Interference | Bird
16532 | 2010 | 7 | 21 | 0.83056 |  | 414 | 21 | 3 | Long Fields | 27KV | 210F1 | Transformer X36956 @ 22 Fieldcrest Ave elbow failed due to lightning strike on transformer. 3 customers were affected. Circuit feeding transformer is abnormal. Normal configuration from 7F2. | Nepean | Lightning
16535 | 2010 | 7 | 21 | 0.83056 |  | 1680 | 3640 | 130 | Longfields | 27KV | 210F1 | Lighnting storm caused a blown elbow at TE3193 @ Central Park Lodge, causing blue phase of S7086 to open. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
16538 | 2010 | 7 | 22 | 0.45486 |  | 110 | 2 | 1 | Longfields | 27.6/16kV | 210F1 | TE3193, Central Park lodge in Barhaven was isolated to repair damaged elbows & bushings from earlier lightning strike. | Nepean | Adverse Weather | Lightning
5567 | 2004 | 7 | 26 | 0.4 |  | 216 | 29 | 8 | Longfield |  | 210F1 | scheduled outage to replace transformer | Nepean | Scheduled Outage | Preventive Maintenance
5656 | 2004 | 8 | 10 | 0.81181 |  | 11 | 38 | 210 | Longfield | 27.6/16kV | 210F1 | 210F1 open up veritied with Hydro one of any problems none found closed back in and holding. | Nepean | Adverse Weather | Lightning
7116 | 2005 | 8 | 10 | 0.66319 |  | 5 | 33 | 400 | Longfields | 27.6/16kV | 210F1 | Longfields 210F1 auto trip, closed via SCADA. | Nepean | Adverse Weather
11057 | 2007 | 8 | 15 | 0.079861 |  | 10 | 83 | 500 | Longfields | 8/4.8kV | 210F1 | 210F1 Breaker auto reclosed, tripped due to severe lightning storm in effect. | Nepean | Adverse Weather | Lightning
11097 | 2007 | 8 | 19 | 0.275 |  | 168 | 6 | 2 | Longfields | 27.6/16kV | 210F1 | Scada indicated that the 210F1 auto reclosed at 6:36 AM, trouble call came from 3102 Woodroffe Ave, 24/7 reports squirrle contact caused the transformer fuse to blow, 24/7 refused transformer, all power restored. | Nepean | Foreign Interference | Animal
14993 | 2009 | 8 | 22 | 0.32986 |  | 46 | 153 | 200 | Longfields | 27.6/16kV | 210F1 | 210F1 tripped open with no attempt to auto reclose, crew patrolled quickly and found nothing, closed via scada and all load seems to have been restored. | Nepean | Unknown/Other
11259 | 2007 | 9 | 6 | 0.43056 |  | 120 | 6 | 3 | Longfields | 27.6/16kV | 210F1 | Section of o/h line on Deerfield at Woodroffe isolated for working clearance to transfer plant to new pole. | Nepean | Scheduled Outage | Construction
9160 | 2006 | 9 | 8 | 0.75694 |  | 114 | 665 | 350 | Longfields | 27.6/16kV | 210F1 | Severe Storm caused 210F1 at Longfields to trip. No SCADA control. Unable to close from station, because RTU power was down. Picked up from S7000, 606F1 circuit. | Nepean | Adverse Weather
16995 | 2010 | 9 | 25 | 0.1125 |  | 376 | 215 | 85 | Longfields | 27.6/16kV | 210F1 | A defcective leaking transformer, TE2508 at 143 Woodgate caused 210F1 to A/R & S7021W to blow. Customers restored in stages as defective transformer identified & isolated. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4191 | 2003 | 10 | 1 | 0.45556 |  | 93 | 89 | 150 | Longfield | 27.6/16kV | 210F1 | TE3590 was isolated to raise Trans. Grade. There was an outage because of an out of phase switch that had to be operated to restore the remaining Trans. It was performed twice to restore TE3590. | Nepean | Scheduled Outage | Preventive Maintenance
9377 | 2006 | 10 | 4 | 0.38889 |  | 98 | 3 | 2 | Longfields | 27.6/16kV | 210F1 | Transformer #NP750 located at 23 Deerfox isolated to allow plant transfer. PC10A #1474 | Nepean | Scheduled Outage
17078 | 2010 | 10 | 7 | 0.45694 |  | 481 | 132 | 31 | Longfields | 27.6/16kV | 210F1 | Transformers TE2507, TE2508 and TE2509 isolated to allow crew to remove oil contaminated soil. Transformers restored at different times. | Nepean | Scheduled Outage
17233 | 2010 | 11 | 6 | 0.39583 |  | 10 | 167 | 1000 | Longfields | 27.6/16kV | 210F1 | 210F1 carrying some Fallowfield load, tripped for no apparent reason. Waiting on OMS calls. | Nepean | Unknown/Other | No Apparent Cause
15423 | 2009 | 11 | 25 | 0.58889 |  | 22 | 1283 | 3500 | Longfields | 27.6/16kV | 210F1 | 210F1 opened under hold off. Apparent cause was a defective transformer which caused CB to open when crew attempted to re-fuse. | Nepean | Defective Equipment
9757 | 2006 | 11 | 30 | 0.24236 |  | 163 | 7156 | 2634 | Longfields | 27.6/16kV | 210F1 | 210F1 breaker carrying all of 606F1 due to bank out of service at Fallowfield. 210F1 tripped and could not be closed due to loss of AC supply. No manual close. (Why do we buy reclosers that can't be closed manually ?) 634 customers from 210F1, 2000 customers from 606F1 | Nepean | Unknown/Other | No Apparent Cause
4724 | 2004 | 1 | 23 | 0.30903 |  | 86 | 573 | 400 | Longfields |  | 210F2 | 210F2 locked out line patrolled no cause found | Nepean | Unknown/Other | No Apparent Cause
14004 | 2009 | 2 | 25 | 0.44792 |  | 65 | 5 | 5 | Longfields | 27.6/16kV | 210F2 | TP2829 @ 14 tradewinds was replaced due to contact with a snowplow. | Nepean | Foreign Interference | Vehicle
8409 | 2006 | 6 | 2 | 0.23681 |  | 12 | 73 | 367 | Longfields | 27.6/16kV | 210F2 | Breaker open for no apparent cause. Breaker closed from SCADA and holding | Nepean | Unknown/Other | No Apparent Cause
20906 | 2012 | 7 | 1 | 0.86597 |  | 12 | 442 | 2211 | Longfields | 27.6/16kV | 210F2 | 210F2 breaker opened and locked out fire and police were called and circuit was closed and held. Crew patrolled circuit and no sign of fault was found. Longfieds ID#20906 | Nepean | Unknown/Other
8793 | 2006 | 7 | 21 | 0.31181 |  | 13 | 43 | 200 | Longifleds | 27.6/16kV | 210F2 | 210F2 Breaker Tripped under hold off. Patrolled Circuit. Nothing found | Nepean | Unknown/Other
5657 | 2004 | 8 | 10 | 0.81181 |  | 12 | 5 | 25 | Longfield | 27.6/16kV | 210F2 | 210F2 opened up notified Hydro One if they have any problem none was found, closed back in and holding | Nepean | Adverse Weather | Lightning
3959 | 2003 | 8 | 27 | 0.375 |  | 75 | 4 | 3 | LONGFIELD |  | 210F2 | THE TRANSFORMER AT 6058 FALLOWFIELD WAS OPENED TO REPLACE CONNECTION AT BUSHING | Nepean | Defective Equipment | Equipment Deterioration Due to Age
19402 | 2011 | 10 | 18 | 0.41667 |  | 50 | 23 | 27 | Longfields | 27.6/16kV | 210F2 | Isolated transformer TP7284 at 3144 Burritts Rapids Pl and TP7283 at 2032 Seeleys Bay St for electrician to pull in new secondary conductor for new services | Nepean | Scheduled Outage | Emergency Services Request
19410 | 2011 | 10 | 19 | 0.41667 |  | 175 | 79 | 27 | Longfields | 27.6/16kV | 210F2 | Isolated transformer TP7284 at 3144 Burritts Rapids Pl and TP7283 at 2032 Seeleys Bay St for electrician to pull in new secondary conductor for new services | Nepean | Scheduled Outage | Construction
17250 | 2010 | 11 | 9 | 0.39931 |  | 104 | 53 | 83 | Longfields | 27.6/16kV | 210F2 | At 09:35 transformer TP5818 at 3534 Cambrian Road was isolated to allow crew to repair ground grid. 9 customers were affected for 74 minutes and 83 customers were affected for a total of 30 minutes due to out of phase conditions. Longfields (210F2) ID #17250 | Nepean | Scheduled Outage
9842 | 2006 | 12 | 14 | 0.97014 |  | 20 | 0 | 1 | Albion | 13.2kV | 2201 | VT399 @ 1670 Heron Rd was isolated to allow cable crew to check S-287. Cable crew reports interal switch looks to be in good shape. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8394 | 2006 | 5 | 31 | 0.73958 |  | 48 | 755 | 944 | ALBION | 13.2kV | 2201, 2205 | TA06 breaker tripped during a thunder storm, lightning reported in area at time of trip, circuit patrolled & no problem found, breaker closed & held. | Ottawa | Adverse Weather | Lightning
17061 | 2010 | 10 | 5 | 0.61458 |  | 91 | 1462 | 1750 | Albion | 13.2kV | 2201, 2205 | TA06 breaker- 2201, 2205 circuit tripped off due to fault on cable or overhead. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8583 | 2006 | 6 | 23 | 0.72917 |  | 25 | 389 | 934 | Albion TA | 13.2kV | 2201-2205 | TA06 Breaker opened Circuits 2201 & 2205. 24/7 crew was in the west end, Fire and Police called, no rpts made. TA06 Breaker closed in, All load restored. Crew to patrol Lines. Howatt rpts relay flags - Grd -time | Ottawa | Unknown/Other | No Apparent Cause
12029 | 2008 | 2 | 9 | 0.41667 |  | 229 | 8 | 2 | Albtion | 13.2kV | 2202 | SW 137 @ 2151 Thurston to allow crew to change PT 151. 2 customers affected. 2202 circuit. | Ottawa | Scheduled Outage
12830 | 2008 | 7 | 12 | 0.375 |  | 1137 | 67 | 480 | Albion | 13.2kV | 2202 | At 9:00am vault VT654 was isolated to allow contractor to perform customer vault maintenance, 1 customer was originally affected until restoration, when the TA24 breaker opened due to a transformer fault in VT654. 480 customers were then affected for 6 minutes while isolation was given back to VT654. After cleanup of explosion and replacement of transformer was completed the 1 remaining customer had their power restored at 3:57am. Albion (2202). ID#12830. | Ottawa | Defective Equipment
19120 | 2011 | 9 | 8 | 0.63542 |  | 209 | 86 | 30 | Albion | 13.2kV | 2202 | Switch SC7 was found with the SC701-F fuses blown for no apparent reason. Cables were picked one at a time to allow for crew to hi pot each section. Albion (2202) ID#19120. | Ottawa | Unknown/Other | No Apparent Cause
17440 | 2010 | 12 | 21 | 0.15347 |  | 103 | 1590 | 926 | Albion | 13.2kV | 2202 | Defective Cable on TA02 circuit was isolated and all power restored. Lorry Greenber, Huntclub, Cahill area. | Ottawa | Defective Equipment
12825 | 2008 | 7 | 12 | 0.60764 |  | 6 | 48 | 480 | Albion | 13.2kV | 2202 - TA3UZ | TA24 breaker at albion opened when energizing VT654 @ 2340 St. Laurent. A 347/600 transformer in the vault exploded. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
13970 | 2009 | 2 | 12 | 0.95139 |  | 100 | 1813 | 1088 | Albion TS | 13.2kV | 2202 & TA3UZ | TA24 CB opened up due to a cable fault between Albion TS & VT562. | Ottawa | Defective Equipment
12733 | 2008 | 6 | 26 | 0.68125 |  | 90 | 1431 | 954 | Albion | 13.2kV | 2202 & TA3UZ | SC7 was hit by lightning causing a flash on overhead circuit. | Ottawa | Adverse Weather | Lightning
13846 | 2009 | 1 | 7 | 0.57431 |  | 51 | 349 | 411 | Albion | 13.2kV | 2203 | Tandem Network dug into 2203 cable to VT318 at 1800 Walkley causing TA21 breaker to trip. Damaged cable was isolated & power restored. | Ottawa | Foreign Interference | Dig-in
14110 | 2009 | 3 | 29 | 0.60833 |  | 91 | 170 | 112 | Albion | 13.2kV | 2203 | TB22 breaker A/R at same time that TA21 tripped, possible insulator leakage caused flash & grass is smouldering at bottom of pole. 24/7 reports primary conductors are intact, OK to restore cct. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14113 | 2009 | 3 | 29 | 0.67431 |  | 159 | 297 | 112 | Albion | 13.2kV | 2203 | Circuit tripped after attempting to restore, possible defective insulators or wet weather. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16063 | 2010 | 5 | 8 | 0.38056 |  | 68 | 98 | 113 | Albion | 13.2kV | 2203 | TA21 breaker tripped interrupting power to 2203 line. All customers were restored from alternate sources. Circuit isolated for repairs. | Ottawa | Unknown/Other
12734 | 2008 | 6 | 26 | 0.67431 |  | 123 | 843 | 411 | Albion | 13.2kV | 2203 | SC7 was hit by lightning causing flash on overhead circuit | Ottawa | Adverse Weather | Lightning
12629 | 2008 | 6 | 15 | 0.3375 |  | 54 | 101 | 112 | Albion | 13.2kV | 2203 (TA21) | TA21 breaker tripped open. Fuses to underground not blown, overhead placed on potential and held, then underground load restored to normal. Crew to patrol overhead for possible cause. Squirrel found at switch 5309-2203. | Ottawa | Foreign Interference | Animal
10030 | 2007 | 2 | 16 | 0.73472 |  | 12 | 5 | 23 | Albion | 13.2kV | 2204 | Transformer KT0352 at 40 Castlegreen blew (SC1702) a fuse,We refused transformer and restored power | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3290 | 2003 | 3 | 23 | 0.13611 |  | 13 | 169 | 778 | Albion | 13.2kV | 2204 | Bad Lightnig arrestor on TA1AN circuit flashed over and took out circuit. MDF See outage 3291 - same outage on diff cct. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14119 | 2009 | 3 | 30 | 0.52083 |  | 70 | 14 | 12 | Albion | 13.2kV | 2204 | Transformer MT1643 at 13 Craighall isolated for planned replacement of damaged transformer. | Ottawa | Scheduled Outage | Repair
5106 | 2004 | 5 | 5 | 0.59722 |  | 10 | 2 | 14 | Albion | 13.2kV | 2204 | To reconnect U/G service at KT244 at address 19 Thornhedge. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8344 | 2006 | 5 | 24 | 0.40833 |  | 352 | 12 | 2 | Albion | 13.2kV | 2204 | SW102 was found to be badly burned and required emergency isolation and replacement. Crew found a burnt mouse. Installed new PMH-9 switch | Ottawa | Scheduled Outage | Repair
18426 | 2011 | 6 | 16 | 0.39375 |  | 249 | 2270 | 547 | Albion | 13.2kV | 2204 | SW102 at 270 Lorry Greenberg was isolated to allow crews to replace defective operating springs | Ottawa | Scheduled Outage | Repair
5560 | 2004 | 7 | 24 | 0.0076389 |  | 3 | 39 | 778 | Albion | 13.2kV | 2204 | Appears that a defective arrestor at Lorry Greenberg and Huntclub, was responsible for causing 2204 circuit to open. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8832 | 2006 | 7 | 25 | 0.42361 |  | 100 | 2 | 1 | Albion | 13.2kV | 2204 | Fuse on switch to transformer at 3145 Conroy Rd was found blown due to bird contact | Ottawa | Foreign Interference | Bird
8912 | 2006 | 8 | 2 | 0.93889 |  | 21 | 272 | 778 | Albion | 13.2kV | 2204 | Circuit tripped during thunderstorm at the same time as TA1AN & AN06 tripped. All 3 circuits run together. Reclosure was in service however SCADA Event Summary does not show breaker attempted a reclose. Breaker was closed manually from SCADA after the area was confirmed clear of emergency calls. | Ottawa | Adverse Weather | Lightning
4594 | 2003 | 12 | 12 | 0.61458 |  | 33 | 5 | 9 | Albion | 13.2kV | 2204 | Transformer opened to install cab tire. 9 customers effected in power outage. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13775 | 2008 | 12 | 17 | 0.84653 |  | 108 | 38 | 21 | Albion | 13.2kV | 2204 | Transformer #KT402 located at 77 Finland Pvt isolated due to a blown transformer fuse. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5556 | 2004 | 7 | 23 | 0.51042 |  | 80 | 27 | 20 | TA | 13.2kV | 2204/SC1101 | KT366 at 82 Burlington opened to replace defective transformer. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6115 | 2005 | 1 | 3 | 0.66667 |  | 40 | 8 | 12 | Albion | 13.2kV | 2205 | Transformer was isolated to make perminant repairs to transformer switches. See interuption 6111 for initial interruption. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9916 | 2007 | 1 | 11 | 0.43056 |  | 5 | 1 | 12 | Albion | 13.2kV | 2205 | Dave Howat isolated KT029 to connect a repaired defective service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19814 | 2012 | 1 | 11 | 0.39931 |  | 120 | 34 | 17 | Albion | 13.2kV | 2205 | KT117 and KT118 transformers on Tapiola were isolated to replace defective insulators. | Ottawa | Scheduled Outage | Repair
19824 | 2012 | 1 | 13 | 0.43403 |  | 58 | 14 | 15 | Albion | 13.2kV | 2205 | KT101 at 9 Brando cres. Was isolated to check for cracked insultors, inspection , cleaning and torque. | Ottawa | Scheduled Outage | Preventive Maintenance
19870 | 2012 | 1 | 20 | 0.43264 |  | 124 | 27 | 13 | Albion | 13.2kV | 2205 | Transformer KT63 at 37 Gentle Gate isolated to replace defective terminations | Ottawa | Scheduled Outage
19878 | 2012 | 1 | 23 | 0.40903 |  | 83 | 0 | 13 | Albion | 13.2kV | 2205 | KT64 @ 13 Gentle gate was isolated for maintenance. | Ottawa | Scheduled Outage | Repair
19899 | 2012 | 1 | 26 | 0.40556 |  | 94 | 30 | 19 | Albion | 13.2kV | 2205 | 13KV transformer KT0025 at 2 Fallow was isolated to allow crew to replace cable termination. | Ottawa | Scheduled Outage | Preventive Maintenance
19922 | 2012 | 1 | 30 | 0.39931 |  | 71 | 27 | 23 | Albion | 13.2kV | 2205 | KT120 at 537 Wingale Private was isolated for HOL crew to repair defective elbow and insert. | Ottawa | Scheduled Outage
19949 | 2012 | 2 | 2 | 0.40139 |  | 67 | 22 | 20 | Albion | 13.2kV | 2205 | KT27 @ 61 Greenboro was isolated to allow crews to do preventive maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
19955 | 2012 | 2 | 3 | 0.40139 |  | 77 | 19 | 15 | Albion | 13.2kV | 2205 | KT39 @ 16 Fireside was isolated to repair secondary connections. | Ottawa | Scheduled Outage | Repair
20030 | 2012 | 2 | 17 | 0.39375 |  | 113 | 45 | 24 | Albion | 13.2kV | 2205 | Transformer KT156 @ Verdon Pvt. Was isolated to allow crew to repair broken elbow/insert. | Ottawa | Scheduled Outage | Repair
20149 | 2012 | 3 | 10 | 0.40417 |  | 6 | 182 | 1821 | Albion | 13.2kV | 2205 | TA06 breaker opened due to defective bushing on S21142 pothead at 1650 Walkley. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3312 | 2003 | 4 | 2 | 0.53819 |  | 12 | 2 | 12 | Albion | 13.2kV | 2205 | Defective secondary cable at Kt129. | Ottawa | Defective Equipment
3325 | 2003 | 4 | 8 | 0.44931 |  | 2 | 0 | 12 | Albion | 13.2kV | 2205 | Power off to KT129 in order to open cover on secondary pedestal to make temporary repairs to 10 Tammela. All customers notified in person of the momentary outages. | Ottawa | Scheduled Outage | Repair
18453 | 2011 | 6 | 21 | 0.47222 |  | 45 | 16 | 22 | Albion | 13.2kV | 2205 | Transformer #KT0153 located at 496 Sandhamn Pvt opened by crew to make repairs to secondary buss bar that burnt up. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3921 | 2003 | 8 | 20 | 0.57639 |  | 31 | 4 | 7 | Albion | 12/7.2kV | 2205 | Transformer KT117 isolated to disconnect defective street light service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16817 | 2010 | 8 | 25 | 0.75833 |  | 125 | 21 | 10 | Albion | 13.2kV | 2205 | Pete Bishop and Richard Barnett report PPH switch at Johnston and Tapiola feeding 10 red phase kiosks is closed and holding as per OTOJWF25AUG. | Ottawa | Unknown/Other | No Apparent Cause
4186 | 2003 | 9 | 30 | 0.40972 |  | 45 | 4 | 6 | Albion | 13.2kV | 2205 | Transformer #KT0117 at 126 Borga in Ottawa was isolated to allow the hook-up of streetlights. | Ottawa | Scheduled Outage | Construction
13308 | 2008 | 10 | 1 | 0.43403 |  | 156 | 52 | 20 | Albion TS | 13.2kV | 2205 | KT65 on Gentle Gate was isolated to replace rusted kiosk with a padmount transformer. 2205 out of Albion, 20 customers affected. | Ottawa | Scheduled Outage
13416 | 2008 | 10 | 23 | 0.37847 |  | 75 | 14 | 11 | Albion | 13.2kV | 2205 | KT64 at 13 Gentle Gate isolated to replace broken porcelain insulators in kiosk. | Ottawa | Scheduled Outage | Repair
13418 | 2008 | 10 | 23 | 0.43056 |  | 5 | 8 | 99 | Albion | 13.2kV | 2205 | Switching error caused loss of power to 9 transformers for 5 minutes in the Gentle Gate area out of Albion | Ottawa | Human Element | Switching Errors
4377 | 2003 | 11 | 3 | 0.40625 |  | 30 | 12 | 24 | Albion | 13.2kV | 2205 | Transformer #KT0028, at 86 Greenboro in Ottawa, was isolated to allow for the repair of a defective service at 106 Greenboro. ID#4377 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6111 | 2004 | 12 | 31 | 0.46111 |  | 121 | 143 | 140 | Albion | 13.2kV | 2205 | 2205 line fuse blew at dip pole to KT217 on blue phase at Johnson & Tapiola due to rainwater accumulating on insulating board in KT100 at 25 Brando and the insulators flashing over. The transformer was isolated and power restored to rest of customers. Temporary repairs made and KT100 restored. Follow up outage req'd to replace switchgear in KT100. | Ottawa | Adverse Weather | Rain
18957 | 2011 | 8 | 18 | 0.42153 |  | 13 | 6 | 26 | Albion | 13.2kV | 2205/SC401 | Transformer KT184 located at 44 Patola Pvt opened by crew to isolate metering cabinet that fell to the ground when a contractor was working around the gang meter base. | Ottawa | Scheduled Outage | Repair
19928 | 2012 | 1 | 30 | 0.52986 |  | 85 | 18 | 13 | Albion | 13.2kV | 2206 | KT196 at 66 Fardon Way was isolated for HOL crew to replace L/B Elbows on both primary cables | Ottawa | Scheduled Outage
9985 | 2007 | 2 | 3 | 0.40764 |  | 143 | 5 | 2 | Albion | 13.2kV | 2206 | Transformer PT118 on Stevenage Dr in Ottawa isolated for transformer upgrade. | Ottawa | Scheduled Outage | Construction
15735 | 2010 | 2 | 21 | 0.22222 |  | 70 | 9 | 8 | Albion | 13.2kV | 2206 | PT87 at Lorry Greenberg and Blohm DR isolated to make repairs to a hot connection in Sw117-F2 | Ottawa | Scheduled Outage | Preventive Maintenance
3273 | 2003 | 3 | 20 | 0.69097 |  | 29 | 718 | 1485 | TA | 13.2kV | 2206 | 2206 cct opened fault no cause found at this time. | Ottawa | Unknown/Other
4963 | 2004 | 4 | 2 | 0.42708 |  | 5 | 2 | 22 | Albion | 13.2kV | 2206 | Transformer KT0374 at 73 Woodbury Cre isolated to replace rusted out pedestal cover. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15958 | 2010 | 4 | 19 | 0.86597 |  | 443 | 81 | 11 | Albion |  | 2206 | KT506 on Pimlico was fauly and had to be replaced | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14256 | 2009 | 4 | 28 | 0.63333 |  | 112 | 589 | 876 | Albion | 13.2kV | 2206 | Blown termination at S27243 blue phase, Dip pole to SC12, caused outage to blue phase customers only out of SC12, at Hunt Club and Esson. Due to the lead blowing in the wind close to the neutral, System decided to expand the outage in order to pick up all load from the alternate source, TA1AN. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8430 | 2006 | 6 | 5 | 0.70833 |  | 100 | 35 | 21 | Albion | 13.2kV | 2206 | Transformer #KT0276 located at 1077 Ewing isolated due to blown fuse. Cause by a squirrel | Ottawa | Foreign Interference | Animal
10533 | 2007 | 6 | 5 | 0.39583 |  | 60 | 10 | 10 | Albion | 13.2kV | 2206 | Isolated transformer KT254 at 26 Raj to replace connections on secondary | Ottawa | Scheduled Outage | Preventive Maintenance
10534 | 2007 | 6 | 5 | 0.54167 |  | 30 | 8 | 16 | Albion | 13.2kV | 2206 | Isolated transformer KT277 at 37 Clifford to replace connections on secondary | Ottawa | Scheduled Outage | Preventive Maintenance
10686 | 2007 | 6 | 20 | 0.90972 |  | 68 | 14 | 12 | Albion | 13.2kV | 2206 | KT 264 at 22 Wallack Private isolated for replacment due to oil leak. Circuit 2206 off SC10 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12732 | 2008 | 6 | 26 | 0.67431 |  | 119 | 2945 | 1485 | Albion | 13.2kV | 2206 | SC7 switch was hit by lightning causing a flash on overhead circuit. | Ottawa | Adverse Weather | Lightning
8665 | 2006 | 7 | 5 | 0.44444 |  | 28 | 6 | 12 | Albion | 13.2kV | 2206 | Isolated transformer KT 253 at 865 Karsh Dr to repair underground service | Ottawa | Scheduled Outage | Repair
5470 | 2004 | 7 | 8 | 0.60417 |  | 45 | 8 | 10 | Albion | 13.2kV | 2206 | Isolate transformer KT 313 at the rear of 23 Hime Crst to relocate the service around the pool. | Ottawa | Scheduled Outage | Construction
3796 | 2003 | 7 | 19 | 0.85417 |  | 540 | 63 | 7 | Albion | 13.2kV | 2206 | Vehicle hit PT78 padmount transformer on Lorry Greenberg and shifted it off pad. Transformer was still energized. Transformer was isolated and replaced. Power was restored at 05:30 | Ottawa | Foreign Interference | Vehicle
8886 | 2006 | 8 | 1 | 0.079861 |  | 108 | 2700 | 1500 | Abion | 13.2kV | 2206 | Circuit tripped during heavy storm along with adjacent cct, TA1AN. | Ottawa | Adverse Weather | Lightning
8887 | 2006 | 8 | 1 | 0.15694 |  | 146 | 3500 | 1500 | Albion | 13.2kV | 2206 | Part of load transferred, problem identified at SC28, all customers except those supplied from SC28 restored. Fault finding continues. | Ottawa | Adverse Weather | Lightning
8899 | 2006 | 8 | 1 | 0.27083 |  | 428 | 2018 | 588 | Albion | 13.2kV | 2206 | 2206 outage was sectionalized down to a problem on SC2801. Cause of outage was a blown elbow @ KT1559.Circuit was sectionalized, customers were restored in stages with the last customers being restored at 12:10 | Ottawa | Defective Equipment
8902 | 2006 | 8 | 1 | 0.95139 |  | 430 | 79 | 11 | Albion | 13.2kV | 2206 | On call crew needed a crane to help change a backyard transformer at 11 Degas crt. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7332 | 2005 | 9 | 16 | 0.10417 |  | 275 | 5339 | 1485 | Albion | 13.2kV | 2206 | Circuit 2206 tripped due to fault at sectionalizer SC1360, load transferred to other supply. | Ottawa | Defective Equipment
4200 | 2003 | 10 | 2 | 0.73125 |  | 86 | 2110 | 1483 | Albion | 13.2kV | 2206 | Blown lightning arrestor probably caused by the wet weather opened 2206 circuit. | Ottawa | Defective Equipment
5826 | 2004 | 10 | 4 | 0.41528 |  | 129 | 2906 | 1485 | ALBION | 13.2kV | 2206 | A mouse caused a phase to phase flash in SC1360 | Ottawa | Foreign Interference | Animal
15251 | 2009 | 10 | 12 | 0.75 |  | 11 | 1 | 8 | Albion | 13.2kV | 2206 | At 18:00 trans KT501 at 59 Picasso Dr was isolated in order to make repairs in Ped 501P1 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19435 | 2011 | 10 | 21 | 0.4 |  | 384 | 128 | 20 | Albion | 4.16kV | 2206 | Crews isolated KT266 at 2 Moxley to change leaking transformer. | Ottawa | Scheduled Outage
5860 | 2004 | 11 | 5 | 0.42917 |  | 138 | 28 | 12 | TA | 13.2kV | 2206 | MT41 at 90 Allenford isolated to change leaking transformer. | Ottawa | Scheduled Outage | Repair
9699 | 2006 | 11 | 22 | 0.40347 |  | 34 | 7 | 12 | Albion | 13.2kV | 2206 | KT508 was isolated to allow crews to lift pedestal cover to repair U/G service. Unable to operate elbows due to shed. | Ottawa | Scheduled Outage | Preventive Maintenance
11869 | 2007 | 12 | 22 | 0.57292 |  | 112 | 202 | 108 | Albion | 13.2kV | 2206 | At 1:45pm, City of Ottawa dispatch informed us that one of their snowplows made contact with a pole at 2636 Stevenage Road at Swansea Road, causing a fused cutout to open at S-254, 108 customers were affected for 112 min. ID#11869. | Ottawa | Foreign Interference | Vehicle
6240 | 2005 | 2 | 28 | 0.53681 |  | 61 | 9 | 9 | Albion | 13.2kV | 2207 | Isolated transformer KT0762 at 75 Kimberwick Cres to fault find secondary service | Ottawa | Scheduled Outage | Repair
12109 | 2008 | 3 | 7 | 0.40347 |  | 89 | 15 | 10 | Albion |  | 2207 | Isolation of KT22 at 38 Rich Little to replace termination. | Ottawa | Scheduled Outage
12110 | 2008 | 3 | 7 | 0.52014 |  | 84 | 14 | 10 | Albion | 13.2kV | 2207 | KT24 at 22 Fox Hunt isolated to replace termination. | Ottawa | Scheduled Outage
3277 | 2003 | 3 | 21 | 0.94583 |  | 255 | 385 | 100 | Albion | 13.2kV | 2207 | SC1602-F blue phase fuse blew due to a barrier board falling in KT59. Cable betweenKT32 & KT59 left isolated due to poor megger reading. To be hipotted in day. Momentary outage taken on SC16 during restoration to refuse with no potential due to rain. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12244 | 2008 | 4 | 6 | 0.87361 |  | 980 | 16 | 1 | Albion | 13.2kV | 2207 | Defective cables to VT660 at 280 Hunt Club (Nav Canada) caused all 3 fuses at dip pole to blow. Oncall U/G & dayshift U/G crews spliced cables in MH2099. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14202 | 2009 | 4 | 23 | 0.39583 |  | 575 | 115 | 12 | Albion | 13.2kV | 2207 | KT331 @ 101 Twyford was isolated to allow the crew to cleanup previous oil leak with Drain All | Ottawa | Scheduled Outage | Repair
5321 | 2004 | 6 | 16 | 0.76528 |  | 423 | 49 | 10 | Albion | 13.2kV | 2207 | Defective minipad xfmr MT1737 changed. 10 customers on Annapolis Circle were affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12690 | 2008 | 6 | 18 | 0.83819 |  | 125 | 1466 | 1265 | Albion | 13.2kV | 2207 | SC16 at 3048 Uplands Dr customer reported sparking. Crew found terminations burnt and SC16 needs to be isolated. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12691 | 2008 | 6 | 19 | 0.42014 |  | 5 | 0 | 1 | Albion | 13.2kV | 2207 | VT351 at 3301 Uplands was isolated due to vent screen had fallen onto non-shield primary cable feeding transformer at VT351. | Ottawa | Defective Equipment
6986 | 2005 | 7 | 18 | 0.11111 |  | 270 | 2387 | 1101 | Albion TS | 13.2kV | 2207 | TA18 @ & breaker @ Albion TS tripped. 2207 was sectionalized and suspected cable fault isolated between SC19 & VT352. Further calls indicated not al power restored and SC1601-L at SC16 was found flashed over. Cable was not faulted as originally isolated and SC16 was isolated. | Ottawa | Defective Equipment
7143 | 2005 | 8 | 16 | 0.47917 |  | 24 | 4 | 10 | Albion | 12/7.2kV | 2207 | Trans KT340 was isolated at 5 Chancellor Crt in order to connect a new service | Ottawa | Scheduled Outage | Construction
4056 | 2003 | 9 | 11 | 0.54028 |  | 477 | 8 | 1 | TA | 13.2kV | 2207 | VT590, Cognos at 3755 Riverside was isolated to allow customer to make repairs to VT590-L xfmr bus cables. Loose connections were found on 13kv cable terminations which overheated & caused the cable to fail. The original trouble call came in at 10:30 a.m. | Ottawa | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
4227 | 2003 | 10 | 8 | 0.70486 |  | 203 | 177 | 100 | TA | 13.2kV | 2207 | A squirrel caused a flash at KT32, 23 Archer, causing the blue phase of SC1602 to open. 9 KT's were affected. The primary fuse @ KT32 also opened & had to be replaced resulting in an extended outage for the last 10 customers. | Ottawa | Foreign Interference | Animal
5833 | 2004 | 10 | 8 | 0.39583 |  | 60 | 13 | 13 | Albion | 13.2kV | 2207 | Secondary cable fault repairs. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13433 | 2008 | 10 | 27 | 0.022917 |  | 78 | 1667 | 1282 | Albion | 13.2kV | 2207 | TA18 breaker feeding 2207 cable (1282 customers) & TA2AE cable (0 customers, on pot only) tripped due to a probable cable faulted. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9592 | 2006 | 11 | 3 | 0.41667 |  | 32 | 6 | 12 | Albion | 13.2kV | 2207 | Transformer #KT288 located at 207 Twyford isolated to make repairs to U/G service | Ottawa | Scheduled Outage | Repair
11843 | 2007 | 12 | 13 | 0.41875 |  | 85 | 89 | 63 | Albion | 13.2kV | 2207 | At 10:03am transformer KT330 on Twyford Road was isolated for crews to repair a leak, 63 customers affected for 85 min. ID#11843. | Ottawa | Scheduled Outage | Repair
10593 | 2007 | 6 | 11 | 0.21528 |  | 103 | 258 | 150 | Albion | 13.2kV | 2207 (SC1301) | 3 phase fuses found open on Circuit 1301, suspected fault within Sectionalizer SC13. Sectionalizer to be | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11247 | 2007 | 9 | 4 | 0.69792 |  | 386 | 6 | 1 | Albion | 13.2kV | 2207 (SC1601) | Cable dig-in between KT379 and pole 11 as well as nicking cable between pole 6 and pole 11 caused outage at 220 Hunt Club, later determined nicked cable could be used and power restored. | Ottawa | Foreign Interference | Dig-in
5201 | 2004 | 5 | 23 | 0.69931 |  | 22 | 0 | 1 | TA | 13.2kV | 2208 | Jerome Daly of Cutler Hammer rpts new equip installed during planned shut down 24 hours previously @ VT265 not phased correctly & requested emergency isolation of main & xfmr busses @ VT265, 1495 Heron rd. | Ottawa | Human Element | Incorrect Installation
8451 | 2006 | 6 | 8 | 0.375 |  | 410 | 20 | 3 | Albion | 13.2kV | 2208 | 13KV vaults at VT465, VT467 & VT468 were isolated to allow contractor to clean & torque connections. Also remove asbestos in hydro vaults on Cedarwood. | Ottawa | Scheduled Outage | Preventive Maintenance
6813 | 2005 | 6 | 27 | 0.11181 |  | 164 | 2246 | 906 | Albion | 13.2kV | 2208 | 2208 faulted cable section isolated between VT265 & VT696 by 24/7. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3911 | 2003 | 8 | 16 | 0.56944 |  | 1635 | 27 | 1 | TA | 13.2kV | 2208 | 1495 Heron rd, VT265, reported all out Aug 16th. May have been out since power restored to line on Friday. No one in building to notice. 24/7 found 13kv main breaker open, breaker was tried once but tripped. Customer arranged for a contractor to be called. Vault was isolated & restored to service on the 17th. Contractor reported no problem found. | Ottawa | Unknown/Other | No Apparent Cause
13440 | 2008 | 10 | 28 | 0.55347 |  | 97 | 13 | 13 | Albion | 13.2kV | 2208 | Cable dig in by contractor working for Enbridge, on 2208 cable section between S-198 @ VT472 and S239 @ VT219. Circuit sectionalized to restore Power. | Ottawa | Foreign Interference | Dig-in
3099 | 2003 | 1 | 9 | 0.69375 |  | 116 | 2 | 1 | Albion TS | 13.2kV | 2209 | 2209 line tripped feeding VT16 Central Heating Plant at Confederation Heights. Line tested OK up to VT16 at 17:10. Cusromer owned cable from CB4 found defective. 2209 line and the Heating Plant load, except for CB4, was restored at 18:35. Public works switched internally to restore the remaining CB4 load. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5152 | 2004 | 5 | 14 | 0.73889 |  | 2518 | 42 | 1 | Albion | 13.2kV | 2209 | Q2 bus failure @ VT16 -- Central heating plant caused 2209 circuit to open. Q2 bus load was transferred to Q1 bus with the exception of one Building due to the load. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8515 | 2006 | 6 | 19 | 0.25694 |  | 115 | 2 | 1 | Albion | 13.2kV | 2209 | 2209 circuit tripped due to problem on customer secondary of VT16. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14645 | 2009 | 6 | 30 | 0.027778 |  | 40 | 1 | 1 | Albion | 13.2kV | 2209 | At 00:40am TA13 breaker opened. Breaker feeds VT16 (Central Heating Plant on Heron rd.) Crew fed vault from TA1AF line until line can be patrolled. Customer power was restored at 1:20am. | Ottawa | Unknown/Other
16653 | 2010 | 8 | 4 | 0.65694 |  | 228 | 4 | 1 | Albion | 13.2kV | 2209 | TA13 breaker tripped during heavy rain & lightning due to a blown arrestor and burnt lead. Hanging lead also took out 2210. Only VT16, the Central Heating Plant was affected. | Ottawa | Lightning
11024 | 2007 | 8 | 9 | 0.41667 |  | 30 | 320 | 639 | Albion | 13.2kV | 2209 | Tree made contact and caught on fire in an overhead section of TA16 and TA13, TA16 breaker tripped and locked out, and TA13 breaker was opened by System office. | Ottawa | Tree Contacts | Tree Limb Fallen
3461 | 2003 | 5 | 22 | 0.11806 |  | 60 | 1 | 1 | ALBION | 13.2kV | 2210 | Fault is unknown at this time. There is unground cable & O/H on this line. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18231 | 2011 | 5 | 27 | 0.51042 |  | 26 | 0 | 1 | Albion | 12/7.2kV | 2210 | TA16 breaker, circuit 2210 which supplies half of Heating plant on Heron @ Riverside Dr Heating plant picked up from TA1AF.Overhead patroled nothing found. U/G to fualt locate. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8383 | 2006 | 5 | 30 | 0.38194 |  | 70 | 1 | 1 | Albion | 13.2kV | 2210 | cable fault between VT16 at the central heating plant and Albion station caused TA16 breaker to open. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8514 | 2006 | 6 | 19 | 0.25694 |  | 115 | 2 | 1 | Albion | 13.2kV | 2210 | 2210 circuit tripped due to problem on customer secondary of VT16. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16654 | 2010 | 8 | 4 | 0.65694 |  | 194 | 3 | 1 | Albion | 13.2kV | 2210 | TA16 breaker tripped during heavy rain & lightning. Blown arrestor on 2209 and lead hanging down tripped this circuit. Only VT16, the Central Heating Plant was affected. | Ottawa | Lightning
11023 | 2007 | 8 | 9 | 0.39097 |  | 67 | 1137 | 1018 | Albion | 13.2kV | 2210 | Tree made contact and caught on fire in an overhead section of TA16 and TA13, TA16 breaker tripped and locked out, and TA13 breaker was opened by System office. | Ottawa | Tree Contacts | Tree Limb Fallen
8384 | 2006 | 5 | 30 | 0.38194 |  | 642 | 5565 | 613 | Albion | 13.2kV | 2211 | 2211 circuit fed from UACB2 at Albion sub opened possibly due to defective porcelin arc strangler at KT24 @ 3275 McCarthy. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8443 | 2006 | 6 | 7 | 0.58333 |  | 61 | 20 | 20 | Albion | 13.2kV | 2211 | KT24 isolated to allow crew to change defective switch on KT24 @ 22 Foxhunt. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14707 | 2009 | 7 | 11 | 0.47292 |  | 3 | 71 | 1429 | Nepean | 44kV | 22M224 | 22M4 opened and locked out during lighteming storm. Circuit closed in under direction of System Office | Nepean | Adverse Weather
6117 | 2005 | 1 | 5 | 0.46667 |  | 3 | 142 | 2850 | Nepean TS | 44kV | 22M23 | 22M23 feeder from Hydro One tripped and locked out. Closed manually from H1. Paulo R was at QC DS and saw 44 kv line moving, no wind. Line patrolled by Graham S and nothing found. | Nepean | Unknown/Other | No Apparent Cause
15615 | 2010 | 1 | 5 | 0.69514 |  | 21 | 1506 | 4302 | Nepean | 44kV | 22M23 | At 4:41pm Hydro Ottawa lost the 22M23 breaker supply from Hydro One. Hydro One stated 22M23 breaker went through it's cycle and locked out. After declaring Fire and Police clear, Hydro One retried 22M23 breaker with no load from QCH & Bayshore. Breaker held and Hydro Ottawa brought each feeder back on line from QCH and Bayshore. Hydro Ottawa crews patrolled 22M23 circuit from Nepean TS to EOL with no issues found. 22M23 Auto reclosed at 6:34pm once again. Crews will continue to patroll. Nepean (22M23). ID#15615. | Nepean | Loss of Supply
15760 | 2010 | 3 | 2 | 0.62569 |  | 48 | 1562 | 3107 | Nepean | 44kV | 22M23 | A blown lightening arrestor on the 44kv structure at Bayshore DS caused a fault that tripped the 22M23 at Nepean TS | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10132 | 2007 | 3 | 14 | 0.55 |  | 31 | 1474 | 2853 | Nepean TS | 44kV | 22M23 | 22M23 tripped, (while under hold off) due to phase to phase flash on the lower circuit, which was the 49F3 supply. The white phase fell on to the blue phase from the 49F3 cct, which also tripped. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18749 | 2011 | 7 | 17 | 0.80903 |  | 3 | 158 | 3164 | Nepean TS | 44kV | 22M23 | Hydro One reported 22M23 breaker at Nepean TS tripped. Closed with success 3 minutes later | Nepean | Adverse Weather | Lightning
8881 | 2006 | 8 | 1 | 0.063194 |  | 465 | 9319 | 4601 | Nepean | 44kV | 22M23 | Lightning in the area causing a flash over on an arrestor at QT129 at Nortel. | Nepean | Adverse Weather | Lightning
11185 | 2007 | 8 | 29 | 0.78125 |  | 149 | 8584 | 5000 | Nepean | 44kV | 22M23 | A phase came down at 44LB46 @ RMOC QT133 @ Aero DR. Crews isolated QT133 RMOC pumping station, and remains out, until morning. | Nepean | Lightning | Direct Strike
19325 | 2011 | 10 | 5 | 0.45417 |  | 31 | 1647 | 3188 | Nepean TS | 44kV | 22M23 | A switch fell across across the 22M23 and 200F3 circuits while a crew were installing them to replace the MSO370 (Job# 1187, PC2-61569) at 4 Cassidy . Crew clear the overhead and breakers were closed back in. Queensway Carleton and Bayshore substations were affected. 47F6 load was transfered to the 160F3 and was also affected. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7465 | 2005 | 10 | 16 | 0.3625 |  | 2 | 100 | 3000 | Nepean TS | 44kV | 22M23 | 22M23 circuit auto reclosed & locked out. Hydro One operator closed breaker after 1 min. 24/7 dispatched to patrol overhead circuit, and found a broken insulator conductor laying on crossarm at QT133 Holly Arces. | Nepean | Loss of Supply | HEPC Circuit Fault
7467 | 2005 | 10 | 16 | 0.47917 |  | 130 | 2 | 1 | Nepean TS | 44kV | 22M23 | QT133 isolated from all Hydro Ottawa sources to all crews to replace insulator and deadends. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3645 | 2003 | 6 | 30 | 0.038194 |  | 286 | 7834 | 5885 | Nepean TS | 44kV | 22M24 | The 44Kv 22M24 feeder auto reclosed and autoed to lockout. The feeder sectionalized with Parkwood Hills station restored at 00:55, Rideau Heights & Provincial Fruit restored at 01:42 and Canada Post restored at 04:30. Fault was caused by a blown lightening arrestor at Canada Post QT127. The arrestor is part of the Canada Post station. | Nepean | Foreign Interference | Customer Plant
4103 | 2003 | 9 | 20 | 0.0034722 |  | 40 | 1 | 1 | Nepean T.S. | 44kV | 22M24 | A sparking wire was called in from the Canada Post building at 141 Colonnade. The problem was isolated to allow for repairs to be made. Repairs were made and full power was restored. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
7400 | 2005 | 9 | 29 | 0.53264 |  | 78 | 7150 | 5500 | NEPEAN TS | 44kV | 22M24 | TREE FELL IN THE 44KV OVERHEAD ON WOODROFFE CAUSING THE 22M24 TO OPEN AND LOCK OUT. CIRCUIT FEEDING RIDEAU HIGHTS AND PARKWOOD HILLS. | Nepean | Adverse Weather | Wind
15468 | 2009 | 12 | 3 | 0.91319 |  | 50 | 1 | 2 | Nepean | 44kV | 22M25 | To facilitate switching of 44kv mso loops, there was an outage to QT126, Mallorn center off Moodie Dr. | Nepean | Scheduled Outage | Preventive Maintenance
4700 | 2004 | 1 | 15 | 0.31181 |  | 126 | 8 | 5 | Nepean | 44kV | 22M26 | S. Cunningham reports Phase down on the east side of 44LB44 switch. Overhead section of 44KV isolated and power restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3320 | 2003 | 4 | 6 | 0.64861 |  | 125 | 3488 | 8000 | Nepean TS | 44kV | 22M26 | 22M26 locked out causing loss of feed to woodroffe and Parkwoodhills substation. Most of the load was transferred off and then circuit was energized and held.No cause was found, circuit will be patrolled. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20292 | 2012 | 4 | 6 | 0.375 |  | 481 | 16 | 2 | Nepean TS | 44kV | 22M26 | At 09:00am crews isolated a section of the 22M26 to perform maintenance on the line and a supporting guarantee was issued to 2 contractors to perform work in QT120 and QT215. 2 customers affected for 481mins. Nepean TS 22M26, ID# 20292 | Nepean | Scheduled Outage
5588 | 2004 | 7 | 31 | 0.99306 |  | 270 | 9 | 2 | Nepean Ts | 44kV | 22M26 | Isolated O/H circuit between 44LB09 and 44LB24 to replace Live line clamps to QT120. The Nortel building (QT215) was involve for this isolation while Algonquin College (QT120) is isolated for maintenance. | Nepean | Scheduled Outage | Preventive Maintenance
10985 | 2007 | 8 | 1 | 0.82986 |  | 335 | 14713 | 5874 | Nepean TS | 44kV | 22M26 | An insulator on the 22M26 broke causing the conductor to sag into the 8 Kv underbuilt 170F4 feeder. Both the 22M26 and 170F4 were sectionalized with customers being restored in stages. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11377 | 2007 | 9 | 24 | 0.63889 |  | 28 | 392 | 5874 | NEPEAN TS | 44kV | 22M26 | A pole fire on the 22M26 circuit, was caused by a defective insulator, at Greenbank and Bellman. 22M26 Breaker opened by System, due to broken cross arm, which was ready to fall on 8kv supply. 44kv o/h section isolated and power restored. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
11857 | 2007 | 12 | 17 | 0.21528 |  | 13 | 867 | 4000 | Nepean TS | 44kV | 22M26 | Cct A/R/A & locked out. Police reported no problems, cct tried once & held. To be patrolled. | Nepean | Unknown/Other
12012 | 2008 | 2 | 6 | 0.44444 |  | 185 | 1117 | 7906 | Nepean TS | 44kV | 22M27 | City-plow brought down a concrete light-pole which fell into the 44 & 8KV circuits on Fallowfield & Orr, causing 22M27 to open & lock-out. Jockvale & Barrhaven & 1 44KV customer interupted. | Nepean | Foreign Interference | Vehicle
19993 | 2012 | 2 | 8 | 0.78403 |  | 2 | 233 | 6978 | Nepean TS | 44kV | 22M27 | Car accident at Cedarview and West Hunt Club caused the 22M27 to open. Hydro One closed the circuit back in and it held. Nepean TS (22M27) ID#19993 | Nepean | Foreign Interference | Vehicle
17763 | 2011 | 3 | 22 | 0.51806 |  | 100 | 8403 | 7420 | Nepean | 44kV | 22M27 | 22M27, 44kv separated at an isnsulator and dropped in to the 145F2 8kv, 1345F2 had to remain open, forced out, to repair damaged 8kv. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20477 | 2012 | 5 | 8 | 0.17153 |  | 596 | 959 | 2942 | Nepean TS | 44kV | 22M28 | 22M28 auto reclosed and locked out, pole fire found at QT125 (General Dynamics) | Nepean | Adverse Environment | Salt Spray
18451 | 2011 | 6 | 21 | 0.33681 |  | 60 | 2914 | 2914 | Nepean TS | 44kV | 22M28 | 22M28 conductor at MSO 355 dropped to the ground causing outage. Section isolated and customers restored on 200F5, F6 and 160 F3, F4. Nortel QT104 and EMR QT205 both have auto transfer so only short interruption to them. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16374 | 2010 | 6 | 30 | 0.64583 |  | 100 | 2 | 1 | Nepean | 44kV | 22M28 | 22M28 circuit auto reclosed, and No load lost. Circuit is to be patrolled. Carleton Electric & 24/7 reports crow found on open bus @ QT205 EMR. No Damage to bus, and power restored to QT205. | Nepean | Foreign Interference | Bird
12962 | 2008 | 7 | 29 | 0.55833 |  | 446 | 7 | 1 | Nepean TS | 44kV | 22M28 | The 22M28 circuit auto/reclosed due to a bird contact on the station bus at customer owned QT205 substation. QT205 substation was restored from A9M1 supply and 205M25-OB was left out of service. | Nepean | Foreign Interference | Bird
7477 | 2005 | 10 | 18 | 0.77431 |  | 218 | 1362 | 1200 | Nepean TS | 44kV | 22M28 | Pole fire at 34 Stafford Road - required the 44kv and 8kv circuits to be interrupted for the fire department to extinguish the flames. Damaged poles were sectionalized to restore most of the power. On-call crew made temporary repairs and the rest of the customers were restored. | Nepean | Adverse Environment | Fire
19807 | 2012 | 1 | 10 | 0.38542 |  | 52 | 0 | 4 | leitrim MS | 27.6/16kV | 249F1 | Transformer X15385 at 3199 Lynch St. isolated to redo all connections at transformer neutral and paddles on secondary side of transformer | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
17490 | 2011 | 1 | 17 | 0.46042 |  | 129 | 86 | 40 | Leitrim | 27.6/16kV | 249F1 | At switch G953 at 1717 Queensdale one phase was found blown. Crew then found a broken insulator up the line. | Gloucester | Defective Equipment
17495 | 2011 | 1 | 19 | 0.38611 |  | 176 | 29 | 10 | Lietrim | 27.6/16kV | 249F1 | TP6752 at Mocha and Espresso was isolated to allow contractor to pull in new secondary service. | Gloucester | Scheduled Outage | Construction
17515 | 2011 | 1 | 24 | 0.23681 |  | 2 | 102 | 3058 | LEITRIM | 27.6/16kV | 249F1 | 249F1 forced out of service due to low voltage at station. Load picked up from CS24615 via SCADA. Cause of low voltage found to be blown transformer fuse at Leitrem, cause of blown fuse unknow. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17520 | 2011 | 1 | 25 | 0.44444 |  | 110 | 6 | 3 | Leitrim | 27.6/16kV | 249F1 | Transformer #X14761 located at 3231 Lynch St opened by crew to install a pole | Gloucester | Scheduled Outage | Construction
17543 | 2011 | 1 | 31 | 0.56944 |  | 60 | 3 | 3 | Leitrim | 27.6/16kV | 249F1 | Transformer #X14761 located at 3246 Braddish opened by crew to re-arrange plant | Gloucester | Scheduled Outage | Construction
17561 | 2011 | 2 | 7 | 0.86111 |  | 57 | 20 | 21 | Leitrim | 27.6/16kV | 249F1 | 2 fuses at G260 found open at Del Zotto and Albion. Crews refused and closed after patrol turned up no cause for outage. | Gloucester | Unknown/Other | No Apparent Cause
17676 | 2011 | 3 | 7 | 0.43958 |  | 484 | 8 | 1 | Leitrim | 27.6/16kV | 249F1 | Transformer #867 located at 4660 Bank St opened up due to defective equipment, 3 fuses blown at switch | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20154 | 2012 | 3 | 12 | 0.68056 |  | 91 | 14 | 9 | Leitrim | 27.6/16kV | 249F1 | Isolated transformer X15530 at 23 Kemp Dr to disconnect service to 22 Kemp due to fire | Gloucester | Scheduled Outage | Emergency Services Request
20158 | 2012 | 3 | 13 | 0.50694 |  | 40 | 9 | 14 | Leitrim | 27.6/16kV | 249F1 | Trans X14391 was isolated inorder to replace a broken cutout | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
17713 | 2011 | 3 | 15 | 0.45833 |  | 30 | 3 | 6 | Leitrum | 27.6/16kV | 249F1 | Trans at 3002 VICTORIA HEIGHTS CRES GLOU was isolated in order to replace defective cutout | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
20172 | 2012 | 3 | 16 | 0.47153 |  | 62 | 3437 | 3359 | Lietrem |  | 249F1 | 249F1 opened due to an unknown relay failure. Carrying 249F2 load at the time of the trip. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17733 | 2011 | 3 | 18 | 0.4375 |  | 57 | 4 | 4 | Leitrim | 27.6/16kV | 249F1 | Transformer X18296 at 4237 Russell Rd isolated to allow for pole change | Gloucester | Scheduled Outage | Preventive Maintenance
17744 | 2011 | 3 | 20 | 0.72708 |  | 10 | 516 | 3094 | Leitrim | 27.6/16kV | 249F1 | An insulator on a 27Kv switch G954LB broke apon opening and the circuit had to be dump to all the crew to safely cut the leads clear. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
17745 | 2011 | 3 | 20 | 0.38542 |  | 75 | 36 | 29 | Letrim |  | 249F1 | At 9:15 crew isolate SK11 section to tranfer it to the UN06. 29 customers affected for 75 mins. King Edward SK11 ID # 17745 | Gloucester | Scheduled Outage | Construction
17752 | 2011 | 3 | 22 | 0.42708 |  | 48 | 2 | 3 | Leitrim | 27.6/16kV | 249F1 | Transformer #X18297 located at 4236 Russell Rd opened by crew for a pole replacement | Gloucester | Scheduled Outage | Construction
17753 | 2011 | 3 | 22 | 0.42708 |  | 48 | 3 | 4 | Leitrim | 27.6/16kV | 249F1 | Transformer #X18294 located at 4281 Blake opened by crew for a pole replacement | Gloucester | Scheduled Outage | Construction
17782 | 2011 | 3 | 25 | 0.41319 |  | 35 | 4 | 6 | Leitrim MS | 27.6/16kV | 249F1 | Three Trans isolated at 3995 Russell Rd in order to switch phasing on the primay ( 249F1) | Gloucester | Scheduled Outage | Preventive Maintenance
17909 | 2011 | 4 | 12 | 0.18889 |  | 80 | 4 | 3 | Leitrim | 27.6/16kV | 249F1 | Crew opened overhead transformer X14761 at Lynch & Braddish to repair downed secondary neutral. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
20319 | 2012 | 4 | 13 | 0.35764 |  | 87 | 3 | 2 | Leitrim | 27.6/16kV | 249F1 | Transformer X24449 for 4723 Bank St. isolated under 10A-007739 for tree removal | Gloucester | Scheduled Outage | Preventive Maintenance
17930 | 2011 | 4 | 14 | 0.44097 |  | 51 | 3 | 3 | Leitrim | 27.6/16kV | 249F1 | Transformer X14761 at 3246 Braddish was opened to allow crew to repair downed guy on secondary cable. Customers were affected for 51 minutes. Leitrim (249F1) | Gloucester | Unknown/Other
18198 | 2011 | 5 | 22 | 0.37847 |  | 81 | 76 | 56 | Leitrim | 27.6/16kV | 249F1 | defective arrestor @ 1537 Queensview caused G474 to open. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
20616 | 2012 | 5 | 25 | 0.78819 |  | 1215 | 122 | 6 | Leitrim | 27.6/16kV | 249F1 | Adverse weather caused fuse G654R blown on Belgreen/Russell | Gloucester | Adverse Weather | Lightning
20678 | 2012 | 6 | 2 | 0.84375 |  | 22 | 28 | 77 | Lietrim | 27.6/16kV | 249F1 | Crew had to isolate a section of overhead on Rosebella to allow them to remove a tree limb on the primary that was burning up. | Gloucester | Tree Contacts | Tree Limb Fallen
20851 | 2012 | 6 | 22 | 0.5375 |  | 281 | 2764 | 3400 | Leitrim | 27.6/16kV | 249F1 | 249F1 breaker tripped due to dump truck pulling down system neutral on Del Zotto, G260 opened to sectionalize and make reapirs to neutral and transormer on Del Zotto was replaced.. Transformer at 2550 Del Zotta was also replaced. | Gloucester | Foreign Interference | Vehicle
18549 | 2011 | 6 | 28 | 0.92292 |  | 21 | 9 | 25 | Leitrim | 27.6/16kV | 249F1 | Transformer #X13925 located at 1719 Kingsdale opened up due to lightning storm | Gloucester | Adverse Weather | Lightning
18725 | 2011 | 7 | 18 | 0.79861 |  | 13 | 1425 | 6575 | leitrim | 27.6/16kV | 249F1 | 249F1 circuit was opened to allow crew to remove tree from overhead circuit at bank and Queensdale. | Gloucester | Tree Contacts | Tree Fallen
18985 | 2011 | 8 | 20 | 0.60764 |  | 115 | 10 | 5 | Leitrim | 27.6/16kV | 249F1 | Crews isolated leaking transformer TE809 @ 3317 Hogarth. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19046 | 2011 | 8 | 29 | 0.42361 |  | 85 | 11 | 8 | Leitrim | 27.6/16kV | 249F1 | Transformer X15351 @ 2 Melva was isolated to allow crew to perform work on transformer secondary | Gloucester | Scheduled Outage
19049 | 2011 | 8 | 29 | 0.39583 |  | 235 | 12 | 3 | Leitrim | 27.6/16kV | 249F1 | Transformer GL0454 @ 392 Kent was isolated to allow crew to transfer plant to new pole. 5 customer were affected. | Nepean | Scheduled Outage
19059 | 2011 | 8 | 31 | 0.45486 |  | 85 | 7 | 5 | Leitrim | 27.6/16kV | 249F1 | Transformer X15356 at 12 Melva Ave isolated to transfer secondary | Gloucester | Scheduled Outage | Construction
19499 | 2011 | 10 | 30 | 0.42917 |  | 177 | 24 | 8 | Leitrim | 27.6/16kV | 249F1 | The 249F1 auto reclosed, a burnt connection on one phase at switch G216 cause the auto. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17325 | 2010 | 11 | 22 | 0.41111 |  | 194 | 42 | 13 | Leitrim | 27.6/16kV | 249F1 | TP6753 at 151 Mocha Pvt was isolated to allow crews to pull new secondary, 13 customers affected for 194 minutes. | Gloucester | Scheduled Outage
17426 | 2010 | 12 | 15 | 0.47431 |  | 124 | 151 | 73 | Leitrim DS | 27.6/16kV | 249F1 | G316R opened up due to squirrell contact at X13860 located at 1547 Kingsdale Ave. Crews patrolled, made necessary repairs & restored power. | Gloucester | Foreign Interference | Animal
17452 | 2010 | 12 | 24 | 0.045139 |  | 375 | 113 | 42 | Leitrim | 27.6/16kV | 249F1 | Defective tranformer, GLTE804 at 3353 Hogarth caused G474B to open. Defective transformer isolated & power restored to 4 Tx's. On call crew called in to replace transformer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18710 | 2011 | 7 | 17 | 0.82153 |  | 35 | 579 | 992 | Leitrim | 27.6/16kV | 249F1, 249F2 | 249T1 transformer @ leitrim high side fuses blew forcing system to offload feeders and transfer to other sources. | Gloucester | Adverse Weather | Wind
17516 | 2011 | 1 | 24 | 0.23681 |  | 106 | 1758 | 995 | LEITRIM | 27.6/16kV | 249F2 | 249F2 forced out of service due to low voltage at Leitrem DS after an auto-reclose on the 48M2. Load transfered to Limebank 7F2. Cause of low voltage found to be blown transformer fuse. Cause of blown fuse unknown. | Gloucester | Defective Equipment
17517 | 2011 | 1 | 24 | 0.38681 |  | 143 | 942 | 2171 | LEITRIM | 27.6/16kV | 249F2 | crews found damaged Insulator on Leitrim Rd near ramsayville. Isolated, repaired and restored,. Circuit fed from RX2016 (7F2). | Gloucester | Defective Equipment
17532 | 2011 | 1 | 27 | 0.65417 |  | 100 | 163 | 109 | Leitrem | 27.6/16kV | 249F2 | Ottawa Fire Dept. Reported pole fire on Leitrem Rd. E of Russel. Crews found a broken isnulator at X20023 which caused G606R and G959R to open. Crews isolated the section of O/H with the damaged pole and picked up part of the load before making repairs and restoring the line to normal. Pole to be replaced at a later date due to fire damage. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
19915 | 2012 | 1 | 28 | 0.78264 |  | 87 | 4 | 3 | Leitrim | 27.6/16kV | 249F2 | 249F2 CB A/R, no FCI's flashing on SCADA. Patrol found G831R blown on Anderson Rd & Leitrim. O/H was clear. Refused closed & Holding | Gloucester | Unknown/Other
19916 | 2012 | 1 | 28 | 0.79861 |  | 75 | 1 | 1 | Leitrim | 27.6/16kV | 249F2 | 249F2 CB A/R, no FCI's flashing on SCADA. Patrol found TX fuse blown due to ice build up. Refused and holding | Gloucester | Unknown/Other
17603 | 2011 | 2 | 17 | 0.61806 |  | 97 | 65 | 40 | Leitrim | 27.6/16kV | 249F2 | Crew found G434B open, line patrolled & no problems found, G434 replaced & power restored. Hawthorne rd / Rideau rd area. | Gloucester | Unknown/Other | No Apparent Cause
17604 | 2011 | 2 | 17 | 0.97639 |  | 199 | 133 | 40 | Leitrim | 27.6/16kV | 249F2 | G434 Blue phase opened again. Corner of Mitch Owens and Hawthorn Pole X16527 had a 44kV down guy fused to the 27kV conductor arm. 24/7 crew made safe distance between the guy and conductor arm and re-fused G434. Repairs also made to melted service connections at 5529 Hawthorn. | Gloucester | Foreign Interference | Foreign Object
20058 | 2012 | 2 | 27 | 0.41319 |  | 15 | 7 | 27 | Leitrim | 27.6/16kV | 249F2 | 249F2 white phase overhead section on Mitch Owens from G271w load transfered to G880B on Hall rd. For construction of new overhead three phase section. | Gloucester | Scheduled Outage | Construction
20171 | 2012 | 3 | 16 | 0.47153 |  | 15 | 271 | 1085 | Leitrem | 27.6/16kV | 249F2 | 249F2 load was transferred to the 249F1 to allow stations to make relay changes for Green Soilders Solar Farm. 249F1 CB tripped due to an unknown relay failure, interrupting all customers on the 249F2. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20191 | 2012 | 3 | 21 | 0.38681 |  | 13 | 10 | 45 | Leitrim | 27.6/16kV | 249F2 | crew restored an out of phase condition to normal on Mitch owen and Hall rd. 45 customers were interrupted. | Gloucester | Scheduled Outage | Construction
20248 | 2012 | 3 | 27 | 0.46528 |  | 22 | 2 | 6 | Leitrim | 27.6/16kV | 249F2 | Trans X20686 at 5036 Ninth Line Rd Glou was isolated in order to replace a defecvtive trans cutout , | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
20249 | 2012 | 3 | 28 | 0.45486 |  | 15 | 0 | 1 | Leitrim | 27.6/16kV | 249F2 | Tranformer #X20033 located at 5970 Russell Rd opened by crew to replace defective cutout and 21KV arrestor. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
17871 | 2011 | 4 | 11 | 0.083333 |  | 177 | 142 | 48 | Leitrim | 27.6/16kV | 249F2 | Switch G959R found opened after circuit was patrolled. | Gloucester | Adverse Weather | Lightning
17884 | 2011 | 4 | 11 | 0.41111 |  | 55 | 1 | 1 | Leitrim | 27.6/16kV | 249F2 | Transformer #X24312 located at 5790 Russell Rd opened up due to lightning | Gloucester | Adverse Weather | Lightning
20609 | 2012 | 5 | 25 | 0.78819 |  | 1192 | 278 | 14 | Leitrim | 27.6/16kV | 249F2 | Switch 960R at 5380 Leitrim Rd was hit by lightning, crews replaced and holding. | Gloucester | Adverse Weather | Lightning
20615 | 2012 | 5 | 25 | 0.78819 |  | 1130 | 94 | 5 | Leitrim | 27.6/16kV | 249F2 | Adverse weather caused fuse G427R blown on Hall Rd | Gloucester | Adverse Weather | Lightning
20617 | 2012 | 5 | 25 | 0.78819 |  | 1225 | 510 | 25 | Leitrim | 27.6/16kV | 249F2 | Adverse weather caused fuse G289R blown on Russell/Ramsayville | Gloucester | Adverse Weather | Lightning
20618 | 2012 | 5 | 26 | 0.66042 |  | 14 | 0 | 2 | Leitrim | 27.6/16kV | 249F2 | A tree fell on the O/H at 4420 Hall Rd, crews had to isolated the O/H to remove the tree. | Gloucester | Adverse Weather | Wind
20724 | 2012 | 6 | 8 | 0.97083 |  | 89 | 71 | 48 | Leitrim | 27.6/16kV | 249F2 | At 23:18 G540 Red phase blew open due to animal contact. Crews refused and closed to restore power. Leitrim 249F2 ID# 20724 | Gloucester | Foreign Interference | Animal
18579 | 2011 | 7 | 4 | 0.62778 |  | 167 | 448 | 161 | Leitrim |  | 249F2 | At 15:04 a truck hit a pole in front of 6209 Russell Rd causing the 249F2 breaker to reclose and G606R fuse blow. Crews repaired the pole and a service to a house. Leitrim (249F2) ID # 18579 | Gloucester | Foreign Interference | Vehicle
18624 | 2011 | 7 | 9 | 0.052083 |  | 187 | 25 | 8 | Leitrim | 27.6/16kV | 249F2 | Crew replaced defective cutout at G180W on Mitch Owens Rd. | Gloucester | Defective Equipment
18651 | 2011 | 7 | 13 | 0.58056 |  | 6 | 99 | 989 | Leitrim | 27.6/16kV | 249F2 | Adverse weather and lightning caused the 249F2 circuit to open. Circuit was patrolled nothing was found. | Gloucester | Adverse Weather | Lightning
18701 | 2011 | 7 | 17 | 0.8125 |  | 1030 | 137 | 8 | Lietrem | 27.6/16kV | 249F2 | Fallen Tree cause G180W to blow | Gloucester | Tree Contacts
18733 | 2011 | 7 | 17 | 0.91667 |  | 1413 | 1130 | 48 | Lietrim | 27.6/16kV | 249F2 | Tree damage took out the local on Farmer's way, isolated and repaired | Gloucester | Tree Contacts
18809 | 2011 | 7 | 24 | 0.68056 |  | 25 | 2 | 4 | Leitrim | 27.6/16kV | 249f2 | Trans at 8881 Mitch Owens Rd was isolated in order to replace defective arrestor & LLC and check connections | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
18859 | 2011 | 7 | 29 | 0.95972 |  | 508 | 508 | 60 | Lietrem | 27.6/16kV | 249F2 | Tree contact at 5127 9th Line Rd. caused G380B to open. Crews removed trees and re-fused. | Gloucester | Tree Contacts | Tree Limb Fallen
18976 | 2011 | 8 | 18 | 0.88403 |  | 87 | 4 | 3 | Leitrim | 27.6/16kV | 249F2 | G964 B closed after line partol. Possible lightning strike. | Gloucester | Lightning | Direct Strike
19038 | 2011 | 8 | 29 | 0.27014 |  | 156 | 21 | 8 | LEITRIM | 27.6/16kV | 249F2 | 249F2 auto reclosed. Found G180W blown due to dead animal. G180W refused and closed. | Gloucester | Foreign Interference | Animal
19166 | 2011 | 9 | 13 | 0.74861 |  | 220 | 293 | 80 | Leitrim | 27.6/16kV | 249F2 | During lightning storm a tree limb fell across wires. Leitrim (249F2) ID# 19166 | Gloucester | Tree Contacts
19167 | 2011 | 9 | 13 | 0.91319 |  | 12 | 2 | 8 | Leitrim | 27.6/16kV | 249F2 | Switch G381 was defective and burning up. Leitrim (249F2) ID# 19167. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
19417 | 2011 | 10 | 20 | 0.13681 |  | 278 | 537 | 116 | Leitrim DS | 27.6/16kV | 249F2 | 249F2 A/R, switch switch G735 was found open due to a tree on the O/H. | Gloucester | Unknown/Other
17286 | 2010 | 11 | 17 | 0.275 |  | 87 | 67 | 46 | Leitrim | 8/4.8kV | 249F2 | A pole on Farmers Way was reopted broken. Crew isolated line section to allow for braceing to be applied. | Gloucester | Defective Equipment | Vehicle
17367 | 2010 | 12 | 2 | 0.40278 |  | 267 | 9 | 2 | Leitrum | 27.6/16kV | 249F2 | Trans at 4467 FARMERS WAY GLOUC was isolated in order to replace a pole | Gloucester | Scheduled Outage | Preventive Maintenance
17372 | 2010 | 12 | 3 | 0.37917 |  | 150 | 85 | 34 | Leitrim | 27.6/16kV | 249F2 | At 09:06 switch G323 was isolated for Hydro One. 34 customers were affected for 150 minutes. Leitrim (249F2) ID#17372 | Gloucester | Scheduled Outage
4689 | 2004 | 1 | 9 | 0.5 |  | 80 | 40 | 30 | Beaverbrook | 8/4.8kV | 24F1 | A flashed over insulator was found in transformer #6027 | Kanata | Defective Equipment | Equipment Deterioration Due to Age
13902 | 2009 | 1 | 28 | 0.53819 |  | 45 | 7 | 9 | Beaverbrook | 13.2kV | 24F1 | Transformer #2643 located at 8 Tiffany isolated to try to locate fault. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
13903 | 2009 | 1 | 28 | 0.83542 |  | 27 | 4 | 8 | Beaverbrook | 12/7.2kV | 24F1 | Transformer 2643 in rear of 8 Tiffany isolated to allow for repairs to defective U/G service at # 0 Tiffany | Kanata | Scheduled Outage | Repair
15721 | 2010 | 2 | 12 | 0.41389 |  | 7 | 6 | 48 | Beaver Brook | 12/7.2kV | 24F1 | TP6152W-H1B openned to Break Paralell dropped customers, TP6152W-H1B closed back in to restore customers. Outage due to switcing error at S8. Circuit Paralell saw negledgable AMP movement. | Kanata | Human Element | Switching Errors
17601 | 2011 | 2 | 17 | 0.41667 |  | 66 | 6 | 5 | Beaverbrook | 12/7.2kV | 24F1 | Tx 6026 at 69 Reaney crt was isolated to make repairs tio internal barrier boards. | Kanata | Scheduled Outage | Repair
14268 | 2009 | 4 | 30 | 0.41667 |  | 10 | 2 | 12 | Beaverbrook | 12/7.2kV | 24F1 | Transformer #TP6152 located at 34 Tiffany Cres isolated for clearance | Kanata | Scheduled Outage | Preventive Maintenance
14641 | 2009 | 6 | 29 | 0.38611 |  | 188 | 25 | 8 | Beaverbrook | 12/7.2kV | 24F1 | TP6150R @ 56 Reany was isolated for the PCB transformer replacement program. | Kanata | Scheduled Outage | Repair
14804 | 2009 | 7 | 22 | 0.42778 |  | 417 | 83 | 12 | Beaverbrook | 13.2kV | 24F1 | At 10:16 transformer TP6152 at 28 Tiffany was isolated to allow crew to replace PCB transformer as part of PCB transformer change west. 12 customers were affected. | Nepean | Scheduled Outage
11411 | 2007 | 9 | 28 | 0.53472 |  | 15 | 2 | 10 | Beaverbrook | 12/7.2kV | 24F1 | Isolated transformer 2651 at 62 Pentland to disconnect service | Kanata | Scheduled Outage | Emergency Services Request
13669 | 2008 | 11 | 26 | 0.37847 |  | 32 | 1 | 2 | Beaverbrook | 12/7.2kV | 24F1 | Transformers TP5405 @ 10 Beaverbrook Lane & 2507 @ 17 Varley were isolated to replace broken insert at 2507 & then replace PCB Tx TP5405. Tx 2507 was restored after repair & TP5405 remained isolated. | Kanata | Scheduled Outage | Repair
13703 | 2008 | 12 | 5 | 0.39583 |  | 340 | 46 | 34 | Beaverbrook | 12/7.2kV | 24F1 | TP5501 at 44 Tiffany Cr isolated to replace PCB transformer. Breif outage to transformers 728, 2646 & 2640 during switching due to live front configuration. | Kanata | Scheduled Outage | Repair
15593 | 2009 | 12 | 30 | 0.15139 |  | 424 | 1347 | 437 | Beaverbrook | 12/7.2kV | 24F1 | 24F1 locked out, Crews found RED Phase fault indicated at Sub. Crews isolated from S14 to S2 and restored power to 49 customers Crews proved cable section to S2, Closed S2-4 & S2-2(B&W only) Found FCI indicated fault at 2654R but FCI was clear at 2582R, Isolated cables section btw 3048R & TP5405R | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6679 | 2005 | 6 | 7 | 0.38194 |  | 565 | 122 | 13 | Beaverbrook | 12/7.2kV | 24F1 & 24F2 | Transformer #3071 at 15 Sandwell isolated due to replacing transformer | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
9936 | 2007 | 1 | 16 | 0.88403 |  | 140 | 2372 | 1100 | Beaverbrook | 12/7.2kV | 24F2 | Defective Switch at S585 caused the 24F2 Breaker to open. Circuit Sectionalized to restore power. Repairs made to Switch. Also carrying the South March F2 & F3 | Kanata | Defective Equipment
5350 | 2004 | 6 | 21 | 0.94583 |  | 1463 | 195 | 8 | Beaverbrook | 12/7.2kV | 24F2 | Switching to restore load to BBF1 closed switch 2583-2 to 3069 which caused S55-3 Red phase to blow. Fuse replased and closed. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14648 | 2009 | 6 | 30 | 0.41181 |  | 148 | 22 | 9 | BEAVERBROOK | 12/7.2kV | 24F2 | Transformer TP5151 at 56 Reaney was isolated to change transformer as part of PCB replacement program. | Kanata | Scheduled Outage
3814 | 2003 | 7 | 29 | 0.35556 |  | 333 | 50 | 9 | Beaverbrook | 12/7.2kV | 24F2 | Transformer 3150 at 55 Selwyn in Kanata isolated for replacement of the transformer and cables. 9 customers on Penfield & Selwyn affected. | Kanata | Scheduled Outage | Preventive Maintenance
3821 | 2003 | 7 | 30 | 0.70972 |  | 67 | 91 | 575 | Beaverbrook | 8/4.8kV | 24F2 | Beaverbrook F2 breaker locked open due to switching to isolate the secondary on transformer #3158 to allow for a crew to disconnect an U/G service. It also caused the switch at S8-3W to open also therefore also isolating transformers #3159 & #3160. Once the breaker was closed and the secondary was disconnected the switch at S8-3 was closed. | Kanata | Unknown/Other | No Apparent Cause
3824 | 2003 | 7 | 31 | 0.37917 |  | 429 | 143 | 20 | Beaverbrook | 12/7.2kV | 24F2 | Planned outage to replace TX3151 & TX3157 in Kanata. All customers were notified of outage July 30. | Kanata | Scheduled Outage | Preventive Maintenance
5709 | 2004 | 8 | 24 | 0.42361 |  | 156 | 408 | 408 | Beaverbrooke | 12/7.2kV | 24F2 | The Beaverbrooke 24F2 auto tripped while under Hold Off to contractor Marc Prezeau of Bradley Kelly who is excavating for Hydro Ottawa. They severed 13 Kv primary cable at transformer TP4595W on Leacock Dr. Load restored in 2 sections. Cable was spliced and load restored. | Kanata | Foreign Interference | Dig-in
4224 | 2003 | 10 | 8 | 0.35833 |  | 377 | 63 | 10 | Beaverbrooke | 8/4.8kV | 24F2 | Planned outage to replace transformer 3054 on Penfield Dr in Kanata. | Kanata | Scheduled Outage | Construction
4232 | 2003 | 10 | 9 | 0.39306 |  | 537 | 179 | 20 | Beaverbrook | 12/7.2kV | 24F2 | Isolation of under ground section was to replace transformer & bases. 20 customers effected in power outage. | Kanata | Scheduled Outage | Construction
4278 | 2003 | 10 | 16 | 0.38542 |  | 412 | 69 | 10 | Beaverbrooke | 12/7.2kV | 24F2 | Planned outage to replace transformer TE3149W on Penfield Dr in Kanata. | Kanata | Scheduled Outage | Preventive Maintenance
9684 | 2006 | 11 | 19 | 0.70694 |  | 47 | 274 | 350 | Beaverbrook | 12/7.2kV | 24F2 | South March bus and reclosers out of service for upgrade. 24F1 was carrying SMF1,SMF2 and BBF2 due to a cable fault on Thursday. Load through S8-5 to high caused fuse to blow. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
15543 | 2009 | 12 | 22 | 0.54097 |  | 33 | 3 | 5 |  | 12/7.2kV | 24F2 | TP6150 isolated to test ground grid at 41 Reaney Crt. | Kanata | Scheduled Outage
13625 | 2008 | 11 | 17 | 0.37708 |  | 121 | 22 | 11 | BeaverBrook | 12/7.2kV | 24F5 | TP5492W at 352 Atowe Cres. was isolated to allow crew to replace transformer | Kanata | Scheduled Outage
13637 | 2008 | 11 | 19 | 0.37639 |  | 120 | 20 | 10 | Beaverbrook | 12/7.2kV | 24F5 | Crew isolated transforemer so that it could be replaced. | Kanata | Scheduled Outage | Repair
10085 | 2007 | 3 | 2 | 0.28819 |  | 64 | 64 | 60 | Beaverbrook | 13.2kV | 24F8 | White phase lead on switch S550 on Chimo burnt off. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
12165 | 2008 | 3 | 21 | 0.57639 |  | 61 | 111 | 109 | Beaverbrook | 12/7.2kV | 24F8 | White phase lead fell out of switch 525W on Beaufort in Kanata. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
20571 | 2012 | 5 | 25 | 0.38056 |  | 126 | 19 | 9 | Beaverbrook | 12/7.2kV | 24F8 | Transformer 3928 isolated to replace leaking transformer on Chimo Drive, Kanata. | Kanata | Scheduled Outage | Repair
16407 | 2010 | 7 | 6 | 0.81111 |  | 77 | 965 | 752 | Beaverbrook | 12/7.2kV | 24F8 | Mapping Issue on OMS indicated 24F8. 624F4 circuit was in NIU section of overhead line. | Kanata | Human Element | Incorrect Records
14957 | 2009 | 8 | 18 | 0.79583 |  | 570 | 130 | 108 | Beaverbrook | 12/7.2kV | 24F8 | Suspect transformer 3763 failed due to oil leakage. Outage was expanded briefly to isolate the transformer due to an out of phase back up supply. Transformer was replaced by Oncall crew and load restored. | Kanata | Defective Equipment
7172 | 2005 | 8 | 19 | 0.91736 |  | 309 | 77 | 15 | Beaverbrook | 12/7.2kV | 24f8 | Transformer TE4135 at 2 McClure was replaced. Transformer was leaking oil. Replacement transformer crew brought out was defective, blown bayonet fuse and oil was black. Returned back to Albion and another replacement transformer was used. | Kanata | Defective Equipment
14967 | 2009 | 8 | 19 | 0.66667 |  | 435 | 107 | 121 | Beaverbrook | 8/4.8kV | 24F8 | Transformer 3763 @ 31 Beaufort wa isolated fro soil remediation. To isolate transformer an outage was required due to an out of phase conditon, and 11 transformers were interrupted. | Kanata | Scheduled Outage | Repair
19063 | 2011 | 8 | 31 | 0.43125 |  | 103 | 21 | 12 | Beaverbrook | 13.2kV | 24F8 | At 10:21 transformer 3767 was isolatedd to replace defective transformer and clean oil spill. 12 customers were affected for 103 minutes. Beaverbrook (24F8) ID#19063. | Kanata | Scheduled Outage
7322 | 2005 | 9 | 14 | 0.38403 |  | 5 | 7 | 80 | Beaverbrooke | 13.2kV | 24F8 | 10 transformers interupted for switching to return feeder to normal, off phase condition, outage required. | Kanata | Scheduled Outage
19174 | 2011 | 9 | 14 | 0.375 |  | 711 | 142 | 12 | Beaverbrook | 12/7.2kV | 24F8 | transformer 3767 at 31 Brodeur was isolated to clear away the contaminated soil, at the transformer's base from, previous oil leak | Kanata | Scheduled Outage | Repair
13414 | 2008 | 10 | 23 | 0.38056 |  | 150 | 30 | 12 | Beaverbrook | 12/7.2kV | 24F8 | TP5490W @ 98 McClintock was isolated to allow the crew to change out the transformer because it contained PCB. | Kanata | Scheduled Outage | Preventive Maintenance
11620 | 2007 | 10 | 29 | 0.53472 |  | 22 | 3 | 9 | Beaverbrook | 12/7.2kV | 24F8 | Isolated transformer 5942 at 21 Chimo to repair service | Kanata | Scheduled Outage | Preventive Maintenance
13565 | 2008 | 11 | 5 | 0.37569 |  | 299 | 169 | 34 | Beaverbrook | 12/7.2kV | 24F8 | TP5427, TP5426 & TP5425 on McClintock on the blue phase has been isolated to replace PCB contaminated transformers. 34 customers affected. | Kanata | Scheduled Outage
11820 | 2007 | 12 | 7 | 0.89583 |  | 65 | 49 | 45 | Beaverbrook | 12/7.2kV | 24F8 | A switch 550 W phase at Chimo/Nanook was found broken. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
7721 | 2005 | 12 | 13 | 0.71875 |  | 405 | 153 | 50 | Beaverbrook | 12/7.2kV | 24F8 | Defective barrier board in transformer 3438 on McClintock Way in Kanata caused S539R to blow. 5 transformers affected. Repairs Made. | Kanata | Foreign Interference
19503 | 2011 | 10 | 30 | 0.92639 |  | 190 | 431 | 136 | Woodroffe | 13.2kV | 2804 | Vault VT435 & VT435A were isolated to allow contractor (Sproule) to perform customer vault maintenance in both vault and repair arc tip blade at VT435. Woodroffe (2804) | Ottawa | Scheduled Outage | Preventive Maintenance
14406 | 2009 | 5 | 24 | 0.59653 |  | 61 | 430 | 423 | Woodroffe | 13.2kV | 2806 | 2806 circuit auot trip. Circuit sectionalized and section isolated. Testing to be done to determine fault location. | Ottawa | Unknown/Other | No Apparent Cause
18232 | 2011 | 5 | 27 | 0.625 |  | 102 | 18 | 12 | Woodroffe TS | 12/7.2kV | 2806 | Crew at VT258 at 310 Pinecrest found water leaking into vault and the second crew SC2971 determined SC2971-CB3 defective at Algonquin College. VT258 was isolated and SC2971-CB3 was opened contractors and crews sent to both locations to resolve issues. Customers were picked at different stages. | Ottawa | Defective Equipment
18233 | 2011 | 5 | 28 | 0.575 |  | 855 | 787 | 429 | Woodroffe TW | 13.2kV | 2806 | 2806 cable tripped. During restoration 2 problems were found, water was leaking into VT258 at 1310 Pinecrest, the vault was isolated to allow customer to make repairs. Also, SC2971 at Algonquin college appeared to have an internal fault. On call crews isolated & tested switch & cables & then restored SC2971 without incident. | Ottawa | Defective Equipment
5641 | 2004 | 8 | 10 | 0.75417 |  | 8 | 1 | 10 | Woodroffe | 13.2kV | 2806 | Lightning storm, heavy rain & wind in area at time of trip. TW07 supply breaker closed manually after no Police or Fire reports were rec'd. 10 customer vaults affected. | Ottawa | Lightning
16875 | 2010 | 9 | 5 | 0.43472 |  | 26 | 183 | 423 | Woodroffe TW | 13.2kV | 2806 | TW07 tripped, no apparent cause. No calls from fire or police. Breaker closed via scada & held. To be patrolled. | Ottawa | Unknown/Other | No Apparent Cause
9143 | 2006 | 9 | 7 | 0.78264 |  | 545 | 9 | 1 | Woodroffe | 13.2kV | 2806 | 13 kv vault VT355 at 1000 Morrison, was isolated for Simpson Electric to repair customer's defective secondary main. Only the one customer, Lee Valley Tools, was affected. Vault was attempted to be restored at 1:50 but one of the R1-F fuses was blown. Crew had to find fuses & return to replace them which delayed restoration by 2 hrs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9946 | 2007 | 1 | 18 | 0.34375 |  | 345 | 69 | 12 | Richmond South | 8/4.8kV | 28F1 | At 08:15 transformer at Cockburn St Richmond was isolated in order to transfer services to new pole | Goulburn | Scheduled Outage | Preventive Maintenance
10005 | 2007 | 2 | 9 | 0.46042 |  | 162 | 8 | 3 | Richmond South | 8/4.8kV | 28F1 | Isolated Transformer at 32 Douglas st in Richmond to relocate services. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10060 | 2007 | 2 | 24 | 0.44444 |  | 110 | 2 | 1 | Richmond South | 8/4.8kV | 28F1 | Transformer lead at RX# 3137 found broken. Lead replaced all load restored to normal. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
7984 | 2006 | 3 | 3 | 0.42708 |  | 55 | 37 | 40 | Richmond South | 8/4.8kV | 28F1 | Planned outage to relocate o/h circuit on Murry Street. | Goulburn | Loss of Supply
17687 | 2011 | 3 | 9 | 0.32153 |  | 82 | 3 | 2 | Richmond South | 8/4.8kV | 28F1 | Replaced blown fuse at transformer X09120 at 6531 Franktown Rd (Cause unknown) | Goulburn | Defective Equipment | No Apparent Cause
3267 | 2003 | 3 | 17 | 0.87639 |  | 228 | 203 | 65 | Richmond South | 8/4.8kV | 28F1 | Two insulators were found flashed at 3540 Mc Bean st in Richmond. On the white phase overhead circuit was isolated between SW313-s W and S336 W phase fuse. Load restored to 65 customers at 23:16. Repairs made to blown insulator, and all power restored at 00:50. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
12281 | 2008 | 4 | 14 | 0.33333 |  | 620 | 10 | 1 | Richmond South | 8/4.8kV | 28F1 | Pole dip at 3344 Huntley Rd had cable pulled free of switch S29 by contractor on the 28F1. Switch removed and new switch S12259 installed on west side of road off of the 28F2 circuit. Cable no longer runs under Huntley Rd. 1 customer fed from TP5295 afffected. | Goulburn | Foreign Interference | Dig-in
8168 | 2006 | 4 | 19 | 0.76181 |  | 133 | 4 | 2 | Richmond South | 8/4.8kV | 28F1 | Top of switch to transformer 3257 at 3257 Joy's Rd broke off causing an outage to two customers cause unknown | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
5044 | 2004 | 4 | 23 | 0.39375 |  | 104 | 26 | 15 |  | 8/4.8kV | 28F1 | Isolated transformer 6746 & 6747 to replace bushings between Huntley and Fernbank | Goulburn | Scheduled Outage | Repair
5069 | 2004 | 4 | 28 | 0.91667 |  | 45 | 30 | 40 | Richmond South | 8/4.8kV | 28F1 | 28F1 O/H section between S316 and S360 isolated to repair pole damaged by fire at 6152 Ottawa St. Pole reframed, transformer cut out and lightening arrestor changed. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
5092 | 2004 | 5 | 3 | 0.29306 |  | 83 | 55 | 40 | Richmond S | 8/4.8kV | 28F1 | Switch at 336 B phase fell open. Peter Barr patrolled the curcuit and found nothing, he reclosed the switch and it held. | Goulburn | Unknown/Other | No Apparent Cause
6528 | 2005 | 5 | 10 | 0.29167 |  | 60 | 1 | 1 | Richmond South | 27.6/16kV | 28F1 | Isolated Transformer # 35 at 36 Colonel Murray in Richmond to replace bad arrestor | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6603 | 2005 | 5 | 25 | 0.54861 |  | 110 | 2 | 1 | Richmond Soutrh | 8/4.8kV | 28F1 | 2 transformers, 1 at 169 Nixon Farm Dr & one at 6182 Garvin Rd isolated to change lightning arresters. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
6649 | 2005 | 6 | 3 | 0.30208 |  | 16 | 1 | 4 | Richmond South | 8/4.8kV | 28F1 | Isolated Transformer # 6048 at 6048 Perth st in Richmond to change a blown arrestor | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3866 | 2003 | 8 | 6 | 0.37153 |  | 15 | 2 | 8 | Richmond South | 8/4.8kV | 28F1 | Transformer 49 at 3518 McBean was taken out of service to dig a secondary service. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
16745 | 2010 | 8 | 16 | 0.19514 |  | 269 | 166 | 37 | Richmond South | 8/4.8kV | 28F1 | Due to ligning storm crew replaced defective switches at SW611 on Joy's Rd. 37 customers affected. | Goulburn | Adverse Weather | Lightning
4097 | 2003 | 9 | 19 | 0.82292 |  | 75 | 524 | 419 | Richmond South | 8/4.8kV | 28F1 | Tree fell on the line on the end of the circuit on Franktown Road in Richmond. The reclosures opened. When the tree was removed the power was restored. | Goulburn | Tree Contacts | Tree Fallen
4145 | 2003 | 9 | 19 | 0.90278 |  | 20 | 72 | 419 | Richmond South DS | 8/4.8kV | 28F1 | Tree fell on R phase during wind storm. B & W phases opened by 24/7 crew in order to perform repairs. | Ottawa | Tree Contacts | Tree Fallen
9436 | 2006 | 10 | 16 | 0.45486 |  | 80 | 8 | 6 | Richmond South | 8/4.8kV | 28F1 | Transformer located at 6 Evelyn isolated to relocate plant. PC10A #98 | Goulburn | Scheduled Outage | Preventive Maintenance
5945 | 2004 | 11 | 28 | 0.60486 |  | 69 | 13 | 11 | Richmond South | 8/4.8kV | 28F1 | Re-fused O/H xfmr at 48 Cockburn | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
6208 | 2005 | 2 | 14 | 0.52083 |  | 352 | 6 | 1 | Richmond | 13.2kV | 28F1 Richmond | Blown Transformer in a 3 Phase Bank.at 6054 perth st in Richmond Reliability crew assisted the 24/7 crew | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4681 | 2004 | 1 | 6 | 0.5 |  | 20 | 2 | 6 | Richmond South | 8/4.8kV | 28F2 | Transformer at 51 Royal York in Richmond isolated to upgrade equipment. | Goulburn | Scheduled Outage | Construction
9950 | 2007 | 1 | 19 | 0.35417 |  | 240 | 80 | 20 | Richmond South | 8/4.8kV | 28F2 | At 08:30 trans on Cockburn St Richmond was isolated in order to perform transformer mtce | Goulburn | Scheduled Outage | Preventive Maintenance
9959 | 2007 | 1 | 22 | 0.35417 |  | 240 | 32 | 8 | Richmond South | 8/4.8kV | 28F2 | Bruce Baker isolated TRF 37 & 200 at 43 and 49 Colonel Murray st to relocate conductor to new poles | Goulburn | Scheduled Outage | Preventive Maintenance
9977 | 2007 | 1 | 31 | 0.59722 |  | 75 | 9 | 7 | Richmond South | 8/4.8kV | 28F2 | Bruce Baker isolated TRF. #125 @ 10 Maitland in Richmond to repair sec. Buss dead end | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
12002 | 2008 | 2 | 1 | 0.61667 |  | 7 | 1 | 8 | Richmond South | 8/4.8kV | 28F2 | Transformer 238B at 6 Queen Charlotte in Richmond was isolated to reposition transformer on base. Transformer was previously knocked out of position by an unknown vehicle. 8 customers interrupted on Queen Charlotte & Hamilton streets. | Goulburn | Foreign Interference | Vehicle
9987 | 2007 | 2 | 4 | 0.31181 |  | 196 | 33 | 10 | Richmond South | 8/4.8kV | 28F2 | 28F2 O/H section on Perth St in Richmond isolated for conductor replacement. | Goulburn | Scheduled Outage | Construction
8052 | 2006 | 3 | 23 | 0.24653 |  | 30 | 0 | 1 | Richmond South | 8/4.8kV | 28F2 | Vault 108 the Richmond Mall isolated to replace defective switch. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
4943 | 2004 | 3 | 28 | 0.95833 |  | 120 | 20 | 10 | Richmond South | 8/4.8kV | 28F2 | TX20122 had to be replaced due to an oil leak | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
8084 | 2006 | 3 | 30 | 0.52083 |  | 73 | 170 | 140 | Richmond South | 27.6/16kV | 28F2 | RICHMOND SOUTH F2 TRIPPED WHILE ON HOLD OFF DUE TO BLOWN ARRESTER @ 45 MAITLAND ST. Red Phase | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
4949 | 2004 | 3 | 31 | 0.39861 |  | 283 | 52 | 11 | Richmond South | 27.6/16kV | 28F2 | Transformer 20122 on Perth St in Stittsville isolated to remove contaminated soil from under the transformer. | Goulburn | Scheduled Outage
4957 | 2004 | 4 | 2 | 0.375 |  | 660 | 121 | 11 | Richmond South | 8/4.8kV | 28F2 | Transformer 20122 on Perth St in Stittsville isolated to remove contaminated soil from under the transformer. | Kanata | Adverse Environment | Industrial Contamination
10224 | 2007 | 4 | 8 | 0.37431 |  | 64 | 10 | 9 | Richmond South | 8/4.8kV | 28F2 | At 08:59 trans #77 at 6059 Ottawa St Richmond opened due to a broken trans sw.. Sw was replaced and power restored | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
8143 | 2006 | 4 | 13 | 0.21528 |  | 76 | 4 | 3 | Riichmond South | 27.6/16kV | 28F2 | S312 OPENED FOR SWITCH MAINTANCE ON PERTH ST. | Goulburn | Scheduled Outage | Preventive Maintenance
5005 | 2004 | 4 | 15 | 0.46528 |  | 290 | 10 | 2 | Richmond South | 8/4.8kV | 28F2 | Crews replaced defective O/H transformer #12541 at 3062 Joys Rd. | Goulburn | Scheduled Outage | Repair
14209 | 2009 | 4 | 24 | 0.53125 |  | 50 | 8 | 9 | Richmond South | 8/4.8kV | 28F2 | Isolated transformer X36027 at 103 Strachan St for service up-grade | Goulburn | Scheduled Outage | Construction
12368 | 2008 | 4 | 30 | 0.70347 |  | 111 | 231 | 125 | Richmond South | 8/4.8kV | 28F2 | Blown Arrestor at 6151 Perth Street caused S417 to blow. Arrestor cut clear, and switch refused to restore power. | Goulburn | Defective Equipment
12371 | 2008 | 5 | 1 | 0.56528 |  | 416 | 7 | 1 | Richmond South | 8/4.8kV | 28F2 | Customer at 6179 Perth Street Richmond experiencing partial power, bad XLPE cable feeding TV5850CHZ isolated and repaired. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
12376 | 2008 | 5 | 2 | 0.4375 |  | 16 | 3 | 10 | RICHMOND DS | 8/4.8kV | 28F2 | Removal of crossarm in front of 102 Fowler Ave | Goulburn | Scheduled Outage | Preventive Maintenance
18184 | 2011 | 5 | 19 | 0.4375 |  | 52 | 6 | 7 | Richmond South | 8/4.8kV | 28F2 | Transformer X35418 @ 80 Colonel Murray was open to allow tree trimmers to remove tree in proximity of power line. 7customer were affected. Richmond South (28F2) | Goulburn | Scheduled Outage
6579 | 2005 | 5 | 20 | 0.41667 |  | 116 | 19 | 10 | Richmond F2 | 27.6/16kV | 28F2 | L. Lauzon reports all tree triming is now complete on Perth St. RX 125,RX181, & RX126 is now restored. | Kanata | Scheduled Outage | Preventive Maintenance
16125 | 2010 | 5 | 22 | 0.54375 |  | 297 | 50 | 10 | Richmond S | 8/4.8kV | 28F2 | A broken bushing on a transformer located at 77 Fortune. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
18276 | 2011 | 6 | 1 | 0.73542 |  | 114 | 1786 | 940 | Richmond South | 27.6/16kV | 28F2 | 28F2 Red & Blue phase recloser at Richmond South found open. Circuit was patrolled and no cause was found. | Kanata | Adverse Weather | Wind
18279 | 2011 | 6 | 1 | 0.96181 |  | 7 | 7 | 60 | Richmond South |  | 28F2 | At 23:05 crews open SW63 White phase to repair TE20124 in front of 17 Rochelle. 60 customers affected for 7 mins. Richmond South 28F2 ID# 18279 | Goulburn | Scheduled Outage | Repair
4032 | 2003 | 6 | 23 | 0.38611 |  | 4 | 6 | 90 | Richmond South | 8/4.8kV | 28F2 | Transferring S333-S to the white phase to remove out of phase condition. | Goulburn | Scheduled Outage | Construction
5362 | 2004 | 6 | 24 | 0.60069 |  | 97 | 242 | 150 | Richmond South | 8/4.8kV | 28F2 | The Richmond South F2 R phase recloser opened while under Hold Off, circuit was patrolled and now apparent cause found. Recloser closed to restore power. | Goulburn | Unknown/Other
8673 | 2006 | 7 | 6 | 0.38194 |  | 164 | 14 | 5 | Richmond South | 8/4.8kV | 28F2 | Isoalted transformer 132 at 122 Burk St to relocate services | Goulburn | Scheduled Outage | Preventive Maintenance
16404 | 2010 | 7 | 6 | 0.67431 |  | 77 | 385 | 300 | Richmond South | 8/4.8kV | 28F2 | G358 fuse was found to be blown. Crew re-fused and switch held. No cause found at this time. | Goulburn | Unknown/Other | No Apparent Cause
18621 | 2011 | 7 | 9 | 0.94792 |  | 105 | 84 | 79 | Richmond S | 8/4.8kV | 28F2 | Tree Fallen across primary at Strachan and Fowler. Circuit isolated to remove tree. 34 customers affected on Strachan, Fowler and Lennox. Isolation expanded because neutral became taught on the load side of the isolation. During restoration S924W blew. S924W refused and all load restored. | Goulburn | Tree Contacts | Tree Fallen
11011 | 2007 | 8 | 8 | 0.34375 |  | 60 | 100 | 100 | Richmond South | 8/4.8kV | 28F2 | A truck pulled down overhead conductor at 6143 Perth st in Richmond. | Goulburn | Foreign Interference | Vehicle
16731 | 2010 | 8 | 13 | 0.42222 |  | 15 | 223 | 892 | Richmond South | 8/4.8kV | 28F2 | 28F2 RWB reclosers were opened instead of blocked. Crew waited for nearby lines crew to assist in closing and then W & B phases would not stay closed on first attempts. | Goulburn | Human Element | Switching Errors
11149 | 2007 | 8 | 24 | 0.32361 |  | 134 | 4 | 2 | Richmond South | 27.6/16kV | 28F2 | Transformer switch at 8 Fowler St in Richmond opened during thunderstorm. No apparent problem found, switch refused and closed. | Goulburn | Defective Equipment
3988 | 2003 | 9 | 1 | 0.38542 |  | 25 | 2 | 6 | Richmond | 27.6/16kV | 28F2 | Transformer # 27 was isolated to allow for the replacement of a defective lightning arrestor. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
4016 | 2003 | 9 | 5 | 0.38542 |  | 136 | 41 | 18 | Richmond S | 27.6/16kV | 28F2 | Scheduled Outage to performer transformer maintenance. | Goulburn | Scheduled Outage | Preventive Maintenance
13216 | 2008 | 9 | 11 | 0.375 |  | 163 | 5 | 2 | Richmond South | 8/4.8kV | 28F2 | At 09:00 trans at 126 MARTIN ST GOULBOURN was isolated for trans replacement | Kanata | Scheduled Outage | Preventive Maintenance
15146 | 2009 | 9 | 22 | 0.59722 |  | 75 | 8 | 6 | Richmond South | 8/4.8kV | 28F2 | Transformer #X10585 located at 77 Fortune St isolated do make repairs to triplex | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
4147 | 2003 | 9 | 25 | 0.21875 |  | 165 | 30 | 11 | Richmond South | 8/4.8kV | 28F2 | Tx 401B & 182W were opened to make repairs to common neutral. 11 customers on Hamilton, Fortune, Maitland & Perth st affected. Damaged neutral allowed voltage to fluctuate, customer complaints of damaged electronics etc. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
19422 | 2011 | 10 | 20 | 0.10625 |  | 345 | 230 | 40 | Richmond South | 8/4.8kV | 28F2 | Switch SW428 was found opened due to fallen primary conductor. | Goulburn | Tree Contacts
5909 | 2004 | 11 | 20 | 0.97569 |  | 64 | 32 | 30 | Richmond N | 8/4.8kV | 28F2 | A defective arrestor & damaged pole top at TX150 on Ottawa st in Richmond caused SW180R to open. The line section was cleared & power restored to all but the 1 customer on Tx150 ( a barn ). Further Repairs req'd to repair damaged pole, possibly customer owned. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17403 | 2010 | 12 | 10 | 0.43194 |  | 54 | 7 | 8 | Richmond S | 8/4.8kV | 28F2 | Transformer #X10576 located at 41 Fortune St opened by crew to repair cable fault | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
4620 | 2003 | 12 | 18 | 0.37153 |  | 134 | 4 | 2 | Richmond S F2 | 27.6/16kV | 28F2 | Transfomer isolated to allow contractor to install new secondary services. | Kanata | Scheduled Outage | Construction
9887 | 2006 | 12 | 28 | 0.375 |  | 58 | 10 | 10 | Richmond S | 8/4.8kV | 28F2 | Transformer 20125 @ 9 Rochelle in Richmond was isolated by the crew to the services. | Goulburn | Scheduled Outage | Repair
18378 | 2011 | 6 | 9 | 0.55278 |  | 102 | 524 | 308 | Richmond South | 8/4.8kV | 28F2 B | A truck caught the overehead wires at 6179 Perth and caused a flash taking out the blue phase from 28F2 recloser, dead end pole was secured and crew closed in at the station | Goulburn | Foreign Interference | Vehicle
6143 | 2005 | 1 | 17 | 0.89028 |  | 58 | 2 | 2 | Richmond South | 8/4.8kV | 28F3 | Broken fuse on Transformer # 4042 front of 4052 McBean St in Richmond | Goulburn | Unknown/Other | No Apparent Cause
12037 | 2008 | 2 | 11 | 0.85486 |  | 104 | 7 | 4 | Richmond S | 8/4.8kV | 28F3 | Transformer #TP2498 located at 18 Underhill isolated due to bad connection at the end of the fuse barrell | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
10080 | 2007 | 3 | 1 | 0.47917 |  | 62 | 1 | 1 | Richmond South | 8/4.8kV | 28F3 | The main breaker at the school at 3673 McBean was closed after it tipped open from the Richmond south auto-relose. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
10081 | 2007 | 3 | 1 | 0.47917 |  | 239 | 4 | 1 | Richmond South | 8/4.8kV | 28F3 | defective transformer T406 @ 5395 Barnsdale opened and was replaced by crew.(Transformer also caused the 28F3 feeder to auto-reclose.) | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
12155 | 2008 | 3 | 19 | 0.42708 |  | 18 | 2 | 8 | Richmond South | 8/4.8kV | 28F3 | At 10:15 trans at 108 KING ST GOULBOURN was isolated ini order to transfer cond | Goulburn | Scheduled Outage | Repair
10294 | 2007 | 4 | 22 | 0.80556 |  | 35 | 41 | 70 | Richmond South | 8/4.8kV | 28F3 | PC10A established at SW324 on McBean in Richmond to repair broken insulator. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
20493 | 2012 | 5 | 10 | 0.40069 |  | 135 | 144 | 64 | Richmond South | 8/4.8kV | 28F3 | Crew found S937 white phase switch open. Line patrolled nothing found. Fuse replaced. | Goulburn | Unknown/Other | No Apparent Cause
8363 | 2006 | 5 | 28 | 0.27083 |  | 390 | 78 | 12 | Richmond South | 8/4.8kV | 28F3 | 50kva transformer #4 on Hemphill/ Richmond defective and replaced by on-call | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12614 | 2008 | 6 | 12 | 0.46389 |  | 32 | 4 | 7 | Richmond South DS | 8/4.8kV | 28F3 | Transformer #X12619 located at 3837 McBean St Goul isolated to change an arrestor | Goulburn | Scheduled Outage | Preventive Maintenance
5457 | 2004 | 7 | 7 | 0.38403 |  | 124 | 83 | 40 | Richmond South | 27.6/16kV | 28F3 | Lorne had scheduled Outage off McBean in Goulbourn to check nomenclature | Goulburn | Scheduled Outage | Construction
5464 | 2004 | 7 | 8 | 0.38194 |  | 206 | 141 | 41 | Richmond South | 27.6/16kV | 28F3 | Underground section isolated between SW447R & TE70 to allow crews to remove old cable between 71R & 174R. Approx 41customers affected in planned power outage. | Kanata | Scheduled Outage | Construction
6906 | 2005 | 7 | 12 | 0.34792 |  | 420 | 70 | 10 | Richmond S | 8/4.8kV | 28F3 | Isolated Transformer 69 on MacBean St to install new cable. | Goulburn | Scheduled Outage | Preventive Maintenance
12826 | 2008 | 7 | 12 | 0.59028 |  | 153 | 82 | 32 | Richmond South | 8/4.8kV | 28F3 | Broken tree limb @ 4000 McBean St. in Richmond, contacted O/H 28F3 W-phase circuit & also caused fused switch 443W to blow. Crew cleared branch & restored all power. | Goulburn | Tree Contacts | Tree Limb Fallen
6918 | 2005 | 7 | 13 | 0.35417 |  | 429 | 72 | 10 | Richmon S | 8/4.8kV | 28F3 | Isolate transformer 173 on MacBean st for clearance for digging. | Goulburn | Scheduled Outage
6989 | 2005 | 7 | 18 | 0.39931 |  | 365 | 61 | 10 | Richmond North | 8/4.8kV | 28F3 | Pole transformer T175 returned to service as part of the conversion to pad mount transformer. Richmond Village. | Goulburn | Scheduled Outage | Construction
6997 | 2005 | 7 | 20 | 0.34028 |  | 410 | 34 | 5 | Richmond North | 27.6/16kV | 28F3 | transformer T175 was isolated to allow crews to re-arrange plant. | Goulburn | Scheduled Outage | Construction
5551 | 2004 | 7 | 22 | 0.29306 |  | 487 | 524 | 150 | Richmond North | 8/4.8kV | 28F3 | Boom truck in the wires on Ottawa street in Richmond 2 spans east of the railway tracks. 28F3 white phase has tripped. | Goulburn | Foreign Interference | Vehicle
5552 | 2004 | 7 | 22 | 0.35139 |  | 6 | 20 | 200 | Richmond South | 8/4.8kV | 28F3 | Emergency switching to clear boom truck in the wires on Ottawa Street. Load picked up on the 28 F1. | Goulburn | Foreign Interference
7040 | 2005 | 7 | 29 | 0.425 |  | 6 | 2 | 20 | Richmond north | 8/4.8kV | 28f3 | A. Cooney reports SW911B switch is now opened. To transfer 20 transformers along Fernbank RD to NEW Rabbit off Alex F3 circuit. | Kanata | Scheduled Outage | Construction
13043 | 2008 | 8 | 12 | 0.44444 |  | 80 | 9 | 7 | Richmond South | 8/4.8kV | 28F3 | Transformer #X12624 located at 3883 McBean St isolated due to stringing primary | Goulburn | Scheduled Outage | Preventive Maintenance
8967 | 2006 | 8 | 15 | 0.38403 |  | 211 | 53 | 15 | Richmond South | 8/4.8kV | 28F3 | Isolation of O/H line on Burke Street, to string new conductor. | Goulburn | Scheduled Outage | Construction
9112 | 2006 | 9 | 2 | 0.34097 |  | 69 | 2 | 2 | Richmond South | 8/4.8kV | 28F3 | Transformer located at 62 Lennox isolated due to animal contact (squirrel) | Goulburn | Foreign Interference | Animal
7284 | 2005 | 9 | 6 | 0.42083 |  | 264 | 66 | 15 | Richmond South | 8/4.8kV | 28F3 | Pole transformer 175 replaced with TP2495 in Richmond. | Goulburn | Scheduled Outage | Construction
15081 | 2009 | 9 | 10 | 0.42639 |  | 31 | 5 | 9 | Richmond South | 8/4.8kV | 28F3 | Energized new O/H from S19072 & feed new customers from Hydro One, S257 Guaranteed open | Goulburn | Scheduled Outage
9318 | 2006 | 9 | 26 | 0.58681 |  | 110 | 9 | 5 | Richmond S | 8/4.8kV | 28F3 | Bruce Baker isolated xfmr at 62 Strachan to move the xfmr to a new pole he used tag PC10A#576 | Goulburn | Scheduled Outage | Preventive Maintenance
9328 | 2006 | 9 | 27 | 0.38542 |  | 295 | 30 | 6 | Richmond S | 8/4.8kV | 28F3 | Transformer located at 77 Strachan isolated to transfer to new pole | Goulburn | Scheduled Outage | Construction
13542 | 2008 | 10 | 31 | 0.78125 |  | 85 | 35 | 25 | RICHMOND SOUTH | 8/4.8kV | 28F3 | Greg Bell reports S937W is defective, replaced, closed and holding | Goulburn | Defective Equipment
13656 | 2008 | 11 | 23 | 0.40903 |  | 123 | 2 | 1 | Richmond South | 8/4.8kV | 28F3 | Transformer fuse at 3825 McBean St in Richmond blew for no apparent reason, crew re-fused transformer to restore all load. | Goulburn | Unknown/Other | No Apparent Cause
7763 | 2005 | 12 | 26 | 0.34722 |  | 245 | 15 | 8 | Richmond North | 8/4.8kV | 28F3 | A pole fire at 5496 Fallowfield Rd. R/C 1084 was opened to allow fire department to put out the fire. 24/7 crews cut in temp MSO, and energized 7 transformers. On call crew to complete repairs on pole. | Kanata | Adverse Weather | Rain
4686 | 2004 | 1 | 7 | 0.375 |  | 75 | 5 | 4 | Richmond North | 8/4.8kV | 29F1 | Transformer 91 out to upgrade equipment at 81 King St in Richmond. | Goulburn | Scheduled Outage | Construction
4687 | 2004 | 1 | 7 | 0.52083 |  | 40 | 3 | 4 | Richmond North | 8/4.8kV | 29F1 | Upgrade equipment.Transformer 91 at 81 King St Richmond | Goulburn | Scheduled Outage | Construction
4696 | 2004 | 1 | 13 | 0.35417 |  | 50 | 7 | 8 | Richmond N | 27.6/16kV | 29F1 | Transformer at 4 Temple was opened to repair a pedastal. ID #4696 | Goulburn | Scheduled Outage | Repair
3147 | 2003 | 1 | 30 | 0.60069 |  | 47 | 9 | 11 | Richmond South | 8/4.8kV | 29F1 | Blown elbow found by crew at transformer 88 at 68 King St in Richmond. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
3157 | 2003 | 2 | 4 | 0.47708 |  | 88 | 15 | 10 | Richmond North | 8/4.8kV | 29F1 | Failure of top wire allowed conductor to float and contact structure causing fault . | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
3162 | 2003 | 2 | 4 | 0.79167 |  | 140 | 30 | 13 | Richmond South | 8/4.8kV | 29F1 | Crew found switch 371 at McBean and McCassland damaged and made repairs. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
4774 | 2004 | 2 | 10 | 0.38194 |  | 380 | 21 | 50 | Richmond N | 27.6/16kV | 29F1 | TP2309 isolated to dig under transformer. 50 customers where affected in power outage. While 4 transformers were backfed via red phase. One 3 phase transformer was energized via generator. At TP2309 10 customers were affected in power outage, but portable generators were connected to secondary side of the transformers. One generator failed. 2 Customers were out of power until a backup unit was installed. | Kanata | Scheduled Outage | Preventive Maintenance
4778 | 2004 | 2 | 10 | 0.93056 |  | 20 | 13 | 42 | Richmond N | 27.6/16kV | 29F1 | Customers on Chanonhouse and Dallaire in Richmond interrupted to remove generators and transfer them to normal supplies after soil was removed from under transformer TP2309. | Goulburn | Scheduled Outage
6211 | 2005 | 2 | 17 | 0.20208 |  | 90 | 38 | 25 | Richmond north | 12/7.2kV | 29F1 | M. Brown reports SW450R feeding TE88 found blown. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12078 | 2008 | 2 | 25 | 0.54167 |  | 50 | 2 | 2 | Richmond North | 8/4.8kV | 29F1 | Isolated transformer X09306 at 6054 Fernbank Rd to replace switch and arrester | Goulburn | Scheduled Outage | Repair
4847 | 2004 | 3 | 2 | 0.60417 |  | 95 | 3 | 2 | Richmond North | 8/4.8kV | 29F1 | Transformers to 5264 & 5306 Fernbank were interrup[ted to string conductor overtop. | Goulburn | Unknown/Other
10142 | 2007 | 3 | 16 | 0.40903 |  | 36 | 20 | 34 | Richmond N. | 8/4.8kV | 29F1 | A section of O/H line on Gamble N. of Moore was isolated to re-arrange conductor & repair defective switch 344. | Goulburn | Scheduled Outage | Repair
10143 | 2007 | 3 | 16 | 0.57639 |  | 10 | 3 | 16 | Richmond N. | 8/4.8kV | 29F1 | Due to an off-phase condition, Tx 157 on Moore st in Richmond was taken off potential during switching to restore a section of the 29F1. | Goulburn | Scheduled Outage | Repair
4926 | 2004 | 3 | 22 | 0.63194 |  | 30 | 0 | 1 | Richmond N | 8/4.8kV | 29F1 | Replace arrester at transformer 2815 at 5571 Fernbank Rd. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
14167 | 2009 | 4 | 11 | 0.62639 |  | 133 | 31 | 14 | Richmond North | 8/4.8kV | 29F1 | At 3:00pm, customers in the are of Huntley & Queenston called in with no power, overhead line clamp at S19958 let go on oe phase, 14 customers were affected for 133 min. (Richmond North 29F1) ID#14167. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
8217 | 2006 | 5 | 2 | 0.36458 |  | 95 | 8 | 5 | Richmond North | 8/4.8kV | 29F1 | Transformer isolated at 19 Meadowland for a change over | Goulburn | Scheduled Outage | Construction
10379 | 2007 | 5 | 7 | 0.61458 |  | 37 | 10 | 16 | Richmond North | 8/4.8kV | 29F1 | 2 overhead xfmrs were interrupted in Richmond to make emergency repairs to SW373B. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
8260 | 2006 | 5 | 9 | 0.53819 |  | 75 | 9 | 7 | Richmond North | 8/4.8kV | 29F1 | Isolated transformer 3404 at 3398 Shea Rd and replaced it | Goulburn | Scheduled Outage | Construction
8262 | 2006 | 5 | 9 | 0.59375 |  | 75 | 5 | 4 | Richmond North | 8/4.8kV | 29F1 | Transformer #209 located at 3354 Shea Rd isolated to replace transformer | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
10391 | 2007 | 5 | 9 | 0.05 |  | 80 | 1 | 1 | Richmond North | 12/7.2kV | 29F1 | Broken insulator found switch 118 on Brownlee rd caused outaage. 24/7 crew rplaced insulator & restored power. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
14352 | 2009 | 5 | 14 | 0.023611 |  | 66 | 2 | 2 | Richmond | 8/4.8kV | 29F1 | Primary o/h line isolated at Eagleson & Akins at S12318 to make repairs to broken insulators. | Gloucester | Defective Equipment
8304 | 2006 | 5 | 16 | 0.47917 |  | 98 | 163 | 100 | Richmond North | 8/4.8kV | 29F1 | Defective in line fuses opened when during switching operations. Swutches are normal open points that had to be closed for planned work. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
18229 | 2011 | 5 | 27 | 0.49306 |  | 70 | 1 | 1 | Richmond North | 8/4.8kV | 29F1 | Transformer #X36941 located at 5576 Faulkner opened by crew to renew connections at the barn. | Goulburn | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
5216 | 2004 | 5 | 28 | 0.41319 |  | 54 | 1 | 1 | Richmond North | 8/4.8kV | 29F1 | Transformer at 5706 Fernbank Rd isolated to repair a defective transformer switch. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
6643 | 2005 | 6 | 2 | 0.40347 |  | 304 | 208 | 41 | Richmond North | 8/4.8kV | 29F1 | TP2308 was leaking oil and replaced. On Channonhouse in Richmond. | Goulburn | Scheduled Outage | Repair
6766 | 2005 | 6 | 20 | 0.83681 |  | 23 | 3 | 8 | Richmond N | 8/4.8kV | 29F1 | A broken hot line that fell onto the primary and weld onto the primary. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
6790 | 2005 | 6 | 24 | 0.34722 |  | 210 | 7 | 2 | Richmond North | 12/7.2kV | 29F1 | Terry Fox extension work | Kanata | Scheduled Outage | Construction
14615 | 2009 | 6 | 25 | 0.7 |  | 92 | 123 | 80 | Richmond N | 8/4.8kV | 29F1 | Switch 582 on Stittsville main was open with burn marks, refused and closed found nothing wrong. | Goulburn | Unknown/Other | No Apparent Cause
6822 | 2005 | 6 | 28 | 0.32361 |  | 209 | 7 | 2 | Richmond North | 8/4.8kV | 29F1 | Scheduled outage for construcrion work on the Terry Fox Extension at Fernbank | Goulburn | Scheduled Outage | Construction
8622 | 2006 | 6 | 29 | 0.52292 |  | 152 | 20 | 8 | Richmond North | 8/4.8kV | 29F1 | In line switch S249 and tx fuse at tx 5616 on Aikins Rd found opened, thunderstorms in the area. | Goulburn | Adverse Weather | Lightning
14640 | 2009 | 6 | 29 | 0.4375 |  | 30 | 5 | 10 | Richmond North | 8/4.8kV | 29F1 | Isolated transformer X33174 at 40 Gamble Dr to install new pole | Goulburn | Scheduled Outage | Construction
14650 | 2009 | 6 | 30 | 0.4375 |  | 197 | 23 | 7 | Richmond N | 8/4.8kV | 29F1 | Transformer #X33154 located at 10 Gamble Dr isolated to repair services | Goulburn | Scheduled Outage | Construction
6851 | 2005 | 7 | 2 | 0.44514 |  | 425 | 7 | 1 | Richmond North | 12/7.2kV | 29F1 | R. Blair reports transformer fuse at 5686 Fernbank Rd is now closed. | Kanata | Adverse Weather | Lightning
14672 | 2009 | 7 | 6 | 0.39583 |  | 50 | 8 | 10 | Richmond North | 8/4.8kV | 29F1 | Transformer #X33155 located at 24 Gamble isolated to install new pole | Goulburn | Scheduled Outage | Construction
14675 | 2009 | 7 | 6 | 0.4375 |  | 80 | 7 | 5 |  |  | 29F1 | Transformer #X33258 located at 16 Gamble isolated to intall a pole | Goulburn | Scheduled Outage | Construction
14743 | 2009 | 7 | 14 | 0.39931 |  | 235 | 39 | 10 | Richmond N | 8/4.8kV | 29F1 | Transformer #X33174 located at 39 Gamble Dr isolated to transfer to new plant | Goulburn | Scheduled Outage | Construction
14753 | 2009 | 7 | 15 | 0.375 |  | 255 | 21 | 5 | Richmond N | 8/4.8kV | 29F1 | Transformer #X33157 located at 30 Gamble isolated to transfer to new plant | Goulburn | Scheduled Outage | Construction
14770 | 2009 | 7 | 17 | 0.375 |  | 180 | 30 | 10 | Richmond | 8/4.8kV | 29F1 | At 12:00 trans at 24 GAMBLE DR GOUL was isolated to transfer plant to new pole | Goulburn | Scheduled Outage | Construction
14792 | 2009 | 7 | 20 | 0.38056 |  | 222 | 44 | 12 | Richmond N | 8/4.8kV | 29F1 | Two transformers #X33154 & X33258 located at 12 & 16 Gamble isolated to install new wire. | Goulburn | Scheduled Outage | Construction
16508 | 2010 | 7 | 21 | 0.46667 |  | 78 | 16 | 12 | South Richmond | 8/4.8kV | 29F1 | TP6653 at 45 Moore was Isolated to allow ccrews to replace damaged transformer, 12 customers affected for 78 minutes. | Goulburn | Scheduled Outage | Repair
12968 | 2008 | 7 | 29 | 0.39375 |  | 111 | 11 | 6 | Richmond N. | 8/4.8kV | 29F1 | Crew isolated lsection of O/H line from S28340 on conley S of Flewelyn to make repairs. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
3842 | 2003 | 8 | 4 | 0.34583 |  | 70 | 7 | 6 | Richmond | 8/4.8kV | 29F1 | our first call of no power came in at 08:18. One of the effected customers reports power has been out since 02:30 am when a lightning storm went through the area. | Goulburn | Adverse Weather | Rain
14940 | 2009 | 8 | 12 | 0.76181 |  | 250 | 8 | 2 | Richmond North |  | 29F1 | S11907 at 2974 Shea road opened for no appaernt reason, crew inspected the 2 transformers, and re-fused S11907. | Goulburn | Unknown/Other | No Apparent Cause
7145 | 2005 | 8 | 16 | 0.41667 |  | 300 | 20 | 4 | Richmond South | 8/4.8kV | 29F1 | Transformer #6600 located at 6605 Ottawa St isolated to relocate services. | Goulburn | Scheduled Outage | Construction
11092 | 2007 | 8 | 17 | 0.72917 |  | 262 | 472 | 150 | Richmond North | 27.6/16kV | 29F1 | Overhead transformer 4777B on Sunnyside in Stittsville failed causing the B phase on reclose GR1056 to open. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
3938 | 2003 | 8 | 26 | 0.36944 |  | 68 | 51 | 45 |  | 27.6/16kV | 29F1 | Planned outage occurred because out of phase switching was in volve. To replace cable between transformer 100 & 101 on Dallaire Cr in Richmond | Goulburn | Scheduled Outage | Construction
3960 | 2003 | 8 | 28 | 0.39028 |  | 50 | 38 | 45 | Richmond North | 8/4.8kV | 29F1 | Part of Richmond cable replacement. | Goulburn | Scheduled Outage | Construction
3961 | 2003 | 8 | 28 | 0.5625 |  | 40 | 30 | 45 | Richmond North | 8/4.8kV | 29F1 | Part of the Richmond cable replacment. | Goulburn | Scheduled Outage | Construction
3979 | 2003 | 9 | 3 | 0.35625 |  | 54 | 40 | 45 | Richmond North | 8/4.8kV | 29F1 | Planned outage to customers on Dallairde Cr in Richmond to isolate cables for cable replacement. | Goulburn | Scheduled Outage | Construction
19081 | 2011 | 9 | 3 | 0.29583 |  | 159 | 3 | 1 | Richmond North | 8/4.8kV | 29F1 | Replaced broken switch feeding transformer X10193 at 5479 Faulkner Trail | Goulburn | Defective Equipment
4015 | 2003 | 9 | 5 | 0.35972 |  | 47 | 35 | 45 | Richmond N F1 | 27.6/16kV | 29F1 | Cable section section isolated between TX104 & TX105 in Richmond. To allow contractor to dig. | Goulburn | Scheduled Outage | Construction
7318 | 2005 | 9 | 12 | 0.54792 |  | 6 | 0 | 5 | Richmond North | 8/4.8kV | 29F1 | Cable section isolated between TP20178 & TP 20179 to include TP20179. 5 Customers effected in outage. | Kanata | Scheduled Outage | Construction
15111 | 2009 | 9 | 17 | 0.21111 |  | 266 | 106 | 54 | Richmond North | 8/4.8kV | 29F1 | Cable section from SW343 to transformer 20175 Queenston isolated due to cable fault. One transformer was out of power due to switching error. Transformer and cable tested, and restored power to 20175. | Goulburn | Defective Equipment | No Apparent Cause
4083 | 2003 | 9 | 18 | 0.3625 |  | 43 | 14 | 20 | Richmond N | 8/4.8kV | 29F1 | There was a plan outage to allow isolation of cables between to out of phase transformer. | Goulburn | Scheduled Outage | Construction
7351 | 2005 | 9 | 20 | 0.425 |  | 48 | 4 | 5 | Richmond North | 8/4.8kV | 29F1 | Transformer 154 at 54 Royal York was isolated to replace a blown arrester | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
4144 | 2003 | 9 | 24 | 0.37153 |  | 34 | 8 | 15 | Richmond North | 8/4.8kV | 29F1 | Planned outage to allow for isolation of cables between 2 out of phase transformers. | Goulburn | Scheduled Outage | Construction
4160 | 2003 | 9 | 26 | 0.35069 |  | 10 | 3 | 20 | Richmond North | 27.6/16kV | 29F1 | Richmond cable replacement on 29F1. | Goulburn | Scheduled Outage | Construction
15175 | 2009 | 9 | 27 | 0.55139 |  | 82 | 1 | 1 | Richmond North | 8/4.8kV | 29F1 | Transformer #X35914 located at 5854 Fallowfield isolated due to bird contact | Nepean | Foreign Interference | Bird
15192 | 2009 | 9 | 30 | 0.71458 |  | 151 | 3 | 1 | Richmond North | 8/4.8kV | 29F1 | Refused blown fuse in switch feeding transformer X10335 at 5910 Brownlee Rd | Goulburn | Unknown/Other | No Apparent Cause
15197 | 2009 | 10 | 1 | 0.79861 |  | 585 | 23 | 10 | Richmond North | 8/4.8kV | 29F1 | Dump truck collision broke a pole at Flewellyn & Eagleson. 24/7 established a PC10A at S28354 to disconnect the section of line with the broken pole and then restore the affected customers on Faulkner Trail. Repairs were then made by an Oncall Crew and the remaining 2 customers on Eagleson, both commercial, were restored. | Goulburn | Foreign Interference | Vehicle
4259 | 2003 | 10 | 15 | 0.077083 |  | 729 | 670 | 130 | Richmond North | 8/4.8kV | 29F1 | 29F1 blue phase circuit tripped only. Circuit was tagged hold off at the time of outage. Blue phase reclosure closed restoring power to circuit. Received calls from Ormsby area power still off. SW451 blue phase fuse found blown. Approx 48 customers out of power. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
17134 | 2010 | 10 | 18 | 0.64792 |  | 82 | 69 | 316 | Richmond N | 8/4.8kV | 29F1 | 29F1 Blue phase opened. System closed 29F1 blue phase and holding. 24/7 report RX2028 at Fallowfield and Shea Road is smoking and has a broken connection, scorch marks on side of tank, burn on arrester and is smoking. Crew believe there is no oil or very little oil in tank. RX2028 disconnected and restored on by-pass. | Goulburn | Defective Equipment
19403 | 2011 | 10 | 18 | 0.52778 |  | 100 | 8 | 5 | 28F1 | 8/4.8kV | 29F1 | Isolated transformer X36425 at 11 Pretty St to re-arrange hydro plant | Goulburn | Scheduled Outage | Construction
4333 | 2003 | 10 | 23 | 0.42014 |  | 84 | 11 | 8 | Richmond North | 27.6/16kV | 29F1 | Transformer # 95 opened to allow excavating for fault. Outage effected power to 8 customers on Channon House & Ormsky in Richmond. | Kanata | Scheduled Outage | Repair
4334 | 2003 | 10 | 23 | 0.64583 |  | 75 | 10 | 8 | Richmond North | 27.6/16kV | 29F1 | G. Morrice reports transformer isolated to replace unit at Ormsby & Chanonhouse. Outage effected 8 customers. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
13488 | 2008 | 10 | 28 | 0.87083 |  | 3 | 19 | 384 | RICHMOND NORTH | 8/4.8kV | 29F1 | 29F1 red phase closed from SCADA | Gloucester | Adverse Weather
13533 | 2008 | 10 | 30 | 0.72014 |  | 364 | 55 | 9 | Richmond North | 8/4.8kV | 29F1 | Richmond North 29F1 section was isolated to replace broken hydro pole. 9 customers on Shea, Atkin, and Brownlee were interrupted. | Goulburn | Defective Equipment
15356 | 2009 | 11 | 6 | 0.57778 |  | 103 | 43 | 25 | RICHMOND NORTH | 8/4.8kV | 29F1 | A car hit a pole at the corner of Flewelyn and Shea Rd. Crews required isolation to make temporary repairs. 25 customers affected. | Goulburn | Foreign Interference | Vehicle
13586 | 2008 | 11 | 10 | 0.086111 |  | 69 | 17 | 15 | Richmond North | 8/4.8kV | 29F1 | crew replaced LLC and stirrup on field phase tap off at the corner of King and Royal York st. 15 customers affected. | Goulburn | Defective Equipment
4524 | 2003 | 11 | 27 | 0.63889 |  | 17 | 36 | 128 | Richmond North | 8/4.8kV | 29F1 | On restoration of isolated section Tx 107 to Tx106 should have been left grounded but grounds were actually on at Tx107 to S18856 which resulted in the red phase recloser tripping. | Goulburn | Human Element | Switching Errors
4544 | 2003 | 12 | 2 | 0.41667 |  | 164 | 33 | 12 | Richmond | 8/4.8kV | 29F1 | Tramsformer replacement. | Goulburn | Scheduled Outage | Construction
4553 | 2003 | 12 | 3 | 0.37708 |  | 263 | 66 | 15 | Richmond North | 8/4.8kV | 29F1 | Removing pole transformers and installing mini pad transformers. | Goulburn | Scheduled Outage | Construction
15478 | 2009 | 12 | 6 | 0.30208 |  | 380 | 32 | 5 | Richmond North | 8/4.8kV | 29F1 | Radial line on Flewellyn running west from Shea Rd disconnected to change a broken pole. | Goulburn | Scheduled Outage | Repair
19738 | 2011 | 12 | 18 | 0.34514 |  | 80 | 31 | 23 | Richmond North | 8/4.8kV | 29F1 | GR1034 at 5189 Flewellyne Bypass switch opened due to defective fuse cut-out. | Goulburn | Defective Equipment
6081 | 2004 | 12 | 20 | 0.34375 |  | 249 | 227 | 130 | Richmond North | 8/4.8kV | 29F1 | 2 spans of red phase conductor down on Akins RD. Down section cut clear to restore majority of customers. Repairs made and last 9 restored. | Goulburn | Adverse Weather | Extreme Ambient Temperature
13798 | 2008 | 12 | 26 | 0.25 |  | 192 | 80 | 25 | Richmond N. | 8/4.8kV | 29F1 | bad cable section from S343 riser to T20174W caused S343W to open interrupting three transformers on Doctor Neelin and Grovewood. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
11912 | 2008 | 1 | 9 | 0.36806 |  | 7 | 7 | 58 | Richmond N | 8/4.8kV | 29F1(GR1056) | While the crew was string new O/H conductor the wind blew it into the energized section causing the GR1056 recloser to trip | Goulburn | Adverse Weather | Wind
7597 | 2005 | 11 | 12 | 0.34375 |  | 104 | 38 | 22 | Richmond N | 8/4.8kV | 29F1R | A cable fault between switch SW450R to transformer 88R @ 68 King St Richmond. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
6625 | 2005 | 5 | 31 | 0.45625 |  | 155 | 542 | 210 | Rich S | 8/4.8kV | 29F2 | Richmond S F2 red phase opened, circuit was patrolled & no problems found. Power was restored once Hydro - 1 crew arrived & closed the 28F2 red phase recloser. Hydro - 1 owned station. | Goulburn | Unknown/Other | No Apparent Cause
7536 | 2005 | 10 | 29 | 0.35764 |  | 50 | 1 | 1 | Richmond North | 8/4.8kV | 29F2 | 29F2 white phase recloser open for no apparent reason. Would not close from SCADA. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
7592 | 2005 | 11 | 11 | 0.38889 |  | 115 | 10 | 5 | Richmond North | 8/4.8kV | 29F2 | Transformer #36 at 68 Martin was isoalted to replace service | Goulburn | Scheduled Outage | Preventive Maintenance
6086 | 2004 | 12 | 22 | 0.084028 |  | 72 | 1 | 1 | Richmond North | 8/4.8kV | 29F2 | 29F2 B phase opened, circuit patrolled, no cause found, light snow in the area. | Goulburn | Unknown/Other
6092 | 2004 | 12 | 23 | 0.60069 |  | 85 | 1 | 1 | Richmond N | 8/4.8kV | 29F2 | While setting a hold off on the 28F2 the B phase opened, Billy Seaman patroll curcuit found nothing. | Goulburn | Unknown/Other | No Apparent Cause
9924 | 2007 | 1 | 13 | 0.98611 |  | 55 | 47 | 51 | Richmond South | 8/4.8kV | 29F3 | S264 at Main St and Elm St in Stittsville open to allow crew to repair secondary bus at T 2933. Secondary bus only 18 inches from Primary. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
6164 | 2005 | 2 | 1 | 0.83333 |  | 68 | 28 | 25 | Richmond N | 8/4.8kV | 29F3 | A broken lighning arrester in front of 7470 Fallowfield Rd. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12010 | 2008 | 2 | 6 | 0.39236 |  | 80 | 11 | 8 | Richmond N | 8/4.8kV | 29F3 | Transformer #X36469 located at 43 Norway Spruce isolated due to transformer being replaced due to broken bushing. | Goulburn | Scheduled Outage | Repair
12026 | 2008 | 2 | 8 | 0.53819 |  | 70 | 2 | 2 | Richmond North | 8/4.8kV | 29F3 | Transformer #2960 located at 53 Norway Spruce isolated to change cut out & re-arrange plant | Goulburn | Scheduled Outage | Construction
6199 | 2005 | 2 | 10 | 0.38333 |  | 103 | 34 | 20 |  | 8/4.8kV | 29F3 | Planned outage to reconfigure o/h line on Fernbank Rd. | Goulburn | Scheduled Outage
12134 | 2008 | 3 | 12 | 0.49861 |  | 130 | 9 | 4 | JANET KING | 8/4.8kV | 29F3 | TRANSFORMER #X36459 AT 60 NORWAY SPRUCE ISOLATED TO ALLOW FOR REPLACEMENT OF TRANSFORMER | Goulburn | Scheduled Outage | Preventive Maintenance
6287 | 2005 | 3 | 15 | 0.59722 |  | 95 | 27 | 17 | Richmond North | 8/4.8kV | 29F3 | TE6746 & TE6747 isolated to allow crews to transfer plant to new hydro pole. | Kanata | Scheduled Outage | Construction
6300 | 2005 | 3 | 17 | 0.40625 |  | 398 | 86 | 13 | Richmond North | 12/7.2kV | 29F3 | J. Heerkins from DunDas Power isolated 8kv O/H section of line from GR1020 to end of line. 13 Customers affected in this Planned outage to allow crews to upgrade services to 27/16 KV. To be re-energized VIA Alex F3 circuit. | Kanata | Scheduled Outage | Construction
17726 | 2011 | 3 | 17 | 0.39236 |  | 243 | 8 | 2 |  | 8/4.8kV | 29F3 | 29F3 section on Huntley Rd isolated to transfer equipment to new pole. Goulburn Middle School. | Goulburn | Scheduled Outage | Construction
15891 | 2010 | 4 | 5 | 0.65486 |  | 47 | 1 | 1 | Richmond N | 8/4.8kV | 29F3 | Transformer #X33330 located at 2980 Conley Rd opened due to tree contact | Goulburn | Tree Contacts | Tree Limb Fallen
12270 | 2008 | 4 | 10 | 0.50347 |  | 232 | 39 | 10 | Richmond North | 8/4.8kV | 29F3 | Section of overhead line on Huntley Rd just north of Flewellyn was isolated to install new poles & transfer circuit. | Goulburn | Scheduled Outage | Construction
10251 | 2007 | 4 | 13 | 0.77292 |  | 69 | 1 | 1 | Richmond North | 8/4.8kV | 29F3 | Transformer fuse 11542 at 7219 Fallowfield Rd was found blown no cause found refused switch restored power | Goulburn | Unknown/Other | No Apparent Cause
12298 | 2008 | 4 | 17 | 0.50278 |  | 351 | 58 | 10 | Richmond North | 12/7.2kV | 29F3 | Overhead section between S18540 & Temp 922 on Huntley RD | Goulburn | Scheduled Outage | Construction
8275 | 2006 | 5 | 11 | 0.47917 |  | 60 | 1 | 1 | Richmond North | 8/4.8kV | 29F3 | Isolated transformer 2135 at 2135 Huntley Rd to replace a connection on the underground service | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
3503 | 2003 | 5 | 30 | 0.42014 |  | 40 | 7 | 10 | Richmond North | 8/4.8kV | 29F3 | Planned outage on Fernbank Rd to transfer tx's to newly strung conductor. | Goulburn | Scheduled Outage | Construction
20669 | 2012 | 6 | 2 | 0.033333 |  | 144 | 137 | 57 | Richmond North | 8/4.8kV | 29F3 | Heavy rain and wind was current when SW775 cutout broke apart and blew S19112. Crew made repairs and restored power. | Goulburn | Adverse Weather | Rain
3573 | 2003 | 6 | 17 | 0.50764 |  | 45 | 150 | 200 | Richmond North | 8/4.8kV | 29F3 | Person injured while moving ladder at 1829 Main St. in Stittsville. Ladder contacted overhead causing reclosure GR1027 B to lock out. Approx 250 customers affected in power outage. | Kanata | Foreign Interference | Foreign Object
16273 | 2010 | 6 | 17 | 0.17361 |  | 220 | 26 | 7 | Richmond North | 8/4.8kV | 29F3 | Transformer X36706 was opened due to fire at 1686 Stittsville Main St. | Goulburn | Scheduled Outage | Emergency Services Request
8582 | 2006 | 6 | 23 | 0.27083 |  | 90 | 2 | 1 | Richmond North | 8/4.8kV | 29F3 | Transformer located at 1876 Stittsville Main isolated due to squirrel interference | Goulburn | Foreign Interference | Animal
6808 | 2005 | 6 | 25 | 0.625 |  | 382 | 967 | 100 | RICHMOND | 8/4.8kV | 29F3 | Blown cut out at 6948 Fernbank caused recloser GR1087B to blow. Refused transformer, closed in GR1087B picked up half and SW911 to restore other half. | Goulburn | Defective Equipment
12814 | 2008 | 7 | 10 | 0.40417 |  | 169 | 39 | 14 | Richmond N | 8/4.8kV | 29F3 | TP5499 and TP5500 new transformers installed and old PCB transformers 3860 and 3861 removed. | Goulburn | Scheduled Outage | Construction
18697 | 2011 | 7 | 17 | 0.8125 |  | 1025 | 4766 | 279 | Richmond North |  | 29F3 | Fallen tree broke conductor | Goulburn | Tree Contacts | Tree Limb Fallen
5515 | 2004 | 7 | 18 | 0.49653 |  | 75 | 1 | 1 | Richmond north | 27.6/16kV | 29F3 | 6974 FLEWELLYN RD GOUL reports power outage. 24/7 reports fuse opened at road feeding RX #6974. Squirrel found in transformer. Transformer fuse replaced power restored to normal. | Kanata | Foreign Interference | Animal
6990 | 2005 | 7 | 18 | 0.67153 |  | 93 | 139 | 100 | Richmond North | 8/4.8kV | 29F3 | On closeing in to restore 1 transformer on Flewellyn recloser 1087 tripped. There was to much cold load pick up for recloser so bypass fuse closed. Replacement recloser to installed latter today. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12981 | 2008 | 7 | 31 | 0.38472 |  | 166 | 83 | 30 | Richmond North | 27.6/16kV | 29F3 | TP6145 isolated for PCB change and transformers 3857 and 3858 isolated for minor work to be completed. | Goulburn | Scheduled Outage
3867 | 2003 | 8 | 6 | 0.84167 |  | 471 | 78 | 10 | Richmond North | 8/4.8kV | 29F3 | Traffic accident at the corner of Bleeks Rd and Conley Rd. 8kv pole broken and wires down. | Goulburn | Foreign Interference | Vehicle
13025 | 2008 | 8 | 8 | 0.65694 |  | 59 | 1 | 1 | Richmond North | 8/4.8kV | 29F3 | Transformer #X11831 located at 6313 Flewellyn Rd isolated due to animal contact. | Goulburn | Foreign Interference | Animal
8941 | 2006 | 8 | 10 | 0.38194 |  | 45 | 4 | 5 | Richmond North | 8/4.8kV | 29F3 | Transformer located at 2431 Conley Rd isolated due to a new connection & upgrade to the transformer | Goulburn | Scheduled Outage | Construction
8942 | 2006 | 8 | 10 | 0.54167 |  | 30 | 2 | 4 | Richmond North | 8/4.8kV | 29F3 | Transformer located at 2344 Conley isolated to connect service to 2321 Conley | Goulburn | Scheduled Outage | Construction
8951 | 2006 | 8 | 11 | 0.35417 |  | 100 | 3 | 2 | Richmond North | 8/4.8kV | 29F3 | Transformer located at 2431 Conley isolated due to a transformer upgrade & a new service connection | Goulburn | Scheduled Outage | Construction
18998 | 2011 | 8 | 22 | 0.67708 |  | 95 | 2 | 1 | Richmond N | 8/4.8kV | 29F3 | Transformer#X33300 located at 6832 Mansfield opened up due to animal contact | Goulburn | Foreign Interference | Animal
16853 | 2010 | 9 | 2 | 0.44444 |  | 81 | 8 | 6 | Richmond North | 8/4.8kV | 29F3 | Transformer X3592 at 21 Sunnyside was isolated to allow crew to install new service. | Goulburn | Scheduled Outage
13201 | 2008 | 9 | 6 | 0.45486 |  | 230 | 4 | 1 | Richmond North | 8/4.8kV | 29F3 | Refused switch to transformer X11972 at 7070 Fallowfield Rd | Goulburn | Adverse Weather | Rain
7304 | 2005 | 9 | 9 | 0.91806 |  | 143 | 188 | 79 | Richmond North | 8/4.8kV | 29F3 | Switch 542 blue phase broken, leads removed and switch S911 closed (off phase condition) Flewellyn Rd west of Huntley. | Goulburn | Defective Equipment
7319 | 2005 | 9 | 12 | 0.57639 |  | 10 | 7 | 47 | Richmond South | 8/4.8kV | 29F3 | SW542B switch restored to normal. A out of phase condition between SW542 & SW911. Customers were dumped off to complete the restorion of SW542B. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
7323 | 2005 | 9 | 14 | 0.37639 |  | 88 | 147 | 100 | Richmond South | 8/4.8kV | 29F3 | Scheduled outage to transfer customers to new in line step down tx fed from the 27Kv Wonderland DS feeder. | Goulburn | Scheduled Outage
19232 | 2011 | 9 | 21 | 0.67708 |  | 85 | 1 | 1 | Richmond N | 8/4.8kV | 29F3 | Transformer #X33300 located at 6832 Mansfield Rd opened up, no cause found by crew | Goulburn | Unknown/Other | No Apparent Cause
9293 | 2006 | 9 | 24 | 0.42361 |  | 301 | 50 | 10 | Richmond N | 8/4.8kV | 29F3 | With the high winds the O/H line slap together causing the switch 616 to open on Conley Rd at Mansfeild. | Goulburn | Adverse Weather | Wind
9309 | 2006 | 9 | 25 | 0.86458 |  | 372 | 112 | 18 | Richmond N | 8/4.8kV | 29F3 | J. Ryan reports single phase line down south of Bleeks Rd. on Conoly causing switch 616R to burn up and power was loast to about 18 customers. Crew made repairs to switch and line. All power restored. | Goulburn | Foreign Interference | Foreign Object
17136 | 2010 | 10 | 18 | 0.36111 |  | 85 | 11 | 9 | North Richmond | 8/4.8kV | 29F3 | Cable fault caused transformers TP5500 and TP5499 to be affected while crew located fault. Richmond North (29F3) ID# 17136 | Goulburn | Defective Equipment
11615 | 2007 | 10 | 28 | 0.31806 |  | 162 | 3 | 1 | Richmond North | 8/4.8kV | 29F3 | Replaced broken cutout to transformer X11828 at 6249 Flewellyn Rd | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17258 | 2010 | 11 | 11 | 0.42014 |  | 18 | 3 | 9 | Richmond North | 8/4.8kV | 29F3 | At 10:05, transformers TP5499 & TP5500 on Huntely were off potential to allow crews to restore repaired cable back to Normal. Richmond North (29F3) | Goulburn | Scheduled Outage
17295 | 2010 | 11 | 17 | 0.72014 |  | 213 | 4 | 1 | Richmond N | 8/4.8kV | 29F3 | Transformer #X33328 located at 6990 Bleeks Rd opened due to tree contact | Goulburn | Tree Contacts | Tree Fallen
5931 | 2004 | 11 | 26 | 0.43819 |  | 54 | 1 | 1 | Richmond North |  | 29F3 | Transformer 6591 at 6591 Fernbank Rd taken out of service to replace a blown arrestor. 1 customer affected. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
15508 | 2009 | 12 | 13 | 0.54167 |  | 135 | 4 | 2 |  | 8/4.8kV | 29F3 | At 13:00 trans was isoalted in order to replace insulators on A9M3 . And re-arrange some matl on pole | Goulburn | Scheduled Outage | Preventive Maintenance
15512 | 2009 | 12 | 14 | 0.53125 |  | 135 | 4 | 2 | Richmond N | 8/4.8kV | 29F3 | Transformer #X12106 located at 6980 Mansfield Rd isolated to re-configure 8kv transformers | Goulburn | Scheduled Outage | Construction
13812 | 2008 | 12 | 28 | 0.55833 |  | 326 | 5 | 1 | Richmond North | 8/4.8kV | 29F3 | Broken cutout at X11504 at 2657 Conley Rd, crew replaced switch and closed. 1 customer affected | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
6256 | 2005 | 3 | 9 | 0.46944 |  | 649 | 11 | 1 | Uplands D.S. | 8/4.8kV | 2F2 | cable dig in at TE2981. Teraflex backhoe dug into blue phase cable and cut cable as well as broke insert at TE2981, and oil is leaking. | Gloucester | Foreign Interference | Dig-in
8062 | 2006 | 3 | 24 | 0.77847 |  | 39 | 2 | 3 | Uplands | 8/4.8kV | 2F2 | Primary B phase on the 2F5 down between the 2F2 curcuit, 2F2 was isolated to allow crews to fix the primary. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10206 | 2007 | 3 | 29 | 0.35764 |  | 65 | 108 | 100 | Uplands | 8/4.8kV | 2F2 | Junction box on 2F2 circuit at uplands failed causing outage on circuit. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
8192 | 2006 | 4 | 26 | 0.70764 |  | 34 | 1 | 1 | Uplands | 8/4.8kV | 2F2 | Fuse in TE2991 found blown. TE2991 was isolated to all crew to replace fuse. All power was restored @ 512 DE Niverville. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16151 | 2010 | 5 | 26 | 0.56458 |  | 272 | 444 | 98 | Uplands | 8/4.8kV | 2F2 | G857 broke interupting power to part of Uplands Air Base. New switch installed & load restored. Restoration was delayed due to broken boom line during repairs. | Gloucester | Defective Equipment
7308 | 2005 | 9 | 10 | 0.58819 |  | 315 | 105 | 20 | Uplands DS | 4.16kV | 2F2 | Scada indicates 2F2, 2F4 circuits opened. No reports of Fire or MVA from Ottawa Fire or Police. 14:30 2F2 breaker closed via scada. B. Wills reports 2F5 blue phase wrapped into 2F2 & 2F4 circuits. 2F2 breaker reopened via scada. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4396 | 2003 | 11 | 5 | 0.60347 |  | 52 | 8 | 11 | Uplands | 8/4.8kV | 2F2 | D. Martin reports digin in cable between T3097 & SE39. 11 customers effected in power outage. | Gloucester | Foreign Interference | Dig-in
4504 | 2003 | 11 | 22 | 0.33056 |  | 379 | 13 | 2 | Uplands | 8/4.8kV | 2F2 | 2 transformer where isolated to install new padmount transformer in Uplands area. 2 customers were affected in this outage. Outage was planned. | Gloucester | Scheduled Outage | Construction
6047 | 2004 | 12 | 10 | 0.875 |  | 501 | 25 | 3 | Uplands | 8/4.8kV | 2F2 | Fused in line S950 found open, heavy snow fall & high winds. | Gloucester | Adverse Weather
6048 | 2004 | 12 | 11 | 0.22222 |  | 1 | 0 | 1 | Uplands | 8/4.8kV | 2F2 | 2F2 bkr open for crew to replace blown fused in lines S950. | Gloucester | Adverse Weather
6070 | 2004 | 12 | 16 | 0.73472 |  | 252 | 17 | 4 | Uplands | 8/4.8kV | 2F2 | 24/7 Replaced defective transformer switch. Work order taken out by 24/7 crew for snow removal at pole. | Gloucester | Defective Equipment
20077 | 2012 | 2 | 29 | 0.45833 |  | 10 | 0 | 2 | Uplands | 8/4.8kV | 2F3 | 2F3 feeder load transfered to new 27KV/8KV rabbit TP9224 (4801F7), outage required due to 30degree phase shift thru rabbit | Gloucester | Scheduled Outage | Construction
15977 | 2010 | 4 | 23 | 0.58681 |  | 215 | 4 | 1 | Uplands | 8/4.8kV | 2F3 | Animal contact in switch S41 at the airport caused an outage to TE2982 @ Bell Canada. | Gloucester | Foreign Interference | Animal
16445 | 2010 | 7 | 9 | 0.51944 |  | 9 | 81 | 538 | Uplands | 8/4.8kV | 2F3 | Uplands 2F3 A/R several times and opened during severe thunderstorm in the area. 2F3 closed and held but not restoring all of the load. Overhead crew assisted in restoring various lost load in the Uplands area in section. | Gloucester | Adverse Weather | Lightning
12897 | 2008 | 7 | 19 | 0.33333 |  | 410 | 27 | 4 | Uplands | 8/4.8kV | 2F3 | (Airport property) 2F3 cable section between SE39 & G808LB was isolated for crew to prepare cables & SC5370 for energization. SC5370 is now energized & all customers power is restored. | Gloucester | Scheduled Outage | Construction
19924 | 2012 | 1 | 30 | 0.35764 |  | 164 | 394 | 144 | Uplands | 8/4.8kV | 2F4 | G745 operating mechanism was found damaged by an apparent vehicle contact, switch was isolated and temporary repairs completed. | Gloucester | Foreign Interference | Vehicle
7945 | 2006 | 2 | 17 | 0.70833 |  | 32 | 11 | 20 | Uplands | 8/4.8kV | 2F4 | A broken 90 degree cross over loop north of switch 739 on the Uplands Base. | Gloucester | Adverse Weather | Wind
15748 | 2010 | 2 | 26 | 0.48889 |  | 121 | 133 | 66 | Uplands | 8/4.8kV | 2F4 | Crews found G739 WHITE phase open, patrolled lline but no fault found. Refused, closed and holding. | Gloucester | Unknown/Other | No Apparent Cause
20078 | 2012 | 2 | 29 | 0.50347 |  | 1 | 12 | 729 | Uplands | 8/4.8kV | 2F4 | 2F4 feeder transferred to new 27KV/8KV rabbit TP9224 (4801F7). Outage required due to 30 degree phase shift thru rabbit. | Gloucester | Scheduled Outage | Construction
17707 | 2011 | 3 | 12 | 0.42708 |  | 15 | 0 | 1 | Uplands | 8/4.8kV | 2F4 | Transformer #X17664 located at 25 Curtis Pvt opened by crew to change neutral wire at xfmr, stir up and live line clamp | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6526 | 2005 | 5 | 9 | 0.68889 |  | 62 | 2 | 2 | Uplands | 8/4.8kV | 2F4 | Tx 7652 at 14 Sampson St disconnected for Dan Blackburn to make emergency repairs to meter box coming off pole. ESA # 11392497 | Gloucester | Scheduled Outage | Repair
16158 | 2010 | 5 | 28 | 0.39236 |  | 145 | 899 | 372 | Uplands | 8/4.8kV | 2F4 | 2F4 O/H isolated to allow crews to re-configure circuit | Ottawa | Scheduled Outage | Construction
14477 | 2009 | 6 | 6 | 0.58681 |  | 40 | 3 | 5 | Uplands MS | 8/4.8kV | 2F4 | Switch at transformer X17665 opened up at 3 Mcallister Pvt, cause unknown | Gloucester | Unknown/Other | No Apparent Cause
16316 | 2010 | 6 | 23 | 0.84653 |  | 226 | 1401 | 372 | Uplands | 8/4.8kV | 2F4 | G739 opened up due to a defective line tap. | Gloucester | Defective Equipment
16338 | 2010 | 6 | 27 | 0.67153 |  | 213 | 1894 | 535 | Uplands 8kV | 8/4.8kV | 2F4 | 2F4 circuit opened due to animal contact on G915. | Gloucester | Foreign Interference | Animal
18547 | 2011 | 6 | 28 | 0.625 |  | 60 | 180 | 180 | Uplands | 8/4.8kV | 2F4 | A truck caught o/h bell & cable wires on Curtis ave causing G739 R & W to blow. Hydro plant patrolled & G739 R & W replaced. | Gloucester | Foreign Interference | Vehicle
14730 | 2009 | 7 | 11 | 0.73264 |  | 115 | 188 | 98 | Uplands |  | 2F4 | Downed conductor at 40 Kingsland due to lightening storm | Gloucester | Adverse Weather | Lightning
6922 | 2005 | 7 | 13 | 0.89653 |  | 4 | 13 | 200 | Uplands | 27.6/16kV | 2F4 | Severe lightning storm in effect. 2F4 breaker tripped. | Gloucester | Adverse Weather | Lightning
14767 | 2009 | 7 | 16 | 0.88194 |  | 65 | 69 | 505 | Uplands | 8/4.8kV | 2F4 | Red phase tap at corner pole X17651 burned off. No access to line switches, 2F4 CB opened to allow crew to make repairs. Uplands airbase - De Niverville pvt, Sampson pvt area. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8871 | 2006 | 7 | 30 | 0.37639 |  | 61 | 0 | 11 | Uplands | 8/4.8kV | 2F4 | Trans 770 at 106 De Niverville was refused and power restored due to animal contact | Gloucester | Foreign Interference | Animal
16631 | 2010 | 8 | 3 | 0.66042 |  | 159 | 297 | 143 | Uplands | 8KV | 2F4 | Crews patroled line and found neutral on secondary which caused fuse G741 red phase at 92 Mcgill to open. 10 customer on Mcgill and Kingsland remain out of power. | Gloucester | Defective Equipment
13016 | 2008 | 8 | 7 | 0.74375 |  | 84 | 220 | 157 | Uplands | 8/4.8kV | 2F4 | G739W was found blown open. Circuit patrolled nothing found. Lightning storm in the area. Switch refused and held. | Gloucester | Lightning
7309 | 2005 | 9 | 10 | 0.58819 |  | 315 | 315 | 60 | Uplands D.S | 8/4.8kV | 2F4 | B. Wills reports 2F5 blue phase wrapped into 2F2 & 2F4 circuits. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17224 | 2010 | 11 | 4 | 0.99167 |  | 107 | 18 | 10 | Uplands | 8/4.8kV | 2F4 | Overhead transformer X22937 at 165 McGill Pvt interrupted from squirrel contact. Crew replaced transformer cut-out & line clamp. 5 customers on McGill Pvt & 5 on Kingsland were affected. | Gloucester | Foreign Interference | Animal
4412 | 2003 | 11 | 7 | 0.41667 |  | 114 | 23 | 12 | Uplands | 8/4.8kV | 2F4 | Crew opened transformer to change connection. Outage affected power to 12 Customers. | Gloucester | Defective Equipment
17341 | 2010 | 11 | 24 | 0.78472 |  | 400 | 87 | 13 | Uplands | 8/4.8kV | 2F4 | Transformer X17654 replaced, due to transformer bushing heating up and seized. 105 De Niverville Pvt. | Gloucester | Defective Equipment
7860 | 2006 | 1 | 26 | 0.51389 |  | 70 | 42 | 36 | UPLANDS | 8/4.8kV | 2F5 | CUSTOMERS @ 33 CLEMENTS AND 106 RAYMOND CALLED POWER OUT. TRANSFORMERS 721 & 724 OUT. CREW FOUND BAD CUTOUT @ G741 W PHASE. REPLACED CUTOUT AND RESTORED POWER. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7944 | 2006 | 2 | 17 | 0.54167 |  | 115 | 58 | 30 | Uplands | 8/4.8kV | 2F5 | With the high winds caused the B phase at switch 787 to brake and a broken lead on the R phase at switch 728. | Gloucester | Adverse Weather | Wind
15732 | 2010 | 2 | 19 | 0.62847 |  | 65 | 11 | 10 | Uplands | 8/4.8kV | 2F5 | Transformer #X22937 located at 22 Kingsland Pvt isolated to replace connections | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8063 | 2006 | 3 | 24 | 0.77847 |  | 40 | 57 | 85 | Uplands | 8/4.8kV | 2F5 | A B phase primary down on the ground, curcuit had to be isolated to be re-install. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6392 | 2005 | 4 | 8 | 0.78125 |  | 160 | 587 | 220 | uplands | 8/4.8kV | 2F5 | G727 blue phase switch found defective. Switch was replaced by 24/7 all power restored as of 21:25. 230 customers affected in power outage. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15949 | 2010 | 4 | 18 | 0.58333 |  | 45 | 8 | 10 | Uplands | 8/4.8kV | 2F5 | Refused switch feeding transformer X22937 at 41 Clements Ave (squirrel contact) | Gloucester | Foreign Interference | Animal
10316 | 2007 | 4 | 24 | 0.41667 |  | 30 | 3 | 6 | Uplands | 4.16kV | 2F5 | Transformer located at 160 Mcgill isolated to clear defective service from the storm | Ottawa | Scheduled Outage | Preventive Maintenance
5124 | 2004 | 5 | 9 | 0.92153 |  | 123 | 205 | 100 | Uplands | 8/4.8kV | 2F5 | Switch S365 found defective and repaired. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16111 | 2010 | 5 | 20 | 0.39583 |  | 104 | 234 | 135 | Uplands | 8/4.8kV | 2F5 | Planned outage on McGill Ave to transfer the O/H fed from G741 from the 2F5 to the 2F2 as part of a future construction project. | Gloucester | Scheduled Outage | Construction
6660 | 2005 | 6 | 6 | 0.055556 |  | 147 | 1541 | 629 | Uplands | 8/4.8kV | 2F5 | Lightening strike caused all 3 fuses at in line switch G727 to open, no other damage found. Crew repaired one fuse holder and then refused and closed. | Gloucester | Lightning | Direct Strike
10774 | 2007 | 7 | 2 | 0.56181 |  | 56 | 5 | 5 | Uplands | 8/4.8kV | 2F5 | Crew found fuse blown on Transformer GL0731 at 120 McGill Ave due to squirrel contact | Gloucester | Foreign Interference | Animal
10828 | 2007 | 7 | 9 | 0.58264 |  | 52 | 5 | 6 | Uplands | 8/4.8kV | 2F5 | Fuse was found blown on transformer 763 at 89 De-Niverville Dr due to squirrel contact | Gloucester | Foreign Interference | Animal
7244 | 2005 | 8 | 30 | 0.40764 |  | 108 | 126 | 70 | Uplands | 8/4.8kV | 2F5 | Isolation of Transformers and cables to remove old cables at dip G244. | Gloucester | Scheduled Outage
7246 | 2005 | 8 | 30 | 0.51806 |  | 109 | 127 | 70 | Uplands | 8/4.8kV | 2F5 | Isolation of 7 transformers to remove old cables. | Gloucester | Scheduled Outage
7310 | 2005 | 9 | 10 | 0.61111 |  | 282 | 2860 | 650 | Uplands D.S. | 8/4.8kV | 2F5 | B. Wills reports 2F5 blue phase wrapped into 2F2 & 2F4 circuits. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7356 | 2005 | 9 | 21 | 0.35208 |  | 158 | 474 | 180 | Uplands | 8/4.8kV | 2F5 | 18 transformer isolated in the Downpatrick,Wyman area for cable replacement and transformer ratio. | Gloucester | Scheduled Outage | Preventive Maintenance
7358 | 2005 | 9 | 21 | 0.53125 |  | 101 | 286 | 170 | Uplands | 8/4.8kV | 2F5 | 17 transformers isolated in the Downpatrick,Wayman are for cable replacement and transformer ratio. | Gloucester | Scheduled Outage | Preventive Maintenance
13314 | 2008 | 10 | 3 | 0.40625 |  | 89 | 15 | 10 | Uplands | 8/4.8kV | 2F5 | Transformer #X17849 located at 30 Clements Pvt isolated due to run a service | Gloucester | Scheduled Outage | Preventive Maintenance
14756 | 2009 | 7 | 15 | 0.26944 |  | 17 | 179 | 632 | Uplands | 8/4.8kV | 2T2 | A squirrel flashed over the merivale MS 72B1-B2 tie switch which caused the A3RM to open which supplies the 2T2 | Gloucester | Foreign Interference
13856 | 2009 | 1 | 11 | 0.37986 |  | 408 | 14 | 2 | Carling | 13.2kV | 301 | VT450 and VT550 at 1545 and 1525 Carling Ave isolated for routine maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
17636 | 2011 | 2 | 23 | 0.0069444 |  | 195 | 6 | 2 | Carling | 13.2kV | 301 | VT770 and VT901 at Hampton Park Plaza was isolated to allow the contractopr to perform vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
3905 | 2003 | 8 | 15 | 0.55208 |  | 1422 | 24 | 1 | TM | 13.2kV | 301 | The main bus at VT95, 1316 Carling av flashed over due to water in the vault & was isolated for repairs. | Ottawa | Adverse Environment | Flooding
3278 | 2003 | 3 | 20 | 0.95694 |  | 93 | 3 | 2 | Hinchey | 13.2kV | 302 | The 302 line was taken out of service for repairs due to a pole fire on Shillington causing outage to 1150 & 1157 Fisher | Ottawa | Adverse Environment | Salt Spray
10525 | 2007 | 6 | 4 | 0.61389 |  | 48 | 2 | 2 | TM | 13.2kV | 302 | The two customers on this circuit are large apartement buildings on Fisher Ave. | Ottawa | Foreign Interference | Dig-in
8586 | 2006 | 6 | 24 | 0.70556 |  | 184 | 3 | 1 | Carling | 13.2kV | 302 | the main switch in VT133 @ 1170 Fisher was opened at request of the building superintendent due to water flooding near the secondary room. After investigation and ESA approval vault was re-energized. Isolation was not required. | Ottawa | Adverse Environment | Flooding
19137 | 2011 | 9 | 12 | 0.32083 |  | 40 | 1 | 2 | Carling TM | 13.2kV | 302 | 302 circuit opened due to anamal contact at riser pole on Shillington. | Ottawa | Foreign Interference | Animal
19525 | 2011 | 11 | 4 | 0.088194 |  | 957 | 16 | 2 | Carling TM | 13.2kV | 302 | TM05 CB (302) tripped. 24/7 found CB1 @ VT163 tripped, vault had been recently restored after maintenance outge, Xfmr bus isolated at VT163 & other customer on line restored. Transformer in vault may have to be replaced. | Ottawa | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
20098 | 2012 | 3 | 3 | 0.37917 |  | 215 | 233 | 65 | Carling |  | 303 | Crew patrolled after finding blue phase fuse blown in SC2101, patrol revealed no cause, blue phase riser cable tested and fuse closed back in. | Ottawa | Adverse Weather | Wind
20116 | 2012 | 3 | 3 | 0.79167 |  | 224 | 243 | 65 | Carling | 13.2kV | 303 | blue phase fuse blown in SC2101, patrol , found a blown lproclain lighting arrestor at switch S13554 @ Rideauview terr and princes of Whales. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20224 | 2012 | 3 | 26 | 0.097222 |  | 666 | 866 | 78 | Carling | 13.2kV | 303 | Customer calls indicated power out on SC2101, crew delayed by TH11 outage, on site at 04:00, found 2 phases blown in SC21. Line patrol found broken insulator at pole X31356. Crew called away for new problem at Hinchey, on -call called in. | Ottawa | Adverse Weather | Wind
20229 | 2012 | 3 | 26 | 0.40625 |  | 205 | 403 | 118 | Carling | 13.2kV | 303 | Broken insulators on the SC2101 circuit in the Princess of Whales area. | Ottawa | Adverse Weather | Wind
14131 | 2009 | 4 | 1 | 0.46181 |  | 71 | 6 | 5 | Carling | 13.2kV | 303 | Transformer #X33533 located at 61 Forest Hill Ave isolated to remove tree branch from the service. | Ottawa | Tree Contacts | Tree Limb Fallen
20749 | 2012 | 6 | 12 | 0.52778 |  | 185 | 53 | 19 | Carling | 13.2kV | 303 | At 12:40, PC10a #7888 was established at S29199 to allow crews to repair damaged pole at S28226 due to pole fire. O-Train fed from S28226 backed up by Generator required a co-ordinated restore. With crews energizing PT146 separatly from rest of circuit. Carling (SC2101 [303]) ID #20749 | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14697 | 2009 | 7 | 11 | 0.38194 |  | 375 | 12 | 2 | Carling | 13.2kV | 303 | VT284 at 1380 Prince of Wales was isolated to allow the customer's contractor to perform standard vault maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
10879 | 2007 | 7 | 16 | 0.32083 |  | 58 | 7 | 7 | Carling | 12/7.2kV | 303 | At 07:42 trans at 984 Green Valley was refused due to squirrel contact | Ottawa | Scheduled Outage | Repair
3854 | 2003 | 8 | 6 | 0.59097 |  | 6 | 119 | 1122 | Carling | 13.2kV | 303 | Lightning storm caused 303 circuit to open. Recloser was out of service. Circuit was closed by scada and held. | Ottawa | Adverse Weather | Lightning
4194 | 2003 | 10 | 2 | 0.033333 |  | 86 | 1095 | 1122 | Carling | 13.2kV | 303 | TM25 -- 303 cable opened due to Cable fault bet. VT284 and VT210. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7595 | 2005 | 11 | 12 | 0.083333 |  | 115 | 13 | 7 | Carling | 13.2kV | 303 | Suspect cable fault on 303 dip to VT211 (1375 Prince of Wales). All customers restored from alternate source. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13632 | 2008 | 11 | 17 | 0.27847 |  | 170 | 3 | 1 | Carling | 13.2kV | 303 | 13 kv vault VT250 at 1481 Fisher was interrupted when a mouse made contact in the vault & caused one fuse of R1-F to open. No damage was done to euipment, crew replaced fuse & restored power. Only the one customer, Pious High School was affected. | Ottawa | Foreign Interference | Animal
19612 | 2011 | 11 | 21 | 0.42917 |  | 23 | 3 | 7 | Carling | 13.2kV | 303 | Crew isolated transformer at 94 Forest Hill to install a new service. | Ottawa | Scheduled Outage | Construction
10500 | 2007 | 5 | 31 | 0.93056 |  | 205 | 308 | 90 | Carling | 13.2kV | 303 (SC2101) | 2 phases opened at SC21, circuit was patrolled, refused and restored, no problem found. Lightning storm in the area | Ottawa | Adverse Weather | Lightning
19968 | 2012 | 2 | 6 | 0.020833 |  | 918 | 15 | 1 | Carling | 13.2kV | 305 | TM22 breaker opend due to fault on customer secondary equippment at VT855 Central Experimental Farm | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19972 | 2012 | 2 | 6 | 0.020833 |  | 918 | 15 | 1 | Carling | 13.2kV | 305 | 13KV vault VT855 at Carling and Maple Dr tripped open due to fault on customer secondary equipment. 1 customer was affected | Ottawa | Defective Equipment
20822 | 2012 | 6 | 21 | 0.44028 |  | 165 | 3 | 1 | Carling | 13.2kV | 305 | at10:34, TM22 breaker tripped, crews dispatched to VT855 (experimental farm) and reported customer owned pad mount transformer was smoking. Customer called Ed Malik (Carleton Elect) to perform switching on customer owned gear. Potential to Vault resttored at 13:19 and Rob Twon reports PS3 isolated and all other load restored at 14:00. | Ottawa | Human Element | Incorrect Protection Settings
20877 | 2012 | 6 | 26 | 0.48819 |  | 46 | 1 | 1 | Carling | 13.2kV | 305 | VT855 caused the 305 circuit to open for no apparent reason, crew opened 305-L1 and breaker (TM22) held proving our equipment to be fine. 1 customer was affected for 46 minutes. Carling (305) ID#20877. Animal contact in customers secondary cable network | Ottawa | Foreign Interference | Animal
20879 | 2012 | 6 | 26 | 0.68958 |  | 57 | 1 | 1 | Carling | 13.2kV | 305 | VT855 caused the 305 circuit to open for no apparent reason, crew opened 305-L1 and breaker (TM22) held proving our equipment to be fine. 1 customer was affected for 57 minutes. Carling (305) ID#20879. Crew found a burnt switch on in Customers secondary network | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11030 | 2007 | 8 | 10 | 0.61042 |  | 38 | 1 | 1 | CARLING | 13.2kV | 305 | A rat in the customer owned switchgear, at VT855 caused TM22 Breaker to trip. CB2 breaker in the vault, should have cleared the customer fault, but failed to trip. | Ottawa | Defective Equipment
20148 | 2012 | 3 | 9 | 0.70833 |  | 163 | 547 | 400 | Carling | 13.2kV | 307 | A animal made contact inside switch gear SC76 @ Merivale/Central Park causing the fuses to blow at SC7601-F and SC7602-F. | Ottawa | Foreign Interference | Animal
8141 | 2006 | 4 | 12 | 0.86806 |  | 150 | 32 | 13 | Carling | 13.2kV | 307 | MT1607 was isolated to allow crews to replace transformer. Transformer # MT1607 was leaking may have been hit. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8225 | 2006 | 5 | 4 | 0.34028 |  | 501 | 167 | 20 | Carling | 13.2kV | 307 | MT1607 isolated to clean up leaking transformer & replace same on Scott St. Approx 20 customers effected in power outage. | Ottawa | Scheduled Outage | Preventive Maintenance
14808 | 2009 | 7 | 23 | 0.38056 |  | 444 | 111 | 15 | Carling | 13.2kV | 307 | Transformer MT1370 at 187 Central Park Dr isolated for replacement. | Ottawa | Scheduled Outage | Repair
9566 | 2006 | 10 | 31 | 0.47222 |  | 88 | 353 | 279 | Carling | 13.2kV | 307 | Faulted cable between VT214, 1400 Lepage & VT338, 1220 Merivale caused circuit to trip. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11890 | 2007 | 12 | 28 | 0.48125 |  | 29 | 48 | 100 | Carling | 13.2kV | 307 | Duriing restoration of cable section between MT1610 and MT1607, one switch inside new installation of transformer TP5036 was left open. Switch closed to restore power. | Ottawa | Human Element | Commissioning Errors
10495 | 2007 | 5 | 31 | 0.46528 |  | 157 | 5 | 2 | CARLING | 4.16kV | 307 (SC8101) | PT1725 supplying 310 & 314 Central Park was isolated for Electrician to repair defective main. PC10C#1843 issued to Labelle Electric. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5036 | 2004 | 4 | 22 | 0.46806 |  | 116 | 142 | 110 | Camp Temp | 27.6/16kV | 310F1 | A cable dig in between Transformer 4350B and 76B causing the fuse to blow at S104-4. | Kanata | Foreign Interference | Dig-in
3441 | 2003 | 5 | 14 | 0.375 |  | 126 | 116 | 55 | Campeau | 27.6/16kV | 310F1 | Transformers isolated to insert vents. | Kanata | Scheduled Outage | Preventive Maintenance
3442 | 2003 | 5 | 14 | 0.46319 |  | 39 | 6 | 10 |  | 27.6/16kV | 310F1 | Installing transformer inserts at trans.#32. | Kanata | Scheduled Outage | Preventive Maintenance
3456 | 2003 | 5 | 20 | 0.37639 |  | 137 | 194 | 85 | Campeau | 27.6/16kV | 310F1 | Isolation of transformers 4413,4414,4415,4416,4417,4249,4250 & 4251 for elbow replacement. | Kanata | Scheduled Outage | Repair
3466 | 2003 | 5 | 22 | 0.37708 |  | 233 | 478 | 123 |  | 27.6/16kV | 310F1 | Transformer outages for vent inserts | Kanata | Scheduled Outage | Preventive Maintenance
5268 | 2004 | 6 | 8 | 0.35417 |  | 480 | 96 | 12 | Camp. Temp | 27.6/16kV | 310F1 | To allow contractor to reground transformer & allow installation of split duct. | Kanata | Scheduled Outage | Preventive Maintenance
5308 | 2004 | 6 | 15 | 0.38056 |  | 422 | 84 | 12 | Campeau | 27.6/16kV | 310F1 | Transformer 76B at Castlefrank and Young isolated for replacement. | Kanata | Scheduled Outage | Preventive Maintenance
5489 | 2004 | 7 | 13 | 0.45833 |  | 30 | 15 | 30 | CAMPEAU TEMP | 27.6/16kV | 310F1 | White phase cable failure between S486-4 and transformer #217. Outage affected 30 customers in Katimavic area. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3896 | 2003 | 8 | 13 | 0.42708 |  | 187 | 62 | 50 | Campeau | 27.6/16kV | 310F1 | Defective U/G primary cable between transformers #283 & #125 in the Hungerford area of Kanata 3283 and #125 | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5768 | 2004 | 9 | 3 | 0.37847 |  | 103 | 69 | 40 | Campeau | 27.6/16kV | 310F1 | Planned outage to isolate txs 1709, 2232, 2231 & 2230 on Baton Cres. for elbow & insert replacement. | Kanata | Scheduled Outage | Construction
4212 | 2003 | 10 | 5 | 0.89722 |  | 195 | 2035 | 877 | Campeau Temp | 27.6/16kV | 310F1 | Red phase cable fault between switch 147 & S51. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4237 | 2003 | 10 | 10 | 0.38194 |  | 85 | 17 | 12 | Campeau | 27.6/16kV | 310F1 | B. Seaman reports repairs have been made to te152 on McCurdy Way. | Kanata | Scheduled Outage | Repair
4422 | 2003 | 11 | 11 | 0.40625 |  | 130 | 442 | 216 | Campeau | 27.6/16kV | 310F1 | Fault at elbow and insert on transformer 421B when it was opened, fuse at switch 641 and S59-4B blew. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4423 | 2003 | 11 | 11 | 0.40625 |  | 193 | 199 | 62 | Campeau | 27.6/16kV | 310F1 | Planned outage to isolate B phase transformers to install vented elbows, replacement could not be completed due to repairs required to blown insert and elbow at tx 421. | Kanata | Scheduled Outage | Preventive Maintenance
4429 | 2003 | 11 | 12 | 0.38542 |  | 185 | 290 | 94 | Campeau | 27.6/16kV | 310F1 | Transformers in the Pickford Dr area of Kanata isolated for the installation of vented elbows. | Kanata | Scheduled Outage
5888 | 2004 | 11 | 16 | 0.38472 |  | 26 | 4 | 10 | Campeau | 27.6/16kV | 310F1 | Isolate TP32B to replace defective inserts. | Kanata | Scheduled Outage | Repair
4468 | 2003 | 11 | 17 | 0.38333 |  | 178 | 549 | 185 | Camp Temp | 27.6/16kV | 310F1 | Transformer isolation for Elbow and Inserts replacement. | Kanata | Scheduled Outage | Preventive Maintenance
4475 | 2003 | 11 | 18 | 0.40139 |  | 222 | 296 | 80 |  | 27.6/16kV | 310F1 | Transformer isolation for upgrade | Kanata | Scheduled Outage | Preventive Maintenance
4502 | 2003 | 11 | 22 | 0.28611 |  | 108 | 153 | 85 | Campeau | 27.6/16kV | 310F1 | B. Baker reports transformers #932,933,935,936,937,934,3377 & 3605 is now isolated to change inserts & eblows. 85 customers effected in planned power outage. On Cohen Ave & Angus Dr. | Kanata | Scheduled Outage | Repair
4561 | 2003 | 12 | 5 | 0.45486 |  | 71 | 1 | 1 | Camp Temp | 27.6/16kV | 310F1 | Trans. 754 was isolated at 5:00 this morning and was restored without any problems. At 10:55 the W phase at switch 387 blew. Bruce Baker re-isolated Trans.754 to inspect the cause of the blown fuse. He found nothing wrong on Hydro side. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8374 | 2006 | 5 | 30 | 0.37292 |  | 599 | 2812 | 406 | Hazeldean | 8/4.8kV | 35F4 | Hazeldean 35F4 feeder auto tripped, bad cbl sections found between 3564b and 3565b; and 3567b and 3566. Sections isolated and power restored to all customers. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8376 | 2006 | 5 | 30 | 0.40347 |  | 105 | 14 | 8 | Hazeldean | 8/4.8kV | 35F4 | TRANSFORMER 3574 WAS FOUND TO HAVE AN UNDERSIZED SECONDARY FUSE. THE FUSE BLEW AND CAUSED OUTAGE. CREW REPLACED FUSE TO PICK UP CUSTOMERS. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
7663 | 2005 | 11 | 28 | 0.80625 |  | 124 | 3674 | 1822 | Bridlewood | 8/4.8kV | 35F4,F5,F6 | Load normally being carried by 115 kv transformer T2 was on 44kv 35T3. T2 out for PCB oil change. | Kanata | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
8350 | 2006 | 5 | 25 | 0.51597 |  | 42 | 10 | 14 | Hazeldean | 8/4.8kV | 35F5 | Isolated Transformer 3121 at 14 Clarendon to repair underground service | Kanata | Defective Equipment | Equipment Deterioration Due to Age
6892 | 2005 | 7 | 9 | 0.49792 |  | 190 | 152 | 50 |  | 8/4.8kV | 35F5 | Defective cable between T2521 and T2522 on Old Colony Road, 35F5 cable. | Kanata | Defective Equipment
8808 | 2006 | 7 | 24 | 0.90972 |  | 192 | 2266 | 1020 | Hazeldean | 8/4.8kV | 35F5 | White phase cable fault between 2522 and 2521Old Colony Road. S299w blown and 35f5 recloser tripped. Could not close from SCADA. Recloser reset at station and closed. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5807 | 2004 | 9 | 15 | 0.96875 |  | 234 | 321 | 130 | Hazeldean MS | 8/4.8kV | 35F5 | Cable failure on Abbeyhill Dr. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11622 | 2007 | 10 | 29 | 0.47917 |  | 70 | 14 | 12 | BRIDLEWOOD | 27.6/16kV | 35F5 | Tranformer #003120 at 3 Courtney isolated to allow contractor to complete service repairs | Kanata | Scheduled Outage | Repair
9708 | 2006 | 11 | 23 | 0.37153 |  | 120 | 87 | 52 | Hazeldean | 8/4.8kV | 35F5 | Transformer 2521W on Old Colony Rd and 2522W on Post Rd was isolated to connect new cable after a fault. | Kanata | Scheduled Outage | Repair
6770 | 2005 | 6 | 21 | 0.39583 |  | 126 | 429 | 400 | Hazeldean MS | 8/4.8kV | 35F6 | Primary cable dig in at 79 Castlefrank caused the 35F6 to A/R A, cables isolated and load restored in stages. | Kanata | Foreign Interference | Dig-in
8846 | 2006 | 7 | 26 | 0.375 |  | 220 | 34 | 30 | Hazeldean | 8/4.8kV | 35F6 | Transformer T2522 on Old Colony Rd. isolated for repairs, due to live front txs T2528 & T2529 were interupted for switching purposes. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
8611 | 2006 | 6 | 28 | 0.28819 |  | 337 | 6729 | 2534 | HAZELDEAN | 8/4.8kV | 35T3 | There was a bus failure and flashed over insulator at the Hazedldean station plus a blown W phase cable bet S15-1 and 541. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
8615 | 2006 | 6 | 28 | 0.59097 |  | 11 | 276 | 2022 | Hazeldean | 8/4.8kV | 35T3 | The load had to be dump so the individaul feeders be pick up safley. The scada would not work properly so the F4,F5,F6 had to be closed manually. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
12827 | 2008 | 7 | 12 | 0.82639 |  | 9 | 2 | 14 | Beaverbrook | 12/7.2kV | 39F1 | At 7:50pm transformer TE2506 at 50 Beaverbrook Lane was isolated to allow crew to short out burning up CT's on secondary bus of transformer, 14 customers were affected and power was restored at 7:59pm. Beaverbrook (39F1). ID#12827. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
13779 | 2008 | 12 | 18 | 0.37847 |  | 295 | 25 | 5 | Soth March | 12/7.2kV | 39F1 | Tx 2504R at 1 Chisholm was isolated to replace leaking Tx. | Kanata | Scheduled Outage | Repair
15682 | 2010 | 1 | 25 | 0.51389 |  | 298 | 45 | 9 | South March | 12/7.2kV | 39F2 | Crew broke bushing of transformer 5799W at 13 Best Way while isolating the secondary to install a new service. Transformer was isolated to clean up the oil spill & replace the defective transformer. Customers affected were on Best Way & Bethune Way. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19966 | 2012 | 2 | 5 | 0.79167 |  | 230 | 336 | 562 | South March | 12/7.2kV | 39F2 | 39F2 breaker opened under protection. Breaker closed and held via SCADA after calling Police and Fire. Part of R phase load not recovered. Crews found a blown fuse at S3, affecting 9 transformers on Teron Rd, Pellan and Varley Dr. Cable sectionalized and faulted cable section between transformers 2546R and 2540R isolated. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
12160 | 2008 | 3 | 20 | 0.45486 |  | 7 | 12 | 100 | South March | 8/4.8kV | 39F2 | While breaking parallel on the S58-4, the blue phase fuse flashed to ground, causing the blue phase fuse at S10-3 to blow. Crew refused and closed the S58-4 to restore power. | Kanata | Human Element | Incorrect Use of Equipment
17868 | 2011 | 4 | 11 | 0.97361 |  | 208 | 1061 | 850 | South March | 12/7.2kV | 39F2 | 39F2 circuit opened causing outage on Teron Rd area. Circuit was sectionized and overhead portion was energized. Underground was sectionalizer were check for fault indicaties flagged. No fault found. 39F2 breaker reopened and S58-1 closed. 39F2 breaker closed at station and holding. Blue phase indicates still power out. 24/7 reports Varley lane still out of power. 24/7 to hi pot blue phase cable section between TP6154 & S3-1 blue phase. Blue phase fuse found blown at S3-1 | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8150 | 2006 | 4 | 14 | 0.19028 |  | 119 | 278 | 140 | SOUTH MARCH | 12/7.2kV | 39F2 | 39F2 W PHASE OPENED @ SOUTH MARCH, NO APPARENT CAUSE. | Kanata | Unknown/Other | No Apparent Cause
8184 | 2006 | 4 | 23 | 0.8125 |  | 95 | 95 | 60 | South March | 12/7.2kV | 39F2 | A defective recloser on the 39F2 R phase at Southmarch. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20461 | 2012 | 5 | 4 | 0.46458 |  | 16 | 150 | 562 | South March | 12/7.2kV | 39F2 | Customers in the beaverbrook and teron rd area were interupted when the 39F2 breaker opened due to a flashed insulator at S18 | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20567 | 2012 | 5 | 24 | 0.42153 |  | 234 | 148 | 38 | South March MS | 12/7.2kV | 39F2 | Hydro Ottawa crews isolated the S18 sectionalizer including transformers 5789B, 5788B, 5787B, 5786B & 5790W to allow for repairs on S18. | Kanata | Scheduled Outage | Repair
8351 | 2006 | 5 | 25 | 0.45833 |  | 193 | 35 | 11 | South March | 27.6/16kV | 39F2 | Isolated transformer 3201 at 46 Carmichael Crt for Maintenance | Kanata | Scheduled Outage | Preventive Maintenance
18223 | 2011 | 5 | 26 | 0.15486 |  | 77 | 815 | 635 | South March | 13.2kV | 39F2 | 39F2 breaker opened and did not reclose. SCADA indicated a Blue phase trip flag. The circuit was sectionalized and eventually all restored with no cause found. | Kanata | Unknown/Other | No Apparent Cause
16178 | 2010 | 6 | 2 | 0.37222 |  | 430 | 86 | 12 | South March | 12/7.2kV | 39F2 | Transformer 5797 at 25 Bethune isolated for oil spill clean up. | Kanata | Scheduled Outage | Preventive Maintenance
16210 | 2010 | 6 | 7 | 0.042361 |  | 98 | 278 | 213 | South March | 12/7.2kV | 39F2 | 39F2 breaker tripped open, no auto reclose. Breaker flagged white phase. Load restored in three sections | Kanata | Unknown/Other | No Apparent Cause
16227 | 2010 | 6 | 7 | 0.042361 |  | 2239 | 37 | 1 | Southmarch | 12/7.2kV | 39F2 | A defective cable that feeds the vault 2834 @ 365 March Rd. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3602 | 2003 | 6 | 24 | 0.81042 |  | 11 | 64 | 350 | South March | 12/7.2kV | 39F2 | The control fuses to 39F3 had been removed while a WT permit was in effect. On returning load to normal with no metering we could not tell if a parrallel had been made, and on opening S58-4 load was lost. | Kanata | Human Element | Switching Errors
20922 | 2012 | 7 | 4 | 0.36944 |  | 17 | 4 | 13 | South March MS |  | 39F2 | Transformer 002540 at 14 Milne Ave isolated for service upgrade | Kanata | Scheduled Outage | Construction
3752 | 2003 | 7 | 17 | 0.42222 |  | 101 | 19 | 11 | Southmarch | 12/7.2kV | 39F2 | Isolation of Tx 2552 for maintenance | Kanata | Scheduled Outage | Preventive Maintenance
14788 | 2009 | 7 | 20 | 0.42292 |  | 328 | 33 | 6 |  | 12/7.2kV | 39F2 | Transformer TP6154 was isolated for the transformer PCB replacment program. | Nepean | Scheduled Outage
12985 | 2008 | 8 | 1 | 0.39444 |  | 78 | 6 | 5 | SouthMarch | 12/7.2kV | 39F2 | Transformer 2506R at 61 Beaverbrook isolated to allow metering to replace equipment on the secondary bars. 5 customers affected, power was restored at 10:46 am. | Kanata | Scheduled Outage
15288 | 2009 | 10 | 21 | 0.6875 |  | 320 | 513 | 105 | South March | 12/7.2kV | 39F2 | Blue phase cable fault found between TP6154B-H1A & TE2543B-H1B. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19606 | 2011 | 11 | 19 | 0.95833 |  | 242 | 509 | 637 | South March ms | 12/7.2kV | 39F2 | 39F2 tripped & locked out. A faulted B phase cable was eventually found downstream of S3 on Varley lane. After patrolling sectionalizers on Teron rd, 39F2 was closed apparently restoring all customers. New customer calls indicated 3 tx's on Varley lane were still off. S3-1B was found blown, FCI's indicated a defective cable between 2542 & 2543. Tx 2541 & 2542 were restored from S3 but when the crew attempted to restore 2543, S10-2 B opened. A misleading FCI indication led to closing on a faulted cable section. S10-2B was replaced, cable between TP6154 & 2543 isolated & all power restored. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
13694 | 2008 | 12 | 2 | 0.39097 |  | 482 | 64 | 8 | South March | 12/7.2kV | 39F2 | TP5403 at 38 Lismer was isolated to replace transformer due to PCB contamination. | Kanata | Scheduled Outage
13696 | 2008 | 12 | 3 | 0.38333 |  | 473 | 95 | 24 | South March | 12/7.2kV | 39F2 | TP5494 at 6 Binning Cresent was isolated for replacement. 24 customers initiall out for 2min due to live front transformers in circuit; 12 customers remained out until W/P completed | Kanata | Scheduled Outage
13735 | 2008 | 12 | 11 | 0.37639 |  | 354 | 59 | 10 | South March | 12/7.2kV | 39F2 | Transformer 2503 isolated at 17 Beaverbrook for transformer change. Nomenclature changed to TP6617 | Kanata | Scheduled Outage
7985 | 2006 | 3 | 3 | 0.52083 |  | 15 | 4 | 16 | South March | 12/7.2kV | 39F3 | Isolated transformer 3203 at 2 Carmichael Crt to disconnected broken meter base | Kanata | Scheduled Outage | Repair
6452 | 2005 | 4 | 24 | 0.45278 |  | 148 | 437 | 300 | South March | 12/7.2kV | 39F3 | Outage caused by broken insulator on the structor of South march 39F3 circuit. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
12419 | 2008 | 5 | 9 | 0.24653 |  | 192 | 178 | 65 | South March | 12/7.2kV | 39F3 | Underground cable fault between Tx TP5403 & Tx 3088 on Lismer cr in Kanata caused W phase fuse to blow at sectionalizer S10. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
10423 | 2007 | 5 | 16 | 0.77708 |  | 225 | 210 | 75 | South March | 12/7.2kV | 39F3 | Cable fault between TE2543 & TE2523 on blue phase. NO spare fuses or barrels left in S3. 24/7 has to go to Kanata and find fuses & barrels. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
14563 | 2009 | 6 | 18 | 0.38403 |  | 70 | 14 | 12 | South March MS | 12/7.2kV | 39F3 | Transformer 2525W was isolated to allow the metering dept to install new metering equipment. | Kanata | Scheduled Outage | Preventive Maintenance
3659 | 2003 | 7 | 1 | 0.76806 |  | 282 | 242 | 200 | South March | 12/7.2kV | 39F3 | Red phase cable section between S10-2 and transformer 2553 found blown. Cable section isolated by 24/7 & oncall crew. Cable crew to locate faulted section of cable tonight, and crews to make repairs in morning. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
12865 | 2008 | 7 | 16 | 0.94722 |  | 358 | 6 | 1 | South March | 8/4.8kV | 39F3 | Lightning activity possible cause for outage to transformer T2881 at 2881 Huntley rd. | Goulburn | Defective Equipment
14810 | 2009 | 7 | 23 | 0.38194 |  | 323 | 32 | 6 | South March | 12/7.2kV | 39F3 | Crew isolated TP6153 as part of PCB replacement program. | Kanata | Scheduled Outage | Preventive Maintenance
18875 | 2011 | 8 | 3 | 0.74306 |  | 291 | 53 | 11 | Southmarch | 13.2kV | 39F3 | Crews replace leaking Transformer 3252 @ 31A Varley Dr. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
18876 | 2011 | 8 | 3 | 0.74306 |  | 10 | 1 | 4 | Southmarch | 13.2kV | 39F3 | When crews completed isolating transformer 3252 from transformer 3259 the -1 & -2 were reversed causing a breif outage on transformer 3259 @ 6 JACKSON CRT | Kanata | Human Element | Incorrect Records
7119 | 2005 | 8 | 10 | 0.64583 |  | 315 | 184 | 35 | Richmond North | 12/7.2kV | 39F3 | M. Brown reports arrester & fuse replaced at RX6693 & R/C 1087 is now closed restoring all load. 35 customers affected by power outage. | Goulburn | Adverse Weather | Lightning
13058 | 2008 | 8 | 14 | 0.39028 |  | 446 | 74 | 10 | Southmarch | 12/7.2kV | 39F3 | Transformer TP5402 @ 40 Vareley Dr was isolated to allow the crew to replace the transformer under the PCB replacement program and install a new base. | Kanata | Scheduled Outage | Preventive Maintenance
19020 | 2011 | 8 | 26 | 0.66597 |  | 190 | 148 | 56 | South March | 12/7.2kV | 39F3 | cable fault between TP5495 and 2555 on Carr and Borduas caused S10-2 white phase to blow, load restored in stages. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
9187 | 2006 | 9 | 9 | 0.74236 |  | 391 | 421 | 120 | South March | 12/7.2kV | 39F3 | 39F3 B phase tripped due tp cbl fault between S10-3 and transformer 2551. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11298 | 2007 | 9 | 13 | 0.38889 |  | 325 | 32 | 6 | South March | 8/4.8kV | 39F3 | Transformer # 3250 on Varley Dr was isolated to replace leaking transformer and oil spill clean up. | Kanata | Defective Equipment
13225 | 2008 | 9 | 13 | 0.44583 |  | 823 | 14 | 1 | South March | 12/7.2kV | 39F3 | Cable faulted between TP5402 and S4-2 on red phase at 40 Varley. Crews located fault and made splicing repairs. 1 customer affected. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
4267 | 2003 | 10 | 15 | 0.65972 |  | 155 | 565 | 320 | South March | 12/7.2kV | 39F3 | Tree on the line and is burning causing the 39F3 R&W Kyles to open. The BØ Kyle was opened to allow for the tree to be removed and the power restored. | Kanata | Tree Contacts | Tree Fallen
11584 | 2007 | 10 | 24 | 0.62292 |  | 156 | 146 | 72 | South March MS | 12/7.2kV | 39F3 | At 1:38 pm, customers in the area of Milne and Varley Road reported of outages. 24-7 crew dispatched and discovered a cable fault on the 39F3 circuit on the blue phase cable section between T2523B (27 Milne) and T2543B (80 Varley) transformers. 72 customers affected for 146 min, ID #11584. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
13450 | 2008 | 10 | 28 | 0.88889 |  | 110 | 587 | 320 | South March | 12/7.2kV | 39F3 | SWITCH CLOSED BY BILL SEAMAN | Kanata | Adverse Weather
9537 | 2006 | 10 | 29 | 0.46875 |  | 170 | 861 | 320 | South March | 8/4.8kV | 39F3 | Tree fell on the O/H behind the south march station. | Kanata | Adverse Weather | Wind
13650 | 2008 | 11 | 21 | 0.40694 |  | 401 | 53 | 8 | South March | 12/7.2kV | 39F3 | Transformer TP5495 @ Beaverbrook rd. was isolated to change transfomer because of PCB's | Kanata | Scheduled Outage
19637 | 2011 | 11 | 26 | 0.97292 |  | 149 | 118 | 50 | South March | 13.2kV | 39F3 | Defective cable between 3088W and TP5403 W on Lismer in Kanata. | Ottawa | Defective Equipment
15514 | 2009 | 12 | 14 | 0.45 |  | 55 | 13 | 14 | South March | 12/7.2kV | 39F3 | TP5494 was isolated at 53 Lismer for underground creww to test the ground grid | Kanata | Scheduled Outage
15515 | 2009 | 12 | 14 | 0.54653 |  | 41 | 7 | 10 | South March | 12/7.2kV | 39F3 | TP5403 at 36 Lismer was isolated for underground crew to test the ground grid | Kanata | Scheduled Outage
15517 | 2009 | 12 | 15 | 0.43194 |  | 53 | 26 | 30 | South March | 12/7.2kV | 39F3 | TP5496, TP6154, & 3076 were isolated to allow crews to test ground grid. | Kanata | Scheduled Outage | Preventive Maintenance
15539 | 2009 | 12 | 21 | 0.55278 |  | 44 | 9 | 12 | South March | 12/7.2kV | 39F3 | Transformer TP5495 @ Beaverbrook and Coady was isolated for crew to test ground grid. | Kanata | Scheduled Outage | Repair
20076 | 2012 | 2 | 28 | 0.60417 |  | 485 | 8 | 1 | Beacon Hill | 8/4.8kV | 3F1 | On call underground crew was called in to repair defective primary cable feeding GLVE2 at 635 Laverendrye. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16038 | 2010 | 5 | 4 | 0.44097 |  | 180 | 33 | 11 | Beacon Hill MS | 8/4.8kV | 3F1 | TE769 at 1476 Lassiter terr isolated to allow crews to replace defective xfmr. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5584 | 2004 | 7 | 30 | 0.80486 |  | 231 | 289 | 75 | Beacon | 8/4.8kV | 3F1 | Dave Guy reports a blown cable between SE6 and T376 on the B phase @ Ogilvie and La Verendrye. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13120 | 2008 | 8 | 18 | 0.36042 |  | 1661 | 0 | 1 | Beacon Hill |  | 3F1 | 635 Laverendre Dr. Repaired Red Phase cable from S1 feeding VE2 at school | Gloucester | Defective Equipment
13121 | 2008 | 8 | 18 | 0.36042 |  | 1661 | 28 | 1 | BeaconHill | 8/4.8kV | 3F1 | Repaired faulted Red Phase Cable from S1 feeding VE2 at school, 635 Leverendre Dr. | Gloucester | Defective Equipment
5790 | 2004 | 9 | 9 | 0.58681 |  | 587 | 319 | 80 | Beaconhill | 8/4.8kV | 3F1 | While pin pointing the fault a fault indicator was faulty causing a larger outage while restoring the load. A blown transformer at 695 La Verendrye was the problem. | Gloucester | Adverse Weather | Rain
15298 | 2009 | 10 | 24 | 0.42917 |  | 78 | 6 | 5 | Beaconhill | 8/4.8kV | 3F1 | Transformer #X16959 located at 2087 Montreal Rd isolated due to squirrel contact | Gloucester | Foreign Interference | Animal
15425 | 2009 | 11 | 26 | 0.40833 |  | 327 | 267 | 49 | Beacon Hill | 8/4.8kV | 3F1 | Cable sections to SE7 were isolated including transformers TE2700, TE775, TE768 & vault VE47 in the Lassiter Terrace / Ogilvie Rd area. Hydro Ottawa cable crews were cutting in new cables, new switchgear and replacing elbows as part of the cable replacement program. | Gloucester | Scheduled Outage | Preventive Maintenance
11807 | 2007 | 12 | 4 | 0.63472 |  | 74 | 84 | 68 | Beacon Hill | 8/4.8kV | 3F1 | A barrier board fell across the B phase at T373B(TP4873) 687 La Verendry. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15519 | 2009 | 12 | 15 | 0.38542 |  | 200 | 283 | 85 | Beacon Hill | 8/4.8kV | 3F1 | To allow crews to change inserts & L/B elbows on T772 T2675 T2674 & T2700 IN THE Lassiter & Locksley | Gloucester | Scheduled Outage | Construction
15596 | 2009 | 12 | 30 | 0.41389 |  | 133 | 22 | 10 | Beacon Hill | 8/4.8kV | 3F1 | Crew replaced TP6146 at 1314 Lassiter Terr to allow for PCB transformer replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
7778 | 2006 | 1 | 6 | 0.40278 |  | 58 | 6 | 6 | Beacon Hill | 8/4.8kV | 3F3 | Transformer T156R at 594 Eastvale isolated for cable replacement. | Gloucester | Scheduled Outage | Construction
13855 | 2009 | 1 | 11 | 0.48681 |  | 181 | 220 | 105 | Beaconhill | 8/4.8kV | 3F3 | A bad cable bet transformer T260W and T261W at 616 Clancy. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9945 | 2007 | 1 | 18 | 0.54167 |  | 35 | 6 | 11 | Beaconhill | 8/4.8kV | 3F3 | Transformer #TP3981 located at 1999 Woodway isolated due to cable replacement | Gloucester | Scheduled Outage | Preventive Maintenance
7831 | 2006 | 1 | 20 | 0.39583 |  | 345 | 75 | 13 | Beacon Hill | 8/4.8kV | 3F3 | Transformer T140 at 2512 Filmore St was isolated for an upgrade | Gloucester | Scheduled Outage | Preventive Maintenance
7844 | 2006 | 1 | 23 | 0.52083 |  | 84 | 13 | 9 | Beacon Hill | 8/4.8kV | 3F3 | Transformer T141 at 2125 Fillmore Dr was isolated for primary cable replacment | Gloucester | Scheduled Outage | Construction
13891 | 2009 | 1 | 23 | 0.42083 |  | 105 | 14 | 8 | Beacon Hill | 27.6/16kV | 3F3 | T261 was isolated to allow crews to repair cable section at 619 Gaines. | Ottawa | Scheduled Outage | Preventive Maintenance
7859 | 2006 | 1 | 26 | 0.40625 |  | 143 | 29 | 12 | BEACON HILL | 8/4.8kV | 3F3 | XMER T147W @ 2160 BLUE JAY CR. IN BEACON HIL FOR CBL REPLACEMENT | Gloucester | Scheduled Outage | Construction
7864 | 2006 | 1 | 27 | 0.40278 |  | 170 | 28 | 10 | Beacon Hill | 27.6/16kV | 3F3 | Planned outage to T148 at 2150 Monson Cres, to terminate new u/g cable. | Gloucester | Scheduled Outage
3195 | 2003 | 2 | 17 | 0.125 |  | 210 | 4 | 1 | Beaconhill | 8/4.8kV | 3F3 | Crew isolated vault at 614 Eastvale V19 to replace defective 347/600 transformer. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
14028 | 2009 | 3 | 8 | 0.020139 |  | 436 | 3386 | 466 | Beacon Hill | 8/4.8kV | 3F3 | 3F3 circuit was isolated as part of a schedualled outage to Beacon Hill sub station to allow crews to replace 44kV structure at Montreal & Shefford, and to allow Station's crew to perform sub station maintenance. | Gloucester | Scheduled Outage | Preventive Maintenance
14063 | 2009 | 3 | 15 | 0.73542 |  | 1 | 8 | 466 | Beacon Hill | 8/4.8kV | 3F3 | Beacon Hill 3F3 load was interrupted to transfer load to temp substation supply. | Gloucester | Scheduled Outage | Construction
14205 | 2009 | 4 | 23 | 0.67708 |  | 1 | 8 | 466 | Beacon Hill | 8/4.8kV | 3F3 | 3F3 circuit load dumped from MUS supply & restored on new BHTT1 supply. | Gloucester | Scheduled Outage | Construction
8200 | 2006 | 4 | 28 | 0.20139 |  | 149 | 76 | 37 | Beaconhill | 8/4.8kV | 3F3 | A cable fault bet transformer T232 (550 Buchanan) and T233 (543 Buchanan) on the B phase. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14271 | 2009 | 5 | 1 | 0.11458 |  | 663 | 546 | 125 | Beaconhill | 8/4.8kV | 3F3 | A cable fault in LA VERENDRYE DR area, oncall had to be called in to assist in the restoration, a broken switch was also found ,the crew were called away to respond to a bigger outage in the Parkwood area. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14274 | 2009 | 5 | 1 | 0.42569 |  | 662 | 211 | 115 | Beaconhill | 8/4.8kV | 3F3 | Defective cable section between T263W and T173. Outage was lengthy do to crew leaving the site for pole fire in Parkwood Hills. During fault finding, G56W blew, cable isolated and customers restored. | Gloucester | Defective Equipment
8230 | 2006 | 5 | 4 | 0.52014 |  | 138 | 16 | 7 | Beaconhill | 8/4.8kV | 3F3 | D. MARTIN REMOVED T232B ON BUCHMAN CR. FROM SERVICE TO REPAIR CBL FAULTED SECTION. | Gloucester | Scheduled Outage | Repair
12444 | 2008 | 5 | 16 | 0.37639 |  | 323 | 329 | 105 | Beacon Hill | 8/4.8kV | 3F3 | 3F3 circuit auto-reclosed twice. Cause was later determined to be a cable fault between T252 & T253. Restoration was delayed due to switch G56W having to be replaced under a work permit. Also cable between T254 & T255 did not pass hipot and was thought to be the cause of the outage. After the cable between T252 & T253 was also found to be bad, the cable between T254 & T255 was isolated under a work permit & tested more accurately, proving it to be OK for service. | Gloucester | Defective Equipment
18176 | 2011 | 5 | 18 | 0.41667 |  | 105 | 18 | 10 | Beacaon Hill | 8/4.8kV | 3F3 | R Grisel isoalted TP3975 at 1999 Quincy Ave in order to make repairs to a sec u/g service | Gloucester | Scheduled Outage | Preventive Maintenance
20538 | 2012 | 5 | 18 | 0.53472 |  | 51 | 346 | 407 | Beacon Hill | 8/4.8kV | 3F3 | at 12:50, SC7988-3F3 tripped at beacon Hill DS. Steve pranschki reports Ligtning arrestor blown behind station. Mark branchaud reports Blown arrestor at TEMP151, cut clear and power restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6619 | 2005 | 5 | 30 | 0.82431 |  | 112 | 91 | 50 |  | 8/4.8kV | 3F3 | Cable fault between T30 and T31 on Dutton in Gloucester. | Gloucester | Defective Equipment
6671 | 2005 | 6 | 7 | 0.40278 |  | 155 | 26 | 10 | Beaconhill | 8/4.8kV | 3F3 | Transformer 60 @ 2102 Kender was isolated to install new cable and connection. | Gloucester | Scheduled Outage | Repair
6675 | 2005 | 6 | 7 | 0.54167 |  | 105 | 18 | 10 | Beaconhill | 8/4.8kV | 3F3 | Transformer 61 @ 648 Ingram was isolated to install new cable and connection. | Gloucester | Scheduled Outage | Repair
18385 | 2011 | 6 | 10 | 0.69792 |  | 432 | 2663 | 474 | Beaconhill | 8/4.8kV | 3F3 | 3F3 tripped shortly after the 3F5, which run together at Eastvale and Tisdale. Due to paving company striking the down guy on the corner pole and two woodden pins are broken. On-call crew called in to make repairs | Ottawa | Foreign Interference | Vehicle
16250 | 2010 | 6 | 11 | 0.45625 |  | 91 | 687 | 453 | Beacon Hill | 8/4.8kV | 3F3 | Power out on 3F3 cuses by tree contractor dropping limb on overhead. (Neds tree service). | Gloucester | Foreign Interference | Foreign Object
6706 | 2005 | 6 | 13 | 0.83819 |  | 263 | 53 | 12 | Beacon Hill | 4.16kV | 3F3 | Isolated Transformer at 2112 Graston to repair a bad underground service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20864 | 2012 | 6 | 25 | 0.23125 |  | 267 | 49 | 11 | Beaconhill | 8/4.8kV | 3F3 | Replaced broken fuse at transformer X20814 at 2050 Kings Grove Crers | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
5462 | 2004 | 7 | 8 | 0.39583 |  | 202 | 34 | 10 | Beaconhill | 8/4.8kV | 3F3 | T320 at 1952 OaKDale to replace defective transformer. 10 Customers affected in power outage. | Gloucester | Scheduled Outage | Preventive Maintenance
8713 | 2006 | 7 | 13 | 0.52083 |  | 105 | 19 | 11 | Beacon Hill | 8/4.8kV | 3F3 | Rick Barnett opened transformer TE233B to do an u/g primary cable installation | Ottawa | Scheduled Outage | Construction
8716 | 2006 | 7 | 13 | 0.45486 |  | 35 | 4 | 6 | Beaconhill | 4.16kV | 3F3 | Rick Barnett opened transformer TE232B to do a new primary cable installation | Gloucester | Scheduled Outage | Construction
8735 | 2006 | 7 | 15 | 0.66806 |  | 190 | 32 | 10 | Beaconhill | 8/4.8kV | 3F3 | A broken meter base and burnt connection at 2012 Hollybrook Cres caused the fuse to blow at transformer T231B phase. | Gloucester | Foreign Interference | Foreign Object
18775 | 2011 | 7 | 19 | 0.22083 |  | 621 | 5111 | 1000 | Beacon Hill | 8/4.8kV | 3F3 | At 05:18 am 3F3 at beacon hill tripped. Crews found two different cable faults, one at the station on 3F3 riser and on White Phase between TE172 and TE17and a burnt Red Phase switch at S26873. | Gloucester | Defective Equipment
3768 | 2003 | 7 | 21 | 0.45833 |  | 72 | 14 | 12 | Beaconhill | 8/4.8kV | 3F3 | § At 11:00am on Monday, approximately 12 customers in the Oakdean Street area of Beaconhill were interrupted due maintenance on a transformer. Transformer was maintained and all customers were restored at 12:12pm. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
7021 | 2005 | 7 | 25 | 0.5375 |  | 28 | 8 | 18 | Beacon Hill | 8/4.8kV | 3F3 | Isolated Transformer 0172 at 633 Clancy to install a new service | Ottawa | Scheduled Outage | Preventive Maintenance
18817 | 2011 | 7 | 25 | 0.48264 |  | 33 | 261 | 474 | Beacon Hill | 8/4.8kV | 3F3 | While completing OTO 17-58825 to restore 3F3 cable between TE172 and TE173 to normal, 3F3 Circuit opened and Al St. Martin reports a fault located between the two transformers at 6 feet from the original fault when making parallel. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
18845 | 2011 | 7 | 28 | 0.80625 |  | 157 | 592 | 474 | Beaconhill | 8/4.8kV | 3F3 | Cable fault between TE172 to TE173 on Clancy. Circuit sectionalized and power restored in stages for fault finding. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
18926 | 2011 | 8 | 14 | 0.51875 |  | 69 | 764 | 664 | Beacon Hill | 8/4.8kV | 3F3 | Defective calbe caused 3F3 to open. Beacon Hill (3F3) ID#18926 | Gloucester | Defective Equipment
11186 | 2007 | 8 | 29 | 0.7375 |  | 58 | 650 | 672 | Beacon Hill | 8/4.8kV | 3F3 | 3F3 circuit opened and locked out, was closed back in via SCADA and circuit held. Cause due to adverse weather, | Gloucester | Adverse Weather | Lightning
15036 | 2009 | 8 | 31 | 0.42083 |  | 109 | 178 | 98 | Beacon Hill | 8/4.8kV | 3F3 | Cable fault located between G56 and T252 on Oakdean and Duff on the 3F3 white phase out of Beacon Hill, cable isolated and customers restored via backfeed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19095 | 2011 | 9 | 6 | 0.39861 |  | 243 | 89 | 22 | Beacon Hill | 8/4.8kV | 3F3 | TE172 & TE173 on Gaines & Laverendrye were isolated to to complete installation of new primary cable. | Gloucester | Scheduled Outage | Construction
19104 | 2011 | 9 | 6 | 0.6375 |  | 350 | 192 | 33 | Beacon Hill | 8/4.8kV | 3F3 | Refused Transformer GLTE0173 at 641 Clancy; all power restored | Ottawa | Scheduled Outage | Repair
19221 | 2011 | 9 | 21 | 0.45139 |  | 30 | 6 | 11 | Beaconhill | 8/4.8kV | 3F3 | Isolated transformer GLTP0255 at 1951 Oakdean Cres to reconnect U/G service | Gloucester | Scheduled Outage | Emergency Services Request
11361 | 2007 | 9 | 22 | 0.44792 |  | 60 | 11 | 11 | Beacon Hill | 8/4.8kV | 3F3 | At 10:45 trans GL5746 at 2030 Quincy was isolated in order to make repairs to sec conductor | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
17008 | 2010 | 9 | 27 | 0.39444 |  | 132 | 33 | 15 | Beacon Hill | 8/4.8kV | 3F3 | TE172 at 633 Clancy isolated to pull in new secondary service for 634 Laverendry . 15 customers on Laverendry & Clancy were affected. | Gloucester | Scheduled Outage
17009 | 2010 | 9 | 27 | 0.61944 |  | 27 | 7 | 15 | Beacon Hill | 8/4.8kV | 3F3 | TE172 at 633 Clancy isolated to connect new secondary service to 634 Laverendry . 15 customers on Laverendry & Clancy were affected. | Gloucester | Scheduled Outage
15277 | 2009 | 10 | 19 | 0.85764 |  | 25 | 3 | 8 | Beaconhill | 8/4.8kV | 3F3 | Transformer #GLTE0036 located at 754 Eastvale isolated to reconnect service (was disc for elec to make repairs) | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7572 | 2005 | 11 | 6 | 0.86806 |  | 64 | 819 | 768 | Beaconhill | 8/4.8kV | 3F3 | M. Byers reports tree branch removed from overhead circuit | Gloucester | Tree Contacts | Tree Limb Fallen
7578 | 2005 | 11 | 7 | 0.45833 |  | 272 | 5 | 1 | Beacon Hill | 8/4.8kV | 3F3 | Vault V19 at La Verendrye School was isolated to replace defective transformers. | Gloucester | Defective Equipment
19542 | 2011 | 11 | 7 | 0.66111 |  | 20 | 158 | 475 | Beaconhill | 27.6/16kV | 3F3 | During fault finding on the 3F5 red phase, the 3F3 breaker tripped. No SCADA available to close breaker in, crew closed breaker from Station. Power restored | Gloucester | Defective Equipment
9623 | 2006 | 11 | 9 | 0.4375 |  | 105 | 28 | 16 | Becon Hill | 8/4.8kV | 3F3 | Transformers on Buchanan Cres were isolated for cable and transformer replacement. WP 2-2197. | Gloucester | Scheduled Outage | Construction
11727 | 2007 | 11 | 16 | 0.57292 |  | 5 | 1 | 10 | Beacon Hill | 8/4.8kV | 3F3 | Transformer #TE167 located at 574 Laverendrye Dr isolated due to removing a cab tire | Gloucester | Scheduled Outage | Construction
9728 | 2006 | 11 | 25 | 0.39931 |  | 105 | 61 | 35 | Beacon Hill | 8/4.8kV | 3F3 | Dip pole switch S187B on Quincy Ave in Gloucester failed and had to be replaced. | Gloucester | Defective Equipment
9744 | 2006 | 11 | 28 | 0.40417 |  | 121 | 40 | 20 | BEACONHILL | 27.6/16kV | 3F3 | TP3975 & TP3976 isolated for cable replacement program on Buchanan Cres in Beaconhill. | Gloucester | Scheduled Outage
11783 | 2007 | 11 | 28 | 0.53542 |  | 460 | 195 | 60 | Beaconhill | 8/4.8kV | 3F3 | defective transformer TP3086 @ 2148 Dutton caused G17W to open interrupting 5 transformers. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
9750 | 2006 | 11 | 29 | 0.48958 |  | 171 | 23 | 11 | Beacon Hill | 27.6/16kV | 3F3 | Transformer TP3977 at 2007 Woodway in Gloucester isolated for cable replacement. | Gloucester | Scheduled Outage | Construction
9758 | 2006 | 11 | 30 | 0.4375 |  | 122 | 16 | 8 | Beaconhill | 8/4.8kV | 3F3 | Greg Bell isolated Transformer TP3978 at 531 Buchanan to connect underground service | Ottawa | Scheduled Outage | Preventive Maintenance
13705 | 2008 | 12 | 5 | 0.90972 |  | 21 | 2 | 8 | Beacon Hill | 8/4.8kV | 3F3 | Transformer #T261 located at 628 Clancy St isolated to make repairs (line side wires burnt up in meter base, crew sleeved in a new piece of wire) | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7701 | 2005 | 12 | 8 | 0.52014 |  | 113 | 47 | 25 | Beaconhill | 8/4.8kV | 3F3 | Isolation of transformers on 2112 Grafton to connect new primary cable. | Gloucester | Scheduled Outage | Preventive Maintenance
7705 | 2005 | 12 | 9 | 0.39792 |  | 142 | 47 | 20 | Beaconhill | 8/4.8kV | 3F3 | Isolation of transformers T32 (2100 Grafton) & T33(2146 Dutton) to reconnect new primary cable. | Gloucester | Scheduled Outage | Preventive Maintenance
7706 | 2005 | 12 | 9 | 0.51042 |  | 134 | 45 | 20 | Beaconhill | 8/4.8kV | 3F3 | Isolated transformers T34W(2158 Dutton) & T35W (768 Eastvale) for new primary cable replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
7751 | 2005 | 12 | 20 | 0.98611 |  | 26 | 6 | 13 | Beaconhill | 8/4.8kV | 3F3 | Doug McKay reports transformer # 2724 opened to all crews to replace bushing and repair underground service. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
20341 | 2012 | 4 | 17 | 0.36806 |  | 490 | 4614 | 565 | Beacon Hill | 8/4.8kV | 3F3 & 3F5 | At 08:50 overhead line sections on the 3F3 and 3F5 circuits were isolated to allow crews to repair a broken crossarms and remove porcelain switches. 511 customers were affected for 490 minutes. Beacon Hill (3F3 & 3F5) ID#20341 | Gloucester | Scheduled Outage | Repair
18083 | 2011 | 5 | 2 | 0.84375 |  | 2 | 75 | 2248 | Beacon Hill | 8/4.8kV | 3F3, 3F5 | 3F3 & 3F5 opened to remove tree limb across both cct's at rear of 2028 Quincy. | Gloucester | Tree Contacts | Tree Limb Fallen
9738 | 2006 | 11 | 27 | 0.47708 |  | 88 | 18 | 12 | Beacon Hill | 8/4.8kV | 3F3-3F5 | Greg Bell isolated trf. # 5749 @ 1994 Quincy for cable work | Gloucester | Scheduled Outage | Preventive Maintenance
19888 | 2012 | 1 | 24 | 0.71875 |  | 225 | 8 | 2 | Beaconhill | 8/4.8kV | 3F4 | TE2460 at 5310 Canotek was isolated to allow the crew to transfer riser cable to new pole and switches | Gloucester | Scheduled Outage | Construction
19889 | 2012 | 1 | 24 | 0.88194 |  | 230 | 54 | 14 | Beaconhill | 8/4.8kV | 3F4 | TE2327 at 5303 Canotek was isolated to allow the crew to transfer riser cable to new pole and switches | Gloucester | Scheduled Outage | Construction
3294 | 2003 | 3 | 23 | 0.03125 |  | 45 | 1 | 1 | Beaconhill | 8/4.8kV | 3F4 | Opened transformer feeding 1011 Canotek to replace cutout. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
8305 | 2006 | 5 | 16 | 0.54306 |  | 25 | 0 | 1 | Beaconhill | 8/4.8kV | 3F4 | G872RWB opened to replace defective hot line clamp at 5303 Canotek Road. 1 customer affected. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3607 | 2003 | 6 | 24 | 0.46528 |  | 67 | 35 | 31 | Beaconhill | 8/4.8kV | 3F4 | 5450 Canotek road repairs | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16822 | 2010 | 8 | 28 | 0.36806 |  | 450 | 15 | 2 | Beacon Hill | 8/4.8kV | 3F4 | at 8:50am, Transformer TE2055 at 5510 Cantoek was Isolated to allow crews to replacer transformer and clean up leaking oil. 2 customers affected for 450 minutes. Beacon hill (3F4) ID #16822 | Gloucester | Scheduled Outage
16975 | 2010 | 9 | 21 | 0.45278 |  | 158 | 480 | 364 | Beacon Hill MS | 8/4.8kV | 3F4 | S21787 at 1209 Rainbow St. was found blown. The cause was tree over growth making contact with the 3F3 O/H conductor. Power restored to 363 customers. 1 customer fed from transformer TE2067 remained out for an additional 79 minutes as crews had to replace an overhead switch. | Gloucester | Tree Contacts | Inadequate Trimming
15409 | 2009 | 11 | 22 | 0.29861 |  | 351 | 23 | 4 | Beaconhill |  | 3F4 | TE2330 @ 5315 Caotek Rd was isolated to allow the crews to transfer riser cables from pole # X17039 to new pole. | Gloucester | Scheduled Outage | Construction
6053 | 2004 | 12 | 12 | 0.23194 |  | 346 | 2255 | 391 | Beacon Hill | 8/4.8kV | 3F4 | Planned outage for installation of new poles and conductor at Beacon Hill DS. | Gloucester | Scheduled Outage | Preventive Maintenance
15622 | 2010 | 1 | 6 | 0.50625 |  | 404 | 657 | 194 | Beacon Hill | 8/4.8kV | 3F5 | Defective cable between T648 & T436 caused red phase fuse to blow at G109. Flagged FCI's indicated 12 of the 16 affected transformers could be restored at 8:04. The remaining sections were tested, sectionalized & restored at 10:40 to what we believed was all customers.Transformer fuse at T433 was later found to be blown, outage was expanded briefly to refuse T433 off potential and power was then restored to all customers. Affected customers were in the Eastvale / Loyola area of Beacon Hill. | Gloucester | Defective Equipment
6124 | 2005 | 1 | 7 | 0.41667 |  | 70 | 14 | 12 | Beacon Hill | 8/4.8kV | 3F5 | Transformer at the rear of 567 Eastvale Dr off to replace Pedestal | Gloucester | Scheduled Outage | Preventive Maintenance
7800 | 2006 | 1 | 12 | 0.43542 |  | 88 | 18 | 12 | BEACON HILL | 27.6/16kV | 3F5 | T160R OUT TO ALLOW CREW TO MAKE NEW TERMINATIONS ON FILLMOR CR. | Gloucester | Scheduled Outage | Construction
9930 | 2007 | 1 | 16 | 0.44306 |  | 5 | 1 | 8 | Beacon Hill | 8/4.8kV | 3F5 | Transformer TP3978 on Buchanan Cr in Gloucester isolated for cable replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
9933 | 2007 | 1 | 16 | 0.52083 |  | 69 | 10 | 9 | Beacon Hill | 8/4.8kV | 3F5 | Transformer TP3979 on Buchanan Cr in Gloucester isolated for cable replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
9943 | 2007 | 1 | 18 | 0.39236 |  | 100 | 17 | 10 | Beacon Hill | 8/4.8kV | 3F5 | At 09:25 trans #3980 at 509 Buchanan Cres was isolated in order to replace sec service | Gloucester | Scheduled Outage | Preventive Maintenance
7830 | 2006 | 1 | 20 | 0.40139 |  | 337 | 45 | 8 | BEACON HILL | 8/4.8kV | 3f5 | OUTAGE ON T140R TO NEW TERMINATIONS TO TRANSFORMER. | Gloucester | Scheduled Outage | Construction
7848 | 2006 | 1 | 24 | 0.5 |  | 110 | 22 | 12 | Beacon Hill | 8/4.8kV | 3F5 | transformer T62R out for cable replacement. | Gloucester | Scheduled Outage | Construction
7853 | 2006 | 1 | 25 | 0.41319 |  | 95 | 19 | 12 | Beacon Hill | 8/4.8kV | 3F5 | Transformer T145 on 2153 Blue Jay Cr isolated for cable replacment. (customers on Filmore & Blue Jay) | Gloucester | Scheduled Outage | Construction
7855 | 2006 | 1 | 25 | 0.53125 |  | 87 | 16 | 11 | Beacon Hill | 8/4.8kV | 3F5 | Transformer T146 on 2172 Blue Jay Cr isolated for cable replacment. (customers on Filmore & Blue Jay) | Gloucester | Scheduled Outage | Construction
7875 | 2006 | 2 | 1 | 0.42361 |  | 152 | 25 | 10 | Beacon Hill | 8/4.8kV | 3F5 | Transformers T58 & T59 in the Beacon Hill area isolated for cable replacement affecting 10 customers on Kender & Ingram. | Gloucester | Scheduled Outage | Construction
7879 | 2006 | 2 | 2 | 0.42361 |  | 170 | 57 | 20 | Beaconhill | 8/4.8kV | 3F5 | T56,T57 cable replacement in Beaconhill on Ingram St. Cable replacement complete | Gloucester | Scheduled Outage | Construction
10004 | 2007 | 2 | 8 | 0.63542 |  | 15 | 2 | 10 | Beaconhill | 8/4.8kV | 3F5 | Isolated transformer TP3348 at 2106 Dutton Cres to replace secondary connections on the service to 2106 (Live front transformer) | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
17580 | 2011 | 2 | 14 | 0.56667 |  | 174 | 23 | 8 | Beaconhill | 8/4.8kV | 3F5 | Broken insulator on live front transformer TE45 at the rear of 862 Eastvale Dr | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17583 | 2011 | 2 | 14 | 0.56667 |  | 174 | 23 | 8 | Beacon Hill | 8/4.8kV | 3F5 | Broken insulator found at TE45, 826 Eastvale, switching performed to restore power, permanent repairs to be made. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20027 | 2012 | 2 | 16 | 0.99167 |  | 42 | 35 | 50 | Beacon Hill |  | 3F5 | crews found defective arrester, repaired and refused. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17633 | 2011 | 2 | 22 | 0.375 |  | 102 | 14 | 8 | Beaconhill | 8/4.8kV | 3F5 | TE45 @ 824 Eastvale was isolated to replace defective insulators. | Gloucester | Scheduled Outage | Repair
17699 | 2011 | 3 | 11 | 0.25347 |  | 545 | 265 | 78 | Beaconhill | 8/4.8kV | 3F5 | G90 white phase blew. Sectionalized circuit and found T144 Flooded at 567 Eastvale. Crew installed portable sump pump next to transformer and customer power restored. | Gloucester | Adverse Environment | Flooding
12142 | 2008 | 3 | 15 | 0.34306 |  | 336 | 45 | 8 | Beacon Hill | 8/4.8kV | 3F5 | Overhead transformer at 2225 Fillmore, Beacon Hill was replaced by Oncall crew due to no secondary power output. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6361 | 2005 | 4 | 3 | 0.66667 |  | 183 | 131 | 43 | Beaconhill | 27.6/16kV | 3F5 | A faulted cable bet. Trans T178 & T179 @ 751 Stiles. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10246 | 2007 | 4 | 12 | 0.86806 |  | 40 | 7 | 11 | Beaconhill | 8/4.8kV | 3F5 | Transformer # GL5744 was opened to allow crew to replace connections @ 2451 Ogilvie Rd | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
17922 | 2011 | 4 | 13 | 0.39931 |  | 680 | 147 | 13 | Beaconhill | 8/4.8kV | 3F5 | Transformer TP3103 at 2455 Ogilive Rd. Was isolated to change leaking transformer. | Gloucester | Scheduled Outage
6440 | 2005 | 4 | 22 | 0.40972 |  | 79 | 17 | 13 |  | 8/4.8kV | 3F5 | Isolation of T179 on Stiles. Planned outage. | Gloucester | Scheduled Outage
6443 | 2005 | 4 | 22 | 0.52778 |  | 67 | 10 | 9 |  | 8/4.8kV | 3F5 | Scheduled outage on Stiles, | Gloucester | Scheduled Outage
17984 | 2011 | 4 | 22 | 0.34375 |  | 20 | 4 | 12 | BEACONHILL | 8/4.8kV | 3F5 | ISOLATED TRANSFORMER X16996 TO REPLACE CONNECTIONS ON THE SECONDARY BUSS | Gloucester | Scheduled Outage | Preventive Maintenance
14206 | 2009 | 4 | 23 | 0.67708 |  | 1 | 29 | 1769 | Beacon Hill | 8/4.8kV | 3F5 | 3F5 circuit load dumped from MUS supply & restored on new BHTT1 supply. | Gloucester | Scheduled Outage | Construction
20532 | 2012 | 5 | 17 | 0.45486 |  | 22 | 4 | 10 | Beacon Hill | 8/4.8kV | 3F5 | Transformer TE229 @ 2043 was isolated to allow the crews repair defective under ground service. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20539 | 2012 | 5 | 18 | 0.53472 |  | 66 | 228 | 207 | Beacon Hill | 8/4.8kV | 3F5 | at 12:50, Lightning arrestor at TEMP151 blew, causing G109 White phase to blown, Arrestor cut clear and G109 refused and holding | Gloucester | Defective Equipment
14395 | 2009 | 5 | 21 | 0.41667 |  | 218 | 33 | 9 | Beaconhill | 8/4.8kV | 3F5 | Crews isolated TP3094 in order to replace transformer as part of PCB replacement program. | Gloucester | Scheduled Outage | Preventive Maintenance
6589 | 2005 | 5 | 23 | 0.33681 |  | 243 | 397 | 100 | Beaconhill | 8/4.8kV | 3F5 | A cable fault bet transformer 60 and 61 on the B phase on Kender. The 4 fault indicator did not work making the restoration time longer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3514 | 2003 | 6 | 3 | 0.38542 |  | 30 | 5 | 10 | Beacon Hill | 8/4.8kV | 3F5 | Transformer isolated to repair a defective service. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
6670 | 2005 | 6 | 6 | 0.86458 |  | 45 | 9 | 12 | Beacon Hill | 8/4.8kV | 3F5 | Transfomer #GL005749 at 1990 Quincy Ave isolated to make repairs-found loose connections that are sparking | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12592 | 2008 | 6 | 10 | 0.77361 |  | 218 | 4276 | 1177 | Beacon Hill | 8/4.8kV | 3F5 | 3F5 breaker auto reclosed twice before locking out, two phase were wrapped around each other and trees in wires. | Gloucester | Adverse Weather
18384 | 2011 | 6 | 10 | 0.69236 |  | 440 | 5168 | 1772 | Beaconhill | 8/4.8kV | 3f5 | 3F3 opened due to paving company contacting the down guy on the corner ole and two wooden pins are broken, at Eastvale and Tisdale. 3F3 and 3F5 circuits run together, 3F3 tripped off at 16:45. On-call crew called in to make repairs. | Gloucester | Foreign Interference | Vehicle
3557 | 2003 | 6 | 12 | 0.46875 |  | 31 | 1 | 2 | Beacon Hill | 8/4.8kV | 3F5 | Planned outage to transformer 5656 on Bickerton Ave to relocate transformer supply. | Gloucester | Scheduled Outage | Construction
20762 | 2012 | 6 | 13 | 0.38264 |  | 184 | 37 | 12 | Beacon Hill | 8/4.8kV | 3F5 | TP3094 @ 2356 Oglivie Rd was isolated to allow cable crew to upgrade pedistal at the rear of 2360 Oglivie Rd. | Gloucester | Scheduled Outage | Preventive Maintenance
8496 | 2006 | 6 | 16 | 0.39583 |  | 12 | 2 | 9 | Beaconhill | 8/4.8kV | 3F5 | Transformer #GLTE0141 located at 2125 Fillmore isolated due to service upgrade | Gloucester | Scheduled Outage | Preventive Maintenance
6771 | 2005 | 6 | 21 | 0.45625 |  | 18 | 2 | 7 | Beacon Hill | 8/4.8kV | 3F5 | Transformer TE30 at 3558 Ogilvie Rd isolated for cable replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
6772 | 2005 | 6 | 21 | 0.52778 |  | 70 | 12 | 10 | Beacon Hill | 8/4.8kV | 3F5 | Transformer TE31 at 2112 Grafton isolated for cable replacement. | Gloucester | Scheduled Outage
5471 | 2004 | 7 | 8 | 0.61806 |  | 310 | 16 | 3 | Beaconhill | 8/4.8kV | 3F5 | Isolated transformer TE104 at 660 Glenhurst Crst to move pedestal | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16597 | 2010 | 7 | 31 | 0.84375 |  | 129 | 74 | 53 | Beacon Hill | 8/4.8kV | 3F5 | Cable fault between transformers TP3960 and TP3961 in Rivershore area caused switch S28758 fuses to blow. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5604 | 2004 | 8 | 2 | 0.81042 |  | 215 | 369 | 103 | Beacon Hill | 8/4.8kV | 3F5 | Blown elbow and insert at transformer TE49B had to be replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14939 | 2009 | 8 | 12 | 0.79236 |  | 102 | 170 | 100 | Beacon Hill | 8/4.8kV | 3F5 | Due to incorrect fuse size, G109 White pahse tripped on overload. Fuse re-fused at 140A. Affecting customers on Montreal Rd, Loyola Ave, Ogilvie Rd, and Eastvale Dr | Gloucester | Human Element | Incorrect Protection Settings
16724 | 2010 | 8 | 12 | 0.69861 |  | 445 | 3223 | 1771 | Beacon Hill | 8.32 | 3F5 | Defective T428 caused G109 white phase to blow & break which also caused 3F5 breaker at Beacon Hill station to trip. | Nepean | Defective Equipment
3898 | 2003 | 8 | 13 | 0.43056 |  | 15 | 3 | 12 | Beaconhill | 27.6/16kV | 3F5 | Transformer was isolated to disconnect a home at 2145 Monson cres. Customer had a deffective panal. Service was disconnected to repair panel. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
3899 | 2003 | 8 | 13 | 0.55556 |  | 36 | 7 | 12 | Beaconhill | 27.6/16kV | 3F5 | D. Provost isolated TE154 to reconnect a customer sevice at 2145 Monson after panel was replaced. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
16742 | 2010 | 8 | 16 | 0.20347 |  | 46 | 652 | 850 | Beacon Hill | 8/4.8kV | 3F5 | 3F5 breaker at Beaconhill found opened. Circuit breaker closed at station all load restored. | Gloucester | Lightning | Direct Strike
9265 | 2006 | 9 | 21 | 0.52083 |  | 33 | 4 | 8 | Beacon Hill | 8/4.8kV | 3F5 | Transformer #GLTE0321 located at 618 Gaines isolated to repair secondary service | Gloucester | Scheduled Outage | Repair
4172 | 2003 | 9 | 28 | 0.77431 |  | 211 | 317 | 153 | BeaconHill | 8/4.8kV | 3F5 | Defective undergroud cable section Tx44 byTX45 on Eastvale. G7 red phase fuse and G15 Red phase fuse had both blown. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4238 | 2003 | 10 | 10 | 0.44028 |  | 80 | 27 | 20 | Beaconhill | 8/4.8kV | 3F5 | R. Barnett reports all repairs are now completed to cable section between T44 & T45. | Gloucester | Scheduled Outage | Construction
9458 | 2006 | 10 | 18 | 0.41597 |  | 66 | 11 | 10 | Beaconhill | 8/4.8kV | 3F5 | Isolated transformer TP3893 @ DeSalaberry to reconnect new cables. | Gloucester | Scheduled Outage | Preventive Maintenance
9469 | 2006 | 10 | 19 | 0.5125 |  | 101 | 20 | 12 | Beaconhill | 8/4.8kV | 3F5 | Transformer TP3892 on De Salaberry was isolated to allow the crew to reconnect new cables under the cable replacement program. | Gloucester | Scheduled Outage | Preventive Maintenance
19427 | 2011 | 10 | 20 | 0.35764 |  | 60 | 50 | 50 | Beaconhill | 8/4.8kV | 3F5 | A burnt switch G44B @ 655 Sefford Rd caused the outage to four transformers. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9505 | 2006 | 10 | 24 | 0.44167 |  | 109 | 18 | 10 | Beaconhill | 27.6/16kV | 3F5 | TP3347 was isolated for transformer replacement on Ingram Street. | Gloucester | Scheduled Outage | Preventive Maintenance
9512 | 2006 | 10 | 25 | 0.57431 |  | 25 | 5 | 11 | Beacon Hill | 8/4.8kV | 3F5 | Transformer TE483 located at 2166 Loyola isolated for service repair. PC10A#38. | Gloucester | Defective Equipment
19494 | 2011 | 10 | 29 | 0.40625 |  | 5 | 1 | 11 | Beaconhill | 8/4.8kV | 3F5 | Isolated transformer X20814 at 2050 Kings Grove Cres to replace blown seconday fuse feeding Rogers power surply | Gloucester | Scheduled Outage | Emergency Services Request
9555 | 2006 | 10 | 30 | 0.40139 |  | 40 | 7 | 10 | Beaconhill | 8/4.8kV | 3F5 | Isolated transformer TP3891 near Ranford Crt in Beaconhill to reconfigure the cables. | Gloucester | Scheduled Outage | Preventive Maintenance
7573 | 2005 | 11 | 6 | 0.86806 |  | 64 | 1255 | 1177 | Beaconhill | 8/4.8kV | 3F5 | M. Byers reports tree branch removed from overhead circuit All power restored. | Gloucester | Tree Contacts | Tree Limb Fallen
19541 | 2011 | 11 | 7 | 0.58681 |  | 237 | 758 | 400 | Beaconhill | 8/4.8kV | 3F5 | Cable fault on Red and White phases between T440 to T155 and T439 to T155. During fault finding the 3F3 breaker tripped. | Gloucester | Defective Equipment
9633 | 2006 | 11 | 10 | 0.42153 |  | 90 | 27 | 18 | Beacon Hill | 8/4.8kV | 3F5 | TP3972 and TP3966 transformer and cablle replacement Buchanan Cres Beaconhill | Gloucester | Scheduled Outage | Construction
9636 | 2006 | 11 | 10 | 0.55417 |  | 50 | 7 | 8 | Beacon Hill | 8/4.8kV | 3F5 | AT 13:18 trans GL5747 at 2014 Quincy Ave was isolated in order to transfer plant to new pole | Gloucester | Scheduled Outage | Preventive Maintenance
5882 | 2004 | 11 | 13 | 0.72222 |  | 120 | 160 | 80 | Beaconhill | 8/4.8kV | 3F5 | Broken switch at G142R at 2012 Quincy. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7661 | 2005 | 11 | 28 | 0.58889 |  | 78 | 13 | 10 |  | 27.6/16kV | 3F5 | Planned outage to T50R (TP3083) on Eastvale Drive, to connect new cables for cable replacement program. | Gloucester | Scheduled Outage
7692 | 2005 | 12 | 6 | 0.41667 |  | 125 | 63 | 30 | Beaconhill | 8/4.8kV | 3F5 | C. Donaldson reports blue phase cable replaced between T51B & T52B on 3F5 circuit. In the Dutton Cres area. | Gloucester | Scheduled Outage | Construction
7694 | 2005 | 12 | 6 | 0.56597 |  | 90 | 45 | 30 | Beaconhill | 8/4.8kV | 3F5 | Blue phase cable section between T58 & T61 to allow crews to replace cables. | Gloucester | Scheduled Outage | Construction
5990 | 2004 | 12 | 7 | 0.97222 |  | 70 | 21 | 18 |  | 27.6/16kV | 3F5 | Defective Pedestal at 741 Stiles, opened Transformer 180 while repairs made. | Gloucester | Defective Equipment
7698 | 2005 | 12 | 7 | 0.42361 |  | 135 | 81 | 36 | Beaconhill | 27.6/16kV | 3f5 | blue phase cable and elbow replacment on Dutton St. in Gloucester | Gloucester | Scheduled Outage | Preventive Maintenance
9818 | 2006 | 12 | 9 | 0.52083 |  | 59 | 22 | 29 | Beaconhill | 27.6/16kV | 3f5 | A customer @ 2101 Kender reports transformer in his backyard is smoking. 24/7 reports transformer has been isolated to replace transformer. TP3348 was found to have a broken primary bushing & breaken fibre board. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9819 | 2006 | 12 | 9 | 0.52083 |  | 345 | 121 | 29 | Beaconhill | 8/4.8kV | 3F5 | M. Byers reports primary bushing has cracked. Oncall crew to replace bushing in TP3348. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7722 | 2005 | 12 | 14 | 0.43056 |  | 99 | 41 | 25 | Beaconhill | 27.6/16kV | 3f5 | On going cable replacement program in Beaconhill. 3 transformers affected. | Gloucester | Scheduled Outage
4603 | 2003 | 12 | 15 | 0.50833 |  | 468 | 580 | 146 | Beaconhill | 27.6/16kV | 3F5 | 3F5 circuit auto reclosed. The cause of the autoreclose also ruptured switches G7B and G14B. G7B was re-fused and closed and due to crews thinking that the cause was the same as the earlier outage and that they were coming up to a shift change they headed back to the shop feeling that all the power had been restored. It was later found out that customers off of G14B were still without power. The outage cause was found to be a baffle board in transformer TE56 had come into contact with primary voltage and had burnt a hole in the top of the transformer. The transformer was isolated and repairs were made. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4604 | 2003 | 12 | 15 | 0.076389 |  | 100 | 243 | 146 | Beaconhill | 27.6/16kV | 3F5 | 3F5 circuit auto reclosed at 01:50. Received a call from Radford area report power outage. Crews reports G101B phase arrester found blown clear. G7B fuse replaced and closed restoring power to 175 customers. R. Blair patrolled overhead along Casey. No other problem found. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7762 | 2005 | 12 | 25 | 0.15069 |  | 61 | 1197 | 1177 | Beaconhill | 8/4.8kV | 3F5 | Auto reclose on the 3F3 and lockout on the 3F5. All fault indicator flagged to the end of the line, but nothing found. | Gloucester | Unknown/Other
14062 | 2009 | 3 | 15 | 0.73264 |  | 1 | 29 | 1769 | Beacon Hill | 8/4.8kV | 3F5, 3F9 | Beacon Hill 3F5 & 3F9 load was interrupted to transfer load to temp substation supply. | Gloucester | Scheduled Outage | Construction
15641 | 2010 | 1 | 12 | 0.40347 |  | 103 | 34 | 20 | Beacon Hill | 8/4.8kV | 3F8 | Transformer T457W & T458W on Beaverhill were isolated to all ow crews to locate faulted service to 2021 Beaverhill Dr. | Gloucester | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
10021 | 2007 | 2 | 13 | 0.26181 |  | 242 | 4064 | 1135 | Beaconhill | 8/4.8kV | 3F8 | G191 switch was found broken & wires were down at the corner of Montreal & Ogilvie Rd. 24/7 crew isolated overhead section on 3F8 circuit. Approx 500 customers were restored at 08:21. The remaining customers were restored when repairs were made to the overhead circuit. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10023 | 2007 | 2 | 13 | 0.625 |  | 49 | 61 | 75 | Beaconhill | 8/4.8kV | 3F8 | G331 white phase fuse found opened. Steve reports switch also needs to be replaced. G331 replaced and all power restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17582 | 2011 | 2 | 14 | 0.63542 |  | 225 | 108 | 52 | Beacon Hill | 8/4.8kV | 3F8 | The B phase of 3F8 came down at Blair & Ogilvie causing an outage to 42 customers in the Bathgate / Ogilvie area, theses customers were restored from alternate supply. A single O/H Tx X16845 at 2011 Ogilvie was in the area isolated for repair & was also transferred to alternate supply. (dual voltage transformer removed from 3F8 to 8F4 supply) | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20153 | 2012 | 3 | 12 | 0.53264 |  | 28 | 381 | 815 | Beaconhill | 8/4.8kV | 3F8 | While trying to backfeed customer interupted on the 6F10 white phase circuit tripped out due to a defective underground cable. 815 customer affected for a total 28 mins. Beaconhill 3F8 ID# 20153 | Gloucester | Defective Equipment
14050 | 2009 | 3 | 14 | 0.12014 |  | 6 | 20 | 200 | Beacon Hill | 8/4.8kV | 3F8 | Juggling load between 6F10 and 4F1 for Beacon Hill load, outages opted to prevent parrallels | Gloucester | Scheduled Outage | Load Shedding
14051 | 2009 | 3 | 14 | 0.14792 |  | 6 | 22 | 221 | Beacon Hill | 8/4.8kV | 3F8 | Juggling load between 6F10 and 4F1 for Beacon Hill load, outages opted to prevent parrallels | Gloucester | Scheduled Outage | Load Shedding
20236 | 2012 | 3 | 26 | 0.43472 |  | 234 | 448 | 115 | Beacon Hill | 8/4.8kV | 3F8 | Hydro Ottawa crews isolated transformers TP9362, TP9363 & TP9364 to allow for the repair of defeciencies found during the NRC cable testing. | Gloucester | Scheduled Outage | Repair
5090 | 2004 | 5 | 3 | 0.16806 |  | 68 | 1286 | 1135 | Beacon Hill | 8/4.8kV | 3F8 | 3F8 opened at the request of crews due to switch burning G67rwb Montreal and Ogilvie breaker was opened by scada but could not be closed crew was sent to the station and Bypassed recloser | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
6571 | 2005 | 5 | 18 | 0.55764 |  | 74 | 12 | 10 |  | 27.6/16kV | 3f8 | Scheduled outage to replace noisy transformer T546R, on Marquis St. | Gloucester | Scheduled Outage
8398 | 2006 | 6 | 1 | 0.36806 |  | 19 | 4 | 14 | Beacon Hill | 8/4.8kV | 3F8 | Mark Rushton opened trans# GLTE0331 @ 1037 Bourget for service upgrade | Gloucester | Scheduled Outage | Preventive Maintenance
8401 | 2006 | 6 | 1 | 0.53472 |  | 15 | 4 | 14 | Beacon Hill | 8/4.8kV | 3F8 | Transformer # GLTE0331 located at 1037 Bourget isolated to reconnect service | Gloucester | Scheduled Outage | Construction
16205 | 2010 | 6 | 6 | 0.27014 |  | 224 | 37 | 10 | BeaconHill | 8/4.8kV | 3F8 | Outage cause by deffective cable between S16193 and transformer TP3613B @ 1870 Appleford. | Gloucester | Defective Equipment
12611 | 2008 | 6 | 12 | 0.42361 |  | 235 | 39 | 10 | Beacon Hill | 8/4.8kV | 3F8 | TE202 at 1870 Appleford was isolated to replace tranaformer & switches at dip pole. | Gloucester | Scheduled Outage | Repair
6741 | 2005 | 6 | 15 | 0.92153 |  | 173 | 283 | 98 | Beaconhill | 8/4.8kV | 3F8 | G331R phase found blown two transformers checked for fault inducator nothing found ,first cable hipotted okay. Fuse installed ans holding. Mulberry Ave, Marquis Ave BeaconHill. | Gloucester | Unknown/Other | No Apparent Cause
3604 | 2003 | 6 | 24 | 0.22917 |  | 250 | 38 | 9 | Beaconhill | 8/4.8kV | 3F8 | Auto reclose of 3F8 at 03:09. First customer call at 05:30. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
16328 | 2010 | 6 | 25 | 0.7375 |  | 48 | 65 | 81 | Beaconhill | 8/4.8kV | 3F8 | defective G905 White phase switch caused interruption to customers on Bathgate dr. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
3697 | 2003 | 7 | 8 | 0.54167 |  | 155 | 16 | 6 | Beaconhill | 8/4.8kV | 3F8 | Transformer TE323 was isolated to allow for the re-routing of primary U/G cable. | Gloucester | Scheduled Outage | Construction
12997 | 2008 | 8 | 4 | 0.35764 |  | 79 | 1885 | 1506 | Beaconhill DS | 8/4.8kV | 3F8 | A squirrel contacted the 3F8 recloser to trip and blow the busings off, as well as cause the insulators to Flash on the 3F4 recloser and blow two fuses on the 3T2 transformer at Beaconhill. 24/7 crew isolated damaged equipment and performed switching to restore power. | Gloucester | Foreign Interference | Animal
13029 | 2008 | 8 | 9 | 0.34583 |  | 77 | 13 | 10 | Beacon Hill | 8/4.8kV | 3F8 | S26277B feeding transformer TP3613B at 1075 Cloverlawn found open due to cable fault between S16193 N.O. and TP3613B. Single transformer loop. Crew isolated cable section and restored all power. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
18945 | 2011 | 8 | 16 | 0.50347 |  | 10 | 135 | 812 | Beacon Hill | 8/4.8kV | 3F8 | 3F8 interupter opened for no apparent reason, interupter closed at station, Circuit patroled nothing found. | Gloucester | Unknown/Other | No Apparent Cause
11153 | 2007 | 8 | 24 | 0.41181 |  | 262 | 245 | 56 | Beacon Hill | 8/4.8kV | 3F8 | Switch 905R opened due to faulted cable bewteen vault V24 and transformer T351R on Bathgate in Gloucester. Cable isolated and customers restored. | Gloucester | Defective Equipment
9258 | 2006 | 9 | 21 | 0.084722 |  | 284 | 464 | 98 | Beacon Hill | 8/4.8kV | 3F8 | G311R phase opened crews hi potted cbls and found that they hi potted good. G311R closed and holding. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9262 | 2006 | 9 | 21 | 0.45417 |  | 319 | 482 | 98 | Beacon Hill | 8/4.8kV | 3F8 | G331R reopened. 24/7 reports that FCI @ T509 saw fault. After sectionalizing crew found bad cbl between T508 and T546. Cable isolated and all load picked up. | Gloucester | Defective Equipment
13633 | 2008 | 11 | 17 | 0.80764 |  | 133 | 162 | 73 | Beaconhill | 8/4.8kV | 3F8 | Blown termination at G1003 White phase at 1170 Foxborough, crew isolated and picked up customers from alternate source. | Gloucester | Defective Equipment
13642 | 2008 | 11 | 20 | 0.45486 |  | 25 | 5 | 13 | Beaconhill | 4.16kV | 3F8 | At 10:55 trans at 1437 Matheson Rd was isolated in order for a service upgrade | Gloucester | Scheduled Outage | Repair
19693 | 2011 | 12 | 6 | 0.42014 |  | 215 | 150 | 42 | Blackburn MS | 8/4.8kV | 3F8 | Blue phase cable section between S15440B & TP8545 was isolated to allow Hydro Ottawa crews to replace cables, elbows & inserts. | Gloucester | Scheduled Outage | Construction
17429 | 2010 | 12 | 16 | 0.875 |  | 255 | 4 | 1 | Beacon Hill | 8/4.8kV | 3F8 | crews found blown fuse on a single phase feeding VE38 at 1425 Ogilvie. 1 customer affected for 255 minutes. Beacon Hill (3F8) | Gloucester | Defective Equipment
14027 | 2009 | 3 | 8 | 0.020139 |  | 438 | 4300 | 589 | Beacon Hill | 8/4.8kV | 3F9 | 3F9 circuit was isolated as part of a schedualled outage to Beacon Hill sub station to allow crews to replace 44kV structure at Montreal & Shefford, and to allow Station's crew to perform sub station maintenance. | Gloucester | Scheduled Outage | Preventive Maintenance
14156 | 2009 | 4 | 8 | 0.73542 |  | 6 | 2 | 16 | Beaconhill | 8/4.8kV | 3F9 | Transformer #433 located at 2166 Loyola Ave isolated to reconnect service after defective U/G serv repaired | Gloucester | Scheduled Outage | Repair
14396 | 2009 | 5 | 21 | 0.79167 |  | 192 | 575 | 189 | Beacon Hill |  | 3F9 | 3F9 cable fault on cable section TEMP155 by T441. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5209 | 2004 | 5 | 26 | 0.42569 |  | 77 | 13 | 10 | Moulton | 27.6/16kV | 3F9 | TE653 at 2111 Montreal RD to replace defective transformer | Gloucester | Scheduled Outage | Repair
5312 | 2004 | 6 | 15 | 0.38542 |  | 71 | 19 | 16 | BEACON HILL | 8/4.8kV | 3F9 | TE445 ISOLATED TO REPLACE DEFECTIVE METERS | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
5313 | 2004 | 6 | 15 | 0.44653 |  | 65 | 14 | 13 | 3F9 | 8/4.8kV | 3F9 | TE443 ISOLATED TO CYANGE DEFECTIVE METERS | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
9836 | 2006 | 12 | 14 | 0.40278 |  | 387 | 13 | 2 | King Edward TK | 13.2kV | 401 | VT436 & VT437 at Guiges & Rose were isolated for planned asbestos removal. | Ottawa | Scheduled Outage | Preventive Maintenance
12183 | 2008 | 3 | 27 | 0.99306 |  | 75 | 4 | 3 | King Edward | 13.2kV | 401, 403 | At 11:50pm SCADA indicates TK13 circuit breaker has opened. 24-7 crews dispatched to sectionalize and restore power. 24-7 crews and system restore power and isolated 403 & 401 cable section from Station to VT32 & VT128. 2 customers affected and power restored at 1:05am. ID#12183 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19931 | 2012 | 1 | 31 | 0.375 |  | 163 | 149 | 55 | King Edward | 13.2kV | 403 | The 13kV transformer bus at VT462, 181 Bruyere was isolated to allow an electrician to install micro fit equipment in the customer secondary room. No work took place in the vault. | Ottawa | Scheduled Outage | Construction
18215 | 2011 | 5 | 25 | 0.40278 |  | 140 | 128 | 55 | King Edward | 13.2kV | 404 | Vault VT462 @ 181 Bruyere was isolated to allow contractor to perform vault maintenance and Asbestos removal. 55 customers were affected. King Edward (404) | Ottawa | Scheduled Outage
15668 | 2010 | 1 | 19 | 0.175 |  | 80 | 17 | 13 | King Edward | 13.2kV | 405 | TK11 breaker opened interrupting power to 13 vaults on the 405 circuit in the downtown area of Rideau, St. Patrick and Wilbrod. Fault was sectionalized to cable section between station & first vault, all load was then restored from alternate source. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6051 | 2004 | 12 | 11 | 0.82917 |  | 311 | 5 | 1 | King Edward | 13.2kV | 405 | Water leaking from ceiling in vault caused two insulators to flash over and the vault supply to open. Contractor cut insultors out since they were at the dead end. ESA approved and vault was re-energized. Future shutdown will be arranged to replace insulators. | Ottawa | Adverse Environment | Flooding
7907 | 2006 | 2 | 12 | 0.67708 |  | 1 | 0 | 5 | King Edward | 13.2kV | 408 | When opening cell door to rack out TK20 for planned outage, adjacent breaker TK22 tripped. | Ottawa | Human Element | Incorrect Protection Settings
19372 | 2011 | 10 | 14 | 0.23889 |  | 118 | 979 | 498 | King Edward | 13.2kV | 408 | Cable fault at Man hole # 377. Cable crew to determine cause. Cable section isolated. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14121 | 2009 | 3 | 31 | 0.95764 |  | 139 | 40 | 20 | King Edward | 13.2kV | 409 | TK09 breaker tripped for a 409 cable fault interrupting power to 20 - 13 kv vaults in the Rideau, King Edward, George, Dalhousie area. The cable section between VT703 & VT404 on King Edward was isolated and power restored to the 20 vaults. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10925 | 2007 | 7 | 22 | 0.052083 |  | 319 | 11 | 2 | King Edward | 13.2kV | 409 | Isolated VT458 and VT721 at 73 Rideau to allow the contractor to remove asbestos from the cables. | Ottawa | Scheduled Outage | Preventive Maintenance
18933 | 2011 | 8 | 15 | 0.019444 |  | 89 | 13 | 9 | King Edward | 13.2kV | 409 | VT339 at 130 George was isolated to allow the customer's contractor to perform standard vault maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
4209 | 2003 | 10 | 5 | 0.16319 |  | 255 | 132 | 31 | King Edward | 13.2kV | 409 | 13 kv vault VT458 at 73 Rideau isolated for Hydro Ottawa to perform routine maintenance & protect from leaking ceiling. | Ottawa | Scheduled Outage | Preventive Maintenance
19763 | 2011 | 12 | 27 | 0.5 |  | 342 | 285 | 50 | King Edward |  | 409 | VT808 at 145 York a 13kv distribution vault was found to be flooded by a broken water main and required isolation to safely remove the water. | Ottawa | Adverse Environment | Flooding
10290 | 2007 | 4 | 20 | 0.70833 |  | 196 | 4 | 2 | King Edward | 13.2kV | 412 | Blown pothead on the white phase of S241 at VT1454, at 275 Rideau caused TK12 to trip. | Ottawa | Unknown/Other | Preventive Maintenance
14955 | 2009 | 8 | 17 | 0.73889 |  | 3865 | 78 | 6 | King Edward | 13.2kV | 412 | Circuit 412 tripped due to defective 13kv Vault at VT1454, 275 Rideau blowing up. | Ottawa | Defective Equipment
11017 | 2007 | 8 | 9 | 0.083333 |  | 570 | 10 | 1 | King Edward | 13.2kV | 413 | A blown transformer in the vault VT865 @ 361 Rideau | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7982 | 2006 | 3 | 3 | 0.91667 |  | 420 | 42 | 6 | King Edward | 600/347 | 414 | HH1839 reported sparking and smoking by F/D, isolated 600V feed 852-160 from VT852 for repair | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19383 | 2011 | 10 | 16 | 0.10903 |  | 155 | 26 | 10 | King Edward TK | 13.2kV | 415 | VT475 at 45 Clarence isolated for customer vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
4512 | 2003 | 11 | 25 | 0.51736 |  | 153 | 73 | 71 | King Edward | 13.2kV | 415 | Back Hoe from Tesc Contracting brok into a cable duct and damaged the cable in question at Sussex west side and south of St Andrew. | Ottawa | Foreign Interference | Dig-in
4513 | 2003 | 11 | 25 | 0.55556 |  | 1 | 0 | 1 | King Edward | 13.2kV | 416 | Cable fault was determined to be on the wrong section of 415 cable and was inadvertantly energized through VT575 on 416 cable. | Ottawa | Human Element | Switching Errors
20226 | 2012 | 3 | 26 | 0.19306 |  | 6 | 5 | 50 | Hinchey | 13.2kV | 4301 | TH04 tripped when a broken insulator on adjacent cct (TH11) caused a flash. | Ottawa | Defective Equipment
17903 | 2011 | 4 | 11 | 0.74653 |  | 116 | 93 | 48 | Hinchey | 13.2kV | 4301 | TH11 phase down, and broken insulator caused 4301 circuit to open. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8282 | 2006 | 5 | 12 | 0.20556 |  | 221 | 9 | 3 | Hinchey | 13.2kV | 4301 | Vehicle accident broke 2 poles off on Scott west of Bayview. Poles are also carrying 4303 and TH11 lines, not interupted. | Ottawa | Foreign Interference | Vehicle
8523 | 2006 | 6 | 19 | 0.79028 |  | 18 | 2 | 7 | Hinchey | 13.2kV | 4301 | Lightning storm in area. TH04 was carrying 4303 as well due to Hinchey Q bus outage. Also TH12 breaker tripped at the same time which was carrying TH01 & TH11 thru the 00. Breaker closed manually from SCADA. | Ottawa | Lightning
16643 | 2010 | 8 | 4 | 0.65556 |  | 248 | 198 | 48 | Hinchey | 13.2kV | 4301 | The 4301 O/H at Scott and Bayview conductor fell into the TH11 circuit | Ottawa | Adverse Weather | Wind
19073 | 2011 | 9 | 2 | 0.2875 |  | 74 | 59 | 48 | HINCHEY | 13.2kV | 4301 | Squirell caused a flash at the pole pothead to 175 Loretta, and brunt terminations. | Ottawa | Foreign Interference | Animal
13445 | 2008 | 10 | 29 | 0.053472 |  | 268 | 3216 | 720 | Hinchey | 13.2kV | 4301 | neutral down bet the 4301 and 4303 phases at Scott and Parkdale | Ottawa | Adverse Weather | Wind
11833 | 2007 | 12 | 12 | 0.35 |  | 161 | 3 | 1 | Hinchey | 13.2kV | 4301 | At 8:24am VT848 Lemieux Island reported loss of supply due to switching error, 1 customer affected for 161 min. ID#11833. | Ottawa | Human Element | Switching Errors
5767 | 2004 | 9 | 2 | 0.70625 |  | 63 | 1 | 1 | Hinchey | 13.2kV | 4302 | Squirrel contact caused flashover of 13 kv metering pots in VT323 at the Jean Talon Bldg, Tunney's Park. Power was restored to half of the vault at 18:00. All power was restored by Public Works from alternate sources. Hydro Ottawa Stations crew repaired pots overnight with a followup by Metering Dept the next day. | Ottawa | Foreign Interference | Animal
9989 | 2007 | 2 | 5 | 0.53542 |  | 64 | 4 | 4 | Hinchey | 13.2kV | 4303 | Hinchey cct 4303 auto trip when a contractor contacted cable while sample drilling. | Ottawa | Foreign Interference | Dig-in
20227 | 2012 | 3 | 26 | 0.175 |  | 25 | 75 | 181 | Hinchey | 13.2kV | 4303 | TH03 tripped when a broken insulator on adjacent cct (TH11) caused a flash. | Ottawa | Defective Equipment
17905 | 2011 | 4 | 11 | 0.74653 |  | 116 | 350 | 181 | Hinchey | 13.2kV | 4303 | TH11 phase down, and broken insulator caused 4303 circuit to open. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
13446 | 2008 | 10 | 29 | 0.053472 |  | 268 | 22 | 5 | Hinchey | 13.2kV | 4303 | neutral down bet the 4301 and 4303 phases at Scott and Parkdale | Ottawa | Adverse Weather | Wind
4598 | 2003 | 12 | 13 | 0.35 |  | 122 | 43 | 21 | Hinchey | 13.2kV | 4303 | VT579 was isolated for standard vault maintenance at 1010 Somerset, ID #4598 | Ottawa | Scheduled Outage | Preventive Maintenance
20469 | 2012 | 5 | 7 | 0.40972 |  | 79 | 47 | 37 | Hinchy | 13.2kV | 4304 | TH02 breaker tripped affecting Tunney pasture, Hollands cross & SW167. Tunneys pastures restored via TH05, then TH1SH-L3 at VT653 openned and breaker closed to test cable (held), TH1sh-L5 openned and breaker closed to energized VT653 and test cable between VT653 & SM167 (held). TH02 OPEN, dropping Hollands cross and TH1SH-L5 at Sw167 closed then energized and all load restored from TH02 breaker. | Ottawa | Unknown/Other
20554 | 2012 | 5 | 22 | 0.44306 |  | 96 | 58 | 37 | Hinchey | 13.2kV | 4304 | TH02 CB opened due to cable fault on 4304/TH1SH between TH and VT45 (Tunny's). | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20095 | 2012 | 3 | 3 | 0.34167 |  | 135 | 490 | 318 | Munster | 8/4.8kV | 43F2 | Munster 43F2 W & B tripped due to tree contact at rear of 32 Dogwood. Circuit closed via scada & tripped a second time after 6 min. R phase opened at request of crew to clear tree of o/h line. | Goulburn | Adverse Weather | Wind
12128 | 2008 | 3 | 11 | 0.80903 |  | 85 | 1 | 1 | Munster | 8/4.8kV | 43F2 | Transformer #X12454 located at 7732 Soldier's Line Goubourn isolated-they had to replace the cutout | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
4916 | 2004 | 3 | 18 | 0.41667 |  | 45 | 3 | 4 | Munster | 8/4.8kV | 43F2 | Transformer 8359 at 5 Butterfield isolated to change arresters. | Goulburn | Scheduled Outage | Preventive Maintenance
4918 | 2004 | 3 | 18 | 0.54167 |  | 33 | 3 | 5 | Munster | 8/4.8kV | 43F2 | Transformer 8093 at 18 Butterfield isolated to change arresters. | Goulburn | Scheduled Outage
4919 | 2004 | 3 | 18 | 0.41667 |  | 45 | 3 | 4 | Munster | 8/4.8kV | 43F2 | Transformer 8359 at 5 Butterfield isolated to change arresters. | Goulburn | Scheduled Outage | Preventive Maintenance
8056 | 2006 | 3 | 23 | 0.53472 |  | 55 | 2 | 2 | Munster | 8/4.8kV | 43F2 | Transformer located at 8775 Franktown isolated to make repairs to the service | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
8145 | 2006 | 4 | 13 | 0.25347 |  | 135 | 68 | 30 | Munster | 12/7.2kV | 43F2 | Tree fell on the line at Dwyer Hill Rd and Jocktrail Rd causing the red phase at Local / Reclosure GR884 to open | Goulburn | Tree Contacts | Tree Fallen
17945 | 2011 | 4 | 16 | 0.64236 |  | 3 | 16 | 315 | Munster | 8/4.8kV | 43F2 | Planned interruption to customers in the Bleeks and Munster Rd. area due to out of phase condition. | Goulburn | Scheduled Outage
17950 | 2011 | 4 | 17 | 0.62361 |  | 3 | 16 | 315 | Munster | 8/4.8kV | 43F2 | Planned interruption to customers in the Franktown and Munster Rd. area due to out of phase condition | Goulburn | Scheduled Outage
10312 | 2007 | 4 | 23 | 0.95833 |  | 98 | 588 | 360 | Munster | 8/4.8kV | 43F2 | While attempting to transfer Munster 43F2 load to Black's Corners supply, an outage occurred when it was found that an overhead line section at Franktown & Dwyer Hill was not connected as shown on system board. | Goulburn | Human Element | Incorrect Records
20464 | 2012 | 5 | 4 | 0.60417 |  | 15 | 2 | 7 | Munster DS | 8/4.8kV | 43F2 | Transformer X35243 at 50 Owlshead Rd isolated to allow for repairs to the u/g service at 40 Owlshead. | Goulburn | Scheduled Outage | Repair
12429 | 2008 | 5 | 12 | 0.39583 |  | 210 | 7 | 2 | Beckwith | 8/4.8kV | 43F2 | Transformer at 7904 Franktown Rd isolated to allow for transformer replacement | Goulburn | Scheduled Outage | Preventive Maintenance
14345 | 2009 | 5 | 12 | 0.38194 |  | 40 | 10 | 15 | Munster | 8/4.8kV | 43F2 | The W & B phase O/H was isolated on Franktown Rd bet Dwyerhill and Ashton Rd to allow crews to install new poles. | Goulburn | Scheduled Outage | Construction
12443 | 2008 | 5 | 15 | 0.40625 |  | 90 | 15 | 10 | MUNSTER DS | 8/4.8kV | 43F2 | Transformer #X36038 removed | Goulburn | Scheduled Outage | Construction
6573 | 2005 | 5 | 19 | 0.39583 |  | 1 | 0 | 10 | Munster | 8/4.8kV | 43F2 | L. Lauzon reports while restoring R/C 884 white phase reclosure opened. Reclosure was reclosed ,restoring all power. Approx 10 customers effected in power outage. In the Franktown & Wood's Rd area. | Kanata | Human Element | Switching Errors
5202 | 2004 | 5 | 24 | 0.38542 |  | 75 | 1 | 1 | Munster | 8/4.8kV | 43F2 | Transfomer 7671 ar 7675 Soldiers Lane out to replace a broken awitch. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
6597 | 2005 | 5 | 24 | 0.64097 |  | 1 | 2 | 120 | Munster | 8/4.8kV | 43F2 | While restoring 43F2 white phase recloser to normal the recloser opened. 31 amps . | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
20566 | 2012 | 5 | 24 | 0.45278 |  | 6 | 1 | 6 | Munster | 8/4.8kV | 43F2 | Transformer #X33334 located at 33 Owlshead Rd opened by crew for electrician to repair customer owned connection. | Goulburn | Scheduled Outage | Repair
14468 | 2009 | 6 | 5 | 0.41319 |  | 10 | 0 | 2 | Munster | 8/4.8kV | 43F2 | Isolated transformer X09017 at 8472 Franktown Rd to move from one phase to another phase | Goulburn | Scheduled Outage | Construction
12580 | 2008 | 6 | 9 | 0.40278 |  | 148 | 10 | 4 | Munster DS | 8/4.8kV | 43F2 | Transformer at 8410 Franktown Rd isolated to change CT & wiring for meter dept. | Goulburn | Scheduled Outage | Construction
8476 | 2006 | 6 | 12 | 0.39236 |  | 380 | 32 | 5 | Munster | 8/4.8kV | 43F2 | Transformer located at 7232 Franktown isolted due to upgrade of service | Goulburn | Scheduled Outage | Preventive Maintenance
16385 | 2010 | 7 | 3 | 0.65972 |  | 7 | 47 | 405 | MUNSTER | 8/4.8kV | 43F2 | Load transfer of Munster 43F2 to Beckwith for planned work on the A9M3 to install new poles and transfer plant. | Goulburn | Scheduled Outage
16390 | 2010 | 7 | 4 | 0.0076389 |  | 2 | 14 | 405 | Munster | 8/4.8kV | 43F2 | Interruption to transfer Munster 43F2 back from Beckwith F2 due to low voltage complaints at City Pumping & Sewage stations as well as residential customers. | Goulburn | Unknown/Other
16392 | 2010 | 7 | 4 | 0.27153 |  | 4 | 30 | 450 | Munster | 8/4.8kV | 43F2 | To allow crew to transfer Munster load to Beckwith F2 | Goulburn | Unknown/Other
16393 | 2010 | 7 | 4 | 0.56944 |  | 28 | 216 | 463 | Munster | 8/4.8kV | 43F2 | 43F2 & part of 43F3 customers dropped to allow for transfer of customer off Beckwith F2. 463 customers affected for 28 minutes. | Goulburn | Scheduled Outage | Construction
8662 | 2006 | 7 | 5 | 0.85278 |  | 452 | 616 | 361 | Munster | 8/4.8kV | 43F2 | Severe wind storm in Goulborn has caused tree to come down across 3 phase section of 43F2 on Franktown Rd circuit opened due to tree burning, customers restored in sections. O/H line section rebuilt and final customers restored at 04:00. | Goulburn | Adverse Weather | Wind
16448 | 2010 | 7 | 9 | 0.75972 |  | 216 | 4 | 1 | Munster | 8/4.8kV | 43F2 | At 21:50 trans at 8633 PURDY RD GOULBOURN was reenergized after replaceing defective cutout due to lightning strike | Goulburn | Adverse Weather | Lightning
18631 | 2011 | 7 | 9 | 0.34931 |  | 179 | 3 | 1 | Munster | 8/4.8kV | 43F2 | Replaced blown fuse feeding transformer X12182 at 8271 Bleeks Road | Goulburn | Adverse Weather | Lightning
13006 | 2008 | 8 | 6 | 0.052778 |  | 544 | 99 | 17 | Munster | 27.6/16kV | 43F2 | Power out calls in the Jock Trail road area. Crew found S883 at Woods and Franktown open. Red phase of 43F2 down broken at mid span on Woods. Crew performed switching to isolate downed phase and to restore half of the customers affected. | Goulburn | Adverse Weather | Lightning
7092 | 2005 | 8 | 10 | 0.29167 |  | 120 | 160 | 80 | Munster | 8/4.8kV | 43F2 | 24/7 crew found solid blade switch 644 R phase had fallen open, same had to be replaced. | Goulburn | Defective Equipment
15059 | 2009 | 9 | 6 | 0.41875 |  | 69 | 1 | 1 | Munster |  | 43F2 | replaced blown fuse at transformer X33256 at 8286 Franktown Rd | Goulburn | Foreign Interference | Bird
13222 | 2008 | 9 | 12 | 0.41667 |  | 135 | 9 | 4 | Marchwood | 27.6/16kV | 43F2 | At 10:00 trans at 8735 Purdy Rd was isolated in order to install a sec service | Goulburn | Scheduled Outage | Repair
15101 | 2009 | 9 | 14 | 0.46458 |  | 56 | 4 | 4 | MUNSTER DS | 8/4.8kV | 43F2 | Transformer X36299 at 21 Coldstream Crt isolated to allow for transfer of secondary to new pole | Goulburn | Scheduled Outage
7357 | 2005 | 9 | 21 | 0.44792 |  | 45 | 2 | 2 | Munster | 8/4.8kV | 43F2 | Transformer 8065 at 8089 Franktown rd was isolated for electrician to make repairs to secondary service | Goulburn | Scheduled Outage | Repair
9284 | 2006 | 9 | 22 | 0.96944 |  | 128 | 213 | 100 | Munster | 8/4.8kV | 43F2 | An animal and blown arrester at GR872B caused the 43F2 to trip. Cleared animal and changed arrester at GR872B, and restored power to Recloser. | Goulburn | Foreign Interference | Animal
13297 | 2008 | 9 | 27 | 0.53333 |  | 142 | 38 | 16 | Munster | 8/4.8kV | 43F2 | Squirrel contact at 15 Cranberry Crt caused transformer fuse to blow. Arrester and fuse cut-out replaced. | Goulburn | Foreign Interference | Animal
13298 | 2008 | 9 | 27 | 0.53333 |  | 142 | 38 | 16 | Munster | 8/4.8kV | 43F2 | Animal contact at 15 Cranberry Crt caused transformer cut out to open. | Goulburn | Foreign Interference | Animal
5823 | 2004 | 10 | 2 | 0.75556 |  | 60 | 2 | 2 | Munster | 8/4.8kV | 43F2 | Roy trim trees and then closed in switch 404 | Goulburn | Tree Contacts | Inadequate Trimming
15201 | 2009 | 10 | 3 | 0.3125 |  | 3 | 11 | 221 | Munster | 8/4.8kV | 43F2 | Munster 43F2 circuit customers were temporarily interrupted to transfer them over to Hydro One Beckwith feeder for duration of Munster Sub maintenance. | Goulburn | Scheduled Outage | Repair
15205 | 2009 | 10 | 3 | 0.72569 |  | 2 | 7 | 221 | Munster | 8/4.8kV | 43F2 | Munster 43F2 circuit customers were temporarily interrupted to transfer load back to 43F2 from Hydro One's Beckwith feeder. | Goulburn | Scheduled Outage | Repair
19377 | 2011 | 10 | 15 | 0.37361 |  | 2 | 16 | 467 | Munster | 8/4.8kV | 43F2 | Customers on the 43F2 circuit to rabbit transformer 7786 were interrupted for switching to transfer them to the BECKF2 circuit. | Goulburn | Scheduled Outage | Construction
19396 | 2011 | 10 | 17 | 0.35556 |  | 3 | 23 | 467 | Munster | 8/4.8kV | 43F2 | Customers on the 43F2 circuit to rabbit transformer 7786 were interrupted for switching to transfer them back to normal. | Goulburn | Scheduled Outage | Construction
13411 | 2008 | 10 | 22 | 0.62222 |  | 94 | 2 | 1 | Munster DS | 8/4.8kV | 43F2 | Replaced broken switch feeding customer owned line at 8775 FRANKTOWN Road | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
7511 | 2005 | 10 | 24 | 0.39583 |  | 5 | 30 | 361 | Munster | 8/4.8kV | 43F2 | Tree fell across double 8kv circuits 12 spans west of the station. Isolation required on 43F2 and 43F3 ccts. to remove tree. | Goulburn | Tree Contacts | Tree Fallen
13465 | 2008 | 10 | 28 | 0.99722 |  | 229 | 1378 | 361 | Munster | 8/4.8kV | 43F2 | B Seaman has patrolled line, found sw644 R phase blown, same now replaced. Munster rd near Copeland. | Goulburn | Adverse Weather
13477 | 2008 | 10 | 28 | 0.84444 |  | 40 | 107 | 160 | MUNSTER | 8/4.8kV | 43F2 | 20:16 - Blue phase auto; white phase open 20:56 - White phase recloser closed from SCADA | Goulburn | Adverse Weather
15339 | 2009 | 10 | 31 | 0.64167 |  | 216 | 4 | 1 | Munster | 8/4.8kV | 43F2 | Broken lead to O/H Transformer at 3135 Munster Rd replaced. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
7567 | 2005 | 11 | 6 | 0.52083 |  | 80 | 20 | 15 | Munster | 8/4.8kV | 43F2 | Switch S232R at Jock Trail & Munster Rd opened due to a blown arrestor. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17281 | 2010 | 11 | 16 | 0.47917 |  | 60 | 2 | 2 | Munster | 8/4.8kV | 43F2 | Isolated primary line fed from Switch S25438 at 7935 Jock Trail Rd To remove tree from the primary | Goulburn | Tree Contacts | Tree Fallen
17336 | 2010 | 11 | 24 | 0.41667 |  | 213 | 7 | 2 | Munster DS | 8/4.8kV | 43F2 | Transformer 1860 at 8795 Franktown Road was isolated to allow crew to re-configure plant. 2 customers were affected for 213 minutes. | Goulburn | Scheduled Outage
9783 | 2006 | 12 | 2 | 0.091667 |  | 426 | 1065 | 150 | Munster | 8/4.8kV | 43F2 | Ice storm and high winds caused three trees to come down at different run offs and a section of primary to burn off to the ground. Circuit was sectionalized to restore power. | Goulburn | Adverse Weather | Ice Storm
17425 | 2010 | 12 | 14 | 0.59375 |  | 460 | 38 | 5 | Munster | 8/4.8kV | 43F2 | On call crew called in to replace defective transformer, switch & arrestor at 3 Cade Crt in Munster. Transformer # X36443 | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
19740 | 2011 | 12 | 19 | 0.35625 |  | 120 | 70 | 35 | Munster | 8/4.8kV | 43F2 | Switch S12137 at Bleeks and Munster rd, was opened to allow crews to install new poles. | Goulburn | Scheduled Outage | Construction
19752 | 2011 | 12 | 20 | 0.375 |  | 390 | 228 | 35 | Munster | 8/4.8kV | 43F2 | Switch S12137 at Bleeks and Munster rd, was opened to allow crews to install new poles. | Goulburn | Scheduled Outage | Preventive Maintenance
15578 | 2009 | 12 | 27 | 0.82986 |  | 103 | 14 | 8 | Munster | 8/4.8kV | 43F2 | Crews required isolation of overhead single phase 8kV on Jock Trail Road to repair downed conductor. | Goulburn | Adverse Weather | Ice Storm
4663 | 2003 | 12 | 29 | 0.86458 |  | 69 | 21 | 18 | Munster | 8/4.8kV | 43f2 | Probable contact by animal, Transformer 5512 located on Cobblestone Crt. | Goulburn | Foreign Interference | Animal
6286 | 2005 | 3 | 15 | 0.60556 |  | 4 | 3 | 40 | Munster | 12/7.2kV | 43F2 white | While restoring 43F2 white phase reclosure at station via scada 43F2 reclosure tank opened. This caused an outage to 40 customers. Reclosure was reclosed via scada, and checked in the field by G. Ryan. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
15574 | 2009 | 12 | 26 | 0.94722 |  | 48 | 473 | 591 | Munster | 8/4.8kV | 43F2, F3 | Forced outage on the Munster F2 and F3 feeders for crew to remove tree wrapped in adjacent overhead lines West of Munster Sub on Bleeks Road. | Goulburn | Tree Contacts | Tree Limb Fallen
6525 | 2005 | 5 | 9 | 0.35556 |  | 13 | 126 | 669 | Munster | 8/4.8kV | 43F2,43F3 | Munster T1 off loaded and load picked up from Beckwith F2 through step down transformers. Out of phase condition so load loss for switching. | Goulburn | Scheduled Outage | Preventive Maintenance
3581 | 2003 | 6 | 19 | 0.36458 |  | 25 | 279 | 669 | Munster | 8/4.8kV | 43F2,43F3 | Line crew sent to Munster to block recloser for contractor and opened reclosers by mistake. | Goulburn | Human Element | Switching Errors
15202 | 2009 | 10 | 3 | 0.32361 |  | 7 | 53 | 452 | Munster | 8/4.8kV | 43F2/F3 | Munster 43F2 & 43F3 circuit customers were temporarily interrupted to transfer them over to Hydro One Beckwith feeder for the duration of Munster Sub maintenance. | Goulburn | Scheduled Outage | Repair
19794 | 2012 | 1 | 6 | 0.47569 |  | 42 | 4 | 5 | Munster | 8/4.8kV | 43F3 | Gaetan Godard reports transformer #X12339 located at 8195 Purdy opened by crew to run a new service | Goulburn | Scheduled Outage | Construction
13944 | 2009 | 2 | 9 | 0.54861 |  | 60 | 5 | 5 | Munster | 8/4.8kV | 43F3 | Transformer X35239 at 3 Coolbrook isolatedto repair defective service. | Goulburn | Defective Equipment
13959 | 2009 | 2 | 11 | 0.67708 |  | 45 | 4 | 5 | Munster | 8/4.8kV | 43F3 | Transformer #X36715 located at 14 Cove Crt isolated to replace secondary connections | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12094 | 2008 | 3 | 3 | 0.45833 |  | 40 | 4 | 6 | MUNSTER DS | 8/4.8kV | 43F3 | Transformer # X32965 at 16 Lucas isolated to allow for replacement of switch & arrestor | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
4917 | 2004 | 3 | 18 | 0.45833 |  | 36 | 3 | 5 | Munster | 8/4.8kV | 43F3 | Transformer 10495 at 44 Dogwood isolated to change arresters | Goulburn | Scheduled Outage | Preventive Maintenance
12225 | 2008 | 4 | 2 | 0.39236 |  | 305 | 15 | 3 | Munster | 8/4.8kV | 43F3 | Isolated and replaced defective transformer 7491 at the rear of 24 Stroughton Cres | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17943 | 2011 | 4 | 16 | 0.62847 |  | 5 | 20 | 246 | Munster | 8/4.8kV | 43F3 | Planned interruption to customers in the Franktown and Munster Rd. area due to out of phase condition. | Goulburn | Scheduled Outage
17944 | 2011 | 4 | 16 | 0.64236 |  | 3 | 16 | 326 | Munster | 8/4.8kV | 43F3 | Planned interruption to customers in the Bleeks and Munster Rd. area due to out of phase condition. | Goulburn | Scheduled Outage
17948 | 2011 | 4 | 17 | 0.64236 |  | 11 | 45 | 246 | Munster | 8/4.8kV | 43F3 | Planned interruption to customers in the Franktown and Munster Rd. area due to out of phase condition | Goulburn | Scheduled Outage
17949 | 2011 | 4 | 17 | 0.62361 |  | 3 | 17 | 346 | Munster | 8/4.8kV | 43F3 | Planned interruption to customers in the Bleeks and Munster Rd. area due to out of phase condition | Goulburn | Scheduled Outage
10313 | 2007 | 4 | 23 | 0.96667 |  | 8 | 41 | 308 | Munster | 8/4.8kV | 43F3 | While attempting to transfer 43F3 load to BeckwithF2 through rabbits at Dwyer Hill & Bleeks, the 43F3 was opened & SW424 supplying the rabbits failed to operate, 43F3 supply was restored to normal but 2 phases of Beckwith F2 opened on the attempted close of SW424. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
14331 | 2009 | 5 | 9 | 0.36111 |  | 75 | 2 | 2 | Munster | 8/4.8kV | 43F3 | Transformer #X35757 located at 8230 Bleeks isolated due to possible animal contact | Goulburn | Foreign Interference | Animal
18249 | 2011 | 5 | 30 | 0.48611 |  | 95 | 3 | 2 | Munster | 8/4.8kV | 43F3 | Replaced blown fuse feeding transformer X12357 at 3436 Dwyer Hill Rd (Cause un-known ) | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
20664 | 2012 | 6 | 1 | 0.65069 |  | 118 | 14 | 7 | Munster |  | 43F3 | fuse at switch SW883 on Franktown rd, opened, for no apparent reason. | Goulburn | Unknown/Other | No Apparent Cause
8457 | 2006 | 6 | 9 | 0.82708 |  | 364 | 218 | 36 | Munster | 8/4.8kV | 43F3 | Tree Fallen on O/H Primary circuit at 45 Butterfield causing S7702 to blow.. Asplundh called in to remove large tree. S7702 Refused and closed. | Goulburn | Tree Contacts | Tree Fallen
8475 | 2006 | 6 | 12 | 0.43819 |  | 175 | 146 | 50 | Munster | 8/4.8kV | 43F3 | Sleeved out set defective solid blade switches (sw231) | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
10616 | 2007 | 6 | 13 | 0.48958 |  | 15 | 2 | 9 | MUNSTER | 8/4.8kV | 43F3 | Transformer #8360 at 58 Owls Head isolated to allow for meter base repair | Goulburn | Scheduled Outage | Repair
10617 | 2007 | 6 | 13 | 0.375 |  | 15 | 2 | 9 | MUNSTER | 8/4.8kV | 43F3 | Transformer #8360 at 58 Owls Head isolated to allow for service upgrade | Goulburn | Scheduled Outage | Repair
12716 | 2008 | 6 | 24 | 0.47569 |  | 15 | 1 | 3 | Munster MS | 8/4.8kV | 43F3 | Transformer #X36418 located at 10 Carlisle Cir Goulbourn isolated to change blown arrestor. | Goulburn | Scheduled Outage | Repair
14644 | 2009 | 6 | 29 | 0.86458 |  | 107 | 0 | 1 | Munster | 8/4.8kV | 43F3 | Customer called in for no power. Crew found blown fuse at transformer X35756 at 8034 Bleeks rd. Crew replaced fuse and restored power to 1 customer. | Goulburn | Unknown/Other
14657 | 2009 | 7 | 3 | 0.89167 |  | 474 | 143 | 44 | Munster | 8/4.8kV | 43F3 | Red phase fuse @ switch S12137 opened due to primary growing through a tree. Three phase overhead was isolated and tree was removed. | Goulburn | Tree Contacts | Inadequate Trimming
16384 | 2010 | 7 | 3 | 0.63889 |  | 10 | 50 | 303 | MUNSTER | 8/4.8kV | 43F3 | Load transfer of Munster DS to Beckwith for planned work on the A9M3 supply to install new poles and transfer plant. | Goulburn | Scheduled Outage
16389 | 2010 | 7 | 4 | 0.0034722 |  | 1 | 7 | 303 | Munster | 8/4.8kV | 43F3 | Interruption to transfer Munster 43F3 back from Beckwith F2 due to low voltage complaints at City Pumping & Sewage stations as well as residential customers. | Goulburn | Unknown/Other
16391 | 2010 | 7 | 4 | 0.26736 |  | 4 | 16 | 245 | Munster | 8/4.8kV | 43F3 | To transfer Munster DS load to BeckwithF2. | Goulburn | Unknown/Other
16394 | 2010 | 7 | 4 | 0.60417 |  | 3 | 12 | 245 | Munster | 8/4.8kV | 43F3 | 43F3 customers supplied from SW644 were dropped to allow for transfer of customer off Beckwith F2. 245 customers affected for 3 minutes. | Goulburn | Scheduled Outage
16447 | 2010 | 7 | 9 | 0.52292 |  | 477 | 40 | 5 | Munster | 8/4.8kV | 43F3 | Fuse cutout on Munster RD south of Soldier lane found blown due to adverse weather. | Goulburn | Adverse Weather | Lightning
18623 | 2011 | 7 | 9 | 0.90833 |  | 264 | 37 | 11 | Munster | 8/4.8kV | 43F3 | S25347 found blown due to tree on primary. S16776 found blown, circuit patrolled nothing found. S16776 closed and all power restored. | Goulburn | Tree Contacts | Tree Fallen
3722 | 2003 | 7 | 12 | 0.51389 |  | 55 | 92 | 100 | Munster | 8/4.8kV | 43F3 | Due to high winds a tree contacted the R phase of the Munster F3 causing the R phase of the F3 reclosure to open. Reclosure closed to restore power. Tree to be removed. | Goulburn | Tree Contacts | Inadequate Trimming
8909 | 2006 | 8 | 2 | 0.61597 |  | 123 | 41 | 20 | Munster | 8/4.8kV | 43F3 | 5 transformers out on Owlshead(one address is 2 Owlshead) & Coolbrook due to tree on primary | Goulburn | Tree Contacts | Tree Fallen
14909 | 2009 | 8 | 4 | 0.83194 |  | 157 | 75 | 31 | Munster | 8/4.8kV | 43F3 | At 18:15 switch S12137 RWB opened crew at first re-fused white phase then found that the other two fuses where blown aswell. 31 customers where affected. | Nepean | Adverse Weather | Lightning
7104 | 2005 | 8 | 10 | 0.61458 |  | 169 | 141 | 50 | Munster | 8/4.8kV | 43F3 | Tree fell on O/H circuit opening switch 231R phase. | Goulburn | Foreign Interference | Foreign Object
18911 | 2011 | 8 | 11 | 0.58333 |  | 225 | 4 | 1 | Munster | 8/4.8kV | 43F3 | Transformer #X35421 located at 7827 Jock Trail opened up due to defective switch | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
13064 | 2008 | 8 | 15 | 0.74444 |  | 268 | 13 | 3 | Munster | 8/4.8kV | 43F3 | Transformer #9693 located at 1444 Dwyer Hill Rd isolated due to lightning | Goulburn | Adverse Weather | Lightning
11147 | 2007 | 8 | 24 | 0.175 |  | 7 | 23 | 200 | Munster | 8/4.8kV | 43F3 | The Munster 43F3 B phase recloser tripped during a thunderstorm, same closed from SCADA to restore. | Goulburn | Defective Equipment
11187 | 2007 | 8 | 29 | 0.96389 |  | 119 | 496 | 250 | Munster | 8/4.8kV | 43F3 | 3 insulators failed at 7930 Bleek's rd. Munster F3 circuit was isolated to all crews to replace same. | Goulburn | Adverse Weather | Lightning
11220 | 2007 | 8 | 30 | 0.67639 |  | 37 | 0 | 10 | Munster | 8/4.8kV | 43F3 | Transformer # GB006974 at 6974 Flewellyn isolated to replace broken cut-out | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
19098 | 2011 | 9 | 6 | 0.49167 |  | 54 | 2 | 2 | Munster | 8/4.8kV | 43F3 | Transformer X12459 and X32839 at 7639 Soldier's Line were opened to allow crew to replace cut-out. | Goulburn | Scheduled Outage | Load Shedding
11314 | 2007 | 9 | 15 | 0.93681 |  | 60 | 5 | 5 | Munster | 8/4.8kV | 43F3 | Squirrell contact caused transformer 8357 fuse to open at 4 Owlshead. Transformer re-fused and customers restored. | Goulburn | Foreign Interference | Animal
13245 | 2008 | 9 | 16 | 0.43542 |  | 93 | 2 | 1 | Munster | 8/4.8kV | 43F3 | Transformer #S11603 located at 7449 Fallowfield Rd isolated due to tree interference | Goulburn | Tree Contacts | Inadequate Trimming
19264 | 2011 | 9 | 27 | 0.23611 |  | 60 | 13 | 13 | Munster | 8/4.8kV | 43F3 | Pole on Conley broken at the base and leaning over Conely required isolation to safeley secure. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
15204 | 2009 | 10 | 3 | 0.70833 |  | 5 | 38 | 452 | Munster | 8/4.8kV | 43F3 | Munster 43F3 circuit customers were temporarily interrupted to transfer load back to Munster 43F3 from Hydro One's Beckwith feeder. | Goulburn | Scheduled Outage | Repair
11460 | 2007 | 10 | 4 | 0.42708 |  | 135 | 90 | 40 | Beckwith | 27.6/16kV | 43F3 | Overhead section of BeckwithF2 isolated for reconstruction at Dwyer Hill and Hwy #7 | Goulburn | Scheduled Outage | Construction
19376 | 2011 | 10 | 15 | 0.35694 |  | 5 | 22 | 267 |  | 8/4.8kV | 43F3 | Customers on the 43F3 circuit from SW482 to rabbit transformer 7877 were interrupted for switching to transfer them to the BECKF2 circuit. | Goulburn | Scheduled Outage | Construction
19398 | 2011 | 10 | 17 | 0.36389 |  | 3 | 13 | 267 | Munster | 8/4.8kV | 43F3 | Customers on the 43F3 circuit from SW482 to rabbit transformer 7877 were interrupted for switching to transfer them back to normal. | Goulburn | Scheduled Outage | Construction
13390 | 2008 | 10 | 19 | 0.72847 |  | 2 | 16 | 476 | Munster | 8/4.8kV | 43F3 | Planned outage as per PC17A# 17-23704 to restore Munster DS. SW424 (rabbit) opened, 43F3 breaker closed. Approx 476 customers for 2 minutes. | Goulburn | Scheduled Outage | Preventive Maintenance
13391 | 2008 | 10 | 19 | 0.73056 |  | 4 | 14 | 204 | Munster | 8/4.8kV | 43F3 | Planned outage as per PC17A# 17-23704 to restore Munster DS. SW468 (rabbit) opened, S15259 closed. Approx 204 customers affected for 4 mins. | Goulburn | Scheduled Outage | Preventive Maintenance
7512 | 2005 | 10 | 24 | 0.39583 |  | 40 | 129 | 208 | Munster DS | 8/4.8kV | 43F3 | Tree fell across double 8kv circuits 12 spans west of the staion. Isolation required on the 43F2, and 43F3 ccts to remove tree. 43F3 white phase would not stay closed (would fall open). The 43F3 circuit was transferred to the 43F2 to restore load. | Goulburn | Tree Contacts | Tree Fallen
19686 | 2011 | 12 | 5 | 0.975 |  | 299 | 55 | 11 | Munster | 8/4.8kV | 43F3 | Primary conductor came off its insulator and came down on the cross arm at 7615 Soldiers Line | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
19748 | 2011 | 12 | 20 | 0.375 |  | 460 | 23 | 3 |  | 8/4.8kV | 43F3 | A section of line from MC2084 on Jock Trail & Franktown rd was isolated to re-configure the o/h line | Goulburn | Scheduled Outage | Construction
19771 | 2011 | 12 | 30 | 0.060417 |  | 318 | 5 | 1 | Munster DS | 8/4.8kV | 43F3 | X08909 at 7865 Franktown Rd had to be opened to allow Hydro Ottawa crews to make temporary repairs to a defective underground service. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
18160 | 2011 | 5 | 15 | 0.675 |  | 66 | 54 | 49 | Munster | 8/4.8kV | 43F3R | Customer was cutting trees and had one contact the primary getting hung up on the neutral causing S15839 to open | Goulburn | Tree Contacts | Tree Fallen
6546 | 2005 | 5 | 12 | 0.35764 |  | 31 | 232 | 668 | Munster | 8/4.8kV | 43T1 | Munster T1 transformer was isolated to install fall arrest bracket, service tap changer and change bus insulator. For this restoration there had to be an outage because the out off phase rabbits between the 27Kv & 8Kv O/H. | Goulburn | Scheduled Outage | Preventive Maintenance
19798 | 2012 | 1 | 8 | 0.58542 |  | 41 | 280 | 410 | Janet King | 8/4.8kV | 44F1 | customer reported outage on 44F1 circuit, SCADA indicates RED phase fault. Patrol found swicth 920 RED phase fuse blown. Refused and closed. No apparent cause found | Goulburn | Unknown/Other
19799 | 2012 | 1 | 8 | 0.70833 |  | 60 | 410 | 410 | Janet King | 8/4.8kV | 44F1 | customer reported outage on 44F1 circuit, SCADA indicates RED phase fault. Patrol found swicth 920 RED phase fuse blown (again). Refused and closed. Load transfered from Janet King back to Richmond North to prevent further outages | Goulburn | Unknown/Other
19811 | 2012 | 1 | 11 | 0.020833 |  | 65 | 2 | 2 | Janet King DS | 8/4.8kV | 44F1 | Transformer TP5581 at 10 Warner Colpitts Lane was isolated to allow a contractor to install a new service. | Goulburn | Scheduled Outage | Construction
13875 | 2009 | 1 | 17 | 0.95764 |  | 180 | 348 | 200 | Janet king | 8/4.8kV | 44F1 | defective 44F1 red phase recloser at Janet King substation opened interrupting customers on Elm, Norway spruce, white cedar in stittsville, and on stittsville main st.. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
20173 | 2012 | 3 | 17 | 0.095139 |  | 378 | 404 | 167 | Janet King | 8/4.8kV | 44F1 | A Blown white phase elbow at S17 on Stittsville main cause white phase fuse at 921 to blow. Elbows replaced and all power restored | Goulburn | Defective Equipment
17787 | 2011 | 3 | 28 | 0.086111 |  | 133 | 155 | 70 | Janet King | 8/4.8kV | 44F1 | S908 White phase broken. Repairs made, switch closed and holding | Goulburn | Defective Equipment
12346 | 2008 | 4 | 25 | 0.56597 |  | 50 | 4 | 5 | Janet King | 8/4.8kV | 44F1 | Isolated transformer X36390 at 10 Coach Av to repair a service | Goulburn | Scheduled Outage | Repair
12347 | 2008 | 4 | 25 | 0.52083 |  | 130 | 13 | 6 | Janet King | 8/4.8kV | 44F1 | Isolated transformer X36392 at 107 Lanigan Cres to replace the pole | Goulburn | Scheduled Outage | Construction
18193 | 2011 | 5 | 20 | 0.75417 |  | 50 | 22 | 27 | Janet King |  | 44F1 | At 18:06 customer isolated 44F1 from S18-4 to end of line to replace broken switch S12402 at Manchester and Main in Stittsville. 27 customers affected for 48 mins. Janet King 44F1 ID # 18193 | Goulburn | Scheduled Outage | Repair
12459 | 2008 | 5 | 21 | 0.57014 |  | 41 | 2 | 3 | Janet King | 8/4.8kV | 44F1 | Transformer legacy #2936 - X35285 at 7 Hobin isolated to allow for installation of new pole | Goulburn | Scheduled Outage | Construction
12490 | 2008 | 5 | 28 | 0.39236 |  | 125 | 83 | 40 | Janet King | 4.16kV | 44F1 | The transformers on Ember Glow were isolated to string in new secondary. | Goulburn | Scheduled Outage | Preventive Maintenance
5249 | 2004 | 6 | 2 | 0.53125 |  | 45 | 14 | 18 | Janet King | 8/4.8kV | 44F1 | Transformer at 35 Pretty isolated to replace defective connections. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
5250 | 2004 | 6 | 2 | 0.56944 |  | 30 | 6 | 12 | Janet King | 8/4.8kV | 44F1 | Transformer at 30 Ralph Park isolated to replace defective connections. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
14444 | 2009 | 6 | 2 | 0.42361 |  | 115 | 8 | 4 | Janet King | 8/4.8kV | 44F1 | 44F1 OH section between switch 920 and S11273 on McCooeye was isolated to allow crews to re-insulate and install new poles, 2 OH xfmrs 4 customers affected. | Goulburn | Scheduled Outage | Construction
20722 | 2012 | 6 | 8 | 0.76597 |  | 272 | 36 | 8 | Janet King | 8/4.8kV | 44F1 | transformer X36722 was found defective and replaced. Janet King (44F1) ID #20722 | Goulburn | Defective Equipment
20806 | 2012 | 6 | 19 | 0.63958 |  | 79 | 5 | 4 | Janet King | 8/4.8kV | 44F1 | Transformer #X35289 located at 31 Orville St opened up due to broken switch | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
19064 | 2011 | 8 | 31 | 0.61181 |  | 129 | 32 | 15 | Janet King | 8/4.8kV | 44F1 | A defective blue phase fuse at S921 opened on Stittsville Main. Janet King (44F1) ID#19064 | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
19747 | 2011 | 12 | 20 | 0.36458 |  | 41 | 1 | 2 | Janet King | 8/4.8kV | 44F1 | At 8:26am crew isolated transformer TP5581 at 10 Warner Colpitts Lane but was not able to complete their work because School affected was not prepared for this planned outage. Janet King 44F1 ID# 19747 | Goulburn | Scheduled Outage
11033 | 2007 | 8 | 11 | 0.29931 |  | 109 | 1146 | 807 | Janet King | 8/4.8kV | 44F1, F3 | 44kv R&W phase fuses supplying Janet King T1 blew. Stations crew found 2 blown lightning arrestors & 2 defective insulators on the 8kv structure. Customers were restored by transferring load to alternate supply, Richmond N. 29F1. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
11907 | 2008 | 1 | 8 | 0.40972 |  | 20 | 2 | 7 | Janet King | 8/4.8kV | 44F3 | Isolated transformer GB2933 at 32 Ember Glow Crt to replace switch | Goulburn | Scheduled Outage | Preventive Maintenance
12036 | 2008 | 2 | 11 | 0.88194 |  | 6 | 0 | 5 | Janet King | 8/4.8kV | 44F3 | Transformer #2955 located at 20 Bell St isolated due to loose connections at the transformer | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
7949 | 2006 | 2 | 19 | 0.61458 |  | 86 | 16 | 11 | Janet King | 8/4.8kV | 44F3 | Defective tx switch at tx 2973 on Bradley St in Stittsville replaced. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
10041 | 2007 | 2 | 19 | 0.86458 |  | 95 | 16 | 10 | Janet King | 8/4.8kV | 44F3 | Replaced broken switch to transformer 2947 at 1600 Stitsville Main St | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12060 | 2008 | 2 | 19 | 0.48681 |  | 42 | 5 | 7 | Janet King | 8/4.8kV | 44F3 | At 11:41 trans at 27 Norway was isolated in order to replace a pole | Goulburn | Scheduled Outage | Preventive Maintenance
6265 | 2005 | 3 | 11 | 0.57639 |  | 30 | 2 | 5 |  | 8/4.8kV | 44F3 | Transformer switch opened to replace blown lightning arrester at 26 Ember Glow. | Goulburn | Defective Equipment
12140 | 2008 | 3 | 14 | 0.37361 |  | 122 | 12 | 6 | Janet King | 12/7.2kV | 44F3 | At 09:58 trans at 6 Carlet Cathcart was isolated for trans replacement | Ottawa | Scheduled Outage | Repair
10138 | 2007 | 3 | 15 | 0.60069 |  | 20 | 1 | 2 | Janet King | 8/4.8kV | 44F3 | Isolated transformer 2962 at 8 Donegal Rd to repair service | Goulburn | Scheduled Outage | Preventive Maintenance
12158 | 2008 | 3 | 20 | 0.42361 |  | 90 | 3 | 2 | Janet King | 8/4.8kV | 44F3 | Transformer #X35274 located at 30 Ralphpark isolated to re-do switches & re-new service | Goulburn | Scheduled Outage | Repair
12252 | 2008 | 4 | 8 | 0.58333 |  | 60 | 3 | 3 | Janet King | 8/4.8kV | 44F3 | Transformer #X35289 located at 33 Orville isolated due to re-arranging plant | Goulburn | Scheduled Outage | Preventive Maintenance
15915 | 2010 | 4 | 9 | 0.40764 |  | 240 | 400 | 100 | Janet King MS | 8/4.8kV | 44F3 | Transformer 4867 isolated to allow crews to replace elbows and inserts. | Goulburn | Scheduled Outage | Preventive Maintenance
12272 | 2008 | 4 | 11 | 0.40625 |  | 105 | 14 | 8 | JANET KING | 8/4.8kV | 44F3 | Transformer #4864 on Ember Glow isolated to allow for repairs to secondary | Goulburn | Scheduled Outage | Repair
4996 | 2004 | 4 | 13 | 0.63611 |  | 270 | 1144 | 800 | Janet King | 8/4.8kV | 44F3 | Switches at the riser pole tracked across causing the pole fire. The pole broke dropping the O/H line to the ground and open the reclosour at Janet King. Partial switching was performed and a new O/H switch was install to restore load. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12280 | 2008 | 4 | 14 | 0.54167 |  | 80 | 11 | 8 | JANET KING | 8/4.8kV | 44F3 | Transformer X36464 at 8 Ember Glow isolated to relocate cut-out to install new pole | Ottawa | Scheduled Outage | Construction
12322 | 2008 | 4 | 22 | 0.39306 |  | 76 | 15 | 12 | Janet King | 8/4.8kV | 44F3 | Transformer #X36392 located at 106 Lanigan Cres isolated due to pole installation | Goulburn | Scheduled Outage | Preventive Maintenance
12363 | 2008 | 4 | 29 | 0.55208 |  | 80 | 8 | 6 | Janet King | 8/4.8kV | 44F3 | Transformer #X36391 located at 15 Coach Ave isolated due to transferring plant | Goulburn | Scheduled Outage | Preventive Maintenance
5079 | 2004 | 4 | 30 | 0.61458 |  | 11 | 0 | 1 | Janet King | 8/4.8kV | 44F3 | Stiitsville Public portable class rooms isolated due to broken meter. Meter was broken by a brick. Outage was planned with school election. To allow meter dept. to change meter. | Kanata | Foreign Interference | Sabotage
12431 | 2008 | 5 | 12 | 0.55556 |  | 100 | 15 | 9 | Janet King | 8/4.8kV | 44F3 | Isolated transformer X36390 at 10 Coach Rd to transfer triplex services | Goulburn | Scheduled Outage | Construction
12441 | 2008 | 5 | 15 | 0.44792 |  | 40 | 5 | 7 | JANET KING | 8/4.8kV | 44F3 | TRANSFORMER X32596 AT30 EMBERGLOW ISOLATED TO ALLOW FOR POLE UPGRADE | Goulburn | Scheduled Outage | Preventive Maintenance
12442 | 2008 | 5 | 15 | 0.48056 |  | 17 | 2 | 7 | JANET KING | 8/4.8kV | 44F3 | TRANSFORMER X32596 AT30 EMBERGLOW ISOLATED TO ALLOW FOR POLE UPGRADE | Goulburn | Scheduled Outage
12543 | 2008 | 6 | 4 | 0.39583 |  | 120 | 14 | 7 | JANET KING | 8/4.8kV | 44F3 | Transformer #X35296 at 32 Ember Glow isolated to allow for service upgrade | Goulburn | Scheduled Outage | Construction
12547 | 2008 | 6 | 4 | 0.53333 |  | 102 | 8 | 5 | JANET KING | 8/4.8kV | 44F3 | Transformer X32595 at 23 Ember Glow Crt isolated to allow for system upgrade | Goulburn | Scheduled Outage | Construction
12581 | 2008 | 6 | 9 | 0.375 |  | 216 | 7 | 2 | JANET KING | 8/4.8kV | 44F3 | Transformer #35285 @ 9 Hobin isolated to allow for new secondary & new pole | Goulburn | Scheduled Outage | Construction
5391 | 2004 | 6 | 28 | 0.49722 |  | 13 | 1 | 3 | Janet King | 8/4.8kV | 44F3 | Transformer T8122 at 5899 Hazeldean opened for testing. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
8679 | 2006 | 7 | 8 | 0.19306 |  | 82 | 102 | 75 | Janet king | 8/4.8kV | 44F3 | Scada and Idispatched had failed at Merivale site. No alarms or phone calls. Outage on the white phase only was noticed after Albion site was activated. Power was restored after white phase breaker was closed via scada at Albion. Patrolled Mon. July 10/06 and no problems found. | Goulburn | Unknown/Other | No Apparent Cause
7079 | 2005 | 8 | 6 | 0.4875 |  | 101 | 13 | 8 | JANET kING | 12/7.2kV | 44F3 | Vehicle pulled down overhead service at RX2955 on the corner of Elm & Bell st in stittsville. Police report # 05-219925. | Goulburn | Foreign Interference | Vehicle
7229 | 2005 | 8 | 28 | 0.38542 |  | 200 | 47 | 14 | Janet King | 8/4.8kV | 44F3 | Transformer TE8270 at 1559 Main St in Stittsville was isolated for replacement and oil clean up. | Goulburn | Scheduled Outage
15329 | 2009 | 10 | 29 | 0.41667 |  | 120 | 10 | 5 | Janet King | 8/4.8kV | 44F3 | Transformer #X35527 located at 19 Ralphpark St isolated to install new poles | Goulburn | Scheduled Outage | Construction
15353 | 2009 | 11 | 5 | 0.38542 |  | 185 | 15 | 5 | Janet King | 8/4.8kV | 44F3 | Transformer #X35527 located at 20 Ralphpark isolated due to new sec buss install | Goulburn | Scheduled Outage | Construction
17441 | 2010 | 12 | 21 | 0.46181 |  | 20 | 4 | 11 | Janet King | 8/4.8kV | 44F3 | At 11:05 transformer X36436 at 20 Bell Street was isolated to allow crew to repair defective terminations. 11 customers were affected for 20 minutes. Janet King (44F3) ID#17441 | Goulburn | Scheduled Outage
12972 | 2008 | 7 | 30 | 0.39236 |  | 230 | 34 | 9 | BAYSHORE DS | 8/4.8kV | 46F6 | Transformer #NPTE0080 at 52 Horner Dr isolated to allow for pamount transformer change | Nepean | Scheduled Outage | Preventive Maintenance
9912 | 2007 | 1 | 9 | 0.68403 |  | 35 | 18 | 30 | Bells Coners | 8/4.8kV | 47F1 | While restoring 47F1 circuit L. Armstrong reports switch S1142 fuse opened, also S1141 opened causing outage to approx 30 customers. S1141 was reefused and closed restoring all load. L. Armstrong reports that the arrestor has blown at S1142. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9931 | 2007 | 1 | 16 | 0.39028 |  | 136 | 73 | 32 | Bells Corners | 8/4.8kV | 47F1 | Transformers TE934 & TE935 on Hadley Cr in nepean isolated to transfer conductor to new poles. | Gloucester | Scheduled Outage | Construction
7897 | 2006 | 2 | 6 | 0.45833 |  | 15 | 1 | 4 | Bells Corners | 8/4.8kV | 47F2 | Dave Jones opened transformer NP1070 at 11 Edgebrook to change connections. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
3253 | 2003 | 3 | 15 | 0.069444 |  | 99 | 412 | 250 | Bells Corners | 8/4.8kV | 47F2 | 47F2 auto/reclose/auto trip, feeder was sectionalized and no apperant cause found for trip. All load restored. | Nepean | Unknown/Other | No Apparent Cause
3297 | 2003 | 3 | 25 | 0.18056 |  | 39 | 162 | 250 | Bells Corners DS | 8/4.8kV | 47F2 | The Bells Corners 47F2 fdr tripped to lockout, 60 amps (approx 1 Mw) interrupted. Overhead section of fdr patrolled and no apparent trouble found. 47F2 breaker closed to restore feeder. | Nepean | Unknown/Other
3435 | 2003 | 5 | 13 | 0.84375 |  | 97 | 75 | 150 | Bell's Corners | 8/4.8kV | 47F2 | A defective termination caused the 47F2 breaker out of Bells Corners to trip to lockout. The defective termination or switch at S1480, Richmond at Robertson Roads, was isolated and the circuit returned to normal. See OTO#131-003 for restoration information. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10561 | 2007 | 6 | 8 | 0.72569 |  | 115 | 58 | 30 | Bells Corners | 8/4.8kV | 47F2 | Tree branches contacted the O/H on Bonner St in the Bells Corners traller park causing the fuse at switch S14 to open. The location where the trees made contact may be private O/H section. | Nepean | Tree Contacts | Inadequate Trimming
10764 | 2007 | 6 | 29 | 0.79097 |  | 91 | 11 | 7 | Bells Corners | 8/4.8kV | 47F2 | Broken Switch to transformer NP4080 at 5 Bonner St no cause found | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14926 | 2009 | 8 | 9 | 0.93472 |  | 404 | 13 | 2 | Bells Corners | 8/4.8kV | 47F2 | PC10A in effect on S1249 feeding TP5259 at 15 Roberson Rd, Local Hero's and Second Cup, isolated to allow crew to perform soil remediation. | Nepean | Scheduled Outage
3886 | 2003 | 8 | 10 | 0.63889 |  | 30 | 2 | 4 | Bell's Corners | 8/4.8kV | 47F2 | M. Brown reports No Apparent Cause for fuse cutout to open. Fuse replaced and closed. | Nepean | Unknown/Other | No Apparent Cause
16823 | 2010 | 8 | 28 | 0.32431 |  | 88 | 82 | 56 | Bells Corners |  | 47f2 | B1 bus insulator fault caused T1 white phase fuse blown 47F2 breaker open from SCADA control. Load restored fron Stafford F2. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
9141 | 2006 | 9 | 7 | 0.41528 |  | 142 | 71 | 30 | Bells Corners | 8/4.8kV | 47F2 | Single phase 8 Kv O/H line section on Kimberly dr isolated to transfer it to a new supply. | Nepean | Scheduled Outage
4045 | 2003 | 9 | 10 | 0.55972 |  | 60 | 1 | 1 | Bells Corners | 8/4.8kV | 47F2 | TE763 at the Bells Corners Fire Station was leaking and had to be replaced. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
15176 | 2009 | 9 | 27 | 0.63958 |  | 105 | 23 | 13 | Bells Corners | 8/4.8kV | 47F2 | Crew replaced defective arrestor and switch on Bonner St. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13430 | 2008 | 10 | 26 | 0.0013889 |  | 138 | 9 | 4 | Bells corners | 8/4.8kV | 47F2 | SC6936 on Richmond Rd was isolated and replaced due to gas level problems | Nepean | Scheduled Outage | Repair
9707 | 2006 | 11 | 23 | 0.28125 |  | 40 | 1 | 2 | Bellscorners | 8/4.8kV | 47F2 | Isolate transformer TE764 @ Richmond Lane-BC Public School and TE2428 @ 3825 Richmond to connect in cables. | Nepean | Scheduled Outage | Preventive Maintenance
5951 | 2004 | 11 | 29 | 0.29167 |  | 810 | 338 | 25 | Bell's Corners | 8/4.8kV | 47F2 | TE2408 on 47F2 circuit isolated to allow contractor to connect a new secondary switch. 25 Customers affected in planned outage. | Nepean | Scheduled Outage | Preventive Maintenance
3106 | 2003 | 1 | 11 | 0.03125 |  | 233 | 106 | 30 | Bells Corners DS |  | 47F3 | SW1053B was found blown including 2 bad elbows and a bad cable TE870 to TE869 cable was isolated and bad elbows were replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3111 | 2003 | 1 | 12 | 0.72014 |  | 73 | 24 | 20 | Bell's Corners DS | 8/4.8kV | 47F3 | Bushing on transfer leaking oil, caused tranformer to track to ground. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
3112 | 2003 | 1 | 13 | 0.54514 |  | 40 | 13 | 20 | Bells Corners DS | 8/4.8kV | 47F3 | Planned emergency repair to replace leaking transformer at 451 Moodie Drive. Customers notified. | Nepean | Scheduled Outage | Repair
11932 | 2008 | 1 | 13 | 0.60069 |  | 70 | 12 | 10 | Bells corners | 8/4.8kV | 47F3 | Defective secondary cable on transformer TE1 @ 3 Harwick st. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
6137 | 2005 | 1 | 15 | 0.81944 |  | 101 | 10 | 6 | Bells Corners | 8/4.8kV | 47F3 | Transformer at 38 Longwood isolated to make repairs to defective service. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7890 | 2006 | 2 | 4 | 0.92917 |  | 342 | 125 | 22 | Bells Corners | 8/4.8kV | 47F3 | Switch S464 at 33 Harwick in Bells Corners broke and fell open, switch replaced. | Nepean | Adverse Weather | Wind
6337 | 2005 | 3 | 30 | 0.28125 |  | 107 | 12 | 7 | Bells Corners | 8/4.8kV | 47F3 | Transformer #1030 isolated at 12 Ascot, Nepean possibly due to a squirrel | Nepean | Foreign Interference | Animal
14120 | 2009 | 3 | 30 | 0.74583 |  | 66 | 44 | 40 | Bells Corners | 8/4.8kV | 47F3 | Defective overhead transformer cutout caused pole fire at 32 Evergreen. 24/7 crews isolated damaged pole at S143 under a PC10A and made temporary repairs. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
14134 | 2009 | 4 | 2 | 0.38958 |  | 126 | 21 | 10 | Bells Corners | 8/4.8kV | 47F3 | At 9:21am isolated a transformer at 6 Edgebrook for PCB change, 10 customers were affected for 126min. Bells Corners (47F3). ID#14134. | Nepean | Scheduled Outage | Preventive Maintenance
14160 | 2009 | 4 | 9 | 0.58681 |  | 13 | 5 | 22 | Bells Corners | 8/4.8kV | 47F3 | Single phase O/H section of the 47F3 from tap at 17 Ascot to end of line isolated for tx replacement. 3 txs isolated on Ascot and Evergreen. | Nepean | Scheduled Outage | Repair
3357 | 2003 | 4 | 18 | 0.94444 |  | 79 | 8 | 6 | Bells Corners | 8/4.8kV | 47F3 | Fused disconnect blown due to defective line clamp. Clamp was replaced, sw refused and closed. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12378 | 2008 | 5 | 2 | 0.39236 |  | 35 | 2 | 4 | Bells Corners | 8/4.8kV | 47F3 | Transformer #NP000990 at 32 Stinson isolated to allow for service upgrade | Nepean | Scheduled Outage | Construction
8396 | 2006 | 6 | 1 | 0.81806 |  | 577 | 2204 | 315 | Bells Corners | 8/4.8kV | 47F3 | Lightning strike fallen tree 3 burnt transformer connects and a recloser that could not be operated. | Nepean | Lightning | Direct Strike
16262 | 2010 | 6 | 14 | 0.48819 |  | 217 | 4 | 1 | Bells Corners | 8/4.8kV | 47F3 | TE1441 at 50 Cassidy replaced due to oil leak. Only the one customer, a City of Ottawa building, was affected & they ran on generator during the outage. Nomenclature changed to TP7310. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16312 | 2010 | 6 | 22 | 0.018056 |  | 154 | 26 | 10 | Bells Corners | 8/4.8kV | 47F3 | 47F3 auto reclosed, due to racoon making contact with transformer. | Nepean | Foreign Interference | Animal
20866 | 2012 | 6 | 25 | 0.37708 |  | 125 | 19 | 9 | Bells Corner | 8/4.8kV | 47F3 | Replaced blown fuse feeding transformer X39546 at 7 Floral Pl | Nepean | Tree Contacts | Inadequate Trimming
12729 | 2008 | 6 | 26 | 0.065972 |  | 269 | 380 | 311 | Bells Corners | 8/4.8kV | 47F3 | Tree limb came into contact with dead end pole at rear of 4 Grangemill causing a pole fire. The circuit auto reclosed once & 5 minutes later tripped & locked out. The damaged section was isolated & O/C crew called in to make repairs. | Nepean | Tree Contacts | Tree Limb Fallen
14626 | 2009 | 6 | 27 | 0.97917 |  | 125 | 80 | 50 | Bells Corners | 8/4.8kV | 47F3 | Possible lightning strike at Tx 40037, 24 Cedarbank caused S478 to blow also. Line patrolled, S478 replaced then fuse to Tx X40037 rreplaced. | Nepean | Adverse Weather | Lightning
20889 | 2012 | 6 | 27 | 0.39028 |  | 189 | 132 | 42 | Bells Corners | 8/4.8kV | 47F3 | 47F3 section from S143 to EOL to include S143 was isolated to allow crew to replace crossarms and allow contractor to remove a tree from primary. | Nepean | Scheduled Outage | Repair
6838 | 2005 | 7 | 1 | 0.63264 |  | 59 | 481 | 489 | Bells Corners | 8/4.8kV | 47F3 | A tree fell into wires at 39 Evergreen. | Nepean | Tree Contacts | Tree Limb Fallen
20921 | 2012 | 7 | 4 | 0.36528 |  | 21 | 2 | 6 | Bells Corners DS | 8/4.8kV | 47F3 | Transformer NP000546 at 5 Evergreen isolated for Microfit | Nepean | Scheduled Outage | Construction
16456 | 2010 | 7 | 11 | 0.67361 |  | 81 | 9 | 7 | Bells Corners | 8/4.8kV | 47F3 | Transformer X39542 @ rear of 15 Ridgefield was opened to replace faulty triplex. | Nepean | Defective Equipment
3839 | 2003 | 8 | 4 | 0.14583 |  | 37 | 123 | 200 | Bells Corners | 8/4.8kV | 47F3 | Tree limb contacted overhead circuit at 76 Stinson. Limb was removed and load was restored. | Nepean | Tree Contacts | Tree Limb Fallen
7158 | 2005 | 8 | 18 | 0.34306 |  | 240 | 240 | 60 | Bells Corners | 8/4.8kV | 47F3 | Overhead section was isolated to remove a large tree threatening the overhead, too close for removal without isolation | Nepean | Scheduled Outage | Preventive Maintenance
18980 | 2011 | 8 | 19 | 0.39583 |  | 266 | 18 | 4 | Bells Corners | 8/4.8kV | 47F3 | Transformer TP7310 was isolated to allow crew to transfer plant to new pole. | Nepean | Scheduled Outage | Preventive Maintenance
16824 | 2010 | 8 | 28 | 0.31736 |  | 121 | 135 | 67 | Bells Corners | 8/4.8kV | 47F3 | 47F3 auto reclosed and opened. Cause found to be bus insulators broken and T1 white phase fuse blown. 47F3 load picked up from QCH F3 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16925 | 2010 | 9 | 12 | 0.46181 |  | 80 | 67 | 50 | Munster | 8/4.8kV | 47F3 | customers reported outage on Munster rd, south of Franktown, patrol found & clerared limbs from O/H on Jock Trail East of Green. S15839 refused and closed. | Goulburn | Tree Contacts | Tree Limb Fallen
19172 | 2011 | 9 | 13 | 0.73194 |  | 531 | 319 | 36 | Bells Corners | 8/4.8kV | 47F3 | Large tree limb had fallen behind 38 Evergreen. Forestry crew called in to relimb, then power restored. | Nepean | Tree Contacts | Tree Limb Fallen
9351 | 2006 | 9 | 30 | 0.49931 |  | 167 | 6 | 2 | Bells Corners | 8/4.8kV | 47F3 | TE760 and TE761 isolated to allow crew to replace O/H switch and upgrade transformers. | Nepean | Scheduled Outage | Construction
17062 | 2010 | 10 | 5 | 0.88819 |  | 93 | 6 | 4 | Bells Corners DS | 8/4.8kV | 47F3 | Transformer X39895 AT 33 Ridgefield refused due to animal contact | Nepean | Foreign Interference | Animal
4252 | 2003 | 10 | 13 | 0.79931 |  | 109 | 15 | 8 | Bell's Corners | 8/4.8kV | 47F3 | 24/7 reports cause as due to age. Replaced fuse cutout, and arrester on overhaed transformer. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
7466 | 2005 | 10 | 16 | 0.51806 |  | 44 | 356 | 486 | Bell's Corner | 8/4.8kV | 47F3 | 47F3 circuit auto reclosed & locked out. D. Provost & G. McGee dispatched. 26 Ridgefield reports heard 2 bangs at this location. D. Provost reports limb across two phases at this location. Limb removed 47F3 closed and holding. | Nepean | Tree Contacts | Tree Limb Fallen
11567 | 2007 | 10 | 21 | 0.62361 |  | 52 | 43 | 50 | Bells Corners | 8/4.8kV | 47F3 | Switch 478 failed & was replaced. Homes on Harwick, Cedarbank & Longwood were affected. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13524 | 2008 | 10 | 29 | 0.37153 |  | 105 | 63 | 36 | STAFFORD | 8/4.8kV | 47F3 | PC10A #1819 established by P.Barr at S1354 to repaired downed primary | Nepean | Adverse Weather | Wind
9825 | 2006 | 12 | 11 | 0.23056 |  | 24 | 3 | 7 | Bells Corners | 8/4.8kV | 47F3 | Customer reported sparking wires, bad connection on the secondary bus repaired, | Nepean | Defective Equipment | Equipment Deterioration Due to Age
9881 | 2006 | 12 | 24 | 0.47222 |  | 87 | 450 | 310 | Bells Corners | 8/4.8kV | 47F3 | Breaker trip caused by tree limb on wires behind Bell High School, limb removed and power restored. | Nepean | Tree Contacts | Tree Limb Fallen
4658 | 2003 | 12 | 27 | 0.49653 |  | 54 | 14 | 16 | Bells Corners | 8/4.8kV | 47F3 | B phase switch 997 on Richmond Rd in Bells Corners defective, transformer TE1 interupted. Switch replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11918 | 2008 | 1 | 9 | 0.65694 |  | 129 | 64 | 30 | Bells Corners | 8/4.8kV | 47F4 | A burnt hot line clamp at switch 533 at 29 Cherrywood. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3102 | 2003 | 1 | 10 | 0.98958 |  | 58 | 290 | 300 | Bell's Corners DS | 8/4.8kV | 47F4 | The 47F4 cables were isolated by the CA's and load was picked up 47F3 via switch 297. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3118 | 2003 | 1 | 14 | 0.54167 |  | 105 | 14 | 8 | Bells Corners DS | 8/4.8kV | 47F4 | Planned outage to replace transformer TE870. | Nepean | Scheduled Outage
15669 | 2010 | 1 | 19 | 0.37917 |  | 178 | 44 | 15 | Bells Corner | 8/4.8kV | 47F4 | The 47F4 O/H line on Quinpool Cr was isolated to allow crews to replace insulators and xarms. | Nepean | Scheduled Outage | Preventive Maintenance
17510 | 2011 | 1 | 23 | 0.63958 |  | 59 | 3 | 3 | Bells Corner | 8/4.8kV | 47F4 | replaced broken fuse at transformer X39871 at the rear of 45 Cherrywood Dr | Nepean | Defective Equipment | Equipment Deterioration Due to Age
19958 | 2012 | 2 | 3 | 0.55208 |  | 24 | 9 | 23 | Bells Corners | 8/4.8kV | 47F4 | Transformer NPTE0002 at 41 Longwood Ave. isolated to allow for replacement of switch S686 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6203 | 2005 | 2 | 11 | 0.92708 |  | 463 | 54 | 7 | Bells Corners | 8/4.8kV | 47F4 | Primary bushing on transformer at 13 Cherrywood Dr broke. On call crew replaced tx. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3241 | 2003 | 3 | 12 | 0.37639 |  | 184 | 202 | 66 | Bells Corners | 8/4.8kV | 47F4 | Planned interuption to transformers TE863, TE864 and TE865 to replace defective elbows and inserts on the transformers and change one transformer.. | Nepean | Scheduled Outage | Repair
3243 | 2003 | 3 | 12 | 0.54375 |  | 57 | 68 | 72 | Bells Corners | 8/4.8kV | 47F4 | Planned outage to transformers TE869, TE870 & TE871 to replace defective transformer elbows and inserts. | Nepean | Scheduled Outage | Repair
3247 | 2003 | 3 | 13 | 0.38194 |  | 142 | 118 | 50 | Bell's Corners | 8/4.8kV | 47F4 | TE866, TE867, & TE868 white phase transformers isolated to repair elbows & replace inserts. A customers were notified of outage. | Nepean | Scheduled Outage | Preventive Maintenance
8020 | 2006 | 3 | 14 | 0.020833 |  | 165 | 19 | 7 | Bells Corners | 8/4.8kV | 47F4 | Transformer 905 at 125 Ridgefield blown cut out replaced. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4907 | 2004 | 3 | 17 | 0.27083 |  | 121 | 60 | 30 | Bell"s corners | 8/4.8kV | 47F4 | S183 switch failed due to age. Causing outage to 30 customers. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4984 | 2004 | 4 | 8 | 0.50347 |  | 47 | 39 | 50 | Bell's Corners | 8/4.8kV | 47F4 | Crew reports outage caused be a squirrell which blow a fuse at S533. Fuse was replaced restoring all customers. | Nepean | Foreign Interference | Animal
10402 | 2007 | 5 | 10 | 0.625 |  | 15 | 2 | 8 | Bells Corners | 8/4.8kV | 47F4 | Steve Muldoon isolated TRF. 4557 @ 64 Ridgefield to repair defective connection at terminal bar | Nepean | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
3473 | 2003 | 5 | 24 | 0.375 |  | 157 | 8 | 3 | Bells Corners | 8/4.8kV | 47F4 | H1 bushing blown. New bushing installed. Mtce report to be filled by Mike M for tx repacement at a later date. | Nepean | Defective Equipment
18257 | 2011 | 5 | 31 | 0.44444 |  | 10 | 2 | 15 | Bells Corner | 8/4.8kV | 47F4 | Isolated transformer X39854 at 55 Ridgefield Cres and replaced switch,arrester, and bracket | Nepean | Defective Equipment | Imminent Equipment Failure Detected
8419 | 2006 | 6 | 4 | 0.70486 |  | 75 | 22 | 18 | Bells Corners | 8/4.8kV | 47F4 | Transformer TE865 at 481 Moodie Dr isolated to repair service and change elbow. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8442 | 2006 | 6 | 7 | 0.50833 |  | 68 | 49 | 200 | Bells Corners | 8/4.8kV | 47F4 | A limb fell from the tree making contact from the primary to the neutral at 61 Cherrywood Drive. 47F4 circuit was on hold off, and S533 fuse blew. | Nepean | Human Element
10645 | 2007 | 6 | 18 | 0.32222 |  | 91 | 121 | 80 | Bell's Corner's | 8/4.8kV | 47F4 | Overhead section fed from S533 Fused Switch opened due to tree contact affecting Ridgefield & Cherrywood Drive, Nepean | Nepean | Tree Contacts | Inadequate Trimming
3702 | 2003 | 6 | 25 | 0.83333 |  | 281 | 937 | 200 | Bells Corners | 8/4.8kV | 47F4 | Primary circuit was on the ground, broke away from insulator. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5591 | 2004 | 7 | 31 | 0.57431 |  | 145 | 24 | 10 | Bells Corners | 8/4.8kV | 47F4 | Transformer 0079 at 69 Ridgefield Cresent, fuse replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8874 | 2006 | 7 | 31 | 0.37986 |  | 76 | 6 | 5 | Bells Corners | 8/4.8kV | 47F4 | Fuse to transformer NP4546 at 6 Cherrywood Dr was found blown due to a bird contact crew replaced the fuse and restored power | Nepean | Foreign Interference | Bird
3848 | 2003 | 8 | 6 | 0.16528 |  | 82 | 27 | 20 | Bell's Corners | 8/4.8kV | 47F4 | D. Jones reports S839 switch found broken. Equipment Failure - Cause Unknown | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15015 | 2009 | 8 | 27 | 0.39583 |  | 105 | 5 | 3 | Bells Corner | 8/4.8kV | 47F4 | Isolated transformer X39631 at 24 Quinpool Cres for service up-grade | Nepean | Scheduled Outage | Emergency Services Request
15016 | 2009 | 8 | 27 | 0.39583 |  | 105 | 5 | 3 | BELL CORNERS | 8/4.8kV | 47F4 | Transformer X39631 at 24 Quinpool isolated to allow for repairs | Nepean | Scheduled Outage | Repair
3971 | 2003 | 8 | 29 | 0.94097 |  | 145 | 19 | 8 | Bell's Corners | 8/4.8kV | 47F4 | D. Guy reports transformer fuse found open. Fuse was replaces restoring power. | Kanata | Unknown/Other | No Apparent Cause
19039 | 2011 | 8 | 29 | 0.40625 |  | 50 | 21 | 25 | BELLS CORNERS | 8/4.8kV | 47F4 | te866 AT 475 Moodie isolated to replace leaking transformer. | Nepean | Scheduled Outage
15039 | 2009 | 8 | 31 | 0.39931 |  | 144 | 24 | 10 | Bells Corners | 8/4.8kV | 47F4 | Transformer #X39878 located at 9 Aberfeldy isolated for a PCB change | Nepean | Scheduled Outage | Construction
15042 | 2009 | 8 | 31 | 0.68958 |  | 72 | 10 | 8 | Bells Corners | 8/4.8kV | 47F4 | Replaced broken switch at transformer X39854 at the rear of 55 Ridgefield Cres | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19157 | 2011 | 9 | 13 | 0.40278 |  | 462 | 192 | 25 | Bells Corners | 8/4.8kV | 47F4 | Transformer TE866 @ 475 Moodie was isolated to allow crew to install a new base and update grounding. | Nepean | Scheduled Outage | Preventive Maintenance
19179 | 2011 | 9 | 14 | 0.37361 |  | 32 | 3 | 5 | Bells Corners | 8/4.8kV | 47F4 | Transformer X39873 isolated to connect secondary services. | Nepean | Scheduled Outage | Construction
19334 | 2011 | 10 | 6 | 0.40556 |  | 458 | 191 | 25 | Bells Corners | 8/4.8kV | 47F4 | At 9:44 crews isolated TE871 to replace a leaking transformer at 467 Moodie. 25 customers affected for 458 mins. Bells Corners 47F4 ID# 19334 | Nepean | Scheduled Outage
19339 | 2011 | 10 | 7 | 0.44444 |  | 70 | 32 | 27 | Bells Corners | 8/4.8kV | 47F4 | At 10:40am crews isolated TE870 at 459 Moodie to replace the transformer. 27 customers affected for 70 mins. Bells Corners 47F4 ID# 19339 | Nepean | Scheduled Outage
5841 | 2004 | 10 | 12 | 0.35903 |  | 101 | 67 | 40 | Bells Corners | 8/4.8kV | 47F4 | All out residential determined cause to be blown arrestor. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
5845 | 2004 | 10 | 13 | 0.875 |  | 60 | 8 | 8 | Bells Corners | 8/4.8kV | 47F4 | a Bad secondary connection in the transformer @ TE1269, 23 Cheerywood Dr. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9496 | 2006 | 10 | 23 | 0.80556 |  | 45 | 11 | 15 | Bells Corners | 8/4.8kV | 47F4 | Transformer #NP004548 located at 57 Ridgefield isolated due to broken fuse | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19481 | 2011 | 10 | 27 | 0.39722 |  | 462 | 208 | 27 | Bells Corners |  | 47F4 | TE870 at 459 Moodie isolated to clean oil leak and install new transformer base. | Nepean | Scheduled Outage
11645 | 2007 | 11 | 1 | 0.73403 |  | 30 | 2 | 5 | Bells corners | 8/4.8kV | 47F4 | 47F4 overhead section between S385 & S386 was isolated to include transformer T4324 to repair secondary. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
11830 | 2007 | 12 | 11 | 0.72917 |  | 95 | 872 | 551 | Bells Corners | 8/4.8kV | 47F4 | 47F4 feeder auto tripped due to a faulted primary cable. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13820 | 2008 | 12 | 30 | 0.25625 |  | 1097 | 352 | 56 | Bells Corners | 8/4.8kV | 47F4 | A tree fell onto the conductor of the 47F4 feeder causing 2 poles to break and S533 fuses to open. The 2 poles, conductor and 1 transformer had to be replaced causing extended outage times. | Nepean | Adverse Weather | Wind
9909 | 2007 | 1 | 9 | 0.51736 |  | 125 | 17 | 8 | Bells Corners | 8/4.8kV | 47F6 | Replaced transformer 3059 at 572 Moodie Dr (Upgrade) | Nepean | Scheduled Outage | Preventive Maintenance
12048 | 2008 | 2 | 15 | 0.43889 |  | 232 | 3521 | 925 | Bells Corners | 8/4.8kV | 47F6 | At 10:32 am Bells Corners 47F6 auto-reclosed. 24/7 located blown white phase fuse @ S1177; caused by vehicle/snow-plow contact to padmount TE1310. Padmount isolated & crew called in to replace damaged transformer. | Nepean | Foreign Interference | Vehicle
14011 | 2009 | 2 | 27 | 0.25 |  | 15 | 2 | 7 | Bells Corners | 8/4.8kV | 47F6 | 3 phase O/H transformer NPTE 00698 at 999 Moodie was opened to replace a defective hot line clamp. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
17736 | 2011 | 3 | 18 | 0.475 |  | 108 | 18 | 10 | Bells Corner DS | 8/4.8kV | 47F6 | Transformer X39859 at 10 Elmsley Cres. Refused - squirrell contact | Nepean | Foreign Interference | Animal
14128 | 2009 | 4 | 1 | 0.42014 |  | 110 | 7 | 4 | Bells Corners | 8/4.8kV | 47F6 | Transformer #X39785 and X39784 located at 129 & 125 Ridgefield Cres isolated due to pole replacement | Nepean | Scheduled Outage | Preventive Maintenance
17902 | 2011 | 4 | 11 | 0.65625 |  | 84 | 861 | 615 | Bells Corner | 8/4.8kV | 47F6 | Circuit auto re-closed and then later auto re-closed and locked out. System closed the breaker via SCADA suspecting the cause being inclement weather. The circuit held for 40 min. And then auto re-closed and locked out again. Crews found a fallen tree limb on the overhead at 4061 Richmond Rd. Limb was removed and circuit restored. | Ottawa | Tree Contacts | Tree Limb Fallen
3337 | 2003 | 4 | 12 | 0.97917 |  | 32 | 107 | 200 | Bell's Corners | 8/4.8kV | 47F6 | Insulator at the rear of 58 Forest View cres failed. Section of overhead isolated to replace defective insulator. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12304 | 2008 | 4 | 19 | 0.34028 |  | 286 | 5 | 2 | Bells Corners | 8/4.8kV | 47F6 | Hydro Ottawa crew isolated customer owned line fed from S79 to replace a pole for the customer. The main customer affected was Lafarge Canada Inc. at 998 Moodie, but there was also an MCI tower affected fed off the customer line. | Nepean | Scheduled Outage | Repair
6537 | 2005 | 5 | 11 | 0.10278 |  | 166 | 1065 | 450 | Bells Corners | 8/4.8kV | 47F6 | 47F6 feeder trip, a broken top pin insulator found on Richmond Rd, same replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18170 | 2011 | 5 | 17 | 0.51736 |  | 16 | 3 | 11 | Bells Corners | 8/4.8kV | 47F6 | TP1306 isolated to allow crew to move transformer back on base after being hit by a snowplow during winter. | Nepean | Scheduled Outage | Repair
20547 | 2012 | 5 | 21 | 0.43403 |  | 35 | 2 | 3 | Bell's Corners | 8/4.8kV | 47F6 | Transformer #X39789 located at 43 Sycamore Dr opened by crew to replace switch and arrestor. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
8393 | 2006 | 5 | 31 | 0.93125 |  | 122 | 41 | 20 | Bells Corners | 8/4.8kV | 47F6 | 24/7 have found S19 at Twin Elm and Strandherd, all three phases blown open. Customers reports lightning strike and loud bang just before power out. New fuses installed and closed | Nepean | Lightning | Direct Strike
20701 | 2012 | 6 | 5 | 0.66597 |  | 81 | 4 | 3 | Bells Corner | 8/4.8kV | 47F6 | Replaced blown fuse feeding transformer X40030 at 11 Arnold Dr | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6676 | 2005 | 6 | 7 | 0.375 |  | 170 | 3 | 1 | Bells Corners | 8/4.8kV | 47F6 | Isolated transformer 4624 at 61 Quinpool to replace pole | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12667 | 2008 | 6 | 16 | 0.42014 |  | 122 | 16 | 8 | Bells Corners | 8/4.8kV | 47F6 | Transformer TP3527 @ 131 Songbird Pvt was isolated to pull in secondary cables. | Nepean | Scheduled Outage | Preventive Maintenance
18545 | 2011 | 6 | 28 | 0.48333 |  | 314 | 89 | 17 | Bells Corner | 8/4.8kV | 47F6 | Transformer TE1318 @ 29 Forester was isolated to allow crew to replace transformer, elbows and inserts. 17 customers were affected. Bellscorner (47F6) | Nepean | Scheduled Outage | Repair
18546 | 2011 | 6 | 28 | 0.41181 |  | 295 | 84 | 17 | Bells Corners | 8/4.8kV | 47F6 | Transformer TE1312 @ 21 Forester was isolated to allow crew to replace transformer,elbows and inserts. 17 customers were affected. Bellscorner (47F6) | Nepean | Scheduled Outage
18580 | 2011 | 7 | 4 | 0.89653 |  | 515 | 686 | 638 | Bells Corners | 8/4.8kV | 47F6 | Transformer TE1311 one of the inserts blew out. Crew replaced the defective transformer. Bells Corners (47F6) ID#18580 | Nepean | Defective Equipment
8674 | 2006 | 7 | 6 | 0.38542 |  | 97 | 11 | 7 | Bells Corners | 8/4.8kV | 47F6 | Isoalated transformer NPE598 at 17 Arnold St to replace connections on the secondary side of the transformer | Nepean | Scheduled Outage | Preventive Maintenance
14673 | 2009 | 7 | 6 | 0.40972 |  | 20 | 1 | 2 | Bells Corners | 8/4.8kV | 47F6 | Transformer #X39806 located at 1027 Moodie isolated due to tree interference | Nepean | Tree Contacts | Inadequate Trimming
18644 | 2011 | 7 | 12 | 0.39583 |  | 210 | 60 | 17 | Bells Corners | 8/4.8kV | 47F6 | Trans at 29 Forester Cres was isolated was pole change | Nepean | Scheduled Outage
18646 | 2011 | 7 | 12 | 0.40347 |  | 399 | 27 | 4 | Bells Corners | 8/4.8kV | 47F6 | TP8942 @ 29 forester was isolated to replace transformer base and clean up oil. | Nepean | Scheduled Outage | Repair
5494 | 2004 | 7 | 14 | 0.67639 |  | 51 | 1 | 1 | Bell's Corner | 8/4.8kV | 47F6 | There was a broken switch that feeds transformer 151 at Richmond Rd and Seyton that feeds traffic lights. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18737 | 2011 | 7 | 17 | 0.83333 |  | 1824 | 2280 | 75 | Bells Corners | 8/4.8kV | 47F6 | S672 found blown. Cleared branch on Overhead line. Refused and flosed. Arnold/Sycamore/Trevor | Nepean | Tree Contacts | Tree Limb Fallen
16494 | 2010 | 7 | 19 | 0.46667 |  | 85 | 3 | 2 | Bells Corners | 8/4.8kV | 47F6 | S819 at 4420 West Hunt Club Rd was opened to isolate customer overhead line to remove tree branches. 2 customers affected were Lone Star Ranch & a Bell Mobility Tower. | Nepean | Tree Contacts
18803 | 2011 | 7 | 23 | 0.74861 |  | 466 | 2261 | 638 | Bells Corners | 8/4.8kV | 47F6 | At 17:58 47F6 tripped open. Ottawa fire reported down conductor on Moodie South of Hunt Club. Upon isolation of the fault we tried to pick up the line with the breaker. SCADA indicated a SBO relay fail and the Breaker would not close. Load was picked up from the 200F5 at Stafford Road. 638 customers affected for 204 mins. | Nepean | Tree Contacts | Tree Fallen
8824 | 2006 | 7 | 25 | 0.28333 |  | 87 | 3 | 2 | Bells Corner | 8/4.8kV | 47F6 | Switch to transformer NP1201 at 3610 Twin Elm was found broken crew replaced the switch and restored power | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18831 | 2011 | 7 | 26 | 0.67361 |  | 61 | 1 | 1 | Bells corners | 8/4.8kV | 47F6 | transformer 505 at 595 moodie was isolated to check voltage issues and repair burnt hot line clamp. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
18889 | 2011 | 8 | 7 | 0.59792 |  | 39 | 4 | 6 | Bells Corner | 8/4.8kV | 47F6 | Replaced blown fuse feeding transformer X39859 at Elmsley Cres (Squirrel contact) | Nepean | Foreign Interference | Animal
18894 | 2011 | 8 | 8 | 0.52431 |  | 75 | 11 | 9 | Bells Corner | 8/4.8kV | 47F6 | Replaced blown fuse fro transformer X39859 at 10 Elmsley Cres (Squirrel contact) | Nepean | Foreign Interference | Animal
5652 | 2004 | 8 | 10 | 0.79722 |  | 875 | 73 | 5 | Bells Corners | 8/4.8kV | 47F6 | 47F6 auto reclosed lightning in the area. TE1119 transformer was replaced by on call crew. | Nepean | Adverse Weather | Lightning
5665 | 2004 | 8 | 11 | 0.44792 |  | 320 | 5 | 1 | Bell's Corners | 8/4.8kV | 47F6 | P. Barr reports S1553 R&W fuses oped B fuse found opened on arrivel. Transformer TE2110 isolated due to flash mark on bushing. | Nepean | Adverse Weather | Lightning
5691 | 2004 | 8 | 18 | 0.37639 |  | 198 | 33 | 10 | Bells Corners | 8/4.8kV | 47F6 | TE1119 removed from service to remove contaminated soil from earlier oil spill. | Nepean | Scheduled Outage | Repair
13135 | 2008 | 8 | 21 | 0.41667 |  | 245 | 4 | 1 | Bells Corners | 8/4.8kV | 47F6 | A portion of a City of Ottawa yard at 1159 Moodie was isolated from a 15kva transformer X34799 to clear and replace a damaged meter base and replace a broken cut out at X5874 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19170 | 2011 | 9 | 13 | 0.73403 |  | 402 | 47 | 7 | Bell Corners | 8/4.8kV | 47F6 | Tree limb had to be removed from overhead and S671 closed. | Nepean | Tree Contacts | Tree Limb Fallen
9271 | 2006 | 9 | 21 | 0.46667 |  | 213 | 18 | 5 | Bells Corners | 8/4.8kV | 47F6 | Transformer NP001457 located at 4475 Trail Rd isolated to install new pole | Nepean | Scheduled Outage | Construction
11603 | 2007 | 10 | 26 | 0.41389 |  | 139 | 14 | 6 | BELLS CORNERS | 8/4.8kV | 47F6 | TP3527 at 123 Songbird isolated to pull in secondaries | Nepean | Scheduled Outage | Construction
13461 | 2008 | 10 | 28 | 0.92986 |  | 200 | 3233 | 970 | Bells Corners | 8/4.8kV | 47F6 | A Cooney rpts S1176 open, 47F6 closed & holding | Nepean | Adverse Weather
13580 | 2008 | 11 | 8 | 0.95069 |  | 66 | 4 | 4 | Bells Corner | 8/4.8kV | 47F6 | Transformer fuse opened up, no apperent cause crew refused and change LLC. At 560 Moodie dr. | Nepean | Unknown/Other
7614 | 2005 | 11 | 14 | 0.90417 |  | 303 | 5 | 1 | Bells Corners | 8/4.8kV | 47F6 | The R phase cable termination at dip switch S11168 burnt and had to be replaced. Transformer TE795 at the church at 3955 Richmond Rd which is fed by defective cable was interrupted to make repairs. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7621 | 2005 | 11 | 16 | 0.42639 |  | 238 | 48 | 12 | BELLS CORNER | 8/4.8kV | 47F6 | BELLS CORNERS (47F6) AUTO-RECLOSE, DOUG MCKAY PATROLLING CIRCUIT. CUSTOMER REPORTS SPARKS IN FRONT YARD OF 62 ARNOLD ST. DOUG FOUND TREES ON THE SINGLE PHASE RUN OFF S672 AND A OPENED FUSE @ S672. DOUG PROCEEDED TO REMOVE TREES AND REPLACE FUSE. | Nepean | Adverse Weather | Wind
11778 | 2007 | 11 | 27 | 0.69722 |  | 48 | 3 | 4 | Bells corners | 8/4.8kV | 47F6 | Section of 47F6 circuit on Moodie dr. between S1019,S344 and S1182 was isolated to remove tree from primary. | Nepean | Tree Contacts | Tree Limb Fallen
13702 | 2008 | 12 | 4 | 0.81528 |  | 161 | 46 | 17 | Bells corners | 8/4.8kV | 47F6 | the fuse barrel burnt on single phase Fused switch S129 on Sycamore in Nepean causing fuse to open feeding three transformers. Crew had to jump out switch due to lack of parts to restore power. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
4664 | 2003 | 12 | 30 | 0.010417 |  | 63 | 63 | 60 | BellsCorners | 8/4.8kV | 47F6 | Lightning arrester boke and fell into switch 949R and broke switch. Switch and arrester repair and customers back on. | Nepean | Defective Equipment
18576 | 2011 | 7 | 3 | 0.80208 |  | 350 | 117 | 20 | Uplands | 27.6/16kV | 4801 F8 | Lid blew off transformer X13785 at 1464 Goth, transformer then caught fire. On call crew called in to replace defective Tx. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14124 | 2009 | 3 | 31 | 0.39236 |  | 180 | 15 | 5 | Uplands | 27.6/16kV | 4801/F8 | Transformer #X13581 located at Maple Key & Albion isolated for an upgrade | Gloucester | Scheduled Outage | Preventive Maintenance
12050 | 2008 | 2 | 16 | 0.0090278 |  | 597 | 10 | 1 | Uplands | 27.6/16kV | 4801F7 | The 4801F7 autoreclosed, waiting for calls to come. P. Breoron reports 5 Bell Cables are pulled off Hydro pole, and 4801F7 circuit neutral is also pulled down @ 08:15. Dispatch reports 2320 Lessiter is out of power since last night. After hours call center put message on RAN stating outage in the Uplands area. NRC failed to report outage after hearing message on RAN. NRC transformer # U89 | Gloucester | Unknown/Other
4857 | 2004 | 3 | 4 | 0.59375 |  | 45 | 8 | 11 | Uplands | 27.6/16kV | 4801F7 | G775 had 3 blown fuses due to parallel on secondary without parallel on primary.11 transformers at the airport out of service. Mistake on switching order not an error by switching Crew. | Gloucester | Human Element | Switching Errors
4924 | 2004 | 3 | 21 | 0.45833 |  | 127 | 2 | 1 | Uplands | 27.6/16kV | 4801F7 | O/H section of the 4801F7 along Canook (private) between Lester & Alert isolated to replace tracking insulators and burnt crossarm. Transformers 173, 615, 218 & 3271 interupted affecting one customer NRC. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20686 | 2012 | 6 | 3 | 0.46458 |  | 74 | 1 | 1 | Uplands |  | 4801F7 | 27kV fuse G656 at Alert and Lancaster opened, no cause found. | Gloucester | Unknown/Other | No Apparent Cause
8879 | 2006 | 8 | 1 | 0.048611 |  | 205 | 1755 | 595 | Uplands | 27.6/16kV | 4801F7 | Uplands T3 high and low side tripped and F7 and F8 breakers. | Gloucester | Adverse Weather | Lightning
5808 | 2004 | 9 | 15 | 0.34097 |  | 25 | 7 | 17 | Uplands MTS | 27.6/16kV | 4801F7 | Squirrel contact on 72B1-B2 bus tie switch @ Merivale MS tripped both 115kV supply circuits. Uplands MTS may have overtripped. Stations advised. See Int #5809 | Gloucester | Foreign Interference | Animal
15131 | 2009 | 9 | 19 | 0.4375 |  | 30 | 0 | 1 | Uplands | 27.6/16kV | 4801F7 | at 9:08am, Customer called with outage at NRC-U89. Crews patrolled line and found G656-B & S17903-B openned. NRC-U89 is a customer owned Sub, fault is with there equipment, informed customer to call a qualified HV electrician, Sub Isolated from S17903. Part outage for 2hrs prior to isolation. Cutler- Hammer has determined that a 1P 500KVA, 16/4.8 - 347 Transformer will need to be replaced. | Gloucester | Unknown/Other
15148 | 2009 | 9 | 20 | 0.45833 |  | 60 | 1 | 1 | Uplands | 27.6/16kV | 4801F7 | Replaced a 500KVA, 16/4.8 - 347 Transformer at U86 @ 2320 Lester Rd. Restored Sept. 22, 2009 @ 16:46 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15373 | 2009 | 11 | 9 | 0.41458 |  | 33 | 1 | 1 | Uplands | 27.6/16kV | 4801F7 | Tree contact caused blue phase to open at G656, crews isolated RWB and the tree contact and untangled the conductor | Gloucester | Tree Contacts
14034 | 2009 | 3 | 11 | 0.50347 |  | 41 | 1 | 4 |  |  | 4801-F7 | damaged cut out was tracking, reported by customer, interuption was required to isolate damaged cut out, all cutomers are on a single NRC campus, 1 building was left out while the cut out was replaced | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10140 | 2007 | 3 | 15 | 0.52292 |  | 77 | 287 | 500 | Uplands | 27.6/16kV | 4801F7, F8 | 4801F7 tripped due to a cable fault on the trunk feeder at the cable dip under the Airport Parkway. The high fault current caused the 4801T3Z breaker to open also which removed supply to the 4801F8 feeder. The station was inspected & power restored to 4801F8, then 4801F7 was sectionalized & patrolled to restore power. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14015 | 2009 | 2 | 28 | 0.90764 |  | 313 | 21 | 4 | Uplands DS | 27.6/16kV | 4801F8 | Transformer T1724W at 3757 Autumnwood St was isolated to allow crew to replace a defective transformer | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20167 | 2012 | 3 | 15 | 0.50694 |  | 9 | 672 | 4477 | Uplands | 27.6/16kV | 4801F8 | 4801F8 breaker opened. RTU was shutdown at Uplands. Calls came in on OMS. No targets at staion, 4801F8 closed manually and held. | Gloucester | Unknown/Other
14125 | 2009 | 3 | 31 | 0.38681 |  | 191 | 19 | 6 | UPLANDS | 27.6/16kV | 4801F8 | TP3344 @ 174 Maple key was isolated from Hydro Ottawa sources for contractor to replace damaged grounding grid. | Gloucester | Scheduled Outage | Repair
14146 | 2009 | 4 | 6 | 0.33125 |  | 138 | 12 | 5 | Uplands | 27.6/16kV | 4801F8 | T1148 on Uplands dr. isolated to allow crews to replace the transformer and change nomenclature to TP6681 | Ottawa | Scheduled Outage | Repair
17853 | 2011 | 4 | 7 | 0.37778 |  | 464 | 62 | 8 | Uplands | 27.6/16kV | 4801F8 | TE1457 at 2554 Hunters Point was isolated to allow crews to replace the leaking transformer. | Gloucester | Scheduled Outage | Repair
15931 | 2010 | 4 | 13 | 0.37847 |  | 145 | 72 | 30 | Uplands | 27.6/16kV | 4801F8 | TE1475 and TE1476 on Pimlico isolated to repair secondary connections and replace elbows | Gloucester | Scheduled Outage
15945 | 2010 | 4 | 16 | 0.37847 |  | 106 | 32 | 18 | Uplands | 27.6/16kV | 4801F8 | T1221 at 2778 Equis Way required isolation to allow Hydro Crews to repair secondary connections | Gloucester | Scheduled Outage | Repair
14261 | 2009 | 4 | 29 | 0.42361 |  | 409 | 82 | 12 | Uplands | 27.6/16kV | 4801F8 | At 10:10am T1030 at 3158 Quail Ridge was isolated to allow crews to replace and cleanup leaking transformer, all power restored at 4:59pm. Uplands DS (4801F8). ID#14261. | Ottawa | Scheduled Outage | Repair
14309 | 2009 | 5 | 5 | 0.75139 |  | 448 | 149 | 52 | Uplands | 27.6/16kV | 4801F8 | Defective Transformer T927R at 2281 Shanegal, caused G591R to blow. Transformer replaced. | Gloucester | Defective Equipment
20516 | 2012 | 5 | 15 | 0.39583 |  | 276 | 41 | 9 | Uplands | 27.6/16kV | 4801F8 | TE1029 AT 3173 Quail was isolated to change leaking transformer. | Gloucester | Scheduled Outage | Repair
8300 | 2006 | 5 | 16 | 0.41181 |  | 269 | 49 | 11 | Uplands | 27.6/16kV | 4801F8 | Transformer T929R at 2329 Shenegal isolated for replacement due to leak. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
18180 | 2011 | 5 | 19 | 0.0034722 |  | 74 | 14 | 11 | Uplands | 27.6/16kV | 4801F8 | Transformer fuse at X13777 blown due to animal contact. | Gloucester | Foreign Interference | Animal
12463 | 2008 | 5 | 22 | 0.50347 |  | 100 | 18 | 11 | Uplands | 27.6/16kV | 4801f8 | At 12:05 PM transformer T1741 isolated to replace leaking transformer on 4801F8 out of Uplands. 11 customers affected, transformer restored at 13:45PM. | Gloucester | Scheduled Outage | Repair
16219 | 2010 | 6 | 7 | 0.70417 |  | 69 | 64 | 65 | Uplands | 27.6/16kV | 4801F8 | Tree contact with primary line into Conroy PIT caused supply fuse at X14525 to blow as well as next two upstream fuses G748Wand G749W to blow. Line into pit remains out of service pending tree trimming. | Gloucester | Tree Contacts | Inadequate Trimming
14495 | 2009 | 6 | 8 | 0.51736 |  | 52 | 71 | 82 | UPLANDS | 27.6/16kV | 4801F8 | G398 white phase at 1409 Mory Street was blown crew patrolled line and found no cause. | Nepean | Unknown/Other | No Apparent Cause
14500 | 2009 | 6 | 10 | 0.093056 |  | 166 | 94 | 58 | UPLANDS | 27.6/16kV | 4801F8 | Animal contact on transfomer #X14542 at 1647 St. Barbara St. caused G435R to open. | Ottawa | Foreign Interference | Animal
16252 | 2010 | 6 | 12 | 0.034722 |  | 56 | 49 | 53 | UPLANDS DS | 27.6/16kV | 4801F8 | 4801F8 faulted between G425R & TE1069, causing an outage to 4 down stream transformers. Crews isolated the fault and restored power through the open point at TE1072. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16286 | 2010 | 6 | 18 | 0.6875 |  | 34 | 2493 | 4400 | Uplands | 27.6/16kV | 4801F8 | A bird came in contact with an overhead transformer switch at 3600 Uplands which blew the transformer fuse, caused G508 blue phase to blow and tripped the 4801F8 feeder breaker. | Gloucester | Foreign Interference | Bird
12753 | 2008 | 6 | 26 | 0.71528 |  | 300 | 530 | 147 | Uplands | 27.6/16kV | 4801F8 | Stormy weather caused G435R, G749W & G748W on Athans ave, St Barbara & Councillors Way to blow. A fused cut-out to Tx X14542 was also repaired. | Gloucester | Adverse Weather | Lightning
12754 | 2008 | 6 | 26 | 0.79861 |  | 190 | 225 | 71 | Uplands | 27.6/16kV | 4801F8 | Stormy weather caused G666W at Des Mesanges & Albion to blow. Area patrolled & fuse replaced. | Gloucester | Adverse Weather | Lightning
16357 | 2010 | 6 | 29 | 0.42014 |  | 199 | 56 | 17 | Uplands | 27.6/16kV | 4801F8 | Q4801F8 isolated between S15598 and TP4619 to allow Crane to install a pool at 3709 Alderwood. Two O/H transformers wre affected feeding customers on Alderwood and Trapper Rd. | Gloucester | Scheduled Outage
16366 | 2010 | 6 | 29 | 0.91042 |  | 51 | 3744 | 4405 | Uplands | 27.6/16kV | 4801F8 | Balloon streamers went phase to phase on 4801F8 causing it to a/r/a and lockout. Balloons removed breaker closed and holding. | Gloucester | Foreign Interference | Foreign Object
14646 | 2009 | 6 | 30 | 0.26458 |  | 108 | 220 | 122 | UPLANDS | 27.6/16kV | 4801F8 | A bird caused an o/h transformer to blow, causing G210 R to blow. G210 R and transformer refused to restore power. | Gloucester | Foreign Interference | Bird
16415 | 2010 | 7 | 6 | 0.85 |  | 497 | 41 | 5 | Uplands | 27.6/16kV | 4801F8 | Defective transformer at 3365 Hogarth, crews replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16429 | 2010 | 7 | 8 | 0.64514 |  | 147 | 123 | 50 | Uplands | 27.6/16kV | 4801F8 | defective red phase cable section between S13039 & T4614 on Mozart. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
14687 | 2009 | 7 | 9 | 0.46181 |  | 175 | 29 | 10 | UPLANDS | 27.6/16kV | 4801F8 | TP2921 AT 416 DEERVIEW WAS ISOLATED DUE TO DIG IN BY CONTRACTOR CAUSING DAMAGE TO THE TRANSFORMER. TRANSFORMER ISOLATED AND REPAIRED. | Ottawa | Foreign Interference | Dig-in
14688 | 2009 | 7 | 9 | 0.75278 |  | 506 | 84 | 10 | Uplands | 27.6/16kV | 4801F8 | TP2921 at 416 Deer Field isolated again to remove contaminated soil around transformer. | Gloucester | Scheduled Outage
12812 | 2008 | 7 | 10 | 0.14583 |  | 120 | 16 | 8 | Uplands | 27.6/16kV | 4801F8 | Secondary service opened at X14776 due to working fire, the secondary wires were burnt together. Switch was found in the open position once 24/7 crew was able to inspect after fire was extinguished. Switch closed and power returned to normal. | Gloucester | Adverse Environment | Fire
18728 | 2011 | 7 | 18 | 0.79861 |  | 54 | 818 | 909 | Uplands | 27.6/16kV | 4801F8 | G347 white phase termination blew causing the 4801F8 circuit to open. Load was 480 on circuit. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
16555 | 2010 | 7 | 25 | 0.025 |  | 333 | 166 | 30 | Uplands | 27.6/16kV | 4801F8 | T2276 isolated to allow crews to Replace leaking transformer and Drain to to clean up Oil Spill. 30 Customers affected for 333 minutes. Uplands (4801F8) ID #16555 | Gloucester | Scheduled Outage | Repair
16566 | 2010 | 7 | 27 | 0.38889 |  | 568 | 104 | 11 | Uplands | 27.6/16kV | 4801F8 | T2638 at 2922 Sable Ridge isolated to allow for transformer replacement due to leaking transformwer and oil spill clean up. | Gloucester | Scheduled Outage | Repair
8880 | 2006 | 8 | 1 | 0.048611 |  | 215 | 358 | 100 | Uplands | 27.6/16kV | 4801F8 | Uplands T3 high and low side F7 and F8 tripped. F8 with IOGEN picked up through SC27522 supplird from 7F2. | Gloucester | Adverse Weather | Lightning
15029 | 2009 | 8 | 30 | 0.25903 |  | 84 | 80 | 82 | Uplands | 27.6/16kV | 4801F8 | G398W fuse at 1409 Mory & Albion Rd blew for a problem after G523W on the underground section. Overhead section from G398W to G523W was re-energized successfully and the underground section was then sectionalized and restored. Cable section found blown between TE1062 & TE1063 on Autumnwood | Gloucester | Defective Equipment
19122 | 2011 | 9 | 8 | 0.40347 |  | 376 | 31 | 5 | Uplands | 27.6/16kV | 4801F8 | At 09:41 transformers TP3046 and TP3047 at 3528 Downpatrick Road were made available to allow contractor to perform secondary maintenance. 5 customers were affected for 376 minutes. Uplands (4801F8) | Gloucester | Scheduled Outage
9188 | 2006 | 9 | 10 | 0.20833 |  | 244 | 8 | 2 | Uplands | 27.6/16kV | 4801F8 | TP 1782 and PT1852 removed from SC1601 and transferred to new TP3985 and TP3986 on Rivergate Way now being supplied from Uplands F8 27KV. | Gloucester | Scheduled Outage | Construction
13242 | 2008 | 9 | 16 | 0.32917 |  | 357 | 267 | 96 | Uplands | 27.6/16kV | 4801F8 | Failed elbow & insert @ TE1467, 2577 Bridle Path caused B phase fuse to blow @ SE30, 7 Tx's affected. TE1497 isolated to make repairs. LCM crew replaced transformer as it was due for replacement due to leakage. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19449 | 2011 | 10 | 23 | 0.4875 |  | 55 | 3960 | 4426 | Uplands | 27.6/16kV | 4801F8 | 4801F8 breaker auto reloced and stayed open crew found a fuse blown at a three phase bank X14494. Uplands (4801F8) ID#19449 | Gloucester | Unknown/Other
15236 | 2009 | 10 | 8 | 0.40694 |  | 485 | 65 | 8 | Uplands | 27.6/16kV | 4801-F8 | TE1031B (new TP6729B) at 1564 Feather Lane isolated for replacement due to leak. | Gloucester | Scheduled Outage | Preventive Maintenance
11900 | 2008 | 1 | 4 | 0.75694 |  | 96 | 796 | 500 | Uplands MS | 27.6/16kV | 4801T3 | Uplands MTS 4801T3 transformer secondary cable W phase stress cane failed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14754 | 2009 | 7 | 15 | 0.26944 |  | 19 | 1390 | 4390 | uplands | 27.6/16kV | 4801T3 | A squirrel flashed over the merivale MS 72B1-B2 tie switch which caused the A3RM to open which supplies the 4801T3. | Gloucester | Foreign Interference | Animal
13090 | 2008 | 8 | 18 | 0.69097 |  | 1 | 66 | 3979 | UPLANDS | 27.6/16kV | 4801T3 | HIGH SIDE BREAKER OPENED DUE TO STORM, CLOSED VIA SCADA | Gloucester | Adverse Weather | Lightning
9983 | 2007 | 2 | 2 | 0.9375 |  | 10 | 1 | 4 | Uplands | 27.6/16kV | 48F1 | Graham isolated TRF. At 2958 Lester to inspect arcing noise | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15311 | 2009 | 10 | 26 | 0.52083 |  | 103 | 17 | 10 | EPWORTH | 8/4.8kV | 48F1 | Transformer X36507 at 82 Rossland Ave isolated to allow crew to rearrange plant | Nepean | Scheduled Outage | Construction
7704 | 2005 | 12 | 9 | 0.15417 |  | 165 | 154 | 56 | Manordale | 8/4.8kV | 48F5 | Switch S707 burnt connection repaired. 7 transformers power out. Canfield,Parkmount,Keppler and Cramer. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15896 | 2010 | 4 | 5 | 0.77569 |  | 324 | 54 | 10 | Hawthorne | 44kV | 48M1 | Hydro One 48M1 insulator broke causing J bus differential at Hawthorne. Loops had to opened and 48M2 relay setting change before load restored. 10 Hydro Ottawa transfer customers effected. | Gloucester | Loss of Supply | HEPC Station Fault
13740 | 2008 | 12 | 11 | 0.73194 |  | 70 | 6808 | 5835 | Hawthorn | 44kV | 48M1 | Switching performed to restore load at 48M2-1 switch which failed to close properly causing Acring between phases. 48M1 & 48M2 breakers opened from SCADA by H1 (Jason) at our request | Gloucester | Defective Equipment
12114 | 2008 | 3 | 7 | 0.99028 |  | 125 | 635 | 2100 | Hawthrone | 27.6/16kV | 48M2 | At 21:45 Scada indicatied 49F1 opened. Also Hydro One reports 48M2 circuit auto reclosed, causing a momentary outage at Borden Farms. Leitrim station remained out. 24/7 reports highside fuse found blown on 49T1 transformer, and 49F1 reclosure bushing blown. Leitrim station isolated and 49F1, & 49F2 load transferred to Limebank. | Gloucester | Adverse Weather | Snow
15894 | 2010 | 4 | 5 | 0.77569 |  | 10 | 691 | 4148 | Hawthorne | 44kV | 48M2 | Hydro One reports J bus differential that caused our 48M2 feeder to open. Bus and load restored by H. Load loss to Borden Farms and Leitrim | Gloucester | Loss of Supply | HEPC Station Fault
16450 | 2010 | 7 | 9 | 0.52431 |  | 672 | 11 | 1 | Hawthron | 44kV | 48M2 | 48M2 overhead overhead conductor failed due to lightening strom. | Gloucester | Adverse Weather | Lightning
16632 | 2010 | 8 | 3 | 0.82778 |  | 84 | 5483 | 5156 | Hawthorne | 44kV | 48M2 | Hydro 1 reported their 48M2 breaker auto reclosed and tripped again locking out, Borden Farm and Lietrim stations fed on this Circuit | Gloucester | Loss of Supply | HEPC Circuit Fault
18903 | 2011 | 8 | 10 | 0.56944 |  | 114 | 5880 | 4139 |  |  | 48M2 | Lightning strike hit pole at 3375 Hawthorne causing the 48M2 breaker to open. All load fed out of Litriem DS affected and restored in stages from alternate circuits. Hydro One reported damage to the 48M2 breaker and left it out of service. The 48M2 feeder was restored through the Hydro One 48M3 circuit to pick up Ottawa Fibre. | Ottawa | Adverse Weather | Lightning
3257 | 2003 | 3 | 16 | 0.53958 |  | 7 | 369 | 3161 | Hawthorne TS | 44kV | 48M3 | 44KV line (48M3) feeding Blackburn MS and the Detention Centre tripped to lockout. After checking fault indication on SCADA 48M3-2 was opened since it did not show the fault and 48M3 tried. It tripped free. 48M3-M4-6 was closed to restore power on 48M4. 24/7 visually checked o/H line from Hawthorne TS and other side of Queensway to open 48M3-2. They reported nothing obvious seen. Hydro One advised breaker checked OK and reported burn mark on polymer insulator at Innes & Blair. | Gloucester | Unknown/Other | Equipment Deterioration Due to Age
20369 | 2012 | 4 | 22 | 0.26389 |  | 1 | 52 | 3147 | Hawthorn | 44kV | 48M3 | Hydro One 48M3 tripped and was closed back in by Hydro One causing Blackburn sub to be momentarily interrupted. | Gloucester | Loss of Supply | HEPC Circuit Fault
18082 | 2011 | 4 | 28 | 0.58889 |  | 56 | 2922 | 3131 | Blackburn | 44kV | 48M3 | Loss of supply of the 48M3 circuit from Hydro One cause Blackburn DS outage. | Gloucester | Loss of Supply | HEPC Circuit Fault
20601 | 2012 | 5 | 26 | 0.017361 |  | 6 | 314 | 3135 | Hawthorne | 44kV | 48M3 | 48M3 was interupted via a SCADA line switch to allow crew to open non load break switch for isolation of a broken pole. Hawthorne (48M3) ID#20601 | Gloucester | Adverse Weather | Wind
14980 | 2009 | 8 | 21 | 0.038194 |  | 13 | 654 | 3962 | Hawthorn | 8/4.8kV | 48M3 | Moulton 8F4 Autotripped, no reclose. H1 reports Hawthorn 48M3 Auto closed then tripped open (feeds Blackburn DS) On phone with H1, 48M3 closed and held (Blackburn restored). Moulton 8F4 closed and held. | Gloucester | Loss of Supply | Rain
5810 | 2004 | 9 | 16 | 0.38333 |  | 53 | 2782 | 3150 | Hawthorne TS | 44kV | 48M3 | Cable joint failure @ 417 underground crossing. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
6210 | 2005 | 2 | 15 | 0.58542 |  | 11 | 1356 | 7398 | Hawthorne | 44kV | 48M3, M4 | While installing new poles on isolated section of 48M4, 48M3 tripped while also carrying 48M4 load when a pole came in contact with the energized 48M3 circuit. | Gloucester | Human Element | Commissioning Errors
3249 | 2003 | 3 | 13 | 0.58056 |  | 1 | 80 | 4805 | Hawthorne | 44kV | 48M4 | Circuit tripped A/R during switching to restore 48M5 from planned maintenance. Hydro Ottawa Operators mistook communication from Hydro One to understand that 48M5 breaker was closed, when in fact it was not. | Ottawa | Human Element | Switching Errors
15895 | 2010 | 4 | 5 | 0.85764 |  | 7 | 161 | 1382 | Startop | 44kV | 48M4 | Hydro One tried to pick up 48M1 load on the 48M4 which caused to M4 feeder to trip. M1 overhead removed and 48M4 breaker closed by H1 | Gloucester | Loss of Supply | HEPC Circuit Fault
14637 | 2009 | 6 | 29 | 0.084028 |  | 33 | 1134 | 2061 | Hawthorne | 44kV | 48M4 | 44kv dead end insulator at MC2029 to Stats Canada let go and caused the 48M4 to open, load was restored and the broken insulator was discovered when patrolled. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9299 | 2006 | 9 | 25 | 0.33681 |  | 32 | 2267 | 4250 | Hawthrone | 44kV | 48M4 | A blown arrestor at the Pollotion control centre on Shefford Rd. did not blow clear causing the 48M4 circuit to trip. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9302 | 2006 | 9 | 25 | 0.33681 |  | 220 | 4 | 1 | Hawthrone | 44kV | 48M4 | A blown lightning arrestor at the Pollution control center caused the 48M4 circuit to blow. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7406 | 2005 | 9 | 29 | 0.82569 |  | 63 | 4476 | 4263 | Beaconhill | 44kV | 48M4 | 44kv lightning arrester blown on customer owned line section to Greens Creek Arrester cleared and line closed in. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17381 | 2010 | 12 | 5 | 0.025694 |  | 334 | 11 | 2 | Hawthrone | 44kV | 48M4 | Two 44Kv customers St Joseph Printing and Stats Can were isolated to allow Hydro Ottawa line crews to cutover the new conductor on the Southeast side of Cyrville bridge @ Labrie. | Gloucester | Scheduled Outage | Construction
3250 | 2003 | 3 | 13 | 0.58056 |  | 4 | 107 | 1603 | Hawthorne | 44kV | 48M5 | Circuit tripped Auto during switching to restore 48M5 from planned maintenance. Hydro Ottawa Operators mistook communication from Hydro One to understand that 48M5 breaker was closed, when it was not. | Ottawa | Human Element | Switching Errors
3370 | 2003 | 4 | 24 | 0.17361 |  | 1 | 267 | 1603 | Startop | 44kV | 48M5 | Auto reclose, auto. After one minute breaker closed by Hydro One operator, Doug Schoffield. | Gloucester | Loss of Supply
8234 | 2006 | 5 | 4 | 0.71181 |  | 115 | 2163 | 1604 | Hawthorne | 44kV | 48M5 | 48M5 TRIPPED DUE TO FAULTED ARRESTOR FEEDING THE STARTOP STATION. CAUSED THE STARTOP STATION TO ALSO LOOSE ALL LOAD. ARRESTOR WAS ISOLATED AND 48M5 CLOSED PICKING UP ALL BUT 2 FEEDERS AT STARTOP (6F7) (6F1). 66F7 CLOSED, BUT 6F1 WOULD NOT CLOSE. | Gloucester | Lightning | Lightening Strike on adjacent circuit
9504 | 2006 | 10 | 24 | 0.5375 |  | 72 | 3531 | 4237 | Hawthorne | 44kV | 48M5 | Electrical Contact by Contractor at the Pollution Control Center on secondary side caused the 48M5 Breaker to trip. | Gloucester | Foreign Interference | Vehicle
7538 | 2005 | 10 | 29 | 0.67708 |  | 95 | 2533 | 1600 | Startop | 44kV | 48M5 | 48M5 reported tripped by Hydro One. Blown arrester found at Canada Life Building on Comsotck. 1 blown arrester and 1 damaged arrester cut clear. Power restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4632 | 2003 | 12 | 19 | 0.70069 |  | 5 | 134 | 1603 | STARTOP | 44kV | 48M5 | 48M5 FEEDING STARTOP STATION TRIPPED OUT BREAKER WAS CLOSED AND HELD CREW TO PATROL | Gloucester | Unknown/Other | No Apparent Cause
4636 | 2003 | 12 | 20 | 0.20347 |  | 2 | 53 | 1603 | Hawthorne | 44kV | 48M5 | 48M5 FEEDING STARTOP STATION AUTO TRIPPED TO LOCKOUT, BREAKER WAS CLOSED VIA SCADA. TWO LIGHTENING ARRESTORS FOUND BLOWN AT STATION END OF CABLE GOING UNDER THE QUEENSWAY. | Gloucester | Unknown/Other
3239 | 2003 | 3 | 9 | 0.18056 |  | 288 | 4448 | 5750 | Hawthorne | 44kV | 48M5 & 48M4 | A pole fire at Innes and Stonehenge caused both the 48M4 & 48M5 circuits to go to lockout. Both circuits were isolated and power was restored using motorized airbrake switches. Also part of the 4F4 circuit was isolated, just in time as a matter of fact, before the pole and wires fell down upon it. Openers are to be cut in and the 4F4 restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4683 | 2004 | 1 | 7 | 0.52083 |  | 20 | 3 | 10 | Leitrim | 27.6/16kV | 49F1 | Replaced cut out on transformer 3415 on Kingsdale Ave. | Gloucester | Scheduled Outage | Preventive Maintenance
4694 | 2004 | 1 | 12 | 0.42778 |  | 68 | 14 | 12 | Lietrim | 27.6/16kV | 49F1 | Leaking triangle at 1913 Kingsdale required changing ID #4841 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13862 | 2009 | 1 | 13 | 0.86667 |  | 66 | 77 | 70 | Leitrim |  | 49F1 | G316 on First St near Kingsdale opened for no apparent reason. Crew patrolled overhead, found nothing, re-fused, closed and holding all power restored | Gloucester | Unknown/Other | No Apparent Cause
3134 | 2003 | 1 | 21 | 0.63889 |  | 483 | 64 | 8 | Leitrim | 27.6/16kV | 49F1 | TE805 was found with secondary fuse blown 24/7 was first to respond but then had to go to another call then Rowland was called in crew isolated transformer but didn’t have a fuse to replace. Nepean crew was called in to load a transformer from Nepean and asked to meet Roland on Bannon Way. The Transformer was then replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
11963 | 2008 | 1 | 21 | 0.42014 |  | 28 | 14 | 30 | Bayshore | 8/4.8kV | 49F1 | Five transformers on the 49F1 Blue phase between S740 & S689 were transferred to red phase supply. | Nepean | Scheduled Outage | Construction
13896 | 2009 | 1 | 26 | 0.84653 |  | 122 | 120 | 59 | Lietrim | 27.6/16kV | 49F1 | Blown fuse on White phase only at G216, after patrol nothing was found, crew re-fused and it held. | Gloucester | Unknown/Other
3150 | 2003 | 1 | 31 | 0.79028 |  | 330 | 46 | 11 | Leitrim | 27.6/16kV | 49F1 | Dig-in to primary & secondary cables at transformer #1912 on Sixth st in Gloucester sector. On call crew repaired switch G477, and primary cable at transformer. Crew reports at 18:58 power restored to all customers, but one at 3715 Sixth st.. On call crew reports power restored 3715 Sixth st at 20:30 | Gloucester | Foreign Interference | Dig-in
6176 | 2005 | 2 | 4 | 0.37222 |  | 203 | 7 | 2 | Leitrim | 27.6/16kV | 49F1 | Defective trans replaced at 3894 Russell Rd Glou | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
10002 | 2007 | 2 | 8 | 0.17014 |  | 621 | 257 | 50 | Leitrim | 27.6/16kV | 49F1 | The 49F1 feeder auto/reclosed and in line switch S992 opened when a truck hit and damaged a pole on Belgreen ave. This section was isolated to cut in new switches for isolation of the damaged area only, power restored to all but 2 customers for duration of repairs. Pole replaced and conductor repaired. | Gloucester | Foreign Interference | Vehicle
12028 | 2008 | 2 | 9 | 0.31736 |  | 908 | 30 | 2 | Leitrim | 27.6/16kV | 49F1 | TP5547 (TE2718) at 3429 Hawthorne Rd was isolated to upgrade the transformer. | Gloucester | Scheduled Outage | Preventive Maintenance
13966 | 2009 | 2 | 12 | 0.024306 |  | 377 | 94 | 15 | Lietrim | 27.6/16kV | 49F1 | Transformer X14417 at 1909 Queensdale failed and had to be replaced. On call has replaced transformer. | Gloucester | Defective Equipment
12056 | 2008 | 2 | 18 | 0.41667 |  | 108 | 1119 | 1143 | Leitrim | 27.6/16kV | 49F1 | An Insulator on 49F1 circuit failed causing conductor to fall across a metal bracket at the corner of Conroy & Queensdale. Section of 49F1 on Conroy & Queensdale was isolated until crews replaced insulator. | Gloucester | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
3211 | 2003 | 2 | 24 | 0.66667 |  | 473 | 87 | 11 | Leitrim | 27.6/16kV | 49F1 | TE818 at 3181 Stockton had to be replaced due to a defective transformer | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4829 | 2004 | 2 | 26 | 0.39583 |  | 113 | 40 | 21 | Leitrim | 27.6/16kV | 49F1 | A defective insulator at transformer X13925 @ 1719 Kingsdale. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4852 | 2004 | 3 | 3 | 0.39097 |  | 478 | 88 | 11 | Leitrim | 27.6/16kV | 49F1 | Transformer TE1808 at 3181 Stockton was taken out of service for planned maintenance to high voltage cables. 11 customers from 3166 to 3186 Stockton were affected. | Gloucester | Scheduled Outage | Preventive Maintenance
4855 | 2004 | 3 | 4 | 0.40833 |  | 87 | 19 | 13 | Leitrim | 27.6/16kV | 49F1 | TE817 replaced due to defective insert. Stockton Dr Blossom Park. | Gloucester | Scheduled Outage | Repair
12119 | 2008 | 3 | 10 | 0.42431 |  | 57 | 3 | 3 | Leitrim |  | 49F1 | Isolated pad-mount transformer TP3277 and place it back on the base (knocked partway off by a bulldozer) | Gloucester | Foreign Interference | Vehicle
4890 | 2004 | 3 | 14 | 0.57569 |  | 1 | 19 | 1144 | Leitrim | 27.6/16kV | 49F1 | 49F1 breaker open from SCADA and the G367SM close in the field by 24/7. Switching required to transferr load due to blue pahse fuse blown on 49T1 | Gloucester | Defective Equipment
4892 | 2004 | 3 | 14 | 0.59028 |  | 67 | 251 | 759 | Leitrim | 27.6/16kV | 49F1 | 49F2 recloser open from SCADA switch G782 open and switch G313 close 759 customers on . Repair to insulator completed and G254LB closed last 120 customers on. Part of blown blue phase high side 49T1 transformer. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
6329 | 2005 | 3 | 27 | 0.1875 |  | 100 | 28 | 17 | Leitrim | 27.6/16kV | 49F1 | transformer 3019 on Kingsdale was opened to disconnect triplex feeding 1749 Kingsdale for a working fire. | Gloucester | Scheduled Outage | Emergency Services Request
15876 | 2010 | 3 | 31 | 0.85625 |  | 66 | 18 | 16 | Leitrim | 27.6/16kV | 49F1 | defective switch G654W at the corner of Belgreen and Russell rd, was replaced. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
14152 | 2009 | 4 | 7 | 0.27361 |  | 936 | 31 | 2 | Leitrm | 27.6/16kV | 49F1 | At 6:34am, cutomers at TE2175 4080 & 4090 Belgreen called in with no power. Crews report bad underground, power was restored to the two customers by 10:10pm. (Leitrim 49F1) ID#14152 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12288 | 2008 | 4 | 15 | 0.78403 |  | 637 | 11 | 1 | Leitrim | 27.6/16kV | 49F1 | Transformer T1363 at 2919 Bank Street, Gloucester was found defective and was replaced. | Gloucester | Defective Equipment
14180 | 2009 | 4 | 16 | 0.21667 |  | 68 | 2 | 2 | Bayshore | 8/4.8kV | 49F1 | At 5:12am customers at 58 Bayshore Drive called in with partial power call. Crews found defective white phase switch at switch 807. Crews restored power and isolated switch for repair. All power restored at 6:20am.(Bayshore F1). ID#14180. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15954 | 2010 | 4 | 19 | 0.35903 |  | 13 | 3 | 12 | LEITRIM | 27.6/16kV | 49F1 | @ 8:37 Transformer X13853 @ 1599 Kingsdale isolated for secondary service work | Gloucester | Scheduled Outage | Preventive Maintenance
3375 | 2003 | 4 | 26 | 0.10903 |  | 10 | 11 | 66 | Leitrim |  | 49F1 | G316R was opened to safely disconnect cutout on transformer T3548 at 1547 Kingsdale. | Gloucester | Scheduled Outage | Repair
3376 | 2003 | 4 | 26 | 0.020833 |  | 170 | 20 | 7 | Leitrim | 27.6/16kV | 49F1 | Racoon caused damage to a cutout that opened Transformer 3548 on Kingsdale affecting 7 customers. | Gloucester | Foreign Interference | Animal
5075 | 2004 | 4 | 29 | 0.63889 |  | 30 | 6 | 12 | Leitrim | 27.6/16kV | 49F1 | To repair defective switch to transformer 3636 at 1633 Queensdale. | Gloucester | Defective Equipment
6560 | 2005 | 5 | 15 | 0.24097 |  | 223 | 229 | 76 | Lietrim | 27.6/16kV | 49F1 | Blown arrestor and defective tx fuse at O/H tx 3347 on Hawthorne Rd, in line fused switch G81R also opened. G81R refused and closed, tx switch and arrestor at tx 3347 replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12447 | 2008 | 5 | 17 | 0.46875 |  | 780 | 13 | 1 | Lietrim | 27.6/16kV | 49F1 | defective red phase cable from G548 to T1147 at 4561 Bank required isolation of remaining 2 phases, to on-call. G548 closed back in with repairs made at 00:15. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
16127 | 2010 | 5 | 24 | 0.67014 |  | 65 | 1 | 1 | Bayshore | 8/4.8kV | 49F1 | VE33N at 3100 Carling was isolated for the customer to make emergency repairs in secondary splitter box. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
16143 | 2010 | 5 | 25 | 0.85625 |  | 407 | 34 | 5 | Lietrim | 27.6/16kV | 49F1 | T798 at 3360 Hogarth was found blown and in need of replacement, 49F1, Lietrim - isolated by 24/7 and handed over to on-call | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12479 | 2008 | 5 | 26 | 0.30208 |  | 76 | 81 | 64 | Leitrim | 27.6/16kV | 49F1 | G624 white phase cutout failed causing fuse G614 W at the other end to blow interrupting power to 64 customers on Olympic Way (Blossom Park area). Power was restored and all 3 switches at G624 were replaced. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
8377 | 2006 | 5 | 30 | 0.44236 |  | 97 | 752 | 1149 | Leitrim | 27.6/16kV | 49F1 | BACKHOE MADE CONTACT WITH O/H BEYOND SWITCH G81 CAUSING ONE PHASE OF THE 3 PHASE TO FALL. 49F1 CIRCUIT WAS OPENED TO ALLOW CREW TO ISOLATE FROM G81. 49F1 CLOSED AGAING UNTIL REPAIRS WERE MADE. | Gloucester | Foreign Interference | Vehicle
5230 | 2004 | 5 | 31 | 0.78819 |  | 85 | 6 | 4 | Leitrim | 27.6/16kV | 49F1 | The switch at G216 opened on the B phase on Stevenage Dr affecting 4 customers no apperant cause. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10511 | 2007 | 6 | 1 | 0.59514 |  | 98 | 7 | 4 | Leitrim | 27.6/16kV | 49F1 | 49F1 breaker auto reclosed once, cause was later determined to be from a bird contact with the O/H transformer at 2709 Stevenage. Transformer was refused successfully. | Gloucester | Foreign Interference | Bird
14441 | 2009 | 6 | 1 | 0.76736 |  | 37 | 77 | 125 | Bayshore | 8/4.8kV | 49F1 | PC10a004780 into effect on switch 433 that feeds VE69 @ 3105 Carling to replace burnt switches | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10513 | 2007 | 6 | 2 | 0.24514 |  | 297 | 20 | 4 | Leitrim | 27.6/16kV | 49F1 | Circuit a/r. Customer later reported all out at 2705 Stevenage. Removed bird nest from top of Tx 58 & replaced fuse. | Gloucester | Foreign Interference | Bird
10560 | 2007 | 6 | 8 | 0.83125 |  | 248 | 62 | 15 | Leitrim | 27.6/16kV | 49F1 | 49F1 feeder auto/reclose. G216RWB fuses found opened at Stevenage Dr. Circuit patrolled no fault found. G216 RWB closed all load restored. | Gloucester | Lightning | Lightning Strike on Adjacent Circuit Flashed Over
10597 | 2007 | 6 | 11 | 0.45694 |  | 17 | 4 | 15 | Leitrim | 27.6/16kV | 49F1 | Transformer #3440 isolated by Mark Brown due to service torn down by Home Depot truck. | Gloucester | Foreign Interference | Vehicle
5299 | 2004 | 6 | 13 | 0.83125 |  | 153 | 3 | 1 | Leitrim | 27.6/16kV | 49F1 | Transformer 3589 at 3136 Conroy Rd transformer fuse replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5300 | 2004 | 6 | 14 | 0.00069444 |  | 19 | 1 | 3 | Leitrim | 27.6/16kV | 49F1 | Report of sparking wires on Conroy north of Roesbella. Switch G476W arch from fuse barrell. Fuse replaced. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
14542 | 2009 | 6 | 16 | 0.37778 |  | 397 | 13 | 2 | Bayshore | 8/4.8kV | 49F1 | TP6148 @ 114 Woodrige was isolated for the transformer PCB replacement program | Nepean | Scheduled Outage | Preventive Maintenance
10688 | 2007 | 6 | 20 | 0.91667 |  | 276 | 23 | 5 | Leitrim | 27.6/16kV | 49F1 | Customer owned line was isolated to install a new transformer TP4869 | Gloucester | Scheduled Outage | Construction
10689 | 2007 | 6 | 21 | 0.11458 |  | 5 | 95 | 1143 | Leitrim | 27.6/16kV | 49F1 | S. Broman from K-line reports while restoring customer owned. New insulator on customer's pole failed causing a pole fire. Overhead line re-isolated for contractor to replace hydro pole and insulators. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10690 | 2007 | 6 | 21 | 0.12153 |  | 220 | 18 | 5 | Leitrim | 27.6/16kV | 49F1 | re-isolate customer owned overhead line to allow contractor to replace defective insulators | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
6809 | 2005 | 6 | 25 | 0.625 |  | 300 | 375 | 75 |  | 27.6/16kV | 49F1 | Heavy rains caused tree branches to touch o/h line and blew switch fuse at G570. | Gloucester | Tree Contacts | Inadequate Trimming
12768 | 2008 | 6 | 29 | 0.71319 |  | 448 | 107 | 70 | Lietrim | 27.6/16kV | 49F1 | Fuse at transformer 3547, 1469 Kingsdale found opened. Crew refused and closed but fuse opened again as well as the upstream local G316 because tx had failed.. G316 refused and tx was then replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16409 | 2010 | 7 | 6 | 0.51944 |  | 292 | 5 | 1 | Bayshore | 8/4.8kV | 49F1 | VE33 at 3100 Carling was isolated to allow for emergency secondary main replacement, secondary main was defective. | Nepean | Defective Equipment
16438 | 2010 | 7 | 9 | 0.55833 |  | 47 | 979 | 1250 | Leitrim | 27.6/16kV | 49F1 | 49F1 opened due to severe strom, circuit back fed from Uplands 4801F8 and load restored. | Gloucester | Adverse Weather | Lightning
6938 | 2005 | 7 | 14 | 0.0069444 |  | 350 | 2042 | 350 | Leitrim | 27.6/16kV | 49F1 | Many single blue phase switches blown on o/h line and GR6 Blue phase was blown. | Gloucester | Adverse Weather | Lightning
6939 | 2005 | 7 | 14 | 0.0069444 |  | 350 | 2042 | 350 |  | 27.6/16kV | 49F1 | GR6 Blue opened due to lightning stikes on o/h line. Refused single phase cut outs and then closed GR6 Blue restoring line | Gloucester | Lightning
10936 | 2007 | 7 | 24 | 0.19653 |  | 307 | 51 | 10 | leitrim | 27.6/16kV | 49F1 | circuit auto-reclosed. To be patrolled. Received no calls as of yet. Customer calls from Sixth & St Bernard, crew found G477W blown feeding 1 transformer, TE1912.. Cable isolated & tested OK, TE1912 restored & cable to G414W isolated. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10937 | 2007 | 7 | 24 | 0.27639 |  | 202 | 27 | 8 | LEITRIM | 8/4.8kV | 49F1 | Crew found switch G477 open and broken at Sixth St and St Bernard St crew replaced the switch and restored power | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5566 | 2004 | 7 | 25 | 0.92014 |  | 35 | 1 | 2 | Leitrim | 27.6/16kV | 49F1 | Squirrel caused transformer TE1179 at 3637 Bank st. to open. | Gloucester | Foreign Interference
3882 | 2003 | 8 | 8 | 0.40139 |  | 232 | 19 | 5 | Leitrim | 27.6/16kV | 49F1 | G427R opened in the Halls road area to change a fuse | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
13035 | 2008 | 8 | 10 | 0.5625 |  | 25 | 2 | 4 | Leitrim | 27.6/16kV | 49F1 | Isolated transformer X18294 at 4305 Blake Rd to repair secondary neutral | Gloucester | Scheduled Outage | Repair
11035 | 2007 | 8 | 11 | 0.70625 |  | 117 | 4 | 2 | Bayshore | 8/4.8kV | 49F1 | Switch feeding VE69 @ 3099 & 3105 Carling Ave has a defective white phase cuttout. Vault was isolated from RWB phases to make repairs to switch white phase. Switch repaired and customer power was restored. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
8965 | 2006 | 8 | 14 | 0.64931 |  | 173 | 379 | 160 | Leitrim | 27.6/16kV | 49F1 | Blown arrestor, possibly due to animal contact, at G474R on Queensdale faulted causing fused switches G470R and G517R to open. | Gloucester | Foreign Interference | Animal
14944 | 2009 | 8 | 14 | 0.39583 |  | 90 | 24 | 16 | Leitrim | 27.6/16kV | 49F1 | 2 transformers were interrupted on Bellmanor in order to replace dip switches G406R & G253R on Sixth St. | Gloucester | Scheduled Outage | Repair
15006 | 2009 | 8 | 26 | 0.12222 |  | 34 | 6 | 11 | Leitrim | 27.6/16kV | 49F1 | Transformer X13868 at 1475 Kingsdale blew a fuse, crews replaced fuse power restored | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
15009 | 2009 | 8 | 26 | 0.28333 |  | 182 | 33 | 11 | Leitrim | 27.6/16kV | 49F1 | Replaced blown transformer X13868 at 1469 Kingsdale Ave | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7222 | 2005 | 8 | 27 | 0.10694 |  | 53 | 15 | 17 | Leitrim | 27.6/16kV | 49F1 | G654W phase fuse found blown, circuit was patrolled. No Apparent cause. Fuse was replaced & closed . All power was restored. | Gloucester | Unknown/Other | No Apparent Cause
5746 | 2004 | 8 | 29 | 0.67014 |  | 125 | 96 | 46 | Leitrim | 27.6/16kV | 49F1 | Fuse blown at switch G321, circuit patrol revealed a blown tie-top insulator. Insulator replaced & circuit refused. All customers in Kemp Park area restored. | Gloucester | Adverse Weather | Lightning
7278 | 2005 | 9 | 4 | 0.39792 |  | 167 | 11 | 4 | Leitrim | 27.6/16kV | 49F1 | Dave Guy found a blown switch at G216B at 12:01 pm on Stevenage & Hawthrone and patrol the O/H and found nothing, refused and holding. The outage was longer then normal because they were busy with an outage in Kanata. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9165 | 2006 | 9 | 8 | 0.73681 |  | 77 | 1467 | 1143 | LEITRIM | 27.6/16kV | 49F1 | Severe storm in effect, Tree branch on primary on Albion Road. Branch removed and breaker closed and holding. | Ottawa | Adverse Weather | Wind
5797 | 2004 | 9 | 10 | 0.48958 |  | 145 | 123 | 51 | Billberry | 27.6/16kV | 49F1 | A crane made contact with the O/H and left causing the switch G953 trip on Queensdale Ave. | Gloucester | Foreign Interference | Vehicle
13220 | 2008 | 9 | 12 | 0.14514 |  | 195 | 3578 | 1143 | Leitrim | 27.6/16kV | 49F1 | SCADA indicates 49F1 auto reclosed twice before locking out. Cause was a 49F1 cable fault at the Leitrim station between the station breaker and the overhead. Load was restored in sections due to cold load pick up. | Gloucester | Defective Equipment
11300 | 2007 | 9 | 13 | 0.44514 |  | 47 | 10 | 13 | Leitrim | 27.6/16kV | 49F1 | Refused transformer X13879 at 1613 Queensdale Ave (Squirrel contact) | Gloucester | Foreign Interference | Animal
13240 | 2008 | 9 | 16 | 0.36458 |  | 25 | 2 | 4 | Leitrim | 27.6/16kV | 49F1 | Transformer #18294, located at 4281 Blake Rd. Isolated due to neutral down on Open Bus, to make repairs | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17030 | 2010 | 9 | 30 | 0.38472 |  | 281 | 66 | 14 | Leitrim | 27.6/16kV | 49F1 | Transformer TP6751 @ 201 ESPRESSO PVT was isolated to allow a contractor to pull in copper secondary cables. | Gloucester | Scheduled Outage | Construction
15234 | 2009 | 10 | 8 | 0.54722 |  | 185 | 371 | 131 | Bayshore | 8/4.8kV | 49F1 | Cable ault cause R and B phase fuses to blow at S807. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13349 | 2008 | 10 | 9 | 0.43333 |  | 101 | 163 | 97 | Lietrim | 27.6/16kV | 49F1 | 10:24 customer calls from Kingsdale Ave, OMS reports G302 Bphase is suspected open, S Muldoor reports bottom lead is off of switch, restore efforts delayed as Muldoon's partner A Langville is on light duty. Muldoon had to wait for a 3rd man. Cut out replaced and switch close to restore all load at 12:05 pm. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17089 | 2010 | 10 | 10 | 0.46042 |  | 61 | 18 | 18 | Leitrim | 27.6/16kV | 49F1 | Squirrel caused the fuse to blow at transformer 18237. | Gloucester | Foreign Interference | Animal
4241 | 2003 | 10 | 11 | 0.36528 |  | 275 | 33 | 29 | Leitrim | 27.6/16kV | 49F1 | Blown lightning arrester . | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7473 | 2005 | 10 | 17 | 0.69653 |  | 67 | 22 | 20 | Bayshore | 8/4.8kV | 49F1 | TE260 found partially knocked off pad & elbow pulled off feed to TE256. Transformer put back on pad & elbow installed. | Nepean | Foreign Interference | Vehicle
9519 | 2006 | 10 | 26 | 0.50347 |  | 19 | 158 | 500 | Leitrim | 27.6/16kV | 49F1 | During switching to transfer part of Leitrim 49F1 load to Limebank7F2, GR1 tripped causing an outage to part of 49F1 & part of 7F2. The recloser trip setting was checked at request of system by stations dept & reported in correct position to accept increased load. Recloser reset & closed restoring all customers. | Gloucester | Human Element | Incorrect Protection Settings
15342 | 2009 | 10 | 31 | 0.79236 |  | 188 | 6 | 2 | Bayshore | 8/4.8kV | 49F1 | Crew replaced defective switch at overhead transformer X37042 feeding 3095 carling ave. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
15357 | 2009 | 11 | 6 | 0.38889 |  | 226 | 19 | 5 | Leitrim | 27.6/16kV | 49F1 | Crew replaced transformer TE809 @ 3323 Hogarth. | Gloucester | Scheduled Outage | Construction
13582 | 2008 | 11 | 9 | 0.33333 |  | 102 | 101 | 95 | Lietrim | 27.6/16kV | 49F1 | Squirrell made contact on the overhead at Queensdale between Bank and Conroy caused G953 white phase to open, refused. Transformer X14417 at 1909 Queensdale fuse blown, also refused | Gloucester | Foreign Interference | Animal
17255 | 2010 | 11 | 10 | 0.5625 |  | 40 | 3 | 5 | Leitrim | 27.6/16kV | 49F1 | Transformer #X13911 located at 1473 Queensdale opened by crew to install new service | Gloucester | Scheduled Outage | Construction
4449 | 2003 | 11 | 13 | 0.89583 |  | 30 | 2 | 3 | Leitrim | 27.6/16kV | 49F1 | Switch G476W, on Conroy Road, opened due to tree interference. The problem was removed and power was restored.ID#4449 | Gloucester | Adverse Weather | Wind
7604 | 2005 | 11 | 13 | 0.38125 |  | 61 | 10 | 10 | Leitrim | 27.6/16kV | 49F1 | Refused Transformer # GL003549 at 1611 Kingsdale and restored power | Ottawa | Unknown/Other
7615 | 2005 | 11 | 15 | 0.49722 |  | 49 | 1 | 1 | BAYSHORE | 8/4.8kV | 49F1 | AL COONEY REPORTED POLE FIRE @ S433 WITH ONE APARTMENT BUILDING FED OFF THE SWITCH (VT69). FIRE WAS EXTINGUISHED BUT DUE TO DAMAGES REPAIRS HAD TO BE MADE. THE 49F1 CIRCUIT WAS DUMPED FOR EMERGENCY REPAIRS. | Nepean | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
7616 | 2005 | 11 | 15 | 0.51042 |  | 30 | 322 | 643 | bayshore | 8/4.8kV | 49F1 | DUE TO POLE FIRE AT S433, 49F1 HAD TO BE OPENED FOR EMERGENCY REPAIRS. REPAIRS WERE MADE TO POLE 49F1 CLOSED AND HELD TO RESTORE POWER TO ALL CUSTOMERS. | Nepean | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
15412 | 2009 | 11 | 23 | 0.48958 |  | 217 | 25 | 7 | Letrim | 27.6/16kV | 49F1 | TP3056 @ 100 Issam Pvt was isolated by the crew for transformer replacement. | Gloucester | Scheduled Outage | Repair
4555 | 2003 | 12 | 4 | 0.5 |  | 54 | 579 | 643 | Bayshore | 8/4.8kV | 49F1 | An insulator at the corner of Carling and Maplehurst failed causing a flash and the opening of the 49F1 breaker at the station. As the breaker was on hold-off at the time, the circuit tripped instantaneously and went to lockout. The defective insulator was replaced and the power was restored. ID#4555 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
5991 | 2004 | 12 | 8 | 0.32153 |  | 151 | 189 | 75 | Leitrim | 27.6/16kV | 49F1 | An insulator broke on the O/H line on Russell Rd, The switch at G216 W,B phase was found blown. The O/H line from switch 216 was isolated for repairs. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6002 | 2004 | 12 | 9 | 0.7125 |  | 30 | 2 | 4 | Leitrim | 8/4.8kV | 49F1 | Transformer 3155 off Queensdale | Gloucester | Scheduled Outage | Repair
11848 | 2007 | 12 | 14 | 0.15972 |  | 90 | 45 | 30 | Leitrim | 27.6/16kV | 49F1 | At Glenfield and Overton in the Hawthorn area, at the entrance to a snow dump a bell wire was down which caused phases to slap together blowing G216 RWB fuses. Bell and Police notified and G216 closed and holding. | Gloucester | Foreign Interference | Vehicle
4615 | 2003 | 12 | 17 | 0.55208 |  | 47 | 1 | 1 | Limebank | 27.6/16kV | 49F1 | Sectionalizer switch SE43-VE85 tripped open, interupting vaults VE85 & VE86 at the Ottawa Airport. Testing of switch required to verify cause of switch operation. | Gloucester | Defective Equipment
4616 | 2003 | 12 | 17 | 0.63542 |  | 30 | 0 | 1 | Limebank | 27.6/16kV | 49F1 | Sectionalizer switch SE43-VE85 tripped open, interupting vaults VE85 & VE86 at the Ottawa Airport. Testing of switch required to verify cause of switch operation. | Gloucester | Defective Equipment
4889 | 2004 | 3 | 14 | 0.51597 |  | 174 | 4518 | 2558 | Leitrim | 27.6/16kV | 49F1 49F2 | Insulator broke between G254LB and Hawthorne Rd on the 49F2. 49F2 recloser operated but fault also caused the blue phase high side fuse to blow on the 49T1. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9900 | 2007 | 1 | 3 | 0.96528 |  | 80 | 1 | 1 | LEITRIM | 27.6/16kV | 49F2 | Transformer switch failed at 6055 RUSSELL RD. 24/7 replaced defective cut-out all power was restored. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
13837 | 2009 | 1 | 5 | 0.43681 |  | 10 | 326 | 1956 | Leitrim | 27.6/16kV | 49F2 | 49F2 circuit open NO apperant cause found at this time. | Gloucester | Unknown/Other | No Apparent Cause
13870 | 2009 | 1 | 15 | 0.19375 |  | 129 | 17 | 8 | Leitrim | 27.6/16kV | 49F2 | Wire down on Mitch Own 6 span east of G180W. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9954 | 2007 | 1 | 20 | 0.3 |  | 493 | 25 | 3 | Leitrim | 27.6/16kV | 49F2 | Line section at Leitrim & Hawtorne was isolated to move conductor to new poles. 3 overhead transformers were interrupted. | Gloucester | Scheduled Outage | Construction
3151 | 2003 | 2 | 1 | 0.56597 |  | 50 | 48 | 58 | Leitrim | 27.6/16kV | 49F2 | Fire call, 24/7 crew found that the crossarm on the pole was burnt in two. Line was isolated using Scadamate G26SM. Repairs were made and power restored. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
15705 | 2010 | 2 | 3 | 0.95625 |  | 333 | 17 | 3 | Leitrim | 27.6/16kV | 49F2 | 24/7 reported that Transformer X20107 at 6037 Russell rd was defective. Oncall replaced transfomer | Gloucester | Defective Equipment
3158 | 2003 | 2 | 4 | 0.65417 |  | 69 | 15 | 13 | Leitrim MS | 27.6/16kV | 49F2 | Section of the 49F2 at Ramsey and Russel Rd had to be interupted so as Line Crew could extinguish pole fire. | Gloucester | Adverse Weather | Rain
15730 | 2010 | 2 | 19 | 0.40556 |  | 119 | 44 | 22 | Lietrim | 27.6/16kV | 49F2 | PC10A# 7615, placed in effect to allow crew to relocate the feed to this switch, affecting 22 customers on Analdea Dr. | Gloucester | Scheduled Outage
4851 | 2004 | 3 | 3 | 0.65625 |  | 660 | 11 | 1 | Leitrim | 27.6/16kV | 49F2 | D. Howat reports transformer # 1147 is defective and needs to be replaced. On call crew called into replace 150 KVA transformer. Crew replaced transformer, and found secondary defective. Cia isolation taken by Black Electric to repair secondary. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10090 | 2007 | 3 | 5 | 0.40347 |  | 209 | 17 | 5 | Leitrim | 27.6/16kV | 49F2 | At 09:41 trans at 4269 Ramsayville Rd was isolated in order to transfer plant to new pole | Gloucester | Scheduled Outage | Preventive Maintenance
7990 | 2006 | 3 | 6 | 0.0090278 |  | 58 | 1 | 1 | Leitrim | 27.6/16kV | 49F2 | Racoon cause fue to blow on overhead transformer at 4879 Bank St | Gloucester | Foreign Interference | Animal
3230 | 2003 | 3 | 7 | 0.57292 |  | 18 | 1 | 3 | Leitrim | 27.6/16kV | 49F2 | Transformer #574 fuse opened by Lineman, due to secondary connections burning up. Customers notified. | Gloucester | Defective Equipment
10105 | 2007 | 3 | 10 | 0.94792 |  | 74 | 57 | 46 | Leitrim | 27.6/16kV | 49F2 | 49F2 A/R when G321B opened. Patrol found no problem except branches in vicinity of o/h line. Branches trimmed & fuse replaced. | Gloucester | Tree Contacts | Inadequate Trimming
4891 | 2004 | 3 | 14 | 0.57986 |  | 7 | 45 | 385 | Leitrim | 27.6/16kV | 49F2 | G254LB opened in the field and G635SM closed in the field by Howat. 49T1 blue pahse fuse blown and load transferred to 7F4. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4893 | 2004 | 3 | 14 | 0.59028 |  | 67 | 251 | 759 | Leirtim | 27.6/16kV | 49F2 | 49F2 breaker open trom SCADA switch G782 open and G313 closed to pick up customers. Repairs to insulator nade and switch G254LB closed and the last of the customers on. Switching due to blue phase high side fuse blown on 49F1 | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
8043 | 2006 | 3 | 17 | 0.83333 |  | 40 | 3 | 4 | Leitrim | 27.6/16kV | 49F2 | Jiim Yeldon opened transformer GL5505 at 4282 Eighth Line to change a broken switch | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15817 | 2010 | 3 | 18 | 0.44653 |  | 49 | 18 | 22 | Leitrim | 27.6/16kV | 49F2 | Overhead crew isolated customers fed from G667 Bank at Analdea in order to return the feed to its normal red phase feed. | Gloucester | Scheduled Outage
10155 | 2007 | 3 | 21 | 0.96667 |  | 15 | 11 | 45 | Lietrim | 27.6/16kV | 49F2 | G321B single phase radial local was isolated to replace an insulator on Orville Kemp that was tracking in the wet weather | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
3284 | 2003 | 3 | 22 | 0.55208 |  | 35 | 5 | 9 | Leitrim | 27.6/16kV | 49F2 | 24/7 reports open bus service to 5003 9th line rd defective. Transformer open to repair service to customers. All customers notified to outage to repair defective wire. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
10160 | 2007 | 3 | 22 | 0.70903 |  | 343 | 5040 | 1401 | Leitrim | 27.6/16kV | 49F2 | SCADA indicated 49F2 tripped 3 times, A/R/A/R/A and locked out. Two locations on Louis Sieze found with broken insulators, section on Louis Sieze isolated for repair | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3303 | 2003 | 3 | 26 | 0.78472 |  | 340 | 40 | 7 | Leitrim MS | 27.6/16kV | 49F2 | Overhead transformer 3235 at 2149 Ramseyville Rd had to be replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10176 | 2007 | 3 | 26 | 0.44236 |  | 111 | 1778 | 1410 | Leitrim | 27.6/16kV | 49F2 | 49F2 cct tripped when an insulator on the primary line at 4794 Bank st failed. A section of line was isolated & power restored to most customers. Remaining customers power was restored when repairs were completed. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
15856 | 2010 | 3 | 26 | 0.42014 |  | 135 | 7 | 3 | Leitrim | 27.6/16kV | 49F2 | TP5561 at 353 Widgeon Way, Findlay Creek was replaced due to a broken bushing that was leaking oil. Only 2 of the 9 houses were occupied the rest were still under ownership of Tartan/Tamarack Homes. | Gloucester | Defective Equipment
6338 | 2005 | 3 | 30 | 0.55556 |  | 27 | 3 | 6 | Leitrim | 27.6/16kV | 49F2 | Isolated Transformer 237 at 4517 Anderson rd to replace a defective cutout | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15873 | 2010 | 3 | 30 | 0.38611 |  | 679 | 23 | 2 | Leitrim | 27.6/16kV | 49F2 | transformer TP5561 @ 355 widgeon was was isolated for crew to remove transformer and pad for oil spill cleanup. | Gloucester | Scheduled Outage | Repair
3321 | 2003 | 4 | 7 | 0.57083 |  | 2 | 47 | 1414 | Leitrim | 4.16kV | 49F2 | 49F2 tripped and locked out under hold off circuit was closed right away and held.The cause was later found to be a squirrel on Anderson road. | Gloucester | Foreign Interference | Animal
12249 | 2008 | 4 | 8 | 0.10764 |  | 7 | 323 | 3274 | Liembank | 27.6/16kV | 49F2 | 49F2 (carrying 49F1 as well) was opened due to blown fuse at 49T1L-X, to separate and restore 49F1 and 49F2 on separate Limebank supplies | Gloucester | Unknown/Other | No Apparent Cause
12254 | 2008 | 4 | 8 | 0.12083 |  | 831 | 14 | 1 | leitrim | 27.6/16kV | 49F2 | Rideau Carleton Raceway was unable to close secondary breakers after outage on 49T1 transformer. PMH9 was isolated to all contactor to megger cables from switch gear to transformer, and test 3000/4000 KVA transformer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14154 | 2009 | 4 | 8 | 0.34583 |  | 412 | 69 | 10 | Leitrim | 27.6/16kV | 49F2 | TP3117 transformer on Henry Farm Dr isolated to allow 18 new transformers to be added to the loop. | Gloucester | Scheduled Outage | Construction
14165 | 2009 | 4 | 11 | 0.47361 |  | 58 | 52 | 54 | Leitrim | 27.6/16kV | 49F2 | At 11:22am customers in the area of Leitrim & Hawthorne called in with no power calls. Crews found broken fuse insert at G902R. Crews replaced broken cutout, 54 customers affected for 58min. (Leitrim 49F2) ID#14165. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6401 | 2005 | 4 | 12 | 0.41944 |  | 129 | 28 | 13 |  | 27.6/16kV | 49f2 | Planned outage to 3 transformers on Kemp Drive. (removed 2 spans of conductor) | Gloucester | Scheduled Outage
14169 | 2009 | 4 | 12 | 0.91458 |  | 48 | 1 | 1 | Lietrim | 27.6/16kV | 49F2 | Transformer at rear of 4135 Ramseyville Rd was isolated to allow crew to fix sparking transformer and replace fuse. | Gloucester | Defective Equipment
15942 | 2010 | 4 | 15 | 0.47361 |  | 179 | 30 | 10 | Leitrim | 27.6/16kV | 49F2 | TP4994 at 153 Bufflehead was isolated to replace transformer. | Gloucester | Scheduled Outage
6420 | 2005 | 4 | 18 | 0.40625 |  | 42 | 1 | 1 | Leitrim | 27.6/16kV | 49F2 | Transformer #GL000414 located at 4650 Leitrim Rd, Gloucester, isolated due to system neutral was broken at the tranformer location | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12326 | 2008 | 4 | 23 | 0.39514 |  | 86 | 26 | 18 | Leitrim | 27.6/16kV | 49F2 | TP2947 at 4075 Kelly Farm Dr replaced due to a oil leak. TP3116 also out due to being a radial supply. | Gloucester | Scheduled Outage | Preventive Maintenance
12327 | 2008 | 4 | 23 | 0.39583 |  | 104 | 36 | 21 | Leitrim | 27.6/16kV | 49F2 | 2 transformers (#TP2947 & TP3116) isolated at 4073 & 4080 Kelly Farm Dr to replace a leaking transformer | Gloucester | Scheduled Outage | Construction
15992 | 2010 | 4 | 25 | 0.69167 |  | 114 | 142 | 107 | Leitrim | 27.6/16kV | 49F2 | Switch G271 W blew due to tractor running into Hydro Pole and caused wires to come down. Secondary Wires cleared. G271 Refused and closed. Repairs made to secondary, refused transformer and restored power to remaining five customers. | Gloucester | Foreign Interference | Vehicle
14255 | 2009 | 4 | 27 | 0.65625 |  | 315 | 116 | 22 | Leitrim | 27.6/16kV | 49F2 | A fallen tree caused a section of primary line on Ramsayville rd N. of Leitrim rd to come down. Crew opened G738R to make repairs. | Gloucester | Tree Contacts | Tree Fallen
16007 | 2010 | 4 | 27 | 0.97222 |  | 320 | 27 | 5 | Leitrim | 27.6/16kV | 49F2 | Defective transformer replaced at 4530 Eighth line | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
3383 | 2003 | 4 | 28 | 0.52222 |  | 570 | 1416 | 998 | Leitrim | 27.6/16kV | 49F2 | Truck hit hydro pole on Albion & Del Zotto st. Causing outage on 49F2 & 7F4 circuits. | Gloucester | Foreign Interference | Vehicle
16039 | 2010 | 5 | 5 | 0.10625 |  | 85 | 60 | 42 | Lietrim | 27.6/16kV | 49F2 | Crew found switch G434 fuse blew on one phase, after a quick patrol, crew re-fused and power was restored. Customers affected on Mitch Owens and Hawthorn Rd. | Gloucester | Unknown/Other
14322 | 2009 | 5 | 7 | 0.25833 |  | 175 | 169 | 58 | Lietrim | 27.6/16kV | 49F2 | A broken insulator on 49F2 red phase overhead on Anderson Road between Eighth Line and Nineth Line Roads caused G212 fused switch to open | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3418 | 2003 | 5 | 9 | 0.43264 |  | 112 | 93 | 50 | Leitrim | 27.6/16kV | 49F2 | A pole top insulator went defective causing switch G271W to break and the fuse to rupture. The switch and fuse were replaced and closed without first patrolling the line and the fuse once again ruptured. The insulator was temporarily repaired and the fuse replaced and closed. Full power was restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10394 | 2007 | 5 | 9 | 0.62153 |  | 35 | 4 | 7 | Leitrim | 27.6/16kV | 49F2 | Transformer #GL000279 located at 3732 8th Line Rd isolated due to changing insulators & switches | Gloucester | Scheduled Outage | Preventive Maintenance
10399 | 2007 | 5 | 10 | 0.44097 |  | 25 | 3 | 7 | Leitrim | 27.6/16kV | 49F2 | Isolated transformer 4885 at 1400 Louiseize Rd to replace switch and primary insulator | Gloucester | Scheduled Outage | Preventive Maintenance
5131 | 2004 | 5 | 11 | 0.50347 |  | 145 | 22 | 9 | Leitrim | 27.6/16kV | 49F2 | Transformer at 3839 Leitrim Rd relocated. | Gloucester | Scheduled Outage | Construction
5135 | 2004 | 5 | 12 | 0.43056 |  | 64 | 21 | 20 | LIETRIM | 27.6/16kV | 49F2 | To allow crews to re-arrange primary cables to transformers. | Gloucester | Scheduled Outage | Construction
10415 | 2007 | 5 | 14 | 0.47014 |  | 12 | 0 | 1 | Leitrim | 27.6/16kV | 49F2 | isolated transformer 137, at 3940 eighth line rd, to replace broken insulator | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10416 | 2007 | 5 | 14 | 0.56528 |  | 46 | 1 | 1 | Leitrim | 27.6/16kV | 49F2 | isolated transformer 997, at 4100 eighth line rd, to replace broken insulator | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14356 | 2009 | 5 | 14 | 0.43542 |  | 273 | 287 | 63 | Lietrim | 27.6/16kV | 49F2 | Tree fell onto circuit causing switch G308B to open. Tree removed and customers restored from the alternate feed switch G381W. | Gloucester | Tree Contacts
14357 | 2009 | 5 | 14 | 0.63194 |  | 20 | 6 | 19 | Lietrim | 27.6/16kV | 49F2 | Switch G900 on Farmers Way at Eighth Line was overheating and had to be replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14364 | 2009 | 5 | 15 | 0.41528 |  | 86 | 34 | 24 | Leitrim | 27.6/16kV | 49F2 | Transformer TP4985 at 322 Creston Valley Way isolated for replacement. Transformers TP4984, 4983 & 4986 in the Findley Creek area also affected. | Gloucester | Scheduled Outage
6565 | 2005 | 5 | 17 | 0.39931 |  | 93 | 16 | 10 |  | 27.6/16kV | 49f2 | Planned outage Findlay Creekto raise transformer base. | Gloucester | Scheduled Outage
6566 | 2005 | 5 | 17 | 0.475 |  | 65 | 11 | 10 |  | 27.6/16kV | 49f2 | Isolation of T3187 in Findlay Creek to raise transformer base. | Gloucester | Scheduled Outage
3457 | 2003 | 5 | 20 | 0.85694 |  | 373 | 108 | 40 | Leitrim | 27.6/16kV | 49F2 | Red phase conductor crossing 417 fell into the neutral due to pole fire. Cuts installed on each side of the 417 and customers restored. | Gloucester | Defective Equipment
8356 | 2006 | 5 | 26 | 0.020139 |  | 261 | 748 | 249 | Leitrim | 27.6/16kV | 49F2 | Insulator flashed over at transformer 660, 5205 Farmers Way, causing GR6 Blue phase to open. Crew had difficulty closing GR6, due to blown control fuse. | Gloucester | Defective Equipment
3499 | 2003 | 5 | 29 | 0.83333 |  | 135 | 4 | 2 | Leitrim | 27.6/16kV | 49F2 | Blown fuse replaced. Crew could not find any noticable cause. | Gloucester | Unknown/Other
5228 | 2004 | 5 | 31 | 0.39583 |  | 55 | 11 | 12 | Leitrim | 27.6/16kV | 49F2 | To allow crew to remove double insert. | Gloucester | Scheduled Outage | Preventive Maintenance
5241 | 2004 | 6 | 1 | 0.82847 |  | 90 | 10 | 7 | Leitrim | 27.6/16kV | 49F2 | Switch G880B opened on Hall Rd in Gloucester because of weather and lightning. | Gloucester | Adverse Weather | Lightning
8410 | 2006 | 6 | 2 | 0.375 |  | 78 | 18 | 14 | Bayshore | 8/4.8kV | 49F2 | isolated transformer TP2967 at 188 woodridge so it could be changed out | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14459 | 2009 | 6 | 4 | 0.45556 |  | 289 | 202 | 42 | Bayshore | 8/4.8kV | 49F2 | TP5513 at 106 Woodbridge was isolated to allow crew to replace transformer for the PCB replacement program. | Ottawa | Scheduled Outage | Preventive Maintenance
14506 | 2009 | 6 | 10 | 0.37778 |  | 341 | 11 | 2 | Bayshore | 8/4.8kV | 49F2 | TP5514 @ 110 Woodridge was isolated for PCB transformer replacement program. | Nepean | Scheduled Outage | Repair
14509 | 2009 | 6 | 10 | 0.35903 |  | 373 | 62 | 10 | Bayshore |  | 49F2 | At 08:37 trans at 106 woodridge cres was isoalted ini oder to make repairs to the trans base | Nepean | Scheduled Outage | Repair
5284 | 2004 | 6 | 11 | 0.42708 |  | 200 | 3 | 1 | Leitrim | 27.6/16kV | 49F2 | Transformer GL 000590 at 3344 Rideau Rd out to reconstuct pole. | Gloucester | Defective Equipment
14521 | 2009 | 6 | 11 | 0.39306 |  | 393 | 196 | 30 | Bayshore | 8/4.8kV | 49F2 | TP5515 was isolated to allow crews to replace transformer due to PCB. | Nepean | Scheduled Outage | Preventive Maintenance
16251 | 2010 | 6 | 11 | 0.47014 |  | 21 | 35 | 100 | Leitrim | 27.6/16kV | 49F2 | S25064 opened to allow broken insulator to be replaced by overhead crew. Location is trailer park. | Gloucester | Scheduled Outage | Repair
6713 | 2005 | 6 | 14 | 0.57292 |  | 185 | 109 | 70 | Leitrim | 27.6/16kV | 49F2 | 49F2 circuit auto reclosured due to a fuse cutout switch blown at 5220 Eight Line RD. Switch cutout replaced at 5220 eight line RD all power restored. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
3566 | 2003 | 6 | 15 | 0.57292 |  | 74 | 125 | 101 | Leitrim | 27.6/16kV | 49F2 | G606R Blown due to a vehicle accident on Russel road pole was broken clear and circuit was reenergized. NOTE: First calls received from customers have power out and call from police of a traffic accident. 14:02 | Gloucester | Foreign Interference | Vehicle
12675 | 2008 | 6 | 16 | 0.81597 |  | 199 | 72 | 50 | Leitrim | 27.6/16kV | 49F2 | Lightning caused tree to fall on section of 49F2 along Mitch Owens Rd which also caused G271W fuse to blow. Crew reported 3 spans of neutral & primary have been taken down east of G180W, from tree contact. G180W to end of line was isolated & power was restored from G271W to G180W. Crew repaired line section then restored power by closing G180W to end of line, all customers are restored. | Gloucester | Adverse Weather | Lightning
14548 | 2009 | 6 | 16 | 0.36111 |  | 415 | 14 | 2 | Bayshore | 8/4.8kV | 49F2 | Transformer #TP6148 located at 114 Woodridge Cres Nepean isolated due to a PCB change | Nepean | Scheduled Outage | Construction
16282 | 2010 | 6 | 17 | 0.90625 |  | 82 | 1 | 1 | Leitrim | 27.6/16kV | 49F2 | Transformer #GL87 located at 8515 Mitch Owens opened up, crew patrolled and could not find cause | Gloucester | Unknown/Other | No Apparent Cause
6759 | 2005 | 6 | 18 | 0.78125 |  | 325 | 27 | 5 | Leitrim | 27.6/16kV | 49F2 | RX401 was changed at 5980 Eight Line Rd. Transformer was flashed at primary bushing. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12687 | 2008 | 6 | 18 | 0.38958 |  | 74 | 583 | 473 | Lietrim | 27.6/16kV | 49F2 | Sectionalizer SC2000 isolated to pull new cables into the -L2 cubicle. | Gloucester | Scheduled Outage | Construction
14568 | 2009 | 6 | 18 | 0.37917 |  | 405 | 256 | 38 | Bayshore | 8/4.8kV | 49F2 | Transfomer TP5516 @ 118 Woodridge was isolated for PCB transformer replacement program. | Ottawa | Scheduled Outage | Repair
8545 | 2006 | 6 | 19 | 0.80694 |  | 223 | 697 | 225 | Leitrim | 27.6/16kV | 49F2 | G283 W&B Found Blown, as well as G959R found blown causing 49F2 to auto reclose. Severe thunder and lightning storm in effect. | Gloucester | Adverse Weather | Lightning
14602 | 2009 | 6 | 24 | 0.38542 |  | 177 | 32 | 11 | Leitrim | 27.6/16kV | 49F2 | TP3116 at 4084 Kelly Farm in Findlay Creek was isolated to allow crews to pull in new primary cables to extend Tx loop. | Gloucester | Scheduled Outage | Construction
6811 | 2005 | 6 | 25 | 0.63889 |  | 300 | 250 | 50 |  | 27.6/16kV | 49f2 | Heavy rains caused branches to touch circuit and fuse blow at G271. | Gloucester | Adverse Weather
6812 | 2005 | 6 | 25 | 0.63889 |  | 325 | 103 | 19 | Leitrim | 27.6/16kV | 49F2 | Heavy rains caused branches to touch wires and cause G230 to blow. | Gloucester | Adverse Weather | Rain
12751 | 2008 | 6 | 26 | 0.76389 |  | 90 | 64 | 43 | Leitrim | 27.6/16kV | 49F2 | Stormy weather caused G271W on Mitch Owens @ Farmers way to blow. Line sectin patrolled & fuse replaced. | Gloucester | Adverse Weather | Lightning
14625 | 2009 | 6 | 26 | 0.82917 |  | 241 | 177 | 44 | Leitrim | 27.6/16kV | 49F2 | Crew patrolled line N. 8th line on Farmers Way , found defective fuse barrel @ G540R, same replaced & power restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6827 | 2005 | 6 | 28 | 0.41806 |  | 392 | 155 | 30 | Bayshore | 8/4.8kV | 49F2 | Replace cables and relocate transformer on Woodridge cresant Bayshore Area. TE170 and TE171 and TE152 | Nepean | Scheduled Outage | Preventive Maintenance
16359 | 2010 | 6 | 29 | 0.43125 |  | 113 | 41 | 22 | Leitrim | 27.6/16kV | 49F2 | TP2254 and TP2257 on Meadowilly and Cache Bay were isolated to allow crews to rearrange primary conductor. | Ottawa | Scheduled Outage | Construction
6847 | 2005 | 7 | 1 | 0 |  | 1925 | 642 | 20 | leitrim | 27.6/16kV | 49F2 | Circuit patrolled, and found G289R phase fuse opened. Fuse replaced and closed . | Gloucester | Adverse Weather | Lightning
14666 | 2009 | 7 | 4 | 0.60833 |  | 128 | 4 | 2 | Leitrim | 27.6/16kV | 49F2 | Transformer #X18134 located at 4516 Ramsayville Rd Glouc isolated, no apparent cause | Gloucester | Unknown/Other | No Apparent Cause
3691 | 2003 | 7 | 7 | 0.25556 |  | 47 | 39 | 50 | Leitrim | 27.6/16kV | 49F2 | Mike reports G271W phase fuse found open. Circuit was patrolled no cause found. G271W phase fuse was replaced all power restored. | Gloucester | Unknown/Other | No Apparent Cause
10813 | 2007 | 7 | 8 | 0.18333 |  | 246 | 418 | 102 | Leitrim | 27.6/16kV | 49F2 | 49F2 circuit auto reclosed. Outage reported on Hall St & Russell Rd. On call crew dispatched to area. Broken cutout feeding Transformer 399 was replaced, and refused G606R to restore all power. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
10815 | 2007 | 7 | 8 | 0.38194 |  | 10 | 1 | 7 | Leitrim | 27.6/16kV | 49F2 | Transformer #GL004206 located at 4906 Eighth Line Rd isolated to replace broken cutout | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16440 | 2010 | 7 | 9 | 0.72014 |  | 316 | 7384 | 2217 | Leitrim | 27.6/16kV | 49F2 | 49F2 opened due to multiple tree contacts in various location on the 49F2 overhead. The 49F2 was restored in sections as crews were able to remove tree obstructions. | Gloucester | Adverse Weather
14717 | 2009 | 7 | 11 | 0.5 |  | 255 | 187 | 44 | Leitrim | 8/4.8kV | 49F2 | Brian Kuhn reported Pole fire on Mitch Ownes, East of Anderson (8369), Opened G271W to isolate. Drain All required | Gloucester | Defective Equipment
16460 | 2010 | 7 | 12 | 0.80833 |  | 31 | 3 | 20 | Leitrim | 8/4.8kV | 49F2 | Tree contact caused transfomer 5761at 5775 9th Line and G880 fuse cut out to open interrupting customers on Halls and 9th line for 31 minutes. 20 customers were affected. Leitrim (49F2) | Gloucester | Tree Contacts | Tree Limb Fallen
16466 | 2010 | 7 | 13 | 0.66806 |  | 51 | 4 | 5 | Leitrim | 27.6/16kV | 49F2 | A blown lightning arrestor on nineth Line Rd caused the G880 b phase to blow. | Gloucester | Adverse Weather | Lightning
6925 | 2005 | 7 | 14 | 0.98958 |  | 125 | 450 | 1414 | Leitrim | 27.6/16kV | 49F2 | G54RB blown due to defective transformer at 4930 Bank St. Opened 49F2 breaker for crew to perform dead operation and pick up from breaker. | Gloucester | Adverse Weather | Lightning
8750 | 2006 | 7 | 17 | 0.98403 |  | 121 | 2844 | 1410 | Letrium | 27.6/16kV | 49F2 | 49F2 circuit patrolled and no aparant cause found. Trip due to lightining. | Gloucester | Lightning | Direct Strike
8767 | 2006 | 7 | 18 | 0.38542 |  | 130 | 2 | 1 | Leitrim | 27.6/16kV | 49F2 | Transformer located at 3799 Hawthorne isolated due to lightning | Gloucester | Lightning | Direct Strike
7005 | 2005 | 7 | 21 | 0.9625 |  | 194 | 213 | 66 | Leitrim |  | 49F2 | Transformer 1794 secondary switch at 4747 Anderson Rd replaced. G212 new fuse installed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10927 | 2007 | 7 | 22 | 0.56597 |  | 186 | 149 | 65 | Leitrim | 27.6/16kV | 49F2 | Customer was trimming trees a branch fall on overhead conductor causing Blue phase to burn down. Tree was located at 5470 Ninth line RD. | Gloucester | Tree Contacts | Tree Limb Fallen
5565 | 2004 | 7 | 25 | 0.24306 |  | 130 | 17 | 8 | Leitrim | 27.6/16kV | 49F2 | Sqirrel opened transfomer T402 at 6007 eighth line rd. | Gloucester | Foreign Interference | Animal
12954 | 2008 | 7 | 27 | 0.37431 |  | 160 | 8 | 3 | Bayshore | 8/4.8kV | 49F2 | At 11:37 trans at 7 Leeming Dr was refused power restored.. No apparent cause for failure | Ottawa | Unknown/Other
14876 | 2009 | 7 | 29 | 0.55972 |  | 116 | 100 | 534 | Leitrim | 8/4.8kV | 49F2 | GR6 locked out due to Reclosure Blocked, Forestry Surrendered Holdoff and restored Crews patrolling the circuit found S23796 Fuse blown | Gloucester | Adverse Weather | Lightning
14887 | 2009 | 7 | 31 | 0.91319 |  | 30 | 2 | 3 | Leitrim | 27.6/16kV | 49F2 | Pole on Anderson South of Lietrim was broken off by vehicle. Crews replaced pole and required short outage to attach plant to new pole. | Gloucester | Foreign Interference | Vehicle
14888 | 2009 | 8 | 1 | 0.18125 |  | 159 | 124 | 55 | Leitrim | 27.6/16kV | 49F2 | Rx'd customer cals of outage in Carlsbad area, Crew patrolled line and found broken cutout (barrel still in tack) on radial feed at 6097 Russell. Further Patrol Found G606R. G606R closed then crew repaired broken cutout. | Gloucester | Defective Equipment
7055 | 2005 | 8 | 2 | 0.77292 |  | 202 | 113 | 59 | Leitrim | 27.6/16kV | 49F2 | D. Howart reports two trees found in overhead circuit along ninth line Rd. G308B fuse replaced and holding. 2 transformer cutouts replaced in the area of Halls & Ninth Line. | Gloucester | Tree Contacts | Tree Limb Fallen
3844 | 2003 | 8 | 4 | 0.82083 |  | 51 | 1 | 1 | Leitrim | 27.6/16kV | 49F2 | Customer reports power at barn out. Fuse blown at pole. 24/7 refused transformer all power restored to normal. | Gloucester | Adverse Weather | Lightning
14911 | 2009 | 8 | 4 | 0.80208 |  | 136 | 111 | 49 | Leitrim | 27.6/16kV | 49F2 | Switch G540R fuse blew due to adverse weather. | Nepean | Adverse Weather | Lightning
14914 | 2009 | 8 | 4 | 0.80208 |  | 198 | 198 | 60 | Leitrim | 27.6/16kV | 49F2 | Switch G606R blew due to adverse weather. | Nepean | Adverse Weather | Lightning
16634 | 2010 | 8 | 4 | 0.016667 |  | 148 | 96 | 39 | Leitrim | 27.6/16kV | 49F2 | G260RWB found blown. Circuit patrolled nothing found. Lightning in the area. G260RWB closed. | Gloucester | Unknown/Other
13027 | 2008 | 8 | 8 | 0.68472 |  | 353 | 439 | 90 | Bayshore | 8/4.8kV | 49F2 | A defective cable on the W phase bet TE518(133 Woodridge) and Z2-CA2 @ SE1 at Bayshore Ds. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16693 | 2010 | 8 | 8 | 0.47778 |  | 127 | 106 | 75 | Lietrim | 27.6/16kV | 49F2 | Customer reported outage, Crews found G901 Red pahse blown and trees down on Customer owned lines at transformer 238. Customer informed he will require HV contractor and ESA, O/H disconnected and CT'd & G901 refused. | Gloucester | Tree Contacts | Tree Limb Fallen
5661 | 2004 | 8 | 10 | 0.88194 |  | 111 | 111 | 60 | Leitrim | 27.6/16kV | 49F2 | Rudy found G54B blown on Bank St, they patrol the O/H and found nothing. They refused and closed and holding. Lightning in the area. | Gloucester | Adverse Weather | Lightning
5662 | 2004 | 8 | 10 | 0.875 |  | 375 | 250 | 40 | Leitrim | 27.6/16kV | 49F2 | Rudy Grisel reports the G654W on Belgreen, and G289R on sixth line Rd & Russell have blown. The O/H in the area has been patrol and found nothing. The switches has been refused. | Gloucester | Adverse Weather | Lightning
7091 | 2005 | 8 | 10 | 0.30556 |  | 130 | 151 | 100 | Lietrim | 8/4.8kV | 49F2 | G54 RWB fused in line switches found open, flashed insulators found on Bank St near Rideau Rd, also a defective tx switch and blown arrestor at O/H tx 497. Isulators replaced and G54 RWB closed, power restored at 08:50. Tx 497 switch and arrestor replaced power restored at 09:30. | Gloucester | Defective Equipment
16732 | 2010 | 8 | 13 | 0.4375 |  | 80 | 4 | 3 | Leitrim | 27.6/16kV | 49F2 | Trans at 4664 Boundry Rd was isolated in order to change a pole | Gloucester | Scheduled Outage | Preventive Maintenance
8970 | 2006 | 8 | 15 | 0.48472 |  | 32 | 2 | 3 | LEITRIM | 27.6/16kV | 49F2 | G559 ON BLAIS ROAD OPENED TO CHANGE CRACKED INSULATORS. 3 CUSTOMERS AFFECTED. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
16761 | 2010 | 8 | 17 | 0.45486 |  | 75 | 6 | 5 | Leitrim | 27.6/16kV | 49F2 | Transformer #X20318 located at 4692 Boundary opened by crew for pole installation | Gloucester | Scheduled Outage | Construction
14963 | 2009 | 8 | 19 | 0.375 |  | 73 | 13 | 11 | Leitrim | 27.6/16kV | 49F2 | Transformer #TP3116 located at 4084 Kelly farm Dr isolated to repair cracked bushing on transformer | Gloucester | Scheduled Outage | Repair
16779 | 2010 | 8 | 19 | 0.52083 |  | 100 | 5 | 3 | Leitrim | 27.6/16kV | 49F2 | Isolated transformer X20312 at 4739 Boundary Rd to replace pole | Gloucester | Scheduled Outage | Construction
11134 | 2007 | 8 | 23 | 0.39722 |  | 60 | 500 | 500 | Lietrim | 27.6/16kV | 49F2 | Lietrim 49F2 egress cable termination failed and the bus side lead to the R phase of 49F2 also burnt off. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13144 | 2008 | 8 | 24 | 0.99236 |  | 124 | 2261 | 1410 | Leitrim | 27.6/16kV | 49F2 | 49F2 locked out after full reclose cycle (A/R/A/R/A). Crew patrolled & restored power up to G254LB at 1:03. Patrol downstream of G254LB also did not reveal a cause. 49F2 recloser was opened from SCADA for crew to close G254LB in case of fault. All load was restored with no cause found. | Gloucester | Unknown/Other
3944 | 2003 | 8 | 27 | 0 |  | 148 | 2 | 1 | Leitrim | 27.6/16kV | 49F2 | Crews found a ruptured fuse at switch G968 and in order to investigate the problem the remain two fuses were opening. Upon further investigation no cause was found so the fuse was replaced and all three fuses were closed. Power was restored. | Castleman | Unknown/Other | No Apparent Cause
16836 | 2010 | 8 | 30 | 0.5625 |  | 60 | 4 | 4 | LEITRIM MS | 27.6/16kV | 49F2 | Transformer X16477 at 5638 Power Rd isolated to change cable | Gloucester | Scheduled Outage | Repair
5754 | 2004 | 8 | 31 | 0.56528 |  | 40 | 1 | 1 | LEITRIM | 27.6/16kV | 49F2 | A defective switch feeding Tx GL5691 @ 5529 Hawthorne rd was replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13176 | 2008 | 9 | 1 | 0.32292 |  | 98 | 41 | 25 | Lietrim |  | 49F2 | G572 field side phase opened at Bank and Conroy, circuit patrolled and no apparent cause revealed. Refused and closed | Gloucester | Unknown/Other | No Apparent Cause
5771 | 2004 | 9 | 3 | 0.59375 |  | 49 | 1 | 1 | Lietrim | 27.6/16kV | 49F2 | O/H section on Blais Rd isolated at G559 RWB to repair neutral conductor pulled down by dump truck. | Gloucester | Foreign Interference | Vehicle
11266 | 2007 | 9 | 6 | 0.80903 |  | 491 | 136 | 34 | Lietrim | 27.6/16kV | 49F2 | The X2 bushing on TP3174 blew out, causing oil to spill. Underground crew was called in to replace transformer. Transformer was replaced and system back to normal. Cause to why X2 bushing blew is unknown. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16915 | 2010 | 9 | 9 | 0.69792 |  | 330 | 6 | 1 | Leitrim | 27.6/16kV | 49F2 | Overhead transformer # X16488 @ 5555 Rideau Rd was isolated to all crews to replace broken Hydro pole due to MVA. | Gloucester | Foreign Interference | Vehicle
4046 | 2003 | 9 | 10 | 0.35417 |  | 60 | 1 | 1 | Leitrim | 27.6/16kV | 49F2 | Transformer Maintenance as reported by dispatch. | Gloucester | Defective Equipment
4048 | 2003 | 9 | 10 | 0.46042 |  | 29 | 8 | 16 | Leitrim | 27.6/16kV | 49F2 | Switch G571 on fire . Transformers 5535 and 5534 off loaded to repair. | Gloucester | Defective Equipment
16917 | 2010 | 9 | 10 | 0.56944 |  | 60 | 6 | 6 | Leitrim | 27.6/16kV | 49F2 | Transformer #X20331 located at 4567 Boundary Rd opened by crew for a pole replacement | Gloucester | Scheduled Outage | Construction
13228 | 2008 | 9 | 14 | 0.59375 |  | 185 | 498 | 200 | Leitrim | 27.6/16kV | 49F2 | Transformer cutout at 5127 Ninth Line faulted and caused GR6 blue phase to trip and lock out. Crews cleared the cutout from the line the restored all customers but 1 via the blue phase bypass at GR6 as reclose fuse on the blue was blown and would not close. Cutout replaced and final customer restored. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
16941 | 2010 | 9 | 14 | 0.46944 |  | 74 | 9 | 7 | Leitrim | 27.6/16kV | 49F2 | O/H transformer #X19951 located at 3370 Farmer's Way opened up and caused switch G493 to open up also due to squirrel contact | Gloucester | Foreign Interference | Animal
16948 | 2010 | 9 | 15 | 0.42014 |  | 95 | 8 | 5 | Leitrim | 27.6/16kV | 49F2 | Transformer #X42056 located at 4618 Boundary Rd opened by crew for pole replacement | Gloucester | Scheduled Outage | Construction
16961 | 2010 | 9 | 17 | 0.34722 |  | 130 | 4 | 2 | Leitrim | 27.6/16kV | 49F2 | Transformer #X20315 located at 4716 Boundary Rd opened by crew for a pole replacement | Gloucester | Scheduled Outage | Construction
16962 | 2010 | 9 | 17 | 0.50347 |  | 105 | 9 | 5 | Leitrim | 27.6/16kV | 49F2 | Transformer #X20318 located at 4686 Boundary Rd opened by crew for a pole replacement | Gloucester | Scheduled Outage | Construction
4090 | 2003 | 9 | 18 | 0.375 |  | 15 | 1 | 5 | Leitrim | 27.6/16kV | 49F2 | D. Priaulx reports transformer # 2216 opened for Pole testing with Bell Canada. Outage effected 5 customers . Power was restored at 09:15 am. | Gloucester | Scheduled Outage | Preventive Maintenance
16969 | 2010 | 9 | 20 | 0.375 |  | 105 | 5 | 3 | Leitrim | 27.6/16kV | 49F2 | Trans at 46664 Boundry rd was isoalted for a pole change | Gloucester | Scheduled Outage | Preventive Maintenance
16971 | 2010 | 9 | 20 | 0.50625 |  | 111 | 18 | 10 | Leitrim MS | 27.6/16kV | 49F2 | Trans at 4626 BOUNDARY RD CUMBERLAND was isolated in order to replace a pole | Gloucester | Scheduled Outage | Preventive Maintenance
16986 | 2010 | 9 | 23 | 0.35417 |  | 150 | 15 | 6 |  | 27.6/16kV | 49F2 | Isolated transformer X20331 at 4550 Boundary Rd to install new pole | Gloucester | Scheduled Outage | Construction
16988 | 2010 | 9 | 24 | 0.22083 |  | 378 | 539 | 105 | Leitrim | 27.6/16kV | 49F2 | Blown arrestor on transformer caused switch G271 @ Mitch Owen/Anderson to open. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
13301 | 2008 | 9 | 28 | 0.84097 |  | 104 | 3413 | 1969 | Leitrim | 27.6/16kV | 49F2 | 49F2 Breaker at Leitrim tripped, RTU was failed at Leitrim. Not sure if breaker attempted reclose but reclosing indicated in service at the station. Crew thoroughly checked station, tested cable. 24/7 Crew closed 49F2 breaker restoring load. To be patrolled in daylight. | Gloucester | Unknown/Other
13303 | 2008 | 9 | 29 | 0.26389 |  | 42 | 1378 | 1969 | Leitrim | 27.6/16kV | 49F2 | 49F2 opened station SCADA down. Overhaed line givenfull thermo vision. Breaker at station found to have recloser blocked, which explains no reclose. | Gloucester | Unknown/Other | No Apparent Cause
4189 | 2003 | 9 | 30 | 0.69583 |  | 378 | 13 | 2 | Leitrim | 27.6/16kV | 49F2 | Transformer #5246 at 4207 Farmer's Way in South Gloucester was defective and was replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13319 | 2008 | 10 | 3 | 0.40347 |  | 396 | 816 | 2553 | Leitrim | 27.6/16kV | 49F2 | 49F2 tripped under hold off while carrying all 49F1 load due to ongoing work on the 49F1 recloser. Problem was later determined to be blown fuses at G180W & G377 due to tree contact on customer owned line on Boundary Rd. Power out was unknown till late in the afternoon when Hydro One reported transfer customers were without power. | Gloucester | Tree Contacts | Inadequate Trimming
5828 | 2004 | 10 | 5 | 0.48611 |  | 10 | 0 | 3 | Leitrim | 27.6/16kV | 49F2 | A Bad neutral connection at the Transformer | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
5838 | 2004 | 10 | 11 | 0.89097 |  | 62 | 310 | 300 | Leitrim | 27.6/16kV | 49F2 | A car hit a Bell pole at 4723 Bank st. Crew cleared our plant and refused G54 Red phase. | Gloucester | Foreign Interference | Vehicle
4247 | 2003 | 10 | 12 | 0.35417 |  | 90 | 18 | 12 | Leitrim | 27.6/16kV | 49F2 | South Clark Fenton Rd transformer 66 out for mtce. | Gloucester | Scheduled Outage | Preventive Maintenance
4248 | 2003 | 10 | 12 | 0.41667 |  | 90 | 4 | 3 | Leitrim | 27.6/16kV | 49F2 | Transformer 340 at Fenton Rd disconnected for Mtce. | Gloucester | Scheduled Outage
4298 | 2003 | 10 | 19 | 0.35417 |  | 80 | 3 | 2 | Leitrim | 27.6/16kV | 49F2 | Transformer #803, on Fenton Road, was isolated to allow for the replacement of high voltage insulators on the pole above. | Gloucester | Scheduled Outage | Construction
4300 | 2003 | 10 | 19 | 0.42361 |  | 100 | 3 | 2 | Leitrim | 27.6/16kV | 49F2 | Transformer #83, on Fenton Road, was isolated to allow for the replacement of high voltage insulators on the pole above. | Gloucester | Scheduled Outage | Construction
7484 | 2005 | 10 | 19 | 0.59167 |  | 7 | 0 | 3 | LETRIUM | 27.6/16kV | 49F2 | G559 OPENED TO REPAIR BROKEN INSULATOR ON BANK ST AND BLAIS RD. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4316 | 2003 | 10 | 21 | 0.10556 |  | 188 | 17 | 7 | Leitrim | 27.6/16kV | 49F2 | In line fused switch G932B on Farmers Way found blown as well as fuse for transformer 913, no apparent cause for 913 , both refused and closed. Fuse at transformer 910 on Farmers Way found burning, same replaced and load restored to 910. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4317 | 2003 | 10 | 21 | 0.088194 |  | 251 | 209 | 50 | Leitrim | 27.6/16kV | 49F2 | Switch G271W found blown, no apparent cause found on patrol, switch refused and closed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
11654 | 2007 | 11 | 3 | 0.78819 |  | 450 | 8 | 1 | Lietrim | 27.6/16kV | 49F2 | Vehicle accident at 4869 Bank broke a pole, isolation required for rescue and repair | Gloucester | Foreign Interference | Vehicle
9598 | 2006 | 11 | 4 | 0.37153 |  | 60 | 49 | 75 | Leitrim | 27.6/16kV | 49F2 | G. Schwartz reports transformer fuse @ 4547 Anderson Rd found opened, which caused G212R phase to open @ Anderson & Eight line. G212R phase fuse was replaced @ 08:55, and transformer fuse at 4547 Anderson Rd. Caused by an animal contacted. | Gloucester | Foreign Interference | Animal
5856 | 2004 | 11 | 5 | 0.36042 |  | 52 | 40 | 46 | Leitrim | 27.6/16kV | 49F2 | Blown fuse found at G321B. Line patrolled and nothing found. Very Windy. New fuse installed and holding. | Gloucester | Adverse Weather | Wind
7574 | 2005 | 11 | 7 | 0.0625 |  | 21 | 35 | 100 | Leitrim | 27.6/16kV | 49F2 | M. Byers reports G606 is now opened to isolate overhead section to remove tree. | Gloucester | Tree Contacts | Tree Fallen
4452 | 2003 | 11 | 14 | 0.12847 |  | 550 | 611 | 100 | Leitrim | 27.6/16kV | 49F2 | Trees came down across the line east of switch G901W on Eighth Line in Carlsbad Springs. The line was repaired and the power was restored. ID#4452 | Gloucester | Adverse Weather | Wind
11705 | 2007 | 11 | 14 | 0.61111 |  | 146 | 16 | 17 | Leitrim | 27.6/16kV | 49F2 | Neutral conductor on customer owned primary line at Livingston Farms (7901 Mitch Owens) was pulled down by a truck, causing transformer 962 cutout to blow and upstream line fuse G230B to blow. G230B was refused & repairs were made to neutral by Oncall crew. Customer ran their own generator during repairs to neutral and then xfmr 962 was restored. | Gloucester | Foreign Interference | Vehicle
9685 | 2006 | 11 | 19 | 0.83819 |  | 225 | 75 | 20 | Leitrim | 27.6/16kV | 49F2 | Switch 289R on Whyte side Rd open caused by a car hitting and breaking a stub pole causing the guy wire that was attached to that pole to snap and fall into the single phase primary. | Gloucester | Foreign Interference | Vehicle
7634 | 2005 | 11 | 20 | 0.35903 |  | 93 | 2 | 1 | Leitrim | 27.6/16kV | 49F2 | Customer reports fuse opened on pole. 24/7 reports transformer refused all load restored to normal. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4530 | 2003 | 11 | 27 | 0.98611 |  | 10 | 0 | 3 | Leitrim | 27.6/16kV | 49F2 | Transformer #3679 at 4323 Ninth Line interrupted to repair defective line clamp. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
5943 | 2004 | 11 | 28 | 0.44236 |  | 432 | 14 | 2 | Leitrim | 27.6/16kV | 49F2 | Replaced O/H xfmr at 3894Russell Rd | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4573 | 2003 | 12 | 8 | 0.55208 |  | 49 | 106 | 130 | leitrim | 27.6/16kV | 49F2 | Blown lightning arrestor at Hawthorne and Leitrim on transformer 303 caused the G240R fuse to operate on the Leitrim F2 circuit. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
4574 | 2003 | 12 | 8 | 0.55208 |  | 89 | 3 | 2 | Leitrim F2 | 27.6/16kV | 49F2 | A blown lighning arrestor on transformer 303 caused G240R phase fuse to operate and the 303 transformer fuse. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
13720 | 2008 | 12 | 8 | 0.87153 |  | 53 | 3 | 3 | leitrum | 27.6/16kV | 49F2 | At 20:55 trans at 4330 Bank St was isolated in order to replace defective connections | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
13726 | 2008 | 12 | 9 | 0.54514 |  | 50 | 2 | 2 | Leitrim | 27.6/16kV | 49F2 | Isolated transformer 419 at 4356 Eighth Line Rd to replace switch and primary Insulators | Gloucester | Scheduled Outage | Preventive Maintenance
13732 | 2008 | 12 | 10 | 0.40625 |  | 40 | 3 | 4 | Leitrim | 27.6/16kV | 49F2 | Isolated transformer GL5505 at 4401 Eighth Line Rd to replace switch and primary insulators | Gloucester | Scheduled Outage | Preventive Maintenance
13733 | 2008 | 12 | 10 | 0.47917 |  | 95 | 6 | 4 | Leitrim | 27.6/16kV | 49F2 | Isolated transformer GL5698 at 4660 Eighth Line Rd to replace switch and primary insulators | Gloucester | Scheduled Outage | Preventive Maintenance
11831 | 2007 | 12 | 12 | 0.9375 |  | 75 | 10 | 8 | Lietrim | 27.6/16kV | 49F2 | Overhead section of the 49F2 feeder on Doncaster Rd isolated to reinforce cracked pole. | Gloucester | Foreign Interference | Vehicle
9850 | 2006 | 12 | 15 | 0.78125 |  | 405 | 7 | 1 | leitrim | 27.6/16kV | 49F2 | Crew replaced defective transformer GL101 at 4570 bank st. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
13755 | 2008 | 12 | 15 | 0.54861 |  | 45 | 2 | 2 | Leitrim | 27.6/16kV | 49F2 | Transformer #5937 located at 4360 Eighth Line Rd isolated to change cut out & re-insulate pole | Gloucester | Scheduled Outage | Preventive Maintenance
13756 | 2008 | 12 | 15 | 0.59375 |  | 40 | 5 | 7 | Leitrim | 27.6/16kV | 49F2 | Transformer #GL4206 located at 4915 Eighth Line Rd isolated to replace cut out & re-insulate pole | Gloucester | Scheduled Outage | Preventive Maintenance
13757 | 2008 | 12 | 15 | 0.65278 |  | 55 | 3 | 3 | Leitrim | 27.6/16kV | 49F2 | Transformer #GL3897 located at 5115 Eighth Line Rd isolated to replace cut out & re-insulate pole. | Gloucester | Scheduled Outage | Preventive Maintenance
13760 | 2008 | 12 | 16 | 0.38542 |  | 45 | 2 | 2 | Leitrim | 27.6/16kV | 49F2 | Transformer #GL1999 located at 5080 Eighth Line Rd isolated to replace cut out & re-insulate pole. | Gloucester | Scheduled Outage | Preventive Maintenance
13765 | 2008 | 12 | 16 | 0.62986 |  | 69 | 2 | 2 | LEITRIM | 27.6/16kV | 49F2 | Transformer #gl005941 AT 5490 Eighth Line Rd isolated to replace switch and re-insulate pole | Gloucester | Scheduled Outage | Repair
13772 | 2008 | 12 | 17 | 0.60903 |  | 63 | 3 | 3 | Leitrim | 27.6/16kV | 49F2 | Transformer #GL000089 located at 5577 Eighth Line Rd isolated to re-insulate pole & change cut out | Gloucester | Scheduled Outage | Preventive Maintenance
13774 | 2008 | 12 | 17 | 0.48958 |  | 90 | 9 | 6 | Leitrim | 27.6/16kV | 49F2 | Transformer #GL1334 located at 5544 Eighth Line Rd isolated to re-insulate pole & change cut out | Gloucester | Scheduled Outage
6077 | 2004 | 12 | 19 | 0.29028 |  | 130 | 100 | 46 | Leitrim | 27.6/16kV | 49F2 | G321B blown fused cutout. Hot line clamp repaired. | Gloucester | Unknown/Other | No Apparent Cause
11872 | 2007 | 12 | 23 | 0.33194 |  | 182 | 87 | 38 | Leitrim | 27.6/16kV | 49F2 | A squirrel made contact with transformer GL3901 @ 5853 Eigth Line Rd causing the fuse to blow and also causing the GR6 W recloser to failed. | Gloucester | Foreign Interference | Animal
15575 | 2009 | 12 | 27 | 0.10625 |  | 174 | 252 | 87 | Leitrim | 27.6/16kV | 49F2 | G735B at Ninth Line & Ramsayville opened for tree branches on line. Branches knocked off & power restored. Customers affected on Ninth Line, Anderson & Farmer's Way. | Gloucester | Adverse Weather | Ice Storm
11449 | 2007 | 10 | 3 | 0.40972 |  | 570 | 95 | 10 | Leitrim | 27.6/16kV | 49F2 (GR6) | TP3174 on Country Trail (Andeson/Eighth Line) isolated to clean up oil spill from previous failed transformer | Gloucester | Scheduled Outage | Repair
10133 | 2007 | 3 | 14 | 0.55 |  | 70 | 211 | 181 | Bayshore | 8/4.8kV | 49F3 | The 49F3 breaker tripped due to the white phase falling on to the blue phase at Acres and 417 off ramp. The 22M23 was underhold off and also tripped. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6742 | 2005 | 6 | 15 | 0.93889 |  | 268 | 27 | 6 | Bayshore | 8/4.8kV | 49F3 | Tree limb contact with secondary and TX5007 fuse blown. At #4 Valley Ridge. Bayshore Area. | Nepean | Tree Contacts | Inadequate Trimming
20932 | 2012 | 7 | 5 | 0.4125 |  | 196 | 10 | 3 | Bayshore | 8/4.8kV | 49F3 | Vaults VE1 & VE2 on Woodridge were isolated to allow contractor to perform vault maintenance. | Nepean | Scheduled Outage | Preventive Maintenance
11337 | 2007 | 9 | 19 | 0.52847 |  | 144 | 58 | 24 | Bayshore | 8/4.8kV | 49F3 | Bayshore 49F3 breaker auto-reclosed due to a red phase cable fault between TE512 and SE1 on woodridge cres. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
17527 | 2011 | 1 | 27 | 0.015278 |  | 356 | 12 | 2 | Bayshore | 8/4.8kV | 49F4 | Vault VE44 & VE66 was isolated for the contractor for routine maintenance. | Nepean | Scheduled Outage | Preventive Maintenance
17746 | 2011 | 3 | 20 | 0.88889 |  | 267 | 9 | 2 | Bayshore | 8/4.8kV | 49F4 | VE40N & VE66N was isolated to allow contractor to perform planned vault maintenance & secondary breaker repairs. | Nepean | Scheduled Outage | Preventive Maintenance
7121 | 2005 | 8 | 10 | 0.72361 |  | 2 | 26 | 767 | Bayshore | 8/4.8kV | 49F4, F5 & F6 | Bayshore 49T2 load interupted due to one open phase on the transformer, load restored from the 49T1. | Nepean | Adverse Weather
20474 | 2012 | 5 | 7 | 0.41181 |  | 13 | 0 | 1 | Bayshore |  | 49F5 | While switching PC17-71089 to isolate cable section between VE39 and VE41 at Bayshore Shopping Centre, switch S650 blue phase fuse blew causing an outage at VE41 when VE41 to VE39 was opened. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18429 | 2011 | 6 | 16 | 0.98333 |  | 150 | 8 | 3 | Bayshore | 27.6/16kV | 49F5 | VE39, VE41 and VE42 all at 100 Bayshore were isolated to allow the customer's contractor to service the main secondary breaker | Nepean | Scheduled Outage | Preventive Maintenance
15531 | 2009 | 12 | 20 | 0.058333 |  | 561 | 9 | 1 | Bayshore | 8/4.8kV | 49F5 | Crew isolated VE66, at Bayshore Shopping center to allow for a defective transformer to be replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13836 | 2009 | 1 | 4 | 0.50139 |  | 81 | 154 | 114 | Bayshore | 8/4.8kV | 49F6 | Crew found Blown arrestor at 89 Stillwater, causing S961 blue phase to open. Crew refused switch and restored power. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11920 | 2008 | 1 | 9 | 0.72639 |  | 276 | 156 | 34 | Bayshore | 8/4.8kV | 49F6 | S960 blue phase and S961 blue & red phase fuses blew during periods of extreme high wind gusts. Overhead circuit patrol did not reveal any obvious cause and S960 & S961 were refused successfully restoring all power. Customers affected were in the Stillwater area of Crystal Beach. | Nepean | Unknown/Other
17493 | 2011 | 1 | 19 | 0.37986 |  | 131 | 120 | 55 | Bayshore | 8/4.8kV | 49F6 | 49F6 overhead between S12290 and S961 was isolated affecting 55 customers on Stillwater, Erskine and Ararat. Isolated to allow crews to replace a pole, replace a broken crossarm and sleve out a set of switches. | Nepean | Scheduled Outage | Preventive Maintenance
15685 | 2010 | 1 | 26 | 0.47917 |  | 230 | 31 | 8 | Bayshore | 8/4.8kV | 49F6 | Transformer #X37027 located at 40 Horner was isolated in order replace bad transformer | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7867 | 2006 | 1 | 29 | 0.034722 |  | 125 | 17 | 8 | Bayshore | 8/4.8kV | 49F6 | Crew replaced switch to transformer 4460 at 40 Aero. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19935 | 2012 | 1 | 31 | 0.44097 |  | 25 | 3 | 8 | Bayshore | 8/4.8kV | 49F6 | Transformer #NP001335 located at 21 Cleadon Dr opened by crew to change O/H service | Nepean | Scheduled Outage | Construction
13937 | 2009 | 2 | 6 | 0.44583 |  | 38 | 6 | 10 | Bayshore | 8/4.8kV | 49F6 | xfmr X39656 at 121 Corkstown Rd isolated to change cutout bracket | Nepean | Scheduled Outage | Repair
7968 | 2006 | 2 | 25 | 0.40972 |  | 87 | 44 | 30 | Bayshore | 8/4.8kV | 49F6 | A broken switch at 960 R phase @ Carling Ave at Bedale Dr. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20092 | 2012 | 3 | 2 | 0.25 |  | 465 | 62 | 8 | Bayshore | 8/4.8kV | 49F6 | At 6:00am transformer TE685 at the rear of 23 Erskine was damaged as a result of a blown elbow. Crews replaced TE685 with new TP9342. 8 customers were affected for 465 mins. Bayshore 49F6 ID# 20092 | Nepean | Defective Equipment
8019 | 2006 | 3 | 14 | 0.0625 |  | 34 | 7 | 12 | Bayshore | 8/4.8kV | 49F6 | Transformer 1110 with open bus isolated to allow replacement on triplex to 11 Whitburn, Nepean | Nepean | Defective Equipment | Equipment Deterioration Due to Age
17772 | 2011 | 3 | 23 | 0.40278 |  | 333 | 39 | 7 | Bayshore | 8/4.8kV | 49F6 | Transformer #NPTE00684 located at 9 Erskine Pl opened by crew to replace elbows and then they had to replace the transformer due to a leaker. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
20244 | 2012 | 3 | 27 | 0.64375 |  | 73 | 6 | 5 | Bayshore | 8/4.8kV | 49F6 | replaced broken fuse in switch feeding transformer X39773 at 68 Stillwater Dr (Cause unknown) | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5019 | 2004 | 4 | 19 | 0.74653 |  | 73 | 15 | 12 | Bayshore | 8/4.8kV | 49F6 | The lead to switch S691 on Carling Ave has burnt off, same replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20388 | 2012 | 4 | 25 | 0.39167 |  | 449 | 195 | 26 | Bayshore | 8/4.8kV | 49F6 | An overhead section on Aero Dr was isolated to allow crews to crane in and set new poles | Nepean | Scheduled Outage | Preventive Maintenance
20455 | 2012 | 5 | 3 | 0.80208 |  | 60 | 8 | 8 | Bayshore | 8/4.8kV | 49F6 | Transformer NP004460 at 42 Aero Dr isolated to make temporary repairs (jumped buss) till transformer can be replaced tomorrow | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16068 | 2010 | 5 | 8 | 0.91181 |  | 269 | 86 | 25 | Bayshore DS | 8/4.8kV | 49F6 | Bayshore 49F6 auto-reclosed due to a pole fire at S691. This also caused a transformer at the rear of 55 Aero Dr to open up. Crews refused and restored power to 8 customers. Crews determined that S691 requires replacing. Crews replaced and restored power to 17 remaining customers. | Nepean | Adverse Environment
12426 | 2008 | 5 | 11 | 0.044444 |  | 436 | 246 | 110 | Bayshore | 8/4.8kV | 49F6 | S961 Blue phase fuse melted, and white and blue phase arresters blown. Circuit patrolled nothing found. Closed in S961B, and held. Crew repaired defective switch. There was also an O/H transformer fuse that had blown as well. | Nepean | Defective Equipment
18182 | 2011 | 5 | 19 | 0.39167 |  | 558 | 74 | 8 | Bayshore | 8/4.8kV | 49F6 | Transformer TP8587 @ 9 Erskine was isolated to allow crews to perform soil remediation. 7 Customers were affected. Bayshore (49F6) | Nepean | Scheduled Outage
18186 | 2011 | 5 | 19 | 0.39583 |  | 325 | 38 | 7 | Bayshore | 8/4.8kV | 49F6 | Transfromer 2656 @ 16 Aparat was open to allow crew to replace dammaged fro wind storm in early May. 7 customers were affected. Bayshore 49F6 | Nepean | Scheduled Outage
18206 | 2011 | 5 | 24 | 0.375 |  | 210 | 24 | 7 | Bayshore | 8/4.8kV | 49F6 | Isolated transformer NP2656 at 16 Ararat Crt to transfer hydro plant to new pole | Nepean | Scheduled Outage | Construction
18256 | 2011 | 5 | 31 | 0.37847 |  | 519 | 61 | 7 | Bayshore | 8/4.8kV | 49F6 | Transformer TE684 @ 9 Erskine was isolated to allow crew to repair transformer base. 7 cusotmers were affected. Bayshore (49F6) | Nepean | Scheduled Outage | Repair
20690 | 2012 | 6 | 4 | 0.39375 |  | 447 | 499 | 67 | Bayshore |  | 49F6 | 49F6 O/H section between S22493 and S545 on Herrington Crt. Was isolated to allow contractor to install new poles with a crane. | Nepean | Scheduled Outage | Construction
20703 | 2012 | 6 | 6 | 0.38194 |  | 518 | 302 | 35 | Bayshore |  | 49F6 | Black & Macdonald isolated the 49F6 O/H between S22493 & S545 to allow for poles & a leaky transformer to be changed. | Nepean | Scheduled Outage | Preventive Maintenance
20750 | 2012 | 6 | 12 | 0.38125 |  | 486 | 259 | 32 | Bayshore |  | 49F6 | Planned outage in the Cleadon & Herrington area to allow Black & Mack to replace hydro pole. | Nepean | Scheduled Outage | Construction
18414 | 2011 | 6 | 15 | 0.38472 |  | 519 | 61 | 7 | Bayshore | 8/4.8kV | 49F6 | Transformer TP8587 @ 9 Erskine was isolated to allow crew replace leaking transformer. 7 customer were affected. Bayshore (49F6) | Nepean | Scheduled Outage
18433 | 2011 | 6 | 17 | 0.78264 |  | 95 | 11 | 6 | Bayshore | 8/4.8kV | 49F6 | At 18:48 crews isolated transformer at 9 Erskine fed from S1010 to preform repairs. 6 customers affected for 95 mins. Bayshore (49F6) ID# 18433 | Nepean | Defective Equipment
20789 | 2012 | 6 | 18 | 0.38194 |  | 443 | 347 | 47 | Bayshore | 8/4.8kV | 49F6 | Bayshore cable section on Cleadon was isolated for contractor to crane in new poles | Nepean | Scheduled Outage | Construction
20799 | 2012 | 6 | 19 | 0.375 |  | 520 | 321 | 37 | Bayshore | 8/4.8kV | 49F6 | A section of 49F6 between S592, S545 & S12 was isolated for pole replacement in the Crystal Beach area. | Nepean | Scheduled Outage | Construction
20810 | 2012 | 6 | 20 | 0.37639 |  | 369 | 289 | 47 | Bayshore | 8/4.8kV | 49F6 | A section of the 49F6 was isolated to allow Black & Macdonald crews to change poles | Nepean | Scheduled Outage | Construction
10706 | 2007 | 6 | 21 | 0.94861 |  | 49 | 7 | 8 | Bayshore | 8/4.8kV | 49F6 | Transformer number NP004455 located at 51 Horner Dr. isolated due to animal contact | Nepean | Foreign Interference | Animal
14608 | 2009 | 6 | 24 | 0.40625 |  | 105 | 9 | 5 | Bayshore | 8/4.8kV | 49F6 | Transformer #X40184 located at 3 Leeming Dr isolated for a pole change | Nepean | Scheduled Outage | Construction
12799 | 2008 | 7 | 7 | 0.28125 |  | 195 | 62 | 19 | Bayshore | 8/4.8kV | 49F6 | Customers fed from TE81 and TE80 in the Corkstown area reported power out. Crews found S521 and S732 open on the B phase 49F6 Bayshore. Suspected cable fault was sectionalized and isolated for further pinpointing. 19 customers affected, power restored 10:00am. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
6897 | 2005 | 7 | 10 | 0.64375 |  | 53 | 3 | 3 | Bayshore | 8/4.8kV | 49F6 | Transformer #NP000621 located at 29 River Bend isolated possibly due to tree interference | Nepean | Foreign Interference | Foreign Object
10844 | 2007 | 7 | 10 | 0.77361 |  | 146 | 219 | 90 | Bayshore | 8/4.8kV | 49F6 | 49F6 circuit section was isolated between S922 & S1117 to repair damaged equipment on pole on Aero Drive, Crystal Beach. Damage is believed to have been caused by lightning strikes on Friday, July 6th. (see ID # 10803) | Nepean | Defective Equipment | Imminent Equipment Failure Detected
8765 | 2006 | 7 | 17 | 0.98958 |  | 765 | 13 | 1 | Bayshore | 8/4.8kV | 49F6 | Transformer #NP000304 located at 61 Corkstown isolated due to a blown transformer that needed to be replaced | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8756 | 2006 | 7 | 18 | 0.98403 |  | 419 | 3310 | 865 | Bayshore | 8/4.8kV | 49F6 | 49F6 @ Bayshore tripped and went to lock-out. Crew sent to partoll and found downed primary on Areo Dr. and Corkstown. O/H isolated and 49F6 closed to pick up most of the customers. S1117 opened to isolate section about 110 customers out until 6:36. | Nepean | Lightning | Direct Strike
12886 | 2008 | 7 | 18 | 0.22569 |  | 250 | 183 | 57 | Bayshore | 8/4.8kV | 49F6 | Crew found S521 & S732 blown on Horner Ave. O/H section patrolled & restored from S521. Cables tested & TE80 & TE81 restored from S732 1 at a time. | Nepean | Adverse Weather | Lightning
12895 | 2008 | 7 | 19 | 0.013889 |  | 369 | 144 | 57 | Bayshore | 8/4.8kV | 49F6 | S521 & S732 on Horner Drive both blew. Overhead section was restored by 24/7 from S521. Underground section fed from S732 was restored by Oncall. Defective cable between TE80 & TE81 caused outage. | Nepean | Defective Equipment
12899 | 2008 | 7 | 19 | 0.77917 |  | 370 | 354 | 100 | Bayshore | 8/4.8kV | 49F6 | Downed Primary Wire, at 23 Stillwater Drive was isolated and repaired by On-Call crew. All three phases were isolated, to make repairs safely. | Nepean | Defective Equipment
8813 | 2006 | 7 | 24 | 0.51181 |  | 98 | 5 | 3 | Bayshore | 8/4.8kV | 49F6 | Transformer located at 28 Corkstown isolated due to slow burning fuse, possibly caused by a defective cable | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8814 | 2006 | 7 | 24 | 0.51181 |  | 93 | 14 | 9 | Bayshore | 8/4.8kV | 49F6 | Crew found bad cbl section between TE82 and S731 on Corkstown Rd. NO point was at TE82 so only TE82 was out. Crew isolated cbl section and restored power to 9 Customers. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
5580 | 2004 | 7 | 28 | 0.42292 |  | 111 | 13 | 7 | Leitrim | 27.6/16kV | 49F6 | Transfomer at 12 Riverbend interrupted by a squirrel contact. Crew had to leave to attend to a fire call, just after arriving the first time. | Ottawa | Foreign Interference | Animal
12977 | 2008 | 7 | 30 | 0.40347 |  | 215 | 32 | 9 | Bayshore | 27.6/16kV | 49F6 | TE80 (new TP6350) @ 52 Horner was isolated to replace transformer for elbow connected model. | Nepean | Scheduled Outage | Preventive Maintenance
3845 | 2003 | 8 | 4 | 0.87639 |  | 151 | 20 | 8 | Bayshore | 8/4.8kV | 49F6 | 24/7 crews reports Arrester, cut out switch, and bracket all replaced at the rear of 28 Harlowe cres. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11032 | 2007 | 8 | 11 | 0.015972 |  | 187 | 25 | 8 | Bayshore | 8/4.8kV | 49F6 | Transformer 4777 at 8 Harrogate interrupted due to leakage | Nepean | Defective Equipment | Equipment Deterioration Due to Age
5681 | 2004 | 8 | 14 | 0.75764 |  | 95 | 16 | 10 | Bayshore | 8/4.8kV | 49F6 | S731 fuse blown. Cable between TE82 & S731 failed Hi-pot test, TE82 successfully restored from alternate source. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13092 | 2008 | 8 | 18 | 0.68056 |  | 137 | 23 | 10 | Bayshore | 8/4.8kV | 49F6 | center phase of S961 primary fused switch @ 6 bedale opened due to extreme lighning activity. No other cause found. | Nepean | Adverse Weather | Lightning
11152 | 2007 | 8 | 24 | 0.30208 |  | 390 | 39 | 6 | Bells Corners | 8/4.8kV | 49F6 | Defective O/H transformer 1171 at 25 Harlowe in Nepean replaced. | Nepean | Defective Equipment
9113 | 2006 | 9 | 3 | 0.96319 |  | 489 | 1823 | 865 | Bayshore | 8/4.8kV | 49F6 | Motor vehicle hit and knocked down a pole, same pole isolated and replaced. | Nepean | Foreign Interference | Vehicle
19082 | 2011 | 9 | 3 | 0.53889 |  | 34 | 5 | 8 | Bells Corner | 8/4.8kV | 49F6 | Isolated transformer X37026 at 18 Horner Dr to replace secondary service connections at the transformer | Nepean | Defective Equipment | Imminent Equipment Failure Detected
11238 | 2007 | 9 | 4 | 0.40625 |  | 95 | 14 | 9 | Bayshore | 8/4.8kV | 49F6 | Transformer TE3148 at 25 Creekwood Cr was isolated to replace leaking transformer. | Nepean | Scheduled Outage | Repair
15064 | 2009 | 9 | 8 | 0.40625 |  | 60 | 10 | 10 | Bayshore | 8/4.8kV | 49F6 | Transformer #X39669 located at 27 Cleadon Dr isolated for an upgrade | Nepean | Scheduled Outage | Construction
4118 | 2003 | 9 | 21 | 0.65347 |  | 48 | 4 | 5 | Bayshore | 8/4.8kV | 49F6 | Old fuse failed and was replaced | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11617 | 2007 | 10 | 28 | 0.56736 |  | 529 | 171 | 100 | BAYSHORE | 8/4.8kV | 49F6 | At 15 Harlowe Cres, a customer was cutting a tree down and a tree limb caused the transformer fuse to blow, affecting 10 customers. After clearing the tree limb, the transformer fuse was closed and blew the downstream fuse, causing a large outage to 100 customers. S960 Blue phase fuse closed restoring power to all but the originial 10 customers. Defective Transformer #4763 replaced. | Nepean | Tree Contacts | Tree Limb Fallen
11618 | 2007 | 10 | 28 | 0.56736 |  | 529 | 141 | 16 | Bayshore | 8/4.8kV | 49F6 | crew replaced defective transformer at 15 harlowe. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
19488 | 2011 | 10 | 28 | 0.39583 |  | 32 | 4 | 8 | 49F6 | 8/4.8kV | 49F6 | Transformer #1210 located at 63 Aero opened by crew to change connections and cut out | Nepean | Defective Equipment | Imminent Equipment Failure Detected
19510 | 2011 | 11 | 1 | 0.39931 |  | 194 | 365 | 113 | Bayshore | 8/4.8kV | 49F6 | 49F6 line section between S545 and S587 was isolated to allow crew to replace broken cross arm at 56 Crystal Beach. | Nepean | Scheduled Outage | Repair
9620 | 2006 | 11 | 7 | 0.34514 |  | 28 | 5 | 10 | Bayshore | 8/4.8kV | 49F6 | Transformer opened at 66 Crystal Beach tyo replace service | Ottawa | Scheduled Outage | Preventive Maintenance
5875 | 2004 | 11 | 11 | 0.82292 |  | 75 | 38 | 30 |  | 8/4.8kV | 49F6 | Defective Transformer Switch. | Nepean | Defective Equipment
5911 | 2004 | 11 | 21 | 0.17847 |  | 73 | 10 | 8 | Bayshore | 8/4.8kV | 49F6 | Crew replaced blown fuse at 21 Herrington, Tx1010. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
15457 | 2009 | 12 | 2 | 0.42708 |  | 190 | 22 | 7 | Bayshore | 8/4.8kV | 49F6 | Transformer #4775 located at 20 Hexham isolated due to PCB change | Nepean | Scheduled Outage | Construction
15470 | 2009 | 12 | 4 | 0.40139 |  | 115 | 10 | 5 | Bayshore | 8/4.8kV | 49F6 | Transformer X40048 at 70 Crystal Beach was interrupted for crew to change out transformer due to PCB's | Nepean | Scheduled Outage | Preventive Maintenance
15472 | 2009 | 12 | 4 | 0.51042 |  | 95 | 19 | 12 | Bayshore | 8/4.8kV | 49F6 | Transformer X40235 at 17 Bedale was interrupted for crew to change xfmr due to PCB's | Nepean | Scheduled Outage | Preventive Maintenance
15488 | 2009 | 12 | 8 | 0.43056 |  | 170 | 14 | 5 | Bayshore | 8/4.8kV | 49F6 | Transformer #X39657 located at 72 Cleadon isolated due to PCB change | Nepean | Scheduled Outage | Construction
15492 | 2009 | 12 | 10 | 0.4375 |  | 170 | 14 | 5 | Bayshore | 8/4.8kV | 49F6 | Transformer #X39770 located at 66 Cleadon Dr isolated for PCB change | Nepean | Scheduled Outage | Construction
13796 | 2008 | 12 | 25 | 0.12708 |  | 303 | 758 | 150 | Bayshore | 8/4.8kV | 49F6 | no immediate cause was found, but crew says it may have been tree contact due to high winds. Crew refused and closed red and blue phases at S961. | Nepean | Unknown/Other | No Apparent Cause
19769 | 2011 | 12 | 29 | 0.65972 |  | 120 | 26 | 13 | Bayshore | 8/4.8kV | 49F6 | Replaced defective cut out at Trans NP004453 at :34 HORNER DR Nepean | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3193 | 2003 | 2 | 15 | 0.79167 |  | 69 | 15 | 13 | Blackburn | 8/4.8kV | 4F1 | Crew opened transformer T187 at 47 centrepark feeding customers on Silver Aspen and Redbury to repair secondary service to three customers on Silver Aspen. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
17593 | 2011 | 2 | 16 | 0.5625 |  | 37 | 6 | 10 | Blackburn | 8/4.8kV | 4F1 | Mike Irven isolated trans at 13 Parklane Crt to make repairs to sec connections | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
3198 | 2003 | 2 | 19 | 0.48958 |  | 32 | 5 | 13 | Blackburn | 8/4.8kV | 4F1 | Transformer TE0187, in Blackburn Hamlet was isolated to allow for the isolation of a pedestal that needed repairs. Power was restored to the transformer while repairs were being made. The transformer was then again isolated to allow for the re-connection of the pedestal. After connection full power was restored. | Gloucester | Scheduled Outage | Repair
17738 | 2011 | 3 | 18 | 0.66667 |  | 10 | 2 | 9 | Blackburn | 8/4.8kV | 4F1 | TE191 at 47 Silver Aspen Crescent was isolated to allow crew to repair secondary service service. 9 customers were affected for 10 minutes. Blackburn (4F1) ID# 17738 | Gloucester | Scheduled Outage
6321 | 2005 | 3 | 24 | 0.54236 |  | 53 | 4 | 5 | Blackburn | 8/4.8kV | 4F1 | Isolated Transformer # 5582 at 5 Bearbrook to repair service | Ottawa | Scheduled Outage | Preventive Maintenance
20293 | 2012 | 4 | 6 | 0.72917 |  | 15 | 2 | 9 | Blackburn | 8/4.8kV | 4F1 | Transformer TP2630 at 19 Centrepark was opened to allow crew to pin point voltage leak at 17 Centrepark. | Gloucester | Scheduled Outage | Repair
20300 | 2012 | 4 | 7 | 0.39306 |  | 79 | 12 | 9 | Blackburn | 8/4.8kV | 4F1 | Transformer TP2630 at 19 Centrepark was opened to allow crew to pin point voltage leak at 17 Centrepark. | Gloucester | Scheduled Outage | Repair
20313 | 2012 | 4 | 12 | 0.38889 |  | 415 | 42 | 6 | Blackburn | 8/4.8kV | 4F1 | TP2630 was isolated at 5 Aspen Cres to allow crews replace transformer & base, and renew grounding grid. | Gloucester | Scheduled Outage | Preventive Maintenance
14383 | 2009 | 5 | 20 | 0.72917 |  | 545 | 779 | 668 | Blackburn | 8/4.8kV | 4F1 | While switching on a 3 phase underground a white phase transformer failed causing a series of events leading to 2 more transformers to have components fail. Isolation of faulty equipment completed before restoration could be performed | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8450 | 2006 | 6 | 8 | 0.25208 |  | 147 | 12 | 5 | Blackburn | 8/4.8kV | 4F1 | Crew found fuse blown on transformer 873 at 15 Tauvette St due to a Squirrel | Gloucester | Foreign Interference | Animal
5323 | 2004 | 6 | 17 | 0.52778 |  | 93 | 19 | 12 | Blackburn | 8/4.8kV | 4F1 | TE65 now called TP2618 abck in service after cable replacement. | Gloucester | Scheduled Outage | Construction
5353 | 2004 | 6 | 22 | 0.43472 |  | 76 | 9 | 7 | Blackburn | 8/4.8kV | 4F1 | Replace broken insulators on Parkridge. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5496 | 2004 | 7 | 14 | 0.51181 |  | 148 | 2 | 1 | Blackburn | 8/4.8kV | 4F1 | To repair broken pole at transformer 672 at 1649 Bearbrook Rd. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5577 | 2004 | 7 | 28 | 0.4375 |  | 75 | 9 | 7 | Blackburn | 8/4.8kV | 4F1 | T83 W phase at the rear of 59 Highpark cres isolated to connect new cables. | Gloucester | Scheduled Outage | Repair
5578 | 2004 | 7 | 28 | 0.54167 |  | 76 | 9 | 7 | Blackburn | 8/4.8kV | 4F1 | Transformer TE69W at 53 Westpark isolated for cable connection. | Gloucester | Scheduled Outage | Repair
8943 | 2006 | 8 | 10 | 0.56597 |  | 10 | 1 | 8 | Blackburn | 8/4.8kV | 4F1 | Transfomer #GL005718 located at 40 Bearbrook isolated to take an oil sample from the transformer | Gloucester | Scheduled Outage | Construction
5688 | 2004 | 8 | 17 | 0.58333 |  | 43 | 7 | 10 | Blackburn | 8/4.8kV | 4F1 | Termination of cable end at TE69. | Gloucester | Scheduled Outage | Construction
5708 | 2004 | 8 | 24 | 0.44792 |  | 90 | 15 | 10 | Blackburn | 8/4.8kV | 4F1 | Transformer T71W at 20 Parkwood isolated to install new cables. | Gloucester | Scheduled Outage | Preventive Maintenance
5711 | 2004 | 8 | 24 | 0.55903 |  | 60 | 6 | 6 | Blackburn | 8/4.8kV | 4F1 | Transformer T72W at 45 Westpark isolated to install new cables. | Gloucester | Scheduled Outage | Preventive Maintenance
5723 | 2004 | 8 | 26 | 0.40417 |  | 146 | 71 | 29 | Blackburn | 8/4.8kV | 4F1 | TE 182,183,184 on Centrepark out for cable replacement in Blackburn. | Gloucester | Scheduled Outage | Construction
16818 | 2010 | 8 | 26 | 0.82292 |  | 168 | 61 | 25 | Blackburn | 8/4.8kV | 4F1 | Defective cable section caused G369B fuse to blow interrupting power to one transformer on Bearbrook & one on Northpark. | Gloucester | Defective Equipment
16869 | 2010 | 9 | 4 | 0.16667 |  | 144 | 12 | 5 | Blackburn | 8/4.8kV | 4F1 | Vines caused transformer X24215 at the rear of 76 Bearbrook to open. | Gloucester | Tree Contacts | Inadequate Trimming
4389 | 2003 | 11 | 4 | 0.45139 |  | 119 | 26 | 13 | Blackburn | 8/4.8kV | 4F1 | Transformer TE0073 at 7 Parkwood Crescent in Blackburn Hamlet was isolated to allow for the repair of a secondary service. ID#4389 | Gloucester | Foreign Interference | Equipment Deterioration Due to Age
5876 | 2004 | 11 | 12 | 0.40625 |  | 165 | 36 | 13 | Blackburn | 8/4.8kV | 4F1 | Planned outage to transformer TE187 at 47 Centrepark Dr for replacment. | Gloucester | Scheduled Outage | Repair
5898 | 2004 | 11 | 17 | 0.40625 |  | 135 | 11 | 5 | Blackburn | 8/4.8kV | 4f1 | Maintenance work ? | Gloucester | Scheduled Outage | Preventive Maintenance
7688 | 2005 | 12 | 5 | 0.57639 |  | 20 | 3 | 9 | Blackburn | 8/4.8kV | 4F1 | Transformer 226 at 25 Burndale was isolated to replace service | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
12549 | 2008 | 6 | 4 | 0.73056 |  | 142 | 6789 | 3043 | Blackburn | 8/4.8kV | 4F1, 4F4 | At 5:32pm the 4F1(backfeeding F3) and 4F4(backfeeding F8) tripped open. Circuit patrolled by 24/7 crews and no apparent cause could be found. Circuits were split and picked up one at a time. All circuits held and no loss of load showed on trend graphs. 3043 customers affected, power was restored at 19:54. | Gloucester | Unknown/Other | No Apparent Cause
3122 | 2003 | 1 | 17 | 0.24167 |  | 152 | 1510 | 676 | Blackburn | 8/4.8kV | 4F3 | G176R OPENED CAUSING SINGLE PHASE ON 4F3 BREAKER WAS OPENED CREW WIRED AND INTSALLLED JUMPER ON G176 AND THE 4F3 WAS RESTORED | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15686 | 2010 | 1 | 26 | 0.84375 |  | 40 | 1 | 2 | Blackburn | 8/4.8kV | 4F3 | At 2655 Innes Rd, transformer TP2180 was isolated from G827 due to defective Live Line Clamps. Crews dropped load from G827, replaced Live Line Clamps on Two phases and restored customers. | Gloucester | Defective Equipment
3177 | 2003 | 2 | 9 | 0.76736 |  | 115 | 243 | 127 | Blackburn | 8/4.8kV | 4F3 | Blown fuse on dip pole found but switch did not open, same re-fused and closed to restore load. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20003 | 2012 | 2 | 12 | 0.60417 |  | 97 | 2 | 1 | Blackburn | 8/4.8kV | 4F3 | Transformer #X19493 located at 3341 Navan Rd opened up due to squirrel contact | Gloucester | Foreign Interference | Animal
20031 | 2012 | 2 | 17 | 0.39583 |  | 92 | 21 | 14 | Blackburn | 8/4.8kV | 4F3 | At 09:30 transformer TE425 at 28 Glenpark was isolated to allow crew to replace defective elbows and inserts. 14 customers were affected for 92 minutes. Blackburn (4F3) ID# 20031 | Gloucester | Scheduled Outage
10042 | 2007 | 2 | 20 | 0.39028 |  | 146 | 487 | 200 | BLACKBURN | 8/4.8kV | 4F3 | Section of 77M5 was isolated to allow Hydro One to remove section of 115KV overhead line, whick is over our circuits. | Gloucester | Scheduled Outage | Construction
10148 | 2007 | 3 | 19 | 0.39653 |  | 103 | 65 | 38 | Blackburn | 8/4.8kV | 4F3 | T691W, T692W and T700W padmount transformers on Orient Dr in Blackburn Hamlet were isolated for elbow and insert replacement | Gloucester | Scheduled Outage | Preventive Maintenance
20179 | 2012 | 3 | 19 | 0.375 |  | 150 | 30 | 12 | Blackburn | 8/4.8kV | 4F3 | TE392 at 52 Glenn Park was isolated to allow crews to replace defective elbows and insters. 12 customers affected for 150 minutes. Blackburn (4F3) | Gloucester | Scheduled Outage | Repair
4921 | 2004 | 3 | 20 | 0.57639 |  | 340 | 51 | 9 | Blackburn | 8/4.8kV | 4F3 | D. Provost reports elbows repair and transformer replaced. All power restored at TE2144. Transformer failed due to water damage. | Gloucester | Adverse Environment | Flooding
10208 | 2007 | 4 | 3 | 0.40486 |  | 167 | 125 | 45 | Blackburn | 8/4.8kV | 4F3 | Scheduled outaged to replace elbows and inserts on T1239, T1240, T1241, & T694 | Gloucester | Scheduled Outage | Preventive Maintenance
10209 | 2007 | 4 | 3 | 0.53264 |  | 173 | 130 | 45 | Blackburn | 8/4.8kV | 4F3 | Scheduled outaged to replace elbows and inserts on T695, T696, T697 | Gloucester | Scheduled Outage | Preventive Maintenance
10215 | 2007 | 4 | 5 | 0.41667 |  | 126 | 63 | 30 | Blackburn | 8/4.8kV | 4F3 | Transformers T690, T689 and T688 on Orient park dr. were isolated for elbow and insert replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
10216 | 2007 | 4 | 5 | 0.53472 |  | 95 | 48 | 30 | Blackburn | 8/4.8kV | 4F3 | Transformers T687, T1237 and TP4208 on Orient park dr. were isolated for elbow and insert replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
12273 | 2008 | 4 | 12 | 0.74722 |  | 232 | 457 | 864 | Blackburn | 8/4.8kV | 4F3 | Defective cable between T281 and T282 on Eastpark found. Fault isolated and customers restored via backfeed of circuit loop on the 4F3 out of Blackburn. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12380 | 2008 | 5 | 3 | 0.92986 |  | 428 | 606 | 100 | BLACKBURN | 8/4.8kV | 4F3 | Blown elbow at T411, 33 Oakhurst, Gloucester caused an outage to 10 transformers in Blackburn. When 24/7 crew closed in the normal open point to restore power, the fuse at G305W blew. Crew found Defective cable between T291W and T490. On-call crew called in to repair blown elbow and assist with outage. | Gloucester | Defective Equipment
8226 | 2006 | 5 | 4 | 0.33125 |  | 73 | 1 | 1 | Blackburn | 27.6/16kV | 4F3 | Transformer #5041 located at 2401 Cleroux isolated due to fuse being open, possibly due to hot line clamp that needs to be replaced | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8324 | 2006 | 5 | 19 | 0.41667 |  | 395 | 132 | 20 | Blackburn | 8/4.8kV | 4F3 | T442W and T518W removed from service and replaced with TP3176 on Glen Park Rd, Blackburn | Gloucester | Scheduled Outage | Preventive Maintenance
3488 | 2003 | 5 | 26 | 0.39306 |  | 114 | 19 | 10 | Blackburn | 8/4.8kV | 4F3 | Transformer #2159 isolated to change leaking transformer. All customers notified. 10 customers affected in outage to replace transformer. | Gloucester | Scheduled Outage | Repair
8405 | 2006 | 6 | 1 | 0.54167 |  | 65 | 12 | 11 | Blackburn | 8/4.8kV | 4F3 | Isolated transformer 1398 at 2577 Cleroux Cres to replace the pole | Gloucester | Scheduled Outage | Construction
10627 | 2007 | 6 | 14 | 0.42639 |  | 109 | 0 | 17 | Blackburn | 8/4.8kV | 4F3 | Transformer TE1114 at 2026 Keldon was isolated to replace defective elbow inserts. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
10680 | 2007 | 6 | 20 | 0.52778 |  | 360 | 12 | 2 | Blackburn | 8/4.8kV | 4F3 | VE26G & VE27G at 2737 & 2767 Innes rd were isolated for planned customer maintenance | Gloucester | Scheduled Outage | Preventive Maintenance
20856 | 2012 | 6 | 24 | 0.61458 |  | 173 | 58 | 20 | Blackburn | 8/4.8kV | 4F3 | Transformer # X24219 at 2035 Gravelle was opened to allow crew to repair dammaged secondaries | Gloucester | Scheduled Outage | Repair
16417 | 2010 | 7 | 7 | 0.34375 |  | 28 | 5 | 10 | BLACKBURN MS | 8/4.8kV | 4F3 | TRANSFORMER GLTE0272 AT 45 WEDGEWOOD ISOLATED TO ALLOW FOR SERVICE UPGRADE | Gloucester | Scheduled Outage | Construction
14746 | 2009 | 7 | 14 | 0.53125 |  | 99 | 3 | 2 | Blackburn | 8/4.8kV | 4F3 | Transformer #X19493 located at 3341 Navan Rd isolated for a pole change | Gloucester | Scheduled Outage | Construction
18757 | 2011 | 7 | 17 | 0.81181 |  | 20 | 299 | 896 | Blackburn MS | 8/4.8kV | 4F3 | 4F3 Circuit Tripped during severe storm and was closed with success 20 minutes later | Gloucester | Adverse Weather | Wind
14803 | 2009 | 7 | 21 | 0.91111 |  | 44 | 1 | 1 | Blackburn | 8/4.8kV | 4F3 | At 21:52 trans fuse failed to due bird contact .at 3433 NAVAN ROAD, GLOU. Refused power restored | Goulburn | Foreign Interference | Bird
10943 | 2007 | 7 | 24 | 0.42222 |  | 95 | 16 | 10 | Blackburn | 8/4.8kV | 4F3 | TE318 at 2296 Orient Park was isolated for repairs to cable terminations. | Gloucester | Scheduled Outage | Repair
10944 | 2007 | 7 | 24 | 0.56458 |  | 57 | 10 | 10 | Blackburn | 8/4.8kV | 4F3 | TE779 at 46 Compata Way was isolated for cable termination repairs. | Gloucester | Scheduled Outage | Repair
3825 | 2003 | 7 | 31 | 0.74306 |  | 88 | 186 | 127 | Blackburn | 8/4.8kV | 4F3 | Switch G202W on Innes Road went defective. As there was digging going on in the area and a U/G Bell wire was damaged in the trench it was though that a hydro cable may have been damaged also. Crews investigated the outage as such and upon further investigation found that it was only the switch. The switch was replaced and full power was restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5598 | 2004 | 8 | 1 | 0.84028 |  | 448 | 75 | 10 | Blackburn | 8/4.8kV | 4F3 | Blown Transformer @ 409 at 18 Oakhurst. On call crew called in. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14929 | 2009 | 8 | 10 | 0.68125 |  | 14 | 1 | 5 | Blackburn MS | 8/4.8kV | 4F3 | Transformer GLTE1171 at 30 Ridgeburn Gate isolated to allow for reconnection after repairs to defective u/g | Gloucester | Scheduled Outage | Repair
18934 | 2011 | 8 | 15 | 0.37153 |  | 15 | 0 | 1 | Blackburn | 8/4.8kV | 4F3 | Ottawa Fire reported sparking wires at transformer pole X19500 at 3270 Navan Road. Crews replaced defective cutout and restored transformer. 1 customer affected | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7142 | 2005 | 8 | 16 | 0.43403 |  | 15 | 2 | 10 | Blackburn | 8/4.8kV | 4F3 | transformer 1199 on Navan Rd. taken out of service for new line construction. 10 customers on navan Rd affected | Gloucester | Scheduled Outage | Construction
13112 | 2008 | 8 | 19 | 0.080556 |  | 29 | 12 | 25 | Blackburn | 8/4.8kV | 4F3 | Blown arrestor on the O/H on Navan Rd, caused the 4F3 to auto reclosed. | Gloucester | Adverse Weather | Lightning
5700 | 2004 | 8 | 20 | 0.52778 |  | 135 | 22 | 10 |  | 27.6/16kV | 4F3 | Scheduled outage. | Gloucester | Scheduled Outage
11117 | 2007 | 8 | 21 | 0.38542 |  | 110 | 302 | 165 | Blackburn | 8/4.8kV | 4F3 | Overhead section of 4F3 on Navan road required isolation for Hydro 1 to remove 115kv NIU overhead transmission lines. | Gloucester | Scheduled Outage | Construction
7182 | 2005 | 8 | 22 | 0.60417 |  | 2 | 2 | 49 | Blackburn | 8/4.8kV | 4F3 | On restoring GR4 recloser the white phase opened. Crew reported that recloser was difficult to close and get it to stay closed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5703 | 2004 | 8 | 23 | 0.52847 |  | 69 | 9 | 8 |  | 120/208 | 4F3 | T70 at 63 Westpark Dr isolated toallow crews to replace cables and terminate ends. | Gloucester | Scheduled Outage | Repair
9039 | 2006 | 8 | 24 | 0.41319 |  | 50 | 8 | 10 | Blackburn | 8/4.8kV | 4F3 | Transformer #GL005982 located at 2631 Cleroux isolated due to crew spinning in new secondary buss | Gloucester | Scheduled Outage | Construction
9043 | 2006 | 8 | 24 | 0.48958 |  | 35 | 4 | 7 | Blackburn | 8/4.8kV | 4F3 | Jamie Leblanc opened transformer at 2551 Cleroux to install new spun buss | Gloucester | Scheduled Outage | Preventive Maintenance
9057 | 2006 | 8 | 25 | 0.44792 |  | 105 | 12 | 7 | Blackburn | 8/4.8kV | 4F3 | Dolton Henry opened transformer 1398 at 2561 Cleroux to change an open wire servie to a triplex | Gloucester | Scheduled Outage | Preventive Maintenance
7261 | 2005 | 9 | 2 | 0.52083 |  | 40 | 3 | 4 | Blackburn | 8/4.8kV | 4F3 | Transformer at 1030 Navan rd was isolated to relocate services | Gloucester | Scheduled Outage | Preventive Maintenance
4134 | 2003 | 9 | 23 | 0.43056 |  | 141 | 7 | 3 | Blackburn | 8/4.8kV | 4F3 | the transformer at 2878 Navan road was shutdown to add a new service. | Gloucester | Scheduled Outage | Construction
11365 | 2007 | 9 | 23 | 0.37847 |  | 55 | 2 | 2 | Blackburn | 120/208 | 4F3 | Triplex disconnected to 3326 & 3330 Navan Rd to relocate on new pole. Pole was replaced due to vehicle accident earlier this morning. | Gloucester | Foreign Interference | Vehicle
15155 | 2009 | 9 | 23 | 0.38958 |  | 72 | 14 | 12 | Blackburn | 8/4.8kV | 4F3 | TE392 at 52 Glen Park was isolated from Hydro Ottawa Sources to take transformer PCB samples. | Gloucester | Scheduled Outage
19241 | 2011 | 9 | 23 | 0.40972 |  | 10 | 0 | 2 | Blackburn | 8/4.8kV | 4F3 | Isolated transformer X19422 at 3689 Navan Rd to disconnect service | Gloucester | Scheduled Outage | Emergency Services Request
9385 | 2006 | 10 | 5 | 0.44236 |  | 91 | 15 | 10 | Blackburn | 8/4.8kV | 4F3 | Transformer #TP4208 (formerly T1238B) located on Belmore Lane was isolated to replace padmount transformer. WP #2-834 | Gloucester | Scheduled Outage | Preventive Maintenance
5829 | 2004 | 10 | 6 | 0.45417 |  | 96 | 3 | 2 | Blackburn | 8/4.8kV | 4F3 | Contractor dug into the cable at the rear of 2739 Innes Rd. | Nepean | Foreign Interference | Dig-in
4253 | 2003 | 10 | 14 | 0.59375 |  | 469 | 493 | 157 | Blackburn | 8/4.8kV | 4F3 | Customer dig in between Transformer TE516 and TE517 which inturn caused switch G226W to rupture and transformer TE422 to go defective and needed to be changed out. | Gloucester | Foreign Interference | Dig-in
13438 | 2008 | 10 | 27 | 0.90694 |  | 19 | 10 | 33 | Blackburn | 8/4.8kV | 4F3 | On restoring the recloser on RX2031 RWB recloser to blue phase switch opened causing a power interruption to 33 customers. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4436 | 2003 | 11 | 12 | 0.41667 |  | 60 | 1 | 1 | Blackburn | 8/4.8kV | 4F3 | Transformer #874 2850 Navan Road was isolated to allow for the upgrade of the transformer. ID#4436 | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
5877 | 2004 | 11 | 12 | 0.54167 |  | 150 | 22 | 9 | Blackburn | 8/4.8kV | 4F3 | Planned outage to transformer TE415 at 32 Eastpark for replacment. | Gloucester | Scheduled Outage | Repair
5889 | 2004 | 11 | 16 | 0.40972 |  | 79 | 16 | 12 | Blackbrun | 8/4.8kV | 4F3 | TE188 isolated to allow crews to replace cables in the area of Redberry. 12 Customers affected in planned power outage. | Gloucester | Scheduled Outage | Construction
5890 | 2004 | 11 | 16 | 0.52431 |  | 72 | 14 | 11 | Blackbrun | 8/4.8kV | 4F3 | TE189 on Silver Aspen is now isolated to allow crews to replace cables. 12 Customers affected in planned outage. | Gloucester | Scheduled Outage | Preventive Maintenance
19656 | 2011 | 12 | 1 | 0.40833 |  | 88 | 21 | 14 | Blackburn | 8/4.8kV | 4F3 | Underground Crew isolated submersable transformer TE0425 at 28 Glenn Park to make repairs to customers faulted service | Gloucester | Scheduled Outage
5970 | 2004 | 12 | 4 | 0.52083 |  | 45 | 8 | 11 | Blackburn | 8/4.8kV | 4F3 | Service upgrade | Gloucester | Scheduled Outage | Preventive Maintenance
7758 | 2005 | 12 | 23 | 0.51042 |  | 385 | 132 | 32 | Blackburn | 8/4.8kV | 4f3 | Dump Truck contacted primary neutral, and bell wire which broke hydro pole. Openers cut in to restore power to all customers except one business, who closed early for the holidays. | Gloucester | Foreign Interference | Vehicle
15084 | 2009 | 9 | 10 | 0.46528 |  | 270 | 9 | 2 | Blackburn | 8/4.8kV | 4F3, 4F8 | VE26G @ 2737 Innes & VE27G @ 2767 Innes were isolated for planned customer maintenance. | Gloucester | Scheduled Outage | Preventive Maintenance
11911 | 2008 | 1 | 9 | 0.35347 |  | 117 | 1016 | 521 | Blackburn | 8/4.8kV | 4F4 | Found a blown lightning arrestor at switch 162R @ 22 Beaverbrook | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7803 | 2006 | 1 | 13 | 0.024306 |  | 230 | 15 | 4 | Blackburn | 8/4.8kV | 4F4 | T3088 on Innes Rd /Blair Rd out to allow cable at riser pole to be shortened. | Gloucester | Scheduled Outage | Construction
9963 | 2007 | 1 | 24 | 0.39583 |  | 155 | 13 | 5 | Blackburn | 8/4.8kV | 4F4 | Transformer isolated at 2477 Cleroux due to pole change | Gloucester | Scheduled Outage | Construction
6305 | 2005 | 3 | 20 | 0.38611 |  | 23 | 4 | 10 | Blackburn | 8/4.8kV | 4F4 | Isolate Transformer #5582 at 5 Bearbrook to replace bad connector | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5034 | 2004 | 4 | 21 | 0.51319 |  | 117 | 165 | 115 | Blackbrun | 12/7.2kV | 4F4 | White phase cable section failed between T125 & T124 on Woodburn St. Cable section isolated for crew to repair cable. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
20602 | 2012 | 5 | 26 | 0.072917 |  | 161 | 8 | 3 | Blackburn | 8/4.8kV | 4F4 | Storm casused the pole at Innes and Anderson to break. Crew reqired isolation of all circuits on the pole to make temporary repairs. Blackburn (4F4) ID#20602 | Gloucester | Adverse Weather
5213 | 2004 | 5 | 27 | 0.38681 |  | 71 | 12 | 10 | Blackburn | 8/4.8kV | 4F4 | Transformer T125 on Woodburn isolated to allow contractor to drill into concert base. | Gloucester | Scheduled Outage | Repair
5315 | 2004 | 6 | 16 | 0.41319 |  | 163 | 62 | 23 | Blackburn | 8/4.8kV | 4F4 | Isolation of transformers TE89 & TE90 on Parkridge Cr for cable replacement. | Gloucester | Scheduled Outage | Construction
5316 | 2004 | 6 | 16 | 0.55556 |  | 78 | 9 | 7 | Blackburn | 8/4.8kV | 4F4 | Transformer TE91 on Parkridge Cr. isolated for cable replacement. | Gloucester | Scheduled Outage | Construction
5322 | 2004 | 6 | 17 | 0.4125 |  | 87 | 17 | 12 | Blackburn | 8/4.8kV | 4F4 | TE65 R now called TP2617 as part of cable replacement in Blackburn. 13 Parkridge. | Gloucester | Scheduled Outage | Construction
5529 | 2004 | 7 | 20 | 0.45833 |  | 90 | 9 | 6 | Blackburn | 8/4.8kV | 4F4 | Transformer TE72W isolated to make connections to new cable. | Gloucester | Scheduled Outage | Construction
5531 | 2004 | 7 | 20 | 0.5625 |  | 79 | 17 | 13 | Blackburn | 8/4.8kV | 4F4 | Transformer TE73W isolated to make connections to new cable. | Gloucester | Scheduled Outage | Construction
5543 | 2004 | 7 | 21 | 0.54514 |  | 25 | 5 | 13 | Blackburn | 8/4.8kV | 4F4 | Transformer TE73W isolated to make connections to new cable. | Gloucester | Scheduled Outage | Construction
7061 | 2005 | 8 | 4 | 0.68403 |  | 39 | 6 | 9 | Blackburn | 8/4.8kV | 4F4 | Truck pulled down neutral wire on Ridge Rd at Anderson. G60R opened to make repairs. | Gloucester | Foreign Interference | Vehicle
9011 | 2006 | 8 | 21 | 0.48264 |  | 175 | 155 | 72 | Blackburn | 8/4.8kV | 4F4 | A cable fault bet Transformer T127W(36 Southpark) and G79W(Gravelle north of east entrance) | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9118 | 2006 | 9 | 4 | 0.67431 |  | 63 | 46 | 54 | Blackburn | 8/4.8kV | 4F4 | Cable fault between T499R and T121R On Woodburn and Woodhill in Gloucester. Cable isolated and all customers restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19092 | 2011 | 9 | 4 | 0.5625 |  | 120 | 30 | 15 | Blackburn | 8/4.8kV | 4F4 | TE223 at 53 Bearbrook was isolated to allow crew to replace a secondary pedestal | Gloucester | Defective Equipment
9261 | 2006 | 9 | 21 | 0.41667 |  | 104 | 19 | 11 | Blackburn | 8/4.8kV | 4F4 | Transformer #GL004605 located at 2551 Gravelle isolated due to pole change | Gloucester | Scheduled Outage | Preventive Maintenance
9324 | 2006 | 9 | 27 | 0.43056 |  | 120 | 24 | 12 | Blackburn | 8/4.8kV | 4F4 | Cable section still reads bad after repair, needs to be reisolated. | Gloucester | Scheduled Outage | Repair
15352 | 2009 | 11 | 5 | 0.38194 |  | 74 | 7 | 6 | Blackburn | 8/4.8kV | 4F4 | Bill Poston opened TE728 to perform repairs to secondary services of transformer. | Gloucester | Scheduled Outage | Repair
4428 | 2003 | 11 | 12 | 0.39931 |  | 275 | 69 | 15 | Blackburn | 8/4.8kV | 4F4 | Transformer 454 on Valewood Cr isolated for replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
4459 | 2003 | 11 | 14 | 0.36111 |  | 236 | 63 | 16 | Blackburn | 8/4.8kV | 4F4 | Plan outage to change transformer | Gloucester | Scheduled Outage | Preventive Maintenance
4469 | 2003 | 11 | 17 | 0.36875 |  | 301 | 80 | 16 | Blackburn | 8/4.8kV | 4F4 | Cable and transformer replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
11759 | 2007 | 11 | 24 | 0.44028 |  | 91 | 39 | 26 | Blackburn | 8/4.8kV | 4F4 | Barrier board had fallen across primary cables @ TE451, 52 Woodburn, G266R replaced & closed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6084 | 2004 | 12 | 21 | 0.58333 |  | 7 | 1 | 9 | BLACKBURN | 27.6/16kV | 4F4 | Reconnct underground service in GLTE218 rear of 7 Highburn | Gloucester | Scheduled Outage | Repair
7790 | 2006 | 1 | 10 | 0.42292 |  | 224 | 22 | 6 | Blackburn | 27.6/16kV | 4F5 | T2410B out of service to allow crew to reterminate cbls. | Gloucester | Scheduled Outage | Construction
15658 | 2010 | 1 | 15 | 0.42014 |  | 377 | 14 | 5 | Blackburn | 8/4.8kV | 4F5 | Tree branches and conductor downed caused one phase of G51 at Dolman Ridge & Anderson to blow as well as single phase fuse G392B to blow. Crews restored power up to G392B then repaired the downed conductor & cleared branches before restoring G392B. | Gloucester | Tree Contacts | Tree Limb Fallen
7821 | 2006 | 1 | 18 | 0.77292 |  | 147 | 22 | 9 | Blackburn | 8/4.8kV | 4F5 | Tree contact with O/H caused switch G60R to open, tree removed and switch closed. | Gloucester | Tree Contacts | Inadequate Trimming
19934 | 2012 | 1 | 31 | 0.45556 |  | 164 | 3 | 1 | Blackburn | 8/4.8kV | 4F5 | Tree contact caused the transformer fuse to open at transformer X24122 located at 5795 Dolman Ridge Rd. Crews patrolled & cleared the obstruction. | Gloucester | Tree Contacts | Inadequate Trimming
7892 | 2006 | 2 | 5 | 0.11111 |  | 599 | 178 | 34 | Blackburn | 8/4.8kV | 4F5 | Adverse weather conditions, leaking insulators and defective cutouts on Ridge Road/Ramysville caused G59R to blow. GR14 tripped during restoration. All repairs made and power restored. | Gloucester | Adverse Weather
13978 | 2009 | 2 | 14 | 0.89097 |  | 250 | 41 | 18 | Blackburn | 8/4.8kV | 4F5 | S16751 was blown due to a vehicle accident contacting a pole at Ramsyville Road and Ridge Rd. G59R had to be opened to allow crew to replace neutral on broken pole. Once neutral was repaired G59R closed and S16751 was left open while crew make temporary repairs to broken pole. | Gloucester | Foreign Interference | Vehicle
14066 | 2009 | 3 | 16 | 0.36111 |  | 28 | 0 | 1 | Blackburn | 8/4.8kV | 4F5 | S272R on Anderson rd. was opened to remove tree from overhead line. | Gloucester | Tree Contacts | Tree Fallen
15865 | 2010 | 3 | 29 | 0.13125 |  | 71 | 7 | 6 | Blackburn | 8/4.8kV | 4F5 | Crew found tree limb on wires. Limb removed and G60R fuse replaced to restore power to Ridge Rd | Gloucester | Tree Contacts | Tree Limb Fallen
10268 | 2007 | 4 | 16 | 0.31597 |  | 440 | 29 | 4 | Blackburn | 8/4.8kV | 4F5 | Tree contacted O/H causing G60R fuse to open. | Gloucester | Adverse Weather | Snow
10269 | 2007 | 4 | 16 | 0.3375 |  | 427 | 36 | 5 | Blackburn | 8/4.8kV | 4F5 | G51W,& B phase fuses opened due to tree contact. | Gloucester | Adverse Weather | Snow
16064 | 2010 | 5 | 8 | 0.31458 |  | 303 | 56 | 11 | Blackburn | 8/4.8kV | 4F5 | G50 found blown, after quick partol, no apperent cause found and G50 was re-fused and all load restored. Customers on Renaud and Maurice were affected. | Gloucester | Unknown/Other | No Apparent Cause
18239 | 2011 | 5 | 28 | 0.81181 |  | 136 | 2 | 1 | Blackburn | 8/4.8kV | 4F5 | tree contact caused transformer X24074 @ 4642 Ridge rd to open. | Gloucester | Tree Contacts | Inadequate Trimming
12540 | 2008 | 6 | 4 | 0.27778 |  | 165 | 29 | 18 | Blackburn | 8/4.8kV | 4F5 | Branches in contact with primary lead of Tx. X19670 @ 4777 Ridge rd caused the transformer fuse to blow as well as line switch G59R. Line patrolled, G59R closed restring most customers. Branches removed at Tx. X19670 and fuse replaced. | Gloucester | Tree Contacts | Inadequate Trimming
8459 | 2006 | 6 | 9 | 0.84861 |  | 655 | 33 | 3 | Blackburn | 8/4.8kV | 4F5 | Tree Limb caught service wire at 2180 Desjardins Street and broke pole. Pole and Transformer GO3044 were replaced as well as a new switch installed. | Gloucester | Tree Contacts | Tree Limb Fallen
16349 | 2010 | 6 | 28 | 0.66042 |  | 174 | 9 | 3 | Blackburn | 8/4.8kV | 4F5 | G50B found Blown on Renaud. Crew patrolled no problem found. Refused and closed in switch. | Gloucester | Unknown/Other
14742 | 2009 | 7 | 14 | 0.28472 |  | 90 | 2 | 1 | Blackburn | 8/4.8kV | 4F5 | Transformer #X19679 located at 4727 Ridge Rd isolated due to animal contact | Gloucester | Foreign Interference | Animal
18707 | 2011 | 7 | 17 | 0.81319 |  | 891 | 653 | 44 | Blackburn | 8/4.8kV | 4F5 | 4F5 circuit opened due a downed conductor during the wind storm. O/H circuit complete was isolated to allow crew to repair broken conductor. | Gloucester | Adverse Weather | Wind
16670 | 2010 | 8 | 4 | 0.75972 |  | 796 | 186 | 14 | Blackburn | 8/4.8kV | 4F5 | Adverse weather caused G59 on Anderson and Ridge. | Ottawa | Adverse Weather
16679 | 2010 | 8 | 5 | 0.65278 |  | 55 | 13 | 14 | Blackburn | 8/4.8kV | 4F5 | Down neutral on Ridge Rd, crew opened G59 to make repairs. Caused from storm on Aug 4, 2010. | Gloucester | Defective Equipment
11054 | 2007 | 8 | 14 | 0.89097 |  | 255 | 4 | 1 | Blackburn |  | 4F5 | 4727 Ridge Rd transformer fuse blew due to vines growing up the pole, vines cleared and transformer re-fused. | Gloucester | Tree Contacts | Inadequate Trimming
11101 | 2007 | 8 | 19 | 0.85417 |  | 41 | 3 | 5 | Blackburn | 8/4.8kV | 4F5 | overhead Transformer X18853 was opened to isolate single phase overhead line to remove tree limb. | Gloucester | Tree Contacts | Tree Limb Fallen
11126 | 2007 | 8 | 22 | 0.38194 |  | 200 | 240 | 72 | Blackburn | 8/4.8kV | 4F5 | 4F5 line required isolation for Hydro 1 to remove 115kv NIU overhead transmission lines. | Gloucester | Scheduled Outage | Construction
5702 | 2004 | 8 | 23 | 0.42361 |  | 58 | 8 | 8 | Blackbrun | 27.6/16kV | 4F5 | Transformer isolated to allow crews to replace cable section, and terminate same. At 4 Parkridge Cres. | Gloucester | Scheduled Outage | Construction
16855 | 2010 | 9 | 2 | 0.84375 |  | 88 | 4 | 3 | Blackburn | 8/4.8kV | 4F5 | Fuse at G349 on Ramsyville rd. Opened for no apparent reason. Crew patrolled refused and closed. | Gloucester | Unknown/Other | No Apparent Cause
9237 | 2006 | 9 | 16 | 0.65903 |  | 161 | 121 | 45 | Blackburn | 8/4.8kV | 4F5 | B & W phase arrestors of the 4F5 failed at Blackburn station causing the 4F5S-X fuses to open. Arrestors cut free and fuses closed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
11319 | 2007 | 9 | 17 | 0.48542 |  | 323 | 24 | 68 | Blackburn | 8/4.8kV | 4F5 | While opening a switch supplying Tx 5637 at 2617 Anderson to replace a defective hot line clamp, lead to arrestor at this location failed & caused a flash tripping the circuit. Scada control problems added to length of outage. Run - off to Tx 5637 was then isolated to repair insulators & arrestors. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9273 | 2006 | 9 | 21 | 0.72569 |  | 88 | 88 | 60 | Blackburn | 8/4.8kV | 4F5 | 4F5 feeder isolated to allow crews to replace insulatore at Blackburn Station. | Gloucester | Scheduled Outage | Repair
9292 | 2006 | 9 | 24 | 0.4375 |  | 229 | 57 | 15 | Blackburn | 8/4.8kV | 4F5 | John Streng found switch G50B open, patrolled O/H on Renaud and found tree on O/H. | Gloucester | Adverse Weather | Wind
15189 | 2009 | 9 | 29 | 0.96875 |  | 90 | 14 | 9 | Blackburn | 8/4.8kV | 4F5 | G60R fuse found opened on Ridge Rd. 9 Customers effected in power outage due to tree contact. | Gloucester | Tree Contacts | Inadequate Trimming
19309 | 2011 | 10 | 3 | 0.24375 |  | 83 | 8 | 6 | Blackburn | 8/4.8kV | 4F5 | G60 red on Ridge Road found blown, patrol revealed no apparent cause | Gloucester | Unknown/Other | No Apparent Cause
19310 | 2011 | 10 | 3 | 0.33333 |  | 132 | 13 | 6 | Blackburn | 8/4.8kV | 4F5 | G60 red on Ridge Road found blown for a second time, patrol revealed a tree limb had fallen onto the red phase. Crew cleared the limb, refused and closed. | Gloucester | Tree Contacts | Tree Limb Fallen
7444 | 2005 | 10 | 11 | 0.49306 |  | 50 | 4 | 5 | BeaconHill | 8/4.8kV | 4F5 | G60R open to allow removal of large tree from overhead line. | Gloucester | Tree Contacts | Tree Limb Fallen
13531 | 2008 | 10 | 29 | 0.24722 |  | 846 | 99 | 7 | Blackburn | 8/4.8kV | 4F5 | possible tree contact caused the G59R fuse to pen @ Anderson and Ridge rd. crew patrolled refused and closed. | Gloucester | Tree Contacts
13534 | 2008 | 10 | 29 | 0.39653 |  | 1171 | 59 | 3 | Blackburn | 8/4.8kV | 4F5 | crew repaired red phase primary that came down at 2811 Ramsyville rd. feeding three overhead transformers. | Gloucester | Adverse Weather | Snow
11682 | 2007 | 11 | 8 | 0.23472 |  | 399 | 53 | 8 | Blackburn | 8/4.8kV | 4F5 | Primary conductor was found down in corn field on Ridge Rd fed from G59 at Anderson Rd crew had to sleeve #4 conductor in 6 locations to restore power | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
13795 | 2008 | 12 | 25 | 0.083333 |  | 358 | 119 | 20 | Blackburn | 8/4.8kV | 4F5 | Tree fell into secondary on Maurice causing G50B to open. Tree was removed and G50 was refused and closed. | Gloucester | Tree Contacts | Tree Fallen
19791 | 2012 | 1 | 5 | 0.43681 |  | 121 | 60 | 30 | Blackburn MS | 8/4.8kV | 4f8 | TP7180R at 2510 Autumn Hill Cres & TP8539 at 2524 Autumn Hill Cres were isolated to allow Hydro Ottawa crews to upgrade cables & change inserts. | Gloucester | Scheduled Outage | Repair
19792 | 2012 | 1 | 5 | 0.56667 |  | 94 | 19 | 12 | Blackburn MS | 8/4.8kV | 4F8 | Transformer TP8541 at 2469 Orient Park was isolated to allow Hydro Ottawa crews to replace cable & elbow & inserts. | Gloucester | Scheduled Outage | Repair
11905 | 2008 | 1 | 8 | 0.16667 |  | 460 | 647 | 90 | Blackburn | 8/4.8kV | 4F8 | Cable fault found at Innes and Eastpark between G249B and TP2614. 4 transformers, approx 90 customers were affected. Cable isoalted and all load restored. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4749 | 2004 | 2 | 1 | 0.63194 |  | 86 | 1648 | 1150 | Blackburn | 8/4.8kV | 4F8 | A broken insulator was detected at switch G305 at Orient Park Dr. Repairs were made, all customers rstore. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6202 | 2005 | 2 | 11 | 0.75694 |  | 169 | 330 | 117 | Blackburn | 8/4.8kV | 4F8 | 4F8 feeder auto/reclosed, faulted W phase cable between Txs TE292W & TE1163W, cable isolated and load restored from G315W. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10092 | 2007 | 3 | 6 | 0.97222 |  | 106 | 258 | 146 | Blackburn | 8/4.8kV | 4F8 | Insert at transformer T274R on Orient Park blew out interrupting the down stream txs. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10094 | 2007 | 3 | 6 | 0.43611 |  | 102 | 34 | 20 | Blackburn | 8/4.8kV | 4F8 | TE274R @ 2336 Orient Park was isolated to make permanent repairs to a blown elbow insert, transformer was replaced. | Gloucester | Scheduled Outage | Repair
12115 | 2008 | 3 | 9 | 0.66736 |  | 19 | 48 | 151 | Blackburn | 8/4.8kV | 4F8 | 4F8 auto reclosed, blue phase stress cone at G371 on Innes at Rondell showed flash, cable isolated | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14044 | 2009 | 3 | 12 | 0.13889 |  | 118 | 1753 | 1201 | Blackburn | 27.6/16kV | 4F8 | At 3:20am Scada indicated 4F8 Breaker Opened. 24-7 reported broken insulator on pole is root cause. At 5:18am customers power restored and insulator was replaced and repaired. 4F8 Blackburn. ID#14044 | Gloucester | Adverse Weather | Wind
10118 | 2007 | 3 | 13 | 0.45833 |  | 103 | 21 | 12 | Blackburn | 8/4.8kV | 4F8 | TE693W on Orient Park was isolated to replace elbows & inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
10121 | 2007 | 3 | 13 | 0.5625 |  | 60 | 12 | 11 | Blackburn | 8/4.8kV | 4F8 | TE691 on Orient Park isolated to replace elbows & inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
3348 | 2003 | 4 | 16 | 0.26944 |  | 337 | 608 | 120 | Blackburn Station | 8/4.8kV | 4F8 | Faulted cable between transformers T1357 and T1358 caused loss of 9 transfortmers, customers restored in two sections. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6462 | 2005 | 4 | 25 | 0.80139 |  | 106 | 2 | 1 |  | 8/4.8kV | 4f8 | Defective switch at transformer 100 at 2675 Innes Road. | Gloucester | Defective Equipment
20389 | 2012 | 4 | 25 | 0.38889 |  | 107 | 18 | 10 | Blackburn | 8/4.8kV | 4F8 | TE1160 at 1960 Fallkirk was isolated to allow crews to replace the leaking transformer. | Gloucester | Scheduled Outage | Repair
12351 | 2008 | 4 | 26 | 0.90347 |  | 104 | 19 | 11 | Blackburn | 8/4.8kV | 4F8 | TE1359 @ 1959 Greenway Lane replaced with new transformer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12399 | 2008 | 5 | 6 | 0.40556 |  | 431 | 93 | 13 | Blackburn | 8/4.8kV | 4F8 | TE1359 at 1959 Greenway isolated to clean up oil contaminated soil from previous leakage. Nomenclature changed to TP4199. | Gloucester | Scheduled Outage | Repair
20487 | 2012 | 5 | 9 | 0.75208 |  | 600 | 130 | 13 | Blackburn | 8/4.8kV | 4F8 | Transformer X18764 @ 2 Pennington Lane was found to be deffective. Crews replaces transformer. | Gloucester | Defective Equipment
20501 | 2012 | 5 | 11 | 0.38958 |  | 87 | 14 | 10 | Blackburn | 8/4.8kV | 4F8 | TE776 at 161 Glen Park was isolated to allow crew to replace leaking transformer, | Gloucester | Scheduled Outage | Repair
10583 | 2007 | 6 | 9 | 0.37222 |  | 154 | 3 | 1 | Blackburn | 8/4.8kV | 4F8 | Transformer #X19169 located at 2679 Innes isolated due to Def U/G at Orient Park Pumping Station, caused fuse to blow at this transformer. Defective U/G disconnected & customer to arrange for repairs, they will run on generator as required until repairs are made. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18395 | 2011 | 6 | 13 | 0.39792 |  | 241 | 8 | 2 | Blackburn | 8/4.8kV | 4F8 | Vault Ve26 and VE27 @ 2737 Innes rd were isolated to aloow contractor to perfrom vault maintenance. 2 customers were affected. Blackburn (4F8) | Gloucester | Scheduled Outage
10624 | 2007 | 6 | 14 | 0.9875 |  | 163 | 3302 | 1642 | BLACKBURN | 8/4.8kV | 4F8 | During sectionalizing the cable between 4F8 and G174 was found to be defective. When the 4F8 closed into the fault, it blew the blue phase high side transformer fuse. At the same time a gas detection alarm reported on SCADA, on the 4T2 Transformer. 4F4 breaker was opened by System. Load transferred from the 4F4 to the 4F5, and the 4F8 transferred to the 4F3. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3701 | 2003 | 6 | 25 | 0.80625 |  | 48 | 111 | 139 | Blackburn MS | 8/4.8kV | 4F8 | No cause. | Gloucester | Unknown/Other
3714 | 2003 | 7 | 10 | 0.25694 |  | 4 | 93 | 1400 | Blackburn | 8/4.8kV | 4F8 | G344b isolated to open G344 defective switch. At the request of Jim Kelly. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
8805 | 2006 | 7 | 23 | 0.33333 |  | 120 | 16 | 8 | Blackburn | 8/4.8kV | 4F8 | Mike Gruich opened xfmr X18760 at Innes/Gravelle to do a pcb change | Gloucester | Scheduled Outage | Repair
16756 | 2010 | 8 | 16 | 0.7625 |  | 497 | 182 | 35 | Blackburn |  | 4F8 | TP2615 @ 93 East Park was isolated to allow crew to replace leaking defective transformer. | Gloucester | Defective Equipment
5693 | 2004 | 8 | 18 | 0.40556 |  | 90 | 38 | 25 | Blackburn | 8/4.8kV | 4F8 | TE 415 and TE416 on Eastpark out for termination of new underground cable. | Gloucester | Scheduled Outage | Construction
5694 | 2004 | 8 | 18 | 0.46806 |  | 37 | 8 | 13 | Blackburn | 8/4.8kV | 4F8 | TE413 out for termination of new underground cable. | Gloucester | Scheduled Outage | Construction
17077 | 2010 | 10 | 7 | 0.42153 |  | 128 | 73 | 34 | Blackburn | 8/4.8kV | 4F8 | Two transformers T414 and TP2626 were isolated to connect new cables in transformer. | Gloucester | Scheduled Outage
11865 | 2007 | 12 | 22 | 0.97917 |  | 95 | 32 | 20 | Blackburn | 8/4.8kV | 4F8 | TE1324 secondary at 2666 Innes was isolated to connect new service for new Tim Hortons. 20 commercial customers were affected, but all were closed during the outage. LOEB ran on generator during outage. | Gloucester | Scheduled Outage | Construction
12262 | 2008 | 4 | 9 | 0.97083 |  | 60 | 1 | 1 | Riverdale | 13.2kV | 501 | The 501 cable trip that feeds half of VT8 Carleton Univ. | Ottawa | Unknown/Other
18260 | 2011 | 5 | 31 | 0.49931 |  | 15 | 0 | 1 | Riverdale | 13.2kV | 501 | TR21 (501) circuit tripped due to Carleton University energizing new equipment. 501 feeds only half of Carleton University at VT8. | Ottawa | Unknown/Other
16784 | 2010 | 8 | 20 | 0.11806 |  | 186 | 3 | 1 | Riverdale | 13.2kV | 501 | 501 circuit that is direct feed to Carleton University tripped due to fault on secondary loop fed from vault. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7901 | 2006 | 2 | 8 | 0.31319 |  | 114 | 1623 | 945 | Riverdale | 13.2kV | 502 | TR07 (502) circuit opened fault due to a cable fault between VT196 @ 170 Lees and VT377 @ VT180 Lees. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4822 | 2004 | 2 | 24 | 0.86944 |  | 98 | 16 | 10 | Riverdale | 13.2kV | 503 | 13KV vault, VT247, at 1355 Bank St. shut down for electrical contractor to do emergency repair to 120/208 customer main | Ottawa | Scheduled Outage | Repair
12450 | 2008 | 5 | 19 | 0.125 |  | 150 | 2 | 1 | Riverdale | 13.2kV | 503 | Lemieux island reported loss of power at the Billings Bridge Pumping station (VT156). 24/7 dispatched and found that CB1 was in the open state. Lemieux operator called electrician and they found that the rapid rise relay shorted out due to leaking water damage. Relay was removed and CB1 closed back in by electrician without consent from System Office. | Ottawa | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
5224 | 2004 | 5 | 30 | 0.030556 |  | 268 | 268 | 60 | Riverdale |  | 503 | scheduled outage to 13KV main & xfmr buses @ VT890, Billings Bridge Plaza, for routine maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
19099 | 2011 | 9 | 6 | 0.51111 |  | 52 | 5 | 6 | Riverdale | 13.2kV | 503 | Transformer P300 @ 1187 Bank was opened to allow crew to replace cut-out. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15220 | 2009 | 10 | 6 | 0.18264 |  | 118 | 1375 | 699 | Riverdale | 13.2kV | 503 | Circuit 503 tripped due to a faulted cable between VT64 and SC7949. | Ottawa | Defective Equipment
15273 | 2009 | 10 | 17 | 0.89097 |  | 266 | 18 | 4 | Riverdale | 13.2kV | 503 | Four 13kV vaults were shutdown at Billings Bridge Plaza to allow for a contractor to perform customer owned maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
4378 | 2003 | 11 | 3 | 0.95486 |  | 429 | 15 | 30 | Riverdale | 13.2kV | 503 | Apparent cable fault on the cable section at Billings Bridge Shopping Center between VT890 and VT890W1 caused 503 circuit to be interupted while refusing and re-energizing the blue phase of this cable. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13611 | 2008 | 11 | 14 | 0.61806 |  | 60 | 2 | 2 | King Edward Sub | 4.16kV | 503 | V193 and V195 on Broadview isolated to transfer the 2 vault loads from the AH13 to the AH04 | Ottawa | Scheduled Outage
10851 | 2007 | 7 | 11 | 0.75 |  | 628 | 16 | 6 | Riverdale | 13.2kV | 504 | Circuit 504 (TR06) tripped due to tracking on the 13 kv bus bars in VT580, likely due to dust buildup. Vault equipment was cleaned & repaired by Carleton Electric. | Ottawa | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
7147 | 2005 | 8 | 16 | 0.42361 |  | 204 | 1319 | 388 | Riverdale | 13.2kV | 504 | Scheduled outage at VT580 & VT624, Riviera Apt's 1 & 11 @ 1500 & 1510 Riverside Dr for routine maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
7148 | 2005 | 8 | 16 | 0.58681 |  | 154 | 501 | 195 | Riverdale | 13.2kV | 504 | Scheduled outage at VT708, Riviera Apt's 111 @ 1480 Riverside Dr for routine maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
5717 | 2004 | 8 | 25 | 0.39931 |  | 227 | 2251 | 595 | Riverdale | 13.2kV | 504 | VT389 @ 1551 Riverside was shutdown for clean and torque. | Ottawa | Scheduled Outage | Preventive Maintenance
11929 | 2008 | 1 | 13 | 0.41875 |  | 82 | 12 | 9 | Riverdale | 13.2kV | 505 | Squirrel caused transformer fuse to blow @ 1095 Second Ave. Transformer # OTT3116 | Ottawa | Foreign Interference | Animal
19852 | 2012 | 1 | 18 | 0.081944 |  | 467 | 2755 | 1035 | Riverdale | 13.2kV | 505 | Pole fire at 1382 Kilborn caused SC2-CB3 to trip. SC201 line complete was isolated to allow crews to make repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19932 | 2012 | 1 | 31 | 0.39792 |  | 242 | 238 | 59 | Riverdale | 13.2kV | 505 | The 13kV transformer bus at VT719, 1161 Belanger was isolated to allow an electrician to install micro fit equipment in the customer secondary room. No work took place in the vault. | Ottawa | Scheduled Outage | Construction
19959 | 2012 | 2 | 3 | 0.63958 |  | 129 | 22 | 10 | Riverdale | 13.2kV | 505 | Replaced broken switch feeding transformer X28321 at 1256 Livgstone Ave | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12047 | 2008 | 2 | 15 | 0.34028 |  | 50 | 8 | 9 | Riverdale | 4.16kV | 505 | Fuse to transformer OTT3116 was found blown due to animal contact (Squirrel ) | Ottawa | Foreign Interference | Animal
20038 | 2012 | 2 | 21 | 0.40625 |  | 45 | 14 | 18 | Riverdale | 13.2kV | 505 | Trans X28173 was isolated at 1108 Richard Ave in order to upgrade secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
20119 | 2012 | 3 | 3 | 0.65764 |  | 548 | 73 | 8 | Riverdale | 13.2kV | 505 | crews installed new drop lead and line clamp to X28232. 8 customers affected for 548 minutes. Riverdale TS (505) | Ottawa | Defective Equipment
20133 | 2012 | 3 | 7 | 0.375 |  | 120 | 20 | 10 | Riverdale | 13.2kV | 505 | At 09:00 transformer X28194 at 1394 Kilborn Avenue was isolated to allow crew to replace pole. 10 customers were affected for 120 minutes. Riverdale (505) ID#20133 | Ottawa | Scheduled Outage
3368 | 2003 | 4 | 23 | 0.41111 |  | 268 | 237 | 53 | Riverdale | 13.2kV | 505 | 13kV Vault @ 1177 Belanger/VT621 was shut-down for cleaning. | Ottawa | Scheduled Outage | Preventive Maintenance
12385 | 2008 | 5 | 3 | 0.95139 |  | 50 | 12 | 14 | Riverdale | 13.2kV | 505 | Fuse cut out broken due to age. Fuse replaced. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20603 | 2012 | 5 | 26 | 0.058333 |  | 166 | 149 | 54 | Riverdale | 13.2kV | 505 | Switch feeding blue phase SC201 section on rachael was isolated by crews to remove tree. | Ottawa | Adverse Weather | Wind
16189 | 2010 | 6 | 3 | 0.49306 |  | 41 | 7 | 10 | Riverdale | 13.2kV | 505 | Schedule outage, transformer X27485 at 215 Niagra Dr was isolated for service up-grade. | Ottawa | Scheduled Outage | Preventive Maintenance
6662 | 2005 | 6 | 6 | 0.29097 |  | 46 | 8 | 10 | Riverdale | 13.2kV | 505 | Trans at 182 Crocus Ave refused due to squirrel contact causing outage | Ottawa | Foreign Interference | Animal
10555 | 2007 | 6 | 8 | 0.52361 |  | 56 | 10 | 11 | Riverdale | 4.16kV | 505 | Fuse to Transformer OTT5503 at 1188 Rockingham ave was found blown due to squirrel contact | Ottawa | Foreign Interference | Animal
12596 | 2008 | 6 | 10 | 0.60417 |  | 35 | 2 | 3 | Riverdale | 4.16kV | 505 | Refused blown fuse on transformer OTT3116 at 1096 Secord Av | Ottawa | Adverse Weather | Lightning
8509 | 2006 | 6 | 18 | 0.60208 |  | 163 | 27 | 10 | Riverdale | 13.2kV | 505 | tree contract caused transformer fuse to blow. Fuse replaced all power restored to customers at 1266 Randall st. | Ottawa | Tree Contacts | Inadequate Trimming
18478 | 2011 | 6 | 24 | 0.045833 |  | 206 | 124 | 36 | Riverdale | 13.2kV | 505 | dip to PT173 at 1126 Rockingham one phase of 3 had a sparking termination that was heating up, forced outage to prevent failure and excessive damage | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10812 | 2007 | 7 | 8 | 0.15625 |  | 59 | 10 | 10 | Riverdale | 13.2kV | 505 | Squirrell contact cause transformer fuse to blow Ott1773 at @ 265 Crocus | Ottawa | Foreign Interference | Animal
14836 | 2009 | 7 | 25 | 0.25625 |  | 387 | 45 | 7 | Riverdale | 13.2kV | 505 | Transformer fuse at 2071 Niagara blown due to squirrel contact, same refused and closed to restore power. | Nepean | Foreign Interference | Animal
16675 | 2010 | 8 | 5 | 0.47778 |  | 89 | 13 | 9 | Riverdale | 13.2kV | 505 | Transformer X28235 @ 1360 Dowler was opened due to storm. | Ottawa | Adverse Weather
19495 | 2011 | 10 | 29 | 0.48958 |  | 105 | 19 | 11 | Riverdale | 13.2kV | 505 | Replaced blown fuse feeding transformer X38553 at 1359 Dowler Ave (Squirrel contact ) | Ottawa | Foreign Interference | Animal
13570 | 2008 | 11 | 6 | 0.52431 |  | 34 | 5 | 8 | RIVERDALE | 13.2kV | 505 | At 13:09 transformer @ 1092 Secord Ave. due to animal contact. | Gloucester | Foreign Interference | Animal
13571 | 2008 | 11 | 6 | 0.52431 |  | 30 | 4 | 8 | Riverdale | 13.2kV | 505 | At 13:05 transformer x28120 at 1096 Secord Ave was refused due to animal contact. | Ottawa | Foreign Interference | Animal
4482 | 2003 | 11 | 19 | 0.22639 |  | 67 | 15 | 13 | Riverdale | 13.2kV | 505 | Lameroux reports transformer at 1360 dowler refused and holding. 13 customers interrupted. Possible cause was trees and winds. | Ottawa | Adverse Weather | Wind
10435 | 2007 | 5 | 22 | 0.26111 |  | 120 | 26 | 13 | Riverdale | 4.16kV | 505 (SC201) | Transformer #OTT4487 located at 1376 Micmac St isolated due to animal contact | Ottawa | Foreign Interference | Animal
10441 | 2007 | 5 | 22 | 0.60764 |  | 108 | 32 | 18 | Riverdale | 13.2kV | 505 (SC201) | Transformer #OTT2233 located at 1301 Essex St isolated to repair conductor, as per PC10A#02668 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10457 | 2007 | 5 | 24 | 0.58333 |  | 35 | 2 | 4 | Riverdale | 13.2kV | 505 (SC201) | Transformer #OTT3581 located at 1344 Kilborn Ave isolated due to animal contact | Ottawa | Foreign Interference | Animal
10563 | 2007 | 6 | 8 | 0.84375 |  | 266 | 160 | 36 | Riverdale | 13.2kV | 505 (SC202) | A Local fuse opened feeding customers on Richard due to tree contacts. Crew reports follow up tree trimming is required. | Ottawa | Tree Contacts | Inadequate Trimming
4666 | 2003 | 12 | 30 | 0.51042 |  | 180 | 27 | 9 | TR | 13.2kV | 505 (SC202) | A defective switch caused an outage at Tx OTT2667, 1545 Gilles st. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15822 | 2010 | 3 | 19 | 0.41667 |  | 120 | 12 | 6 | Riverdale | 13.2kV | 505/SC201 | Transformer #X27488 located at 1364 Kilborn isolated for a pole change | Ottawa | Scheduled Outage | Construction
15847 | 2010 | 3 | 25 | 0.80833 |  | 56 | 5 | 5 | Riverdale | 13.2kV | 505/SC201 | Transformer #X28195 located at 1344 Kilborn isolated due to defective primary lead | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18481 | 2011 | 6 | 24 | 0.29792 |  | 113 | 30 | 16 | Riverdale | 13.2kV | 505/SC201 | Transformer #X27479 located at 1335 Kilborn Ave opened up due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
10751 | 2007 | 6 | 28 | 0.35417 |  | 55 | 11 | 12 | Riverdale | 13.2kV | 505/SC201 | Transformer #OTT2235 located at 1330 Kilborn isolated due to animal contact | Ottawa | Foreign Interference | Animal
16812 | 2010 | 8 | 25 | 0.84375 |  | 120 | 20 | 10 | Riverdale | 13.2kV | 505/SC201 | Transformer #X27485 located at 2115 Niagara opened up due to animal contact | Ottawa | Foreign Interference | Animal
13336 | 2008 | 10 | 8 | 0.42292 |  | 66 | 14 | 13 | Riverdale | 4.16kV | 505/SC202 | Transformer #OTT156 located at 1123 Guertin isolated due to squirrel | Ottawa | Foreign Interference | Animal
17188 | 2010 | 10 | 28 | 0.45486 |  | 35 | 6 | 10 | Riverdale | 13.2kV | 505/SC202 | Transformer #X28243 located at 1105 Aldea opened by crew for a scheduled disconnect/reconnect | Ottawa | Scheduled Outage | Construction
18773 | 2011 | 7 | 19 | 0.61458 |  | 558 | 990 | 301 | Riverdale TS | 13.2kV | 506/508/503 | Cable fault on 503 cable section at TV5458 to VT64. Vault remained isolated due to no access. Also overhead section at SC7949-CB3 branch across 2 conductors. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11751 | 2007 | 11 | 22 | 0.41042 |  | 101 | 370 | 220 | RIVERDALE | 13.2kV | 508 | Isolation of SC1576 main bus, to allow crew to connect and energize new SC3057 and TP4909 on Valour St. | Ottawa | Scheduled Outage
18057 | 2011 | 4 | 29 | 0.7375 |  | 78 | 90 | 69 | McCarthy | 13.2kV | 5102 | The 1601 & 5102 O/H on North Bowesville was isolated to allow the crew to remove a tree of the O/H | Ottawa | Tree Contacts | Tree Fallen
18467 | 2011 | 6 | 22 | 0.89514 |  | 119 | 8 | 5 | LISGAR | 13.2kV | 5201 | 5201 BREAKER TRIPPED (TL01) DUE TO DEFECTIVE CABLE BETWEEN VT17 AMD VT30. CABLE ISOLATED AND ALL LOAD RESTORED. | Ottawa | Defective Equipment
3932 | 2003 | 8 | 23 | 0.90625 |  | 371 | 12 | 2 | Lisgar | 13.2kV | 5201 | Scheduled outage to VT723 & VT469, Constitution Bldgs at 360 & 350 Albert for routine maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
19375 | 2011 | 10 | 15 | 0.026389 |  | 369 | 12 | 2 | Lisgar | 13.2kV | 5201 | VT469 & VT723 at 350, 360 Albert isolated for customer maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
15616 | 2010 | 1 | 6 | 0.0125 |  | 432 | 7 | 1 | Lisgar | 13.2kV | 5202 | R1-F red and white phase fuses blown and crew found blown transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8338 | 2006 | 5 | 22 | 0.96528 |  | 7 | 80 | 687 | Lisgar | 13.2kV | 5202 | While switching to isolate the Q bus at Lisgar from Hydro-Ottawa sources, the wrong switch was left open resulting in an outage at a later point in the order to operate. | Ottawa | Human Element | Switching Errors
11906 | 2008 | 1 | 8 | 0.92153 |  | 193 | 19 | 7 | Lisgar | 13.2kV | 5203 | 5203 line tripped due to bus fault at VT43. 24/7 report high humidity in vault. Public works reported a smell of smoke in Centre block and West block and requested no power be restored to any of the Federal buildings until high voltage contractor inspected vaults. | Ottawa | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
15670 | 2010 | 1 | 19 | 0.43403 |  | 150 | 12 | 7 | Lisgar | 13.2kV | 5203 | A construction crew working for PWGSC bored into a concrete duct bank & caused a cable fault. The dig in was not reported for almost 2 hours while normal fault finding was performed to isolate the damaged cable & restore power. | Ottawa | Foreign Interference | Dig-in
14663 | 2009 | 7 | 4 | 0.25208 |  | 564 | 19 | 2 | Lisgar | 13.2kV | 5203 | VT43 & VT898 at Parliament Hill isolated for Public Works to perform routine maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
9428 | 2006 | 10 | 14 | 0.19792 |  | 770 | 26 | 2 | Lisgar | 13.2kV | 5203 | VT43 & VT898 isolated for scheduled maintenance and testing | Ottawa | Scheduled Outage | Preventive Maintenance
6223 | 2005 | 2 | 21 | 0.62222 |  | 6 | 0 | 2 | Lisgar | 13.2kV | 5208 | 5208-L3 inadvertantly placed in earth position during switching. Bank of Canada & Place de Ville were the 2 affected customers. | Ottawa | Human Element | Switching Errors
8013 | 2006 | 3 | 11 | 0.71736 |  | 70 | 4 | 3 | Lisgar | 13.2kV | 5208 | Circuit 5208 tripped off due to a faulted cable section between station and first vault out. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20261 | 2012 | 3 | 31 | 0.038889 |  | 84 | 4 | 3 | Lisgar | 13.2kV | 5208 | Vault VT 891 att 275 Sparks was isolated to allow contractor Eaton to measure duct bank and details of duct bank after duck bank failed past August. | Ottawa | Scheduled Outage | Construction
18885 | 2011 | 8 | 6 | 0.54583 |  | 99 | 5 | 3 | Lisgar | 13.2kV | 5208 | 13KV vault transformer bus at 275 Sparks St failed cause unknown at this time. Secondary bus cables to customer secondary room found heavy damaged and transformer flashed. | Ottawa | Adverse Environment | Flooding
18895 | 2011 | 8 | 6 | 0.54514 |  | 3156 | 53 | 1 | Lisgar | 13.2kV | 5208 | 13KV vault VT891 @ 275 Sparks St faulted due to water damage causing secondary bus to flash and causing fire in vault. | Ottawa | Adverse Environment | Fire
5137 | 2004 | 5 | 13 | 0.37639 |  | 226 | 4 | 112 | TL | 13.2kV | 5209 | VT548 @ 556 Laurier isolated for planned maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
20772 | 2012 | 6 | 14 | 0.39028 |  | 392 | 732 | 112 | Lisgar | 13.2kV | 5210 | Vault VT548 at 556 Laurier was isolated to allow contractor to perform vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
5545 | 2004 | 7 | 21 | 0.66875 |  | 37 | 556 | 241 | Lisgar | 13.2kV | 5210 | suspected cable fault caused TL22 breaker at station TL to open. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9904 | 2007 | 1 | 5 | 0.23125 |  | 81 | 2 | 2 | Lisgar | 13.2kV | 5211 | Customer breaker (CB2) @ Minto place is probable cause of 5211 circuit opening. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8004 | 2006 | 3 | 10 | 0.13403 |  | 94 | 2 | 2 | Lisgar | 13.2kV | 5211 | Outage on 5211 & TL6SB cable section. Possible cable fault between VT644 & VT307. Later found a flashed 833kva transformer in VT644S that caused the customers VCB6, CB1 & HOL TL20 breakers to trip. All load was restored at 9:38 except for VCB6 xfmr bus which may have been transferred on secondary equipment by the customer. | Ottawa | Human Element | Incorrect Protection Settings
10249 | 2007 | 4 | 13 | 0.027083 |  | 310 | 6 | 2 | Lisgar | 13.2kV | 5211 | While performing OTO switch CB2-L1 was opened and flash occurred. Causing TL20 breaker to open and loss of load at VT644 Minto Place and 1/2 of C.D. Howe building. East Vault remained O/s for entire time. # min outage to entire building to restore east vault CB8 load. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3895 | 2003 | 8 | 13 | 0.40417 |  | 51 | 2 | 2 | Lisgar | 13.2kV | 5211 | Barrier boards fell across the main bus on the CB2 at VT307 causing a flash and the circuit to trip. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16156 | 2010 | 5 | 27 | 0.94236 |  | 38 | 4 | 7 | Lisgar | 13.2kV | 5213 | A cable fault bet VT268(255 Albert) and VT736(111 Albert) caused the TL13 breaker to trip. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13227 | 2008 | 9 | 10 | 0.33333 |  | 5912 | 99 | 1 | Lisgar | 13.2kV | 5213 | 13KV vault located at 255 Albert St has blown up due to water damage. Power restored to 13 KV vault after transformers & bus was replaced on Sunday @ 10:32. | Ottawa | Adverse Environment | Flooding
13249 | 2008 | 9 | 16 | 0.77917 |  | 593 | 16 | 6 | Lisgar | 13.2kV | 5213 | TL13 breaker tripped interupting circuits 5213 & TL1TH. Fault on the 13 Kv bus work on the load side of the CB1 breaker. Vault isolated for customer repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12292 | 2008 | 4 | 16 | 0.44792 |  | 87 | 39 | 35 | Russell | 13.2kV | 5301 | 5301 line tripped off due to a failed porcelan insulator that allowed the 13kv conductor to drop down on to the crossarm of the 4kv underbuild. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14288 | 2009 | 5 | 2 | 0.24028 |  | 94 | 116 | 77 | Russell | 13.2kV | 5301 | Auto reclose on TB24 (TB2AL) and TB21 (5301) opened and locked out, crew found white phase cable blown on the line side of 5301-L15 at SW147. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16053 | 2010 | 5 | 6 | 0.67431 |  | 400 | 13 | 2 | Russell | 13.2kV | 5301 | VT273 at 2464 Sheffielkd was isolated to allow the customers contractors to perform vault maintenance, VT217 at 2575 Sheffield was also interupted due to TB2AL cable to VT217 being faulted | Ottawa | Scheduled Outage | Preventive Maintenance
8266 | 2006 | 5 | 10 | 0.041667 |  | 152 | 152 | 60 | Russell | 13.2kV | 5301 | 5301 circuit tripped @ 01:00. Approx 60 customer on Sheffield RD & Leeds affected in power outage. All power was restored at 03:32. Crew found a blown cable termination going into SW147 at 2870 Sheffield | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9004 | 2006 | 8 | 19 | 0.49514 |  | 110 | 14 | 10 | Russell | 13.2kV | 5301 | 5301 TB21 breaker tripped, after auto-reclose, cable sectionalized and tried as OK, load transferred | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13331 | 2008 | 10 | 6 | 0.53472 |  | 199 | 3 | 1 | Russell | 13.2kV | 5301 | VT893 at 2555 Sheffield isolated for emergency repairs, apparent tracking across metalclad insulators | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5851 | 2004 | 11 | 2 | 0.525 |  | 66 | 13 | 12 | Russell | 13.2kV | 5301 | O/H line patroled nothing found | Ottawa | Unknown/Other | No Apparent Cause
3729 | 2003 | 7 | 13 | 0.20694 |  | 5 | 296 | 3550 | Russell | 13.2kV | 5301,5308,TB1AL | During planned test trip of Hydro One A3RM the supply to TB Q bus was interrupted unintentionally. | Ottawa | Loss of Supply | HEPC Station Fault
8415 | 2006 | 6 | 2 | 0.75903 |  | 93 | 805 | 670 | Russell | 13.2kV | 5303 | 5303 (TB10) breaker at Russell tripped no cause found. Crew found a cable fault between Stn TB and Riser Pole | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18808 | 2011 | 7 | 24 | 0.60069 |  | 423 | 78 | 11 | Russell | 13.2kV | 5303 | TP2021 was reported to be faulted and was isolated to allow for replacement | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18819 | 2011 | 7 | 25 | 0.92986 |  | 271 | 50 | 11 | Russell | 13.2kV | 5303 | TP2021 at Elmvale acres shopping plaza was isolated to allow contractor to pull in new secondary cables. | Ottawa | Scheduled Outage | Repair
8853 | 2006 | 7 | 26 | 0.61736 |  | 109 | 1212 | 667 | Rusell | 13.2kV | 5303 | CABLE FAULT BETWEEN RUSSELL STATION AND OVERHEAD CAUSED TB10(5303) BREAKER TO OPEN. LOAD WAS RESTORED USING TB3LE CIRCUIT. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3869 | 2003 | 8 | 7 | 0.39444 |  | 427 | 1029 | 665 | TB | 13.2kV | 5303 | Contractor from Teraflex drove nail into live 5303 cable while performing construction. Circuit 5303 had H/O protection, TB3LE cable running parrallel was isolated. | Ottawa | Foreign Interference | Dig-in
9375 | 2006 | 10 | 4 | 0.49514 |  | 56 | 28 | 30 | Russell | 13.2kV | 5303 | A meter reader entered hydro vault VT71 and tripped off the main breaker. An underground crew restored power as an agent of system. | Ottawa | Human Element | Incorrect Use of Equipment
9473 | 2006 | 10 | 20 | 0.054861 |  | 70 | 778 | 667 | Russell | 13.2kV | 5303 | 5303 tripped due to a possible defective cable on TB3LE at dip to VT274. Both switches of the dual radial supply at VT274 were found closed ( TB3LE normal open ) which caused the normal feed (5303) to trip also. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12569 | 2008 | 6 | 7 | 0.48056 |  | 68 | 470 | 415 | Russell | 4 & 13kv | 5303, AE01,AE06 | Russell TB10 (5303 circuit) auto-reclosed & AE01/AE06 circuits opened & locked out. Police & Fire dept. called in reporting flash near Elmvale Shopping Mall. Crew dispatched to mall area; helium balloon wrapped up on overhead circuits AE01 & AE06. Balloon removed & circuits restored. | Ottawa | Foreign Interference | Foreign Object
6508 | 2005 | 5 | 4 | 0.61806 |  | 1 | 0 | 2 | Russell | 13.2kV | 5304 | Crew was switching on 5304 to isolate B11-E disconnects. Load was indavertently dropped at the General hospital campus. At item #4 they opened the S-60 @ SW188 and the generator started a the Childrens Hospital next door to the switching center. Thinking that they had caused the outage they quickly closed the switch back in and power was restored. It was found that a switch that was pinned on the system board as closed (S-101 @ SW188) and was in fact Open. This switch was closed and switching proceeded normally without interuption. | Ottawa | Human Element | Incorrect Records
6587 | 2005 | 5 | 22 | 0.49722 |  | 24 | 0 | 1 | Russell | 13.2kV | 5305 | 5305 opened fault, interupting power to General Hospital Campus. Flagged ground inst. Overhead patrolled and no problems found. On Call called in to fault find on underground sections | Ottawa | Unknown/Other | No Apparent Cause
7125 | 2005 | 8 | 11 | 0.38889 |  | 35 | 1 | 1 | TB | 13.2kV | 5305 | A cable splice let go in a manhole at Smyth & Linda lane, load was transferred to alternate supply. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11982 | 2008 | 1 | 26 | 0.55972 |  | 112 | 13 | 7 | Russell | 13.2kV | 5306 | 5306 line tripped from protection. No immediate cause found, futher searching required. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4925 | 2004 | 3 | 21 | 0.74236 |  | 3 | 0 | 10 | Russell | 13.2kV | 5306 | Line patrolled and nothing obvious found | Ottawa | Unknown/Other | No Apparent Cause
5011 | 2004 | 4 | 18 | 0.23403 |  | 311 | 10 | 2 | TB | 13.2kV | 5306 | A section of 5306 & 5307 lines on Russell rd supplying VT212 & VT170 was isolated to replace defective wart insulators. Vault maintenance was also performed at VT212 by the customer during the line outage. | Ottawa | Scheduled Outage | Repair
5426 | 2004 | 7 | 1 | 0.62639 |  | 318 | 2772 | 523 | TB | 13.2kV | 5306 | Cct opened during storm, lightning damaged neutral on Belfast rd | Ottawa | Adverse Weather | Lightning
16699 | 2010 | 8 | 9 | 0.44722 |  | 50 | 106 | 128 | Russell TS |  | 5306 | A cable section between S-247 @ VT50 & O/H switches S12207 faulted causing the pothead to VT50 to blow. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5919 | 2004 | 11 | 23 | 0.42083 |  | 5 | 1 | 8 | Russell | 13.2kV | 5306 | 5306 circuit was removed from potential via SCADA in order to remove guy wire from live phase. See ID# 5918 | Ottawa | Foreign Interference | Vehicle
5975 | 2004 | 12 | 4 | 0.4875 |  | 668 | 11 | 1 | TB | 13.2kV | 5306 | SW187 supplying VT481 & VT631, OC Transpo at 1500 St Laurent flashed internally. The entire PMH9 switch was replaced with a PMH10 swtich. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5918 | 2004 | 11 | 23 | 0.34097 |  | 10 | 2 | 11 | Russell | 13.2kV | 5306, 5307 | Pole was struck by vehicle at 1418 Michael, vehicle left the scene but not before bystander recorded plate number. Accident caused guy wire to break & fall into live circuit. Both circuits were re-energized manually from SCADA. | Ottawa | Foreign Interference | Vehicle
20054 | 2012 | 2 | 25 | 0.14167 |  | 353 | 206 | 35 | Russell | 13.2kV | 5307 | 5306 / 5307 / TB07 O/H line on Micheal North of Belfast were isolated on to allow crew to make repair to dammaged pole due to pole fire at 1500 Micheal St. | Ottawa | Scheduled Outage
5427 | 2004 | 7 | 1 | 0.62639 |  | 318 | 1230 | 232 | TB | 13.2kV | 5307 | Cct opened during storm. Pole P/H to VT230 on Belfast rd destroyed, was cut clear of O/H to allow cct to be picked up. | Ottawa | Adverse Weather | Lightning
19453 | 2011 | 10 | 23 | 0.53472 |  | 923 | 15 | 1 | RUSSELL | 13.2kV | 5307 | SW187 at 1500 St. Laurent flashed over. Switchgear replaced and power restored to OC Transpo. | Ottawa | Defective Equipment
7549 | 2005 | 11 | 1 | 0.23819 |  | 37 | 1 | 3 | Russell | 13.2kV | 5307 | 5307 circuit opened and locked out. Load was picked up on 5306. circuit to be patrolled. | Ottawa | Defective Equipment
13831 | 2008 | 12 | 31 | 0.8125 |  | 60 | 3 | 5 | Russell | 13.2kV | 5307 | Power interrupted to 5307 line caused by faulted cable termination in VT206 at 740 Belfast on the 5307 N.O. point. | Ottawa | Defective Equipment
8418 | 2006 | 6 | 4 | 0.10903 |  | 205 | 765 | 550 | Russell | 13.2kV | 5308 | Scada indicates 5308 tripped. UPT1 load transferred to TB2JP circuit at Kilbourn station. Circuit was sectionized at TA10 switch 5308 overhead put on pot. Under ground cables were sectionized on Don Ried. No fault found on underground circuit SC2302. Overhead to be patrolled this morning. Crew found a dead racoon at the riser pole switch S-12432 | Ottawa | Foreign Interference | Animal
6910 | 2005 | 7 | 12 | 0.92083 |  | 8 | 106 | 798 | TB | 13.2kV | 5308/TA1JP | TB19 tripped, no reports from police or fire, cct closed via scada & load restored. | Ottawa | Unknown/Other
6911 | 2005 | 7 | 12 | 0.93056 |  | 50 | 495 | 798 | TB | 13.2kV | 5308/TA1JP | TB19 tripped a second time, load transferred to alternate supply. Cct to be patrolled, cause unknown at this time. | Ottawa | Unknown/Other
7847 | 2006 | 1 | 23 | 0.98403 |  | 113 | 1669 | 886 | Russell | 13.2kV | 5309 | 5310 circuit opened & locked out. Circuit to be patrolled & Isolated in Morning. All load was transferred to 5309 circuit. Crews were sent to another outage on Sixth Line Rd in Kanata. | Ottawa | Unknown/Other | No Apparent Cause
20804 | 2012 | 6 | 19 | 0.675 |  | 31 | 85 | 165 | Russell | 13.2kV | 5309 | TB20 CB auto reclosed and locked out. Circuit patrolled, no cause found. | Ottawa | Unknown/Other | No Apparent Cause
14658 | 2009 | 7 | 3 | 0.46042 |  | 44 | 89 | 122 | Russell | 13.2kV | 5309 | TB20 breaker at Russell tripped the same time as TB03, AL10 and ALK1Y1 breakers and TB24 breaker auto reclosed. Recloser was O/S for forestry, no apparent cause was found during patrol | Ottawa | Unknown/Other | No Apparent Cause
4082 | 2003 | 9 | 18 | 0.36667 |  | 14 | 0 | 2 | TB | 13.2kV | 5309 | 2 customers were isolated to repair a burnt main secondary. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19774 | 2011 | 12 | 31 | 0.92986 |  | 734 | 727 | 125 | Russel TS | 13.2kV | 5309 | TB20 breaker carrying 5309 opened up due to a MVA accident at 2495 Lancaster Rd. | Ottawa | Foreign Interference | Vehicle
19777 | 2011 | 12 | 31 | 0.92986 |  | 1595 | 27 | 1 | Russell TS | 13.2kV | 5309 | A MVA accident caused severe damage to the cables feeding VT298 at 1495 Lancaster resulting in no power to VT298. | Ottawa | Foreign Interference | Vehicle
3143 | 2003 | 1 | 27 | 0.43056 |  | 150 | 765 | 882 | Russell TS | 13.2kV | 5310 | 5310 circuit opened red phase inst. Recloser was out of service. Circuit was patrolled and nothing was found.Circuit will be left abnormal overnight and restored to normal. | Ottawa | Unknown/Other | No Apparent Cause
19969 | 2012 | 2 | 6 | 0.40972 |  | 40 | 8 | 12 | Russell | 13.2kV | 5310 | 13KV transfromer KT50 at 2570 Southvale was isolated to allow crew to perform maintenance on primary and secondary connections | Ottawa | Scheduled Outage | Preventive Maintenance
15733 | 2010 | 2 | 20 | 0.75 |  | 205 | 48 | 14 | Albion |  | 5310 | Norm Leroux reports PC10A in effect on PT158 @ 2920 Sheffield from hydro Ottawa sources at SW152. 14 customers affected for minutes. Russell (5310) ID #15733 | Ottawa | Scheduled Outage | Construction
8268 | 2006 | 5 | 10 | 0.42708 |  | 74 | 22 | 18 | Russell | 13.2kV | 5310 | KT49 at 2570 Southvale was isolated to repair broken insulators. | Ottawa | Scheduled Outage | Repair
14334 | 2009 | 5 | 10 | 0.99792 |  | 48 | 76 | 239 | Russel | 13.2kV | 5310 | 5310 circuit auto/reclose/auto and AE01 auto trip at the same time. AE01 circuit bkr closed to restore same. 5310 sectionalised and completely restored with no apparent cause found. Daylight patrol to be done tomorrow. | Ottawa | Unknown/Other | Inadequate Trimming
14358 | 2009 | 5 | 14 | 0.46528 |  | 106 | 165 | 251 | Russel | 13.2kV | 5310 | Cable pothead at VT184 2480 Walkley failed causing circuit 5310 to open. Circuit sectionalized, pothead isolated and customers restored in stages. | Ottawa | Defective Equipment
20530 | 2012 | 5 | 16 | 0.10417 |  | 732 | 134 | 11 | Russell | 13.2kV | 5310 | Hydro Ottawa crews isolated PT90 at 3150 Hawthorne Rd to include the P.P.H switches. Hydro Ottawa crews replaced the transformer and P.P.H switches. | Ottawa | Scheduled Outage | Preventive Maintenance
16180 | 2010 | 6 | 2 | 0.74514 |  | 99 | 69 | 42 | Russell |  | 5310 | 5310 cct. Auto reclosed, lightning storm in the area. Fuse blew at SC102, refused and closed to restore power. | Ottawa | Adverse Weather | Lightning
18347 | 2011 | 6 | 8 | 0.70417 |  | 11 | 45 | 243 | Russell | 13.2kV | 5310 | Circuit opened due to storm activity, no cause reported yet, closed in via scada. | Ottawa | Adverse Weather
8540 | 2006 | 6 | 19 | 0.80417 |  | 346 | 692 | 120 | Russell | 13.2kV | 5310 | TB03 breaker auto-reclosed once for 5310 circuit. Suspect cause was from 3 fuses blown at SC101 riser which interrupted approx 120 customers in the Southvale Cres area. The crew also found a fuse blown at VT295B-F, fuses were left open until back up cable can be tested. All power restored. | Ottawa | Lightning
14659 | 2009 | 7 | 3 | 0.46042 |  | 45 | 190 | 254 | Russell | 13.2kV | 5310 | TB03 breaker at Russell tripped the same time as TB20, AL10 and ALK1Y1 breakers and TB24 breaker auto reclosed. Recloser was O/S for forestry, no apparent cause was found during patrol | Ottawa | Unknown/Other | No Apparent Cause
5608 | 2004 | 8 | 3 | 0.65972 |  | 38 | 6 | 9 | Russel | 4.16kV | 5310 | Transformer KT498 isolated to disconnect a service from a pedestal. | Ottawa | Scheduled Outage
16655 | 2010 | 8 | 4 | 0.65903 |  | 16 | 65 | 242 | Russell | 13.2kV | 5310 | TB03 breaker tripped during heavy rain & lightning. Breaker closed manually from SCADA. | Ottawa | Unknown/Other
9529 | 2006 | 10 | 28 | 0.41944 |  | 321 | 161 | 65 | Russell | 13.2kV | 5310 | 5310 auto reclosed, 2 phases of SC102 opened at riser from SC1, this was isolated then to restore power to the rest of SC102, SC2702 had to be opened to close in-line switches S-154 | Ottawa | Foreign Interference | Vehicle
9625 | 2006 | 11 | 9 | 0.40972 |  | 25 | 10 | 24 | Russell | 13.2kV | 5310 | Isolation of trf. To make service upgrades | Ottawa | Scheduled Outage | Preventive Maintenance
12206 | 2008 | 3 | 31 | 0.045139 |  | 75 | 1 | 1 | Lincoln Heights | 13.2kV | 5401 | On call crew called in to replace defective 13kv to 120 / 240V transformer in VT122, 61 McEwen. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3495 | 2003 | 5 | 28 | 0.62986 |  | 33 | 73 | 259 | Lincoln Heights | 13.2kV | 5401 | Red phase cable to VT122 @ 61 McEwan was defective and cut clear from the O/H line. Only VT513 & VT122 were being fed from cct. 5401at the time of outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12510 | 2008 | 5 | 31 | 0.71528 |  | 68 | 247 | 258 | Lincoln Heights | 13kv | 5401 | 5401 circuit opened. Ottawa Fire & Ottawa Police reports a pothead at 31 McEwan is smoking. 24/7 reports 5407 P/P/H is now isolated, and all load restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8779 | 2006 | 7 | 19 | 0.29583 |  | 66 | 8 | 7 | Lincoln Heights | 13.2kV | 5401 | 5401 & 5409 circuits tripped, patrol of O/H found remains of a balloon near 30 McEwen. | Ottawa | Foreign Interference | Foreign Object
3823 | 2003 | 7 | 30 | 0.94375 |  | 80 | 840 | 630 | Lincoln | 13.2kV | 5401 | A blown pot head on 5409 caused by a racoon occurred the same time as this interuption indicating it may be related. | Ottawa | Foreign Interference | Animal
15614 | 2010 | 1 | 5 | 0.24375 |  | 417 | 7 | 1 | Lincoln Heights | 13.2kV | 5402 | At 5:51am customer at VT329 at 1190 Richmond Road called in a no power call. Crews found blown R1-F fuse in VT329, probable cause is assumed to be a bad insulator. Contractor received permit and removed insulator and floated the bus. ESA has approved this action and has given customer a second 30 day warning to have water leak and insulator repaired before having Hydro instructed to turn off power. 1 Customer was affected and power was restored at 12:48pm. Lincoln Heights (5402). ID#15614. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19944 | 2012 | 2 | 1 | 0.22153 |  | 463 | 8 | 1 | Lincoln | 13.2kV | 5402 | The R1-F at VT329 at 1190 Richmond Rd tripped off. Upon investigation it was discovered that wter had leaked into the vault and tracked down an insulator and onto the 13kV bus. Carleton Electric made all necessary repairs & inspections. | Ottawa | Adverse Environment | Flooding
13924 | 2009 | 2 | 2 | 0.34792 |  | 159 | 3 | 1 | Lincoln Heights | 13.2kV | 5402 | At 8:21am Jeff Magee reports R1-F at VT329 has tripped open. He will establish self protection and ground and test transformers for possible fault on our side.Brent Duncan established PC10A#1792 on the R1-F at VT329 inspect insulator and water damage in vault. Brent Duncan surrendered to system PC10A#1792 to system and system terminated the same. ESA Approval came in and water damaged insulator has been isolated and all men and grounds are clear and vault can be restored back to normal. At 11:00am Jeff Magee and Brent Duncan reports all power restored to vault. Future shutdown will be required to have vault ceiling and insulator replaced. Lincoln Heights (5402). ID#13924. | Ottawa | Adverse Environment | Flooding
12185 | 2008 | 3 | 28 | 0.1875 |  | 570 | 33 | 8 | Lincolin Heights | 13.2kV | 5404 | The switch gear in VT178 @ 2651 Regina short out causing 5405/5404 cable section to trip. There was damage to the 5404-L5 switch grear. To restore power the bus bar had to be cut clear and further work will be require to make full repairs. The 5405 cable sect bet TD16 and VT317 was out under permit. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12184 | 2008 | 3 | 28 | 0.29514 |  | 250 | 31 | 8 | Lincoln Heights | 13.2kV | 5404/5405 | At 4:30am, customers called in the area of Richmond, Carling with reports of outage. No Scada to indicate any breaker operations at Lincoln Heights due to a damaged RTU. 24-7 Dispatched and during restoration of circuit they discovered at VT178, insulators and switchgear had flashed over. Crews isolated and restored remaining customers. 8 customers were affected and all power restored at … ID#12184. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3184 | 2003 | 2 | 12 | 0.95694 |  | 181 | 2983 | 990 | Lincoln | 13.2kV | 5405 | All customers restored by 1:59 except Central Park Lodge ( VT317 at 2370 Carling). The R1-F at VT317 had a blown fuse. After the fuse was replaced the switch would not close. | Ottawa | Defective Equipment
18570 | 2011 | 7 | 1 | 0.79236 |  | 102 | 19 | 16 | Lincoln Heights | 13.2kV | 5405 | A suspect cable fault bet VT147(2525 Carling and VT317(2370 Carling). | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19909 | 2012 | 1 | 27 | 0.54167 |  | 68 | 80 | 71 | Lincoln Heights | 13.2kV | 5407 | 5407 dip to VT157 at 2880 Carling cable and switch damaged due to fault. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19912 | 2012 | 1 | 27 | 0.85833 |  | 564 | 9 | 1 | Lincoln Hieghts |  | 5407 | VT121 @ 2841 Richmond Rd defective transformer in vault. All 3 transformers replaced and 3 fuses replaced in R1--F Reyrolle switch gear. After 600 volt disconnect switch was replaced by T & M Electrical. Matthew reports building out of power, and gen 24/7 was dispatched and found R1-F opened and blown fuse in switch gear. Also crew found defective transformer. Oncall crew replaced all 3 transformers & fuses in switch gear. All power was restored at 06:00. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4790 | 2004 | 2 | 15 | 0.69444 |  | 1 | 12 | 742 | Lincoln | 12/7.2kV | 5407 | TD06 bkr auto tripped, reclosing was blocked for Hold Off, bkr was closed via SCADA to restore ckt. | Ottawa | Unknown/Other
20033 | 2012 | 2 | 17 | 0.92431 |  | 138 | 663 | 432 | Lincoln |  | 5407 | Cable dip on SC157201 to PT12 at 2700 Queensview failed causing the white and blue phase fuses to open at SC157201-F | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8012 | 2006 | 3 | 11 | 0.58472 |  | 108 | 1973 | 1492 | Lincoln | 13.2kV | 5407 | Defective pothead to VT114 at 2900 Carling caused both circuits to trip. 5408 line was restored after the problem was identified. The remaining 6 vaults (742 customers) were restored one at a time with the last one restored at 15:50. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14057 | 2009 | 3 | 15 | 0.52153 |  | 64 | 836 | 784 | Lincoln | 13.2kV | 5407 | Defective riser cable feeding VT157 @ 2880 Carling caused TD08 breaker, 5407 circuit to open. Section between overhead riser and vault was isolated and power was restored. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
5324 | 2004 | 6 | 17 | 0.59028 |  | 100 | 1237 | 742 | TD | 13.2kV | 5407 | 5407 p/p/h to VT157 @ 2880 Carling failed. Staged restoration of power. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8534 | 2006 | 6 | 19 | 0.79306 |  | 23 | 2 | 6 | Lincoln | 13.2kV | 5407 | TD08 breaker closed manually from SCADA. TD08 breaker did not attempt a reclose according to SCADA, also breaker timed out several times while trying to close breaker. | Ottawa | Lightning
6935 | 2005 | 7 | 13 | 0.88472 |  | 8 | 1 | 6 | Lincoln | 13.2kV | 5407 | Circuit was re-energized manually from SCADA after an auto/reclose/auto. Suspect trip was from a problem found later, a downed skywire on Richmond Rd. | Ottawa | Adverse Weather | Lightning
19263 | 2011 | 9 | 26 | 0.51667 |  | 95 | 363 | 229 | Lincoln Heights | 13.2kV | 5407 | Vault VT505 @ 2871 Richmond was isolated by crews to allow contractor to change lightning arrestors in switchgear. | Ottawa | Scheduled Outage
4268 | 2003 | 10 | 15 | 0.69861 |  | 77 | 589 | 459 | Lincoln Heights | 13.2kV | 5407 | 5407 (TD08) tripped at 16:46 but audible alarm not received on SCADA. Closed by SCADA at 18:03 | Ottawa | Adverse Weather | Wind
6926 | 2005 | 7 | 14 | 0.06875 |  | 50 | 65 | 78 | Lincoln | 13.2kV | 5407,5408 | 5407, 5408 & TD12 circuits were interrupted in order to remove skywire that had fallen between the circuits. See ID #6927 for TD12. Both circuits tripped earlier. | Ottawa | Adverse Weather | Lightning
19910 | 2012 | 1 | 27 | 0.54167 |  | 67 | 875 | 784 | Lincoln Heights | 13.2kV | 5408 | Fault on 5407 at S21641 dip to VT157 2880 Carling caused flash that also caused 5408 to trip. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12046 | 2008 | 2 | 15 | 0.24514 |  | 44 | 8 | 11 | Lincoln | 13.2kV | 5408 | 5408 Line (TD17 Breaker) tripped. No reports of accidents, relay checked at station, no fault indication. Closed in breaker to restore load. | Ottawa | Unknown/Other
20086 | 2012 | 3 | 1 | 0.50069 |  | 197 | 1123 | 342 | Lincoln | 13.2kV | 5408 | SC1572 at Pincrest and Queensview opened due to cable fault between SC1572 and S-349. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20199 | 2012 | 3 | 22 | 0.50347 |  | 1 | 0 | 1 | Lincoln | 13.2kV | 5408 | VT505 at 2871 was interrupted due to incorrect pin board in system. | Ottawa | Human Element | Incorrect Records
20489 | 2012 | 5 | 9 | 0.83194 |  | 288 | 162 | 34 | Lincoln | 13.2kV | 5408 | leads burnt off one phase of 13kv switch S-301 at 2550 queensview dr.on 5408 circuit Falling into the 13kv underbuilt causing one phase to blow on SC157201 circuit. Switch S-301 was isolated with a brief interruption to Ottawa citizen and Baxter center, and circuit SC157201 was interrupted while switch S301 was replaced and leads repaired. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6804 | 2005 | 6 | 25 | 0.84028 |  | 518 | 2268 | 750 | Lincoln | 13.2kV | 5408 | Lightening strike broke pole at rear of 2656 Moncton conductors on 5408 & td05 came togeather. | Ottawa | Lightning | Direct Strike
6934 | 2005 | 7 | 13 | 0.88333 |  | 6 | 7 | 72 | Lincoln | 13.2kV | 5408 | Circuit was re-energized manually from SCADA . Suspect trip was from a problem found later, a downed skywire on Richmond Rd. | Ottawa | Adverse Weather
10905 | 2007 | 7 | 18 | 0.5625 |  | 163 | 3 | 1 | Linclon Heights | 13.2kV | 5408 | Isolated VT364 @ 2881 Richmond Rd to repair a hole in the cement ceiling caused by a dig in. | Ottawa | Foreign Interference | Foreign Object
6014 | 2004 | 12 | 11 | 0.29028 |  | 5 | 1 | 11 | Lincoln | 13.2kV | 5408 | Cause unknown, suspect heavy snowfall may have caused a flashover. Circuit was re-energized manually from SCADA. Circuit patrol on Mon, Dec 13 did not reveal any problems. | Ottawa | Adverse Weather | Snow
6100 | 2004 | 12 | 25 | 0.98264 |  | 57 | 59 | 62 | Lincoln Hts | 13.2kV | 5408 | 5408 line tripped. The crew found 3 arrestors blown at dip to Ottawa Citizen. The flash over had caused some burning at the crossarm and damage to 6 strands of conductor. The arrestors were cleared and power restored. The conductor cand be repaired later. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13634 | 2008 | 11 | 17 | 0.98958 |  | 115 | 2 | 1 | Lincoln Heights | 13.2kV | 5409 | VT255 at 1171 Ambleside isolated to change out defective transformer | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4403 | 2003 | 11 | 7 | 0.50486 |  | 28 | 0 | 1 | Lincoln Hts | 13.2kV | 5412 | Britannia Filtration B1-B2 breaker tripped during OTO to unload B2 bus at Lincoln Hts when TD04 breaker opened. They requested that they remain on generator until bus restored. They called again due to generator problems and requested we put them back on our supply. | Ottawa | Human Element | Switching Errors
4543 | 2003 | 12 | 1 | 0.91042 |  | 165 | 6 | 2 | Epworth | 8/4.8kV | 54F4 | TE801 had wrong phasing at installation outage was to correct phasing | Nepean | Human Element | Incorrect Installation
4986 | 2004 | 4 | 8 | 0.69444 |  | 112 | 4 | 2 | S. Gloucester | 8/4.8kV | 56 F4 | Transformer fuse failed due to age. Fuse barrel replaced and closed. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
13893 | 2009 | 1 | 25 | 0.28472 |  | 32 | 1 | 1 | South Glouchester | 27.6/16kV | 56F1 | A failed Hot line clamp was replaced at St. Mary's school, 5536 Bank St. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19933 | 2012 | 1 | 31 | 0.35417 |  | 120 | 6 | 3 | South Gloucester | 8/4.8kV | 56F1 | Isolated transformer GL005880 at 7244 Mitch Owens Rd for a pole replacement (Feeds 3 Hydro One load transfer customers) | Gloucester | Scheduled Outage | Construction
19985 | 2012 | 2 | 8 | 0.375 |  | 52 | 42 | 49 | South Gloucester | 8/4.8kV | 56F1 | At 09:00 switch G461W at 5393 Bank Steet was isolated to allow crew to remove tree from the line. 49 customers were affected for 52 minutes. South Gloucester 56F1 ID# 19985. | Gloucester | Tree Contacts | Tree Fallen
17879 | 2011 | 4 | 11 | 0.28125 |  | 260 | 30 | 7 | SOUTH GLOUCESTER | 8/4.8kV | 56F1 | Transformer X16380 at 5323 Bank Street replaced | Gloucester | Lightning | Direct Strike
20521 | 2012 | 5 | 15 | 0.39583 |  | 278 | 46 | 10 | South Gloucester | 8/4.8kV | 56F1 | Transformer GL00576 at 5385 Bank St. isolated for contractor | Gloucester | Scheduled Outage | Preventive Maintenance
20522 | 2012 | 5 | 15 | 0.39583 |  | 278 | 46 | 10 | South Gloucester | 8/4.8kV | 56F1 | Transformer X16512 at 5393 Bank St. isolated for contractor | Gloucester | Scheduled Outage | Preventive Maintenance
11560 | 2007 | 10 | 19 | 0.78611 |  | 221 | 44 | 12 | South Gloucester | 8/4.8kV | 56F2 | Fallen tree went into the primary and caused a pole fire at the corner of Mitch Owens and Stagecoach. South Gloucester F2 opened, causing the loss of 12 Hydro Ottawa transfer customers. | Gloucester | Tree Contacts | Tree Fallen
13861 | 2009 | 1 | 13 | 0.82222 |  | 68 | 1 | 1 | GLOUCESTER DS | 8/4.8kV | 56F4 | Refused switch feeding Transformer X16392 at 5496 BANK STREET | Gloucester | Adverse Weather | Wind
4705 | 2004 | 1 | 16 | 0.26389 |  | 88 | 7 | 5 | South Gloucester | 8/4.8kV | 56F4 | D. Provost reports 100 amp fuse replaced and closed. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
14020 | 2009 | 3 | 3 | 0.91667 |  | 325 | 5 | 1 | South Gloucester DS | 8/4.8kV | 56F4 | Cust called at 22:00 power has gone out we will have to replace trans X16392 tonight. At 3:25am on call crew reports all power restored and equipment restored to normal. 56F4 South Gloucester DS. ID#14020. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4908 | 2004 | 3 | 17 | 0.32361 |  | 94 | 34 | 22 | Queens | 4.16kV | 56F4 | Fused switch to K617 blew due to defective cable between K617 & K616. Normal open point is at K616 to K617. 22 customers on Blair St & Station Blvd affected by outage to K617. Cable was isolated and K617 restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10558 | 2007 | 6 | 8 | 0.90625 |  | 120 | 140 | 70 | South Gloucester | 8/4.8kV | 56F4 | G461W phase phase opened @ 5401 Bank St to remove tree in overhead line. (tree is on fire) | Gloucester | Tree Contacts | Tree Fallen
3623 | 2003 | 6 | 28 | 0.59375 |  | 90 | 6 | 4 | South Gloucester | 8/4.8kV | 56F4 | Make repairs to cable that was dug up by a customer. | Gloucester | Foreign Interference | Dig-in
3635 | 2003 | 6 | 29 | 0.70833 |  | 30 | 86 | 172 | South Gloucester Ds | 8/4.8kV | 56F4 | Hydro One 56T2L-X has a blown fuse due to a broken 115 Kv insulator. 56F4 was open to allow 56T2 to be switched out of service. Hydro One bus tie switch closed and T1 now suppling F4 load. NOTE: Limebank auto at 15:17 was caused by the South Gloucester DS insulator blowing. | Gloucester | Loss of Supply | HEPC Station Fault
9208 | 2006 | 9 | 12 | 0.3375 |  | 514 | 600 | 70 | South Gloucester | 8/4.8kV | 56F4 | Hydro One South Gloucester DS was interupted due to a failed feeder breaker causing the loss of the 56F4 feeder which supplies Hydro Ottawa customers. | Gloucester | Loss of Supply | HEPC Station Fault
7650 | 2005 | 11 | 23 | 0.95833 |  | 124 | 4 | 2 |  | 8/4.8kV | 56F4 | defective fuse switch replaced. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
6132 | 2005 | 1 | 13 | 0.63333 |  | 51 | 5 | 6 | Epwoth | 8/4.8kV | 58F1 | Transformer rear of 79 Tower Rd replaced paddles on secondary | Nepean | Defective Equipment | Imminent Equipment Failure Detected
15647 | 2010 | 1 | 13 | 0.55764 |  | 61 | 5 | 5 | Epworth | 8/4.8kV | 58F1 | Transformer #X36508 located at 74 Rossland Ave isolated for service upgrade | Nepean | Scheduled Outage | Construction
4704 | 2004 | 1 | 16 | 0.10764 |  | 40 | 4 | 6 | Epworth | 8/4.8kV | 58F1 | Transformer at 95 lotta was refused. Cause for outage not apparent. | Nepean | Unknown/Other | No Apparent Cause
15672 | 2010 | 1 | 20 | 0.39097 |  | 274 | 85 | 60 | Epworth | 8/4.8kV | 58F1 | Transformer TE591 @ 8 Deerfield was isolated to replace the insulators in the switch gear, the transformer @ 2,4 & 6 Deerfeild were also affect for a momentary outage because they were live front transformers. | Nepean | Scheduled Outage | Preventive Maintenance
15673 | 2010 | 1 | 20 | 0.74583 |  | 163 | 3 | 1 | Epworth | 8/4.8kV | 58F1 | Transformer TE591 @ 8 Deerfield was isolated for customer to make repairs to main secondary breaker. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
17502 | 2011 | 1 | 21 | 0.39583 |  | 25 | 4 | 10 | Epworth | 8/4.8kV | 58F1 | Transformer X36635 at 38 Granton Ave isolated to allow for new service | Nepean | Scheduled Outage
6156 | 2005 | 1 | 29 | 0.36806 |  | 7 | 1 | 6 | Epworth | 8/4.8kV | 58F1 | TX 2232 at 30 Chippewa hot line clamp replaced | Nepean | Defective Equipment | Equipment Deterioration Due to Age
19967 | 2012 | 2 | 6 | 0.019444 |  | 37 | 2 | 4 | Epworth | 8/4.8kV | 58F1 | 8kV transformer X22470 at 72 Withrow was isolated to allow crews to replace triplex service. | Nepean | Scheduled Outage | Repair
20126 | 2012 | 3 | 5 | 0.67361 |  | 28 | 3 | 7 | Epworth | 8/4.8kV | 58F1 | Transformer #X35834 located at 51 Tower Rd opened by crew to change live line clamp | Nepean | Defective Equipment | Imminent Equipment Failure Detected
3260 | 2003 | 3 | 16 | 0.5625 |  | 110 | 29 | 16 | Epworth | 8/4.8kV | 58F1 | Switch S553 at 84 Starwood found defective and replaced by 24/7. 16 customers restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14067 | 2009 | 3 | 16 | 0.45903 |  | 206 | 17 | 5 | Epworth | 8/4.8kV | 58F1 | A tree caused transformer X35980 on corner of withrow & indian to open. Tree was removed and transformer was closed in. then transformer started boiling, crew reopend transformer and it was replaced. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
14149 | 2009 | 4 | 6 | 0.76181 |  | 79 | 13 | 10 | Epworth | 8/4.8kV | 58F1 | Transformer 752 & X35976 located at 125 & 109 Rita Ave isolated due to neutral down below bare open buss | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17977 | 2011 | 4 | 20 | 0.38889 |  | 60 | 10 | 10 | Epworth | 8/4.8kV | 58F1 | Trans X36633 at 85 Lotta was isolated in order to replace the sec service | Nepean | Scheduled Outage | Repair
18089 | 2011 | 5 | 4 | 0.40556 |  | 627 | 21 | 2 | Epworth | 8/4.8kV | 58F1 | Transformer at 1720 Baseline rd was isolated to allow crew to replace elbows and fix the concrete pad. | Nepean | Scheduled Outage | Repair
18091 | 2011 | 5 | 4 | 0.40972 |  | 621 | 21 | 2 | Epworth | 8/4.8kV | 58F1 | Transformer TE422 @ 6 Deerfield was isolated to allow crew to replace live front transformer to dead front. 2 customer were affected. Epworth 58F1 | Nepean | Scheduled Outage | Construction
18131 | 2011 | 5 | 11 | 0.40208 |  | 476 | 48 | 6 | Epworth | 8/4.8kV | 58F1 | At 09:39 transformer TE587 at 11 Deerfield was isolated to allow crew to replace the transformer. 6 customers were affectex for 476 minutes. Epworth (58F1) ID#18131. | Nepean | Scheduled Outage
16101 | 2010 | 5 | 19 | 0.42431 |  | 116 | 492 | 757 | Epworth | 8/4.8kV | 58F1 | A cable dig in on a street lighting cable damaged the system neutral causing the 58F1 to auto, which then caused the EPWT2B to open. EPWT2B closed via SCADA soon after and the 58F2 & 58F3 loads restored. Repairs were made to the system neutral and the 58F1 was closed. Transformer X36012 on Cordova S of Lotta remained open while crews repaired the damaged street lighting cable. Repairs completed and all load restored. | Nepean | Foreign Interference | Dig-in
14390 | 2009 | 5 | 21 | 0.56944 |  | 40 | 3 | 5 | 58F1 | 8/4.8kV | 58F1 | Transformer #X36638 located at 10 Cote De Neiges isolated due to clearance | Nepean | Scheduled Outage | Construction
20555 | 2012 | 5 | 22 | 0.41667 |  | 360 | 30 | 5 | Epworth |  | 58F1 | Isolated transformer X37104 at 21 Epworth Ave to replace the pole | Nepean | Scheduled Outage | Preventive Maintenance
5242 | 2004 | 6 | 1 | 0.75 |  | 251 | 63 | 15 | Epworth | 8/4.8kV | 58F1 | Switch 72 at Rita and Withrow open due to lightning. | Nepean | Adverse Weather | Lightning
16187 | 2010 | 6 | 3 | 0.31875 |  | 152 | 18 | 7 | Epworth | 8/4.8kV | 58F1 | Secondary Bus of transformer X36631 caused tranformer fused to open interrupting power to customers on Starwood and St Claire. 24/7 repaired secondary bus and restored power. | Nepean | Defective Equipment
20697 | 2012 | 6 | 5 | 0.32639 |  | 135 | 20 | 9 | Epworth | 8/4.8kV | 58F1 | at 07:50 customer reported outage, transformer X36639 was openned up to allow crews to repair hot line clamp that was loose. Crews also repalced porcelien switches and lightning arrestor. 9 customers affected for 135 minutes. Epworth (58F1) ID #20697 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
18304 | 2011 | 6 | 6 | 0.32917 |  | 44 | 4 | 6 | Epworth | 8/4.8kV | 58F1 | Transformer #X35848 located at 106 Starwood opened up due to bird contact, crew installed bird guard after refusing the transformer. | Nepean | Foreign Interference | Bird
8452 | 2006 | 6 | 8 | 0.425 |  | 308 | 59 | 16 | Epworth | 8/4.8kV | 58F1 | TE588 and TE589 isolated to replace rusty transformers in Nepean on the 58F1 out of Epworth. | Nepean | Scheduled Outage | Repair
20740 | 2012 | 6 | 11 | 0.57292 |  | 45 | 12 | 16 | Epworth | 8/4.8kV | 58F1 | At 13:45, transformer TE0469 located at 81 Starwood was isolated to allow cerws to perform service upgrade. 16 customers affected for 45 minutes. Epworth (58F1) ID #20740 | Nepean | Scheduled Outage
18396 | 2011 | 6 | 13 | 0.93264 |  | 187 | 37 | 12 | Epworth | 8/4.8kV | 58F1 | Pole fire in the rear of 82 Tower required isolation of 58F1 white phase to X36645 and X36645 to allow crew to repair the burnt pole | Nepean | Adverse Environment | Fire
6768 | 2005 | 6 | 21 | 0.38958 |  | 69 | 7 | 6 | Epworth | 8/4.8kV | 58F1 | Transformer #2580 located rear of 93 Rossland isolated possibly due to animal interference (squirrel) | Nepean | Foreign Interference | Animal
18473 | 2011 | 6 | 24 | 0.23958 |  | 561 | 61 | 12 | Epworth |  | 58F1 | AT 09:08 crew took TE443 off potential @ 122 Chippewa to allow contractor to perform work on customer secondary. 1 customer was affected for 370 mins. Epworth 58F1 ID# 18473 | Nepean | Defective Equipment
3618 | 2003 | 6 | 28 | 0.6 |  | 54 | 14 | 15 | Epworth | 8/4.8kV | 58f1 | Fuse at switch S169 as well as the fuse at one of the transformers it feeds found ruptured on St Claire Ave. Fuses replaced and power restored, no apparent cause found. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3720 | 2003 | 7 | 11 | 0.36667 |  | 7 | 82 | 700 | Epworth | 8/4.8kV | 58F1 | A branch fell on the circuit circuit was opened to clear the branch | Nepean | Tree Contacts | Tree Limb Fallen
18743 | 2011 | 7 | 17 | 0.80694 |  | 475 | 3713 | 469 | Epworth DS | 8/4.8kV | 58F1 | 58F1 tripped during strom. Crews cleared trees off overhead in multiple locations to make restoration possible | Nepean | Tree Contacts
18718 | 2011 | 7 | 18 | 0.086111 |  | 966 | 290 | 18 | Epworth | 8/4.8kV | 58F1 | 58F1 overhead on Tower rd, was isolated at switch S14963, to remove tree, and repair downed phase. | Nepean | Tree Contacts
14816 | 2009 | 7 | 23 | 0.91875 |  | 72 | 5 | 4 | Epworth | 8/4.8kV | 58F1 | Replaced blown fuse feeding transformer X36010 at the rear of 69 Starwood Rd due to tree contact | Nepean | Tree Contacts | Inadequate Trimming
16561 | 2010 | 7 | 26 | 0.30347 |  | 64 | 9 | 8 | Epworth | 8/4.8kV | 58F1 | Replaced blown fuse feeding transformer X36022 at the rear of 37 Rita Ave (Squirrel contact) | Nepean | Foreign Interference | Animal
18839 | 2011 | 7 | 27 | 0.70903 |  | 4 | 0 | 5 | Epworth | 8/4.8kV | 58F1 | Transformer #X35835 located at 58 Cote De Neiges Rd opened by crew to clear branch from secondary | Nepean | Tree Contacts | Tree Limb Fallen
7034 | 2005 | 7 | 28 | 0.30347 |  | 49 | 10 | 12 | Epworth | 8/4.8kV | 58F1 | Raccoon caused transformer #2236 @ 50 Starwood to open. | Nepean | Foreign Interference | Animal
8866 | 2006 | 7 | 28 | 0.82083 |  | 83 | 12 | 9 | Epworth | 8/4.8kV | 58F1 | Fuse was found blown to transformer NP904 at 66 St Claire Ave due to animal contact (squirrel) | Nepean | Foreign Interference | Animal
18844 | 2011 | 7 | 28 | 0.37708 |  | 327 | 136 | 25 | Epworth |  | 58F1 | At 09:03 crews isolated two run offs on the 58F1 to transfer conductor and re locate run offs. Epworth 58F1 ID# 18844 | Nepean | Scheduled Outage
8988 | 2006 | 8 | 16 | 0.375 |  | 180 | 6 | 2 | Epworth | 8/4.8kV | 58F1 | Transformer #NP001170 located at 7 Starwood isolated to change a service pole | Nepean | Scheduled Outage | Construction
15000 | 2009 | 8 | 24 | 0.51042 |  | 50 | 17 | 20 | Epworth | 8/4.8kV | 58F1 | Customers on Tower and Rita Ave were inturupted to allow crews to repair a broken neutral. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3977 | 2003 | 8 | 30 | 0.45833 |  | 24 | 3 | 7 | Epworth | 8/4.8kV | 58F1 | Transformer #3028 was isolated in order to reconnect triplex to a customer following repairs by a contractor. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15035 | 2009 | 8 | 31 | 0.39931 |  | 52 | 9 | 10 | Epworth | 8/4.8kV | 58F1 | Transformer #X36507 located at 82 Rossland isolated for service upgrade | Nepean | Scheduled Outage | Construction
16874 | 2010 | 9 | 4 | 0.68819 |  | 281 | 28 | 6 | Epworth | 8/4.8kV | 58F1 | One span of open wire bus burned down due to tree contact and opened transformer X35980. | Nepean | Tree Contacts
5802 | 2004 | 9 | 14 | 0.56458 |  | 20 | 5 | 16 | Epworth MS | 8/4.8kV | 58F1 | Fence contractor damaged several underground services. | Ottawa | Human Element | Incorrect Construction
15143 | 2009 | 9 | 22 | 0.20903 |  | 52 | 3 | 4 | Epworth | 8/4.8kV | 58F1 | Transformer in the rear of 69 Starwood opened due to animal contact, crew re-fused. | Nepean | Foreign Interference | Animal
4244 | 2003 | 10 | 11 | 0.60764 |  | 55 | 6 | 6 | Epworth | 8/4.8kV | 58F1 | Transformer fuse replaced, no apparent case for blown fuse. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4281 | 2003 | 10 | 16 | 0.84375 |  | 120 | 12 | 6 | Epworth | 8/4.8kV | 58F1 | To change open wire service to triplex. Open wire had come disconnected. | Nepean | Adverse Weather | Wind
4315 | 2003 | 10 | 21 | 0.17569 |  | 37 | 5 | 8 | Epworth | 8/4.8kV | 58F1 | Transformer arrestor found blown, same cut away and transformer refused and customers restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5849 | 2004 | 10 | 21 | 0.46875 |  | 30 | 2 | 5 | Epworth Sub | 8/4.8kV | 58F1 | New service connection. | Nepean | Scheduled Outage | Construction
7517 | 2005 | 10 | 25 | 0.73264 |  | 80 | 7 | 5 | Epworth | 8/4.8kV | 58F1 | A burnt out transformer cut out at the rear of 82 Lotta. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19489 | 2011 | 10 | 28 | 0.46528 |  | 102 | 10 | 6 | Epworth | 8/4.8kV | 58F1 | Transformer on Lotta isolated to allow crew to change pole. | Nepean | Scheduled Outage
13526 | 2008 | 10 | 29 | 0.49167 |  | 92 | 2 | 1 | EPWORTH | 8/4.8kV | 58F1 | PC10A #4103 established by P.Barr at tap off to single phase line on Tower Rd to repair neutral conductor at 71 Tower | Nepean | Adverse Weather
15354 | 2009 | 11 | 5 | 0.86944 |  | 48 | 6 | 8 | Epworth | 8/4.8kV | 58F1 | Transformer #X36022 located at 26 Tower Rd isolated due to vine interference & squirrels nest on transformer | Nepean | Tree Contacts | Inadequate Trimming
11678 | 2007 | 11 | 7 | 0.39236 |  | 4 | 0 | 4 | Epworth | 8/4.8kV | 58F1 | Transformer #2687 located at 68 Withrow isolated due to smart meter change | Nepean | Scheduled Outage | Preventive Maintenance
15368 | 2009 | 11 | 9 | 0.55208 |  | 120 | 10 | 5 | EPWORTH | 8/4.8kV | 58F1 | Transformer X36507 at 88 Rossland Ave isolated to transfer secondary | Nepean | Scheduled Outage | Construction
17271 | 2010 | 11 | 14 | 0.825 |  | 42 | 5 | 7 | Epworth | 8/4.8kV | 58F1 | Squirrel caused transformer 1307 at rear of 81 Withrow to open. | Nepean | Foreign Interference | Animal
11724 | 2007 | 11 | 16 | 0.45833 |  | 65 | 3 | 3 | Epworth | 8/4.8kV | 58F1 | Transformer #X35981 located at 116 Rossland isolated to string a new line | Nepean | Scheduled Outage | Construction
19587 | 2011 | 11 | 16 | 0.37847 |  | 60 | 7 | 7 | Epworth | 8/4.8kV | 58F1 | Transformer #X35828 located at 97 Cote Des Neiges opened by crew to run a new service up the pole | Nepean | Scheduled Outage | Construction
17361 | 2010 | 12 | 1 | 0.26667 |  | 96 | 19 | 12 | Epworth | 8/4.8kV | 58F1 | Transformer #X36023 located at 57 Rita Ave opened due to defective fuse barrel | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15486 | 2009 | 12 | 8 | 0.35556 |  | 163 | 3 | 1 | Epworth | 8/4.8kV | 58F1 | At 08:32 transformer TE591 at 4 Deefield Drive was found with two fuses blown due to berrier board falling which caused the two fuses to open. 1 customer was affected for 163 minutes. ID# 15486. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
17393 | 2010 | 12 | 8 | 0.45486 |  | 25 | 2 | 6 | Epworth | 8/4.8kV | 58F1 | Isolated transformer X36627 at 18 Chippewa Ave for a service up-grade | Nepean | Scheduled Outage | Emergency Services Request
15497 | 2009 | 12 | 11 | 0.42361 |  | 103 | 9 | 5 | Epworth | 8/4.8kV | 58F1 | Transformer #X35832 located at 17 Tower Rd isolated for a PCB change | Nepean | Scheduled Outage | Construction
15511 | 2009 | 12 | 14 | 0.39375 |  | 44 | 2 | 3 | Epworth | 8/4.8kV | 58F1 | transformer X37105 isolated for PCB change at 34 Epworth Ave. | Nepean | Scheduled Outage | Preventive Maintenance
7760 | 2005 | 12 | 23 | 0.86806 |  | 20 | 1 | 4 | Epworth | 8/4.8kV | 58F1 | Repaired connectoions in open wire service. Transformer NP002234 open for repaires | Nepean | Defective Equipment | Equipment Deterioration Due to Age
19790 | 2012 | 1 | 5 | 0.58889 |  | 40 | 4 | 6 | Epworth DS | 8/4.8kV | 58F2 | A snow plow operating at Myers Chevy on Baseline Rd, hit a lstreet light pole causing it to fall into a bell wire that. When the pole hit the bell wire it caused two phases of the 58F2 to slap together. This caused S23683 B phase to open up. The pole was cleared, switch was refused and power restored. | Nepean | Foreign Interference | Foreign Object
14055 | 2009 | 3 | 15 | 0.22569 |  | 141 | 33 | 37 | Epworth | 8/4.8kV | 58F2 | crew replaced Broken switch S258 @ Pender and Withrow feeding customers on Rossland and Pender. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
10213 | 2007 | 4 | 5 | 0.43542 |  | 13 | 1 | 3 | Epworth | 8/4.8kV | 58F2 | Transformer #711 located at 1543 Merivale Rd isolated to transfer to another phase. | Nepean | Scheduled Outage | Construction
18053 | 2011 | 4 | 28 | 0.68194 |  | 6 | 10 | 98 | Epworth | 8/4.8kV | 58F2 | 58F2 auto-reclosed during wind/lightning storm. While switching, the breaker had to be opened to isolate a section. Power was restored once the section was isolated. | Nepean | Adverse Weather | Wind
16197 | 2010 | 6 | 4 | 0.80139 |  | 28 | 2 | 5 | EPWORTH DS | 8/4.8kV | 58F2 | Transformer X37102 at 2 Epworth Ave isolated to reconnect after service upgrade | Nepean | Scheduled Outage | Construction
16344 | 2010 | 6 | 28 | 0.34306 |  | 76 | 4 | 3 | Epworth | 8/4.8kV | 58F2 | Replaced broken fuse feeding transformer X35865 at 46 St. Helen's Pl | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16421 | 2010 | 7 | 7 | 0.73889 |  | 121 | 123 | 61 | Epworth | 8/4.8kV | 58F2 | Crew found a broken fuse in switch S351 at the rear of 29 Lyall St | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16446 | 2010 | 7 | 9 | 0.58472 |  | 373 | 1469 | 624 | Epworth | 8/4.8kV | 58F2 | Down conductor at switch SW28, phase down in high winds and lightning. Conductor repaired and all load restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12832 | 2008 | 7 | 13 | 0.35 |  | 51 | 4 | 5 | Epworth | 8/4.8kV | 58F2 | Replaced broken switch (Fuse Barrel) feeding transformer X36502 at 38 Rita Ave | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16493 | 2010 | 7 | 19 | 0.40278 |  | 28 | 4 | 8 | Epworth | 8/4.8kV | 58F2 | Transformer #X35990 located at 32 Gilbey Dr opened by crew to replace defective cut out and burning live line clamp | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16944 | 2010 | 9 | 14 | 0.42083 |  | 264 | 26 | 6 | Epworth | 8/4.8kV | 58F2 | TP6614 at 24 Northview isolated to allow contractor to pull in new secondary cable. | Nepean | Scheduled Outage | Construction
7382 | 2005 | 9 | 27 | 0.49514 |  | 64 | 9 | 8 | Epworth | 8/4.8kV | 58F2 | Transformer switch NP001064 at 11 Kerry Cres opened due to animal contact (Squirrel) refused the switch restored power | Nepean | Foreign Interference | Animal
5837 | 2004 | 10 | 9 | 0.76042 |  | 715 | 12 | 1 | Epworth | 8/4.8kV | 58F2 | Pyrotenic service repaired. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
20247 | 2012 | 3 | 27 | 0.84167 |  | 107 | 21 | 12 | Epworth | 8/4.8kV | 58F3 | Switch S1197 and S1202 feeding Vault VE58 @ 1460 Merivale were found blown due to a blown arrestor. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17818 | 2011 | 4 | 1 | 0.41667 |  | 225 | 8 | 2 | Epworth | 8/4.8kV | 58F3 | Transformer #X36258 located at 42 Kerry Cres opened by crew to replace pole and transformer | Nepean | Scheduled Outage | Construction
20671 | 2012 | 6 | 1 | 0.98889 |  | 288 | 48 | 10 | Epworth | 8/4.8kV | 58F3 | X37233 at 59 viewmount drive crew found a broken down ground that was tangled up in the secondary bus, crew removed it and re-fused. | Nepean | Foreign Interference | Foreign Object
18978 | 2011 | 8 | 19 | 0.13472 |  | 181 | 9 | 3 | Epworth | 8/4.8kV | 58F3 | VE58N at1460 Merivale Rd isolated to allow crew to replace ground fault relay on 600 volt. | Nepean | Scheduled Outage | Repair
3984 | 2003 | 9 | 2 | 0.48958 |  | 90 | 3 | 2 | Epworth | 8/4.8kV | 58F3 | Transformer #1 had to be isolated to allow for the replacement of a defective switch. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4014 | 2003 | 9 | 4 | 0.47153 |  | 41 | 4 | 6 | Epworth | 8/4.8kV | 58F3 | Transformer fuse blew for no apparent reason and was refussed successfully. | Ottawa | Unknown/Other | No Apparent Cause
19123 | 2011 | 9 | 8 | 0.68056 |  | 146 | 24 | 10 | Epworth | 8/4.8kV | 58F3 | Crew isolated a section of overhead fed from S1202 at 1458 Merivale to allow crew to replace a defective switch. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
17316 | 2010 | 11 | 21 | 0.30625 |  | 264 | 35 | 8 | Epworth | 8/4.8kV | 58F3 | TE2209 at 1370 Clyde was isolated to allow crews to transfer cable and switch to new pole. 8 customers affected for 264 minutes. Epworth (58F3). | Nepean | Scheduled Outage
15485 | 2009 | 12 | 8 | 0.44792 |  | 110 | 24 | 13 | Parkwoodhills | 8/4.8kV | 58F3 | The O/H line on Capilano Dr bet S540 & S1298 was isolated to replace conductor | Nepean | Scheduled Outage | Preventive Maintenance
11917 | 2008 | 1 | 9 | 0.70139 |  | 66 | 1 | 1 | Epworth | 8/4.8kV | 58F4 | The Transformer TE2314 the Scotia bank at 1649 Merivale had to be isolated because of water entering the main disconnect. | Nepean | Adverse Weather | Rain
13988 | 2009 | 2 | 17 | 0.49653 |  | 45 | 6 | 8 | Epworth | 8/4.8kV | 58F4 | S959 re-opened at 1558 Merivale Rd, to replace bayonette fuse. | Nepean | Defective Equipment
4813 | 2004 | 2 | 21 | 0.47083 |  | 217 | 479 | 158 | Epworth | 8/4.8kV | 58F4 | The W phase insulator near TE861 broke and fell into the R phase causing the 58F4 breaker to open. The W phase became tangled with the R phase not allowing for proper restoration. Switch 1418 was opened and the 58F4 breaker was closed picking up half the customers. Greg Bell repairs the insulator and closed in the 1418 switch picking up the remaining customers. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14081 | 2009 | 3 | 19 | 0.39583 |  | 125 | 12 | 6 | Epworth | 8/4.8kV | 58F4 | Transformer #X33242 located at 9 Glenridge isolated due to installing new line | Nepean | Scheduled Outage | Preventive Maintenance
10468 | 2007 | 5 | 28 | 0.44444 |  | 120 | 14 | 7 | Epworth | 8/4.8kV | 58F4 | Transformer #NP000352 located at 36 David isolated to re-locate service | Nepean | Scheduled Outage | Construction
10501 | 2007 | 6 | 1 | 0.027778 |  | 60 | 1 | 1 | Epworth | 8/4.8kV | 58F4 | transformer at Meadowlands at Merivale opened to repair a sparking hotline clamp | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10674 | 2007 | 6 | 20 | 0.13542 |  | 125 | 2 | 1 | Epworth | 8/4.8kV | 58F4 | Crew replaced leaking transformer TE861 @ 1675 Merivale | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
5618 | 2004 | 8 | 6 | 0.99375 |  | 73 | 4 | 2 |  | 8/4.8kV | 58F4 | Planned shutdown to 3 transformers at Emerald Plaza | Nepean | Scheduled Outage
7231 | 2005 | 8 | 29 | 0.43611 |  | 22 | 3 | 8 | Epworth | 8/4.8kV | 58F4 | Mark had NPOO2427 @ 19 Laird out to install new services | Nepean | Scheduled Outage | Construction
9084 | 2006 | 8 | 29 | 0.39514 |  | 85 | 71 | 50 | Epworth | 8/4.8kV | 58F4 | O/H run off fed from switch S831 isolated to transfer same to new pole. Customers on Davis & Harris Drs affected. | Nepean | Scheduled Outage | Construction
19233 | 2011 | 9 | 22 | 0.38194 |  | 30 | 4 | 9 | Epworth | 8/4.8kV | 58F4 | Isolated transformer X36514 at 18 David Dr for a service up-grade | Nepean | Scheduled Outage | Emergency Services Request
11409 | 2007 | 9 | 28 | 0.38542 |  | 42 | 12 | 17 | Epworth | 8/4.8kV | 58F4 | 58F4 o/h section on Laird and Meadowlands was restored to normal. Temp switch was removed, an outage to two transformers was required. | Nepean | Scheduled Outage | Construction
7399 | 2005 | 9 | 29 | 0.51042 |  | 60 | 10 | 10 | EPWORTH | 8/4.8kV | 58F4 | FOUND SWITCH BROKEN AT S831 WHICH WAS CAUSED BY DOWNED NETURAL | Gloucester | Adverse Weather | Wind
17067 | 2010 | 10 | 6 | 0.50694 |  | 29 | 4 | 8 | Epworth | 8/4.8kV | 58F4 | S830 located at 10 Canter opened by crew to replace defective hot line clamp and switch | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19456 | 2011 | 10 | 24 | 0.38958 |  | 24 | 89 | 223 | Epworth | 8/4.8kV | 58F4 | 58T1 all 3 high side fuses blown from Squirrel, bus transferred to T2 | Nepean | Foreign Interference | Animal
17174 | 2010 | 10 | 26 | 0.375 |  | 104 | 9 | 5 | EPWORTH | 8/4.8kV | 58F4 | Transformer X33360 at 1 Peter Street isolated to change openwire service to triplex | Nepean | Scheduled Outage | Repair
4539 | 2003 | 11 | 30 | 0.41667 |  | 353 | 23 | 4 | Epworth | 8/4.8kV | 58F4 | Planned outage, 1580 Merivale was isolated to replace leaking transformers TE801 and TE800 | Nepean | Scheduled Outage | Repair
9799 | 2006 | 12 | 5 | 0.61736 |  | 36 | 6 | 10 | Epworth | 8/4.8kV | 58F4 | John isolated TRF # 2223 @ 4 CoteDe Neige to change service wires | Nepean | Scheduled Outage | Preventive Maintenance
15521 | 2009 | 12 | 15 | 0.71875 |  | 3 | 18 | 368 | Epworth | 8/4.8kV | 58F4 | 58F4 P/P/H started to arc while restoring Epworth B buss to normal. 58F4 was carrying both 58F3 & 58F2 load. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17465 | 2011 | 1 | 3 | 0.34375 |  | 55 | 10 | 11 | Epworth | 8/4.8kV | 58F5 | Transformer #X36269 located at 23 Laird St opened up due to defective hot line clamp | Nepean | Defective Equipment | Imminent Equipment Failure Detected
3120 | 2003 | 1 | 15 | 0.21736 |  | 297 | 30 | 6 | Epworth | 8/4.8kV | 58F5 | Neutral wire burnt down causing a flash between the two 120v wires rupturing the transformer fuse to Tx#833 on Brooks Lane in Nepean. New wire was installed and full power was restored. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4780 | 2004 | 2 | 11 | 0.41944 |  | 145 | 14 | 6 | Epworth | 8/4.8kV | 58F5 | Transformer 1105 at 2 Oakridge BLVD defective, replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10017 | 2007 | 2 | 12 | 0.56597 |  | 16 | 1 | 4 | Epworth | 8/4.8kV | 58F5 | Graham repaired decfective live line clamp on TRF. NP1181 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
17622 | 2011 | 2 | 19 | 0.51389 |  | 50 | 4 | 5 | Epworth | 8/4.8kV | 58F5 | Isolated transformer X33374 at 4 Oakridge Blvd to replace damaged triplex service | Nepean | Scheduled Outage | Emergency Services Request
3227 | 2003 | 3 | 6 | 0.42708 |  | 15 | 34 | 135 | Epworth | 8/4.8kV | 58F5 | Outage required to remove tree from overhead primary . | Nepean | Tree Contacts | Tree Limb Fallen
6458 | 2005 | 4 | 25 | 0.39931 |  | 490 | 87 | 20 | Bilberry | 8/4.8kV | 58F5 | TE493 was dumped off while crews isolated TE494, due to live front transformer. 10 Customers were affected in power outage at this location. While restoring TE494 (TP2478) M. McLellan reports smoke coming elect. panel at 41 Sullivan. Transformer re-isolated to check services. M. McLellan reports all power restored. | Nepean | Scheduled Outage | Construction
20391 | 2012 | 4 | 25 | 0.38681 |  | 249 | 21 | 5 | Epworth | 8/4.8kV | 58F5 | TE489 at 56 Sullivan was isolated to allow crews to replace transformer and bring the base and grounding up to Hydro Ottawa standards | Nepean | Scheduled Outage | Repair
6465 | 2005 | 4 | 26 | 0.40208 |  | 289 | 29 | 6 | Epworth | 8/4.8kV | 58F5 | Transformer TE495 isolated for replacement. | Nepean | Scheduled Outage
6478 | 2005 | 4 | 29 | 0.40625 |  | 440 | 59 | 8 | Epworth | 8/4.8kV | 58F5 | Transformer Te503 live front replaced with TP2481 dead front.Sullivan Ave/Parker Ave. | Nepean | Scheduled Outage | Repair
6497 | 2005 | 5 | 3 | 0.39375 |  | 296 | 39 | 8 | Epworth | 8/4.8kV | 58F5 | Isolate transformer TE498 @ 65 Sullivan to replace it from live front to dead front. | Nepean | Scheduled Outage | Repair
6503 | 2005 | 5 | 4 | 0.45139 |  | 15 | 3 | 12 | Epworth | 8/4.8kV | 58F5 | Opened transformer NP002427 At 19 Laird St to diconnect a service to this address | Nepean | Scheduled Outage | Emergency Services Request
18105 | 2011 | 5 | 6 | 0.50694 |  | 60 | 10 | 10 | Epworth | 8/4.8kV | 58F5 | Isolated transformer X37233 at 59 Viewmount Dr to replace span of secondary open wire buss | Nepean | Scheduled Outage | Preventive Maintenance
6547 | 2005 | 5 | 12 | 0.37708 |  | 247 | 25 | 6 | Epworth | 8/4.8kV | 58F5 | Transformer TE504 @ 7 Donland was isolated for replacement and clean up oil spill. | Nepean | Scheduled Outage | Repair
3479 | 2003 | 5 | 21 | 0.59028 |  | 45 | 8 | 11 | Epworth | 8/4.8kV | 58F5 | Planned outage to transformer 2427 at 40 Meadowlands to repair customer service. | Nepean | Scheduled Outage
10483 | 2007 | 5 | 30 | 0.4375 |  | 265 | 13 | 3 | Epworth | 8/4.8kV | 58F5 | Isolated transformer NP3719 at 43 Meadowlands Dr to replace pole | Nepean | Scheduled Outage | Construction
18265 | 2011 | 5 | 31 | 0.81181 |  | 43 | 82 | 115 | Epworth | 8/4.8kV | 58F5 | 24/7 replaced 2 hot line clamps and 2 stirup the closed S304 to restore power. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
20633 | 2012 | 5 | 31 | 0.45139 |  | 55 | 7 | 8 | Epworth | 8/4.8kV | 58F5 | Isolated transformer X36199 at 49 Oakridge Blvd for a service upgrade | Nepean | Scheduled Outage | Emergency Services Request
18277 | 2011 | 6 | 1 | 0.98958 |  | 35 | 6 | 10 | Epworth | 8/4.8kV | 58F5 | Transformer # X36587 was isolated to allow crews to replace defective secondary service 115 Fieldrow | Nepean | Adverse Weather | Wind
20661 | 2012 | 6 | 1 | 0.29236 |  | 79 | 9 | 7 | Epworth | 8/4.8kV | 58F5 | Replaced blown fuse feeding transformer X36197 at 111 Palsen St (Squirrel contact) | Nepean | Foreign Interference | Animal
16195 | 2010 | 6 | 4 | 0.42639 |  | 108 | 9 | 5 | Epworth | 8/4.8kV | 58F5 | TE489 at 56 Sullivan was isolated to allow crews to install new secondary service. | Nepean | Scheduled Outage | Construction
3544 | 2003 | 6 | 9 | 0.86111 |  | 24 | 1 | 2 | Epworth | 8/4.8kV | 58F5 | Faulty linlets on TE809 at 11 Laird caused transformer to open.Two customers affected. Crew repaired problem. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
18386 | 2011 | 6 | 11 | 0.38958 |  | 99 | 101 | 61 | Epworth | 8/4.8kV | 58F5 | Vines on the O/H at 55 Glenridge cause the fuse to burn up at transformer X37231 which also cause switch S25900 to open. | Nepean | Tree Contacts | Inadequate Trimming
8494 | 2006 | 6 | 15 | 0.52778 |  | 70 | 5 | 4 | Epworth | 8/4.8kV | 58F5 | Transformer #NP004492 located at 26 Parkside isolated to install a new pole | Nepean | Scheduled Outage | Construction
3625 | 2003 | 6 | 23 | 0.4125 |  | 36 | 2 | 4 | Epworth MS | 8/4.8kV | 58F5 | Transformer isolated to make repairs to defective seconadry service. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20885 | 2012 | 6 | 26 | 0.71875 |  | 345 | 29 | 5 | Epworth | 8/4.8kV | 58F5 | Defective 50 kva transformer @ 41 Oakridge blvd was replaced on 58F5 circuit. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
14654 | 2009 | 7 | 2 | 0.59722 |  | 105 | 116 | 66 | Epworth | 8/4.8kV | 58F5 | Crew found S1522 at 51 Palsen open, line section patrolled, no problems found, S1522 replaced & closed, | Nepean | Unknown/Other | No Apparent Cause
8661 | 2006 | 7 | 4 | 0.40972 |  | 400 | 207 | 31 | Epworth | 4.16kV | 58F5 | Transformer #NP1176 located on Parkside & Viewmount isolated due to setting poles | Nepean | Scheduled Outage | Construction
10868 | 2007 | 7 | 14 | 0.27292 |  | 339 | 164 | 29 | Epworth | 8/4.8kV | 58F5 | 58F5 line section between S24782 and S601 isolated for pole replacment. | Nepean | Scheduled Outage
8733 | 2006 | 7 | 15 | 0.60764 |  | 96 | 48 | 30 | Epworth | 8/4.8kV | 58F5 | Switch 1605 B phase @ Sullivan/Whitehill was found open, O/H patrolled found nothing, closed back in and holding. | Nepean | Unknown/Other
6974 | 2005 | 7 | 16 | 0.78125 |  | 410 | 68 | 10 | Epworth | 8/4.8kV | 58F5 | Lightning struck a transformer at 107 FieldRow Cres in Nepean. | Nepean | Adverse Weather | Lightning
8769 | 2006 | 7 | 18 | 0.55556 |  | 207 | 138 | 40 | Epworth | 8/4.8kV | 58F5 | Switch S17331 open to end of line for pole replacement on Parkside Ave/ Viewmount Ave. | Nepean | Scheduled Outage | Construction
18729 | 2011 | 7 | 18 | 0.59583 |  | 204 | 391 | 115 | Epworth | 27.6/16kV | 58F5 | tree down on primary at 20 Palsen. Crew isolated and removed tree. | Nepean | Tree Contacts | Tree Limb Fallen
5581 | 2004 | 7 | 29 | 0.63472 |  | 170 | 306 | 200 | Epworth | 8/4.8kV | 58F5 | Home owner at 30 Palsen was trimming his own tree when tree contacted the 58F5 circuit. His ladder was on the branch that contacted the o/h and he fell approx 30 ft. to the ground. Fire dept. requested that we dump the circuit when they thought the man was wrapped up in the o/h still. The tree was isolated from switch S-304 and asplund removed the tree from o/h. the remainder of the circuit was then energized. | Nepean | Scheduled Outage | Emergency Services Request
16603 | 2010 | 8 | 2 | 0.33333 |  | 116 | 19 | 10 | Epworth | 8/4.8kV | 58F5 | Transformer #X37233 located at 59 Viewmount opened up due to squirrel contact | Nepean | Foreign Interference | Animal
11002 | 2007 | 8 | 6 | 0.40833 |  | 30 | 6 | 12 | Epworth | 8/4.8kV | 58F5 | Transformer #NP002427 located at 19 Laird St isolated, no apparent cause | Nepean | Unknown/Other
5628 | 2004 | 8 | 9 | 0.63889 |  | 20 | 2 | 6 | Epworth | 8/4.8kV | 58F5 | Replace secondary connection at transformer NP0357 @ 18 Westwood. | Nepean | Defective Equipment
8990 | 2006 | 8 | 16 | 0.67361 |  | 70 | 9 | 8 | Epworth | 8/4.8kV | 58F5 | Larry from K-Line opened transformer NP003783 @ 31 Westwood to move a primary lead to set a pole | Nepean | Scheduled Outage | Preventive Maintenance
7152 | 2005 | 8 | 17 | 0.375 |  | 252 | 34 | 8 | Epworth | 8/4.8kV | 58F5 | Isolate transformer TE496 @ 16 Parker Ave to change it from a live front to a dead front. | Nepean | Scheduled Outage | Repair
7159 | 2005 | 8 | 18 | 0.37083 |  | 281 | 28 | 6 | Epworth | 8/4.8kV | 58F5 | Transformer TE497 isolated for replacement for upgrade. | Nepean | Scheduled Outage | Preventive Maintenance
14972 | 2009 | 8 | 20 | 0.39306 |  | 532 | 53 | 6 | Epworth |  | 58F5 | TP6149 at 7 Parker isolated form Hydro Ottawa Sources to change transformer due to PCB levels. | Nepean | Scheduled Outage
9110 | 2006 | 9 | 1 | 0.38889 |  | 135 | 27 | 12 | Epworth | 8/4.8kV | 58F5 | Pole on corner of Oakridge and Viewmount replaced with pole 5 feet taller. | Nepean | Scheduled Outage | Construction
16867 | 2010 | 9 | 4 | 0.061806 |  | 106 | 12 | 7 | Epworth | 8/4.8kV | 58F5 | transformer X26540 at 12 Meadowlands was opened to replace open bus service with 1/0 triplex. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
16897 | 2010 | 9 | 8 | 0.045833 |  | 85 | 14 | 10 | Epworth | 8/4.8kV | 58F5 | Transformer X36762 arcing,at 35 Largo Cres, Nepean. Crew replaced Lightning arrestor switch, & stirrup. | Nepean | Defective Equipment
9196 | 2006 | 9 | 11 | 0.55833 |  | 141 | 59 | 25 | Epworth | 8/4.8kV | 58F5 | A section of overhead line on Westwood ave was isolated to transfer plant to new poles. | Nepean | Scheduled Outage | Construction
16956 | 2010 | 9 | 16 | 0.68889 |  | 370 | 296 | 48 | Epworth | 8/4.8kV | 58F5 | Large tree limb fell on the primary conductor at the side of 12 Ashwood Cres causing the conductor to break and fall to ground also secondary triplex pulled down | Nepean | Tree Contacts | Tree Limb Fallen
17000 | 2010 | 9 | 25 | 0.67292 |  | 31 | 4 | 8 | Epworth | 8/4.8kV | 58F5 | Transformer X36589 at 8 Wolmsley isolated to make repairs to secodary triples connections | Nepean | Defective Equipment | Equipment Deterioration Due to Age
17085 | 2010 | 10 | 8 | 0.40972 |  | 30 | 4 | 8 | Epworth | 8/4.8kV | 58F5 | Trans at 97 Norice ST was isolated for a service upgrade | Nepean | Scheduled Outage
15261 | 2009 | 10 | 14 | 0.42986 |  | 221 | 37 | 10 | Epworth | 8/4.8kV | 58F5 | TE488 at 68 Sullivan isolated to install new transformer. | Nepean | Scheduled Outage
19457 | 2011 | 10 | 24 | 0.38958 |  | 24 | 295 | 738 | Epworth | 8/4.8kV | 58F5 | 58T1 all 3 high side fuses blown from squirrel, load transferred to T2 | Nepean | Foreign Interference | Animal
19516 | 2011 | 11 | 2 | 0.43611 |  | 72 | 79 | 66 | Epworth | 8/4.8kV | 58F5 | S1522 White phase fuse found opened. No apperant cause found for outage. Circuit was patrolled by 24/7. | Nepean | Unknown/Other | No Apparent Cause
17455 | 2010 | 12 | 28 | 0.28125 |  | 87 | 26 | 18 | Epworth | 8/4.8kV | 58F5 | Faulted cable section between TE614 & S952 @ 120 Sullivan. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8061 | 2006 | 3 | 24 | 0.69583 |  | 524 | 369 | 250 | Epworth | 8/4.8kV | 58F6 | Transformer at 2 Rally flashed and burned causing a fault to go back to Epworth DS | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6490 | 2005 | 5 | 2 | 0.51528 |  | 108 | 185 | 103 | Manordale | 8/4.8kV | 58F6 | switch S850 blue phase fuse found blown after fire department call in pole fire. Switch replaced and on closeing switch 58F6 tripped and lockout. See next outage slip. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5169 | 2004 | 5 | 18 | 0.29167 |  | 100 | 77 | 46 | Epworth | 8/4.8kV | 58F6 | Switch S34 blown and tap burnt off between switch 304 and 305. Palson St/ Laird St | Nepean | Adverse Weather | Lightning
5206 | 2004 | 5 | 25 | 0.58819 |  | 108 | 146 | 260 | Epworth | 8/4.8kV | 58F6 | 58F6 circuit auto reclosed causing outage to 350 customers. Ottawa Fire reports pole fire at 96 Canter. L. Piper dispatched to S911 at 96 Canter Ave. 30 Customers out of power on the blue phase. L. Piper reports white phase switch arcing. Fuse blow causing 58F6 breaker to lock out ( circuit tagged H/O). L. Piper reports S911 rwb isolated from O/H. Breaker closed restoring load to 260 customers. RWB cable section to be isolated from transformers to replace switch & restore load to 100 customers. L. Piper reports red phase transformers restored at 15:30. White phase transformer restored at 15:47. Blue phase transformer restored at 15:55. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
5208 | 2004 | 5 | 25 | 0.70139 |  | 66 | 11 | 10 | Epworth | 8/4.8kV | 58F6 | Transformer TE389 on Canter Blvd isolated to complete repairs to defective switch 911. | Nepean | Defective Equipment
8764 | 2006 | 7 | 18 | 0.26875 |  | 154 | 10 | 4 | Epworth | 8/4.8kV | 58F6 | Transformer #NP001156 located at 26 Harris Place isolated due to lightning | Nepean | Adverse Weather | Lightning
18772 | 2011 | 7 | 18 | 0.19792 |  | 3 | 15 | 293 | Epworth | 8/4.8kV | 58F6 | The Epworth 58F6 breaker opened during the wind and lightning storm. Circuit to be patrolled. 293 customers were affected. Circuit was closed VIA Scada. Breaker held all load restore. | Nepean | Adverse Weather
8863 | 2006 | 7 | 28 | 0.47917 |  | 72 | 733 | 611 | Epworth | 8/4.8kV | 58F6 | AT 75 David a rotten cross arm was replaced T1172 defective and 3 customers transferred to T3871 until overhead transfomrer replaced. | Nepean | Scheduled Outage | Repair
8940 | 2006 | 8 | 10 | 0.40278 |  | 120 | 22 | 11 | Epworth | 8/4.8kV | 58F6 | Transformer #NP001172 located at 75 David isolated due to a transformer change | Nepean | Scheduled Outage | Construction
7191 | 2005 | 8 | 23 | 0.5 |  | 45 | 6 | 8 | Epworth | 8/4.8kV | 58F6 | Transformer #NP002758 located at 12 Harris Place isolated due to hooking up a new service | Nepean | Scheduled Outage | Construction
16985 | 2010 | 9 | 23 | 0.55208 |  | 35 | 5 | 9 | Epworth | 8/4.8kV | 58F6 | Isolated transformer X36512 at 28 Indian Rd to install new service | Ottawa | Scheduled Outage | Emergency Services Request
4276 | 2003 | 10 | 15 | 0.64583 |  | 715 | 12 | 1 | Epworth | 8/4.8kV | 58F6 | Triplex found down earlier in the day. No man power available till 03:25 Thursday. | Nepean | Adverse Weather | Wind
19458 | 2011 | 10 | 24 | 0.38958 |  | 24 | 150 | 374 | Epworth | 8/4.8kV | 58F6 | 58T1 all 3 fuses blown from squirrel contact. Load transferred to T2 | Nepean | Foreign Interference | Animal
4491 | 2003 | 11 | 20 | 0.38264 |  | 31 | 2 | 3 | Epworth | 8/4.8kV | 58F6 | Transformer 3942 at 144 David Dr isolated to verify customer connections. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9844 | 2006 | 12 | 15 | 0.375 |  | 150 | 20 | 8 | Epworth | 8/4.8kV | 58F6 | Tony Tallor had PC10A1440 on Transformer TE402 at 18 Parkglen to install new services | Ottawa | Scheduled Outage | Preventive Maintenance
18792 | 2011 | 7 | 21 | 0.625 |  | 22 | 443 | 1208 | Epworth | 8/4.8kV | 58T1 | A tree fell (probably Thrown) in to the secondary of the 58T1 transformer. Load was restored via 58T2. | Nepean | Tree Contacts | Tree Limb Fallen
17887 | 2011 | 4 | 11 | 0.22222 |  | 12 | 154 | 768 | Epworth | 8/4.8kV | 58T2 | Loss of Supply from H1 | Nepean | Loss of Supply | HEPC Circuit Fault
5736 | 2004 | 8 | 28 | 0.125 |  | 659 | 11 | 1 | Slater | 13.2kV | 604 | CB1 transfomer bus at VT108 (Place de Ville) isolated for Eaton Electric to repair secondary fault. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11469 | 2007 | 10 | 5 | 0.12639 |  | 665 | 22028 | 8600 | Bridlewood | 27.6/16kV | 605-S7M | 605-S7M ciruit switcher opened. Loss of supply to BRDT1 & BRDT2. BRDT2 load transferred to BRDT3. Unable to close 605-S7M to energize BRD B1 BUS @ station. BRDT4 was energized restoring OCR-TF2 load. UnAble to close OCR-TF1 breaker. S352-4 was closed restoring BRDF3 load. BRDF1 load was restored in section due to ind. Cable fault from station to S78. Crews found S210 tracking badly. When crews hi potted backup to Kanata Bussiness park cable meggered dead short. Crews closed S210 tripping 605-S7M again. All load on BRDT1 was restored @ 03:14. 23 customers main out at the Kanata Bussiness Park. S210 is now isolated. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4761 | 2004 | 2 | 4 | 0.059028 |  | 70 | 5718 | 6176 | Bridlewood | 27.6/16kV | 605W6MC | Snow plow hit a pole on Eagleson at the 417. Police report # 04-30177. Fault on BRDF4 caused total station outage at Bridlewood station. 12kv load restored via scada, BRD-B1 would not operate by scada delaying restoration. | Kanata | Foreign Interference | Vehicle
6112 | 2005 | 1 | 1 | 0.0013889 |  | 853 | 15 | 2 | Slater | 13.2kV | 606 | Fault in switchgear at VT508 (Provincial Courthouse at 161 Elgin), power was restored to Place Bell at 160 Elgin shortly after fault was determined. Hydro Ottawa Stations crew repaired damaged switchgear in VT508 and restored power to vault. Vault still requires metalclad work to complete the repairs. | Ottawa | Defective Equipment
20834 | 2012 | 6 | 23 | 0.081944 |  | 51 | 3 | 4 | Slater | 13.2kV | 606 | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
19037 | 2011 | 8 | 29 | 0.083333 |  | 129 | 2 | 1 | Slater | 13.2kV | 606 | VT126 @ 160 Elgin St Bell Canada building. CB2 opened due to high voltage relay protection. Relay protection was cleared by P. Bedard of McAuley electric and power was restored. ( Scada indicated high voltage at Slater at approx 01:20. Eves Belaer from the building also reports his relay protection ind. Voltage went up to 15.4KV causing relay protection to trip breaker at 01:25.) Hydro One reports a tapchanger was inadvertently left on manual following capacitor switching. | Ottawa | Human Element | Incorrect Use of Equipment
9899 | 2007 | 1 | 3 | 0.52083 |  | 62 | 10 | 10 | Fallowfield | 27.6/16kV | 606F1 | TE3409 on Roswell in Barrhaven was damaged by a vehicle accident & had to be replaced. 6 xfmrs were interrupted as it is a radial incomplete loop in a new subdivision, not many customers are connected yet. | Nepean | Foreign Interference | Vehicle
19828 | 2012 | 1 | 14 | 0.25 |  | 125 | 2 | 1 | Fallowfield | 27.6/16kV | 606F1 | S10110 feeding customer owned primary at 4282 Cedarview Rd. Blew due to tree contact, refused and closed | Nepean | Tree Contacts | Inadequate Trimming
3121 | 2003 | 1 | 16 | 0.44097 |  | 110 | 4 | 2 | Fallowfield DS | 27.6/16kV | 606F1 | Scheduled outage to TE3445 on Failop Way in the Longfields area for circuit reconfiguration. | Nepean | Scheduled Outage
7842 | 2006 | 1 | 21 | 0.95486 |  | 230 | 8 | 2 | Fallowfield | 27.6/16kV | 606F1 | Transformers TP3140 and TP2761 at Greenbank and Strandherd were isolated to install new transformer TP3503. | Nepean | Scheduled Outage
7843 | 2006 | 1 | 22 | 0.5 |  | 269 | 22 | 5 | Fallowfield | 27.6/16kV | 606F1 | A transformer TE3422 @ 11 Heritage Glen had to be isolated and replace because it was it by a snowplow the night before. | Nepean | Foreign Interference | Vehicle
4738 | 2004 | 1 | 27 | 0.38194 |  | 79 | 14 | 11 | Fallowfield | 27.6/16kV | 606F1 | Transformer TE3305 on Mountain Ash in Nepean isolated to make repairs to transformer secondary. | Nepean | Scheduled Outage | Repair
15689 | 2010 | 1 | 27 | 0.41458 |  | 63 | 9 | 9 | Fallowfield | 27.6/16kV | 606F1 | Isolation of TP2392 to allow Contractor to pull in new cable. | Nepean | Scheduled Outage
13906 | 2009 | 1 | 30 | 0.41181 |  | 85 | 34 | 24 | Fallowfield | 27.6/16kV | 606F1 | Transformer TP4944 @ Beatrice and Chapman mills was isolated for contractor to install secondary runs and connect to our buss. | Nepean | Scheduled Outage | Construction
3148 | 2003 | 1 | 31 | 0.375 |  | 84 | 18 | 13 | Fallowfield DS | 27.6/16kV | 606F1 | Te3312 at 32 Redpath isolated for crew to remove sand from transformer. | Nepean | Scheduled Outage | Preventive Maintenance
6171 | 2005 | 2 | 2 | 0.40972 |  | 61 | 10 | 10 | Fallowfield | 27.6/16kV | 606F1 | Transformer TE3693 on Upminister Way isolated to install new cables. | Nepean | Scheduled Outage
13921 | 2009 | 2 | 2 | 0.41667 |  | 20 | 0 | 1 | Fallowfield DS | 27.6/16kV | 606F1 | xfmr X34566 across from 4100 Gorman refused due to foreign interference | Nepean | Foreign Interference | Foreign Object
6173 | 2005 | 2 | 3 | 0.54583 |  | 9 | 504 | 3360 | Fallowfield | 27.6/16kV | 606F1 | Contractor (summerville construction) dug-in to cable at 3161 Strandherd Rd. Caused circuit to open. | Nepean | Foreign Interference | Dig-in
6180 | 2005 | 2 | 5 | 0.20417 |  | 130 | 108 | 50 | Fallowfield | 27.6/16kV | 606F1 | The R Phase cable burnt off at the connection of the O/H switch at S7113 on Cedarview North of Strandherd | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15723 | 2010 | 2 | 16 | 0.35417 |  | 15 | 2 | 10 | Fallowfield | 27.6/16kV | 606F1 | S27672 at 4344 TRAIL RD was reported sparking, crews found fuse barrel stil in place but bottom burning up. Suspect defective fuse. re-fused and holding | Nepean | Defective Equipment
3215 | 2003 | 2 | 27 | 0.48472 |  | 37 | 7 | 12 | Fallowfield | 27.6/16kV | 606F1 | Underground Crew encountered difficulty replacing an underground cable section and therefore required a short interruption to the adjacent transformer to inspect the cable duct. The duct was found to be collapsed, and will require excavation & repair. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
14070 | 2009 | 3 | 17 | 0.43125 |  | 79 | 4392 | 3336 | Fallowfield | 27.6/16kV | 606F1 | 606F1 Recloser tripped as well as the 606F2 recloser. The 606F2 recloser is burnt up. Fallowfield Station is being further investigated to check transformer and bus. All load restored. | Nepean | Loss of Supply | Animal
4932 | 2004 | 3 | 24 | 0.034722 |  | 51 | 8 | 9 | FALLOWFIELD | 27.6/16kV | 606F1 | Bad underground service at TE3051, 152 Beatrice. Crews installed tempory service. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3299 | 2003 | 3 | 25 | 0.63611 |  | 104 | 433 | 250 | Fallowfield | 27.6/16kV | 606F1 | A contractor trying to install a screw anchor into the ground near switch pole S7026 inadvertently screwed it into the blue phase cable causing the 606F1 circuit to auto reclose and the fuse to rupture. Crews were sent and power was diverted in order to bring power to all affected customers. | Nepean | Foreign Interference | Dig-in
14097 | 2009 | 3 | 25 | 0.39236 |  | 183 | 40 | 80 |  | 27.6/16kV | 606F1 | TP2970 was isolated to install secondary service. 10 customers effected in this outage. 9 other transformers were de-energized for 3 mins. For out of phase switching. | Nepean | Scheduled Outage | Preventive Maintenance
14104 | 2009 | 3 | 27 | 0.38125 |  | 148 | 123 | 50 | Fallowfield | 27.6/16kV | 606F1 | TP5166 & TP5165 on Madrid Ave. isolated to allow crews to excavate and install new duct work. | Ottawa | Scheduled Outage | Construction
12210 | 2008 | 3 | 31 | 0.38542 |  | 210 | 35 | 10 | FALLOWFIELD | 27.6/16kV | 606F1 | TRANSFORMER #4945 & 3154 ISOLATED TO ALLOW FOR STEAM CLEANING OF TRANSFORMERS | Nepean | Scheduled Outage | Preventive Maintenance
15901 | 2010 | 4 | 7 | 0.575 |  | 154 | 28 | 11 | Fallowfield | 4.16kV | 606F1 | Transformer NPTE3565 at 263 Portrush isolated to allow for replacement of leaking transformer | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4999 | 2004 | 4 | 14 | 0.44792 |  | 135 | 29 | 13 | Fallowfield | 27.6/16kV | 606F1 | Isolated TE3530 transformer for replacement. | Nepean | Scheduled Outage | Repair
15944 | 2010 | 4 | 15 | 0.51181 |  | 35 | 79 | 135 | Fallowfield | 27.6/16kV | 606F1 | Isolation of 606F1 cable section betweenTP3141 and TP2979 on Kenevale in Barhaven required a short outage to 8 transformers due to out of phase condition on the back-up supply from PP2103. | Nepean | Scheduled Outage | Construction
10259 | 2007 | 4 | 16 | 0.42014 |  | 494 | 26946 | 3540 | Fallowfield | 27.6/16kV | 606F1 | Cct tripped due to a broken insulator on O'Keefe crt. The insulator failed during a heavy snow storm & allowed the conductor to fall into the 8kv underbuild ( 145F3 ). Due to cold load pickup the feeder had to be sectionalized for restoration. | Nepean | Adverse Weather | Snow
17951 | 2011 | 4 | 17 | 0.67083 |  | 85 | 8 | 6 | Fallowfield | 27.6/16kV | 606F1 | Tree on the overhead on Cedarview south of Barnsdale, crew removed tree and re-fused line switch. | Nepean | Tree Contacts | Tree Limb Fallen
10280 | 2007 | 4 | 19 | 0.43333 |  | 226 | 264 | 70 | Fallowfield | 27.6/16kV | 606F1 | 7 Tx's on Upminster, Claridge & Upney in Barhaven were isolated to re-configure primary cables. | Nepean | Scheduled Outage | Construction
17991 | 2011 | 4 | 25 | 0.52986 |  | 33 | 0 | 1 | Fallowfield DS | 27.6/16kV | 606F1 | Refused transformer X34557 located at 3270 Cedarview Dr - squirrel contact | Nepean | Foreign Interference | Animal
15999 | 2010 | 4 | 26 | 0.52083 |  | 121 | 24 | 22 | Fallowfield | 27.6/16kV | 606F1 | TP2978 at 742 Cobble Hill isolated for replacement, short outage required to TP2979 at 766 Cobble Hill due to an out of phase conditon on the loop. | Nepean | Scheduled Outage | Construction
5064 | 2004 | 4 | 27 | 0.43958 |  | 112 | 224 | 120 | Fallowfield | 27.6/16kV | 606F1 | TE3650 had to be replaced but was in a radial feed therefore 12 transformers were affected | Nepean | Defective Equipment | Imminent Equipment Failure Detected
10361 | 2007 | 5 | 3 | 0.77847 |  | 64 | 1 | 1 | Fallowfield | 27.6/16kV | 606F1 | Fuse to transformer 1439 at 3231 Cedarview Rd was found blown due animel contact (Squirrel) Refused switch restored power | Nepean | Foreign Interference | Animal
14302 | 2009 | 5 | 4 | 0.71389 |  | 416 | 115 | 26 | Fallowfield | 27.6/16kV | 606F1 | TE3038 was isolated to allow crews to change a defective transformer. During switching TE3037 was accidently disconnected due to a switching error. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14319 | 2009 | 5 | 7 | 0.11319 |  | 347 | 231 | 210 | Fallowfield | 27.6/16kV | 606F1 | Transformer TE2742 at 79 Astoria Cresent was isolated due to a motor vehicle accident. Once the transformer was isolated S7026 blue phase was re-fused and closed. The remaining customers were picked up from normally open point at TE2735. 14 customers remained out of power while crew replace transformer. | Nepean | Foreign Interference | Vehicle
16057 | 2010 | 5 | 7 | 0.40278 |  | 615 | 113 | 11 | FALLOWFIELD | 27.6/16kV | 606F1 | Transformer NPTE3565 at 263 Portrush Ave isolated to replace leaking transformer | Nepean | Scheduled Outage | Repair
12423 | 2008 | 5 | 10 | 0.26181 |  | 253 | 4 | 1 | Fallowfield | 27.6/16kV | 606F1 | Transformer #NP001439 located at 3231 Cedarview Rd isolated due to squirrel interference | Nepean | Foreign Interference | Animal
5127 | 2004 | 5 | 11 | 0.39792 |  | 156 | 117 | 45 | Fallowfield | 27.6/16kV | 606F1 | 7 B phase txs isolated in the Claridge Dr & Upney Dr area of Longfields to energize 2 new tx's. | Nepean | Scheduled Outage | Construction
6608 | 2005 | 5 | 26 | 0.41319 |  | 135 | 68 | 30 |  | 27.6/16kV | 606F1 | Scheduled outages removing cable for rerouting of duct structure at Berrigan and Claridge. | Nepean | Scheduled Outage
3517 | 2003 | 6 | 4 | 0.37569 |  | 190 | 13 | 4 | Fallowfield | 27.6/16kV | 606F1 | Cable section isolated to repair cable damaged by contractor in new sub-division. Outage affected 7 new transformers, but only 4 customers in new housing development. | Nepean | Scheduled Outage | Repair
12550 | 2008 | 6 | 5 | 0.39931 |  | 137 | 171 | 75 | Fallowfield | 27.6/16kV | 606F1 | Transformers in the Strandheard/Cobblehill area on the Blue phase from switch S14611 were isolated to energize 8 new transformers. | Nepean | Scheduled Outage | Construction
14504 | 2009 | 6 | 10 | 0.40694 |  | 158 | 198 | 75 | Fallowfield | 27.6/16kV | 606F1 | Transformers TP5167, 5168 & 5169 on Haydon and Madrid isolated to install tx base extensions. | Nepean | Scheduled Outage | Construction
10656 | 2007 | 6 | 19 | 0.44097 |  | 82 | 16 | 50 | Fallowfield |  | 606F1 | Transformer TP3402 0n Sorento st was isolated to install a 6" collar on the transformer pad (raise the transformer). There was an outage to 10 other transformers during switching due to an out of phase condition. Customer count is estimate, area under construction. | Nepean | Scheduled Outage | Preventive Maintenance
6824 | 2005 | 6 | 27 | 0.73125 |  | 3 | 167 | 3336 | Fallowfield | 27.6/16kV | 606F1 | Hydro One reported that 606F1 opened fault. Circuit was manually closed restoring all customers. | Nepean | Unknown/Other | No Apparent Cause
18531 | 2011 | 6 | 27 | 0.27569 |  | 98 | 2 | 1 | Fallowfield | 27.6/16kV | 606F1 | Replaced blown fuse feeding transformer X39610 at 3717 Cedarview Rd | Nepean | Lightning | Lightning Strike on Adjacent Circuit Flashed Over
6818 | 2005 | 6 | 28 | 0.96389 |  | 537 | 6933 | 3362 | Fallowfield | 27.6/16kV | 606F1 | 606F1 circuit opened and locked out crews restored load in section. 606F1 circuit re-opened during oto to restore power between S7008 & S7093. All dips were opened and picked up one at a time. | Nepean | Adverse Weather | Extreme Ambient Temperature
3647 | 2003 | 6 | 30 | 0.3875 |  | 75 | 12 | 10 | Fallowfield | 27.6/16kV | 606F1 | Planned interruption to repair the secondary cable fed from TE3530W on San Mateo Drive in Nepean. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12809 | 2008 | 7 | 9 | 0.42431 |  | 106 | 37 | 21 | Fallowfield | 27.6/16kV | 606F1 | Isolation of transformer TP4945 which has a radial feed for transformer TP3154 was isolated to allow contractor to pull in secondary conductor. | Nepean | Scheduled Outage
14739 | 2009 | 7 | 13 | 0.57778 |  | 56 | 25 | 27 | Fallow field | 27.6/16kV | 606F1 | TP4970 at 265 Serena Way was replaced due to damage | Nepean | Scheduled Outage
12860 | 2008 | 7 | 16 | 0.67222 |  | 3 | 197 | 3936 | Fallowfield | 27.6/16kV | 606F1 | 606F1 auto reclosed auto. Circuit closed manually to restore load. Lightning storm in effect. | Nepean | Adverse Weather | Lightning
7000 | 2005 | 7 | 21 | 0.41667 |  | 82 | 10 | 7 | Fallowfield | 27.6/16kV | 606F1 | Isolate TP2783 at Crestway & Watersbridge to raise up transformer by 6". | Nepean | Scheduled Outage | Repair
16516 | 2010 | 7 | 21 | 0.84306 |  | 9 | 262 | 1750 | Fallowfield | 27.6/16kV | 606F1 | At 20:14 the Fallowfields 606F1 Breaker tripped open during the heavy rain and lightning. 544 customer were affected. | Nepean | Unknown/Other
16521 | 2010 | 7 | 21 | 0.84306 |  | 376 | 6 | 1 | Fallowfield | 27.6/16kV | 606F1 | Lightning strike to the Trail Road area caused S29666 White and Blue phases to blow. Lacking 2 phases Trail Road was unable to generate. White and Blue phases re-fused and closed restoring Trail Road Facility. | Nepean | Lightning | Direct Strike
12990 | 2008 | 8 | 2 | 0.025694 |  | 89 | 25 | 17 | Fallowfield | 27.6/16kV | 606F1 | TP2882 @ 3141 Strandherd was isolated to replace defective insert on transformer. | Nepean | Scheduled Outage | Repair
7064 | 2005 | 8 | 4 | 0.74792 |  | 243 | 99 | 50 | Fallowfield | 27.6/16kV | 606F1 | A blown transformer TP2169 @ 61 Whetstone & Oldfield. Wayne Reid suggest the transformer was hit of it pedestal and place back on. It is a new sub division and there is no one living at this place and will be looked at in the morning. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7130 | 2005 | 8 | 4 | 0.74792 |  | 53 | 2947 | 3336 | Fallowfield | 27.6/16kV | 606F1 | SEE outage # 7064 for the rest of the details. Bulldozer hit transformer | Nepean | Foreign Interference | Vehicle
13001 | 2008 | 8 | 5 | 0.38889 |  | 149 | 50 | 20 | Fallowfield | 27.6/16kV | 606F1 | Isolate transformer TP4945 on Chapman Mills to allow contractor to install secondary. | Nepean | Scheduled Outage | Construction
16744 | 2010 | 8 | 16 | 0.29722 |  | 168 | 3 | 1 | Fallowfield | 27.6/16kV | 606F1 | 606F1 auro reclosed with no apparent load lost, customer on 4334 Cedarview transformer switch blew due to lightning. | Nepean | Adverse Weather | No Apparent Cause
16751 | 2010 | 8 | 16 | 0.37083 |  | 62 | 1 | 1 | Fallowfield | 27.6/16kV | 606F1 | Lightning caused transformer switch S23526 feeding transformer 39608 to open @ 4334 Cedarview. | Nepean | Adverse Weather | Lightning
16760 | 2010 | 8 | 17 | 0.51111 |  | 76 | 14 | 11 | Fallowfeild | 27.6/16kV | 606F1 | A crow caused the fuse to blow at switch S28057 a private run off on Barnsdale Rd which also caused switch S27961 to open. | Nepean | Foreign Interference | Bird
13166 | 2008 | 8 | 29 | 0.44236 |  | 291 | 388 | 80 | FALLOWFIELD | 27.6/16kV | 606F1 | Isolation of transformers on Stonehedge and Copperfield area, to allow rew to remove and reroute primary cables. | Nepean | Scheduled Outage
13204 | 2008 | 9 | 8 | 0.37708 |  | 79 | 21 | 16 | Fallowfield | 27.6/16kV | 606F1 | TP3154 and TP4945 on Taradale and Meadgate were isolated to allow contractor to connect secondary lugs. | Nepean | Scheduled Outage
15070 | 2009 | 9 | 8 | 0.52083 |  | 90 | 4 | 3 | Fallowfield | 27.6/16kV | 606F1 | Transformer #TP3503 located at 3775 Strandherd isolated to do repairs to a cable. | Nepean | Scheduled Outage | Repair
17066 | 2010 | 10 | 6 | 0.38889 |  | 94 | 13 | 8 | Fallowfield | 27.6/16kV | 606F1 | TE3562 at 126 Redcliff was isolated to allow crews to perform Hydro-Vac of the transformer base. 8 customers affected. | Nepean | Scheduled Outage | Preventive Maintenance
17080 | 2010 | 10 | 7 | 0.34444 |  | 536 | 161 | 18 | Fallowfield | 27.6/16kV | 606F1 | 606 F1 o/h section between T75 and S24218 to allow line crews to string new conductor thru existing pole line. | Nepean | Scheduled Outage
7454 | 2005 | 10 | 14 | 0.42708 |  | 290 | 290 | 60 | Fallowfield | 27.6/16kV | 606F1 | Install new cable into three phase transformer at TP3178, affecting 6 transformers on Madelon, and Croxley in Longfields. | Nepean | Scheduled Outage
11558 | 2007 | 10 | 19 | 0.45486 |  | 130 | 26 | 12 | Fallowfield | 27.6/16kV | 606F1 | TP2098 at 275 Keltie, Barrhaven isolated for contractor to install secondary cables. | Nepean | Scheduled Outage | Construction
11585 | 2007 | 10 | 24 | 0.38889 |  | 259 | 43 | 10 | Fallowfield | 27.6/16kV | 606F1 | Transformers TP2081 and TP2080 in longfields area were isolated for contractor to pull new secondary cables. | Nepean | Scheduled Outage | Construction
13587 | 2008 | 11 | 10 | 0.41944 |  | 4 | 81 | 1219 | Fallowfield | 27.6/16kV | 606F1 | While setting a hold off for Hydro Ottawa the Hydro 1 operator inadvertantly opened the breaker, crews were verified as clear and the breaker was closed back in | Nepean | Loss of Supply | operator error
4462 | 2003 | 11 | 15 | 0.80069 |  | 119 | 121 | 61 | Fallowfield | 27.6/16kV | 606F1 | Transformers 2631 & 2632 on Madden Crt in Longfields area of Barrhaven isolated to reloacate tranformer 2632 which had been backed into and moved by a vehicle. | Nepean | Foreign Interference | Vehicle
7652 | 2005 | 11 | 25 | 0.54861 |  | 116 | 31 | 16 | Fallowfield | 27.6/16kV | 606F1 | Isolation of blue phase to allow red and white phases to be connected Clearbrook Dr and Nittany Barrhaven | Nepean | Scheduled Outage | Construction
4537 | 2003 | 11 | 29 | 0.72917 |  | 16 | 24 | 90 | Fallowfield | 27.6/16kV | 606F1 | Isolated transformer TE3448 at 46 Golden Green Lane to relocate it. Transformer was hit by vehicle and moved off its pad. 12 other transformers will also be off due to off phase feed. | Nepean | Foreign Interference | Vehicle
17355 | 2010 | 11 | 29 | 0.38125 |  | 322 | 188 | 35 | Fallowfield | 27.6/16kV | 606F1 | Isolation between TP2978 and TP3141 to allow crews to reconfigure the U/G and cut in 3 new transformers, 35 customers affected in the Cobble Hill and Kinevale area. | Nepean | Scheduled Outage | Construction
19660 | 2011 | 12 | 2 | 0.38194 |  | 278 | 154 | 168 | Fallowfield | 27.6/16kV | 606F1 | TP5715 on Tipperary and TP5717 on Hornchurch were isolated to remove cables between transformers and prepare for future expansion. Equipment failure during switching caused short outage to part of the transformer blue phase loop. Overhead SW7102 Blue re-fused and customers restored. | Nepean | Scheduled Outage
17373 | 2010 | 12 | 3 | 0.40069 |  | 323 | 54 | 10 | Fallowfield | 27.6/16kV | 606F1 | At 09:37 transformer TP5716 was isolated to allow contractor to install new secondary. Customers were affected for minutes. Fallowfield (606F1) ID# 17373. | Nepean | Scheduled Outage
11811 | 2007 | 12 | 5 | 0.40556 |  | 74 | 10 | 8 | Fallowfield | 27.6/16kV | 606F1 | Isolated TP3154 @ 814 Taradale to connect two new transformers. | Nepean | Scheduled Outage | Construction
13751 | 2008 | 12 | 15 | 0.35069 |  | 25 | 7 | 16 | Fallowfield | 27.6/16kV | 606F1 | Crew isolated cable section and transformer TP4184 & TP4183 to allow contractor to blow rope through the ducts. 16 customers affected. | Nepean | Scheduled Outage | Preventive Maintenance
15520 | 2009 | 12 | 15 | 0.54167 |  | 18 | 33 | 110 |  | 27.6/16kV | 606F1 | 16 tranformers in the area of River Run & Nicollis creek were off loaded to allow crews to return an out-phase condition to normal | Nepean | Scheduled Outage | Construction
15541 | 2009 | 12 | 22 | 0.42014 |  | 251 | 100 | 24 | Fallowfield | 27.6/16kV | 606F1 | TP2079 on Keltie Pvt, Nepean was isolated to allow contractor to pull secondary into transformer. | Nepean | Scheduled Outage
13880 | 2009 | 1 | 20 | 0.40278 |  | 126 | 105 | 50 | FALLOWFIELD & JOCKVALE | 27.6/16kV | 606F1 & 145F4 | Crew isolated 5 transformers to raise the transformers to grade | Nepean | Scheduled Outage | Preventive Maintenance
3306 | 2003 | 3 | 29 | 0.32292 |  | 85 | 4791 | 5000 | Fallowfield DS | 27.6/16kV | 606F1 & F2 | Defective insulator on the 606F2 feeder caused surge arrestor to blow and connection to surge arrestor to swing into 606F1 feeder. Load restored in stages as surge arrestor was cleared from F1 and as insulator was replaced on F2. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11899 | 2008 | 1 | 4 | 0.41944 |  | 68 | 170 | 150 | Fallowfield | 27.6/16kV | 606F2 | 17 transformers fed from S26565 in the Greenbank and Dundonald area on the Fallowfield F2 isolated to re-route cable to accommodate for future loop. | Nepean | Scheduled Outage | Construction
7781 | 2006 | 1 | 8 | 0.038194 |  | 207 | 9157 | 3000 | Fallowfield | 27.6/16kV | 606F2 | A blown viper switch RX2004 at the corner of Greenbank & Starndherd. Conflicting reports from customers land access to switching devices (snow) led to a longer restoration time | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3117 | 2003 | 1 | 14 | 0.425 |  | 206 | 275 | 80 | Fallowfield DS | 27.6/16kV | 606F2 | Planned outage to reconfigure feeder cable section and energize new transformer. | Nepean | Scheduled Outage
11933 | 2008 | 1 | 14 | 0.41667 |  | 77 | 175 | 150 | Fallowfield | 27.6/16kV | 606F2 | To allow crews to rearrange cables in the area of Shadehill, Kilbirnie, & Brookwood. | Nepean | Scheduled Outage | Construction
17499 | 2011 | 1 | 20 | 0.425 |  | 103 | 17 | 10 | Fallowfield | 27.6/16kV | 606F2 | TP5822 at 2520 Stonecove was isolated to raise the transformer | Nepean | Scheduled Outage | Preventive Maintenance
15676 | 2010 | 1 | 22 | 0.42361 |  | 130 | 41 | 60 | Fallowfield | 27.6/16kV | 606F2 | 5 transformer off loaded to allow crews to isolate TP5811 due to an out of phase conduction. TP5811 remained isolated to allow crews to replace damaged transformer on Foxhound. | Nepean | Scheduled Outage | Repair
3149 | 2003 | 1 | 31 | 0.54375 |  | 30 | 5 | 10 | Fallowfield DS | 27.6/16kV | 606F2 | Planned outage to TE3134 on Pondhollow Way and Golflinks Dr to 10 customers to rearrange primary cables. | Nepean | Scheduled Outage | Preventive Maintenance
13952 | 2009 | 2 | 11 | 0.29236 |  | 124 | 11174 | 5407 | Fallowfield | 27.6/16kV | 606F2 | Hydro one reported that the 606F2 had opened and not re-closed due to a hold off. Crews completed Patrol, nothing found, Hydro One restored reclosing, and 606F2 auto reclosed auto. | Ottawa | Unknown/Other | No Apparent Cause
13953 | 2009 | 2 | 11 | 0.31944 |  | 85 | 212 | 150 | Fallowfield | 27.6/16kV | 606F2 | Hydro One reported 606F2 had opened and not re-closed due to a hold off. Crews completed Patrol, nothing found, Hydro One restored reclosing, and 606F2 auto reclosed auto. | Ottawa | Unknown/Other | No Apparent Cause
3188 | 2003 | 2 | 14 | 0.44792 |  | 105 | 7 | 4 | Fallowfield DS | 27.6/16kV | 606F2 | TE3369 planned interruption to maintain supply cables. |  | Scheduled Outage | Preventive Maintenance
15725 | 2010 | 2 | 17 | 0.40278 |  | 70 | 12 | 10 | Fallowfield | 27.6/16kV | 606F2 | PC10a #3557 established at 9:40am, TP5798 was Isolated to allow crews to replace damagaed transformer. 10 customers affected for 70 minutes. Fallowfield (606F2) ID #15725 | Nepean | Scheduled Outage | Repair
17602 | 2011 | 2 | 17 | 0.40625 |  | 235 | 68 | 100 | Fallowfield | 27.6/16kV | 606F2 | TP6940 in the Jockvale / Cambrian rd area was isolated to allow contractor to pull in new secondary conductor. Short outages were required to additional customers during switching due to an out of phase condition. | Nepean | Scheduled Outage | Construction
14001 | 2009 | 2 | 24 | 0.41944 |  | 508 | 677 | 80 | Fallowfield | 27.6/16kV | 606F2 | Isolated red phase cable from S12382 on Greenbank S of Camrian to allow crew to reconfigure duct structure and energize new transfomer. | Nepean | Scheduled Outage | Construction
20052 | 2012 | 2 | 24 | 0.89514 |  | 120 | 10 | 5 | Fallowfield | 27.6/16kV | 606F2 | S12018W at 551 Pinawa opened due to Snowplow hitting pole at 3990 Price of Whales. | Nepean | Foreign Interference | Vehicle
14009 | 2009 | 2 | 26 | 0.38194 |  | 330 | 165 | 30 | Fallowfield | 27.6/16kV | 606F2 | At 9:10am crews established PC10#004201 on the red phase at switch S12382 to allow secondary connections and cleaning of duct structure. All power restored at 14:40 to all customers. 606F2 (Fallowfield). ID#14009. | Nepean | Scheduled Outage | Construction
20101 | 2012 | 3 | 3 | 0.53958 |  | 51 | 8 | 10 | Fallowfield | 27.6/16kV | 606F2 | TP3814 at 125 Tapestry was replaced by on-call crew after being hit by a car. | Nepean | Foreign Interference | Vehicle
6252 | 2005 | 3 | 8 | 0.42708 |  | 63 | 3 | 3 | Fallowfield | 27.6/16kV | 606F2 | isolated Transformer NP1430 for mtce at 3650 Jockvale rd | Ottawa | Scheduled Outage | Preventive Maintenance
17681 | 2011 | 3 | 8 | 0.45972 |  | 12 | 4 | 20 | Fallowfield | 27.6/16kV | 606F2 | At 11:02 4 transformers were affected to allow crews to isolate cable section between TP6609 and TP7364 due to out phase conditions. 20 customers were affected for 12 minutes. Fallowfield (606F2) ID #17681. | Nepean | Scheduled Outage | Preventive Maintenance
17684 | 2011 | 3 | 8 | 0.57292 |  | 5 | 2 | 20 | Fallowfield | 27.6/16kV | 606F2 | At 13:45 4 transformers were affected to allow crews to restore new cable section between TP6609 and TP7364 and two new transformers due to out phase conditions. 20 customers were affected for 5 minutes. Fallowfield (606F2) ID #17684. | Nepean | Scheduled Outage
12133 | 2008 | 3 | 12 | 0.54097 |  | 58 | 14 | 15 | Fallowfeild | 27.6/16kV | 606F2 | Transformers TP4222,TP4221 and TP4220 was isolated by the crew to allow them to place transformer TP4222 back on it's pad after it was hit by snow removal crew. | Nepean | Foreign Interference | Vehicle
14072 | 2009 | 3 | 17 | 0.43125 |  | 72 | 4522 | 3768 | Fallowfield | 27.6/16kV | 606F2 | 606F2 Recloser burnt up as well as the 606F1 tripping at the same time. Hydro One to further investigate Bus and Transformer. All load restored. | Nepean | Loss of Supply | Animal
15836 | 2010 | 3 | 24 | 0.39583 |  | 311 | 311 | 60 | Fallowfield | 27.6/16kV | 606f2 | 13 tansformers were isolated to all crews to install new transformer on River Run. | Gloucester | Scheduled Outage | Construction
15838 | 2010 | 3 | 24 | 0.42431 |  | 229 | 65 | 17 | Fallowfield | 27.6/16kV | 606F2 | at 10:11am, Transformer TP5474 at 598 Chapma mills was Isolated to connect secondary cables. 17 customers affected for 229 minutes. Fallow Field (606F2) ID #15838 | Nepean | Scheduled Outage
15855 | 2010 | 3 | 26 | 0.37708 |  | 342 | 633 | 111 | Fallowfield | 27.6/16kV | 606F2 | 11 transformers on a radial feed from TP5789 in the River Run area of Barrhaven near Greenbank & Cambrian were isolated to connect in 4 new transformers. | Nepean | Scheduled Outage | Construction
12188 | 2008 | 3 | 28 | 0.48611 |  | 98 | 7 | 4 | Fallowfield | 27.6/16kV | 606F2 | TP 4877 in Chapman Mills TP4877 isolated and replaced after being damaged by contractor. | Kanata | Foreign Interference | Vehicle
10207 | 2007 | 3 | 30 | 0.38542 |  | 180 | 60 | 20 | Fallowfield | 27.6/16kV | 606F2 | Isolated transformer TP 3665 at Longfields and Berrigan for service isolation for customer | Nepean | Scheduled Outage | Preventive Maintenance
17862 | 2011 | 4 | 9 | 0.038889 |  | 136 | 39 | 17 | Fallowfield | 27.6/16kV | 606F2 | TE3715 at 3560 Strandherd was isolated for crew to transfer feed | Nepean | Scheduled Outage
20318 | 2012 | 4 | 13 | 0.40972 |  | 89 | 13 | 9 | Fallowfield | 27.6/16kV | 606F2 | Transformer TP5789 at 3426 River Run Ave. isolated to remove old transformer and install a new one | Nepean | Scheduled Outage
17968 | 2011 | 4 | 19 | 0.59097 |  | 13 | 3 | 13 | Fallowfield | 27.6/16kV | 606F2 | While switching to isolate a line section for planned work, NPTE3160 at 7 Burnt Oak had to be isolated to repair a broken insert. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15974 | 2010 | 4 | 22 | 0.43056 |  | 190 | 317 | 100 | Fallowfield | 27.6/16kV | 606F2 | Multiple transformers in the Cambrian & Greenbank area were isolated for crews to re-configure underground plant | Nepean | Scheduled Outage
12332 | 2008 | 4 | 23 | 0.66875 |  | 87 | 44 | 30 | Fallowfield | 27.6/16kV | 606F2 | TP4893 damaged by vehicle contact and leaking oil on Marjan in Barrhaven. Total of 4 transformer on radial feed off to make repairs. | Nepean | Foreign Interference | Vehicle
20396 | 2012 | 4 | 26 | 0.54931 |  | 223 | 109 | 153 | Fallowfield | 27.6/16kV | 606F2 | Transformer TP6939 at 3387 Cambrian was isolated to allow contractor to install new secondary cables. Due to out of phase condition, an outage occured to the rest of the transformer loop while switching was performed. | Nepean | Scheduled Outage | Construction
14305 | 2009 | 5 | 5 | 0.39306 |  | 202 | 24 | 7 | Fallowfield | 8/4.8kV | 606F2 | Transformer TP5857 at 756 Kilbirnie isolated to allow for replacement of secondary cables. | Nepean | Scheduled Outage | Construction
12439 | 2008 | 5 | 15 | 0.44931 |  | 143 | 50 | 21 | Fallowfield | 27.6/16kV | 606F2 | TP3664 at 130 Berrigan isolated for contractor to install secondary cables. 21 customers, all at 130 Berrigan, were affected. | Nepean | Scheduled Outage | Construction
12440 | 2008 | 5 | 15 | 0.39583 |  | 78 | 13 | 10 | LIMEBANK | 27.6/16kV | 606F2 | Transformer at Woodroffe & Strandherd isolated to allow for maintenance on traffic lights | OV | Scheduled Outage | Construction
5178 | 2004 | 5 | 19 | 0.10347 |  | 183 | 3 | 1 | Fallowfield | 27.6/16kV | 606F2 | One phase out and transformer had to be replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14379 | 2009 | 5 | 19 | 0.37639 |  | 360 | 72 | 14 | Fallowfield | 27.6/16kV | 606F2 | TE2742 at 79 Astoria was isolated for repairs and clean up from damaged caused by a vehicle accident last week | Nepean | Scheduled Outage | Repair
14398 | 2009 | 5 | 22 | 0.38542 |  | 335 | 78 | 14 | Fallowfeild | 27.6/16kV | 606F2 | TE2742 @ 62 Astoria was isolated to allow the crew to remove soil remediation. | Nepean | Scheduled Outage | Repair
16128 | 2010 | 5 | 24 | 0.76736 |  | 82 | 6127 | 6300 | Fallowfield | 27.6/16kV | 606F2 | 606F2 tripped, A/R/A showing 400A load. No fault indicators found flagged. Load restored in stages & some load transferred to Longfields. | Nepean | Unknown/Other | No Apparent Cause
20575 | 2012 | 5 | 25 | 0.5 |  | 105 | 4 | 2 | Fallowfield | 27.6/16kV | 606F2 | Transformer #X4704 located at 3697 Jockvale Rd opened by crew to re-arrange plant on pole | Nepean | Scheduled Outage | Construction
12487 | 2008 | 5 | 28 | 0.39583 |  | 91 | 46 | 30 | Fallowfeild | 27.6/16kV | 606F2 | isolation of transformer TP3257 @ 340 Blackleaf Dr for replacement. | Nepean | Scheduled Outage
12535 | 2008 | 6 | 3 | 0.38542 |  | 310 | 155 | 30 | Fallowfield | 27.6/16kV | 606F2 | 4 radially fed transformers, TP4893, TP4892, TP4891 & TP4889 at Woodroffe W. of Cresthaven were isolated to clean up contaminated soil at TP4893. | Nepean | Scheduled Outage | Repair
12565 | 2008 | 6 | 6 | 0.78194 |  | 297 | 9220 | 5178 | Fallowfield | 27.6/16kV | 606F2 | Possible overloading of 606F2 may have caused cct to trip, crews reported a flagged FCI on Greenbank S. of Strandherd, sectionalizing allowed the cct to be picked up but it tripped again when attempting to pick up remaining load. H - 1 reported the breaker had a "duty cycle" flag after the 3rd close attempt during sectionalizing & could not be tried again for 30 to 40 min. The line was further sectioned by transferring load to Longfields station allowing H - 1 to close 606F2.The area where the suspected fault was was picked up 1 loop at a a time. 606F2 was abnormal due to work being done on the Limebank river crossing supply & this source was not available at this time. Line supervisor was contacted & he reported approx 6 hrs of work to make river crossing supply available. | Nepean | Human Element | Switching Errors
16235 | 2010 | 6 | 9 | 0.63542 |  | 217 | 40 | 11 | FALLOWFIELD DS | 27.6/16kV | 606F2 | TP4891 at 239 Marjan Cres had to be isolated to allow for working clearance to allow Enbridge crews to repair a broken gas main. | Nepean | Adverse Environment
10594 | 2007 | 6 | 11 | 0.36111 |  | 50 | 6 | 7 | Fallowfield | 27.6/16kV | 606F2 | Transformer #3567 isolated by Greg Forbes of JW Leslie to allow for installation of underground cable for new construction | Nepean | Scheduled Outage
16265 | 2010 | 6 | 15 | 0.40278 |  | 61 | 24 | 24 | Fallowfield | 27.6/16kV | 606F2 | TP6707 @ 2802 Grand Canal was isolated to allow crews to repair ground grid. | Nepean | Scheduled Outage | Repair
16268 | 2010 | 6 | 15 | 0.575 |  | 38 | 3842 | 6518 | Fallowfield | 27.6/16kV | 606F2 | SCADA indicated 606F2 tripped, while under holdoff. Also switching section of line to normal. Checked FCI's red phase flagged at FC2061-3. Line patrolled. Nothing found, closed CS23854 to restore remaining load. | Nepean | Unknown/Other
6777 | 2005 | 6 | 22 | 0.17014 |  | 28 | 3 | 7 | Fallowfield | 27.6/16kV | 606F2 | Sparking hot line clamp at 77 Ben Mar Rd. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3599 | 2003 | 6 | 23 | 0.69861 |  | 36 | 2400 | 4000 | Fallowfield | 27.6/16kV | 606F2 | Breaker had red and blue targets..Breaker inspected by Hydro One, only a blown close fuse found. Breaker returned to service. NOTE 1: 4000 customers is only an estimate. NOTE 2: Nepean SCADA time 1HR and 3 minutes behind Ottawa SCADA. Times entered are adjusted. | Nepean | Loss of Supply | HEPC Station Fault
16322 | 2010 | 6 | 23 | 0.40556 |  | 8 | 100 | 900 | Fallwofield | 27.6/16kV | 606F2 | 606F2 tripped while crew was switching on o/h line, flash from load break tool. | Nepean | Human Element
18509 | 2011 | 6 | 24 | 0.79514 |  | 93 | 9056 | 6993 | Fallowfield |  | 606F2 | At 18:07 606F2 breaker tripped due to lightening. One attempt was made to close the breaker back in but it tripped again due to cold load pick-up. 606F2 circuit was then picked up in sections. Fallowfield (606F2) ID#18509 | Nepean | Lightning
16348 | 2010 | 6 | 28 | 0.71528 |  | 73 | 8265 | 6793 | Fallowfield | 27.6/16kV | 606F2 | 606F2 tripped off due to circuit overload. Loading reached it maximum on this circuit due to apparent overload. | Nepean | Human Element | Incorrect Use of Equipment
18561 | 2011 | 6 | 28 | 0.84583 |  | 92 | 6486 | 6993 | Fallowfield | 27.6/16kV | 606F2 | 606F2 circuit opened during lightening storm. Circuit was sectionized and picked up. On call crews were dispatched to S7084 to open switch. | Nepean | Adverse Weather | Lightning
6848 | 2005 | 7 | 2 | 0 |  | 581 | 387 | 40 | Fallowfield | 27.6/16kV | 606F2 | B. Armstrong reports repairs at TE2311 is now complete. S7114 white phase is now closed and enrgized. | Nepean | Adverse Weather | Lightning
18578 | 2011 | 7 | 4 | 0.28125 |  | 50 | 4160 | 6000 | Fallowfield |  | 606F2 | At 6:45 am 606F2 tripped. Crews sectionalized and picked up the circuit. There is no cause found at this time. Fallowfield 606F2 ID# 18578 | Nepean | Unknown/Other
5444 | 2004 | 7 | 5 | 0.46319 |  | 43 | 9 | 12 | Fallowfield | 27.6/16kV | 606F2 | Transformer on Gleason isolated to fix defective transformer damaged in Storm on Thursday July 1 /04 | Nepean | Defective Equipment | Imminent Equipment Failure Detected
5447 | 2004 | 7 | 5 | 0.46319 |  | 43 | 9 | 12 | Fallowfield | 27.6/16kV | 606F2 | Transformer i3167 on 84 Gleeson solated to make repairs after the July 1 lightning storm. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
8677 | 2006 | 7 | 7 | 0.43056 |  | 240 | 140 | 35 | Fallowfield | 27.6/16kV | 606F2 | Isolated transformer on Kilbirnie to reroute the cables. | Nepean | Scheduled Outage | Construction
14679 | 2009 | 7 | 8 | 0.40625 |  | 55 | 22 | 24 | Fallowfield | 27.6/16kV | 606F2 | TP 5830 was isolated to allow crews to replace ground grid. | Nepean | Scheduled Outage | Preventive Maintenance
14680 | 2009 | 7 | 8 | 0.46597 |  | 59 | 42 | 100 | Fallowfield | 27.6/16kV | 606F2 | TP5815 was isolated to allow crews to replace ground grid. 17 other transformers were opened to allow crews to switch on an out of phase condition. | Nepean | Scheduled Outage | Preventive Maintenance
14696 | 2009 | 7 | 10 | 0.54028 |  | 2 | 4 | 130 | Fallowfield | 27.6/16kV | 606F2 | 13 transformers on Cambrian were dumped then picked up again on another phase, in order for crews to isolate a cable section with an out of phase condition. | Nepean | Human Element
14751 | 2009 | 7 | 15 | 0.41319 |  | 5 | 3 | 40 | Fallowfield | 27.6/16kV | 606F2 | 13 transformers interrupted due to off phase condition, load transferred to normal feed. | Nepean | Scheduled Outage
14755 | 2009 | 7 | 15 | 0.41736 |  | 5 | 3 | 40 | Fallowfield | 27.6/16kV | 606F2 | 12 transformers in the Cambrian & Greenbank area interrupted due to off phase condition to complete isolation of txs. | Nepean | Scheduled Outage
14757 | 2009 | 7 | 15 | 0.57986 |  | 5 | 3 | 40 | Fallowfield | 27.6/16kV | 606F2 | 12 transformers in the Cambrian & Greenbank area interrupted due to off phase condition, load transferred to normal feed. | Nepean | Scheduled Outage
16476 | 2010 | 7 | 15 | 0.39583 |  | 330 | 2338 | 425 | Fallowfield | 27.6/16kV | 606F2 | Crews isolated 20 transformers in the Half Moon Bay area to pull in cables and reconfiger underground plant. | Nepean | Scheduled Outage | Construction
14858 | 2009 | 7 | 27 | 0.61389 |  | 86 | 22 | 15 | Fallowfield | 27.6/16kV | 606F2 | Blue phase cable section us damage due to a dig-in. TP2435 was isolated to allow crew to check transformer and pull cable loop back into transformer. | Nepean | Foreign Interference | Dig-in
16568 | 2010 | 7 | 27 | 0.37639 |  | 319 | 713 | 281 | Fallowfield | 27.6/16kV | 606F2 | 281 customers out of power to accomidate an out of phase switching, and 111 customers remain out of power during the duration of the work permit on Greenbank and Cambrian to allow crews to re-configure the overhead. All 281customers out of power again to switch it all back to normal. | Nepean | Scheduled Outage | Construction
16574 | 2010 | 7 | 28 | 0.41528 |  | 78 | 112 | 86 | Fallowfield | 27.6/16kV | 606F2 | 9 transformers on Kilbirnie, Cheyenne, Blackleaf and Decona were isolated to allow crews to re-configure the underground plant. | Nepean | Scheduled Outage | Construction
14881 | 2009 | 7 | 29 | 0.52292 |  | 5 | 242 | 2899 | Fallowfield | 27.6/16kV | 606F2 | 606F2 tripped and locked out due to Holdoff in place after loss of supply from Hydro One | Ottawa | Loss of Supply | Rain
16684 | 2010 | 8 | 6 | 0.41597 |  | 111 | 115 | 62 | Fallowfield | 27.6/16kV | 606F2 | Crew has 3 transformers on Deercroft and Keltie to allow a contractor to pull in secondary cables and allow crew to replace a leaking transformer. | Nepean | Scheduled Outage | Repair
16718 | 2010 | 8 | 12 | 0.38889 |  | 250 | 125 | 30 | Fallowfield | 27.6/16kV | 606F2 | S27946 red phase was opened to isolate TP6606 and install 3 new transformers and cables. 30 customers affected in the new Stonebridge subdivivion at Jockvale & Cambrian. | Nepean | Scheduled Outage | Construction
5690 | 2004 | 8 | 18 | 0.35764 |  | 190 | 48 | 15 | Jockvale | 27.6/16kV | 606F2 | Step down transformer WX2000 has been removed from service and transformers switched over from 8kv to 27Kv along Jockvale Rd. | Nepean | Scheduled Outage | Construction
14960 | 2009 | 8 | 18 | 0.41806 |  | 24 | 118 | 540 | Fallowfield | 27.6/16kV | 606F2 | Transformer TP5815 @ 3589 was isolated to repair the ground grid that was damaged by a backhoe. | Nepean | Scheduled Outage | Repair
14966 | 2009 | 8 | 19 | 0.39653 |  | 100 | 20 | 12 | Fallowfield |  | 606F2 | Transformer TP5823 @ 2536 Stone Cove was isolated to repair damaged ground grid. | Nepean | Scheduled Outage | Repair
14968 | 2009 | 8 | 19 | 0.52847 |  | 27 | 27 | 60 | Fallowfield | 27.6/16kV | 606F2 | Transformer TP5830 was isolated to repair damaged ground grid. Due to radial feed configuration 10 transformers were interuupted. | Nepean | Scheduled Outage
5712 | 2004 | 8 | 24 | 0.41111 |  | 353 | 1177 | 200 | Fallowfield | 27.6/16kV | 606F2 | B & W phase txs in the Woodroffe/Cresthaven/Willow Creek area of Nepean isolated to cut in new txs and rearrange cables. | Nepean | Scheduled Outage | Construction
16843 | 2010 | 8 | 31 | 0.38819 |  | 117 | 23 | 12 | Fallowfield | 27.6/16kV | 606F2 | Transformer TP6707 @ 2404 Nutgrove was isolated to rplace ground grid. | Nepean | Scheduled Outage | Construction
15077 | 2009 | 9 | 9 | 0.43889 |  | 403 | 606 | 3265 | Fallowfield | 27.6/16kV | 606F2 | Hydro One reported the 606F2 breaker tripped while under hold off for Hydro ottawa crews. Crews contacted and they did not cause trip and surrendered their hold offs. No trouble reports from OFD or Police, breaker closed successfully by Hydro One. Cause was later determined to be a crow making contact & interrupting the transformer fuse at 1634 McGarry Terrace, transformer was refused successfully. | Nepean | Foreign Interference | Bird
15088 | 2009 | 9 | 11 | 0.43403 |  | 25 | 1360 | 3265 | Fallowfield | 27.6/16kV | 606F2 | Cct tripped under H/O while crew was switching to isolate a cable section for planned work, the elbow at Tx TP5816 flashed to ground causing trip. The damaged cable section was isolated before restoring the cct. Mattamy Homes, Cambrian & Greenbank area. | Nepean | Human Element | Switching Errors
15089 | 2009 | 9 | 11 | 0.43403 |  | 53 | 88 | 100 | Fallowfield | 27.6/16kV | 606F2 | Due to an off phase condition, power was off to 14 transformers while switching was performed to isolate primary cables for planned reconfiguration. Mattamy Homes, Cambrian & Greenbank area. New housing development, customer count is estimate. | Nepean | Scheduled Outage | Construction
15090 | 2009 | 9 | 11 | 0.58889 |  | 17 | 11 | 40 | Fallowfield | 27.6/16kV | 606F2 | Due to an off phase condition, power was off to 6 transformers while switching was performed to restore primary cables after reconfiguration. Mattamy Homes, Cambrian & Greenbank area. New housing development, customer count is estimate. | Nepean | Scheduled Outage | Construction
15091 | 2009 | 9 | 11 | 0.60764 |  | 9 | 9 | 60 | Fallowfield | 27.6/16kV | 606F2 | Due to an off phase condition, power was off to 11 transformers while switching was performed to restore primary cables after reconfiguration. Mattamy Homes, Cambrian & Greenbank area. New housing development, customer count is estimate. | Nepean | Scheduled Outage | Construction
19175 | 2011 | 9 | 14 | 0.37083 |  | 203 | 78 | 23 | Fallowfield | 27.6/16kV | 606F2 | TP5688 and TP5689 on Halfmoon bay were isolated to raise the transformers to grade and instal spacers | Nepean | Scheduled Outage
15114 | 2009 | 9 | 17 | 0.39722 |  | 29 | 87 | 180 | FALLOWFIELD |  | 606F2 | Planned switching interrupted 18 transformers, due to out of phase condition. | Nepean | Scheduled Outage
15116 | 2009 | 9 | 17 | 0.57014 |  | 20 | 60 | 180 | FALLOWFIELD | 27.6/16kV | 606F2 | 18 transformers were interrupted due to out of phase condition for planned switching. | Nepean | Scheduled Outage
13264 | 2008 | 9 | 19 | 0.40278 |  | 137 | 5 | 2 | Fallowfield | 27.6/16kV | 606F2 | Transformer #NP1712 located at 3645 Strandherd isolated to cut down some wire. | Nepean | Scheduled Outage | Preventive Maintenance
15145 | 2009 | 9 | 22 | 0.45556 |  | 48 | 2 | 2 | Fallowfield | 27.6/16kV | 606F2 | At 10:56am crews isolated transformer for working clearance to pull in some new cables. | Nepean | Scheduled Outage | Construction
15163 | 2009 | 9 | 24 | 0.43403 |  | 235 | 59 | 15 | Fallowfield | 27.6/16kV | 606F2 | TP5801 and TP5802 in the Greenbank and Cambrian area were isolated from Hydro Ottawa Sources to install new primary cable. | Nepean | Scheduled Outage
19251 | 2011 | 9 | 25 | 0.42847 |  | 305 | 10 | 2 | Fallowfield | 27.6/16kV | 606F2 | Fallowfield 606F2 A/R, customer called at 14:30 to report no power, crew found bird contact at X36918, 3664 Greenbank had caused transformer fuse to blow.. | Nepean | Foreign Interference | Bird
19294 | 2011 | 9 | 30 | 0.4125 |  | 255 | 42 | 10 | Fallowfield | 27.6/16kV | 606F2 | Transformer TP4398 was isolated @ 410 Blackleaf to allow crew to make cable section N.I.U. To allow new transformers to be cut in. | Nepean | Scheduled Outage | Construction
15195 | 2009 | 10 | 1 | 0.41667 |  | 16 | 45 | 170 | Fallowfield | 27.6/16kV | 606F2 | Defective primary pedestal PP2110 on River Run. Isolation required an outage to 16 transformers due to out of phase condition. | Nepean | Defective Equipment | Repair
15196 | 2009 | 10 | 1 | 0.54722 |  | 12 | 34 | 170 | Fallowfield | 27.6/16kV | 606F2 | Repaired PP2110 on River run. Restoration required an outage to 16 transformers due to out of phase condition. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17053 | 2010 | 10 | 5 | 0.38542 |  | 335 | 188 | 144 | Fallowfield | 27.6/16kV | 606F2 | 144 customers were interupted in the Mattamy Half Moon Bay subdivision due to an out of phase condition, crews isolated TP5814 and the same 144 customers were interupted again when power was restored. | Nepean | Scheduled Outage | Construction
17107 | 2010 | 10 | 13 | 0.59722 |  | 309 | 205 | 90 | Fallowfield | 27.6/16kV | 606F2 | 3 transformers TP5815, TP5805 & TP5804 isolated to lower the base of TP5815 and repair the ground grid at TP5804. 5 other transformers were interrupted during isolation and restoration due to the out of phase back up supply. Customers affected in the new Half Moon Bay subdivision off Cambrian Rd. | Nepean | Scheduled Outage
19401 | 2011 | 10 | 18 | 0.0625 |  | 160 | 61 | 23 | Fallowfield | 27.6/16kV | 606F2 | TP7363 at 960 Caldermill had a defective secondary cable. Replaced by on-call. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17137 | 2010 | 10 | 19 | 0.42361 |  | 262 | 444 | 150 | Fallowfield | 27.6/16kV | 606F2 | At 9 transformers on in Halfmoon Bay were isolated to allow crews to raise transformer bases and repair ground grids. Fallowfield (606F2) ID# 17137 | Nepean | Scheduled Outage
15293 | 2009 | 10 | 22 | 0.53264 |  | 222 | 168 | 184 | Fallowfield | 27.6/16kV | 606F2 | Scheduled outage to TP5815 to allow crew to repair ground grid, interruption affected 20 transformers momentarily due to out of phase condition. Switching performed to restore 19 of the transformers. | Nepean | Scheduled Outage
15306 | 2009 | 10 | 26 | 0.38889 |  | 95 | 111 | 160 | Fallow Field | 27.6/16kV | 606F2 | TP5814 at 3631 Cambrian was isoalted for to install sec-service cable. Fallow Field (606F2). affected 9 additional Xfrm'rs during isolation and restore | Nepean | Scheduled Outage
17178 | 2010 | 10 | 26 | 0.71528 |  | 502 | 390 | 87 | Fallowfield | 27.6/16kV | 606F2 | At 09:19 5 transformers in Halfmoon Bay were isolated to allow crew to repair ground grid and lower transformer base. Out of phase condition caused 4 extra transformer to be affected before and after isolation. | Nepean | Scheduled Outage
19486 | 2011 | 10 | 28 | 0.38194 |  | 267 | 156 | 35 | Fallowfield | 27.6/16kV | 606F2 | Transformers TP7284 and TP7283 isolated to install new primary cables at Seelys Bay and Cambrian. | Ottawa | Scheduled Outage
11626 | 2007 | 10 | 29 | 0.38264 |  | 307 | 2047 | 400 | Fallowfield | 27.6/16kV | 606F2 | Isolation from S15639, on Cambrian Rd, to reroute blue phase cable section and connect/energize new padmounts. | Nepean | Scheduled Outage
15323 | 2009 | 10 | 29 | 0.39653 |  | 141 | 25 | 110 | Fallowfield | 27.6/16kV | 606F2 | TP5816 at 3590 Cambrian was isolated for crew to replace damaged ground grid, 10 transforners interrupted during restore switching due to out of phase conditions. | Nepean | Scheduled Outage | Repair
19511 | 2011 | 11 | 1 | 0.40764 |  | 235 | 12 | 3 | Fallowfield | 27.6/16kV | 606F2 | Transformer TP3575 at Marketplace/Sue Holloway was isolated to allow crew to cut in new transformer TP7477. | Nepean | Scheduled Outage | Construction
19521 | 2011 | 11 | 2 | 0.43889 |  | 319 | 271 | 51 | Fallowfield | 27.6/16kV | 606F2 | Transformers TP5806, TP5807, TP5799 and TP5839 in Fallowfield were isolated to allow crews to cut in new transformers for new housing development. | Goulburn | Scheduled Outage | Construction
19544 | 2011 | 11 | 8 | 0.40903 |  | 102 | 27 | 16 | Fallowfield |  | 606F2 | TP 5685 at 109 Abetti Ridge was damaged and replaced with new TP | Nepean | Scheduled Outage | Preventive Maintenance
15379 | 2009 | 11 | 11 | 0.42153 |  | 253 | 105 | 25 | Fallowfield | 27.6/16kV | 606F2 | TP5467 on Temagami in Chapman Mills was isolated to allow contractor to pull in new secondary conductors. | Nepean | Scheduled Outage | Construction
11706 | 2007 | 11 | 14 | 0.66667 |  | 58 | 23 | 24 | Fallowfield | 27.6/16kV | 606F2 | TP3664 at 152 Berrigan was taken out of service incase wall removal by Fire Depatment fell on transformer. Wall & new buildings were damaged by fire on Berrigan, afternoon of Nov 13th. No damage was done by wall removal & xfmr was restored. | Nepean | Adverse Environment | Fire
4523 | 2003 | 11 | 27 | 0.45833 |  | 1 | 3 | 190 | Fallowfield | 27.6/16kV | 606F2 | TE3086 to 3087 was identified as close, all transformers were checked closed. Parallel was thought to be ineffect and when switch 3032 to S7045 opened potential to 19 transformers lost. Switch closed and normal open point found. | Nepean | Human Element | Switching Errors
19657 | 2011 | 12 | 1 | 0.33681 |  | 485 | 113 | 14 | Fallowfield | 27.6/16kV | 606F2 | TP5685 at 111 Abetti Ridge isolated to change out defective transformer | Nepean | Defective Equipment | Equipment Deterioration Due to Age
5968 | 2004 | 12 | 4 | 0.041667 |  | 212 | 14 | 4 | Fallowfield | 27.6/16kV | 606F2 | TE 3715 at 3585 Strandherd out to make new connections to secondary. | Nepean | Scheduled Outage | Construction
7695 | 2005 | 12 | 6 | 0.58472 |  | 31 | 31 | 60 | FALLOWFEILD | 27.6/16kV | 606F2 | FIVE NEW XMERS ENERGIZED, OUTAGE DUE TO CUSTOMERS BETWEEN WORK AREA AND END OF LINE. | Nepean | Scheduled Outage | Construction
15484 | 2009 | 12 | 8 | 0.42292 |  | 36 | 60 | 100 | Fallowfield | 27.6/16kV | 606F2 | Isolation of PP2110 required out of phase transformer loop to be off loaded and restored from different phase. | Nepean | Scheduled Outage | Construction
7726 | 2005 | 12 | 14 | 0.38542 |  | 1190 | 198 | 10 | Fallowfield | 27.6/16kV | 606F2 | Transformer at Harbourview & Felicia, TP2765 the secondary failed and transformer fuse opened. Crew isolated and replaced the transformer. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
15518 | 2009 | 12 | 15 | 0.42708 |  | 259 | 86 | 20 | Fallowfield | 27.6/16kV | 606F2 | TP5474 at 598 Chapman Mills was isolated to allow clearance for installing secondary cables | Nepean | Scheduled Outage | Construction
13783 | 2008 | 12 | 19 | 0.6875 |  | 35 | 10 | 18 | Fallowfield | 27.6/16kV | 606F2 | TP4952 at 535 Sandgate was hit by a car & pushed off its base. Customers on TP4953 were also off while TP4952 was replaced on its base. (off phase condition on Tx loop) | Nepean | Foreign Interference | Vehicle
7194 | 2005 | 8 | 23 | 0.375 |  | 342 | 86 | 15 | Falowfield | 27.6/16kV | 606F2 & 7F1 | TP2367 and TE3669 were isolated to reconfigure red and white cable loops and complete the cable loop between 606 F1 and 7F1 | Nepean | Scheduled Outage | Construction
14857 | 2009 | 6 | 24 | 0.89931 |  | 266 | 28857 | 10332 | Fallowfield | 27.6/16kV | 606F2, 606F1 | Fallowfield F1 & F2 opened due to a bad contactor on the T1-L at Fallowfield. Hydro One reports Fallowfield will be unavailable to Hydro Ottawa until repairs can be made. All load transferred to Limebank and Longfields. Fallowfield (606F1 & 606F2). Fallowfield (606F1, 606F2). ID#14857. | Nepean | Loss of Supply | Equipment Failure - Cause Unknown
19825 | 2012 | 1 | 13 | 0.54931 |  | 4 | 0 | 1 | Slater TS | 13.2kV | 608 | Vault VT146 was interrupted due to Hydo Ones forced outage to King Edwards Y bus winding while our circuits were in parallel. Slater (TS77) ID#19825 | Ottawa | Human Element | Switching Errors
20409 | 2012 | 4 | 28 | 0.59653 |  | 1381 | 23 | 1 | Slater | 13.2kV | 608 | A contractor working at VT39 at 320 Sussex Dr. had a flashover while doing customer secondary work on VT39 C bus. The contractor was doing some control wiring on the customer's secondary breaker. When he racked in and closed the breaker it flashed phase to ground and caused a fuse in the the R3-F to blow. SCADA indicated a spike on TS77 at 14:19. System Office issued a PC10C to Dave Lavictoire of Eaton Electric on the C bus fed by R3-F. | Ottawa | Foreign Interference
10605 | 2007 | 6 | 11 | 0.93194 |  | 76 | 8 | 6 | Slater | 13.2kV | 608 | TS77 breaker tripped Cable section between Vt405 old War Museum amd and VT575 Gallery of Canada. Breaker relays show Red and white phase instantaneous. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10613 | 2007 | 6 | 13 | 0.046528 |  | 1171 | 31 | 6 | Slater | 13.2kV | 608 | Flashed switch VT145-L1 at Elizabeth Brueyere Hospital. Switch will need repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12645 | 2008 | 6 | 15 | 0.65764 |  | 3 | 66 | 1321 | OVERBROOKE | 13.2kV | 608 (TO46) | TO46 Breaker tripped (608 Line). Severe lightning storm in effect. Breaker closed and holding via SCADA. | Ottawa | Adverse Weather | Lightning
17054 | 2010 | 10 | 5 | 0.3625 |  | 14 | 2 | 10 | Slater | 13.2kV | 609 | TS58 breaker tripped due to underground crew checking rotation on a transformer at VT302 - 141 Somerset when a malfuntion occured on their testing equipment. Circuit was abnormal for vault shutdown at that same address, but the vault was not isolated at the time. 626, 609 and 611 circuits were affected. | Ottawa | Human Element | Incorrect Use of Equipment
7713 | 2005 | 12 | 11 | 0.57083 |  | 2 | 0 | 4 | Slater | 13.2kV | 609 & 611 | While fault locating on the 616 cable, because the CB1 breaker at VT173 did not open we closed into fault. | Ottawa | Defective Equipment
20838 | 2012 | 6 | 23 | 0.081944 |  | 126 | 2 | 1 | Slater | 13.2kV | 610 | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
4934 | 2004 | 3 | 24 | 0.21528 |  | 45 | 3 | 4 | Slater | 13.2kV | 611 & 609 | TS58 breaker opened, cause unknown. 4 13kv vaults interupted on Laurier, Slater, and Kent | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4839 | 2004 | 2 | 28 | 0.96319 |  | 533 | 80 | 9 | Slater | 13.2kV | 613 | Transformer bus at VT372, National Press Club at 165 Sparks, isolated for maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
6397 | 2005 | 4 | 10 | 0.37847 |  | 175 | 6 | 2 | Slater | 13.2kV | 613 | VT22 at 75 Albert was shutdown for cleaning and fibre optic installation. 85 Albert is fed from the vault as well. Interrupted | Ottawa | Scheduled Outage | Preventive Maintenance
13324 | 2008 | 10 | 4 | 0.40972 |  | 240 | 8 | 2 | Slater |  | 613 | VT22 at 75 Albert was isolated to allow customer contractor to perform vault maintanence | Ottawa | Scheduled Outage | Preventive Maintenance
19568 | 2011 | 11 | 13 | 0.35417 |  | 270 | 36 | 8 | Slater | 13.2kV | 613 | Vault VT100 @ 130 was isolated to allow contractor to perform customer vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
5443 | 2004 | 7 | 5 | 0.43958 |  | 2 | 0 | 11 | Slater | 13.2kV | 614 | While performing maintenance on the TS72 breaker, the S72-E disc was accidently opened from inside the cubicle. | Ottawa | Human Element | Switching Errors
4292 | 2003 | 10 | 19 | 0.055556 |  | 438 | 146 | 20 | Slater | 13.2kV | 614 | 13 kv vault VT736 at 111 Albert isolated for Imperial Electric to perform routine maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
3136 | 2003 | 1 | 22 | 0.6875 |  | 120 | 2 | 1 | Slater TS | 13.2kV | 615 | Temporary Service, white phase 400 amp fuse feeding 140 Slater found blown by 24/7 crew. Refused and closed restoring power. | Ottawa | Defective Equipment
3137 | 2003 | 1 | 22 | 0.88403 |  | 117 | 2 | 1 | Slater TS | 13.2kV | 615 | 24/7 Crew responded to no power call. Trouble Crew assisted. Replaced 400 amp fuse and closed restoring power. Customer reduced loading to 380 amps and is arranging for a generator. | Ottawa | Defective Equipment
5701 | 2004 | 8 | 21 | 0.36458 |  | 565 | 19 | 2 | Slater | 13.2kV | 615 | Scheduled outage to VT898 & VT43 main & xfmr buses at Parliament Hill for routine maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
20836 | 2012 | 6 | 23 | 0.081944 |  | 82 | 30 | 22 | Slater |  | 616 | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
18872 | 2011 | 8 | 3 | 0.13889 |  | 145 | 12 | 5 | Slater | 13.2kV | 616 | 13KV transformer bus at VT715 (116 Lisgar St) was isolated to allow hydro crew to install a new main breaker pannel in this distribution vault. | Ottawa | Scheduled Outage | Construction
7712 | 2005 | 12 | 11 | 0.49167 |  | 129 | 18 | 9 | Slater | 13.2kV | 616 | A faulty transformer at VT173 at 111 cooper caused 616 cable to open. The CB! Main breaker at vault VT173 did not operate to isolate faulty transformer. While fault locating because the CB1 breaker did not open the transformer blew up. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20839 | 2012 | 6 | 23 | 0.081944 |  | 138 | 253 | 110 | Slater |  | 617 | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
3165 | 2003 | 2 | 5 | 0.23681 |  | 140 | 91 | 39 | Greenland DS | 8/4.8kV | 61M2 | Transfer customers fed from Arnprior TS which is a Hydro One supply were interupted due to floating conductors contacting one another. | Kanata | Loss of Supply | HEPC Circuit Fault
20843 | 2012 | 6 | 23 | 0.081944 |  | 153 | 5 | 2 | Slater | 13.2kV | 621 | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
10549 | 2007 | 6 | 7 | 0.52847 |  | 50 | 5 | 6 | Slater | 13.2kV | 622 | TS73 breaker tripped open. Did in reported at North East corner of Bank and Slater. 622 cable section isolated and all power restored. | Ottawa | Foreign Interference | Dig-in
10517 | 2007 | 6 | 3 | 0.125 |  | 8 | 0 | 1 | Slater | 13.2kV | 623 | While 24/7 was partially isolating VT299 @ 99 Bank St. An item on the order to operate was missed. Causing an outage at 99 Bank st. | Ottawa | Human Element | Switching Errors
7740 | 2005 | 12 | 16 | 0.44792 |  | 7 | 350 | 3000 | KANATA MTS | 27.6/16kV | 624 T2B2 | 624 T2B2 breaker opened at Kanata MTS. Loss of load to 624F4, 624F5, & 624F6 circuits. Tim Bastin reports NO relays flagged on breaker at the station. 624 T2B2 breaker closed via scada. All power restored to normal. | Kanata | Unknown/Other | No Apparent Cause
9120 | 2006 | 9 | 5 | 0.47014 |  | 24 | 262 | 656 | Kanata | 27.6/16kV | 624B1 | The 624B1 bus trip under differentail because of the new relaying setting being install on the 624F1 breaker. The 624F1 was isolated at the time. Load loss was on the F2 & F3 | Kanata | Human Element | Incorrect Protection Settings
7829 | 2006 | 1 | 20 | 0.36944 |  | 204 | 2421 | 2000 | KANATA | 27.6/16kV | 624F1 | Animal flashed 2 insulator at the rear of Canadian Tire. On Didsbury st. Approx 50 customers remain out of power while repairs were made. | Kanata | Foreign Interference | Animal
6198 | 2005 | 2 | 10 | 0.43819 |  | 53 | 261 | 3120 | Kanata | 27.6/16kV | 624F1 | T1B1, B1B2 & 624F1 breakers opened while a Stations Crew was downloading information into the 624F2 breaker. S183 transfer switch at the Corel Centre did not transfer properly, resulting in a longer outage to them, until 24/7 could restore power manually. Stations crews are investigating both problems. | Kanata | Human Element | Commissioning Errors
17571 | 2011 | 2 | 11 | 0.37639 |  | 126 | 25 | 12 | Kanata MTS | 27.6/16kV | 624F1 | Transformer 1854 at 163 Hemlo isolated to allow Greely to clear out transformer base. | Kanata | Scheduled Outage | Repair
7938 | 2006 | 2 | 17 | 0.425 |  | 55 | 2750 | 3000 | Kanata | 27.6/16kV | 624F1 | Primary wire down on a dead end on Richardson Rd and Terry Fox, cut clear. | Kanata | Adverse Weather | Wind
17620 | 2011 | 2 | 19 | 0.25 |  | 20 | 0 | 1 | Kanata MTS | 27.6/16kV | 624F1 | Defective red phase termination at Switch 835. Customer was single phase. Switching performed to isolate 3 phase cable section and restore power from alternate feed. | Kanata | Defective Equipment
13995 | 2009 | 2 | 20 | 0.40972 |  | 130 | 130 | 60 | Kanata MTS | 27.6/16kV | 624F1 | Isolation of Transformers to allow crew to reconfigure line and energize 2 new transformers, in the Keyrock and Kanata Ave, area. | Kanata | Scheduled Outage
20050 | 2012 | 2 | 23 | 0.42708 |  | 280 | 355 | 76 | Kanata | 27.6/16kV | 624F1 | After switching to isolate a line section for planned work, a customer call was received reporting power out on Huntsville Dr & Ingersol. Investigation showed that record maps were incorrrect & 6 transformers were unintentionally left without power. | Kanata | Human Element | Incorrect Records
15762 | 2010 | 3 | 3 | 0.03125 |  | 225 | 4 | 1 | Kanata | 27.6/16kV | 624F1 | Transformer #3414 at 21 Didsbury was found deferctive, ONCALL required to replace | Kanata | Defective Equipment
4858 | 2004 | 3 | 4 | 0.71597 |  | 53 | 11 | 12 | KanataMTS |  | 624F1 | Transformer hit by truck and had to be replaced. TX2293 at 7 Macassa Circle. | Kanata | Scheduled Outage | Preventive Maintenance
15801 | 2010 | 3 | 15 | 0.37847 |  | 94 | 16 | 10 | Kanata MTS | 27.6/16kV | 624F1 | TP5763 @ 346 Laughlin was isolated to allow a crew to change a defective transformer. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14162 | 2009 | 4 | 10 | 0.063194 |  | 220 | 55 | 15 | Kanata | 8/4.8kV | 624F1 | Transformer 1955 at 499 Terry Fox was isolated to allow crews to replace it due to an oil leak. | Ottawa | Scheduled Outage | Repair
8171 | 2006 | 4 | 20 | 0.25625 |  | 101 | 1714 | 1820 | Kanata | 27.6/16kV | 624F1 | The Kanata MTS 624F1 feeder tripped due to a faulted 3 phase overhead transformer at Farleyan church on Didsbury Rd. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
15976 | 2010 | 4 | 23 | 0.41667 |  | 23 | 1037 | 2704 | Kanata MTS | 27.6/16kV | 624F1 | While restoring circuit back to normal, a red phase insulator broke on switch 195 @ palladium dr. While crew was breaking a parallel, causing the circuit to open. Crew cleared the insulator and power was restored. | Kanata | Defective Equipment
6494 | 2005 | 5 | 3 | 0.375 |  | 304 | 51 | 10 | Kanata | 27.6/16kV | 624F1 | Transformer 2383 @ 9 Keno Dr was isolated to change leaking transformer and clean up oil spill. | Kanata | Scheduled Outage | Repair
18102 | 2011 | 5 | 6 | 0.23819 |  | 169 | 8 | 3 | Kanata | 27.6/16kV | 624F1 | 27kV transformer TP3832 at 35 Didsburry was isolated to allow crews to re-arrange secondary cables | Kanata | Scheduled Outage | Repair
18112 | 2011 | 5 | 7 | 0.61111 |  | 536 | 18 | 2 | Kanata | 27.6/16kV | 624F1 | A section of o/h line at Terry Fox & 417 from sw. 648 was isolated for working clearance while crews made repairs to A9M3 cct. Transformer X45575 & X06632 were affected, X06632 feeds traffic lights only & City was notified in advance. | Kanata | Scheduled Outage | Repair
8358 | 2006 | 5 | 26 | 0.63542 |  | 125 | 4 | 2 | Kanata | 27.6/16kV | 624F1 | Transformer #1548 located at 285 Didsbury isolated due to animal contact | Kanata | Foreign Interference | Animal
6645 | 2005 | 6 | 2 | 0.66528 |  | 90 | 4131 | 3105 | Kanata | 27.6/16kV | 624F1 | Cable fault between S608-4 & S597-2. Approx 3105 customers affected in power outage. North of the Queensway & Terry Fox to Kanata Lakes. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
10564 | 2007 | 6 | 8 | 0.80903 |  | 4 | 121 | 1820 | Kanata | 27.6/16kV | 624F1 | Kanata 624F1 feeder auto/reclose/auto, circuit energized via SCADA, patrol to be performed later. | Kanata | Unknown/Other
3650 | 2003 | 6 | 10 | 0.48125 |  | 11 | 0 | 2 |  | 27.6/16kV | 624F1 | At 11:33pm Tuesday evening while switching to shutdown the vault at the Corel Center for transfer switch repair, a sectionalizing switch malfunctioned causing an interruption to 2 buildings beside the Corel center. Power was restored at 11:44pm. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
18519 | 2011 | 6 | 24 | 0.93472 |  | 514 | 9 | 1 | Kanata MTS | 27.6/16kV | 624F1 | Lightning storm caused two blown current limiting fuses to blow on transformer 1972 and caused secondary cables to fail. Customer got a generator until cables are repaired. Kanata (624F1) ID#18519 | Kanata | Lightning
10755 | 2007 | 6 | 28 | 0.55556 |  | 60 | 1 | 1 | Kanata | 27.6/16kV | 624F1 | Customer at 285 Didsbury rd called in a part-out condition. The crew found 1 phase at switch 1548 open. The transformer was isolated & equipment tested with no problems found. Blown fuse was replaced & transformer energized. | Kanata | Unknown/Other | No Apparent Cause
6835 | 2005 | 6 | 30 | 0.68611 |  | 125 | 5838 | 3105 | KANATA MTS | 27.6/16kV | 624F1 | CABLE FAULT BETWEEN S597-2 AND S608-4. SECTIONALIZED TO RESTORE POWER. AFFECTING KANATA LAKES, CENTRUM MALL AREA. | Kanata | Defective Equipment
6928 | 2005 | 7 | 14 | 0.0375 |  | 185 | 4552 | 3105 | KANATA | 27.6/16kV | 624F1 | 624F1 TRIPPED DUE TO DEFECTIVE CABLE BETWEEN S11004 AND S597-1. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8753 | 2006 | 7 | 17 | 0.98403 |  | 103 | 5356 | 3120 | Kanata | 27.6/16kV | 624F1 | B. Seaman patrolled 624F1 and found no apparent cause for line trip. 624F1 trip caused due to lightining. 624F1 closed and all customers restored. | Kanata | Lightning | Direct Strike
16550 | 2010 | 7 | 24 | 0.39931 |  | 40 | 277 | 415 | Kanata | 27.6/16kV | 624F1 | SC4399-CB3 found opened NO fault inds flagged on transformer loop. First cable section hipotted. Cable tested good from SC4399-CB3 to T1529. SC4399-CB3 closed restoring lost load to 7 transformerin the area. | Kanata | Unknown/Other | No Apparent Cause
18915 | 2011 | 8 | 12 | 0.22917 |  | 225 | 11 | 3 | Kanata MTS | 27.6/16kV | 624F1 | TP3832 was isolated to allow crew to remove a temporary service. | Kanata | Scheduled Outage | Construction
3918 | 2003 | 8 | 20 | 0.26597 |  | 8 | 200 | 1500 | Kanata MTS | 27.6/16kV | 624F1 | 624F1 tripped and stayed open due to recloser always set in block postion. Ground instantaneous was flagged. Closed by SCADA | Kanata | Unknown/Other
19034 | 2011 | 8 | 28 | 0.72361 |  | 11 | 589 | 3213 | Kanata | 27.6/16kV | 624F1 | 624F1 breaker tripped with no attempt at auto-reclose, breaker closed by SCADA | Kanata | Unknown/Other | No Apparent Cause
5773 | 2004 | 9 | 3 | 0.77778 |  | 354 | 13650 | 3100 | Kanata | 27.6/16kV | 624F1 | A faulted cable between sectionlizers S208 and S237 caused the 624F1 brk to trip in Kanata. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5774 | 2004 | 9 | 4 | 0.89583 |  | 303 | 86 | 49 | Kanata | 27.6/16kV | 624F1 | A faulty transformer 2293W on Macasses had to be replaced. To isolate this transformer there was no secondary supply for the remaining transformers down line because of the earlier cable fault. This remaining transformer were also effected. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5800 | 2004 | 9 | 11 | 0.46181 |  | 128 | 4 | 2 | Kanata MTS | 27.6/16kV | 624F1 | Blown termination at S81R @ Kanata Rockeries | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11295 | 2007 | 9 | 13 | 0.020833 |  | 260 | 35 | 8 | Kanata | 27.6/16kV | 624F1 | Transformer 2055 at Best Buy at 790 Kanata Ave isolated for replacement with a larger transformer | Kanata | Scheduled Outage | Construction
11407 | 2007 | 9 | 27 | 0.92708 |  | 323 | 43 | 8 |  | 27.6/16kV | 624F1 | Transformer 1370 at195 Roland Mitchner was isolated to allow crews to replace transformer. | Kanata | Scheduled Outage
15186 | 2009 | 9 | 29 | 0.0083333 |  | 461 | 31 | 4 | Kanata MTS | 27.6/16kV | 624F1 | Transformer 478 at 151 Roland Mitchner replaced due to oil leak. New transformer # TP6928. | Kanata | Scheduled Outage | Repair
7456 | 2005 | 10 | 14 | 0.70833 |  | 101 | 15 | 9 | Kanata | 27.6/16kV | 624F1 | Transformer 867 on Knudson Dr defective and replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11683 | 2007 | 11 | 8 | 0.38194 |  | 135 | 4 | 5 |  | 27.6/16kV | 624F1 | Contractor dig in at Canadian tire on Campeau Dr. caused the switch #196 blue phase fuse to blow, red and white phases had to be opened to isolate damaged cable and eliminate single phasing condition to 3 phase customers, broken switches at #196 delayed restoration of the last customer (Canadian Tire). | Kanata | Foreign Interference | Dig-in
5955 | 2004 | 11 | 30 | 0.39583 |  | 52 | 171 | 200 | Kanata MTS | 27.6/16kV | 624F1 | White phase cable section isolated between TE1892 by 1893 for suspected fault. Customer interruption due to other end of cable isolated for permit. Permit had to be terminated to restore customer load. Cause determined to be a defective secondary service cable. | Kanata | Scheduled Outage | Repair
13730 | 2008 | 12 | 10 | 0.46528 |  | 2 | 0 | 6 | Kanata | 27.6/16kV | 624F1 | A Cooney isolated 4 transformers (TP3602, TP3603, TP3604 & TP3605) on Remnor, in Kanata, during switching in a Primary Pedistal to prevent an out of phase condition | Kanata | Scheduled Outage | Construction
9874 | 2006 | 12 | 22 | 0.85278 |  | 322 | 54 | 10 | Kanata | 27.6/16kV | 624F1 | A car hit a transformer T1883W @ 14 Sherring knocking it off it pedestal. | Nepean | Foreign Interference | Vehicle
3965 | 2003 | 8 | 29 | 0.37083 |  | 6 | 302 | 3020 | Kanata MTS | 27.6/16kV | 624F1,F2,F3 | Thunder storm and heavy rain, Auto reclose on the Hydro One circuit 3CS. | Kanata | Loss of Supply | HEPC Circuit Fault
6218 | 2005 | 2 | 20 | 0.375 |  | 210 | 175 | 50 | Eastview | 27.6/16kV | 624F2 | 5 transformers on Carlotta & Marguerite were interrupted in order to transfer them to upgraded conductor. | Ottawa | Scheduled Outage | Preventive Maintenance
15774 | 2010 | 3 | 5 | 0.36181 |  | 281 | 9 | 2 | KANATA MTS | 27.6/16kV | 624F2 | Transformer X07194 at 1090 March Rd isolated to allow for service upgrade | Kanata | Scheduled Outage | Construction
20652 | 2012 | 5 | 29 | 0.38889 |  | 69 | 240 | 209 | Kanata DS | 27.6/16kV | 624F2 | Transformers between S292 and S312 in Morgans Grant were isolated for elbow and insert replacement. | Kanata | Scheduled Outage
14432 | 2009 | 5 | 30 | 0.43889 |  | 343 | 6 | 2 | Kanata | 27.6/16kV | 624F2 | Vaults 1373, 1420 and 2622T1 & T2 at Alcatel (600 March Rd.) isolated to allow contractor to service customer owned transformers and secondary equipment. | Kanata | Scheduled Outage | Preventive Maintenance
6691 | 2005 | 6 | 10 | 0.35347 |  | 67 | 29 | 43 | Kanata MTS | 27.6/16kV | 624F2 | 624F2 feeder auto trip due to faulted cable between S461 & SC2175. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5435 | 2004 | 7 | 2 | 0.091667 |  | 997 | 33 | 2 | Kanata | 27.6/16kV | 624F2 | Lightning strike in area caused cable section 5878-2 by 158 to blow. Radial underground suuply had to be repaired to get power restored. | Kanata | Lightning | Lightening Strike on adjacent circuit
5436 | 2004 | 7 | 2 | 0.61458 |  | 1684 | 79 | 4 | Kanata | 27.6/16kV | 624F2 | Lightning strike caused cable to fault. 2 customers restore with normal switching and last 2 customers restored after cable repaired. Radial underground supply. Great planning. | Kanata | Lightning | Lightning Strike on Adjacent Circuit Flashed Over
5696 | 2004 | 8 | 18 | 0.99583 |  | 21 | 1358 | 4300 | Kanata | 27.6/16kV | 624F2 | While switching Kanata MTS back to normal a flash occurred at a switch S478 causing the MWDF2, 624F2 and the BRDF4(which was carrying the 624F1 load) to trip. We pick up the MWDF2 load, then BRDF4 would not close back in via scada so we pick up the BRDF4 by the 624F1. Then the 624F2 load was pick up. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5796 | 2004 | 9 | 9 | 0.87847 |  | 802 | 13 | 1 | Kanata | 27.6/16kV | 624F2 | Transformer 2598 @ 305 Leggett Dr the Kanata Pumping Station was isolated to dry off the customers electrical system. | Kanata | Adverse Weather | Rain
7391 | 2005 | 9 | 28 | 0.68958 |  | 97 | 3 | 2 | Kanata MTS | 27.6/16kV | 624F2 | Al Cooney reports S461 connection are burning up. S461 isolated to renew all connection & grounds strips. 2 Customers effected in power planned outage. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
11537 | 2007 | 10 | 16 | 0.89236 |  | 795 | 40 | 3 | Kanata | 27.6/16kV | 624F2 | Tx 4439 supplying 106 Schneider was isolated to provide a safe work area for Ottawa fire dept. Unit 106A isolated at transformer Meter# 727221 removed. | Kanata | Adverse Environment | Fire
5987 | 2004 | 12 | 7 | 0.3875 |  | 212 | 85 | 24 | Kanata MTS | 27.6/16kV | 624F2 | Isolation of txs 2163 & 2164 on Turtle Point Way for installation of new txs. | Kanata | Scheduled Outage | Construction
4660 | 2003 | 12 | 29 | 0.37014 |  | 27 | 4 | 10 | Kanata MTS | 27.6/16kV | 624F2 | Transformer 4325 was isolated due to elbow not being vented | Kanata | Scheduled Outage | Construction
13947 | 2009 | 2 | 9 | 0.61389 |  | 9 | 4 | 28 | Kanata | 27.6/16kV | 624F3 | Single phase overhead section on Fringwood Dr in Stittsville isolated to remove fallen tree limb. | Kanata | Tree Contacts | Tree Limb Fallen
8276 | 2006 | 5 | 11 | 0.38542 |  | 235 | 98 | 25 | Kanata | 27.6/16kV | 624F3 | T2206 and T2207 were isolated to re-arrange cables on Edenvale in Kanata. | Kanata | Scheduled Outage
8296 | 2006 | 5 | 15 | 0.41042 |  | 84 | 10 | 7 | Kanata | 27.6/16kV | 624F3 | Transformer 2938 on Birkendale in Kanata Isolated to replace leaking XMER. | Kanata | Scheduled Outage | Repair
7375 | 2005 | 9 | 25 | 0.4 |  | 189 | 263 | 103 | Kanata MTS | 27.6/16kV | 624F3 | Cable fault from S259 to TE576. Hearst Way, Roberge Crescent | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11587 | 2007 | 10 | 24 | 0.46667 |  | 123 | 904 | 631 | Kanata MTS | 27.6/16kV | 624F3 | 624F3 feeder auto trip due to internal faults in sectionalizer S311. S311 isolated for repairs. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11604 | 2007 | 10 | 26 | 0.43403 |  | 65 | 2 | 2 | Kanata | 8/4.8kV | 624F3 | Refused line switch feeding transformer at 21 Bayfield Ave no cause found for blown fuse | Nepean | Unknown/Other | No Apparent Cause
11662 | 2007 | 11 | 5 | 0.41319 |  | 227 | 30 | 8 | Kanata MTS | 8/4.8kV | 624F3 | At 9:55 am transformer 277 at 283 Pickford Avenue in Kanata was isolated for soil cleanup, 12 customers were affected for 227 min. ID 11662. | Nepean | Scheduled Outage | Construction
11676 | 2007 | 11 | 6 | 0.56667 |  | 47 | 9 | 12 | Kanata | 27.6/16kV | 624F3 | Tx 276R at 16 Clarkson crt was isolated to repair broken insert. | Kanata | Scheduled Outage | Repair
19687 | 2011 | 12 | 6 | 0.017361 |  | 63 | 3584 | 3672 | Kanata | 27.6/16kV | 624F3 | 624F3 carrying part 624F1 load auto reclosed then tripped caused by a cable fault between SC2260 and SC4565 | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19699 | 2011 | 12 | 7 | 0.67917 |  | 115 | 958 | 568 | Kanata MTS | 27.6/16kV | 624F3 | 624F3 breaker opend due to a cable fault. Kanata ID# DEC-7-11-LA | Kanata | Defective Equipment
9868 | 2006 | 12 | 19 | 0.5625 |  | 160 | 867 | 630 | Kanata | 27.6/16kV | 624F3 | A contractor dug into the B phase cable at Irwin and Bachman. | Kanata | Foreign Interference | Dig-in
9894 | 2006 | 12 | 30 | 0.61389 |  | 215 | 22 | 6 | Kanata | 27.6/16kV | 624F3 | Transformer T278 on Pickford Dr in Kanata was hit by a vehicle, damaged and had to be replaced. | Kanata | Foreign Interference | Vehicle
14251 | 2009 | 4 | 27 | 0.63403 |  | 343 | 145 | 60 | Kanata | 27.6/16kV | 624F4 | A blown insert at transformer 203 @ 140 McCurdy. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8211 | 2006 | 5 | 1 | 0.39583 |  | 105 | 18 | 10 | Kanata | 27.6/16kV | 624F4 | Transformer #157 located at 4 Liston isolated due to leaking transforming being replaced | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8221 | 2006 | 5 | 3 | 0.40278 |  | 70 | 12 | 10 | Kanata | 27.6/16kV | 624F4 | Planned outage to transformer 1196 (edenvale dr.) to upgrade transformer from 50kva to 75kva. | Kanata | Scheduled Outage
6511 | 2005 | 5 | 4 | 0.92708 |  | 106 | 21 | 12 |  | 27.6/16kV | 624f4 | Blown transformer fuse at T1263 on Ironside in Kanata Lakes. Isolated transformer refused , closed and restored to normal. | Kanata | Defective Equipment
10370 | 2007 | 5 | 6 | 0.032639 |  | 318 | 198 | 57 | Kanata MTS | 27.6/16kV | 624F4 | Blue phase cable fault between T259 and T576B on Hearst way and Roberge in Kanata, caused S639B to open. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
10371 | 2007 | 5 | 6 | 0.38333 |  | 208 | 827 | 1000 | KANATA MTS | 27.6/16kV | 624F4 | Defective Switch S639 and white phase cable caused the 624F4 circuit to trip. Circuit sectionalized to restore power, and repairs made to switch. White phase cable isolated between transformer 38 and 259. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8310 | 2006 | 5 | 17 | 0.38194 |  | 232 | 39 | 10 | Kanata | 27.6/16kV | 624F4 | Transformer TE157R on Lisbon St isolated for replacement due to oil leak. | Kanata | Scheduled Outage | Repair
8428 | 2006 | 6 | 5 | 0.57778 |  | 53 | 6 | 7 | Kanata | 27.6/16kV | 624F4 | Transformer T246R on Pickford Dr isolated for replacement due to oil leak. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
12677 | 2008 | 6 | 16 | 0.87708 |  | 219 | 4833 | 3000 | Kanata MTS | 27.6/16kV | 624F4 | Kanata 624F4, which was supplying load normally supplied by Marchwood MWDF2 tripped. Scada showed a 2 phase fault at the station. Downstream FCI's showed 3 phase faults. Load restored in stages using FCI's at SC2260-L4, S486-2 (B&R), S486-1 (RWB), S330-1 (RWB), S69, S28 & S87 all gave clear indications. FCI's indicated possible fault between S330, S69 & S28, these cables all tested OK. Remaining cable sections were also tested & overhead portion patrolled to restore remaining customers. | Kanata | Unknown/Other | No Apparent Cause
8577 | 2006 | 6 | 22 | 0.35417 |  | 150 | 12 | 5 | Kanata | 27.6/16kV | 624F4 | Transformer located at 1780 Maple Grove isolated due to upgrading transformer | Kanata | Scheduled Outage | Preventive Maintenance
10713 | 2007 | 6 | 23 | 0.15972 |  | 286 | 1706 | 1000 | Kanata | 27.6/16kV | 624F4 | Customer calls indicated an outage downstream of S104. The crew found no potential at S104, went back to S51 & found no pot. Went back to dip pole S147 & found the red phase open. The fault indicator at S51 was clear indicating a possible cable fault between S51 & 147R. This sectiion was isolated & power restored from an alternate source.Due to gang operated switches, the single phase outage was expanded to all three phases while switching to alternate supply. At this point, further customer calls indicated a problem from S52-2. S52-2 red phase was found open. A defective cable section between transformer 152R & 4247R was isolated & all power restored. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
16406 | 2010 | 7 | 6 | 0.7125 |  | 449 | 10785 | 3372 | Kanata MTS | 27.6/16kV | 624F4 | Broken insulator at Chimo and Anik caused 624F4 overhead phase to drop into a NIU 8kV overhead circuit. Restoration was encumbered by high load and misleading fault indicators. | Kanata | Defective Equipment | No Apparent Cause
16418 | 2010 | 7 | 7 | 0.45208 |  | 31 | 155 | 300 | Kanata MTS | 27.6/16kV | 624F4 | While switching 624F4 circuit to normal white phase fuse opened at switch #147. No apperant cause at this time. | Kanata | Unknown/Other | No Apparent Cause
12879 | 2008 | 7 | 18 | 0.24236 |  | 25 | 1250 | 3000 | Kanata MTS | 27.6/16kV | 624F4 | lightning activity in the area, Caused the 624F4 breaker to open. Closed the breaker after sectionalizing. | Kanata | Adverse Weather | Lightning
9197 | 2006 | 9 | 11 | 0.65972 |  | 57 | 866 | 1000 | Kanata | 27.6/16kV | 624F4 | Target Constuctiion pulled down the overhead conductor at Maplegrove and Huntmar. | Kanata | Foreign Interference | Vehicle
9287 | 2006 | 9 | 24 | 0.42431 |  | 41 | 410 | 600 | Kanata | 27.6/16kV | 624F4 | Tree fell into the O/H at Grey and Campeau. | Kanata | Adverse Weather | Wind
13396 | 2008 | 10 | 20 | 0.38056 |  | 406 | 41 | 6 | Kanata | 27.6/16kV | 624F4 | Transformer 56 at 26 Young failed, crew replaced xfmr, during restoration, customers complained of overvoltage, crew forgot to adjust taps on transformer, crews adjusted taps and restored xfmr56 to normal. 6 customers affected. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
13449 | 2008 | 10 | 28 | 0.88889 |  | 109 | 1017 | 560 | KANATA | 27.6/16kV | 624F4 | SWITCH CLOSED BY BILL SEAMAN | Kanata | Adverse Weather
13494 | 2008 | 10 | 28 | 0.87569 |  | 4 | 37 | 560 | Kanata | 27.6/16kV | 624F4 | CLOSED THROUGH SCADA | Kanata | Adverse Weather
9763 | 2006 | 12 | 1 | 0.42708 |  | 392 | 62 | 49 | Kanata | 27.6/16kV | 624F4 | A defective transformer 979 B phase @ 198 Walden There was also a bad secondary feeding 205 Walden, to isolate this transformer 4 other transformer in that area had to off for app 5 min because of temperature of -1. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
9862 | 2006 | 12 | 19 | 0.38194 |  | 50 | 2 | 2 | Kanata | 27.6/16kV | 624F4 | Transformer located at Palladium & Silver Seven isolated to connect temporary service | Kanata | Scheduled Outage | Construction
6302 | 2005 | 3 | 17 | 0.52222 |  | 106 | 21 | 20 | Kanata | 27.6/16kV | 624F5 | A. Cooney reports S111B phase fuse found open, also TX384 fuse found blown. S111B was refused and closed at 12:32. Restoring approx 20 customers. Possible animal contact at transformer #384. 624F5 circuit carring MWDF3 & MWDF4 load also. Location of transformer as at 36 O'Hara st. A. Cooney reports TX384 switch replaced. All power restored on O'Hara & Rochon st. | Ottawa | Foreign Interference | Animal
6308 | 2005 | 3 | 21 | 0.70486 |  | 75 | 188 | 150 | Kanata mts | 27.6/16kV | 624F5 | M. Byers reports RX2009 found flashed over on RX2009 reclosure. Approx 150 customers affected in power outage. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6314 | 2005 | 3 | 23 | 0.36875 |  | 179 | 156 | 150 | Kanata MTS | 27.6/16kV | 624F5 | Defective overhead transformer 358 on O'Hara caused sw 111B and reclosure RX2009 to open. Tx 358 replaced. | Kanata | Defective Equipment
14098 | 2009 | 3 | 25 | 0.53889 |  | 8 | 1 | 5 | Kanata | 27.6/16kV | 624F5 | While attrmpting to perform a PC14, B Seaman was instructed to operate SC2512-L3, when doing so, the SC2512-CB4 opened. Inturupting 5 transformers on Legget Dr. Load restored by closing the SC2512-CB4. | Kanata | Unknown/Other
14139 | 2009 | 4 | 2 | 0.75208 |  | 642 | 11 | 1 | Kanata | 27.6/16kV | 624F5 | At 6:08pm TP4820 at 1001 Farara was isolated to allow | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20322 | 2012 | 4 | 13 | 0.75 |  | 151 | 5 | 2 | Kanata | 27.6/16kV | 624F5 | Hydro Ottawa crews opened transformers TP6649B & TP6650 so that cut outs, elbows & inserts could be replaced. | Kanata | Scheduled Outage | Preventive Maintenance
8213 | 2006 | 5 | 2 | 0.022222 |  | 88 | 16 | 11 | Kanata | 27.6/16kV | 624F5 | The S189-1 switch at Solandt and Hines opened up for no aparent cause | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8214 | 2006 | 5 | 2 | 0.26319 |  | 40 | 7 | 11 | Kanata | 27.6/16kV | 624F5 | S189-1 opened interrupting load to 11 transformers. SC2512-L2 closed to restore load to customers on Leggett Drive. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14311 | 2009 | 5 | 6 | 0.39583 |  | 160 | 5 | 2 | Kanata | 27.6/16kV | 624F5 | Transformer T4820 @ 1001 Farrar was isolated to change transformer. | Kanata | Scheduled Outage | Repair
18804 | 2011 | 7 | 23 | 0.85903 |  | 173 | 275 | 166 | Kanata | 27.6/16kV | 624F5 | S177 switch gear failed. Causing outage on 624F5 circuit. While restoring load to 624F5 circuit. 624F6 opened during power restoration of customers load on Leggett. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
15049 | 2009 | 9 | 2 | 0.4125 |  | 641 | 534 | 50 | Kanata | 27.6/16kV | 624F5 | 4 Transformers in Marsh Sparrow area were isolated for soil remediation of 2164 transformer | Kanata | Scheduled Outage | Repair
13873 | 2009 | 1 | 16 | 0.32153 |  | 154 | 103 | 40 | Kanata | 12/7.2kV | 624F6 | 12 kv single phase line on Sixth Line Rd fell down causing S13487 to blow on low side of rabbit WX2035. Radial line section was isolated at rabbit & repaired. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
13910 | 2009 | 1 | 31 | 0.91667 |  | 250 | 64 | 26 | Kanata | 27.6/16kV | 624F6 | Transformer 2164 and 2165 @ 72 Marsh Sparrow Priv was push of there pedestal by snow removing equipment. | Kanata | Foreign Interference | Dig-in
19961 | 2012 | 2 | 4 | 0.50278 |  | 116 | 39 | 20 | Kanata | 27.6/16kV | 624F6 | At 12:04 switch 240 W at 18 Hardwood Lane blew due to animal contact. Crews refused and restored power to 20 customers. Kanata MTS 624F6 ID# 19961 | Kanata | Foreign Interference | Animal
19962 | 2012 | 2 | 4 | 0.96875 |  | 15 | 0 | 1 | Kanata | 27.6/16kV | 624F6 | Crews found fuse half blown, refused and closed | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19977 | 2012 | 2 | 7 | 0.45833 |  | 100 | 3 | 2 | Kanata | 12/7.2kV | 624F6 | Replaced blown fuse feeding transformer 003196 at 1869 Dunrobin Rd (squirrel contact) | Kanata | Foreign Interference | Animal
20015 | 2012 | 2 | 14 | 0.59375 |  | 200 | 20 | 6 | Kanata | 27.6/16kV | 624F6 | At 350 Berry Side rd, 216R, 336R blown, 215 R also found blown but had not dropped down. All replaced & power restored. Squirrel contact, 6 cust. | Kanata | Foreign Interference | Animal
20020 | 2012 | 2 | 15 | 0.39861 |  | 86 | 9 | 6 | Kanata | 12/7.2kV | 624F6 | At 9:34 a squirrel cause three fuses to blow at 350 Berry Side Rd. Crew refused and restored power. Kanata MTS, 624F6 ID# 20020 | Kanata | Foreign Interference | Animal
17590 | 2011 | 2 | 16 | 0.18125 |  | 424 | 64 | 9 | Kanata MTS | 27.6/16kV | 624F6 | Replaced defective transformer 1715W on Billingham in Kanata. | Kanata | Defective Equipment
17614 | 2011 | 2 | 18 | 0.87153 |  | 422 | 2279 | 411 | Kanata MTS | 27.6/16kV | 624F6 | 624F6 auto reclosed, tree fallen across on three phase primary cct on Dunrobin Road. 624F6 cct, auto reclosed twice and RX2007 tripped. Circuit isolated tree removed, and all power restored. | Kanata | Tree Contacts
17628 | 2011 | 2 | 20 | 0.84861 |  | 20 | 0 | 1 | Kanata MTS | 27.6/16kV | 624f6 | Transformer X37488 was opened to allow crew to replace leads. | Kanata | Defective Equipment
15781 | 2010 | 3 | 8 | 0.52778 |  | 134 | 11 | 11 | Kanata | 27.6/16kV | 624F6 | at 12:40, transformer TP3003 at 361 Kinghorn was Isolated to allow crews to replace it. Struck by Plow in the winter. 11 customers affected for 134 minutes. Kanata (624F6) ID #15781 | Kanata | Foreign Interference | Vehicle
15782 | 2010 | 3 | 8 | 0.52083 |  | 140 | 26 | 11 | Kanata | 27.6/16kV | 624F6 | Transformer #TP3003 located at 361 Kinghorn Cres isolated to replace transformer | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8060 | 2006 | 3 | 24 | 0.3625 |  | 288 | 5 | 1 | Kanata | 27.6/16kV | 624F6 | Transformer #3923 located at 48 Richardson Side Rd isolated to repair a neutral that is down | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
17805 | 2011 | 3 | 30 | 0.21528 |  | 290 | 5 | 1 | Kanata MTS | 27.6/16kV | 624F6 | Transformer TP3923 @ 48 Richardson rd opened due to a faulty arrestor. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
17907 | 2011 | 4 | 11 | 0.65833 |  | 224 | 34 | 9 | Kanata MTS | 8/4.8kV | 624F6 | Tree contacts caused the red, white and blue phase rabbits on Riddell to open. | Kanata | Tree Contacts | Tree Limb Fallen
18064 | 2011 | 4 | 30 | 0.49653 |  | 115 | 2 | 1 | Kanata | 27.6/16kV | 624F6 | Switch 3604 was isolated to allow crew to remove trees from lines. 1 customer was affected for minutes. Kanata (624F6) ID#18064. | Kanata | Adverse Weather | Wind
16067 | 2010 | 5 | 8 | 0.37083 |  | 531 | 97 | 11 | Kanata | 12/7.2kV | 624F6 | crew replaced defective WX2015 white phase rabbit, 11 customers affected on Riddell and Sixth line. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8354 | 2006 | 5 | 25 | 0.55556 |  | 65 | 10 | 9 | Kanata | 27.6/16kV | 624F6 | Transformer TP2781 at 622 Aberfoyle isolated for replacement due to oil leak at bushing. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
16172 | 2010 | 6 | 1 | 0.38889 |  | 70 | 1 | 1 | Kanata | 27.6/16kV | 624F6 | Padmount transformer at 2206 Sixth Line was reported defective during the night but customer requested work be done during the day. Transformer 1292 replaced by Kanata crew. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
18271 | 2011 | 6 | 1 | 0.55208 |  | 123 | 2 | 1 | Kanata MTS | 27.6/16kV | 624F6 | Transformer #X40207 located at 1913 Dunrobin Rd opened up due to tree contact. | Kanata | Tree Contacts | Inadequate Trimming
20662 | 2012 | 6 | 1 | 0.29583 |  | 164 | 3 | 1 | Kanata | 27.6/16kV | 624F6 | Replaced broken dead end insulator at transformer X39675 at 325 Barry Side Rd | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
18309 | 2011 | 6 | 6 | 0.28542 |  | 210 | 7 | 2 | Kanata | 27.6/16kV | 624F6 | Transformer #X39577 located at 17 Mowbray opened up due to squirrel contact. | Kanata | Foreign Interference | Animal
14482 | 2009 | 6 | 7 | 0.33056 |  | 199 | 3 | 1 | Kanata MTS | 27.6/16kV | 624F6 | Transformer #3336 located at 360 Berry Side Rd isolated due to interference from vines | Kanata | Tree Contacts | Inadequate Trimming
8449 | 2006 | 6 | 8 | 0.125 |  | 160 | 3 | 1 | Kanata | 27.6/16kV | 624F6 | Transformer T3923 at 48 Richardson Side Rd isolated to investigate blown B phase fuse, no problems located and power restored. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20746 | 2012 | 6 | 12 | 0.3625 |  | 182 | 24 | 8 | Kanata | 27.6/16kV | 624F6 | Switch 126B and 2130 located 269 and 273 Pinhey Point Rd opened up due to raccoon contact. | Kanata | Foreign Interference | Animal
20752 | 2012 | 6 | 12 | 0.71597 |  | 96 | 46 | 29 | Kanata | 27.6/16kV | 624F6 | A limb made contact with the O/H causing the fuse to blow at 111b phase 1048 KERWIN RD. | Kanata | Tree Contacts | Tree Limb Fallen
20754 | 2012 | 6 | 12 | 0.79306 |  | 60 | 1 | 1 | Kanata | 27.6/16kV | 624F6 | Transformer X07397 at 2060 Fifth Line Rd. isolated to change cut-out. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20781 | 2012 | 6 | 16 | 0.77569 |  | 228 | 4 | 1 | Kanata | 27.6/16kV | 624F6 | 624F6 A/R, OFD reports sparking transformer at 910 march Rd, crews defective lead burnt off fused cut out. Replace cutout and refused. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20800 | 2012 | 6 | 19 | 0.34167 |  | 237 | 39 | 29 | Kanata | 27.6/16kV | 624F6 | Switch 111B found blown, patrol of line found bad Tx at 4 O'Hara, X39591. 111B replaced restoring most customers. X39591 replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
12699 | 2008 | 6 | 20 | 0.3875 |  | 116 | 242 | 125 | Kanata | 27.6/16kV | 624F6 | S394 was isolated to allow crew to pull new primary cable into sectionalizer | Kanata | Scheduled Outage | Preventive Maintenance
16309 | 2010 | 6 | 21 | 0.39514 |  | 93 | 42 | 27 | Kanata F6 | 27.6/16kV | 624F6 | Transformers 1524, 1528, 1532, 1533 on Monaghan Lane were isoalted for elbow and insert replacement. | Kanata | Scheduled Outage
16320 | 2010 | 6 | 23 | 0.40278 |  | 128 | 4 | 2 | Kanata | 27.6/16kV | 624F6 | Transformer 1464 at 20 Marchbrook was isoalted to replace elbows and inserts. | Kanata | Scheduled Outage
18516 | 2011 | 6 | 24 | 0.85833 |  | 269 | 40 | 9 | Kanata MTS | 27.6/16kV | 624F6 | S25743 blew due to fallen trees into conductors. Kanata (624F6) ID#18516 | Kanata | Lightning
16288 | 2010 | 6 | 25 | 0.38194 |  | 175 | 6 | 2 | Kanata | 27.6/16kV | 624F6 | transformer 1471 at 40 Marchbrook Circ. Was isolated to allow crews to change inserts and elbows | Kanata | Scheduled Outage | Preventive Maintenance
16290 | 2010 | 6 | 25 | 0.50417 |  | 141 | 5 | 2 | Kanata | 27.6/16kV | 624F6 | transformer 1459 at 4 Marchbrook Circ.was isolated to allow crews to change elbows and inserts | Kanata | Scheduled Outage | Preventive Maintenance
20871 | 2012 | 6 | 26 | 0.37153 |  | 81 | 39 | 29 | Kanata | 27.6/16kV | 624F6 | Switch 111B at Kerwin and O'Hara was found open due to Crow contact. | Kanata | Foreign Interference | Bird
14665 | 2009 | 7 | 4 | 0.29167 |  | 199 | 10 | 3 | Kanata MTS | 27.6/16kV | 624F6 | Transformer #X7284 located at 1085 Riddell Dr isolated, no cause found | Kanata | Unknown/Other | No Apparent Cause
18805 | 2011 | 7 | 23 | 0.92361 |  | 3 | 77 | 1535 | Kanata | 27.6/16kV | 624F6 | While restoring 624F5 load, 624F6 ciruit opened during power restoration. Due to switching center S177 failure. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14833 | 2009 | 7 | 24 | 0.95833 |  | 222 | 4 | 1 | Kanata | 27.6/16kV | 624F6 | Transformer X39510 at 2006 Sixth Line cut out was blown due to adverse weather. | Nepean | Adverse Weather
18816 | 2011 | 7 | 25 | 0.54028 |  | 14 | 358 | 1535 | Kanata |  | 624F6 | While performing and order to restore S177 a set of grounds was left on at transformer 235 in error and became energized when the oder was being performed | Kanata | Human Element | Switching Errors
14879 | 2009 | 7 | 29 | 0.73194 |  | 346 | 6 | 1 | Kanata MTS | 27.6/16kV | 624F6 | Transformer #X36611 located at 2160 Sixth Line Rd isolated due to lightning strike | Kanata | Adverse Weather | Lightning
16783 | 2010 | 8 | 20 | 0.020139 |  | 93 | 11 | 7 | Kanata MTS | 27.6/16kV | 624F6 | crew refused switch S126B on Phiney point rd, feeding customers on Sixth line rd. No cause was found. | Kanata | Unknown/Other | No Apparent Cause
16785 | 2010 | 8 | 20 | 0.39931 |  | 85 | 14 | 10 | Kanata | 27.6/16kV | 624F6 | Transformer 1688R @ 1420 Houston Cres was isolated to change transformers elbows & inserts. | Kanata | Scheduled Outage | Construction
11210 | 2007 | 8 | 30 | 0.14583 |  | 255 | 478 | 200 | Kanata | 27.6/16kV | 624F6 | Red phase cable fault between S251-4 & S292-4 @ Shirley Brook & March Rd. Outage was expanded to HI pot cable section between S251 & S292. All power restored @ 04:16 | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19055 | 2011 | 8 | 30 | 0.48611 |  | 132 | 125 | 57 | Kanata MTS | 27.6/16kV | 624F6 | Animal contact at transformer X06940 caused switch S24972 to open. Kanata (624F6) ID#19055 | Kanata | Foreign Interference | Animal
9198 | 2006 | 9 | 11 | 0.67014 |  | 32 | 320 | 600 | Kanata | 27.6/16kV | 624F6 | Opened 3080-L3 to separate F4 from F6. SCADA showed switch time out failed to open. Misreading of maps. Switch did open and load loss of 624F6 load. F6 breaker closed to restore load. | Kanata | Human Element | Switching Errors
15104 | 2009 | 9 | 14 | 0.89375 |  | 412 | 27 | 4 | Kanata MTS | 27.6/16kV | 624F6 | X37479 at 840 Berry Side Rd Hit by Lightning. PC10A #3669 used by Magee at S15431 to isolate and replace transformer | Kanata | Adverse Weather | Lightning
15120 | 2009 | 9 | 17 | 0.54861 |  | 138 | 2 | 1 | Kanata | 27.6/16kV | 624F6 | Overhead line at 1620 Sixth Line isolated from S363 to remove fallen tree. Tree removed and power restored. | Kanata | Tree Contacts | Tree Fallen
19209 | 2011 | 9 | 19 | 0.82986 |  | 105 | 100 | 57 | Kanata | 27.6/16kV | 624F6 | A defective fuse barrell at 1240 Old Carp rd, transformer X06948 caused S24972 to blow. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11355 | 2007 | 9 | 21 | 0.42847 |  | 18 | 120 | 400 | Kanata | 27.6/16kV | 624F6 | SC3080-L2 opened after RTU & Radio connections were disconnected. Overhead circuit was patrolled NO fault found. | Kanata | Unknown/Other | No Apparent Cause
19227 | 2011 | 9 | 21 | 0.36458 |  | 75 | 2 | 2 | Kanata | 27.6/16kV | 624F6 | Isolated transformer X07178 at 13 Campbell Reid Crt for a service up-grade | Kanata | Scheduled Outage | Emergency Services Request
7386 | 2005 | 9 | 27 | 0.68958 |  | 114 | 2 | 1 |  | 27.6/16kV | 624F6 | 624F6 scada ind circuit auto reclosed. Scada indicates all load restored. No reports of outages at this time. At 17:13 dispatched report customer called from 750 March Rd reporting outage. J Streng dispatched to area. John reports blown arresterat this location. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
15188 | 2009 | 9 | 29 | 0.41042 |  | 163 | 56 | 35 | Kanata MTS | 27.6/16kV | 624F6 | Tree on the wire at Phiney Point caused low side fuse S13487 on step down transformer to blow. Switch S126 tagged PC10 A to remove tree from line. | Kanata | Tree Contacts | Tree Fallen
15198 | 2009 | 10 | 2 | 0.52083 |  | 100 | 3 | 2 | Kanata | 27.6/16kV | 624F6 | Transformer #X36823 located at 1055 Klondike & X06882 located at 1062 Klondike isolated to re-arrange plant. | Kanata | Scheduled Outage | Construction
17109 | 2010 | 10 | 13 | 0.42708 |  | 57 | 5 | 5 | Kanata | 27.6/16kV | 624F6 | Transformer #X06943 located at 1216 Old Carp Rd opened up due to animal contact (squirrel) | Kanata | Foreign Interference | Animal
9521 | 2006 | 10 | 26 | 0.19792 |  | 123 | 955 | 400 | Kanata | 27.6/16kV | 624F6 | 624F6 feeder A/R/A due to faulted sectionalizer switch S267 at Herzburg & Terry Fox. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
15350 | 2009 | 11 | 3 | 0.57361 |  | 72 | 4 | 3 | Kanata | 27.6/16kV | 624F6 | Transformer #X7176 located at 6 Campbell Reid Crt isolated due to tree contact | Kanata | Tree Contacts | Inadequate Trimming
13558 | 2008 | 11 | 4 | 0.39444 |  | 330 | 6 | 1 | Kanata | 12/7.2kV | 624F6 | WX2015 Blue phase rabbit failed causing an outage to 1 customer, A Cooney swung the customer to the White phase and power restored. B phase rabbit remains isolated | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
15384 | 2009 | 11 | 13 | 0.41667 |  | 10 | 0 | 2 | Kanata | 27.6/16kV | 624F6 | Transformer #X06884 located at 1083 Klondike isolated for clearances. | Kanata | Scheduled Outage | Construction
19596 | 2011 | 11 | 18 | 0.54375 |  | 67 | 2 | 2 | Kanata | 27.6/16kV | 624F6 | Replaced blown fuse feeding transformer X40084 at 10 Mowbray St due to Squirrel contact | Kanata | Foreign Interference | Animal
19661 | 2011 | 12 | 2 | 0.50625 |  | 155 | 3 | 1 | Kanata MTS | 27.6/16kV | 624F6 | Crew found a tree limb on a customer owned primary at 2215 Sixth line Rd which caused an auto reclose on RX2009 and blew the fuses 746 where the primary runs into the customer property. KANATA (624F6) ID# 19661 | Kanata | Tree Contacts | Tree Limb Fallen
17396 | 2010 | 12 | 9 | 0.32431 |  | 111 | 33 | 18 | Kanata | 27.6/16kV | 624F6 | switch 239B at 2145 fifth line rd in Kanata opened. Crew found no apparent cause for blow, suspect possible load issues. | Kanata | Unknown/Other | No Apparent Cause
15495 | 2009 | 12 | 10 | 0.54167 |  | 306 | 211 | 145 | KANATA MTS | 27.6/16kV | 624F6 | At 9:32 crews opened S13586 to install a new step down transformer WX2037. When crew was closing S19826 to restore customers a new 21Kv Arrestor Blew causing RX2009 to open. Crew also found a bad transformer X36607 affecting 1 customer. | Kanata | Scheduled Outage | Construction
7724 | 2005 | 12 | 14 | 0.42014 |  | 140 | 152 | 65 | Kanata | 27.6/16kV | 624F6 | Replacement of defective sectionalizer S394, outage to 9 Transformers on Shirley Brook, Catterick,in Kanata. | Kanata | Scheduled Outage
13776 | 2008 | 12 | 17 | 0.57292 |  | 1245 | 21 | 1 | Kanata MTS | 27.6/16kV | 624F6 | Customer at 22 Richardson Side rd required isolation to clean & repair defective switchgear after arcing caused 2 fuses to blow at primary dip switch 261. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
15532 | 2009 | 12 | 20 | 0.35208 |  | 94 | 2 | 1 | Kanata MTS | 27.6/16kV | 624F6 | Bird contact caused o/h transformer feeding 351 sandhill to open. | Kanata | Foreign Interference | Animal
15536 | 2009 | 12 | 20 | 0.80556 |  | 80 | 1 | 1 | KANATA | 27.6/16kV | 624F6 | Outage report by customer at 9 Campbell Reid, crews found tree interference, limbed trouble area and refused. | Kanata | Tree Contacts
11522 | 2007 | 10 | 15 | 0.35972 |  | 262 | 4 | 1 | Kanata | 27.6/16kV | 624F6 (MWDF 3) | Transformer #781 located at 1235 March Rd isolated due to broken SMU switch | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
7725 | 2005 | 12 | 14 | 0.58333 |  | 4 | 73 | 1100 | Kanata | 27.6/16kV | 624T2 BUS | 624B1-B2, 624F4, 624F5, 624F6, tripped due to commissioning testing at Kanata MTS by station crew. Power restored by SCADA. | Kanata | Human Element
20844 | 2012 | 6 | 23 | 0.081944 |  | 163 | 8 | 3 | Slater | 13.2kV | 625 | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
4070 | 2003 | 9 | 6 | 0.98472 |  | 617 | 21 | 2 | Slater | 12/7.2kV | 625 | 13 kv vault VT307 at 240 Sparks isolated for customer to perform major maintenance. | Ottawa | Scheduled Outage
14262 | 2009 | 4 | 29 | 0.82986 |  | 178 | 3 | 1 | Slater | 13.2kV | 626 | VT23 at 141 Laurier isolated for crew to replace defective transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4007 | 2003 | 9 | 4 | 0.38889 |  | 882 | 28 | 15 | Slater | 13.2kV | 626 | Fault on 13 kv switchgear at VT510 (180 Elgin) caused circuit 626 to be automatically removed from service. The defective vault was isolated & the remaining customers were restored. Siemens-Westinghouse repaired switchgear with Hydro Ottawa cable crew redoing cable terminations in the vault. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3154 | 2003 | 2 | 2 | 0.64792 |  | 902 | 30 | 2 | Slater TS | 13.2kV | 628 | 13 kv breaker found open at VT159 60 Queen st. Vault relay ind. R&W phase inst. Water found on open transformer bus. Tracked across to ground. Building electrian to repair same. Esa Ralph Danis ok verbal to energize vault. | Ottawa | Adverse Environment | Flooding
20841 | 2012 | 6 | 23 | 0.081944 |  | 153 | 41 | 16 | Slater |  | 628 | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
15209 | 2009 | 10 | 4 | 0.31458 |  | 145 | 12 | 5 | Slater | 13.2kV | 628 | At 7:33am SCADA indicates TS37 breaker opened. After trying first cable out from station and breaker opening again under fault. 24-7 proceeded to isolate cable fault between TS & 628-L1 at VT581 55 Metcalfe restoring power to 5 customers at 9:58am. Slater (TS37) ID#15209. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4372 | 2003 | 11 | 3 | 0.00625 |  | 61 | 1 | 1 | Slater | 12/7.2kV | 628 | 24/7 reported arching sound from pot fuse on restoration of vault. On call crew came in to repair contacts. | Ottawa | Defective Equipment
7823 | 2006 | 1 | 19 | 0.047917 |  | 59 | 1180 | 1200 | Casselman | 8/4.8kV | 62M2 | Hydro One outage to 62M2 feeder which supplies Casselman DS to make temperary repairs to 2 damaged poles. | Casselman | Loss of Supply | HEPC Circuit Fault
12008 | 2008 | 2 | 4 | 0.39444 |  | 6 | 120 | 1200 | Castleman | 8/4.8kV | 62M2 | Hydro One reports 230 Line trip causing loss of supply to Castleman | Castleman | Loss of Supply | HEPC Circuit Fault
6188 | 2005 | 2 | 8 | 0.18403 |  | 185 | 3083 | 1000 | V11 | 44kV | 62M2 | Hydro One reports 62M2 circuit has locked out. Pole fire at Rose DS. | Castleman | Loss of Supply | HEPC Circuit Fault
17565 | 2011 | 2 | 9 | 0.078472 |  | 35 | 1 | 2 | Casselman | 8/4.8kV | 62M2 | Loss of supply to transfer customers on Route 500 East in Casselman fed from a recloser. Hydro One dispatched crew and restored power. Actual 8kV circuit not identified on any of our maps. | Castleman | Loss of Supply
16695 | 2011 | 2 | 12 | 0.44722 |  | 121 | 2823 | 1400 | Casselman MS | 8/4.8kV | 62M2 | Hydro One reports broken hydro pole on backup supply to Casselman MS (Crysler supply). Emergency repairs are required to replace broken pole. Normal supply still has faulted overhead section between Rose Corners DS & Casselman MS. | Casselman | Loss of Supply | HEPC Circuit Fault
17575 | 2011 | 2 | 13 | 0.52639 |  | 19 | 443 | 1400 | Casselman | 8/4.8kV | 62M2 | Casselman DS was offloaded in order for Hydro One crew to switch the 62M2 44kV supply to the normal feed. | Castleman | Scheduled Outage
14195 | 2009 | 4 | 21 | 0.19097 |  | 145 | 3606 | 1492 | Casselman | 8/4.8kV | 62M2 | A section of Hydro One circuit 62M2 fell to the ground causing an outage to Casselman DS. Repairs made and circuit energized. | Castleman | Loss of Supply
18081 | 2011 | 4 | 28 | 0.65278 |  | 720 | 17304 | 1442 | Casselman | 8/4.8kV | 62M2 | Loss of supply on the 62M2 from HydroOne caused Casselman MS outage. | Castleman | Loss of Supply | HEPC Circuit Fault
12810 | 2008 | 7 | 9 | 0.73264 |  | 170 | 2833 | 1000 | V11 Castleman | 44kV | 62M2 | Hydro One had a loss of supply on the 62M3/M4 tied circuits. Hydro One performed switching to restore Castleman, power was restored at 20:25, 1000 customers affected. H1 patrolling for permanent fault in the Winchester area. | Castleman | Loss of Supply | HEPC Circuit Fault
14766 | 2009 | 7 | 16 | 0.73194 |  | 10 | 253 | 1520 | Casselman | 44kV | 62M2 | Hydro One report there 230 Kv circuit feeding the 62M2 out of St. Isadore tripped, causing loss of supply to Casselman DS. | Castleman | Loss of Supply | HEPC Circuit Fault
8841 | 2006 | 7 | 25 | 0.61597 |  | 118 | 2360 | 1200 | Casselman | 8/4.8kV | 62M2 | Hydro One outage to 62M2 feeder which supplies Casselman DS, blown insulatorand pole fire. | Castleman | Loss of Supply | HEPC Circuit Fault
8842 | 2006 | 7 | 25 | 0.70278 |  | 22 | 440 | 1200 | Casselman | 8/4.8kV | 62M2 | Hydro One interupted the 62M2 and Casselamn DS to extinguish fire and replace blown insulator. | Castleman | Loss of Supply | HEPC Circuit Fault
3831 | 2003 | 8 | 3 | 0.15625 |  | 42 | 560 | 800 | Casselman DS | 44kV | 62M2 | Hydro One had their 230Kv ckts trip which feed St Isadore TS which in turn feed Casselman DS. The fault was caused by flashed insulators of one of their customers. | Castleman | Loss of Supply | HEPC Circuit Fault
5685 | 2004 | 8 | 16 | 0.67361 |  | 1 | 20 | 1200 | V11 | 8/4.8kV | 62M2 | Crews report blown Arrester in the station. Caused 62M2 circuit to lock out. Hydro One reclosed circuit restoring power. Hydro One Failed to call Hydro Ottawa about outage. | Castleman | Loss of Supply | HEPC Circuit Fault
13141 | 2008 | 8 | 22 | 0.59653 |  | 38 | 934 | 1474 |  | 44kV | 62M2 | Bus protection at St Isisdore TS cleared the 44kv bus due to 62M2 breaker failure. Bus was re-energized & 62M2 load restored via tie switch to adjacent cct. | Castleman | Loss of Supply | HEPC Station Fault
4084 | 2003 | 9 | 18 | 0.54792 |  | 11 | 110 | 600 | V11 | 44kV | 62M2 | Hydro One lost supply to Casselman. The 62M2 had a Hold Off on the circuit when it trip. | Castleman | Loss of Supply | HEPC Circuit Fault
16978 | 2010 | 9 | 22 | 0.34028 |  | 10 | 258 | 1550 | Casselman | 8/4.8kV | 62M2 | Customer reported outage, Contacted H1, 62M2 Supply to Casselman Stn was interupted. Cause was corrected and no further interuption expected. | Castleman | Loss of Supply
15359 | 2009 | 11 | 7 | 0.14583 |  | 4 | 102 | 1525 | Rose Corner DS | 44kV | 62M2 | Hydro One had to dump Casselman in order to open a switch at Rose Corner DS. | Casselman | Scheduled Outage
4529 | 2003 | 11 | 28 | 0.0069444 |  | 5 | 100 | 1200 | Casselman | 8/4.8kV | 62M2 | Hydro One report due to MVA on the 44kv from St. Isdore. 62M2 breaker (hydro one) had to be opened to allow crews to make repairs. Approx 1200 customers affected in power outages. | Casselman | Loss of Supply | HEPC Circuit Fault
20840 | 2012 | 6 | 23 | 0.081944 |  | 136 | 7 | 3 | Slater | 13.2kV | 630 | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
4302 | 2003 | 10 | 20 | 0.93542 |  | 5 | 26 | 314 | Beckwith/Wonderland | 27.6/16kV | 631F2 & 630F2 | Hydro One 230Kv circuit M29C auto tripped interupting the supply to the Beckwith F2 & Wonderland F2. | Goulburn | Loss of Supply | HEPC Circuit Fault
16218 | 2010 | 6 | 7 | 0.47569 |  | 294 | 5 | 1 | Slater | 13.2kV | 633 | TN6805CHZ was isolated beacuse a concrete fell on the outdoor vault. Concrete was cleared away, no damage was incurred, and vault was restored. | Ottawa | Foreign Interference | Foreign Object
10026 | 2007 | 2 | 14 | 0.64236 |  | 54 | 7560 | 10000 | King Edward | 13.2kV | 63T3Z | Hydro One load side breaker 63T3Z failed. Which caused an outage on both King Edward Q & Z busses. Q bus was isolated for Hydro One bus maintenance at the time. 24/7 restored Q bus to normal, and isolated TK Z bus load transferred to TK Q bus. | Ottawa | Loss of Supply | HEPC Station Fault
15464 | 2009 | 12 | 3 | 0.39028 |  | 238 | 4 | 1 | Kanata MTS | 12/7.2kV | 642F6 | Trans was replaced at 360 BERRY SIDE ROAD, KANATA due to defective transformer | Kanata | Defective Equipment | Imminent Equipment Failure Detected
14292 | 2009 | 5 | 3 | 0.42361 |  | 10 | 252 | 1513 | Castleman | 44kV | 64M2 | During switching Hydro One had complications while switching which caused loss of supply to Casselman. | Castleman | Loss of Supply
15312 | 2009 | 10 | 26 | 0.5625 |  | 53 | 1344 | 1522 | Casselman | 44kV | 66M2 | The power outage was caused by a motor vechicle accident which caused the 66M2 to auto'd and locked out. | Castleman | Loss of Supply | HEPC Circuit Fault
9990 | 2007 | 2 | 5 | 0.47083 |  | 60 | 1 | 1 | Star Top | 8/4.8kV | 6F1 | Transformer T2642R was hit by vehicle and had to be isolated to reposition it back into place. | Gloucester | Foreign Interference | Vehicle
12159 | 2008 | 3 | 20 | 0.5 |  | 95 | 25 | 16 | Star Top | 8/4.8kV | 6F1 | Transformer #X17702 located at 1541 Star Top isolated due to blown arrestor & bad cut out | Gloucester | Scheduled Outage | Repair
20380 | 2012 | 4 | 24 | 0.48681 |  | 189 | 47 | 15 | Startop | 8/4.8kV | 6F1 | GLTE1432 at 1422 Eastcliffe was isolated to replace leaking Tx. | Gloucester | Scheduled Outage | Repair
20435 | 2012 | 5 | 1 | 0.41667 |  | 254 | 51 | 12 | Star Top | 8/4.8kV | 6F1 | Transformer GLTE1430 at 1497 Meadowbrook Rd. isolated to change leaking transformer | Gloucester | Scheduled Outage
10432 | 2007 | 5 | 20 | 0.90278 |  | 155 | 5 | 2 | Startop | 8/4.8kV | 6F1 | On call crew was called in to replace a defective 600/347 V transformer supplying 1575 Cyrville rd. Customer was part out since 10:23 am. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14415 | 2009 | 5 | 27 | 0.17847 |  | 50 | 1 | 1 | Startop | 8/4.8kV | 6F1 | Switch at transformer TE266, 1257 Algoma rd. on the 6F1 was arching, crew replaced defective switch. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8400 | 2006 | 6 | 1 | 0.4375 |  | 162 | 38 | 14 | Startop | 8/4.8kV | 6F1 | Isolate transformer T1444R @ 1370 Foxwell to replace damaged padmount. | Gloucester | Scheduled Outage | Repair
10522 | 2007 | 6 | 4 | 0.44097 |  | 175 | 258 | 439 | Startop | 8/4.8kV | 6F1 | 6F1 cct tripped, found a blown switch & arrestor at Tx # 530, 1594 Cyrville rd. Equipment cleared from o/h & cct restored. Tx 530 also blown & was replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10524 | 2007 | 6 | 4 | 0.45 |  | 165 | 8 | 3 | Startop | 8/4.8kV | 6F1 | Replaced blown transformer #X17871 located at 1601 Cyrville Rd | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20704 | 2012 | 6 | 6 | 0.40625 |  | 405 | 81 | 12 | Star Top | 8/4.8kV | 6F1 | Isolated and replaced transformer GLTE1956 at 1408 Progress Pl due to oil leak | Gloucester | Scheduled Outage | Repair
10591 | 2007 | 6 | 11 | 0.063889 |  | 85 | 54 | 436 | Sartop | 8/4.8kV | 6F1 | Two faulty lightning arrestors at switch G384 @ 1650 Comstock feeding T2490 caused circuit to open and two fuses at G384 to open. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
8759 | 2006 | 7 | 18 | 0.015972 |  | 386 | 290 | 45 | StarTop | 8/4.8kV | 6F1 | Calls from Star Top Rd. on the 6F1. Crew sent to check problem. Crew reports one phase of G441 on Star Top Rd. open. Crew to refuse and close. | Gloucester | Adverse Weather | Lightning
8768 | 2006 | 7 | 18 | 0.34722 |  | 107 | 9 | 5 | Startop | 8/4.8kV | 6F1 | Transformer #GLTE2490 located at 1650 Comstock isolated due to lightning blew arrestor, replaced fuse | Gloucester | Lightning | Direct Strike
3916 | 2003 | 8 | 12 | 0.74097 |  | 218 | 7 | 2 | Startop | 27.6/16kV | 6F1 | Replace blown transformer | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13104 | 2008 | 8 | 18 | 0.66042 |  | 4 | 29 | 439 | Startop | 8/4.8kV | 6F1 | Startop 6F1 circuit opened due to lightning activityand possiblly Transformer at 1380 cyrville. | Gloucester | Adverse Weather | Lightning
14971 | 2009 | 8 | 20 | 0.42778 |  | 97 | 16 | 10 | Startop |  | 6F1 | TP1442 at 1432 Foxwell isolated from Hydro Ottawa Sources to change defective transformer | Gloucester | Scheduled Outage
11219 | 2007 | 8 | 30 | 0.78264 |  | 34 | 1 | 4 | Startop | 8/4.8kV | 6F1 | Transformer #128 at 1435 Cyrville Rd isolated to allow for repairs to connection at transformer | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3985 | 2003 | 9 | 2 | 0.72917 |  | 55 | 1 | 1 | Startop | 8/4.8kV | 6F1 | Connections at transformer #005817 had to be replaced due to looseness. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19513 | 2011 | 11 | 1 | 0.71319 |  | 148 | 2 | 1 | Startop | 8/4.8kV | 6F1 | 6F1 breaker auto-reclosed and transformer 878 AT 1670 Constock was found open, faulty cut out appears to have been the problem. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7769 | 2005 | 12 | 30 | 0.375 |  | 85 | 4 | 3 | Startop | 8/4.8kV | 6F1 | Isolated transformer TE2125 @ 1499 Startop Rd to replace defective elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
3125 | 2003 | 1 | 20 | 0.5 |  | 20 | 161 | 483 | Startop DS | 8/4.8kV | 6F10 | 6F7, 6F10 Breakers at Startop DS Tripped. Reports of Car accident Ogilvie , Cyrville Rd. and Cummings. Eric Newman reports car accident was earlier and cleared away. Closed breakers and restored power to customers. Crew to finish patrol. At present, high winds are being reported. | Gloucester | Unknown/Other
3129 | 2003 | 1 | 20 | 0.60903 |  | 6 | 48 | 483 | Startop DS | 8/4.8kV | 6F10 | 6F10 breaker tripped under hold off. Hold off removed and closed 6F10 breaker. Cause unknown. High winds at present. | Gloucester | Unknown/Other
13984 | 2009 | 2 | 14 | 0.69236 |  | 413 | 308 | 86 | Startop | 8/4.8kV | 6F10 | 6F10 auto re-closed once. Cause was later determined to be a defective transformer TE966 at 1453 Murdock flashed over from tracking. Fault surge or re-close caused elbow T969WT968 to fault. All but the 4 transformers between the 2 defective points were restored at 17:30. T966 was repaired and power restored to 36 more customers. Repairs then made to TE969 and power restored to remaining customers. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4801 | 2004 | 2 | 18 | 0.39375 |  | 22 | 0 | 1 | Star Top | 8/4.8kV | 6F10 | Transformer 4967 at 1162 Cyrville Rd in Gloucester isolated to repair arcing connection to transformer switch. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7994 | 2006 | 3 | 8 | 0.98542 |  | 278 | 460 | 437 | Startop | 8/4.8kV | 6F10 | Conductor broke at switch G589 at Ogilvie & Cyrville causing the conductor & inline switch to fall on roadway. Damaged section was isolated restoring power to all but 4 transfomers (7 customers). On-call crew made repairs & restored power to the remaining customers. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20152 | 2012 | 3 | 12 | 0.45764 |  | 333 | 350 | 1181 | Startop | 8/4.8kV | 6F10 | 6F10 circuit breaker opened due to blown elbow at TE325 and a defective cable between TE329 and VE24. Crews isolated TE325 and White phase cable between TE329 and VE24 to make repairs. 32 customer were affected for 333 mins. Startop 6F10 ID# 20152 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10124 | 2007 | 3 | 14 | 0.39931 |  | 7 | 51 | 437 | STARTOP | 8/4.8kV | 6F10 | An overhead transformer at 1425 Ogilvie on the 8F2 circuit faulted, the flash caused the 6F10 cicuit to trip but it did not reclose.After the Fire Department reported the blown transformer the breaker was closed from SCADA. The 8F2 breaker also tripped but reclosed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15934 | 2010 | 4 | 14 | 0.36181 |  | 139 | 5 | 2 | STARTOP | 8/4.8kV | 6F10 | Transformer X23906 at 1150 Cyrville isolated to allow for service upgrade | Gloucester | Scheduled Outage | Construction
20497 | 2012 | 5 | 10 | 0.4625 |  | 200 | 17 | 5 | Startop | 8/4.8kV | 6F10 | Transformer TE1544 at 4038 Eady was isolated to allow crew to replace leaking transformer | Gloucester | Scheduled Outage | Repair
16112 | 2010 | 5 | 20 | 0.42708 |  | 39 | 1 | 2 | Startop | 8/4.8kV | 6F10 | Defective sec lug on trans heated up melting the conductor which faulted the trans ,, repairs were made to trans bushing/lead | Gloucester | Defective Equipment
20816 | 2012 | 6 | 20 | 0.74514 |  | 304 | 6752 | 1409 | Startop | 27.6/16kV | 6F10 | 15:06 6F10 opened when primary conductor at corner of Labrie & Cyrville failed. 17:28 Aprox. 1000 customers were transferred to the 6F7 17:53 6F7 overload and tripped 1000 customers were removed from 6F7 and remaind off until circuit was restored at 20:10 Cross reference outage ID # 20817 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18458 | 2011 | 6 | 21 | 0.47222 |  | 350 | 6 | 1 | Startop | 8/4.8kV | 6F10 | Transformer at 1349 Cyrville was isolated due to contractor dig in. 1 customer was affected for 350 minutes. Startop (6F10) ID# 18458 | Gloucester | Foreign Interference | Dig-in
8639 | 2006 | 7 | 2 | 0.027778 |  | 105 | 280 | 160 | Startop | 8/4.8kV | 6F10 | Lightning strike on the open point switch 410 WB which caused 405 WB to open. | Gloucester | Lightning | Lightening Strike on adjacent circuit
8642 | 2006 | 7 | 2 | 0.25 |  | 155 | 103 | 40 | Startop | 8/4.8kV | 6F10 | Elbow and insert at T960 found blown off from lightning strike on overhead. Power restored to customers and T960 to be repaired by on-call | Gloucester | Lightning | Lightning Strike on Adjacent Circuit Flashed Over
8643 | 2006 | 7 | 2 | 0.43194 |  | 93 | 14 | 9 | Startop | 8/4.8kV | 6F10 | T960 isolated to repair blown insert and elbow from lightning strike earliaer this morning. | Gloucester | Lightning | Direct Strike
16431 | 2010 | 7 | 8 | 0.022917 |  | 707 | 708 | 72 | Star Top | 8/4.8kV | 6F10 | Customer reported outage on Murcdock Gate area, patrol found defective transformer TE968, Isolated and attempted to restore from G10 & 6F7 A/R. Crews hipoted cables and restored customers asuntil fault found from TE1493 to TE965., TE1453 transformer found defective as well and cahnged. All customers restored by 12:20pm | Gloucester | Unknown/Other
12839 | 2008 | 7 | 14 | 0.94861 |  | 105 | 861 | 492 | Startop | 8/4.8kV | 6F10 | The 6F10 on Cyrville/Ogilivie trip, circuit patrol and sectionalized but nothing was found, more should be done in the daylight. | Gloucester | Unknown/Other
6999 | 2005 | 7 | 20 | 0.59861 |  | 643 | 54 | 437 | Startop | 8/4.8kV | 6F10 | 6F10 circuit opened via scada due to a Dump truck hitting a Hydro Pole at the rear of 1055 St. Laurent Blvd. Section of overhead isolated and power restored. Dip pole at the rear of 1055 to be replaced. | Gloucester | Foreign Interference | Vehicle
12956 | 2008 | 7 | 28 | 0.41319 |  | 55 | 2 | 2 | Star Top | 8/4.8kV | 6F10 | Isolated 3-phase transformer bank GL4965 at 1057 Cyrville Rd to replace hotline clamps and stirrups and tighten secondary connections | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
7154 | 2005 | 8 | 17 | 0.44236 |  | 113 | 4 | 2 | Startop | 8/4.8kV | 6F10 | Transformer #GL004965 located at 1020 Ogilvie Rd isolated due to a crow. | Gloucester | Foreign Interference | Bird
19088 | 2011 | 9 | 4 | 0.15903 |  | 74 | 620 | 503 | Startop | 8/4.8kV | 6F10 | 6F10 lightning in the area. | Gloucester | Lightning | Direct Strike
16928 | 2010 | 9 | 12 | 0.72639 |  | 74 | 36 | 29 | Star top | 8/4.8kV | 6F10 | 6F10 at Star Top Sub A/R, 502 customers affected, crews found trees cut down at 1106 Cyrville at damage to G200 Red Phase, G353 opened to allow crews to install temp jump at G200 red phase. | Gloucester | Unknown/Other
9354 | 2006 | 10 | 1 | 0.35417 |  | 140 | 9 | 4 | Startop | 8/4.8kV | 6F10 | Transformer #GL005700 located at 1336 Labrie isolated due to a blown arrestor. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5830 | 2004 | 10 | 7 | 0.66667 |  | 11 | 2 | 12 |  | 8/4.8kV | 6F10 | Crew disconnented a bad secondary service at TE326 - 1033 Adley | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
17326 | 2010 | 11 | 22 | 0.65764 |  | 447 | 975 | 503 | Star Top | 8/4.8kV | 6F10 | at 14:20 6F10 A/R & Tripped OPEN, Patrol found no issues, circuit sectionalized at G680, Breaker closed & held. G680 Closed & Breaker closed A/R x2 the tripped open. Circuit sectionalized at G462, Breaker closed and Held. More extensive patrol found TE335 with damaged Insulators & Arc stranglers. TE335 at 1304 Lotus was isolated and remaining customers restored. After TE335 was restored, cable section between TE335 and V24 was isolated due to cable fault. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13670 | 2008 | 11 | 27 | 0.061806 |  | 288 | 470 | 98 | Startop | 8/4.8kV | 6F10 | Outage caused by a broken insert at T 955 & a broken switch at G 405 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13671 | 2008 | 11 | 27 | 0.26181 |  | 83 | 1 | 1 | Startop | 8/4.8kV | 6F10 | Crew restored power to 97 customers from the previous outage. One 3 phase customer remained out. Crew replaced switch to restore 3 phase customer. | Gloucester | Defective Equipment
9811 | 2006 | 12 | 8 | 0.47014 |  | 56 | 427 | 457 | Startop | 8/4.8kV | 6F10 | 6F10 Breaker tripped, cause unknown. Circuit patrolled. Cummings, Ogilvie and Cyrville Road area affected. | Gloucester | Unknown/Other | No Apparent Cause
8017 | 2006 | 3 | 13 | 0.36458 |  | 30 | 6 | 12 | Startop | 8/4.8kV | 6F2 | Isolated transformer 5576 at 1663 Cyrville Rd to replace stand off insulator | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
6666 | 2005 | 6 | 6 | 0.66806 |  | 83 | 1 | 10 |  | 8/4.8kV | 6F2 | Blown Elbow blue phase at V55 -1440 Cyrville - 10 customers affected. | Gloucester | Defective Equipment
19626 | 2011 | 11 | 23 | 0.71528 |  | 75 | 5 | 4 | Star Top | 8/4.8kV | 6F2 | G128 was opened to isolate X23942 to allow crews to transfer feed from 6F2 to 6F1 | Gloucester | Scheduled Outage | Construction
9951 | 2007 | 1 | 19 | 0.49514 |  | 52 | 2 | 2 | Star Top | 8/4.8kV | 6F4 | Isolated transformer GL 3252 at 1040 Parisien St to replace secondary service connections | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
6152 | 2005 | 1 | 24 | 0.6125 |  | 10 | 1 | 4 | Startop | 8/4.8kV | 6F4 | Transformer 5218 at 1101 Pareisen out for 10 minutes to make repairs at the pole. | Gloucester | Scheduled Outage | Repair
6153 | 2005 | 1 | 24 | 0.61111 |  | 15 | 1 | 3 | Startop | 8/4.8kV | 6F4 | Replaced one connection on the secondary side of the bank of transformers at 1101 Parisien St | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4732 | 2004 | 1 | 25 | 0.97917 |  | 60 | 1 | 1 | Startop | 8/4.8kV | 6F4 | Fire Department reported fire. Cause found to be burnt fuse barrel . 2 switches replaced. Switch G828 transformer 2319 at 1252 Micheal St. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4733 | 2004 | 1 | 26 | 0.38264 |  | 57 | 1 | 1 | Startop | 8/4.8kV | 6F4 | Customer at 1223 Michael St. @ TE2319, Their transfer switch did not operate correctly, which required an emergency shutdown to adjust the switch. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15761 | 2010 | 3 | 2 | 0.9375 |  | 160 | 3 | 1 | Startop | 8/4.8kV | 6f4 | at 22:30, Transformer TP6354 at 1170 Algoma was Isolated with PC10C #2560 to allow contractor to clean up flood damage in customers secondary transformer room. Startop (6F4) ID #15761 | Gloucester | Adverse Environment | Flooding
17978 | 2011 | 4 | 20 | 0.90278 |  | 49 | 10 | 12 | Startop | 8/4.8kV | 6F4 | G510 feeding VE44 at 1151 Parisien was opened to allow crews to replace a defective cut-out. | Gloucester | Defective Equipment
17986 | 2011 | 4 | 22 | 0.65278 |  | 25 | 2 | 6 | Startop | 8/4.8kV | 6F4 | Isolated transformer X23927 at 1155 Joseph Cyr St to replace secondary connections | Gloucester | Scheduled Outage | Preventive Maintenance
5200 | 2004 | 5 | 23 | 0.41667 |  | 100 | 5 | 3 | Startop | 8/4.8kV | 6F4 | Transformer 4729 at 1300 Micheal St out to change lightning arrester and check for hot connections from thermovision. | Gloucester | Scheduled Outage | Preventive Maintenance
18607 | 2011 | 7 | 7 | 0.43056 |  | 21 | 1 | 3 | Startop | 8/4.8kV | 6F4 | Transformer X43543 at 1149 Kenaston St isolated for reconfiguration of circuit | Gloucester | Scheduled Outage | Construction
18653 | 2011 | 7 | 13 | 0.72222 |  | 150 | 8 | 3 | Startop | 8/4.8kV | 6F4 | TP3118 at 1095 Kenaston was isolated to allow crews to transfer the cable to a new pole | Gloucester | Scheduled Outage | Construction
16477 | 2010 | 7 | 15 | 0.92569 |  | 47 | 5 | 6 | Startop | 8/4.8kV | 6F4 | Transformer X24295 @ 1328 Michael was opened to allow crews to clean and replace secondary leads. | Gloucester | Scheduled Outage | Repair
16611 | 2010 | 8 | 3 | 0.53958 |  | 25 | 2 | 6 |  |  | 6F4 | Transformer X24295 at 1303 Michael St isolated for infra-red scanning repairs | Ottawa | Scheduled Outage
7081 | 2005 | 8 | 6 | 0.99375 |  | 5 | 14 | 167 | Moulton | 27.6/16kV | 6F4 | 6F4 breaker open for emergenct repairs to switch G610. Connection to switch burning and opening switch while live considered safety harzard. Kenaston at Marchand. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
16811 | 2010 | 8 | 25 | 0.76667 |  | 187 | 37 | 12 | Startop | 8/4.8kV | 6F4 | Vault VE44 at 1163 Parisien was isolated to allow contractor to perform vault maintenance. | Gloucester | Scheduled Outage
13254 | 2008 | 9 | 17 | 0.37014 |  | 1067 | 39 | 3 | Startop | 8/4.8kV | 6F4 | Defective 3 phase transformer located at 1120 Parisien | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
7361 | 2005 | 9 | 21 | 0.76042 |  | 75 | 11 | 9 | Star Top | 27.6/16kV | 6F4 | Trans GL583 was replaced due to trans leaking oil | Goulburn | Scheduled Outage | Repair
9511 | 2006 | 10 | 25 | 0.46389 |  | 82 | 5 | 4 | STAR TOP | 8/4.8kV | 6F4 | Isolated transf. @ 11 Algoma to rearrange hydro plant | Gloucester | Scheduled Outage | Preventive Maintenance
17204 | 2010 | 11 | 2 | 0.027083 |  | 356 | 955 | 161 | Startop | 8/4.8kV | 6F4 | Truck clipped bell line on the Hwy417 at St Laurent exit causing the 6F4 breaker to trip, broken pole, broken insulators and a broken neutral were repaired over the Hwy417. | Gloucester | Foreign Interference | Vehicle
17209 | 2010 | 11 | 2 | 0.52639 |  | 87 | 1 | 1 | Startop | 8/4.8kV | 6F4 | A vehicle hit a pole damaging the cables feeding V53 which caused one of the phases at G583 to blow. | Gloucester | Foreign Interference | Vehicle
9760 | 2006 | 11 | 30 | 0.98264 |  | 55 | 153 | 167 | Startop | 8/4.8kV | 6F4 | Arrestors at the 6F4 recloser blew causing the 6F4 to A/R/A. Arrestors were cleared and the recloser closed in. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5998 | 2004 | 12 | 9 | 0.45833 |  | 77 | 6 | 5 | Startop | 8/4.8kV | 6F4 | Up-grade to larger transformer from 15 to 25 Location #3657 at 1160 Kenaston St | Gloucester | Scheduled Outage | Construction
7749 | 2005 | 12 | 19 | 0.7375 |  | 243 | 4 | 1 | Startop | 8/4.8kV | 6F4 | Transformer #T2622 located at 4000 Labelle isolated due to a defective cutout | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13802 | 2008 | 12 | 28 | 0.00069444 |  | 22 | 0 | 1 | Startop | 8/4.8kV | 6F4 | Transformer at 1303 Micheal St isolate to allow crew to repair secondary connection. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7785 | 2006 | 1 | 9 | 0.56597 |  | 25 | 3 | 7 | Startop | 8/4.8kV | 6F7 | Dave Howat and Steve Muldoon had to open transformer GL00261 to change connections @ 1018 Cryville Rd | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
3101 | 2003 | 1 | 10 | 0.54861 |  | 100 | 52 | 31 | Startop DS | 8/4.8kV | 6F7 | TE267, 268, 269 on Cummings ave were isolated for working clearance while installing new primary cable at TE267. | Gloucester | Scheduled Outage | Repair
3126 | 2003 | 1 | 20 | 0.5 |  | 20 | 160 | 480 | Startop DS | 8/4.8kV | 6F7 | 6F7, 6F10 Breakers at Startop DS tripped. Report of car accident at Ogilvie, Cummings and Cyrville Road. Eric Newman reports car accident cleared earlier, this was not the cause. Breakers closed restoring load. Eric Newman to finish patrol. | Gloucester | Unknown/Other
15683 | 2010 | 1 | 26 | 0.42778 |  | 119 | 30 | 15 |  |  | 6F7 | TE1077 at 1240 Donald St, was isolated to replace rusty padmount. | Gloucester | Scheduled Outage
15684 | 2010 | 1 | 26 | 0.40625 |  | 150 | 38 | 15 | Startop | 8/4.8kV | 6F7 | Transformer #TE1077 located at 1240 Donald St isolated for transformer replacement | Gloucester | Scheduled Outage | Construction
4758 | 2004 | 2 | 3 | 0.52083 |  | 83 | 4 | 3 | Startop | 8/4.8kV | 6F7 | Tx 347 opened for maintenance at Cummings & Weldon. | Gloucester | Defective Equipment
3225 | 2003 | 3 | 2 | 0.93681 |  | 35 | 280 | 480 | Startop | 8/4.8kV | 6F7 | 6F7 tripped reclosed and locked out. Customer at 1368 Labrie reports seeing sparks. 24/7 inspected line ,could not find any damage. High winds may have caused the lines to slap together. Line to be patrolled again in the daylight. | Gloucester | Adverse Weather | Wind
17672 | 2011 | 3 | 5 | 0.74931 |  | 536 | 63 | 9 | Startop | 8/4.8kV | 6F7 | Snow Plow contact pushed the transformer TE1082 at 4334 Stella off its base. Crews isolated transformer to clean up compacted snow, make repairs and re-set the pad to its base. | Gloucester | Foreign Interference | Vehicle
17985 | 2011 | 4 | 22 | 0.46181 |  | 15 | 0 | 2 | STARTOP | 8/4.8kV | 6F7 | ISOLATED TRANSFORMER X23934 AT 1120 CUMMINGS AVE TO REPLACE SECONDARY CONNECTIONS | Gloucester | Scheduled Outage | Preventive Maintenance
5063 | 2004 | 4 | 27 | 0.44583 |  | 274 | 58 | 20 | Startop | 8/4.8kV | 6F7 | Scheduled outage for construction adding new Subdivisioon | Gloucester | Scheduled Outage | Construction
10360 | 2007 | 5 | 3 | 0.40972 |  | 418 | 139 | 20 | Startop | 8/4.8kV | 6F7 | TP4280 isoalted to allow crews to move transformer & base at Cumming north of Thibault | Gloucester | Scheduled Outage | Construction
12405 | 2008 | 5 | 7 | 0.38333 |  | 200 | 167 | 50 | Startop | 8/4.8kV | 6F7 | Planned outage to 5 transformers on Elaine, Bowmont, Hendon, to replace switches and install smart meters. | Gloucester | Scheduled Outage
12412 | 2008 | 5 | 7 | 0.52222 |  | 121 | 202 | 100 | Startop | 8/4.8kV | 6F7 | Crew replacing switches and meter dept, installing smart meters, in the Stella, Caron St. area. | Gloucester | Scheduled Outage
12432 | 2008 | 5 | 12 | 0.39583 |  | 585 | 58 | 6 | Startop | 8/4.8kV | 6F7 | TE1097 was isolated for oil clean up | Gloucester | Scheduled Outage | Repair
10463 | 2007 | 5 | 25 | 0.40139 |  | 425 | 85 | 12 | Startop | 8/4.8kV | 6F7 | TP4281 @ 984 Cummings was isolated to replace the transformer & base & re-arrange primary plant. | Gloucester | Scheduled Outage | Construction
10491 | 2007 | 5 | 31 | 0.39653 |  | 263 | 44 | 10 | Startop | 8/4.8kV | 6F7 | Transformer TP4282 at 994 Cummings was replaced & cables were reconfigured. | Gloucester | Scheduled Outage | Preventive Maintenance
10639 | 2007 | 6 | 16 | 0.27292 |  | 192 | 42 | 13 | StarTop | 8/4.8kV | 6F7 | Fuse to Transformer GL1822 at 1148 Thibault St was found blown due to a squirrel contact | Gloucester | Foreign Interference | Animal
12685 | 2008 | 6 | 17 | 0.40069 |  | 467 | 54 | 7 | Startop | 8/4.8kV | 6F7 | TP5784 isolated at 4864 Caron to remove transformer and pad for further oil spill cleanup | Gloucester | Scheduled Outage | Emergency Services Request
20817 | 2012 | 6 | 20 | 0.74514 |  | 5 | 89 | 1072 | Startop | 8/4.8kV | 6F7 | 17:27 6F7 auto reclosed when picking up aprox 300 customers from 6F10 + 72 6F7 customers 17:28 6F7 auto reclosed when picking up an additional 300 customers from 6F10 + 72 6F7 customers 17:41 6F7 auto reclosed while carring aprox 1000 customers from the 6F10 + 72 F7 customers 17:53 6F7 opened and locked out, 1000 customers from the 6F10 + 72 F7 customers 17:58 6F10 customers were removed from 6F7 and circuit closed restoring 6F7 to normal (72 customers) Cross reference outage ID # 20816 | Gloucester | Human Element | Incorrect Use of Equipment
12723 | 2008 | 6 | 25 | 0.40833 |  | 419 | 56 | 8 | Startop | 8/4.8kV | 6F7 | Transformer TE1094 at 4301 Stella Cr isolated to replacement transforemr. | Gloucester | Scheduled Outage | Repair
5453 | 2004 | 7 | 6 | 0.55208 |  | 81 | 43 | 32 | Startop | 8/4.8kV | 6F7 | Contractor dug into cable on Cummings while fixing a water main cable was isolated and power restored | Gloucester | Foreign Interference | Dig-in
16610 | 2010 | 8 | 3 | 0.42778 |  | 60 | 12 | 12 | STAR TOP | 8/4.8kV | 6F7 | Transformer X23930 at 1138 Thibault St isolated for infra-red scanning | Gloucester | Scheduled Outage | Preventive Maintenance
11019 | 2007 | 8 | 9 | 0.27431 |  | 105 | 21 | 12 | Startop | 8/4.8kV | 6F7 | Transformer #GL001832 located at 971 Cummings Ave isolated to transfer secondary | Gloucester | Scheduled Outage | Construction
18996 | 2011 | 8 | 22 | 0.60208 |  | 55 | 688 | 750 | Startop | 8/4.8kV | 6F7 | One phase of the new section of primary on the 6F7 fell into the under build 6F4 at the corner of Micheal and Parisien | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19041 | 2011 | 8 | 29 | 0.56736 |  | 6 | 75 | 750 | STARTOP | 27.6/16kV | 6F7 | 6F7 Tripped under holdoff. System closed and held. | Gloucester | Human Element | Incorrect Use of Equipment
4004 | 2003 | 9 | 4 | 0.39653 |  | 267 | 27 | 6 | Startop | 8/4.8kV | 6F7 | Transformers was opened on to repair connections on aecondary. At request of customer. | Gloucester | Scheduled Outage | Repair
11330 | 2007 | 9 | 18 | 0.77639 |  | 234 | 4 | 1 | Startop | 8/4.8kV | 6F7 | TP3837 at 1171 Kenestan was replaced due to oil leak. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
19348 | 2011 | 10 | 9 | 0.30556 |  | 45 | 5 | 6 | Startop | 8/4.8kV | 6F7 | 6F7 CB auto-reclosed due to animal contact at X24295 at 1303 Micheal St. | Gloucester | Foreign Interference
4380 | 2003 | 11 | 4 | 0.54167 |  | 83 | 44 | 32 | Startop | 8/4.8kV | 6F7 | Elbow blew at T269R causing the fuse at G234 to open. Isolate the elbow and restore load from G267R. ID#4380 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4499 | 2003 | 11 | 21 | 0.52083 |  | 130 | 22 | 10 | Startop | 8/4.8kV | 6F7 | Transformer 1089 isolated to replace it due to leaks. | Gloucester | Scheduled Outage | Repair
19627 | 2011 | 11 | 23 | 0.85764 |  | 115 | 4 | 2 | Startop | 8/4.8kV | 6F7 | G556 @ Labell St. Was isolated to allow crew to transfer it from 6F7 to 6F10 for future conversion. | Gloucester | Scheduled Outage | Construction
3240 | 2003 | 3 | 9 | 0.34028 |  | 760 | 3435 | 784 | Startop | 8/4.8kV | 6F7 & 6F10 | The original trouble call was due to a wire down on Labrie Street. This problem was isolated and a bigger trouble call broke out along Innes at Stonehenge so crews were re-routed there. When back on site the crews tried to do switching to get most of the customers back on. While doing this a switch went defective at G411W, Donald and St. Laurent. This cause the circuit to go to lockout. The circuit was left out until repairs were made at both places and then the power was restored to normal. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13402 | 2008 | 10 | 21 | 0.45764 |  | 129 | 371 | 899 | Merivale | 8/4.8kV | 72 T2 | 72T2 transformer tripped off when Hydro One relays failed and cuased the high side circuit switcher 6T2-A3RM opened improperly. Attempts to restore load on Hydro Ottawa side met with limited success, Rideau Hieghts 180F5 breaker would not close underload to pick up 72F7, all other load was sucessfully switched over. 72F7 load was finally restored thru its normal feed when 72T2 was recovered. | Nepean | Loss of Supply | relay failure
12698 | 2008 | 6 | 20 | 0.013194 |  | 107 | 1657 | 1856 | Merivale | 8/4.8kV | 72B1/B2 bus | Both highside switches open at Merivale that feeds the T1 & T2 transformers, system scada and coporate computers crashed, took 6 minutes to start scada up. Found gas relay flagged on the 72T1 tansformer. | Nepean | Defective Equipment
19945 | 2012 | 2 | 1 | 0.3125 |  | 407 | 47 | 7 | Merivale DS | 8/4.8kV | 72F1 | OMS reported a confirmed outage at 51 Medhurst. Upon arrival, 24/7 crews inspected and found transformer TE1042 to be defective. A line crew was called in to replace the transformer. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20366 | 2012 | 4 | 21 | 0.69792 |  | 76 | 47 | 37 | Merivale | 8/4.8kV | 72F1 | S1091 at 24 Shehyn opened due to defective switch. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16160 | 2010 | 5 | 28 | 0.75556 |  | 141 | 95 | 45 | Merivale | 8/4.8kV | 72F1 | SCADA indicated 72F1 Auto-reclosed, twice. Customers reported load noise from Kid Grove area, patrol found S969B blown. Patrolled transformers in loop, no damage or evidence of on animal found. Refused S969, closed and blew. 72F1 auto-reclosed again. Crews will hipot cable and restore transformeer at a time. Problem was determined to be a defective cable between TE681 & TE682. | Nepean | Defective Equipment
8425 | 2006 | 6 | 5 | 0.39583 |  | 75 | 8 | 6 | Merivale | 8/4.8kV | 72F1 | Switch to Transformer NP2757 at 9 David St opened due to animal contact (Squirrel) | Nepean | Foreign Interference | Animal
16852 | 2010 | 9 | 2 | 0.46944 |  | 18 | 1 | 4 | Merivale | 8/4.8kV | 72F1 | TE734 at 272 Wood field was isoalted to allow crew to repairtransformer secondary leg. | Nepean | Scheduled Outage
17103 | 2010 | 10 | 13 | 0.18819 |  | 196 | 222 | 68 | Merivale | 8/4.8kV | 72F1 | Defective fuse barrel at S1095 caused switch to fall open interrupting power to 10 transformers in the Woodfield / Medhurst area. Transformer loop was abnormal at the time, switch S1095 was carrying 7 extra transformers due to a planned isolation for insulator replacement. Switch was replaced, refused & closed successfully restoring all power. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
20037 | 2012 | 2 | 21 | 0.12431 |  | 111 | 202 | 109 | Merivale | 8/4.8kV | 72F2 | 72F2 breaker auto reclosed due to defective lead at S871. Merivale ID#20037 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20200 | 2012 | 3 | 22 | 0.57153 |  | 11 | 24 | 386 | Merivale | 8/4.8kV | 72F2 | While crew was restoring a transformer loop to normal the crew closed into a cable fault. Merivale (72F2) ID#20200 | Nepean | Defective Equipment
20277 | 2012 | 4 | 4 | 0.40347 |  | 294 | 1553 | 317 | Merivale | 8/4.8kV | 72F2 | Crews isolated the cable sect bet S871 & TE424,TE426,TE427 to allow them to expose all the cables to make repairs the the faulted cable, in the Woodsfeild/Downsview area | Nepean | Scheduled Outage | Preventive Maintenance
3402 | 2003 | 5 | 4 | 0.35556 |  | 233 | 346 | 89 | Merivale MS | 8/4.8kV | 72F2 | One phase of the fused cutout and surge arresters at S871 on the 72F2 feeder found blown. All were replaced and load restored. Note: Required outage to the other two phases of the cutout for clearance purposes, see other interruption report. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3403 | 2003 | 5 | 4 | 0.48958 |  | 40 | 104 | 156 | Merivale MS | 8/4.8kV | 72F2 | Two phases of the fused cutout S871 required open for clearance to repair defective third phase switch as well as blown surge arresters. | Nepean | Defective Equipment | Repair
8273 | 2006 | 5 | 11 | 0.40972 |  | 25 | 3 | 8 | Merivale | 8/4.8kV | 72F2 | Isolation of TE818 on Benlea to place transformer back on pad. (Planned Job, Transformer was hit some time ago) | Nepean | Scheduled Outage | Repair
8274 | 2006 | 5 | 11 | 0.42153 |  | 86 | 11 | 8 | Merivale | 8/4.8kV | 72F2 | TE817 W isolated to replace transformer & remove contaminated soil on Benlea Drive. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
3493 | 2003 | 5 | 27 | 0.47986 |  | 147 | 192 | 200 | Merival | 8/4.8kV | 72F2 | Underground cable between TE423 & TE788 on the red phase has blown, creating the outage. The Hold Off was left on circuit 72F2, which did not allow the breaker to close. The Hold Off was removed and the breaker was closed back in picking up more then half the customers. The crew was dispatched and found the R phase at S871 was found open and blown affecting 7 transformer. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8381 | 2006 | 5 | 30 | 0.4 |  | 374 | 118 | 19 | Merivale | 8/4.8kV | 72F2 | TE3884 ISOLATED TO ALLOW CREW TO CLEAN OIL. BENLEA DR. ON 72F2. | Nepean | Scheduled Outage | Repair
10494 | 2007 | 5 | 31 | 0.40764 |  | 146 | 30 | 20 | Merivale | 8/4.8kV | 72F2 | TE816 at 22 Benlea was replaced due to an oil leak. Transformer TP3884 on Benlea was interrupted for 37 min due to back up feed being out of phase. | Nepean | Scheduled Outage | Repair
10543 | 2007 | 6 | 6 | 0.375 |  | 329 | 22 | 4 | Merivale | 8/4.8kV | 72F2 | Peter Barr isolated TRF TP4950 @ | Nepean | Scheduled Outage | Preventive Maintenance
10544 | 2007 | 6 | 6 | 0.375 |  | 329 | 22 | 4 | Merivale | 8/4.8kV | 72F2 | Peter Barr isolated TRF TP 4950 @ 22 Benlea for clean up of oil spill | Nepean | Scheduled Outage | Preventive Maintenance
10554 | 2007 | 6 | 8 | 0.41111 |  | 3 | 1 | 20 | Merivale | 8/4.8kV | 72F2 | 2 transformers were unloaded due to an out-of-phase conduction on Benlea DR. Transformer # TP5950 & TP4950. | Nepean | Scheduled Outage | Repair
20814 | 2012 | 6 | 20 | 0.59236 |  | 512 | 9 | 1 | Merivale | 8/4.8kV | 72F2 | Scada indicates 72F2 circuit auto reclosed. Transformer TE2784 at 25 Camelot was found to be defective.Changed by on-call. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10787 | 2007 | 7 | 4 | 0.44097 |  | 1 | 1 | 50 | Merivale | 8/4.8kV | 72F2 | Power was interuped to 5 transformers to allow crews to isolate a section of cable between TE788 & TE423. An out-of-phase condition at S3-3. | Nepean | Human Element | Incorrect Construction
10864 | 2007 | 7 | 12 | 0.61806 |  | 2 | 2 | 57 | Merivale | 8/4.8kV | 72F2 | Transformer TE4234 at 119 Woodfield was interrupted due to out of phase switching | Nepean | Scheduled Outage | Repair
15218 | 2009 | 10 | 5 | 0.62292 |  | 45 | 87 | 400 | Merivale | 8/4.8kV | 72F2 | 72F2 opened when T424 secondary fuse flashed during open | Nepean | Human Element
19575 | 2011 | 11 | 15 | 0.35556 |  | 127 | 203 | 390 | Merivale |  | 72F2 | At 8:03 72F2 breaker tripped. Ottawa fire reported a pole fire at Hunt Club and Cleopatra. Crews found a burnt crossarm and 2 phases about 15 feet off the ground. Merivale 72F2 ID# 19575 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6222 | 2005 | 2 | 21 | 0.27083 |  | 115 | 6 | 3 |  | 8/4.8kV | 72f4 | BROKEN CUTOUT AT37 BURNBANK CAUSED AN OUTAGE TRANSFORMER IS IN FRONT OF 37 BURNBANK | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4871 | 2004 | 3 | 9 | 0.59028 |  | 35 | 1 | 2 | Merivale | 8/4.8kV | 72F4 | Repair neutral connection to 5 Jay Ave. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8006 | 2006 | 3 | 10 | 0.35417 |  | 110 | 16 | 9 | Merivale | 8/4.8kV | 72F4 | Mike Mcllellan opened transformer 893 at 17 Adams to do a transformer changed | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12127 | 2008 | 3 | 11 | 0.5625 |  | 57 | 3 | 3 | MERIVALE | 8/4.8kV | 72F4 | Transformer #36363 (NP283) at 37 Burnbank isolated to allow for replacement of broken insulator | Nepean | Scheduled Outage | Repair
8042 | 2006 | 3 | 17 | 0.44861 |  | 38 | 1 | 1 | Merivale | 8/4.8kV | 72F4 | Blue phase fuse at switch S-497 opened due to bad secondary cable on secondary of TE2823.(152 cleopatra) | Nepean | Defective Equipment | Imminent Equipment Failure Detected
10297 | 2007 | 4 | 23 | 0.52083 |  | 80 | 7 | 5 | Merivale | 8/4.8kV | 72F4 | Isolated transformer 696 at Jay Ave and Arco Way to transfer service | Nepean | Scheduled Outage | Preventive Maintenance
12336 | 2008 | 4 | 23 | 0.77292 |  | 3 | 5 | 100 | Merivale | 8/4.8kV | 72F4 | 72F4 Circuit out of Merivale MS, tripped under hold off, lighting storm goring through the Ottawa area. | Nepean | Adverse Weather | Lightning
3392 | 2003 | 5 | 1 | 0.63958 |  | 359 | 24 | 4 | Merivale | 8/4.8kV | 72F4 | Overhead insulator failed at 162 Cleopatra Dr. in Nepean. Top 5 feet of hydro pole brunt off. Hydro plant on pole was repaired. At S400 while crew went to restore power to 3 customers, White phase switch failed to close properly. Caused extended outage time to 3 customers. S400 white phase switch jumped out. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6501 | 2005 | 5 | 4 | 0.40625 |  | 20 | 1 | 4 | Merivale | 8/4.8kV | 72F4 | Opened switch to transformer NP001047 at 6 Redwin to give clearance when working in vicinity of the primary | Nepean | Scheduled Outage | Construction
14316 | 2009 | 5 | 6 | 0.43056 |  | 80 | 3 | 2 | Merivale | 8/4.8kV | 72F4 | Isolated and replaced transformer 1048 at 5 Jay Aver (PCB oil) | Nepean | Scheduled Outage | Preventive Maintenance
20693 | 2012 | 6 | 4 | 0.70486 |  | 43 | 10 | 14 | Merivale | 8/4.8kV | 72F4 | 72F4 from S675 to EOL was isolated to allow crews to repair a burning switch and secondary conductor on Caesar Ave. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
5291 | 2004 | 6 | 12 | 0.80625 |  | 134 | 4 | 2 | Merivale | 8/4.8kV | 72F4 | Overhead transformer 1048 at 5 Jay Street in Nepean blown fuse replaced. No apparent cause. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18390 | 2011 | 6 | 12 | 0.43819 |  | 59 | 3 | 3 | Merivale | 8/4.8kV | 72F4 | Replaced blown fuse feeding transformer X36316 at 17 Jay Ave (Vines around switch) | Nepean | Tree Contacts | Inadequate Trimming
8508 | 2006 | 6 | 18 | 0.60208 |  | 94 | 86 | 55 | Merivale | 8/4.8kV | 72F4 | 72F4 auto-reclosed. Crew found downed conductor between S407W and S339W on Burnbank. Section of conductor isolated between two temp openers and power restored to all customers. | Nepean | Tree Contacts | Inadequate Trimming
14598 | 2009 | 6 | 23 | 0.39583 |  | 280 | 9 | 2 | Merivale | 8/4.8kV | 72F4 | Transformer #X37056 located at 45 Slack Rd isolated for service upgrade | Nepean | Scheduled Outage | Construction
3737 | 2003 | 7 | 13 | 0.71875 |  | 40 | 5 | 7 | Merivale | 8/4.8kV | 72F4 | A defective fused cut-out was replaced on a 3 phase bank, Tx16 at 21 Caeser. 7 - 3 phase customers from #5 to #21 Caeser were affected. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16505 | 2010 | 7 | 21 | 0.29167 |  | 260 | 9 | 2 | Merivale | 8/4.8kV | 72F4 | Isolated 3 phase pole mount transformer X37212 at 16 Enterprise Ave (Up-grade from 600v to 347/600v service) | Nepean | Scheduled Outage | Construction
5624 | 2004 | 8 | 8 | 0.71528 |  | 52 | 3 | 4 | Merivale | 8/4.8kV | 72F4 | 72F4 auto/reclose due to squirel contact at transformer 3739 at 80 Vaan Dr, tx fuse opened. 24/7 refused and closed. | Nepean | Foreign Interference | Animal
3927 | 2003 | 8 | 21 | 0.97778 |  | 105 | 262 | 150 | Merivale | 8/4.8kV | 72F4 | Merivale 72F4 tripped due to a tree contacting the line. The tree was cleared and power restored. | Nepean | Tree Contacts | Tree Fallen
16957 | 2010 | 9 | 16 | 0.72083 |  | 52 | 4 | 5 | Merivale | 8/4.8kV | 72F4 | Refused switch feeding transformer X36319 at 69 Arco Way that had opened due to vines that had grown around the switch | Nepean | Tree Contacts | Inadequate Trimming
17012 | 2010 | 9 | 28 | 0.38889 |  | 186 | 3 | 1 | Merivale | 8/4.8kV | 72F4 | TE3049 on Cleopatra was disconnected for arrears at the transformer switch. | Nepean | Unknown/Other
7463 | 2005 | 10 | 16 | 0.083333 |  | 345 | 6 | 1 | Merivale | 8/4.8kV | 72F4 | MVA broke hydro Pole at WOODROFFE AVE/PINELAND AVE NEPN. Case #294-190. Located at 1751 Woodroffe WO#30471 | Nepean | Foreign Interference | Vehicle
9506 | 2006 | 10 | 24 | 0.68125 |  | 138 | 28 | 12 | Merivale MS | 8/4.8kV | 72F4 | A truck pulled down and broke the service wire at 42 Cleopatra, and bent the Mast at 41 Cleopatra causing the 72F4 to auto reclose and S713 to blow open. | Nepean | Foreign Interference | Vehicle
17343 | 2010 | 11 | 25 | 0.47569 |  | 41 | 4 | 6 | MERIVALE | 8/4.8kV | 72F4 | Transformer X26303 at 37 Arco Way isolated for upgrade | Nepean | Scheduled Outage | Construction
11785 | 2007 | 11 | 28 | 0.71528 |  | 174 | 3 | 1 | Merivale | 8/4.8kV | 72F4 | TE2634 at 162 Cleopatra was isolated to replace leaking transformer. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6045 | 2004 | 12 | 11 | 0.093056 |  | 146 | 7 | 3 | Merivale | 8/4.8kV | 72F4 | In line fused disconnects S400 on Cleopatra 2 phases found blown, O/H is clear, heavy snow fall & high winds, same refused and closed. | Nepean | Adverse Weather
11860 | 2007 | 12 | 17 | 0.82292 |  | 110 | 64 | 59 | Merivale | 8/4.8kV | 72F4 | At 7:45pm Merivale 72F4 autoreclosed. White Phase has loss of load. 24-7 dispatched to patroll circuit. White phase overhead circuit down. Crew had isolation and made repairs to overhead circuit. All load restored. ID#11860. | Nepean | Unknown/Other
11864 | 2007 | 12 | 21 | 0.86458 |  | 59 | 2 | 2 | MERIVALE | 8/4.8kV | 72F4 | TRANSF #X37056 AT 51 SLACK RD ISOLATED TO ALLOW FOR CHANGE OF LEAKING CUTOUT | Nepean | Scheduled Outage | Emergency Services Request
15565 | 2009 | 12 | 27 | 0.125 |  | 663 | 785 | 71 | Merivale | 8/4.8kV | 72F4 | A tree fell on the O/H in the ARCO WAY causing switch S501 to open. | Nepean | Adverse Weather | Ice Storm
6109 | 2004 | 12 | 30 | 0.95139 |  | 25 | 0 | 1 | Merivale | 8/4.8kV | 72F4 | Transfoprmer 16 at 21 Ceasar Ave isolated to repair tx switches. | Nepean | Defective Equipment
4775 | 2004 | 2 | 10 | 0.66528 |  | 66 | 9 | 8 | Merivale | 8/4.8kV | 72F5 | TX833 @ 21 Brooklane secondary wires raped together. Causing fuse to blow effecting power to 8 customers. | Nepean | Adverse Weather | Wind
14040 | 2009 | 3 | 11 | 0.79028 |  | 127 | 19 | 9 | Merivale | 8/4.8kV | 72F5 | Replaced broken switch feeding transformer NP0916 at 9 Norice St | Nepean | Adverse Weather | Wind
12173 | 2008 | 3 | 25 | 0.63542 |  | 85 | 10 | 7 | MERIVALE DS | 8/4.8kV | 72F5 | Transformer #X36548 at 64 Palsen isolated to replace triplex (open wire buss - tree interferrence) | Nepean | Scheduled Outage | Repair
5007 | 2004 | 4 | 16 | 0.41319 |  | 41 | 8 | 12 | MERIVALE | 8/4.8kV | 72F5 | Replace broken switch at transformer NP000908 @ 10 nSpring Garden. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10346 | 2007 | 5 | 1 | 0.37153 |  | 20 | 2 | 6 | Merivale | 8/4.8kV | 72F5 | ISOLATED TRANSFORMER NP196 AT 19 CANTER ST. TO REPLACE ARRESTER. | Nepean | Scheduled Outage | Preventive Maintenance
5108 | 2004 | 5 | 5 | 0.5625 |  | 48 | 6 | 8 | Merivale D.S. | 8/4.8kV | 72F5 | Isolated transformer NP0833 at 21 Brook Lane. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10430 | 2007 | 5 | 20 | 0.51806 |  | 589 | 167 | 17 | Merivale | 8/4.8kV | 72F5 | defective transformer TE613 @ 120 Sullivan was replaced. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
10538 | 2007 | 6 | 5 | 0.83819 |  | 119 | 28 | 14 | Merivale | 8/4.8kV | 72F5 | 72F5 circuit auto-reclosed twice due to a tree contact with single phase lateral at 27 Spring Garden. The lateral burnt off at tap to main line. The tree branch was cleared & lateral single phase line reconnected to main line. | Nepean | Tree Contacts | Tree Limb Fallen
14485 | 2009 | 6 | 8 | 0.36458 |  | 30 | 3 | 6 | Merivale | 8/4.8kV | 72F5 | At 08:45am transformer TP6149 at 9 Parker was isolated to for contractor to work on secondary. | Nepean | Scheduled Outage
12591 | 2008 | 6 | 10 | 0.67014 |  | 387 | 97 | 15 | Merivale | 8/4.8kV | 72F5 | S25338 opened due to primary conductor down Oncall crew made repairs to line & restored power to 15 customers on Spring Garden & Glenridge. | Nepean | Defective Equipment
8599 | 2006 | 6 | 27 | 0.28194 |  | 79 | 11 | 8 | MERIVALE | 8/4.8kV | 72F5 | Switch to transformer NP004478 at the rear of 39 Viewmount Dr was found open due to contact with a squirrel refused the switch and restored power | Nepean | Foreign Interference | Animal
11012 | 2007 | 8 | 8 | 0.38542 |  | 298 | 497 | 100 | Merivale | 8/4.8kV | 72F5 | 72F5 overhead cable section between S1588 and S24782 interrupted for pole changes. | Nepean | Scheduled Outage | Preventive Maintenance
11088 | 2007 | 8 | 17 | 0.69722 |  | 353 | 861 | 785 | Merivale | 8/4.8kV | 72F5 | 72 F5 auto reclosed, fuse at S526 to a single phase runoff on Viewmount Dr opened. Tree has fallen onto the conductor causing the conductor to break. When crew closed S526 with hold off to restore section the 72F5 auto tripped but fuse did not blow. Patrol found nothing alse wrong so fuse was closed in with the 72F5 breaker reclosing enabled. Breaker and fuse held and power was restored. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9136 | 2006 | 9 | 7 | 0.39583 |  | 160 | 16 | 6 | Merivale | 8/4.8kV | 72F5 | Tony Taylor opened transformer #NP001266 at 6 Viewmont and performed a complete pole change. | Nepean | Scheduled Outage | Preventive Maintenance
11336 | 2007 | 9 | 19 | 0.33472 |  | 465 | 1550 | 200 | Merivale | 8/4.8kV | 72F5 | 72F5 cable section between S1588 and S24782 isolated for crew to change poles and line section. | Nepean | Scheduled Outage | Construction
7359 | 2005 | 9 | 21 | 0.56111 |  | 57 | 8 | 8 | Merrivale | 8/4.8kV | 72F5 | Fused switch to Transformer NP 5050 at 3 Whitehill opened due to squirrel contact | Nepean | Foreign Interference | Animal
11428 | 2007 | 10 | 1 | 0.39931 |  | 90 | 20 | 13 | Merivale | 8/4.8kV | 72F5 | Transformer #NP004597 located at 54 Glenmanor isolated due to working clearances. | Nepean | Scheduled Outage
11429 | 2007 | 10 | 1 | 0.40625 |  | 120 | 32 | 16 | Merivale | 8/4.8kV | 72F5 | Transformer located at 99 Viewmount isolated due to working clearances. | Nepean | Scheduled Outage
15199 | 2009 | 10 | 2 | 0.5625 |  | 30 | 2 | 3 | Merivale | 8/4.8kV | 72F5 | Transformer #X36758 located at 1 Largo isolated for a service upgrade | Nepean | Scheduled Outage | Construction
11453 | 2007 | 10 | 3 | 0.39236 |  | 75 | 15 | 12 | Merivale DS | 8/4.8kV | 72F5 | Transformer #NP000908 at 10 Spring Garden isolated to allow for transfer of plant | Nepean | Scheduled Outage | Construction
5850 | 2004 | 10 | 21 | 0.40625 |  | 30 | 4 | 9 | Merivale Sub | 8/4.8kV | 72F5 | New service connection. | Nepean | Scheduled Outage | Construction
11609 | 2007 | 10 | 27 | 0.83889 |  | 8 | 1 | 10 | Merivale M.S. | 8/4.8kV | 72F5 | O/H Transformer NP2897 at 16 Oakridge was opened to allow crew to trim trees around open secondary bus. | Nepean | Tree Contacts | Inadequate Trimming
11610 | 2007 | 10 | 27 | 0.84444 |  | 24 | 4 | 11 | Merivale M.S. | 8/4.8kV | 72F5 | O/H Transformer NP3340 at 24 Oakridge was opened to allow crew to trim trees around open secondary bus. | Nepean | Tree Contacts
13752 | 2008 | 12 | 15 | 0.36111 |  | 60 | 34 | 121 | Merivale | 8/4.8kV | 72F5 | Crew had to open S315 on fieldrow due to pole fire in front of 70 Fieldrow, crew removed hot line clamp at this OH transformer and closed S315 back in picking up all customers except for 6 customers. Cutout replaced and last 6 customers picked up. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4619 | 2003 | 12 | 17 | 0.875 |  | 60 | 14 | 14 | Merivale | 8/4.8kV | 72F5 | A defective fuse at transformer #2427 at 32 Meadowlands in Nepean cause an outage. The fuse was replaced and power restored. ID#4619 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
13811 | 2008 | 12 | 28 | 0.64514 |  | 158 | 295 | 112 | Merivale | 8/4.8kV | 72F5 | Gazebo at rear of 79 Viewmount blew into the primary causing the 72F5 to auto reclose and S26712 fuse to blow, crew removed gazebo and re-fused switch, picking up 112 customers. | Nepean | Foreign Interference | Foreign Object
6260 | 2005 | 3 | 11 | 0.49653 |  | 15 | 0 | 1 | Merivale | 8/4.8kV | 72F6 | Transformer #TE1374 interrupted to replace cut out At 229 Colonnade | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17761 | 2011 | 3 | 22 | 0.52639 |  | 134 | 150 | 97 | Merivale | 8/4.8kV | 72F6 | Isolation to repair S449 required and 17 customers were affected by the isolation, remaining 80 customers were restored on Borden Farm 130F3 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8196 | 2006 | 4 | 27 | 0.80903 |  | 260 | 4 | 1 | Merivale | 8/4.8kV | 72F6 | TE1085 on Colonnade Rd North replaced due to oil Leak. New TP2876 installed | Nepean | Defective Equipment | Equipment Deterioration Due to Age
3459 | 2003 | 5 | 21 | 0.36736 |  | 589 | 129 | 16 | Merivale | 8/4.8kV | 72F6 | 72F6 tripped to lock out due to a pole fire behind 30 Colonade which burned the top of the pole off. The pole top was being supported by the 44KV line. The 44 KV was isolated adding a JDS building to the outage. The 8KV was isolated but the 11 commercial buildings containing commercial units could not be restored until switches were cut in to isolate the pole. Cuts were also cut in to restore JDS. One building at 210 Colonade with about 8 units could not be restored until the pole was repaired. One three phaze cust at 210 Colonade is still out but is hook up to a generator untill the pole is replaced. | Nepean | Adverse Weather | Rain
8468 | 2006 | 6 | 11 | 0.3125 |  | 279 | 46 | 10 | Merivale | 8/4.8kV | 72F6 | Isolate the O/H on Colonnade Rd south to reinsulate the O/H. | Nepean | Scheduled Outage | Preventive Maintenance
10715 | 2007 | 6 | 23 | 0.31181 |  | 309 | 10 | 2 | Merivale | 8/4.8kV | 72F6 | TE1372 and TP4226 @ 199 Colonade were isolated for customer maintenance. | Nepean | Scheduled Outage | Preventive Maintenance
10756 | 2007 | 6 | 28 | 0.57986 |  | 165 | 6 | 2 | Merivale | 8/4.8kV | 72F6 | Customer at 14 & 20 Colonade called in reporting a part out condition. TE1994 isolated to make repairs to cable terminations. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10874 | 2007 | 7 | 15 | 0.37153 |  | 365 | 12 | 2 | Merivale | 8/4.8kV | 72F6 | Switch S1194 at 45 Colonnade was isolated to replace porcelain insulator type switch & replace transformer TE1660. (TE1660 will be changed to TP5002) | Nepean | Scheduled Outage | Preventive Maintenance
16700 | 2010 | 8 | 9 | 0.38611 |  | 239 | 56 | 14 | Merivale | 8/4.8kV | 72F6 | TP4239 on Citiplace isolated to allow contractor to pull in new secondary cables. | Nepean | Scheduled Outage
3966 | 2003 | 8 | 29 | 0.44583 |  | 23 | 2 | 5 | Merivale MS | 27.6/16kV | 72F6 | Live line clamp replaced to switch 1475 supply to Te1994 at 20 Colonnade Ave. Line crew notified customers of short outage to make repairs. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
17321 | 2010 | 11 | 22 | 0.38333 |  | 138 | 103 | 45 | Merivale | 8/4.8kV | 72F6 | 2 downed conductors on Colonnade were isolate and repaired, affecting 2 transformers, 45 customers in total. | Nepean | Defective Equipment
7771 | 2006 | 1 | 1 | 0.13056 |  | 572 | 10 | 1 | Merivale | 8/4.8kV | 72F7 | Defective Transformer TE2534 at 1691 Merivale Road, caused 3 auto recloses on the 72F7. Repairs made, new transformer installed. | Nepean | Defective Equipment
19980 | 2012 | 2 | 7 | 0.60903 |  | 68 | 1 | 1 | Merivale | 8/4.8kV | 72F7 | Transformer #X37076 located at 37 Grenfell opened up due to broken cut out | Nepean | Defective Equipment | Imminent Equipment Failure Detected
17631 | 2011 | 2 | 22 | 0.43056 |  | 40 | 2 | 3 | Merivale | 8/4.8kV | 72F7 | X37124 at 1989 merivale was isolated to allow crews to repair defective cutout & arrester. 3 customers affected for 40 minutes. Merivale (47F7) | Nepean | Defective Equipment
20129 | 2012 | 3 | 6 | 0.37083 |  | 66 | 7 | 6 | Merivale | 8/4.8kV | 72F7 | Replaced primary riser from switch feeding transformer X37082 at 55 Grenfell Cres | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14303 | 2009 | 5 | 4 | 0.83333 |  | 85 | 1 | 1 | Merivale | 8/4.8kV | 72F7 | Customer owned overhead line & cable to TP5396 at 1961 Merivale was isolated at S217 for Black & Mac to determine cause of blown fuse and make repairs. | Nepean | Defective Equipment
16257 | 2010 | 6 | 13 | 0.31667 |  | 386 | 595 | 110 | Merivale | 8/4.8kV | 72F7 | 72F7 radial O/H line isolated from S20559 to end of line to allow crew to install two new pole at 49 Grenfell. All power restored at 12:56 pm except for transformer X37080 at 43 Grenfell which required work on the secondary. | Nepean | Scheduled Outage | Construction
16261 | 2010 | 6 | 14 | 0.38194 |  | 20 | 2 | 7 | Merivlae | 8/4.8kV | 72F7 | At 09:10 trans at 43 Grenfel Cres was isolated to make emerg repairs | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16336 | 2010 | 6 | 27 | 0.21458 |  | 380 | 6 | 1 | Merivale | 8/4.8kV | 72F7 | 72F7 circuit auto-reclosed due to blown elbow, fuse and arrestor on white phase at transformer TE2625 at 1849 Merivale (Costco). | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13005 | 2008 | 8 | 6 | 0.22569 |  | 32 | 1 | 1 | Merivale | 8/4.8kV | 72F7 | Lightening strike caused Blue phase at S1618 to blow causing 72F7 to A/R. Crews opened remaing RW phase to make repairs to broken blue phase fuse. | Nepean | Lightning
19131 | 2011 | 9 | 11 | 0.17708 |  | 145 | 17 | 7 | Merivale | 8/4.8kV | 72F7 | TP2217 at 1876 Merivale was isolated to allow customer to disconnect secondary to East Side Mario's & begin work for new secondary cables. Note: East Side Mario's will be on Generator until second shut down to install new secondary cables. | Nepean | Scheduled Outage | Construction
19283 | 2011 | 9 | 28 | 0.99653 |  | 440 | 51 | 7 | Merivale | 8/4.8kV | 72F7 | TP2217 at 1876 Merivale was isolated for upgrade | Nepean | Scheduled Outage | Construction
7428 | 2005 | 10 | 6 | 0.40278 |  | 21 | 0 | 1 | Merivale | 8/4.8kV | 72F7 | J. McGee reports TE1769 isolated to replace hot line clamp at 61 BONGARD AVE NEPN. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
19333 | 2011 | 10 | 6 | 0.57292 |  | 23 | 3 | 9 | Rideau Heights | 8/4.8kV | 72F7 | Trans X37078 at 39 Grenfell Cres was isolated in order to replace a broken transformer cutout | Nepean | Defective Equipment | Equipment Deterioration Due to Age
11477 | 2007 | 10 | 8 | 0.97569 |  | 40 | 31 | 46 | Merivale | 8/4.8kV | 72F7 | hot line clamp burned off at Merivale and Woodfield | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4321 | 2003 | 10 | 21 | 0.83333 |  | 28 | 0 | 1 | Merivale MS | 8/4.8kV | 72F7 | Swtch S4 at Merivale & Slack found burning, customer isolated while switch was being jumpered out. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15363 | 2009 | 11 | 8 | 0.54653 |  | 83 | 8 | 6 | Merivale | 8/4.8kV | 72F7 | Transformer at 21 Grenfell was isolated by overhead crew for PCB replacement | Nepean | Scheduled Outage | Preventive Maintenance
13603 | 2008 | 11 | 13 | 0.6125 |  | 16 | 32 | 120 | Merivale | 8/4.8kV | 72F7 | Pole fire at dip pole to TE2627 caused 72F7 breaker to auto-reclose and lock out. | Nepean | Defective Equipment
13606 | 2008 | 11 | 13 | 0.62361 |  | 655 | 160 | 84 | Merivale | 8/4.8kV | 72F7 | Pole fire at 33 Royden on pole carrying S390 feeding 8kv pad mounted transformer TE2627 caused the 72F7 breaker to trip. Radial 3 phase over head to S390 was cut clear to isolate damaged pole and restore load to the rest of the circuit. | Nepean | Adverse Environment | Fire
11771 | 2007 | 11 | 27 | 0.1875 |  | 142 | 5 | 2 | Merivale | 4.16kV | 72F7 | TE2353 at 1916 Merivale (Merivale Bowling Centre) was replaced due to oil leak. | Nepean | Scheduled Outage | Repair
9762 | 2006 | 12 | 1 | 0.325 |  | 85 | 1 | 1 | Merivale | 8/4.8kV | 72F7 | The 72F7 circuit auto reclosed caused by a blown arrestor and fuse on a O/H transformers that feeds 1922 Merivale. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14716 | 2009 | 7 | 11 | 0.48542 |  | 41 | 1086 | 1590 | Merivale | 8/4.8kV | 72T1 | 72T1 tripped due to low-low voltage. Crew found discoloured Insulator, possibly cracked insulator on Xfrmr. 72F1, F2 & F4 auto reclosedprior to Xfrmr trip. & 72F1, F2 & F4 restore via 72T2 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8958 | 2006 | 8 | 13 | 0.48333 |  | 102 | 1408 | 1911 | Merivale | 115kV | 72T1 | Hydro One A8M circuit auto/reclose from the Merivale MS 72T1 O/C trip protection. Squirrel contact with the 72B1 Bus damaging insulators caused trip and B1 Bus load interupted. The A8M at Uplands MTS & MS remained o/s due to H1 86-A8M switch opened from U/V protection interupting both stations. The 4801 T3 high & low side sws and the 4801 F7 & F8 breakers also opened tripped. | Nepean | Foreign Interference | Animal
14417 | 2009 | 5 | 27 | 0.72569 |  | 335 | 575 | 854 | Merivale | 8/4.8kV | 72T2 | Cross arm brace broke and fell on S1533 that caused damage to the switch and isulators. 72F6 breaker did not open causing 72T2 to trip on over current and auto reclose the A3RM. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6803 | 2005 | 6 | 25 | 0.76111 |  | 3 | 37 | 742 | Lincoln | 13.2kV | 7407 | Circuit was opened via scada to allow crew to open in-line switches to allow for isolation of broken pole at Muncton nad Queensview | Ottawa | Scheduled Outage | Repair
8000 | 2006 | 3 | 9 | 0.75278 |  | 236 | 120 | 35 | Merivale | 8/4.8kV | 74F2 | 72f4 Auto reclosed. Crew found a broken bushing on transformer # 893 @ 21 Adams St. Crew opened 893 and jumpered secondary bus. Customers fed from transformer 4461. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6712 | 2005 | 6 | 14 | 0.34792 |  | 141 | 33 | 20 | Merivale | 8/4.8kV | 74F4 | Scada indicates 72F4 circuit has auto reclosed. Customers report power outage on Burnbank st. W. Ried reports tree in overhead section between S407 and MSO @ 190 brunbank. | Nepean | Adverse Weather | Lightning
9798 | 2006 | 12 | 5 | 0.53472 |  | 110 | 22 | 12 | Bilberry | 27.6/16kV | 77 M2 | Greg isolated TRF. @ 1233 dussere to change TRF. | Gloucester | Scheduled Outage | Preventive Maintenance
5827 | 2004 | 10 | 4 | 0.59028 |  | 80 | 16 | 12 | Bilberry | 27.6/16kV | 7756 | Repaired a cable fault at TE1659R50 (7979 De Carie) | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15611 | 2010 | 1 | 5 | 0.45694 |  | 221 | 325 | 93 | Bilberry | 27.6/16kV | 77M1 | Blue phase fuse opened at SE25 to TE1748 for a cable fault between transfomers TE1741 & TE1465. Outage affected customers west of Orleans Blvd & north of Jeanne d'Arc | Gloucester | Defective Equipment
13874 | 2009 | 1 | 17 | 0.052778 |  | 1356 | 10545 | 3067 | Bilberry Creek | 27.6/16kV | 77M1 | 27kV, 77M1 circuit phase came down at G615, onto the Hydro One circuit 77M4. Interuptions to 77M1 feeder to safely perform switching to sectionalize and restore power.transformer at 1001 Cloister Gardens had defective insert and transformer T1282 @ 927 Chaleur had to be replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4754 | 2004 | 2 | 3 | 0.17361 |  | 35 | 163 | 3279 | Bilberry | 27.6/16kV | 77M1 | Tracking at switch G402 which had caused two previous autos on the 77M1 required the circuit to be off laoded for the switch to be opened safely. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
4755 | 2004 | 2 | 3 | 0.19444 |  | 2 | 103 | 3089 | Bilberry | 27.6/16kV | 77M1 | Switch at live front transformer TE1242 did not close properly and began to arch, Lineman requested load dropped before flashover in transformer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3171 | 2003 | 2 | 6 | 0.60417 |  | 60 | 9 | 9 | Bilberry | 27.6/16kV | 77M1 | TE1409 main fuse cut out open to repair secondary side lugs. All customers notified to outage. | Gloucester | Scheduled Outage | Preventive Maintenance
7993 | 2006 | 3 | 7 | 0.45347 |  | 67 | 892 | 3287 | Bilberry | 27.6/16kV | 77M1 | 77M1 feeder tripped while crew was restoring repaired cables. Feeder was under Hold Off, same breaker closed from SCADA and cable dip G396W fuse blew. Cables reisolated and switch G396W closed to restore the rest of the customers. Appears the same cable has faulted. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17718 | 2011 | 3 | 15 | 0.41528 |  | 564 | 94 | 10 | Bilberry | 27.6/16kV | 77M1 | TE1461 at 6420 Glenn Knolls was isolated from Hydro Ottawa Sources to replace leaking transformer. New TP8565 for nomenclature. | Gloucester | Scheduled Outage | Repair
10149 | 2007 | 3 | 19 | 0.89931 |  | 90 | 300 | 200 | Bilberry | 27.6/16kV | 77M1 | The blue phase termination at G401 failed & the flash also caused G401 W to open. Convent Glen N. area. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15835 | 2010 | 3 | 24 | 0.40903 |  | 58 | 14 | 15 | Bilberry Creek | 27.6/16kV | 77m1 | Transformer #T874 (TP7034) was isolated to allow crews to change elbows & inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
15841 | 2010 | 3 | 24 | 0.41736 |  | 104 | 21 | 12 | BILBERRY TS | 27.6/16kV | 77M1 | Transformer GLTE0868 at 1140 St.Jerome Cres isolated to allow for elbow repairs | U | Scheduled Outage | Repair
15844 | 2010 | 3 | 25 | 0.39028 |  | 37 | 7 | 11 | Bilberry | 27.6/16kV | 77M1 | TP7036 at 6260 Fortune isolated to upgrade elbows & inserts. 11 customers on Fortune were affected. | Gloucester | Scheduled Outage | Preventive Maintenance
15845 | 2010 | 3 | 25 | 0.53819 |  | 45 | 8 | 10 | Bilberry | 27.6/16kV | 77M1 | TP6975 at 1096 St. Lucia isolated to upgrade elbows & inserts. 8 customers on St. Lucia & 2 on Vorlage were affected. | Gloucester | Scheduled Outage | Preventive Maintenance
15854 | 2010 | 3 | 26 | 0.39931 |  | 47 | 11 | 14 | Bilberry | 27.6/16kV | 77M1 | TP7035 at 1213 St Moritz isolated to upgrade elbows & inserts. 13 customers on St Moritz & Jerome and 1 on Fortune were affected. | Gloucester | Scheduled Outage | Preventive Maintenance
15858 | 2010 | 3 | 26 | 0.40972 |  | 40 | 9 | 14 | Billberry | 27.6/16kV | 77M1 | At 09:45 trans at 1213 St Moritz was isolated in order to make repairs to a defective elbow | Gloucester | Scheduled Outage | Repair
6335 | 2005 | 3 | 30 | 0.97569 |  | 139 | 328 | 240 | Bilberry | 27.6/16kV | 77M1 | A partly open fuse was found at SE31, defective blue phase insulator at SE31 flashed over when the switch was opened causing G242B to open. G242B was replaced, the defective insulator at SE31 was switched out before power could be restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6336 | 2005 | 3 | 30 | 0.19583 |  | 103 | 206 | 120 | Bilberry | 27.6/16kV | 77M1 | SE31 white phase to T1288 blown tracking on bottom insulator. SE31 may be have moved in the frost. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15877 | 2010 | 4 | 1 | 0.41042 |  | 61 | 10 | 10 | Bilberry | 27.6/16kV | 77M1 | TP7028 at 1143 St Jovite isolated for elbow and insert replacement. | Gloucester | Scheduled Outage | Repair
15892 | 2010 | 4 | 5 | 0.62292 |  | 106 | 602 | 373 | Bilberry | 27.6/16kV | 77M1 | G120 blue phase fuse blew causing an outage in the Hiawatha Park / Convent Glen area of Orleans. The overhead section was patrolled but did not reveal a cause. The affected circuit section was restored successfully one section at time.. No cause was ever determined. | Gloucester | Unknown/Other
6391 | 2005 | 4 | 8 | 0.64236 |  | 10 | 2 | 11 | Bilberry | 27.6/16kV | 77M1 | While switching a fuse blew while closing the cover at transformer 1184B @ 1050 Chablis. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15929 | 2010 | 4 | 13 | 0.39583 |  | 195 | 49 | 15 | BILBERRY TS | 27.6/16kV | 77M1 | Transformer TE2590 at 6353 Roslyn and TE2591 at 6401 Roslyn isolated to change inserts and elbows | Gloucester | Scheduled Outage | Preventive Maintenance
15930 | 2010 | 4 | 13 | 0.40139 |  | 153 | 38 | 15 | Bilberry Creek | 27.6/16kV | 77M1 | T2590 & T2591 on Roslyn isolated to replace cutouts, bushing inserts and elbows | Gloucester | Scheduled Outage
15937 | 2010 | 4 | 14 | 0.47639 |  | 73 | 12 | 10 | Bilberry | 27.6/16kV | 77M1 | TP7029 at 1125 St Jovite isolated from Hydro Sources to change inserts and elbows | Gloucester | Scheduled Outage
15943 | 2010 | 4 | 15 | 0.54167 |  | 163 | 38 | 14 | Bilberry | 27.6/16kV | 77M1 | 2 transformers (#TE2454 and TE2453) opened by crew at 887 Sigma and 6196 Ravine Way to replace elbows and inserts | Gloucester | Scheduled Outage | Construction
15961 | 2010 | 4 | 20 | 0.41944 |  | 240 | 152 | 38 | Bilberry | 27.6/16kV | 77M1 | 3 transformers on St Louis and Snowshow were isolated to allow crews to replace a leaking transformer and change elbows and inserts. | Gloucester | Scheduled Outage | Repair
15973 | 2010 | 4 | 22 | 0.41181 |  | 209 | 132 | 38 | Bilberry | 27.6/16kV | 77M1 | TP6978, TP6977, TP6985, S11940, in area of Paddler & Vorlage Gloucester isolated for crew to replace cutouts and change inserts / elbows at transformers. | Gloucester | Scheduled Outage
15978 | 2010 | 4 | 23 | 0.39236 |  | 186 | 34 | 11 | Billberry | 27.6/16kV | 77M1 | TE1391 @ 934 Raftsman was isolated for crew to replace swollen elbows and inserts. | Gloucester | Scheduled Outage | Repair
10330 | 2007 | 4 | 26 | 0.52431 |  | 110 | 18 | 10 | Bilberry | 27.6/16kV | 77M1 | TE1272 at 6092 Voyageur isolated to replace it, due to an oil leak. Nomenclature changed to TP4901. | Gloucester | Scheduled Outage | Repair
16014 | 2010 | 4 | 29 | 0.41806 |  | 225 | 112 | 30 | Bilberry | 27.6/16kV | 77M1 | T857, T860, T864 and G401 isolated to allow crew to replace the switch and replace elbows and inserts customers effected on Fortune, St Jerome and St Therese, 30 customers. | Gloucester | Scheduled Outage | Repair
16050 | 2010 | 5 | 6 | 0.41875 |  | 87 | 164 | 113 | Bilberry | 27.6/16kV | 77M1 | S26669 (G401) white phase fuse blown. Cable fault located on first cable section. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16052 | 2010 | 5 | 6 | 0.41875 |  | 423 | 103 | 42 | Bilberry | 27.6/16kV | 77M1 | T863 had a blown secondary fuse and the transformer had to be isolated to replace fuse. Due to the bad white phase cable to S26667 three other transformers had to be isolated to replace fuse. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16077 | 2010 | 5 | 11 | 0.40764 |  | 232 | 116 | 30 | Bilberry | 27.6/16kV | 77M1 | Transformers TE893 at 1139 Sautern, TE890 at 1146 Sautern and TE887 at 6126 Vineyard isolated to replace elbows and inserts | Gloucester | Scheduled Outage | Repair
16081 | 2010 | 5 | 13 | 0.42917 |  | 237 | 134 | 34 | Billberry | 27.6/16kV | 77M1 | Transformers T931, T945 and T937 on Burgundy isolated to allow crews to change elbows and inserts. | Gloucester | Scheduled Outage | Repair
16138 | 2010 | 5 | 25 | 0.41389 |  | 210 | 105 | 30 | Bilberry | 27.6/16kV | 77M1 | Transformers T935, T950 and T941 were isolated to allow crews to replace inserts and elbows | Gloucester | Scheduled Outage | Preventive Maintenance
5218 | 2004 | 5 | 29 | 0.30903 |  | 284 | 384 | 109 | Bilberry | 27.6/16kV | 77M1 | Blue phase cable blown between T940 & T939. Power restored to 70 customers at @ 07:25. The remain customers restored at 09:05. (crews had to pick up fuses at stores) | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
18266 | 2011 | 6 | 1 | 0.01875 |  | 93 | 93 | 68 | Bilberry | 27.6/16kV | 77M1 | Blue phase cable fault between TE1482 and TE1479 on St. Louis Drive was isolated and customers were restored in two sections. | Gloucester | Defective Equipment
20685 | 2012 | 6 | 3 | 0.34236 |  | 367 | 18 | 3 | Bilberry | 27.6/16kV | 77M1 | 27kV transformer TP6983 at 6384 Fortune was isolated to allow crews to change the transformer. | Gloucester | Scheduled Outage | Preventive Maintenance
18314 | 2011 | 6 | 6 | 0.43056 |  | 131 | 107 | 49 | Bilberry | 27.6/16kV | 77M1 | Isolation of TP7975, TP7974, TP7973 and TP7972 for elbow insert replacement.. Meadow Glen, Summerfield Cres. | Gloucester | Scheduled Outage | Preventive Maintenance
18349 | 2011 | 6 | 8 | 0.70556 |  | 397 | 6141 | 3691 | Bilberry | 27.6/16kV | 77M1 | 77M1 opened under hold off due to lightning strike to G120. Closed circuit in and circuit held. Crew patrolled and refused and closed at G120RWB at 758 Andre. | Gloucester | Adverse Weather | Lightning
12655 | 2008 | 6 | 16 | 0.0097222 |  | 651 | 508 | 130 | Bilberry | 27.6/16kV | 77M1 | Defective transformer caused G482 R to blow interrupting 7 transformers. FCI which didn't flag at T1211 mislead restoration & caused outage to expand. Problem was then determined to be a blown elbow & defective insert at T1209. T1209 was replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8559 | 2006 | 6 | 20 | 0.45833 |  | 130 | 758 | 350 | Bilberry | 27.6/16kV | 77M1 | Switch G120 B phase found opened, patrol and investigation of padmount equipment revealed nothing. Switch closed and load restored. Suspect adverse weather may have been cause of blown switch. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18468 | 2011 | 6 | 22 | 0.83056 |  | 122 | 45 | 22 | Bilberry TS | 27.6/16kV | 77M1 | Trans X24275 at 937 BEAUCHAMP AVE GLOU was refused and power restored after bird contact | Gloucester | Foreign Interference | Bird
6823 | 2005 | 6 | 27 | 0.71528 |  | 18 | 970 | 3232 | Billberry |  | 77M1 | Hydro One reports H9A & Billberry T2 exceeded its thermal limits and load had to be shedded immediately. | Gloucester | Loss of Supply | HEPC Load Shedding
5401 | 2004 | 6 | 30 | 0.24653 |  | 118 | 650 | 570 | Billberry | 27.6/16kV | 77M1 | A switch at RX1923 @ 6345 Roslyn failed causing G242 red phase fuse to blow. Outage was caused by a CROW at RX1923. | Gloucester | Foreign Interference | Bird
14661 | 2009 | 7 | 3 | 0.48611 |  | 75 | 108 | 86 | Bilberry | 27.6/16kV | 77M1 | Crew found G421 R at Bilberry station blown, cable below stress cone appeared damaged. Cable section from G421 to TE931 isolated & load recovered from alternate source. Jeanne D'Arc & Vineyard Dr area. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10839 | 2007 | 7 | 10 | 0.55347 |  | 103 | 19 | 11 | Billberry | 27.6/16kV | 77M1 | Transformer T1008 @ 1184 Priory was isolated to replace same. | Gloucester | Scheduled Outage | Repair
8706 | 2006 | 7 | 12 | 0.44097 |  | 245 | 111 | 100 | Bilberry | 27.6/16kV | 77M1 | A planned outage to T1379 and TE1057W on the 77M1 circuit, Terry Fox School to make repairs to the padmount, and during restoration the white phase cable between T1055W and T1379 blew, causing G401W to blow. The cable was re-isolated and power restored. | Gloucester | Scheduled Outage | Preventive Maintenance
6961 | 2005 | 7 | 16 | 0.030556 |  | 106 | 159 | 90 | Bilberry | 27.6/16kV | 77M1 | A blown cable bet T1748(750 St Andre) and S25(Orleans Blvd) on the B phase. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8796 | 2006 | 7 | 21 | 0.78681 |  | 132 | 165 | 75 | Bilberry | 27.6/16kV | 77M1 | Cable from T1109R to T1379 placed back on potential after work at T1379 completed. Arrester at T1379 blown and fuse at switch 482 red blown. Elbow pulled at T1109R and new fuse installed at G482 red. Buckskin Way and Snowshoe Cres. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10940 | 2007 | 7 | 24 | 0.40625 |  | 95 | 13 | 8 | Bilberry | 27.6/16kV | 77M1 | Transformer #TP5083 located at 6232 Ravine Way isolated to replace leaker | Gloucester | Scheduled Outage | Repair
12942 | 2008 | 7 | 25 | 0.33819 |  | 124 | 294 | 166 | Bilberry | 27.6/16kV | 77M1 | Bird contact with O/H xfmr 1923 at 6344 Roslyn caused xfmr cutout fuse to blow as well as the red phase fuse at G242. Both were refused successfully. | Gloucester | Foreign Interference | Bird
12951 | 2008 | 7 | 26 | 0.55556 |  | 243 | 4496 | 1110 | Bilberry | 27.6/16kV | 77M1 | G120 RWB at the N. end of Orleans Blvd blew during thunderstorm. 48M3, 48M5 a/r & 77M5 also tripped at the same time. O/H patrolled & fuses replaced. | Gloucester | Lightning
14896 | 2009 | 8 | 4 | 0.52153 |  | 153 | 521 | 220 | Bilberry | 27.6/16kV | 77M1 | SE25 blue phase blown due to defective cable between T1465, and T1741. Cable isolated and customers restored | Ottawa | Defective Equipment
16635 | 2010 | 8 | 4 | 0.097917 |  | 279 | 288 | 62 | Billberry | 27.6/16kV | 77M1 | Crews found faulted cable from TE1479 to TE1107 while restoring customers. 62 customers affected for 279 minutes. (Billery Creek (77M1) | Gloucester | Defective Equipment
18887 | 2011 | 8 | 7 | 0.3625 |  | 90 | 152 | 101 | Billberry |  | 77M1 | At 8:42am SC2140 Red phase tripped. Crews found a faulted cable section between TE722 and TE723 on Harvest Cresent in Orleans. Billberry Creek (77M1) ID# 18887 | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
16691 | 2010 | 8 | 8 | 0.36458 |  | 326 | 1336 | 266 | Bilberry | 27.6/16kV | 77M1 | Crews found S31BT1411 fuse blown, Patroll found FCI at T1414 is Clear, T1416 is flagged, TP7230 is Flagged, T1367 is clear and T1369 is clear, Openned T1367BTP7230 & TP7230-H1A, Closed SE31BT1411, 187 customers restored. Hipot found 77M1 U/G cable fault from TE1367 to TP7230. Closed at T1811BT1382 & all customers restored | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18896 | 2011 | 8 | 8 | 0.95278 |  | 428 | 71 | 10 | Bilberry | 27.6/16kV | 77M1 | TE7230 defective and transformer replaced by on call crew | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3881 | 2003 | 8 | 9 | 0.094444 |  | 450 | 3098 | 542 | Bilberry | 27.6/16kV | 77M1 | 77M1 autoreclosed due to a raccoon getting into an open point switch G396RWB causing G433RWB to blow. The elbow on the white phase at TE685 had come off due to the fault and repairs were made at 02:16 G433 RWB was closed but the blue phase blew due to and elbow burnt off at transformer TE598 repairs were made and power restored | Gloucester | Foreign Interference | Animal
18914 | 2011 | 8 | 12 | 0.26042 |  | 155 | 1310 | 507 | Bilberry | 27.6/16kV | 77M1 | G120 blue phase was found open. Line was patrolled and no apparent cause was found. | Gloucester | Unknown/Other | No Apparent Cause
14942 | 2009 | 8 | 13 | 0.45278 |  | 238 | 135 | 34 | Bilberry |  | 77M1 | Transformer TE1496 at 1775 Axminster isolated to change terminations. 2 retirement residences were affected at 6410 & 6420 Lumberman affecting 34 units. | Gloucester | Scheduled Outage | Preventive Maintenance
16735 | 2010 | 8 | 15 | 0.31458 |  | 94 | 263 | 168 | Bilberry | 27.6/16kV | 77M1 | Crow contact at transformer X23123 at Roslyn and Amyot, caused G242 red phase fuses to blow. | Gloucester | Foreign Interference | Bird
3904 | 2003 | 8 | 16 | 0.16667 |  | 777 | 3299 | 537 | Bilberry | 27.6/16kV | 77M1 | Darcy reports TE596 @ 1727 Fieldstone isolated to remove defective transformer. 520 customers power restored. 14 customers still out of power. D. Provost reports cable at T595 to short, unable to re-arrange cables. G396R is now reclosed power restored to 180 customers. D. Provost reports T580RT596 closed restored to all customers. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7275 | 2005 | 9 | 3 | 0.55208 |  | 337 | 124 | 34 | BILBERRY | 27.6/16kV | 77M1 | The city of Ottawa dug into a cable bet 6442 & 6444 Sugar Creek because of broken water main, there was a cable locate done that morning by Pro Mark ticket # 53612393. | Gloucester | Foreign Interference | Dig-in
19125 | 2011 | 9 | 9 | 0.41389 |  | 76 | 10 | 8 | Bilberry | 27.6/16kV | 77M1 | TP7186W @ 6274 Steamer was isolated to allow crew to remove steel fish tape pushed into base by contractor. | Gloucester | Scheduled Outage
15082 | 2009 | 9 | 10 | 0.41458 |  | 103 | 21 | 12 | Bilberry | 8/4.8kV | 77M1 | TE1462 @ 6412 Glen Knolls isolated to replace defective Tx. New Tx # TP6894 | Gloucester | Scheduled Outage | Repair
16968 | 2010 | 9 | 20 | 0.42153 |  | 211 | 141 | 40 | Billberry Creek | 27.6/16kV | 77M1 | T1675, T1676, T1678 and S12254 isolated to allow crew to replace switch and elbows and inserts on Avenue Du Bois | Gloucester | Scheduled Outage | Preventive Maintenance
19220 | 2011 | 9 | 21 | 0.40417 |  | 127 | 42 | 20 | Bilberry Creek | 27.6/16kV | 77M1 | TP8025 and TP7184 on Friar gate and Bonnaventure were isolated to allow crews to replace elbows and inserts | Gloucester | Scheduled Outage | Preventive Maintenance
19226 | 2011 | 9 | 21 | 0.52708 |  | 92 | 31 | 20 | Billberry Creek | 27.6/16kV | 77M1 | TP8024 and TP8023 on Bonaventure were isolated to allow crews to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
15167 | 2009 | 9 | 26 | 0.04375 |  | 252 | 333 | 89 | Billberry | 27.6/16kV | 77M1 | blue phase cable fault between transformers T1051 and T1052 on St. Germaine and ST. Emmanuel caused the G401 blue phase fuse to open. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
7385 | 2005 | 9 | 27 | 0.41667 |  | 299 | 50 | 10 | Bilberry | 27.6/16kV | 77M1 | TE893 was isolated to replace leaking transformer. | Gloucester | Scheduled Outage | Repair
19272 | 2011 | 9 | 27 | 0.38333 |  | 190 | 54 | 17 | Billberry |  | 77M1 | At 9:12 crews isolated 2 transformers on the 77M1 for elbow and insert replacement. 17 customers affected for 190 mins. Billberry 77M1. | Gloucester | Scheduled Outage
19273 | 2011 | 9 | 27 | 0.51528 |  | 115 | 27 | 14 | Billberry | 27.6/16kV | 77M1 | At 12;22 crews isolated 2 transformers on the 77M1 to replace elbows and inserts. 14 customers affected for 190 mins. Billberry (77M1) | Gloucester | Scheduled Outage
17027 | 2010 | 9 | 29 | 0.67986 |  | 320 | 779 | 3074 | Bilberry | 27.6/16kV | 77M1 | Transformers T849, T850 and T1260 were isoalted to allow crew to replace transformer elbows and switches, Sugar Creek & Taffy Lane. Upon restore of the transformer loop, elbows blew at T1260 and tripped the 77M1 circuit. Customers were restored in section, repairs made and power restored. | Gloucester | Scheduled Outage
19288 | 2011 | 9 | 29 | 0.37917 |  | 133 | 38 | 17 | Billberry | 27.6/16kV | 77M1 | crew isolated transformers TP8019 at Bonaventure, and TP7020 at Friar gate for elbow and insert replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
17039 | 2010 | 10 | 1 | 0.38542 |  | 255 | 85 | 20 | Bilberry | 27.6/16kV | 77M1 | TP7016 & TP7183 on Fieldstone Ave were isolated during planned work on primary cables. | Gloucester | Scheduled Outage | Construction
4203 | 2003 | 10 | 3 | 0.55556 |  | 100 | 17 | 10 | Bilberry | 27.6/16kV | 77M1 | Pad mount transformer mtce. | Gloucester | Scheduled Outage | Preventive Maintenance
9369 | 2006 | 10 | 3 | 0.42222 |  | 247 | 25 | 6 | Billberry | 27.6/16kV | 77M1 | T761B @ Stoneboat Cres. Isolated to allow crew to change transformer. | Gloucester | Scheduled Outage | Repair
9372 | 2006 | 10 | 3 | 0.42222 |  | 247 | 49 | 12 | Bilberry | 27.6/16kV | 77M1 | Transformer TE761 at 1772 Stoneboat Cr isolated for replacement. | Gloucester | Scheduled Outage | Construction
17047 | 2010 | 10 | 3 | 0.70486 |  | 212 | 18 | 5 | BILBERRY | 27.6/16kV | 77M1 | T2238 was isolated to replace elbows and inserts | Gloucester | Scheduled Outage
17048 | 2010 | 10 | 4 | 0.38819 |  | 232 | 4 | 9 | Bilberry | 27.6/16kV | 77M1 | TP7021 and 7184 on Gray Nuns isolated for insert and elbow replacement and new cable reconfiguration. | Gloucester | Scheduled Outage | Construction
17055 | 2010 | 10 | 5 | 0.40833 |  | 317 | 53 | 10 | Billberry Creek MS |  | 77M1 | TP7182 at 6279 Sundown Cres. was isolated to allow crews to re-configure the circuit & transfer it from the blue phase to the white phase and change the elbows & inserts. | Gloucester | Scheduled Outage | Construction
17094 | 2010 | 10 | 12 | 0.39306 |  | 119 | 12 | 8 | Bilberry Creek | 27.6/16kV | 77M1 | G408 and T926 were isolated to replace elbow and inserts aswell as cutout. | Gloucester | Scheduled Outage
17096 | 2010 | 10 | 12 | 0.50139 |  | 68 | 15 | 13 | Bilberry | 27.6/16kV | 77M1 | TE921 at 1862 Axminster in Orleans isolated to upgrade elbows & inserts. 13 customers on Axminster affected. | Gloucester | Scheduled Outage | Preventive Maintenance
17097 | 2010 | 10 | 12 | 0.38889 |  | 210 | 49 | 14 |  | 27.6/16kV | 77M1 | Isolated transformer TP7285 at 6278 Sundown Cres to replace primary Elbows and inserts | Gloucester | Scheduled Outage | Preventive Maintenance
17101 | 2010 | 10 | 12 | 0.62222 |  | 70 | 12 | 10 | Bilberry | 27.6/16kV | 77M1 | G473B & TE757 at 1749 Stoneboat in Orleans isolated to replace switch and upgrade elbows & inserts. 10 customers on Stoneboat affected. | Gloucester | Scheduled Outage | Preventive Maintenance
17113 | 2010 | 10 | 14 | 0.38333 |  | 68 | 12 | 11 | Bilberry Creek | 27.6/16kV | 77M1 | T911 at 7893 Jeanne D'Arc was isolated to allow crwew to change elbowsd and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
17114 | 2010 | 10 | 14 | 0.41111 |  | 93 | 14 | 9 | Bilberry Creek | 27.6/16kV | 77M1 | T2239 at 1232 joseph drouin was isolated to allow crew to replace switch G183 and replace elbows and inserts at T2239. | Gloucester | Scheduled Outage | Preventive Maintenance
17117 | 2010 | 10 | 14 | 0.47569 |  | 77 | 13 | 10 | Bilberry creek MS | 27.6/16kV | 77M1 | T2243 at 1292 Joseph Drouin was isolated to allow crews to replace elbows & inserts. | Gloucester | Scheduled Outage | Repair
17118 | 2010 | 10 | 14 | 0.59167 |  | 83 | 11 | 8 | Bilberry creek MS | 27.6/16kV | 77M1 | T2247 at 1232 St Jean Street was isolated to allow crews to change elbows & inserts. | Gloucester | Scheduled Outage | Repair
17120 | 2010 | 10 | 15 | 0.45833 |  | 135 | 76 | 34 | Bilberry Creek MS | 27.6/16kV | 77M1 | 77M1 blue phase cable section between TP7053 & T851 faulted causing an outage to TP7053, T851, T1098 & T1099. Crews isolated the fault & restored power. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7493 | 2005 | 10 | 20 | 0.4 |  | 216 | 29 | 8 | BILBERRY | 27.6/16kV | 77M1 | T936 RED PHASE @ 6052 VINYARD DR OUTAGE FOR REPLACEMENT DUE TO LEAKING TRANSFORMER, ON THE 77M1. | Gloucester | Scheduled Outage | Repair
17159 | 2010 | 10 | 21 | 0.92708 |  | 205 | 133 | 39 | Billberry Creek | 27.6/16kV | 77M1 | TE2367 & TE2101 at Dussere were isolated to allow crews to replace elbows and inserts. 39 customers affected for 205 minutes | Gloucester | Scheduled Outage
13434 | 2008 | 10 | 27 | 0.37083 |  | 72 | 349 | 291 | Billberry | 27.6/16kV | 77M1 | G401 blue and white phase fuses opened. Flash marks on pole. Fault indicators clear. Crew refused and closed to restore power. Possible UFO contact. | Gloucester | Foreign Interference | Animal
17183 | 2010 | 10 | 27 | 0.35417 |  | 160 | 27 | 10 | Bilberry | 27.6/16kV | 77M1 | TE997 at 1067 Grenoble was isolated to allow crew to replace elbows and inserts. 10 customers were affected for 160minutes. Bilberry (77M1) ID #17183. | Gloucester | Scheduled Outage
17187 | 2010 | 10 | 28 | 0.40556 |  | 66 | 10 | 9 | Bilberry | 27.6/16kV | 77M1 | T727 at 1632 Grey Nuns isolated to replace elbows and inserts. Nomenclature changed to TP7445 and new normal opn point. | Gloucester | Scheduled Outage | Construction
9585 | 2006 | 11 | 2 | 0.41111 |  | 146 | 22 | 9 | Bilberry | 27.6/16kV | 77M1 | Isolated Transformer at 1344 Belcourt for pole replacement | Gloucester | Scheduled Outage | Preventive Maintenance
17215 | 2010 | 11 | 3 | 0.52569 |  | 14 | 273 | 1168 | Bilberry | 27.6/16kV | 77M1 | RX2018 tripped under holdoff. Crew replaced transformer T998, and upon energization of the new transformer RX2018 tripped. Transformer re-isolated and RX2018 closed. RX2018 auto reclosed upon energization. | Gloucester | Defective Equipment
11674 | 2007 | 11 | 6 | 0.49306 |  | 175 | 84 | 34 | Bilberry | 27.6/16kV | 77M1 | Cable between TE1099B & TE1098B on Sugarcreek Way failed causing G539B to open. Defective cable isolated & power restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17275 | 2010 | 11 | 15 | 0.52222 |  | 70 | 36 | 31 | Billberry | 27.6/16kV | 77M1 | At 12:32 trasnformer TE1300 at 6483 JEANNE D'ARC was isolated to allow crew to replace elbows and inserts. 31 customers were affected for 70 minutes. ID# 17275. | Gloucester | Scheduled Outage
17277 | 2010 | 11 | 15 | 0.59097 |  | 63 | 8 | 8 | Bilberry | 27.6/16kV | 77M1 | Transformer @ T1528 at 1092 Millwood was isolated by the crew for elbow and inserts replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
17302 | 2010 | 11 | 18 | 0.41597 |  | 89 | 22 | 15 | Bilberry Creek | 27.6/16kV | 77M1 | TE2043 at 6800 Jeanne D'Arc was isolated to allow crews to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
11743 | 2007 | 11 | 21 | 0.28611 |  | 176 | 99 | 34 | Billberry Creek | 27.6/16kV | 77M1 | G539 on Surgar Creek blue phase opened due to cable fault between T1099B and T1098B on the Bilberry Creek M1 feeder. Fault was isolated and customers have been restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17345 | 2010 | 11 | 25 | 0.64583 |  | 410 | 7 | 1 | Bilberry | 27.6/16kV | 77M1 | Defective transformer TE2505 at 879 Hiawatha was replaced. (Seniors residence, was supported by back up generator for the length of the outage) | Gloucester | Defective Equipment
17356 | 2010 | 11 | 29 | 0.43056 |  | 322 | 54 | 10 | Bilberry Creek | 27.6/16kV | 77M1 | TE1385 at 1093 Moselle isolated to allow crew to perform elbow and insert replacement | Gloucester | Scheduled Outage | Preventive Maintenance
15462 | 2009 | 12 | 3 | 0.55903 |  | 65 | 11 | 10 | Bilberry Creek | 27.6/16kV | 77M1 | TE1285 at 896 Explorer was isolated for crews to replace defective elbows and inserts | Gloucester | Scheduled Outage | Repair
9816 | 2006 | 12 | 9 | 0.014583 |  | 32 | 2 | 3 | Bilberry | 27.6/16kV | 77M1 | T1496 at 1024 Axminster isolated to remove barrier board and replace transformer fuses. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
11863 | 2007 | 12 | 20 | 0.45139 |  | 142 | 2599 | 1098 | Bilberry | 27.6/16kV | 77M1 | G120 RWB at N. end of Orleans Blvd blew. O/H sections from G120 & on Roslynn & Hiawatha patrolled, report of snow removal crew hitting pole checked & no problems found. G120 RWB fuses replaced & all power restored. | Gloucester | Unknown/Other | No Apparent Cause
11916 | 2008 | 1 | 9 | 0.6375 |  | 370 | 56 | 9 | Bilberry | 27.6/16kV | 77M2 | A blown elbow & bushing at transformer TE2445 @ 1719 Country Walk. Transformer was replaced & oil spill cleaned up. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19818 | 2012 | 1 | 12 | 0.14375 |  | 196 | 1078 | 1200 | Billberry | 27.6/16kV | 77M2 | RX2020 tripped open (no A/R), crews reported nothing evident at reclosure, closed and held. Crews continued patrol south on Boyer then EAST on Innes, no issue found recieved customer call at 01:45 that power is out, crews Isolated possible cable fault from TE1485 to TE1131 G552 WHITE phase refused closed and holding - 47 customers restore G763 WHITE phase closed and holding - 121 customers restore | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4714 | 2004 | 1 | 19 | 0.58889 |  | 32 | 2 | 3 | BILBERRY | 27.6/16kV | 77M2 | Transformer #142 @ 2916 mer bleu was isolated to RE-SAG service. | Gloucester | Scheduled Outage | Repair
11969 | 2008 | 1 | 23 | 0.38333 |  | 388 | 52 | 8 | Bilberry | 27.6/16kV | 77M2 | TE2445 at 1717 Country Walk was isolated to clean up previous oil spill. Transformer was already replaced since oil spill on Jan 9th, 08. 8 customers on Country Walk were interrupted. | Gloucester | Scheduled Outage | Repair
19917 | 2012 | 1 | 28 | 0.93542 |  | 125 | 4526 | 3400 | Bilberry TS | 27.6/16kV | 77M2 | RX2020 & 77M2 both indicates open. Blue phase fault indicater flagged on RX2020. 77M2 circuit closed via scada and holding. RX2020 reclosure wouldn't close via scada. 77M2 breaker opened again 24/7 crew seen a flash east of RX2020. Circuit was patrolled no problem found. 77M2 circuit breaker closed restoring 40 customers. 24/7 patrolled south of RX2020 no apparent fault found on overehead circuit. RX2020 closed by 24/7 locally and holding. 24/7 reports lots of ice on overhead circuit and strong winds at this time. | Gloucester | Adverse Weather | Ice, Sleet, Freezing Rain (not Trees)
17576 | 2011 | 2 | 13 | 0.78333 |  | 612 | 51 | 5 | Bilberry Creek | 27.6/16kV | 77M2 | Customers report tranformer #X21860 fuse has opened. 5 Customer affected in power outage at 3681 Innes Rd. 24/7 reports transformer has failed primary bushing brunt & lid blown off. | Gloucester | Adverse Weather | Rain
13983 | 2009 | 2 | 14 | 0.72361 |  | 115 | 19 | 10 | Billberry | 27.6/16kV | 77M2 | Transformer T2479 @ 6577 Morningview was isolated to allow crews to put it back on it's base. | Gloucester | Foreign Interference | Vehicle
17581 | 2011 | 2 | 14 | 0.57431 |  | 51 | 883 | 3360 | Bilberry | 27.6/16kV | 77M2 | 77M2 & RX2020 tripped at same time. Most customers restored up to open RX2020. 24/7 found broken stand off pin @ pole X17368, 2062 St Joseph, repairs made & remaining customers restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20019 | 2012 | 2 | 15 | 0.40417 |  | 88 | 47 | 32 | Bilberry | 27.6/16kV | 77M2 | TP7526, TP7527 and TP7528 on Orleans Blvd were isolated for cable and insert replacement | Gloucester | Scheduled Outage | Preventive Maintenance
20021 | 2012 | 2 | 15 | 0.5 |  | 103 | 55 | 32 | Bilberry | 27.6/16kV | 77M2 | TP7534, TP7535 and TP7536 on Orleans Blvd were isolated for cable and insert replacement | Gloucester | Scheduled Outage | Preventive Maintenance
7970 | 2006 | 2 | 26 | 0.45139 |  | 40 | 7 | 11 | Bilberry | 8/4.8kV | 77M2 | Isolated transformer Gl5530 at 2544 Mer Bleue Rd to replace one phase of open wire buss that had burnt down | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20096 | 2012 | 3 | 3 | 0.37708 |  | 59 | 3024 | 3401 | Bilberry | 27.6/16kV | 77M2 | Bilberry 77M2 A/R/A during wind storm, scada later indicated RX2020 also tripped at the same time. 77M2 restored up to open RX2020 via scada. No reports form police or fire, attempted to close RX2020, would not close via scada, crew dispatched to site. RX2020 finally closed via scada. | Gloucester | Adverse Weather | Wind
20108 | 2012 | 3 | 3 | 0.54792 |  | 248 | 8323 | 3401 | Bilberry | 27.6/16kV | 77M2 | 77M2 tripped as well as RX2020, 77M2 closed up to open RX2020, tripped again, line patrolled, no problem found. 77M2 closed & held for 3 min to open RX2020. Circuit patrolled again. RX2020 load restored via alternate sources. 77M2 riser cable tested OK, G104B at Duserre & St Joseph replaced, 77M2 closed & holding | Gloucester | Adverse Weather | Wind
20110 | 2012 | 3 | 3 | 0.73819 |  | 25 | 170 | 409 | Bilberry | 27.6/16kV | 77M2 | 77M2 tripped again, egress cable & dip to SC2130 open, load restored via 77M6. | Gloucester | Adverse Weather | Wind
20128 | 2012 | 3 | 6 | 0.39444 |  | 221 | 365 | 99 | Billberry | 27.6/16kV | 77M2 | 11 transformers isolated to allow crew to replace elbow and inserts and replace insulatrs at O/H Switch. Boyer & Orleans area. | Gloucester | Scheduled Outage
10102 | 2007 | 3 | 9 | 0.47222 |  | 15 | 1 | 5 | Bilberry | 27.6/16kV | 77M2 | Darcy Provost isolated TRF # 5536 @ 2390 Mer Blue to change defective TRF sw. & arrestor | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10108 | 2007 | 3 | 11 | 0.70278 |  | 43 | 40 | 56 | Bilberry | 27.6/16kV | 77M2 | Fuse blew on Meadowglen at S27 during planned switching. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
8037 | 2006 | 3 | 16 | 0.56042 |  | 52 | 3181 | 3670 | Bilberry | 27.6/16kV | 77M2 | Faulted 77M2 W phase cable termination at egress cable riser near the Bilberry station. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20215 | 2012 | 3 | 23 | 0.71597 |  | 176 | 21 | 7 | Bilberry Creek | 27.6/16kV | 77M2 | TP7914 at 1955 Kimball was isolated to replace leaking transformer | Gloucester | Scheduled Outage
8058 | 2006 | 3 | 24 | 0.44792 |  | 80 | 16 | 12 | Bilberry | 27.6/16kV | 77M2 | Transformer #2864 located at 1121 Cholette isolated to replace transformer | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20245 | 2012 | 3 | 27 | 0.39306 |  | 494 | 58 | 7 | Billberry |  | 77M2 | At 09:26am crews isolated TP7914 at 1955 Kimball to remove contaminated soil. 7 customers affected for 494 mins. Billberry 77M2 ID# 20245 | Gloucester | Scheduled Outage
8080 | 2006 | 3 | 30 | 0.43403 |  | 100 | 17 | 10 | BILBERRY | 27.6/16kV | 77M2 | T592W ON 77M2 (BILBERRY) OUT FOR MAINTANCE. | Gloucester | Scheduled Outage | Repair
15884 | 2010 | 4 | 2 | 0.66875 |  | 98 | 18 | 11 | Bilberry | 27.6/16kV | 77M2 | T2131 at 1798 Robinwood leaking oil and isolated for replacement. | Gloucester | Scheduled Outage | Repair
12231 | 2008 | 4 | 3 | 0.375 |  | 410 | 72 | 13 | Bilberry | 27.6/16kV | 77M2 | Transformer T2443 at 1701 Country Walk flashed and blew, required replacement, customer restoration delayed because of transformers in front yards being buried under lots of snow and ice. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4967 | 2004 | 4 | 4 | 0.72917 |  | 81 | 236 | 175 | Bilberry | 27.6/16kV | 77M2 | Defective cable section between G710 W & transformer #T1638WG710. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
17833 | 2011 | 4 | 5 | 0.5 |  | 60 | 2 | 2 | Bilberry | 27.6/16kV | 77M2 | Transformer #X21865 located at 6470 Viseneau Dr opened by crew to relocate transformer to new pole. | Gloucester | Scheduled Outage | Construction
20284 | 2012 | 4 | 5 | 0.38472 |  | 44 | 8 | 11 | Bilberry | 27.6/16kV | 77M2 | At 9:14am crews isolated TP7539 at 6342 Beausejour for elbow and insert replacement. Bilberry 77M2 ID# 20284 | Gloucester | Scheduled Outage
6383 | 2005 | 4 | 7 | 0.40972 |  | 48 | 11 | 14 | Bilberry | 27.6/16kV | 77m2 | Isolated Transformer 1231 at 6169 Brookside to relocate service | Ottawa | Scheduled Outage | Construction
20296 | 2012 | 4 | 7 | 0.88194 |  | 20 | 2 | 6 | Billerry | 27.6/16kV | 77M2 | At 21:10, secondary service feeding 1320 St.Jean down due to house fire. Transformer X23870 was refused and all byt 1 cutomer restored. | Gloucester | Adverse Environment | Fire
4983 | 2004 | 4 | 8 | 0.55278 |  | 43 | 90 | 125 | Bilberry | 27.6/16kV | 77M2 | On switching section G710 by T1638 the G710 fuse blow while crew was opening G689W causing an interruption to 125 customers. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6390 | 2005 | 4 | 8 | 0.54167 |  | 94 | 9 | 6 | Bilberry | 27.6/16kV | 77M2 | Isolated Transformer # 1231 at 6169 Brookside to repair a bad UG service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17883 | 2011 | 4 | 11 | 0.27708 |  | 2 | 97 | 2913 | Bill Berry | 27.6/16kV | 77M2 | RX2020 A/R then tripped after CS15245 closed to restore load during 77M6 outage. CS15245 was openned and then load restored. | Gloucester | Adverse Weather | Rain
20310 | 2012 | 4 | 12 | 0.39167 |  | 91 | 12 | 8 | Bilberry | 27.6/16kV | 77M2 | Crews isolated TP8028 @ 6464 Beausjour to allow them to install vented elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
5014 | 2004 | 4 | 18 | 0.72917 |  | 109 | 218 | 129 | Billberry | 27.6/16kV | 77M2 | Mike Lamoureux found a cable fault between Transformer T1630B and T2036B in the Viseneau / Innes area. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6423 | 2005 | 4 | 18 | 0.8125 |  | 325 | 92 | 17 | Bilberry | 27.6/16kV | 77M2 | TE2687 @ 1560 Cedar Mills failed Cause unknown. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5017 | 2004 | 4 | 19 | 0.64375 |  | 18 | 16 | 52 | Bilberry | 27.6/16kV | 77M2 | Switch G552 open to install fuse in transformer T1127. New xfmr fuse installed and blow again so transfomer is defective and will have to be replaced today. We are required to dump 52 customers becase of a cable fault on the same loop section that began yesterday. | Gloucester | Scheduled Outage | Repair
5020 | 2004 | 4 | 19 | 0.79097 |  | 88 | 92 | 63 | Bilberry | 27.6/16kV | 77M2 | Transformer 1127 on Viseneau Cr in Gloucester had to be replaced, due to a faulted B phase cable 7 other transformers in the Innes Rd & Belcourt area required o/s to isolate T1127. | Gloucester | Defective Equipment
5022 | 2004 | 4 | 19 | 0.55208 |  | 432 | 79 | 11 | Bilberry | 27.6/16kV | 77M2 | Transformer 1127 on Viseneau Cr in Gloucester faulted, same had to be replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3358 | 2003 | 4 | 20 | 0.20486 |  | 353 | 179 | 41 | Bilberry TS | 27.6/16kV | 77M2 | Vehicle knocked transformer off pad requiring it to be replaced. Reliability crew restored 4 other interrupted transformers and replaced TE1557 at 6325 Beausejour. | Gloucester | Foreign Interference | Vehicle
3362 | 2003 | 4 | 20 | 0.58333 |  | 1350 | 248 | 11 | Bilberry TS | 27.6/16kV | 77M2 | Reliability Crew replaced defective transformer TE1563. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3374 | 2003 | 4 | 24 | 0.31875 |  | 105 | 70 | 40 | Bilberry TS | 27.6/16kV | 77M2 | Fused disconnect blew due to defective arrestor, refused and closed, surge arrestor to be repaired. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16022 | 2010 | 4 | 30 | 0.44444 |  | 70 | 6 | 5 | Bilberry | 27.6/16kV | 77M2 | Transformer #X21856 located at 3681 Innes Rd opened to move transformer 1 pole east | Gloucester | Scheduled Outage | Construction
20452 | 2012 | 5 | 3 | 0.41944 |  | 224 | 287 | 77 | Bilberry | 27.6/16kV | 77M2 | Customers on Loire , Gaultoise, bedeque and Boyer were interupted due to elbow and insert replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
5098 | 2004 | 5 | 4 | 0.45486 |  | 205 | 27 | 8 | Bilberry | 27.6/16kV | 77M2 | TE 1769 on the blue phase at 6464 Beausejour was replaced due to a small leak noticed in the case. | Gloucester | Scheduled Outage | Repair
10366 | 2007 | 5 | 5 | 0.22847 |  | 161 | 275 | 170 | Bilberry | 27.6/16kV | 77M2 | White phase fuse blew at G710 interrupting power to 17 transformers in the Chateau Neuf area of Orleans. Fault was due to a defective cable section on Viseneau between TE1647 & TE1648. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16047 | 2010 | 5 | 6 | 0.22222 |  | 112 | 4 | 2 | Bilberry | 27.6/16kV | 77M2 | TE2250 at 1243 Meranger isolated from Hydro Ottawa Sources to change elbows and inserts in transformer | Gloucester | Scheduled Outage
10388 | 2007 | 5 | 8 | 0.41319 |  | 266 | 40 | 9 | Bilberry | 27.6/16kV | 77M2 | Jamie Leblanc isolated TRF @ 1707 Country Walk for a trf change | Gloucester | Scheduled Outage | Preventive Maintenance
8264 | 2006 | 5 | 9 | 0.45069 |  | 248 | 50 | 12 | Bilberry | 27.6/16kV | 77M2 | TE1548B leaking oil and replaced with TP3882. 1635 Baie Verte Orleans | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
16072 | 2010 | 5 | 10 | 0.76319 |  | 131 | 22 | 10 | Bilberry | 27.6/16kV | 77M2 | Transformer at 1445 Youville Dr (TE2176) was isolated to allow crew to change elbows and inserts | Gloucester | Scheduled Outage
20496 | 2012 | 5 | 10 | 0.41389 |  | 224 | 355 | 95 | Billberry | 27.6/16kV | 77M2 | Red phase transformers on Boyer and Jeanne D'arc between switch S10119 and S10124 were isolated to allow crew to perform elbow and insert replacment | Gloucester | Scheduled Outage | Preventive Maintenance
18147 | 2011 | 5 | 13 | 0.60972 |  | 134 | 25 | 11 | Bilberry Creek | 27.6/16kV | 77M2 | transformer at 1866 Longman was isolated to replace leaking transformer. | Gloucester | Scheduled Outage | Repair
18167 | 2011 | 5 | 17 | 0.39583 |  | 236 | 173 | 44 | Bilberry | 27.6/16kV | 77M2 | Transformer TE2265, TE2266, TE2267 on Coutnry Walk Dr were isolated to allow crew to replace elbows and inserts. 44 Customers were affected. Billberry (77M2) | Gloucester | Scheduled Outage
5173 | 2004 | 5 | 18 | 0.38472 |  | 392 | 72 | 11 | 77 | 27.6/16kV | 77M2 | TE1718 @ 2451 St Joseph was off at 09:14 & power restored to 11 customers @ 15:46 due to blown transformer. As per dispatch | Gloucester | Adverse Weather | Lightning
18172 | 2011 | 5 | 18 | 0.39097 |  | 218 | 233 | 64 | Billberry | 27.6/16kV | 77M2 | Transformers TP7615, TP7614, TP7613, TP7612, TP7611, TP7609, TP7608 on Hunters Run DR were isolated to allow crew to replace elbows and inserts in transformers and one cut out on the red phase. 64 customers were affected. Billberry (77M2) | Gloucester | Scheduled Outage
18179 | 2011 | 5 | 18 | 0.8625 |  | 58 | 6 | 6 | Bilberry | 27.6/16kV | 77M2 | Transformer X23875 at 6243 Sundown refused - outage caused by animal contact - racoon | Gloucester | Foreign Interference | Animal
12468 | 2008 | 5 | 23 | 0.42778 |  | 120 | 22 | 11 | Billberry Creek | 27.6/16kV | 77M2 | At 10:16 AM T1637B at 1871 Markwell was isolated to replace transformer and elbows on the 77M2 out of Billberry Creek. 11 customers affected, transformer was back on at 12:16PM. | Gloucester | Scheduled Outage | Repair
18202 | 2011 | 5 | 24 | 0.39792 |  | 109 | 16 | 9 | Billberry | 27.6/16kV | 77M2 | Transformer TP7600 at 1663 Autumn Ridge was isolated to allow crew to change leaking transformer. 9 cusotmers were affected. Billberry (77M2) | Gloucester | Scheduled Outage
18203 | 2011 | 5 | 24 | 0.55139 |  | 154 | 144 | 56 | Billberry | 27.6/16kV | 77M2 | Transformer TP7607, TP7606, TP7605, TP7604, TP7603, TP7602, TP7601 on Autumn Ridge were isolated to allow crew to replace elbows and inserts. 56 customers were affected. Billberry 77M2. | Gloucester | Scheduled Outage
18251 | 2011 | 5 | 30 | 0.44792 |  | 135 | 27 | 12 | Bilberry |  | 77M2 | At 10:45 crews isolated Transfromer TE1813 for repairs. 12 customers were affected for 135 mins. Billberry 77M2 ID# 18251 | Gloucester | Scheduled Outage
18261 | 2011 | 5 | 31 | 0.44444 |  | 90 | 18 | 12 | Billberry | 27.6/16kV | 77M2 | TE1814 @ 6463 Natalie Way was isolated to allow crew to replace leaking transformer. 12 customers were affected. Billberry 77M2 | Gloucester | Scheduled Outage
10520 | 2007 | 6 | 3 | 0.45139 |  | 55 | 1 | 1 | Bilberry | 27.6/16kV | 77M2 | Builders Warehouse at 3636 Innis rpt'd no power, found 1 phase of 3 phase supply open at cut -out & also a k-link fuse blown at Tx 618. Primary run-off to transformer was isolated to make repairs. | Gloucester | Unknown/Other | No Apparent Cause
10521 | 2007 | 6 | 3 | 0.88403 |  | 297 | 5 | 1 | Bilberry Creek | 27.6/16kV | 77M2 | D. McKay reports tree branches trimmed & 3 switches replaced @ 3636 Innes Rd. | Gloucester | Tree Contacts | Inadequate Trimming
18291 | 2011 | 6 | 4 | 0.24861 |  | 233 | 1102 | 4900 | Bilberry | 27.6/16kV | 77M2 | RX2020 tripped affecting Boyer, Jeanne D'arc, Notre Damme area. Recloser closed and held. Crew found transformer #GL003804 located at 6627 Benoit opened up due to tree contact (vines). | Gloucester | Tree Contacts
18319 | 2011 | 6 | 7 | 0.37847 |  | 78 | 36 | 28 | Billberry | 27.6/16kV | 77M2 | TP7966, TP7965, and TP7967 transformers on Willowbark were isolated for elbow and insert replacment. | Gloucester | Scheduled Outage | Repair
18320 | 2011 | 6 | 7 | 0.50208 |  | 66 | 30 | 27 | Billberry | 27.6/16kV | 77M2 | transformers TP7962, TP7963, and TP7964 were isolated for elbow, and insert replacement. | Gloucester | Scheduled Outage
18381 | 2011 | 6 | 10 | 0.39444 |  | 551 | 101 | 11 | Bilberry | 27.6/16kV | 77M2 | TP7911 at 1700 Teakdale was isolated to deal with an clean up of contaminated soil after an oil leak | Gloucester | Scheduled Outage | Preventive Maintenance
14514 | 2009 | 6 | 11 | 0.40694 |  | 19 | 912 | 2879 | bilberry | 27.6/16kV | 77M2 | RX2020 recloser opened when 77M5 breaker opened at the station due to bird in overhead circuit. | Gloucester | Foreign Interference | Bird
6708 | 2005 | 6 | 13 | 0.73958 |  | 165 | 355 | 132 | Bilberry | 27.6/16kV | 77M2 | Cable fault on R phase between TE2074T & TE2165R on Tooney Dr, dip G541R fuse opened. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18408 | 2011 | 6 | 14 | 0.50694 |  | 68 | 41 | 36 | Billberry | 27.6/16kV | 77M2 | At 12:10 crews isolated TP7914,TP7915 and TP7916 to replace elbows. 36 customers affected for 68 mins. Billberry 77M2 ID# 18408 | Gloucester | Scheduled Outage
18419 | 2011 | 6 | 15 | 0.38889 |  | 67 | 34 | 30 | Billberry |  | 77M2 | At 9:20am crew isolated TP7923, TP7922 and TP7921 to replace elbows and inserts. 30 customers affected for 67 mins. Billberry 77M2 ID# 18419 | Gloucester | Scheduled Outage
18420 | 2011 | 6 | 15 | 0.5 |  | 63 | 32 | 30 | Billberry |  | 77M2 | At 12:00 crews isolate TP7920, TP7919 and TP7918 to replace elbows and inserts. 30 customers affected for 63 mins. Billberry 77M2 ID# 18420 | Gloucester | Scheduled Outage
18430 | 2011 | 6 | 17 | 0.37847 |  | 147 | 37 | 15 | Billberry | 27.6/16kV | 77M2 | Transformer TP7917 @ 1722 Aspen Village was isolated to allow crew to replace elbows and inserts. 15 customers were affected. Billberry (77M2) | Gloucester | Scheduled Outage
8513 | 2006 | 6 | 18 | 0.76597 |  | 839 | 98 | 7 | Billberry | 27.6/16kV | 77M2 | T756 @ 1749 Bonaventure defective, crew called to replace XFMR. 7 customers. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10664 | 2007 | 6 | 19 | 0.79514 |  | 76 | 220 | 198 | Bilberry | 27.6/16kV | 77M2 | G541R at dip opened due to cable fault between T2075R and T2166R. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6773 | 2005 | 6 | 21 | 0.7375 |  | 28 | 33 | 103 | Bilberry | 27.6/16kV | 77M2 | Fused switch G104B and tx fuse at T5835 blew due to tree branch contact, branches cleared and both switches refused. | Gloucester | Defective Equipment
18450 | 2011 | 6 | 21 | 0.37708 |  | 100 | 52 | 31 | Billberry | 27.6/16kV | 77M2 | Transformer TP7913, TP7912, TP6896 on Teakdale Ave were isolated to allow crew to replace elbows and inserts. 31 customers were affected. Billberry (77M2) | Gloucester | Scheduled Outage
18452 | 2011 | 6 | 21 | 0.5 |  | 70 | 32 | 27 | Billberry | 27.6/16kV | 77M2 | Transformers TP7910, TP7909 and TP7908 on Teakdale were isolated to allow crew to replace elbows and inserts. 27 customers were affected. Billberry (77M2) | Gloucester | Scheduled Outage
18460 | 2011 | 6 | 22 | 0.38889 |  | 166 | 64 | 23 | Billberry | 27.6/16kV | 77M2 | Transformers TP7905, TP7906 and TP7907 on Teakdale were isolated to allow crew to replace elbows and inserts. 23 customers were affected. Billberry (77M2) | Gloucester | Scheduled Outage
18523 | 2011 | 6 | 25 | 0.64792 |  | 50 | 2476 | 5383 | Billerry | 27.6/16kV | 77M2 | White phase line side lead on RX2020 at St Joseph and Boyer burnt off and flashed causing the 77M2 circuit to auto-reclose and the RX2020 to open. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
20874 | 2012 | 6 | 26 | 0.39097 |  | 339 | 62 | 11 | Bilberry | 27.6/16kV | 77M2 | Transformer TP9113 at 1866 Longman was isolated to allow crew to replace leaking transformer. | Gloucester | Scheduled Outage | Repair
20882 | 2012 | 6 | 26 | 0.33333 |  | 432 | 79 | 11 | Bilberry | 27.6/16kV | 77M2 | Isolated and replaced transformer GLTE1642 at 1878 Longman Cres (Leaking oil) | Gloucester | Scheduled Outage | Preventive Maintenance
6826 | 2005 | 6 | 27 | 0.79444 |  | 17 | 1039 | 3667 | Billberry | 27.6/16kV | 77M2 | Rotational load shedding | Gloucester | Loss of Supply | HEPC Load Shedding
18539 | 2011 | 6 | 27 | 0.89583 |  | 62 | 5 | 5 | Bilberry | 27.6/16kV | 77M2 | Transformer #X21860 located at 3681 Innes Rd opened up due to bird contact. | Gloucester | Foreign Interference | Bird
14656 | 2009 | 7 | 3 | 0.088889 |  | 402 | 737 | 110 | Billberry | 27.6/16kV | 77M2 | RX2020 auto-reclosed due to a failed cable at G541 W phase. Faulted section isolated & load restored from alternate source. Innes & Jeanne D'Arc area. No crew available, on call not available due to other problems. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18574 | 2011 | 7 | 3 | 0.33472 |  | 136 | 14 | 6 | Bilberry | 27.6/16kV | 77M2 | Transformer #X23875 and G365 located at 6243 Sundown Cres opened up due to animal contact | Gloucester | Foreign Interference | Animal
20914 | 2012 | 7 | 3 | 0.38958 |  | 209 | 463 | 133 | Billberry Creek | 27.6/16kV | 77M2 | 11 white phase transformers between S22244 and TP8186 on Jeanne D'Arc were interrupted to replace elbows and inserts. | Gloucester | Scheduled Outage
14682 | 2009 | 7 | 8 | 0.3125 |  | 400 | 100 | 15 | Bilberry | 27.6/16kV | 77M2 | TP3458 transformer failed cause unknown. R. Grisel reports transformer was replaced all power restored | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10847 | 2007 | 7 | 11 | 0.70625 |  | 218 | 738 | 287 | Billberry | 27.6/16kV | 77M2 | On the 77M2 All three phases of G566 opened, they were closed and held. No cause found. One pole down red phase of G843 opened as well this was caused by bad cable section between T2224R and T2431R. both are fed from GR12 which also auto-reclosed, as well as two other circuits 77M5 & 77M6 circuits auto reclosed at the same time (and one circuit that is NOT ours the 77M3. We suspect lighning strike and cable fault. (what do you think Travis) | Gloucester | Adverse Weather | Lightning
14727 | 2009 | 7 | 11 | 0.66667 |  | 390 | 312 | 48 | Bilberry TS | 27.6/16kV | 77M2 | G561 Red phase current limiter found blown & G562 Blue phase current limmiter found blown, 48 customers affected and power was restored at 10:30pm. Bliberry TS (77M2). ID#14727. | Gloucester | Adverse Weather | Rain
10859 | 2007 | 7 | 12 | 0.43056 |  | 107 | 18 | 10 | Bilberry | 27.6/16kV | 77M2 | Transformer TE2516 at 1969 Rolling Brook Drive was interrupted for replacement due to heating secondary bushing. | Gloucester | Scheduled Outage | Preventive Maintenance
14732 | 2009 | 7 | 12 | 0.56736 |  | 70 | 19 | 16 | Bilberry | 27.6/16kV | 77M2 | A bird made contact with o/h lines at Tx location X24259, 1906 Boyer causing RX2020 to A/R & fuse to open at this Tx.. | Gloucester | Foreign Interference | Bird
14733 | 2009 | 7 | 12 | 0.57431 |  | 58 | 15 | 16 | Bilberry | 27.6/16kV | 77M2 | Replaced blown fuse on switch feeding transformer X24259 at 1906 Boyer Rd | Gloucester | Foreign Interference | Bird
8721 | 2006 | 7 | 14 | 0.014583 |  | 118 | 20 | 9 | Billberry | 27.6/16kV | 77M2 | Defective transformer GL3788 at 1118 Gabriel was changed. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
10872 | 2007 | 7 | 14 | 0.93958 |  | 118 | 1007 | 512 | Bilberry | 27.6/16kV | 77M2 | GR12 auto-reclosed. Red and Blue phase fuses G843 at Boyer and Huntersrun opperated. Crew refused and closed. No problem found. Heavy rain and no other apparent cause. | Gloucester | Unknown/Other | No Apparent Cause
12834 | 2008 | 7 | 14 | 0.3625 |  | 63 | 5 | 5 | Bilberry | 27.6/16kV | 77M2 | Blown fuse feeding transformer X21856 at 3698 INNES RD due to a bird contact (Crow) | Gloucester | Foreign Interference | Bird
3782 | 2003 | 7 | 15 | 0.28542 |  | 74 | 12 | 10 | Bilberry | 27.6/16kV | 77M2 | The fuse blew at transformer 496 due to a crow affecting 10 customers on St. Joseph Blvd. | Gloucester | Foreign Interference | Bird
18667 | 2011 | 7 | 15 | 0.55833 |  | 440 | 81 | 11 | Bilberry | 13.2kV | 77M2 | Transformer #X23873 located at 1313 Cousineau opened up, defective transformer that was replaced by On Call. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
14762 | 2009 | 7 | 16 | 0.24306 |  | 107 | 23 | 13 | Bilberry | 27.6/16kV | 77M2 | TE2378 @ 6628 Tooney was isolated to replace damaged inserts & elbows that had flashed over during previous switching. Small retail mall affected. | Gloucester | Scheduled Outage | Repair
12915 | 2008 | 7 | 22 | 0.42153 |  | 26 | 2 | 5 | Bilberry | 27.6/16kV | 77M2 | Transformer #X21856 located at 3681 Innes isolated due to bird contact | Gloucester | Foreign Interference | Bird
12928 | 2008 | 7 | 23 | 0.475 |  | 92 | 2 | 1 | Bilberry Creek | 8/4.8kV | 77M2 | Squirrel contact caused fuse to open at transformer X13370 at 5393 Riverside Cres. Refused and transformer restored. | Gloucester | Foreign Interference | Animal
7051 | 2005 | 8 | 2 | 0.45139 |  | 118 | 354 | 180 | Billbery | 27.6/16kV | 77M2 | G541 blue phase switch was popped by apparent pole contact by construction machines, no faults found and fuse not blown. Other phases checked as properly closed. | Gloucester | Foreign Interference | Vehicle
10997 | 2007 | 8 | 4 | 0.30764 |  | 127 | 203 | 96 | Bilberry | 27.6/16kV | 77M2 | Suspected blue phase cable fault on Hunters Run Gate between dip G843 and transformer 2218 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13065 | 2008 | 8 | 17 | 0.30208 |  | 627 | 651 | 178 | Bilberry | 27.6/16kV | 77M2 | T593 @ 1674 Grey Nuns insert flashed over and possible fault on red phase cable from T593 to G396 caused fuse at G433 to open. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
7167 | 2005 | 8 | 19 | 0.03125 |  | 180 | 15 | 5 | Bilberry | 27.6/16kV | 77M2 | 3 phase overhead transformer #5974 at 3605 Innes was isolated for customer to make secondary modifications. | Gloucester | Scheduled Outage | Repair
3924 | 2003 | 8 | 21 | 0.20833 |  | 288 | 283 | 59 | Bilberry | 27.6/16kV | 77M2 | 24/7 crews were dispatched to call and found a rupture SMD fuse. The fuse was replaced and closed but power was not restored as the Current Limiting Fuse had also ruptured. The crew was unaware of this fact and did not do any checks before assuming that full power was restored and left the area. No power calls in the area continued to flow in and regular day shift crew was dispatched and found the problem as a defective U/G primary cable between TE1227 & TE1228. Cable was isolated and full power was restored. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
16796 | 2010 | 8 | 22 | 0.46944 |  | 192 | 442 | 225 | Bilbberry | 27.6/16kV | 77M2 | 24/7 Crew found cable between T714 and T713 at 1728 Meadowview Cres defective. | Gloucester | Defective Equipment
13142 | 2008 | 8 | 23 | 0.83264 |  | 128 | 384 | 180 | BILBERRY | 27.6/16kV | 77M2 | G433R phase blew due to defective cable between G396R and T593. Cable isolated and G433R closed to restsore power. | Gloucester | Defective Equipment
7239 | 2005 | 8 | 30 | 0.33403 |  | 64 | 13 | 12 | Bilberry | 27.6/16kV | 77M2 | Transformer switch for GL0644 at 1596 Boyer rd opened due to squirrel contact | Gloucester | Foreign Interference | Animal
3978 | 2003 | 9 | 1 | 0.97917 |  | 180 | 51 | 17 | Bilberry | 27.6/16kV | 77M2 | Transformer 2858 at 2040 was found to have a defective secondary winding on one leg and was changed. 17 customers on Boyer and Visineau affected. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15051 | 2009 | 9 | 3 | 0.36806 |  | 147 | 17 | 7 | BILBERRY TS | 27.6/16kV | 77M2 | TRANSFORMER TE2152 AT 1738 ASPEN VILLAGE CIRCLE ISOLATED TO ALLOW FOR CHANGING OF ELBOWS AND INSERTS | Gloucester | Scheduled Outage | Construction
9144 | 2006 | 9 | 7 | 0.96389 |  | 423 | 755 | 130 | BILBERRY | 27.6/16kV | 77M2 | GR12 Auto Reclosed and G552 Blue phase blew. Defective Cable between T1630 and T2036. Power restored in Stages. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7303 | 2005 | 9 | 9 | 0.85278 |  | 217 | 348 | 102 | Bilberry | 27.6/16kV | 77M2 | G708 white phase fuse blown. Cable fault between T1758 and T1756. Beausejour. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19160 | 2011 | 9 | 13 | 0.625 |  | 17 | 986 | 3481 | Bilberry | 27.6/16kV | 77M2 | 77M2 circuit locked out during lightning storm. Circuit closed via SCADA and holding. RX2020 auto-reclosed at the same time, as well as upon restoration. | Gloucester | Lightning
13246 | 2008 | 9 | 16 | 0.55556 |  | 40 | 4 | 6 | Bilberry | 27.6/16kV | 77M2 | Transformer #934 located at 1318 St. Jean St isolated to repair/replace broken cut out | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15108 | 2009 | 9 | 16 | 0.38889 |  | 155 | 26 | 10 | Bilberry Creek | 27.6/16kV | 77M2 | TE2137 was isolated to allow under ground crew to replace transformer. | Gloucester | Scheduled Outage | Preventive Maintenance
16959 | 2010 | 9 | 17 | 0.16944 |  | 436 | 3895 | 2954 | Bilberry | 27.6/16kV | 77M2 | RX2020 RWB, A/R/A crews found S26543 blown. RX2020 RWB closed and holding. TP7240 remains off, it was recently energized. | Gloucester | Unknown/Other
16960 | 2010 | 9 | 17 | 0.17014 |  | 78 | 3840 | 2954 | Billberry |  | 77M2 | RX2020 A/R and locked out, patroll found S26543 RWB fuses & arresters blown, cleared, RX2020 closed, power restored. | Gloucester | Defective Equipment
15122 | 2009 | 9 | 18 | 0.4375 |  | 207 | 34 | 10 | Bilberry | 27.6/16kV | 77M2 | Transformer TE1750 was isolated for transformer replacement program, at 1725 Smithers. Nomenclature changed to TP6897. | Gloucester | Scheduled Outage | Preventive Maintenance
19245 | 2011 | 9 | 24 | 0.38125 |  | 139 | 227 | 98 | Bilberry | 27.6/16kV | 77M2 | W phase Tx's from S13747 isolated for elbow & insert upgrades. Beausejour / Hunters Run area. | Gloucester | Scheduled Outage | Preventive Maintenance
19248 | 2011 | 9 | 24 | 0.54653 |  | 173 | 288 | 100 | Bilberry | 27.6/16kV | 77M2 | B phase Tx's from S13747 isolated for elbow & insert upgrades. Beausejour / Hunters Run area. | Gloucester | Scheduled Outage | Preventive Maintenance
19270 | 2011 | 9 | 27 | 0.38403 |  | 120 | 48 | 24 | Billberry |  | 77M2 | At 9:13 crews isolated 3 Transformer on the 77M2 to replace elbows and inserts. 24 customers affected for 120 mins. Billbery (77M2) | Gloucester | Scheduled Outage
19271 | 2011 | 9 | 27 | 0.54028 |  | 62 | 27 | 26 | Billberry | 27.6/16kV | 77M2 | At 12:58 crews isolated 2 transformers on the 77M2 to replace elbows and inserts. 26 customers affected for 62 mins. Billberry (77M2) | Gloucester | Scheduled Outage
17021 | 2010 | 9 | 29 | 0.375 |  | 120 | 24 | 12 | Bilberry | 27.6/16kV | 77M2 | Transformer TP7019 (old # GLTE0593) at 1674 Grey Nuns Drive isolated for cable replacement | Gloucester | Scheduled Outage | Preventive Maintenance
7426 | 2005 | 10 | 5 | 0.43681 |  | 21 | 3 | 8 | BILBERRY | 27.6/16kV | 77M2 | EMERGENCY SWITCHING TO ISOLATE DEFECTIVE ELBOW @ T592W. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
17155 | 2010 | 10 | 21 | 0.68611 |  | 46 | 1582 | 3460 | Bilberry |  | 77M2 | RX2020 tripped during restoration to place it in service while opening the bypass switches , red phase bypass was still closed. RX2020 tripped again on successive attempts to restore power. 77M2 breaker was opened to close RX2020-L1 bypass switches and then the breaker was closed restored picking up all customers. Boyer Rd/Innes Rd area of Orleans. | Gloucester | Unknown/Other
17160 | 2010 | 10 | 22 | 0.38194 |  | 150 | 25 | 10 | Bilberry | 27.6/16kV | 77M2 | TP7017 at 1776 Grey Nuns isolated for the ongoing Grey Nuns Reconfiguration, Job #1243 Step 11. The 10 customers affected were on Grey Nuns Dr & Lumberman Way. | Gloucester | Scheduled Outage | Preventive Maintenance
19617 | 2011 | 11 | 22 | 0.41528 |  | 488 | 73 | 9 | Bilberry Creek | 27.6/16kV | 77M2 | TP7896R at 1749 Hunters Run Dr was isolated to change leaking transformer | Gloucester | Scheduled Outage
19630 | 2011 | 11 | 24 | 0.41319 |  | 95 | 10 | 6 | Bilberry | 27.6/16kV | 77M2 | Transformer #X21870 located at 1917 Markwell Cres opened by crew to transfer plant | Gloucester | Scheduled Outage | Construction
4556 | 2003 | 12 | 4 | 0.49444 |  | 68 | 8 | 7 | 77 | 27.6/16kV | 77M2 | G356W feeding Tx 5943 @ 6239 Sundown was found open due to a defective arrestor . Fuse replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6041 | 2004 | 12 | 11 | 0.079861 |  | 7 | 428 | 3670 | Bilberry | 27.6/16kV | 77M2 | Bilberry 77M2 auto/reclose no apparent load loss, heavy snow fall & high winds. | Gloucester | Adverse Weather
6042 | 2004 | 12 | 11 | 0.0875 |  | 3 | 184 | 3670 | Bilberry | 27.6/16kV | 77M2 | Bilberry 77M2 auto/reclose no apparent load loss, heavy snow fall & high winds. | Gloucester | Adverse Weather
6050 | 2004 | 12 | 11 | 0.46875 |  | 20 | 3 | 9 | Bilberry | 27.6/16kV | 77M2 | Transformer at 2440 St. joseph. Isolated to repair defective hot line clamp. | Gloucester | Adverse Weather
3292 | 2003 | 3 | 23 | 0.50694 |  | 216 | 479 | 155 | Bilberry | 27.6/16kV | 77M2 & 77M6 | 24/7 crew reports S18 switch gear found flashed at Jeanne D'arc & Orleans Blvd. Causing the blue phase fuse to open at G709 & G670. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14455 | 2009 | 6 | 3 | 0.54444 |  | 48 | 8 | 10 | Billberry creek | 27.6/16kV | 77M2(RX2020) | TP6080 at 1447 Gaultois was isolated to allow crew to perfom transformer maintenance. | Gloucester | Scheduled Outage | Preventive Maintenance
10311 | 2007 | 4 | 24 | 0.71875 |  | 780 | 7489 | 3000 | Bilberry | 27.6/16kV | 77M2/GR12 | GR12 tripped due to broken poles & wire down on a lateral run-off to TP2937 (Wal-Mart on Innis) during a wind storm. A section of line was isolated to allow the crew to install switches to isolate the damaged section. A partially installed section of cable was completed to supply TP2937 because of the damage to the pole line. | Gloucester | Adverse Weather | Wind
9422 | 2006 | 10 | 12 | 0.58333 |  | 90 | 26 | 17 | Bilberry | 27.6/16kV | 77M3 | Isolated transformer GL001457 at 1435 Belcourt Blvd for pole replacment | Gloucester | Scheduled Outage | Construction
13832 | 2009 | 1 | 1 | 0.73125 |  | 386 | 7772 | 4041 | Bilberry | 27.6/16kV | 77M5 | G235 has pulled apart on Youville Dr, causing the 77M5 breaker to open, On Call crew repaired switch. During restoration, GR16 auto reclosed and locked out. When closing GR16, caused RX2020 to auto reclose. | Gloucester | Defective Equipment
7775 | 2006 | 1 | 5 | 0.32431 |  | 71 | 8 | 7 | Bilberry | 27.6/16kV | 77M5 | Transformer T980 at St. Joseph & Youville isolated to replace elbows and inserts. | Gloucester | Scheduled Outage | Repair
17482 | 2011 | 1 | 12 | 0.40625 |  | 105 | 10 | 6 | Bilberry | 27.6/16kV | 77M5 | Isolated transformer X40579 at 6173 Renaud Rd for service up-grade | Gloucester | Scheduled Outage | Preventive Maintenance
6131 | 2005 | 1 | 13 | 0.53125 |  | 100 | 8 | 5 | Bilberry | 27.6/16kV | 77M5 | Opened transformer 1187 to move new service | Gloucester | Scheduled Outage | Preventive Maintenance
7849 | 2006 | 1 | 24 | 0.70833 |  | 27 | 112 | 250 | Bilberry | 27.6/16kV | 77M5 | T1611 red phase at 1520 Forest Valley Dr. S672R opened for isolation. 20 transformers out. Non vented elbows load had to be dropped. | Gloucester | Foreign Interference | Vehicle
3180 | 2003 | 2 | 10 | 0.47222 |  | 10 | 717 | 4300 | Bilberry | 27.6/16kV | 77M5 | Cable insert failed under Hold Off while removing cover/cap in preparation to install elbow. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10018 | 2007 | 2 | 12 | 0.77986 |  | 408 | 141 | 200 | Bilberry | 27.6/16kV | 77M5 | TE1615 at 6063 Meadowhill failed. Blue phase loop from G672 isolated ( 24 xfmrs ) to install vented inserts at TE1616 & TE1614, loop restored leaving TE1615 isolated. Transformer replaced & restored to normal. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7952 | 2006 | 2 | 20 | 0.20347 |  | 157 | 7450 | 4000 | Bilberry | 27.6/16kV | 77M5 | 77M5 @ Bilberry Creek tripped @ 4:53. Crews dispatched and found the fault to be between S9 and G675 underground trunk cable. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6224 | 2005 | 2 | 22 | 0.43194 |  | 63 | 13 | 12 | Billberry | 27.6/16kV | 77M5 | TE2292 isolated to repair insert on transformer Ashmount St Glou | Gloucester | Scheduled Outage | Repair
14068 | 2009 | 3 | 16 | 0.63194 |  | 86 | 3 | 2 | Billberry | 27.6/16kV | 77M5 | Crew replaced faulty three phase switch G840 @ 1400 Youville dr. feeding one transformer T2212. | Gloucester | Defective Equipment
10189 | 2007 | 3 | 27 | 0.43611 |  | 4 | 281 | 4210 | Bilberry | 27.6/16kV | 77M5 | While energizing the 77M5 cable from G675 to check phasing, The 77M5 breaker opened due to a blue phase cable fault. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
3309 | 2003 | 3 | 31 | 0.3625 |  | 88 | 9 | 6 | Bilberry TS | 27.6/16kV | 77M5 | Transformer T421 interrupted due to defective fuse dip G241R, sw repaired and load restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8160 | 2006 | 4 | 19 | 0.41458 |  | 103 | 17 | 10 | BILBERRY | 27.6/16kV | 77M5 | T1611 AT 1520 FOREST VALLEY DR. ISOLATED TO ALLOW CREW TO CHANGE RUSTY TRANSFORMER. | Gloucester | Scheduled Outage | Repair
8165 | 2006 | 4 | 19 | 0.375 |  | 120 | 18 | 9 | Billberry | 27.6/16kV | 77M5 | Transformer GLTE 1611 at 1520 Forest was isolated and replaced | Gloucester | Scheduled Outage | Repair
14339 | 2009 | 5 | 11 | 0.27639 |  | 376 | 5129 | 4210 | Bilberry | 27.6/16kV | 77M5 | White phase line side lead of G675 at forest Valley & St Joseph came loose, casuing 77M5 out of Bilberry to open. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16076 | 2010 | 5 | 11 | 0.39722 |  | 138 | 23 | 10 | Bilberry | 27.6/16kV | 77M5 | Transformer at 6173 Renaud Rd isolated for pole change, unable to confirm XFRM # in OMS | Gloucester | Scheduled Outage | Preventive Maintenance
12436 | 2008 | 5 | 13 | 0.42222 |  | 112 | 19 | 10 | Bilberry | 27.6/16kV | 77M5 | TE1601 at 1479 Forest Valley was isolated & replaced. | Gloucester | Scheduled Outage | Repair
12437 | 2008 | 5 | 13 | 0.52847 |  | 119 | 26 | 13 | Bilberry | 27.6/16kV | 77M5 | TE1589 at 1437 Forest Valley was isolated & replaced. | Gloucester | Scheduled Outage | Repair
16094 | 2010 | 5 | 17 | 0.76181 |  | 218 | 51 | 14 | Bilberry |  | 77M5 | TE2252 & G458 at 1410 Youville Dr were isolated to allow crews to replace the elbows & inserts & change the nomeclature. | Gloucester | Scheduled Outage | Preventive Maintenance
8332 | 2006 | 5 | 20 | 0.62986 |  | 310 | 26 | 6 | Bilberry | 27.6/16kV | 77M5 | Defective Transformer 421 on Notre Dame, required replacement due to burnt up windings. O/H Switch G241R was opened interrupting power to 1 additional customer while the crew examined transformer 421, which had an internal blown switch. Power was restored to the additional 1 customer and the remaining 5 customers were restored when the transformer was changed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14389 | 2009 | 5 | 21 | 0.55278 |  | 43 | 293 | 409 | Billberry | 27.6/16kV | 77M5 | Crane contacted the o/h @ 2743 Page rd. causing the GR16 to open. | Gloucester | Foreign Interference | Vehicle
5253 | 2004 | 6 | 4 | 0.46875 |  | 23 | 1521 | 4144 | Bilberry | 27.6/16kV | 77M5 | Hi Hoe caused 27kv overhead line to slap together at 8030 Innes RD . E. Neumann reports overhead line ind. Flash marks, but ok to re-energize circuit. All power stored as of 11:38. | Gloucester | Defective Equipment | Foreign Object
18313 | 2011 | 6 | 6 | 0.53889 |  | 90 | 72 | 48 |  |  | 77M5 | Transformers TP7971R, TP7970B, TP7969B and TP7968B on Summerfield were isolated to allow crew to perform elbow and inserts replacement. 48 customers were affected. Billberry 77M5 | Gloucester | Scheduled Outage
8436 | 2006 | 6 | 7 | 0.0625 |  | 185 | 540 | 175 | Bilberry | 27.6/16kV | 77M5 | A racoon made contact with the O/H and caused the G373W and G852W to blow on Renaud Rd. Other calls came in at the same time making the outage look bigger then it actually is. | Gloucester | Foreign Interference | Animal
8437 | 2006 | 6 | 7 | 0.30278 |  | 481 | 524 | 4210 | Bilberry | 27.6/16kV | 77M5 | Defective cable section between S16R and T2356 on the 77M5 circuit. Defective fault indicator at T2297, caused the 77M5 breaker to trip. Isolated defective cable section and restoring power to 60 customers. When S16RT2356 was closed, it blew the fuse at S163R. System office was unaware of this outage, and the 24/7 crew were dismissed. Power was restored to the remaining customers (40) at 9:31. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18333 | 2011 | 6 | 8 | 0.41597 |  | 166 | 82 | 35 | Billberry | 27.6/16kV | 77M5 | 77M5 circuit auto-reclosed during Swithching for an isolation. fuse blew at SC9416. Crew sectionalized and isolated. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
18379 | 2011 | 6 | 9 | 0.91667 |  | 1 | 4 | 250 | Bilberry | 27.6/16kV | 77M5 | Power lost to customers during switching. Primary parallel had been made, then on second loop parallel was made, a fuse had blown in switchSC9416 and when crew went to break parallel one minute load loss. Fuses at SC9416-F changed from 40 amp to 65 amp | Gloucester | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
14513 | 2009 | 6 | 11 | 0.40694 |  | 17 | 1193 | 4210 | Bilberry | 27.6/16kV | 77M5 | Caustomer reports bird in overhead circuit 1455 Youville Dr. Also RX2020 has opened. | Gloucester | Foreign Interference | Bird
6709 | 2005 | 6 | 13 | 0.97569 |  | 82 | 15 | 11 | Bilberry | 27.6/16kV | 77M5 | Transformer TE1608 at 6078 Rideaucrest isolated for replacement due to oil leaking. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18399 | 2011 | 6 | 14 | 0.20903 |  | 92 | 247 | 161 | Bilberry | 27.6/16kV | 77M5 | G672 red phase at 1708 St Joseph was found opened, no FCI's flagged, cable from G672 opened and customers picked up from the SC2425, the other end of the loop. | Gloucester | Unknown/Other | No Apparent Cause
18403 | 2011 | 6 | 14 | 0.41389 |  | 101 | 49 | 29 | Billberry |  | 77M5 | Transformers TP7960 and TP7961 were isolated to allow crew to replace elbows and inserts. 29 customers were affected. Billberry (77M5) | Gloucester | Scheduled Outage
18427 | 2011 | 6 | 16 | 0.41667 |  | 90 | 6 | 4 | Billberry |  | 77M5 | TP7958 was isolated for elbow, and insert replacement. | Gloucester | Scheduled Outage | Repair
10708 | 2007 | 6 | 22 | 0.24722 |  | 86 | 533 | 572 | Billberry | 27.6/16kV | 77M5 | Crow in the overhead at Du Palais and Mer Blu opened 2 sets of fusses and GR16 recloser | Gloucester | Foreign Interference | Animal
10710 | 2007 | 6 | 22 | 0.44028 |  | 91 | 659 | 572 | Bilberry | 27.6/16kV | 77M5 | GR16 opened (in single shot for H1) when a squirrell made contact at a cut out on Navan Rd | Gloucester | Foreign Interference | Animal
18464 | 2011 | 6 | 22 | 0.63542 |  | 92 | 273 | 178 | Bilberry | 27.6/16kV | 77M5 | G672 white phase fuse had blown while restoing cable loop to normal. No defective equipment found, all load restored from SC2425 end of loop. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
14600 | 2009 | 6 | 23 | 0.80625 |  | 399 | 66 | 10 | Bilberry | 27.6/16kV | 77M5 | Transformer T2582W at 2207 Nature Trail Cr isolated to replace defective transformer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3615 | 2003 | 6 | 27 | 0.37847 |  | 94 | 2 | 1 | Bilberry | 27.6/16kV | 77M5 | GR15 reclosure auto reclosed 34 customers affected in auto reclose. Crews dispatcted to patrol circuit. 1600 St Joesph reports all out. D. Martin reports fuse blown at transformer to pumping station. D. Martin reports fuse cutout replaced all power restored . | Gloucester | Unknown/Other | No Apparent Cause
20898 | 2012 | 6 | 28 | 0.40347 |  | 78 | 131 | 1559 | Billberry | 27.6/16kV | 77M5 | Crow caused fused switch G842 @ 1825 St. Joseph blvd to open, also causing the 77M5 breaker to open. (circuit was under h/o) | Gloucester | Foreign Interference | Animal
6859 | 2005 | 7 | 2 | 0.94722 |  | 175 | 35 | 12 | Bilberry | 27.6/16kV | 77M5 | T 2838 at 1946 Montclair replaced due to noise and arching in transformer | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20931 | 2012 | 7 | 5 | 0.38611 |  | 454 | 53 | 7 | Bilberry | 27.6/16kV | 77M5 | Transformer TE2109 at 1641 Des Ravins was isolated to allow crew to replace leaking transformer. | Gloucester | Scheduled Outage | Repair
3699 | 2003 | 7 | 7 | 0.27361 |  | 96 | 2 | 1 | Bilberry TS | 27.6/16kV | 77M5 | Bilberry 77M5 auto reclose, R phase fuse feeding the Ottawa pumping station at 1600 St. Joseph Blvd found open but no apparent cause found for the blown fuse. Fuse replaced & closed to restore the pumping station. | Gloucester | Unknown/Other | No Apparent Cause
14684 | 2009 | 7 | 8 | 0.33333 |  | 380 | 95 | 15 | Bilberry Creek | 27.6/16kV | 77M5 | TP3458 was isolated to allow crews to replace defective transformer @ 412 Keith St | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6903 | 2005 | 7 | 11 | 0.375 |  | 5 | 351 | 4210 | Bilberry | 27.6/16kV | 77M5 | 77M5 cct tripped & locked out, H- 1 closed the cct after 5 minutes& it held. Patrol of the cct found a blown arrestor on customer owned line at 1510 St Joseph. ( City of Ottawa ) | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8718 | 2006 | 7 | 13 | 0.65625 |  | 75 | 112 | 90 | Bilberry | 27.6/16kV | 77M5 | Blue phase cable section T2621 & G796 found faulted. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8744 | 2006 | 7 | 17 | 0.58403 |  | 65 | 1622 | 4200 | Bilberry | 27.6/16kV | 77M5 | A blown splice on the R phase cable sec bet transformer T2132 @ 1784 Robinwood and T2164 @ 1858 Thornecrest. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
8745 | 2006 | 7 | 17 | 0.72986 |  | 167 | 320 | 115 | Billberry | 8/4.8kV | 77M5 | Fuse @ S21B found blown. Blue phase section of cbl between S21B and T2866 was thaught to have faulted. Crew checked cable and isolated section. All blue phase customers restored. | Gloucester | Unknown/Other | No Apparent Cause
12914 | 2008 | 7 | 22 | 0.35208 |  | 95 | 13 | 8 | Bilberry | 27.6/16kV | 77M5 | Transformer #GL005219 located at 2223 Page Rd isolated due to squirrel contact. | Gloucester | Foreign Interference | Animal
12920 | 2008 | 7 | 22 | 0.6625 |  | 76 | 13 | 10 | Bilberry Creek | 27.6/16kV | 77M5 | G576W on Page Rd refused out of Bilberry on the 77M5. Fuse blew due to age. 10 customers affected, power restored at 17:10. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
3774 | 2003 | 7 | 23 | 0.73333 |  | 86 | 1 | 1 | Bilberry | 27.6/16kV | 77M5 | Hydro One reports 77M5 circuit auto reclosed. Lightening storm in the area may have caused outage. Also scada ind GR15 as auto reclosed. 24/7 dispatched to patroll circuit. Andy reports red phase opened at pumping station. Andy reports s986 red phase fuse closed restoring all 3 phase load. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12953 | 2008 | 7 | 26 | 0.60694 |  | 341 | 13987 | 5264 | Bilberry | 27.6/16kV | 77M5 | Cct tripped during thunderstorm,. 48M3, 48M5 a/r, GR16 & 77M5 all tripped at the same time. No reports of problems from police, FD, tried to restore, breaker tripped. Line sectionalized at GR15, breaker closed & held for apprx 2 minutes at which time GR15 blew apart tripping the breaker. The recloser was cleared from the line, & as there was some concern over the condition of G977 by-pass switches at GR15, these were not operated as there were other options. Majority of customers restored at this time. After attempts to operate 2 separate scada mate switches by 24/7 failed, O/C stations were called in. At this time the o/h section W. of GR15 had been patrolled multiple times, 77M5 was opened, G977 by-pass switches closed to restore cct in original configuration, breaker tripped. G977 opened & majority of customers restored again. Stations crew were able to operate scada mate switches from alternate supply & load was restored without further problems. Unknown why cct would not restore from G977. | Gloucester | Lightning
8873 | 2006 | 7 | 29 | 0.9875 |  | 103 | 15 | 9 | Bilberry | 27.6/16kV | 77M5 | Transformer T3021B at 2164 Cavalier Way hit by vehicle and damaged. Transformer was cracked and had to be replaced. Vehicle did not remain on site. | Gloucester | Foreign Interference | Vehicle
12973 | 2008 | 7 | 30 | 0.42361 |  | 150 | 28 | 11 | BILBERRY | 27.6/16kV | 77M5 | Transformer #TE1582 at 1406 Forest Valley Dr isolated to allow for transformer change | Gloucester | Scheduled Outage
12976 | 2008 | 7 | 30 | 0.42292 |  | 239 | 48 | 12 | Billberry | 27.6/16kV | 77M5 | TE1582W (new TP6346) on forest valley dr. was isolated to replace the transformer. | Gloucester | Scheduled Outage | Repair
8910 | 2006 | 8 | 2 | 0.74931 |  | 273 | 3379 | 4210 | Bilberry | 27.6/16kV | 77M5 | A cable fault bet S35 and S17130 on the new trunk feeder on the Innes Rd by pass/Navan Rd. The curcuit had to be sectionalize to find the fault, the curcuit was on and off to find the fault. Also blown arrester at G780W, causing fuse to blow. Repairs made and switch closed in. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16712 | 2010 | 8 | 10 | 0.76667 |  | 127 | 273 | 129 | Bilberry | 27.6/16kV | 77M5 | Transformer X19201 @ 6173 Renaud and switch G373W @ 6147 Renaud opened due to bird contact. | Gloucester | Foreign Interference | Bird
13044 | 2008 | 8 | 12 | 0.40625 |  | 92 | 18 | 12 | Bilberry Creek | 27.6/16kV | 77M5 | TE1602 at 1488 Forest Valley was isolated and changed due to an oil leak, new TP6348 installed | Gloucester | Scheduled Outage | Repair
16720 | 2010 | 8 | 12 | 0.42778 |  | 216 | 36 | 10 | Billberry | 27Kv | 77M5 | T2581 @ 2213 Nature trail was isolated to allow crew to replace elbow and inserts and remove slab from base to clean out dirt off cables | Gloucester | Scheduled Outage
3908 | 2003 | 8 | 16 | 0.55139 |  | 181 | 3 | 1 | Bilberry | 27.6/16kV | 77M5 | Bird made contact with cut-out at Tx959, 1426 St Joseph. | Gloucester | Foreign Interference | Bird
13069 | 2008 | 8 | 18 | 0.041667 |  | 285 | 59 | 52 | Billberry Creek | 27.6/16kV | 77M5 | A car hit T2656, at 6072 Longleaf, knocking it from its base, requiring isolation and replacement | Gloucester | Foreign Interference | Vehicle
7181 | 2005 | 8 | 22 | 0.54236 |  | 29 | 2 | 4 | Bilberry | 27.6/16kV | 77M5 | Isolated Transformer # 2874 at 1585 Belleterre to do emergency repair | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15043 | 2009 | 8 | 31 | 0.76458 |  | 422 | 56 | 8 | Billberry | 27.6/16kV | 77M5 | transformer TP5213 @ 109 whispering winds way was replaced due to an oil leak. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
13183 | 2008 | 9 | 3 | 0.41736 |  | 104 | 17 | 10 | Bilberry | 27.6/16kV | 77M5 | Transformer TE1825 @ 6052 Meadowglen was isolated to replace rusted tranformer. | Gloucester | Scheduled Outage | Repair
9189 | 2006 | 9 | 9 | 0.76875 |  | 7 | 58 | 499 | Bilberry | 27.6/16kV | 77M5 | Report of switch G208 sparking. GR16 open to allow crew to install jumper on G208. Then GR16 closed. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
13209 | 2008 | 9 | 9 | 0.50139 |  | 87 | 17 | 12 | Bilberry | 27.6/16kV | 77M5 | Transformer T2576 at2241 Nature Trail isolayed for replacement due to oil leak. New transfomer # TP 3636W | Gloucester | Scheduled Outage | Repair
16911 | 2010 | 9 | 9 | 0.43333 |  | 159 | 26 | 10 | Billbery Creek | 27.6/16kV | 77M5 | transformer at 6117 Forest Glen was isolated to allow crews to replace defective transformer. | Gloucester | Scheduled Outage | Preventive Maintenance
15099 | 2009 | 9 | 14 | 0.38333 |  | 184 | 37 | 12 | Bilberry | 27.6/16kV | 77M5 | TE1843 at 6042 Willowbark isolated for transformer replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
9267 | 2006 | 9 | 21 | 0.42569 |  | 207 | 21 | 6 | Billberry | 27.6/16kV | 77M5 | T2500 @ 3080 innes rd isoleted to allow contractor to upgrade secondary | Gloucester | Scheduled Outage | Construction
7436 | 2005 | 10 | 7 | 0.87778 |  | 482 | 161 | 20 | BILBERRY | 27.6/16kV | 77M5 | Defective transformer T2614 on Pineglade was isolated and replaced. Delays in looking for stock and vehicle breakdown added significant time to this outage. | Gloucester | Defective Equipment
19440 | 2011 | 10 | 22 | 0.34514 |  | 157 | 288 | 110 | Bilberry | 27.6/16kV | 77M5 | Insert elbow replacment between SE22 and TP7942 on 77M5 on Street maple Run and Red Willow | Gloucester | Scheduled Outage | Preventive Maintenance
19442 | 2011 | 10 | 22 | 0.50139 |  | 106 | 154 | 87 | Bilberry | 27.6/16kV | 77M5 | 77M5 insert elbow replacement on 6 red phase transformers on Red Willow and Des Ravins in Gloucester. | Gloucester | Scheduled Outage | Preventive Maintenance
19473 | 2011 | 10 | 26 | 0.38194 |  | 187 | 293 | 94 | Bilberry Creek | 27.6/16kV | 77M5 | 5 transformers in the Heritage Park and Tealwood area were isolated to allow crews to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
19474 | 2011 | 10 | 26 | 0.54167 |  | 156 | 192 | 74 | Bilberry Creek | 27.6/16kV | 77M5 | 6 transformers on Heritage Park and Oak Meadows Dr. Were isolated to allow crews to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
19487 | 2011 | 10 | 28 | 0.39236 |  | 158 | 211 | 80 | Bilberry | 27.6/16kV | 77M5 | 8 transformers isolated in the Maple Run/Des Ravins Place area for elbow and insert replacement. | Gloucester | Scheduled Outage
7571 | 2005 | 11 | 6 | 0.71111 |  | 38 | 127 | 200 | Billberry | 27.6/16kV | 77M5 | Tree limb has fallen on the O/H of circuit 77M5/GR16 at 2544 Page, GR16 opened, tree cleared and recloser closed. | Gloucester | Adverse Weather | Lightning
17232 | 2010 | 11 | 6 | 0.375 |  | 391 | 59 | 9 | BILBERRY | 27.6/16kV | 77M5 | Transformer X40582 at 6208 Renaud Rd isolated to transfer plant | Gloucester | Scheduled Outage | Construction
5881 | 2004 | 11 | 13 | 0.67708 |  | 125 | 2 | 1 | Bilberry | 27.6/16kV | 77M5 | A broken insulator in TE2725 was repaired & a fuse at G984 replaced to restore power to 1438 Youville , Jim Keay Ford. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4488 | 2003 | 11 | 20 | 0.41319 |  | 87 | 14 | 10 | Bilberry | 27.6/16kV | 77M5 | Transformer TE2865W isolated to replace it due to leaks. | Gloucester | Scheduled Outage | Repair
13645 | 2008 | 11 | 20 | 0.5 |  | 110 | 16 | 9 | Billberry | 8/4.8kV | 77M5 | Isolated transformer X18945 at 2687 Page rd and relocated transformer to new pole | Gloucester | Scheduled Outage | Construction
19628 | 2011 | 11 | 24 | 0.40625 |  | 510 | 136 | 16 | Bilberry | 27.6/16kV | 77M5 | TP7943 at 6066 Red Willow was isolated to replace leaking transformer. | Gloucester | Scheduled Outage | Repair
5956 | 2004 | 12 | 1 | 0.45139 |  | 105 | 114 | 65 | Bilberry | 27.6/16kV | 77M5 | Switch G373W found blown, suspect tree contacts, 2 trees removed. | Gloucester | Tree Contacts | Inadequate Trimming
19683 | 2011 | 12 | 5 | 0.51042 |  | 188 | 162 | 179 | Bilberry Creek | 27.6/16kV | 77M5 | Crew had an Elbow flash on them while breaking parallel on Valley Field, Crew is OK, crew replaced the transformer at 6091 Forest Valley. | Gloucester | Defective Equipment
19695 | 2011 | 12 | 6 | 0.39583 |  | 310 | 52 | 10 | Bilberry | 27.6/16kV | 77M5 | Isolated and replaced transformer GLTE1598 at 6069 Valley Field Crers (leaking oil) | Gloucester | Scheduled Outage | Repair
13717 | 2008 | 12 | 8 | 0.10694 |  | 347 | 58 | 10 | Bilberry | 27.6/16kV | 77M5 | Defective TP3472 at 617 Amelia was replaced by oncall crew. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7777 | 2006 | 1 | 5 | 0.58333 |  | 30 | 20 | 40 | Bilberry | 27.6/16kV | 77M6 | Transformer TE2942 at 1344 Belcourt isolated to replace defective switches G301. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
17508 | 2011 | 1 | 22 | 0.49167 |  | 92 | 8 | 5 | Bilberry | 27.6/16kV | 77M6 | Replaced blown fuse for transformer X17261 1943 St Joseph Blvd (Squirrel contact) | Gloucester | Foreign Interference | Animal
9969 | 2007 | 1 | 25 | 0.77778 |  | 30 | 1 | 2 | Billberry | 12/7.2kV | 77M6 | At 18:20 trans GL5815 was isolated at 2795 St Pierre St in order to repair a broken trans lead | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
13932 | 2009 | 2 | 3 | 0.67708 |  | 173 | 257 | 89 | Billberry | 27.6/16kV | 77M6 | G595 @ Notre Dame and Leblanc opened due to no apparent cause. No fault indicators were flagged on transformers. Crew refused and closed. | Gloucester | Unknown/Other | No Apparent Cause
6181 | 2005 | 2 | 5 | 0.36736 |  | 79 | 5 | 4 | Bilberry | 27.6/16kV | 77M6 | changed over to a new line: transformer 1184 @ 3817 Innes Road | Gloucester | Scheduled Outage | Construction
7917 | 2006 | 2 | 15 | 0.4625 |  | 112 | 39 | 21 | BILBERRY | 27.6/16kV | 77M6 | XMERS T3197, 3203, & 3196 OUT OF SERVICE TO REPLACE CONNECTIONS. JEAN D'ARC/ST. JOSEPH/WOODCLIFF. | Gloucester | Scheduled Outage | Construction
6220 | 2005 | 2 | 20 | 0.44514 |  | 569 | 598 | 150 | Bilbery | 27.6/16kV | 77M6 | At S19, Reliability suspected a bad u/g cable after high potting and meggaring cable. On-call crew thumped cable and proved good. Flashed insulators were found at S19. Last customers restored after switchs in 2 txs had to be closed. | Gloucester | Defective Equipment
20079 | 2012 | 2 | 29 | 0.41667 |  | 180 | 165 | 55 | Bilberry | 27.6/16kV | 77M6 | 5 transformer were isolated on Kamouraska & Hartland streets in Orleans to change elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
12091 | 2008 | 3 | 3 | 0.19583 |  | 417 | 182 | 114 | Billberry | 27.6/16kV | 77M6 | TE1875 hit by snow plow and needed to be replaced. Isolation needed to be expanded, due to non-vented elbows in transformers. Transformer replaced by on-call crew and power restored. | Gloucester | Foreign Interference
20113 | 2012 | 3 | 3 | 0.88403 |  | 224 | 1925 | 5493 | Billberry | 27.6/16kV | 77M6 | 77M6 (carrying 77M2) tripped. Calls to OFD & OPD all clear. At 19:20 OPD report sparkin wires at 2470 St.Joseph (sourced from 77M2). CS26844 openned via SCADA and 77M6 breaker closed with H1. 5084 customers restored. Larry Sisson & Chris Sommers patrolled and found twisted wires in the rear of 2454/2470 St.Joseph. | Gloucester | Adverse Weather | Wind
20137 | 2012 | 3 | 7 | 0.42917 |  | 207 | 224 | 65 | Billberry | 27.6/16kV | 77M6 | A red phase section of the 77M6 including red phase transformers TP7583, TP7584, TP7585, TP7586, TP7587, TP7588, TP7589, was isolated to allow Hydro Ottawa crews to change elbows & inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
17692 | 2011 | 3 | 9 | 0.66111 |  | 102 | 104 | 61 | Bilberry | 27.6/16kV | 77M6 | G537 white phase found blown and patrol found nothing. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17693 | 2011 | 3 | 9 | 0.83333 |  | 55 | 2 | 2 | Bilberry | 27.6/16kV | 77M6 | Transformer #X17906 located at 1581 Belleterre St opened up due to bird contact | Gloucester | Foreign Interference | Bird
6264 | 2005 | 3 | 11 | 0.45 |  | 190 | 532 | 168 | Bilberry | 27.6/16kV | 77M6 | SE19 isolated to all crews to replace SE19 switch gear. 168 Customers affected in planned power outage. | Gloucester | Scheduled Outage | Repair
6267 | 2005 | 3 | 12 | 0.77917 |  | 349 | 57 | 10 | Bilberry | 27.6/16kV | 77M6 | Bad insert found at T2695. Performed switching to restore power. | Gloucester | Defective Equipment
6271 | 2005 | 3 | 12 | 0.44931 |  | 344 | 280 | 183 | Billberry | 27.6/16kV | 77M6 | The H1B bushing at transformer T1982W @ 1583 Des Serins failed. The fault caused the G703W phase to blow and the GR11 and 77M6 to Auto reclosed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20155 | 2012 | 3 | 13 | 0.38403 |  | 151 | 194 | 77 | Bilberry | 27.6/16kV | 77M6 | Transformers TP8029, 8030, 8031, 8032, 8033, 8034 and 8035 at Beausejour/Belcourt in Orleans were isolated to allow crew to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
20190 | 2012 | 3 | 21 | 0.4 |  | 158 | 390 | 148 | Billberry | 27.6/16kV | 77M6 | 12 transformers in the Orleans blvd , Belcourt area were isolated for elbow and insert replacement. 148 customers were interrupted. | Gloucester | Scheduled Outage | Preventive Maintenance
14116 | 2009 | 3 | 30 | 0.28264 |  | 98 | 3095 | 1895 | Bilberry | 27.6/16kV | 77M6 | Circuit A/R, did not pick up all load. Customer calls indicated RX2019 tripped. On arrival at RX2019, crew found control panel blank, unable to confirm status. Crew proceeded with patrol of o/h line beyond RX2019 & found no problems. Scada group advised crew of method to activate RX2019 control panel, same closed locally to restore all customers. | Gloucester | Unknown/Other | No Apparent Cause
17815 | 2011 | 3 | 31 | 0.38889 |  | 560 | 93 | 10 | Billberry | 27.6/16kV | 77M6 | TP2200 at 1731 SilverBark was isolated to allow crews to replace leaking transformer and drain-all to clean contaminated soil. 10 customers affected | Gloucester | Scheduled Outage
8090 | 2006 | 4 | 1 | 0.35208 |  | 163 | 3 | 1 | BILBERRY | 27.6/16kV | 77M6 | BROKEN SWITCH G634 CAUSED RED PHASE OF G363 TO OPEN. THIS CAUSED LOBLAWS TO BE FEED ONLY ON TWO PHASES. CREW ISOLATED AND REPAIRED G364 AND RESTORED LOAD TO LOBLAWS. (PLACE D'ORLEANS) | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3315 | 2003 | 4 | 2 | 0.86458 |  | 536 | 89 | 10 | Bilberry TS | 27.6/16kV | 77M6 | Transformer TE1795 was hit by a vehicle moving it a few feet and causing supply fuse to blow. | Gloucester | Foreign Interference | Vehicle
17828 | 2011 | 4 | 4 | 0.37639 |  | 613 | 143 | 14 | Bilberry | 27.6/16kV | 77M6 | TE2194 was isolated to allow crew to replace leaking transformer on Winter Rose. | Ottawa | Scheduled Outage
20278 | 2012 | 4 | 4 | 0.39236 |  | 192 | 474 | 148 | Billbery | 27.6/16kV | 77M6 | Crews isolated the transformers in the Champneuf and Rodin area to allow them to replace the elbows and inserts | Gloucester | Scheduled Outage | Preventive Maintenance
12253 | 2008 | 4 | 8 | 0.41667 |  | 380 | 51 | 8 | Bilberry Creek | 27.6/16kV | 77M6 | TP5751R transformer @ 1699 Country Walk in Orleans was isolated to allow crews to clean up oil leak. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17878 | 2011 | 4 | 11 | 0.275 |  | 190 | 11691 | 4550 | Bill berry | 27.6/16kV | 77M6 | 77M6 breaker A/R then tripped open, RX2018 tripped open at sam time. M6 circuit sectionalized at CS17181 & CS14140 then CS18617 closed to restore some customers Crews reported RX2019 damaged and evidence of phase to phase tracking, isolated CS17181 & CS15245 closed to restor load. RX2018 would not operate VIA SCADA, Local controls or Manual operation, RX2018-L1 closed to restore all Load | Gloucester | Adverse Weather | Rain
20316 | 2012 | 4 | 13 | 0.38611 |  | 178 | 134 | 45 | Bilberry | 27.6/16kV | 77M6 | 4 transformes isolated in the Notre Dame & Barona area to replace elbows & inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
20320 | 2012 | 4 | 13 | 0.55972 |  | 164 | 109 | 40 | Bilberry | 27.6/16kV | 77M6 | 3 transformers were isolate on 77M6 in the Bonneville & St Joseph area. To allow crews to replace inserts and elbows. | Gloucester | Scheduled Outage | Preventive Maintenance
20334 | 2012 | 4 | 16 | 0.3875 |  | 217 | 163 | 45 | Bilberry | 27.6/16kV | 77M6 | At 09:18am crews isolated 77M6 red phase between G213R and G122R for elbow and insert replacement. 45 customers affected for 45 mins. Billberry 77M6 ID# 20334 | Gloucester | Scheduled Outage
20340 | 2012 | 4 | 17 | 0.49306 |  | 230 | 188 | 49 | Bilberry | 27.6/16kV | 77M6 | At 11:50 4 transformers between G213B and G122B were isolated to allow crews to replace elbows and inserts. 49 customers were affected for 230 minutes. Bilberry (77M6) ID#20340 | Gloucester | Scheduled Outage | Preventive Maintenance
8163 | 2006 | 4 | 19 | 0.525 |  | 166 | 36 | 13 | BILBERRY | 27.6/16kV | 77M6 | T1757R ON BEAUSEJOUR ISOLATED TO REPLACE RUSTED TRANSFORMER. | Gloucester | Scheduled Outage | Repair
8172 | 2006 | 4 | 20 | 0.40972 |  | 269 | 49 | 11 | Bilberry | 27.6/16kV | 77M6 | Transformer TE1555 at 6340 Beausejour in Gloucester isolated for replacement. | Gloucester | Scheduled Outage | Repair
15959 | 2010 | 4 | 20 | 0.41597 |  | 157 | 37 | 14 | Bilberry | 27.6/16kV | 77M6 | Transformer at 7884 Decarie was isolated to allow crews to replace swollen elbows and inserts. | Gloucester | Scheduled Outage | Repair
20360 | 2012 | 4 | 20 | 0.89028 |  | 709 | 3736 | 4995 | Bilberry | 27.6/16kV | 77M6 | Pole fire at 2656 St. Joseph Blvd. Caused 77M6 circuit to auto reclose and lock out. Load picked up in sections. | Gloucester | Adverse Environment | Fire
20407 | 2012 | 4 | 28 | 0.72639 |  | 129 | 4 | 2 | Billberry | 27.6/16kV | 77M6 | TP7579 at 1705 Orleans Blvd. was isolated to allow Hydro Ottawa crews to install new 27kV vented elbows and new inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
18086 | 2011 | 5 | 3 | 0.38333 |  | 128 | 28 | 13 | Bilbery Creek | 27.6/16kV | 77M6 | TP6855 at 1230 Marenger was isolated to allow contactor to pull in new secondary. | Gloucester | Scheduled Outage | Construction
3410 | 2003 | 5 | 7 | 0.39583 |  | 150 | 28 | 11 |  | 27.6/16kV | 77M6 | To replace leaking transformer TE1556 at 6360 Beausejour Dr. | Gloucester | Scheduled Outage | Repair
20468 | 2012 | 5 | 7 | 0.38472 |  | 157 | 89 | 34 | Bilberry | 27.6/16kV | 77M6 | Transformers TP8080, 8081, 8082, 8083 on des Serins was isolated to allow crew to replace leaking transformer and replace elbows and inserts. | Gloucester | Scheduled Outage | Repair
8285 | 2006 | 5 | 12 | 0.91528 |  | 332 | 89 | 16 | Bilberry | 27.6/16kV | 77M6 | Switch G802 on St Joesph BLVD blue phase defective. On call crew called in and replaced all 3 switches. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5139 | 2004 | 5 | 13 | 0.41181 |  | 235 | 31 | 8 | Bilberry | 27.6/16kV | 77M6 | T1769 on Beausejour isolated to remove soil contaminated with oil from previous oil spill. | Gloucester | Scheduled Outage | Repair
12438 | 2008 | 5 | 15 | 0.12847 |  | 180 | 38 | 19 | Bilberry | 27.6/16kV | 77M6 | Line fuse G371R on 1113 Maisonneuve blown as well as fuse at transformer 5690 Minor repairs made on secondary and power restored | Gloucester | Foreign Interference | Animal
20526 | 2012 | 5 | 16 | 0.40486 |  | 107 | 221 | 124 | Billberry | 27.6/16kV | 77M6 | 12, 27kV transformers in the Belcourt and Sunview area we isolates to allow crews to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
3451 | 2003 | 5 | 17 | 0.97431 |  | 57 | 19 | 20 | Bilberry | 27.6/16kV | 77M6 | Transformer #667 at 6632 Notre Dame isolated to repair secondary neutral bushings & cables. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5186 | 2004 | 5 | 20 | 0.44306 |  | 173 | 32 | 11 | Bilberry | 27.6/16kV | 77M6 | Transformer TE1778 isolated for replacment due to leaks. | Gloucester | Scheduled Outage | Repair
5188 | 2004 | 5 | 20 | 0.44306 |  | 8 | 1 | 11 | Bilberry | 27.6/16kV | 77M6 | Transformer TE1779W inadvevtantly interupted during switching to isolate TE1778W. | Gloucester | Human Element | Switching Errors
14380 | 2009 | 5 | 20 | 0.29306 |  | 158 | 1380 | 4216 | Bilberry | 27.6/16kV | 77M6 | At 07:02 the 77M6 and the RX2019 both opened, due to hold offs they did not auto reclose. Once all men were clear of there hold offs and fire and police were contacted, Hydro One closed the 77M6 and the circuit held up to the RX2019. Then the RX2019 was closed and held. Crew faund G122 blue phase blown due to squirrel contact. | Nepean | Foreign Interference | Animal
5195 | 2004 | 5 | 21 | 0.43125 |  | 159 | 32 | 12 | Bilberry | 27.6/16kV | 77M6 | Transformer TE1979W on Des Grives isolated for replacement. | Gloucester | Scheduled Outage
20559 | 2012 | 5 | 23 | 0.38542 |  | 160 | 253 | 95 | Bilberry | 27.6/16kV | 77M6 | At 09:15 11 transformers on Sunview were isolated to allow crews to replace elbow and inserts. 95 customers were affected for 160 minutes. Bilberry (77M6) ID#20559 | Gloucester | Scheduled Outage
3494 | 2003 | 5 | 27 | 0.56597 |  | 46 | 3 | 4 | Bilberry | 27.6/16kV | 77M6 | Transformer # 643 isolated to replace blown arrester. 4 Customers at 1690 Boyer Rd. affected in outage. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20625 | 2012 | 5 | 28 | 0.38889 |  | 55 | 10 | 11 | Bilberry | 27.6/16kV | 77M6 | Transformer TP8048 @ 6566 Richer Dr had the wrong nomenclature and was accidently turn off. | Gloucester | Human Element | Incorrect Records
20627 | 2012 | 5 | 28 | 0.38542 |  | 245 | 127 | 31 | Bilberry | 27.6/16kV | 77M6 | Transformer TP8044,TP8045,TP8046,TP8047 in the Richer/Leblanc area were isolated to allow the crews to replace the elbow and insert to vented load break elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
20628 | 2012 | 5 | 28 | 0.57639 |  | 220 | 213 | 58 | Bilberry | 27.6/16kV | 77M6 | Transformer TP8048,TP8049,TP8050,TP8051,TP8052,TP853 in the Michaelsem/Leblanc area were isolated to allow the crews to replace the elbow and insert to vented load break elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
12497 | 2008 | 5 | 29 | 0.42222 |  | 92 | 12 | 8 | Bilberry | 27.6/16kV | 77M6 | Transformer T1522 at 1445 Gaultois in Gloucester isolated for replacement. | Gloucester | Scheduled Outage | Repair
10479 | 2007 | 5 | 30 | 0.29028 |  | 336 | 112 | 20 | Billberry Creek | 27.6/16kV | 77M6 | Transformer TE3199 @ 203 Hidden Valley is defective. 24/7 replaced fuse in transformer, and fuse re-opened. D. Martin crew isolated transformer & replaced same. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20645 | 2012 | 5 | 30 | 0.40764 |  | 203 | 321 | 95 | Bilberry | 27.6/16kV | 77M6 | 13 B & W phase Tx's in the Sunview / Burning Tree area of Orleans were isolated for elbow & insert upgrades. | Gloucester | Scheduled Outage
16169 | 2010 | 5 | 31 | 0.76042 |  | 190 | 6 | 2 | Bilberry Creek | 27.6/16kV | 77M6 | TE2207 at 1951 St Joseph was isolated to change transformer elbows and inserts | Gloucester | Scheduled Outage
10505 | 2007 | 6 | 1 | 0.43264 |  | 92 | 15 | 10 | Bilberry | 27.6/16kV | 77M6 | TE1848 at 1591 Champneuf was replaced due to an oil leak. Nomenclature changed to TP4898. | Gloucester | Scheduled Outage | Repair
20663 | 2012 | 6 | 1 | 0.39931 |  | 308 | 56 | 11 | Billberry | 27.6/16kV | 77M6 | transformer TP8128 at 1859 Belcourt was isolated to replace leaking transformer. | Gloucester | Scheduled Outage | Repair
5248 | 2004 | 6 | 2 | 0.44444 |  | 65 | 13 | 12 | Bilberry | 27.6/16kV | 77M6 | Transformer TE1979 at 1593 Des Grives Cr isolated for removal of contaminated soil. | Gloucester | Scheduled Outage
16175 | 2010 | 6 | 2 | 0.41458 |  | 173 | 78 | 27 | Bilberry | 27.6/16kV | 77M6 | Transformers T1579, T1580 and T1659 off of Champlain St. In Orleans were isolated to allow crews to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
20670 | 2012 | 6 | 2 | 0.080556 |  | 124 | 149 | 72 | Bilberry Creek | 27.6/16kV | 77M6 | Tree in the overhead on Carrierre caused Red and Blue fuses to blow at G279. Crews cleared the overhead from tree contact and restored all customers affected. | Gloucester | Tree Contacts | Tree Limb Fallen
16184 | 2010 | 6 | 3 | 0.56944 |  | 568 | 912 | 1168 | Bilberry | 27.6/16kV | 77M6 | Transformers T1141, T999 and T993 on Grenoble Cres. were isolated to allow crews to replace elbows and inserts. During restoration the insert faulted at T999 (now TP7091) causing RX2018 to trip which was under Hold Off and the white phase fuse at S26 to open. The defective transformer was re-isolated, RX2018 closed, then S26WT1195 refused and T993 from the original planned outage restored. | Gloucester | Scheduled Outage | Preventive Maintenance
20687 | 2012 | 6 | 3 | 0.24167 |  | 172 | 530 | 185 | Bilberry |  | 77M6 | 27kV fuse G537 and Belcourth and Notre Dame opened due to an animal contact. | Gloucester | Foreign Interference | Animal
5254 | 2004 | 6 | 4 | 0.39375 |  | 393 | 79 | 12 | Bilberry | 27.6/16kV | 77M6 | Transfomer T1979 at 1591 Des Grives replaced due to oil leak. | Ottawa | Scheduled Outage | Repair
18292 | 2011 | 6 | 4 | 0.28542 |  | 180 | 33 | 11 | Bilberry | 27.6/16kV | 77M6 | Transformer #GL003804 located at 6627 Benoit opened up due to tree contact (vines) | Gloucester | Tree Contacts | Inadequate Trimming
3523 | 2003 | 6 | 5 | 0.32292 |  | 111 | 148 | 165 | Bilberry | 27.6/16kV | 77M6 | Cable fault between transformer #2203 & #1891 Silver Bark area of Orleans. Caused the blue phase fuse to blow at G703B. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10541 | 2007 | 6 | 6 | 0.38333 |  | 123 | 20 | 10 | Bilbarry | 27.6/16kV | 77M6 | Fuse was found blown on transformer GLTE3199 at 195 Hidden Vally Pvt cause unknown | Gloucester | Unknown/Other | No Apparent Cause
12561 | 2008 | 6 | 6 | 0.48889 |  | 106 | 37 | 21 | Bilberry | 27.6/16kV | 77M6 | Crew replaced blown switch to transformer 3803 at 6910 Notre Dame St caused by a bird contact (Crow) | Gloucester | Foreign Interference | Bird
12562 | 2008 | 6 | 6 | 0.48889 |  | 106 | 37 | 21 | Bilberry | 27.6/16kV | 77M6 | The 77M6 auto reclosed, The Crew had to replaced blown switch to transformer 3803 at 6910 Notre Dame St caused by a bird contact (Crow), | Gloucester | Foreign Interference | Bird
3535 | 2003 | 6 | 7 | 0.65764 |  | 175 | 9 | 3 | Bilberry | 27.6/16kV | 77M6 | Surge arrester and hot line clamp at overhead transformer tx 896 blew. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14489 | 2009 | 6 | 8 | 0.35069 |  | 27 | 1664 | 4216 | Bilberry Creek | 27.6/16kV | 77M6 | 77M6 breaker blocked for forestry tripped, for no apparent reason, cleared all crews and closed by H1 successfully, RX2019 then opened, also blocked for forestry, recloser reset and recloser RX2019 successfully closed. | Gloucester | Unknown/Other | No Apparent Cause
14493 | 2009 | 6 | 8 | 0.36528 |  | 156 | 81 | 31 | Bilberry Creek | 27.6/16kV | 77M6 | G595 appears to have opened when 77M6 was re-energized due to weak or faulty fuse, no other causes found | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18351 | 2011 | 6 | 8 | 0.70556 |  | 4 | 171 | 2572 | Bilberry | 27.6/16kV | 77M6 | 77M6 opened due to lightning storm. Closed in by Hydro One and held. | Gloucester | Adverse Weather
18356 | 2011 | 6 | 8 | 0.70556 |  | 3 | 129 | 2572 | Billberry | 27.6/16kV | 77M6 | Circuit opened due to storm activity, no cause reported yet, closed in via scada. | Gloucester | Adverse Weather
14510 | 2009 | 6 | 10 | 0.65486 |  | 61 | 1940 | 4216 | Billberry | 27.6/16kV | 77M6 | Billberry 77M6 breaker and RX2019 recloser on Belcourt opened due to tractor trailer contacting hydro pole on Carriere west of belcourt. Only two fuses @ G279 on carriere operated causing the downstream devices RX2019 and 77M6 to open. | Gloucester | Foreign Interference | Vehicle
20737 | 2012 | 6 | 11 | 0.38194 |  | 224 | 355 | 95 | Bilberry | 27.6/16kV | 77M6 | At 09:10 16 transformers in the Sunview area were isolated to allow crew to replace elbow and inserts. 95 customers werea affected for 224 minutes. Bilberry (77M6) ID#20737 | Gloucester | Scheduled Outage | Preventive Maintenance
14527 | 2009 | 6 | 13 | 0.55278 |  | 79 | 5551 | 4216 | Bilberry | 27.6/16kV | 77M6 | 77M6 auto-reclosed and locked out, white phase amps went high, both RX2018 & RX2019 auto-reclosed once and stayed closed and both had R & B trip flags. An arrestor blew at dip to G920 which flashed over an insulator. Defective equipment was cleared from the overhead and power restored to all but one MTO streetlighting transformer, TE2399. Oncall Crew replaced defective arrestor & insulator at G920. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8498 | 2006 | 6 | 16 | 0.38958 |  | 344 | 86 | 15 | Bilberry | 27.6/16kV | 77M6 | Isolation of T2300, now TP3935 for transformer replacement. 1464 Belcourt | Gloucester | Scheduled Outage | Preventive Maintenance
14550 | 2009 | 6 | 16 | 0.82153 |  | 97 | 4986 | 4216 | Bilberry Creek | 27.6/16kV | 77M6 | 77M6 and RX2018 auto reclosed and locked out. Crew found RX2019 blew up at St Joseph and Boyer, crew closed by-pass, closed in 77M6 breaker, had difficult time closing in RX2018. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16270 | 2010 | 6 | 16 | 0.41528 |  | 244 | 150 | 37 | Bilberry | 27.6/16kV | 77M6 | Transformers TP7048, TP7047, TP7046 and TP6986 on Jeanne D'Arc were isolated to allow crews to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
16281 | 2010 | 6 | 17 | 0.41042 |  | 160 | 21 | 8 | Billberry | 27.6/16kV | 77M6 | T906 at 1086 Chateau Cres was isolated to allow crews to replace the elbows & inserts. | Gloucester | Scheduled Outage | Repair
10644 | 2007 | 6 | 18 | 0.23056 |  | 98 | 26 | 16 | Bilberry | 27.6/16kV | 77M6 | Fuse to transformer GL5921 at 7000 Notre Dame St was found blown due to squirrel contact | Gloucester | Foreign Interference | Animal
20795 | 2012 | 6 | 18 | 0.37847 |  | 205 | 468 | 137 | Bilberry | 27.6/16kV | 77M6 | Transformers between S21717 and S22073 on Belcourt isolated to replace elbows and inserts. | Gloucester | Scheduled Outage
8543 | 2006 | 6 | 19 | 0.80556 |  | 6 | 75 | 750 | Bilberry | 27.6/16kV | 77M6 | Hydro One Reports 77M6 has tripped. Report of 2 insulators at Place D'Orleans blown. Hydro One closed 77M6 and holding. Repairs to be made in daylight. | Gloucester | Adverse Weather | Lightning
10662 | 2007 | 6 | 19 | 0.81597 |  | 63 | 13 | 12 | Billberry | 27.6/16kV | 77M6 | A crow got into transformer TX5921 at 6988 Notre Dame which caused the Billberry M6 feeder to auto reclose. | Gloucester | Foreign Interference | Animal
12692 | 2008 | 6 | 19 | 0.40972 |  | 320 | 53 | 10 | Bilberry | 13.2kV | 77M6 | T1850 on Champneuf, Orleans was replaced due to oil leak. 10 customers on Champneuf were affected. Nomenclature changed to TP6123. | Gloucester | Scheduled Outage | Repair
16301 | 2010 | 6 | 20 | 0.20139 |  | 72 | 5 | 4 | Bilberry | 27.6/16kV | 77M6 | Bird contact at transofmrer cused transformer to blow, arrestor and hot line clamp replaced. 77M6 auto reclosed. | Gloucester | Foreign Interference | Animal
18446 | 2011 | 6 | 20 | 0.86528 |  | 2 | 205 | 6163 | Bilberry | 27.6/16kV | 77M6 | 77M6 breaker tripped open under holdoff, no incident with holder, Hydro one closed the breaker to restore all load, when breaker was closed the RX2018 auto reclosed. | Gloucester | Unknown/Other | No Apparent Cause
14597 | 2009 | 6 | 22 | 0.76667 |  | 138 | 71 | 31 | Billberry | 27.6/16kV | 77M6 | Fuse G595R @ Leblanc & Notredame opened for no apparent cause. Crew refused and closed. | Gloucester | Unknown/Other | No Apparent Cause
16315 | 2010 | 6 | 23 | 0.43264 |  | 122 | 24 | 12 | Bilberry |  | 77M6 | Bird contacted transformer X24457 causing fuse to blow. | Gloucester | Foreign Interference | Bird
20862 | 2012 | 6 | 25 | 0.38125 |  | 148 | 123 | 50 | Bilberry | 27.6/16kV | 77M6 | 77M6 white phase transformers between S21416 and S21519 were isolated to allow crew to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
6825 | 2005 | 6 | 27 | 0.78333 |  | 14 | 1019 | 4369 | Billberry | 27.6/16kV | 77M6 | Rotational load shedding. | Gloucester | Loss of Supply | HEPC Load Shedding
20888 | 2012 | 6 | 27 | 0.38472 |  | 62 | 11 | 11 | Bilberry | 27.6/16kV | 77M6 | Transformer TE1693 at 6830 Bilberry was isolated to allow crew to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
3653 | 2003 | 6 | 30 | 0.47847 |  | 111 | 15 | 8 | Bilberry | 27.6/16kV | 77M6 | Xfmr cutout fuse blew at xfmr #5690 on Maisonneuve in Orleans. No obvious cause found. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10765 | 2007 | 6 | 30 | 0.30972 |  | 109 | 173 | 95 | Bilberry | 27.6/16kV | 77M6 | A blown switch G655B and lightning arrestor on Boyer at Simard. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8657 | 2006 | 7 | 3 | 0.80903 |  | 155 | 7918 | 4370 | Bilberry | 27.6/16kV | 77M6 | The 77M6 feeder A/R/A during a thunderstorm with very strong winds, tree found against circuit neutral on the load side of GR10 on Champlain but no other problem found. | Gloucester | Adverse Weather | Wind
20909 | 2012 | 7 | 3 | 0.24028 |  | 79 | 195 | 5319 | Billberry Creek TS |  | 77M6 | The Billbery Creek TS 77M6 breaker opened while under hold off. Transformer fuse on Notre Dame was open. No apparent cause found. | Gloucester | Unknown/Other
14668 | 2009 | 7 | 4 | 0.92569 |  | 72 | 50 | 42 | Bilberry Creek | 27.6/16kV | 77M6 | Cable fault on Leblanc caused G595 to blow, crew isolated and picked up customers from an alternate source. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20930 | 2012 | 7 | 5 | 0.38125 |  | 117 | 23 | 12 | Bilberry | 27.6/16kV | 77M6 | Transformer TP8177W at 6691 Tooney was isolated to allow crew to replace leaking transformer. | Gloucester | Scheduled Outage | Repair
14685 | 2009 | 7 | 8 | 0.83333 |  | 525 | 9 | 1 | Billberry | 27.6/16kV | 77M6 | The oncall crew of Dalton Henry,Bob Cooper,Scott Barkley and Jamie Leblan came in to replace the defective transformer at 2555 St Joseph Blvd. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16428 | 2010 | 7 | 8 | 0.375 |  | 112 | 19 | 10 | Bilberry Creek | 27.6/16kV | 77M6 | T1794 at 1737 Perdrix was isolated to upgrade elbows and change transformer | Gloucester | Scheduled Outage
18652 | 2011 | 7 | 13 | 0.55556 |  | 105 | 324 | 185 | Billberry | 27.6/16kV | 77M6 | A crow caused overhead transformer X17906 @ 1573 Belltarre to open which also caused G537 white phase to open. | Gloucester | Foreign Interference | Animal
8758 | 2006 | 7 | 18 | 0.055556 |  | 303 | 71 | 14 | Bilberry | 27.6/16kV | 77M6 | Crew check calls from Grenoble Cres. and found Bayonet fuses in T1000 and T999 blown. Crew to isolate transformers and refused to test transformers. Crew found transformers good and fuses held to restore power. | Gloucester | Lightning | Direct Strike
8763 | 2006 | 7 | 18 | 0.3875 |  | 82 | 3 | 2 | Bilberry | 27.6/16kV | 77M6 | Transformer #GL005517 located at 1080 St. Pierre St due to crow interference | Gloucester | Foreign Interference | Bird
8770 | 2006 | 7 | 18 | 0.56597 |  | 10 | 578 | 3470 | Bilberry | 27.6/16kV | 77M6 | Broken insulator causeing floating cunductor at 6600 Carriere Ave. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8771 | 2006 | 7 | 18 | 0.62639 |  | 18 | 1 | 3 | Bilberry | 27.6/16kV | 77M6 | Switch S279 opened to repair floating conductor at 6600 Carriere. | Gloucester | Scheduled Outage | Repair
14785 | 2009 | 7 | 19 | 0.51111 |  | 494 | 8 | 1 | Bilberry | 27.6/16kV | 77M6 | Customer at 2580 St. Joseph reported no power. Crew found a fuse blown at the transformer by crow, refused and resored power. | Gloucester | Foreign Interference | Bird
14802 | 2009 | 7 | 21 | 0.87847 |  | 5 | 4 | 50 | Bilberry Creek | 27.6/16kV | 77M6 | When crew was restoring 77M6 loop from G595 to normal, 4 transformers were dumped when N.O. point was opened. Crew closed back in and found the line side lead at G595 disconnected. Crew re-connected and restored loop successfully. | Gloucester | Human Element | Incorrect Installation
8828 | 2006 | 7 | 25 | 0.40972 |  | 62 | 18 | 17 | Bilberry | 27.6/16kV | 77M6 | Transformers TE999 & TE1000 on Grenoble Cr in Gloucester isolated to replace internal fuses. | Gloucester | Scheduled Outage | Preventive Maintenance
14875 | 2009 | 7 | 29 | 0.54306 |  | 3 | 0 | 4214 | Billberry | 8/4.8kV | 77M6 | Tripped off due to storms in the area. Contacted H1 & they closed CB RX2018 auto-reclosed upon energizing 77M6 | Gloucester | Adverse Weather | Lightning
16586 | 2010 | 7 | 29 | 0.40069 |  | 173 | 86 | 30 | Bill berry | 27.6/16kV | 77M6 | T1197R, T1191W, T1190B at Beauclarie were isolated to allow crews to replace Elbows & Inserts. 30 customers affected for 173 minutes. Billberry Creek (77M6) Crewws report new nomenclatuire has been installed | Gloucester | Scheduled Outage
12978 | 2008 | 7 | 30 | 0.92639 |  | 131 | 194 | 89 | Bilberry | 27.6/16kV | 77M6 | Cct A/ R, customers reported porcelain on the ground at corner of Notre Dame & Leblanc. Crew found blown fuse & arrestor at G595. Repairs made & power restored. | Gloucester | Adverse Weather | Lightning
16639 | 2010 | 8 | 4 | 0.43403 |  | 415 | 173 | 25 | Bilberry | 27.6/16kV | 77M6 | TE2624 at 1940 St Joseph was replaced due to oil leak. 25 customers at 1940 St Joseph were affected. | Gloucester | Scheduled Outage | Repair
16646 | 2010 | 8 | 4 | 0.43403 |  | 415 | 83 | 12 | Bilberry Creek | 27.6/16kV | 77M6 | TE2624 at 1940 St. Joseph was isolated from Hydro Ottawa Sources to change leaking transformer, clean up oil spill and to perform civil work. | Gloucester | Scheduled Outage
5620 | 2004 | 8 | 6 | 0.95625 |  | 53 | 71 | 80 | Bilberry | 27.6/16kV | 77M6 | S. Cunningham reports red phase cable blown at riser pole G453. Cable section isolated restoring power to all customers. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
8955 | 2006 | 8 | 12 | 0.39028 |  | 128 | 17 | 8 | Billberry | 27.6/16kV | 77M6 | Fuse to transformer GL0470 at 6730 Barsona Pl opened due to Blown arrester | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
13054 | 2008 | 8 | 13 | 0.42708 |  | 105 | 26 | 15 | Bilberry | 27.6/16kV | 77M6 | Transformer #X24462 located at 6853 Notre Dame St isolated for pole replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
16739 | 2010 | 8 | 15 | 0.75833 |  | 143 | 26 | 11 | Bilberry creek | 27.6/16kV | 77M6 | 24/7 report transformer fuse & G980R found opened due to a bird. Transfromer & G980R fuse was replaced all power restored. | Gloucester | Foreign Interference | Bird
13127 | 2008 | 8 | 17 | 0.45833 |  | 3138 | 52 | 1 | BILBERRY | 27.6/16kV | 77M6 | VE5 (School) at 6664 Carrier was isolated due to blue phase cable fault. Repairs made, and re-energized. | Gloucester | Defective Equipment
3912 | 2003 | 8 | 18 | 0.44306 |  | 350 | 2966 | 4369 | Bilberry | 27.6/16kV | 77M6 | Hydro One reports77M6 circuit has locked out. Overhead crews dispatched. Ottawa fire reports transformer blown at WildBerry & Henry Lauzon. Crew reports primary wire down. Circuit is now cut away. 77M6 circuit is now reclosed restoring 4312 customers in Orleans. 57 crews will be out of power until promary line is repaired. Crews report outage caused conductor failure. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3914 | 2003 | 8 | 18 | 0.37292 |  | 63 | 9 | 9 | Billberry | 27.6/16kV | 77M6 | Crow contact caused the transformer feeding customers on Notre Dame to open. | Gloucester | Foreign Interference | Animal
13114 | 2008 | 8 | 19 | 0.27083 |  | 234 | 168 | 43 | Bilberry | 27.6/16kV | 77M6 | defective overhead transformer caused G224 (red) to blow Open. Switch Closed to restore most customer. Transformer 98 isolated for repairs. | Gloucester | Defective Equipment
13126 | 2008 | 8 | 19 | 0.51181 |  | 114 | 30 | 16 | BILBERRY | 27.6/16kV | 77M6 | Crew found blown arrester and two fuses blown at G596. Switch at G639 flashed over. Section isolated, and arresters and switches replaced. | Gloucester | Defective Equipment
5699 | 2004 | 8 | 20 | 0.50139 |  | 18 | 572 | 1905 |  | 27.6/16kV | 77M6 | Replacing Transformer and arrester blew. GR11 tripped | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
9013 | 2006 | 8 | 21 | 0.4375 |  | 120 | 24 | 12 | Billberry | 27.6/16kV | 77M6 | Transformer #T2203 located at 1753 Silverbark isolated to change transformer-leaker | Gloucester | Scheduled Outage | Repair
18989 | 2011 | 8 | 21 | 0.61458 |  | 398 | 4688 | 4480 | Bilberry | 27.6/16kV | 77M6 | An animal got into the primary at Henrie Louzon and Notre Dame causing the conductor to come down across the street. | Gloucester | Foreign Interference | Animal
16797 | 2010 | 8 | 22 | 0.69722 |  | 78 | 13 | 10 | Billberry | 27.6/16kV | 77M6 | G802 at 2828 ST Joseph BLVD opened due to animal contact in the line. | Gloucester | Foreign Interference | Animal
19014 | 2011 | 8 | 25 | 0.42569 |  | 599 | 110 | 11 | Bilberry Creek | 27.6/16kV | 77M6 | TE1643 at 1866 Longman was isolated to allow crews to perform oil clean up. | Gloucester | Scheduled Outage | Repair
3955 | 2003 | 8 | 27 | 0.80556 |  | 15 | 1125 | 4500 | BILBERRY | 27.6/16kV | 77M6 | 77M6 tripped and locked out at the same time 77M4 locked out and the capacitor bank at Bilberry tripped off. The 77M6 was patrolled and a flashed over insulator on Roque street was found along with flashed insulators on 77M4. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
7253 | 2005 | 8 | 31 | 0.575 |  | 64 | 10 | 9 | Bilberry | 27.6/16kV | 77M6 | Transformer #5779 at 1760 Belcourt blew a fuse because of bird interference | Ottawa | Foreign Interference | Bird
16846 | 2010 | 9 | 1 | 0.42917 |  | 75 | 11 | 9 | BILBERRY TS | 27.6/16kV | 77M6 | Transformer GLTE1692 at 6870 Bilberry isolated for elbow and insert replacement | Gloucester | Scheduled Outage | Repair
19065 | 2011 | 9 | 1 | 0.046528 |  | 445 | 4607 | 1297 | Billberry | 27.6/16kV | 77M6 | Two faults found downstream from RX2018 (tansformer TP7048R and cable TE1262W x TE1263W). | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19067 | 2011 | 9 | 1 | 0.83819 |  | 570 | 4289 | 1297 | Bilberry | 27.6/16kV | 77M6 | Defective Red phase Transformer TP7048 as well as defective white phase cable on another u/g loop caused RX2018 to trip off and on. Both sections sectionalized, repairs made to transformer. 77M6 ID#21478 | Gloucester | Defective Equipment
16851 | 2010 | 9 | 2 | 0.42431 |  | 57 | 10 | 11 | Billberry | 27.6/16kV | 77M6 | TP2248 at 150 Copperwood was isolated to allow crew to replace elbows and insert. | Gloucester | Scheduled Outage
9159 | 2006 | 9 | 8 | 0.74583 |  | 148 | 10779 | 4370 | BILBERRY | 27.6/16kV | 77M6 | 77M6 Breaker tripped due to burnt up Switch G822 on St. Joseph Blvd. Severe Storm in progress, Switch cut clear, 77M6 closed and power restored. | Gloucester | Adverse Weather
9168 | 2006 | 9 | 8 | 0.77083 |  | 1122 | 19 | 1 | Bilberry | 27.6/16kV | 77M6 | Switch G822 replaced after being damaged by lightning, switches and arresters replaced. | Gloucester | Adverse Weather | Lightning
4063 | 2003 | 9 | 13 | 0.31319 |  | 62 | 11 | 11 | Bilberry | 27.6/16kV | 77M6 | D. Howett reports Squirrel has caused fuse on transformer to blow. Fuse replaced all power restored to normal. 11 customers effected power outage. | Gloucester | Foreign Interference | Animal
19159 | 2011 | 9 | 13 | 0.625 |  | 1 | 74 | 4462 | Bilberry | 27.6/16kV | 77M6 | 77M6 circuit auto-reclosed during lightning storm. RX2018 auto-reclosed at the same time. | Gloucester | Lightning
11307 | 2007 | 9 | 14 | 0.73611 |  | 60 | 7 | 7 | Billberry | 27.6/16kV | 77M6 | Isolated transformer GL189 at 2834 St Joseph Blvd to replace secondary lead at the transformer | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13238 | 2008 | 9 | 15 | 0.75347 |  | 498 | 208 | 4000 | Billberry | 27.6/16kV | 77M6 | TP5878 @ 1261 cousineau was isolated to repair red phase cable fault. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
11354 | 2007 | 9 | 21 | 0.43958 |  | 22 | 4 | 10 | Billberry Creek | 27.6/16kV | 77M6 | While isolating G800. G445 RW fuses opened when parellall was broken. Crews found fusing was only 10AMPS at G445. System Design changed on new cables and transformer at Place de Orleans fuse size was not increased. | Gloucester | Human Element | Commissioning Errors
16972 | 2010 | 9 | 21 | 0.94931 |  | 138 | 339 | 172 | Billberry | 27.6/16kV | 77M6 | Cable section between T1796 and T2054 was found defective by 24/7 after Hi Pot test Dead Short | Gloucester | Defective Equipment
15147 | 2009 | 9 | 22 | 0.42986 |  | 16 | 1124 | 4214 | Bilberry | 27.6/16kV | 77M6 | During OTO 17-34679 to isolate Transformer 2213 at 2806 St Joseph. The porcelaine insulators for G833 broke during the operation of the switch causing the 77M6 to open under hold-off protection. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
9305 | 2006 | 9 | 25 | 0.54514 |  | 100 | 25 | 15 | Billberry | 27.6/16kV | 77M6 | Transformer #GL2096 located at 1696 Belcourt isolated to install pole, PC10A#00679 | Gloucester | Scheduled Outage | Construction
17006 | 2010 | 9 | 27 | 0.44722 |  | 170 | 68 | 24 | Bilberry Creek | 27.6/16kV | 77M6 | Transformers T1694 and T1687 on Du Bois and Bilberry were isolated to replace elbows, inserts and switch G719. | Gloucester | Scheduled Outage
4196 | 2003 | 10 | 2 | 0.39931 |  | 10 | 2 | 10 | Bilberry | 27.6/16kV | 77M6 | Tx915 for minor mtce after cable section repaired. | Gloucester | Scheduled Outage | Repair
19308 | 2011 | 10 | 3 | 0.097917 |  | 311 | 52 | 10 | Billberry | 27.6/16kV | 77M6 | At 02:21am the City of Ottawa reported and outage at 2831 St Joseph. 24/7 crew found transformer X17466 defective and On-call crews were called in to replace it. 10 customers affected for __ mins. Billberry (77M6) ID#19308 | Gloucester | Defective Equipment
15212 | 2009 | 10 | 4 | 0.34375 |  | 162 | 60 | 23 | Bilberry Creek | 27.6/16kV | 77M6 | Crow caused xfmr fuse to blow on Edgar Brault and also blew 2 upstream fuses. Fuses closed back in, crow cleared and xfmr restored. Bilberry Creek 77M6 | Gloucester | Foreign Interference | Animal
9388 | 2006 | 10 | 5 | 0.40972 |  | 160 | 16 | 6 | Bilberry | 27.6/16kV | 77M6 | Transformer located at 1544 Belcourt isolated to allow pole change. PC10A #678 | Gloucester | Scheduled Outage | Preventive Maintenance
7429 | 2005 | 10 | 6 | 0.41319 |  | 401 | 127 | 19 | Bilberry | 27.6/16kV | 77M6 | TE1796 & TE1803 isolated to allow crews to replace leaking transformers on Sunview. | Gloucester | Scheduled Outage | Repair
17095 | 2010 | 10 | 12 | 0.39931 |  | 135 | 22 | 10 | Bilberry Creek | 27.6/16kV | 77M6 | Transformer T989R was isolated to allow crew to replace elbows and inserts. 10 customers were affected for 135 minutes. Bilberry Creek (77M1) ID #17095 | Gloucester | Scheduled Outage
17106 | 2010 | 10 | 13 | 0.39722 |  | 108 | 18 | 10 | Bilberry | 27.6/16kV | 77M6 | TE904 at 1093 Chateau in Orleans isolated to upgrade elbows & inserts. 10 customers on Chateau affected. | Gloucester | Scheduled Outage | Preventive Maintenance
17119 | 2010 | 10 | 15 | 0.41597 |  | 39 | 7 | 11 | Bilberry | 27.6/16kV | 77M6 | Motor Vehical accident at Gabriel and Rocque caused G980R to blow, crew inspected equipment and re-fused. | Gloucester | Foreign Interference | Vehicle
17153 | 2010 | 10 | 21 | 0.42986 |  | 231 | 281 | 73 | Bilberry | 27.6/16kV | 77M6 | TE1701 & TE1703 on Bilberry Drive, Orleans isolated to upgrade elbows & inserts. 64 customers at 6434 Bilberry and 9 other customers on Bilberry were affected. | Gloucester | Scheduled Outage | Preventive Maintenance
7513 | 2005 | 10 | 24 | 0.46944 |  | 35 | 5 | 8 | Billberry | 27.6/16kV | 77M6 | Defective switch at G839White phase interrupted power to Two transformers T2207 and T2208. Isolated switch and repairs will be made tomorrow. | Gloucester | Defective Equipment
19514 | 2011 | 11 | 1 | 0.6875 |  | 99 | 287 | 174 | Bilberry | 27.6/16kV | 77M6 | Red phase fuse G703 at Belcourt and Sunview was found blown due to a cable fault on cable section between G722 and TE1891. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
11675 | 2007 | 11 | 6 | 0.44444 |  | 110 | 22 | 12 | Bilberry | 27.6/16kV | 77M6 | TE1844B at 1579 Montcerf isolated to replace leaking transformer. | Gloucester | Scheduled Outage | Repair
17260 | 2010 | 11 | 11 | 0.43194 |  | 161 | 30 | 11 | Billberry | 27.6/16kV | 77M6 | Transformer TE1035 at 7812 Jean D'arc was isolated to allow crews to replace leaking transformer, along with elbow & inserts. 11 cusomers affected. Billberry Creek 77M6) | Gloucester | Scheduled Outage
15385 | 2009 | 11 | 13 | 0.40347 |  | 149 | 149 | 60 | Bilberry | 27.6/16kV | 77M6 | A squirrel cause the W phase fuse to blow at switch S537 at Notre Dame. There was no crews available at the time that is why restoration was delayed. | Gloucester | Foreign Interference | Animal
4472 | 2003 | 11 | 18 | 0.43264 |  | 96 | 16 | 10 |  | 27.6/16kV | 77M6 | Leaking transformer had to be replaced | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
4478 | 2003 | 11 | 18 | 0.41319 |  | 95 | 11 | 7 | Bilberry | 27.6/16kV | 77M6 | D. Provost reports transformer TE1776 isolated to replace transformer. 7 Customers affected in power outage on Sunview Dr. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7641 | 2005 | 11 | 21 | 0.4375 |  | 10 | 1 | 5 | Billberry | 27.6/16kV | 77M6 | Trans 5584 isolated @ 2742 St Joseph Blvd to make repairs to sec leads | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
15441 | 2009 | 11 | 30 | 0.41389 |  | 54 | 2 | 2 | Billberry | 27.6/16kV | 77M6 | O/H section from St Joseph to CS27576 on St Peire was Isolated. Temporary outage to 2 customers to allow for isolation | Gloucester | Scheduled Outage
15459 | 2009 | 12 | 2 | 0.52778 |  | 134 | 22 | 10 | Bilberry | 27.6/16kV | 77M6 | At 12:40 crews opened transformer TE1849 at 1581 Champneuf on the 77M6 to replace a leaking transformer and elbow connectors. 10 customers affected for 134 mins. Bilberry 77M6 ID# 15459. | Gloucester | Scheduled Outage | Repair
15469 | 2009 | 12 | 4 | 0.37847 |  | 185 | 34 | 11 | Bilberry Creek | 27.6/16kV | 77M6 | Transformer X23947 was interrupted for crew to perform maintenance | Gloucester | Scheduled Outage | Preventive Maintenance
13725 | 2008 | 12 | 9 | 0.5625 |  | 89 | 18 | 12 | Billberry | 27.6/16kV | 77M6 | Defective transformer at 6437 Nathan court replaced by D Provost, Affecting 12 customers | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17402 | 2010 | 12 | 10 | 0.39583 |  | 55 | 14 | 15 | Bilberry | 27.6/16kV | 77M6 | Transformer #X17473 located at 2767 St. Joseph Blvd opened by crew to sleeve the open buss and replace cut out. The 110 was down | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4651 | 2003 | 12 | 25 | 0.048611 |  | 197 | 255 | 85 | Bilberry | 27.6/16kV | 77M6 | G122R & G537R fuses blew due to a blown stress cone at G122R. 85 customers on Edgar Brault, Barsona, Pascal & Bonneville affected. G537R was refused and closed to pick up 27 customers on Barsona & Pascal. The cable to G122R was isolated at T2780R & G213R closed to restore remaining customers. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4661 | 2003 | 12 | 29 | 0.41667 |  | 45 | 38 | 50 | Bilberry | 27.6/16kV | 77M6 | T2627 T2623 T2624 T2625 and T2626 were isolated due to elbows not being vented to add on new transformers | Gloucester | Scheduled Outage | Construction
9892 | 2006 | 12 | 29 | 0.5125 |  | 92 | 11 | 7 | Bilberry | 27.6/16kV | 77M6 | Transformer #GL005690 located at 1113 Maisonneuve St isolated due to broken cut out & blown arrestor | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
11344 | 2007 | 9 | 20 | 0.43542 |  | 21 | 123 | 350 | Billberry Creek | 27.6/16kV | 77M6 (GR11) | While restoring GR11 reclosurer to normal. GR11 reclosurer operated serveral times when Blue phases bypass was opened. 77M6 circuit also auto reclosed effecting power to 4730 customer. G196 blue phase switch was closed restoring power, and GR11 was re-isolated. | Gloucester | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
12482 | 2008 | 5 | 27 | 0.29861 |  | 95 | 218 | 138 | Bilberry | 27.6/16kV | 77M6(GR11) | A cable fault bet transformer T1915B(1943 Belval) and T1916B(1827 Belval) | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6692 | 2005 | 6 | 10 | 0.77986 |  | 102 | 14 | 8 | Billberry | 27.6/16kV | 77M6/GR11 | Transformer TE2202 isolated to replace leaking transformer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12820 | 2008 | 7 | 11 | 0.74653 |  | 14 | 940 | 4220 | Bilberry | 27.6/16kV | 77M9 | 77M5 breaker tripped. No calls to identify problem. SM834 opened and breaker closed and holding. 77M5 breaker opened from SCADA, scadamate 834 closed and 77m5 breaker closed for second time with full circuit and holding. | Gloucester | Unknown/Other | No Apparent Cause
7460 | 2005 | 10 | 15 | 0.65278 |  | 243 | 6628 | 4500 | LIMEBANK | 27.6/16kV | 7CS2-L | 7CS2-L opened at Limebank station. Load loss to 7F2 & 7F4 circuits. Ottawa Fire reports working fire at Leitrim & Bank st area, also Rideau Carleton Race track reports MVA with hydro pole. On-call person dispatched to Limebank 24/7 crew dispatched to Rideau Carleton & J. Kelly dispatched to working fire. Also J. Kelly reports lightning storm in area. 7T2 bank energized @ 16:15. Circuit 7F2 energized at 16:32. 7F4 circuit auto reclosed & locked out. Circuit patrolled found broken insulator at Rideau & Bowesville area. Overhead section isolated on Rideau RD. 3000 customer restored at 17:07. Approx 300 customers remained out until insulator can be replaced by oncall crew. Tempory repair copper jumper installed. Permanent repairs required. | Gloucester | Adverse Weather | Wind
18116 | 2011 | 5 | 9 | 0.225 |  | 47 | 1 | 1 | Limebank | 27.6/16kV | 7F | Squirrel contact caused a transformer at 538 River Rd to open. | Gloucester | Foreign Interference | Animal
11897 | 2008 | 1 | 4 | 0.41319 |  | 120 | 10 | 5 |  | 8/4.8kV | 7F1 | Isolated transformer TE 3422 at 3 Heritage Glen for service work | Nepean | Scheduled Outage | Repair
3097 | 2003 | 1 | 8 | 0.047917 |  | 191 | 150 | 47 | Limebank | 27.6/16kV | 7F1 | 24/7 Crew responded to a pole fire at 429 River Road. Due to adverse weather top of pole was burnt off damaging top of pole and transformer 2245. On-call crew called in to make repairs. | Gloucester | Adverse Weather | Snow
4688 | 2004 | 1 | 8 | 0.36806 |  | 56 | 2961 | 3173 | Limebank | 27.6/16kV | 7F1 | A broken insulator approximately 10 spans east of reclosure GR1 failed causing the reclosure to go to lockout. Repairs were made and power was restored. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
11942 | 2008 | 1 | 16 | 0.42708 |  | 100 | 3 | 2 | LIMEBANK | 27.6/16kV | 7F1 | Transformer #NP000382 (X36953) located at 3112 Woodroffe isolated to allow for removal of transformer & livening up new transformer | Nepean | Scheduled Outage | Construction
4734 | 2004 | 1 | 26 | 0.52083 |  | 20 | 7 | 21 | Limebank | 27.6/16kV | 7F1 | Transformer #2600 at 1460 Goth interrupted to replace a stripped bolt on secondary bushing. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
13962 | 2009 | 2 | 12 | 0.019444 |  | 32 | 19 | 35 | Limebank | 27.6/16kV | 7F1 | Switch G4W found open, circuit patrolled , no problem found. Switch G4W closed and power restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15742 | 2010 | 2 | 25 | 0.41528 |  | 125 | 31 | 15 | Limebank | 27.6/16kV | 7F1 | at 9:58am, Transformer TE3371 Isolated toi allw crews to install new secondary. 15 customers affected for 125 minutes. Limebank (7F1) ID #15742 | Gloucester | Scheduled Outage
3256 | 2003 | 3 | 15 | 0.96389 |  | 266 | 13 | 3 | Limebank MS | 27.6/16kV | 7F1 | Transformer 3278 on Jarvis Dr in Gloucester replaced. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4953 | 2004 | 4 | 1 | 0.39931 |  | 25 | 0 | 1 | Limebank | 27.6/16kV | 7F1 | Isolated transformer GL005172 @ 472 River Rd to replace broken cut out. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3332 | 2003 | 4 | 10 | 0.59375 |  | 45 | 6 | 8 | Limebank | 27.6/16kV | 7F1 | Xfmr 532 taken out of service to replace the defective cutout. 8 customers on Alderwood affected | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3350 | 2003 | 4 | 16 | 0.39583 |  | 79 | 47 | 36 | Limebank MS | 27.6/16kV | 7F1 | Fused switch blew due to blown surge arrester, arrester replaced, switch was refused and closed to restore load. G455W | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5122 | 2004 | 5 | 9 | 0.50278 |  | 64 | 1 | 1 | Limebank | 27.6/16kV | 7F1 | No apparent cause. Cable & RFI to be checked. | Gloucester | Unknown/Other | No Apparent Cause
3480 | 2003 | 5 | 22 | 0.48611 |  | 15 | 2 | 8 | Limebank | 27.6/16kV | 7F1 | Planned outage to transformer 362 at 3960 Autumnwood to change insulators. | Gloucester | Scheduled Outage
3472 | 2003 | 5 | 24 | 0.25139 |  | 68 | 41 | 36 | Limebank | 27.6/16kV | 7F1 | Squirrel caused fuse to blow. Refused by 24/7 | Gloucester | Foreign Interference | Animal
6593 | 2005 | 5 | 24 | 0.45972 |  | 206 | 34 | 10 | Limebank | 27.6/16kV | 7F1 | Transformer T2940 white phase out of service to move transformer on Shoreline Dr in Riverside South. | Gloucester | Scheduled Outage | Construction
3496 | 2003 | 5 | 28 | 0.44097 |  | 113 | 15 | 8 | Limebank | 27.6/16kV | 7F1 | Outage at 20 Reyburn due to Squirrel contact. | Gloucester | Foreign Interference | Animal
3498 | 2003 | 5 | 29 | 0.39583 |  | 75 | 15 | 12 | Limebank | 27.6/16kV | 7F1 | XFMR 325 @ 1458 GOTH TAKEN OUT OF SERVICE FOR REPAIRS | Gloucester | Scheduled Outage | Repair
5232 | 2004 | 6 | 1 | 0.10347 |  | 247 | 13992 | 4510 | Limebank | 27.6/16kV | 7F1 | The 7F1 curcuit trip causing an outage to app. 4500 customers. While tring to find the problem and restoring the airport we trip the 4801F7 out of Uplands causing a momentary outage to app.10 more customers. While sectionalizing the circuit we restore power to the airport and found a blown termination at switch G969. We isolated the switch and pick up the remaining customers through scada mate switching. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3512 | 2003 | 6 | 3 | 0.39583 |  | 120 | 26 | 13 | Limebank MS | 27.6/16kV | 7F1 | Transformer 5760 at Albion & Ridgedale isolated for repairs. | Gloucester | Scheduled Outage | Preventive Maintenance
3513 | 2003 | 6 | 3 | 0.5625 |  | 37 | 4 | 6 | Limebank | 27.6/16kV | 7F1 | Transformer 441 at 4120 Riverside Dr in Ottawa interupted due to defective fused switch. Switch repaired. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
3547 | 2003 | 6 | 10 | 0.46042 |  | 17 | 2 | 8 | Limebank | 27.6/16kV | 7F1 | Crew working in area noticed a broken switch at xfmr 4010 on Shirley. Crew took xfmr out of service and replaced switch. 8 customers on Lowen & Shirley affected. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
3548 | 2003 | 6 | 10 | 0.54861 |  | 59 | 1 | 1 | LIMEBANK | 27.6/16kV | 7F1 | Crew working in area noticed a broken switch at xfmr 425 @ 1425 Mulligan. Crew took xfmr out of service and replaced switch. 1 customers affected. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5282 | 2004 | 6 | 11 | 0.40625 |  | 115 | 12 | 6 | Limebank | 27.6/16kV | 7F1 | Transformer GL0837 at332 River Rd out for switch and arrester replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
18400 | 2011 | 6 | 14 | 0.25 |  | 130 | 4 | 2 | Limebank | 27.6/16kV | 7F1 | Transformer #X13098 located at 622 River Rd opened up due to bird contact | Gloucester | Foreign Interference | Bird
12713 | 2008 | 6 | 23 | 0.40556 |  | 85 | 50 | 35 | Limebank | 27.6/16kV | 7F1 | Transformer fuse at X13045 opened due to bird contact, also caused G4 W phase to open, crew refused both and restored power. Honey Gables / River rd. | Gloucester | Foreign Interference | Animal
3605 | 2003 | 6 | 24 | 0.34444 |  | 89 | 12 | 8 | limebank | 27.6/16kV | 7F1 | Possible animal in primary | Gloucester | Foreign Interference | Animal
18515 | 2011 | 6 | 25 | 0.94375 |  | 81 | 16 | 12 | Limebank | 27.6/16kV | 7F1 | S28401 fuse blew due to lighning. Limebank (7F1) ID#18515 | Gloucester | Adverse Weather | Lightning
5397 | 2004 | 6 | 29 | 0.75 |  | 205 | 512 | 150 | Limebank | 8/4.8kV | 7F1 | lightning was the probable cause of the G2 at Rideau and Limebank feeding customers in the Manotick area. Crew refused and closed. | Gloucester | Adverse Weather | Lightning
5398 | 2004 | 6 | 29 | 0.75 |  | 102 | 71 | 42 | limebank | 27.6/16kV | 7F1 | lightning was the probable cause of the G325 opening in the Gloucester Glen area off of River road. Crew refused and closed. | Gloucester | Adverse Weather | Lightning
6840 | 2005 | 7 | 1 | 0.69722 |  | 178 | 6969 | 2720 | LIMEBANK | 27.6/16kV | 7F1 | 500 custmer sent back to 210F2. Fire at VE74 airport data centre isolated, closeing fuse replaced in Limebank 7F1 recloser. | Gloucester | Adverse Weather | Lightning
3674 | 2003 | 7 | 5 | 0.32292 |  | 423 | 14 | 2 | Limebank | 27.6/16kV | 7F1 | Contractor reports all work complete at VE85 & VE86. Surrenders CIA 1980. Vaults isolated for contractor to clean and torque connections. | Gloucester | Scheduled Outage | Preventive Maintenance
3690 | 2003 | 7 | 6 | 0.32639 |  | 389 | 13 | 2 | Limebank | 27.6/16kV | 7F1 | VE87 & VE88 isolated at customers request. Contractor to clean & torque connections. | Gloucester | Scheduled Outage | Preventive Maintenance
6885 | 2005 | 7 | 7 | 0.55972 |  | 65 | 5 | 5 | Limebank |  | 7F1 | TP2897 on Versilla in Barrhaven isolated to change leaking site glass. | Gloucester | Scheduled Outage | Preventive Maintenance
5487 | 2004 | 7 | 13 | 0.59722 |  | 61 | 20 | 20 | Limebank | 27.6/16kV | 7F1 | Report of a truck hitting a pole. In order to make temporary repairs switch G806W phase was opened. Police report # in OMS. | Gloucester | Foreign Interference | Vehicle
8743 | 2006 | 7 | 17 | 0.49306 |  | 35 | 2 | 3 | Limebank | 27.6/16kV | 7F1 | Isolated transformer GL 809 at 788 River Rd to re-insulate the pole | Gloucester | Scheduled Outage | Preventive Maintenance
18756 | 2011 | 7 | 17 | 0.81042 |  | 514 | 22942 | 2678 | Limebank MS | 27.6/16kV | 7F1 | 7F1 Circuit tripped during severe storm, closed back in and held | Gloucester | Adverse Weather
3760 | 2003 | 7 | 18 | 0.84722 |  | 445 | 44 | 6 | Limebank | 27.6/16kV | 7F1 | 27Kv supply to Black Rapids one span of conductor found on the ground. | Gloucester | Defective Equipment
8766 | 2006 | 7 | 18 | 0.48472 |  | 42 | 2 | 3 | Limebank | 27.6/16kV | 7F1 | Transformer located at 848 River Rd isolated due to re-insulating | Gloucester | Scheduled Outage | Construction
5523 | 2004 | 7 | 19 | 0.42917 |  | 60 | 400 | 400 | Limebank | 27.6/16kV | 7F1 | While isolating S28 a switching error was made. R. Roy advised, and will be following up with a report. | Gloucester | Human Element | Switching Errors
8782 | 2006 | 7 | 19 | 0.47917 |  | 25 | 2 | 4 | Limebank | 27.6/16kV | 7F1 | Transformer #GL000313 located at 872 River Rd isolated due to insulator change | Gloucester | Scheduled Outage | Construction
8785 | 2006 | 7 | 19 | 0.625 |  | 35 | 2 | 3 | Limebank | 27.6/16kV | 7F1 | Transformer #GL002689 located at 884 River Rd isolated due to re-insulating | Gloucester | Scheduled Outage | Construction
8843 | 2006 | 7 | 25 | 0.74306 |  | 435 | 335 | 83 | Limebank | 27.6/16kV | 7F1 | S13201 found blown due to defective Transformer elbow and insert at TE3658, 177 Grovemount. Customers restored in stages. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5574 | 2004 | 7 | 27 | 0.54236 |  | 138 | 12 | 5 | Limebank | 27.6/16kV | 7F1 | Replacement of TE 2374 at 1111 Waterpark Place in Manotick. | Gloucester | Scheduled Outage | Repair
5575 | 2004 | 7 | 27 | 0.63819 |  | 296 | 84 | 17 | Limebank | 27.6/16kV | 7F1 | On switching Te2374 back in service G892 had blown. We were unaware of the power out to 3 transformers until customers began calling around 16:30. All cables and transformers checked okay.Power restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3815 | 2003 | 7 | 29 | 0.45833 |  | 20 | 1 | 2 | Limebank | 27.6/16kV | 7F1 | Transformer 2214 at 4269 Limebank taken out of service to replace an insulator. 2 customers affected | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
3818 | 2003 | 7 | 30 | 0.41458 |  | 92 | 53 | 49 | Limebank | 27.6/16kV | 7F1 | Sw 460R blew as well as the fuse to an overhead tx on Mulligan St due to an animal contact. Both sws were refused and load restored. No damage found. | Gloucester | Foreign Interference | Animal
16710 | 2010 | 8 | 10 | 0.41736 |  | 261 | 87 | 20 | Limebank | 27.6/16kV | 7F1 | transformer # T2899 @ 4082 Otter Trail Cres was isolated to allow crews to replace leaking transformer | Gloucester | Scheduled Outage | Preventive Maintenance
16711 | 2010 | 8 | 10 | 0.41736 |  | 136 | 68 | 30 | Limebank | 27.6/16kV | 7F1 | While isolating T2899R @ 4082 Otter Trail Cres. Crew failed to close transformer switch in T2902 propperly. Causeing an outage to T2901R & T2900R. | Gloucester | Human Element | Switching Errors
11068 | 2007 | 8 | 15 | 0.51181 |  | 118 | 5013 | 4720 | Limebank | 27.6/16kV | 7F1 | Crew insatlled elbow to close at normally open point and forgot to close the transformer switch at TE3362. When crew was breaking parallel switch at S21208 flashed over causing the 7F1 recloser to open. | Gloucester | Human Element | Incorrect Use of Equipment
5706 | 2004 | 8 | 23 | 0.47361 |  | 58 | 41 | 42 | Limebank | 27.6/16kV | 7F1 | G3265R fuse blew on River Rd in Gloucester when Bell cable wrapped around the primary. May have been caught by a tractor. Bell wire was removed and the switch refused & closed to resore power to 42 customers on River Rd & Balmoral. | Gloucester | Foreign Interference | Foreign Object
9064 | 2006 | 8 | 26 | 0.80278 |  | 5 | 250 | 3000 | Limebank | 27.6/16kV | 7F1 | 7F1 auto reclose auto. Fire department has no calls. Breaker closed and holding. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9067 | 2006 | 8 | 26 | 0.84375 |  | 293 | 5 | 1 | Limebank | 27.6/16kV | 7F1 | Fire Department reports smoke coming from SE26 at JDS Uinphase at 3800 Merivale RD. S7001 opened to allow crew to isolate the switch and transfer load to back-up cables. Time delay due to no fuse barrels for SE27. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5747 | 2004 | 8 | 29 | 0.73542 |  | 182 | 3 | 1 | Limebank |  | 7F1 | Crew refused transformer at 466 River Road which opened due to storm conditions. | Gloucester | Adverse Weather | Lightning
4019 | 2003 | 9 | 5 | 0.54583 |  | 39 | 8 | 12 | Limebank | 27.6/16kV | 7F1 | A leaking transformer at 1348 Autmnwood was replaced. | Gloucester | Scheduled Outage
4042 | 2003 | 9 | 9 | 0.48472 |  | 42 | 1 | 2 | Limebank | 27.6/16kV | 7F1 | Darcy Provost reports Transformer # 3771 isolated for transformer maintenance. 2 customers effected in outage. | Gloucester | Scheduled Outage
4053 | 2003 | 9 | 11 | 0.39236 |  | 110 | 4 | 2 | limebank | 27.6/16kV | 7F1 | Insulator replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
9204 | 2006 | 9 | 12 | 0.4 |  | 229 | 38 | 10 | Limbank | 27.6/16kV | 7F1 | TP3183 and TP3182 interupeted to allow contractor to install secondaries iin duct work. Furness Way, Nepean. | Nepean | Scheduled Outage | Construction
11312 | 2007 | 9 | 14 | 0.90417 |  | 188 | 53 | 17 | Limebank | 27.6/16kV | 7F1 | Switch G695 at St Bernard and Bank white phase fuse opened due to object interference, possibly a group of balloons from car sales lot. | Gloucester | Foreign Interference | Foreign Object
4092 | 2003 | 9 | 18 | 0.45833 |  | 40 | 7 | 10 | Limebank | 27.6/16kV | 7F1 | E. Neumann reports GL5861 at 5310 Hillcrest blown cutout. Cutout replaced restoring all power at 11:40. 10 customers effected in power outage. | Gloucester | Unknown/Other | No Apparent Cause
4093 | 2003 | 9 | 18 | 0.54167 |  | 30 | 2 | 4 | Limebank | 27.6/16kV | 7F1 | R. Barnett reports transformer # 5655 opened for maintenance. 4 customers affected by planned power outage. All power was restored by 13:30. | Gloucester | Scheduled Outage | Preventive Maintenance
4128 | 2003 | 9 | 23 | 0.079167 |  | 283 | 1298 | 570 | Limebank | 27.6/16kV | 7F1 | Insulator on Rideau Road went defective causing GR2 BW to trip power was rerouted from G983 BW phases insulators was replaced and switching was restored to normal. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
4156 | 2003 | 9 | 26 | 0.55903 |  | 55 | 7 | 8 | Limebank | 27.6/16kV | 7F1 | To install animal proof guards.Transformer 4328 at 1458 Rhea Place. | Gloucester | Scheduled Outage | Preventive Maintenance
4157 | 2003 | 9 | 26 | 0.47917 |  | 30 | 4 | 9 | Limebank | 27.6/16kV | 7F1 | Installing animal guards on transformer 4315 at 12 Lennon | Gloucester | Scheduled Outage | Preventive Maintenance
4158 | 2003 | 9 | 26 | 0.44097 |  | 15 | 0 | 2 | Limebank | 27.6/16kV | 7F1 | Installing wild-life guards on transformer 4447 at 18 Mary St. | Gloucester | Scheduled Outage | Preventive Maintenance
4159 | 2003 | 9 | 26 | 0.40972 |  | 20 | 1 | 2 | Limebank | 27.6/16kV | 7F1 | Installing wild life guards on transformer 513 at 33 Mary Dr | Gloucester | Scheduled Outage | Preventive Maintenance
7380 | 2005 | 9 | 26 | 0.72292 |  | 59 | 88 | 90 | Limebank | 27.6/16kV | 7F1 | Burnt termination at S7025R toTE2528 Woodroffe at Earl Mulligan | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7388 | 2005 | 9 | 27 | 0.60347 |  | 316 | 32 | 6 | Limebank | 27.6/16kV | 7F1 | When new equipment was energized and the W phase tx loop on Flodden Way in the Longfields area was restored to its new normally open points, it appears the tx switches at TP2892W were left in the open position. Power out calls were not received until 17:30. | Nepean | Human Element | Incorrect Installation
4187 | 2003 | 9 | 30 | 0.41667 |  | 30 | 3 | 6 | Limebank | 27.6/16kV | 7F1 | Transformer #5654 at 1476 Jarvis in South Gloucester was isolated to allow for the installation of squirrel guards. | Gloucester | Scheduled Outage | Preventive Maintenance
19307 | 2011 | 10 | 2 | 0.55 |  | 53 | 1 | 1 | Limebank | 27.6/16kV | 7F1 | 7F1 auto reclosed then customer called and led the crew to transformer X13091 at 2 Honey Gables Dr fuse blown feeding here caused by squirrel contact | Gloucester | Foreign Interference | Animal
17064 | 2010 | 10 | 5 | 0.97708 |  | 333 | 11 | 2 | Limebank | 27.6/16kV | 7F1 | Sections of 7F1, 7F2, 7F4 o/h lines on River rd N. of Earl Armstrong were isolated to re-arrange primary conductor. TP6365 at 660 River rd & TP2877 @ 645 Earl Armstrong were affected by this outage. | Gloucester | Scheduled Outage | Construction
4221 | 2003 | 10 | 6 | 0.45833 |  | 50 | 22 | 27 | Limebank | 27.6/16kV | 7F1 | A crow caused the fuse at transformer 2751 and switcg G696 to blow. 27 customers on Autumnwood, Ridgedale & McMahon were affected. | Gloucester | Foreign Interference | Bird
11474 | 2007 | 10 | 6 | 0.82847 |  | 127 | 58 | 36 | Limebank | 27.6/16kV | 7F1 | Squirrel caused cut out at Tx 3987, 40 Ryeburn to fail, this also caused the G4W at Honey Gables & River to open. | Gloucester | Foreign Interference | Animal
5834 | 2004 | 10 | 8 | 0.34236 |  | 10 | 2 | 11 | Limebank | 27.6/16kV | 7F1 | New service connections | Gloucester | Scheduled Outage | Construction
5835 | 2004 | 10 | 8 | 0.30903 |  | 5 | 1 | 9 | Limebank | 27.6/16kV | 7F1 | New service connections. | Gloucester | Scheduled Outage | Construction
5836 | 2004 | 10 | 8 | 0.32292 |  | 10 | 2 | 12 | Limebank | 27.6/16kV | 7F1 | New service connections. | Gloucester | Scheduled Outage | Construction
4231 | 2003 | 10 | 9 | 0.55278 |  | 195 | 51 | 92 | Limebank | 27.6/16kV | 7F1 | R. Barnett reports G460R switch found opened. Transformer 813 found defective. Ottawa fire department reports sparking wires at G325RR switch. Switch was isolated and fuse replaced. G325 R phase switch outage was caused by outage on G460R. R. Barnett reports transformer 2198 is now restored to normal. No apparent cause for outage. Transformer tested defective in the field. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4263 | 2003 | 10 | 15 | 0.59722 |  | 40 | 7 | 10 | Limebank | 27.6/16kV | 7F1 | Top pin insulator sheared off in the wind causing a phase to phase fault rupturing switch G657. Top pin replaced and full power restored. | Gloucester | Adverse Weather | Wind
9523 | 2006 | 10 | 27 | 0.38194 |  | 50 | 9 | 11 | Limebank | 27.6/16kV | 7F1 | AT 09:20 tans GL2361 at 321 River rd was isolated to replace defective connections | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
11606 | 2007 | 10 | 27 | 0.24583 |  | 96 | 8 | 5 | Limebank | 27.6/16kV | 7F1 | 7F1 feeder auto/reclose due to failed switch to O/H tx at 532 River Rd. 24/7 replaced switch & restored O/H xfmr. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17288 | 2010 | 11 | 17 | 0.67708 |  | 98 | 3 | 2 | Limebank | 27.6/16kV | 7F1 | Transformer #2154 located at 540 River Rd opened due to tree contact | Gloucester | Tree Contacts | Inadequate Trimming
4510 | 2003 | 11 | 25 | 0.0041667 |  | 14 | 2 | 8 | Limebank | 27.6/16kV | 7F1 | Switch G324B on River Rd opened to replace a buning hot line clamp. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15447 | 2009 | 12 | 1 | 0.39167 |  | 196 | 75 | 23 | Limebank | 27.6/16kV | 7F1 | TE3396 @ 48 Collington, and TE3382 at 11 Barnstone were isolated for crew to prepare for new installation of transformers. | Gloucester | Scheduled Outage | Construction
4567 | 2003 | 12 | 5 | 0.47222 |  | 29 | 1 | 2 | Limebank | 27.6/16kV | 7F1 | Replace open wire service | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
19720 | 2011 | 12 | 14 | 0.90972 |  | 99 | 1744 | 2176 | LIMEBANK |  | 7F1 | 7F1 breaker opened due to plane contacting overhead neutral and damaged two poles. Circuit isolated and power restored | Gloucester | Foreign Interference | Vehicle
6073 | 2004 | 12 | 17 | 0.84028 |  | 50 | 6 | 7 | LimebanK | 27.6/16kV | 7F1 | A burnt off 110 leg at 1399 Emerald Ave @ transformer 000341. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4643 | 2003 | 12 | 22 | 0.16667 |  | 160 | 179 | 118 | Limebank | 27.6/16kV | 7F1 | Bad underground cable. | Gloucester | Defective Equipment
4644 | 2003 | 12 | 22 | 0.44375 |  | 50 | 2 | 3 | Limebank | 27.6/16kV | 7F1 | SE43-3129 opened due to ??? | Gloucester | Unknown/Other
15590 | 2009 | 12 | 29 | 0.50694 |  | 75 | 1 | 1 | Limebank | 27.6/16kV | 7F1 | M. Gruich reports tree limb fall on customer owned service blowing 2 fuses at G933. M. Gruich removed limb off overhead service. G933RWB was refused restoring all power. | Gloucester | Tree Contacts | Tree Limb Fallen
3671 | 2003 | 7 | 4 | 0.32153 |  | 55 | 62 | 68 | Limebank | 27.6/16kV | 7F1 / GR1 | Squirrel contact with feeder caused fused sw to blow. Switch refused and load restored. | Gloucester | Foreign Interference | Animal
6738 | 2005 | 6 | 15 | 0.80278 |  | 33 | 2219 | 4815 | Limebank | 27.6/16kV | 7F1,7F4 | Lightning strike in the area and graph from 7F4 showed spikein Amps. T2 hi side switch opened with load loss to F2 and F4. On return to service as 7F2 was closed from SCADA 7F1 opened? Not sure why. T2 flagged red phase timed. Stations will check bank tomorrow, MaGil and Rivard on site. | Gloucester | Lightning | Lightening Strike on adjacent circuit
15630 | 2010 | 1 | 8 | 0.42014 |  | 10 | 4 | 22 | Limebank | 27.6/16kV | 7F2 | TP4921 at 114 Jersey Tea was isolated from Hydro Ottawa Sources to remove red phase NIU cable | Gloucester | Scheduled Outage
15631 | 2010 | 1 | 8 | 0.40139 |  | 19 | 3 | 10 | Limebank | 27.6/16kV | 7F2 | TP3708 at 6069 North Bluff was isolated from Hydro Ottawa Sources to remove blue phase NIU cable | Gloucester | Scheduled Outage
15632 | 2010 | 1 | 8 | 0.43542 |  | 18 | 1 | 4 | Limebank | 27.6/16kV | 7F2 | TP3707 at 119 Coral Berry was isolated from Hydro Ottawa Sources to remove white phase NIU cable | Gloucester | Scheduled Outage
9908 | 2007 | 1 | 9 | 0.42639 |  | 129 | 17 | 8 | Limebank | 27.6/16kV | 7F2 | Transformer TP2910 located of Lester Rd was isolated for repair due to vehicle accident. | Gloucester | Scheduled Outage | Repair
9911 | 2007 | 1 | 9 | 0.56736 |  | 130 | 22 | 10 | Limebank | 27.6/16kV | 7F2 | TP3221 White phase transformer was isolated to allow crews to replace same, on Lester Rd. | Gloucester | Scheduled Outage | Repair
17537 | 2011 | 1 | 30 | 0.036111 |  | 218 | 47 | 13 | Limebank | 27.6/16kV | 7F2 | TP2878 at 665 Earl Armstrong isolated to transfer plant to new pole. | Gloucester | Scheduled Outage | Construction
3172 | 2003 | 2 | 7 | 0.58333 |  | 31 | 1 | 2 | Limebank | 27.6/16kV | 7F2 | Crews reports T229 on 5461 Long island isolated to replace switch. All customers notified to outage. | Gloucester | Scheduled Outage | Preventive Maintenance
12051 | 2008 | 2 | 16 | 0.51319 |  | 72 | 20 | 17 | Limebank | 27.6/16kV | 7F2 | Transformer #X14791 located at 1382 McMahon Ave isolated due to squirrel contact | Gloucester | Foreign Interference | Animal
12052 | 2008 | 2 | 16 | 0.58333 |  | 15 | 4 | 17 | Limebank | 27.6/16kV | 7F2 | Switch barrel at G469B failed. Switch was opened & replaced all power restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12085 | 2008 | 2 | 28 | 0.375 |  | 336 | 22 | 4 | Limebank | 27.6/16kV | 7F2 | Isolated transformer X 12819 at River Rd and Limebake to replace pole | Gloucester | Scheduled Outage | Construction
12138 | 2008 | 3 | 12 | 0.56181 |  | 218 | 44 | 12 | Limebank | 27.6/16kV | 7F2 | A city Snow plow hit transformer T2824B @ Bridlepath & Crosscut. Crew repaired and re-energized. | Gloucester | Foreign Interference | Vehicle
12139 | 2008 | 3 | 13 | 0.5 |  | 60 | 8 | 4 | Limebank | 27.6/16kV | 7F2 | At 12:00 trans at 2555 Bank St was isolated in order to replace defective switches | Gloucester | Scheduled Outage | Repair
6297 | 2005 | 3 | 16 | 0.59514 |  | 69 | 94 | 82 | Limebank | 27.6/16kV | 7F2 | Bird contact at G474R caused fused switch G517R to open interrupting 11 txs, bird and flashed lightening arrestor cleared G517R closed to restore. | Gloucester | Foreign Interference | Bird
10164 | 2007 | 3 | 23 | 0.40972 |  | 90 | 28 | 19 | Limebank | 27.6/16kV | 7F2 | Transformers TE1965 & TE1966 on Massicotte Lane were isolated to replace elbows & inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
10168 | 2007 | 3 | 23 | 0.53472 |  | 85 | 8 | 6 | Limebank | 27.6/16kV | 7F2 | Transformer TE1419 on Cinanni Crt was isolated to replace elbows & inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
10185 | 2007 | 3 | 27 | 0.37847 |  | 175 | 29 | 10 | Limebank | 27.6/16kV | 7F2 | Transformer TE1061 at 3924 Automwood, isolated for elbow & insert replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
10187 | 2007 | 3 | 27 | 0.54167 |  | 120 | 50 | 25 | Limebank | 27.6/16kV | 7F2 | Transformers TE1719,T1721, and T1897 on Wyldewood were isolated for elbow and insert replacement. | Gloucester | Scheduled Outage
12182 | 2008 | 3 | 27 | 0.44861 |  | 100 | 25 | 15 | Limebank | 27.6/16kV | 7F2 | TP2911at 230 Stedman isolated to replace damaged transformer. ( Lester Rd @ Albion) | Gloucester | Scheduled Outage | Repair
12187 | 2008 | 3 | 28 | 0.42708 |  | 90 | 10 | 7 | Limebank | 8/4.8kV | 7F2 | Isolated transformer X14772 at 3723 Alderwood Dr to replace pole | Gloucester | Scheduled Outage | Construction
15867 | 2010 | 3 | 29 | 0.41111 |  | 171 | 6 | 2 | Limebank | 27.6/16kV | 7F2 | Transformers TP5481 isolated for crew to install primary cable | Gloucester | Scheduled Outage
15868 | 2010 | 3 | 29 | 0.42569 |  | 75 | 12 | 10 | Limebank | 27.6/16kV | 7F2 | Transformer TP5482 was isolated for crew to install primary cable | Gloucester | Scheduled Outage
12204 | 2008 | 3 | 30 | 0.46597 |  | 82 | 55 | 40 | Limebank | 27.6/16kV | 7F2 | Crew refused and closed G460R at Mulligan and River rd. overhead patrolled clear, no dead animals. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
12207 | 2008 | 3 | 31 | 0.19306 |  | 17 | 0 | 1 | Limebank | 27.6/16kV | 7F2 | At Mulligan and Emily a fused cut-out failed and caused an outage to 1413 Mulligan, cut-out barrell was replaced and transformer 5836 refused | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
17821 | 2011 | 4 | 2 | 0.525 |  | 116 | 15 | 8 | Limebank | 27.6/16kV | 7F2 | TE3644 @ 339 Chestermere was replace because of a defective transformer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12233 | 2008 | 4 | 3 | 0.38889 |  | 145 | 22 | 9 | Limebank | 27.6/16kV | 7F2 | Transformer #X14776 located at 3723 Alderwood isolated to transfer plant to new pole | Gloucester | Scheduled Outage | Preventive Maintenance
17867 | 2011 | 4 | 10 | 0.68542 |  | 517 | 13 | 5 | Limebank | 27.6/16kV | 7F2 | Burnt crossarm at G468, 2101 Alert caused 2 fuses to blow at G657. G657 opened, to clear tank and power restored to 4 customers, On call coming in to make repairs. | Gloucester | Defective Equipment
10264 | 2007 | 4 | 16 | 0.38194 |  | 90 | 4350 | 2900 | Limebank | 27.6/16kV | 7F2 | Tree limb contacted an O/H runoff causing the GR1 to trip. 7F2 also auto/reclosed. | Gloucester | Adverse Weather | Snow
20342 | 2012 | 4 | 17 | 0.95903 |  | 160 | 59 | 22 | Limebank | 27.6/16kV | 7F2 | Te3018 @ 937 Goose River Cres was isolated to allow crew to check secondary service and primary cables. Crews found 4 secondary service burnt off and the primary cable damaged between TE3017 & TE3018. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10274 | 2007 | 4 | 18 | 0.34722 |  | 153 | 18 | 7 | Limebank | 27.6/16kV | 7F2 | TE2099 on Bridalpath was isolated to change elbows & inserts. Nomenclature was then changed to TP4613. | Gloucester | Scheduled Outage | Preventive Maintenance
6425 | 2005 | 4 | 19 | 0.42014 |  | 59 | 9 | 9 | Limebank | 27.6/16kV | 7F2 | Transformer T1065 at 3935 Autumnwood isolated to check length of cables to allow transformer to be raised due to flooding. | Gloucester | Scheduled Outage | Preventive Maintenance
10279 | 2007 | 4 | 19 | 0.41458 |  | 217 | 127 | 35 | Limebank | 27.6/16kV | 7F2 | 3 transformers on Mozart crt. & Alserwood st were isolated for planned elbow & insert upgrades. | Gloucester | Scheduled Outage | Preventive Maintenance
20355 | 2012 | 4 | 19 | 0.37778 |  | 263 | 96 | 22 | Limebank | 27.6/16kV | 7F2 | Hydro Ottawa crews isolated TE3018 at 937 Goose River Ave. due to faulted primary & secondary cables. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10289 | 2007 | 4 | 20 | 0.52083 |  | 75 | 6 | 5 | Limebank | 27.6/16kV | 7F2 | Mark Branchaud isolated TRF @ Lester & Albion to chg pole | Gloucester | Scheduled Outage | Preventive Maintenance
10320 | 2007 | 4 | 24 | 0.73958 |  | 11 | 9 | 50 | Limebank | 27.6/16kV | 7F2 | T1341 & T1342 outage due to a human error. (Failed to close primary switch at T1341) | Gloucester | Human Element | Switching Errors
10322 | 2007 | 4 | 24 | 0.21389 |  | 732 | 183 | 15 | Limebank | 27.6/16kV | 7F2 | Tony Taylor Isolated TRF @ 2582 Fox Hollow to change a defective TRF. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6469 | 2005 | 4 | 27 | 0.5 |  | 55 | 38 | 42 | Limebank | 27.6/16kV | 7F2 | In-line fused switch G325R found opened, circuit patrolled and no cause found, sw refused and closed. | Gloucester | Unknown/Other
16004 | 2010 | 4 | 27 | 0.35 |  | 54 | 3 | 3 | Limebank | 27.6/16kV | 7F2 | G657 one blown fuse field phase. Overhead aptroled and nothing found. New fuse installed | Gloucester | Unknown/Other | No Apparent Cause
18077 | 2011 | 5 | 1 | 0.59097 |  | 137 | 120 | 55 | Limebank | 27.6/16kV | 7F2 | Recloser RX2001 auto re-closed due to a tree falling onto the line behind 11 Mary Street which in turn caused S17881 and G806 fuses to blow. Limebank (7F2) ID#18077 | Gloucester | Tree Contacts | Inadequate Trimming
18080 | 2011 | 5 | 1 | 0.73819 |  | 467 | 221 | 59 | Limebank | 27.6/16kV | 7F2 | Tree damage caused the G806W and S17881 to blow, sectionalized and restored in stages during patrol, repairs made before final customers can be restored | Gloucester | Tree Contacts | Tree Fallen
8224 | 2006 | 5 | 3 | 0.65139 |  | 2 | 2 | 60 | Limebank | 27.6/16kV | 7F2 | During restoration of S32 on Spratt Road, an outage occurred on the red phase between PP2001RTP2033 and T3019RS32 interrupting power to 7 transformers. The Crew installed the elbow at T3019RS32 but left the internal position inside the transformer in the off position. | Gloucester | Human Element | Switching Errors
18128 | 2011 | 5 | 10 | 0.37639 |  | 508 | 76 | 9 | Limebank | 27.6/16kV | 7F2 | GLTE2885 at 4148 Wolf Point Way isolated by Hydro Ottawa Crew to change out leaking transformer | Gloucester | Scheduled Outage
6535 | 2005 | 5 | 11 | 0.14444 |  | 199 | 139 | 42 | Limebank | 27.6/16kV | 7F2 | G325R on River rd. opened due to craked insulator. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
14367 | 2009 | 5 | 15 | 0.78264 |  | 126 | 1242 | 925 | Limebank | 27.6/16kV | 7F2 | The cable dip at G15429, Limebank station went bad and cause the 7F2 circuit to trip. When we tried to close in the 7F2 breaker it tripped and also caused the 7F4 to trip. The section was isolated and the 7F2 was restored through the 7F4. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20534 | 2012 | 5 | 17 | 0.42361 |  | 202 | 50 | 15 | Limebank | 27.6/16kV | 7F2 | Transformer TE2887 @ 4116 Wolfe Point was isolated by the crew to allow them to replace it because it was leaking. | Gloucester | Scheduled Outage | Repair
16124 | 2010 | 5 | 22 | 0.63056 |  | 41 | 1708 | 2500 | Limebank | 27.6/16kV | 7F2 | 7F2 breaker A/R/A. Customer reported flash & explosion on Earl Armstrong E. Of Spratt, line patrolled, no problems found, breaker closed & held. Suspect lightning strike. Note: Barhaven not affected as circuit in abnormal condition. | Gloucester | Adverse Weather | Lightning
8346 | 2006 | 5 | 24 | 0.32222 |  | 374 | 50 | 8 | Limebank | 27.6/16kV | 7F2 | Isolated transformer TP3905 on Rideau Cove to replace leaking transformer and the porcelain switches. | Gloucester | Scheduled Outage | Repair
16209 | 2010 | 6 | 6 | 0.67569 |  | 62 | 50 | 48 | Limebank | 27.6/16kV | 7F2 | Tree contact Mulligan and River area caused G460R to open, line patrolled, reported clear and re-fused. | Gloucester | Tree Contacts
10565 | 2007 | 6 | 8 | 0.8375 |  | 302 | 206 | 41 | Leitrim | 27.6/16kV | 7F2 | Crew refused G325 on River rd. they report that no cause was found. Area has history of outages due to tree contacts. | Gloucester | Tree Contacts
14543 | 2009 | 6 | 16 | 0.39583 |  | 85 | 425 | 300 | Limebank | 27.6/16kV | 7F2 | The R & B phase transformers in the Spratt Rd and Bluff Dr area which are fed from PP2056 had to be off loaded because of the out phase condition and return them back to normal supply | Gloucester | Scheduled Outage
5346 | 2004 | 6 | 21 | 0.44792 |  | 51 | 10 | 12 | Limebank | 27.6/16kV | 7F2 | Tx 2361 @ 308 River rd opened to replace a defective insulator | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
8570 | 2006 | 6 | 22 | 0.19792 |  | 55 | 5 | 5 | Limbank | 27.6/16kV | 7F2 | Crew sent to Alert Rd. and they found that one phase of G657 was open. They patrolled the O/H, found nothing and closed the fuse in again to pick up phase. | Gloucester | Unknown/Other | No Apparent Cause
10712 | 2007 | 6 | 22 | 0.89236 |  | 25 | 2 | 6 | Limebank | 27.6/16kV | 7F2 | Transformer #2262 located at 5442 North Riverside Dr isolated to make repairs to burnt secondary connection at the transformer | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18514 | 2011 | 6 | 24 | 0.8 |  | 583 | 233 | 24 | Limebank | 27.6/16kV | 7F2 | Switch G608 in Black Rapids blew due to tree falling into lines. | Gloucester | Adverse Weather | Wind
16333 | 2010 | 6 | 26 | 0.79097 |  | 129 | 2 | 1 | Limebank | 27.6/16kV | 7F2 | Crow contact cause Fuse at S29290 @ 335 River Road to blow. | Gloucester | Foreign Interference | Bird
10744 | 2007 | 6 | 27 | 0.40278 |  | 60 | 6 | 6 | Limebank | 27.6/16kV | 7F2 | Isolated GL4227 transformer at 5 Lewer St to replace defective transformer | Gloucester | Scheduled Outage | Repair
6849 | 2005 | 7 | 1 | 0.75 |  | 1276 | 21 | 1 | Limebank | 27.6/16kV | 7F2 | R. Blair reports insulator replaced on overhead section between G933 & TE2503. All power restored to normal. | Gloucester | Adverse Weather | Lightning
6850 | 2005 | 7 | 1 | 0.75 |  | 1295 | 22 | 1 | Limebank | 27.6/16kV | 7F2 | M. Gruich reports G760 rwb is now closed restoring T2003 load to normal | Gloucester | Adverse Weather | Lightning
6858 | 2005 | 7 | 1 | 0.6875 |  | 1928 | 64 | 2 | Limebank | 27.6/16kV | 7F2 | VE74 at 1600 Tom Roberts Rd, Airport Data Centre out due to fire in the vault as a result of lightning. Vault totally cleaned and switch SE14 replaced with mole. | Gloucester | Adverse Weather | Lightning
6865 | 2005 | 7 | 4 | 0.36597 |  | 163 | 3 | 1 | Limebank | 27.6/16kV | 7f2 | S. Cunningham arrester and switch replaced at this location. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6888 | 2005 | 7 | 8 | 0.73403 |  | 62 | 5 | 5 | Limebank | 27.6/16kV | 7F2 | Local fuse at G657B found opened, run off patrolled and no problem found, refused and closed. | Gloucester | Unknown/Other
10818 | 2007 | 7 | 8 | 0.59375 |  | 101 | 7 | 12 | LIMEBANK | 27.6/16kV | 7F2 | Bird contact caused transformer to blow at Rideau Rd and River Rd, and they later found G444R LLC was burning up. Refused transformer and replaced switch to restore power to all customers. | Gloucester | Defective Equipment
16451 | 2010 | 7 | 9 | 0.77083 |  | 317 | 5 | 1 | Limebank | 27.6/16kV | 7F2 | Defective transformer at 4600 High St was replaced, and power restored. | Gloucester | Adverse Weather | Lightning
18643 | 2011 | 7 | 12 | 0.39583 |  | 226 | 11 | 3 | Limebank | 27.6/16kV | 7F2 | Trans at 497 River Rd was isolated in order to replace the trans | Gloucester | Scheduled Outage | Preventive Maintenance
7020 | 2005 | 7 | 13 | 0.95833 |  | 595 | 416 | 42 | Limebank | 27.6/16kV | 7F2 | In-line fused switch G325R found opened, circuit patrolled and no cause found, sw refused and closed. | Gloucester | Unknown/Other | No Apparent Cause
8731 | 2006 | 7 | 15 | 0.34514 |  | 100 | 82 | 49 | Limebank | 27.6/16kV | 7F2 | A crow cause a transformer fuse and an in line fuse G460R to blow on River Rd at Mulligan. | Gloucester | Foreign Interference | Bird
18717 | 2011 | 7 | 18 | 0.68056 |  | 103 | 82 | 48 | limebank | 27.6/16kV | 7F2 | tree limb came down on overhead at 3990 shirley caused fuse G460R at Mulligan and River rd. To open. | Gloucester | Tree Contacts | Tree Limb Fallen
7012 | 2005 | 7 | 23 | 0.24306 |  | 280 | 196 | 68 | Limebank | 27.6/16kV | 7F2 | A large crow flew into the O/H at transformer 5820 causing switch G435R to open. Arrester at tx 5820 was damaged and tx had to be isolated to change the arrester and install a tx switch. | Gloucester | Foreign Interference | Animal
18832 | 2011 | 7 | 26 | 0.51806 |  | 218 | 59 | 21 | Limebank | 27.6/16kV | 7F2 | G47 and G638 on Rhea place opened due to defective insulator. | Gloucester | Defective Equipment
13101 | 2008 | 8 | 18 | 0.68958 |  | 78 | 1290 | 992 | LIMEBANK | 27.6/16kV | 7F2 | SOMETIME BETWEEN 16:33, AND 17:45 WE LOST COMUNICATION WITH THE LIMEBANK RTU, SOMETIME DURING THAT LOSS OF COMUNICATION THE 7F2 BREAKER OPENED, WHEN THE RTU CAME BACK UP, THE BREAKER WAS CLOSED VIA SCADA AT 17:51. | Gloucester | Adverse Weather | Lightning
7177 | 2005 | 8 | 21 | 0.48264 |  | 182 | 3123 | 2500 | Limebank | 27.6/16kV | 7F2 | Blown cable terminated found at G754 at south end of runway on Leitrim Rd. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9038 | 2006 | 8 | 24 | 0.32639 |  | 50 | 11 | 13 | Limebank | 27.6/16kV | 7F2 | Transformer #GL002601 located at 1566 Goth isolated due to squirrel interference | Gloucester | Foreign Interference | Animal
9055 | 2006 | 8 | 25 | 0.42986 |  | 26 | 4 | 9 | Limebank | 27.6/16kV | 7F2 | Transformer #GL000191 located at 3572 Albion isolated due to squirrel interference | Gloucester | Foreign Interference | Animal
19022 | 2011 | 8 | 26 | 0.95556 |  | 184 | 6 | 2 | Limebank | 27.6/16kV | 7F2 | At 22:56 crews isolated SC6340 at 4231 Golden Eye Way to repair charging springs. 2 customers affected for 184 mins. Limebank 7F2 ID# 19022 | Gloucester | Scheduled Outage
16866 | 2010 | 9 | 3 | 0.85903 |  | 275 | 37 | 8 | Limebank | 27.6/16kV | 7F2 | tree contacts caused the G324 blue phase fuse to open at 318 riverside dr. | Gloucester | Tree Contacts | Inadequate Trimming
15058 | 2009 | 9 | 5 | 0.72708 |  | 161 | 27 | 10 | Limebank | 27.6/16kV | 7F2 | Police reported wires down at 11 Lennon Cres, Crew Opened Xfrm'r X12809, Crews repaired wired and all power restored | Gloucester | Defective Equipment
5794 | 2004 | 9 | 9 | 0.86042 |  | 51 | 23 | 36 | Limebank | 27.6/16kV | 7f2 | Tree branch fell into transformer and blow out fuse at G455W.Transformer switch open G455w closed branch removed and transformer closed back in. | Gloucester | Adverse Weather | Wind
16967 | 2010 | 9 | 20 | 0.39583 |  | 247 | 54 | 13 | Limebank | 8/4.8kV | 7F2 | TP5475 at 656 Chapman mills isolated to allow contractor to pull in new secondary. | Gloucester | Scheduled Outage | Construction
15138 | 2009 | 9 | 21 | 0.54028 |  | 57 | 16 | 17 | Limebank | 27.6/16kV | 7F2 | GLTE3087 at 873 Schooner was isolated to replace leaking transformer. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
5819 | 2004 | 9 | 24 | 0.51042 |  | 70 | 112 | 94 | Limebank | 27.6/16kV | 7F2 | Replaced a blown fuse (40 amp) replace it with a 65 amp fuse which was in the other two phases | Gloucester | Defective Equipment
15168 | 2009 | 9 | 25 | 0.8 |  | 41 | 68 | 100 | Limebank | 27.6/16kV | 7F2 | transformer TP5787 @ Cambrian and Greenbank was isolated to repair damaged ground dug up by contractor. 12 transformers were interrupted on radial feed. | Nepean | Scheduled Outage
15200 | 2009 | 10 | 3 | 0.36458 |  | 356 | 18 | 3 | Limebank | 27.6/16kV | 7F2 | 3 customers in the area of 3500 Limebank were removed from Hydro Ottawa Supply in order to transfer them over to newly constructed overhead line. | Gloucester | Scheduled Outage | Construction
17046 | 2010 | 10 | 3 | 0.48125 |  | 87 | 1 | 1 | Limebank | 27.6/16kV | 7F2 | Replaced blown fuse feeding trtansformer 925 at 1425 Mulligan (Squirrel contact) | Gloucester | Foreign Interference | Animal
13330 | 2008 | 10 | 6 | 0.41389 |  | 34 | 57 | 100 | Limebank | 27.6/16kV | 7F2 | 12 R phase tx's & 18 B phase tx's were affected during switching to isolate cable sections to reconfigure cables & install 13 new transformers. The outage was necessary due to an out of phase condition. | Gloucester | Scheduled Outage | Construction
13395 | 2008 | 10 | 20 | 0.39931 |  | 315 | 94 | 18 | Limebank | 27.6/16kV | 7F2 | Schedualled outage to TP2042 to allow crews to move transformer from the red phase to the blue phase. 18 customers affected | Gloucester | Scheduled Outage | Construction
11568 | 2007 | 10 | 21 | 0.42083 |  | 249 | 203 | 49 | Limebank | 27.6/16kV | 7F2 | Blue phase cable section between TE2825 & SE30 on Millstream failed. Cable isolated & power restored | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9518 | 2006 | 10 | 26 | 0.50347 |  | 19 | 158 | 500 | Limebank | 27.6/16kV | 7F2 | During switching to transfer part of Leitrim 49F1 load to Limebank7F2, GR1 tripped causing an outage to part of 49F1 & part of 7F2. The recloser trip setting was checked at request of system by stations dept & reported in correct position to accept increased load. Recloser reset & closed restoring all customers. | Gloucester | Human Element | Incorrect Protection Settings
13528 | 2008 | 10 | 29 | 0.13194 |  | 608 | 203 | 20 | LIMEBANK | 27.6/16kV | 7F2 | G806W fuse blew due to broken pole and downed conductor in Black's Rapids area | Gloucester | Defective Equipment
9571 | 2006 | 11 | 1 | 0.4 |  | 80 | 5 | 4 | Limebank | 27.6/16kV | 7F2 | At 09:30 am Darcy replaced trf. @303 river rd. | Gloucester | Scheduled Outage | Preventive Maintenance
13561 | 2008 | 11 | 4 | 0.41806 |  | 268 | 49 | 11 | Limebank | 27.6/16kV | 7F2 | TP2053 at 5011 North Bluff was isolated to re-arrange ducts to move transformer from red phase to blue phase of Limebank F2 circuit. | Gloucester | Scheduled Outage
17299 | 2010 | 11 | 18 | 0.34375 |  | 24 | 1 | 2 | Limebank | 27.6/16kV | 7F2 | Isolated transformer GL005069 at 7 Rapids View St to disconnect/reconnect secondary service | Gloucester | Scheduled Outage | Emergency Services Request
11744 | 2007 | 11 | 21 | 0.38819 |  | 164 | 8 | 3 | LIMEBANK | 27.6/16kV | 7F2 | Primary switch at Transf #GL2689 located at 884 River Rd was found open due to tree contact on primary | Gloucester | Tree Contacts | Tree Limb Fallen
13667 | 2008 | 11 | 25 | 0.41667 |  | 190 | 38 | 12 | Limebank | 27.6/16kV | 7F2 | Tx X12809 at 17 Lennon Dr isolated to replace pole & rearrange Hydro plant | Gloucester | Scheduled Outage | Repair
5948 | 2004 | 11 | 29 | 0.17708 |  | 50 | 1 | 1 | Limebank | 27.6/16kV | 7F2 | Re-fused O/H transformer at 466 River Rd | Gloucester | Unknown/Other | No Apparent Cause
9765 | 2006 | 12 | 1 | 0.43056 |  | 30 | 2 | 5 | Limebank | 27.6/16kV | 7F2 | Darcy isolated trf. # 2193 @1422 mulligan to repair tpx. | Gloucester | Scheduled Outage | Preventive Maintenance
15455 | 2009 | 12 | 2 | 0.53681 |  | 14 | 302 | 1294 | Limebank | 27.6/16kV | 7F2 | The Limebank 7F2 breaker auto tripped while under Hold off. 7F2 bkr closed from SCADA and all load restored. Circuit to be patrolled when possible. | Gloucester | Unknown/Other
19662 | 2011 | 12 | 2 | 0.42361 |  | 2 | 3 | 82 | Limebank | 27.6/16kV | 7F2 | Due to an out of phase condition, 8 Blue phase transformers in the area of Claridge were interrupted to perform switching on the loop configuration | Gloucester | Scheduled Outage
7716 | 2005 | 12 | 12 | 0.43125 |  | 115 | 38 | 20 | LIMEBANK | 27.6/16kV | 7F2 | Transformers T3159 & T3160 isolated to repair bent neutral bus bars. | Gloucester | Scheduled Outage | Preventive Maintenance
17448 | 2010 | 12 | 22 | 0.42083 |  | 161 | 8 | 3 | Limebank | 27.6/16kV | 7F2 | TP3701 isolated from Hydro Ottawa Sources for crew to replace damaged transformer at 794 Bowercrest | Gloucester | Scheduled Outage
19760 | 2011 | 12 | 23 | 0.49792 |  | 18 | 20 | 67 | Limebank | 27.6/16kV | 7F2 | While restoring SE28 crew installed elbow but forgot to check transformer switch closed. Parrallel on itself so no amp checkes to check from system office. Holiday brain fart. | Gloucester | Human Element | Switching Errors
15583 | 2009 | 12 | 28 | 0.69792 |  | 121 | 91 | 45 | Limebank | 27.6/16kV | 7F2 | Conductor down and switch 806W open to make repairs to customers at Blacks Rapids. | Gloucester | Scheduled Outage | Repair
19297 | 2011 | 10 | 1 | 0.31042 |  | 142 | 9327 | 5205 | Limebank | 27.6/16kV | 7F2 & 7F4 | 7F2 breaker tripped and would not close back in so the circuit was sectionalized and transfered in sections to the 7F4. The 7F4 then tripped when the second section of 7F2 was energized which revealed a tree branch contacted 2 phases of the primary overhead at the river crossing. The 7F2 was re-sectionalized and 7F4 closed back in. Once the branch was cleared the remaining customers were restored. | Gloucester | Tree Contacts | Tree Limb Fallen
11326 | 2007 | 9 | 17 | 0.80069 |  | 469 | 154 | 57 | Limebank | 27.6/16kV | 7F2 (GR1) | TE2588 at 3395 Daoust failed causing G695 RWB to blow. The transformer was isolated & replaced by the on-call crew and oil spill cleaned up. During isolation the crew found a broken bushing at TE702. 3 transfomers were isolated together to repair TE702 & replace TE2588. The expanded isolation only affected a City Pool & baseball diamoind which were not being used during the outage. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6843 | 2005 | 7 | 1 | 0.88194 |  | 929 | 10131 | 3115 | Limebank | 27.6/16kV | 7F2,7F4 | Overhead crews removed trees from overhead circuit, and isolated a section of head circuit on 7F4 circuit. | Gloucester | Adverse Weather | Lightning
4678 | 2004 | 1 | 5 | 0.40972 |  | 25 | 1 | 3 | Limebank | 27.6/16kV | 7F4 | Transformer 5930 at 5030 Lime bank Rd out to replace cutout. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4690 | 2004 | 1 | 9 | 0.33333 |  | 160 | 3 | 1 | Limebank | 27.6/16kV | 7F4 | Transformer #003649 at the corner of Earl Armstrong and Spratt Rd went defective. Transformer was changed and power restored. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
6134 | 2005 | 1 | 14 | 0.049306 |  | 100 | 548 | 329 | Limebank | 27.6/16kV | 7F4 | D. Howat reports broken insulator found infront of 817 River Rd. Insulator was replaced and all power was restored to normal. | Gloucester | Defective Equipment
13866 | 2009 | 1 | 14 | 0.23264 |  | 226 | 38 | 10 | Limebank | 27.6/16kV | 7F4 | Defective feedthrough bushing at the normally open point at TP2491 at 708 Merlin, glouchester. Crew replaced feed through. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6161 | 2005 | 1 | 31 | 0.64097 |  | 142 | 5 | 2 | Limebank | 8/4.8kV | 7F4 | Replaced broken switch on transformer #475 at 5549 Ficko Cres | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7883 | 2006 | 2 | 2 | 0.56042 |  | 189 | 915 | 1115 | Limebank | 27.6/16kV | 7F4 | 7F4 tripped open. Broken insulator found on Rideau west of switch 328. Partial restoration, all 3 insulator replaced. Outage effected Manotick Island, South Gloucester. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15700 | 2010 | 2 | 2 | 0.42361 |  | 10 | 4 | 21 | Limebank | 27.6/16kV | 7F4 | Momentary outages to 6 transformers on Mclean, West River, Hilltop on Manotik Island for Hydro crew to operate non-vented elbows safely. | Gloucester | Scheduled Outage
15821 | 2010 | 2 | 2 | 0.4375 |  | 10 | 4 | 22 | Limebank | 27.6/16kV | 7F4 | Short interruption to customers on McLean, West River and Hilltop in Manotick for crew to operate non-vented elbows. | Gloucester | Scheduled Outage
15703 | 2010 | 2 | 3 | 0.40278 |  | 266 | 71 | 16 | Limebank | 27.6/16kV | 7F4 | Customers fed from overhead transformers on McClean and Hilltop on Manotik Island were interrupted for Hydro crew to replace a damaged pole. | Gloucester | Scheduled Outage
7899 | 2006 | 2 | 6 | 0.66181 |  | 33 | 193 | 350 | Limebank | 27.6/16kV | 7F4 | 7F4 Breaker opened by system to enable crew to brace pole with RBD. Limebank, Rideau Road, Albion, Earl Armstrong area. | Gloucester | Foreign Interference | Vehicle
15714 | 2010 | 2 | 10 | 0.43125 |  | 66 | 7 | 6 | Limebank | 27.6/16kV | 7F4 | Crew isolated T1206 on Hilltop to repair broken insert and elbow. Affected 6 customers on Hilltop. | Gloucester | Scheduled Outage | Repair
12035 | 2008 | 2 | 11 | 0.58472 |  | 27 | 9 | 20 | Limebank | 27.6/16kV | 7F4 | Vehicle hit a pole on Limebank Rd which caused the poletop insulator to break & fall on the side insulator with the conductor still attached. The 20 affected customers were inside the section of line isolated for repairs. | Gloucester | Foreign Interference | Vehicle
4808 | 2004 | 2 | 20 | 0.46736 |  | 1 | 0 | 12 | Limebank | 27.6/16kV | 7F4 | R. Barnett reports GR444R phase switch is now replaced. Switch was defective. 12 Customers effected in power outage notified the day of the outage. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4810 | 2004 | 2 | 20 | 0.34722 |  | 85 | 1 | 1 | Gloucester | 27.6/16kV | 7F4 | Transformer GL1880 at 5504 Spratt Rd interrupted to repair broken switch. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15747 | 2010 | 2 | 26 | 0.20694 |  | 268 | 1117 | 363 | limebank | 27.6/16kV | 7F4 | J. Leblanc reports branch on overhead circuit at 1109 Irene. J. Leblance reports branch removed burn marks on overhead conductor at this location. 24/7 reports G718 R & B fuses closed. Restoring approx 260 customers. S18183 B phase fuse closed restoring 30 customers. Hydro One dispatch reports wire down at 1096 Lena ave. 24/7 dispatched to check reports of downed wire. Mike reports bell wire. Steve reports S18183W phase now closed restoring load. | Gloucester | Tree Contacts | Tree Limb Fallen
4853 | 2004 | 3 | 3 | 0.48403 |  | 33 | 1 | 2 | Limebank | 27.6/16kV | 7F4 | A cutout was replaced to an overhead transformer 5606 at 4955 Limebank Rd. 2 customers at 4955 & 4967 Limebank were affected. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15769 | 2010 | 3 | 4 | 0.64861 |  | 126 | 32 | 15 | Limebank | 27.6/16kV | 7F4 | G605 at Rideau rd & Downey was found blown due to tree contacts. Tree cleared & G605 replaced. | Gloucester | Tree Contacts
15771 | 2010 | 3 | 4 | 0.64861 |  | 126 | 32 | 15 | Limebank | 27.6/16kV | 7F4 | G605 at Rideau rd & Downey blew due to tree contacts. Tree cleared & G605 replaced. | Gloucester | Tree Contacts
20106 | 2012 | 3 | 4 | 0.10347 |  | 690 | 8695 | 1155 | Limebank | 27.6/16kV | 7F4 | 7F4 A/R a second time, customer calls indicate G2 feeding Manotick area is blown. Tree on River rd has taken down 3 phase primary line. 7F4 circuit opened at station to allow crews to close G2 in-line fused switch. G2 switch was closed restoring all load. | Gloucester | Adverse Weather | Wind
12105 | 2008 | 3 | 5 | 0.50694 |  | 100 | 5 | 3 | Limebank | 8/4.8kV | 7F4 | Isolated and replaced defective transformer X13184 at 819 River Rd | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15777 | 2010 | 3 | 6 | 0.6375 |  | 90 | 21 | 14 | Limebank | 27.6/16kV | 7F4 | G605B phase fuse found open at Downey Rd & Rideau Rd due to tree limb on customer owned primary. G605B closed restoring load to 14 Customers. | Gloucester | Tree Contacts | Tree Limb Fallen
12117 | 2008 | 3 | 10 | 0.026389 |  | 130 | 178 | 94 | Limebank | 27.6/16kV | 7F4 | At 12:38am customers in the area of McLean, Driscoll and Hillcrest called in with loss of power complaints. 24-7 dispatched and found G443 and G677 open and fuse blown at G443. Refused and closed and all power restored to customers. No apparent cause. 28 customers affected for 71 min and 68 customers for 130min. ID#12117. | Gloucester | Unknown/Other | No Apparent Cause
12120 | 2008 | 3 | 10 | 0.25 |  | 149 | 169 | 68 | Limebank | 27.6/16kV | 7F4 | Customers down stream of G677 reported power out again. 24/7 reports white phase fuse blown and they suspect fuse installed earlier this morning was bad. After doing a patrol of the overhead. G677 at 5286 Mclean re-fused and closed back in and holding. | Gloucester | Unknown/Other
12130 | 2008 | 3 | 12 | 0.21875 |  | 95 | 108 | 68 | Limebank | 27.6/16kV | 7F4 | G677 on Maclean in Manotick blew. Fuse also blew twice on Monday but patrol did not reveal a cause. G677W refused successfully, still no cause. Dayshift to patrol again. | Gloucester | Unknown/Other
12131 | 2008 | 3 | 12 | 0.35417 |  | 330 | 372 | 89 | Limebank | 27.6/16kV | 7F4 | G443W on Maclean in Manotick blew. Fuse also blew this morning and also twice on Monday but patrol did not reveal a cause. Upon further investigation it was suspected underground cables are the cause. Crews have cut in new switches and installed temporary o/h to energize two transformers on Driscoll & Hillcrest. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
12137 | 2008 | 3 | 12 | 0.65694 |  | 84 | 8 | 6 | Limebank | 27.6/16kV | 7F4 | Transformer #GL5789 located at 5358 Mclean Cres isolated due to squirrel contact | Gloucester | Foreign Interference | Animal
12162 | 2008 | 3 | 20 | 0.55208 |  | 47 | 2 | 2 | Limebank | 27.6/16kV | 7F4 | Transformer #13129 at 733 River Rd. isolated to allow for service installation | Gloucester | Scheduled Outage | Repair
20206 | 2012 | 3 | 22 | 0.875 |  | 10 | 0 | 1 | Limebank | 27.6/16kV | 7F4 | Transformer #X14207 located at 5199 Limebank Rd opened by crew to replace broken cut out | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
8086 | 2006 | 3 | 30 | 0.72222 |  | 40 | 5 | 7 | Limebank | 27.6/16kV | 7F4 | Transformer #GL5512 located at 5457 Albion Rd isolated to make repairs on secondary | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14115 | 2009 | 3 | 30 | 0.32986 |  | 335 | 8339 | 2910 | Limebank | 27.6/16kV | 7F4 | 7F4 opened and locked out when an insulator broke at Limebank north of Rideau. 7F1 load and part of 7F2 was transferred to the 7F4 at the time. Most load was restored except at Rideau and Limebank while emergency repairs where made | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4954 | 2004 | 4 | 1 | 0.44792 |  | 22 | 2 | 6 | Limebank | 27.6/16kV | 7F4 | Isolate transformer GL03899 @ 5422 West River Rd to replace switch. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4955 | 2004 | 4 | 1 | 0.53472 |  | 40 | 3 | 5 | Limebank | 27.6/16kV | 7F4 | Isolate transformer GL5659 @ 5428 North Riverside Dr to replace arrester. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4956 | 2004 | 4 | 1 | 0.58333 |  | 20 | 4 | 11 | Limebank | 27.6/16kV | 7F4 | Isolate transformer GL2262 @ 5454 North River Rd to replace switch. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8089 | 2006 | 4 | 1 | 0.29375 |  | 117 | 624 | 320 | LIMBANK | 27.6/16kV | 7F4 | CREW FOUND BAD INSULATOR ON METERING UNIT @ 989 RIVER RD. CAUSING THE WHITE PHASE OF G2 TO OPEN. CREW ISOLATED BAD INSULATOR AND CLOSED G2 WHITE PHASE TO PICK UP LOAD. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15878 | 2010 | 4 | 1 | 0.39236 |  | 135 | 4 | 2 | Limebank | 27.6/16kV | 7F4 | Transformer #X14168 located at 4689 Limebank Rd isolated for pole replacement | Gloucester | Scheduled Outage | Construction
4964 | 2004 | 4 | 2 | 0.56944 |  | 20 | 1 | 2 | Limebank | 27.6/16kV | 7F4 | Transformer GL000876 on 7F4 located at 5308 Long Island Addresses affected 5301 and 5304 Long Island. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
12222 | 2008 | 4 | 2 | 0.84167 |  | 431 | 1153 | 1036 | Limebank | 27.6/16kV | 7F4 | Broken insulator at Rideau Carleton Raceway caused 7F4 breaker to open. G903 opened and 7F4 closed to restore power to Manotick. G312 opened and G903 closed torestore Rideau Rd. Insulators and conductor replaced and last 32 customers restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6359 | 2005 | 4 | 3 | 0.29861 |  | 150 | 230 | 92 | Limebank | 27.6/16kV | 7F4 | Blown switch to transformer at 5466 North Ave. Switch repaired and fused switch G166B closed all power restored. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
3318 | 2003 | 4 | 4 | 0.57639 |  | 200 | 27 | 8 | Limebank | 27.6/16kV | 7F4 | Switch G57 RWB opened to isolate line on Spratt Road to allow for the replacement and temporary repairs to a crossarm. Further repairs to be done. | Gloucester | Scheduled Outage | Preventive Maintenance
14143 | 2009 | 4 | 4 | 0.53542 |  | 46 | 826 | 1078 | Limebank | 27.6/16kV | 7F4 | 7F4 breaker tripped due to defective insulator causing wire to come down at station. Circuit isolated, and load restored. | Gloucester | Defective Equipment
15923 | 2010 | 4 | 11 | 0.73542 |  | 71 | 133 | 112 | Limebank | 27.6/16kV | 7F4 | G166B opened, single phase overhead was patrolled and nothing found, load restored successfuly | Gloucester | Unknown/Other | No Apparent Cause
10245 | 2007 | 4 | 12 | 0.6875 |  | 160 | 131 | 49 | Limebank | 27.6/16kV | 7F4 | 24/7 reports broken insulator at Bank St & Bowsville. Insulator replaced & G30R fuse replaced & closed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14178 | 2009 | 4 | 15 | 0.65972 |  | 105 | 2 | 1 | Limebank | 27.6/16kV | 7F4 | Crew replaced defective cut-out, G574 at 449 Nichols Island rd | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10275 | 2007 | 4 | 18 | 0.39583 |  | 100 | 5 | 3 | Limebank | 27.6/16kV | 7F4 | BruceKerfoot isolated TRF 229 @ 5463 Long Island to change insulators | Gloucester | Scheduled Outage | Preventive Maintenance
10276 | 2007 | 4 | 18 | 0.47569 |  | 41 | 3 | 5 | Limebank | 27.6/16kV | 7F4 | Bruce Kerfoot isolated TRF 2440 @ 5437 Long Island to change insulators | Gloucester | Scheduled Outage | Preventive Maintenance
12338 | 2008 | 4 | 23 | 0.78889 |  | 159 | 11 | 4 | Limebank | 27.6/16kV | 7F4 | 7F4 auto-reclosed once at the same time as Leitrim 49F2 auto-reclosed. G823B on High Rd was found blown apart and appeared to have been hit by lightning. Switch was replaced by 24/7 and power restored to 3 customers on High Rd & 1 on Earl Armstrong. | Gloucester | Lightning
3377 | 2003 | 4 | 26 | 0.47222 |  | 47 | 23 | 36 | Limebank | 27.6/16kV | 7F4 | Fuse at o/h Tx503 on Honey Gables opened & G4W also opened causing an outage to 7 transformers affecting 36 customers on Honey Gables, Little & Ryeburn. The O/H was patrolled, no problems found & switches were refused. | Gloucester | Unknown/Other | No Apparent Cause
3382 | 2003 | 4 | 28 | 0.53819 |  | 230 | 1731 | 1414 | 7F4 | 27.6/16kV | 7F4 | Truck hit hydro poles on Albion & Del Zotto st. | Gloucester | Foreign Interference | Vehicle
8201 | 2006 | 4 | 28 | 0.71875 |  | 30 | 2 | 3 | Limebank | 27.6/16kV | 7F4 | Transformer #GL005844 located at 740 River Rd isolated to make repairs:loose connections in the meter base | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12364 | 2008 | 4 | 29 | 0.65486 |  | 82 | 96 | 70 | Limebank | 27.6/16kV | 7F4 | G733 white phase fuse blew, circuit was patrolled with no obvious cause found. G733 W was refused successfully. | Gloucester | Unknown/Other
5080 | 2004 | 4 | 30 | 0.69097 |  | 20 | 2 | 5 | Limebank | 27.6/16kV | 7F4 | J. Streng reports anchor on pole let go, causing the service at road crossing to hang low. Service was pulled down by a truck. Crew isolated transformer replaced switch & repaired service. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3419 | 2003 | 5 | 9 | 0.3375 |  | 443 | 22 | 7 | Limebank | 27.6/16kV | 7F4 | A pole top insulator went defective causing switch G53W&B to rupture and the pole to start on fire. The fuse to G53R was opened to make minor repairs and then all three fuses were replaced and closed. Full power was restored to all customers except the Radio Station. More repairs were made to the line at the Radio Station before it was re-energized bringing everyone back online. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8265 | 2006 | 5 | 9 | 0.58889 |  | 160 | 27 | 15 | Limebank | 27.6/16kV | 7F4 | 4-5 transformers affected from switch #G823 due to high hoe contact with primary wire. NO injuries. | Gloucester | Foreign Interference | Vehicle
14335 | 2009 | 5 | 9 | 0.72917 |  | 167 | 3 | 1 | Limebank | 27.6/16kV | 7F4 | Crew refused transformer 345 @ 752 river rd. that opened due to tree contact. | Gloucester | Tree Contacts | Inadequate Trimming
10411 | 2007 | 5 | 13 | 0.70139 |  | 30 | 6 | 13 | Limebank | 27.6/16kV | 7F4 | 24/7 reports insulators on Hydro pole at 5300 Limebank Rd are tracking due to an earlier MVA. 24/7 replaced insulators and reinstalled down guy. | Gloucester | Foreign Interference | Vehicle
14365 | 2009 | 5 | 15 | 0.35972 |  | 128 | 2 | 1 | Limebank | 27.6/16kV | 7F4 | Transformer #133 located at 5127 Spratt Rd isolated due to wind | Gloucester | Adverse Weather | Wind
14368 | 2009 | 5 | 15 | 0.80903 |  | 16 | 495 | 1856 | Limebank | 27.6/16kV | 7F4 | The cable dip at G15429, Limebank station went bad and cause the 7F2 circuit to trip. When we tried to close in the 7F2 breaker it tripped and also caused the 7F4 to trip. The section was isolated and the 7F2 was restored through the 7F4. | Gloucester | Defective Equipment
18158 | 2011 | 5 | 15 | 0.35764 |  | 22 | 1 | 4 | Limebank | 27.6/16kV | 7F4 | The cutout feeding transformer X13184 at 821 River Rd was sparking and finally opened, defective barrell on cutout replaced | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12445 | 2008 | 5 | 16 | 0.42361 |  | 181 | 57 | 19 | Limebank | 27.6/16kV | 7F4 | S21533 was isolated to install new pole, 19 customers on Driscoll & Hillcrest in Manotick were interupted. | Gloucester | Scheduled Outage
14375 | 2009 | 5 | 18 | 0.32847 |  | 141 | 82 | 35 | Limebank | 27.6/16kV | 7F4 | Power out calls from Manotick, Connection to G280R burnt off, crew made to connectios and restored power | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
6591 | 2005 | 5 | 24 | 0.51042 |  | 39 | 1 | 2 | Limebank | 27.6/16kV | 7F4 | At 12:15 Trans @ 5291 Bowesville Rd Glou isolated to replace defective sw | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
6592 | 2005 | 5 | 24 | 0.54167 |  | 30 | 1 | 2 | Limebank | 27.6/16kV | 7F4 | AT 13:00 trans @ 1309 Bowesville Rd Glou isolated to replace defective sw | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
12480 | 2008 | 5 | 26 | 0.9375 |  | 88 | 21 | 14 | Limebank | 27.6/16kV | 7F4 | 24/7 reports 2 line fuses found blown on Downey Rd. Fuses replaced all power restored to normal. | Gloucester | Adverse Weather | Lightning
20626 | 2012 | 5 | 28 | 0.45625 |  | 73 | 34 | 28 | LIMEBANK | 27.6/16kV | 7F4 | 7F4 circuit auto reclosed. Customer reports power outage on Downey Rd. 24/7 reports tree branch found on overhead line causing G608 & G605 blue phase fuses to blow. Both fuses replaced all power restored. | Gloucester | Tree Contacts | Tree Limb Fallen
18244 | 2011 | 5 | 29 | 0.50069 |  | 101 | 27 | 16 | Limebank | 27.6/16kV | 7F4 | Blown fuse at SE G605B no apparent cause ,, refused power restored | Gloucester | Unknown/Other | No Apparent Cause
10480 | 2007 | 5 | 30 | 0.46528 |  | 36 | 7 | 12 | LIMEBANK | 27.6/16kV | 7F4 | TRANSFORMER #474 AT 5377 LONG ISLAND ISOLATED TO CHANGE INSULATOR & SWITCH | Gloucester | Scheduled Outage | Construction
10490 | 2007 | 5 | 31 | 0.37847 |  | 40 | 3 | 4 | Limebank | 27.6/16kV | 7F4 | Steve isolated TRF. GL840 @ 5312 Long Island for an insulator change | Gloucester | Scheduled Outage | Preventive Maintenance
10492 | 2007 | 5 | 31 | 0.51042 |  | 20 | 2 | 5 | Limebank | 27.6/16kV | 7F4 | Transformer#4363 at front of 5413 Long Island Rd isolated to allow for insulator change | Ottawa | Scheduled Outage | Repair
12516 | 2008 | 5 | 31 | 0.775 |  | 80 | 7 | 5 | Limebank | 27.6/16kV | 7F4 | G53 opened during heavy rain and extreme lightning avtivity. Crew refused and closed. | Gloucester | Adverse Weather
12523 | 2008 | 5 | 31 | 0.86736 |  | 519 | 9 | 1 | limebank | 27.6/16kV | 7F4 | Crew replaced faulted transformer T3118 @ 685 river rd. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
8397 | 2006 | 6 | 1 | 0.14722 |  | 148 | 99 | 40 | Limebank | 27.6/16kV | 7F4 | Blown arrester at 4992 Bowesville Rd changed and new fuse installed to G30R Rideau Rd | Gloucester | Lightning | Direct Strike
18294 | 2011 | 6 | 4 | 0.84444 |  | 46 | 33 | 43 | Limebank | 27.6/16kV | 7F4 | G224R on Driscol in Manotic opened, customers on Jean Park reported a flash and bang in the rear of 1147 Jean Park. Patrol revealed no obvious problems, Fuse closed successfully. Customer called back after G224R was refused reported sparkin at the transformer in her back yard, turned out to be a bad barrel on the fused cut out, transformer opened and fuse replaced. | Gloucester | Defective Equipment | No Apparent Cause
18295 | 2011 | 6 | 4 | 0.89097 |  | 13 | 3 | 15 | Limebank | 27.6/16kV | 7F4 | Customer called back after G224R was refused reported sparkin at the transformer in her back yard, turned out to be a bad barrel on the fused cut out, transformer opened and fuse replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16202 | 2010 | 6 | 5 | 0.82153 |  | 130 | 49 | 112 | Limebank | 27.6/16kV | 7F4 | TX 3862 at 5440 West River Dr tree limb made contact with secondary causing fuse cut out to blow. Transformer switch broke on closing which caused G166B to fail. G166B replaed and TX cutout repaired and cloed. | Gloucester | Tree Contacts | Tree Limb Fallen
8434 | 2006 | 6 | 6 | 0.58681 |  | 23 | 3 | 7 | Limebank | 27.6/16kV | 7F4 | Transformer GL5190 located at 4952 Bowesville isolated due to replacing arrestor | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5259 | 2004 | 6 | 7 | 0.42917 |  | 37 | 3 | 5 | Limebank | 27.6/16kV | 7F4 | Switch G832B was open because of a broken insulator that is tracking across and down the pole on High Rd | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
20718 | 2012 | 6 | 8 | 0.54514 |  | 105 | 54 | 38 | Limebank | 27.6/16kV | 7F4 | At 13:05, Switch G49B & S29528 was found blown due to animal contact. 38 customers affected for 105 minutes. Limebank (7F4) | Gloucester | Foreign Interference | Animal
8458 | 2006 | 6 | 9 | 0.89653 |  | 419 | 35 | 5 | Limebank | 27.6/16kV | 7F4 | G53R phase found blown. Broken cutout ot Transformer 5874. Also, very heavily treed area, 24/7 believe this may have been the initial cause. Replaced cutout, closed G53R. (No crews available to respond to this call until 3:12 am) | Gloucester | Tree Contacts | Inadequate Trimming
8467 | 2006 | 6 | 10 | 0.93403 |  | 535 | 36 | 4 | Limebank | 27.6/16kV | 7F4 | Vehicle hit Hydro Pole at 821 River Road. Transformer 5510 opened. The old pole has been temporray straped to the new one. | Gloucester | Foreign Interference | Vehicle
12587 | 2008 | 6 | 10 | 0.61042 |  | 117 | 258 | 266 | LIMEBANK | 27.6/16kV | 7F4 | GR2 blue phase tripped under hold off. Crew found G49B at Rideau & Spratt blown as well as switch 1881 blown due to tree contact with customer owned primary fed from 1881. GR2 B was closed then G49B. Customer to trim trees before restoring line fed from 1881. | Gloucester | Tree Contacts | Inadequate Trimming
8465 | 2006 | 6 | 11 | 0.025 |  | 139 | 12 | 5 | Limebank | 27.6/16kV | 7F4 | Crew reports G53R blown, and G5660 R is blown. Broken insulator on customer owned line. Customer was advised his power will stay off until repairs are made. | Gloucester | Adverse Weather | Wind
10600 | 2007 | 6 | 11 | 0.44792 |  | 91 | 3 | 2 | Limebank | 27.6/16kV | 7F4 | Transformer #GL000876 isolated by Steve of K-Line to allow for insulator change | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
12598 | 2008 | 6 | 11 | 0.088889 |  | 51 | 4 | 5 | Limebank | 27.6/16kV | 7F4 | The transformer that feeds 5630 Ficko was isolated because of Top pine broke on the primary that feeds that transformer | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12606 | 2008 | 6 | 11 | 0.53333 |  | 67 | 290 | 260 | Limebank | 27.6/16kV | 7F4 | GR2 white phase tripped under hold off. Trip was not caused by crew with hold off and recloser was closed back in restoring all load. Patrol revealed probable cause was tree contact with line on MacLean Drive, 24/7 trimmed back branches. | Gloucester | Tree Contacts | Inadequate Trimming
18388 | 2011 | 6 | 11 | 0.44583 |  | 188 | 19 | 6 | Limebank | 8/4.8kV | 7F4 | replaced blown fuse at S11694 at 1088 Lena Ave feeding a pad mount transformer T1952 at 1134 Cindy Hill Cres (Squirrel contact) | Gloucester | Foreign Interference | Animal
3558 | 2003 | 6 | 12 | 0.43542 |  | 72 | 2 | 2 | Limebank | 27.6/16kV | 7F4 | A bird got caught in the line opening the fuse feeding transformer 229 on Long Island Dr in Gloucester. | Gloucester | Foreign Interference | Animal
14531 | 2009 | 6 | 14 | 0.22569 |  | 72 | 60 | 50 | Limebank | 27.6/16kV | 7F4 | possible tree contact caused the G30R at 1963 Rideau rd. to open. | Gloucester | Tree Contacts | Inadequate Trimming
14534 | 2009 | 6 | 14 | 0.40625 |  | 35 | 5 | 9 | Limebank | 27.6/16kV | 7F4 | Isolated and replaced defective switch to transformer X15873 at 5643 Ficko Cres | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
6726 | 2005 | 6 | 15 | 0.069444 |  | 257 | 1045 | 244 | Limebank | 27.6/16kV | 7F4 | Fused in line sws G733 RWB found blown, circuit patrolled, no problems found, sws refused and closed. Thunderstorm in the area. | Gloucester | Adverse Weather | Lightning
12653 | 2008 | 6 | 15 | 0.74167 |  | 322 | 5984 | 1115 | Limebank | 27.6/16kV | 7F4 | 7F4 breaker opened during heavy rain, high wind & lightning. Restoration was hampered by RTU not reporting to SCADA and 7F4 breaker would not close from local control which required Stations to repair. Stations found control fuse blown and replaced it. Initial cause was believed to be from storm which blew fuse G263 on Albion Rd and breaker probably did not reclose due to blown control fuse. | Gloucester | Lightning
5319 | 2004 | 6 | 16 | 0.4375 |  | 24 | 4 | 9 | Limebank | 27.6/16kV | 7F4 | E. Neumann replaced O/H transformer #3650 at 5474 West River Dr. 9 Customers effected in power outage. | Gloucester | Scheduled Outage | Load Shedding
6743 | 2005 | 6 | 16 | 0.70833 |  | 630 | 1142 | 246 | Limebank | 27.6/16kV | 7F4 | conductor down behind 5313 Driscoll, switch 733 R fuse blown. 733R switch and fuse replaced. TX5811 at 5309 Mclean connections repaired. TX 5733 at 5298 Driscoll cutout switch replaced and a damaged crossarm replaced. Number of customers out increased because SW 733 W,B were opened to allow repairs to be made on all damaged equipment. 6 linemen on site. | Gloucester | Lightning
6755 | 2005 | 6 | 17 | 0.62778 |  | 56 | 7 | 7 | Limebank | 27.6/16kV | 7F4 | Switch G53 opened at Spratt & Earl Armstrong to repair broken switches & insulators | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20782 | 2012 | 6 | 17 | 0.12708 |  | 74 | 62 | 50 | Limebank | 27.6/16kV | 7F4 | The 7F4 auto reclosed,G30R burnt insulators on the O/H | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8504 | 2006 | 6 | 18 | 0.24236 |  | 106 | 14 | 8 | LIMEBANK | 27.6/16kV | 7F4 | Fused switch on transformer GL3842 at 1101 Sunrise Ave opened due to an animal (Bird) contact | Gloucester | Foreign Interference | Bird
18437 | 2011 | 6 | 19 | 0.44583 |  | 177 | 104 | 35 | Limebank | 27.6/16kV | 7F4 | G280R opened, cable to G713 tested bad cable isolated load restored from G281 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12703 | 2008 | 6 | 20 | 0.74792 |  | 100 | 74 | 53 | Limebank | 27.6/16kV | 7F4 | G231W blew for bird contact with O/H xfmr. G231W was refused then xfmr cutout. Albion Rd area south of Rideau Rd. | Gloucester | Foreign Interference | Bird
14583 | 2009 | 6 | 20 | 0.88542 |  | 302 | 10 | 2 | Limebank | 27.6/16kV | 7F4 | Customer called in saying power was out. 24/7 crews investigate and found a defective transformer. Crews change overhead transformer X15702 at 5265 Downey Rd. and cutouts. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12704 | 2008 | 6 | 21 | 0.020833 |  | 85 | 3 | 2 | LIMEBANK | 27.6/16kV | 7f4 | Transformer fuse found blown @ 4088 Albion Rd. Fuse was replaced all power restored | Gloucester | Unknown/Other | No Apparent Cause
14585 | 2009 | 6 | 21 | 0.29583 |  | 72 | 14 | 12 | Limebank | 27.6/16kV | 7F4 | Animal contact caused a local fuse and G673 to blow on Limebank Rd. Crew re-fused both and all load restored. | Gloucester | Foreign Interference | Animal
14586 | 2009 | 6 | 21 | 0.34722 |  | 75 | 99 | 79 | Limebank | 27.6/16kV | 7F4 | S18183 white phase found blown on Long Island Rd, crew re-fused. | Gloucester | Unknown/Other
20848 | 2012 | 6 | 23 | 0.45556 |  | 194 | 71 | 27 | Limebank | 27.6/16kV | 7F4 | G987R fuse blown as well as TX X15813 fuse blown. Line ptrolled and G987 closed. TX 15813 check by crew and closed restoring all power. | Gloucester | Unknown/Other | No Apparent Cause
10718 | 2007 | 6 | 24 | 0.38819 |  | 86 | 1 | 1 | Limebank | 27.6/16kV | 7F4 | Transformer #X15837 located at 2422 Rideau Rd isolated due to animal contact | Gloucester | Foreign Interference | Animal
10735 | 2007 | 6 | 26 | 0.40278 |  | 8 | 1 | 8 | Limebank | 8/4.8kV | 7F4 | Isolated transformer 4105 at 5288 Mclean Cre to cut jumpers on the open buss | Gloucester | Scheduled Outage | Repair
10741 | 2007 | 6 | 26 | 0.21806 |  | 220 | 29 | 8 | LIMEBANK | 27.6/16kV | 7F4 | A defective transformer GL005773 at 5322 McLean, crews jumper out the bus to transformer 4106 to restore power, untill the defective transformer is replace. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12749 | 2008 | 6 | 26 | 0.87083 |  | 86 | 9 | 6 | Limebank | 27.6/16kV | 7F4 | Stormy weather caused G823B on High rd n. of Albion & the upstream device, G263B to blow. Line section patrolled & fuses replaced. | Gloucester | Adverse Weather | Lightning
18529 | 2011 | 6 | 26 | 0.80764 |  | 91 | 33 | 22 | Limebank | 27.6/16kV | 7F4 | Faulted cable section between TE210 and G712W caused G118W to blow. Limebank (7F4) ID#18529 | Gloucester | Defective Equipment
8606 | 2006 | 6 | 27 | 0.57639 |  | 100 | 8 | 5 | LIMEBANK | 27.6/16kV | 7F4 | Switch G49 at Spratt Rd at Rideau Rd due to Lightning | Gloucester | Adverse Weather | Lightning
12757 | 2008 | 6 | 27 | 0.40486 |  | 117 | 2 | 1 | Limebank | 27.6/16kV | 7F4 | Transformer #X16045 located at 4770 Albion Rd isolated due to crow contact | Gloucester | Foreign Interference | Bird
12758 | 2008 | 6 | 27 | 0.36389 |  | 191 | 3 | 1 | Limebank | 27.6/16kV | 7F4 | Transformer #X25004 located at 2220 Earl Armstrong isolated due to crow contact | Gloucester | Foreign Interference | Bird
8630 | 2006 | 6 | 29 | 0.75417 |  | 69 | 7 | 6 | Limebank | 27.6/16kV | 7F4 | A tree fell across the o/h line on High Road. G263 blew. Tree removed and G263 closed. | Gloucester | Tree Contacts | Tree Fallen
10768 | 2007 | 6 | 30 | 0.83333 |  | 135 | 2 | 1 | QueeLimebank | 27.6/16kV | 7F4 | Overhead transformer 5967 at 885 River Rd was isolated to replace 1 phase. Only the 1 customer, Fernlea Flowers was affected. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12773 | 2008 | 6 | 30 | 0.86458 |  | 223 | 15 | 4 | Limebank | 27.6/16kV | 7F4 | Defective transformer X13134 at 740 River road. On Call crew replaced and power restored at 12:28am. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
6863 | 2005 | 7 | 3 | 0.81528 |  | 146 | 108 | 95 | Limebank | 27.6/16kV | 7F4 | G166 blue blown open. T5699 at 5402 west River dr defective. Secondary connected to T3899 at5422 West River Dr. Transformer will be changed on Monday July 4 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16383 | 2010 | 7 | 3 | 0.085417 |  | 57 | 11 | 12 | Limebaank | 27.6/16kV | 7F4 | At 3:00 am switch G444R at 450 Rideau open due to animal contact. 12 customers affected ( Limebank 7F4) | Ottawa | Foreign Interference | Animal
6866 | 2005 | 7 | 4 | 0.39028 |  | 74 | 6 | 5 | Limebank | 27.6/16kV | 7F4 | T5699 at 5402 west River Dr was replaced due to defective trans | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20925 | 2012 | 7 | 4 | 0.67986 |  | 46 | 2 | 2 | Limebank | 27.6/16kV | 7F4 | Replaced blown fuse feeding transformer GL000961 at 1058 Bravar Dr (Crow contact) | Gloucester | Foreign Interference | Bird
16436 | 2010 | 7 | 9 | 0.57639 |  | 5 | 90 | 1074 | Limbank | 27.6/16kV | 7F4 | Attempt to pick up 49F2, the 7F4 opened on overload due to tree contact still existing on the 49F2. | Gloucester | Tree Contacts | Tree Limb Fallen
8688 | 2006 | 7 | 10 | 0.39583 |  | 45 | 4 | 6 | Limebank | 27.6/16kV | 7F4 | K-Line opened transformer at 873 River Road to do insulator changes. | Gloucester | Scheduled Outage
8696 | 2006 | 7 | 11 | 0.43056 |  | 30 | 1 | 2 | Limebank | 12/7.2kV | 7F4 | Isolated transformer GL 3399 at 725 River Rd to replace the primary conductor pole insulators | Gloucester | Scheduled Outage | Preventive Maintenance
8698 | 2006 | 7 | 11 | 0.63333 |  | 48 | 2 | 3 | Limebank | 27.6/16kV | 7F4 | Isolated transformer GL5844 at 740 River Rd to replace the primary conductor pole insulators | Gloucester | Scheduled Outage | Preventive Maintenance
8715 | 2006 | 7 | 13 | 0.34028 |  | 55 | 7 | 8 | Limebank | 27.6/16kV | 7F4 | Donny from K'Line opened transformer GL0245 to do insulator change | Gloucester | Scheduled Outage | Preventive Maintenance
12882 | 2008 | 7 | 18 | 0.18403 |  | 132 | 37 | 17 | Limebank | 27.6/16kV | 7F4 | G49 on Spratt South of Rideau rd. opened due to lightning activity. Refused and closed. | Gloucester | Adverse Weather | Lightning
12883 | 2008 | 7 | 18 | 0.17014 |  | 195 | 767 | 236 | Limebank | 27.6/16kV | 7F4 | Crew refused and closed the S18183 @ long island and Lena in manotick. Crew patrolled and found nothing. Lightning in area. | Gloucester | Adverse Weather | Lightning
8783 | 2006 | 7 | 19 | 0.35625 |  | 230 | 230 | 60 | Limebank | 27.6/16kV | 7F4 | Switch S677W On Manotick Island open to allow tree trimming. Driscoll Dr and Hillcrest Dr. | Gloucester | Scheduled Outage | Preventive Maintenance
12906 | 2008 | 7 | 21 | 0.39306 |  | 34 | 1 | 1 | Limebank | 27.6/16kV | 7F4 | Transformer #GL000472 located at 5332 Long Island Rd isolated due to bird contact. | Gloucester | Foreign Interference | Bird
14799 | 2009 | 7 | 21 | 0.52431 |  | 458 | 2877 | 1078 | Limebank | 27.6/16kV | 7F4 | A truck caught the bell at 5353 Driscoll which caused the pole to lean and break the cross arm. | Gloucester | Foreign Interference | Vehicle
18796 | 2011 | 7 | 22 | 0.49028 |  | 145 | 36 | 15 | Limebank | 27.6/16kV | 7F4 | Crew isolated local on North River rd, to repair broken hydro pole. | Gloucester | Tree Contacts
8807 | 2006 | 7 | 23 | 0.77569 |  | 103 | 60 | 35 | Limebank | 27.6/16kV | 7F4 | Riverside Cres on Manotick Island blown fuse at G280R. Replaced all customers happy. | Gloucester | Foreign Interference | Bird
12979 | 2008 | 7 | 31 | 0.03125 |  | 105 | 16 | 12 | Limebank | 27.6/16kV | 7F4 | Ottawa police reported power out on Mitch Owens at Limebank, crew found line switch G673W & fuse at Tx X14190 blown. Line patrolled & fuses replaced. No customer calls were received. | Gloucester | Unknown/Other | No Apparent Cause
14892 | 2009 | 8 | 2 | 0.30625 |  | 80 | 67 | 50 | Limebank | 27.6/16kV | 7F4 | racoon caused red phase transfomer to open on bowesville which in turn caused the G30R on Rideau rd. to open. Both were refused and closed. | Gloucester | Foreign Interference | Animal
5605 | 2004 | 8 | 3 | 0.28125 |  | 52 | 11 | 13 | Limebank | 27.6/16kV | 7F4 | P. Fisher reports fuse cutout on limebank & Rideau blown open. 24/7 dispatched. Overhead circuit patrolled no fault foun. Fuse replaced and closed. All power restored to normal. 13 Customers affected in power outage. | Gloucester | Unknown/Other | No Apparent Cause
14895 | 2009 | 8 | 3 | 0.45 |  | 57 | 3 | 3 | Limebank | 27.6/16kV | 7F4 | Transformer #X13307 located at 956 River Rd isolated due to animal contact | Gloucester | Foreign Interference | Animal
18890 | 2011 | 8 | 7 | 0.6875 |  | 35 | 5 | 9 | Limebank | 27.6/16kV | 7F4 | At 16:30 crews isolated transformer 5726 at 5296 Hillcrest in Manotick to replace a broken switch. 9 customers affected for 35 mins. Limebank (7F4) ID# 18890 | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
14921 | 2009 | 8 | 8 | 0.37778 |  | 76 | 101 | 80 | Limebank | 27.6/16kV | 7F4 | The 24/7 found S18183 W on Driscoll and McLean phase blown patrolled the circuit and found nothing | Gloucester | Unknown/Other
5648 | 2004 | 8 | 10 | 0.76111 |  | 120 | 2200 | 1100 | Limebank | 27.6/16kV | 7F4 | Problems with closing the 7F4 recloser, had to pick it up through a scada mate G635 out of Leitrim. | Gloucester | Adverse Weather | Lightning
18904 | 2011 | 8 | 10 | 0.65 |  | 87 | 72 | 50 | Limebank | 27.6/16kV | 7F4 | G30R at 1963 Rideau Rd. opened due to a lightning strike. Pole X23210 lightning damage on pole ..plant ok .. storm Wed Aug 10 2011. | Gloucester | Adverse Weather | Lightning
3891 | 2003 | 8 | 11 | 0.91944 |  | 107 | 21 | 12 | Limebank | 27.6/16kV | 7F4 | A tree make contact with the 7F4 along Spratt Rd near Earl Armstrong causing 2 phases of the G53 to blow. The third phase was opened to isolate the section, the tree was removed and the customers were restored. | Gloucester | Tree Contacts | Tree Fallen
8954 | 2006 | 8 | 11 | 0.93333 |  | 34 | 27 | 48 | Limbank | 27.6/16kV | 7F4 | While performing switching crew notices that an under oil switch had been left in the H1A position instead of feed through position. | Gloucester | Human Element | Switching Errors
13062 | 2008 | 8 | 15 | 0.71111 |  | 82 | 1217 | 1037 | LIMEBANK | 27.6/16kV | 7F4 | 7F4 Breaker tripped. Lightning Storm, and Hail going thru parts of the City. Patrolled circuit, Sectionalized to restore power. Found o/h transformer blown at Rideau & Limebank. | Ottawa | Adverse Weather
3910 | 2003 | 8 | 17 | 0.4375 |  | 70 | 1 | 1 | Limebank | 27.6/16kV | 7F4 | Fused switch to overhead transformer 995 at Albion & Rideau Rd blown, cause unknown. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13100 | 2008 | 8 | 18 | 0.74375 |  | 4 | 69 | 1037 | LIMEBANK | 27.6/16kV | 7F4 | SCADA INDICATES BREAKER OPENED, CLOSED VIA SCADA, SEVER STORM IN EFFECT | Gloucester | Adverse Weather | Lightning
13125 | 2008 | 8 | 18 | 0.70833 |  | 1160 | 58 | 3 | Limebank | 27.6/16kV | 7F4 | Transformer #X13145 for 788 River Rd isolated due to storm from yesterday. Call was lost when it rolled up with another outage. | Gloucester | Adverse Weather | Lightning
18982 | 2011 | 8 | 20 | 0.29097 |  | 8922 | 149 | 1 | Limebank | 27.6/16kV | 7F4 | Circuit Auto/Reclose. One phase out of three blown at switch S18742 @ 3150 Rideau Rd, 24/7 opened the remaining two fuses, leaving one customer off. Inspection revealed bird contact on Hydro Ottawa metering unit. | Gloucester | Foreign Interference | Bird
16791 | 2010 | 8 | 21 | 0.53681 |  | 47 | 1 | 1 | Limebank | 27.6/16kV | 7F4 | S29617 at 5151 Albion Rd opened, no apparent cause. 24/7 refused S29617 and fuse is holding load. | Gloucester | Unknown/Other
18990 | 2011 | 8 | 21 | 0.57569 |  | 116 | 31 | 16 | Limebank | 27.6/16kV | 7F4 | Tree in primary at 5480 Downy Rd causing the fuse to blow at O/H transformer 4277 and G605B | Gloucester | Tree Contacts | Inadequate Trimming
19007 | 2011 | 8 | 24 | 0.63889 |  | 40 | 7 | 11 | Limebank | 27.6/16kV | 7F4 | Transformer #4102 located at 5261 Driscoll Dr opened by crew to replace broken cutout and arrestor | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
5727 | 2004 | 8 | 26 | 0.46181 |  | 288 | 53 | 11 | Limebank | 27.6/16kV | 7F4 | TE 3084 at 682 Wildshore Cres in South Urban area to move transformer 1 meter closer to sidewalk. | Gloucester | Scheduled Outage | Construction
19029 | 2011 | 8 | 28 | 0.49514 |  | 57 | 6 | 6 | Limebank | 27.6/16kV | 7F4 | Transformer #4975 located at 5447 North opened by crew to replace switch and arrestor | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
3973 | 2003 | 8 | 29 | 0.80347 |  | 403 | 54 | 8 | Limebank | 27.6/16kV | 7F4 | The crews had to replace the transformer and the cut out. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7252 | 2005 | 8 | 31 | 0.54861 |  | 50 | 1 | 1 | Limebank | 27.6/16kV | 7F4 | Transformer at 965 River Rd was found open due to bird contact refused the switch restored power | Gloucester | Foreign Interference | Bird
11277 | 2007 | 9 | 9 | 0.38333 |  | 13 | 1 | 5 | Limebank | 27.6/16kV | 7F4 | Overhead transformer 13372 on Riveside Cres. Had the barrell of the cutout burning and sparking, required replacement. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
11287 | 2007 | 9 | 11 | 0.36806 |  | 62 | 51 | 49 | Limebank | 27.6/16kV | 7F4 | A broken insulator a few spans north of G30 on Bowesville caused fuse to blow at switch. G30 was opened to isolate for repairs and customers were restored. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4079 | 2003 | 9 | 17 | 0.61806 |  | 70 | 2 | 2 | Limebank | 27.6/16kV | 7f4 | Transformer was opened to string on a new circuit | Gloucester | Scheduled Outage | Construction
15125 | 2009 | 9 | 18 | 0.59375 |  | 119 | 99 | 50 | Limebank | 27.6/16kV | 7F4 | Animal contact caused a transformer fuse to blow, an arrester and the line switch to blow. Transformer switch and arrester replaced. G30R closed to restore power. | Ottawa | Foreign Interference | Animal
4098 | 2003 | 9 | 19 | 0.57847 |  | 112 | 452 | 242 | Limebank | 27.6/16kV | 7F4 | A downed wired caused G2BØ fuse, on River Road at Spratt Road, to rupture. The wire was repaired and the power was restored. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
7370 | 2005 | 9 | 23 | 0.62153 |  | 101 | 145 | 86 | Limebank | 27.6/16kV | 7F4 | Switch G733W found blown, O/H patrolled, no apparent cause found, refused and closed. | Gloucester | Unknown/Other
15156 | 2009 | 9 | 23 | 0.69167 |  | 69 | 1 | 1 | Limebank | 27.6/16kV | 7F4 | Transformer #X14312 located at 4623 Spratt Rd isolated, cause unknown | Gloucester | Unknown/Other | No Apparent Cause
15172 | 2009 | 9 | 26 | 0.86042 |  | 111 | 2 | 1 | limebank | 27.6/16kV | 7F4 | G53 on spratt rd. burnt up, interrupting customer at 4623 Spratt. Crew refused and closed. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
15178 | 2009 | 9 | 27 | 0.58333 |  | 516 | 17 | 2 | Limebank | 27.6/16kV | 7F4 | At 14:00pm transformer X1387 feeding 2 customers at 4915 Limebank Rd failed. On Call crew replaced defective transformer and power was restored at 22:36pm. Limebank 7F4 ID# 15178 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17004 | 2010 | 9 | 27 | 0.38542 |  | 125 | 6 | 3 | LIMEBANK MS | 27.6/16kV | 7F4 | Transformers X13204 & X13206 at 415 Nicolls Island Rd isolated to cut in an opener on the line. | Gloucester | Scheduled Outage | Construction
9356 | 2006 | 10 | 2 | 0.44097 |  | 30 | 1 | 2 | Limebank | 27.6/16kV | 7F4 | Transformer #GL005687 located at 442 Rideau Rd (GR2) isolated for Insulator changes. PC10A#4730 | Gloucester | Scheduled Outage | Preventive Maintenance
9373 | 2006 | 10 | 4 | 0.38889 |  | 20 | 2 | 5 | Limebank | 27.6/16kV | 7F4 | Transformer #T1572 located at 964 River Rd S isolated to re-insulate. PC10A #124 | Gloucester | Scheduled Outage | Repair
17075 | 2010 | 10 | 7 | 0.48333 |  | 70 | 213 | 1076 | Limebank | 27.6/16kV | 7F4 | 7F4 cct. a/r/a/r/trip. Crane contact east of S10711. Electrical contact as well. Circuit isolated and all power restored. | Gloucester | Foreign Interference | Foreign Object
13353 | 2008 | 10 | 10 | 0.43264 |  | 224 | 19 | 5 | Limebank | 27.6/16kV | 7F4 | Contracror pulled secondary services out of transformer @ 160 Winnards Perch. Transformer #TP2490 was replaced and all power restored to customers. | Gloucester | Foreign Interference | Dig-in
11502 | 2007 | 10 | 12 | 0.38958 |  | 94 | 33 | 21 | Limebank | 27.6/16kV | 7F4 | Squirrel contact at Tx 1309, 5335 Bowesville rd caused the cut-out to open & also caused the local, G987R to open. | Gloucester | Foreign Interference | Animal
4260 | 2003 | 10 | 15 | 0.23611 |  | 33 | 28 | 50 | Limebank | 27.6/16kV | 7F4 | Defective insulator caused pole to catch on fire. Customers were interrupted, by opening G30R, to replace defective insulator. | Gloucester | Adverse Environment | Fire
11521 | 2007 | 10 | 15 | 0.50347 |  | 5 | 4 | 45 | Limebank | 27.6/16kV | 7F4 | Tree limb on the overhead required white phase lateral be isolated from Rideau feeding south on Albion to remove the limb | Gloucester | Tree Contacts | Tree Limb Fallen
9467 | 2006 | 10 | 19 | 0.39583 |  | 25 | 1 | 3 | Limebank | 27.6/16kV | 7F4 | Transformer #GL005071 located at 950 River isolated for re-insulating. PC10A #122 | Gloucester | Scheduled Outage | Preventive Maintenance
17154 | 2010 | 10 | 21 | 0.53542 |  | 71 | 41 | 35 | Limebank | 27.6/16kV | 7F4 | RX2016 auto-reclosed once with a white phase fault target. Momentary interruption to Gloucester south area of Albion Rd, Rideau Rd & Manotick. G713R was found blown, interrupting power to 35 customers on Riverside Cres & North Riverside Dr in Manotick. Circuit patrol did not reveal a cause, G713R re-fused successfully. 7F4 load was on 7F2 due to line work on Limebank Rd under Job #1360. | Gloucester | Unknown/Other
13468 | 2008 | 10 | 29 | 0.11944 |  | 63 | 1171 | 1115 | LIMEBANK | 27.6/16kV | 7F4 | Line patrolled from station to corner of Limebank & Rideau, cct closed & holding | Gloucester | Adverse Weather
9558 | 2006 | 10 | 30 | 0.40625 |  | 127 | 15 | 7 | Limebank | 27.6/16kV | 7F4 | G207W located near River Rd / Nichol Island was isolated to replace primary conductor. PC10A #119 | Gloucester | Scheduled Outage | Preventive Maintenance
9619 | 2006 | 11 | 7 | 0.41667 |  | 165 | 14 | 5 | Limebank | 27.6/16kV | 7F4 | Bruce Kerfoot had Transformer # 3567 at 1963 Ridea Rd open to install a new pole | Ottawa | Scheduled Outage | Preventive Maintenance
13585 | 2008 | 11 | 9 | 0.92361 |  | 40 | 13 | 19 | Limebank | 27.6/16kV | 7F4 | PC10A# 2723 established on S21533 affecting 19 customers on Hillcrest and Driscoll. Crew replacing burning up hot line clamp at 5283 Hillcrest. | Gloucester | Defective Equipment
9694 | 2006 | 11 | 21 | 0.42708 |  | 75 | 19 | 15 | Limebank | 27.6/16kV | 7F4 | Transformer #GL005867 located at 1145 Jean Park isolated due to crew replaced secondary lead & changed the porcelain | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15408 | 2009 | 11 | 21 | 0.89653 |  | 62 | 46 | 68 | Limebank | 27.6/16kV | 7F4 | S677W fuse blown due to animal contact at transformer 4101 on McClean Cres. Switch S677W refused and closed, transformer 4101 refused and closed. | Gloucester | Foreign Interference | Animal
5917 | 2004 | 11 | 23 | 0.55972 |  | 95 | 27 | 17 | Limebank | 27.6/16kV | 7F4 | Fuse Blown at S49B due to defective switch at S661. | Gloucester | Defective Equipment
9717 | 2006 | 11 | 23 | 0.81181 |  | 191 | 6 | 2 | Limebank | 27.6/16kV | 7F4 | Transformer #GL000091 located at 5278 Limebank isolated-cut out was open, cause unknown | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17348 | 2010 | 11 | 27 | 0.33681 |  | 171 | 6 | 2 | Limebank | 27.6/16kV | 7F4 | PC10A# 3542, established on G574R to isolate oh on River rd to allow crews to perform insulator replacement. | Gloucester | Scheduled Outage | Preventive Maintenance
11781 | 2007 | 11 | 28 | 0.41667 |  | 45 | 1 | 1 | LIMEBANK | 27.6/16kV | 7F4 | TRANSFORMER #G327 LOCATED ON ALBION RD AT RIDEAU CARLETON SLOTS TO ALLOW FOR TRANSFER OF PLANT DUE TO BROKEN POLE | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13681 | 2008 | 11 | 29 | 0.42361 |  | 30 | 4 | 7 | Limebank | 27.6/16kV | 7F4 | Isolated transformer X16083 to replace primary pole mount insulators | Gloucester | Scheduled Outage | Preventive Maintenance
15451 | 2009 | 12 | 1 | 0.45556 |  | 367 | 184 | 30 | Limebank | 27.6/16kV | 7F4 | At 10:56 crews isolated transformers TP3708,TP4921 and TP3707 near Earl Armstrong and Spratt, for working clearance to pull cables. | Gloucester | Scheduled Outage | Construction
4546 | 2003 | 12 | 2 | 0.73472 |  | 142 | 355 | 150 | Limebank | 27.6/16kV | 7F4 | Red phase stirrup burnt of due to loose hot line clamp @ G718. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
11806 | 2007 | 12 | 4 | 0.5625 |  | 40 | 1 | 2 | Limebank | 27.6/16kV | 7F4 | Transformer #2765 located at 4690 Albion isolated to re-arrange plant | Gloucester | Scheduled Outage | Preventive Maintenance
17433 | 2010 | 12 | 19 | 0.38194 |  | 310 | 15 | 6 | Limebank | 27.6/16kV | 7F4 | Broken pole, hit by city snow plow on High rd N. Of Earl Armstrong caused G823B to open. Dead end run-off N. Of Earl Armstrong cut clear to restore most customers, on call crew called in to complete repairs. | Gloucester | Foreign Interference | Vehicle
15554 | 2009 | 12 | 26 | 0.63542 |  | 75 | 19 | 15 | Limebank | 27.6/16kV | 7F4 | Tree fell on the O/H on Downey Rd, which cause switch G605 to open. | Gloucester | Adverse Weather | Rain
12774 | 2008 | 7 | 1 | 0.58611 |  | 248 | 62 | 15 | LIMEBANK | 27.6/16kV | 7F4(GR2) | A defective transformer 5867 @ 5333 McLean. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17554 | 2011 | 2 | 5 | 0.55278 |  | 45 | 60 | 80 | Manotick | 8/4.8kV | 81F2 | blown 115kV insulator on the power fuse holder caused brown outs to all customers fed from Manotick DS. Hydro One crews dumped the station load to make repairs. Power restored from an alternate source. | Nepean | Loss of Supply | HEPC Station Fault
17557 | 2011 | 2 | 5 | 0.81597 |  | 12 | 12 | 59 | Manotick | 8/4.8kV | 81F2 | Power outage to customers to restore customers to nornal Hydro One supply after Manotick DS outage. | Nepean | Scheduled Outage | Repair
14136 | 2009 | 4 | 2 | 0.56944 |  | 13 | 0 | 2 | Manotick DS | 8/4.8kV | 81F2 | Transformer #X39732 located at 4314 Rideau Valley Dr isolated for Meter Dept to change some meters | Nepean | Scheduled Outage | Preventive Maintenance
6635 | 2005 | 6 | 1 | 0.76458 |  | 214 | 54 | 15 | Manotick DS | 8/4.8kV | 81F2 | Termination on the Blue phase switch S11014 brunt off. 24/7 transferred Blue phase transformers to Red phase at PP2036. On Lockmaster St. in Manotick. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14769 | 2009 | 7 | 17 | 0.55208 |  | 45 | 2 | 2 | Manotick | 8/4.8kV | 81F2 | At 13:15 trans at 4306 RIDEAU VALLEY DR NEPEAN was isolated for service upgrade | Nepean | Scheduled Outage | Preventive Maintenance
12901 | 2008 | 7 | 20 | 0.13264 |  | 247 | 11 | 6 | Manotick | 8/4.8kV | 81F2 | Tree contact with 81F2 on Rideau Valley Rd caused one phase of S80 to blow. Oncall crew opened remaining 2 phases to establish isolation at S80 & remove tree under PC10A. | Nepean | Tree Contacts | Tree Fallen
18940 | 2011 | 8 | 16 | 0.39583 |  | 302 | 272 | 54 | Manotick | 8/4.8kV | 81F2 | All customers on Lockmaster Cresent in Manotick were isolated to allow crews to perform a voltage conversion. | Nepean | Scheduled Outage | Construction
17442 | 2010 | 12 | 21 | 0.46875 |  | 207 | 17 | 5 | Manotick | 8/4.8kV | 81F2 | At 11:15 transformer X4480 at 4383 Prince of Wales was isolated to allow crew to upgrade service. | Gloucester | Scheduled Outage
17454 | 2010 | 12 | 28 | 0.29861 |  | 80 | 80 | 60 | Manotick | 8/4.8kV | 81F2 | Manotick 81F2 circuit breaker locked out. Hydro One Todd Findley reports Hydro One crew has been dispatched. 24/7 crew dispatched to check Hydro Ottawa section of overhead. Nick report our section section of overhead checks ok. Nick also reports Manotick reclosers are all on single shot! Hydro One reports breaker is now closed restoring lost load @ 08:30 | Nepean | Loss of Supply | HEPC Circuit Fault
17460 | 2010 | 12 | 30 | 0.36458 |  | 245 | 12 | 3 | Manotick | 8/4.8kV | 81F2 | At 08:45 transformer X4480 at 369 Bankfield was isolated to allow crew to reconfigure plant for tranfer customers. | Nepean | Scheduled Outage
18157 | 2011 | 5 | 15 | 0.22083 |  | 212 | 226 | 64 | Manotick | 8/4.8kV | 81F2 & F5 | Hydro 1 feeders out of Manotick DS 81F2 and 81F5 were interupted to allow for isolation of the overhead for defective corrections, affecting Hydro Ottawa transfer customers | Nepean | Scheduled Outage | Repair
15610 | 2010 | 1 | 5 | 0.425 |  | 128 | 11 | 5 | Manotick | 8/4.8kV | 81F5 | Radial line on Cedarview north of Bankfield isolated at TEMP96 for crews to rebuild pole line. | Nepean | Scheduled Outage | Preventive Maintenance
15656 | 2010 | 1 | 15 | 0.20694 |  | 390 | 6 | 1 | Manotick | 8/4.8kV | 81F5 | Transformer fuse at 39620 found blown at 4134 Cedarview Road. Defective transformer replaced and power restored. | Nepean | Defective Equipment
17556 | 2011 | 2 | 5 | 0.55278 |  | 284 | 38 | 8 | Manotick | 8/4.8kV | 81F5 | blown 115kV insulator on the power fuse holder caused brown outs to all customers fed from Manotick DS. Hydro One crews dumped the station load to make repairs. Customers out of power for the duration of the station outage. | Nepean | Loss of Supply | HEPC Station Fault
14744 | 2009 | 7 | 14 | 0.42569 |  | 122 | 12 | 6 | Manotick | 8/4.8kV | 81F5 | Hydro Ottawa tree contractor dropped a tree on the the primary neutral @ 4134 Cederview. Hydro Ottawa owned single phase local fed from H1 circuit 81F5. Refused and closed at our fuse S204. | Gloucester | Tree Contacts | Tree Limb Fallen
11138 | 2007 | 8 | 23 | 0.76597 |  | 57 | 4 | 6 | Manotick DS | 8/4.8kV | 81F5 | Tree contact on customer owned line fed from S1796 caused both S1796 & S204 fuses to blow, both were fused at 40 amps. S204 was refused with a 40 amp fuse & S1796 was replaced with a 30 amp fuse. Area affected Cedarview between Barnsdale & Bankfield. | Gloucester | Tree Contacts | Tree Limb Fallen
13289 | 2008 | 9 | 25 | 0.4375 |  | 75 | 25 | 20 | Manotic | 8/4.8kV | 81F5 | A car hit the guy wire on Cederview at Barnsdale and broke the top of the pole, a temp switch was cut in to restore power. | Nepean | Foreign Interference | Vehicle
13366 | 2008 | 10 | 14 | 0.73958 |  | 529 | 62 | 7 | Manotick DS (Hydro One) | 8/4.8kV | 81F5 | Broken pole at 3285 Eagleson rd caused fuse to blow at S257. B Seaman issued PC10A# 4535 on S257 replaces pole and refused switch to pick up all 7 customers. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13608 | 2008 | 11 | 14 | 0.42222 |  | 47 | 5 | 6 | Manotick | 8/4.8kV | 81F5 | PC10A# 4179 established by S Driscol to allow crew to dead end circuit at Temp53 on Cedarview. | Nepean | Scheduled Outage
15397 | 2009 | 11 | 17 | 0.37153 |  | 203 | 17 | 5 | Manotick | 8/4.8kV | 81F5 | 5 customers on Cedarview between Barnsdale & Bankfield were interrupted for Hydro Ottawa crews to replace poles & conductor. | Nepean | Scheduled Outage | Preventive Maintenance
5908 | 2004 | 11 | 20 | 0.61389 |  | 256 | 4 | 1 | Manotick (H-1) | 8/4.8kV | 81F5 | On call crew replaced broken switch supplying 4282 Cedarview | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15413 | 2009 | 11 | 23 | 0.41806 |  | 138 | 12 | 5 | Manotick | 8/4.8kV | 81F5 | A section of O/H line on Bankfield Rd was isolated to allow the crew to rearrange plant. | Gloucester | Scheduled Outage | Construction
15442 | 2009 | 11 | 30 | 0.42361 |  | 205 | 20 | 6 | Manotick | 8/4.8kV | 81F5 | A section of primary line from temp 96 to EOL on Cedarview N. of Bankfield was isolated to allow crews to string new conductor. | Nepean | Scheduled Outage | Construction
15461 | 2009 | 12 | 3 | 0.22639 |  | 95 | 10 | 6 | Manotik DS | 8/4.8kV | 81F5 | Customers reported no power on Cedarview and S204 single phase was found open, no apparent cause was found. 6 Customers affect and power restored at 7:01am with S204 closed back in. | Gloucester | Unknown/Other | No Apparent Cause
6344 | 2005 | 3 | 31 | 0.9375 |  | 184 | 6 | 2 |  | 8/4.8kV | 84F1 | Bad cable between Pedestal and Transformer 139. Crew ran temp services to 15 and 17 Keppler. Email sent to Pete Donnelly to make permanent repairs. | Nepean | Defective Equipment
6354 | 2005 | 4 | 2 | 0.8125 |  | 343 | 57 | 10 | Manordale | 8/4.8kV | 84F1 | The fuse at Transformer TE254 @ 9 Jansen blew because it was under water. | Nepean | Adverse Weather | Rain
6389 | 2005 | 4 | 8 | 0.38056 |  | 545 | 91 | 10 | Manordale | 8/4.8kV | 84F1 | Isolate transformer TE712 at 5 Bentworth to clean up oil spill. | Nepean | Scheduled Outage | Repair
20517 | 2012 | 5 | 15 | 0.40486 |  | 267 | 9 | 2 | Manordale | 8/4.8kV | 84F1 | VE62 at 245 Greenbank was isolated to allow crews to work in the sectionalizer, replace the overhead switches and allow a contractor to clean the vault. | Nepean | Scheduled Outage | Preventive Maintenance
18219 | 2011 | 5 | 25 | 0.625 |  | 66 | 88 | 80 | Manordale | 8/4.8kV | 84F1 | An elbow at transformer TE712 to TE711 @ 76 CRAIG HENRY DR had a defective elbow. The circuit was abnormal because the O/H section between S1369 and S207 & to include dip switches S1149 & S1368 out of centrepointe DS was being isolated | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18883 | 2011 | 8 | 5 | 0.80069 |  | 376 | 150 | 40 | Manordale | 8/4.8kV | 84F1 | A defective cable bet transformer TE1355 and TE1354 and broken insert at TE1355(232 Accolade Pvt) | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
19001 | 2011 | 8 | 23 | 0.38125 |  | 441 | 66 | 9 | Manordale | 8/4.8kV | 84F1 | TE1355 at 30 Ardell changeout for upgrade to new transformer and new splices | Nepean | Scheduled Outage
5762 | 2004 | 9 | 2 | 0.40625 |  | 353 | 88 | 15 | Manordale | 8/4.8kV | 84F1 | Isolation of TE721W at 62 Elvaston to clean up oil spill. | Ottawa | Scheduled Outage | Repair
13371 | 2008 | 10 | 15 | 0.40208 |  | 415 | 83 | 12 | Manordale | 8/4.8kV | 84F1 | TE708 isolated to replace base, transformer and grounding, at 46 Shoreham Dr Craig Henry. . | Nepean | Scheduled Outage | Preventive Maintenance
13393 | 2008 | 10 | 20 | 0.39097 |  | 52 | 13 | 15 | Manordale | 8/4.8kV | 84F1 | TE707 was isolated to replace a defective insert on the elbow. 15 custmers. | Nepean | Scheduled Outage | Repair
17196 | 2010 | 10 | 30 | 0.97708 |  | 128 | 785 | 368 | Manordale | 8/4.8kV | 84F1 | Tree fell on the O/H behind 54 Elveston. | Nepean | Tree Contacts | Tree Fallen
7766 | 2005 | 12 | 29 | 0.40556 |  | 183 | 98 | 244 | Manordale | 8/4.8kV | 84F1 | 24/7 report cable section between TE803B and TE804B has been isolated. Elbow blown off transformer also arrester blown on overhead. | Nepean | Defective Equipment
19913 | 2012 | 1 | 28 | 0.65694 |  | 60 | 5 | 5 | Manordale | 8/4.8kV | 84F2 | Transformer X39707 at 7 Headingly Cres. isolated to repair open wire span (secondary) | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19914 | 2012 | 1 | 28 | 0.6875 |  | 47 | 7 | 9 | Manordale | 8/4.8kV | 84F2 | Transformer NP002053 at 9 Headingly Cres. isolated to repair open wire span (secondary) | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4747 | 2004 | 1 | 30 | 0.33125 |  | 213 | 43 | 12 | Manordale | 8/4.8kV | 84F2 | Transformer 4212 at 40 Millford replaced due to defective transformer | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12040 | 2008 | 2 | 13 | 0.55139 |  | 66 | 44 | 40 | Manordale | 8/4.8kV | 84F2 | Squirrell contact caused fuse to open S411 at 108 Knoxdale, no apparent damage at the flashover sight, S411 refused and restored. | Nepean | Foreign Interference | Animal
6258 | 2005 | 3 | 10 | 0.45833 |  | 50 | 7 | 8 | Manordale | 8/4.8kV | 84F2 | Trans #NP001671 interrupted to change lead in the transformer at Roundhay & Knoxdale | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10113 | 2007 | 3 | 12 | 0.45833 |  | 25 | 2 | 4 | Manordale | 8/4.8kV | 84F2 | Isolated transformer 2052 at the rear of 15 Headingly Cres to replace secondary connections | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12193 | 2008 | 3 | 28 | 0.59236 |  | 52 | 7 | 8 | Manordale | 8/4.8kV | 84F2 | Tx 1671 at 9 Roundhay cutout brown due to squirrel contact. Cut out replaced power restored. | Nepean | Foreign Interference | Animal
17793 | 2011 | 3 | 28 | 0.54861 |  | 230 | 4 | 1 | Manordale | 8/4.8kV | 84F2 | Trans #577 at 55 Dunbar Crt was replaced after being damaged due to a pole fire | Nepean | Adverse Environment | Fire
8096 | 2006 | 4 | 2 | 0.92986 |  | 226 | 188 | 50 | Manordale | 8/4.8kV | 84F2 | S1355 Blue phase broken on Knoxdale at Conover. At first switch did not appear to be broken until they went to operate it. | Nepean | Defective Equipment
5283 | 2004 | 6 | 11 | 0.42431 |  | 53 | 7 | 8 | Manordale | 8/4.8kV | 84F2 | Transformer NP001205 at 8 Newark St out due to bird contact. | Nepean | Foreign Interference | Animal
12792 | 2008 | 7 | 4 | 0.76528 |  | 63 | 210 | 200 | Manordale | 8/4.8kV | 84F2 | Customer phoned in & sent pictures of pole X2712 on knoxdale which has a large burn hole in upper part of pole. Crew sent out to isolate S1355RWB (pole X2712) & temporarily fix pole until permanent fix can be made. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
3829 | 2003 | 8 | 1 | 0.97014 |  | 42 | 7 | 10 | Manordale | 8/4.8kV | 84F2 | Overhead transformer 3554 at 21 Kelvin isolated to repair arcing secondary wires. Insulation had broken down and secondary wire was arcing to neutral. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
3830 | 2003 | 8 | 1 | 0.99097 |  | 12 | 2 | 10 | Manordale | 8/4.8kV | 84F2 | Tx NP3554 at the rear of 21 Kelvin cr was opened to repair a defective secondary service. 10 customers from 11 to 29 Kelvin ( odd #'s only ) were affected. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16662 | 2010 | 8 | 4 | 0.65694 |  | 7 | 51 | 437 | Manordale | 8/4.8kV | 84F2 | 84F2 tripped under hold off, crew was cleared & breaker closed maunually from SCADA. | Nepean | Unknown/Other
11144 | 2007 | 8 | 24 | 0.29583 |  | 20 | 37 | 112 | Manordale | 8/4.8kV | 84F2 | S411 single phase overhead run off fused switch on Knoxdale Rd and Newhaven opened during thunderstorm. No apparent cause found. Switch refused and closed to restore. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7283 | 2005 | 9 | 6 | 0.37847 |  | 260 | 217 | 50 | Manordale | 8/4.8kV | 84F2 | Planned outage to replace crossarm at switch S83 Merivale at Gervin | Nepean | Scheduled Outage | Repair
19380 | 2011 | 10 | 15 | 0.75347 |  | 32 | 21 | 40 | Manordale DS | 8/4.8kV | 84F2 | A broken lead at S411 Red phase caused an outage to 6 O/H transformers and 40 customers. 24/7 crew repaired the broken lead and restored power to all customers. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13554 | 2008 | 11 | 3 | 0.94722 |  | 31 | 5 | 9 | Manordale | 8/4.8kV | 84F2 | Transformer X39703 at rear of 9 Newark st was opened to replace burning hot line clamp. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
19624 | 2011 | 11 | 23 | 0.55556 |  | 45 | 7 | 9 | Manordale | 8/4.8kV | 84F2 | At 13:20 crews isolated transformer X39703 @ 9 Newark to upragde a service. 9 customers affected for 45 mins. Manordale 84F2 ID# 19624 | Nepean | Scheduled Outage
12011 | 2008 | 2 | 6 | 0.40972 |  | 70 | 19 | 56 | Manordale | 8/4.8kV | 84F3 | Transformer TE620 was isolated to replace primary insulator and fibre board. 6 transformers also interrupted for isolation due to TE620 being a live front transformer. | Nepean | Scheduled Outage | Repair
19973 | 2012 | 2 | 7 | 0.39028 |  | 45 | 3 | 4 | Manordale | 8/4.8kV | 84F3 | Replaced broken fuse feeding transformer X36699 at 50 Bellman Dr | Nepean | Defective Equipment | Equipment Deterioration Due to Age
8035 | 2006 | 3 | 15 | 0.64583 |  | 5 | 1 | 7 | Manordale | 8/4.8kV | 84F3 | Transformer #TE222 located at 52 Cramer Dr isolated to pull the lead out of the panel to make repairs | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8153 | 2006 | 4 | 14 | 0.36458 |  | 215 | 54 | 15 | Manordale | 8/4.8kV | 84F3 | Isolated and replaced transformer TE318 at the rear of 79 Hobart Cres due to oil leak | Nepean | Defective Equipment | Equipment Deterioration Due to Age
8343 | 2006 | 5 | 24 | 0.375 |  | 600 | 160 | 16 | Manordale | 8/4.8kV | 84F3 | Isolated TE318 @ 79 Hobart to replace leaking transformer and remove contamineted soil. | Nepean | Scheduled Outage | Repair
8827 | 2006 | 7 | 25 | 0.38472 |  | 8 | 2 | 12 | Manordale | 8/4.8kV | 84F3 | Transformer TE786 on Glencoe Ave isolated to replace defective insert. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11102 | 2007 | 8 | 20 | 0.41389 |  | 114 | 19 | 10 | Manordale | 8/4.8kV | 84F3 | TP4141 at 15 Dexter was replaced due to an oil leak. | Nepean | Scheduled Outage | Repair
9020 | 2006 | 8 | 22 | 0.39583 |  | 320 | 53 | 10 | Manordale | 8/4.8kV | 84F3 | Transformer replacement at 15 Dexter Dr, new TP4141 installed replacing TE231. | Nepean | Scheduled Outage | Preventive Maintenance
9025 | 2006 | 8 | 22 | 0.375 |  | 360 | 60 | 10 | Manordale | 8/4.8kV | 84F3 | At 09:00 trans TE231 at 15 Dexter Dr was isolated in order to change over plant | Nepean | Scheduled Outage | Preventive Maintenance
9091 | 2006 | 8 | 30 | 0.38681 |  | 70 | 12 | 10 | Manordale | 8/4.8kV | 84F3 | Transformer TE630 at 8 Camwood Cr isolated to complete directional boring for cable replacement. | Nepean | Scheduled Outage | Construction
9228 | 2006 | 9 | 15 | 0.61458 |  | 33 | 8 | 14 | Manordale | 8/4.8kV | 84F3 | Transformer #225 located at 141 Mcclellan Rd isolated to do splicing | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5840 | 2004 | 9 | 19 | 0.58889 |  | 22 | 2 | 5 | Manordale | 8/4.8kV | 84F3 | Disconnect faulted service. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
9256 | 2006 | 9 | 20 | 0.41806 |  | 287 | 48 | 10 | MANORDALE | 8/4.8kV | 84F3 | Scheduled outage for TE647 in Arlington Woods to replace transformer. | Nepean | Scheduled Outage
9272 | 2006 | 9 | 21 | 0.39375 |  | 335 | 45 | 8 | Manordale | 8/4.8kV | 84F3 | TE646 on 84F3 isolated to change transformer and base. | Nepean | Scheduled Outage | Construction
9319 | 2006 | 9 | 26 | 0.39097 |  | 357 | 119 | 20 | Manordale | 8/4.8kV | 84F3 | Manordale cable replacement. TE646 and TE644. | Nepean | Scheduled Outage | Construction
7392 | 2005 | 9 | 28 | 0.39514 |  | 471 | 63 | 8 | Manodale | 8/4.8kV | 84F3 | Transformer #254 is now replaced. Transformer upgrade to dead front. | Nepean | Scheduled Outage | Preventive Maintenance
7422 | 2005 | 10 | 3 | 0.40972 |  | 526 | 175 | 20 | Manordale | 8/4.8kV | 84F3 | Transformer TE237 on Grady Cr isolated for replacement. | Nepean | Scheduled Outage | Construction
11533 | 2007 | 10 | 16 | 0.57222 |  | 41 | 12 | 18 | Manordale | 8/4.8kV | 84F3 | Transformer #TE449 located at 28 Parkland Cres isolated due to make repairs to defective connector | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11844 | 2007 | 12 | 13 | 0.56319 |  | 74 | 18 | 44 | Manordale | 8/4.8kV | 84F3 | Isolated transformer TE447 @ 60 Parkland Cr to fix heating connections, switch S884 B phase was open because the 3 other transformer are live front and cannot be operated. | Nepean | Scheduled Outage | Repair
12283 | 2008 | 4 | 15 | 0.036806 |  | 147 | 49 | 20 | Manordale | 8/4.8kV | 84F4 | TP3940 at 33-21 Midland isolated for Oncall crew to repair defective secondary cables. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14386 | 2009 | 5 | 21 | 0.39583 |  | 45 | 10 | 13 | Manordale | 13.2kV | 84F4 | At 09:30 trans at 18 Midland was isolated in order to replace a sec ped | Nepean | Scheduled Outage | Repair
14604 | 2009 | 6 | 24 | 0.39028 |  | 493 | 68 | 21 | Manordale | 8/4.8kV | 84F4 | Changing PCB Tx & primary cable work at TP5512 at 243 McClellan. Short outage to TE455 due to live front Tx's. | Nepean | Scheduled Outage | Preventive Maintenance
9080 | 2006 | 8 | 28 | 0.38264 |  | 351 | 47 | 8 | Manordale | 8/4.8kV | 84F4 | TE630 in Arlington Woods isolated to allow contractor to directional bore. | Nepean | Scheduled Outage | Construction
9301 | 2006 | 9 | 25 | 0.39444 |  | 262 | 74 | 17 | Manordale | 8/4.8kV | 84F4 | Transformer TE645B at 21 Midland Crt was isolated to allow the crew to replace the transformer. | Nepean | Scheduled Outage | Preventive Maintenance
7442 | 2005 | 10 | 10 | 0.71181 |  | 42 | 35 | 50 | Rideau Heights | 8/4.8kV | 84F4 | A defective fuse at switch 934 white phase, replace fuse and holding. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
13522 | 2008 | 10 | 28 | 0.87778 |  | 831 | 14 | 1 | MANORDALE | 8/4.8kV | 84F4 | NRC OUTAGE | Nepean | Adverse Weather
13529 | 2008 | 10 | 28 | 0.95833 |  | 715 | 12 | 1 | MANORDALE | 8/4.8kV | 84F4 | PHASES OF OVERHEAD LINE SECTTION INTO NRC AT S90 AT GREEN BANK ROAD WERE MAKING CONTACT CAUSING THE CIRCUIT TO AUTO RECLOSE, LINE SECTION WAS ISOLATED TO RETENTION CONDUCTOR | Nepean | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
9556 | 2006 | 10 | 30 | 0.40625 |  | 301 | 50 | 10 | Manordale | 8/4.8kV | 84F4 | Isolated transformer TP3955 @ 5 Moss Ct for transformer replacement. | Nepean | Scheduled Outage | Preventive Maintenance
9577 | 2006 | 11 | 1 | 0.39861 |  | 398 | 133 | 20 | Manordale | 8/4.8kV | 84F4 | Transformer and base replacement of TE637 and TE638 to new TP3956 and TP3957. | Nepean | Scheduled Outage | Preventive Maintenance
4849 | 2004 | 3 | 2 | 0.6 |  | 306 | 51 | 10 | Manordale |  | 84F5 | TE254 flooded causing the secondary fuse to blow transformer had to be pumped out. | Nepean | Adverse Weather | Rain
4860 | 2004 | 3 | 5 | 0.55 |  | 213 | 39 | 11 | Manordale | 8/4.8kV | 84F5 | Auto reclose on feeder TE254 flooded. Water pumped down and transformer placed back on load. | Nepean | Adverse Weather | Rain
8038 | 2006 | 3 | 16 | 0.82639 |  | 33 | 1 | 1 | MANORDALE | 8/4.8kV | 84F5 | FOUND HOT-LINE CLAMP BURNT @ 168-170 GREENBANK, S806 OPENED TO FIX. VE29 INTURPED. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
20202 | 2012 | 3 | 22 | 0.54792 |  | 51 | 5 | 6 | Manordale | 8/4.8kV | 84F5 | Squirrel contact caused overhead transformer X36169 @ 41 Dayton to open. | Nepean | Foreign Interference | Animal
8071 | 2006 | 3 | 28 | 0.59722 |  | 125 | 42 | 20 | Manordale | 8/4.8kV | 84F5 | Leaking Transformer TE942 on Banner Road was replaced. Customers notified 20 minutes prior to isolation. | Nepean | Defective Equipment
5038 | 2004 | 4 | 22 | 0.48611 |  | 45 | 30 | 40 | Manordale | 8/4.8kV | 84F5 | The R phase fuse at switch 966 on Greenbank was not making good contact, tempary repairs were made and will be replaced. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
5039 | 2004 | 4 | 22 | 0.58333 |  | 205 | 137 | 40 | Manordale | 8/4.8kV | 84F5 | A cable fault was detected between transformer TE617 and switch 962 B phase. The cables had to be megered to determined the faults location. Before this happened they also found the switch at 966 R phase on the same circuit also broken, they had make repairs first. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14263 | 2009 | 4 | 30 | 0.45903 |  | 41 | 7 | 10 | Manordale | 8/4.8kV | 84F5 | Isolation of TE57 at 11B Majestic, transformer came off it's pad. | Nepean | Defective Equipment
6578 | 2005 | 5 | 20 | 0.39028 |  | 105 | 612 | 653 | Manodale | 8/4.8kV | 84F5 | Cable section between TE295 & TE296 was dig into by contractor at 7 Moorcroft. | Nepean | Foreign Interference | Dig-in
14437 | 2009 | 6 | 1 | 0.41667 |  | 45 | 10 | 14 | Manordale | 8/4.8kV | 84F5 | Isolated transformer TE0312 at 92 Ashgrove Cres to replace defective Ped | Nepean | Scheduled Outage | Preventive Maintenance
3587 | 2003 | 6 | 21 | 0.84653 |  | 191 | 6 | 2 | Manodale | 8/4.8kV | 84F5 | 2 Customers affected in power outage due to a defective fed to a pedestal fed from TE22. At 9 Parkmount, oncall crew ran a Temp fed to pedestal restoring power. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
18738 | 2011 | 7 | 17 | 0.83333 |  | 1930 | 1351 | 42 | Manordale | 8/4.8kV | 84F5 | S1472 isolated to allow crew to change defective stirrup, on Oakmore. | Nepean | Defective Equipment
7123 | 2005 | 8 | 11 | 0.37847 |  | 312 | 125 | 24 | Manordale | 27.6/16kV | 84F5 | Transformer TP2557installed to replace TE18. And new dip switch S16669 installed. Customers on 2-22 even Canfield and 1-8 Valleyview. | Nepean | Scheduled Outage | Construction
9131 | 2006 | 9 | 7 | 0.38542 |  | 302 | 50 | 10 | Manordale | 8/4.8kV | 84F5 | Transformer TE787 at 12 Bellman in Nepean isolated for replacement. | Nepean | Scheduled Outage | Construction
9223 | 2006 | 9 | 15 | 0.38194 |  | 350 | 315 | 54 | Manordale | 8/4.8kV | 84F5 | Transformer on Bellman,Glencoe area was isolated for transformer and cable replacement. | Nepean | Scheduled Outage | Preventive Maintenance
9240 | 2006 | 9 | 18 | 0.40417 |  | 328 | 82 | 15 | Manordale | 8/4.8kV | 84F5 | Transformer TE627 on Basin Crt in Nepean isolated for cable replacement. | Nepean | Scheduled Outage | Construction
4262 | 2003 | 10 | 15 | 0.40625 |  | 232 | 187 | 60 | Manerdale | 8/4.8kV | 84F5 | Cable fault between TE44 and TE143 on the Red phase. The crew had to sectionalize and high pot the cables between each Transformer to determine where the fault was. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4308 | 2003 | 10 | 21 | 0.054167 |  | 114 | 418 | 220 | Manordale | 8/4.8kV | 84F5 | Cct auto reclosed with no load picked up on blue phase. Found broken switch at station. Load transferred to alternate supply & defective equipment isolated. | Nepean | Adverse Weather | Lightning
11839 | 2007 | 12 | 13 | 0.39653 |  | 51 | 6 | 49 | Manordale | 8/4.8kV | 84F5 | Isolated transformer TE144 @ 19 Lambert Dr to fix heating connections, switch S709 R phase was open because the 5 other transformer are live front and cannot be operated. | Nepean | Scheduled Outage | Repair
11842 | 2007 | 12 | 13 | 0.44792 |  | 63 | 87 | 1165 | Manordale | 8/4.8kV | 84F5 | Isolated transformer TE147 @ 3 Keppler to fix heating connections, switch S707 R phase was open because the 7 other transformer are live front and cannot be operated. When switch S707 R was closed back in it trip the 84F5 circuit, it was under hold off and the cold load pick up trip it. | Nepean | Scheduled Outage | Repair
4715 | 2004 | 1 | 16 | 0.52986 |  | 2 | 27 | 750 | Manordale | 8/4.8kV | 84F6 | While restoring power via 84F6 crews closed into a secondary fault. The 84F6 breaker locked out due to circuit tagged hold off. 750 customers were affected including the Queens Way Carleton Hosp. The auto transfer switch operated at the Hospital restoring it's load on the secondary side, the 84F6 closed via scada restoring load.See Interruption 4707 for more info. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
20160 | 2012 | 3 | 13 | 0.72361 |  | 121 | 692 | 443 | Manordale | 8/4.8kV | 84F6 | Cable fault caused the 84F6 breaker to open and due to underground transformer loop fuse not opening caused the 84F6 breaker to open two more times while trouble shooting. Manordale (84F6) ID#20160 | Nepean | Defective Equipment
14100 | 2009 | 3 | 25 | 0.44444 |  | 105 | 19 | 11 | MANORDALE | 8/4.8kV | 84F6 | Transformer X33189 at rear of #32 Harrison isolated to allow for pcb change | Nepean | Scheduled Outage | Preventive Maintenance
14117 | 2009 | 3 | 30 | 0.44236 |  | 68 | 7 | 6 | Manordale | 8/4.8kV | 84F6 | Transformer #X35240 located at 40 Harrison St isolated due to PCB change | Nepean | Scheduled Outage | Preventive Maintenance
12357 | 2008 | 4 | 28 | 0.89306 |  | 19 | 4 | 13 | Manordale | 8/4.8kV | 84F6 | Incorrect padmount was isolated for repair on smoking pedestal at 2 Ashgrove. Records indicate pedestal feeding 2 Ashgrove is fed from TE381 but on/call crew reports otherwise. Day crew to invistigate source of pedestal and repair as neccesary. | Nepean | Human Element | Incorrect Records
6491 | 2005 | 5 | 2 | 0.59028 |  | 362 | 391 | 749 | Manordale | 8/4.8kV | 84F6 | On closeing S850 B phase 84F6 feeder locked out. Suspected cable fault sectionalized and hipotted but nothing found. | Nepean | Unknown/Other | No Apparent Cause
12600 | 2008 | 6 | 11 | 0.39236 |  | 15 | 9 | 35 | Manordale | 8/4.8kV | 84F6 | O/H line fed from S666 was isolated to re-insulate line but job was cancelled because City Traffic could not get generator to run properly. 35 customers on Dayton, Harrison & Lavina were affected. | Nepean | Scheduled Outage | Preventive Maintenance
14535 | 2009 | 6 | 14 | 0.46389 |  | 225 | 221 | 59 | Manordale | 8/4.8kV | 84F6 | a cable fault caused 84F6 CB to auto reclose and S964 to open at the same time. Open point at S791at time of trip. Power restored in stages. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12680 | 2008 | 6 | 17 | 0.41389 |  | 157 | 92 | 35 | Manordale | 8/4.8kV | 84F6 | S666 on Henderson was opened to isolate to end of line under PC10A to replace leaking insulators and revamp some poles. 35 Customers affected, power was restored at 12:33pm. | Nepean | Scheduled Outage | Repair
5469 | 2004 | 7 | 8 | 0.54167 |  | 45 | 4 | 6 | Manordale | 8/4.8kV | 84F6 | Isolate transformer 3930 at the rear of 5 Lavina Crst to change the service. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12864 | 2008 | 7 | 17 | 0.039583 |  | 621 | 666 | 96 | Manordale | 8/4.8kV | 84F6 | A faulted 84F6 blue cable section between TE665 and TE666 on Bainbridge and elvaston caused the fuse at S965 to open. In the Process of fault finding the elbow blew off transformer TE922 @ 43 Wade. Crew had to repair elbow and insert to restore power to all customers. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
5769 | 2004 | 9 | 3 | 0.43264 |  | 97 | 52 | 32 | Manordale | 8/4.8kV | 84F6 | Planned isolation of txs 366, 337 & 374 on Meadowbank Dr in Nepean | Nepean | Scheduled Outage | Construction
4068 | 2003 | 9 | 15 | 0.38681 |  | 406 | 136 | 60 | Manodale | 4.16kV | 84F6 | Scada ind. 84F6 circuit auto reclosed. Queensway Carleton reports bump on system. Circuit to be patrolled. P. Barr reports cable damaged at Pineview Cemetary. Cable repaired all power was restored. | Nepean | Foreign Interference | Dig-in
9350 | 2006 | 9 | 30 | 0.46875 |  | 56 | 9 | 10 | Manordale | 8/4.8kV | 84F6 | Transformer #TE662 located at 101 Craig Henry isolated due to our conductor in meter base of 97 Craig Henry shorted out. Meter was blown off. Transformer was restored but 97 will be isolated until all repairs are made. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4354 | 2003 | 10 | 29 | 0.68889 |  | 391 | 598 | 95 | Manordale | 8/4.8kV | 84F6 | Manordale 84F6 feeder bkr auto/reclose. Fuse at switch 964 found blown, cable fault located and customers restored in sections. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
4355 | 2003 | 10 | 29 | 0.7875 |  | 35 | 36 | 62 | Manordale | 8/4.8kV | 84F6 | Switch 964 Greenbank Rd near Craig Henry opened to attempt restoration of transformers that were off due to cable fault along Craig Henry. When switch closed to attempt restoration fuse opened. Open point was re-established, switch refused and closed to restore customers. | Nepean | Defective Equipment
4357 | 2003 | 10 | 29 | 0.9375 |  | 33 | 34 | 62 | Manordale | 8/4.8kV | 84F6 | Switch 964 Greenbank Rd near Craig Henry opened to attempt restoration of transformers that were off due to cable fault along Craig Henry. When switch closed to attempt restoration the switch broke. Switch was repaired and closed to restore customers. | Nepean | Defective Equipment
4375 | 2003 | 11 | 3 | 0.5625 |  | 39 | 4 | 6 | Manordale | 8/4.8kV | 84F6 | Transformer #5104, at 41 Dayton Crescent in Nepean, was isolated to allow for the removal of a temporary switch. ID#4375 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4383 | 2003 | 11 | 4 | 0.53264 |  | 168 | 41 | 20 | Manordale | 8/4.8kV | 84F6 | 84F6 circuit auto reclosed effecting power to 749 customers. Customers reports power still out at 18 Greenbank. P. Barr reports S762 red phase fuse found open. Smoke & Fire in transformer TE169 at 18 Greenbank. TE169 was isolated, and TE163 & TE201 energized restoring power to 20 customers. P. Barr reports TE169 tests ok & cable section between TE169 & S762 is defective. TE169 energized restoring power to 10 customers. ID#4383 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4487 | 2003 | 11 | 20 | 0.42708 |  | 59 | 8 | 8 | Manordale | 8/4.8kV | 84F6 | Isolate transformer TE667 at 22 Elvaston to repair primary insulator. | Nepean | Scheduled Outage | Repair
11757 | 2007 | 11 | 23 | 0.39722 |  | 1 | 2 | 100 | Manordale | 8/4.8kV | 84F6 | 84F6 red phase load was lost when the recloser was bypassed with a blown fuse for a planned isolation. The recloser was closed manually when load dropped off the 84T2 transformer. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
9741 | 2006 | 11 | 28 | 0.05625 |  | 309 | 103 | 50 | Manordale | 8/4.8kV | 84F6 | A suspected defective transformer TE664 @ 34 Craig Henry, but was a defective cable bet TE665 & TE664. While sectionilizng the 84F6 trip twice. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15466 | 2009 | 12 | 3 | 0.69583 |  | 118 | 20 | 10 | Manordale | 8/4.8kV | 84F6 | Transformer #X36169 located at 41 Dayton isolated due to broken cut out | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
10912 | 2007 | 7 | 19 | 0.25486 |  | 94 | 2895 | 2031 | Manordale | 8/4.8kV | 84T2 | Squirrel got into the B2 bus near the F5 feeder at Manordale causing extensive damage to the Bus and interrupting the 84T2 load. Load was restored using the F2 and F3 feeders. | Nepean | Foreign Interference | Animal
15932 | 2010 | 4 | 13 | 0.47917 |  | 598 | 64 | 12 | King Edward | 600/347 | 852-160 | A defective 600v secondary cable 852-160 in manhole 3786 on King Edward faulted. Crew isolated and repaired cable. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
15644 | 2010 | 1 | 13 | 0.39583 |  | 54 | 6 | 7 | CenterPoint | 8/4.8kV | 87F1 | ttransformer at 23 Howden isolated for tree trimming, PC10# 005100 | Nepean | Scheduled Outage | Preventive Maintenance
15711 | 2010 | 2 | 9 | 0.69306 |  | 72 | 10 | 8 | Centrepointe | 13.2kV | 87F1 | Transformer #X33237 located at 3 Newbury opened due to squirrel contact | Ottawa | Foreign Interference | Animal
10046 | 2007 | 2 | 21 | 0.45694 |  | 102 | 46 | 27 | Centrepoint | 8/4.8kV | 87F1 | The R phase of dip switch S372 broke interrupting 3 transformers on Westpointe Cr and Heminwood Way in Nepean. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16034 | 2010 | 5 | 4 | 0.29167 |  | 35 | 8 | 14 | Centerpoint DS | 8/4.8kV | 87F1 | TE2833 was isolated to allow crews to replace a broken cut out at S524. | Nepean | Scheduled Outage | Repair
14310 | 2009 | 5 | 6 | 0.42222 |  | 29 | 6 | 12 | Centrepointe | 8/4.8kV | 87F1 | TP5322 @ 321 Paseo was isolated to allow contractor to pull secondary cable. Job was suspended when it was discovered there was no duct. | Nepean | Scheduled Outage | Construction
14436 | 2009 | 6 | 1 | 0.40278 |  | 39 | 9 | 14 | Centrepoint | 8/4.8kV | 87F1 | TP5321 @ 290 Paseo Pvt was isolated to install and connect secondary services. | Nepean | Scheduled Outage | Preventive Maintenance
18280 | 2011 | 6 | 2 | 0.375 |  | 66 | 12 | 11 | Centrepointe | 8/4.8kV | 87F1 | Transformer TE2238 @ 17 Strathbury was isolated to allow the crew to check oil level. | Nepean | Scheduled Outage | Preventive Maintenance
10571 | 2007 | 6 | 8 | 0.825 |  | 117 | 85 | 470 | Centrepoint | 8/4.8kV | 87F1 | The Centrpoint 87F4 & 87F7 feeders auto reclosed. 87F1 auto tripped and was closed via SCADA. Connection to switch S31 on Castleton St burnt off of the W phase. Customers transferred and switch isolated. Repairs to be completed later. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14557 | 2009 | 6 | 17 | 0.41736 |  | 276 | 51 | 11 | Centrepoint | 8/4.8kV | 87F1 | Transformer TP5322 was isolated at 321 Paseo Pvt to allow contractor to pull in secondary cables. | Nepean | Scheduled Outage | Construction
10667 | 2007 | 6 | 19 | 0.57431 |  | 37 | 0 | 12 | Centerpointe | 8/4.8kV | 87F1 | Crew isolated transformer TE2233 at 19 Wycliffe to replace defective elbow and insert. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
14572 | 2009 | 6 | 19 | 0.39306 |  | 73 | 10 | 8 | Centerpointe | 8/4.8kV | 87F1 | Transformer TP5322 @ 321 Paseo was isoilated for contractor to connect secondary. | Nepean | Scheduled Outage | Construction
14867 | 2009 | 7 | 28 | 0.65208 |  | 291 | 53 | 11 | Centrepoint | 8/4.8kV | 87F1 | Transformer #TE329 located at 9 Charing Rd isolated due to repairs needed to the 110 buss in the secondary pedestal | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
14910 | 2009 | 8 | 4 | 0.75 |  | 209 | 940 | 270 | Centrepointe | 8/4.8kV | 87F1 | Lightning in the Knowdale area causing the fuse S412 to blow | Nepean | Adverse Weather | Lightning
13012 | 2008 | 8 | 7 | 0.38958 |  | 54 | 4 | 5 | Centerpointe | 8/4.8kV | 87F1 | Transformer TP5317 @ 122 centerpointe was isolated to allow contractor to pull in secondary cable. | Nepean | Scheduled Outage | Construction
16689 | 2010 | 8 | 7 | 0.93403 |  | 80 | 4 | 3 | Centerpoint | 8/4.8kV | 87F1 | Transformer X32858 at 4 Roundhay opened due to animal contact. Transformer was refused by 24/7. 3 customer affected. | Nepean | Foreign Interference | Animal
14933 | 2009 | 8 | 11 | 0.39583 |  | 320 | 21 | 4 | Centrepointe | 8/4.8kV | 87F1 | Overhead section on Viewmount was isolated to string new primary and secondary on the 87F1 out of Centrepoint. 4 customers affected and power was restored at 2:50pm. | Nepean | Scheduled Outage
13123 | 2008 | 8 | 19 | 0.39167 |  | 204 | 34 | 10 | Centre Pointe | 8/4.8kV | 87F1 | Isolation of TP5320 transformer to allow contractor to pull in new Secondary | Nepean | Scheduled Outage | Preventive Maintenance
14975 | 2009 | 8 | 20 | 0.45139 |  | 40 | 5 | 8 | Centrepointe | 8/4.8kV | 87F1 | Transformer #X4201 located at 27 Majestic isolated to change ampacts | Nepean | Scheduled Outage | Construction
5707 | 2004 | 8 | 23 | 0.75 |  | 80 | 120 | 90 | Centerpointe | 8/4.8kV | 87F1 | Mike Lamoureux believes the pole and guy wire were hit by a riding lawn mower and shook the circuit. | Nepean | Foreign Interference
3980 | 2003 | 9 | 3 | 0.57847 |  | 237 | 143 | 180 | Centrepoint | 8/4.8kV | 87F1 | Centre Point 87F1 tripped while under Hold Off. Transformer TE2230 found blown, fused dip S31B opened. Customers restored in sections. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15227 | 2009 | 10 | 7 | 0.39444 |  | 164 | 87 | 32 | Centre Point | 8/4.8kV | 87F1 | TP5321 at 304 Paseo was Isolated to allow Contractor to make new Secondary Concetions and 2/7 to install new Metering. | Nepean | Scheduled Outage
13557 | 2008 | 11 | 4 | 0.4 |  | 114 | 4 | 2 | Centrepointe | 8/4.8kV | 87F1 | TP5320 isolated to connect privately owned secondaries. | Nepean | Scheduled Outage | Construction
13596 | 2008 | 11 | 12 | 0.35903 |  | 323 | 22 | 4 | Centrepointe | 8/4.8kV | 87F1 | TP5319 @ Paseo PVT was isolated for contractor to pull in secondary cable. | Nepean | Scheduled Outage | Construction
13643 | 2008 | 11 | 20 | 0.46528 |  | 8 | 1 | 4 | Centrepointe | 8/4.8kV | 87F1 | Transformers TP5319, TP5316 and TP5317 were interrupted due to incorrect cable tags in the field. Incorrect device was operated to isolate a transfomer. | Nepean | Human Element | Commissioning Errors
13646 | 2008 | 11 | 20 | 0.47639 |  | 198 | 53 | 16 | Centerpointe | 8/4.8kV | 87F1 | Transfomer TP5321@ 290 Paseo was isolated to allow contractor to pull in new cables. | Nepean | Scheduled Outage | Construction
19169 | 2011 | 9 | 13 | 0.90069 |  | 103 | 2746 | 1716 | Centrepointe | 8/4.8kV | 87F1, 87F4 | Ottawa fire reported electrical fire in the the rear of 40 Moorcroft then 87F1 breaker opened and system opened the 87F4 breaker which was at the same pole as the fire. Crews determined that a tree fell into the wires. Centrepointe ID# 19169. | Nepean | Adverse Weather | Lightning
3276 | 2003 | 3 | 20 | 0.86458 |  | 253 | 2530 | 600 | Centrepoint | 8/4.8kV | 87f1,f4,f5 | Pole fire at Centrepoint Dr near switch 262. | Nepean | Adverse Environment | Salt Spray
7857 | 2006 | 1 | 25 | 0.45833 |  | 105 | 7 | 4 | CENTERPOINT | 8/4.8kV | 87F2 | PEDESTAL REPLACED DEFFECTIVE CONNECTION IN PEDESTAL @ NPTE0349 @ 61 Assiniboine Dr. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15979 | 2010 | 4 | 23 | 0.35278 |  | 249 | 8 | 2 | Centrepointe | 8/4.8kV | 87F2 | 87F2 overhead section on Woodroffe was isolated to repair downed phase | Nepean | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
17192 | 2010 | 10 | 29 | 0.42361 |  | 144 | 34 | 14 | Centrepoint | 27.6/16kV | 87F2 | TP5248 at 41 Brockington isolated for soil clean up after oil leak from old transformer. | Nepean | Scheduled Outage | Preventive Maintenance
19868 | 2012 | 1 | 20 | 0.41528 |  | 6 | 1 | 8 | Centerpoint | 8/4.8kV | 87F3 | TP9109 at 12 Colfax was isolated to allow crews to install a double elbow bushing | Nepean | Scheduled Outage | Construction
11984 | 2008 | 1 | 28 | 0.41389 |  | 179 | 45 | 15 | Centrepointe | 8/4.8kV | 87F3 | TE811 @ 25 Colfax S was isolated for replacement. | Nepean | Scheduled Outage | Preventive Maintenance
12101 | 2008 | 3 | 4 | 0.43056 |  | 373 | 62 | 10 | Centrepointe | 8/4.8kV | 87F3 | TP5582 was isolated to all crew to replace transformer base. Located at Colfax St. | Nepean | Scheduled Outage | Construction
17727 | 2011 | 3 | 17 | 0.76944 |  | 110 | 132 | 72 | Centrepoint | 8/4.8kV | 87F3 | S1144 on Craig Henry blue phase switch burned up, crew replaced switch. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3274 | 2003 | 3 | 20 | 0.86458 |  | 130 | 650 | 300 | Centrepoint | 8/4.8kV | 87F3 | Pole top fire caused 87F1,F4,F5 to trip which caused circuitswitcher 87T1-L to open which resulted in the loss of 87F3 | Nepean | Adverse Environment | Salt Spray
12299 | 2008 | 4 | 17 | 0.59931 |  | 485 | 16 | 2 | Centerpoint | 8/4.8kV | 87F3 | TE1696 on 87F3 red phase at 194 Craig Henry was discovered off it's foundation and a hole in the side of the casing leaking oil, isolated for replacement. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
12313 | 2008 | 4 | 21 | 0.40972 |  | 495 | 248 | 30 | Centrepointe | 8/4.8kV | 87F3 | TE1696 at 192 Craig Henry isolated to install new base. TE1697 & TE1698 were included in isolation due to supply cable running in TE1696 pit. | Nepean | Scheduled Outage | Repair
18103 | 2011 | 5 | 6 | 0.45556 |  | 9 | 28 | 188 | Centerpoint | 8/4.8kV | 87F3 | While switching to isolate S1148 the crew inadvertantl opened the S1144 | Nepean | Human Element | Switching Errors
10403 | 2007 | 5 | 11 | 0.39583 |  | 124 | 17 | 8 | Centerpointe | 8/4.8kV | 87F3 | TE1082 @ 62 Fairoaks in Nepean was isolated to allow crew to change transformer. | Nepean | Scheduled Outage | Repair
20514 | 2012 | 5 | 15 | 0.40764 |  | 203 | 41 | 12 | Centerpointe | 8/4.8kV | 87F3 | Transformer TP9189 at 33 Colfax was isoalted to replace leaking transformer. | Nepean | Scheduled Outage | Repair
20557 | 2012 | 5 | 23 | 0.39583 |  | 415 | 97 | 14 | Centerpointe | 8/4.8kV | 87F3 | TE808 at 24 Colfax & TE1720 at 10 Craigmohr were isolated to replace TE1720 with new TP9190, remove TE808 & transfer customers to TP9190. | Nepean | Scheduled Outage | Construction
14425 | 2009 | 5 | 28 | 0.61319 |  | 167 | 22 | 8 | Centrepoint | 8/4.8kV | 87F3 | Broken primary riser on transformer X36523 at the rear of 77 Harris Place | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12541 | 2008 | 6 | 4 | 0.4375 |  | 35 | 4 | 6 | Epworth | 8/4.8kV | 87F3 | Isolated transformer X37119 at 50 Epworth Ave for service up-grade | Nepean | Scheduled Outage | Preventive Maintenance
12570 | 2008 | 6 | 7 | 0.49306 |  | 70 | 2 | 2 | Centrepointe | 8/4.8kV | 87F3 | Transformer# 37118 at 59 David was opened to replace defective customer secondary service. (probable cause of 87F3 reclose?) | Nepean | Defective Equipment | Imminent Equipment Failure Detected
10576 | 2007 | 6 | 8 | 0.84028 |  | 183 | 122 | 40 | Centrepointe | 8/4.8kV | 87F3 | A Burnt stirrup on blue phase Switch S700 at rear of Craig Henry, caused switch to open. Feeding five transformers. | Nepean | Defective Equipment
18401 | 2011 | 6 | 14 | 0.41667 |  | 251 | 577 | 138 | Centrepointe | 8/4.8kV | 87F3 | Transformer TE2076 and TE2075 on Craig Henry Dr were isolated to allow crew to replace insulator and riser. 138 customers were affetced. Centrepointe (87F3). | Nepean | Scheduled Outage
18412 | 2011 | 6 | 14 | 0.39583 |  | 300 | 680 | 136 | Centrepointe | 13.2kV | 87F3 | 2 transformers (#TE2076 and TE2075) located at 239 and 249 Craig Henry opened by crew due to re-insulating the back yard. | Nepean | Scheduled Outage | Construction
6732 | 2005 | 6 | 15 | 0.44444 |  | 100 | 2 | 1 | Centerpointe | 8/4.8kV | 87F3 | At 12:20 Trans TE2421 refused white phase . full power restored to 3 phase cust | Nepean | Adverse Weather | Lightning
6734 | 2005 | 6 | 15 | 0.076389 |  | 660 | 11 | 1 | Merivale | 27.6/16kV | 87F3 | At 12:50 TE1880 at 29 Antares was replaced due due failure | Nepean | Adverse Weather | Lightning
18424 | 2011 | 6 | 16 | 0.42847 |  | 143 | 50 | 21 | Centrepointe | 8/4.8kV | 87F3 | Transformer TE1171 @ 305 Craig Henry was opened to allow crew to replace inserts. 21 Customer were affetced. Centrepointe (87F3) | Nepean | Scheduled Outage
8748 | 2006 | 7 | 17 | 0.98403 |  | 72 | 1806 | 1505 | Centerpointe | 8/4.8kV | 87F3 | 87F3 opened during the lightning storm was found to be on single shot. Breaker was closed and held. | Nepean | Lightning | Direct Strike
8772 | 2006 | 7 | 18 | 0.86319 |  | 38 | 127 | 200 | Centerpointe | 8/4.8kV | 87F3 | 87F3 @ Centerpoint opened to allow for clearance to remove large tree from the 87F3 O/H conductor. Approx 200 customers. | Nepean | Tree Contacts | Tree Fallen
7072 | 2005 | 8 | 5 | 0.54167 |  | 180 | 225 | 75 | Centerpoint | 8/4.8kV | 87F3 | S1144 white phase fuse opened due to a bad cable dip between S1144w and TE1174W, load backfed from TE1382. Cable isolated. | Nepean | Defective Equipment
18900 | 2011 | 8 | 9 | 0.40764 |  | 440 | 59 | 8 | Centrepointe | 8/4.8kV | 87F3 | 8kV transformer TE809 at 12 Colfax St. Was isolated to allow crews to raise the base and replace the transformer. 8 customers affected for 440 min. | Nepean | Scheduled Outage | Repair
18951 | 2011 | 8 | 17 | 0.38333 |  | 636 | 85 | 8 | Centrepoint | 8/4.8kV | 87F3 | TP9109 at 12 Colfax was isolated to allow crews to perform soil remediation. | Nepean | Scheduled Outage | Repair
14991 | 2009 | 8 | 21 | 0.52778 |  | 128 | 65 | 37 | Centrepointe | 8/4.8kV | 87F3 | Outage to 3 transformers fed from S1135 due to cable fault in the Craig Henry and Colfax area. Fault isolated and customers restored as per 24/7 crew and system. 37 Customers affected and all power restored at 12:51 pm. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
19013 | 2011 | 8 | 25 | 0.33472 |  | 128 | 15 | 7 | Centrepoint | 8/4.8kV | 87F3 | TE1523 at 3 Chartwell was isolated to allow crews to replace a leaking transformer. | Nepean | Scheduled Outage | Preventive Maintenance
7218 | 2005 | 8 | 26 | 0.37153 |  | 329 | 49 | 9 | Centerpoint | 8/4.8kV | 87F3 | Leaking transformer changed on Craig henry TE2980 | Nepean | Scheduled Outage | Repair
19150 | 2011 | 9 | 12 | 0.39583 |  | 497 | 58 | 7 | Centrepointe | 8/4.8kV | 87F3 | Transformer TE1523 at 3 Craig Henry isolated from HOL sources for soil remediation of leaking transformer | Nepean | Scheduled Outage | Preventive Maintenance
19239 | 2011 | 9 | 22 | 0.37222 |  | 562 | 66 | 7 | Centerpoint | 8/4.8kV | 87F3 | TE14967 at 47 Bertone was isolated to allow crews to replace and rebuild the transformer and base | Nepean | Scheduled Outage | Construction
19357 | 2011 | 10 | 11 | 0.375 |  | 495 | 83 | 10 | Centrepointe | 8/4.8kV | 87F3 | Transformer TP9109 @ 12 Colfax was isolated to allow the crews to preform transformer remidiation. | Nepean | Scheduled Outage | Preventive Maintenance
13378 | 2008 | 10 | 16 | 0.40486 |  | 285 | 66 | 14 | Centrepointe | 8/4.8kV | 87F3 | Transformer TE1148 @ 289 Craig Henry was isolated to install new base and grounding. | Nepean | Scheduled Outage | Repair
19468 | 2011 | 10 | 26 | 0.42014 |  | 158 | 21 | 8 | Centrepointe | 8/4.8kV | 87F3 | TP9109 at 12 Colfax was isolated to allow crews to complete cable repairs and place the transformer back on its base. | Nepean | Scheduled Outage | Repair
11639 | 2007 | 11 | 1 | 0.13889 |  | 66 | 6 | 5 | Centerpointe | 8/4.8kV | 87F3 | Service Wire at 33 David Drive burnt off, and Transformer 146 was opened for crews to make repairs. 5 Customers affected. | Nepean | Defective Equipment
11665 | 2007 | 11 | 5 | 0.375 |  | 67 | 11 | 10 | CENTREPOINTE | 8/4.8kV | 87F3 | Transformer #X36521 at 64 David Place isolated to allow for service upgrade | Nepean | Scheduled Outage | Repair
11666 | 2007 | 11 | 5 | 0.56667 |  | 54 | 0 | 10 | Centrepointe | 8/4.8kV | 87F3 | Transformer #36521 at 64 David Place isolated to allow for completion of service upgrade | Nepean | Scheduled Outage | Repair
11667 | 2007 | 11 | 5 | 0.56667 |  | 54 | 9 | 10 | Centrepointe | 8/4.8kV | 87F3 | Transformer #36521 at 64 David Place isolated to allow for completion of service upgrade | Nepean | Scheduled Outage | Repair
11690 | 2007 | 11 | 11 | 0.21667 |  | 202 | 142 | 54 | Centerpoint | 8/4.8kV | 87F3 | Circuit auto/reclosed when cable between TE810 & TE1720 faulted causing S1121 to blow. Crew had numerous problems with fault finding, no wells under Tx's & cables frozen into place making operations difficult while sectionalizing. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
11698 | 2007 | 11 | 13 | 0.40139 |  | 332 | 127 | 23 | Centrepoint | 8/4.8kV | 87F3 | TE918 at 209 Craig Henry was replaced due to oil leak and oil spill was cleaned up. New nomenclature for transformer is TP5325. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
11718 | 2007 | 11 | 15 | 0.57292 |  | 70 | 4 | 3 | Centerpoint | 8/4.8kV | 87F3 | Isolated transformer 1273 at 115 Rossland Ave to install new pole | Nepean | Scheduled Outage | Construction
4522 | 2003 | 11 | 27 | 0.55903 |  | 37 | 5 | 8 | Centrepoint | 8/4.8kV | 87F3 | TE808 out for bushing replacement. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
15993 | 2010 | 4 | 25 | 0.87361 |  | 71 | 53 | 45 | Centrepoint | 8/4.8kV | 87F4 | Crew found the lead fell out on S17752 white phase, crew restored power from an alternate source. Affecting 45 customers on Wycliffe,Palisade, Strathbury | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6729 | 2005 | 6 | 15 | 0.46389 |  | 750 | 349 | 40 | Centrepointe | 8/4.8kV | 87F4 | Blown Elbows & insterts at TE1792 crews isolated transformer. | Nepean | Adverse Weather | Lightning
6730 | 2005 | 6 | 15 | 0.069444 |  | 500 | 947 | 115 | Centrepoint | 8/4.8kV | 87F4 | S1410R phase fuse blew and 2 lightning arrestors found blown at S1401 due to lightning. S1401R refused and fuse at TE1845 found blown. 6 out of 7 TE's restored. TE1845 is defective and replaced. | Nepean | Lightning | Direct Strike
19171 | 2011 | 9 | 14 | 0.11042 |  | 141 | 306 | 130 | Centrepoint | 8/4.8kV | 87F4 | S62 was found burnt up and open due to the storm. Centrepointe (87F4) ID# 19171 | Nepean | Adverse Weather
9876 | 2006 | 12 | 23 | 0.28125 |  | 244 | 2375 | 630 | Centrepointe | 8/4.8kV | 87F4 | A broken switch S1391 @ rear of 98 Pinetrail fell to the ground with the O/H | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9880 | 2006 | 12 | 23 | 0.55347 |  | 257 | 1285 | 300 | Centrepoint | 8/4.8kV | 87F4 | 87F4 section north of CNR between Woodroffe and Greenbank isolated to repair broken switch S1391 and conductor down. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
15598 | 2009 | 12 | 30 | 0.68472 |  | 9 | 0 | 2 | Centrepointe | 8/4.8kV | 87F4 | S. Cunningham reports TE2405 @ 1600 Merivale RD had a blown internal fuse. S1429 rwb switch was opened to isolate TE2405 & TE1882.Fuse replaced & all power restored. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
15960 | 2010 | 4 | 20 | 0.40278 |  | 283 | 108 | 23 | Centrepoint | 8/4.8kV | 87F5 | 3 transformers on bennington, hyde park and marble arch were isolated to allow crews to remove sand from the transformer bases. | Nepean | Scheduled Outage | Preventive Maintenance
16040 | 2010 | 5 | 5 | 0.40278 |  | 252 | 126 | 30 | Centerpoint DS | 8/4.8kV | 87F5 | TE2270 at 13 Weymouth Court, TE2271 at 20 Norwich Way, TE2272 at 12 Norwich Way were isolated to allow crews to clean sand out of the bases of the transformers. | Nepean | Scheduled Outage | Preventive Maintenance
16080 | 2010 | 5 | 13 | 0.40278 |  | 210 | 112 | 32 | Centrepointe | 8/4.8kV | 87F5 | Transformers TE2258, TE2259, and TE2260 on Marble Arch and Bennington isolated to allow crews to pump sand out of the bases | Nepean | Scheduled Outage
16147 | 2010 | 5 | 26 | 0.39931 |  | 215 | 79 | 22 | Centerpoint | 8/4.8kV | 87F5 | Transformer TE2277 and TE2278 on Covington isolated to alllow crew to pump out sand from transformer base. | Nepean | Scheduled Outage
3524 | 2003 | 6 | 5 | 0.51042 |  | 124 | 12 | 6 | Centrepointe | 8/4.8kV | 87F5 | Transformer #2268 isolated to allow crews to replace same. | Nepean | Scheduled Outage | Repair
11255 | 2007 | 9 | 5 | 0.75139 |  | 69 | 45 | 39 | Centerpointe | 8/4.8kV | 87F5 | Crew replaced broken switch at S294, at 35 Northgate feeding 4 blue phase transformers. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
15066 | 2009 | 9 | 8 | 0.40833 |  | 123 | 14 | 7 | Centerpointe | 8/4.8kV | 87F5 | Transformer TE2261 at 2 Cheswick was isolated to allow Hydrovac to wash transformer base. | Nepean | Scheduled Outage
9470 | 2006 | 10 | 19 | 0.48542 |  | 193 | 64 | 20 | Centrepointe | 8/4.8kV | 87F5 | Isolated transformer TE2275 @ 7 Hyde park way and TE2276 @ 10 Hyde park way to repair broken elbows. | Nepean | Scheduled Outage | Repair
19698 | 2011 | 12 | 7 | 0.55208 |  | 113 | 17 | 9 | Centrepointe | 8/4.8kV | 87F5 | TE2263 at 27 Hyde Park was isolated from Hydro Ottawa Sources to change out leaking transformer | Nepean | Scheduled Outage
10014 | 2007 | 2 | 11 | 0.54097 |  | 461 | 8 | 1 | Centerpointe | 8/4.8kV | 87F6 | 87F6 auto reclosed, TE3517 to Loblaws at 1980 Baseline appears to be faulted as well as problems on the customers secondary. Defective TE3517 & defective secondary removed from service, TE3517 bypassed to pick up TE3518 & feed customer from one source. Defective secondary equipment including bus tie delayed restoration. Schneider Electric is working on secondary problems. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
17660 | 2011 | 3 | 2 | 0.33333 |  | 20 | 2 | 6 | Centrepointe | 8/4.8kV | 87F6 | Isolated and replaced broken switch SW1651 feeding transformer NPTE3548 at 1365 Woodroffe Ave | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6437 | 2005 | 4 | 21 | 0.40278 |  | 136 | 113 | 50 |  | 8/4.8kV | 87F6 | Planned interruption for insulator changing. | Nepean | Scheduled Outage
17982 | 2011 | 4 | 21 | 0.94375 |  | 225 | 45 | 12 | Centrepointe | 8/4.8kV | 87F6 | TE3548 at College Square in Nepean was isolated to allow contractor to install new secondary cables. | Nepean | Scheduled Outage | Repair
8402 | 2006 | 6 | 1 | 0.54306 |  | 10 | 7 | 44 | Centrepointe | 8/4.8kV | 87F6 | Transformer TE594 @ 25 Deerfeild was isolated to place it back on to its pad. | Nepean | Scheduled Outage | Repair
10785 | 2007 | 7 | 3 | 0.76736 |  | 45 | 11 | 15 | Centrepointe | 8/4.8kV | 87F6 | A bird made contact with the O/H switch 169 causing it ti blow on St Claire. | Nepean | Foreign Interference | Bird
11016 | 2007 | 8 | 8 | 0.60417 |  | 30 | 2 | 4 | Centerpoint | 8/4.8kV | 87F6 | Crew isolated transformer NP752 at 118 Tower Rd to replace service | Nepean | Scheduled Outage | Preventive Maintenance
13377 | 2008 | 10 | 16 | 0.40694 |  | 138 | 5 | 2 | Centrepointe | 8/4.8kV | 87F6 | Transformer TE442 was isolated for customer maintenance. | Nepean | Scheduled Outage | Preventive Maintenance
11737 | 2007 | 11 | 19 | 0.39583 |  | 210 | 28 | 8 | Centerpoint | 8/4.8kV | 87F6 | Isolated transformer 1273 at Indian Rd and Rossland Ave to install new secondary spun buss | Nepean | Scheduled Outage | Construction
17365 | 2010 | 12 | 2 | 0.36806 |  | 140 | 28 | 12 | Centerpointe | 8/4.8kV | 87F6 | Transformer TE3548 at 1365 Woodroffe was isolated to allow contractor to repair defective secondary cables. Generator was installed while contractor repairs secondary. | Nepean | Defective Equipment
17366 | 2010 | 12 | 2 | 0.38542 |  | 96 | 11 | 7 | Centerpoint | 8/4.8kV | 87F6 | Transformer TE3515 at 1971 Baseline Road was isolated to allow contractor to find secondary fault.Transformer was restored with one secondary disconnected effecting 5 customers while contractor repairs faulted cable. A generator was installed to pick up affected customers. | Nepean | Defective Equipment
17386 | 2010 | 12 | 6 | 0.41667 |  | 620 | 83 | 8 |  | 8/4.8kV | 87F6 | Transformer TE3515 at 1971 Baseline isolated to allow for repairs by owners | Nepean | Scheduled Outage | Repair
13814 | 2008 | 12 | 28 | 0.81667 |  | 294 | 5 | 1 | Centrepointe | 8/4.8kV | 87F6 | Blown termination at the riser pole at 1900 Baseline Rd @ transformer TE2923 | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16287 | 2010 | 6 | 19 | 0.1125 |  | 82 | 44 | 32 | Centrepoint | 8/4.8kV | 87F7 | S583 found open but not blown. Switch was closed but would not stay closed. Load restored from back-up supply 58F6 at S869 | Nepean | Defective Equipment | Imminent Equipment Failure Detected
12838 | 2008 | 7 | 14 | 0.70833 |  | 65 | 11 | 10 | Centerpointe | 8/4.8kV | 87F7 | T394 transformer @ rear of 135 withrow opened. Crew refused and closed. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
15038 | 2009 | 8 | 31 | 0.45833 |  | 60 | 18 | 18 | Centrepointe | 13.2kV | 87F7 | Transformer #TE402 located at 14 Parkglen isolated for service upgrade | Nepean | Scheduled Outage | Construction
19071 | 2011 | 9 | 1 | 0.43542 |  | 39 | 10 | 16 | Centrepointe | 8/4.8kV | 87F7 | Transformer NPTE0395 at 21 Suffolk St isolated to allow for repairs to secondary | Nepean | Scheduled Outage | Repair
16857 | 2010 | 9 | 3 | 0.52292 |  | 137 | 128 | 56 | Centerpoint | 8/4.8kV | 87F7 | While swotching to isolate a leaking transformer a fused switch failed, apparently due to age deterioration, and the outage went unnoticed for about 45 minutes when a 3 phase customer approached the crew on site about voltage problems. At that point a quick investigation revealed the failed switch. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16861 | 2010 | 9 | 3 | 0.52292 |  | 177 | 18 | 6 | Centerpoint | 8/4.8kV | 87F7 | Transformer TP5248 at 41 Brockington was isolated to replace the leaking transformer | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16868 | 2010 | 9 | 4 | 0.14444 |  | 52 | 10 | 11 | Centrepoint | 8/4.8kV | 87F7 | Crews opened transformer X36183 at 197 Norice to repair sparkihng wires. | Nepean | Scheduled Outage | Repair
11256 | 2007 | 9 | 6 | 0.37778 |  | 176 | 91 | 31 | Centerpoint | 8/4.8kV | 87F7 | TE1028, 1029, 1034, 1035, & 1036 on Medhurst & Abitibi isolated for installation of smart meters. | Nepean | Scheduled Outage
15087 | 2009 | 9 | 11 | 0.090278 |  | 57 | 37 | 39 | Centerpointe | 8/4.8kV | 87F7 | Cable fault between TE16 and TE17 on Cheryl rd. caused S704W to open. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
11340 | 2007 | 9 | 20 | 0.37847 |  | 192 | 128 | 40 | Centerpointe | 13.2kV | 87F7 | Transformers TE1027, 1031, 1032, and 1033 isolated on Brockington Cres for the Smart Meter program. | Nepean | Scheduled Outage | Preventive Maintenance
15165 | 2009 | 9 | 25 | 0.56042 |  | 103 | 34 | 20 | Centrepointe | 8/4.8kV | 87F7 | Te16 @ 7 Cheryl was isolated to allow crews to replace elbow on cable section between TE16 & TE17. | Nepean | Defective Equipment
11431 | 2007 | 10 | 1 | 0.40278 |  | 134 | 16 | 7 | Centerpoint | 8/4.8kV | 87F7 | TE1826 @ 30 Castlebrook Lane was isolated to allow crew to work on transformer base and secondary bus bars. | Nepean | Scheduled Outage | Construction
11546 | 2007 | 10 | 18 | 0.38889 |  | 380 | 63 | 10 | Centrepointe | 8/4.8kV | 87F7 | TE1030 at 41 Brockington was replaced with TP5248 due to oil leak. | Nepean | Scheduled Outage | Repair
15358 | 2009 | 11 | 6 | 0.92014 |  | 42 | 4 | 6 | Centrepointe | 13.2kV | 87F7 | Transformer #X4165 located at 13 Sherry Lane isolated to replace service | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
8243 | 2006 | 5 | 6 | 0.58681 |  | 43 | 996 | 1390 | Centrepointe | 8/4.8kV | 87T1 | The secondary cables going into transformer 87T1 @ Centrepointe have blown. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6120 | 2005 | 1 | 6 | 0.725 |  | 136 | 5 | 2 | Moulton | 27.6/16kV | 8F1 | Replaced broken switch for transformer #4631 at 2 Briarcliffe | Gloucester | Unknown/Other | No Apparent Cause
3098 | 2003 | 1 | 8 | 0.17014 |  | 154 | 13 | 5 | Moulton | 27.6/16kV | 8F1 | Cable locater requested On-call crew to isolate direct buried primary cables feeding TE420, due to broken water main. Excavation required over top of cables. Notified On-call Supervisor of the situation. | Gloucester | Adverse Environment | Flooding
15649 | 2010 | 1 | 13 | 0.85694 |  | 161 | 3 | 1 | Moulton | 27.6/16kV | 8F1 | RX2017 auto reclosed. 24/7 Crew found G732 R phase blown. Customer owned switchgear looked good. Cause unknown. G732R closed and all power restored. | Gloucester | Unknown/Other
17524 | 2011 | 1 | 26 | 0.21528 |  | 41 | 1 | 2 | Moulton | 27.6/16kV | 8F1 | TP7332 at 2160 Montreal Rd was opened to allow customer's contractor to install a new service to the transformer | Gloucester | Scheduled Outage | Construction
9976 | 2007 | 1 | 31 | 0.085417 |  | 81 | 202 | 150 | Moulton | 8/4.8kV | 8F1 | Transformers on Jasmin Cr in Gloucester interupted due to faulted cable in section between G946W and T475W. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19979 | 2012 | 2 | 7 | 0.55069 |  | 122 | 73 | 36 | Moulton | 27.6/16kV | 8F1 | Switch G190B blew due to defective cut out at transformer X24761at 19 Cedar Road. Moulton (8F1) ID#19979 | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
15718 | 2010 | 2 | 11 | 0.44792 |  | 30 | 3 | 6 | Moulton | 27.6/16kV | 8F1 | Customers on Taunton were interrupted for crew to make repairs to G824 cutout and arrester | Gloucester | Scheduled Outage | Repair
13991 | 2009 | 2 | 18 | 0.93472 |  | 178 | 1071 | 1516 | Moulton | 27.6/16kV | 8F1 | Fire Department called to report a motor vehicle accident on Montreal rd. and Elmwood where a car hit a Hydro pole. Crews on site reported that the pole needed to be changed. Two Temp switches were cut in to on either side of the broken pole. On Call crews were called in to change broken pole. | Gloucester | Foreign Interference | Vehicle
13992 | 2009 | 2 | 18 | 0.87569 |  | 174 | 970 | 704 | Moulton | 27.6/16kV | 8F1 | Fire Department called to report a motor vehicle accident on Montreal rd. and Elmwood where a car hit a Hydro pole. Crews on site reported that the pole needed to be changed. Two Temp switches were cut in to on either side of the broken pole. On Call crews were called in to change broken pole. All power was restored at 23:59. | Gloucester | Foreign Interference | Vehicle
17611 | 2011 | 2 | 18 | 0.89375 |  | 525 | 96 | 11 | Moulton | 27.6/16kV | 8F1 | G465 blew due to tree on primary, affecting customers on Wipperpool and Meadowlark. Tree removed, primary repaired and power restored. | Gloucester | Tree Contacts | Tree Fallen
15740 | 2010 | 2 | 24 | 0.38333 |  | 233 | 50 | 13 | Moulton | 27.6/16kV | 8F1 | Defective transformer X24175 at 40 Crownhill caused RX2017 to A/R when cut-out blew. Transformer replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10077 | 2007 | 3 | 1 | 0.39583 |  | 29 | 14 | 28 | Moulton | 27.6/16kV | 8F1 | 8F1 red phase section between G770R & G769R was dumped of to allow crew to pull 27Kv elbows at T2006R on Gregory court. | Ottawa | Adverse Weather | Extreme Ambient Temperature
3226 | 2003 | 3 | 6 | 0.40625 |  | 25 | 42 | 100 | Moulton | 27.6/16kV | 8F1 | Outage required for switching because the elbows required open were the non-vent type. | Gloucester | Scheduled Outage | Construction
15776 | 2010 | 3 | 6 | 0.35139 |  | 194 | 3 | 1 | Moulton | 27.6/16kV | 8F1 | At 8:26am, Customer Isolated from G732 to allow contractor to trouble shoot for fault. 1 customer affected for 194 minutes. Moulton (8F1) ID #15776 | Gloucester | Tree Contacts | Tree Limb Fallen
10110 | 2007 | 3 | 12 | 0.44444 |  | 20 | 3 | 8 | Moulton | 27.6/16kV | 8F1 | Opened SW G465 feeding two transformers 383 and 15 on Meadowlark dr to repair broken neutral | Gloucester | Scheduled Outage | Repair
17735 | 2011 | 3 | 18 | 0.45139 |  | 110 | 38 | 21 | Moulton |  | 8F1 | Power outage due to tree limb on overhead, caused G529 red phase to blow. Tree removed and fuse replaced. | Gloucester | Tree Contacts | Tree Limb Fallen
8067 | 2006 | 3 | 27 | 0.52083 |  | 58 | 7 | 7 | Moulton | 27.6/16kV | 8F1 | O/H transformer at 41 Kaymar Dr in Gloucester isolated to replace tx switch. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17800 | 2011 | 3 | 29 | 0.55 |  | 215 | 93 | 76 | Moulton | 8/4.8kV | 8F1 | Elbow and insert on TE983 at 1317 Bethany Lane failed during operation while a crew was switching to isolate an underground cable section on the 8F1. The failure caused G439 B phase to open causing an outage to 7 transformers. Crews restored the load, isolated the defective transformer and made the repairs to TE983. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
14123 | 2009 | 3 | 31 | 0.40625 |  | 29 | 1 | 2 | Moulton | 27.6/16kV | 8F1 | Transformer #X17187 located at 1399 St. Joseph Blvd isolated to change defective cut out | Gloucester | Scheduled Outage | Preventive Maintenance
17814 | 2011 | 3 | 31 | 0.32292 |  | 315 | 5 | 1 | Moulton | 27.6/16kV | 8F1 | Transformer #X16891 located at 1815 Montreal Rd blew and the transformer lid was hanging. Transformer was replaced. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
17819 | 2011 | 4 | 1 | 0.54583 |  | 144 | 17 | 10 | MOULTON | 27.6/16kV | 8F1 | TE1296 blue phase insert broke when removing cap causing G611 B. Isolation expanded to allow crew to safely pull elbows at TE1295. Crew replaced insert and all load restored. | Gloucester | Defective Equipment
15893 | 2010 | 4 | 5 | 0.76389 |  | 7 | 0 | 4 | Moulton | 27.6/16kV | 8F1 | Transformer #3119 located at 19 Kindle Crt opened by crew to cut U/G service from transformer pole for a part out, U/G call | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12264 | 2008 | 4 | 9 | 0.94792 |  | 320 | 37 | 7 | Moulton | 27.6/16kV | 8F1 | On Call crew had to change defective O/H transformer 3376 @ 27 Appleford. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17874 | 2011 | 4 | 11 | 0.23333 |  | 191 | 341 | 107 | Moulton | 27.6/16kV | 8F1 | G228B located at 78 Rothwell opened up due to lightning | Gloucester | Lightning | Direct Strike
17882 | 2011 | 4 | 11 | 0.375 |  | 202 | 7 | 2 | Moulton | 27.6/16kV | 8F1 | Transformer X24790 at 13 Oriole to be replaced - lightning | Gloucester | Adverse Weather | Rain
6453 | 2005 | 4 | 24 | 0.45139 |  | 65 | 119 | 110 | Moulton | 27.6/16kV | 8F1 | Tree contact at 33 Kaymar st. Crew removed tree and energized overhead circuit. | Gloucester | Tree Contacts | Tree Fallen
12359 | 2008 | 4 | 29 | 0.33542 |  | 117 | 39 | 20 | Moulton | 27.6/16kV | 8F1 | Switch G884 & transformer #2594 opened up due to bird contact | Gloucester | Foreign Interference | Bird
14260 | 2009 | 4 | 29 | 0.40972 |  | 25 | 2 | 5 | Moulton | 27.6/16kV | 8F1 | Transformer #522 located at 559 Blair Rd isolated to lash spun buss & change defective cut out | Gloucester | Scheduled Outage
5091 | 2004 | 5 | 3 | 0.17222 |  | 18 | 354 | 1179 | Moulton |  | 8F1 | G925SM was opened to isolate G67 RWB at the request of the crew the switch was opened then G925Sm was closed to liven up one side (load to the 8F1) and G89SM was closed to pick up load from the other side (8F4) | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
6527 | 2005 | 5 | 9 | 0.58333 |  | 316 | 58 | 11 | Moulton | 27.6/16kV | 8F1 | Transformer #3326 at 28 Appleford isolated due to a truck that tore down 2 spans of open wire bus & blew the fuse on the transformer | Gloucester | Foreign Interference | Vehicle
18118 | 2011 | 5 | 9 | 0.40694 |  | 59 | 377 | 2140 | Moulton | 27.6/16kV | 8F1 | Moulton 8F1 tripped when a crane made contact with primary conductors on a private line on the CSIS site (Blair / Ogilvie) The line was sectionalized via scada restoring most customers. Connections to the private line were cleared from 8F1 o/h & remaining customers then restored, | Gloucester | Foreign Interference | Vehicle
5126 | 2004 | 5 | 10 | 0.44444 |  | 50 | 2 | 2 | Moulton | 27.6/16kV | 8F1 | Transfomer at 22 Davidson interrupted to upgrade sevice. | Ottawa | Scheduled Outage | Construction
3428 | 2003 | 5 | 12 | 0.36597 |  | 158 | 130 | 122 | Moulton | 27.6/16kV | 8F1 | Squirrel at transformer location 4180 caused flash over rupturing fuses on overhead line. | Gloucester | Foreign Interference | Animal
16118 | 2010 | 5 | 21 | 0.046528 |  | 88 | 59 | 40 | Moulton | 27.6/16kV | 8F1 | G613W phase found blown after auto of RX2017 W. 24/7 believe cause was tree contract. | Gloucester | Tree Contacts | Inadequate Trimming
16120 | 2010 | 5 | 21 | 0.60833 |  | 164 | 8 | 3 | Moulton | 27.6/16kV | 8F1 | Transformer #78 located at 16 Briarcliffe opened up due to vine interference | Gloucester | Tree Contacts | Inadequate Trimming
10460 | 2007 | 5 | 25 | 0.44792 |  | 61 | 10 | 10 | Moulton | 27.6/16kV | 8F1 | At 10:45 trans at 21 Steel was isolated in order to replace a defective Cutout | Gloucester | Scheduled Outage | Repair
10461 | 2007 | 5 | 25 | 0.6125 |  | 120 | 281 | 1200 | Moulton | 27.6/16kV | 8F1 | GR9 tripped under h/o during storm. Found G608W at Blair & Davidson blown, possible lightning strike. Fuse & cut-out replaced. | Gloucester | Adverse Weather | Lightning
20596 | 2012 | 5 | 25 | 0.78542 |  | 160 | 147 | 55 | Moulton | 27.6/16kV | 8F1 | tree contacts due to high winds caused transformer at 42 whipperwill to open which also caused G256B fuse to blow. | Gloucester | Tree Contacts | Inadequate Trimming
12496 | 2008 | 5 | 29 | 0.24792 |  | 355 | 200 | 118 | Moulton | 27.6/16kV | 8F1 | transformer 5110 @ 57 Oriole failed causing G627W & G628W to blow. Crew replaced transformer & restored power. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
20658 | 2012 | 5 | 29 | 0.74306 |  | 162 | 178 | 78 | Moulton | 27.6/16kV | 8F1 | G627W blew during storm. Fuse to xfrm X24793 also blew. Line patrolled, refused and closed G627W. G627 blew again, and xfmr X24793 replaced. | Gloucester | Lightning | Direct Strike
12502 | 2008 | 5 | 30 | 0.425 |  | 84 | 27 | 19 | Moulton | 8/4.8kV | 8F1 | Squirrel contact caused overhead transformer T246 on red phase local to open the G884 @ 881 Blair. | Gloucester | Foreign Interference | Animal
10485 | 2007 | 5 | 31 | 0.10833 |  | 152 | 464 | 620 | Moulton | 27.6/16kV | 8F1 | Fire on Steel and Crownhill appears to have somehow caused 2 phases to open at G285 causing first interuption, then OFD requested safe working clearance, requiring G925 to be opened, area was isolated anf majority of customers were restored. | Gloucester | Adverse Environment | Fire
12572 | 2008 | 6 | 7 | 0.57778 |  | 283 | 281 | 118 | Moulton | 27.6/16kV | 8F1 | Customer reports outages along Massey Lane; dispatched crew to investigate G628W on Blair & Massey. Crew reports G628W blown & G627W blown as well. Crew refused G628W & restored all padmount transformers up to G627W. Crew patrolled all remaining 8F1 overhead up to all open points, lots of tree over burden near or on line sections. Crew removed over burden & refused & closed G627W, which picked up all remaining customers except 6 fed from transformer @ 34 Kaymar. Crew refused transformer & picked up remaining 6 customers, all load restored. | Gloucester | Tree Contacts | Inadequate Trimming
10556 | 2007 | 6 | 8 | 0.77083 |  | 149 | 177 | 100 | Moulton | 27.6/16kV | 8F1 | Transformer fuse at TE1279 opened causing G190W locate fuse to open & GR9 recloser to auto reclose. | Gloucester | Tree Contacts | Inadequate Trimming
18376 | 2011 | 6 | 9 | 0.44097 |  | 472 | 8 | 1 | Moulton | 27.6/16kV | 8F1 | Transformer TE2935 on Ogilivie feeding Future Shop isolated, and when refused transformer blew, Transformer re-isolated for replacement | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12604 | 2008 | 6 | 11 | 0.625 |  | 107 | 141 | 118 | Moulton | 27.6/16kV | 8F1 | G628W & G627W both blew for tree contact at O/H xfmr 892 (53 Rebecca). Cutout at xfmr was also blown. Trees at xfmr were cleared but more trimming in area is required by forestry. G628W fuse was increased from 65 to 100 amps. | Gloucester | Tree Contacts | Inadequate Trimming
3564 | 2003 | 6 | 13 | 0.88194 |  | 283 | 19 | 4 | Moulton | 27.6/16kV | 8F1 | Xfmr TE12 at 1841 Burfield taken out of service to install a temporary jumper due to a defective leg between the xfmr & a pedestal at 1839 Burfield. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12620 | 2008 | 6 | 13 | 0.34306 |  | 99 | 45 | 35 | Moulton | 27.6/16kV | 8F1 | A bird made contact with transformer 00376 at 29 Appleford causing its fuse to blow as well as the line fuse at G490R. Both fuses replaced. | Goulburn | Foreign Interference | Bird
20755 | 2012 | 6 | 13 | 0.15764 |  | 76 | 46 | 36 | Moulton | 27.6/16kV | 8F1 | Tree contact caused G190B to open affecting customers on Beckenham Lane, Cedar rd | Gloucester | Tree Contacts | Inadequate Trimming
20756 | 2012 | 6 | 13 | 0.26389 |  | 145 | 7 | 3 | Moulton | 27.6/16kV | 8F1 | Transformer #X24153 located at 8 Beckenham Lane opened up due to tree contact | Gloucester | Tree Contacts | Inadequate Trimming
10704 | 2007 | 6 | 21 | 0.75417 |  | 105 | 350 | 200 | Moulton | 27.6/16kV | 8F1 | G12 RW phase fuses found blown on overhead circuit. Fuses replaced & all power restored to normal. | Gloucester | Adverse Weather | Lightning
20824 | 2012 | 6 | 21 | 0.90972 |  | 108 | 87 | 66 | Moulton | 27.6/16kV | 8F1 | tree branch caused X24586 to open, G256B to blow and GR5 to trip open affected customers on the blue phase only on Rothwell drive, wren, whipperwill area | Gloucester | Tree Contacts | Tree Limb Fallen
18472 | 2011 | 6 | 23 | 0.625 |  | 30 | 8 | 30 | Moulton |  | 8F1 | Bird found in the overhead caused transformer fuse open & G320 White phase | Gloucester | Foreign Interference | Bird
3622 | 2003 | 6 | 25 | 0.37847 |  | 84 | 27 | 19 | Moulton MS | 12/7.2kV | 8F1 | Planned outage to perform tree trimming. | Gloucester | Scheduled Outage | Preventive Maintenance
5373 | 2004 | 6 | 25 | 0.37917 |  | 251 | 468 | 115 | Moulton | 27.6/16kV | 8F1 | Fuses on the overhead in the Rothwell Heights area blown, no cause found during patrol. | Gloucester | Unknown/Other
6828 | 2005 | 6 | 28 | 0.65764 |  | 207 | 153 | 45 | Moulton | 27.6/16kV | 8F1 | G285 red phase blown. Broken red phase insulator found at Appleford at Crownhill. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10757 | 2007 | 6 | 29 | 0.23611 |  | 72 | 44 | 37 | Moulton | 27.6/16kV | 8F1 | Local fuse G247R found blown. Same refused and closed. No apparent cause found. | Gloucester | Unknown/Other | No Apparent Cause
14647 | 2009 | 6 | 30 | 0.37569 |  | 84 | 41 | 29 | Moulton | 27.6/16kV | 8F1 | RX2017B auto reclosed due to G190 blowing, and transformer 2507 blew on Beckenham Lane. Suspected bird contact at transformer. Swich and transformer refused, and all power restored. | Gloucester | Foreign Interference | Bird
8655 | 2006 | 7 | 3 | 0.76736 |  | 185 | 340 | 120 | Moulton | 27.6/16kV | 8F1 | Rain and high winds caused multiple problems on the Moulton 8F1 section fed from switch G628W. The G627W was also open on the same section. The crew first energized the underground customers fed from the G628W, then Crew replaced a broken cutout and cleared trees and refused and closed the G627W picking up remaining customers. | Gloucester | Adverse Weather | Wind
6873 | 2005 | 7 | 5 | 0.56944 |  | 85 | 129 | 91 | Moulton | 27.6/16kV | 8F1 | Fused switches G228B, G297B & G293B found blown all refused and closed to restore load, O/H tx fuse at tx 826 was found broken, same replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18601 | 2011 | 7 | 6 | 0.42222 |  | 52 | 31 | 36 | Moulton | 27.6/16kV | 8F1 | Switch G190B @ 1745 Montreal open due to lightning storm in the Ottawa area. 36 customers were affected. Moulton (8F1) | Gloucester | Lightning
18629 | 2011 | 7 | 9 | 0.33958 |  | 37 | 22 | 35 | Moulton | 27.6/16kV | 8F1 | G320 white phase blown due to crow contact. Fuse replaced. | Gloucester | Foreign Interference | Animal
3713 | 2003 | 7 | 10 | 0.25278 |  | 34 | 6 | 10 | Beaconhill | 8/4.8kV | 8f1 | 4F1 circuit opened to open G344 blue phase. Unable to close breaker via scada & manual control at the station. | Gloucester | Defective Equipment
8694 | 2006 | 7 | 11 | 0.25833 |  | 151 | 53 | 21 | Moulton | 27.6/16kV | 8F1 | Crew found dead bird on O/H transformer 1 span south of G320. Bird caused white phase of G320 to open loosing power to two single phase transformers and single phasing to three phase transformers. | Gloucester | Foreign Interference | Bird
18640 | 2011 | 7 | 11 | 0.81806 |  | 74 | 58 | 47 | Moulton | 27.6/16kV | 8F1 | bird contact at transformer X24163, 26 Elvina caused the transformer fuse to blow as well as G247R. Both fuses replaced. | Gloucester | Foreign Interference | Bird
3725 | 2003 | 7 | 12 | 0.72431 |  | 32 | 1 | 2 | Moulton | 27.6/16kV | 8F1 | Bird contacted secondary of transformer 3672, fuse blown. Refused and closed. | Gloucester | Foreign Interference | Animal
5490 | 2004 | 7 | 14 | 0.34375 |  | 90 | 104 | 80 | Moulton | 27.6/16kV | 8F1 | Crow contact at transformer caused G320 blue phase fuse to blow. Transformer switch open, G320B replaced crow removed, transformer back on. | Gloucester | Foreign Interference | Bird
12835 | 2008 | 7 | 14 | 0.25208 |  | 132 | 66 | 30 | Moulton | 13.2kV | 8F1 | Switch G190 at Montreal Rd and Becknham Lane opened due to a squirrel contact at transformer X24152 front of 17 Cedar Rd the switch to this transformer was also found blown | Gloucester | Foreign Interference | Animal
18736 | 2011 | 7 | 17 | 0.83333 |  | 1800 | 2370 | 79 | Moulton | 27.6/16kV | 8F1 | G627W found blown. Crew patrolled circuit and found tree contacts. Refused switch and closed to restore power. | Gloucester | Tree Contacts
12889 | 2008 | 7 | 18 | 0.54653 |  | 63 | 4 | 4 | Moulton | 27.6/16kV | 8F1 | Transformer #GL002808 located at 31 Seguin isolated due to bird contact (crow) | Gloucester | Foreign Interference | Bird
18783 | 2011 | 7 | 20 | 0.66736 |  | 89 | 83 | 56 | Moulton |  | 8F1 | At 16:01 crews isolated at section of 8F1 between G137,G781 and G650 blue phase to remove a tree in the primary. | Gloucester | Tree Contacts | Tree Limb Fallen
16522 | 2010 | 7 | 22 | 0.095833 |  | 1 | 35 | 2113 | Moulton | 27.6/16kV | 8F1 | 8F1 & 8F2 were both opened from SCADA to allow crew to open defective CS14688 manually. | Gloucester | Defective Equipment
12932 | 2008 | 7 | 24 | 0.40972 |  | 120 | 18 | 9 | Moulton | 27.6/16kV | 8F1 | Transformer #TP1709 located at 2173 East Acres isolated to replace transformer | Gloucester | Scheduled Outage | Preventive Maintenance
12933 | 2008 | 7 | 24 | 0.38611 |  | 155 | 23 | 9 | Moulton | 27.6/16kV | 8F1 | Transformer T1709R was replaced on 2171 East Acres. | Gloucester | Scheduled Outage
12943 | 2008 | 7 | 25 | 0.74861 |  | 90 | 79 | 81 | Moulton | 27.6/16kV | 8F1 | G627W on the 8F1 found blown. Transformer 3853 cutout also blown. Crews refused G627W and restored overhead transformer. Tree limb contact caused it to blow, 24/7 trimmed in direct area, more trimming required and sent to forestry. | Gloucester | Tree Contacts | Inadequate Trimming
8915 | 2006 | 8 | 2 | 0.94444 |  | 70 | 292 | 250 | Moulton |  | 8F1 | GR9 Auto reclosed. 2 fuses blown at S285 at Montreal Road and Elwood. Crew patrolled circuit, nothing found. Heavy rain and lightning storm was in progress | Gloucester | Adverse Weather | Rain
3836 | 2003 | 8 | 3 | 0.96319 |  | 143 | 2 | 1 | Moulton | 27.6/16kV | 8F1 | Fused cut out to Tx450 at 297 Blair rd N. failed during a lightning storm. The switch was replaced to restore power. | Gloucester | Adverse Weather | Lightning
7088 | 2005 | 8 | 9 | 0.93056 |  | 5 | 1 | 7 | Moulton | 27.6/16kV | 8F1 | Power interrupted to transformer # 4180 at 45 Oriole Dr to replace the hot line clamp | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
8936 | 2006 | 8 | 10 | 0.40139 |  | 99 | 293 | 2019 | Moulton | 27.6/16kV | 8F1 | Switch G521 W phase broke and fell into the primary on Crownhill causing that wire to break off causing the circuit to trip. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14931 | 2009 | 8 | 11 | 0.46181 |  | 55 | 15 | 16 | Moulton | 27.6/16kV | 8F1 | Transformer #X24174 located at 26 Crownhill St Glouc isolated due to truck broke stand pipe & meter base ripped off. Crew had to take service down. | Gloucester | Foreign Interference | Vehicle
7132 | 2005 | 8 | 13 | 0.57639 |  | 70 | 2108 | 1807 | Moulton | 27.6/16kV | 8F1 | GR9 recloser auto-reclosed twice before tripping a third time & locking out. RTU for GR9 was failed at the time of the trip. Overhead patrol revealed no obvious problems. | Gloucester | Unknown/Other | No Apparent Cause
14941 | 2009 | 8 | 13 | 0.4 |  | 780 | 117 | 9 | Moulton | 27.6/16kV | 8F1 | Transformer TE419 at 43 Amberley was isolated to remove oil contaminated soil. 9 customers on Amberly Place were affected. | Gloucester | Scheduled Outage | Repair
14962 | 2009 | 8 | 18 | 0.54861 |  | 333 | 33 | 6 | Moulton | 27.6/16kV | 8F1 | Transformer T419R @ 42 Amberly was isolated for second part of oil spill cleanup. | Gloucester | Scheduled Outage | Repair
18972 | 2011 | 8 | 18 | 0.58194 |  | 345 | 356 | 114 | Moulton | 27.6/16kV | 8F1 | RX2017 Auto Reclosed during lightening storm Crew found later G228B, G256B and G297 blown. Circuit patrolled and | Gloucester | Lightning | Direct Strike
7174 | 2005 | 8 | 20 | 0.39306 |  | 70 | 40 | 34 | Moulton | 27.6/16kV | 8F1 | Dead crow found at T2507 Cedar Rd.with blown cut out. Also G190B blown. Both fuses replaced and power restored. | Gloucester | Foreign Interference | Bird
13136 | 2008 | 8 | 21 | 0.73958 |  | 94 | 82 | 106 | Moulton | 27.6/16kV | 8F1 | Blown lightening arrestor at G137 (normal open) at 1 Rothwell caused G228, G617 and G138 to open | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7192 | 2005 | 8 | 23 | 0.55625 |  | 49 | 3 | 4 | Moulton | 27.6/16kV | 8F1 | Transformer #GL892 located at 53 Rebecca isolated for contractor to do pole testing | Gloucester | Scheduled Outage | Preventive Maintenance
7193 | 2005 | 8 | 23 | 0.54167 |  | 10 | 1 | 5 | Moulton | 27.6/16kV | 8F1 | Transformer #GL3395 located at 78 Rebecca isolated due to contractor doing pole testing | Gloucester | Scheduled Outage | Preventive Maintenance
7199 | 2005 | 8 | 24 | 0.40625 |  | 15 | 2 | 8 | Moulton | 27.6/16kV | 8F1 | Transformer GL3386 at 964 Blair Rd isolated for contractor to do pole testing | Gloucester | Scheduled Outage | Preventive Maintenance
7200 | 2005 | 8 | 24 | 0.4375 |  | 18 | 5 | 17 | Moulton | 27.6/16kV | 8F1 | Transformer GL3387 at 911 Blair Rd isolated for contractor to do pole testing | Gloucester | Scheduled Outage
7204 | 2005 | 8 | 24 | 0.47569 |  | 19 | 4 | 12 | Moulton | 27.6/16kV | 8F1 | Transformer GL3375 at 881 Blair Ed was isolated for contractor to do pole testing | Gloucester | Scheduled Outage | Preventive Maintenance
7206 | 2005 | 8 | 24 | 0.58333 |  | 39 | 6 | 10 | Moulton | 27.6/16kV | 8F1 | Transformer GL514 at 1045 Blair Rd was isolated for contractor to do pole testing | Gloucester | Scheduled Outage | Preventive Maintenance
11145 | 2007 | 8 | 24 | 0.21319 |  | 113 | 47 | 25 | Mouton | 27.6/16kV | 8F1 | S608B single phase overhead run off fused switch on Davidson Rd in Gloucester opened during thunderstorm. No apparent cause found. Switch refused and closed to restore. | Gloucester | Defective Equipment
11146 | 2007 | 8 | 24 | 0.29931 |  | 25 | 8 | 20 | Moulton | 27.6/16kV | 8F1 | S758B single phase overhead run off fused switch on Clovelly Rd in Gloucester opened during thunderstorm. No apparent cause found. Switch refused and closed to restore. | Gloucester | Defective Equipment
16808 | 2010 | 8 | 25 | 0.44236 |  | 4 | 80 | 1200 | Moulton | 27.6/16kV | 8F1 | While crew was performing switching order to isolate RX2017 when the first phase of the G31 pypass was closed the recloser auto reclosed and opened. Power restored when crew closed the remaining 2 phases. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
3946 | 2003 | 8 | 26 | 0.97222 |  | 38 | 1 | 2 | Moulton | 27.6/16kV | 8F1 | Transformer # 002046 on Blair Road north of Montreal Road was opened to allow crews to safely replace a defective transformer switch. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
9068 | 2006 | 8 | 27 | 0.30208 |  | 71 | 5 | 4 | Moulton | 27.6/16kV | 8F1 | Squirrel caused fuse to open in transformer 2590 @ 1426 Innes. | Gloucester | Foreign Interference | Animal
15028 | 2009 | 8 | 29 | 0.90486 |  | 113 | 141 | 75 |  | 27.6/16kV | 8F1 | RX2017 auto reclose, cable fault on red phase cable between T652 and T919 on Bethamy. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
16847 | 2010 | 9 | 1 | 0.36944 |  | 29 | 8 | 17 | MOULTON |  | 8F1 | Transformer X24132 at 911 Blair isolated for testing Bell poles | Gloucester | Scheduled Outage
9114 | 2006 | 9 | 3 | 0.18472 |  | 114 | 163 | 86 | Moulton | 27.6/16kV | 8F1 | Insulators on switch G320 on Montreal Rd failed. Insulators replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13208 | 2008 | 9 | 9 | 0.40139 |  | 70 | 44 | 47 | Moulton | 27.6/16kV | 8F1 | G247R cut out blown and cut out to transformer at 11 Floret. Squirrel nest at top of transformer. Both cut outs replaced. | Gloucester | Foreign Interference | Animal
15126 | 2009 | 9 | 16 | 0.46181 |  | 13 | 427 | 1972 | Moulton | 27.6/16kV | 8F1 | Hydro crew reported they were closing in a 3 phase customer bank for temp construction site on Rainbow St off Shefford and requested hold off protection on the feeding circuit. During the task of closing in the three phase bank, RX2017 opened under hold off protection. Crew opened switches feeding bank and RX2017 closed restoring customers. With reclosing in effect crew was able to energize bank after inspection of the transformer bank. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19186 | 2011 | 9 | 16 | 0.39583 |  | 60 | 8 | 8 | Moulton | 27.6/16kV | 8F1 | Transformer #X24167 located at 9 Elvina St opened up due to secondary buss slack in neutral, caused the fuse to blow | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4091 | 2003 | 9 | 18 | 0.58333 |  | 58 | 3 | 3 | Moulton | 27.6/16kV | 8F1 | R. Barnett reports transformer 3278 at 1485 Jarvis opened for maintence. Outage effected 3 customers. All power was restored at 14:58. | Gloucester | Scheduled Outage
15173 | 2009 | 9 | 27 | 0.96944 |  | 34 | 3 | 6 | Moulton | 27.6/16kV | 8F1 | At 23:16 transformer at 25 Wipoorwill was isolated to allow Asplund to clear fallen limb from tx secondary. Moulton 8F1 ID# 15173. | Gloucester | Tree Contacts | Tree Limb Fallen
5824 | 2004 | 10 | 3 | 0.55903 |  | 20 | 4 | 13 | Moulton | 27.6/16kV | 8F1 | Elbow inoperable at TE914 during switching for cable isolation to repair defective cable. Outage required to pull by hand. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15222 | 2009 | 10 | 6 | 0.29028 |  | 159 | 86 | 47 | Moulton | 27.6/16kV | 8F1 | RX2017 on Blair Rd. auto reclosed when a transformer cut out at 10 Elvina faulted it also caused the G247R fuse to blow. G247 was refused and closed restoring all load except transformer 2809 at 10 Elvina, which was repaired and then restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13404 | 2008 | 10 | 21 | 0.62361 |  | 199 | 282 | 106 | Moulton | 27.6/16kV | 8F1 | a willow tree on Delong made contact and caused 2 fuses and a transformer cutout to blow. Refused in stages and cut outs replaced on 8F1 blue phase at GR7 | Gloucester | Tree Contacts | Tree Limb Fallen
17168 | 2010 | 10 | 25 | 0.46875 |  | 75 | 5 | 4 | MOULTON | 27.6/16kV | 8F1 | Transformer X24771 at 17 Davidson Dr isolated to allow for transformer upgrade | Gloucester | Scheduled Outage | Construction
4360 | 2003 | 10 | 30 | 0.84722 |  | 12 | 1 | 7 | Moulton | 27.6/16kV | 8F1 | Transformer 2244 at 6 Amberly isolated to repair defective line clamp. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5869 | 2004 | 11 | 8 | 0.43264 |  | 95 | 21 | 13 | Moulton | 27.6/16kV | 8F1 | To replace a defective T981 transformer Bethamy Lane. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13641 | 2008 | 11 | 19 | 0.67014 |  | 105 | 7 | 4 | Moulton | 27.6/16kV | 8F1 | Transformer #TP2291 located at 23 Steel isolated due to animal interference, refused transformer switch | Gloucester | Foreign Interference | Animal
19618 | 2011 | 11 | 22 | 0.51597 |  | 251 | 42 | 10 | MOULTON | 27.6/16kV | 8F1 | Transferring plant to new pole. | Gloucester | Scheduled Outage | Preventive Maintenance
7648 | 2005 | 11 | 23 | 0.50833 |  | 146 | 2 | 1 | Moulton | 27.6/16kV | 8F1 | Transformer TE2938 at 2401 City Park in Gloucester defective and replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13699 | 2008 | 12 | 4 | 0.48472 |  | 24 | 3 | 7 | Moulton | 27.6/16kV | 8F1 | G579B & G580B including TE1204 at 4758 Donovan were isolated to replace defective fused switches. | Gloucester | Scheduled Outage | Repair
19701 | 2011 | 12 | 8 | 0.3875 |  | 135 | 22 | 10 | Moulton | 27.6/16kV | 8F1 | Transformer TE1710 at 2163 East Acres Rd was isolated to allow crew to replace leaking transformer. Moulton (8F1). | Gloucester | Scheduled Outage | Preventive Maintenance
17401 | 2010 | 12 | 10 | 0.38542 |  | 60 | 6 | 6 | Moulton | 27.6/16kV | 8F1 | Transformer #X24762 located at 17 Cedar Rd opened by crew to repair bushings | Gloucester | Scheduled Outage | Construction
9849 | 2006 | 12 | 15 | 0.42083 |  | 135 | 22 | 10 | Goulburn | 27.6/16kV | 8F1 | New cable section installed to TP4268, part of cable replacement program. | Gloucester | Scheduled Outage | Construction
9857 | 2006 | 12 | 18 | 0.65278 |  | 147 | 117 | 50 | Moulton | 27.6/16kV | 8F1 | Fuse blew at G52W interrupting power to 5 transformers in Rothwell Heights. Fault indicators indicated a cable fault between T1686 & T1393. The defective cable was isolated & power restored. The affected customers were on Burrows Rd, Veery Lane & Bracken Crt. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15527 | 2009 | 12 | 18 | 0.48194 |  | 9 | 295 | 1964 | Moulton | 27.6/16kV | 8F1 | At 11:34am RX2017 operated and locked out (RX2017 was under holdoff), while crew tried to energize the secondary of TP6678 on Rainbow Street. Crew verified secondary connections and transformer (megger & TTR test) and re-tried to pick up transformer. RX2017 auto reclosed and held on final energization. Beaconhill (RX2017, 3F4). ID#15527. | Gloucester | Unknown/Other | No Apparent Cause
6083 | 2004 | 12 | 21 | 0.43958 |  | 26 | 77 | 189 | Moulton | 27.6/16kV | 8F1 | GR15 tripped due to overload - Settings to low - System not aware of. | Gloucester | Human Element | Incorrect Use of Equipment
9870 | 2006 | 12 | 21 | 0.40833 |  | 402 | 34 | 5 | Moulton | 27.6/16kV | 8F1 | Transformer T1686W on Burrows Rd in Gloucester isolated to complete repairs to faulted cable. | Gloucester | Scheduled Outage
13801 | 2008 | 12 | 27 | 0.86806 |  | 272 | 113 | 25 | Moulton | 27.6/16kV | 8F1 | The fire dept request the O/H line on St Joseph at the house fire 1300 St Joseph Blvd to be isolated for safety reasons | Gloucester | Adverse Environment | Fire
11073 | 2007 | 8 | 15 | 0.73819 |  | 337 | 603 | 125 | Moulton | 27.6/16kV | 8F1 (GR7) | Fused cut-out at Tx 546, 42 Delong blew causing G297B , G228B & GR7 all to open. Line was patrolled & found clear. Line was picked up in sections & Tx 546 tested to restore all customers. Cut-out at Tx 546 was flashed but no sign of animal contact. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10234 | 2007 | 4 | 10 | 0.52083 |  | 60 | 1 | 1 | Moutlon | 27.6/16kV | 8F1 (GR9 ) | Crew investigating all out at 1426 St Joseph, RCMP complex, found cracked switch @ G732. The switch was isolated & all 3 phases replaced. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10760 | 2007 | 6 | 29 | 0.35347 |  | 104 | 17 | 10 | Moulton | 27.6/16kV | 8F1 (GR9) | Transformer #GL005607 located at 3 Seguin isolated due to animal contact | Gloucester | Foreign Interference | Animal
11325 | 2007 | 9 | 17 | 0.64792 |  | 59 | 1 | 1 | Moulton | 27.6/16kV | 8F1 (GR9) | Defective switch & arrestor caused 2 earlier recloses on GR9. Switch was isolated & replaced | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14577 | 2009 | 6 | 20 | 0.2625 |  | 158 | 248 | 105 | Moulton | 27.6/16kV | 8F1 (RX2017) | RX2017 auto reclosed due to crow contact on Rothwell dr causing G228 and G297 fuses to blow. | Gloucester | Foreign Interference | Animal
17969 | 2011 | 4 | 19 | 0.23264 |  | 27 | 1398 | 3800 | Moulton | 27.6/16kV | 8F1, 8F3 | B1 Bus between Moulton T1 and low side switch flashed causing High Side to open losing 8F1 and 8F3 feeder customers. Backfeed from Bilberry and Cyrville used to restore all customers. Damage is under investigation. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15692 | 2010 | 1 | 29 | 0.39236 |  | 75 | 59 | 47 | Moulton | 27.6/16kV | 8F2 | The 8F2 circuit auto reclosed because the stress cone at G525B phase blew at 1352 Ogilive Rd | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3152 | 2003 | 2 | 1 | 0.80208 |  | 255 | 4 | 1 | Moulton | 27.6/16kV | 8F2 | Customer reports partial power. 24/7 crew reports blown fuse on transformer bank. Fuse replaced power restored. | Gloucester | Adverse Weather | Snow
17577 | 2011 | 2 | 14 | 0.96597 |  | 458 | 5367 | 1100 | Moulton | 27.6/16kV | 8F2 | Overhead conductor burnt down and made contact with a bank of overhead transformers. Oncall crew dispatched to made repairs to conductor, and replace blown transformer. Crew also replaced insulators on circuits which were cracked and about to fail. | Gloucester | Adverse Weather | Rain
14003 | 2009 | 2 | 25 | 0.39931 |  | 35 | 1 | 1 | Moulton | 27.6/16kV | 8F2 | At 09:35 transformer at corner of PALMERSTON DR/OGILVIE RD GLOU was isolated to replace a broken cutout | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
3223 | 2003 | 3 | 2 | 0.49306 |  | 274 | 5 | 1 | MOULTON | 27.6/16kV | 8F2 | TF#563 AT 1290 OGILVIE ROAD FEEDING ONE CUSTOMER A CHURCH WAS CHANGED DUE TO TRANSFORMER BEING DEFECTIVE | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
15814 | 2010 | 3 | 16 | 0.57986 |  | 385 | 90 | 14 | Moulton | 27.6/16kV | 8F2 | T2345 at 1330 Ogilvie Rd was isolated to replace the leaking transformer and excavate contaminated soil from the site. | Gloucester | Scheduled Outage | Repair
8193 | 2006 | 4 | 27 | 0.90625 |  | 534 | 536 | 70 | Moultan | 27.6/16kV | 8F2 | Cable fault between T840 and T844 on the white phase of 8F2 | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5143 | 2004 | 5 | 13 | 0.69792 |  | 45 | 1 | 1 | MOULTON | 27.6/16kV | 8F2 | Transformer # GL585 opened to allow crew to renew connection at transformer. Outage affected 1 customer at 1200 Ogilvie Rd. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
16519 | 2010 | 7 | 21 | 0.89583 |  | 441 | 978 | 133 | Moulton | 27.6 KV | 8F2 | G544 @ 1330 Ogilvie Rd opened due to Lightning strike. ON Call crew reports dammage to lightning arrestor, insulator and switch. 1330 Customer were affected. | Gloucester | Lightning | Lightning Strike on Adjacent Circuit Flashed Over
16520 | 2010 | 7 | 21 | 0.89583 |  | 495 | 1402 | 170 | Moulton | 27.6KV | 8F2 | G-203 at 1569 Marley Cres was struck by lightning causing the fuse to open. | Gloucester | Lightning | Direct Strike
16525 | 2010 | 7 | 22 | 0.095833 |  | 1 | 12 | 708 | Moulton | 27.6/16kV | 8F2 | 8F1 & 8F2 were both opened from SCADA to allow crew to open defective CS14688 manually. | Gloucester | Defective Equipment
16540 | 2010 | 7 | 22 | 0.89583 |  | 1135 | 1089 | 65 | Moulton | 27.6/16kV | 8F2 | A lightning strike at G203 caused the R phase fuse to blow & during restoration it was found that TE2707 at 1611 Marley was defective. The other 4 transformers were restored, however a second defective transformer, TE2710 at 1640 Jobin caused S11RT2715 to blow resulting in an outage to all 5 transformers in the loop. TE2707 was replaced & the loop partially restored. TE2710 was replaced & loop restored to normal. | Gloucester | Lightning | Lightning Strike on Adjacent Circuit Flashed Over
16685 | 2010 | 8 | 6 | 0.42083 |  | 333 | 78 | 14 | Moulton | 27.6/16kV | 8F2 | Transformer at 1590 Marley was isolated to allow crew to clean up oil spill. | Gloucester | Scheduled Outage | Preventive Maintenance
16719 | 2010 | 8 | 12 | 0.40694 |  | 444 | 81 | 11 | Moulton | 27.6/16kV | 8F2 | TE2710 at 1640 Jobin isolated to clean up oil contaminated soil. 11 customers on Jobin affected. | Gloucester | Scheduled Outage
16757 | 2010 | 8 | 17 | 0.15417 |  | 134 | 125 | 56 | Moulton | 27.6/16kV | 8F2 | 24/7 found FCI faulted at T845 @ 1450 Palmerston. Cable section between T845 & T1326 was isolated due to defective underground. | Gloucester | Defective Equipment
16764 | 2010 | 8 | 17 | 0.43333 |  | 688 | 161 | 14 | Moulton | 27.6/16kV | 8F2 | TE2707 at 1590 Marley was isolated to allow Drain All & Greely to remove T2707 and base to remove contaminated soil. | Gloucester | Scheduled Outage | Preventive Maintenance
15031 | 2009 | 8 | 30 | 0.60764 |  | 245 | 33 | 8 | Moulton | 27.6/16kV | 8F2 | Reports of power problems on Chicory, electrician on site reported transformer lid had blown and smoking. 24/7 dispatched and transformer isolated. On call changed out defective transformer. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4106 | 2003 | 9 | 19 | 0.68611 |  | 392 | 72 | 11 |  | 27.6/16kV | 8F2 | Blown Transformer, at 1138 Ambercrest Drive. Transformer #GLTE2604 was found defective and needed to be replaced. |  | Defective Equipment
7742 | 2005 | 12 | 16 | 0.78611 |  | 124 | 27 | 13 | Moulton |  | 8F2 | Transformer GLTE1326 at 1477 Palmerston was isolated at the request of the Fire dept due to a fire at 1473 | Gloucester | Adverse Environment | Fire
11944 | 2008 | 1 | 16 | 0.67708 |  | 20 | 27 | 80 | Moulton | 27.6/16kV | 8F3 | During an OTO to restore TE686 on Stonehenge red phase fuse blew at the N.O. point. Customers restored by checking open at transformer and closing back in Red phase at open point switch. Blown arresters found at G564. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
17489 | 2011 | 1 | 17 | 0.39375 |  | 132 | 2910 | 1686 | Moulton | 27.6/16kV | 8F3 | 8F3 circuit auto-reclosed and locked out. Circuit was sectionalized using CS24139 via SCADA. Half of the load was picked up after reciveing no OMS, Fire or Police calls. Second half of load was picked up shortly after and held until 09:13 when the circuit auto-reclosed. At 09:18 the circuit auto-reclosed and locked out. Problem found to be a broken insulator at G322 (1400 Appleton) Half of the load was then picked up from CS24139 while crews used live line techniques to replace the insulator. Remaining load was picked up once repairs completed. | Gloucester | Defective Equipment
13908 | 2009 | 1 | 30 | 0.97986 |  | 449 | 30 | 4 | Moulton | 27.6/16kV | 8F3 | 27kV transformer at 1901 Cyrville TE3114 isolatoed to allow crew to transfer riser cables from and old pole to a new pole. | Gloucester | Scheduled Outage | Construction
13909 | 2009 | 1 | 30 | 0.97986 |  | 449 | 52 | 7 | Moulton | 27.6/16kV | 8F3 | 27kV transformer at 1750 Inness, TE2861 isolatoed to allow crew to transfer riser cables from and old pole to a new pole. | Gloucester | Scheduled Outage | Construction
6163 | 2005 | 2 | 1 | 0.42847 |  | 273 | 32 | 7 | Moulton | 27.6/16kV | 8f3 | Defective transformer at TE2861 (leaking oil) blew fuse at G123 and G705 Red phase. 2 terminations replaced at G123. | Gloucester | Defective Equipment
12004 | 2008 | 2 | 2 | 0.42847 |  | 76 | 120 | 95 | Moulton | 27.6/16kV | 8F3 | G319 at Stonehenge and Whittaker blew a white phase fuse losing 7 transformers. Cable section isolated and all customers restored from backfeed. | Gloucester | Unknown/Other | No Apparent Cause
3156 | 2003 | 2 | 4 | 0.50347 |  | 151 | 96 | 46 | Moulton MS | 27.6/16kV | 8F3 | Faulted underground cable on the 8F3 in section between T1167RG502 and G502R. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9999 | 2007 | 2 | 7 | 0.53125 |  | 85 | 23 | 16 | Star Top | 27.6/16kV | 8F3 | Isoalted transformer GL004038 at 1364 Aurele St to replace pole | Gloucester | Scheduled Outage | Construction
10006 | 2007 | 2 | 10 | 0.32639 |  | 100 | 11 | 12 | Moulton | 8/4.8kV | 8F3 | Bird contacted switches feeding 1951 Cyrville, pumping station, and caused G705 B and 272 B to blow. | Gloucester | Foreign Interference | Animal
17574 | 2011 | 2 | 12 | 0.54167 |  | 335 | 240 | 114 | Moulton | 27.6/16kV | 8F3 | Defective transformer #T615 at 2099 Stonehenge caused G319W phase fuse to blow. Outage to 114 customers in the Stonehenge area. 94 Customers were restored as of 14:32, and T615 was isolated. Transformer was replaced and remaining load was restored as of 18:35 on 8F3 circuit. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15739 | 2010 | 2 | 23 | 0.32639 |  | 435 | 377 | 52 | Moulton | 27.6/16kV | 8F3 | There was a pole fire at switch G502 @ 1471 Blair Rd causing the pole to drop down hitting the neutral causing a surge through the cable making G322 W phase to blow. | Gloucester | Adverse Environment | Fire
10068 | 2007 | 2 | 26 | 0.61806 |  | 27 | 46 | 102 | Moulton | 27.6/16kV | 8F3 | G650 blue phase fuse blew during K-line's pressure washing of the insulators & switch, interrupting power to customers on Eastcliffe, Cedarcroft, Alness & Baintree. 24/7 refused it successfully restoring power to all affected customers. | Gloucester | Human Element
10089 | 2007 | 3 | 5 | 0.47917 |  | 642 | 11 | 2 | Moulton | 27.6/16kV | 8F3 | Crews found blue phase fuse opened @ G854. Power was restored to VE66 Telestat @ 12:45. VE80 MBNA was isolated to allow contractor to check main bus & secondary busses. J. Robinson reports a Squirrel found in s3 cell#8 at MBNA vault. Contractor will repair flash marks & will clean and torque vault. | Gloucester | Foreign Interference | Animal
20144 | 2012 | 3 | 9 | 0.39583 |  | 50 | 4 | 5 | Moulton | 27.6/16kV | 8F3 | Transformer X24192 at 1302 Aurele St was isolated in order to replace the transformer it was rusting out | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
10424 | 2007 | 5 | 16 | 0.85208 |  | 122 | 170 | 90 | Moulton | 27.6/16kV | 8F3 | Blue phase cable fault between TE1666 & Te1667 on Saxony Cres. Night shift crew had to find a truck to respond to this outage. Both 24/7 truck were in Kanata at this time. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
20536 | 2012 | 5 | 17 | 0.75069 |  | 162 | 84 | 31 | Moulton | 27.6/16kV | 8F3 | Bird contact caused a transformer fuse and line fuse G916 to blow on Aurele St | Gloucester | Foreign Interference | Bird
5185 | 2004 | 5 | 19 | 0.95625 |  | 78 | 88 | 68 | Moulton | 27.6/16kV | 8F3 | Fault indicators incate possible fault TE1422w to G649 in Pineview cable isolated crews to check cables in the morning | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16142 | 2010 | 5 | 25 | 0.55139 |  | 15 | 304 | 1216 | Moulton | 27.6/16kV | 8F3 | CS24139 on Telesat Court opened for no apparent reason, cause still under investigation. Switch was closed successfully from SCADA restoring all load. | Gloucester | Unknown/Other
6648 | 2005 | 6 | 3 | 0.1875 |  | 75 | 62 | 50 | Moulton | 27.6/16kV | 8F3 | Burnt termination found at G972 blue phase. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10569 | 2007 | 6 | 8 | 0.83958 |  | 144 | 29 | 12 | Moulton | 27.6/16kV | 8F3 | Tree contact caused a phase of G705 switch at innes & cyrville and a transformer feeding the city yard on cyrville to open. | Gloucester | Tree Contacts | Inadequate Trimming
5269 | 2004 | 6 | 9 | 0.40556 |  | 111 | 22 | 12 | Beacon Hill | 8/4.8kV | 8F3 | Transformer TE537 at 733 Ludgate isolated and replace due defective secondary winding. 8F3 | Gloucester | Scheduled Outage | Repair
18398 | 2011 | 6 | 13 | 0.98125 |  | 61 | 108 | 106 | Moulton | 27.6/16kV | 8F3 | Vines growing up pole and all the rain caused G319W to blow. Vines celared refused and closed. | Gloucester | Unknown/Other
18432 | 2011 | 6 | 17 | 0.2625 |  | 182 | 291 | 96 | Moulton | 27.6/16kV | 8F3 | Squirrel caused G520R and G519R on Meadowbrook to open. Crew refused and closed. | Gloucester | Foreign Interference | Animal
5329 | 2004 | 6 | 18 | 0.61111 |  | 130 | 24 | 11 | Moulton | 27.6/16kV | 8F3 | G153 W phase connection to overhead found burnt off. G153 RWB all three phases opened to allow repairs at 1880 to 1900 Innes Rd. RONA, Dennys, McDonalds. Termination replaced and power on and checked. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10678 | 2007 | 6 | 20 | 0.24028 |  | 232 | 447 | 130 | Moulton | 27.6/16kV | 8F3 | A cable fault between TE764 & TE791 caused G519 W on Meadowbrook dr. to open. Defective section isolated & power restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16306 | 2010 | 6 | 21 | 0.87431 |  | 157 | 175 | 67 | Moulton | 27.6/16kV | 8F3 | Cable fault between T1427 and T1428 at Moulton | Gloucester | Defective Equipment
10739 | 2007 | 6 | 26 | 0.38542 |  | 15 | 45 | 181 | Moulton | 27.6/16kV | 8F3 | TE651 at 1400 Appleton was isolated for Dan Can Electric to perform maintenance on the customer's secondary main. During the switching process 180 customers were inadvertantly interrupted. | Gloucester | Scheduled Outage | Preventive Maintenance
12771 | 2008 | 6 | 30 | 0.42708 |  | 55 | 16 | 17 | Moulton | 27.6/16kV | 8F3 | Refused blown switch to transformer GL5754 at 1319 Maxime St (Outage caused by a Pigeon) | Gloucester | Foreign Interference | Bird
8635 | 2006 | 7 | 1 | 0.0625 |  | 150 | 2 | 1 | Moulton | 27.6/16kV | 8F3 | Transformer T2498 @ 1900 Innes Rd was isolated because it was leaking. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
6860 | 2005 | 7 | 3 | 0.39097 |  | 73 | 83 | 68 | Moulton | 27.6/16kV | 8F3 | Bad white phase cable section between T1422 & G649 on 8F3 circuit. In the area ot Marigold & Cedarcroft. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10808 | 2007 | 7 | 6 | 0.67292 |  | 99 | 41 | 25 | MOULTON MS | 27.6/16kV | 8F3 | Fuse on switch G916 at 1306 Aurele St was found blown due to a bird contact | Gloucester | Foreign Interference | Bird
10814 | 2007 | 7 | 8 | 0.25764 |  | 64 | 123 | 115 | Moulton | 27.6/16kV | 8F3 | Blown Transformer fuse at 5679 Leblanc caused G918R to blow. Transformer and switch refused, all power restored. | Gloucester | Defective Equipment
16427 | 2010 | 7 | 8 | 0.0041667 |  | 326 | 415 | 96 | Moulton | 27.6/16kV | 8F3 | Customer reported outage in Meadow brook area, ON-call in to patroll line, found G533 RED phase blown. Found FCI's flagged at TE1395 & TE1396. TE1313 FCI clear. Isolated cable and restored power from V32. Crews found G520 RED Phase was damaged, suspect from cable fault. Additional patrol found G519 Red Phase blown as well. G520 isolated/ repaired and all power restored | Gloucester | Defective Equipment
3710 | 2003 | 7 | 9 | 0.33681 |  | 50 | 13 | 16 | Moulton | 27.6/16kV | 8F3 | Power was interupted to the transformer bank to allow the Fire Department to extiguish a pole fire and clear a burnt squirrel. The crew then inspected the plant and relocated the apparatus to ensure a solid anchor point on the damaged pole until the pole can be replaced. | Gloucester | Foreign Interference | Animal
14691 | 2009 | 7 | 10 | 0.32639 |  | 2030 | 34 | 1 | Moulton | 27.6/16kV | 8F3 | TP2875 at Telesat was isolated due to water in the secondary room. | Gloucester | Foreign Interference | Foreign Object
14781 | 2009 | 7 | 18 | 0.81806 |  | 214 | 336 | 110 | Moulton | 27.6/16kV | 8F3 | A crow caused local switch G918R on Maxime to open, as well as one overhead transformer at 1435 Maxime. | Gloucester | Foreign Interference | Animal
5614 | 2004 | 8 | 5 | 0.26042 |  | 302 | 444 | 105 | Moulton | 27.6/16kV | 8F3 | Andy Found G650R blown, then inspected the transformers with fault indicators. Found fault indicator at transformer T1407RT1421 flagged. Then found not fault at T1421RT1407 and started to restore. Pick up 71 customers from G650R. While picking up the T1421R by G649R, the fuse blew and also blew G520R causing another outage of 96 customers. Mike Byers refused G520R and holding . 24/7 found cable fault between G649R and T1421R all in the Cedarcroft, Birchmount and Marigold area. More calls came in and Denis Martin found G519R blown which is up stream from G520R, he patrol and found nothing all power restored by 11:17. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7108 | 2005 | 8 | 10 | 0.75 |  | 120 | 6 | 3 | moulton | 27.6/16kV | 8F3 | G705 RWb fuses found opened. Fuses replaced and closed power restored to 3 customers on Innes & Cryville. | Gloucester | Adverse Weather | Lightning
5672 | 2004 | 8 | 13 | 0.38681 |  | 37 | 71 | 115 | Moulton | 27.6/16kV | 8F3 | Dave reports squirrel found at base of transformer #302. Fuse replaced and closed, also G918R refused and closed restoring power to 115 customers. | Gloucester | Foreign Interference | Animal
7259 | 2005 | 9 | 1 | 0.48264 |  | 5 | 1 | 9 | Moulton | 27.6/16kV | 8F3 | Transformer GLTE1310 at 1482 Bortolotti Dr was isoalted to repair service | Gloucester | Scheduled Outage | Repair
4052 | 2003 | 9 | 11 | 0.38333 |  | 78 | 20 | 15 | Moulton | 8/4.8kV | 8F3 | TE0618 isolated for electrician to fix 120 volt leg that was heating up and insulation was melting. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
4077 | 2003 | 9 | 17 | 0.46042 |  | 50 | 11 | 13 | Moulton | 27.6/16kV | 8F3 | Transformer #000831 at 1345 Maxime Street in Gloucester was isolated to allow for its replacement due to it leaking oil. | Gloucester | Scheduled Outage | Preventive Maintenance
11436 | 2007 | 10 | 2 | 0.21736 |  | 147 | 127 | 52 | Moulton | 27.6/16kV | 8F3 | Failed cable section. 24/7 responded to 4323 Meadowvale for further inspection; located failed section & isolated. Power restored to all 52 customers @ 07:40; permit to be made up for cable repair. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
4202 | 2003 | 10 | 3 | 0.39583 |  | 90 | 3 | 2 | Moulton | 8/4.8kV | 8F3 | Overhead tansformer supply moved to new location on the same line. | Gloucester | Scheduled Outage | Construction
19386 | 2011 | 10 | 16 | 0.37708 |  | 207 | 271 | 110 | Moulton MS | 27.6/16kV | 8F3 | G918 failed, causing an outage on the 8F3 red phase to 110 customers. Crew patrolled the line & found an open transformer fuse and G918 open. Crew inspected G918 and found it defective. To restore power crew had to open G917, causing an outage to an additional 46 customers, so that they could jumper out G918. Crew picked up all load except the O/H transformer through G917. After inspecting the transformer, crew refused and restored all power. | Gloucester | Unknown/Other | No Apparent Cause
13593 | 2008 | 11 | 12 | 0.40208 |  | 76 | 13 | 10 | MOULTON | 27.6/16kV | 8F3 | Replaced blown fuse feeding transformer GL831 at 1345 Maxime St (Cause unknown) | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19591 | 2011 | 11 | 17 | 0.39722 |  | 240 | 4 | 1 | Moulton | 27.6/16kV | 8F3 | Transformer TE651 at 1400 Apleton was isoalted to allow crew to replace leaking transformer. 1 customer was affected for 240 minutes. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
15406 | 2009 | 11 | 21 | 0.45139 |  | 235 | 55 | 14 | Moulton | 27.6/16kV | 8F3 | Transformer #TE3051 located at 1880 Innes Rd isolated to re-arrange plant | Gloucester | Scheduled Outage | Construction
17398 | 2010 | 12 | 9 | 0.45833 |  | 135 | 11 | 5 | Moulton | 27.6/16kV | 8F3 | Transformer #TP5743 located at 999 Torovin opened by crew to replace transformer | Gloucester | Scheduled Outage | Construction
13743 | 2008 | 12 | 12 | 0.98264 |  | 365 | 36 | 6 |  | 27.6/16kV | 8F3 | Radial overhead on Cyrville at Innes was isolated to allow construction of new overhead | Gloucester | Scheduled Outage | Construction
7731 | 2005 | 12 | 15 | 0.55 |  | 30 | 5 | 10 | Manordale | 27.6/16kV | 8F3 | Transformer #TE627 located at 4613 Carrington located to re-secure meter bases | Ottawa | Scheduled Outage | Preventive Maintenance
7732 | 2005 | 12 | 15 | 0.43056 |  | 60 | 10 | 10 | Moulton | 27.6/16kV | 8F3 | Transformer #TE624 located at 2124 Canberra isolated to re-secure meter bases | Gloucester | Scheduled Outage | Preventive Maintenance
7733 | 2005 | 12 | 15 | 0.53125 |  | 26 | 4 | 10 | Moulton | 27.6/16kV | 8F3 | Transformer T630 at 4588 Carrington Place was isolated to re-secure meter bases | Gloucester | Scheduled Outage | Preventive Maintenance
7734 | 2005 | 12 | 15 | 0.44792 |  | 38 | 6 | 10 | Moulton | 27.6/16kV | 8F3 | Transformer TE623 at 4577 Carrington Place was isolated to re-secure meter bases | Gloucester | Scheduled Outage | Preventive Maintenance
7735 | 2005 | 12 | 15 | 0.4125 |  | 40 | 5 | 8 | Moulton | 27.6/16kV | 8F3 | Transformer TE629 at 2135 Bowbank was isolated to re-secure meter bases | Gloucester | Scheduled Outage | Preventive Maintenance
9861 | 2006 | 12 | 18 | 0.79444 |  | 46 | 1307 | 1705 | Moulton | 27.6/16kV | 8F3 | 8F3 load was being carried fron 8F4 throught G485 due to 8F3 breaker maintenance. G485 was opened by 24/7 and breaker closed. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9918 | 2007 | 1 | 11 | 0.43472 |  | 181 | 6 | 2 | Moulton | 27.6/16kV | 8F4 | TE2322 and TE2323 on Blair Road were isolated for replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
9932 | 2007 | 1 | 16 | 0.44792 |  | 28 | 7 | 15 | Moulton | 27.6/16kV | 8F4 | Isolated a Transformer at Beaconhill/Bethamy Lane to megger a sevrice | Ottawa | Scheduled Outage | Preventive Maintenance
4740 | 2004 | 1 | 28 | 0.39931 |  | 137 | 5 | 2 | Moulton | 27.6/16kV | 8F4 | To splice broken conductor and replace the broken switches | Gloucester | Scheduled Outage | Repair
4910 | 2004 | 3 | 17 | 0.48958 |  | 167 | 3 | 1 | Moulton | 27.6/16kV | 8F4 | Step down transformer #T2628 isolated at V31 isolated due to oil leak. V31 re-engized via 3F8 circuit. Transformer to be repaired and re-energized. 8F4 circuit to be restored to normal. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
8094 | 2006 | 4 | 2 | 0.74514 |  | 252 | 38 | 9 | Moulton | 8/4.8kV | 8F4 | Transformer GL5613 fuse was blown. Crew refused and held. 9 Customers affected on Elmlea. | Gloucester | Defective Equipment
4961 | 2004 | 4 | 3 | 0.66319 |  | 40 | 1 | 1 | Moulton | 27.6/16kV | 8F4 | M. Byers reports flash at G854 when attaching grounds to neutral. G865 red phase fuse found blown. Fuse replaced and closed. | Gloucester | Human Element | Incorrect Use of Equipment
8103 | 2006 | 4 | 4 | 0.54931 |  | 79 | 12 | 9 | Moulton | 8/4.8kV | 8F4 | Transformer GL5613 fuse was blown. Due to squirrel Crew refused and restored power 9 Customers affected on Elmlea. | Gloucester | Foreign Interference | Animal
6366 | 2005 | 4 | 5 | 0.98403 |  | 113 | 945 | 900 | Moulton | 27.6/16kV | 8F4 | Faulted Cable between vault VE64 at Gloucester Centre and G861SM at City Park & Ogilvie caused 8F4 bkr to trip auto. Circuit sectionalized and restored in two sections. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3329 | 2003 | 4 | 10 | 0.42292 |  | 1 | 1 | 80 | MOULTON | 27.6/16kV | 8F4 | The crew switching for a scheduled outage to TE21B at 1807 Cloverlawn were unable to pull the elbow at TE23B safely at step 2 of OTO due to lack of clearance. The crew opened G55B to pull it dead causing a 1 min. outage to 80 customers on Cloverlawn & Elmlea. | Gloucester | Scheduled Outage | Preventive Maintenance
3330 | 2003 | 4 | 10 | 0.42361 |  | 176 | 29 | 10 | MOULTON | 27.6/16kV | 8F4 | TE21B at 1807 Cloverlawn isolated for replacement of elbows & inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
3331 | 2003 | 4 | 10 | 0.54375 |  | 2 | 3 | 80 | Moulton | 8/4.8kV | 8F4 | Customer outage to replace elbows and inserts, tight area for switching required outage to customers. | Gloucester | Scheduled Outage | Preventive Maintenance
18377 | 2011 | 6 | 9 | 0.56597 |  | 541 | 9 | 1 | MOULTON | 27.6/16kV | 8F4 | TE1494 (Canadian Tire) on Ogilvie Road isolated to replace leaking transformer. | Gloucester | Defective Equipment
10635 | 2007 | 6 | 15 | 0.40972 |  | 120 | 6 | 3 | Moulton | 27.6/16kV | 8F4 | Transformer located at 2026 Ogilvie isolated due to bird interference | Gloucester | Foreign Interference | Bird
12666 | 2008 | 6 | 16 | 0.39236 |  | 150 | 2 | 1 | Moulton | 8/4.8kV | 8F4 | PC10A004476 was put into effect on switch G531 for the isolation of VE45 to replace a defective transformer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10714 | 2007 | 6 | 23 | 0.275 |  | 271 | 14 | 3 | Moulton | 27.6/16kV | 8F4 | Animal contact (squirrel) caused transformer 16838 to open. | Gloucester | Foreign Interference | Animal
10842 | 2007 | 7 | 10 | 0.80278 |  | 89 | 159 | 107 | MOULTON | 27.6/16kV | 8F4 | G496R caused fuse to blow suspect animal contact damage to switch and caused arrester to blow, and autoreclose on the 8F4 circuit. Arrester and switch replaced, and switch closed to restore power. Meadowbrook, Ballard area. | Gloucester | Defective Equipment
7044 | 2005 | 7 | 31 | 0.22361 |  | 66 | 1 | 1 | Moulton | 27.6/16kV | 8F4 | 1 Transformer of 3 phase bank was leaking oil at T370. Replaced transformer and closed. | Gloucester | Defective Equipment
5615 | 2004 | 8 | 5 | 0.76667 |  | 156 | 26 | 10 |  | 27.6/16kV | 8F4 | LLC's burnt off at transformer, and transformer defective #5702. | Gloucester | Defective Equipment
7080 | 2005 | 8 | 6 | 0.70972 |  | 77 | 74 | 58 | Moulton | 27.6/16kV | 8F4 | Ottawa Fire reports an unbrella has been blown up into the overhead circuit @ 2016 Ogilvie Rd. W. Ried reports 2 fuses found blown at this location G334. An unbrella from Gabriel pizza caused outage. | Gloucester | Foreign Interference | Foreign Object
17031 | 2010 | 9 | 30 | 0.425 |  | 415 | 7 | 1 | Moulton | 27.6/16kV | 8F4 | GLVE13 at 2017 Jasmine was isolated for the customer to make emergency repairs to secondary main. They will also perform routine vault maintenance during shut down. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5822 | 2004 | 10 | 2 | 0.51736 |  | 5 | 1 | 10 | Moulton | 27.6/16kV | 8F4 | Secondary cable fault. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
19407 | 2011 | 10 | 18 | 0.70278 |  | 155 | 310 | 120 |  |  | 8F4 | Cable fault between TE918 and TE652. Moulton (8F4) ID#19407 | Goulburn | Defective Equipment
19447 | 2011 | 10 | 23 | 0.18472 |  | 169 | 907 | 618 | Moulton | 27.6/16kV | 8F4 | SE11 hit by vehicle, had to be isolated, damaged and off its foundation. Vehicle hit and run. | Gloucester | Foreign Interference | Vehicle
19520 | 2011 | 11 | 2 | 0.50278 |  | 317 | 11 | 2 | Moulton | 8/4.8kV | 8F4 | Vaults VE28 and VE29 at 2022 Jasmine were isolated to allow contractor to perform vault maintenance. | Gloucester | Scheduled Outage | Preventive Maintenance
4531 | 2003 | 11 | 28 | 0.60347 |  | 71 | 422 | 587 | Moulton | 27.6/16kV | 8F4 | Load transfer for vault shut down, load transferred exceeded fuse size and fuse failed. | Gloucester | Human Element | Switching Errors
9860 | 2006 | 12 | 18 | 0.79444 |  | 127 | 1818 | 859 | Moulton | 27.6/16kV | 8F4 | Cable fault in cable section SE11 by SE15. Load restored from G957SM | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17979 | 2011 | 4 | 20 | 0.98125 |  | 108 | 4 | 2 | 4F5 | 8/4.8kV | 8F5 | Fallen tree branch cause G272 at Russel Rd. and Anderson Rd. to open. Crews cleared the branch, re-fused and closed the switch. | Gloucester | Tree Contacts | Tree Fallen
15839 | 2010 | 3 | 24 | 0.39931 |  | 49 | 3 | 4 | VAUGHAN | 4.16kV | 8G04 | Transformer at Mackay St & Vaughan St isolated to allow for service work | Ottawa | Scheduled Outage | Repair
12639 | 2008 | 6 | 15 | 0.60417 |  | 128 | 7772 | 3643 | Moulton | 27.6/16kV | 8T2 | 8CS2-L circuit switcher trip because of lightning caused the lost of load to 8F2 and the 8F4 which was also carrying the 8F3 circuit. | Gloucester | Adverse Weather | Lightning
3502 | 2003 | 5 | 30 | 0.48611 |  | 6 | 180 | 1800 | Merivale | 115kV | A3RM | Squirrel contact on the Merivale B1 Bus tripped the ckt.A3RM. Station was restored from normal supply. Stations report damaged insulators on the B1 Bus. | Nepean | Foreign Interference | Animal
5295 | 2004 | 6 | 13 | 0.41875 |  | 16 | 5 | 17 | Uplands MTS | 115kV | A3RM | A3RM circuit auto reclosed due to a squirrel on B2 bus at Merivale. Hydro One circuit switcher failed to open (726T2-A3RM) . Which cause A3RM protection to clear the circuit. Which then caused UPLANDS MTS protection to open all breakers. OUTAGE to the OTTAWA AIRPORT. ALSO caused a power outage on Merivale T2 bank | Gloucester | Loss of Supply | HEPC Circuit Fault
5296 | 2004 | 6 | 13 | 0.41875 |  | 59 | 15 | 15 | Merivale | 115kV | A3RM | A3RM circuit auto reclosed due to a squirrel on B2 bus at Merivale. Hydro One circuit switcher failed to open (726T2-A3RM) . Which cause A3RM protection to auto the circuit. 130F3 circuit was open to all crew to close S1075 switch. 130F3 was opened of less then 1 min. | Nepean | Foreign Interference | Animal
8621 | 2006 | 6 | 29 | 0.43889 |  | 6 | 47 | 545 | Merivale MS | 115kV | A3RM | Hydro One A3RM circuit auto/reclosed, Slater J1 bus interrupted because J1J2 tie breaker was open. Had to manually closed by Hydro one scada. (10:32) Merivale T2-A3RM has opened. 72T2 off load, load restored from SCADA.(10:35) Thunderstorms in the area. | Nepean | Loss of Supply | HEPC Circuit Fault
3728 | 2003 | 7 | 13 | 0.17708 |  | 304 | 3293 | 650 | Uplands | 115kV | A3RM | Uplands Station was isolated to allow for the test tripping of Hydro One's A3RM "A" & "B" line protection and the A8M "A" line protection also to install the 115 taps to the new 4801T3 transformer at Uplands station. 2F2, F3 & F5 feeders were restored at 09:19. 2F4 feeder was restored at 09:51 because bkr would not close. | Gloucester | Scheduled Outage | Construction
3952 | 2003 | 8 | 27 | 0.67569 |  | 120 | 1705 | 1800 | Merivale,Uplands | 115kV | A3RM | Squirral cause a flash on the tie switch on the B1-B2 out of Merivale causing the A3RM to trip. IMO delay the restortion of Uplands on the A3RM. Hydro One closed in at 16:37 on the A3RM picking up Uplands. The 72F1& F7 load was pick up through breaker to breaker swichting. While the remainder was pick up through manual switching. | Nepean | Foreign Interference | Animal
13347 | 2008 | 10 | 8 | 0.91806 |  | 54 | 812 | 902 |  | 8/4.8kV | A3RM | An insulator on the 8kv leads to 72F5 flashed over causing 72T2 to trip off (H - 1's 6T2-A3RM switch opened) & 72F5 breaker to trip. The flashed insulator on 72F5 was isolated, the B2 bus restored via 72T1. 72F6 & 72F7 picked up & 72F5 load picked up via 58F5. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9614 | 2006 | 11 | 6 | 0.66389 |  | 32 | 214 | 402 | Merivale | 115kV | A3RM | The A3RM autoreclosed causing a bump on the Slater T1 and Riverdale T3 and causing the 6T2-A3RM to open at Merivale loosing the 72T2 transformer, nothing was found at Merivale. Hydro One reported a squirrel caused the outage at Riverdale.. | Ottawa | Loss of Supply | HEPC Circuit Fault
7618 | 2005 | 11 | 15 | 0.77361 |  | 16 | 235 | 882 | Merivale | 115kV | A3RM | H1 reports 3 115 kv circuits tripped. A3RM, A4K, A5RK. Load loss at 72T2 due to 72T1 being out of service for H1 work. | Nepean | Loss of Supply | HEPC Circuit Fault
6844 | 2005 | 7 | 1 | 0.69514 |  | 139 | 1547 | 1004 | Uplands, Merivale | 115kV | A3RM, A8M | Lightning damaged an insulator on the 115kv supply side of Uplands T1, A3RM A/R, A8M locked out. 4801T3 tripped on differential. Supply was lost to Merivale T1. H - 1 had high voltage problems on A8M before load could be restored at Merivale. 2T1 at uplands was isolated & load restored via 2T2. 4801T3 was visually inspected & then energized to restore 4801F7 & F8. | Gloucester | Lightning
5115 | 2004 | 5 | 7 | 0.38542 |  | 34 | 2820 | 5662 | Moulton |  | A4K | A4K Triiped out (Hydro One Transmission line feeding Moulton) G925SM was opened and scada confirmed and switch was closed to pick up load from 77M5 but switch never opened and 77M5 tripped tie switch was opened and 77M5 was closed immediately also see outage ID#5113 A4Kalso feeds King edward | Gloucester | Loss of Supply | HEPC Station Fault
6169 | 2005 | 2 | 2 | 0.41181 |  | 15 | 4792 | 21436 | King Edward, Overbrook, M | 115kV | A5RK, A4K | Electrical contact from a squirrel caused T3 xfmr at Overbrook to trip on differential resulting in an A5RK cct auto reclose. Normally no load would be lost for this scenario, not even momentarily. However, A4K cct was being fed radial thru Overbrook due to a planned outage at the Hawthorne A4K terminal. After the A5RK circuit auto-reclosed, restoring load to King Edward the load to Moulton & Overbrook still remained off until it could be restored manually from Hydro One SCADA control. | Ottawa | Loss of Supply | HEPC Station Fault
9973 | 2007 | 1 | 30 | 0.17014 |  | 170 | 3022 | 4700 | Uplands | 27.6/16kV | A8M | H1 loss of supply from Billings Jct to Uplands MS & MTS due to a trip from the Billings U/V protection. | Gloucester | Loss of Supply | HEPC Circuit Fault
9975 | 2007 | 1 | 30 | 0.46389 |  | 40 | 959 | 4700 | Uplands | 27.6/16kV | A8M | H1 loss of supply from Billings Jct to Uplands MS & MTS due to a trip from the Billings U/V protection. | Gloucester | Loss of Supply | HEPC Circuit Fault
16439 | 2010 | 7 | 9 | 0.53958 |  | 49 | 625 | 1332 | Merivale | 115kV | A8M | Hydro One's 6T1-A2 at Merivale opened from undervoltage protection interrupting power to 72T1 and 72F1, 72F2 & 72F4 feeders. 72F1 & 72F4 were restored after transformer was restored but 72F2 would not close due to a blown closing fuse. Stations replaced fuse & restored 72F2 load. Cause of undervoltage still not exactly known at this time as line did not trip or auto-reclose. | Nepean | Loss of Supply
8882 | 2006 | 8 | 1 | 0.048611 |  | 4 | 128 | 1914 | Merivale | 115kV | A8M | Hydro one reports Auto reclose on 115 kv circuit A8M Merivale T1 and all Uplands MS | Nepean | Loss of Supply | HEPC Circuit Fault
13318 | 2008 | 10 | 3 | 0.36389 |  | 7 | 111 | 952 | Merivale MS | 115kV | A8M | Hydro One's 6T1-A2 opened on undervoltage protection causing loss of supply to 72T1 transformer (72F2 & 72F4 feeders). Load was restored via 72T1 transformer from SCADA switching. Cause was later determined to be a a defective B undervoltage relay. | Nepean | Loss of Supply | HEPC Station Fault
13320 | 2008 | 10 | 3 | 0.60764 |  | 13 | 54 | 250 | Merivale | 115kV | A8M | Hydro One reports circuit switcher 6T1-A2 (feeds 72T1) has Blue phase interupter open, it did not close properly after previous outage, system transferred load from 72T1 to 72T2, Hydro One opened and closed circuit switcher and reported all 3 phases are field checked and verified closed. | Nepean | Loss of Supply
9414 | 2006 | 10 | 11 | 0.50347 |  | 2 | 55 | 1650 | UPLANDS | 27.6/16kV | A8M | Flashed Insulator on 72T1 Transformer on low side , at Merivale MS caused A8M to trip, causing loss of supply to Uplands DS, Uplands MS and Merivale T1 Supply. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9415 | 2006 | 10 | 11 | 0.50347 |  | 35 | 412 | 750 | MERIVALE MS | 8/4.8kV | A8M | ashed Insulator on 72T1 Transformer on low side , at Merivale MS caused A8M to trip, causing loss of supply to Uplands DS, Uplands MS and Merivale T1 Supply. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
15428 | 2009 | 11 | 26 | 0.75 |  | 28 | 247 | 529 | Uplands | 115kV | A8M | Uplands station and Merivale T1 were interrupted for Hydro One A8M line outage to open defective 86-A8M switch off pot. Uplands 2F3 & 2F4 was the only load interrupted, all other load was transferred to alternate supplies prior to line outage. | Gloucester | Loss of Supply
17413 | 2010 | 12 | 12 | 0.4375 |  | 42 | 3456 | 6485 |  | 115kV | A8M | H1 loss of Supply on the A8M circuit, affecting Mervale T1 & Uplands station. H1 transfered feed to A3RM at Uplands & customers restored at 10:29am, 5000 customers affected 72T1 transfered to 72T2, 72F1, F2 & F4 restored at 11:12am, 1485 customers affected | HYDRO ONE | Loss of Supply
14758 | 2009 | 7 | 15 | 0.27847 |  | 90 | 2609 | 2000 | Merivale MS | 27.6/16kV | A8M, A3RM | A squirrel flashed over the merivale MS 72B1-B2 tie switch which caused the A3RM and the A8M to open. Load was restored from other stations. | Nepean | Foreign Interference
15712 | 2010 | 2 | 9 | 0.94306 |  | 141 | 1432 | 9413 | South March | 44kV | A9 Q BUS | 39F3 showed tripped the same time a Q bus differential at Hydro 1 South March caused an interuption to A9M2, A9M3 and A9M5. A9 Q bus recovered with 39F3 remaining off. 39F3 sectionalized and tried no fault found, load restored problem appears to be on Hydro1 side | Kanata | Loss of Supply | HEPC Station Fault
19847 | 2012 | 1 | 17 | 0.85069 |  | 114 | 12742 | 7105 | South March | 44kV | A9M1 | A9M1 circuit auto-reclosed and BRDT4 high side fuses were found to be blown affecting the BRDF2 and BRDF4 circuits at Bridlewood. Transformer was isolated and circuits restored. | Kanata | Adverse Weather | Ice, Sleet, Freezing Rain (not Trees)
4762 | 2004 | 2 | 4 | 0.54306 |  | 41 | 27 | 40 | Southmarch TS | 44kV | A9M1 | To isolate the pole broken by the snow plow truck the Hazeldean Mall had to be interruded for the removal of the 98m1-LC1 loops of Hydro One. | Kanata | Foreign Interference | Vehicle
8057 | 2006 | 3 | 24 | 0.033333 |  | 9 | 1 | 4 | South March TS | 44kV | A9M1 | H1 said it was a auto reclose, customer at 110 Hertzberg, security guard reported a 9 min power interruption. Crew checked South March yard, nothing unusual. Patrol of 44kv coming back in. | Kanata | Loss of Supply | HEPC Circuit Fault
8059 | 2006 | 3 | 24 | 0.5 |  | 80 | 1 | 1 | South March TS | 44kV | A9M1 | Isolate a sect of O/H bet switches S20476 and A5t-L at Compax on Hertzberg to replace 44Kv insulator that broke which the A9M3 to auto reclosed during the night. | Kanata | Loss of Supply | HEPC Circuit Fault
12448 | 2008 | 5 | 17 | 0.84583 |  | 324 | 86 | 705 | SOUTH MARCH | 27.6/16kV | A9M1 | South March A9M1 circuit auto reclosed then re-opened staying tripped, Terry Dans reports found broken insulator & smoking crossarm at pole # X2661 Corkstown Rd & March Rd. A9M1 overhead restored at 22:45. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
18262 | 2011 | 5 | 31 | 0.53472 |  | 216 | 4 | 1 | South March | 44kV | A9M1 | AMT1 at 62 Steacie was forced out by defective customer equipment, SG was arranged to allow customer's contractor to repair. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
10512 | 2007 | 6 | 2 | 0.34167 |  | 338 | 11 | 2 | South March | 44kV | A9M1 | QT205, EMR off Timm rd isolated for planned maintenance. City pumping station, TE300 also isolated for working clearance for part of job. | Nepean | Scheduled Outage | Preventive Maintenance
8720 | 2006 | 7 | 14 | 0.020833 |  | 60 | 3 | 3 | South March TS | 44kV | A9M1 | Planned interruption to 3 customer owned substations at March Rd & Carling to allow Hydro One to isolate a section of the 44 Kv overhead. | Kanata | Scheduled Outage | Repair
8728 | 2006 | 7 | 15 | 0.025 |  | 84 | 4 | 3 | South March TS | 44kV | A9M1 | Scheduled outage to Optotek, Gilmour Property Management and Drytek, for Hydro One planned outage to restore the 44kv line to normal. | Kanata | Scheduled Outage
12880 | 2008 | 7 | 18 | 0.17083 |  | 23 | 1 | 2 | South March | 44kV | A9M1 | H1 had a differential trip on the Y bus at South March. They picked up circuit. | Nepean | Loss of Supply
11217 | 2007 | 8 | 30 | 0.27778 |  | 185 | 3 | 1 | South March | 44kV | A9M1 | 1 customer at 62 Seacie Dr, lost power due to a hot line clap burned off, power restored at 9:45am | Kanata | Defective Equipment | Equipment Failure - Cause Unknown