11576 | 2007 | 10 | 23 | 0.36875 |  | 5 | 58 | 700 | South March | 44kV | A9M1 | A9M1 feeder auto tripped while under hold off. A defective insulator at customer owned substation Optotek caused feeder to trip. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4485 | 2003 | 11 | 19 | 0.86111 |  | 369 | 24232 | 6886 | South March TS | 44kV | A9M1 | Bridlewood F1,F2 and OCRTF2 as well as HAZ F4,F5,F6 all being supplied from A9M2 , and 1 phase is reported down so at our request Hydro One opened A9M1.115 Kv brought back in service load restored. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4496 | 2003 | 11 | 21 | 0.54167 |  | 276 | 5 | 1 | South March TS | 44kV | A9M1 | The A9M1 44Kv feeder auto/reclosed when sleeve at feed to COMPAQ failed and feeder opened. COMPAQ remained o/s until they repaired defective surge arrestors at their station. (see iteruption ID# ) | Kanata | Defective Equipment
4497 | 2003 | 11 | 21 | 0.63819 |  | 2 | 67 | 2000 | South March TS | 44kV | A9M1 | A9M1 feeder tripped under Hold Off when COMPAQ was restored, A5T-L closed, surge arrestor blew in the customers station tripping the feeder. | Kanata | Foreign Interference
4640 | 2003 | 12 | 21 | 0.0013889 |  | 295 | 10 | 2 | South March TS | 44kV | A9M1 | 44Kv overhead line section on Richardson Side Rd between Carling & March Rd feeding Gilmore Printing and Drytex isolated to install new in line sws. | Kanata | Scheduled Outage | Construction
11761 | 2007 | 11 | 24 | 0.64931 |  | 3 | 152 | 3050 | South March | 44kV | A9M1, M3 | Loss of supply to both cct's during H - 1 switching to restore breakers to service. | Kanata | Loss of Supply
14567 | 2009 | 6 | 18 | 0.60625 |  | 5 | 735 | 8816 | South March TS Hydro One | 44kV | A9M2 | Hydro One reports that the "Q" buss suffered a differential trip, causing complete outages at the following Hydro Ottawa stations: South March, Beaverbrook, Munster, Janet King, Richmond North. Hydro One's Alexander station was also affected. A total of 8816 customers were affected. | Kanata | Loss of Supply
18557 | 2011 | 6 | 28 | 0.79306 |  | 10 | 173 | 1040 | South March TS | 44kV | A9M2 | A9M2 circuit during lightening storm. Circuit was closed by Hydro One restoring all load. | Kanata | Adverse Weather | Lightning
11074 | 2007 | 8 | 16 | 0.35764 |  | 45 | 1 | 1 | South March | 44kV | A9M2 | P. Donnelly reports 2 fuses at Nortel found opened on TF transformer. Eaton Electric onsite to check cause. Nortel has transformered all load off transformer # TF. All power restored. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4324 | 2003 | 10 | 22 | 0.37083 |  | 86 | 3 | 3 | South March | 44kV | A9M2 | Reports of Canada Goose hitting the line. No damage found on the line. Hydro One RTU down. Nortel auto transfer did not operate. Nortel auto switch closed by Pete Barr. A9M2 closed by Hydro One by person at the station. | Nepean | Foreign Interference | Bird
4498 | 2003 | 11 | 21 | 0.72431 |  | 11 | 0 | 1 | Soth March TS | 44kV | A9M2 | Nortel QT131 o/s and 44Kv isolated to remove a tree which is burning from the A9M2. | Kanata | Tree Contacts | Foreign Object
6215 | 2005 | 2 | 17 | 0.65069 |  | 157 | 5 | 2 | South March | 44kV | A9M3 | A9M3 circuit isolated due to 44kv hot sleeve burning on Shea RD. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
8024 | 2006 | 3 | 14 | 0.73958 |  | 223 | 2537 | 696 | Munster | 44kV | A9M3 | Broken 44Kv insulators at the Munster D.S caused for emergency switching that dump all all the Munster customers. The customers were pick up by the out of rabbits. While trying to restore power the crews found a blown fuse at Sw424 which caused the reclosure | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
10161 | 2007 | 3 | 22 | 0.58472 |  | 677 | 22670 | 4415 | South March | 44kV | A9M3 | A9M3 locked out (A/R/A) at the same time as the A9M5, loss of power to Janet King, Munster, Richmond North, south March MS & Beaverbrook. Problem was later determined to be A9M3 conductor down on top of the M5 with the pole top burnt. Power was restored in stages while Hydro One replaced damaged pole & conductor. | Kanata | Loss of Supply | HEPC Circuit Fault
17952 | 2011 | 4 | 17 | 0.28125 |  | 311 | 10 | 2 | South March |  | A9M3 | 44kV customers Canada Float Glass and Goulburn Rec. Centre were interrupted due to a planned outage on the A9M3 | Goulburn | Scheduled Outage | Preventive Maintenance
6448 | 2005 | 4 | 23 | 0.56111 |  | 120 | 532 | 10000 | South March | 44kV | A9M3 | A9M3 circuit opened & locked out. Hydro One closed breaker at our request restoring load. 13:45 received calls from Best Way in Kanata. D. Howart reports SMF2 white phase reclosure opened. Found blown insulator at station. Also due to location of insulator 39F2 circuit red & blue phases open. Circuit energized via S57-1 BBF2 circuit. | Kanata | Loss of Supply | HEPC Circuit Fault
10315 | 2007 | 4 | 24 | 0.40972 |  | 435 | 2839 | 1210 | South March | 44kV | A9M3 | 2 poles on Shea rd S. of Fallowfield were broken during a severe wind storm. A section of the 44kv line as well as a section of Richmond N F1 were isolated to brace the poles. This resulted in a loss of supply to Munster & Richmond N stations as well as 2 direct customers on A9M3. Munster 43F3 load was transferred to Beckwith & Richmond N load was transferred to Richmond S. A9M3 load restored at 09:57. Munster F2 power restored at 10:27. Munster F3 circuit restored to normal at 11:27. | Goulburn | Adverse Weather | Wind
18109 | 2011 | 5 | 6 | 0.6125 |  | 237 | 2997 | 2252 | South March |  | A9M3 | Switch S13321 on A9M3 to Beaverbrook flashed and caused a pole fire and a phase to come down. Isolation for repairs required, 2 customers affected by the isolation | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
10889 | 2007 | 7 | 16 | 0.75486 |  | 1 | 74 | 4415 | South March | 44kV | A9M3 | J. Streng request A9M3 circuit to be opened to allow driver to get clear of truck. | Kanata | Foreign Interference | Vehicle
14805 | 2009 | 7 | 22 | 0.48819 |  | 78 | 937 | 1476 | Southmarch | 44kV | A9M3 | The A9M3 breaker was opened by Hydro One to allow Hydro Ottawa crew to open a nonload break switch for isolation for a broken 44K switch 76M3-1 on Fallowfeild,after the switch was open H1 close the breaker back in limiting outage to just Munster Ds. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
10978 | 2007 | 8 | 1 | 0.45833 |  | 628 | 19159 | 5215 | South March TS | 44kV | A9M3 | Bulldozer hit guy wires which caused pole and crossarm to break, which caused the A9M3 breaker to trip and lock out, affecting South March, Beaverbrook, Janet King, Munster DS, Richmond North, load restored in sections due to loading issues | Kanata | Foreign Interference | Vehicle
11090 | 2007 | 8 | 17 | 0.68056 |  | 445 | 7895 | 4500 | South March | 44kV | A9M3 | Bleeks Side Road, 6 spans from Munster DS a tree fell onto the 8KV and 44KV RWB phase overhead lines causing the SouthMarch A9M3 feeder to open, thus losing Janet King, Richmond North, SouthMarch, BeaverBrook, and Munster. Also after A9M3 was restored found that conductor on the Munster 43F2 and 43F3 was broken on Bleeks Rd and both feeders were isolated to complete repairs. | Kanata | Tree Contacts | Tree Fallen
18961 | 2011 | 8 | 18 | 0.55625 |  | 15 | 340 | 1360 | SOUTH MARCH | 44kV | A9M3 | A9M3 TRIPPED & LOCKED OUT DUE TO HOLDOFF CLOSED AND HOLDING | Nepean | Adverse Weather
4133 | 2003 | 9 | 23 | 0.6875 |  | 90 | 1855 | 2500 | South March | 44kV | A9M3 | A9M3 locked out causing a 10 minute outage to Munster Richmond North Janet King and Alexandre DS stations switching was done and power was restored to all stations except Munster. The cause was a Vehicle accident on Fallowfield .The Munster F3 was backfed from Rabbits from Beckwidth and was restored at 17:20. The Munster F2 was also backfed from rabbits and was restored 18:00. 8 of the 10 customers still off on Fallowfield (richmond N F1) were restored at 19:18 leaving 2 customers on Fallowfield off for the duration of repairs. | Goulburn | Foreign Interference | Vehicle
13532 | 2008 | 10 | 29 | 0.90972 |  | 81 | 918 | 680 | South March | 44kV | A9M3 | A9M3 44Kv overhead section between Munster stn. And 76M3-1 switches was isolated to replace broken crossarm at 6615 Mansfield. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
11728 | 2007 | 11 | 16 | 0.48264 |  | 52 | 2626 | 3030 | South March | 44kV | A9M3 | Circuit tripped while under hold off. Several crews in area took part in patrol of line from clear FCI at Janet King back to terminal, no problems found. Hydro - 1 closed breaker and load recovered. H - 1 indicates R phase fault. | Goulburn | Unknown/Other | No Apparent Cause
13389 | 2008 | 10 | 19 | 0.27778 |  | 330 | 11 | 2 | South March (Hydro One) | 44kV | A9M3 & M5 | Planned outage for Hydro One's A9M3 & A9M5 out of South March TS. All load at Janet King, Richmond North, & Munster was transferred out the day before, only customers affected are Goulburn Rec center & TN2000 (Eastern Float Glass). | Goulburn | Scheduled Outage | Preventive Maintenance
12881 | 2008 | 7 | 18 | 0.17014 |  | 25 | 0 | 1 | South march | 44kV | A9M4 | H1 had a differential trip on the Y bus at South March. They picked up circuit. | Nepean | Loss of Supply
11732 | 2007 | 11 | 17 | 0.34722 |  | 465 | 16 | 2 | South March TS | 44kV | A9M4 | A9M4 was isolated from South March TS to allow for reinsulating of private line to customer sub at Nordion on March Rd | Kanata | Scheduled Outage | Preventive Maintenance
10162 | 2007 | 3 | 22 | 0.93333 |  | 676 | 26413 | 4400 | South March | 44kV | A9M5 | A9M5 locked out (A/R/A) at the same time as the A9M3, loss of power to Alexander DS. Problem was later determined to be A9M3 conductor down on top of the M5 with the pole top burnt. Power was restored in stages while Hydro One replaced damaged pole & conductor. | Kanata | Loss of Supply | HEPC Circuit Fault
18151 | 2011 | 5 | 14 | 0.42083 |  | 2 | 238 | 7137 | Alexander | 44kV | A9M5 | A9M5 which feeds Alexander DS auto reclosed then tripped, Hydro One closed it in, then reported the outage to us. No cause has been dertimined yet. | Goulburn | Loss of Supply | HEPC Circuit Fault
8313 | 2006 | 5 | 17 | 0.60139 |  | 190 | 203 | 4421 | Alexander | 27.6/16kV | A9M5 | Hydro One manually opened the A9M5 feeder due to a burning pole, pole isolated and supply to Alexander DS restored. Carp DS(Hydro One) remains o/s for pole replacement, 18 transfer customers fed from Carp DS interupted. | Goulburn | Loss of Supply | HEPC Circuit Fault
8555 | 2006 | 6 | 20 | 0.4625 |  | 9 | 660 | 4400 | Alexander | 44kV | A9M5 | Hydro One 44Kv feeder A9M5 auto/reclose/auto interupting Alexander DS. Alex F2 & F3 interupted. A9M5 restored via SCADA, no cause found at this time. | Goulburn | Loss of Supply | HEPC Circuit Fault
8562 | 2006 | 6 | 21 | 0.40278 |  | 32 | 519 | 4400 | Alexander | 44kV | A9M5 | Hydro One 44Kv feeder A9M5 auto/reclose/auto interupting Alexander DS. Alex F2 & F3 interupted. A9M5 restored via SCADA, no cause found at this time. When the circuit was restored the Alexander F3 B phase opened due to cold load pickup (same was under Hold Off) same restored on site by Hydro Ottawa crew. | Goulburn | Loss of Supply | HEPC Circuit Fault
19392 | 2011 | 10 | 16 | 0.23958 |  | 405 | 14 | 2 | South March | 44kV | A9M5 | A9M3, A9M5 and a section of 624F1 circuits were isolated at Terry Fox and Richardson Side Rd to allow Hydro One to replace poles and move conductors and to allow Hydro Ottawa crews to remove A9M3-1 switch and install new VBM switches @ 76M3-1 and 76M3-2. Stations affected were Alexander, Carp, Beaverbrook, Janet King, Munster and Kanata. Most of the customers had been transfered prior to outage if possible. | Kanata | Scheduled Outage | Preventive Maintenance
16126 | 2010 | 5 | 23 | 0.28125 |  | 772 | 296 | 23 | South March | 44kV | A9M6 | South March A9M6 feeding Carp DS tripped off affecting approx 23 transfer customers on Huntmar Dr & Old Carp rd.. H - 1 found a broken pole in a swampy area. Poor access extended the length of the outage. | Kanata | Loss of Supply | HEPC Circuit Fault
5873 | 2004 | 11 | 10 | 0.38958 |  | 3 | 450 | 8997 | South March TS | 44kV | A9T1 | While Hydro One was adjusting their taps on the Q bus the voltages ran away and they had to dump off the Q bus causing an outage on the A9M2,3,5 feeders - Customer count numbers updated after verification by J. Rice. | Goulburn | Loss of Supply
14132 | 2009 | 4 | 1 | 0.47917 |  | 75 | 41 | 33 | Church | 4.16kV | AA02 | Opened switch to transformer X23011 to isolated service to 278 Montreal Rd at the request of the Fire dept due to a fire in one of the apartments | Ottawa | Scheduled Outage | Emergency Services Request
16191 | 2010 | 6 | 3 | 0.64236 |  | 107 | 77 | 43 | Church | 4.16kV | AA02 | Defective box style switch at S10513 at Mona and Richelieu, switch was replaced on the centre phase, approx 43 customers. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10621 | 2007 | 6 | 13 | 0.56944 |  | 110 | 16 | 9 | Church | 4.16kV | AA02 | Isolated and replaced transformer at 312 Lafontaine Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
10654 | 2007 | 6 | 19 | 0.020833 |  | 60 | 7 | 7 | Church | 4.16kV | AA02 | Transformer at 309 Mona Avenue in Ottawa defective fuse failed. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14877 | 2009 | 7 | 29 | 0.69306 |  | 8 | 42 | 314 | Church | 4.16kV | AA02 | AA02 tripped when crew attemped to close fuse to Xfrm'r; X23001 at 316 Lafontaine found to be defective. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
7186 | 2005 | 8 | 23 | 0.40972 |  | 5 | 1 | 12 | Church | 4.16kV | AA02 | Transformer at 292 Lajoie St was isolated for contractor to do pole testing | Ottawa | Scheduled Outage | Preventive Maintenance
7187 | 2005 | 8 | 23 | 0.42222 |  | 4 | 1 | 12 | Church | 4.16kV | AA02 | Transformer at 317 Lajoie St was isolated for contractor to do pole testing | Ottawa | Scheduled Outage
9374 | 2006 | 10 | 4 | 0.39236 |  | 100 | 8 | 5 | Church | 4.16kV | AA02 | Transformer located at 310 Richelieu isolated to allow PCB transformer replacement. PC10A #1103 | Ottawa | Scheduled Outage | Preventive Maintenance
9390 | 2006 | 10 | 5 | 0.53125 |  | 105 | 2 | 6 | Church | 4.16kV | AA02 | At 12:45 trans at 400 Richelieu Ave was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9437 | 2006 | 10 | 16 | 0.39931 |  | 240 | 28 | 7 | Church | 4.16kV | AA02 | Transformer located at 353 Lafontaine isolated to change triplex. PC10A #6098 | Ottawa | Scheduled Outage | Preventive Maintenance
7557 | 2005 | 11 | 3 | 0.40625 |  | 83 | 7 | 5 | Church | 4.16kV | AA02 | Transformer located at 280 Richelieu isolated to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
6201 | 2005 | 2 | 11 | 0.39583 |  | 180 | 30 | 10 | Church | 4.16kV | AA03 | Opened Transformer at 221 Alfred to change pole | Ottawa | Scheduled Outage | Construction
10066 | 2007 | 2 | 26 | 0.55903 |  | 94 | 31 | 20 | Church | 4.16kV | AA03 | Blown arrester at K840 on Montfort caused the fuse to blow at Pole 7 Red phase. 2 transformers affected by outage, K840 and K841. Arrester replaced, refused and closed switch. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20099 | 2012 | 3 | 3 | 0.55278 |  | 10 | 106 | 636 | Church | 4.16kV | AA03 | AA03 tripped due wind storm causing overhead contact somewhere. Circuit to be patrolled eventually. | Ottawa | Adverse Weather
20104 | 2012 | 3 | 3 | 0.63264 |  | 15 | 159 | 636 | Church | 4.16kV | AA03 | SCADA Indicated AA03 opened during large wind gusts. No A/R. Circuit closed back in after 25 minutes and holding. | Ottawa | Adverse Weather
20114 | 2012 | 3 | 3 | 0.68333 |  | 308 | 3265 | 636 | Church | 4.16kV | AA03 | Wind storm in the area, circuit patrol found nothing. | Ottawa | Adverse Weather | Wind
6311 | 2005 | 3 | 22 | 0.42708 |  | 95 | 24 | 15 | Church | 4.16kV | AA03 | Transformer isolated to transfer wires to the new pole at 235 Granville (do not have trans #) | Ottawa | Scheduled Outage | Preventive Maintenance
6316 | 2005 | 3 | 23 | 0.38889 |  | 230 | 31 | 8 | Church | 4.16kV | AA03 | Transformer isolated at 142 Granville to transfer secondary | Ottawa | Scheduled Outage | Construction
10299 | 2007 | 4 | 23 | 0.70139 |  | 116 | 333 | 172 | Church | 4.16kV | AA03 | High winds may have caused tree contact. | Ottawa | Adverse Weather | Wind
18045 | 2011 | 4 | 28 | 0.53819 |  | 8 | 76 | 573 | Church | 13.2kV | AA03 | AA03 circuit breaker tripped during wind/lightning storm. Closed via scada and held. | Ottawa | Adverse Weather | Wind
18046 | 2011 | 4 | 28 | 0.56806 |  | 74 | 707 | 573 | Church | 4.16kV | AA03 | AA03 circuit breaker tripped during wind/lightning storm. Closed via scada and held. | Ottawa | Adverse Weather | Wind
18047 | 2011 | 4 | 28 | 0.62431 |  | 299 | 2855 | 573 | Church | 4.16kV | AA03 | AA03 circuit breaker tripped during wind/lightning storm. Crew removed tree from overhead and closed via scada and held. | Ottawa | Tree Contacts | Tree Fallen
18247 | 2011 | 5 | 30 | 0.39583 |  | 40 | 3 | 4 | Church |  | AA03 | Isolated transformer X42326 at 615 Ducharme Blvd for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
10650 | 2007 | 6 | 18 | 0.5625 |  | 105 | 18 | 10 | Church |  | AA03 | Transformer at 238 Granville isolated for replacement | Ottawa | Scheduled Outage | Preventive Maintenance
10651 | 2007 | 6 | 18 | 0.5 |  | 140 | 23 | 10 | Riverdale | 4.16kV | AA03 | Transformer at 381 Iberville isolated to allow for replacement of open wire buss - not transf # available | Ottawa | Scheduled Outage | Repair
3758 | 2003 | 7 | 18 | 0.54167 |  | 90 | 9 | 6 | Church | 4.16kV | AA03 | Unplanned outage to effect minor repairs with customers notified at the premises. | Ottawa | Scheduled Outage | Repair
3759 | 2003 | 7 | 18 | 0.4625 |  | 57 | 2 | 2 | Church | 4.16kV | AA03 | Planned outage to transfer customers from AA03 to AC15 at 300 White Fathers. | Ottawa | Scheduled Outage | Construction
8786 | 2006 | 7 | 19 | 0.60278 |  | 80 | 7 | 5 | Church | 4.16kV | AA03 | Transfomer located at 368 St Denis isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
8815 | 2006 | 7 | 24 | 0.55556 |  | 198 | 0 | 8 | Church | 4.16kV | AA03 | Trans K912 at 364 Monfort isolated to make repairs due to excavating | Ottawa | Foreign Interference | Vehicle
18822 | 2011 | 7 | 26 | 0.35417 |  | 245 | 461 | 113 | Church | 4.16kV | AA03 | AA03 section between S17851 and Temp 55 to allow crew to replace pole and transfer plan | Ottawa | Scheduled Outage | Preventive Maintenance
9434 | 2006 | 10 | 16 | 0.40972 |  | 88 | 15 | 10 | Church | 4.16kV | AA03 | Transformer located at 399 St. Denis isolated to change transformer due to PCB change as per PC10A#1116 | Ottawa | Scheduled Outage | Preventive Maintenance
9448 | 2006 | 10 | 17 | 0.40625 |  | 87 | 12 | 8 | Church | 4.16kV | AA03 | Isolated and replaced transformer 23696 at 127 Granville Ave due to PCB Oil | Ottawa | Scheduled Outage | Preventive Maintenance
15405 | 2009 | 11 | 21 | 0.36111 |  | 285 | 66 | 14 | Church | 4.16kV | AA03 | Transformer #X23743 located at 626 De L'eglise isolated to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
17388 | 2010 | 12 | 7 | 0.48264 |  | 38 | 6 | 9 | Church | 4.16kV | AA03 | Isolated transformer X23732 at 642 Donat St for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
6058 | 2004 | 12 | 13 | 0.51042 |  | 55 | 9 | 10 | Church | 4.16kV | AA03 | Transformer at the rear 111 Granville opened for load balancing. 10 Customers affected in plan power outage. | Ottawa | Scheduled Outage | Preventive Maintenance
13805 | 2008 | 12 | 28 | 0.48056 |  | 22 | 62 | 170 | Church | 4.16kV | AA03 | AA03 breaker opened during heavy winds. Ottawa fire & police called No reports of MVA. Circuit breaker closed via scada all power restored. | Ottawa | Adverse Weather | Wind
13806 | 2008 | 12 | 28 | 0.53958 |  | 8 | 23 | 170 | Church | 4.16kV | AA03 | AA03 circuit breaker opened during heavy winds. Ottawa fire & police called No reports of MVA. Circuit closed via scada all power restored. | Ottawa | Adverse Weather | Wind
6158 | 2005 | 1 | 30 | 0.48125 |  | 52 | 12 | 14 | Church | 4.16kV | AA04 | Replaced broken switch to transformer # OTT2908 at the front of 445 Guy St | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15699 | 2010 | 2 | 2 | 0.41667 |  | 200 | 30 | 9 | Church | 4.16kV | AA04 | Transformer #X23349 located at 755 Rue De L'Eglise (Church St) isolated for pole change | Ottawa | Scheduled Outage | Construction
18148 | 2011 | 5 | 13 | 0.70833 |  | 75 | 15 | 12 | Church | 4.16kV | AA04 | Trans X23548 at 613 Mutual St was isolated in order to replace a leaking trans due to broken bushing | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14393 | 2009 | 5 | 21 | 0.71528 |  | 195 | 59 | 557 | Church | 4.16kV | AA04 | At 5:10pm SCADA indicated AA04 CB opened. Ottawa Police and Fire reports no accidents or fires. Conditions are windy, system reclosed in breaker and all power restored. Customer at 476 Mutual reports fuse blown, probable cause of outage. Crew found blown arrestor caused fuse to blow | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14564 | 2009 | 6 | 18 | 0.39931 |  | 35 | 35 | 60 |  | 4.16kV | AA04 | Isolated transformer X23479 at 495 Guy St to replace service | Ottawa | Scheduled Outage | Emergency Services Request
18543 | 2011 | 6 | 28 | 0.5 |  | 263 | 74 | 24 | Church | 4.16kV | AA04 | Water truck contacted bell cables which broke a pole at 617 Gardenvale causeing a single phase primary conductor to come down. Crews isolated the affected section and made repairs. | Ottawa | Foreign Interference | Vehicle
8747 | 2006 | 7 | 17 | 0.98403 |  | 118 | 197 | 100 | Church | 4.16kV | AA04 | AA04 circuit was also hit by lightning. Circuit was patrolled ono fault found. | Ottawa | Adverse Weather | Lightning
8932 | 2006 | 8 | 8 | 0.5 |  | 55 | 0 | 8 | Church | 4.16kV | AA04 | Trans at 809 Trojan Ave isloated to replace secondary conductor | Ottawa | Scheduled Outage | Preventive Maintenance
11043 | 2007 | 8 | 13 | 0.54861 |  | 170 | 42 | 15 | CHURCH | 4.16kV | AA04 | Transformer #OTT519 at 840 Borthwick Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
11130 | 2007 | 8 | 22 | 0.35417 |  | 210 | 140 | 40 | Church | 4.16kV | AA04 | Isolated 6 transformers between Borthwick and Trojan to allow for tree trimming around secondary buss | Ottawa | Scheduled Outage | Preventive Maintenance
13149 | 2008 | 8 | 26 | 0.325 |  | 13 | 54 | 250 | Church | 4.16kV | AA04 | AA04 circuit was closed via scada all load restored to normal. G. Godard reports pole ground has broken and made contact with AA04 circuit. On Church St @ Guy St. R. Wallace made repairs to pole ground. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7289 | 2005 | 9 | 7 | 0.43056 |  | 123 | 51 | 25 | AA | 4.16kV | AA04 | K668 on Belisle st was isolated to separate & ID cables & provide isolation for a contractor. | Ottawa | Foreign Interference | Dig-in
11290 | 2007 | 9 | 12 | 0.34792 |  | 159 | 42 | 16 | Church | 4.16kV | AA04 | 16 customers between Trojan and Claude south of Mutual isolated to allow removal of trees. | Ottawa | Scheduled Outage | Preventive Maintenance
11299 | 2007 | 9 | 13 | 0.33333 |  | 190 | 61 | 32 | Church | 4.16kV | AA04 | 3 overhead transformers at 722, 744 & 754 Borthwick were isolated for tree trimming near secondary conductors. The 1 transfomer at 744 Borthwick stayed off longer to allow 24/7 to replace a defective cutout. | Ottawa | Scheduled Outage | Preventive Maintenance
11302 | 2007 | 9 | 13 | 0.43056 |  | 40 | 1 | 2 | Church | 4.16kV | AA04 | Transformer #OTT6345 located at 749 Trojan isolated to replace cutout | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9382 | 2006 | 10 | 5 | 0.36806 |  | 130 | 13 | 6 | Church | 4.16kV | AA04 | Transformer located at 452 Blake isolated to allow for PCB transformer replacement. PC10A #1190 | Ottawa | Scheduled Outage | Preventive Maintenance
13363 | 2008 | 10 | 14 | 0.375 |  | 45 | 6 | 8 | Church | 4.16kV | AA04 | Isolated transformer X24689 at 659 Dan Ave to replace switch and arrester | Ottawa | Scheduled Outage | Emergency Services Request
20090 | 2012 | 3 | 2 | 0.37153 |  | 20 | 3 | 10 | Church | 4.16kV | AA05 | Transformer #X29489 located at 386 Spartan Ave opened by crew to cut down an old service | Ottawa | Scheduled Outage | Construction
20146 | 2012 | 3 | 9 | 0.41667 |  | 40 | 7 | 10 | Church | 4.16kV | AA05 | Transformer X29489 at 386 Spartan Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
12125 | 2008 | 3 | 11 | 0.5 |  | 25 | 10 | 23 | Church | 4.16kV | AA05 | Isolated transformer OTT4563 at 902 Moorvale Ave for customer to remove ice build-up on the roof at the service entrance | Ottawa | Scheduled Outage | Preventive Maintenance
14105 | 2009 | 3 | 27 | 0.52083 |  | 45 | 8 | 10 | Church | 4.16kV | AA05 | Isolated transformer X29491 at 398 Spartan Ave for service up-grade | Ottawa | Scheduled Outage | Repair
6502 | 2005 | 5 | 4 | 0.51042 |  | 65 | 11 | 10 | Church | 4.16kV | AA05 | Opened transformer at 341 Montfort St to re-arrange the services | Ottawa | Scheduled Outage | Preventive Maintenance
10548 | 2007 | 6 | 7 | 0.39583 |  | 122 | 20 | 10 | Church | 4.16kV | AA05 | Tranformer #65C1B-0051 at 392 Irwin Miller St isolated to allow for transformer change | Ottawa | Scheduled Outage | Preventive Maintenance
3630 | 2003 | 6 | 29 | 0.013889 |  | 287 | 14 | 3 | AA | 4.16kV | AA05 | P88 at 412 MacArthur was isolated to upgrade it from 150kva to 300kva. | Ottawa | Scheduled Outage | Construction
8746 | 2006 | 7 | 17 | 0.98403 |  | 240 | 600 | 150 | Church | 4.16kV | AA05 | Lightning hit P/P/H switch at Church substation causing power outage. P/P/H was isolated and all load transferred to AA00 circuit. | Ottawa | Adverse Weather | Lightning
7227 | 2005 | 8 | 28 | 0.0625 |  | 140 | 51 | 22 | Church | 4.16kV | AA05 | Transformer at the rear of 928 Moorvale was changed due to oil leak. 22 customer affected in power outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9358 | 2006 | 10 | 2 | 0.47222 |  | 80 | 7 | 5 | Church | 4.16kV | AA05 | Transformer located at 375 Brant isolated to allow for PCB change. PC10A#1139 | Ottawa | Scheduled Outage | Preventive Maintenance
9360 | 2006 | 10 | 2 | 0.46181 |  | 82 | 7 | 5 | Church | 4.16kV | AA05 | Transformer located at 397 Brant isolated for PCB change. PC10A#1145 | Ottawa | Scheduled Outage | Preventive Maintenance
9444 | 2006 | 10 | 16 | 0.75347 |  | 165 | 19 | 7 | Church | 4.16kV | AA05 | At 18:05 trans at 373 McArthur was isolated in order to replace the trans | Ottawa | Scheduled Outage | Preventive Maintenance
13661 | 2008 | 11 | 24 | 0.51042 |  | 35 | 6 | 10 | Church | 4.16kV | AA05 | A transformer at 398 Spartan was isoalted to allow crews to install coverup on overhead circuit | Ottawa | Scheduled Outage | Preventive Maintenance
13674 | 2008 | 11 | 27 | 0.49583 |  | 72 | 12 | 10 | CHURCH | 4.16kV | AA05 | Transformer X29489 at 386 Spartan isolated to replace defective cutout & replace fuse | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9981 | 2007 | 2 | 1 | 0.66319 |  | 105 | 14 | 8 | Church | 4.16kV | AA06 | Dave Jones isolated trf. OTT 4571 @ 640 Morin to replace defective sw. and hook up new tpx. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7880 | 2006 | 2 | 2 | 0.38889 |  | 180 | 30 | 10 | Church | 4.16kV | AA06 | Transformer X24681 at 666 Dan St was isolated for repairs | Ottawa | Scheduled Outage | Preventive Maintenance
12021 | 2008 | 2 | 8 | 0.47917 |  | 45 | 9 | 12 | Church | 4.16kV | AA06 | Transformer #OTT1481 located at 786 Claude isolated for an Arrears acct-crew had to run new triplex before reconnecting service | Ottawa | Scheduled Outage | Construction
8135 | 2006 | 4 | 11 | 0.625 |  | 12 | 1 | 4 | Church | 4.16kV | AA06 | Transformer #OTT6078 located across from 776 St Laurent isolated to replace service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3601 | 2003 | 6 | 23 | 0.77431 |  | 25 | 6 | 15 | Church | 4.16kV | AA06 | Reported to dispatch as sparking wires. | Ottawa | Defective Equipment
8709 | 2006 | 7 | 13 | 0.39583 |  | 120 | 16 | 8 | Church | 4.16kV | AA06 | Chris Williams opened a transformer at St. Laurent and Noranda to to pcb changes | Ottawa | Scheduled Outage | Preventive Maintenance
8711 | 2006 | 7 | 13 | 0.54167 |  | 45 | 2 | 2 | Church | 4.16kV | AA06 | Chris Williams opened transformer X23539 across from 776 St. Laurent to do a pcb change | Ottawa | Scheduled Outage
8723 | 2006 | 7 | 14 | 0.38194 |  | 130 | 24 | 11 | Church | 4.16kV | AA06 | Yannick Fortin opened transformer OTT4695 at 623 Noranda to move a service | Ottawa | Scheduled Outage
12946 | 2008 | 7 | 26 | 0.52917 |  | 57 | 179 | 188 | Church | 4.16kV | AA06 | AA06 riser cable at De L'Eglise and Cote blew causing the AA06 breaker to trip. Load transferred to AA00 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18862 | 2011 | 7 | 30 | 0.93333 |  | 30 | 9 | 18 | Church | 4.16kV | AA06 | Crew isolated transformer X23166 to repair defective connections. Church (AA06) ID#18862 | Ottawa | Defective Equipment
8875 | 2006 | 7 | 31 | 0.39583 |  | 109 | 13 | 7 | Church | 4.16kV | AA06 | Isolated and replaced transformer OTT1705 at 550 Cote St due to oil contaminants (PCB) | Ottawa | Scheduled Outage | Preventive Maintenance
8999 | 2006 | 8 | 18 | 0.4375 |  | 38 | 11 | 17 | Church | 4.16kV | AA06 | At 10:30 trans K539 at 6-653 St Laurent Blvd isolated in order to replace defective switch | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7225 | 2005 | 8 | 27 | 0.61111 |  | 50 | 3 | 4 | Church | 4.16kV | AA06 | Trans OTT1479 @ 664 Claude Ave to replace defective service wires | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19086 | 2011 | 9 | 4 | 0.0041667 |  | 372 | 211 | 34 | Church |  | AA06 | A tree limb fell onto blue phase run off at the rear of 712 Morin Street. Church (AA06) ID#19086. | Ottawa | Tree Contacts | Tree Limb Fallen
19208 | 2011 | 9 | 19 | 0.38194 |  | 320 | 43 | 8 | Church | 4.16kV | AA06 | Transformer #X23384 located at 4 Camil St opened by crew for a pole change | Gloucester | Scheduled Outage
11520 | 2007 | 10 | 15 | 0.48264 |  | 40 | 13 | 20 | Church | 4.16kV | AA06 | Transformer #OTT516 located at 782 Borthwick isolated due to service upgrade | Ottawa | Scheduled Outage | Construction
4282 | 2003 | 10 | 16 | 0.89583 |  | 110 | 18 | 10 | Church | 4.16kV | AA06 | Transformer 4575 off loaded to make reconnections to 3 services on Morin afterhigh winds yesterday. | Ottawa | Scheduled Outage | Repair
19454 | 2011 | 10 | 23 | 0.89583 |  | 266 | 75 | 17 | Church | 4.16kV | AA06 | AA06 blue and white phases in the rear of 844 Claude taken down by a large tree, isolation required to remove tree and repair the overhead | Ottawa | Tree Contacts | Tree Fallen
4367 | 2003 | 11 | 2 | 0.69097 |  | 22 | 3 | 7 | Church | 4.16kV | AA06 | Transformer at 464 Vernon was opened to repair triplex at 480 Vernon that customer cut into when trimming trees around triplex. | Ottawa | Scheduled Outage | Repair
18049 | 2011 | 4 | 28 | 0.55347 |  | 8 | 38 | 284 | Nepean | 4.16kV | AB03 | AB03 CB tripped during wind/lightning storm. Close Via scada and held. | Ottawa | Adverse Weather | Wind
14592 | 2009 | 6 | 22 | 0.2125 |  | 88 | 307 | 209 | Nepean | 4.16kV | AB03 | The AB03 breaker was open via scada at the fire dept request for a fire at 234 Lyon St. | Ottawa | Unknown/Other | Fire
3704 | 2003 | 7 | 7 | 0.87431 |  | 31 | 7 | 13 | AB | 4.16kV | AB03 | An O/H xfmr at 613 Cooper was opened to make repairs to secondary connections. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3703 | 2003 | 7 | 8 | 0.54514 |  | 45 | 10 | 13 | AB | 4.16kV | AB03 | An O/H xfmr, serial # 55d28-017 at 613 Cooper st was opened to replace connections on a service. Affected addresses - 610 to 615 Cooper | Ottawa | Scheduled Outage | Preventive Maintenance
16539 | 2010 | 7 | 22 | 0.66667 |  | 60 | 284 | 284 | Nepean | 4.16kV | AB03 | The AB03 in the Lisgar/Kent /Lyon area trip, patrol found nothing. | Ottawa | Unknown/Other
7270 | 2005 | 9 | 2 | 0.59861 |  | 204 | 585 | 172 | Nepean | 4.16kV | AB03 | Wind storm knocked conductor down, AB00 & AB06 tripped at the same time. | Ottawa | Adverse Weather | Wind
11254 | 2007 | 9 | 5 | 0.56944 |  | 100 | 38 | 23 | Nepean | 4.16kV | AB03 | Isolated and replaced transformer 55D2B-0654 at 507 Cooper St | Ottawa | Scheduled Outage | Preventive Maintenance
7403 | 2005 | 9 | 29 | 0.61667 |  | 226 | 648 | 172 | Nepean | 4.16kV | AB03 | Tree limb pulled down primary conductor at Lyon and Gloucester,circuit isolated fro repairs | Ottawa | Tree Contacts | Tree Limb Fallen
13466 | 2008 | 10 | 29 | 0.060417 |  | 219 | 628 | 172 | NEPEAN | 4.16kV | AB03 | CLOSED CB | Ottawa | Adverse Weather
13530 | 2008 | 10 | 29 | 0.060417 |  | 219 | 683 | 187 | Nepean | 4.16kV | AB03 | AB03 circuit auto trip, one manual attempt to restore failed. Circuit patrolled and no apparent cause found. AB03 breaker closed from SCADA and held. | Ottawa | Unknown/Other
5859 | 2004 | 11 | 5 | 0.40486 |  | 161 | 1124 | 446 | AB | 4.16kV | AB03, AB06 | Primary wires down at Lyon & Somerset. AB03 tripped & AB06 A/R at 09:27. AB06 opened via scada at 9:43 at request of line crew, live wires on the ground. Mapping shows AB06 as road side cct, closed at 10:33 but this energized damaged cct which was the field side cct, AB06 opened, mapping incorrect. | Ottawa | Adverse Weather | Wind
4769 | 2004 | 2 | 8 | 0.53125 |  | 791 | 26 | 2 | AB | 4.16kV | AB04 | OC transpo bus has hit & broken a pole on Albert st. Tx OTT33 feeding 2 customers one 3 phase at 478 Albert and a rooming house at 494 Albert opened to permit pole replacement. | Ottawa | Foreign Interference | Vehicle
4770 | 2004 | 2 | 8 | 0.66389 |  | 39 | 124 | 191 | AB | 4.16kV | AB04 | OC transpo bus has hit & broken a pole on Albert st. AB04 acb opened via scada to permit pole placement. | Ottawa | Foreign Interference | Vehicle
14155 | 2009 | 4 | 8 | 0.49167 |  | 77 | 4 | 3 | NEPEAN | 4.16kV | AB04 | Transformer X31116 at 478 Albert isolated to allow for transformer change | Ottawa | Scheduled Outage | Preventive Maintenance
20336 | 2012 | 4 | 17 | 0.38542 |  | 124 | 35 | 17 | Nepean | 4.16kV | AB04 | Transformer #X31110 located at 407 Queen St opened by crew to transfer services | Ottawa | Scheduled Outage | Construction
6900 | 2005 | 7 | 11 | 0.31458 |  | 79 | 1 | 1 | Nepean | 4.16kV | AB04 | Fuses blew due to bird contact at pot head at 376 Gloucester St (V387). Caused outage at the Centennial Public School | Ottawa | Foreign Interference | Bird
11047 | 2007 | 8 | 14 | 0.58333 |  | 46 | 8 | 11 | Nepean | 4.16kV | AB04 | Transformer #OTT5803 located at 479 Slater isolated due to transferring to a different phase & re-arranging | Ottawa | Scheduled Outage | Construction
7208 | 2005 | 8 | 25 | 0.33056 |  | 110 | 352 | 192 | Nepean | 4.16kV | AB04 | Duct collapse due to a dig in caused the cable between Nepean sub and Albert and Bay to fail. Load restored on AB00 | Ottawa | Foreign Interference | Dig-in
11233 | 2007 | 9 | 3 | 0.32778 |  | 95 | 24 | 15 | Nepean AB | 8/4.8kV | AB04 | At 481 Slater customer reports vehicle hit pole at Slater and Bay. Red Phase fuse opened up affected three Transformers. 24-7 Crew refused and closed in switch. All load restored to customers. Sue Belzac of Dispatch has sent out email for damage to plant work order number. | Ottawa | Foreign Interference | Vehicle
15110 | 2009 | 9 | 16 | 0.71806 |  | 41 | 4 | 6 | NEPEAN | 4.16kV | AB04 | At 5:14pm, Ottawa Police called in a MVA at Bronson & Slater, customers also starting calling in no power calls. Red Phase switch S28677 was found open and blown. 24-7 crew refused and closed, 6 customers were affected and power was restored at 5:55pm. Nepean (AB04). ID#15110. | Ottawa | Foreign Interference | Vehicle
17568 | 2011 | 2 | 9 | 0.47917 |  | 53 | 10 | 11 | Nepean | 4.16kV | AB05 | Transformer X30771 at 492 Cooper isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
10214 | 2007 | 4 | 5 | 0.47222 |  | 55 | 31 | 34 | Nepean | 4.16kV | AB05 | Transformer #OTT3986 located at 415 Lisgar isolated due to installing new cables on the pole | Ottawa | Scheduled Outage | Construction
18201 | 2011 | 5 | 23 | 0.46111 |  | 10 | 4 | 27 | Nepean | 4.16kV | AB05 | Ottawa fire call reporting pole fire. Smoke was found coming from behing cable quard on AB04 dip 2 in front of 397 somerset. Crew opened Dip 1 and investigated. Found to be cigarette. | Ottawa | Adverse Environment | Fire
8633 | 2006 | 6 | 30 | 0.59028 |  | 8 | 2 | 18 | Nepean | 4.16kV | AB05 | Isolated transformer OTT1671 at 250 Bank St to relocate feed to a different phase | Ottawa | Scheduled Outage | Preventive Maintenance
10974 | 2007 | 7 | 31 | 0.92708 |  | 204 | 3 | 1 | Nepean | 4.16kV | AB05 | Replaced defective transformer at V59 @ 240 Bank. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16728 | 2010 | 8 | 13 | 0.39583 |  | 23 | 7 | 17 | Nepean | 4.16kV | AB05 | Trans at 248 Kent St was isolated to replace a pole for sec upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
17496 | 2011 | 1 | 20 | 0.37153 |  | 65 | 48 | 44 | Nepean | 4.16kV | AB06 | Transformer #X37961 located at 733 Cooper opened by crew for a change over | Ottawa | Scheduled Outage | Construction
20118 | 2012 | 3 | 3 | 0.79167 |  | 250 | 83 | 20 | Nepean | 4.16kV | AB06 | A broken cutout at transformer X31168 at 116 Percy St | Ottawa | Adverse Weather | Wind
18050 | 2011 | 4 | 28 | 0.55347 |  | 7 | 70 | 603 | Nepean | 4.16kV | AB06 | AB06 CB tripped during wind/lightning storm. Closed via scada and held. | Ottawa | Adverse Weather | Wind
20901 | 2012 | 6 | 28 | 0.44097 |  | 77 | 56 | 44 | Nepean | 4.16kV | AB06 | Transformer X37961 at 733 Cooper St. isolated to allow for service upgrade | Ottawa | Scheduled Outage
7273 | 2005 | 9 | 2 | 0.63403 |  | 266 | 1215 | 274 | Nepean | 4.16kV | AB06 | AB06 breaker opened manually from SCADA when conductor was found down during patrol. Circuit auto reclosed earlier at 14:22. | Ottawa | Adverse Weather | Wind
11249 | 2007 | 9 | 5 | 0.36458 |  | 191 | 48 | 15 | Nepean | 4.16kV | AB06 | At 08:45 trans at 725 Cooper St was isolated in order to replace a PCB trans | Ottawa | Scheduled Outage | Preventive Maintenance
5783 | 2004 | 9 | 7 | 0.41736 |  | 205 | 448 | 131 | Nepean | 4.16kV | AB06 | 4KV vault V198 @ 175 Bronson was isolated for routine planned maitenance | Ottawa | Scheduled Outage | Preventive Maintenance
15671 | 2010 | 1 | 19 | 0.80208 |  | 15 | 7 | 28 | Nepean | 4.16kV | AB07 | Isolated transformer X31001 at 255 Nepean St to repaire open wire service | Ottawa | Scheduled Outage | Emergency Services Request
4797 | 2004 | 2 | 18 | 0.50764 |  | 17 | 42 | 147 | Nepean | 4.16kV | AB07 | Overhead let go from dead end pole, conductor was only being supported by a line clamp at dip pole. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14935 | 2009 | 8 | 12 | 0.22222 |  | 8 | 22 | 162 | Nepean | 4.16kV | AB07 | OFD reports O/H fuse burning up at Bank & Nepean, Crews found broken cutout at AB07-DIP1 (on Nepean West of Bank). Crew reports SA00-AB07 is siezed, Circuit dumped to make repairs. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11283 | 2007 | 9 | 10 | 0.54167 |  | 120 | 52 | 26 | Nepean | 4.16kV | AB07 | Transformer #OTT4669 at 255 Nepean St isolated to allow for replacement of transformer | Ottawa | Scheduled Outage | Preventive Maintenance
13747 | 2008 | 12 | 14 | 0.33333 |  | 130 | 58 | 27 | Nepean | 4.16kV | AB07 | Isolated transformer X31021 at 177 Nepean St to work on secondary buss in man hole | Ottawa | Scheduled Outage | Preventive Maintenance
9515 | 2006 | 10 | 26 | 0.41667 |  | 96 | 21 | 13 | Dagmar | 4.16kV | AC 05 | Transformer TE 1445 was isolated to allow PCB transf. Change @ 1728Ambrose | Ottawa | Scheduled Outage | Preventive Maintenance
9516 | 2006 | 10 | 26 | 0.43056 |  | 192 | 38 | 12 | Dagmar | 4.16kV | AC 07 | Mike Gruich established a WP on transf. @ 124 Lebrun and changed it as part of the PCB program | Ottawa | Scheduled Outage | Preventive Maintenance
7807 | 2006 | 1 | 14 | 0.84236 |  | 57 | 5 | 5 | DAGMAR | 4.16kV | AC02 | CONNECTION AT TOP OF SWITCH FOUND BROKEN. CONNECTION REPAIRED ALL POWER RESTORED. | Ottawa | Adverse Weather | Wind
20279 | 2012 | 4 | 4 | 0.33333 |  | 323 | 75 | 14 | Dagmar | 4.16kV | AC02 | Transformer X29189 at 143 Carillon St. isolated to allow for pole replacement | Ottawa | Scheduled Outage | Construction
20280 | 2012 | 4 | 4 | 0.33333 |  | 323 | 258 | 48 | Dagmar | 4.16kV | AC02 | Transformer X29191 at 189 Carillon St. isolated to allow for pole replacement | Ottawa | Scheduled Outage | Construction
20381 | 2012 | 4 | 24 | 0.63542 |  | 28 | 6 | 13 | Dagmar | 4.16kV | AC02 | Transformer X29279 at 209 Hannah was isolated for contractor to reconfigure plant. | Ottawa | Scheduled Outage
20392 | 2012 | 4 | 25 | 0.33333 |  | 240 | 52 | 13 | Dagmar | 4.16kV | AC02 | Isolated transformer X29279 at 209 Hannah St to replace the pole | Ottawa | Scheduled Outage | Construction
20393 | 2012 | 4 | 25 | 0.49306 |  | 10 | 3 | 20 | Dagmar | 4.16kV | AC02 | X29184 at 199 Ethel was isolated to reconfigure secondary conductor. | Ottawa | Scheduled Outage
20440 | 2012 | 5 | 2 | 0.35417 |  | 270 | 90 | 20 | Dagmar | 4.16kV | AC02 | Isolated transformer X29184 at 199 Ethel St to transfer hydro plant | Ottawa | Scheduled Outage | Construction
20443 | 2012 | 5 | 2 | 0.4375 |  | 315 | 100 | 19 | Dagmar | 4.16kV | AC02 | Transformer #X29431 located at 176 Dagmar Ave opened by crew for pole replacement. | Ottawa | Scheduled Outage | Repair
8267 | 2006 | 5 | 10 | 0.125 |  | 105 | 10 | 6 | Dagmar | 4.16kV | AC02 | J. Lablanc reports O/H transformer opened to allow fire department to fight house fire @ 241 Carillon st in Vanier. J. Lablanc reports 241& 243 Carillon was damage by fire. | Ottawa | Adverse Environment | Fire
9501 | 2006 | 10 | 24 | 0.41667 |  | 125 | 17 | 8 | Dagmar | 4.16kV | AC02 | Isolate & replace Transf. @101 carillon as / PCB program | Ottawa | Scheduled Outage | Preventive Maintenance
17191 | 2010 | 10 | 28 | 0.50694 |  | 71 | 6 | 5 | Dagmar | 4.16kV | AC02 | Transformer #X24514 located at 83 Carillon opened due to broken lead from cutout. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15849 | 2010 | 3 | 25 | 0.86597 |  | 58 | 14 | 15 | Dagmar | 4.16kV | AC03 | Transformer #K965 located at 41 Jeanneville Pvt opened up due to broken lead on primary dip | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20375 | 2012 | 4 | 24 | 0.33333 |  | 202 | 40 | 12 | Dagmar | 4.16kV | AC03 | Transformer X21676 isolated for contractor to change pole at Hannah and Carillon | Ottawa | Scheduled Outage
20421 | 2012 | 4 | 30 | 0.5 |  | 230 | 126 | 33 | Dagmar | 4.16kV | AC03 | Transformer X29183 at 190 Montfort St. isolated for transformer upgrade | Ottawa | Scheduled Outage | Construction
20427 | 2012 | 5 | 1 | 0.33333 |  | 230 | 73 | 19 | Dagmar | 4.16kV | AC03 | Transformer X29180 at 146 Montfort St. and X29181 at 162 Montfort St. isolated to allow for transfer of plant | Ottawa | Scheduled Outage | Construction
20431 | 2012 | 5 | 1 | 0.68056 |  | 111 | 7 | 4 | Dagmar | 4.16kV | AC03 | Transformer X29179 at 201 Baribeau St. isolated to allow for pole replacement | Ottawa | Scheduled Outage | Construction
6788 | 2005 | 6 | 23 | 0.74306 |  | 60 | 4 | 4 | Dagmar | 4.16kV | AC03 | Transformer #X01445 located at Montreal Rd/Hannah Ave isolated to change a leaking transformer | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7129 | 2005 | 8 | 12 | 0.52153 |  | 11 | 1 | 6 | Dagmar | 4.16kV | AC03 | Isolated Transformer at 260 Hannah to remove a hazard,.( Wire close to Transformerr) | Ottawa | Scheduled Outage | Preventive Maintenance
9248 | 2006 | 9 | 19 | 0.42014 |  | 41 | 1 | 2 | Dagmar | 4.16kV | AC03 | Isolated 3 phase transformer P392 at 276 Emond St to replace broken switch (PC10A#5) | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19323 | 2011 | 10 | 5 | 0.35417 |  | 150 | 25 | 10 | Dagmar | 4.16kV | AC03 | Transformer #X29446 located at 224 Emond St opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
19362 | 2011 | 10 | 12 | 0.35417 |  | 260 | 43 | 10 | Dagmar | 4.16kV | AC03 | Transformer #X29446 located at 224 Emond St opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
19363 | 2011 | 10 | 12 | 0.39583 |  | 200 | 83 | 25 | Dagmar | 4.16kV | AC03 | Transformer #X29445 located at 214 Emond St opened by crew for a pole change | Ottawa | Scheduled Outage
9426 | 2006 | 10 | 13 | 0.54861 |  | 55 | 6 | 6 | Dagmar | 4.16kV | AC03 | Transformer located at 247 Durocher isolated to for PCB transformer replacement. PC10A #1058 | Ottawa | Scheduled Outage | Preventive Maintenance
19409 | 2011 | 10 | 19 | 0.35417 |  | 240 | 56 | 14 | Dagmar |  | AC03 | Isolated transformer X29193 at 212 Deschamps Ave to transfer hydro plant | Ottawa | Scheduled Outage | Construction
19413 | 2011 | 10 | 19 | 0.54861 |  | 200 | 47 | 14 | Dagmar | 4.16kV | AC03 | Transformer X29373 at 236 Deschamps Ave isolated to allow for streetlight repairs | Ottawa | Scheduled Outage | Repair
9478 | 2006 | 10 | 20 | 0.375 |  | 170 | 14 | 5 | Dagmar | 4.16kV | AC03 | Transformer located at 265 Emond isolated for PCB transformer replacement. PC10A #1160 | Ottawa | Scheduled Outage | Preventive Maintenance
9503 | 2006 | 10 | 24 | 0.44514 |  | 209 | 35 | 10 | Dagmar | 4.16kV | AC03 | isolate & replace transf. @ 217 Desraurier for PCB program | Ottawa | Scheduled Outage | Preventive Maintenance
19539 | 2011 | 11 | 7 | 0.35417 |  | 180 | 27 | 9 | Dagmar | 13.2kV | AC03 | Transformer X29371 at 261 1/2 Olmstead St isolated for pole change | Ottawa | Scheduled Outage | Construction
19540 | 2011 | 11 | 7 | 0.35417 |  | 180 | 18 | 6 | Woodroffe | 13.2kV | AC03 | Transformer X29325 at 222 Deschamps Ave. Isolated to allow for pole change | Ottawa | Scheduled Outage
19665 | 2011 | 12 | 3 | 0.36111 |  | 285 | 285 | 60 | Dagmar | 4.16kV | AC03 | The O/H on Desrosiers was isolated to allow the crew to replace a pole. | Ottawa | Scheduled Outage | Preventive Maintenance
19666 | 2011 | 12 | 3 | 0.35417 |  | 310 | 10 | 2 | DAGMAR | 4.16kV | AC03 | Transformer X29195 at 134 Deschamps Ave isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
11939 | 2008 | 1 | 15 | 0.42361 |  | 10 | 1 | 6 | Dagmar | 4.16kV | AC04 | Isolated transformer at 169 Duford St to replace connections and fuse for the streetlight | Ottawa | Scheduled Outage | Repair
19854 | 2012 | 1 | 18 | 0.20833 |  | 167 | 1475 | 530 | Dagmar | 4.16kV | AC04 | AC04 was opened by System Office due to a downed conductor at Montfort/Bradley. | Ottawa | Adverse Weather | Wind (not Trees)
14088 | 2009 | 3 | 23 | 0.39583 |  | 300 | 65 | 13 | DAGMAR | 4.16kV | AC04 | transformer X23295 at 322 St.Denis isolated - no reason for outage indicated | Ottawa | Scheduled Outage | Repair
18250 | 2011 | 5 | 30 | 0.46528 |  | 220 | 33 | 9 | Dagamar | 4.16kV | AC04 | Trans X29331 ata 9 Newark was isolated in order to transfer plant to new poles | Ottawa | Scheduled Outage | Construction
20860 | 2012 | 6 | 24 | 0.73333 |  | 94 | 52 | 33 | Dagmar | 4.16kV | AC04 | At 17:36 crews established a PC10A on a radial section of AC04 on L'allemand in Vanier because a large tree limb on our line. Hydro Ottawa crews waited from 14:50 to 17:36 for the city of Ottawa tree trimmers to show up on site. 33 customers affected. Dagmar AC04 ID# 20860 | Ottawa | Tree Contacts | Tree Limb Fallen
18595 | 2011 | 7 | 6 | 0.35417 |  | 210 | 32 | 9 | Dagmar | 4.16kV | AC04 | Transformer X23749 at 332 St Denis isolated replacment. | Ottawa | Scheduled Outage | Construction
18870 | 2011 | 8 | 2 | 0.35417 |  | 300 | 180 | 36 | Dagmar | 4.16kV | AC04 | Black & Mac replaced a defective pole on Granville St. | Ottawa | Scheduled Outage | Preventive Maintenance
13110 | 2008 | 8 | 18 | 0.67986 |  | 265 | 798 | 211 | Dagmar | 4.16kV | AC04 | The AC04 breaker tripped because of wires down on Granville. Crews isolated the O/H and the breaker was closed in VIA scada, the breaker was reopen after repairs were made to close in inline switches to pick up the remaining customers. | Ottawa | Adverse Weather | Lightning
19158 | 2011 | 9 | 13 | 0.62083 |  | 13 | 114 | 527 | Dagmar |  | AC04 | AC04 circuit opened during lightning storm. Closed via SCADA and is holding. | Ottawa | Lightning
9461 | 2006 | 10 | 18 | 0.49653 |  | 103 | 9 | 5 | Dagmar | 4.16kV | AC04 | Isolated and replaced transformer at 324 Ste Cecile St (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
19470 | 2011 | 10 | 26 | 0.4375 |  | 86 | 14 | 10 | Dagmar | 4.16kV | AC04 | Trans X23696 at 127 Granville St was isolated in order to transfer transformer and plant to new pole | Gloucester | Scheduled Outage | Construction
9561 | 2006 | 10 | 30 | 0.55556 |  | 109 | 15 | 8 | Dagmar | 4.16kV | AC04 | Power was isolated to change PCB trf. # 23691 @ 117 Duford | Ottawa | Scheduled Outage | Preventive Maintenance
19509 | 2011 | 11 | 1 | 0.35903 |  | 231 | 847 | 220 | Dagmar | 4.16kV | AC04 | AC04 overhead circuit from Temp 152 (at pole X21927) to end of line on Granville was isolated to allow crews to replace poles. | Ottawa | Scheduled Outage | Construction
19512 | 2011 | 11 | 1 | 0.54583 |  | 270 | 166 | 37 | Dagmar | 4.16kV | AC04 | AC04 red phase section on Grandmaitre was isolated from S27248 to end of line to allow crew to replace poles. | Ottawa | Scheduled Outage | Construction
13956 | 2009 | 2 | 11 | 0.42361 |  | 20 | 3 | 9 | DAGMAR | 13.2kV | AC05 | xfmr X26098 at 246 Feriand St isolated to allow for new service to infill | Ottawa | Scheduled Outage | Construction
13958 | 2009 | 2 | 11 | 0.42361 |  | 20 | 3 | 9 | Dagmar | 13.2kV | AC05 | Transformer #X26098 located at 246 Feriand St isolated to allow for a new service on an infill. | Ottawa | Scheduled Outage | Preventive Maintenance
20007 | 2012 | 2 | 13 | 0.33333 |  | 240 | 52 | 13 | Dagmar | 4.16kV | AC05 | Isolated transformer X334604 at 65 Jolliet Ave to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Construction
20009 | 2012 | 2 | 14 | 0.33333 |  | 140 | 30 | 13 | Dagmar | 4.16kV | AC05 | Transformer X23596 at 51 Jolliet Ave. isolated by Black and Mac to transfer plant to X44530 | Ottawa | Scheduled Outage | Preventive Maintenance
4796 | 2004 | 2 | 17 | 0.43056 |  | 60 | 8 | 8 | Dagmar | 4.16kV | AC05 | Replace the transformer at 152 Dagmar. | Ottawa | Scheduled Outage | Repair
17632 | 2011 | 2 | 22 | 0.41667 |  | 200 | 27 | 8 | Dagmar | 4.16kV | AC05 | transformer at pole X23466 in the Dagmar area was openned to allow crews to move pole. 3 customers affected for 200 minutes. | Ottawa | Scheduled Outage | Construction
17635 | 2011 | 2 | 22 | 0.41667 |  | 241 | 16 | 4 | DAGMAR | 4.16kV | AC05 | Transformer X23466 at 275 Michel Circle isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
17647 | 2011 | 2 | 25 | 0.375 |  | 200 | 93 | 28 | Dagmar | 4.16kV | AC05 | Isolated overhead primary feeding two transformers X23468 at 265 Michel Cir and X23466 at 275 Michel Cir to replace a pole | Ottawa | Scheduled Outage | Construction
17677 | 2011 | 3 | 8 | 0.38542 |  | 165 | 58 | 21 | DAGMAR | 4.16kV | AC05 | Transformer X24360 at 42 St. Charles isolated to allow transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
17691 | 2011 | 3 | 9 | 0.38542 |  | 205 | 72 | 21 | Dagmar | 4.16kV | AC05 | Transformer X23461at 68 Lavergne St. isolated for transfer of plant | Ottawa | Scheduled Outage | Construction
10203 | 2007 | 3 | 29 | 0.41667 |  | 142 | 17 | 7 | Dagmar | 4.16kV | AC05 | At 10:00 trans at 79 Geneva St was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
14161 | 2009 | 4 | 9 | 0.54097 |  | 247 | 454 | 245 | Dagmar | 4.16kV | AC05 | Dagmar AC05 circuit auto tripped due to a cement truck contacting the O/H circuit. Conductor was broken and circuit was isolated to complete repairs. | Ottawa | Foreign Interference | Vehicle
14220 | 2009 | 4 | 26 | 0.5375 |  | 32 | 131 | 245 | Dagmar | 4.16kV | AC05 | A tree fell on the primary on Michel cir, the circuit had to be isolated for removal. | Ottawa | Tree Contacts | Tree Fallen
16130 | 2010 | 5 | 24 | 0.95 |  | 17 | 4 | 14 | Dagmar | 4.16kV | AC05 | At 22:48 tansformer at 38 LAVERGNE ST VANIER was isolated in order to make repairs to damaged sec services from trees | Ottawa | Tree Contacts | Tree Limb Fallen
12726 | 2008 | 6 | 25 | 0.41736 |  | 124 | 31 | 15 | Dagmar | 4.16kV | AC05 | 2 transformers isolated (X24731 & 65A3D-0344 located at 161 & 169 Genest due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
12731 | 2008 | 6 | 26 | 0.55556 |  | 100 | 17 | 10 | Dagmar | 4.16kV | AC05 | Transformer #X24731 located at 165 Genest St Vanier isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
3791 | 2003 | 7 | 27 | 0.91111 |  | 8 | 1 | 7 | Dagmar | 4.16kV | AC05 | An overhead transformer feeding a 7-unit apt building at 71 St. Charles was interrupted to repair primary neutral connections in order to alleviate flickering lights. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14917 | 2009 | 8 | 5 | 0.53333 |  | 86 | 19 | 13 | Dagmar | 4.16kV | AC05 | Isolated transformer X29443 at 91 At. Ambroise St to replace connectiions on secondary service | Ottawa | Scheduled Outage | Emergency Services Request
13022 | 2008 | 8 | 8 | 0.46181 |  | 124 | 21 | 10 | Dagmar | 4.16kV | AC05 | Transformer #X24731 located at 157 Genest St isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
18893 | 2011 | 8 | 8 | 0.41667 |  | 165 | 96 | 35 | Dagmar | 4.16kV | AC05 | Isolated transformer X24369 and X24368 at 100 Alice St to install new poles | Ottawa | Scheduled Outage | Construction
18899 | 2011 | 8 | 9 | 0.35417 |  | 180 | 180 | 60 | Dagmar | 4.16kV | AC05 | 5 transformers isolated in the Damgar area to allow crews to update services. | Ottawa | Scheduled Outage | Construction
18943 | 2011 | 8 | 16 | 0.35417 |  | 120 | 34 | 17 | Dagmar | 4.16kV | AC05 | Switch S12519 was opened to isolate overhead circuit between St. Ambrose, and St. Charles for pole replacement. | Ottawa | Scheduled Outage | Construction
13132 | 2008 | 8 | 21 | 0.41667 |  | 120 | 32 | 16 | Dagmar | 4.16kV | AC05 | Transformer #X24367 located at 74 Genest isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
13184 | 2008 | 9 | 3 | 0.43542 |  | 63 | 10 | 10 | DAGMAR | 4.16kV | AC05 | Transformer #X24367 at 71 Genest St isolated to allow for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9408 | 2006 | 10 | 10 | 0.43403 |  | 175 | 18 | 6 | Dagmar | 4.16kV | AC05 | Transformer located at 113 Alice St isolated for service upgrade. PC10A #100 | Ottawa | Scheduled Outage | Preventive Maintenance
9409 | 2006 | 10 | 10 | 0.43403 |  | 176 | 21 | 7 | Dagmar | 4.16kV | AC05 | Transformer located at 120 Alice St isolated for service upgrade. PC10A #99 | Ottawa | Scheduled Outage | Preventive Maintenance
9438 | 2006 | 10 | 16 | 0.52431 |  | 55 | 28 | 30 | Dagmar | 4.16kV | AC05 | Transformer #65A3D-0037 located at 150 Barrette St isolated to change transformer due to PCB change as per PC10A#1118 | Ottawa | Scheduled Outage | Preventive Maintenance
9494 | 2006 | 10 | 23 | 0.52431 |  | 99 | 13 | 8 | Dagmar | 4.16kV | AC05 | Transformer location @ 262 Shakespeare was isolated to change transformer for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
7576 | 2005 | 11 | 7 | 0.025694 |  | 138 | 23 | 10 | DAGMAR | 4.16kV | AC05 | M. Byers reports hot line lead has now been replaced. All power restored to normal | Ottawa | Adverse Weather | Wind
4767 | 2004 | 2 | 5 | 0.39931 |  | 177 | 118 | 40 | Dagmar | 4.16kV | AC06 | Transformer interrupted to replace pole. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20243 | 2012 | 3 | 27 | 0.35417 |  | 330 | 44 | 8 | Dagmar | 4.16kV | AC06 | Isolated transformer X23158 at 198 Marier St to transfer hydro plant | Ottawa | Scheduled Outage | Construction
3396 | 2003 | 5 | 2 | 0.67014 |  | 33 | 2 | 4 | Dagmar | 4.16kV | AC06 | Transformer at 219 Carillon opened to safely reconnect customer in arrears. | Ottawa | Scheduled Outage | Repair
16214 | 2010 | 6 | 7 | 0.46528 |  | 50 | 8 | 10 | Dagmar | 4.16kV | AC06 | Transformer #X23106 located at 108 Putman Ave opened by crew to install new 600 volt transformer bank | Ottawa | Scheduled Outage | Construction
16255 | 2010 | 6 | 12 | 0.85556 |  | 4 | 1 | 10 | Dagmar DS | 4.16kV | AC06 | Transformer X23281 at 27 Langevin Ave was opened so crews could clear a dead racooon from the top of the transformer. Callers were complaining that the smell was bad. | Ottawa | Foreign Interference | Animal
12892 | 2008 | 7 | 18 | 0.67708 |  | 10 | 1 | 5 | Dagmar | 4.16kV | AC06 | Transformer #X23590 located at 96 Putman isolated in order to drop the service for 99 Putman that was laying across the street due to a tree that fell on it | Ottawa | Tree Contacts | Tree Fallen
19058 | 2011 | 8 | 31 | 0.31667 |  | 234 | 74 | 19 | Dagmar | 4.16kV | AC06 | Transformer X23282 at 81 Beechwood and X23281 at 27 Langevin isolated to allow for pole change | Ottawa | Scheduled Outage | Construction
9450 | 2006 | 10 | 17 | 0.42431 |  | 114 | 15 | 8 | Dagmar |  | AC06 | Isolated and replaced transformer 23715 at 137 Marier Ave | Ottawa | Scheduled Outage | Preventive Maintenance
9743 | 2006 | 11 | 28 | 0.42639 |  | 46 | 17 | 22 | Dagmar | 4.16kV | AC06 | At 10:14 trans at 34 Douglas Ave was isolated to re-arrange plant for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15625 | 2010 | 1 | 7 | 0.48611 |  | 20 | 6 | 19 | Dagmar | 4.16kV | AC07 | Transformer #X23457 located at 146 Jolliet isolated to change triplex service | Ottawa | Scheduled Outage | Construction
13871 | 2009 | 1 | 15 | 0.70972 |  | 18 | 6 | 19 | DAGMAR | 4.16kV | AC07 | Transformer X39293 at rear of 142 Lebrun isolated to allow for repairs to secondary connections at pole | Ottawa | Scheduled Outage | Repair
17491 | 2011 | 1 | 18 | 0.38611 |  | 171 | 100 | 35 | Dagmar | 4.16kV | AC07 | Switch S23733 feeding customers on Longpre and Tabor was opened for crews to perform tree trimming. | Ottawa | Scheduled Outage | Preventive Maintenance
19938 | 2012 | 1 | 31 | 0.375 |  | 270 | 94 | 21 | Dagmar | 4.16kV | AC07 | Trans at 151 Jolliett St was isolated in order to install a new pole | Ottawa | Scheduled Outage
19981 | 2012 | 2 | 7 | 0.5625 |  | 120 | 64 | 32 | Dagmar | 4.16kV | AC07 | Transformer #X23458 located at 135 Jolliet Ave opened by crew to install new transformer and transfer plant | Ottawa | Scheduled Outage | Construction
19982 | 2012 | 2 | 7 | 0.33333 |  | 300 | 100 | 20 | Dagmar | 4.16kV | AC07 | Transformer #X23459 located at 113 Jolliet Ave opened by crew to install new transformer and transfer plant | Ottawa | Scheduled Outage | Construction
17563 | 2011 | 2 | 8 | 0.42708 |  | 153 | 20 | 8 | DAGMAR | 4.16kV | AC07 | Transformer X29449 at 135 Ste. Cecile isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
19987 | 2012 | 2 | 8 | 0.33333 |  | 143 | 48 | 20 | DAGMAR | 4.16kV | AC07 | Transformer X23459 at 113 Jolliet Ave isolated to transfer plant | Ottawa | Scheduled Outage | Construction
17634 | 2011 | 2 | 22 | 0.42361 |  | 246 | 33 | 8 | Dagmar | 4.16kV | AC07 | Trans at 135 Ste Cecile ST was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
17638 | 2011 | 2 | 23 | 0.36111 |  | 253 | 93 | 22 | Dagmar | 4.16kV | AC07 | At 08:40 trans at 127 STE. CECILE ST VANIER was isolated in order to transfer plant and load to new transformer | Ottawa | Scheduled Outage | Construction
17640 | 2011 | 2 | 24 | 0.45833 |  | 110 | 40 | 22 | Dagmar | 4.16kV | AC07 | Trans at 115 Ste Cecile St isolated trans in order to transfer plant | Ottawa | Scheduled Outage | Construction
17641 | 2011 | 2 | 24 | 0.375 |  | 358 | 54 | 9 | Dagmar | 4.16kV | AC07 | Transformer #X23465 located at 287 Michele isolated by crew to install pole with crane | Ottawa | Scheduled Outage | Construction
20082 | 2012 | 2 | 29 | 0.35417 |  | 240 | 60 | 15 | Dagmar | 4.16kV | AC07 | Isolated transformer X23472 at 251 St Monique St to install new pole | Ottawa | Scheduled Outage | Construction
17664 | 2011 | 3 | 3 | 0.42708 |  | 130 | 46 | 21 | Dagmar | 4.16kV | AC07 | Transformer #X23467 located at 268 Michel isolated by crew to replace transformer. | Ottawa | Scheduled Outage | Construction
17675 | 2011 | 3 | 7 | 0.425 |  | 94 | 13 | 8 | Dagmar | 4.16kV | AC07 | Trans at 68 Lavergne St was isolated inorder to install new sec service conductors | Ottawa | Scheduled Outage | Construction
20139 | 2012 | 3 | 7 | 0.33333 |  | 225 | 71 | 19 | Dagmar | 4.16kV | AC07 | Isolated transformer X23471 at 80 Lavergne St to replace the pole | Ottawa | Scheduled Outage | Construction
20142 | 2012 | 3 | 7 | 0.5625 |  | 150 | 12 | 5 | Dagmar | 4.16kV | AC07 | Transformer #X23469 located at 110 Lavergne St opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
17679 | 2011 | 3 | 8 | 0.39931 |  | 135 | 18 | 8 | Dagmar | 4.16kV | AC07 | At 09:35 switch S13238 at 114 Lebrun Street was isolated to allow crew to reconfigure plant for voltage conversion. 8 customers were affected for 135 minutes. (Dagmar AC07) ID# 17679 | Ottawa | Scheduled Outage | Construction
17682 | 2011 | 3 | 8 | 0.39583 |  | 140 | 21 | 9 | Dagmar | 4.16kV | AC07 | Isolated transformer X37658 at 301 Michel St to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Construction
17710 | 2011 | 3 | 14 | 0.38542 |  | 255 | 38 | 9 | Dagmar | 4.16kV | AC07 | Transformer #X23465 located at 289 Michel Circ opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
17812 | 2011 | 3 | 31 | 0.39236 |  | 222 | 44 | 12 | Dagmar | 4.16kV | AC07 | Transformer #X29277 located at 195 Ste. Monique opened by crew to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
10684 | 2007 | 6 | 20 | 0.53333 |  | 123 | 20 | 10 | Dagmar | 4.16kV | AC07 | Transformer #K00750 located at 202 Peres Blance isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
8596 | 2006 | 6 | 27 | 0.010417 |  | 55 | 16 | 18 | Dagmar | 4.16kV | ac07 | Bad cut out found on AC07 caused outage to two apartment complexes on Lavergne & Le Brun in Vanier. Crew replaced cutout and restored all power. | Ottawa | Unknown/Other | No Apparent Cause
11272 | 2007 | 9 | 8 | 0.050694 |  | 69 | 12 | 10 | Dagmar | 4.16kV | AC07 | O/H transformer between 140 Taber, Vanier was interrupted by tree branches. Tree branches were trimmed & transfomer refused. | Ottawa | Tree Contacts | Inadequate Trimming
19200 | 2011 | 9 | 19 | 0.36806 |  | 220 | 70 | 19 | DAGMAR | 4.16kV | AC07 | ISOLATED TRANSFORMER X24749 AT 93 MARQUETTE AVE FOR POLE REPLACMENT | Ottawa | Scheduled Outage | Construction
19204 | 2011 | 9 | 19 | 0.54167 |  | 180 | 42 | 14 | Dagmar | 4.16kV | AC07 | Transformer #X23174 located at 109 Marquette opened by crew for a pole replacement | Ottawa | Scheduled Outage | Construction
15194 | 2009 | 10 | 1 | 0.375 |  | 440 | 257 | 35 | DAGMAR | 4.16kV | AC07 | CREW ISOLATED 3 TRANSFORMERS TO CHANGE POLES AND HYDRO PLANT ON LAVERGNE ST/LEBRUN ST AND MICHEL CIRCLE | Ottawa | Scheduled Outage | Construction
15221 | 2009 | 10 | 6 | 0.375 |  | 336 | 560 | 100 | Dagmar | 4.16kV | AC07 | A section of AC07 from temp 139 to EOL was isolated for planned pole replacements. Customers on Michel circle & Lebrun st affected. | Ottawa | Scheduled Outage | Construction
9457 | 2006 | 10 | 18 | 0.41806 |  | 77 | 6 | 5 | Dagmar | 4.16kV | AC07 | Transformer located at 133 Marquette isolated to change transformer due to PCB content as per PC10A#1156 | Ottawa | Scheduled Outage | Preventive Maintenance
9477 | 2006 | 10 | 20 | 0.375 |  | 140 | 16 | 7 | Dagmar | 4.16kV | AC07 | Transformer located at 140 Lavergne isolated to change transformer due to PCB content as per PC10A#1098 | Ottawa | Scheduled Outage | Preventive Maintenance
9484 | 2006 | 10 | 20 | 0.52431 |  | 60 | 7 | 7 | Dagmar | 4.16kV | AC07 | Transformer located at 186 Lavergne isolated to change transformer due to PCB content as per PC10A#1097 | Ottawa | Scheduled Outage | Preventive Maintenance
9491 | 2006 | 10 | 23 | 0.36111 |  | 30 | 8 | 17 | Dagmar | 4.16kV | AC07 | isolated transformer ott 5999 @ 66 stewart st. to repair service | Ottawa | Scheduled Outage | Repair
9493 | 2006 | 10 | 23 | 0.52778 |  | 92 | 12 | 8 | Dagmar | 4.16kV | AC07 | Transformer #23472 located at 251 Ste. Monique isolated to change transformer due to PCB content as per PC10A#1062 | Ottawa | Scheduled Outage | Preventive Maintenance
4339 | 2003 | 10 | 24 | 0.56042 |  | 48 | 10 | 12 | Dagmar | 4.16kV | AC07 | Transformer#554437 was opened to replace a service to 87 Jolliette | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9578 | 2006 | 11 | 1 | 0.39792 |  | 230 | 31 | 8 | Dagmar | 4.16kV | AC07 | Isolated and replaced transformer at 158 Labrun St PCB oil | Ottawa | Scheduled Outage | Preventive Maintenance
7558 | 2005 | 11 | 3 | 0.54514 |  | 57 | 9 | 9 | Dagmar | 4.16kV | AC07 | Transformer located at 139 Longpre isolated to replace triplex | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17265 | 2010 | 11 | 13 | 0.57986 |  | 80 | 13 | 10 | Dagmar | 4.16kV | AC07 | Transformer #X23153 located at 179 Longpre opened by crew for a service upgrade | Ottawa | Scheduled Outage | Construction
19691 | 2011 | 12 | 6 | 0.53056 |  | 31 | 7 | 13 | Dagmar | 4.16kV | AC07 | Transformer #X21942 located at 145 Ste. Cecile St opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
19715 | 2011 | 12 | 13 | 0.35417 |  | 225 | 131 | 35 | Dagmar | 4.16kV | AC07 | At 08:30 a section of overhead line was isoalated to allow crew to install a new pole. 35 customers were affected for 131 minutes. Dagmar (AC07) ID#19715 | Ottawa | Scheduled Outage
19717 | 2011 | 12 | 14 | 0.35417 |  | 158 | 105 | 40 | Dagmar | 4.16kV | AC07 | At 08:30 overhead line section from TEMP12 to end of line was isolated to allow crew to replace a pole. 40 customers were affected for 158 minutes. Dagmar (AC07) ID# 19717 | Ottawa | Scheduled Outage
13782 | 2008 | 12 | 19 | 0.39583 |  | 270 | 32 | 7 | Hillcrest | 4.16kV | AC13 | At 09:30 trans at DOVERCOURT AVE/BROADVIEW AVE was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
6114 | 2005 | 1 | 1 | 0.61458 |  | 32 | 1 | 1 | Dagmar | 4.16kV | AC14 | Replaced 3 switchers feeding P57 at 435 Montreal Rd | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17562 | 2011 | 2 | 7 | 0.96667 |  | 12 | 4 | 18 | dagmar | 4.16kV | AC14 | At 23:12 crew opened transformer X39297 at 211 Ethel due to sparking wire. 18 customers affected for 12 mins. Dagmar AC14 ID# 17562 | Ottawa | Unknown/Other
10036 | 2007 | 2 | 19 | 0.39583 |  | 45 | 3 | 4 | Dagmar | 4.16kV | AC14 | Glen Carswell isolated TRF. @ 275 Bradley to change a service | Ottawa | Scheduled Outage | Preventive Maintenance
20184 | 2012 | 3 | 20 | 0.53125 |  | 25 | 7 | 16 | Dagmar | 4.16kV | AC14 | Trans X23156 at 241 Ethel St was isolated in order to set a pole | Ottawa | Scheduled Outage
20272 | 2012 | 4 | 3 | 0.3875 |  | 302 | 133 | 29 | Dagmar |  | AC14 | at 9:08am, AC14 O/H circuit on Anne St was isolated to allow crrews to transfer plant to new pole line | Ottawa | Scheduled Outage | Construction
6445 | 2005 | 4 | 23 | 0.027778 |  | 105 | 2 | 1 | AC | 4.16kV | AC14 | On call crew called in to replace leaking 150kva, 4kv xfmr, P345 at 350 Montreal rd. Spill report by dispatch. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10337 | 2007 | 4 | 28 | 0.74306 |  | 54 | 7 | 8 | Dagmar | 4.16kV | AC14 | Called in by Ottawa Fire. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20472 | 2012 | 5 | 7 | 0.44792 |  | 138 | 55 | 24 | Dagmar | 4.16kV | AC14 | At 10:45, transformer X21903 was isolated to allow crews to transfer plant. 24 customers affected for 138 minutes. Dagmar (AC14) ID #20472 | Ottawa | Scheduled Outage
20484 | 2012 | 5 | 9 | 0.53125 |  | 144 | 43 | 18 | Dagmar | 4.16kV | AC14 | AC14 isolated at the intersection of Marier & Ethel to replace Pole X231156 and transfer plant. Three transformers off X23156, X23157 and X29337 affecting 18 customers. | Ottawa | Scheduled Outage | Preventive Maintenance
18123 | 2011 | 5 | 10 | 0.38889 |  | 298 | 79 | 16 | Dagmar | 4.16kV | AC14 | Transformer X29338 at 239 Ethel St. Isolated to allow for pole and transformer change | Ottawa | Scheduled Outage | Preventive Maintenance
20639 | 2012 | 5 | 30 | 0.33333 |  | 500 | 200 | 24 | Dagmar | 4.16kV | AC14 | Transformer X21903 at 254 Ste. Anne St isolated to transfer plant | Ottawa | Scheduled Outage
18326 | 2011 | 6 | 8 | 0.39236 |  | 150 | 20 | 8 | Dagmar | 4.16kV | AC14 | Transformer X29326 at 225 Carillon Street isolated to relocate to new pole | Ottawa | Scheduled Outage | Construction
18444 | 2011 | 6 | 20 | 0.41667 |  | 342 | 57 | 10 | DAGMAR | 4.16kV | AC14 | Transformer X29192 at 207 Carillon St. Isolated for transfer of plant | Ottawa | Scheduled Outage | Construction
18456 | 2011 | 6 | 21 | 0.42708 |  | 345 | 63 | 11 | Dagmar | 4.16kV | AC14 | Trans X29327 at 231 Carillon St was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
18534 | 2011 | 6 | 27 | 0.38542 |  | 165 | 30 | 11 | Dagmar | 4.16kV | AC14 | Isolated transformer X39327 at 231 Carillon St to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Construction
18573 | 2011 | 7 | 2 | 0.67222 |  | 384 | 1303 | 357 | Dagmar | 4.16kV | AC14 | Crew replaced defective cut out and circuit tripped when trying to restore circuit. Motor vehicle hit pole at Montreal Rd & St.Laurent. Conductors of AC14 were faund tangeled together in two seperate locations. Dagmar (AC14) ID#18573 | Ottawa | Foreign Interference | Vehicle
20912 | 2012 | 7 | 3 | 0.55556 |  | 10 | 6 | 35 | Dagmar | 4.16kV | AC14 | Transformer X29345 at 255 Bradley Ave isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
20913 | 2012 | 7 | 3 | 0.625 |  | 10 | 2 | 14 | Dagmar | 4.16kV | AC14 | Isolated transformer X29341 at 241 Bradley Ave to transfer hydro plant | Ottawa | Scheduled Outage | Construction
20924 | 2012 | 7 | 4 | 0.5625 |  | 210 | 38 | 11 | Dagmar | 4.16kV | AC14 | Isolated transformer X23221 at 275 Bradley Ave to transfer hydro plant | Ottawa | Scheduled Outage | Construction
14671 | 2009 | 7 | 6 | 0.38889 |  | 25 | 6 | 14 | Dagmar | 4.16kV | AC14 | Transformer #X29328 located at 241 Carillon St isolated to install new 200 amp service | Ottawa | Scheduled Outage | Construction
14772 | 2009 | 7 | 17 | 0.87917 |  | 294 | 1017 | 375 | Dagmar | 4.16kV | AC14 | At 16:15 SCADA indicates AC14 CB opened and locked out. 24-7 reports that a tree limb has fallen into the overhead causing 2 overhead conductors to fall and also wrap together. Crews made repairs and power was restored to all customers at 21:09. Dagmar (AC14). ID#14772. | Ottawa | Tree Contacts | Tree Limb Fallen
8787 | 2006 | 7 | 19 | 0.60417 |  | 70 | 6 | 5 | Dagmar | 4.16kV | AC14 | Transformer located at 229 Carillon isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
13109 | 2008 | 8 | 18 | 0.60903 |  | 44 | 272 | 371 | Dagmar | 4.16kV | AC14 | Transformer at 211 Ethel failed causing circuit to trip. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13194 | 2008 | 9 | 5 | 0.66528 |  | 278 | 646 | 189 | Dagmar | 4.16kV | AC14 | 2 phases of the AC14 circuit down on Montreal Rd @ Anne St. Section of circuit isolated to reconnect conductor. Complete circuit interupted to close in line switches after repairs completed. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9459 | 2006 | 10 | 18 | 0.38542 |  | 115 | 10 | 5 | Dagmar | 4.16kV | AC14 | Transformer located at 243 Carillon isolated to change transformer due to PCB content as per PC10A#1059 | Ottawa | Scheduled Outage | Preventive Maintenance
7497 | 2005 | 10 | 21 | 0.40278 |  | 65 | 6 | 6 | Dagmar | 4.16kV | AC14 | Transformer located at 262 Ste Anne isolated due to re-arranging of some secondary wires | Ottawa | Scheduled Outage | Preventive Maintenance
19467 | 2011 | 10 | 25 | 0.54167 |  | 200 | 53 | 16 | Dagmar | 4.16kV | AC14 | Isolated transformer X29374 at 253 Deschamps Ave and X29335 at 250 Marier St for pole change's | Ottawa | Scheduled Outage | Construction
13436 | 2008 | 10 | 27 | 0.52431 |  | 17 | 3 | 11 | DAGMAR | 4.16kV | AC14 | transformer #X29327 at 229 Carillon St isolated to allow for repairs to service at 224 Carillon St | Ottawa | Scheduled Outage | Repair
19506 | 2011 | 10 | 31 | 0.35417 |  | 190 | 51 | 16 | Dagmar | 4.16kV | AC14 | Isolated transformer X29147 at 260 Deschamps Ave for a pole change | Ottawa | Scheduled Outage | Construction
9570 | 2006 | 11 | 1 | 0.29167 |  | 115 | 15 | 8 | Dagmar | 4.16kV | AC14 | M Gruich replaced PCB trf. @ 272 ST. Anne | Ottawa | Scheduled Outage | Preventive Maintenance
20084 | 2012 | 3 | 1 | 0.33333 |  | 165 | 44 | 16 | Dagmar | 4.16kV | AC15 | Transformer #X21936 located at 295 St. Jacques St opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
14077 | 2009 | 3 | 18 | 0.41667 |  | 300 | 45 | 9 | Dagmar | 4.16kV | AC15 | At 10:00 trans at 291 ST. DENIS ST VANIER was isolated to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
17813 | 2011 | 3 | 31 | 0.55764 |  | 27 | 4 | 8 | Dagmar | 4.16kV | AC15 | Transformer #X23685 located at 327 Lavergne opened by crew to remove vines. | Ottawa | Tree Contacts | Inadequate Trimming
10426 | 2007 | 5 | 17 | 0.3 |  | 158 | 26 | 10 | Dagmar | 4.16kV | AC15 | John Streng responded to an all out @ 332 Ste. Cecile and found a blown arrestor that was replaced and power was restored | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20636 | 2012 | 5 | 31 | 0.33333 |  | 180 | 39 | 13 | Dagmar | 4.16kV | AC15 | Isolated transformer X23687 at 303 Lavergne St to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
20794 | 2012 | 6 | 18 | 0.33333 |  | 470 | 1058 | 135 | Dagmar | 4.16kV | AC15 | A section of AC15 circuit was isolated to allow crews to replace poles. Customers in the Lavergne, Dufford, pierre blanc and Perrier area affected. | Ottawa | Scheduled Outage | Construction
8552 | 2006 | 6 | 20 | 0.35069 |  | 17 | 1 | 5 | Dagmar | 4.16kV | AC15 | Transformer located at 258 St. Denis isolated due to running a new service | Ottawa | Scheduled Outage
20876 | 2012 | 6 | 26 | 0.34375 |  | 480 | 160 | 20 | Dagmar | 4.16kV | AC15 | At 08:15 two transformers fed from S21794 at 305 Lavergne Street was isolated to allow crew to replace poles. 20 customers were affected for 480 minutes. Dagmar (AC15) ID#20876. | Ottawa | Scheduled Outage | Construction
3853 | 2003 | 8 | 6 | 0.59514 |  | 8 | 31 | 229 | Dagmar | 4.16kV | AC15 | Lightning storm caused AC15 to open. Recloser was out of service circuit was reclosed by scada and held. | Ottawa | Adverse Weather | Lightning
9462 | 2006 | 10 | 18 | 0.53125 |  | 90 | 8 | 5 | Dagmar | 4.16kV | AC15 | Transformer located at 256 Ste. Cecile isolated to change transformer due to PCB content as per PC10A#1157 | Ottawa | Scheduled Outage | Preventive Maintenance
9557 | 2006 | 10 | 30 | 0.42708 |  | 118 | 10 | 5 | Dagmar | 4.16kV | AC15 | Changed Transformer because of PCB's | Ottawa | Scheduled Outage | Preventive Maintenance
9560 | 2006 | 10 | 30 | 0.45139 |  | 100 | 20 | 12 | Dagmar | 4.16kV | AC15 | Transformer located at 328 Lavergne isolated for PCB transformer replacement. PC10A #1068. | Ottawa | Scheduled Outage | Preventive Maintenance
19616 | 2011 | 11 | 22 | 0.39583 |  | 223 | 56 | 15 | DAGMAR | 4.16kV | AC15 | AC15 Overhead cct on Perrier Ave, Ottawa was isolated to allow Black & Mac to install new poles. | Ottawa | Scheduled Outage
14232 | 2009 | 4 | 25 | 0.80764 |  | 346 | 1372 | 238 | Shillington | 4.16kV | AD02 | AD05 breaker tripped (A/R/A/A/R) during high winds, heavy rain & lightning. S19360 red phase riser switch faulted at the station & numerous secondary problems were found. Load was restored via AD00. AD07 feeder tripped at same time. | Ottawa | Adverse Weather
10679 | 2007 | 6 | 20 | 0.38194 |  | 170 | 34 | 12 | Shillington | 4.16kV | AD02 | Transformer #OTT2113 at 1491 Morisset isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
5359 | 2004 | 6 | 23 | 0.40278 |  | 145 | 19 | 8 | Shillington | 4.16kV | AD02 | O/H transformer at 1489 Morrisette interrupted to change secondary services. | Ottawa | Scheduled Outage | Preventive Maintenance
12908 | 2008 | 7 | 21 | 0.51389 |  | 55 | 5 | 5 | Shillington | 4.16kV | AD02 | Transformer #OTT4587 located at 1494 Edgecliffe Ave isolated to reconnect a service. | Ottawa | Scheduled Outage | Construction
3875 | 2003 | 8 | 8 | 0.44514 |  | 34 | 1 | 2 | Shillington | 4.16kV | AD02 | Transformer opened at 1455 Morisset to effect repairs, interrupting two customers on Edgecliff. | Ottawa | Scheduled Outage | Repair
9061 | 2006 | 8 | 26 | 0.072917 |  | 15 | 6 | 24 | Shillington | 4.16kV | AD02 | Transformer K520 at 1525 CALDWELL AVE OTTW was isolate to allow disconnection at pedestal#2 for unit 7. Burnt connections at meter base for unit 7 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9809 | 2006 | 12 | 7 | 0.89583 |  | 20 | 18 | 55 | Shillington | 4.16kV | AD02 | Transf. Bank # 301 @ 1433 mayview was isolated to replace a defective switch | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13753 | 2008 | 12 | 15 | 0.38958 |  | 84 | 6 | 4 | Shillington | 4.16kV | AD02 | Transformer #X30367 located at 1176 Merivale Rd isolated due to broken cut out | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10190 | 2007 | 3 | 27 | 0.64236 |  | 70 | 13 | 11 | Shillington | 4.16kV | AD03 | Glen Carswell isolated TRF. OTT 1362 @ 1387 Chatelain for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
12246 | 2008 | 4 | 7 | 0.57639 |  | 55 | 7 | 8 | Shillington | 4.16kV | AD03 | Isolated and replaced transformer X30263 at 1408 Larose Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
20321 | 2012 | 4 | 13 | 0.84931 |  | 11 | 82 | 447 | Shillington | 4.16kV | AD03 | Hydro Ottawa crews found sparking line taps at the P.P.H switches feeding V827 at 1435 Larose Ave. Due to possible conductor damage, the circuit had to be opened to allow crews to safely remove the line taps. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12279 | 2008 | 4 | 14 | 0.42014 |  | 115 | 6 | 3 | SHILLINGTON | 4.16kV | AD03 | Transformer X30214 serial #255036 at 1478 Lepage Ave. removed for PCB & load transferred | Ottawa | Scheduled Outage | Preventive Maintenance
14248 | 2009 | 4 | 26 | 0.37083 |  | 556 | 1271 | 245 | Shillington | 4.16kV | AD03 | AD03 breaker was opened manually from SCADA due to live primary conductor down on Chatelaine. Circuit was isolated to install cuts at Chatelaine & Larkin in order to sectionalize the damaged section. Repairs were then made to downed conductor and the remainder of customers were restored. | Ottawa | Adverse Weather
20417 | 2012 | 4 | 30 | 0.40278 |  | 70 | 6 | 5 | Shillington | 4.16kV | AD03 | Isolated transformer X30226 at 1473 Chatelain Ave for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
6519 | 2005 | 5 | 6 | 0.96181 |  | 418 | 42 | 6 | Shillington | 4.16kV | AD03 | At 23:05 trans OTT 5231 at 953 Larkin St isolated in order to replace defective trans | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
18125 | 2011 | 5 | 10 | 0.45833 |  | 66 | 29 | 26 | Shillington | 4.16kV | AD03 | AD03 O/H line section between Canvan and Larkin was isolated from O/H tap on Cavan N of Larose to allow crane to remove falling tree at rear of 1435 Larose. | Ottawa | Scheduled Outage
6688 | 2005 | 6 | 10 | 0.067361 |  | 37 | 8 | 13 | Shillington | 4.16kV | AD03 | O/H transformer fuse blown at 1463 Chatelaine. Refused and closed. | Ottawa | Unknown/Other
14976 | 2009 | 8 | 20 | 0.46528 |  | 80 | 7 | 5 | Shillington | 4.16kV | AD03 | Transformer #X30259 located at 949 Cavan isolated to install new pole guy | Ottawa | Scheduled Outage | Construction
3981 | 2003 | 9 | 3 | 0.41042 |  | 69 | 6 | 5 | Shillington | 4.16kV | AD03 | Transformer OTT6792 on Woodward was isolated to replace a deteriorated open wire service. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9447 | 2006 | 10 | 17 | 0.43056 |  | 20 | 2 | 5 | Shillington | 4.16kV | AD03 | Isolated transformer K00832 at 1389 Lepage Ave to repair U/G service | Ottawa | Scheduled Outage | Repair
7610 | 2005 | 11 | 14 | 0.44514 |  | 148 | 32 | 13 | Shillington | 4.16kV | AD03 | Isolated Transformer OTT1365 at 1447 Chatelain to replace bad connections | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13898 | 2009 | 1 | 27 | 0.625 |  | 25 | 0 | 1 | Shillington | 4.16kV | AD04 | Transformer #X35589 located at Baseline & Merivale isolated to change tap setting on transformer | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10195 | 2007 | 3 | 29 | 0.76944 |  | 292 | 146 | 16 | Shillington | 4.16kV | AD04 | Transformer and cut out replaced. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12212 | 2008 | 3 | 31 | 0.84028 |  | 31 | 4 | 8 | Shillington | 27.6/16kV | AD04 | At 20:10 trans at 1500 Caldwell Ave was isolated due to fire at units 82-96 .. Unilts remain isolated indefeintley | Ottawa | Adverse Environment | Fire
12213 | 2008 | 3 | 31 | 0.84028 |  | 30 | 4 | 8 | Shillington | 4.16kV | AD04 | At 20:10 trans at 1500 Caldwell Ave was isolated due to fire in units 82-96 units have been disconnected until further notice | Ottawa | Adverse Environment | Fire
12316 | 2008 | 4 | 21 | 0.54167 |  | 86 | 9 | 6 | Shillington | 4.16kV | AD04 | Isolated and replaced transformer X30423 at 1414 Rosenthal Ave (PCB Oil) | Ottawa | Scheduled Outage | Preventive Maintenance
12341 | 2008 | 4 | 24 | 0.52083 |  | 120 | 12 | 6 | Sillington | 4.16kV | AD04 | Isolated and replaced transformer OTT4425 at 1114 Merivale rd (PCB Oil) | Ottawa | Scheduled Outage | Preventive Maintenance
13381 | 2008 | 10 | 17 | 0.54028 |  | 17 | 2 | 8 | SHILLINGTON | 4.16kV | AD04 | Transformer #K525 at 1500 Caldwell isolated to allow for repairs to burnt connection | Ottawa | Scheduled Outage | Repair
5858 | 2004 | 11 | 5 | 0.37222 |  | 24 | 6 | 15 | AD | 4.16kV | AD04 | Laneville rpts dip to K1116 opened due to defective hot line clamp, 15 customers off at 1113 Merivale | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13572 | 2008 | 11 | 6 | 0.3125 |  | 227 | 26 | 7 | Shillington | 4.16kV | AD04 | At 07:30 trans at 1435 Caldwell was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15506 | 2009 | 12 | 13 | 0.34722 |  | 100 | 18 | 11 | Shillington | 4.16kV | AD04 | At 08:20 trans at 1072 Merivale re was isolated in order to transfer plant | Nepean | Scheduled Outage | Preventive Maintenance
17421 | 2010 | 12 | 14 | 0.55903 |  | 22 | 3 | 8 | Shillington | 4.16kV | AD04 | Isolated transformer X35350 at 1313 Trenton Ave to replace triplex service | Ottawa | Scheduled Outage | Emergency Services Request
13821 | 2008 | 12 | 30 | 0.27361 |  | 401 | 87 | 13 | Shillington | 4.16kV | AD04 | At 12:00 trans at 1418 Mayview Ave was isolated in order to repace defective trans | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11971 | 2008 | 1 | 23 | 0.41042 |  | 89 | 13 | 9 | Shillington | 4.16kV | AD05 | At 09:51 trans at 966 Fisher Ave was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11975 | 2008 | 1 | 23 | 0.52778 |  | 65 | 8 | 7 | Shillington | 4.16kV | AD05 | At 12:40 trans at 1040 Bakervale was isolated in order for pcb trans replacement | Ottawa | Scheduled Outage
20211 | 2012 | 3 | 23 | 0.42708 |  | 30 | 3 | 6 | Shillington | 4.16kV | AD05 | At 10:45 transformer X31899 at 973 Hollington Street was interupted to allow crew to re-arrange phasing. 6 customers were affected for 30 minutes. Shillington (AD05) ID#20211 | Ottawa | Scheduled Outage
20212 | 2012 | 3 | 23 | 0.45833 |  | 30 | 12 | 25 | Shillington | 4.16kV | AD05 | At 11:00 four transformers on Emperor Avenue east of Hollington Avenue was interupted to allow crew to re-arrange phasing. 25 customers were affected for 30 minutes. Shillington (AD05) ID#20212 | Ottawa | Scheduled Outage
20213 | 2012 | 3 | 23 | 0.54167 |  | 30 | 7 | 14 | Shillington | 4.16kV | AD05 | At 13:00 transformer X35371 at 1205 Dorchester Avenue was interupted to allow crew to re-arrange phasing. 14 customers were affected for 30 minutes. Shillington (AD05) ID#20213 | Ottawa | Scheduled Outage
20217 | 2012 | 3 | 24 | 0.58333 |  | 15 | 4 | 14 | Shillington | 4.16kV | AD05 | Isolated transformer X35369 at 1055 Hollington St to disconnect service | Ottawa | Scheduled Outage | Emergency Services Request
20219 | 2012 | 3 | 24 | 0.80556 |  | 25 | 6 | 14 | Shillington | 4.16kV | AD05 | Tx X35369 at 1220 Dorchester opened to re-install secondary after customer made repairs to standpipe. 14 customers affected for 25 min. Shillington AD05. ID#20219 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10188 | 2007 | 3 | 27 | 0.52083 |  | 120 | 30 | 15 | Shillington | 4.16kV | AD05 | Transformer #OTT3986 located at 415 Lisgar isolated due to installing conductor | Ottawa | Scheduled Outage | Construction
15869 | 2010 | 3 | 30 | 0.42014 |  | 5 | 1 | 7 | SHILLINGTON | 4.16kV | AD05 | Transformer # X38645 located at 1362 woodward isolated to disconnect service for revenue dept. | Ottawa | Scheduled Outage | Construction
18055 | 2011 | 4 | 28 | 0.96667 |  | 1451 | 1890 | 195 | Shillington | 4.16kV | AD05 | Several locations of wind damage, trees on overhead, wires & poles down. | Ottawa | Adverse Weather | Wind
14266 | 2009 | 4 | 30 | 0.50347 |  | 30 | 2 | 5 | Shillington | 4.16kV | AD05 | Transformer #X35351 located at 1202 Emperor Ave isolated to do an emergency disconnect for electrician to make repairs | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16031 | 2010 | 5 | 3 | 0.48125 |  | 142 | 95 | 40 | Shillington | 4.16kV | AD05 | blue phase runoff burnt off at rear of 1159 Dorchester. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6538 | 2005 | 5 | 11 | 0.39236 |  | 35 | 8 | 13 | Shillington | 4.16kV | AD05 | Replaced the switch to transformer OTT5775 at 1148 Shillington | Ottawa | Scheduled Outage | Preventive Maintenance
6543 | 2005 | 5 | 11 | 0.53819 |  | 60 | 14 | 14 | Shillington | 4.16kV | AD05 | Power interrupted to transformer OTT5782 at 1129 Shillington to relocate to other side of pole to facilitate the installation of a new pole | Ottawa | Scheduled Outage | Preventive Maintenance
8290 | 2006 | 5 | 13 | 0.45833 |  | 334 | 17 | 3 | Shillington | 4.16kV | AD05 | Services to 1175,1176,1178 Summerville were disconnected to allow electrian repair standpipes to homes. | Ottawa | Tree Contacts | Tree Fallen
18341 | 2011 | 6 | 8 | 0.69931 |  | 11 | 80 | 438 | Shillington | 4.16kV | AD05 | Circuit opened due to storm activity, no cause reported yet, closed in via scada. | Ottawa | Adverse Weather
12717 | 2008 | 6 | 24 | 0.88194 |  | 40 | 4 | 6 | Shillington | 4.16kV | AD05 | At 21:10 trans at 1203 Summerville was isolated in order to replace 2 existing sec services | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16565 | 2010 | 7 | 26 | 0.67361 |  | 40 | 7 | 11 | Shillington | 4.16kV | AD05 | Transformer #X35667 located at 1075 Chevrier opened by crew to cut tree branches | Ottawa | Tree Contacts | Inadequate Trimming
16820 | 2010 | 8 | 27 | 0.35417 |  | 115 | 19 | 10 | Shillington DS | 4.16kV | AD05 | Transformer X35665 at the rear of 1044 Fisher Ave. Was isolated to allow crews to make secondary connections. | Ottawa | Scheduled Outage | Construction
7235 | 2005 | 8 | 29 | 0.79167 |  | 213 | 45 | 195 | Shillington | 4.16kV | AD05 | phase down on Dover Cres. requiring AD05 to be opened to isolate the affected section. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15248 | 2009 | 10 | 11 | 0.64722 |  | 115 | 25 | 13 | Shiilington | 4.16kV | AD05 | transformer OTT3665 was opened to allow crew to remove tree limb, and repair triplex @ 1230 dorchester. | Ottawa | Tree Contacts | Tree Limb Fallen
17202 | 2010 | 11 | 1 | 0.46944 |  | 4 | 29 | 437 | Shillington | 4.16kV | AD05 | AD05 CB out of Shillington was momentarily opened for equipment protection while crew removed tree from the overhead. | Ottawa | Scheduled Outage | Preventive Maintenance
19584 | 2011 | 11 | 15 | 0.95347 |  | 74 | 27 | 22 | Shillington | 4.16kV | AD05 | Transformer X35327 at 1224 Shillington Ave isolated to change overloaded 50kVA transformer to 100kVA | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10000 | 2007 | 2 | 7 | 0.51389 |  | 130 | 20 | 9 | Shillington | 4.16kV | AD06 | Isolated transformer 6477 at 40 Anna St to replace pole | Ottawa | Scheduled Outage | Construction
15724 | 2010 | 2 | 17 | 0.36111 |  | 35 | 6 | 11 | SHILLINGTON | 4.16kV | AD06 | Xfmr 32328 at 1015 Panet isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
20029 | 2012 | 2 | 17 | 0.40903 |  | 11 | 25 | 139 | Shillington | 4.16kV | AD06 | A section of AD06 was interrupted to allow crews to reconnect a section of N.I.U. overhead line behind 915 Merivale and restore SM02 and AD06 to normal. | Ottawa | Scheduled Outage | Construction
4843 | 2004 | 3 | 1 | 0.55208 |  | 65 | 10 | 9 | Shillington | 4.16kV | AD06 | Transformer at 208 General interrupted to repair secondary service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10241 | 2007 | 4 | 11 | 0.35417 |  | 470 | 298 | 38 | Shillington | 4.16kV | AD06 | Switch #15482 located at 73 Anna Ave isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
12325 | 2008 | 4 | 22 | 0.38333 |  | 173 | 17 | 6 | Shillington | 4.16kV | AD06 | At 09:12 trans at 1309 Emperor was isolated in order to replace a PCB trans | Ottawa | Scheduled Outage | Preventive Maintenance
10325 | 2007 | 4 | 25 | 0.36806 |  | 405 | 236 | 35 | Shillington | 4.16kV | AD06 | Isolation of overhead section Stevenson at Crerar for Balck and MacDonald to change poles.Merivale Carling area. | Ottawa | Scheduled Outage | Construction
10472 | 2007 | 5 | 28 | 0.53472 |  | 140 | 23 | 10 | Shillington | 4.16kV | AD06 | Brian - Black & Mac isolated TRF. OTT 142 @ 35 Anna for TRF change and buss change | Ottawa | Scheduled Outage | Preventive Maintenance
10475 | 2007 | 5 | 29 | 0.35417 |  | 225 | 56 | 15 | Shillington | 4.16kV | AD06 | Transformer #OTT135 located at 17 Anna isolated to allow for relocating to new buss & new pole | Ottawa | Scheduled Outage | Construction
10482 | 2007 | 5 | 30 | 0.35417 |  | 210 | 10 | 3 | Shillington | 4.16kV | AD06 | Transformer #OTT5974 at 71 Stevenson Ave isolated to replace transformer | Ottawa | Scheduled Outage | Construction
10526 | 2007 | 6 | 4 | 0.52083 |  | 180 | 33 | 11 | Shillington | 4.16kV | AD06 | Transformer #OTT5978 located at 63 Stevenson Ave isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
10542 | 2007 | 6 | 6 | 0.35417 |  | 180 | 45 | 15 | Shillington | 4.16kV | AD06 | Isolated and relocated transformer OTT5976 at 31 Stevenson Ave | Ottawa | Scheduled Outage | Construction
6750 | 2005 | 6 | 16 | 0.40694 |  | 29 | 4 | 8 | Shillington | 4.16kV | AD06 | Transformer located at 1220 Shillington isolated re:transferring primary | Ottawa | Scheduled Outage | Construction
18739 | 2011 | 7 | 19 | 0.14792 |  | 2203 | 2882 | 632 | Shillington | 4.16kV | AD06 | A large tree on the primary overhead at 14 Marshall required the cicuit to be opened by SCADA to allow the crew to cut the affected line clear antill the tree could be removed and repairs done | Ottawa | Tree Contacts | Tree Fallen
7019 | 2005 | 7 | 25 | 0.44792 |  | 121 | 46 | 23 | Shillington | 4.16kV | AD06 | transformer P304 was isolated to allow crew to roll overhead conductors.(rolling means changing conductor from crossarm to vertical construction) | Ottawa | Scheduled Outage | Construction
10959 | 2007 | 7 | 27 | 0.38889 |  | 126 | 27 | 13 | Shillington | 4.16kV | AD06 | Transformer #OTT5790 at 1266 Shillington isolated to allow for replacement of transformer | Ottawa | Scheduled Outage | Repair
16648 | 2010 | 8 | 4 | 0.65208 |  | 323 | 3338 | 620 | Shillington | 4.16kV | AD06 | AD06 tripped during heavy rain & lightning. Conductor knocked down had to be repaired by Oncall before circuit could be restored. | Ottawa | Lightning
11020 | 2007 | 8 | 9 | 0.37847 |  | 72 | 7 | 6 | SHILLINGTON | 13.2kV | AD06 | Transformer #OTT1750 at 236 Crerar isolated to allow for service changeover | Ottawa | Scheduled Outage | Construction
5643 | 2004 | 8 | 10 | 0.44097 |  | 33 | 3 | 6 | Shillington | 4.16kV | AD06 | Transformer #OTT5979 at 71 Stevenson was opened to allow for a tree removal. | Ottawa | Tree Contacts
7126 | 2005 | 8 | 11 | 0.47569 |  | 2 | 8 | 253 | AD | 4.16kV | AD06 | A line crew was working in the area of AD06 with h/o in effect & made contact with AD06 o/h conductor. No injuries occurred & power was restored when the crew reported they were clear of the o/h line. | Ottawa | Human Element | Incorrect Use of Equipment
7141 | 2005 | 8 | 16 | 0.37153 |  | 55 | 15 | 16 | Shillington | 4.16kV | AD06 | Transformer #OTT2214 located behind 1277 Emperor Ave isolated due to services were flashing going to the pole. | Ottawa | Unknown/Other
18963 | 2011 | 8 | 18 | 0.56944 |  | 305 | 1783 | 756 | SHILLINGTON | 4.16kV | AD06 | AD06 A/R & LOCKED OUT, due to Primary Down at Crerar/Anna. Downed primary was cut clear to restore majority of customers until repairs could be made | Ottawa | Adverse Weather
7327 | 2005 | 9 | 15 | 0.24028 |  | 16 | 67 | 253 | SHILLINGTON | 4.16kV | AD06 | Line crew requests AD06 circuit opened at request of G.Macmillan to prevent O/H line from burning down & make repairs on same. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7328 | 2005 | 9 | 15 | 0.24028 |  | 24 | 101 | 253 | Shillington | 4.16kV | AD06 | Circuit AD06 opened @ request of line request of line crew ( G.Macmillan) as line was about to burn down affecting about 253 customers. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
19202 | 2011 | 9 | 19 | 0.62153 |  | 39 | 8 | 13 | Shillington | 4.16kV | AD06 | Transformer #X35337 located at 1011 Hooper St opened by crew to put up a new service | Ottawa | Scheduled Outage | Construction
7447 | 2005 | 10 | 12 | 0.39931 |  | 100 | 22 | 13 | Shillington | 4.16kV | AD06 | Transformer #OTT5775 located at 1170 Shillington isolated due to changing poles | Ottawa | Scheduled Outage | Preventive Maintenance
7449 | 2005 | 10 | 12 | 0.54861 |  | 40 | 13 | 20 | Shillington | 4.16kV | AD06 | Transformer #K00670 located at 1180 Shillington isolated due to changing poles | Ottawa | Scheduled Outage | Preventive Maintenance
9460 | 2006 | 10 | 18 | 0.44444 |  | 22 | 3 | 9 | Shillington | 4.16kV | AD06 | Transformer #OTT6477 located at 22 Anna Ave isolated to prepare for pole change. PC10A #1472 | Ottawa | Scheduled Outage | Preventive Maintenance
7490 | 2005 | 10 | 20 | 0.42847 |  | 278 | 97 | 21 | AD | 4.16kV | AD06 | P304 at 1204 Shillington isolated for planned cable replacement. | Ottawa | Scheduled Outage | Construction
9481 | 2006 | 10 | 20 | 0.48472 |  | 22 | 2 | 5 | Shillington | 4.16kV | AD06 | Transformer located at 68 Anna isolated to re-arrange for a pole change. PC10A #1471 | Ottawa | Scheduled Outage | Preventive Maintenance
9509 | 2006 | 10 | 25 | 0.47917 |  | 40 | 5 | 8 | SHILLINGTON | 4.16kV | AD06 | Isolated transf. At 38 Anna to install new pole | Ottawa | Scheduled Outage | Preventive Maintenance
17180 | 2010 | 10 | 26 | 0.5 |  | 120 | 14 | 7 | SHILLINGTON | 4.16kV | AD06 | Transformer X32346 at 812 Fisher isolated to install non metered conduit up pole for Bell | Ottawa | Scheduled Outage | Construction
17181 | 2010 | 10 | 26 | 0.5 |  | 115 | 13 | 7 | SHILLINGTON | 4.16kV | AD06 | Transformer X32346 at 812 Fisher Ave isolated to run wire for Bell service | Ottawa | Scheduled Outage | Repair
7524 | 2005 | 10 | 27 | 0.38889 |  | 150 | 50 | 20 | Shillington | 4.16kV | AD06 | Isolated Transformer # K00670 at 1180 Shillington to install new pole | Ottawa | Scheduled Outage | Construction
9617 | 2006 | 11 | 7 | 0.40972 |  | 135 | 25 | 11 | Shillington | 4.16kV | AD06 | Tony Taylor had Transformer open at 64 Anna to do a pole and transformer change | Ottawa | Scheduled Outage | Preventive Maintenance
19553 | 2011 | 11 | 10 | 0.59722 |  | 29 | 4 | 9 | Shillington | 4.16kV | AD06 | Transformer X37335 at 71 Shillington Ave isolated to allow hydro tree contractor to remove fallen limb off secondary | Ottawa | Tree Contacts | Tree Limb Fallen
19557 | 2011 | 11 | 11 | 0.44444 |  | 60 | 16 | 16 | Shillington | 4.16kV | AD06 | Jim Yeldon reports transformer #X32226 located at 1278 Christine Ave opened by crew to install new service | Ottawa | Scheduled Outage | Construction
9776 | 2006 | 12 | 1 | 0.72639 |  | 194 | 808 | 250 | Shillington | 4.16kV | AD06 | Tree fell on circuit at Fisher/Tuns. Circuit was isolated so that the tree could be removed. | Ottawa | Adverse Weather | Ice Storm
13736 | 2008 | 12 | 11 | 0.41667 |  | 35 | 3 | 5 | Shillington | 4.16kV | AD06 | Transformer #X32242 located at 1273 Emperor isolated due to tree trimming | Ottawa | Scheduled Outage | Preventive Maintenance
17570 | 2011 | 2 | 10 | 0.72222 |  | 15 | 2 | 10 | Shillington | 4.16kV | AD07 | Transformer X35367 at 1254 Emperor Ave isolated to change service wire | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4846 | 2004 | 3 | 2 | 0.53125 |  | 35 | 9 | 15 | Shillington | 4.16kV | AD07 | Transformer at 1294 Trenton isolated at Fire Dept's request due to house fire 1292 Trenton. | Ottawa | Adverse Environment | Fire
15775 | 2010 | 3 | 5 | 0.53125 |  | 35 | 5 | 9 | Shillington | 4.16kV | AD07 | Transformer #X35347 located at 1327 Dorchester isolated due to re-arranging plant | Ottawa | Scheduled Outage | Construction
4876 | 2004 | 3 | 11 | 0.42708 |  | 80 | 9 | 7 | Shillington | 4.16kV | AD07 | Transformer OTT6130 at 1185 Summerville interrupted to repair service. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17897 | 2011 | 4 | 11 | 0.38819 |  | 246 | 70 | 17 | Shillington | 4.16kV | AD07 | Transformer #X35363 located at 1337 Kingston Ave opened up due to lightning and needed to be replaced. | Ottawa | Adverse Weather | Lightning
14183 | 2009 | 4 | 16 | 0.4125 |  | 21 | 8 | 23 | SHILLINGTON | 4.16kV | AD07 | transformer OTT6316 isolated to allow for tree removal - 2nd outage required later today to complete work | Ottawa | Scheduled Outage | Preventive Maintenance
14184 | 2009 | 4 | 16 | 0.47222 |  | 26 | 10 | 23 | SHILLINGTON |  | AD07 | transformer OTT6316 at 1256 Summerville isolated to complete repairs after tree removal | Ottawa | Scheduled Outage | Preventive Maintenance
12317 | 2008 | 4 | 21 | 0.40972 |  | 100 | 10 | 6 | Shillington | 4.16kV | AD07 | Isolated and replaced transformer X35330 at 1247 Dorchester Ave (PCB Oil) | Ottawa | Scheduled Outage | Preventive Maintenance
14233 | 2009 | 4 | 25 | 0.80764 |  | 347 | 1307 | 226 | Shillington | 4.16kV | AD07 | AD07 breaker tripped during high winds, heavy rain & lightning. Primary conductor taken down by fallen tree at 1288 Trenton & numerous secondary problems were found. AD02 feeder tripped at same time. | Ottawa | Adverse Weather | Wind
12400 | 2008 | 5 | 6 | 0.39583 |  | 135 | 32 | 14 | Shillington | 4.16kV | AD07 | Isolated transformer OTT6125 at 1276 DORCHESTER ST to replace the pole | Ottawa | Scheduled Outage | Construction
20507 | 2012 | 5 | 13 | 0.54514 |  | 455 | 91 | 12 | Shillington | 4.16kV | AD07 | Secondary connections failed on transformer # X38690 @ 1233 Summerville Ave.. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14426 | 2009 | 5 | 29 | 0.42361 |  | 20 | 2 | 10 | Shillington | 4.16kV | AD07 | Transformer #OTT3665 located at 1231 Summerville isolated for a tree removal contractor | Ottawa | Scheduled Outage | Preventive Maintenance
14428 | 2009 | 5 | 29 | 0.54861 |  | 70 | 12 | 10 | Shillington | 4.16kV | AD07 | Transformer #OTT3665 located at 1231 Summerville isolated for a tree removal contractor | Ottawa | Scheduled Outage | Preventive Maintenance
6795 | 2005 | 6 | 25 | 0.61875 |  | 7 | 26 | 226 | Shington | 4.16kV | AD07 | AD07,storm and lightning in the area customer called in at 1022 Merivale two fuse of his three phase has blown and his panal is on fire. | Ottawa | Adverse Weather | Lightning
16468 | 2010 | 7 | 14 | 0.54167 |  | 40 | 10 | 15 | Shillington | 4.16kV | AD07 | Transformer #X35336 located at 1202 Kingston opened by crew to replace 2 services | Ottawa | Scheduled Outage | Construction
16471 | 2010 | 7 | 14 | 0.57222 |  | 26 | 3 | 7 | Shillington | 4.16kV | AD07 | Transformer #X35341 located at 1211 Kingston opened by crew to make repairs to secondary service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10891 | 2007 | 7 | 17 | 0.26944 |  | 137 | 27 | 12 | Shillington | 4.16kV | AD07 | Transformer #OTT6125 located at 1259 Summerville isolated due to possible animal contact | Ottawa | Foreign Interference | Animal
3766 | 2003 | 7 | 20 | 0.66319 |  | 103 | 294 | 226 | Shillington | 4.16kV | AD07 | AD07 4KV feeder tripped due to a lightning strike at cutouts to P100 on Dorchester @ Merivale. Crew opened all 3 fused cutouts to P100 and AD07 was closed by SCADA & held. The transformer, P100, feeding the apartment building at 1099 Dorchester was checked OK. The cutouts to P100 were closed & power restored. | Ottawa | Lightning | Direct Strike
14974 | 2009 | 8 | 20 | 0.42014 |  | 69 | 6 | 5 | Shillington | 4.16kV | AD07 | Transformer #OTT3665 located at 1229 Summerville isolated for a pole change | Ottawa | Scheduled Outage | Construction
11116 | 2007 | 8 | 21 | 0.38889 |  | 100 | 40 | 24 | Shillington | 4.16kV | AD07 | Transformer #OTT6327 located at 1080 Silver isolated due to service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
7224 | 2005 | 8 | 27 | 0.53264 |  | 224 | 330 | 225 | Shillington | 4.16kV | AD07 | Tree fell over at 1235 Trenton ave and brought down primary. | Ottawa | Tree Contacts | Tree Fallen
7226 | 2005 | 8 | 27 | 0.68056 |  | 11 | 32 | 175 | Shillington | 4.16kV | AD07 | Circuit was opened for crew to reconnect three phase radial that was isolated to remove tree and repair downed primary. | Ottawa | Tree Contacts
9073 | 2006 | 8 | 27 | 0.775 |  | 86 | 20 | 14 | Shillington | 4.16kV | AD07 | Tree contact with secondary caused transformer fuse to blow. Branches were trimmed & transformer refused successfully. Customers affected were on Trenton, Kingston & Silver in the Experimental Farm area. | Ottawa | Tree Contacts | Inadequate Trimming
15592 | 2009 | 12 | 29 | 0.66319 |  | 10 | 0 | 1 | Shillington | 4.16kV | AD07 | Transformer #X32327 located at 1299 Dorchester isolated to disconnect serv due to s/p pulled off wall | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4741 | 2004 | 1 | 28 | 0.51181 |  | 75 | 5 | 4 | Urbandale | 4.16kV | AE01 | Transformer opened to repair transformer at 2045 Cornish. 4 Customers affected in power outage. | Ottawa | Scheduled Outage | Repair
4742 | 2004 | 1 | 28 | 0.45278 |  | 160 | 13 | 5 | Urbandale | 4.16kV | AE01 | Crews replaced leaking transformer #2013 at 961 Drew Ave. 5 Customers affected in power outage. | Ottawa | Scheduled Outage | Repair
3288 | 2003 | 3 | 21 | 0.47222 |  | 60 | 150 | 150 | urbandale | 4.16kV | AE01 | AE01 circuit was dumped to effect repairs to a broken crossarm. | Ottawa | Scheduled Outage
17926 | 2011 | 4 | 14 | 0.36806 |  | 26 | 4 | 9 | Urbandale | 4.16kV | AE01 | Transformer K00348 at 2314B Russell Rd isolated to disconnect customer for non-pay (Revenue dept) | Ottawa | Scheduled Outage | Construction
16023 | 2010 | 5 | 1 | 0.1125 |  | 53 | 7 | 8 | Urbandale | 4.16kV | AE01 | 24/7 reports a racoon caused transformer fuse to blow. | Ottawa | Foreign Interference | Animal
12422 | 2008 | 5 | 9 | 0.98542 |  | 95 | 32 | 20 | Urbandale | 4.16kV | AE01 | Broken cutout at Dip to K348. Crew replaced switch and resotred power. Walkley/Russell area. | Ottawa | Defective Equipment
14363 | 2009 | 5 | 15 | 0.39583 |  | 6 | 0 | 4 | Urbandale | 4.16kV | AE01 | O/H transformer at 2028 Tawney Dr isolated for service repairs. | Ottawa | Scheduled Outage
14366 | 2009 | 5 | 15 | 0.42014 |  | 50 | 5 | 6 | Urbandale | 4.16kV | AE01 | Transformer #X29383 located at 2042 Tawney isolated to replace a service | Ottawa | Scheduled Outage | Construction
16133 | 2010 | 5 | 25 | 0.38542 |  | 40 | 7 | 11 | Urbandale | 4.16kV | AE01 | Transformer #X29382 located at 2076 St. Laurent opened by crew for an upgrade | Ottawa | Scheduled Outage | Construction
16150 | 2010 | 5 | 26 | 0.55833 |  | 66 | 28 | 25 | Urbandale | 4.16kV | AE01 | At 13:45 the cut out feeding 1991 St. Laurent was found defective. Crews replaced switch and power was restored at 14:30. | Ottawa | Defective Equipment
9021 | 2006 | 8 | 22 | 0.54514 |  | 185 | 37 | 12 | Urbandale | 4.16kV | AE01 | Isolated and replaced transformer OTT4406 at 2171 Melfort St due to contaminated oil (PCB) | Ottawa | Scheduled Outage | Preventive Maintenance
9081 | 2006 | 8 | 28 | 0.54167 |  | 100 | 15 | 9 | Urbandale | 4.16kV | AE01 | At 13:00 trans OTT4298 at 2064 Maywood St was isolated in order to relocate trans | Ottawa | Scheduled Outage | Preventive Maintenance
7242 | 2005 | 8 | 30 | 0.32778 |  | 123 | 8 | 4 | Urbandale | 4.16kV | AE01 | Switch to transformer OTT679 at 2084 Maywood was found broken Replaced the switch restored power | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7383 | 2005 | 9 | 27 | 0.51944 |  | 32 | 3 | 5 | Urbandale | 4.16kV | AE01 | Isolated Transformer # 6420 at 1004 Edmond to install a service | Ottawa | Scheduled Outage | Preventive Maintenance
9544 | 2006 | 10 | 29 | 0.5375 |  | 222 | 814 | 220 | Urbandale | 4.16kV | AE01 | Pole broken at the base, secured by a line truck and re-energized by SCADA | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9588 | 2006 | 11 | 2 | 0.36042 |  | 38 | 6 | 10 | Urbandale | 4.16kV | AE01 | Mark Rushton isolated trf. @ 2109 maywood to do service work | Ottawa | Scheduled Outage | Preventive Maintenance
15349 | 2009 | 11 | 3 | 0.47708 |  | 158 | 29 | 11 | Urbandale | 4.16kV | AE01 | Transformer #X29382 located at 2080 St. Laurent isolated due to tree contact. | Ottawa | Tree Contacts | Inadequate Trimming
9627 | 2006 | 11 | 9 | 0.84375 |  | 50 | 8 | 9 | Urbandale | 4.16kV | AE01 | Transformer #K348 located at 2495 Walkley Rd isolated to reconnect 5 units | Ottawa | Scheduled Outage | Repair
9635 | 2006 | 11 | 10 | 0.56597 |  | 23 | 2 | 5 | Urbandale | 4.16kV | AE01 | At 13:35 trans OTT6420 at 2097 Valley Dr was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
15422 | 2009 | 11 | 25 | 0.43125 |  | 142 | 310 | 131 | Urbandale | 4.16kV | AE01 | At 10:21am Hydro Ottawa opened S25666 on the AE01 overhead circuit to allow tree trimmers proper isolation to do their work, 131 customers were affected and power was restored at 12:44pm. Urbandale (AE01). ID#15422 | Ottawa | Scheduled Outage | Preventive Maintenance
6061 | 2004 | 12 | 14 | 0.33681 |  | 365 | 49 | 8 | URBANDALE | 4.16kV | AE01 | K350 @ 2499 Walkley isolated to allow crews to replace service. 8 Customers affected in power outage. | Ottawa | Scheduled Outage | Repair
4617 | 2003 | 12 | 18 | 0.18264 |  | 158 | 579 | 220 | Urbandale | 4.16kV | AE01 | AE01 interupted with no apparent cause coinciding with auto reclose on TB10 breaker ID#4617. Circuits were both patrolled at night & again during daylight with no cause for a fault found. | Ottawa | Loss of Supply | HEPC Circuit Fault
19779 | 2012 | 1 | 3 | 0.4375 |  | 30 | 6 | 12 | Urbandale | 4.16kV | AE02 | Isolated and checked transformer X27178 at 2081 Bangor St due to complaints of high voltage | Ottawa | Scheduled Outage | Preventive Maintenance
17891 | 2011 | 4 | 11 | 0.225 |  | 28 | 124 | 265 | Urbandale | 4.16kV | AE02 | AE02 breaker tripped, closed & holding | Ottawa | Adverse Weather
3449 | 2003 | 5 | 16 | 0.44097 |  | 40 | 7 | 10 | Urbandale | 4.16kV | AE02 | Transformer at the rear of 2113 Bangor was opened to replace service at 2098 Lemay st. 10 Customers affected in outage. | Ottawa | Scheduled Outage | Repair
18593 | 2011 | 7 | 5 | 0.95486 |  | 34 | 6 | 10 | Urbandale | 4.16kV | AE02 | Isolated transformer X27179 at 2097 Bangor St to replace damaged triplex service feeding 2098 Lemay Cres | Ottawa | Tree Contacts | Tree Limb Fallen
8736 | 2006 | 7 | 15 | 0.90972 |  | 50 | 14 | 17 | Urbandale | 4.16kV | AE02 | Several customers on Bingham & Halifax were experiencing low voltage. Transformer OTT419 interrupted to replace paddle & make secondary repairs. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4427 | 2003 | 11 | 11 | 0.62847 |  | 39 | 3 | 4 | Urbandale | 4.16kV | AE02 | Burning hot line clamp. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9755 | 2006 | 11 | 30 | 0.375 |  | 101 | 17 | 10 | Urbandale | 4.16kV | AE02 | Mike Gruich isolated Transformer # 5665 at 933 Shamir to replace PCB Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
20716 | 2012 | 6 | 8 | 0.48264 |  | 40 | 3 | 4 | Urbandale | 4.16kV | AE03 | Transformer X29077 at 974 Drew Ave. isolated to replace broken arrestor | Ottawa | Scheduled Outage | Repair
16396 | 2010 | 7 | 5 | 0.37222 |  | 91 | 67 | 44 | Urbandale | 4.16kV | AE03 | Transformer K666 at 2231 Walkley isolated for contractor to make repairs | Ottawa | Scheduled Outage | Repair
18776 | 2011 | 7 | 19 | 0.65833 |  | 92 | 402 | 262 | Urbandale | 4.16kV | AE03 | Tree found in overhead circuit of AE03 circuit. Circuit isolated to allow crews to remove tree. | Ottawa | Tree Contacts | Tree Fallen
13023 | 2008 | 8 | 8 | 0.45833 |  | 20 | 2 | 6 |  |  | AE03 | Transformer #X26827 at 2094 Dunelm isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
9123 | 2006 | 9 | 5 | 0.54167 |  | 50 | 37 | 44 | Urbandale | 4.16kV | AE03 | At 13:00 trans K667 at 1032 Dakota Ave isolated for PCB replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9280 | 2006 | 9 | 22 | 0.3875 |  | 112 | 11 | 6 | Urbandale | 4.16kV | AE03 | Transformer #OTT6421 located at 2122 Valley Dr isolated to change transformer due to PCB content, PC10A#1132 | Ottawa | Scheduled Outage | Preventive Maintenance
11475 | 2007 | 10 | 6 | 0.87847 |  | 70 | 146 | 125 | Urbandale | 4.16kV | AE03 | AE03 circuit was isolated to allow tree contractor to remove large tree limb that was broken and hanging over the overhaed line. | Ottawa | Tree Contacts | Tree Limb Fallen
19356 | 2011 | 10 | 11 | 0.38542 |  | 30 | 4 | 7 | Urbandale | 4.16kV | AE03 | Isolated transformer X27767 at 2157 Carnegie St for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
9752 | 2006 | 11 | 29 | 0.39236 |  | 133 | 24 | 11 | Urbandale | 4.16kV | AE03 | Isolated and replaced transformer OTT2049 at 2110 Dunelm Dr (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
7965 | 2006 | 2 | 24 | 0.47917 |  | 385 | 15 | 5 | Urbandale | 4.16kV | AE04 | D. Jones reports red phase fuse closed at AE04-Dip#1. Fuse blow, causing AE04 circuit to auto reclose. Bad cable section between AE04-Dip1 & V227. 5 customers were isolated while emergency switch was completed at 2191 Arch St. V227 was isolated to allow crews to disconnect RWB cable section from V227 to AE04-Dip 1 ar pole# 7. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20262 | 2012 | 3 | 31 | 0.48958 |  | 70 | 10 | 9 | Urbandale | 4.16kV | AE04 | Trans X26795 at 2219 Arch St was isolated in order to reconnect defective sec service repaired by Contractor | Ottawa | Scheduled Outage | Repair
20551 | 2012 | 5 | 22 | 0.37847 |  | 174 | 519 | 179 | Urbandale | 4.16kV | AE04 | Vault V227 transformer bus @ 850 Canterbury was isolated to allow contractor to perform secondary maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
20552 | 2012 | 5 | 22 | 0.38611 |  | 160 | 477 | 179 | Urbandale | 4.16kV | AE04 | Vault V226 transformer bus @ 830 Canterbury was isolated to allow contractor to perform secondary maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
10528 | 2007 | 6 | 5 | 0.375 |  | 155 | 23 | 9 | Urbandale | 4.16kV | AE04 | Rick Wallace isolated TRF OTT6215 @ 2400 Heaton for a TRF change | Ottawa | Scheduled Outage | Preventive Maintenance
10529 | 2007 | 6 | 5 | 0.375 |  | 155 | 31 | 12 | Urbandale | 4.16kV | AE04 | Mike Gruich isolated TRF OTT 3493 @ 2435 Heaton for a TRF change | Ottawa | Scheduled Outage | Preventive Maintenance
14570 | 2009 | 6 | 18 | 0.83333 |  | 42 | 4 | 5 | Urbandale | 4.16kV | AE04 | Transformer #X37967 located at 2266 Harding isolated to reconnect service after elec made repairs | Ottawa | Scheduled Outage | Repair
12736 | 2008 | 6 | 26 | 0.68125 |  | 110 | 352 | 192 | Albion | 4.16kV | AE04 | SC07 hit by lightning causing flash on overhead circuit. | Ottawa | Adverse Weather | Lightning
12796 | 2008 | 7 | 7 | 0.35417 |  | 80 | 13 | 10 | Urbandale | 4.16kV | AE04 | Refused switch feeding X26776 at 2269 Horton St was found blown due to a Raccoon | Ottawa | Foreign Interference | Animal
19559 | 2011 | 11 | 11 | 0.58125 |  | 163 | 3 | 1 | Urbandale | 4.16kV | AE04 | Switch feeding transformer TP3504 at 2140 Walkley was opened by mistake during switching causing an unscheduled outage to 1 customer. | Ottawa | Human Element | Switching Errors
4977 | 2004 | 4 | 7 | 0.4125 |  | 258 | 73 | 17 | AE | 4.16kV | AE05 | V390, V391, K664, K665 on Halifax Drive were isolated to allow crew to install new cable to V390 to new pole . | Ottawa | Scheduled Outage | Construction
20560 | 2012 | 5 | 23 | 0.40764 |  | 278 | 139 | 30 | Urbandale | 4.16kV | AE05 | Vaults V390, V391 and Transformers K664 and K665 on Halifax were isolated to allow crew to replace vault transformers and contractor to perform vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
6665 | 2005 | 6 | 6 | 0.57153 |  | 114 | 433 | 228 | Urbandale | 4.16kV | AE05 | AE05 circuit had to be removed from service manually due to primary wires down & sparking near a propane tank. Repairs were made & all customers restored. See ID #6663 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
18447 | 2011 | 6 | 21 | 0.3125 |  | 70 | 4 | 3 | Urbandale | 4.16kV | AE05 | Transformer #X26819 located at 2300 Urbandale opened up due to raccoon interference | Ottawa | Foreign Interference | Animal
12737 | 2008 | 6 | 26 | 0.68125 |  | 111 | 422 | 228 | Urbandale | 4.16kV | AE05 | SC7 was hit by lightning causing flashing on overhead circuit. | Ottawa | Adverse Weather | Lightning
5493 | 2004 | 7 | 14 | 0.74931 |  | 49 | 4 | 5 | Urbandale | 4.16kV | AE05 | A squirrel made contact at transformer Ott1737 at 2281 Crane St which caused the fuse to blow that feeds that transformer. | Ottawa | Foreign Interference | Animal
12841 | 2008 | 7 | 15 | 0.46736 |  | 14 | 49 | 209 | Urbandale | 13.2kV | AE05 | SCADA indicated AE05 breaker opened. Checked with Police and fire, no reports. AE05 breaker closed and holding. Circuit patrolled nothing found. (Possible tree contact - Heavily treed at Harding and Walkley area). | Ottawa | Unknown/Other
12878 | 2008 | 7 | 18 | 0.17847 |  | 173 | 657 | 228 | Urbandale | 4.16kV | AE05 | AE05 auto trip, attempted one close from SCADA but breaker reopened. Egress cable pohead found blown. Same isolated and load transferred to AE00. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14795 | 2009 | 7 | 21 | 0.37847 |  | 46 | 51 | 67 | Urbandale | 13.2kV | AE05 | At 09:05 S25867 Blue phase at 2083 Walkley was isolated for tree crew. | Nepean | Scheduled Outage | Preventive Maintenance
14885 | 2009 | 7 | 31 | 0.375 |  | 222 | 37 | 10 | Urbandale | 4.16kV | AE05 | The O/H crew isolate the B phase at Harding and Walkley for the tree company to remove a large tree from the primary. | Ottawa | Scheduled Outage | Preventive Maintenance
13013 | 2008 | 8 | 7 | 0.39653 |  | 281 | 140 | 30 | Urbandale | 4.16kV | AE05 | Vaults V390 & V391 and transformers K664 & K665 at 2220 & 2240 Halifax St in Ottawa isolated for customer maintenance.. | Ottawa | Scheduled Outage | Preventive Maintenance
19141 | 2011 | 9 | 12 | 0.43056 |  | 236 | 43 | 11 | Urbandale | 4.16kV | AE05 | Transformer #X26775 located at 2277 Urbandale Dr opened by crew to transfer plant for a pole change | Ottawa | Scheduled Outage | Construction
19142 | 2011 | 9 | 12 | 0.43056 |  | 236 | 39 | 10 | Urbandale | 4.16kV | AE05 | Transformer #X26824 located at 2289 Urbandale Dr opened by crew to transfer plant for a pole change | Ottawa | Scheduled Outage | Construction
17685 | 2011 | 3 | 8 | 0.6125 |  | 108 | 45 | 25 | Urbandale | 4.16kV | AE06 | Transformer #X26878 located at 2189 Valley Dr opened due to defective equipment | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20638 | 2012 | 5 | 30 | 0.56736 |  | 58 | 4 | 4 | Urbandale | 4.16kV | AE06 | Transformer X27017 at 1007 Connery Ave isolated for service upgrade | Ottawa | Scheduled Outage
6765 | 2005 | 6 | 20 | 0.37153 |  | 50 | 1 | 1 | Urbandale | 4.16kV | AE06 | Isolated vault V00701 at 2158 St Laurent to replace broken switch | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3612 | 2003 | 6 | 26 | 0.39236 |  | 317 | 143 | 27 | Urbandale | 4.16kV | AE06 | Vaults V391 & V390 (2220 & 2240 Halifax Drive) isolated for preventive maintenance (torque connections & cleaning). The outage for the vaults also caused an outage to K664 & K665 due to being feed from the same pothead. | Ottawa | Scheduled Outage | Preventive Maintenance
9042 | 2006 | 8 | 24 | 0.375 |  | 135 | 7 | 3 | Urbandale | 4.16kV | AE06 | Transformer #OTT1655 located at 1045 Connery isolated to change transformer due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
9138 | 2006 | 9 | 7 | 0.50347 |  | 115 | 17 | 9 | Urbandale | 4.16kV | AE06 | Chris Williams opened transformer #OTT6175 at 2317 Susan and changed a delta. | Ottawa | Scheduled Outage | Preventive Maintenance
17068 | 2010 | 10 | 6 | 0.52014 |  | 406 | 7 | 1 | Urbandale | 4.16kV | AE06 | defective transformer TP3904 at 2158 St. Laurent was isolated and replaced. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11664 | 2007 | 11 | 5 | 0.71667 |  | 30 | 2 | 4 | Urbandale | 4.16kV | AE06 | O/H transformer at 992 Connery Ave in Ottawa isolated to replace service wires. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13887 | 2009 | 1 | 22 | 0.58333 |  | 30 | 6 | 11 | Urbandale | 4.16kV | AE07 | Transformer #X29707 located at 2381 Howland Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
6236 | 2005 | 2 | 25 | 0.57639 |  | 11 | 45 | 245 | Urbandale |  | AE07 | AE07 circuit was dumped to allow tree crew to remove a tree from the overhead at 2380 Howland. | Ottawa | Tree Contacts | Tree Fallen
17781 | 2011 | 3 | 24 | 0.75694 |  | 5 | 1 | 8 | Urbandale | 4.16kV | AE07 | Transformer #X29712 located at 2207 Audrey Ave opened by crew to cut down a service | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17817 | 2011 | 4 | 1 | 0.40625 |  | 15 | 5 | 19 | Urbandale | 4.16kV | AE07 | Kiosk K00376 at 2306 Russell Rd isolated to disconnect a customer for non-payment | Ottawa | Scheduled Outage
10393 | 2007 | 5 | 9 | 0.49306 |  | 30 | 11 | 22 | Urbundale | 4.16kV | AE07 | Isolated K319 at 2338 Russell Rd to disconnect Ped 349P3 for electrician to repair underground service | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8270 | 2006 | 5 | 10 | 0.59375 |  | 10 | 3 | 18 | Urbandale | 4.16kV | AE07 | Denis has K376 at 2306 Russell out to fix a damaged pedestal. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5172 | 2004 | 5 | 18 | 0.45694 |  | 36 | 5 | 9 | AE | 4.16kV | AE07 | Tx OTT4129 at 2454 Howland was off at 10:58 & power restored to 9 customers @ 11:34 due to defective connections. As per dispatch. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6620 | 2005 | 5 | 30 | 0.69514 |  | 19 | 2 | 7 | Urbandale | 4.16kV | AE07 | Trans @ 2410 Joliffe isolated to relocate sec service to new attachment | Ottawa | Scheduled Outage | Repair
10489 | 2007 | 5 | 31 | 0.38194 |  | 170 | 51 | 18 | Urbandale |  | AE07 | Tranformer #OTT3489 at 2441 Joliffe isolated by Rick Wallace to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
18321 | 2011 | 6 | 7 | 0.43333 |  | 322 | 11 | 2 | Urbandale | 4.16kV | AE07 | V724 and V725 at 2630 and 2650 Southvale were isolated to allow Hydro Ottawa crews to replace transformers containing PCBs and customer to perform vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
8483 | 2006 | 6 | 13 | 0.74236 |  | 431 | 43 | 6 | Urbandale | 4.16kV | AE07 | Defective 75KVA transformer @ 2156 Audrey OTT273 .Crew called to replace XFMR. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5335 | 2004 | 6 | 19 | 0.47222 |  | 10 | 3 | 19 | Urbandale | 4.16kV | AE07 | Transformer K00346 at 2282 Russel Rd isolated to reconnect a service. | Ottawa | Scheduled Outage
8563 | 2006 | 6 | 21 | 0.39583 |  | 50 | 5 | 6 | Urbandale | 4.16kV | AE07 | Transformer #OTT6354 located at rear of 2444 Tupper isolated due to service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
18482 | 2011 | 6 | 24 | 0.4125 |  | 110 | 15 | 8 | Urbandale | 4.16kV | AE07 | Transformer #X29711 located at 2227 Martha Ave opened up due to defective drop lead to transformer | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18777 | 2011 | 7 | 20 | 0.44444 |  | 23 | 3 | 8 | Urbandale | 4.16kV | AE07 | Transformer #X29711 located at 2220 Audrey opened by crew to drop service due to broken stand pipe | Ottawa | Tree Contacts | Tree Limb Fallen
5554 | 2004 | 7 | 22 | 0.69722 |  | 96 | 54 | 34 | Urbandale | 4.16kV | AE07 | A stirrup burned off on the connection at the local run off on Walkley to Audrey | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16605 | 2010 | 8 | 2 | 0.54028 |  | 121 | 20 | 10 | Urbandale | 4.16kV | AE07 | Transformer #X29703 located at 2433 Howland opened up due broken cut out and arrestor | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3874 | 2003 | 8 | 8 | 0.42153 |  | 9 | 2 | 13 | Urbandale | 4.16kV | AE07 | Crew opened transformer to reconnect disc'd customer. | Ottawa | Scheduled Outage
13214 | 2008 | 9 | 10 | 0.85556 |  | 33 | 6 | 10 | Urbandale | 8/4.8kV | AE07 | Transformer #X29716 at 2453 Walkley Rd isolated to allow for repairs to connections at pole | Ottawa | Scheduled Outage | Repair
5870 | 2004 | 11 | 8 | 0.375 |  | 525 | 158 | 18 | Urbandale | 4.16kV | AE07 | Transformer at 2318 Russell isolated for secondary cable arrangement. | Ottawa | Scheduled Outage | Construction
11814 | 2007 | 12 | 5 | 0.39583 |  | 20 | 6 | 18 | Urbandale | 4.16kV | AE07 | Transformer #K346 located at 2179 Melfort isolated to connect a service | Ottawa | Scheduled Outage | Construction
6110 | 2004 | 12 | 31 | 0.17917 |  | 112 | 110 | 59 | Urbandale | 4.16kV | AE07 | Laneville reports Broken switch on AE07 o/h feeding 2669 southvale. 4 transformers out, 59 customers. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18115 | 2011 | 5 | 8 | 0.23403 |  | 52 | 713 | 823 | Urbandale | 13.2kV | AET2 | The AET2 transformer at Urbandale substation tripped due to gas accumualtion. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6293 | 2005 | 3 | 16 | 0.47917 |  | 75 | 5 | 4 | Brookfield | 4.16kV | AF02 | crew opened transformer OTT1308 at 2123 Chalmers to remove old transformer | Ottawa | Scheduled Outage | Preventive Maintenance
18113 | 2011 | 5 | 7 | 0.84236 |  | 226 | 192 | 57 | Brookfield | 4.16kV | AF02 | AF02 circuit was opened to allow crew to cut overhead line from trunk feeder at 2136 chalmers to remove two trees from overhead circuit. | Ottawa | Tree Contacts | Tree Fallen
16259 | 2010 | 6 | 13 | 0.81944 |  | 105 | 2 | 1 | Brookfield | 4.16kV | AF02 | Transformer X27498 supplying 1339 Bank st was opened to repair service damaged by tree contact. Switch supplying Tx also replaced. | Ottawa | Tree Contacts | Tree Limb Fallen
9034 | 2006 | 8 | 23 | 0.55556 |  | 55 | 3 | 3 | Brookfield | 4.16kV | AF02 | Isolated transformer OTT1309 at 2126 Chalmers Rd to repair service | Ottawa | Scheduled Outage | Repair
16859 | 2010 | 9 | 3 | 0.69167 |  | 37 | 35 | 57 | Brookfield | 4.16kV | AF02 | A large tree on Billings east of Cavendish fell on the primary conductor and threatened to pull down the 3 phase overhead. The circuit was dumped to allow crews to remove the offending tree limbs and prevent furthur damage to Hydro plant. | Ottawa | Tree Contacts | Tree Fallen
4037 | 2003 | 9 | 8 | 0.40833 |  | 162 | 24 | 9 | Brookfield | 4.16kV | AF02 | M. Branchaud isolated at the rear of 2634 Trverse. To transfer secondary to new pole. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13344 | 2008 | 10 | 8 | 0.51181 |  | 2 | 3 | 100 | Brookfield | 4.16kV | AF02 | AF02 feeder auto trip due to Fire truck bumped a guy wire shaking the pole and conductors made contact. | Ottawa | Foreign Interference | Vehicle
9454 | 2006 | 10 | 18 | 0.34722 |  | 7 | 0 | 3 | Brookfield | 4.16kV | AF02 | Transformer #OTT1309 located at 2126 Chalmers isolated to disconnect a service for repairs. PC10A #1697 | Ottawa | Scheduled Outage | Preventive Maintenance
4722 | 2004 | 1 | 23 | 0.53056 |  | 15 | 2 | 10 | Brookfield | 4.16kV | AF03 | MT1845 was interrupted in order to change its feed from AF03 white phase to AF03 blue phase. | Ottawa | Scheduled Outage | Construction
15988 | 2010 | 4 | 24 | 0.90972 |  | 13 | 2 | 11 | Brookfield | 4.16kV | AF03 | The overhead transformer at 1727 Grassmere was interrupted to replace sparking line clamp. 11 customers on Grassmere & Alta Vista were affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
18658 | 2011 | 7 | 14 | 0.69931 |  | 193 | 29 | 9 | Brookfield | 4.16kV | AF03 | Dip feeding P334 at 1719 Bank st was isolated due to fire. Service was disconnected to affected building and transformer was restored. | Ottawa | Adverse Environment | Fire
10966 | 2007 | 7 | 30 | 0.46875 |  | 45 | 14 | 18 | Brookfield | 4.16kV | AF03 | Crew isolated transformer OTT2857 at 1692 Grasmere Cres to install new service | Ottawa | Scheduled Outage | Emergency Services Request
16687 | 2010 | 8 | 7 | 0.92222 |  | 161 | 8 | 3 | Brookfield | 4.16kV | AF03 | Vault V0032 at 2710 Alta Vista was isolated to allow contractor to perform vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
18967 | 2011 | 8 | 18 | 0.57847 |  | 8 | 39 | 295 | BROOKFIELD | 4.16kV | AF03 | AF03 opened during lightning storm. Closed via SCADA and held. Brookfield ID# 18967. | Ottawa | Adverse Weather | Lightning
18975 | 2011 | 8 | 18 | 0.78472 |  | 25 | 0 | 1 | Brookfield | 4.16kV | AF03 | Lightning caused V87 CB1 to open and flash over contractor made repairs. Brookfield (AF03) ID#18975 | Ottawa | Lightning
7369 | 2005 | 9 | 23 | 0.22778 |  | 669 | 145 | 5 | Brookfield | 4.16kV | AF03 | 4kV pole pothead feeding 2710 Alta Vista failed. Customers had partial power in the beginning and then were put on generator suuply. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9725 | 2006 | 11 | 24 | 0.375 |  | 225 | 38 | 10 | Brookfield | 4.16kV | AF03 | Isolated and replaced transformer OTT2859 at 1730 Grasmere Cres (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9805 | 2006 | 12 | 7 | 0.38194 |  | 195 | 39 | 12 | Brookfield | 4.16kV | AF03 | Transformer #OTT108 located at 1731 Grasmere Cres isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
19761 | 2011 | 12 | 25 | 0.59444 |  | 42 | 2 | 3 | Brookfield | 4.16kV | AF03 | Transformer P128 at 1753 Bank was isolated to allow crew to replace broken fused cutout. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15602 | 2010 | 1 | 2 | 0.55972 |  | 559 | 9 | 1 | Brookfield | 4.16kV | AF04 | A cable fault between V432 and V431caused a fuse to blow on a three phase cutout feeding V432 and V431 @ 2487 Kaladar. V431 will remain off until cable is repaired. V432 was re-energized. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18022 | 2011 | 4 | 28 | 0.57847 |  | 72 | 102 | 85 | Brookfield | 4.16kV | AF04 | AF04 circuit breaker tripped during wind/lightning storm. Close VIA scada and held. | Ottawa | Adverse Weather | Wind
6792 | 2005 | 6 | 24 | 0.76389 |  | 110 | 15 | 8 | Brookfield | 4.16kV | AF04 | Transformer #OTT3114 located at 1609 Edge Hill Place isolated to replace the lead on the cut out | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6904 | 2005 | 7 | 11 | 0.69792 |  | 295 | 30 | 6 | Brookfield | 4.16kV | AF04 | Replaced transformer OTT 704 at 1656 Bank St as old transformer was found defective | Ottawa | Unknown/Other | No Apparent Cause
16976 | 2010 | 9 | 21 | 0.73958 |  | 235 | 8 | 2 | Brookfield DS |  | AF04 | V0431 & V0432 had to be isolated under a PC10C to allow Balck & Macdonald to repair a duct bank that had collapsed on to customer owned cables running between V0431 & V0432. | Ottawa | Scheduled Outage | Repair
17043 | 2010 | 10 | 2 | 0.78125 |  | 288 | 10 | 2 | Brookfield | 4.16kV | AF04 | V432 at 2487 Kaladar was isolated to allow the customers contractor to reconnect V431 and rebuild duct bank | Ottawa | Scheduled Outage | Preventive Maintenance
19803 | 2012 | 1 | 9 | 0.42708 |  | 195 | 32 | 10 | Brookfield | 4.16kV | AF05 | Transformer #X27721 located at 1530 Bank st opened by crew to replace open wire service | Ottawa | Scheduled Outage | Construction
10091 | 2007 | 3 | 5 | 0.63889 |  | 65 | 13 | 12 | Brookfield | 4.16kV | AF05 | Isolated transformer OTT 1595 at 1278 Anoka St to replace secondary connection on the transformer | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8083 | 2006 | 3 | 30 | 0.57986 |  | 15 | 3 | 12 | Brookfield | 4.16kV | AF05 | Isolated transformer OTT1595 at 1275 Collins Ave to remove Racoon from the switch (Racoon suvived) | Ottawa | Foreign Interference | Animal
18021 | 2011 | 4 | 28 | 0.57639 |  | 74 | 342 | 277 | Brookfield | 4.16kV | AF05 | AF05 circuit breaker auto-reclosed and locked out during wind/lightning storm. Closed VIA scada and held. | Ottawa | Adverse Weather | Wind
16107 | 2010 | 5 | 19 | 0.89583 |  | 55 | 1 | 1 | BROOKFIELD | 4.16kV | AF05 | Transformer P1568 isolated to replace 3 defective switches | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20562 | 2012 | 5 | 23 | 0.48542 |  | 46 | 213 | 278 | Brookfield |  | AF05 | AF05 CB tripped due to a cracked insulator at AF05 PPH. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18538 | 2011 | 6 | 27 | 0.71458 |  | 88 | 1 | 1 | Brookfield | 4.16kV | AF05 | Main breaker at V84, 1376 Bank St. Tripped. Crews tested transformers and restored the vault. No cause found. | Ottawa | Unknown/Other | No Apparent Cause
11884 | 2007 | 12 | 25 | 0.74861 |  | 177 | 35 | 12 | Brookfield | 4.16kV | AF05 | Replaced broken switch feeding transformer OTT1595 at 1279 Collins Ave | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20583 | 2012 | 5 | 25 | 0.78611 |  | 5 | 50 | 605 | Brookfield | 13.2kV | AF06 | Lightning storm and high winds caused circuit to open. Brookfield (AF06) ID#20580 Crew found wires down | Ottawa | Adverse Weather | Wind
20607 | 2012 | 5 | 26 | 0.0041667 |  | 659 | 1801 | 164 | Brookfield | 4.16kV | AF06 | High winds caused the W phase conductor to come down in the Gregg and Falcon area and also a blown R phase arrestor. | Ottawa | Adverse Weather | Wind
10484 | 2007 | 5 | 30 | 0.82986 |  | 374 | 6 | 1 | Brookfeild | 4.16kV | AF06 | Part of the UY04 on Colonel By Dr is being fed from AF06, because of a old cable fault which is own by NCC. The dip switch at pole 7 on AF06 on Clover and Heron Rd open, cable and transformers check out good, suspected problem is with the cable on Colonel By Dr which is also owned by NCC. The remaining transformer that’s out feeds street lights on Colonel By. | Ottawa | Unknown/Other
18397 | 2011 | 6 | 13 | 0.84306 |  | 2 | 0 | 14 | Brookfield | 4.16kV | AF06 | Transformer X28106 at 2496 Clover Ave isolated to remove limb from triplex | Ottawa | Tree Contacts | Tree Limb Fallen
10722 | 2007 | 6 | 25 | 0.21875 |  | 54 | 11 | 12 | Brookfield | 4.16kV | AF06 | Squirrel caused transformer fuse to open at 2418 Clover ave. Transformer OTT3109 | Ottawa | Foreign Interference | Animal
3731 | 2003 | 7 | 13 | 0.30208 |  | 40 | 4 | 6 | AF | 4.16kV | AF06 | A squirrel made contact with the fused cut - out to o/h Tx N1692-35 @ 1514 Clementine. The Tx was re - fused & power restored to 6 customers, 1496 to 1520 Clementine including a Rogers amplifier. | Ottawa | Foreign Interference | Animal
18665 | 2011 | 7 | 15 | 0.47917 |  | 70 | 13 | 11 | Brookfield | 4.16kV | AF06 | Trans at 2409 Carlsen Ave was isolated in order to replace secondary service | Gloucester | Scheduled Outage | Preventive Maintenance
18799 | 2011 | 7 | 22 | 0.76042 |  | 200 | 63 | 19 | BROOKFIELD | 4.16kV | AF06 | REPLACED BROKEN HOT LINE CLAMP ON TRANSFORMER X24244 AT 2459 FALCON AVE | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16834 | 2010 | 8 | 30 | 0.39236 |  | 70 | 23 | 20 | BROOKFIELD | 4.16kV | AF06 | Transformer X28111 at 2436 Carlsen isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
11257 | 2007 | 9 | 6 | 0.41667 |  | 30 | 9 | 18 | BROOKFIELD | 13.2kV | AF06 | TRANSF #OTT1192 - X28145 AT 2466 CARLSEN AVE ISOLATED TO ALLOW FOR SERVICE UPGRADE | Ottawa | Scheduled Outage | Construction
16903 | 2010 | 9 | 8 | 0.43889 |  | 34 | 12 | 21 | Brookfield DS | 4.16kV | AF06 | Transformer X25037 at 2416 Clementine was opened to allow crews to install a new service. | Ottawa | Scheduled Outage | Construction
15193 | 2009 | 10 | 1 | 0.4375 |  | 100 | 17 | 10 | BROOKFIELD | 4.16kV | AF06 | transformer X28123 at 2411 Falcon Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
4216 | 2003 | 10 | 6 | 0.39583 |  | 30 | 7 | 14 | Fisher | 4.16kV | AF06 | Rearrange secondary. | Ottawa | Scheduled Outage | Repair
9568 | 2006 | 10 | 31 | 0.54167 |  | 195 | 49 | 15 | Brookfield | 4.16kV | AF06 | At 13:00 trans OTT3326 at 2415 Huntley was isolated for PCB transformer replacement | Ottawa | Scheduled Outage | Preventive Maintenance
13595 | 2008 | 11 | 12 | 0.44097 |  | 160 | 56 | 8 | Brookfield | 4.16kV | AF06 | Isolated and replaced transformer X28111 at 2436 Carlsen Ave | Ottawa | Scheduled Outage | Preventive Maintenance
13609 | 2008 | 11 | 14 | 0.39583 |  | 165 | 80 | 29 | Brookfield | 4.16kV | AF06 | Transformer #X28110 located at 2417 Clover isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
9745 | 2006 | 11 | 28 | 0.39653 |  | 167 | 11 | 4 | Brookfield | 4.16kV | AF06 | Isolated Transformer at 2479 Clementine to replace Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
13678 | 2008 | 11 | 28 | 0.54514 |  | 35 | 18 | 31 | Brookfield | 4.16kV | AF06 | Transformer #X28110 located at 2417 Clover isolated to allow for final repairs for PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
4798 | 2004 | 2 | 18 | 0.39583 |  | 90 | 14 | 9 | Brookfield | 12/7.2kV | AF07 | Transformer 2351 at 2526 Traverse isolated for cable maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
4800 | 2004 | 2 | 18 | 0.39583 |  | 75 | 24 | 19 | Brookfield | 27.6/16kV | AF07 | Transformer OTT 6299 at 2558 Traverse isolated for High Voltage cable maintenance. | Ottawa | Scheduled Outage
14035 | 2009 | 3 | 11 | 0.52083 |  | 65 | 11 | 10 | BROOKFIELD | 4.16kV | AF07 | transformer X27714 at 2562 Needham Cres. Isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
14075 | 2009 | 3 | 17 | 0.48958 |  | 60 | 5 | 5 | Brookfield | 4.16kV | AF07 | Transformer X27765 at 2590 Needham was disconnect to allow crews to re-arrange plant | Ottawa | Scheduled Outage | Preventive Maintenance
14076 | 2009 | 3 | 17 | 0.48958 |  | 60 | 10 | 10 | Brookfield | 4.16kV | AF07 | transformer X24231 at 2594 Needham was disconnected to allow crews to re-arrange plant | Ottawa | Scheduled Outage | Preventive Maintenance
14099 | 2009 | 3 | 25 | 0.54167 |  | 35 | 3 | 5 | Brookfield | 4.16kV | AF07 | At 13:00 trans at 2590 NEEDHAM was isolated in order to replace a pole | Ottawa | Scheduled Outage | Preventive Maintenance
14126 | 2009 | 3 | 31 | 0.375 |  | 265 | 44 | 10 | Brookfield | 4.16kV | AF07 | Transformer #X27715 located at 2597 Needham isolated for a pole change. | Ottawa | Scheduled Outage | Preventive Maintenance
14133 | 2009 | 4 | 1 | 0.375 |  | 285 | 48 | 10 | Brookfield | 4.16kV | AF07 | Transformer #X24231 located at 2594 Needham Cres isolated for a pole change. | Ottawa | Scheduled Outage | Preventive Maintenance
14137 | 2009 | 4 | 2 | 0.38194 |  | 280 | 23 | 5 | Brookfield | 4.16kV | AF07 | Transformer #X27765 located at 2590 Needham Cres isolated for a pole change | Ottawa | Scheduled Outage | Preventive Maintenance
4978 | 2004 | 4 | 7 | 0.61111 |  | 82 | 22 | 16 | Brookfield | 4.16kV | AF07 | Transformer # Ott6820 isolated to repair overhead services at 2560 Yarmouth. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10233 | 2007 | 4 | 10 | 0.54167 |  | 90 | 15 | 10 | Brookfield | 4.16kV | AF07 | Isolated transformer OTT6304 at 2730 Traverse Dr to install new pole PC10A1590 | Ottawa | Scheduled Outage | Construction
10239 | 2007 | 4 | 11 | 0.56597 |  | 42 | 7 | 10 | Brookfield | 4.16kV | AF07 | Transformer #OTT6304 located at 2730 Traverse Dr isolated due to contractor installing pool | Ottawa | Scheduled Outage | Construction
10244 | 2007 | 4 | 12 | 0.39931 |  | 189 | 25 | 8 | Brookfield | 4.16kV | AF07 | At 09:35 trans OTT6304 at 2730 Traverse Dr was isolated in order to transfer plant to new poles | Ottawa | Scheduled Outage | Preventive Maintenance
14176 | 2009 | 4 | 15 | 0.375 |  | 180 | 48 | 16 | BROOKFIELD | 4.16kV | AF07 | transformer X27714 at rear of 2550 Needham Cres isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
14208 | 2009 | 4 | 24 | 0.40625 |  | 145 | 24 | 10 | Brookfield | 4.16kV | AF07 | Isolated transformer X27716 at 2530 Needham Cres to replace transformer | Ottawa | Scheduled Outage | Construction
12394 | 2008 | 5 | 5 | 0.55556 |  | 40 | 9 | 13 | Hillcrest | 4.16kV | AH02 | isolated transformer X35197 at 380 Roosevelt Ave to install two new services | Ottawa | Scheduled Outage | Construction
8517 | 2006 | 6 | 19 | 0.375 |  | 35 | 4 | 7 | HILLCREST | 4.16kV | AH02 | Isolated transformer OTT5526 at 345 Roosevelt Ave to upgrade service | Ottawa | Scheduled Outage | Repair
13042 | 2008 | 8 | 12 | 0.375 |  | 100 | 12 | 7 | Hillcrest | 4.16kV | AH02 | Transformer #X35195 located at 335 Roosevelt isolated for Jamie Petrachuks crews to do tree trimming | Ottawa | Scheduled Outage
18939 | 2011 | 8 | 15 | 0.375 |  | 665 | 11 | 1 | Hillcrest | 4.16kV | AH02 | At 09:00 vault V639 at 445 Richmond Road was made available to allow crew to repair defective secondary switch. 1 customer was affected. Hillcrest (AH02) ID#18939 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9263 | 2006 | 9 | 21 | 0.44375 |  | 111 | 20 | 11 | Hillcrest | 4.16kV | AH02 | Transformer #OTT1923 located at 383 Dominion isolated due to pole change | Ottawa | Scheduled Outage | Construction
9433 | 2006 | 10 | 15 | 0.39514 |  | 275 | 130 | 159 | Hillcrest AH | 4.16kV | AH02 | A single phase of AH02 between Kirchoff & Atlantis N. of Workman burned down at a transformer connection. The circuit was opened to isolate the damaged section. On call crew made repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17198 | 2010 | 10 | 31 | 0.22222 |  | 15 | 4 | 14 | Hillcrest | 4.16kV | AH02 | Transformer X35193 at 370 Dominion was opened to replace a defective hot line clamp. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7801 | 2006 | 1 | 12 | 0.41667 |  | 80 | 11 | 8 | Hillcrest | 4.16kV | AH04 | Removed transformer OTT6286 at 460 Tillbury re-located 8 services to new transformer | Ottawa | Scheduled Outage
4895 | 2004 | 3 | 15 | 0.40625 |  | 35 | 2 | 4 | Hillcrest | 4.16kV | ah04 | Crew opened transformer at 472 Wellesley to repalce service & cutout. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17830 | 2011 | 4 | 4 | 0.71042 |  | 92 | 301 | 196 | HILLCREST | 4.16kV | AH04 | Pole fire caused AH04 breaker to trip. Down guys cleared and AH04 breaker closed restoring power. | Ottawa | Defective Equipment
13122 | 2008 | 8 | 19 | 0.43403 |  | 2755 | 46 | 1 | Hillcrest | 4.16kV | AH04 | Emergency isolation of V194 at 710 Broadview required due to faulted secondary bus. Repairs to bus as well as routine maintenance and asbestos removal were performed by Eaton Electric. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13648 | 2008 | 11 | 20 | 0.4375 |  | 45 | 6 | 8 | HILLCREST | 4.16kV | AH04 | Xfmr X32076 at 627 Broadview isolated to allow for pole change | Ottawa | Scheduled Outage | Construction
13684 | 2008 | 11 | 29 | 0.58472 |  | 58 | 4 | 4 | Hillcrest | 4.16kV | AH04 | Isolared transformer X32076 to transfer Hydro plant to new pole | Ottawa | Scheduled Outage | Construction
13688 | 2008 | 11 | 30 | 0.38403 |  | 142 | 12 | 5 | Hillcrest | 4.16kV | AH04 | At 09:13 transformer at 637 Broadview was isolated in order to replace a pole | Ottawa | Scheduled Outage | Preventive Maintenance
13748 | 2008 | 12 | 14 | 0.52083 |  | 170 | 14 | 5 | Hillcrest | 4.16kV | AH04 | Isolated transformer X32082 at 575 Broadview Ave for a pole change | Ottawa | Scheduled Outage | Construction
6992 | 2005 | 7 | 19 | 0.41667 |  | 80 | 15 | 11 | Hillcrest | 4.16kV | AH04/AH13 | Transformer#OTT919 isolated at 464 Broadview for preventative maintenance to check transformer | Ottawa | Scheduled Outage | Preventive Maintenance
17765 | 2011 | 3 | 23 | 0.40972 |  | 20 | 1 | 4 | Hillcrest | 4.16kV | AH05 | Trans at 352 Wilmont X34196 was isolated for service work | Ottawa | Scheduled Outage | Preventive Maintenance
15851 | 2010 | 3 | 25 | 0.92431 |  | 116 | 15 | 8 | Hillcrest | 4.16kV | AH05 | Crew replaced broken switch on transformer X33932. | Ottawa | Defective Equipment
6345 | 2005 | 3 | 31 | 0.75139 |  | 18 | 3 | 9 | Hillcrest | 4.16kV | AH05 | Isolated transformer #5346 at 378A Richmond Rd to repair bad secondary | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20434 | 2012 | 5 | 1 | 0.59375 |  | 35 | 5 | 9 | Hillcrest | 4.16kV | AH05 | Transformer X33932 at 376A Wilmont isolated to allow for repairs to service at 375 Wilton Ave. | Ottawa | Scheduled Outage | Repair
16129 | 2010 | 5 | 24 | 0.58333 |  | 334 | 28 | 5 | Hillcrest | 4.16kV | AH05 | A transformer at 426 Churchill was isolated for pole replacement. | Ottawa | Scheduled Outage
16188 | 2010 | 6 | 3 | 0.48194 |  | 20 | 76 | 229 | Hillcrest | 4.16kV | AH05 | AH05 circuit was isolated to allow crews to replace defective porceilin insulator at Richmond and Churchill. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5416 | 2004 | 7 | 1 | 0.61458 |  | 36 | 141 | 235 | Hillcrest | 4.16kV | AH05 | AH05 tripped during a lightening storm on red and blue phase instantaneous, recloser was blocked, closed successfully by SCADA, to be patrolled later. | Ottawa | Adverse Weather | N/A
14920 | 2009 | 8 | 7 | 0.40278 |  | 115 | 17 | 9 | HILLCREST | 4.16kV | AH05 | Transformer X35047 at intersection of Winston Ave & Madison Ave isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
13041 | 2008 | 8 | 12 | 0.375 |  | 100 | 17 | 10 | Hillcrest | 4.16kV | AH05 | Transformer #X33931 located at 344 Winston Ave isolated for Jamie Petrachucks crews to do tree trimming | Ottawa | Scheduled Outage | Preventive Maintenance
19075 | 2011 | 9 | 2 | 0.35764 |  | 7 | 1 | 6 | Hillcrest | 4.16kV | AH05 | Transformer X33929 at 354 Whitby Ave isolated to remove service | Ottawa | Scheduled Outage | Construction
13213 | 2008 | 9 | 10 | 0.67361 |  | 205 | 17 | 5 | HILLCREST | 4.16kV | AH05 | Transformer #OTT4119 at 349 Madison Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
8544 | 2006 | 6 | 19 | 0.86944 |  | 1318 | 157 | 14 | Hillcrest | 4.16kV | AH07 | AH07 breaker was opened form SCADA due to phase taken down by a tree in the backyard of 497 Broadview. Phase down was across a garage roof & had the grass on fire. The single phase run off was isolated from the main line & power was restored. The tree was removed by a crane on Tuesday & the downed phase was repaired and energized. | Ottawa | Tree Contacts | Tree Fallen
13068 | 2008 | 8 | 17 | 0.20139 |  | 120 | 18 | 9 | Hillcrest | 4.16kV | AH07 | Single phase run off with 1 o/h transformer isolated to replace defective cut - out at Tx OTT3170 at 469 Hillcrest. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8149 | 2006 | 4 | 13 | 0.41667 |  | 120 | 16 | 8 | Hillcrest | 4.16kV | AH13 | Tony Taylor opened transformer OTT1582 to replace the transformer interuppting power to 8 customers | Ottawa | Scheduled Outage | Repair
18068 | 2011 | 4 | 30 | 0.57986 |  | 18 | 13 | 42 | Hillcrest | 4.16kV | AH13 | S18892 was isolated to repair radial line and remove trees. 42 customers were affected for 16 minutes. Hillcrest (AH13) ID# 18068 | Ottawa | Adverse Weather
3484 | 2003 | 5 | 25 | 0.79514 |  | 425 | 78 | 11 | AH | 4.16kV | AH13 | A 75kva o/h xfmr at 527 Denbury was damaged by a nearby lightning strike & tree limb contact. The on-call crew was called in to replace it. | Ottawa | Tree Contacts | Tree Limb Fallen
12974 | 2008 | 7 | 30 | 0.4375 |  | 40 | 3 | 5 | HILLCREST | 4.16kV | AH13 | Transformer #OTT3565 at 525 Kenwood Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Repair
15160 | 2009 | 9 | 24 | 0.42361 |  | 30 | 6 | 11 | Hillcrest | 4.16kV | AH13 | Isolated transformer X35512 at 561 Golden Ave for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
11557 | 2007 | 10 | 19 | 0.39236 |  | 105 | 18 | 10 | Hillcrest | 4.16kV | AH13 | Transformers #OTT3148 & OTT3149 located at 581 & 593 Highland isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
9675 | 2006 | 11 | 17 | 0.059722 |  | 23 | 2 | 6 | Hillcrest | 4.16kV | AH13 | O/H transformer at 522 Hillcrest interrupted to replace stirup & hotline clamp. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13640 | 2008 | 11 | 19 | 0.5625 |  | 140 | 23 | 10 | Hillcrest | 4.16kV | AH13 | Transformer #X25821 located at 613 Broadview isolated for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
19610 | 2011 | 11 | 20 | 0.70139 |  | 302 | 50 | 10 | Hillcrest DS | 4.16kV | AH13 | Transformer X26227 at 540 Cole Ave. Caught fire and had to be replaced | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4517 | 2003 | 11 | 26 | 0.375 |  | 220 | 18 | 5 | Hillcrest | 4.16kV | AH13 | Transformer #OTT3565 at 526 Kenwood interrupted to remove a tree. | Ottawa | Scheduled Outage
13676 | 2008 | 11 | 28 | 0.38889 |  | 130 | 17 | 8 | Hillcrest | 4.16kV | AH13 | transformer # X32076 at 637 Broadview Ave isolated to allow for re-arranging of service | Ottawa | Scheduled Outage | Repair
13683 | 2008 | 11 | 29 | 0.55556 |  | 40 | 5 | 8 | Hillcrest | 4.16kV | AH13 | Isolared transformer X32075 to transfer Hydro plant to new pole | Ottawa | Scheduled Outage | Construction
13707 | 2008 | 12 | 6 | 0.375 |  | 293 | 39 | 8 | HILLCREST | 4.16kV | AH13 | Transformer X32076 at 627 Broadview isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
17487 | 2011 | 1 | 14 | 0.3875 |  | 232 | 77 | 20 | Hillcrest | 4.16kV | AH14 | At 9:18 crews opened Temp50 on AH14 to allow tree trimming by contractor. 20 customers affected for 232 mins. Hillcrest AH14 ID# 17487 | Ottawa | Scheduled Outage
8131 | 2006 | 4 | 11 | 0.4625 |  | 79 | 13 | 10 | Hillcrest | 4.16kV | AH14 | Isolated transformer OTT 593 at 529 Briawood to replace the pole | Ottawa | Scheduled Outage | Construction
14203 | 2009 | 4 | 23 | 0.45833 |  | 50 | 3 | 4 | Hillcrest | 4.16kV | AH14 | Isolated transformer X31832 at 586 Edison Ave to install new pole | Ottawa | Scheduled Outage | Construction
14281 | 2009 | 5 | 1 | 0.43403 |  | 100 | 8 | 5 | Hillcrest | 4.16kV | AH14 | Transformer #X31831 located at 610 Edison isolated for clearance | Ottawa | Scheduled Outage | Preventive Maintenance
8348 | 2006 | 5 | 24 | 0.52083 |  | 105 | 18 | 10 | Hillcrest | 4.16kV | AH14 | Glen Carswell had transformer off at 529 Briarwood to change a pole and transformer. | Ottawa | Scheduled Outage | Emergency Services Request
12579 | 2008 | 6 | 9 | 0.36458 |  | 30 | 3 | 6 | Hillcrest | 4.16kV | AH14 | Transformer #X35479 located at 618 Melbourne isolated to run in new service for a service upgrade. PC10C#7861 placed. | Ottawa | Scheduled Outage | Preventive Maintenance
14547 | 2009 | 6 | 16 | 0.57292 |  | 60 | 5 | 5 | Hillcrest | 4.16kV | AH14 | Transformer #X31829 located at 630 Edison isolated due to a pole change | Ottawa | Scheduled Outage | Construction
14549 | 2009 | 6 | 16 | 0.61528 |  | 84 | 7 | 5 | Hillcrest | 4.16kV | AH14 | Transformer #X31830 located at 612 Edison Ave isolated for a pole change | Ottawa | Scheduled Outage | Construction
12836 | 2008 | 7 | 14 | 0.41528 |  | 175 | 9 | 3 | Hillcrest | 4.16kV | AH14 | At 09:58 trans at 519 Edison Ave was isolated in order to replace a pole | Ottawa | Scheduled Outage | Preventive Maintenance
12907 | 2008 | 7 | 21 | 0.375 |  | 190 | 25 | 8 | Hillcrest | 4.16kV | AH14 | Transformer #X31835 located at 531 Edison Ave isolated for a pole change | Ottawa | Scheduled Outage | Preventive Maintenance
12909 | 2008 | 7 | 21 | 0.54861 |  | 115 | 17 | 9 | Hillcrest | 13.2kV | AH14 | Transformer #X31844 located at 508 Melbourne isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
14883 | 2009 | 7 | 30 | 0.375 |  | 120 | 10 | 5 | Hillcrest | 4.16kV | AH14 | Isolated transformer X31830 at 616 Edison Ave to replace pole | Ottawa | Scheduled Outage | Construction
14986 | 2009 | 8 | 21 | 0.38542 |  | 100 | 8 | 5 | Hillcrest | 4.16kV | AH14 | Transformer #X31830 located at 612 Edison isolated for a pole change | Ottawa | Scheduled Outage | Construction
15235 | 2009 | 10 | 8 | 0.39583 |  | 180 | 33 | 11 | Hillcrest | 4.16kV | AH14 | Transformer #X31834 located at 551 Edison Ave isolated for pole replacement | Ottawa | Scheduled Outage | Construction
11490 | 2007 | 10 | 10 | 0.35417 |  | 105 | 12 | 7 | Hillcrest | 4.16kV | AH14 | At 08:30 trans at 540 Edison was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11492 | 2007 | 10 | 10 | 0.4375 |  | 135 | 18 | 8 | Hillcrest | 4.16kV | AH14 | At 10:30 trans at 578 Edison Ave was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11494 | 2007 | 10 | 10 | 0.54167 |  | 100 | 13 | 8 | Hillcrest | 4.16kV | AH14 | At 13:00 trans at 630 Edison was isolated in order to replace as PCB trans | Ottawa | Scheduled Outage | Preventive Maintenance
11582 | 2007 | 10 | 24 | 0.53472 |  | 109 | 9 | 5 | HILLCREST | 4.16kV | AH14 | Transformer #X32033 at 507 Brierwood isolated to allow for PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
15315 | 2009 | 10 | 27 | 0.39583 |  | 150 | 25 | 10 | Hillcrest | 4.16kV | AH14 | at 09:30 trans at 582 EDISON AVE OTTAWA was isolated in order to replace a pole | Ottawa | Scheduled Outage | Preventive Maintenance
15326 | 2009 | 10 | 29 | 0.41319 |  | 120 | 10 | 5 | Hillcrest | 4.16kV | AH14 | Transformer #X31831 located at 604 Edison Ave isolated for a pole change | Ottawa | Scheduled Outage | Construction
15327 | 2009 | 10 | 29 | 0.48542 |  | 16 | 2 | 8 | Hillcrest | 4.16kV | AH14 | Transformer #X31833 located at 574 Edison isolated for a pole change. | Ottawa | Scheduled Outage | Construction
11752 | 2007 | 11 | 22 | 0.48264 |  | 30 | 2 | 5 | Hillcrest | 4.16kV | AH14 | Isolated transformer OTT2130 at 468 Edison Ave for a service transfer | Ottawa | Scheduled Outage | Emergency Services Request
7714 | 2005 | 12 | 12 | 0.375 |  | 240 | 56 | 14 | hillcrest | 4.16kV | AH14 | @ 528 Danforth Tony Taylor did a pole change. | Ottawa | Scheduled Outage | Repair
9942 | 2007 | 1 | 18 | 0.39583 |  | 175 | 64 | 22 | Playfair | 4.16kV | AJ03 | Transformer #OTT2338 located at 1846 Sharel isolated due to transferring plant | Ottawa | Scheduled Outage | Construction
10151 | 2007 | 3 | 20 | 0.50972 |  | 126 | 13 | 6 | Playfair | 4.16kV | AJ03 | Isolated and replaced transformer OTT3354 at 1912 Illinois Ave | Ottawa | Scheduled Outage | Preventive Maintenance
8082 | 2006 | 3 | 30 | 0.51389 |  | 30 | 4 | 9 | ALBION | 13.2kV | AJ03 | Isolated transformer OTT 4849 at 2363 Palm St to make repairs to overhead service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20345 | 2012 | 4 | 18 | 0.42014 |  | 158 | 61 | 23 | Playfair | 4.16kV | AJ03 | AJ03 blue phase section on Louisiana was isolated to allow crew to replace a pole in the rear of 1846 Louisiana. | Ottawa | Scheduled Outage | Construction
14265 | 2009 | 4 | 30 | 0.39236 |  | 139 | 23 | 10 | Playfair | 4.16kV | AJ03 | Transformer #X21660 located at 1872 Featherston Dr isolated to relocate transformer on pole | Ottawa | Scheduled Outage | Preventive Maintenance
14279 | 2009 | 5 | 1 | 0.38889 |  | 40 | 3 | 4 | Playfair | 4.16kV | AJ03 | Transformer #X26989 located at 2328 Atwater isolated for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
14343 | 2009 | 5 | 11 | 0.44792 |  | 218 | 36 | 10 | PLAYFAIR | 4.16kV | AJ03 | transformer X21660 at 1884 Featherston isolated to allow for pole change | Ottawa | Scheduled Outage | Construction
12584 | 2008 | 6 | 9 | 0.96181 |  | 22 | 6 | 16 | Playfair | 4.16kV | AJ03 | Isolated transformer K609 at the rear of 2278 Bowman Rd to repair one leg of the secondary service feeding 609P1 and 609P2 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10660 | 2007 | 6 | 19 | 0.37292 |  | 183 | 12 | 4 | Playfair | 4.16kV | AJ03 | Transformer located at 1887 Featherston isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
12760 | 2008 | 6 | 27 | 0.66667 |  | 35 | 5 | 9 | Playfair | 4.16kV | AJ03 | Isolated transformer X29068 at 2367 Palm St to replace triplex service | Ottawa | Scheduled Outage | Emergency Services Request
3669 | 2003 | 7 | 3 | 0.72847 |  | 61 | 12 | 12 | Playfair | 4.16kV | AJ03 | Switch at 611 broken. Transformers 609 and 611 affected. | Ottawa | Defective Equipment
8724 | 2006 | 7 | 14 | 0.40278 |  | 85 | 3 | 2 | Playfair | 4.16kV | AJ03 | Dean Leduc opened transformeer OTT5524 at 1225 Kilborn to allow an electrician to do emergency repairs | Ottawa | Scheduled Outage | Repair
14759 | 2009 | 7 | 15 | 0.38542 |  | 342 | 228 | 40 | Playfair | 4.16kV | AJ03 | AJ03 O/H section between S13267 & TEMP52 isolated to transfer conductor to new poles. | Ottawa | Scheduled Outage | Construction
14791 | 2009 | 7 | 20 | 0.375 |  | 258 | 26 | 6 | Playfair | 4.16kV | AJ03 | Transformer #X26985 located at 2339 Jefferson isolated to transfer plant to new poles. | Ottawa | Scheduled Outage | Construction
18785 | 2011 | 7 | 20 | 0.95139 |  | 22 | 3 | 8 | Playfair | 4.16kV | AJ03 | Trans X26988 at 1915 Featherston Dr was isolated in order to repair a secondary lead | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
18833 | 2011 | 7 | 26 | 0.73264 |  | 30 | 4 | 8 | Playfair | 4.16kV | AJ03 | Transformer #X26988 located at 1910 Sharel opened by crew to change triplex service | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11044 | 2007 | 8 | 14 | 0.29167 |  | 30 | 2 | 5 | Plasyfair | 4.16kV | AJ03 | At 07:00 trans OTT2516 at 1897 Florida Ave was isolated in order to replace the trans cutout | Ottawa | Scheduled Outage | Repair
15004 | 2009 | 8 | 25 | 0.59722 |  | 49 | 7 | 8 | PLAYFAIR | 4.16kV | AJ03 | Transformer X26988 at rear of 1915 Featherston isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
7257 | 2005 | 8 | 31 | 0.85764 |  | 51 | 6 | 7 | Playfair | 4.16kV | AJ03 | Transformer #OTT4022 located at 1903 Illinois Ave isolated due to a defective switch at the transformer | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15113 | 2009 | 9 | 17 | 0.44792 |  | 12 | 5 | 25 | Playfair | 4.16kV | AJ03 | Transformer #K387 located at 1773 Heron Rd isolated for an Arrears diconnect | Ottawa | Scheduled Outage | Construction
7669 | 2005 | 11 | 30 | 0.50694 |  | 30 | 3 | 6 | Playfair | 4.16kV | AJ03 | At 12:10 trans OTT2514 isolated to replace trans switch | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9845 | 2006 | 12 | 15 | 0.41667 |  | 120 | 16 | 8 | Playfair | 4.16kV | AJ03 | Mark Rushton isolated transformer at 1846 Sharel to replace Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
4645 | 2003 | 12 | 22 | 0.31667 |  | 84 | 7 | 5 | Playfair | 4.16kV | AJ03 | Ott 267 at 2327 Atwater St blown fuse found. | Ottawa | Defective Equipment
6159 | 2005 | 1 | 31 | 0.47222 |  | 45 | 6 | 8 | Playfair | 4.16kV | AJ04 | K601 isolated tor pole change at 2088 Delmar | Ottawa | Scheduled Outage | Repair
20216 | 2012 | 3 | 24 | 0.11806 |  | 25 | 4 | 9 | Playfair | 4.16kV | AJ04 | K608 at 2020 Thistle was opened to re-connect repaired U/G service. 9 customers affected for 25 min. Playfair AJ04. ID#20216. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6340 | 2005 | 3 | 30 | 0.54514 |  | 60 | 11 | 11 | Playfair | 4.16kV | AJ04 | Isolated Transformer # K601 at 1855 Beattie to install cable | Ottawa | Scheduled Outage | Construction
12300 | 2008 | 4 | 17 | 0.37361 |  | 199 | 33 | 10 | PLAYFAIR | 4.16kV | AJ04 | Transformer at Pleasant Park & Delmar Dr isolated for maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
18056 | 2011 | 4 | 29 | 0.61042 |  | 137 | 543 | 238 | Playfair | 4.16kV | AJ04 | AJ04 O/H circuit was isolated to allow the crew to remove a tree of the primary and reconnect the primary. | Ottawa | Tree Contacts | Tree Fallen
18197 | 2011 | 5 | 21 | 0.25 |  | 606 | 178 | 18 | Playfair | 4.16kV | AJ04 | defective blue phase cable between K603 and K608 on Thistle cresent caused AJ04 overhead fuse to blow, interrupting customers on Thistle and one on Beattie. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20598 | 2012 | 5 | 25 | 0.89861 |  | 1834 | 520 | 17 | Playfair | 4.16kV | AJ04 | Downed AJ04W phase at 1796 Devlin caused due to a tree falling. Crew used live line cutters to isolate circuit. Tree removed and circuit restored. | Ottawa | Adverse Weather | Wind
10510 | 2007 | 6 | 1 | 0.53472 |  | 100 | 20 | 12 | Playfair | 4.16kV | AJ04 | Transformer #OTT1871 located at 2141 Delmar isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
20712 | 2012 | 6 | 7 | 0.40139 |  | 332 | 94 | 17 | Playfair | 4.16kV | AJ04 | 2 transformers on Devlin were isolated to replace a broken pole at the rear of 1860 Devlin | Ottawa | Scheduled Outage | Repair
10883 | 2007 | 7 | 16 | 0.55208 |  | 55 | 3 | 3 | Playfair | 4.16kV | AJ04 | At 13:15 trans at 2145 Beaumont was isolated in order to replace a defective sec service | Ottawa | Scheduled Outage | Repair
8969 | 2006 | 8 | 15 | 0.39583 |  | 130 | 26 | 12 | Playfair | 4.16kV | AJ04 | Transformer #OTT1888 located at 1833 Devlin isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
19117 | 2011 | 9 | 8 | 0.4375 |  | 37 | 7 | 12 | Playfiar | 4.16kV | AJ04 | Trans at 1865 Devlin Cres was isolated in order to remove vines from a pole | Ottawa | Tree Contacts | Tree Fallen
9220 | 2006 | 9 | 14 | 0.67014 |  | 15 | 2 | 9 | Playfair | 4.16kV | AJ04 | Transformer #K00602 located at 1829 Beattie isolated to hook up service, crew was having difficulties. | Ottawa | Scheduled Outage | Construction
11738 | 2007 | 11 | 19 | 0.38889 |  | 115 | 19 | 10 | Kilborn | 4.16kV | AJ04 | Isolated and replaced trtansformer K605 at 2101 Thistle Cres (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
20273 | 2012 | 4 | 3 | 0.52083 |  | 120 | 22 | 11 | Playfair | 4.16kV | AJ05 | Isolated transformer X26812 at the rear of 1956 Sharel Dr to re-energize one span of primary | Ottawa | Scheduled Outage | Construction
18164 | 2011 | 5 | 16 | 0.35417 |  | 60 | 6 | 6 | Playfair | 4.16kV | AJ05 | Tim Vallee isolated trans X37968 at 765 Dunrobin Rd for service upgrade | Gloucester | Scheduled Outage | Repair
10455 | 2007 | 5 | 24 | 0.41667 |  | 125 | 27 | 13 | Playfair | 4.16kV | AJ05 | At 10:00 trans at 2193 Fife Cres was isolated in order to replace a line pole | Ottawa | Scheduled Outage | Repair
10470 | 2007 | 5 | 28 | 0.41667 |  | 140 | 19 | 8 | Playfair | 4.16kV | AJ05 | Transformer #OTT2395 located at 2193 Fife isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10473 | 2007 | 5 | 29 | 0.38889 |  | 150 | 10 | 4 | Playfair | 4.16kV | AJ05 | Transformer #OTT2398 located at 804 Flemming isolated due to pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
10481 | 2007 | 5 | 30 | 0.36042 |  | 171 | 17 | 6 | PLAYFAIR | 4.16kV | AJ05 | Transformer #OTT3268 at 757 Fleming isolated to allow for PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10720 | 2007 | 6 | 24 | 0.65694 |  | 166 | 394 | 289 | Playfair | 4.16kV | AJ05 | One phase of the AJ05 in the back yard of Fife Cr found broken. AJ05 feeder isolated to complete repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5390 | 2004 | 6 | 28 | 0.49236 |  | 9 | 45 | 300 | AJ | 4.16kV | AJ05 | AJ05 acb opened via scada at request of J Magee to remove large tree branch from 3 phase primary. Canterbury/Fife area, | Ottawa | Tree Contacts | Tree Limb Fallen
16355 | 2010 | 6 | 28 | 0.80556 |  | 263 | 166 | 284 | Playfair | 4.16kV | AJ05 | AJ05 circuit on Kilborn west of Haig bklue and white phases touched and caused a flash that burned down both phases, emergency switching to restore load required AJ05 breaker to be open momentarily | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18781 | 2011 | 7 | 20 | 0.51042 |  | 25 | 2 | 6 | AJ05 | 4.16kV | AJ05 | Transformer #X26789 located at 2211 Urbandale opened by crew to remove branch from primary | Ottawa | Adverse Weather | Tree Limb Fallen
16669 | 2010 | 8 | 5 | 0.17639 |  | 875 | 1222 | 284 | Kilborn | 4.16kV | AJ05 | Primary O/h down in the Canteberry/Kilborn area, the AJ05 breaker was open for the crew to reinstall the O/H. | Ottawa | Adverse Weather | Rain
13372 | 2008 | 10 | 15 | 0.83333 |  | 20 | 1 | 3 | Playfair | 4.16kV | AJ05 | At 20:00 trans at 2194 Urbandale was isolated ini order to repair defective LLC | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19694 | 2011 | 12 | 6 | 0.72639 |  | 62 | 101 | 98 | Playfair | 4.16kV | AJ05 | AJ05 blue phase outage which was transferred to AE04 circuit. At S21899 Blue fuse found blown. Fuse was replaced and closed restoring all load. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9810 | 2006 | 12 | 8 | 0.375 |  | 75 | 5 | 4 | Playfair | 4.16kV | AJ05 | Isolated and replaced transformer OTT2931 at 2190 Haig Dr (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
17511 | 2011 | 1 | 23 | 0.76458 |  | 157 | 21 | 8 | Playfair | 4.16kV | AJ06 | Crew replaced fuse at 4kv transformer M1 at 20 Roseglen. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
4942 | 2004 | 3 | 28 | 0.63889 |  | 70 | 8 | 7 | Playfair | 4.16kV | AJ06 | Transformer #3590 at 1778 Kilborn interrupted to repair service connections. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12295 | 2008 | 4 | 17 | 0.39931 |  | 130 | 30 | 14 | Playfair | 4.16kV | AJ06 | At 9:35am AJ06 blue phase overhead circuit from Temp103 to end of line on Dunkirk was isolated to allow Ashplund to clear trees. ID#12295 | Ottawa | Scheduled Outage | Preventive Maintenance
20473 | 2012 | 5 | 7 | 0.46319 |  | 50 | 5 | 6 | Bayswater | 4.16kV | AJ06 | At 11:07, transformer X26935 was isolated to allow crews to adjust secondary. 6 customers affected for 50 minutes. Bayswater (AJ06) ID #20473 | Ottawa | Scheduled Outage
18868 | 2011 | 7 | 31 | 0.98542 |  | 86 | 11 | 8 | Playfair | 4.16kV | AJ06 | Animal contact caused the cut out to blow on transformer X27226. Playfair (AJ06) ID#18868 | Ottawa | Foreign Interference | Animal
8987 | 2006 | 8 | 16 | 0.58333 |  | 60 | 5 | 5 | Playfair | 4.16kV | AJ07 | Transformer #OTT2344 located at 2082 Featherston isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
13190 | 2008 | 9 | 4 | 0.3875 |  | 112 | 17 | 9 | PLAYFAIR | 4.16kV | AJ07 | Transformer X29073 at 1945 Connecticut isolated to allow for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
13248 | 2008 | 9 | 16 | 0.375 |  | 120 | 12 | 6 | Playfair | 4.16kV | AJ07 | Isolated transformer X29074 at 1934 Featherston Dr to replace pole | Ottawa | Scheduled Outage | Construction
4693 | 2004 | 1 | 12 | 0.022917 |  | 75 | 16 | 13 | Fisher | 4.16kV | AK02 | The cutout fuse to K259 came apart. Refused and power restored to 13 customers on Lexington | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4711 | 2004 | 1 | 17 | 0.91597 |  | 84 | 18 | 13 | Fisher | 4.16kV | AK02 | Cable between K259 & K260 was determined to be defective. Dip fuse replaced & all customers restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9941 | 2007 | 1 | 18 | 0.36458 |  | 175 | 35 | 12 | Fisher | 4.16kV | AK02 | At 08:45 trans OTT3956 at 1417 Lexington St was isolated in order to replace defective transformer | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4719 | 2004 | 1 | 22 | 0.0076389 |  | 69 | 8 | 7 | Fisher | 4.16kV | AK02 | AK02 white phase fuse to cable feeding K259 at 1470 Lexington blew, cable between K259 and K260 was isolated at the time. ID # 4719 | Ottawa | Unknown/Other | No Apparent Cause
4721 | 2004 | 1 | 23 | 0.47222 |  | 110 | 24 | 13 | Fisher | 4.16kV | AK02 | K259 at 1470 Lexington isolated to replace defective insulator. | Ottawa | Scheduled Outage | Repair
16153 | 2010 | 5 | 27 | 0.38542 |  | 30 | 5 | 10 | Fisher | 4.16kV | AK02 | Transformer #X33540 located at 170 Wilshire Ave opened by crew for a service upgrade | Ottawa | Scheduled Outage | Construction
8553 | 2006 | 6 | 20 | 0.47431 |  | 20 | 3 | 10 | Fisher | 4.16kV | AK02 | Transformer #OTT4592 located at 1383 Morley isolated to re-sag neutral on open wire secondary service | Ottawa | Adverse Weather | Wind
14627 | 2009 | 6 | 27 | 0.038194 |  | 45 | 8 | 11 | Fisher | 4.16kV | AK02 | Crew opened Tx 33551 at 1421 Lexington opened to replace service to 1421 Lexington. | Ottawa | Tree Contacts | Inadequate Trimming
16546 | 2010 | 7 | 23 | 0.36111 |  | 20 | 2 | 6 | Fisher | 4.16kV | AK02 | Transformer #X31358 located at 1348 Lexington opened by crew for a service upgrade | Ottawa | Scheduled Outage | Construction
11028 | 2007 | 8 | 9 | 0.58333 |  | 55 | 12 | 13 | Fisher | 4.16kV | AK02 | At 14:00 trans K259 at 1470 Lexington Ave was isolated in order for a pcb trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
16907 | 2010 | 9 | 8 | 0.64931 |  | 55 | 4 | 4 | FISHER | 4.16kV | AK02 | Transformer X33554 at 199 Sanford Ave isolated to pull up a new service | Ottawa | Scheduled Outage | Construction
7352 | 2005 | 9 | 20 | 0.44097 |  | 60 | 5 | 5 | Fisher | 4.16kV | AK02 | Transformer OTT3303 at 216 Hudson Ave was isolated to replace service's | Ottawa | Scheduled Outage | Preventive Maintenance
13470 | 2008 | 10 | 29 | 0.23125 |  | 194 | 728 | 225 | FISHER | 4.16kV | AK02 | 7:00AM - Jason Walkden reports tree down and primary single phase down at 1272 Prince of Wales. 8:46AM - Denis Martin placed PC10A#0115 into affect for isolation of red phase primary line between Prince of Wales & Morley. 8:47AM - Breaker closed by system and holding. | Ottawa | Adverse Weather
13527 | 2008 | 10 | 29 | 0.23125 |  | 222 | 382 | 122 | Fisher | 4.16kV | AK02 | Tree fell on primary in the rear of Morley and Prince of Wales causing AK02 cct, to open. Circuit isolated to make repairs. | Ottawa | Tree Contacts | Tree Fallen
13536 | 2008 | 10 | 30 | 0.43889 |  | 76 | 5 | 4 | FISHER |  | AK02 | Transformer #X33543 at 212 Wilshire Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
7608 | 2005 | 11 | 14 | 0.50556 |  | 17 | 1 | 4 | Fisher | 4.16kV | AK02 | Transformer #OTT5662 located at 200 Wilshire isolated for Asplundh to remove a tree | Ottawa | Tree Contacts | Tree Fallen
19620 | 2011 | 11 | 22 | 0.59722 |  | 60 | 4 | 4 | Fisher | 27.6/16kV | AK02 | Isolated and replaced transformer X31356 at 1079 Arnot Rd | Ottawa | Scheduled Outage | Preventive Maintenance
11767 | 2007 | 11 | 26 | 0.38542 |  | 115 | 10 | 5 | Fisher | 4.16kV | AK02 | Transformer #X33515 located at 210 Hudson isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
4702 | 2004 | 1 | 15 | 0.49514 |  | 52 | 6 | 7 | Fisher | 4.16kV | AK03 | Transformer was opened at 1760 Ortona to effect repairs to hydro pole. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
4716 | 2004 | 1 | 20 | 0.51875 |  | 93 | 11 | 7 | FISHER | 4.16kV | AK03 | TRANSFORMER # 4796 ISOLATED TO ALLOW CREW TO TRANSFER PLANT. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17644 | 2011 | 2 | 25 | 0.41667 |  | 60 | 2 | 2 | Fisher | 4.16kV | AK03 | At 10:00 crews isolated transformer X09936 at 7 Farm Gate Cres to installed a new pole. 2 customers were affected for 60 mins. Fisher AK02 ID# 17644 | Ottawa | Scheduled Outage | Construction
17662 | 2011 | 3 | 2 | 0.38194 |  | 110 | 13 | 7 | Fisher | 4.16kV | AK03 | Transformer #X09933 located at 1759 Fisher isolated by crew to replace insulators on the pole | Ottawa | Scheduled Outage | Construction
6631 | 2005 | 6 | 1 | 0.69583 |  | 2 | 8 | 247 | Fisher | 13.2kV | AK03 | lightning activity caused AK03 circuit to open. Circuit also caused TM1AK to open. When TM1AK which feeds AKT1 bank was picked up AK03 circuit showed reclosed. AK03 was probably an auto-reclose. | Ottawa | Adverse Weather
6916 | 2005 | 7 | 13 | 0.57292 |  | 58 | 9 | 9 | Fisher | 4.16kV | AK03 | Trans OTT2454 isolated at 1640 Fisher in order to inspect suspect damaged line hardware | Ottawa | Scheduled Outage | Preventive Maintenance
10982 | 2007 | 8 | 1 | 0.36944 |  | 124 | 19 | 9 | Fisher | 4.16kV | AK03 | Transformer #OTT4706 located at 1396 Normandy isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
7087 | 2005 | 8 | 9 | 0.39583 |  | 240 | 36 | 9 | Fisher | 4.16kV | AK03 | Trans OTT2454 @ 1640 Fisher Ave isolated for pole replacement | Ottawa | Scheduled Outage | Repair
16717 | 2010 | 8 | 11 | 0.70625 |  | 506 | 8 | 1 | Fisher | 13.2kV | AK03 | dump truck pulled down wires at 1763 Fisher, W/O 67119 - DTP completed - service to 1763 Fisher - s/p is ok but wires got pulled very hard - also needs to fix point of attachment - disconnected at s/p & broke at the road | Ottawa | Foreign Interference | Vehicle
4146 | 2003 | 9 | 24 | 0.55903 |  | 32 | 1 | 2 | AK | 4.16kV | AK03 | Tx OTT2304 @ 1080 Falaise was opened to repair Tx connections affecting 1080 & 1064 Falaise. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11594 | 2007 | 10 | 25 | 0.69167 |  | 45 | 8 | 10 | FISHER | 4.16kV | AK03 | Transformer #31448 at 1674 Fisher isolated to replace hotline clamp | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4458 | 2003 | 11 | 14 | 0.57778 |  | 101 | 72 | 43 | Fisher | 4.16kV | AK03 | Two fuses blown on AK03, circuit patrolled but no problem found. Circuit re-fused successfully restoring power to all affected customers. | Ottawa | Unknown/Other | No Apparent Cause
11707 | 2007 | 11 | 15 | 0.35764 |  | 65 | 9 | 8 | Fisher | 4.16kV | AK03 | Transformer #K323 located at 40 Appleby Pvt isolated due to smart meter installations | Ottawa | Scheduled Outage | Preventive Maintenance
11709 | 2007 | 11 | 15 | 0.40625 |  | 20 | 2 | 7 | Fisher | 4.16kV | AK03 | Transformer #K324 located at 33 Georgian Pvt isolated due to smart meter installations | Ottawa | Scheduled Outage | Preventive Maintenance
11710 | 2007 | 11 | 15 | 0.42014 |  | 40 | 6 | 9 | Fisher | 4.16kV | AK03 | Transformer #K322 located at 59 Appleby Pvt isolated due to smart meter installations | Ottawa | Scheduled Outage | Preventive Maintenance
11711 | 2007 | 11 | 15 | 0.45139 |  | 40 | 7 | 10 | Fisher | 4.16kV | AK03 | Transformer #K325 located at 1075 Borden Side isolated due to smart meter installations | Ottawa | Scheduled Outage | Preventive Maintenance
11712 | 2007 | 11 | 15 | 0.50694 |  | 25 | 5 | 11 | Fisher | 4.16kV | AK03 | Transformer #K320 located at 8 Moorside isolated due to smart meter installations | Ottawa | Scheduled Outage | Preventive Maintenance
11713 | 2007 | 11 | 15 | 0.45139 |  | 105 | 16 | 9 | Ottawa | 4.16kV | AK03 | Transformer #K321 located at 17 Moorside isolated due to smart meter change | Ottawa | Scheduled Outage
11715 | 2007 | 11 | 15 | 0.52778 |  | 35 | 7 | 12 | Fisher | 4.16kV | AK03 | Transformer#K319 located at 80 Appleby isolated due to smart meter installations | Ottawa | Scheduled Outage | Preventive Maintenance
11716 | 2007 | 11 | 15 | 0.55208 |  | 45 | 9 | 12 | Fisher | 4.16kV | AK03 | Transformer #K318 located at 94 Appleby isolated due to smart meter installations | Ottawa | Scheduled Outage | Preventive Maintenance
11919 | 2008 | 1 | 9 | 0.77917 |  | 2 | 7 | 201 | Fisher | 4.16kV | AK04 | Overhead circuit found on ground burning severely. Last span on white phase before dead end in back yard of Dynes and Eiffel. No customers fed off of the section of overhead. Bob Rolland requested momentary outage on the AK04 circuit to cut free burning conductor on ground. Phil Lucas (On Call Supervisor) gave ok to have momentary outage. AK04 Breaker opened. AK04 White phase, last span section that was on the ground burning was cut away and AK04 circuit brought back online. All load restored to customers, 2 min outage. Bob Rolland will apply to have the service repairs done to White Phase last span overhead circuit on the AK04 tommorow. | Ottawa | Scheduled Outage | Emergency Services Request
17479 | 2011 | 1 | 11 | 0.65347 |  | 17 | 10 | 34 | Fisher | 4.16kV | AK04 | Transformer X31757 at 1431 Claymor Ave isolated to do temporary repairs to triplex | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17483 | 2011 | 1 | 12 | 0.5 |  | 30 | 17 | 34 | Fisher | 4.16kV | AK04 | Isolated transformer X31757 at 1435 Claymor Ave to replace service | Ottawa | Scheduled Outage | Emergency Services Request
4725 | 2004 | 1 | 23 | 0.75208 |  | 31 | 10 | 19 | AK | 4.16kV | AK04 | K284 @ 901 Greenbriar opend to repair defective connection at pedestal. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7926 | 2006 | 2 | 17 | 0.48889 |  | 244 | 854 | 210 | Fisher | 4.16kV | AK04 | opened for isolation Wires down at Prince of Wales and Dynes | Ottawa | Adverse Weather | Wind
17810 | 2011 | 3 | 31 | 0.40625 |  | 124 | 17 | 8 | Fisher | 4.16kV | AK04 | Transformer #X31622 located at 1386 Claymor Ave opened by crew for a PCB change | Ottawa | Scheduled Outage | Construction
6364 | 2005 | 4 | 4 | 0.35417 |  | 28 | 28 | 60 | Fisher | 4.16kV | AK04 | Isolated Transformer # K276 at 955 Debra to repair secondary | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8159 | 2006 | 4 | 19 | 0.017361 |  | 20 | 4 | 12 | Fisher | 4.16kV | AK04 | Transformer K979 opened for clearance to pedestal 979P2, defective underground service at 505 Courtland. Temporary ran from 503 Courtland. | Ottawa | Defective Equipment
3444 | 2003 | 5 | 14 | 0.56667 |  | 64 | 21 | 20 | Fisher | 4.16kV | AK04 | Planned Interruption to repair U/G cable @ Transformer K280 on Meadowlands Drive. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3446 | 2003 | 5 | 15 | 0.6875 |  | 13 | 4 | 20 | Fisher | 4.16kV | AK04 | Transformer K280 at 949 Meadowlands was opened to reconnect service affecting 20 customers. | Ottawa | Scheduled Outage | Repair
8360 | 2006 | 5 | 26 | 0.95139 |  | 50 | 7 | 8 | Fisher | 4.16kV | AK04 | Transformer #K973 located at 1325 Ambridge Way isolated to run a temporary from 1327 due to defective U/G cable | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8404 | 2006 | 6 | 1 | 0.57917 |  | 51 | 7 | 8 | Fisher | 4.16kV | AK04 | Isolated transformer # k973 @ 671 Malibu Terrace to repair u/g service. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6699 | 2005 | 6 | 12 | 0.47917 |  | 15 | 6 | 23 | AK | 4.16kV | AK04 | Dip to K975 was opened to repair a burning hot line clamp. K975 & K978 were off affecting Malibu terrace & Courtland place. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3578 | 2003 | 6 | 18 | 0.37153 |  | 122 | 132 | 65 | Fisher | 4.16kV | AK04 | Four kiosks K274, K275, K278 & K280 were interrupted for ongoing cable replacement on Debra St. | Ottawa | Scheduled Outage | Preventive Maintenance
10745 | 2007 | 6 | 27 | 0.375 |  | 156 | 26 | 10 | Fisher | 4.16kV | AK04 | Interrupted transformer K00974 at 687 Malibu Terrace for a service upgrade. | Ottawa | Scheduled Outage | Preventive Maintenance
10829 | 2007 | 7 | 9 | 0.6875 |  | 50 | 3 | 4 | Fisher | 4.16kV | AK04 | Switch to transformer OTT2445 at 1386 Fisher Ave was found broken crew replaced switch and restored power | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6966 | 2005 | 7 | 16 | 0.51181 |  | 193 | 103 | 32 | Fisher | 4.16kV | AK04 | Replaced broken switch for transformer OTT1492 at 986 Eiffel Ave | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10971 | 2007 | 7 | 31 | 0.375 |  | 105 | 9 | 5 | FISHER | 4.16kV | AK04 | Transformer #OTT1500 at 1470 Claymor isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
9193 | 2006 | 9 | 11 | 0.4375 |  | 77 | 21 | 16 | Fisher | 4.16kV | AK04 | At 13:30 trans OTT18693 at 977 Meadowlands Dr was isolated in order to relocate secondary service | Ottawa | Scheduled Outage | Preventive Maintenance
13250 | 2008 | 9 | 16 | 0.80208 |  | 183 | 18 | 6 | Fisher | 4.16kV | AK04 | At 19:15 trans at 1306 Baseline Rd was isolated for trans removals and replacement |  | Scheduled Outage | Preventive Maintenance
11717 | 2007 | 11 | 15 | 0.39583 |  | 90 | 54 | 36 | Fisher | 4.16kV | AK04 | Transformer #K265 located at 939 Eiffel isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
5906 | 2004 | 11 | 19 | 0.76042 |  | 55 | 24 | 26 | AK | 4.16kV | AK04 | K276 @ 955 Debra ave was opened to install temp U/G feed. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13701 | 2008 | 12 | 4 | 0.8125 |  | 23 | 3 | 8 | FISHER | 4.16kV | AK04 | Transf X31622 at 1386 Claymore isolated to change connection on streetlight & traffic light feed | Ottawa | Scheduled Outage | Repair
11828 | 2007 | 12 | 11 | 0.39931 |  | 70 | 22 | 19 | Fisher | 4.16kV | AK04 | Isolated transformer X31755 at the rear of 967 Eiffel Ave to relocate hydro plant | Ottawa | Scheduled Outage | Preventive Maintenance
9890 | 2006 | 12 | 28 | 0.72222 |  | 140 | 163 | 70 | Fisher | 4.16kV | AK04 | loose and sparking connection on Dynes east of Prince of Wales required emergency repairs with part of AK04 overhead isolated on Belamy, Eiffel and Claymour | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5985 | 2004 | 12 | 5 | 0.75208 |  | 42 | 6 | 9 | AK | 4.16kV | AK04- | fused cut out to transformer feeding 1420 to 1432 Fisher replaced. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15623 | 2010 | 1 | 7 | 0.38194 |  | 30 | 2 | 4 | Fisher | 4.16kV | AK05 | Transformer #X33565 located at 1554 Minaki Ave isolated to install new service | Ottawa | Scheduled Outage | Construction
9960 | 2007 | 1 | 23 | 0.41806 |  | 98 | 16 | 10 | Fisher | 4.16kV | AK05 | At 10:02 trans OTT5126 at 1754 Prince of Wales Dr was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Repair
17534 | 2011 | 1 | 28 | 0.4375 |  | 90 | 12 | 8 | Fisher | 4.16kV | AK05 | Trans at 850 BASELINE RD OTT was isolated in order to replace a pole | Ottawa | Scheduled Outage | Preventive Maintenance
4768 | 2004 | 2 | 6 | 0.84028 |  | 90 | 22 | 15 | Fisher | 4.16kV | AK05 | Made repairs to underground service at Kiosk 00261at rear of 1542 Lexington. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7927 | 2006 | 2 | 17 | 0.48889 |  | 244 | 1004 | 247 | Fisher | 4.16kV | AK05 | opened for isolation Wires down at Prince of Wales and Dynes | Ottawa | Adverse Weather | Wind
4840 | 2004 | 2 | 29 | 0.59931 |  | 44 | 1 | 1 | Fisher | 4.16kV | AK05 | A broken switch was reported by one of our employees at Prince of Wales & Hogs Back. The crew opened at P89 and replaced the 3 cutouts at dip pole to P89. Th bridge & Lock Masters house at Hogs Back was affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8047 | 2006 | 3 | 20 | 0.42569 |  | 137 | 18 | 8 | Fisher | 4.16kV | AK05 | Transformer located at 1270 Lampman isolated due to changing to new pole | Ottawa | Scheduled Outage | Construction
20230 | 2012 | 3 | 26 | 0.40972 |  | 191 | 646 | 203 | Fisher | 4.16kV | AK05 | The AK05 circuit was isolated to allow for clearance on the SC2101 circuit to allow the crews repair broken insulators in the Princess of Whales area | Ottawa | Adverse Weather | Wind
8186 | 2006 | 4 | 25 | 0.45833 |  | 55 | 11 | 12 | Fisher | 4.16kV | AK05 | At 11:00 K979 was islolated for repairs to U/G service 12 custs affected . | Ottawa | Scheduled Outage | Repair
20494 | 2012 | 5 | 10 | 0.53542 |  | 13 | 44 | 204 | Fisher | 4.16kV | AK05 | MVA at 1700 Prince of Wales Dr reported by Fire Department Pete Barr requested AK05 and AK07 breaker opened. Police report # 12-133266 | Ottawa | Foreign Interference | Vehicle
8386 | 2006 | 5 | 31 | 0.39583 |  | 55 | 1 | 1 | Fisher | 4.16kV | AK05 | Transformer #P00053 located at 1301 Prince of Wales isolated in order to replace broken cut out | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5240 | 2004 | 6 | 1 | 0.40278 |  | 13 | 3 | 15 | Fisher | 4.16kV | AK05 | Transformer K261 at 1542 Lexington isolated to replace the pedesal cover. | Ottawa | Scheduled Outage | Equipment Failure - Cause Unknown
16754 | 2010 | 8 | 16 | 0.55208 |  | 28 | 1 | 2 | FISHER | 4.16kV | AK05 | Transformer P00406 at 1315 Prince of Wales Drive isolated to replace 2 cutouts and 3 current limiting fuses | Ottawa | Scheduled Outage | Repair
7285 | 2005 | 9 | 6 | 0.58333 |  | 170 | 17 | 6 | Fisher | 4.16kV | AK05 | Transformer OTT5126 at 1754 Prince of Wales was isolated to relocate to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
16937 | 2010 | 9 | 14 | 0.38889 |  | 45 | 2 | 3 | Fisher | 4.16kV | AK05 | Transformer #X34435 located at 876 Maryland opened by crew to install new service | Ottawa | Scheduled Outage | Construction
16938 | 2010 | 9 | 14 | 0.38889 |  | 45 | 2 | 3 | Fisher | 4.16kV | AK05 | Transformer #X34435 located at 876 Maryland opened by crew to install new service | Ottawa | Scheduled Outage | Construction
7514 | 2005 | 10 | 24 | 0.4375 |  | 240 | 24 | 6 | Fisher | 4.16kV | AK05 | Transformer #OTT5798 located at 1555 Skeena isolated to install a pole | Ottawa | Scheduled Outage | Construction
7520 | 2005 | 10 | 26 | 0.50347 |  | 160 | 27 | 10 | Fisher | 4.16kV | AK05 | Isolated Transformer at 1547 Skeena to relocate plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
7526 | 2005 | 10 | 27 | 0.38542 |  | 188 | 19 | 6 | Fisher | 4.16kV | AK05 | Isolated Transformer # OTT5798 at 1549 Skeena to transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
17195 | 2010 | 10 | 30 | 0.90278 |  | 40 | 7 | 11 | Fisher | 4.16kV | AK05 | Transformer X33527 at 1279 Lampman was opened to remove a tree limb from service wires & disconnect damaged service. | Ottawa | Tree Contacts | Tree Limb Fallen
7547 | 2005 | 10 | 31 | 0.39583 |  | 292 | 92 | 19 | Fisher | 4.16kV | AK05 | Isolated transformer at 1511 Skeena Ave to replace poles | Ottawa | Scheduled Outage | Construction
7559 | 2005 | 11 | 3 | 0.48958 |  | 135 | 43 | 19 | Fisher | 4.16kV | AK05 | Transformer located at 1511 Skeena isolated due to pole transfer | Ottawa | Scheduled Outage | Preventive Maintenance
11741 | 2007 | 11 | 20 | 0.40278 |  | 35 | 6 | 10 | FISHER | 4.16kV | AK05 | TRANSF #33565 AT 1560 MINAKI ISOLATED TO ALLOW FOR SERVICE UPGRADE | Ottawa | Scheduled Outage | Construction
11756 | 2007 | 11 | 23 | 0.37778 |  | 111 | 15 | 8 | Fisher | 4.16kV | AK05 | At 09:04 trans at 1434 Morley was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
7655 | 2005 | 11 | 26 | 0.28333 |  | 239 | 48 | 12 | Fisher | 4.16kV | AK05 | AK05 circuit auto-reclosed once. On-call crew determined the problem to be a faulted cable to K262. K262 switched over to alternate supply.12 customers on Lexington, Morley & Griffith were affected for the duration of outage. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17446 | 2010 | 12 | 22 | 0.35972 |  | 12 | 2 | 11 | FISHER | 4.16kV | AK05 | Transformer X33527 at 1279 Lampman Cres isolated to allow for tree removal | Ottawa | Scheduled Outage | Tree Fallen
17449 | 2010 | 12 | 22 | 0.5625 |  | 15 | 3 | 11 | Fisher | 4.16kV | AK05 | Transformer X33527 was isolated to allow crew to install new service. 11 customers were affected for 15 minutes. | Ottawa | Scheduled Outage
13834 | 2009 | 1 | 2 | 0.17361 |  | 310 | 173 | 80 | Fisher | 4.16kV | AK06 | One phase down of conductor on Fisher. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3181 | 2003 | 2 | 11 | 0.37917 |  | 30 | 106 | 212 | Fisher | 4.16kV | AK06 | AK06 circuit was opened for crews to effect repairs to hydro pole at 936 Baseline that was involved in a multi vehicle accident. Pole was knocked clear off base. | Ottawa | Scheduled Outage | Emergency Services Request
3232 | 2003 | 3 | 7 | 0.51042 |  | 243 | 12 | 3 | Fisher | 4.16kV | AK06 | Crew replaced a 75 KVA xfmr on Baseline resulting from calls of dimming lights from customers to call centre. | Ottawa | Unknown/Other
5102 | 2004 | 5 | 5 | 0.375 |  | 153 | 8 | 3 | AK | 4.16kV | AK06 | V107 @ 1465 Baseline was isolated to inspect cable ducts. V108 & V113 were also off during this outage. | Ottawa | Scheduled Outage | Repair
5175 | 2004 | 5 | 18 | 0.65556 |  | 369 | 55 | 9 | AK | 4.16kV | AK06 | As per dispatch, Tx OTT2448 was off at 15:44 & power restored to 9 customers at 21:53 due to lightning strike. | Ottawa | Lightning | Direct Strike
3469 | 2003 | 5 | 23 | 0.35417 |  | 415 | 1402 | 220 | Fisher |  | AK06 | Dave Stevenson reports blue phase cable to V107 from overhead pole. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16313 | 2010 | 6 | 22 | 0.03125 |  | 140 | 91 | 80 | Fisher |  | AK06 | Transformer X35392 opened, & AK06 isolated after a car hit and broke a pole. | Ottawa | Foreign Interference | Vehicle
9482 | 2006 | 10 | 20 | 0.39583 |  | 165 | 14 | 5 | Fisher | 4.16kV | AK06 | Transformer #OTT792 located at 790 Baseline Rd isolated to change transformer. PC10A #880 | Ottawa | Scheduled Outage | Preventive Maintenance
15618 | 2010 | 1 | 6 | 0.3375 |  | 264 | 4 | 1 | Fisher | 4.16kV | AK07 | At 8:06am vault V617 at 1435 Prince of Whales was isolated to allow crews to replace blown transformer, 1 customer affected and power was resotred at 12:30pm . Fisher (AK07). ID#15618. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17484 | 2011 | 1 | 13 | 0.39444 |  | 44 | 7 | 9 | Fisher AK | 4.16kV | AK07 | TP3129 at 267 Madhu was isolated to replace damaged cover. | Ottawa | Scheduled Outage | Repair
17541 | 2011 | 1 | 31 | 0.3125 |  | 253 | 51 | 12 | Fisher | 4.16kV | AK07 | P302 at 1896 Prince of Whales was isolated to allow crews to transfer the cable and PPH to a new pole | Ottawa | Scheduled Outage | Construction
15722 | 2010 | 2 | 12 | 0.4375 |  | 44 | 4 | 6 |  | 4.16kV | AK07 | At 10:30 trans at 799 MELFA CRES OTTAWA was isoataed in order to install a new pole and transfer the services | Nepean | Scheduled Outage | Preventive Maintenance
7925 | 2006 | 2 | 17 | 0.43264 |  | 325 | 1408 | 260 | Fisher | 4.16kV | AK07 | Wires down at Prince of Wales and Dynes | Ottawa | Adverse Weather | Wind
4938 | 2004 | 3 | 26 | 0.375 |  | 240 | 160 | 40 | Fisher | 4.16kV | AK07 | Scheduled outage to 3 transformers to replace the primary wire on Melfa Cresc.. The 3 transformers were opened and the primary tap knocked off to 5 spans of AK07 primary. | Ottawa | Scheduled Outage | Preventive Maintenance
6530 | 2005 | 5 | 10 | 0.38194 |  | 43 | 7 | 10 | Fisher | 4.16kV | AK07 | Isolated Transformer #265 at 920 Dynes to repair a bad ug | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20495 | 2012 | 5 | 10 | 0.53542 |  | 13 | 94 | 433 | Fisher | 4.16kV | AK07 | MVA at1700 Prince of Wales Dr called in from Fire Departmen. Pete Barr requested AK07 and AK05 breakers open. Police report # 12-133266 | Ottawa | Foreign Interference | Vehicle
12464 | 2008 | 5 | 22 | 0.71389 |  | 97 | 16 | 10 | Fisher | 4.16kV | AK07 | Transformer TP2330 @ 461 Rahul was isolated to allow crews to replace leaking transformer. Transformer was hit and found leaking. | Ottawa | Foreign Interference | Vehicle
12555 | 2008 | 6 | 5 | 0.41458 |  | 546 | 109 | 12 | Fisher | 4.16kV | AK07 | TP2330 isolated to allow for soil remediation at 461 Rahul Dr. | Ottawa | Scheduled Outage | Preventive Maintenance
5262 | 2004 | 6 | 7 | 0.92917 |  | 64 | 29 | 27 | Fisher | 4.16kV | AK07 | The fuse blew at the dip pole to K751 at 1601 Prince of Wales due to a blown arrestor at K752. K752 is normal open point. The arrestor was cleared and the switch refused to restore power to 27 units. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11025 | 2007 | 8 | 9 | 0.4375 |  | 76 | 13 | 10 | Fisher | 4.16kV | AK07 | Transformer #K00258 located at 993 Arnot Rd isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
14988 | 2009 | 8 | 21 | 0.48264 |  | 64 | 6 | 6 | Fisher | 4.16kV | AK07 | Transformer #X33524 located at 799 Melfa Cres isolated for an upgrade | Ottawa | Scheduled Outage | Construction
9092 | 2006 | 8 | 30 | 0.41667 |  | 75 | 15 | 12 | Fisher | 4.16kV | AK07 | Isolated transformer K752 at 1601 Prince of Wales Dr to replace broken primary insulator | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9094 | 2006 | 8 | 30 | 0.47222 |  | 65 | 17 | 16 | FISHER | 4.16kV | AK07 | Isolated transformer K754 at 1601 Prince of Wales Dr to replace broken insulator on the primary side | Ottawa | Scheduled Outage | Repair
11882 | 2007 | 12 | 24 | 0.82639 |  | 15 | 2 | 7 | Fisher | 4.16kV | AK07 | Isolated transformer X31373 at 1757 Prince Of Wales Dr to replace defective hot line clamp | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6310 | 2005 | 3 | 21 | 0.71389 |  | 82 | 5 | 4 | Fisher | 4.16kV | AK10 | Replaced broken switch to transformer OTT4711 at 996 Normandy Cr | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20595 | 2012 | 5 | 25 | 0.78542 |  | 78 | 273 | 210 | Fisher | 4.16kV | AK10 | Defective red phase cable on AK10 riser from station caused breaker to open. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
5369 | 2004 | 6 | 24 | 0.75556 |  | 188 | 38 | 12 | Fisher | 4.16kV | AK10 | Fuse to O/H transformer at 1575 Senio found blown from tree contact due to heavy wind storm. | Ottawa | Tree Contacts | Tree Fallen
11008 | 2007 | 8 | 7 | 0.53056 |  | 148 | 20 | 8 | Fisher | 4.16kV | AK10 | At 12:44 trans 1571 Appledown was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
19162 | 2011 | 9 | 13 | 0.72569 |  | 207 | 728 | 211 | FISHER | 4.16kV | AK10 | Tree limb on wires. Crew removed limb and power restored | Ottawa | Tree Contacts | Tree Limb Fallen
4164 | 2003 | 9 | 27 | 0.60833 |  | 62 | 131 | 127 | Fisher | 4.16kV | AK10 | Tree brought down one phase of AK10 circuit at 1571 Apeldoorn. Circuit was still energized. Was opened to reserect phase. | Ottawa | Tree Contacts | Tree Fallen
11699 | 2007 | 11 | 13 | 0.47917 |  | 75 | 30 | 24 | Fisher | 4.16kV | AK10 | At 11:30 trans at 1035 Meadowlands Dr was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15690 | 2010 | 1 | 27 | 0.61111 |  | 27 | 2 | 5 | Fisher | 4.16kV | AK12 | Transformer #X31350 located at the corner of Fisher/Meadowlands isolated to connect traffic lights after the City made repairs to a defective disconnect | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4828 | 2004 | 2 | 26 | 0.49444 |  | 53 | 19 | 21 | Fisher | 4.16kV | AK12 | Transformer K00285 at 447 Kintyre isolated for U/G secondary cable repair. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17655 | 2011 | 2 | 28 | 0.97847 |  | 7 | 1 | 5 | Fisher | 4.16kV | AK12 | Transformer X26069 opened to allow crew to re-connect service at 1542 Fisher. | Ottawa | Defective Equipment
3229 | 2003 | 3 | 7 | 0.40417 |  | 135 | 135 | 60 | Fisher | 4.16kV | AK12 | A snow plow hit a pole on Fisher north of Meadowlands and damaged the cable section between K289 and the P/P/H. The AK12 circuit autoreclosed and the fuse blew at the white phase P/P/H switch causing an outage to about 60 customers on Trelawnet, Kintyre & Orkney. The crew isolated the cable section and restored power on AK04 | Ottawa | Foreign Interference | Vehicle
3414 | 2003 | 5 | 8 | 0.5 |  | 15 | 5 | 19 | Fisher | 4.16kV | AK12 | Transformer K294 isolated to make repairs to secondary bus. | Ottawa | Scheduled Outage | Repair
3415 | 2003 | 5 | 8 | 0.53125 |  | 30 | 6 | 12 | Fisher | 4.16kV | AK12 | Transformer K289 isolated to disconnect one service so customer can make changes. | Ottawa | Scheduled Outage | Preventive Maintenance
3416 | 2003 | 5 | 8 | 0.8125 |  | 30 | 6 | 12 | Fisher | 4.16kV | AK12 | Transformer K289 isolated to reconnect service after customer changes. | Ottawa | Scheduled Outage | Repair
6637 | 2005 | 6 | 1 | 0.70139 |  | 319 | 133 | 25 | Fisher | 4.16kV | AK12 | Cable dip fuse to K326 opened during lightening storm. Crew found dip #1 cable to K326 deffective. Dip #1 isolated and transformer transferred to dip #2. Power restored at 22:09 | Ottawa | Adverse Weather | Lightning
7002 | 2005 | 7 | 21 | 0.42986 |  | 35 | 9 | 16 | Fisher | 4.16kV | AK12 | Transformer at 1558 Fisher Ave isolated due to cable repair | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11046 | 2007 | 8 | 14 | 0.53819 |  | 140 | 30 | 13 | Fisher | 4.16kV | AK12 | Transformer #OTT6426 located at 1525 Valmarie isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
12065 | 2008 | 2 | 20 | 0.43472 |  | 67 | 11 | 10 | BANTREE | 4.16kV | AL02 | TRANSFORMER #OTT3437 AT 399 BLAKE TERRACE ISOLATED TO ALLOW FOR POLE CHANGE | Ottawa | Scheduled Outage | Preventive Maintenance
16135 | 2010 | 5 | 25 | 0.45833 |  | 10 | 5 | 28 | Bantree | 4.16kV | AL02 | Transformer #K331 located at 2115 Erinbrook opened by crew to isolate service for unit #44 for electrician | Ottawa | Scheduled Outage | Construction
8564 | 2006 | 6 | 21 | 0.45833 |  | 60 | 85 | 10 | Bantree | 4.16kV | AL02 | Transformer #K332 isolated at 2415 Southvale Cres to make repairs on U/G secondary service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3652 | 2003 | 6 | 30 | 0.47917 |  | 60 | 16 | 16 | Bantree | 4.16kV | AL02 | xfmr K342 @ 2225 Erinbrook taken out of service for service repair to 2495 Southvale. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3655 | 2003 | 6 | 30 | 0.70208 |  | 32 | 9 | 16 | Bantree | 4.16kV | AL02 | Transformer K342 taken out of service again to reconnect the service to 2225 Erinbrook following repairs by electrician | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16663 | 2010 | 8 | 4 | 0.65903 |  | 741 | 550 | 222 | Bantree | 4.16kV | AL02 | AL02 breaker atuo-reclosed -auto and stayed off. Lightning strike caused fuses to blow to SW1706 and damage to switchgear. SW1706 was isolated for repairs & main circuit was restored. | Ottawa | Lightning
7074 | 2005 | 8 | 5 | 0.70833 |  | 285 | 171 | 36 | Bantree | 4.16kV | AL02 | Dip pole feeding Transformer #330 and #331 at 2415 Southvale ,off Russell rd was refused and power restored.A bad arrestor caused the outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13140 | 2008 | 8 | 22 | 0.47222 |  | 45 | 6 | 8 | Bantree | 4.16kV | AL02 | Transformer #K339 located at 2163 Erinbrook isolated due to disconnecting from a pedestal for a demolition | Ottawa | Scheduled Outage | Preventive Maintenance
4110 | 2003 | 9 | 19 | 0.70625 |  | 14 | 60 | 255 | Bantree | 4.16kV | AL02 | Tripped the same time as TB1AL and AL04, closed by SCADA successfully. | Ottawa | Adverse Weather | Wind
17324 | 2010 | 11 | 22 | 0.50764 |  | 9 | 33 | 222 | Bantree | 4.16kV | AL02 | Tree trimmers Charlie Godwin of Tamarack had a falling tree cause an unintentional contact made between 2 circuits. Interupting TB3LE (TB01) TB1AL (TB17) and AL02 | Ottawa | Tree Contacts | Tree Fallen
6471 | 2005 | 4 | 28 | 0.39931 |  | 93 | 2 | 1 | AL | 4.16kV | AL03 | V464 at 1255 Leeds ave was isolated to repair a customer problem with water coming into the vault. | Ottawa | Foreign Interference | Foreign Object
18038 | 2011 | 4 | 28 | 0.59514 |  | 247 | 379 | 92 | Bantree | 4.16kV | AL03 | AL03 CB auto-reclosed and locked out during wind/lightning storm. Closed via scada and held. | Ottawa | Adverse Weather | Wind
10711 | 2007 | 6 | 22 | 0.6875 |  | 110 | 2 | 1 | Bantree | 4.16kV | AL03 | One of the fuses that feeds P399 @ 2550 Blackwell just let go, cable,transformer and secondary all tested good. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9104 | 2006 | 8 | 30 | 0.74306 |  | 160 | 16 | 6 | Bantree | 4.16kV | AL03 | Transformer #OTT3877 located at 1300 Leeds isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
15383 | 2009 | 11 | 12 | 0.77361 |  | 85 | 1 | 1 | Bantree | 4.16kV | AL03 | At 6:34pm, SCADA indicates that the AL03 breaker had opened. Crews report fallen tree on two phases at P80 2755 Sheffield Road caused by beaver cutting away poplar tree. Crews cleared fallen tree from overhead andpower was restored to the 86 customers at 7:59pm. Bantree (AL03). ID#15383. | Ottawa | Tree Contacts | Tree Fallen
11236 | 2007 | 9 | 4 | 0.24444 |  | 70 | 112 | 96 | Bantree | 4.16kV | AL04 | A blown lightning arrestor on the AL04 under build which flash up into the the 13 KV which cause it to trip in the St Laurent Gladwin area. All power restored except for 1804 St. Laurent, McDonalds, which has a burnt cable and switches at Pole 105. Crew sent to make repair. | Ottawa | Defective Equipment
11239 | 2007 | 9 | 4 | 0.24444 |  | 308 | 5 | 1 | BANTREE | 4.16kV | AL04 | Burnt Switch and blown arrester, as well as burnt concentric neutral on cable was repaired to restore power to P1871 feeding McDonalds on St. Laurent. | Ottawa | Defective Equipment
11240 | 2007 | 9 | 4 | 0.43611 |  | 32 | 1 | 1 | BANTREE | 4.16kV | AL04 | Blown arrestor cleared to restore power to P503 on St. Laurent. 1 customer affected. | Ottawa | Defective Equipment
11242 | 2007 | 9 | 4 | 0.24444 |  | 355 | 12 | 2 | BANTREE | 4.16kV | AL04 | Burnt switches, burnt cable and arrestors replaced feeding P107 on St. Laurent, affecting Burger King and Tim Hortons. | Ottawa | Defective Equipment
4111 | 2003 | 9 | 19 | 0.70556 |  | 15 | 24 | 96 | Bantree | 4.16kV | AL04 | Tripped the same time as TB1AL and AL04, closed by SCADA successfully. | Ottawa | Adverse Weather | Wind
20527 | 2012 | 5 | 16 | 0.47708 |  | 11 | 5 | 27 | Bantree | 4.16kV | AL05 | A truck hit a guy wire and caused it to tangle into one of the phases on the AL05 circuit. The AL05 circuit had to be opened to allow Hydro Ottawa crews to clear the line | Ottawa | Foreign Interference | Vehicle
17052 | 2010 | 10 | 4 | 0.92917 |  | 60 | 7 | 7 | BANTREE | 4.16kV | AL05 | Transformer X38365 at 1756 Bantree isolated to allow for repairs to neutral | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7810 | 2006 | 1 | 15 | 0.87639 |  | 113 | 2 | 1 | BANTREE | 4.16kV | AL06 | Crew reports broken drop to transformer switch at 2600 Edinburgh. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10011 | 2007 | 2 | 10 | 0.60417 |  | 45 | 4 | 5 | Bantree | 4.16kV | AL06 | At 14:30 trans P73 at 2675 Blackwell St was isolated in order to replace 3 transformer dip sw's | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12074 | 2008 | 2 | 22 | 0.5625 |  | 60 | 32 | 32 | Bantree | 4.16kV | AL06 | P73 at 2675 Blackwell isolated to allow crew to replace broken insulators in live front transformer. | Ottawa | Scheduled Outage | Repair
6879 | 2005 | 7 | 6 | 0.93472 |  | 80 | 13 | 10 | BANTREE | 4.16kV | AL06 | RACOON WAS FOUND ACROSS 3 PHASES OF AL06 CIRCUIT AT THE POTHEAD | Ottawa | Foreign Interference | Animal
6884 | 2005 | 7 | 7 | 0.54167 |  | 34 | 97 | 171 | AL | 4.16kV | AL06 | AL06 o/h line was isolated to make emergency repairs to primary conductor that was damaged earlier by a racoon at the p/p/h. AL06 was on AL00 supply. | Ottawa | Foreign Interference | Animal
5960 | 2004 | 12 | 2 | 0.28958 |  | 593 | 10 | 1 | Bantree | 4.16kV | AL06 | Emergency isolation of transformer P362 at 2628 Edinburgh due to faulted secondary cables & burning main. Transfomer isolated for Teraflex to install new secondary cables. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5965 | 2004 | 12 | 2 | 0.55208 |  | 21 | 0 | 1 | Bantree | 4.16kV | AL06 | Change cut out for transformer P00452 @ 2630 Shefield Rd | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4720 | 2004 | 1 | 22 | 0.78472 |  | 12 | 3 | 15 | Bantree | 4.16kV | AL10 | Lift lid on pedastal | Ottawa | Unknown/Other
6487 | 2005 | 5 | 1 | 0.68194 |  | 23 | 5 | 13 | Bantree | 4.16kV | AL10 | K356 at 2375 Blackstone interrupted to repair service to 2359 Blackstone. Changed current limiter in pedestal. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5100 | 2004 | 5 | 4 | 0.49306 |  | 28 | 6 | 12 | AL | 4.16kV | AL10 | K355 on Blackstone cr. opened to connect temp trailer at pedestal. 12 customers notified. | Ottawa | Scheduled Outage | Construction
19775 | 2011 | 12 | 31 | 0.92986 |  | 712 | 1851 | 156 | Bantree DS | 4.16kV | AL10 | AL10 breaker opened up due to a MVA at 2495 Lancaster Rd. | Ottawa | Foreign Interference
5407 | 2004 | 6 | 30 | 0.2875 |  | 261 | 4 | 1 | Alexander | 27.6/16kV | Alex F1 | Transformer 2786 at 210 Huntmar Rd blown and replaced. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
4484 | 2003 | 11 | 14 | 0.34722 |  | 16 | 1067 | 4000 | Alexander DS | 27.6/16kV | Alex F1 & F2 | After repairing a feeder fault during the windstorm, it was determined that there was a blown fuse on the supply transformer at Hydro One's substation. See Rpt 4455 | Goulburn | Loss of Supply | HEPC Station Fault
13916 | 2009 | 2 | 1 | 0.87917 |  | 313 | 4335 | 2100 | Alexander | 27.6/16kV | Alex F2 | Defective red phase cable section between S22241 and S10930 at Mian Street and Beverly. Anything that could go wrong did go wrong. FCI's incorrect, poor fuse co-ordination, wrong nomenclature, snow covered switchgear and switches breaking. | Gloucester | Defective Equipment
13935 | 2009 | 2 | 5 | 0.41528 |  | 16 | 3 | 10 | Alexander | 27.6/16kV | Alex F2 | Transformer TP5077 @ 106 Majove was isolated to allow the crew to remove a "T" style insert. | Goulburn | Scheduled Outage | Preventive Maintenance
17567 | 2011 | 2 | 9 | 0.39931 |  | 180 | 159 | 53 | Alexander | 27.6/16kV | Alex F2 | 5 transformers downstream of Tx 6991 on Lanigan Cr were isolated to re-configure primary cables. | Goulburn | Scheduled Outage | Construction
4802 | 2004 | 2 | 19 | 0.39583 |  | 77 | 1027 | 800 | Alexander | 27.6/16kV | Alex F2 | While transferring load on Alex F2 to Alex F3 a power outage occuried when crews removed cap at S23-1. Reclosure was set on single shot. All load restored as of 10:47. | Goulburn | Defective Equipment
4856 | 2004 | 3 | 4 | 0.58333 |  | 65 | 1 | 1 | Alexander | 27.6/16kV | Alex F2 | Rabbit 106 on Abbott St in Stittsville the fuses were blown due to tree contact from Hi Hoe operation Cavaughn Construction. | Goulburn | Foreign Interference | Foreign Object
6280 | 2005 | 3 | 14 | 0.50347 |  | 84 | 6 | 4 | Alexander | 27.6/16kV | Alex F2 | Transformer #9677 isolated at 30 Carlisle to replace cut out & arrester | Goulburn | Foreign Interference | Animal
17731 | 2011 | 3 | 18 | 0.375 |  | 81 | 16 | 12 | Alexander | 27.6/16kV | Alex F2 | TP2006 at 138 Westridge replaced | Goulburn | Scheduled Outage | Repair
8216 | 2006 | 5 | 2 | 0.42153 |  | 48 | 480 | 600 | Alexander | 27.6/16kV | Alex F2 | White Phase of Alex F2 tripped under hold off. An area off Carp Road N of Rothborn was supplied from the Alex F2, which is owned by Hydro One, and their work caused the Alex F2 white phase to trip. Hydro One had closed S262 approx. a week ago and never informed Hydro Ottawa. | Goulburn | Loss of Supply | HEPC Circuit Fault
6515 | 2005 | 5 | 5 | 0.375 |  | 268 | 36 | 8 | Alexander | 27.6/16kV | Alex F2 | Transformer #GBO20133 located at 41 Granite Ridge Dr was isolated due to clean up from an oil spill | Goulburn | Scheduled Outage | Repair
6533 | 2005 | 5 | 10 | 0.64444 |  | 114 | 259 | 150 | Alex | 27.6/16kV | Alex F2 | S1 white phase bus bar failed causing outage to approx 150 customers. While switching elbows at transformer 7069 were reversed in the transformer. Power to 10 customers was effected during isolation of S1. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
20499 | 2012 | 5 | 10 | 0.90625 |  | 89 | 12 | 8 | Alexander | 27.6/16kV | Alex F2 | , transformer TP7800 at Renshaw and Kearnsley was isolated to allow crew to disconnect defective secondary connections | Goulburn | Scheduled Outage | Repair
8283 | 2006 | 5 | 12 | 0.43819 |  | 82 | 459 | 750 | Alexander | 27.6/16kV | Alex F2 | A Vehicle hit a pole at the corner of Hobin and Main Street, causing the Hot line clamp at S922Rto burn off, as well as S463 Red to blow. Al Cooney reports pole is okay. Repairs made to S922R. Terminations at S463 were blackened, load was picked up by openening Alex F2 red phase recloser momentarily, and then closing. | Goulburn | Foreign Interference | Vehicle
5142 | 2004 | 5 | 13 | 0.6375 |  | 164 | 14 | 5 | Alexander | 27.6/16kV | Alex F2 | Planned outage to upgrade conductor at Dwyer Hill Rd and Hwy 7 | Goulburn | Scheduled Outage | Construction
10419 | 2007 | 5 | 15 | 0.38681 |  | 81 | 4 | 3 | Alexander | 27.6/16kV | Alex F2 | A section of white phase o/h line on Spruce Ridge rd was isoalted to re-arrange primary plant. | Goulburn | Scheduled Outage | Construction
16145 | 2010 | 5 | 25 | 0.75 |  | 325 | 27 | 5 | Alexander | 27.6/16kV | Alex F2 | Transformer X36550 was found defective. Transformer replaced and load restored. | Goulburn | Defective Equipment
18213 | 2011 | 5 | 25 | 0.36806 |  | 193 | 302 | 94 | Alexander | 27.6/16kV | ALEX F2 | Transformers TP7789, TP7790, TP7791, TP7792, TP7170, TP7793, TP7794, TP7795 on West Ridge were isolated to allow crew to replace elbows and inserts. 94 cusotmers were affected. Alexander (ALEXF2) | Goulburn | Scheduled Outage
18221 | 2011 | 5 | 25 | 0.78958 |  | 80 | 8 | 6 | Alexander | 27.6/16kV | Alex F2 | Trans X36451 cutout was refused due to fuse failure .. No cause found | Goulburn | Unknown/Other | No Apparent Cause
6614 | 2005 | 5 | 29 | 0.30556 |  | 284 | 5 | 1 | Alexander | 27.6/16kV | Alex F2 | Fuse at road found opened. | Kanata | Foreign Interference | Bird
10478 | 2007 | 5 | 30 | 0.041667 |  | 50 | 1 | 1 | Alexander | 27.6/16kV | Alex F2 | Tx 7158 at 1416 Stittsville Main opened to replace defective blue phase cut-out, tracking to pole. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
6714 | 2005 | 6 | 14 | 0.67986 |  | 191 | 16 | 5 | Alexander | 27.6/16kV | Alex F2 | TX5755 @ 11 Pullman st in Stittsville transformer fuse opened due to squirrel contact. | Kanata | Adverse Weather | Lightning
8556 | 2006 | 6 | 20 | 0.26111 |  | 334 | 666 | 277 | Alexander | 27.6/16kV | Alex F2 | Switch S295 W phase dip , S10006 fuse to single phase overhead and O/H tx fuse at 1326 Walker St all found open. Transformer at 1326 Walker faulted and had to be replaced. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
3611 | 2003 | 6 | 25 | 0.71667 |  | 52 | 217 | 250 | Alexander DS | 27.6/16kV | Alex F2 | Switch 463 B phase found open, appears fuse holder is defective and will have to be replaced, same sw closed to restore load. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
10749 | 2007 | 6 | 27 | 0.6875 |  | 125 | 1542 | 1500 | Alexander | 27.6/16kV | Alex F2 | 463 red phase lead broke off to cable termination to S19-1, other 2 phase had to be isolated to make repairs as elbows at S19 are not disconectable. | Goulburn | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
6821 | 2005 | 6 | 28 | 0.2375 |  | 59 | 5 | 5 | Alexander | 27.6/16kV | Alex F2 | 24/7 reports transformer fuse found opened due to bird contact. | Kanata | Foreign Interference | Bird
18588 | 2011 | 7 | 5 | 0.39444 |  | 272 | 530 | 117 | Alexander | 27.6/16kV | Alex F2 | Transformers TP7819, TP7818, TP7817, TP7816, TP7162, TP7814, TP7813, TP7812, TP7173, TP7811, TP7810, TP7809, TP7175 on Crantham and Steventon were isolated to allow crew to replace elbows and inserts on all transformers. 127 customers were affected. Alexander (ALEX F2) | Goulburn | Scheduled Outage | Preventive Maintenance
18606 | 2011 | 7 | 7 | 0.38889 |  | 170 | 212 | 75 | Alexander | 27.6/16kV | Alex F2 | 7 W phase Tx's on Delamere & Heritage Grove were isolated for elbow & insert upgrades. | Goulburn | Scheduled Outage | Preventive Maintenance
3696 | 2003 | 7 | 8 | 0.47917 |  | 55 | 46 | 50 | Alexander | 27.6/16kV | Alex F2 | G. Morris to open switch 909 to allow for the repair of the overhead line. Approximately 50 customers affected. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
16426 | 2010 | 7 | 8 | 0.045139 |  | 363 | 2854 | 2000 | Alexander | 27.6/16kV | Alex F2 | Defective primary cable between S36 and S20 caused S463 to blow. Circuit backfed through primary dips to restore customers. | Goulburn | Defective Equipment
8685 | 2006 | 7 | 10 | 0.54931 |  | 29 | 1 | 3 | Alexander | 27.6/16kV | Alex F2 | Lanny McNabb/K-Line isolation of O/H section between sws S14055 & S551 to I/S new cable under Hwy#7. | Goulburn | Scheduled Outage | Construction
3776 | 2003 | 7 | 24 | 0.22778 |  | 93 | 46 | 30 | Alexander | 27.6/16kV | Alex F2 | 3 switches replaced at 463.Carp rD in Stittsville | Goulburn | Scheduled Outage | Preventive Maintenance
10998 | 2007 | 8 | 5 | 0.27708 |  | 76 | 5 | 4 | Alexander | 27.6/16kV | Alex F2 | Transformer #2705 located at 1246 Carp isolated due to animal contact | Goulburn | Foreign Interference | Animal
7075 | 2005 | 8 | 6 | 0.94861 |  | 139 | 902 | 400 | Alexander | 27.6/16kV | Alex F2 | Switch 922 white phase fuse was broken, not blown. Line sectionalized at 515 and 40 amp fuse installed at S922. Then switch 515 closed and held. 40 amp fuse replaced with 100 amp at Switch 922 | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
5674 | 2004 | 8 | 13 | 0.67014 |  | 339 | 43 | 30 | Alexander | 27.6/16kV | ALEX F2 | Dave Guy reports TE20103 has been damaged in new subdivision. Load was restored to 30 customers by 17:20. Two Customers remain out of power until transformer has been replaced.Transformer replaced and last two customers restored at 21:44 | Kanata | Foreign Interference | Dig-in
11148 | 2007 | 8 | 24 | 0.28542 |  | 159 | 5 | 2 | Alexander | 27.6/16kV | Alex F2 | Transformer switch at 22 John Woods in Stittsville opened during thunderstorm. No apparent problem found, switch refused and closed. | Goulburn | Defective Equipment
13152 | 2008 | 8 | 26 | 0.45 |  | 117 | 16 | 8 | Alexander | 27.6/16kV | Alex F2 | TP2226 at 349 Westridge was isolated to install new base under transformer. | Goulburn | Scheduled Outage | Repair
11173 | 2007 | 8 | 28 | 0.61875 |  | 134 | 45 | 20 | Alexander | 27.6/16kV | Alex F2 | TP2230 @ 322 Westridge st in Stittsville was replaced by crews. Transformer was damaged cause unknown. | Goulburn | Foreign Interference | Foreign Object
13160 | 2008 | 8 | 28 | 0.38889 |  | 131 | 26 | 12 | Alexander | 27.6/16kV | Alex F2 | Isolation of TP2222 at 393 West Ridge to allow crew to raise base of transformer. | Goulburn | Scheduled Outage
3975 | 2003 | 8 | 30 | 0.91944 |  | 56 | 4 | 4 | Alexander | 27.6/16kV | Alex F2 | D. Guy reports transformer fuse replaced, and holding restoing power to customer. Outage was caused by animal. | Goulburn | Foreign Interference | Animal
4161 | 2003 | 9 | 26 | 0.95833 |  | 330 | 165 | 30 | Alexander | 27.6/16kV | Alex F2 | Replacement of S20 sectionalizer. | Goulburn | Scheduled Outage | Repair
19303 | 2011 | 10 | 1 | 0.96319 |  | 52 | 1 | 1 | Alexander | 27.6/16kV | Alex F2 | Crews found transformer fuse X09575 opened. 1 customers affected for 52 mins. | Kanata | Unknown/Other
4320 | 2003 | 10 | 21 | 0.44028 |  | 226 | 4 | 1 | Alexander | 27.6/16kV | Alex F2 | Transformer 2983 found defective due to lightnig strike, replaced by crew. | Goulburn | Lightning | Direct Strike
9581 | 2006 | 11 | 1 | 0.6875 |  | 490 | 65 | 8 | Alexander | 27.6/16kV | Alex F2 | Replaced a defective transformer 8879 @ 67 Crantham. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
7588 | 2005 | 11 | 9 | 0.99653 |  | 90 | 8 | 5 | ALEXANDER | 27.6/16kV | ALEX F2 | Animal contact caused transformer at 2 Carlisle circle to open. | Goulburn | Foreign Interference | Animal
4455 | 2003 | 11 | 13 | 0.95833 |  | 560 | 20571 | 2204 | Alexander | 27.6/16kV | Alex F2 | A tree came down across the line in Stittsville on Hazeldean Road near Hwy#7. The line had to be re-built and then the power was restored. ID#4455 Also a Fuse blew on the high side of the F2 Recloser (Hydro One). F1 was opened to allow a switch 678 to be closed F1 was reclosed and load was pick up. See Rpt 4484 | Goulburn | Adverse Weather | Wind
5903 | 2004 | 11 | 19 | 0.375 |  | 164 | 137 | 50 | Alexander | 27.6/16kV | Alex F2 | Install 6 new transformer in the Coachman Cres Stittsville Area | Goulburn | Scheduled Outage | Construction
9731 | 2006 | 11 | 26 | 0.35069 |  | 140 | 7 | 3 | Alexander | 27.6/16kV | Alex F2 | Hydro One isolated their section of the Alex F2 feeder on Rothburn for construction of new F4 feeder. | Goulburn | Scheduled Outage | Construction
6091 | 2004 | 12 | 23 | 0.5 |  | 149 | 2205 | 2200 | Alexander | 27.6/16kV | Alex F2 | An isulator on the overhead circuit broke at switch 919 on the W phase which caused the W phase recloser to open at Alexander station. The white phase recloser reclosed which caused the W phase on the high side of station transformer to also operate (82T2-L white phase) . The R & B phase reclosers were also opened to fix the repairs safetly. The insulator was repaired and the fuse was replace and all load was restored. | Goulburn | Adverse Weather | Rain
11931 | 2008 | 1 | 13 | 0.61806 |  | 30 | 0 | 1 | Alexander | 8/4.8kV | ALEX F3 | Broken cut on transformer #11741 @ 6400 Flewellyn RD | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17528 | 2011 | 1 | 26 | 0.6875 |  | 583 | 10 | 1 | Alexander | 27.6/16kV | Alex F3 | A defective transformer X32141 @ 6415 FERNBANK RD, no crews were available till 19:30 to investigate the problem. Oncal crews were called in at 21:30 to replace the transformer. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12020 | 2008 | 2 | 8 | 0.45833 |  | 345 | 17 | 3 | Alexander | 27.6/16kV | Alex F3 | Transformer 6378 was isolated to move transformer to new supply from switch S26027. 3 customers at 5977 Hazeldean were interrupted. | Goulburn | Scheduled Outage | Construction
4831 | 2004 | 2 | 27 | 0.44792 |  | 13 | 2 | 10 | Alexander | 27.6/16kV | Alex F3 | Tx 6200W50 at 41 Poole creek cr was opened to check a meter. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
7983 | 2006 | 3 | 3 | 0.39583 |  | 49 | 114 | 140 | Alexander | 27.6/16kV | Alex F3 | Isolation of S886 to replace switches. | Goulburn | Scheduled Outage
14059 | 2009 | 3 | 15 | 0.63889 |  | 420 | 77 | 25 | Alexander | 27.6/16kV | Alex F3 | Transformer 7085 at 15 Sunray failed causing S16483 to blow affecting Tx 7084, 7083 & 7082 on Sunray & Cherry Dr. Defective Tx isolated & replaced by O/C crew. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
4902 | 2004 | 3 | 16 | 0.375 |  | 150 | 450 | 180 | Alexander | 27.6/16kV | Alex F3 | 19 Transformer isolated to replace Elbows & Bushings in Stittsville in the area of Johnwoods. Approx 180 customers affected in power outage. | Goulburn | Scheduled Outage | Preventive Maintenance
6303 | 2005 | 3 | 18 | 0.41458 |  | 73 | 9 | 7 | Alexander | 27.6/16kV | Alex F3 | Dundas power transferring transformer T6747 from 8 kv to 27kv. | Goulburn | Scheduled Outage | Construction
4920 | 2004 | 3 | 19 | 0.58611 |  | 86 | 11 | 8 | Alexander | 27.6/16kV | Alex F3 | Transformer # 3297 isolated to replace arrestor & Wood pins. 8 customers affected in power outage. | Kanata | Defective Equipment
17773 | 2011 | 3 | 23 | 0.62917 |  | 44 | 21 | 29 | Alexander | 27.6/16kV | Alex F3 | During insulator washing S16483 became loose and fell open causing outage to 4 transformers. Switch closed by 24/7 crew and power restored. (Cherry Dr/Sunray) | Goulburn | Human Element
17837 | 2011 | 4 | 6 | 0.40417 |  | 140 | 30 | 13 | Alexander | 27.6/16kV | ALEX F3 | transformer TP3580 was isolated to allow crew to replace leaking transformer. 13 customers were affected. ALEXF3 | Goulburn | Scheduled Outage | Repair
4981 | 2004 | 4 | 8 | 0.51389 |  | 158 | 105 | 40 | Alexander | 27.6/16kV | Alex F3 | Elbow and insert replacementin Stittsvillle Grand Harbour Crt, Old Orchard and cable re-arrangement for the red phase. Transformers 4497,7759 and 7760 off loaded for work to proceed. | Goulburn | Scheduled Outage | Construction
12258 | 2008 | 4 | 9 | 0.52292 |  | 62 | 9 | 9 | Alexerdia | 27.6/16kV | Alex F3 | Transformer #20189 @ 99 Sirocco was isolated to allow crews to replace transformer. | Goulburn | Scheduled Outage | Preventive Maintenance
5004 | 2004 | 4 | 15 | 0.38819 |  | 161 | 335 | 125 | Alexander DS | 27.6/16kV | Alex F3 | Transformers in Stittsville isolated for insert and elbow replacement. | Goulburn | Scheduled Outage | Preventive Maintenance
15940 | 2010 | 4 | 15 | 0.43611 |  | 16 | 399 | 1495 | Alexander | 27.6/16kV | ALEX F3 | While switching on ALEX F3 Al Cooney reports that 2 leads on switch 377 fell off, they appear to have been deteriorated. Switch was opened to prevent single phasing causing an outage to 1495 customers, emergency repairs made | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
15950 | 2010 | 4 | 18 | 0.29861 |  | 274 | 46 | 10 | Alexander | 27.6/16kV | Alex F3 | TX 7779 & TX 7780 were isolated to allow crews to transfer the feed over to a new line. | Goulburn | Scheduled Outage | Construction
6427 | 2005 | 4 | 19 | 0.43681 |  | 223 | 30 | 8 | Alexander | 27.6/16kV | Alex F3 | Leaker T6263 at 8 Sunray replaced with a new transformer. | Goulburn | Scheduled Outage | Repair
6430 | 2005 | 4 | 20 | 0.46875 |  | 229 | 33 | 40 | Alexander | 27.6/16kV | Alex F3 | Contractor working at new school dig into cable and damaged transformer bushing and caused transformer leak. Tx 20133W on Granite Ridge replaced. McDonald Brothers Construction. OMS # 16379 | Goulburn | Foreign Interference | Dig-in
10309 | 2007 | 4 | 23 | 0.88333 |  | 58 | 24 | 25 | Alexander | 27.6/16kV | Alex F3 | Wind storm damaged a single phase line on Hartin & Johnswood | Goulburn | Adverse Weather | Wind
3412 | 2003 | 5 | 7 | 0.56806 |  | 15 | 0 | 1 | Alexander |  | Alex F3 | Customer outage required to repair broken switch. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
18144 | 2011 | 5 | 13 | 0.25486 |  | 129 | 19 | 9 | Alexander | 27.6/16kV | Alex F3 | RX2010 A/R, blown cut-out at X35229 at 7 Savage | Goulburn | Foreign Interference | Bird
3471 | 2003 | 5 | 23 | 0.77083 |  | 290 | 203 | 100 | Alexander | 4.16kV | alex F3 | D. Jones reports insulator & rwb fuses at trans# 3312 have blown causing grass fire. Also at switch 414 red & blue fuses found open. | Kanata | Adverse Environment | Fire
3532 | 2003 | 6 | 7 | 0.077083 |  | 755 | 8063 | 2606 | Alexander | 27.6/16kV | Alex F3 | A motor vehicle accident at the corner of Hazeldean and Cedarow Court caused the Alexander F3 circuit to go to lockout. Switching was completed in sections to re-energize as many customers as possible. The pole was replaced and full power was restored. | Goulburn | Foreign Interference | Vehicle
3533 | 2003 | 6 | 7 | 0.37986 |  | 68 | 283 | 250 | Alexander DS | 27.6/16kV | Alex F3 | Outage required to restore repaired feeder section caused by MVA last evening as well as the customers that remained out. | Kanata | Foreign Interference | Vehicle
10640 | 2007 | 6 | 16 | 0.33333 |  | 702 | 23 | 2 | Alexander | 27.6/16kV | Alex F3 | Transformer 7555 at 110 Iber isolated & replaced with new transformer due to an oil leak. Nomenclature changed to TP4998. | Goulburn | Scheduled Outage | Repair
3610 | 2003 | 6 | 25 | 0.52361 |  | 19 | 5 | 15 | Alexander DS | 8/4.8kV | Alex F3 | Planned outage to transformers 8449R & 8450R on Ravenscroft Crt in Stittsville to place new 3 phase transformer i/s. | Goulburn | Scheduled Outage | Construction
5389 | 2004 | 6 | 28 | 0.25 |  | 45 | 525 | 700 | Alexander | 27.6/16kV | Alex F3 | Mark Brown found a R phase open at the station on the Alex F3. Found know apparent cause. Had a Hold off on it. | Goulburn | Unknown/Other | No Apparent Cause
20919 | 2012 | 7 | 4 | 0.23611 |  | 88 | 6 | 4 | Alexander | 27.6/16kV | ALEX F3 | RX2010 auto reclosed then transformer X35226 at 15 John Woods was found to be open, caused by a squirell contact | Goulburn | Foreign Interference | Animal
5449 | 2004 | 7 | 6 | 0.40208 |  | 203 | 304 | 90 | Alexandre | 27.6/16kV | Alex F3 | 90 customers affected in outage Brightside area in Goulbourn to remove 3 sectionalizers S27 S28 S26 | Goulburn | Scheduled Outage | Construction
5481 | 2004 | 7 | 12 | 0.78681 |  | 157 | 26 | 10 | Alexander | 27.6/16kV | Alex F3 | 24/7 reports squirrel found at base of pole. 10 Customers affected in power outage on Johnwoods in Stittsville. All power restored as of 21:30. | Goulburn | Foreign Interference | Animal
6967 | 2005 | 7 | 16 | 0.78125 |  | 165 | 468 | 170 | Alexander | 27.6/16kV | Alex F3 | Lightning strike caused a broken switch and blown cable connection at 681 B phase on Victor St in Stittsville. | Goulburn | Adverse Weather | Lightning
8788 | 2006 | 7 | 19 | 0.74306 |  | 70 | 101 | 100 | Alexander | 27.6/16kV | Alex F3 | The customers on Black Rd were off because they had to be transfer to a new supply from an out of phase rabbits. | Goulburn | Scheduled Outage | Repair
14787 | 2009 | 7 | 20 | 0.34375 |  | 120 | 669 | 650 | Alexander |  | ALEX F3 | White phase Fuse blown at S23681 due to blown arrester & defective switch at S17830. Customers picked up to S17830 and at S17830 switch and bracket were replaced. | Goulburn | Defective Equipment
5544 | 2004 | 7 | 21 | 0.42569 |  | 190 | 127 | 40 | Alexander DS | 27.6/16kV | Alex F3 | Planned outage to tx's fed from S25 to accommodate the removal of S25. | Goulburn | Scheduled Outage
8798 | 2006 | 7 | 22 | 0.053472 |  | 68 | 9 | 8 | Alexander | 27.6/16kV | Alex F3 | Transformer at 22 Lazy Knoll Crt blown fuse due to racoon. New fuse installed. | Goulburn | Foreign Interference | Animal
12936 | 2008 | 7 | 24 | 0.61319 |  | 129 | 2647 | 1500 | Alexander | 27.6/16kV | Alex F3 | A tree had fallen (by a contractor) on to two phases of the AlexF3, at the Amberwood Village Golf Club. During isolation of the o/h line, the crew accidentally hit the load side of the white phase, at S23681 which caused the white phase of the Alex F3 to open. Everyone ok, no repairs required. Hydro One sent to close in the Alex F3 white phase. Circuit isolated to remove tree, and power restored. | Goulburn | Tree Contacts | Tree Fallen
3794 | 2003 | 7 | 28 | 0.3875 |  | 39 | 13 | 20 | Alexander | 27.6/16kV | Alex F3 | To Change the the arrestor and switch on Martin St. | Goulburn | Scheduled Outage | Preventive Maintenance
8944 | 2006 | 8 | 10 | 0.34931 |  | 347 | 40 | 7 | Alexander | 27.6/16kV | Alex F3 | Transformer #GB020047 located at 6 Slate isolated due to service upgrade | Goulburn | Scheduled Outage | Preventive Maintenance
8997 | 2006 | 8 | 18 | 0.38542 |  | 106 | 11 | 6 | Alexander | 27.6/16kV | Alex F3 | The transformer 7982 on Alon St in Stittsville was isolate because it was leaking. | Goulburn | Scheduled Outage | Preventive Maintenance
8998 | 2006 | 8 | 18 | 0.39583 |  | 95 | 10 | 6 | Alexander | 27.6/16kV | ALEX F3 | At 09:30 Trans 7982 at 6 Alon St Stittsville isolated in order to replace leaking trans | Goulburn | Scheduled Outage | Repair
9045 | 2006 | 8 | 24 | 0.50764 |  | 67 | 1 | 1 | Alexander | 27.6/16kV | Alex F3 | Defective transformer TP2988 at 458 Landswood Way, Stittsville, was isolated to replace transformer, only 1 customer was affected because it is a new subdivision. | Goulburn | Defective Equipment
9050 | 2006 | 8 | 24 | 0.49306 |  | 120 | 2 | 1 | Alexander | 27.6/16kV | Alex F3 | Isolated and replaced defective transformer 2988 at 2988 Landswood Way | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
19246 | 2011 | 9 | 24 | 0.37847 |  | 490 | 3348 | 410 | Alexander | 27.6/16kV | Alex F3 | 48 Tx's from SC4528-CB4 isolated for elbow & insert upgrades. Granite Ridge area. | Goulburn | Scheduled Outage | Preventive Maintenance
17092 | 2010 | 10 | 10 | 0.8125 |  | 10 | 1 | 5 | Alexander | 27.6/16kV | Alex F3 | crew opened transformer X09339 at 6260 fernbank to replace burnt fuse barrel. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
17125 | 2010 | 10 | 17 | 0.30208 |  | 120 | 4 | 2 | Alexander | 8/4.8kV | Alex F3 | At 07:15 trans at 6670 FERNBANK RD GOU was isolated in order to make temp repairs to pole due to MVA | Goulburn | Foreign Interference | Vehicle
13562 | 2008 | 11 | 4 | 0.72639 |  | 4 | 28 | 425 |  | 27.6/16kV | Alex F3 | Mapping error caused outage to 25 transformers in Stittsville in the area of Dolomite & Fringwood. | Kanata | Human Element | Incorrect Records
13569 | 2008 | 11 | 6 | 0.45 |  | 131 | 22 | 10 | Alexander | 27.6/16kV | Alex F3 | Planned outage to Transformer 20073 at 51 Amberlakes Drive, in Stittsville. | Goulburn | Scheduled Outage
11686 | 2007 | 11 | 9 | 0.39514 |  | 472 | 236 | 30 | Alexander | 27.6/16kV | Alex F3 | Transformer 8450 Red isolated for Jim Leslie Utitlies to relocate transformer. 30 Customers affected on Ravencroft in Stittsville. | Goulburn | Scheduled Outage
4430 | 2003 | 11 | 12 | 0.38056 |  | 27 | 18 | 40 | Alexander | 27.6/16kV | Alex F3 | Transformers isolated to transfer them to a off phase supply. | Goulburn | Scheduled Outage
4493 | 2003 | 11 | 20 | 0.72917 |  | 120 | 6 | 3 | Alexander | 27.6/16kV | Alex F3 | Planned outage to 3 customers to 3 phase overhead transformer. | Goulburn | Scheduled Outage | Construction
4583 | 2003 | 12 | 10 | 0.39583 |  | 120 | 96 | 48 | Alexander | 27.6/16kV | Alex F3 | To replace elbows & inserts in transformers and re-arrange plant on pole. | Kanata | Scheduled Outage | Construction
4586 | 2003 | 12 | 10 | 0.54167 |  | 120 | 74 | 37 | Alexander | 27.6/16kV | Alex F3 | 4 transofrmers were isolated in Stittsville to change elbows & inserts in Stittsville. 37 Customers were effected in planned power outage. | Kanata | Scheduled Outage | Preventive Maintenance
7741 | 2005 | 12 | 16 | 0.54306 |  | 35 | 408 | 700 | Alex | 27.6/16kV | Alex F3 | D. McKay reports while removing elbow at S-3 in Stittville, Elbow flashed cauing Alex F3 blue phase reclosure to lock out. (Reclosure was blocked) D. McKay was trying to isolate transformer #6628 @ 60 Lone Meadow. Transformer was hit by a snow removal company. Transformer was placed back on pad, and reclosure closed at station. | Kanata | Human Element
9891 | 2006 | 12 | 29 | 0.11736 |  | 383 | 2523 | 800 | Alexander | 27.6/16kV | Alex F3 | Original problem was pole hit by vehicle, while switching to isolate broken pole incorrect mapping did not identify a switch that was opened in error and undersized fuses blew due to incorrect switching causing load to be picked up in an unexpected fashion. Mapping failed to indicate proper location of switches and fusses and actual fuse sizing was not recorded accurately. | Goulburn | Human Element | Switching Errors
9858 | 2006 | 12 | 18 | 0.72917 |  | 30 | 4 | 8 | Alexander | 27.6/16kV | Alex. F3 | Rob Longpre isolated TRF. @ 27 LazyNOL for service disc./rec. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
9859 | 2006 | 12 | 18 | 0.78472 |  | 60 | 8 | 8 | Alexander | 27.6/16kV | Alex. F3 | Rob Longpre isolated TRF. @ 27 LazyNoL To energize service @ same address | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
5286 | 2004 | 6 | 12 | 0.29861 |  | 110 | 20 | 11 | Alex F3 | 27.6/16kV | Alexander | Darcy reports S272 fuse found open also fuse to TX 2694 also found blown. D. Price reports S272 fuse now closed restoring load to TX2693. D. Price reports TX2693 now restored. D. Price reports vines growing up the pole & in the secondary. | Kanata | Foreign Interference | Foreign Object
6231 | 2005 | 2 | 24 | 0.59167 |  | 30 | 1 | 2 | Alexander | 27.6/16kV | Alexander F2 | Transformer 9676 isolated to change blown arrestor at 24 Canadian dr | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6243 | 2005 | 3 | 2 | 0.57639 |  | 19 | 2 | 5 | Alexander | 27.6/16kV | Alexander F2 | opened transformer 9672 to do switch maintenance; feeds customers, 1,2,3,4,48 Carlisle | Kanata | Scheduled Outage | Preventive Maintenance
6257 | 2005 | 3 | 10 | 0.31042 |  | 123 | 6 | 3 | Alexander | 27.6/16kV | Alexander F2 | Peter Barr opened trans 9327 at 1027 Moodie Dr to change a broken switch | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6312 | 2005 | 3 | 22 | 0.38472 |  | 106 | 2 | 1 | Alexander | 27.6/16kV | Alexander F2 | Transformer isolated at 6559 Hazeldean Rd to change a porcelain insulator | Kanata | Defective Equipment | Equipment Deterioration Due to Age
3310 | 2003 | 4 | 1 | 0.38681 |  | 23 | 23 | 60 | Alexander | 27.6/16kV | Alexander F2 | Energizing 6 new transformers on the W phase required customer interruption to approx. 60 customers on Sirocco Cres in Stittsville. | Goulburn | Scheduled Outage | Construction
3328 | 2003 | 4 | 10 | 0.36181 |  | 79 | 2902 | 2204 | Alexander | 27.6/16kV | Alexander F2 | 08:30 Recloser blocked by Hydro One for Hydro Ottawa. 08:31 hold off issued to Louie Lauzon for tree trimming in Stittsville. 08:41 all 3 phases of the Alex F2 opened. Tree Trimmers report back that they did not get into the lines with a limb. Cause Unknown. | Goulburn | Unknown/Other
13163 | 2008 | 8 | 28 | 0.54028 |  | 122 | 20 | 10 | Alexander | 27.6/16kV | Alexander F2 | TP2223 isolated at 385 West Ridge, to allow crew to raise transformer base. | Goulburn | Scheduled Outage
11228 | 2007 | 9 | 2 | 0.36806 |  | 55 | 1 | 1 | Alexander | 27.6/16kV | Alexander F2 | Transformer located at 8 Sweetnam isolated due to squirrel interference | Goulburn | Foreign Interference | Animal
9378 | 2006 | 10 | 4 | 0.46528 |  | 180 | 3 | 1 | Alexander | 27.6/16kV | Alexander F2 | O/H section of the Alex F2 at Hwy#7 & Jenkinson Rd was isolated for crew to remove a broken pole. Pole was pulled down by a dump truck that hit the guy wires. | Goulburn | Foreign Interference | Vehicle
19845 | 2012 | 1 | 17 | 0.40139 |  | 162 | 78 | 29 | Alexander | 27.6/16kV | Alexander F3 | At 9:38 crews isolated 3 transformers on James Lewis. 1 transformer was replaced and the other two had elbow and insert replacement. Alexander F3 ID# 19845 | Goulburn | Scheduled Outage
19855 | 2012 | 1 | 18 | 0.39306 |  | 82 | 10 | 7 | Alexander | 27.6/16kV | Alexander F3 | At 9:26 crew isolate TP8654 to replace a leaking transformer. Alexander F3. ID#19855 | Goulburn | Scheduled Outage
17522 | 2011 | 1 | 25 | 0.39653 |  | 50 | 82 | 100 | Alexander | 27.6/16kV | ALEXF2 | 10 transformers in the Hobin St area of Stittsville had to be interrupted in order to isolate the S5 pedestal due to non-vented elbows at the isolating points. | Goulburn | Scheduled Outage
6209 | 2005 | 2 | 15 | 0.61111 |  | 88 | 1 | 1 | Alexander | 27.6/16kV | AlexF2 | Red phase section of O/H line at Hwy 7 & Dwyer Hill rd was isolated to repair broken insulators. Customer was notified. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
13985 | 2009 | 2 | 16 | 0.76319 |  | 66 | 1 | 1 | Alexander | 27.6/16kV | ALEXF2 | Replaced blown fuse on switch feeding transformer X09575 at 6423 Hazeldean Rd | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
7962 | 2006 | 2 | 23 | 0.38333 |  | 299 | 1102 | 800 | ALEXANDER | 27.6/16kV | ALEXF2 | ALEX F2 RED PHASE TRIPPED DUE TO A BLOWN ELBOW ON XMER 20014R @ 16 BEVERLY IN STITSVILLE. FUSE FOUND BLOWN @ S35. FUSE REPLACED AND POWER RESTORED TO ALL CUSTOMERS. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
7971 | 2006 | 2 | 26 | 0.73611 |  | 199 | 1072 | 850 | Alexander | 27.6/16kV | ALEXF2 | Burnt Termination at S515R (Beverley & Main St) caused stress cone to fall onto S515W phase. Outage expanded due to abnormal open point at S23. (S23 non-vented elbows). Also during switching S515B switch broke, and was held by switch stick above the Janet King (44F3 cct). 44F3 Breaker opened by System, while they cleared S515B. | Goulburn | Defective Equipment
12260 | 2008 | 4 | 9 | 0.52083 |  | 90 | 15 | 10 | ALEXANDER DS |  | ALEXF2 | Transformer #20189 at 91 Sirocco isolated to allow for replacement of transformer | Goulburn | Scheduled Outage | Repair
17865 | 2011 | 4 | 9 | 0.63681 |  | 393 | 98 | 15 | Alexander | 27.6/16kV | AlexF2 | A defective transformer TP7769 @ 10 STEGGALL CRES was replace by the oncall crew. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17873 | 2011 | 4 | 11 | 0.25208 |  | 132 | 26 | 12 | Alexander | 27.6/16kV | AlexF2 | Transformer #X36388 located at 15 Conductor Ave opened due to lightning | Goulburn | Lightning | Direct Strike
18088 | 2011 | 5 | 3 | 0.66111 |  | 248 | 4 | 1 | Alexander | 27.6/16kV | AlexF2 | Transformer #X09562 located at 6310 Hazeldean Rd opened by crew due to back hoe hitting the neutral | Goulburn | Foreign Interference | Vehicle
6583 | 2005 | 5 | 21 | 0.31458 |  | 62 | 8 | 8 | Alexander | 27.6/16kV | ALEXF2 | Fused cut out to Transformer 5673 at 23 Jonathan Pack St in Stittsville was found blown due to animal contact (Crow) | Goulburn | Foreign Interference | Bird
18194 | 2011 | 5 | 21 | 0.029167 |  | 727 | 2715 | 485 | Alexander | 27.6/16kV | ALEXF2 | A auto re-close on RX2010 due to lightning caused S18407 red phase fuse was found blown crew patrolled line and found no apparent problem and S18407 red phase was closed and RX2010 auto re-closed a second time causing S18407 to blow again. Crew found a defective arrester and closed S18407 red phase was closed and RX2010 auto re-closed a third time causing S18407 to blow again. Crew found a suspect 3 phase dip and closed S18407 red phase and RX2010 auto re-closed a fourth time causing S18407 to blow again. Crew found a defective elbow at transformer 7125 at 1385 Main Street and closed S18407 red phase and held. Customers tranformer at 1385 Main Street had a defective insert. Alexarder (AlexF3) ID#18194 | Goulburn | Adverse Weather | Lightning
18217 | 2011 | 5 | 25 | 0.54167 |  | 119 | 157 | 79 | Alexander | 27.6/16kV | ALEXF2 | Transformers TP7163, TP7769, TP7770, TP7771, TP7171, TP7773 and TP7774 on Whallings and Stegal Cres were isolated to allow crew to replace elbows and inserts. 79 customers were affetected. Alexander (ALEXF2) | Goulburn | Scheduled Outage
10467 | 2007 | 5 | 28 | 0.53819 |  | 22 | 3 | 9 | Alexander | 27.6/16kV | ALEXF2 | 3 transformers on Spruce Ridge Road were interupted for switching purposes, switching on out of phase feeds, to isolate cable section at Hwy #7 for working clearance. | Goulburn | Scheduled Outage | Construction
20674 | 2012 | 6 | 2 | 0.33333 |  | 341 | 74 | 13 | Alexander | 27.6/16kV | ALEXF2 | 27kV transformer TP7794 at 114 Whalings was found to be defective. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
18287 | 2011 | 6 | 3 | 0.38125 |  | 140 | 128 | 55 | ALEXANDER | 27.6/16kV | ALEXF2 | Transformer TP7169, TP7166, TP7784, TP7783, TP7782, TP7781 on Sable Run Dr were isolated to allow crew to replace elbows and inserts. 55 Customers were affected. Alexander (ALEXF2) | Goulburn | Scheduled Outage
8454 | 2006 | 6 | 9 | 0.43056 |  | 155 | 28 | 11 | Alexander | 27.6/16kV | ALEXF2 | Isolated and replaced transformer 6547 at 19 Forest Heights due to oil leak | Goulburn | Scheduled Outage | Repair
8487 | 2006 | 6 | 15 | 0.19236 |  | 73 | 2 | 2 | Alexander | 27.6/16kV | AlexF2 | Tree trimming was required at 1876 STITTSVILLE Main st which caused the fuse to blow. | Goulburn | Tree Contacts | Inadequate Trimming
16342 | 2010 | 6 | 28 | 0.31042 |  | 83 | 6 | 4 | Alexander | 27.6/16kV | ALEXF2 | Replaced blown fuse at transformer X36387 at 15 Pullman Ave (Cause unknown) | Goulburn | Unknown/Other | No Apparent Cause
16376 | 2010 | 7 | 1 | 0.25903 |  | 180 | 30 | 10 | Alexander | 27.6/16kV | AlexF2 | A bird made contact with an O/H transformer causing the fus to blow at transformer X38789 at 12 Ember Glow court in Stittsville which caused the AlexF2 to auto. | Goulburn | Foreign Interference | Bird
12790 | 2008 | 7 | 4 | 0.45139 |  | 100 | 7 | 4 | Alexander DS | 27.6/16kV | ALEXF2 | Isolated transformer X09697 at 1194 Carp Rd to install new pole | Goulburn | Scheduled Outage | Repair
16399 | 2010 | 7 | 5 | 0.61944 |  | 509 | 2936 | 2000 | Alexander | 27.6/16kV | ALEXF2 | The Alexander F2 auto-reclosed due to vines covering transformer X36442 @ 17 Johnathen Pack. The F2 was carrying Alexander F3 load as well. During restoration, due to high load, blue and white phase fuses blew @ Alexander station. Hydro crew restored Alexander F3 circuit and Alexander F2 was then restored to normal. At 22:44 2 customers at 16 & 17 johnathen Pack called in to report they were still out of power. | Goulburn | Tree Contacts | Inadequate Trimming
14689 | 2009 | 7 | 9 | 0.70833 |  | 117 | 312 | 160 | Alexander | 27.6/16kV | AlexF2 | The switch 463 R phase on Carp Rd was under size so when load pick up it blew. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12837 | 2008 | 7 | 14 | 0.62778 |  | 66 | 9 | 8 | Alexander | 27.6/16kV | ALEXF2 | Transformer TP5237 @ 24 Ravenscroft was opened to clean an oil spill. | Goulburn | Scheduled Outage | Repair
18685 | 2011 | 7 | 17 | 0.80833 |  | 381 | 13608 | 2143 | Alexander |  | ALEXF2 | The RX2039 auto reclosed last night during the Wind and lightning storm. Alexander (ALEXF2). | Goulburn | Adverse Weather | Wind
18705 | 2011 | 7 | 18 | 0.10417 |  | 520 | 113 | 13 | Alexander | 27.6/16kV | ALEXF2 | Crew isolated ALEXF2 overhead section between SW1024 and TEMP 2011 on Hazeldean and Junkinson to remove trees and repair downed phase due to wind storm. | Goulburn | Adverse Weather
10917 | 2007 | 7 | 20 | 0.42153 |  | 58 | 7 | 7 | Alexander | 27.6/16kV | ALEXF2 | Crew found blown fuse on transformer GB1027 at 1139 Carp Rd (Cause unknowen) | Goulburn | Unknown/Other | No Apparent Cause
16573 | 2010 | 7 | 28 | 0.39722 |  | 90 | 16 | 11 | Alexander | 27.6/16kV | ALEXF2 | TP2229 at 325 Westridge was isolated to allow crews to replace a defective transformer. | Goulburn | Scheduled Outage | Repair
16600 | 2010 | 8 | 2 | 0.13333 |  | 178 | 6 | 2 | Alexander | 27.6/16kV | ALEXF2 | transformers 8732 and 8733 on Stittsville Main were isolated to allow crews to re-configure the underground cables into a new sectionalizer. | Goulburn | Scheduled Outage | Construction
16601 | 2010 | 8 | 2 | 0.28333 |  | 72 | 7 | 6 | Alexander | 27.6/16kV | AlexF2 | Transformer #X38775 located at 36 Ember Glow opened up due to squirrel contact | Goulburn | Foreign Interference | Animal
7070 | 2005 | 8 | 5 | 0.2875 |  | 286 | 38 | 11 | Alexander | 27.6/16kV | AlexF2 | Service cable faulted and burned thru causing transformer 20082 at 85 Abaca to blow its fuse. Bad service disconnected transformer refused and temporary service installed to 85 Abaca restoreing all load. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
11183 | 2007 | 8 | 29 | 0.50694 |  | 60 | 112 | 112 | Alexander | 27.6/16kV | ALEXF2 | failed conection to blue phase of switch # 56 on Hazeldean and Kitimar caused outage. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17058 | 2010 | 10 | 5 | 0.41667 |  | 180 | 84 | 28 | Alexander | 27.6/16kV | ALEXF2 | transformers 7496, 7620 and 7499 on albury, delamere and Steventon were isolated to allow crews to perform insert and elbow replacment. | Goulburn | Scheduled Outage | Preventive Maintenance
17059 | 2010 | 10 | 5 | 0.55278 |  | 51 | 2142 | 2520 | Alexander | 27.6/16kV | AlexF2 | RX2039 opened under holdoff due to a flash at transformer 7636 during switching, no injuries reported, cerew cleared and system office closed and picked all load back up. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17060 | 2010 | 10 | 5 | 0.57639 |  | 144 | 67 | 28 | Alexander | 27.6/16kV | AlexF2 | transformers 8059, 7637, 7636 on Kearnsley, Basford were isolated tio allow crews to replace elbows and inserts. | Goulburn | Scheduled Outage
15291 | 2009 | 10 | 22 | 0.25556 |  | 47 | 14 | 18 | Alexander | 27.6/16kV | AlexF2 | Transformer TP4907 at 6019 Hazeldean Road was isolated to allow contractor perform maintenance. | Goulburn | Scheduled Outage
17203 | 2010 | 11 | 1 | 0.64931 |  | 215 | 3947 | 2600 | Alexander | 27.6/16kV | ALEXF2 | SCADA indicated RX2039 auto/reclosed/auto and red phase indicated fault. Load could not be picked up by RX2039 but was eventually picked up in sections. No cause has been determined yet, cables at s55 are still out of service pending more testing. | Goulburn | Unknown/Other | No Apparent Cause
5872 | 2004 | 11 | 9 | 0.39236 |  | 470 | 78 | 10 | Alexander | 27.6/16kV | AlexF2 | Isolate transformer 20189 on Sirocco Cres to remove earth that contains oil under the transformer. | Goulburn | Scheduled Outage | Repair
11808 | 2007 | 12 | 4 | 0.74514 |  | 556 | 9 | 1 | Alexander | 8/4.8kV | ALEXF2 | 27kV white phase high side cuttout blown at 6463 Hazeldean. Defective 27kV to 8kV rabbit feeding transformer 3239 is defective. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
17395 | 2010 | 12 | 8 | 0.53125 |  | 45 | 8 | 11 | Alexander | 27.6/16kV | AlexF2 | Transformer #8060 located at 22 Kearnsley Way opened by crew to re-configure cable | Goulburn | Scheduled Outage | Construction
6059 | 2004 | 12 | 14 | 0.37986 |  | 360 | 162 | 27 | Alexander | 27.6/16kV | AlexF2 | Cable and transformer isolated to relocate transformer from customers laneway to front yard on Backway Stistville. | Goulburn | Scheduled Outage | Construction
15564 | 2009 | 12 | 27 | 0.53264 |  | 177 | 2312 | 2181 | Alexander | 27.6/16kV | AlexF2 | The primary O/H on the AlexF2 on Rothbourne fell, to make proper repair the remaining two phases were dump and then pick up by the AlexF3. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
9910 | 2007 | 1 | 9 | 0.47569 |  | 150 | 20 | 8 | Alexander | 27.6/16kV | AlexF3 | Isolated and replaced defective transformer 4831 at 7 Savage Dr | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
7816 | 2006 | 1 | 17 | 0.64861 |  | 427 | 87 | 27 | Alexander | 27.6/16kV | ALEXF3 | WHILE SWITCHING ON XMER 7936 CREW REMOVED DUST CAP FROM XMER AND CAP FLASHED TO GND. THE FLASH CAUSED S709 TO OPEN. XMERS 7936B, 7935B, 7934B OFF. ONE THIRD OF THE CUSTOMERS RETURNED WHEN S709 WAS CLOSED. XMER 7936 WAS DAMAGED AND IS TO BE REPLACED. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
7851 | 2006 | 1 | 24 | 0.58958 |  | 115 | 15 | 8 | Alexander | 27.6/16kV | ALEXF3 | Swich to transformer 2692 at 23 Savage opened due to animal contact (Squirrel) | Goulburn | Foreign Interference | Animal
3141 | 2003 | 1 | 25 | 0.39236 |  | 315 | 42 | 8 | Alexander | 27.6/16kV | AlexF3 | Called 24/7 crew to problem crew found blown arrestor not at problem of blown transformer.Crew changed arrestor and thought power was restored but after checking with customers it was revealed there was still a problem on a different transformer. The transformer cutout was then found open refused and closed all customers restored. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
7957 | 2006 | 2 | 20 | 0.53611 |  | 399 | 80 | 12 | ALEXANDER | 27.6/16kV | ALEXF3 | Transformer TP2237 on Black Bear Way in Stittsville faulted internally and was changed. | Goulburn | Defective Equipment
12070 | 2008 | 2 | 21 | 0.45278 |  | 190 | 4218 | 1400 | Alexander | 27.6/16kV | AlexF3 | All three phases at switch 276 on Hazeldean were found blown, circuit was patrolled but found nothing. | Goulburn | Unknown/Other
10137 | 2007 | 3 | 14 | 0.70833 |  | 521 | 2740 | 1020 | Alexander | 27.6/16kV | AlexF3 | tracking insulators flashed over at switch S29 in fringwood causing four fuses to operate. Switch was isolated for on call to replace defective insulators. Customers fed from switch remained out while repairs were being done. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
17796 | 2011 | 3 | 29 | 0.42847 |  | 2 | 0 | 9 | Alexander | 27.6/16kV | AlexF3 | Transformer #GB20113 located at 31 Harry Douglas opened by crew for switching to prepare for tomorrow to replace a primary switch | Goulburn | Scheduled Outage | Repair
17797 | 2011 | 3 | 29 | 0.44097 |  | 5 | 1 | 14 | Alexander | 27.6/16kV | ALEXF3 | Transformer GB020121 At 9 Azurite Cres isolated for switching to prepare for tomorrow to replace a primary switch | Goulburn | Scheduled Outage | Construction
20252 | 2012 | 3 | 29 | 0.375 |  | 165 | 69 | 25 | Alexander | 27.6/16kV | ALEXF3 | transformers 7936, 7935 and 7934 on Caribou in Stittsville were isolated to allow crews to perform maintenance on switches change transformer elbows | Goulburn | Scheduled Outage | Repair
17826 | 2011 | 4 | 3 | 0.79167 |  | 72 | 10 | 8 | Alexander | 27.6/16kV | ALEXF3 | Transformer X2693 @ rear of 8 Hartin opened, causing the RX2010 to auto-reclose | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
20268 | 2012 | 4 | 3 | 0.27083 |  | 280 | 47 | 10 | Alexander | 27.6/16kV | ALEXF3 | Replaced defective transformer TP2223 at 383 West Ridge Dr | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17831 | 2011 | 4 | 5 | 0.29167 |  | 63 | 3 | 3 | Alexander | 27.6/16kV | ALEXF3 | Transformer X10000 at 6001 Hazeldean rd was poen to allow crew to perfrom service upgrade. 3 Customer affected for 63 minutes. ALEX F3 27.6 KV | Goulburn | Scheduled Outage
15900 | 2010 | 4 | 7 | 0.32083 |  | 100 | 5334 | 3325 | Alexander | 27.6/16kV | ALEXF3 | RX2010 opened close coils are off the load side so no reclose was attempted, unable to close RX2010 so switching was performed to close the bypass and switch the recloser out while restoring load. Patrol revealed no apparent cause and focus went to getting the RX2010 closed | Goulburn | Unknown/Other | No Apparent Cause
4980 | 2004 | 4 | 8 | 0.49375 |  | 29 | 48 | 100 | Alexander | 27.6/16kV | alexF3 | While isolating section of red phase cable insert at 4496R-1 was loose and crew did not want to pull it live. 4494r-1 to 4495 was pulled to take section off potential and pull and tighten 4496R-1insert and continue with planned outage. | Goulburn | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
15909 | 2010 | 4 | 8 | 0.38333 |  | 178 | 326 | 110 | Alexander | 27.6/16kV | ALEXF3 | Temporary outage to allow crews to cutover customers to new O/H line. | Goulburn | Scheduled Outage | Construction
15914 | 2010 | 4 | 9 | 0.48889 |  | 14 | 776 | 3326 | Alexander | 27.6/16kV | ALEXF3 | The RX2010 trip under O/H, no calls came in with an apparent cause, the crew patrolled the O/H on Hazeldean where there is construction but found nothing. | Goulburn | Unknown/Other
15953 | 2010 | 4 | 19 | 0.36667 |  | 41 | 3 | 4 | Alexander | 8/4.8kV | ALEXF3 | While isolating a section of the ALEXF3 overhead 4 customers were interrupted in order to transfer them to another phase. | Ottawa | Scheduled Outage | Construction
18078 | 2011 | 5 | 1 | 0.65278 |  | 279 | 810 | 631 | Alexander | 27.6/16kV | ALEXF3 | Auto re-close on RX2010 then switch gear S12 blue phase was found damaged, load droped and restored to avoid parallel though damaged switch gear. Alexander (ALEXF3) ID#18078 | Goulburn | Defective Equipment
20436 | 2012 | 5 | 1 | 0.875 |  | 1 | 0 | 10 | Alexander | 27.6/16kV | ALEXF3 | Switching error cause transformer 20071 @ 45 Amberlakes to be interrupted momentarily. | Goulburn | Human Element | Switching Errors
16168 | 2010 | 5 | 31 | 0.40486 |  | 90 | 28 | 19 | Alexander | 8/4.8kV | ALEXF3 | Transformers X35229 and X35249 on Savage Dr. Were interrupted as part of an isolation to allow crews to rearrange the overhead | Ottawa | Scheduled Outage | Construction
14486 | 2009 | 6 | 8 | 0.28542 |  | 92 | 26 | 17 | Alexander DS | 27.6/16kV | AlexF3 | Transformer #X35229 located at 9 Savage isolated due to squirrel contact | Goulburn | Foreign Interference | Animal
8489 | 2006 | 6 | 15 | 0.38333 |  | 125 | 23 | 11 | Alexander | 27.6/16kV | AlexF3 | Transformer 6628 on Lonemeadow for transformer replacement. | Goulburn | Scheduled Outage | Preventive Maintenance
14554 | 2009 | 6 | 17 | 0.32153 |  | 52 | 7 | 8 | Alexander | 27.6/16kV | AlexF3 | Transformer #X37179 located at 28 Poole Creek Cres isolated due to squirrel contact | Goulburn | Foreign Interference | Animal
14587 | 2009 | 6 | 21 | 0.32153 |  | 679 | 2401 | 1271 | Alexander DS | 27.6/16kV | ALEXF3 | At 7:43am customers off of the Alexander DS Blue Phase circuit were calling in with no power calls. Hydro One enroute to Alexander DS station to help with restoration. Derrick Burns reports transformer fuse at X09889 on the corner of Alon and Johnwoods Street. All power restored accept for services off of transformer X09889 at 9:35am. (Alexander) (ALEXF3). ID#14587. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
8609 | 2006 | 6 | 27 | 0.71389 |  | 168 | 34 | 12 | ALEXANDER | 27.6/16kV | ALEXF3 | CREW FOUND S127 OPEN FEEDING 27 TRAFALGAR DR. OPEN, CREW CHANGE ARRESTOR AND REFUSED SWITCH TO PICK UP 12 CUSTOMERS. | Goulburn | Adverse Weather | Wind
16343 | 2010 | 6 | 28 | 0.38542 |  | 20 | 3 | 8 | Alexander | 27.6/16kV | ALEXF3 | Rplaced blown fuse at transformer GB2693 at 4 Hartin St (Squirrel contact) | Goulburn | Foreign Interference | Animal
18554 | 2011 | 6 | 28 | 0.90903 |  | 82 | 27 | 20 | Alexander | 27.6/16kV | ALEXF3 | S25956 located at 33 Basswood opened up due to lightning storm | Goulburn | Adverse Weather | Lightning
10845 | 2007 | 7 | 11 | 0.44097 |  | 77 | 13 | 10 | Alexander | 27.6/16kV | ALEXF3 | T8234W at 31 Kathleen was isolated to replace defective elbows and inserts. | Goulburn | Scheduled Outage | Repair
6907 | 2005 | 7 | 12 | 0.42083 |  | 368 | 6 | 1 | Alexander | 27.6/16kV | AlexF3 | Burnt connection at switch S28007 that feeds transformer 20018 @ Gaurding Angle school at 4 Baywood Cres. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
18835 | 2011 | 7 | 27 | 0.39167 |  | 79 | 14 | 11 | Alexander | 27.6/16kV | ALEXF3 | transformer TP2225 at 356 Westridge was isolated to repair grading issues. | Goulburn | Scheduled Outage | Preventive Maintenance
18837 | 2011 | 7 | 27 | 0.46944 |  | 76 | 14 | 11 | Alexander | 27.6/16kV | ALEXF3 | transformer TP2236 at 162 coyote was isolated to repair grading issues. | Goulburn | Scheduled Outage | Preventive Maintenance
5609 | 2004 | 8 | 3 | 0.94097 |  | 43 | 8 | 11 | Alexander | 27.6/16kV | AlexF3 | Transformer fuse at TX 2976 opened due to squirrel contact. | Goulburn | Foreign Interference | Animal
13000 | 2008 | 8 | 4 | 0.94306 |  | 81 | 96 | 71 | Alexander | 27.6/16kV | ALEXF3 | S891 red phase @ Johnwoods and Alon found blown. 24/7 crew found no fault indicators flagged and performed switching to backfeed red phase transformers in loop and all customers power restored. Isolation of first cable from dip S891 provided for meggaring next day as 2 calls still pending for 24/7. | Goulburn | Unknown/Other | No Apparent Cause
11070 | 2007 | 8 | 15 | 0.80278 |  | 169 | 56 | 20 | ALEXANDER | 27.6/16kV | ALEXF3 | Transformer #GB002976 at 20 Basswood isolated to refuse transformer | Goulburn | Foreign Interference | Bird
5728 | 2004 | 8 | 27 | 0.40972 |  | 108 | 32 | 18 | Alexander | 27.6/16kV | AlexF3 | TP 2204 and TP2205 on Hartsmere and Friendly (south Stittsville) out to repair ground grid on 3 single phase transformers. | Goulburn | Scheduled Outage | Preventive Maintenance
9072 | 2006 | 8 | 27 | 0.48611 |  | 83 | 29 | 21 | Alexander | 27.6/16kV | AlexF3 | Crew found Transformer fuse open (2694) feeding Hartin St. and Johnwoods. Caused S272B to open. | Goulburn | Foreign Interference | Animal
13162 | 2008 | 8 | 28 | 0.375 |  | 135 | 18 | 8 | ALEXANDER | 27.6/16kV | ALEXF3 | Isolated and replaced transformer TP2222 at 393 West Ridge Dr | Goulburn | Scheduled Outage | Preventive Maintenance
15056 | 2009 | 9 | 5 | 0.30208 |  | 95 | 16 | 10 | Alexander | 27.6/16kV | ALEXF3 | Replaced blown undersized fuse at transformer X35229 at 9 Savage Dr | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
15107 | 2009 | 9 | 15 | 0.44306 |  | 343 | 74 | 13 | Alexander | 27.6/16kV | ALEXF3 | TP6391 at 77 Kathleen Cres was isolated for Oil Spill Remediation | Goulburn | Scheduled Outage
13299 | 2008 | 9 | 28 | 0.34653 |  | 171 | 14 | 5 | Alexander | 27.6/16kV | AlexF3 | A squirrel made contact with transformer X35229 causing the fuse blow at 9 Savage. | Goulburn | Foreign Interference | Animal
9451 | 2006 | 10 | 17 | 0.56806 |  | 240 | 735 | 600 | ALEXANDER | 27.6/16kV | ALEXF3 | Alexander F3 blue phase breaker found open at Alexander. Blown cut-out 272 also found opened. H1 closed blue phase recloser, restoring load to 572 customers. At 14:44, 26 customers remain without power until O/H pails are checked. Dective lightning arrester on overhead line. Hydro One crew called to close Alex F3 at 13:45. | Goulburn | Unknown/Other | No Apparent Cause
13563 | 2008 | 11 | 4 | 0.80694 |  | 63 | 7 | 7 | Alexander | 27.6/16kV | ALEXF3 | 27kv padmount transformer 20044 at 40 Fieldspar was knocked off its pad somehow and had to be isolated to replace it | Goulburn | Foreign Interference | Vehicle
9609 | 2006 | 11 | 6 | 0.48403 |  | 33 | 4 | 8 | Alexsnder | 27.6/16kV | AlexF3 | Scott changing trf. sw. @ 61 Fernbank | Goulburn | Scheduled Outage | Repair
13578 | 2008 | 11 | 8 | 0.34583 |  | 107 | 130 | 73 | Alexander | 8/4.8kV | ALEXF3 | Primary insulator flashed across at X11742 (6420 Flewelyn), required isolation and replacement | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
5969 | 2004 | 12 | 4 | 0.55556 |  | 130 | 65 | 30 | Alexander | 12/7.2kV | ALEXF3 | S415 white phase switch cut found broken on fridgewood. Outage affected approx 30 customers ( 5 O/H transformers). | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
9820 | 2006 | 12 | 9 | 0.67361 |  | 215 | 22 | 6 | Alexander | 27.6/16kV | AlexF3 | Squirrell contact in the rear of 14 Lazy Knoll. | Kanata | Foreign Interference | Animal
15577 | 2009 | 12 | 26 | 0.75 |  | 195 | 5963 | 3767 | Alexander | 27.6/16kV | ALEXF3 | Customer calls in Stittsville indicated ALEXF3 had a phase out. Hydro Ottawa crews patrolled overhead until Hydro One crew arrived to inspect Alexander Sub and found the High side White phase of transformer blown. Transformer bus was unloaded causing full outage to ALEXF3 for duration of fuse replacement. | Goulburn | Tree Contacts
16743 | 2010 | 8 | 16 | 0.17153 |  | 181 | 3 | 1 | Alexander | 27.6/16kV | ALEXF4 | Lightning caused switch 1327 to open. | Goulburn | Adverse Weather | Lightning
19391 | 2011 | 10 | 16 | 0.23958 |  | 405 | 81 | 12 | Alexander | 27.6/16kV | AlexF4 | A9M3, A9M5 and a section of 624F1 circuits were isolated at Terry Fox and Richardson Side Rd to allow Hydro One to replace poles and move conductors and to allow Hydro Ottawa crews to remove A9M3-1 switch and install new VBM switches @ 76M3-1 and 76M3-2. Stations affected were Alexander, Carp, Beaverbrook, Janet King, Munster and Kanata. Most of the customers had been transfered prior to outage if possible. | Goulburn | Scheduled Outage | Preventive Maintenance
5113 | 2004 | 5 | 7 | 0.37292 |  | 29 | 3388 | 7009 | King Edward | 115kV | all of TK | Hydro One T3 transformer at King Edward tripped from gas protection causing A4K circuit to trip. An A4K terminal breaker at Hawthorne went into breaker fail causing the circuit to lock out instead of reclose. The King Edward T4 transformer was removed from service earlier for planned mtce by H1. With the two transfomers O/S all our customers fed from King Edward station were without power. Overbrook T2 transformer was also O/S but no load was affected. The T4 transformer at King Edward was placed back I/S as well as the A4K circuit restoring all load at King Edward & Moulton. The T3 transfomer which caused the outage is still O/S for further investigation by H1. See ID #5115 for Moulton power outage. | Ottawa | Loss of Supply | HEPC Station Fault
4756 | 2004 | 2 | 3 | 0.4 |  | 62 | 26 | 25 | AM | 4.16kV | AM02 | An o/h Tx was opened to install new equipment at 408 Arlington. | Ottawa | Unknown/Other
19953 | 2012 | 2 | 3 | 0.32292 |  | 19 | 4 | 12 | Cambridge | 4.16kV | AM02 | Transformer #X31820 located at 746 Gladstone opened by crew to hook up new customer | Ottawa | Scheduled Outage | Construction
7887 | 2006 | 2 | 5 | 0.065972 |  | 868 | 99 | 299 | Cambridge | 4.16kV | AM02 | Heavy rain & winds caused pole fire at corner of Cambridge & Arlington. Two phases of a three phase cutout feeding P259 opened causing circuit to auto reclose. Circuit was opened for fire dept to extinguish fire and crew to disconnect three phase switches. Only Queensway Lighting was affected for the duration of outage to P259. Temporary repairs were made to pole & switches. | Ottawa | Adverse Environment
4803 | 2004 | 2 | 19 | 0.38542 |  | 93 | 19 | 12 | Cambridge | 4.16kV | AM02 | Scheduled outage at transformer OTT 1095 at 355 Cambridge to relocate services. | Ottawa | Scheduled Outage | Preventive Maintenance
12073 | 2008 | 2 | 22 | 0.39583 |  | 160 | 77 | 29 | CAMBRIDGE | 4.16kV | AM02 | TRANSFORMER #K01679 AT 11 WILLOW ISOLATED TO ALLOW FOR POLE CHANGE | Ottawa | Scheduled Outage | Preventive Maintenance
4819 | 2004 | 2 | 24 | 0.40486 |  | 182 | 52 | 17 | AM | 4.16kV | AM02 | P391 on Arthur Lane was isolated to break away concrete at riser pole. | Ottawa | Scheduled Outage | Construction
4824 | 2004 | 2 | 25 | 0.40556 |  | 162 | 81 | 30 | AM | 4.16kV | AM02 | Cables to V182 at 219 Bell st N were isolated for relocation. | Ottawa | Scheduled Outage | Construction
17690 | 2011 | 3 | 9 | 0.55903 |  | 49 | 31 | 38 | Cambridge | 4.16kV | AM02 | Transformer X31818 at 333 Cambridge St. N isolated to allow for new service | Ottawa | Scheduled Outage | Construction
4036 | 2003 | 6 | 23 | 0.56806 |  | 26 | 4 | 9 | Cambridge | 4.16kV | Am02 | D'arcy Provost reports broken insulator on TX#4101 at 5258 MaClean. Transformer isolated to replace insulator. | Ottawa | Defective Equipment
6951 | 2005 | 7 | 14 | 0.4125 |  | 54 | 179 | 199 | Cambridge | 4.16kV | AM02 | AM02 circuit was opened to allow crew to repair downed phase at 201 bell st. caused by storm activity. | Ottawa | Adverse Weather | Lightning
5586 | 2004 | 7 | 30 | 0.94028 |  | 202 | 7 | 2 | Cambridge | 4.16kV | AM02 | Primary on Arthur Lane behind 211 & 219 Bell St. came down interupting power to V182 on AM02. Sparking hot line clamp. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8957 | 2006 | 8 | 13 | 0.14583 |  | 170 | 17 | 6 | Cambridge | 13.2kV | AM02 | Fire at 188 Bell S North. Transformer was opened at this location. | Ottawa | Adverse Environment | Fire
9018 | 2006 | 8 | 22 | 0.39931 |  | 30 | 4 | 9 | Cambridge | 4.16kV | AM02 | Transformer OTT199 at 438 Arlington Ave was isolated to replace triplex service | Ottawa | Scheduled Outage | Repair
11243 | 2007 | 9 | 4 | 0.39583 |  | 120 | 18 | 9 | CAMBRIDGE | 13.2kV | AM02 | Transformer #OTT1088 at 273 Cambrdge St isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
4071 | 2003 | 9 | 8 | 0.56806 |  | 26 | 4 | 9 | Cambridge | 4.16kV | AM02 | Transformer isolated to repair broken insulators. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9285 | 2006 | 9 | 23 | 0.82431 |  | 57 | 6 | 6 | Cambridge | 4.16kV | AM02 | Defective cutout replaced feeding 7 Eleven at Gladstone & Bell. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13309 | 2008 | 10 | 1 | 0.58819 |  | 53 | 9 | 10 | Cambridge | 4.16kV | AM02 | Isolated transformer X21508 at 113 Bell st to replace down guy | Ottawa | Scheduled Outage | Emergency Services Request
7417 | 2005 | 10 | 2 | 0.85764 |  | 20 | 1 | 4 | Cambridge | 4.16kV | AM02 | D. Jones reports transformer open at 409 Bronson ave to reconnect service to building. | Ottawa | Scheduled Outage | Repair
19555 | 2011 | 11 | 11 | 0.38194 |  | 62 | 13 | 13 | Cambridge | 4.16kV | AM02 | Transformer X31820 at 746 Gladstone Ave isolated to allow for transformer upgrade | Ottawa | Scheduled Outage | Construction
4441 | 2003 | 11 | 13 | 0.68472 |  | 7 | 35 | 299 | Cambridge | 4.16kV | AM02 | Connection let go on red phase of AM02. Breaker opened manually to allow repairs. | Ottawa | Adverse Weather | Wind
4547 | 2003 | 12 | 2 | 0.52083 |  | 40 | 3 | 5 | Cambridge |  | AM02 | Transformer @ 426 arlington was opened to update plant. | Ottawa | Scheduled Outage | Preventive Maintenance
11845 | 2007 | 12 | 13 | 0.53819 |  | 50 | 26 | 31 | Cambridge | 4.16kV | AM02 | Transformer #K01679 located at 11 Willow isolated to upgrade to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
11849 | 2007 | 12 | 14 | 0.55556 |  | 59 | 10 | 10 | Cambridge | 4.16kV | AM02 | Transformer #OTT6679 located at 22 Willow St isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
9896 | 2007 | 1 | 2 | 0.46181 |  | 20 | 3 | 8 | Cambridge | 4.16kV | AM03 | Glen Carswell isolated the TRF. @ 170 Cambridge to replace a dective cutout | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4821 | 2004 | 2 | 24 | 0.39583 |  | 180 | 51 | 17 | Cambridge | 4.16kV | AM03 | Transformer P00391 opened to relocate service. 17 Customers effected in power outage. | Ottawa | Scheduled Outage | Construction
7995 | 2006 | 3 | 8 | 0.42014 |  | 80 | 31 | 23 | CAMBRIDGE | 4.16kV | AM03 | ISOLATED TRANSFORMER OTT229 AT 143 ARTHUR ST TO RE-LOCATE TRIPLEX SERVICES | Ottawa | Scheduled Outage | Construction
12560 | 2008 | 6 | 6 | 0.47917 |  | 60 | 17 | 17 | Cambridge | 4.16kV | AM03 | Isolated transformer X31406 at 178 Cambridge St to repair broken transformer bracket | Ottawa | Scheduled Outage | Preventive Maintenance
18382 | 2011 | 6 | 10 | 0.54306 |  | 23 | 10 | 26 | CAMBRIDGE | 4.16kV | AM03 | X31412 isolated at 141 Arthur St. isolated to make repairs on 347/600V system - cust lost a phase | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6705 | 2005 | 6 | 13 | 0.4375 |  | 90 | 8 | 5 | Cambridge | 4.16kV | AM03 | Isolated Transformer # 1406 at 57 Arthur as it is a leaker | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8963 | 2006 | 8 | 14 | 0.375 |  | 30 | 5 | 10 | Cambridge | 4.16kV | AM03 | Isolated transformer OTT 1086 at 255 Cambridge St to install new service | Ottawa | Scheduled Outage | Construction
15044 | 2009 | 9 | 1 | 0.47222 |  | 48 | 11 | 14 | CAMBRIDGE | 4.16kV | AM03 | Transformer X31418 at 55 Christie isolated to allow for a new service | Ottawa | Scheduled Outage | Repair
11473 | 2007 | 10 | 5 | 0.54167 |  | 120 | 52 | 26 | Cambridge | 4.16kV | AM03 | at 13:00 trans at 422 Bronson was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15548 | 2009 | 12 | 24 | 0.58333 |  | 30 | 10 | 21 | Cambridge | 4.16kV | AM03 | Transformer X31420 at Bronson & Cristie isolated by request of OFD due to fire at 346 Bronson. Cambridge (AM03) | Ottawa | Adverse Environment | Fire
3095 | 2003 | 1 | 2 | 0.6875 |  | 50 | 4 | 5 | Cambridge | 4.16kV | AM04 | D. Honey reports transformer at 327 Bell st South opened to renew connections, and replace hot line clamp. Customers had flickering lights. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7822 | 2006 | 1 | 18 | 0.96875 |  | 37 | 59 | 96 | Cambridge | 4.16kV | AM04 | Crew replaced a defective centre phase switch on three phase transformer feeding customers at 675 and 673 Somerset at corner of Bronson & Somerset. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14244 | 2009 | 4 | 25 | 0.80972 |  | 129 | 254 | 118 | Cambridge | 4.16kV | AM04 | AM04 breaker tripped during high winds, heavy rain & lightning. No permanent problem was found. | Ottawa | Adverse Weather
16310 | 2010 | 6 | 21 | 0.51736 |  | 80 | 7 | 5 | Cambridge | 4.16kV | AM04 | Transformer X25733 at 21 Cambridge was isoalted to replace broken cutout. | Ottawa | Scheduled Outage
20825 | 2012 | 6 | 21 | 0.80347 |  | 357 | 357 | 60 | Cambridge | 4.16kV | AM04 | 11 primrose, crews found a defective transformer, possible lightning strike during a storm. | Ottawa | Adverse Weather | Lightning
12819 | 2008 | 7 | 11 | 0.23472 |  | 57 | 2 | 2 | Cambridge | 4.16kV | Am04 | Transformer at 661 somerset was isolated to allow crews to renew connection at this location. | Ottawa | Scheduled Outage | Repair
18768 | 2011 | 7 | 17 | 0.80764 |  | 10 | 42 | 253 | Cambridge | 4.16kV | AM04 | AM04 Tripped and was closed with success 10 minutes later | Ottawa | Adverse Weather
4257 | 2003 | 10 | 14 | 0.48403 |  | 23 | 3 | 7 | Cambridge | 4.16kV | AM04 | Planned outage? | Ottawa | Scheduled Outage
15665 | 2010 | 1 | 18 | 0.54167 |  | 18 | 4 | 15 | Cambridge | 4.16kV | AM05 | Transformer #X31428 located at 25 Lorne isolated for service upgrade | Ottawa | Scheduled Outage | Construction
3139 | 2003 | 1 | 25 | 0.44444 |  | 225 | 825 | 220 | Cambridge |  | AM05 | Opened AM05 circuit for fire dept. for arial devices to fight fire at 113 and 111 Primrose. | Ottawa | Scheduled Outage | Emergency Services Request
12003 | 2008 | 2 | 1 | 0.90069 |  | 348 | 70 | 12 | Cambridge | 4.16kV | AM05 | At 9:37pm, customers in the area of 42 Primrose reported of no power, 24-7 crews dispatched and reported that there is a defective transformer. On call came in and replace 37.5kVA transformer. 12 customers affected for 348 min. ID#12003. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6466 | 2005 | 4 | 26 | 0.54167 |  | 90 | 16 | 11 | Cambridge | 4.16kV | AM05 | Transformer #OTT5064 at 114 Primrose Ave isolated due to pole replacement | Ottawa | Scheduled Outage | Repair
15994 | 2010 | 4 | 26 | 0.40625 |  | 35 | 4 | 7 | Cambridge | 4.16kV | AM05 | Transformer #X31426 located at 49 Lorne Ave opened for crew to replace defective hot line clamp and cut out. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5238 | 2004 | 6 | 1 | 0.51389 |  | 153 | 71 | 28 | Cambridge | 4.16kV | AM05 | Transformer 55D2A-0518 isolated to to replace defective transformer at 135 Lorne Ave. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18346 | 2011 | 6 | 8 | 0.7625 |  | 39 | 165 | 254 | Cambridge |  | AM05 | AM05 circuit was isolated to allow crews to reapair a broken conductor on Aurther and Sommerset. | Ottawa | Adverse Weather
18533 | 2011 | 6 | 27 | 0.41667 |  | 140 | 40 | 17 | Cambridge | 4.16kV | AM05 | Isolated transformer X30134 at 90 Cambridge St for a service up-grade | Ottawa | Scheduled Outage | Construction
6991 | 2005 | 7 | 18 | 0.8625 |  | 33 | 3 | 5 | Cambridge | 4.16kV | AM05 | At 20:42 Trans @ 15 Arthur isolated to replace defective connections | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11244 | 2007 | 9 | 4 | 0.52778 |  | 158 | 26 | 10 | Cambridge | 4.16kV | AM05 | At 12:40 trans at 73 Cambridge was isolated in order for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15179 | 2009 | 9 | 28 | 0.38889 |  | 100 | 8 | 5 | Cambridge | 4.16kV | AM05 | Transformer # X30133 located at 79 Cambridge St N isolated for transformer upgrade | Ottawa | Scheduled Outage | Construction
19469 | 2011 | 10 | 26 | 0.35417 |  | 20 | 5 | 15 | Cambridge | 4.16kV | AM05 | Trans X25729 at 19 Perkins St was isolated for sec service work | Ottawa | Scheduled Outage | Preventive Maintenance
12163 | 2008 | 3 | 20 | 0.53819 |  | 40 | 1 | 1 | Cambridge | 4.16kV | AM06 | concrete guard on dip pole had been knocked off, duct was smashed & wires exposed. Pole was roped. Crew made temporary repairs as cable was accesable to grab. Transformer P179 opened and temporary repairs made. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6367 | 2005 | 4 | 5 | 0.083333 |  | 290 | 633 | 131 | Cambridge | 4.16kV | AM06 | AM06 circuit was opened for fire dept to fight fire at 807 Somerset. | Ottawa | Adverse Environment | Fire
6400 | 2005 | 4 | 12 | 0.41667 |  | 35 | 2 | 3 | Cambridge | 4.16kV | AM06 | Power interrupted to O/H line section on Middle St in order to remove duplicate dip cable fro poles. 3 customers the Chaudiere workshop, the Legion & the Rock Climbing building were affected. | Ottawa | Scheduled Outage | Construction
8166 | 2006 | 4 | 19 | 0.56944 |  | 90 | 12 | 8 | Cambridge | 4.16kV | AM06 | Transformer at 247 Booth St was isolated to replace pole | Ottawa | Scheduled Outage | Construction
8169 | 2006 | 4 | 20 | 0.20833 |  | 149 | 50 | 20 | Cambridge | 4.16kV | AM06 | 2 overhead transformers at Booth & Somerset were interrupted in order to transfer plant to new poles. | Ottawa | Scheduled Outage | Construction
8173 | 2006 | 4 | 20 | 0.40625 |  | 160 | 27 | 10 | Cambridge | 4.16kV | AM06 | Larry of K Line opened transformer 55D2A-0158 at 261 Booth in order to change a transformer | Ottawa | Scheduled Outage | Repair
8190 | 2006 | 4 | 26 | 0.20833 |  | 175 | 58 | 20 | Cambridge | 4.16kV | AM06 | Overhead transformers at Booth & Spruce was interrupted in order to transfer plant to new pole. | Ottawa | Scheduled Outage | Preventive Maintenance
14254 | 2009 | 4 | 27 | 0.66667 |  | 146 | 406 | 167 | Cambridge | 4.16kV | AM06 | There was primary down on Somerset @ Empress, the entire circuit was isolated to make repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16114 | 2010 | 5 | 20 | 0.98958 |  | 13 | 2 | 10 | Cambridge | 4.16kV | AM06 | Transformer #X31419 @ 70 Bell St was opened to allow crew to disconnect secandory service due to working fire. | Ottawa | Adverse Environment | Fire
11082 | 2007 | 8 | 16 | 0.18889 |  | 785 | 1444 | 131 | Cambridge | 4.16kV | AM06 | Fire Department requested overhead off for fire at 287 Somerset( at Booth) Temp 89 installed and customers along Somerset and south on Booth restored. All customers off again at 17:34 to allow switching to restore power to all customers. Customers on Booth north of Somerset being supplied fro AM05. | Ottawa | Adverse Environment | Fire
3956 | 2003 | 8 | 27 | 0.92361 |  | 8 | 2 | 12 | Cambridge | 4.16kV | AM06 | Crew opened transformer at 797 Somerset feeding 20 people on Booth and Somerset to disconnect service to 290 Booth at request of fire dept. 8 customers will remain out. | Ottawa | Scheduled Outage | Emergency Services Request
9549 | 2006 | 10 | 29 | 0.73889 |  | 112 | 245 | 131 | Cambridge | 4.16kV | AM06 | Circuit tripped again with reclosure blocked. Extensive patrol did not reveal any obvious cause for trips. Circuit was placed back in service with reclosure blocked. | Ottawa | Adverse Weather | Wind
9550 | 2006 | 10 | 29 | 0.84444 |  | 141 | 308 | 131 | Cambridge | 4.16kV | AM06 | Circuit tripped again with reclosure blocked. Another patrol revealed loose span guys as the possible cause. Span guys were tightened & circuit placed back in sevice with reclosure blocked. | Ottawa | Adverse Weather | Wind
4657 | 2003 | 12 | 26 | 0.10069 |  | 239 | 506 | 131 | Cambridge | 4.16kV | AM06 | Two phases of AM06 came down on Sommerset between Arthur & Cambridge. AM06 autoreclosed and no load was showing on White & Blue phases. The breaker was opened by SCADA. Repairs were made and the breaker closed at 04:58 but did not hold. Patrol found a second problem of a lead blowing ion the wind at Sommerset & Empress. The lead was replaced and power restored. The crew reported the conductor may have let go at the location where grounds had been previously applied to removed some line openers. | Ottawa | Unknown/Other | No Apparent Cause
18331 | 2011 | 6 | 8 | 0.58542 |  | 31 | 633 | 1226 | Cambridge | 4.16kV | AMT1 | Cambirdge AMT1 open under gas protection due to accumulation of gas in the AMT1 main tank. 1226 customers were affected. Cambridge (AMT1) | Ottawa | Defective Equipment
14147 | 2009 | 4 | 6 | 0.38333 |  | 159 | 117 | 44 | Cahill | 4.16kV | AN03 | K77 transformer at 820 Cahill isolated to allow crews to change transformer, insulators and remove asbestos boards. | Ottawa | Scheduled Outage | Repair
10061 | 2007 | 2 | 24 | 0.64583 |  | 35 | 2 | 4 | Cahill | 4.16kV | AN04 | Isolated transformer OTT 5887 at 3253 Southgate Rd to replace triplex service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6428 | 2005 | 4 | 19 | 0.59653 |  | 101 | 29 | 17 | AN | 4.16kV | AN04 | Replaced defective blue phase cut-out to K788 at 12 Brenda. Normal open point was abnormal, K787 also affected. Normal open now restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18065 | 2011 | 4 | 30 | 0.53889 |  | 49 | 298 | 365 | Cahill | 4.16kV | AN04 | AN04 circuit was isolated to allow crew to remove a tree from the line. 365 customers were affected for minutes. Cahill (AN04) ID# 18065 | Ottawa | Tree Contacts | Tree Fallen
12424 | 2008 | 5 | 10 | 0.68056 |  | 77 | 27 | 21 | Cahill | 4.16kV | AN04 | The resident at 3345 Southgate was attemping to remove an old fence post when he dug into the primary cable that feeds transformer K417. | Ottawa | Foreign Interference | Dig-in
10596 | 2007 | 6 | 11 | 0.375 |  | 162 | 22 | 8 | Cahill | 4.16kV | AN04 | Transformer #OTT6461 located at 1362 Viking isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10626 | 2007 | 6 | 14 | 0.38542 |  | 10 | 2 | 11 | Cahill | 4.16kV | AN04 | Transformer #K434 located at 3338 Southgate isolated to reconnect customer after faulted cable was repaired | Ottawa | Scheduled Outage | Repair
8982 | 2006 | 8 | 16 | 0.41667 |  | 90 | 34 | 23 | Cahill |  | AN04 | Trans K417 isolated at 3340 Southgate Rd in order to replace defective insulators | Ottawa | Scheduled Outage | Repair
16753 | 2010 | 8 | 16 | 0.35417 |  | 312 | 73 | 14 | CAHILL | 4.16kV | AN04 | Transformer X27390 at 3313 Clearwater isolated and replaced | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9097 | 2006 | 8 | 30 | 0.52014 |  | 76 | 19 | 15 | Cahill | 4.16kV | AN04 | Fuse to transformer OTT1506 at 3317 Clearwater Cres was found blown due to a bird contact | Ottawa | Foreign Interference | Bird
17200 | 2010 | 10 | 31 | 0.65208 |  | 3 | 18 | 366 | CAHILL | 4.16kV | AN04 | At 15:39, AN04 was open to allow crew to safely remove a tree limb fallen across two phases of AN04. | Ottawa | Tree Contacts | Tree Limb Fallen
9898 | 2007 | 1 | 3 | 0.50069 |  | 54 | 11 | 12 | Cahill | 4.16kV | AN05 | Dave Howat isolated TRF. 427 to deenergize P1 to make repairs to defective U/G | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9901 | 2007 | 1 | 4 | 0.35417 |  | 10 | 2 | 14 | Cahill | 4.16kV | AN05 | Isolated transformer K427 at 3290 Southgate Dr to repair U/G service | Ottawa | Scheduled Outage | Repair
6162 | 2005 | 1 | 31 | 0.6875 |  | 355 | 6 | 1 | Cahill | 4.16kV | AN05 | Replaced one transformer on a 347/600 bankat OTT3483 front of 1365 Johnston Rd | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12090 | 2008 | 3 | 2 | 0.69028 |  | 88 | 21 | 14 | Cahill | 4.16kV | AN05 | Defective cable from K418 to K418 at 3240 Southgate. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12093 | 2008 | 3 | 3 | 0.46319 |  | 30 | 7 | 14 | Cahill | 4.16kV | AN05 | K431 at 3310 Southgate isolated to allow crew to reconnect repaired defective service. | Ottawa | Scheduled Outage | Repair
8016 | 2006 | 3 | 13 | 0.34722 |  | 60 | 11 | 11 | Cahill | 4.16kV | AN05 | Isolated transformer K00434 at 3330 Southgate to repair service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15970 | 2010 | 4 | 21 | 0.42917 |  | 234 | 127 | 56 | Cahill | 4.16kV | AN05 | Defective cable between K428 & K430 caused supply fuse S27796 to blow interrupting power to K428 & K429 at 3290 Southgate. Initial fault assesment determined K429 to be defective until the outage expanded while attempting to restore power. Fault finding continued and determined actual fault was the cable section not the transformer. | Ottawa | Defective Equipment
14285 | 2009 | 5 | 1 | 0.70833 |  | 40 | 53 | 249 | Cahill | 4.16kV | AN05 | Blue phase lead burnt off AN05 circuit at Albion & Johnston interrupting power to most of the blue phase customers. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10389 | 2007 | 5 | 8 | 0.33333 |  | 500 | 75 | 9 | Cahill | 4.16kV | AN05 | Isolate K427 kiosk to replace it with a new minipad transformer TP4908 @ 3290 Southgate. | Ottawa | Scheduled Outage | Repair
8306 | 2006 | 5 | 16 | 0.64583 |  | 118 | 33 | 17 | Cahill | 4.16kV | AN05 | Isolated transformer K427 at 3290 Southvale Dr to repair U/G secondary service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10595 | 2007 | 6 | 11 | 0.37847 |  | 130 | 11 | 5 | Cahill | 4.16kV | AN05 | Transformer located at 1391 Johnston isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10604 | 2007 | 6 | 11 | 0.54306 |  | 105 | 9 | 5 | Cahill | 4.16kV | AN05 | Isolated and replaced transformer 54134D-0146 at 1371 Johnston Rd (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
3686 | 2003 | 7 | 5 | 0.65764 |  | 180 | 45 | 15 | Albion | 4.16kV | AN05 | Started receiving no power calls from customers fed from K423. Line crew found fused cut out blown & holder damaged. The cable to the transformer & K423 both checked out OK. At 18:47 the transformer was picked up from an alternate feed while repairs were made to the normal supply switch. | Ottawa | Unknown/Other | No Apparent Cause
8797 | 2006 | 7 | 21 | 0.83819 |  | 108 | 25 | 14 | Cahill | 4.16kV | AN05 | A defective u/g cable caused an outage to K421 @ 3240 Southgate, units 46 to 59. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3837 | 2003 | 8 | 4 | 0.041667 |  | 10 | 2 | 15 | AN | 4.16kV | AN05 | K434 at 3330 Southgate was opened to make repairs to defective U/G service to 3318 Southgate. 3318 to 3338 Southgate affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3838 | 2003 | 8 | 4 | 0.086806 |  | 40 | 10 | 15 | AN | 4.16kV | AN05 | K434 at 3330 Southgate was opened to make repairs to defective U/G service to 3318 Southgate. 3318 to 3338 Southgate affected. 2nd outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3893 | 2003 | 8 | 12 | 0.53125 |  | 20 | 5 | 15 | AN | 4.16kV | AN05 | K434 at 3318 Southgate was opened to test secondary cables. 3318 to 3338 & 2212 to 2209 Southgate were affected. Customers were notified before the kiosk was opened. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3907 | 2003 | 8 | 14 | 0.58889 |  | 20 | 4 | 13 | Cahill | 4.16kV | AN05 | Isolation to make repairs to pedistal. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13306 | 2008 | 10 | 1 | 0.40208 |  | 96 | 21 | 13 | Cahill | 4.16kV | AN05 | Cable fault between K422 and K423 on the red phase caused dip to K422 to open on Southgate. Crews hipotted, and meggared cable section to determine bad cable. Customers restored and cable fault section isolated. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11465 | 2007 | 10 | 4 | 0.56458 |  | 152 | 38 | 15 | Cahill | 4.16kV | AN05 | Replace a defective transformer K434 @ the rear of 3330 Southgate. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11499 | 2007 | 10 | 12 | 0.03125 |  | 233 | 87 | 39 | Cahill |  | AN05 | At 10:17 pm, customers in the area of Bank Street and Southgate reported outages. 24-7 crew dispatched and discovered a cable fault on the AN05 circuit on the blue phase between the K430 and K428 transformers. 24-7 crew isolated the bad cable section, a total of 39 customers were affected for 233 min, ID 11499. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13360 | 2008 | 10 | 13 | 0.13194 |  | 70 | 5 | 4 | Cahill | 4.16kV | AN05 | O/H transformer at 3255 Southgate isolated to repair services damaged by a fire at 3253 Southgate. | Ottawa | Adverse Environment | Fire
9677 | 2006 | 11 | 17 | 0.47917 |  | 31 | 5 | 10 | Cahill | 4.16kV | AN05 | Isolated and replaced transformer K433 at 3310 Southgate Rd (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9678 | 2006 | 11 | 17 | 0.42153 |  | 67 | 11 | 10 | Cahill | 4.16kV | AN05 | Isolated and replaced transformer K430 at 3308 Southgate Rd (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9686 | 2006 | 11 | 20 | 0.39028 |  | 53 | 10 | 11 | Cahill | 4.16kV | AN05 | Isolated and replaced transformer K435 at 3310 Southgate Dr (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9687 | 2006 | 11 | 20 | 0.38889 |  | 35 | 5 | 9 | Cahill | 4.16kV | AN05 | Isolated and replaced transformer K432at 3310 Southgate Dr (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9688 | 2006 | 11 | 20 | 0.44444 |  | 33 | 5 | 9 | Cahill | 4.16kV | AN05 | At 10:40 trans K431 at 3310 Southgate Ave was isolated in order to replace pedestal cover and make repairs | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19726 | 2011 | 12 | 16 | 0.1375 |  | 77 | 35 | 27 | Cahill | 4.16kV | AN05 | 24/7 Crew made repairs to Live Line Clamp at S27796 at 2210 Bank Street restoring power to 27 customers. | Ottawa | Adverse Weather | Wind (not Trees)
19801 | 2012 | 1 | 9 | 0.51597 |  | 52 | 12 | 14 | Cahill | 4.16kV | AN06 | Transformer K438 @ 1348 HOLMES CRES was isolated by the crew to redo the primary connection. | Ottawa | Scheduled Outage | Repair
11992 | 2008 | 1 | 30 | 0.48333 |  | 29 | 130 | 270 | Cahill | 4.16kV | AN06 | At 11:36am, AN06 circuit A/R/A/L, leaving 270 customers without power. 24-7 dispatched and crew discovered at Cahill sub , AN06 Lightning Arrestor had blown and also made contact to the pothead. 24-7 crew made repairs to arrestor and system tried AN06 breaker. Closed and holding, all load restored, 270 customers affected for 29 min. ID#11992. | Ottawa | Adverse Weather | Wind
10296 | 2007 | 4 | 23 | 0.71042 |  | 1 | 0 | 1 | Cahill | 4.16kV | AN06 | auto reclose | Ottawa | Adverse Weather | Wind
18029 | 2011 | 4 | 28 | 0.5875 |  | 271 | 1220 | 270 | Cahill | 4.16kV | AN06 | AN06 circuit breaker tripped during wind/lightning storm. Closed VIA scada and held. | Ottawa | Adverse Weather | Wind
6488 | 2005 | 5 | 2 | 0.38194 |  | 20 | 5 | 16 | Cahill | 4.16kV | AN06 | Isolated Transtormer # 796 at 2603 Pimlico so Electrician can make repairs to there equipment | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16035 | 2010 | 5 | 4 | 0.61944 |  | 7 | 0 | 2 | Cahill | 4.16kV | AN06 | Transformer #X14835 located at 2676 Mac St Glouc opened by crew to disconnect service due to a grow op | Ottawa | Human Element | Sabotage
12499 | 2008 | 5 | 29 | 0.69514 |  | 84 | 4 | 3 | Cahill | 4.16kV | AN06 | Primary lead on transformer X14840 at 2915 Millstrem Way from the switch to transformer was found burnt off | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14511 | 2009 | 6 | 11 | 0.35417 |  | 20 | 3 | 8 | Cahill | 4.16kV | AN06 | Transformer #K440 located at 1350 Fontenay isolated for a PCB oil sample check | Ottawa | Scheduled Outage | Preventive Maintenance
14515 | 2009 | 6 | 11 | 0.37153 |  | 12 | 3 | 14 | Cahill | 4.16kV | AN06 | Transformer #K437 located at 1328 Holmes isolated for PCB oil sample check | Ottawa | Scheduled Outage | Preventive Maintenance
14918 | 2009 | 8 | 6 | 0.89583 |  | 90 | 26 | 17 | Cahill | 4.16kV | AN06 | At 21:30 trans K439 at 1376 Holmes Cres was isolated for replacement | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7379 | 2005 | 9 | 25 | 0.70486 |  | 289 | 642 | 220 | Cahill | 4.16kV | AN06 | A phase of AN06 circuit came down out side the station. 65 Customers affected on this phase. AN06 circuit was opened for isolation. To allow crews to repair same. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15285 | 2009 | 10 | 21 | 0.37639 |  | 2 | 0 | 12 | Cahill | 4.16kV | AN06 | At 9:02am transformer K439 at 1376 Holmes Crescent was isolated to allow crews to replace arc strangler with a new fuse, 12 customers were affected and power was restored at 9:04am. Cahill (AN06). ID#15285 | Ottawa | Scheduled Outage | Repair
15292 | 2009 | 10 | 22 | 0.3875 |  | 88 | 12 | 8 | Cahill | 4.16kV | AN06 | K440 at 1350 Fontenay Cres was isolated to allow crew to change PCB contaminated transformer and change the primary insulators in the kiosk. | Ottawa | Scheduled Outage | Repair
9828 | 2006 | 12 | 12 | 0.39583 |  | 80 | 16 | 12 | Cahill | 4.16kV | AN06 | Mike Gruich Isolated TRF. # 441 @ 1316 Cahill for TRF. PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
9830 | 2006 | 12 | 12 | 0.52083 |  | 85 | 18 | 13 | Cahill | 4.16kV | AN06 | Isolated and replaced transformer KT444 at 1372 Cahill Dr ( PCB oil ) | Ottawa | Scheduled Outage | Preventive Maintenance
9837 | 2006 | 12 | 14 | 0.51667 |  | 108 | 9 | 5 | Cahill | 4.16kV | AN06 | Isolated and replaced transformer KT442 at 1328 Cahill Dr (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9871 | 2006 | 12 | 21 | 0.40972 |  | 85 | 24 | 17 | Cahill | 4.16kV | AN06 | Transformer #K439 located at 1376 Holmes Cres isolated for PCB change & to change porcelain primary insulators | Ottawa | Scheduled Outage | Preventive Maintenance
14036 | 2009 | 3 | 11 | 0.5625 |  | 14 | 12 | 50 | Langs | 4.16kV | AP02 | AP02 tripped when an insulator on TO2AP on Langs Rd north of Montreal Rd broke and the two came in contact, causing trip and lock out on AP02. TO2AP tripped as well affecting no customers on pot only | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14217 | 2009 | 4 | 25 | 0.81181 |  | 1527 | 4963 | 195 | Langs | 4.16kV | AP02 | AP02 breaker tripped (A/R/A) during high winds, heavy rain & lightning. Problem was later determined to be primary conductor down , damaged pole & blown O/H transformer on Burma south of Venus. Damaged equipment was cleared and power restored to all but the damaged lighting xfmr. | Ottawa | Adverse Weather | Wind
18018 | 2011 | 4 | 28 | 0.67014 |  | 577 | 134 | 14 | Langs Road | 4.16kV | AP02 | AP02 circuit tripped during wind/lightning storm. Closed VIA scada and held. Was re-opened via scada to allow crews to repair downed AP03 ad AP04 conductors. | Ottawa | Adverse Weather | Wind
8293 | 2006 | 5 | 13 | 0.84028 |  | 20 | 2 | 6 | Langs | 4.16kV | AP02 | A transformer in front of 39 Castor was opened to make repairs to secondary bus connections. | Ottawa | Adverse Weather | Wind
9162 | 2006 | 9 | 8 | 0.90417 |  | 298 | 1848 | 372 | Langs | 4.16kV | AP02 | AP02 and AP04 primary on Langs Rd were burnt and wraped requiring isolation for repairs | Ottawa | Lightning | Direct Strike
9296 | 2006 | 9 | 24 | 0.64861 |  | 131 | 279 | 128 | Langs | 4.16kV | AP02 | AP02 isolated for working clearance and to rear lateral damage | Ottawa | Tree Contacts | Inadequate Trimming
4596 | 2003 | 12 | 12 | 0.7375 |  | 73 | 12 | 10 | Langs Rd | 4.16kV | AP02 | Secondary wires were wrapped together. Transformer fuse was replaced. 10 Customers effected in power outage. | Ottawa | Defective Equipment
17569 | 2011 | 2 | 10 | 0.59653 |  | 161 | 1622 | 610 | Langs | 4.16kV | AP03 | Hyhoe on old Uplands base was demolishing houses and pulled down street line which caused AP04 to trip. Wires slapped at corner of Montreal Rd and Langs Rd, AP03 burnt and fell on AP02. AP03 tripped. Crew identified AP03 on AP02 so AP02 open from SCADA. | Ottawa | Foreign Interference | Vehicle
8009 | 2006 | 3 | 10 | 0.68542 |  | 116 | 29 | 15 | LANGS | 4.16kV | AP03 | Broken Switch to transformer 65C2A-0217 at 751 Cummings Ave cause unknown | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8051 | 2006 | 3 | 22 | 0.38542 |  | 135 | 38 | 17 | Langs | 4.16kV | AP03 | Trans at 286 Bell St isolated to upgrade services | Ottawa | Scheduled Outage | Preventive Maintenance
18019 | 2011 | 4 | 28 | 0.62917 |  | 638 | 5870 | 552 | Langs Road | 4.16kV | AP03 | AP03 circuit breaker opened during wind/lightning storm. Closed via scada and held. Tripped again due to downed conductors. Crews repaired downed conductors and power was restored. | Ottawa | Adverse Weather | Wind
12396 | 2008 | 5 | 5 | 0.82986 |  | 161 | 212 | 263 | Langs | 4.16kV | AP03 | A section of O/H line on Borthwick at Wilson fell to the the ground, to make proper and safe repairs the AP03 circuit was isolated. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10577 | 2007 | 6 | 8 | 0.75 |  | 219 | 1606 | 440 | Langs | 4.16kV | AP03 | AP03 feeder auto/reclosed. Crew found that the AP04 conductor had broken and was tangled in AP03. Both circuits isolated and condutor repaired. | Ottawa | Defective Equipment
8699 | 2006 | 7 | 11 | 0.38889 |  | 180 | 84 | 28 | Langs | 4.16kV | AP03 | Isolated and replaced transformers X23983 and X26003 at 814 and 818 Cummings Ave due to contaminated oil (PCB) | Ottawa | Scheduled Outage | Preventive Maintenance
16475 | 2010 | 7 | 15 | 0.43889 |  | 129 | 60 | 28 | Langs | 4.16kV | AP03 | S14507 and S18185 on Cummings Ave at Burn St. isolated to replace switches and insulators and kiosk primary insulators. | Ottawa | Scheduled Outage | Repair
8784 | 2006 | 7 | 19 | 0.375 |  | 210 | 52 | 15 | Langs | 4.16kV | AP03 | Transformer #65C2A-0547 located at 690 Rainsford Ave isolated due to transformer replacement-high PCB count | Ottawa | Scheduled Outage | Preventive Maintenance
10994 | 2007 | 8 | 3 | 0.48056 |  | 138 | 184 | 80 | Langs | 4.16kV | AP03 | Isolated a section of O/H on Rainford bet Quebec and Wilson to perform proper tree trimming. | Ottawa | Tree Contacts | Inadequate Trimming
11106 | 2007 | 8 | 20 | 0.33333 |  | 251 | 84 | 20 | Langs | 4.16kV | AP03 | 6 transformers between 785-845 Borthwick isolated due to tree trimming being done by contractors | Ottawa | Scheduled Outage | Preventive Maintenance
9205 | 2006 | 9 | 12 | 0.54861 |  | 40 | 7 | 11 | Langs | 4.16kV | AP03 | At 13:10 trans K866 at 790 Rainsford Ave was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9224 | 2006 | 9 | 15 | 0.47222 |  | 55 | 8 | 9 | Langs | 4.16kV | AP03 | PCB Testing | Ottawa | Scheduled Outage
4152 | 2003 | 9 | 25 | 0.52153 |  | 23 | 7 | 17 | Langs | 4.16kV | AP03 | Transformer 6SC2C-0050 isolated to relocate a secaondary service. | Ottawa | Defective Equipment
9386 | 2006 | 10 | 5 | 0.53125 |  | 45 | 8 | 10 | Langs Road | 4.16kV | AP03 | Transformer located at 857 Borthwick isolated for service upgrade. PC10A #1700 | Ottawa | Scheduled Outage | Preventive Maintenance
4580 | 2003 | 12 | 9 | 0.40972 |  | 50 | 14 | 17 | Langs | 4.16kV | AP03 | Transformer in the rear of 858 Cummings was opened to change a service. ID#7580 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15533 | 2009 | 12 | 20 | 0.45069 |  | 56 | 13 | 14 | llangs | 4.16kV | AP03 | Crew opened transformer X24692 @ rear of 666 shane, to repair faulty neutral. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10991 | 2007 | 8 | 2 | 0.89444 |  | 817 | 3167 | 298 | LANGS | 8/4.8kV | AP03, AP02 | Scada Indicates AP03 opened and locked out. D.Provost reports phase burnt down at Langs Rd and Montreal Rd. Also tangled in AP02. AP02 circuit Opened Via Scada. L. Lacharity reports AP03 overhead circuit has been repaired. They will be clearing any other trees in overhead circuits (AP02,AP03). Tree trimming will still be required ASAP south on Borthwick Avenue from addresses 743 to 749. After RAN being reset, customer at 800 Rainsford reported still out of power. 24-7 reported AP03 overhead circuit between Wilson St. and Quebec St. phase down in back yard of 702 Rainsford. Sectionalized and restored power using AA04 circuit. | Ottawa | Tree Contacts | Tree Limb Fallen
7911 | 2006 | 2 | 13 | 0.45833 |  | 120 | 4 | 2 | Langs | 4.16kV | AP04 | At 11:00 Trans OTT2276 isolated in order to replace pole | Ottawa | Scheduled Outage | Preventive Maintenance
17665 | 2011 | 3 | 3 | 0.60833 |  | 45 | 34 | 46 | Langs | 4.16kV | AP04 | Cct A/R then locked out. No reports of problems & patrol found no apparent problems. Breaker closed via scada & held | Ottawa | Unknown/Other | No Apparent Cause
18020 | 2011 | 4 | 28 | 0.57431 |  | 649 | 498 | 46 | Langs Road | 4.16kV | AP04 | AP04 circuit breaker tripped during wind/lightning storm. Closed via scada unsuccessfully due to downed overhead lines. Crew repair overhead line and power was restored. | Ottawa | Adverse Weather | Wind
18289 | 2011 | 6 | 3 | 0.61181 |  | 9 | 7 | 46 | Langs AP |  | AP04 | AP04 cct tripped, OFD rpts ballon hit O/H wires at Langs & Montreal rd, AP04 closed via scada. | Ottawa | Foreign Interference | Foreign Object
16984 | 2010 | 9 | 23 | 0.40625 |  | 150 | 5 | 2 | Langs Road | 4.16kV | AP04 | Isolated and re-located transformer X21681 to new pole at 591 Langs Rd | Ottawa | Scheduled Outage | Construction
9297 | 2006 | 9 | 24 | 0.42639 |  | 474 | 1382 | 175 | Langs | 4.16kV | AP04 | AP04 overhead was burned down on Langs at Greenhill by tree contact | Ottawa | Tree Contacts | Inadequate Trimming
9399 | 2006 | 10 | 6 | 0.5 |  | 68 | 2 | 2 | Langs Road | 4.16kV | AP04 | Transformer #65C2B-0209 located at 680 Montreal Rd was isolated for PCB transformer replacement. PC10A #1152 | Ottawa | Scheduled Outage | Preventive Maintenance
19817 | 2012 | 1 | 11 | 0.64792 |  | 55 | 12 | 13 | Langs | 4.16kV | AP05 | Transformer #K633 located at 1325 Alloway Cres opened by crew to redo connections in transformer | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9934 | 2007 | 1 | 16 | 0.43264 |  | 115 | 34 | 18 | Langs | 4.16kV | AP05 | K645 was isolated to replace a faulted cable section. | Ottawa | Scheduled Outage | Repair
10134 | 2007 | 3 | 14 | 0.42083 |  | 136 | 68 | 30 | Langs | 4.16kV | AP05 | The white phase cable between K628 and the PPH Switches blew causing an outage to 3 transformers on Metz and Charlton Drive. Cable isolated and power restored. | Ottawa | Defective Equipment
12255 | 2008 | 4 | 9 | 0.11528 |  | 257 | 156 | 58 | Langs | 4.16kV | AP05 | apparent cable fault between K640 and K642 on The Rockery Prvt caused red phase dip to blow on AP05 out of Langs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3549 | 2003 | 6 | 10 | 0.42708 |  | 20 | 5 | 16 | Langs | 4.16kV | AP05 | Fencing contractor dug outside his isolation causing outage on secondary cable to 16 customers on Romulus fed from K652 on the AP05 circuit. | Ottawa | Foreign Interference | Dig-in
3718 | 2003 | 7 | 10 | 0.45694 |  | 32 | 13 | 24 | Langs Rd | 4.16kV | AP05 | Crews opened K649 to make repairs. Outage affected 24 customers on Stone Quarry. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3719 | 2003 | 7 | 10 | 0.63889 |  | 80 | 13 | 10 | Langs Rd | 4.16kV | AP05 | Crews isolated K647 to repair bad service on Stone Quarry outage effected 10 customers. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6899 | 2005 | 7 | 10 | 0.98264 |  | 765 | 115 | 9 | Langs | 4.16kV | AP05 | Faulty cutout caused transformer at 528 foxview to open. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3757 | 2003 | 7 | 18 | 0.24931 |  | 151 | 81 | 32 | Langs | 4.16kV | AP05 | Cable to K641 faulted causing the AP05 to auto reclose and the fuse to K641, K640 and K642 to blow on the red phase | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8811 | 2006 | 7 | 24 | 0.4375 |  | 55 | 14 | 15 | Langs | 4.16kV | AP05 | Transformer #K641 located at 11 The Rockery Pvt isolated due to transformer replacement for PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
8812 | 2006 | 7 | 24 | 0.375 |  | 90 | 22 | 15 | Langs | 4.16kV | AP05 | Transformer #K640 located at 6 The Rockery Pvt isolated due to transformer change for PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
8925 | 2006 | 8 | 4 | 0.20139 |  | 110 | 64 | 35 | Langs | 4.16kV | AP05 | AP05 auto reclosed once. Problem was later determined to be a faulted cable to K645. The faulted cable was sectionalized by 24/7 & power restored to K645 & K646. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16707 | 2010 | 8 | 10 | 0.18819 |  | 106 | 9 | 5 | Langs Road | 4.16kV | AP05 | K865-W fuses blew due to cable fault between K865 and K864 @ Foxview. | Ottawa | Defective Equipment
18949 | 2011 | 8 | 16 | 0.63681 |  | 29 | 261 | 539 | Langs Road | 4.16kV | AP05 | AP05 breaker Auto reclosed and locked out, after inspecting the pole pothead, System closed the breaker from scada. | Ottawa | Unknown/Other | No Apparent Cause
16786 | 2010 | 8 | 20 | 0.39236 |  | 58 | 9 | 9 | Langs | 4.16kV | AP05 | K 864 and K865 on Foxview place isolated to allow cable crew to pull in new cable. Duct appears to still be blocked, Greely required to dig. | Ottawa | Scheduled Outage | Repair
16802 | 2010 | 8 | 24 | 0.40972 |  | 50 | 10 | 12 | Langs Road | 4.16kV | AP05 | Isolated transformer K635 at 1270 Alloway Cres to connect new streetlight service | Ottawa | Scheduled Outage | Emergency Services Request
16816 | 2010 | 8 | 26 | 0.39028 |  | 61 | 12 | 12 | Langs | 4.16kV | AP05 | K864 & K865 on Foxview Pl. Were isloated to replace defective primary cable. | AP05 | Scheduled Outage | Repair
9213 | 2006 | 9 | 14 | 0.4375 |  | 80 | 25 | 19 | Langs | 4.16kV | AP05 | At 10:30 trans K645 at 149 Birch Hill Priv isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9214 | 2006 | 9 | 14 | 0.40278 |  | 40 | 11 | 16 | Langs | 4.16kV | AP05 | At 09:40 trans K646 at 198 Birch Hill Priv was isolated for PCB trans replacement | Ottawa | Scheduled Outage
9215 | 2006 | 9 | 14 | 0.44792 |  | 85 | 50 | 35 | Langs | 4.16kV | AP05 | At 10:45 trans at 631 Carsons Rd was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9225 | 2006 | 9 | 15 | 0.47222 |  | 55 | 8 | 9 | Langs | 4.16kV | AP05 | At 11:20 tran K870 at 811 Cummings Ave isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9226 | 2006 | 9 | 15 | 0.41667 |  | 225 | 45 | 12 | Langs | 4.16kV | AP05 | At 10:00 trans K624 at 1393 Plummer was isolated for pcb trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9227 | 2006 | 9 | 15 | 0.48264 |  | 90 | 27 | 18 | Langs | 4.16kV | AP05 | At 11:35 trans K643 at 108 Rockery Ave was isolated for pcb trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11317 | 2007 | 9 | 17 | 0.33333 |  | 165 | 38 | 14 | LANGS | 4.16kV | AP05 | Transformer #OTT509 at 672 Borthwick isolated to allow for tree trimming, PC10C#1460 | Ottawa | Scheduled Outage | Preventive Maintenance
11318 | 2007 | 9 | 17 | 0.33333 |  | 165 | 33 | 12 | Langs | 4.16kV | AP05 | Transformer #OTT6342 at 700 Borthwick isolated to allow for tree trimming - PC10C #1459 | Ottawa | Scheduled Outage | Preventive Maintenance
11320 | 2007 | 9 | 17 | 0.33333 |  | 180 | 42 | 14 | LANGS | 4.16kV | AP05 | Transformer #OTT509 at 626 Wilson isolated to allow for tree trimming, PC10C #1458 | Ottawa | Scheduled Outage | Preventive Maintenance
9243 | 2006 | 9 | 18 | 0.40625 |  | 105 | 32 | 18 | Langs | 4.16kV | AP05 | AT 09:45 trans K864 at 535 Foxview Pl was isolated for pcb trans replacement | Ottawa | Scheduled Outage
19320 | 2011 | 10 | 4 | 0.89236 |  | 142 | 77 | 36 | Langs | 4.16kV | AP05 | Cable fault between S18505 and K628 caused S18505 W phase to blow. Outage to 3 transformers on Metz Cres. K628, K629 and K630. Load restored in stages. | Ottawa | Defective Equipment
4218 | 2003 | 10 | 7 | 0.16806 |  | 283 | 170 | 36 | Langs | 4.16kV | AP05 | Scada indicated autoreclose. No customer calls untill after 6 a.m. Defective cable found feeding K643 & K644 on Birch Hill & The Rockery. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7723 | 2005 | 12 | 14 | 0.42708 |  | 241 | 20 | 5 | Langs | 4.16kV | AP05 | 4 kv transformer K865 on Foxview Place was upgraded to a larger model to accommodate new customers. | Ottawa | Scheduled Outage | Preventive Maintenance
6072 | 2004 | 12 | 17 | 0.42708 |  | 45 | 10 | 14 | Langs | 4.16kV | AP05 | Reconnected underground service in live front ped at 6 The Rockery Pvt transformer K00640 | Ottawa | Scheduled Outage | Repair
4629 | 2003 | 12 | 18 | 0.48333 |  | 122 | 33 | 16 | Langs | 4.16kV | AP05 | Transformer at the rear of 215 Romulas, in the Carson Grove area of Ottawa, was isolated to allow for the repair of a secondary wire. ID#4629 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9948 | 2007 | 1 | 19 | 0.26528 |  | 148 | 49 | 20 | Langs | 4.16kV | AP06 | Line switch at Foxview and Brunel was found broken crew replaced the switch and restored power | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12126 | 2008 | 3 | 11 | 0.44097 |  | 50 | 7 | 8 | LANG'S SUB | 4.16kV | AP06 | Transformer #X23830 at 659 Carson's Rd isolated to allow customer to remove eavestroughing from service wires | Ottawa | Scheduled Outage | Repair
14069 | 2009 | 3 | 16 | 0.725 |  | 73 | 34 | 28 | Langs | 4.16kV | AP06 | Defective cable caused the AP06 p/p/h fusesfeeding K618 and K619 at 720 carsons rd. to blow. Crew isolated cablle section and closed at N. O. point at K619 to restore power to two transformers. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14091 | 2009 | 3 | 24 | 0.39792 |  | 192 | 45 | 14 | Langs Road | 4.16kV | AP06 | K618 at 720 Carsons Rd isolated to allow creew to pull in new primary cable and make connections. | Ottawa | Scheduled Outage | Repair
10230 | 2007 | 4 | 10 | 0.39583 |  | 185 | 40 | 13 | LANGS | 4.16kV | AP06 | Isolated and replaced transformer 65C2B-0138 at 698 Eastfield (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
10238 | 2007 | 4 | 11 | 0.375 |  | 180 | 36 | 12 | Langs | 4.16kV | AP06 | Isolated and replaced transformer 65C2B-0269 at 694 Roanoke St (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
10281 | 2007 | 4 | 19 | 0.375 |  | 179 | 12 | 4 | Langs | 4.16kV | AP06 | Mike Gruich isolated TRF @ 698 Eastfield for a PCB TRF change | Ottawa | Scheduled Outage | Preventive Maintenance
12679 | 2008 | 6 | 17 | 0.43819 |  | 119 | 24 | 12 | Lang Road | 4.16kV | AP06 | To rotate transformer on pad due to obstruction. | Ottawa | Scheduled Outage | Construction
12681 | 2008 | 6 | 17 | 0.52569 |  | 85 | 17 | 12 | Langs Road | 4.16kV | AP06 | TP3381 @ 797 Montreal Rd was isolated to all crews to rotate padmount transformer | Ottawa | Scheduled Outage | Construction
14807 | 2009 | 7 | 23 | 0.35417 |  | 37 | 17 | 28 | Langs | 4.16kV | AP06 | Transformer #K618 & K619 located at 725 Carson's Rd isolated for a PCB test | Ottawa | Scheduled Outage | Construction
9219 | 2006 | 9 | 14 | 0.55208 |  | 55 | 16 | 17 | Langs | 4.16kV | AP06 | At 13:15 trans at 713 Carsons Rd was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11380 | 2007 | 9 | 25 | 0.34861 |  | 214 | 136 | 38 | Langs | 4.16kV | AP06 | The O/H line on Charleswood Ave was isolated to allow for clearance for the tree crews. | Ottawa | Scheduled Outage | Preventive Maintenance
7527 | 2005 | 10 | 27 | 0.38889 |  | 30 | 2 | 4 | Langs | 4.16kV | AP06 | Isolated Transformer at 701 Crystal st to disconnect a service | Ottawa | Scheduled Outage | Preventive Maintenance
15694 | 2010 | 1 | 30 | 0.84375 |  | 285 | 81 | 17 | McCarthy | 4.16kV | AQ02 | Customer call lead the crew to check the K22 padmount transformer at 3275 McCarthy and it was found to be in the final stages of failure but still feeding. The transformer was isolated until oncall could arrive to replace the transformer and prevent further damage | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12178 | 2008 | 3 | 27 | 0.52083 |  | 39 | 10 | 15 | McCarthy | 4.16kV | AQ02 | K19 @ 3275 McCarthy was isolated to all the crew to put the transformer back on it's pad after someone hit it while removing snow. | Ottawa | Foreign Interference | Vehicle
6680 | 2005 | 6 | 8 | 0.11597 |  | 85 | 229 | 228 | McCarthy | 4.16kV | AQ02 | Cable fault from Dip pole to KT17 at 3275 McCarthy | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16243 | 2010 | 6 | 10 | 0.38542 |  | 160 | 45 | 17 | MCCARTHY | 4.16kV | AQ02 | Transformer K00025 at 3275 McCarthy Rd isolated for primary compartment insulator change | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16244 | 2010 | 6 | 10 | 0.39722 |  | 118 | 31 | 16 | McCarthy | 4.16kV | AQ02 | K25 at 3275 Mcarthy was isolated to allow crews to replace defective insulator | Ottawa | Scheduled Outage | Repair
3876 | 2003 | 8 | 8 | 0.60764 |  | 23 | 6 | 15 | McCarthy | 4.16kV | AQ02 | Transformer K23 was opened to disconnect underground service at 3275 McCarthy. | Ottawa | Scheduled Outage
15139 | 2009 | 9 | 21 | 0.62222 |  | 4 | 3 | 44 | McCarthy | 4.16kV | AQ02 | M. Byers reports while attempting to isolate services out of K17 he accidentally opened the primary instead of the secondary causing an outage to 3 more transformers. He was instructed to safely reclose the primary and restore the K18, K19 and K20 and continue with the isolation of K17 secondary. | Ottawa | Human Element | Switching Errors
15140 | 2009 | 9 | 21 | 0.64583 |  | 45 | 13 | 17 | Mccarthy | 4.16kV | AQ02 | Transformer #K17 located at 3275 Mccarthy isolated to repair 2 U/G services | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15141 | 2009 | 9 | 21 | 0.68403 |  | 22 | 6 | 17 | Mccarthy | 4.16kV | AQ02 | Transformer #K22 located at 3275 Mccarthy isolated to repair U/G service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7445 | 2005 | 10 | 12 | 0.20833 |  | 107 | 72 | 60 | McCarthy | 4.16kV | AQ02 | AQ02 circuit auto reclosed at 03:44. White phase fuse found blown at dip. While sectionalizing cable between K 18 & k19. AQ02 circuit opened for 1min. Outage to 100 customers. AQ02 closed via scada restoring load to 60 customers. All load restored at 05:30. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7556 | 2005 | 11 | 3 | 0.41319 |  | 117 | 29 | 15 | McCarthy | 4.16kV | AQ02 | K17 at 3275 McCarthy was isolated to install a new cable feed from the AQ02 white phase overhead. | Ottawa | Scheduled Outage | Construction
7738 | 2005 | 12 | 15 | 0.40625 |  | 113 | 21 | 11 | McCarthy | 4.16kV | AQ02 | K19 at 3275 McCarthy was isolated to re-insulate transformer. | Ottawa | Scheduled Outage | Preventive Maintenance
15995 | 2010 | 4 | 26 | 0.25208 |  | 176 | 98 | 35 | MCCARTHY | 4.16kV | AQ03 | Defective switch at S17459 as well as blown arrestor at K133 caused outage to 33 customers at McCarthy/Plante area | Ottawa | Defective Equipment
14257 | 2009 | 4 | 29 | 0.37708 |  | 195 | 42 | 13 | McCarthy | 4.16kV | AQ03 | 4kV transformer at Unit96 - 860 Cahill was isolated to allow underground crew to replace the transformer. | Ottawa | Scheduled Outage | Preventive Maintenance
14381 | 2009 | 5 | 20 | 0.38889 |  | 100 | 25 | 15 | McCarthy | 4.16kV | AQ03 | K745 & K746 on Cobbler & Bankview were isolated to replace defective insulators. | Ottawa | Scheduled Outage | Repair
14384 | 2009 | 5 | 20 | 0.54722 |  | 70 | 7 | 6 | McCarthy | 4.16kV | AQ03 | At 78 Pattermead K744 was isolated to allow crew to replace defective insulators and berrier board. | Nepean | Scheduled Outage | Repair
10675 | 2007 | 6 | 20 | 0.41458 |  | 87 | 29 | 20 | McCarthy | 4.16kV | AQ03 | Isolated transformers K741 & K742 on Pattermede Cres to replace broken insulators in primary switch gear. | Ottawa | Scheduled Outage | Preventive Maintenance
5354 | 2004 | 6 | 22 | 0.46528 |  | 35 | 9 | 16 | AQ | 4.16kV | AQ03 | K78 at 820 Cahill dr was opened to disconnect the service to a bus shelter. | Ottawa | Scheduled Outage | Construction
20907 | 2012 | 7 | 2 | 0.24167 |  | 167 | 120 | 43 | McCarthy | 4.16kV | AQ03 | Customer reported outage at K72 located at 840 Cahill, crews found defective switch S11142, cables hipotted and transformers restored. Switch replaced and circuit restored to Normal. | Ottawa | Defective Equipment
7420 | 2005 | 10 | 3 | 0.54167 |  | 30 | 2 | 5 | Mccarthy | 4.16kV | AQ03 | Transformer #K00737 located at rear of 30 Pattermead cres isolated to determine the problem at 42 Pattermead (defective meter base) | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4650 | 2003 | 12 | 24 | 0.325 |  | 1 | 4 | 218 | McCarthy | 4.16kV | AQ03 | Defective AQ03-Eswitch on AQ00 circuit caused the AQ03 circuit to open. Circuit was closed by scada 1 minute after openeing. Recloser was out of service. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
19785 | 2012 | 1 | 5 | 0.41319 |  | 139 | 32 | 14 | McCarthy | 4.16kV | AQ04 | K798 at 3333 McCarthy was isolated to allow crews to replace a cut-out and repair damaged primary connections due to over heating. | Ottawa | Scheduled Outage | Repair
12030 | 2008 | 2 | 10 | 0.66042 |  | 74 | 12 | 37 | McCarthy | 4.16kV | AQ04 | Broken insulator at K799 to K315 caused fuse barrel to burn up & come apart at K799 & caused interruption to K799 at 3333 McCarthy. Defective cable section was isolated & power restored from alternate source. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12043 | 2008 | 2 | 14 | 0.39931 |  | 68 | 17 | 15 | McCarthy | 4.16kV | AQ04 | Transformer K799 at 3333 McCarthy isolated to replace defective insulators in the kiosk. | Ottawa | Scheduled Outage | Repair
8134 | 2006 | 4 | 11 | 0.73611 |  | 3 | 1 | 12 | McCarthy | 4.16kV | AQ04 | Transformer #K52 located at 222 Huntridge isolated to disconnect secondary service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17872 | 2011 | 4 | 11 | 0.17847 |  | 3 | 17 | 331 | McCarthy |  | AQ04 | At 04:17 SCADA indicated that the AQ04 and AQK1Y1 circuit breakers had open. Todd R closed the AQ04 breaker back in VIA SCADA. 331 customers were affected for 3 mins. McCarthy AQ04 ID# 17872 | Ottawa | Adverse Weather | Lightning
5047 | 2004 | 4 | 24 | 0.99792 |  | 69 | 119 | 205 | McCarthy | 4.16kV | AQ04 | AQ04 blue phase cable at riser pole to P/P/H switches faulted causing AQ04 to autoreclose and loss of about 80 customers in McCarthy & Paul Anka area. AQ04 breaker had to be opened for short while to open the AQ04 P/P/H switches and transfer the load to AQ00. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8189 | 2006 | 4 | 25 | 0.54167 |  | 15 | 2 | 8 | McCarthy | 4.16kV | AQ04 | Mark Rushtong opened transformer K52 at 156 Huntridge Private to repair a defective secondary service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5093 | 2004 | 5 | 3 | 0.38056 |  | 236 | 197 | 50 | McCarthy | 4.16kV | AQ04 | AQ04 load on AQ00 interupted to replace defective insulators on AQ00 and AQ04 circuits, partial load interupted due to no transfer capabilities. | Ottawa | Scheduled Outage | Preventive Maintenance
14501 | 2009 | 6 | 10 | 0.33681 |  | 19 | 4 | 14 | MCCARTHY | 4.16kV | AQ04 | Transformer K45 at 3373 MCCarthy isolated to allow for PCB sampling | Ottawa | Scheduled Outage | Preventive Maintenance
6782 | 2005 | 6 | 22 | 0.54861 |  | 55 | 8 | 9 | Mccarthy | 4.16kV | AQ04 | Transformer #K00049 located at 185 Huntridge isolated to make repairs to 2 homes (secondary services) | Ottawa | Scheduled Outage | Repair
9260 | 2006 | 9 | 21 | 0.39514 |  | 39 | 14 | 21 | Mccarthy | 4.16kV | AQ04 | Transformer #K00999 located at 24 Huntview isolated to change transformer due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
20066 | 2012 | 2 | 28 | 0.39306 |  | 51 | 8 | 10 | McCarthy | 4.16kV | AQ05 | K726 @ 3205 Uplands was isolated by the crew to replace damage lightning arrestor. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14487 | 2009 | 6 | 8 | 0.36806 |  | 33 | 24 | 43 | Mccarthy | 4.16kV | AQ05 | Transformer #K730 located at 3400 Paul Anka isolated to take PCB oil sample | Ottawa | Scheduled Outage | Preventive Maintenance
14490 | 2009 | 6 | 8 | 0.39583 |  | 24 | 0 | 6 | McCarthy | 4.16kV | AQ05 | Transformer K731 isolated for PCB oil sample. | Nepean | Scheduled Outage
16223 | 2010 | 6 | 8 | 0.3875 |  | 142 | 24 | 10 | McCarthy | 4.16kV | AQ05 | K96 at 3415 Uplands Dr was isolated to allow crews to change broken insulators & remove asbestos. | Ottawa | Scheduled Outage | Repair
16232 | 2010 | 6 | 9 | 0.37569 |  | 113 | 19 | 10 | McArthy | 4.16kV | AQ05 | K98 at 3446 McArthy was isolated to replace defective insulators & remove asbestos. | Ottawa | Scheduled Outage | Preventive Maintenance
8872 | 2006 | 7 | 30 | 0.42986 |  | 269 | 45 | 10 | McCarthy | 4.16kV | AQ05 | Defective primary bus & insulators at K107 caused fuse to blow at SW113. The Kiosk was isolated & repairs were made by 24/7 & On-call. Units 219 to 228 at 3445 Uplands were interrupted. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9403 | 2006 | 10 | 8 | 0.69722 |  | 148 | 25 | 10 | mccarthy | 4.16kV | AQ05 | K101 at 825 Cahill opened due to faulty arrestor. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
5356 | 2004 | 6 | 23 | 0.22431 |  | 81 | 40 | 30 | AQ | 4.16kV | AQ06 | Crew found blown arrestor at K103, same cut clear, red phase re-fused at WCS6 picking up K103, 104, 105. 30 customers at 825 Cahill, unit 189 to 218 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10788 | 2007 | 7 | 4 | 0.40625 |  | 105 | 44 | 25 | McCarthy | 4.16kV | AQ06 | K784 and K785 wer isolated to allow crews to replace insulators in transformers. | Ottawa | Scheduled Outage | Preventive Maintenance
14764 | 2009 | 7 | 16 | 0.46111 |  | 108 | 22 | 12 | McCarthy | 4.16kV | AQ06 | At 11:04 transformer K94 at 3415 Uplands was isolated to allow crews to replace a broken insulator at normal open point at K94 transformer, 12 customers were affected and power was restored at 12:52pm. McCarthy (AQ06). ID#14764. | Ottawa | Scheduled Outage | Repair
13153 | 2008 | 8 | 27 | 0.37361 |  | 150 | 59 | 40 | McCarthy | 4.16kV | AQ06 | Outage to K89, K88, K87 at 3415 Uplands Dr due to cable fault between K87 & K86. Due to error in fault indicator, outage was expanded to K86(10 customers). | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4662 | 2003 | 12 | 29 | 0.24653 |  | 185 | 31 | 10 | McCarthy | 4.16kV | AQ06 | Transformer K96 secondary opened to 3415 Uplands due to fire damage to a 10 unit townhome complex. All customer's to remain off until F.D. & ESA have completed inspections. | Ottawa | Foreign Interference | Fire
7774 | 2006 | 1 | 4 | 0.40833 |  | 162 | 32 | 12 | McCarthy | 4.16kV | AQ07 | K760 at 211 Royalton isolated to repair insulators, replace blown arrestor & remove asbestos. | Ottawa | Scheduled Outage | Repair
9971 | 2007 | 1 | 28 | 0.47569 |  | 86 | 136 | 100 | McCarthy | 4.16kV | AQ07 | Blown arrester in K724 caused WSC8 R phase fuse to blow. Arrester cut clear and fuse replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10191 | 2007 | 3 | 27 | 0.8 |  | 58 |  | 60 | McCarthy | 4.16kV | AQ07 | Blown arrester at K726 caused fuse to blown at WCS8R. 5 Kiosks were affected. Arrester cleared and fuse replaced and closed in to restore power on Uplands Drive. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20238 | 2012 | 3 | 27 | 0.41806 |  | 116 | 64 | 33 | McCarthy | 4.16kV | AQ07 | Transformers K784 and K785 at 220 Royalton were isolated to allow crew to perform preventative maintenance on transformers | Ottawa | Scheduled Outage | Preventive Maintenance
20269 | 2012 | 4 | 3 | 0.38056 |  | 54 | 16 | 18 | McCarthy | 4.16kV | AQ07 | at 9:08am,, Kiosk K783 located at 3225 Uplands was isolated to allow crews to repair defective lightning arresters. 18 customers affected for 54 minutes. | Ottawa | Scheduled Outage | Repair
20542 | 2012 | 5 | 20 | 0.55 |  | 116 | 66 | 34 | McCarthy | 4.16kV | AQ07 | WCS7 Blue phase opened due to defective arrestor at K758 at 238 Royalton PVT. | Ottawa | Defective Equipment
14484 | 2009 | 6 | 8 | 0.34722 |  | 25 | 20 | 49 | Mccarthy | 4.16kV | AQ07 | Transformer #K732 located at 3262 Uplands Dr isolated due to crew collecting PCB oil sample | Ottawa | Scheduled Outage | Preventive Maintenance
16319 | 2010 | 6 | 23 | 0.40139 |  | 193 | 39 | 12 | McCarthy | 4.16kV | AQ07 | K782 at 3225 Uplands was isolated to remove asbestos and replace insulatros. | Ottawa | Scheduled Outage
12803 | 2008 | 7 | 8 | 0.44444 |  | 29 | 5 | 10 | MCCARTHY | 4.16kV | AQ07 | TRANSFORMER #K726 AT 3205 UPLANDS UNIT 26 ISOLATED TO ALLOW FOR REPAIRS TO CUSTOMER OWNED EQUIPMENT - PC10#4390 ISSUES @ 10:40 & SURRENDERED @ 11:09 BY JASON WALKDEN | Ottawa | Scheduled Outage | Repair
13604 | 2008 | 11 | 13 | 0.62778 |  | 60 | 30 | 30 | McCarthy | 4.16kV | AQ07 | Blown arrester found at transformer K727 at 3225 Uplands. Crew cut arrester clear and closed back in red phase fuse at WCS8 restoring all customers. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16194 | 2010 | 6 | 4 | 0.40972 |  | 73 | 7 | 6 | McCarthy | 4.16kV | AQ08 | K889 at 13 Finch, isolated to change defective insulators. 6 customers on Finch Pvt affected. | Ottawa | Scheduled Outage | Preventive Maintenance
14483 | 2009 | 6 | 8 | 0.33333 |  | 20 | 3 | 10 | Mccarthy | 4.16kV | AQ08 | Transformer #K478 located at 3372 Uplands Dr isolated for crew to take PCB oil sample | Ottawa | Scheduled Outage | Preventive Maintenance
14786 | 2009 | 7 | 20 | 0.37083 |  | 106 | 14 | 8 | McCarthy | 4.16kV | AQ08 | K887 at 16 Pinson isolated for Cable Crew to replace defective insulators. 8 customers on Pinson Pvt were affected. | Ottawa | Scheduled Outage | Repair
9134 | 2006 | 9 | 7 | 0.52083 |  | 120 | 16 | 8 | McCarthy | 4.16kV | AQ08 | Yannick Fortin opened Transformer #K00891 at 31 Finch to do a PCB Transformer change. | Ottawa | Scheduled Outage | Preventive Maintenance
16989 | 2010 | 9 | 24 | 0.15417 |  | 192 | 304 | 95 | McCarthy | 4.16kV | AQ08 | 2 blown arrestors found in transformer loop caused outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20060 | 2012 | 2 | 27 | 0.51389 |  | 88 | 37 | 25 | McCarthy | 4.16kV | AQ09 | Transformers K123 and K124 on Waxwing were isolated to allow crew to replace elbows and inserts. | Ottawa | Scheduled Outage | Preventive Maintenance
3271 | 2003 | 3 | 19 | 0.013194 |  | 321 | 98 | 30 | McCarthy | 4.16kV | AQ09 | 24/7 found a blown fuse to K130, a broken bushings at K129 & a blown lightning arrestor at K128. The lightning arrestor at K128 was removed, K125 & K128 were picked up on AQ00 blue phase. K129 & K130 were picked up on normal AQ09 supply but cable to K129 from K130 had to be connected directly to primary of transformer. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5032 | 2004 | 4 | 21 | 0.43403 |  | 18 | 4 | 12 | McArthy |  | AQ09 | Transformer Kiosk K37 at 1125 Plante Dr taken out of service to disconnect at a pedestal for emergency repair work to meter base at 1139 Plante. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5033 | 2004 | 4 | 21 | 0.51042 |  | 17 | 3 | 12 | McArthy | 4.16kV | AQ09 | K37 taken out of service again to reconnect secondary at a pedestal to 1139 Plante following meter base repairs. Same 12 customers affected again (See ID#5032) | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16284 | 2010 | 6 | 18 | 0.52639 |  | 7 | 34 | 295 | McCarthy | 4.16kV | AQ09 | While crew was attempting to restore AQ09 to normal supply, the S27194 (AQ09 P/P/H switches) flashed over causing AQK2Y2 breaker to trip. S27194 was opened clearing the o/h line & all customers restored via AQ00 / AQK2Y2. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7739 | 2005 | 12 | 15 | 0.53472 |  | 71 | 18 | 15 | McCarthy | 4.16kV | AQ09 | K122 at 33 Hawk was isolated to re-insulate transformer. | Ottawa | Scheduled Outage
17618 | 2011 | 2 | 18 | 0.97917 |  | 180 | 39 | 13 | McCarthy | 4.16kV | AQ10 | Defective fuse barrell in K800 had to be replaced. | Ottawa | Unknown/Other
15785 | 2010 | 3 | 9 | 0.69375 |  | 76 | 25 | 20 | Mcarthy | 4.16kV | AQ10 | A vehicle accidnet caused the AQ10 red phase switch feeding K115 and K113 on Paul Anka and Bennet to break and open. Crew replaced and refused. | Ottawa | Foreign Interference | Vehicle
14503 | 2009 | 6 | 10 | 0.37431 |  | 26 | 3 | 8 | MCCARTHY | 4.16kV | AQ10 | K0079 at 23 Royal Hunt isolated to allow for PCB sampling | Ottawa | Scheduled Outage | Preventive Maintenance
6752 | 2005 | 6 | 16 | 0.375 |  | 115 | 23 | 12 | Mccarthy | 4.16kV | AQ10 | Transformer #K309 located at 59 Erin Cres isolated to replace insulator | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14556 | 2009 | 6 | 17 | 0.375 |  | 20 | 2 | 7 | Mccarthy | 4.16kV | AQ10 | Transformer #K113 located at 23 Bennett St isolated to get PCB oil sample | Ottawa | Scheduled Outage | Construction
16277 | 2010 | 6 | 17 | 0.39583 |  | 140 | 28 | 12 | McCarthy | 4.16kV | AQ10 | K820 @ 60 Sample was isolated for planned asbestos removal & insulator replacement. | Ottawa | Scheduled Outage | Preventive Maintenance
6779 | 2005 | 6 | 22 | 0.39444 |  | 79 | 16 | 12 | McCarthy | 4.16kV | AQ10 | K305 at 52 Erin isolated to replace cracked insulators. | Ottawa | Scheduled Outage | Repair
14729 | 2009 | 7 | 11 | 0.575 |  | 595 | 10 | 1 | McCarthy | 4.16kV | AQ10 | Transfomer at 770 Huntclub replaced due to storm damage | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18836 | 2011 | 7 | 27 | 0.28194 |  | 117 | 618 | 317 | McCarthy | 4.16kV | AQ10 | Crews found the PPH on the AQ10 to be defective. McCarthy ID#18836. | Ottawa | Defective Equipment
7334 | 2005 | 9 | 16 | 0.47569 |  | 110 | 26 | 14 |  | 4.16kV | AQ10 | Trans K118 isolated to connect new service for Rogers cable. | Nepean | Scheduled Outage | Construction
20047 | 2012 | 2 | 23 | 0.39028 |  | 168 | 56 | 20 | McCarthy | 4.16kV | AQ11 | K14 on Condor isolated for replacement of terminations and K15 on Avacodo isolated for complete board change. | Ottawa | Scheduled Outage | Repair
20197 | 2012 | 3 | 22 | 0.40278 |  | 70 | 10 | 9 | McCarthy | 4.16kV | AQ11 | At 09:40 transformer K11 at 55 Avocado Street was isolated to allow crew to perform maintenance. 9 customers were affected for 70 minutes. McCarthy (AQ11) ID#20197 | Ottawa | Scheduled Outage | Preventive Maintenance
10409 | 2007 | 5 | 11 | 0.72569 |  | 30 | 5 | 10 | McCarthy | 4.16kV | AQ11 | Greg Bell isolated TRF. K001 to disconnect service feeding 3207 McArthy | Ottawa | Foreign Interference | Foreign Object
7041 | 2005 | 7 | 29 | 0.37986 |  | 35 | 6 | 10 | McCarthy | 4.16kV | AQ11 | Isolated Transformer # K0004 at 21 Condor to work on secondary UG | Ottawa | Defective Equipment
19217 | 2011 | 9 | 21 | 0.37361 |  | 331 | 61 | 11 | McCarthy | 4.16kV | AQ11 | 4kV transformer K2 at 14 Impala was isolated to allow a contractor to dig around a secondary pedastal and raise it to grade. | Ottawa | Scheduled Outage | Preventive Maintenance
9200 | 2006 | 9 | 12 | 0.40278 |  | 7 | 49 | 418 | Bells Corners | 8/4.8kV | B1 BUS | The 47F2 & 47F3 feeders interupted due to low voltage condition. The 47T1 B phase high side fuse opened due to a failed arrestor. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
7084 | 2005 | 8 | 7 | 0.48611 |  | 50 | 2 | 2 | Casselman | 8/4.8kV | B11F1 | Transformer #73 isolated at 808 Drouin St, Casselman to replace leaking transformer | Castleman | Defective Equipment | Equipment Failure - Cause Unknown
6155 | 2005 | 1 | 26 | 0.77292 |  | 7 | 346 | 2962 | TD | 13.2kV | B2 bus | During switching to restore TDB2 bus to normal, all load was dumped when the TDB1E transfer breaker was opened before closing the TDB2E breaker. | Ottawa | Human Element | Switching Errors
10867 | 2007 | 7 | 13 | 0.5625 |  | 45 | 1 | 1 | 140F2 | 8/4.8kV | Barrhaven | M. Byers reports tree branch found on customer owned line @ 3700 Prince of Wales Dr. 24/7 isolated line and remove branch all power restored. | Nepean | Tree Contacts | Tree Limb Fallen
7727 | 2005 | 12 | 15 | 0.4375 |  | 156 | 125 | 48 | Bayshore | 8/4.8kV | Bayshore | 6 overhead transformers isolated to allow forestry crew to trim trees in the area of Clebean & Harlow st. | Nepean | Scheduled Outage | Preventive Maintenance
6624 | 2005 | 5 | 31 | 0.40625 |  | 475 | 63 | 8 | BB | 12/7.2kV | BBF1 | Tx 2517 was isolated for replacement. | Kanata | Scheduled Outage | Preventive Maintenance
6634 | 2005 | 6 | 1 | 0.4 |  | 547 | 109 | 12 | Beaverbrook | 12/7.2kV | BBF1 | TX 3070 transformer replacement | Kanata | Scheduled Outage | Preventive Maintenance
6646 | 2005 | 6 | 2 | 0.38542 |  | 579 | 135 | 14 | Beaverbrook | 12/7.2kV | BBF1 | Transformer #3069 @ 10 Sandwell was isolated to replace transformer. 14 ustomers affected in planned outage | Kanata | Scheduled Outage | Repair
5349 | 2004 | 6 | 22 | 0.82639 |  | 354 | 493 | 360 | Beaverbrook | 12/7.2kV | BBF1 | Cable fault located on the last cable section of the last leg of the of the feeder. Fault indicator on the last transformer showed clear but actually had the fault. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5279 | 2004 | 6 | 11 | 0.0034722 |  | 228 | 30 | 8 | Beaverbrook | 12/7.2kV | BBF2 | Leaking transformer 3157R had to be replaced at 22 Selwyn. Secondary bushing caused the leak. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5458 | 2004 | 7 | 7 | 0.41458 |  | 38 | 76 | 120 | Beaverbrook | 12/7.2kV | BBF2 | Cable T2583R to T2517 was repaired and cable was energized but went defective right away cable was reisolated new permit made and S8 was refused and closed | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3747 | 2003 | 7 | 15 | 0.37986 |  | 347 | 116 | 20 | Beaverbrook | 12/7.2kV | BBF2 | Blue phase cable replacement. | Kanata | Scheduled Outage | Preventive Maintenance
5507 | 2004 | 7 | 16 | 0.44375 |  | 101 | 41 | 25 |  | 13.2kV | BBF2 | S55-3 fuse blew due to defective cable between T450 & T2517. Cable was isolated and power restored | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3754 | 2003 | 7 | 17 | 0.38472 |  | 333 | 61 | 11 | Beaverbrook | 12/7.2kV | BBF2 | Isolation of the transformer to install new transformer,cables and connection. | Kanata | Scheduled Outage | Preventive Maintenance
4176 | 2003 | 9 | 29 | 0.60833 |  | 453 | 117 | 18 | Beaverbrook | 8/4.8kV | BBF2 | Tx3058 & Tx3113 taken out of service to install new cables. | Kanata | Scheduled Outage | Construction
4198 | 2003 | 10 | 2 | 0.37153 |  | 493 | 164 | 20 | Beaverbrook | 12/7.2kV | BBF2 | Beaverbrook cable replacement. | Kanata | Scheduled Outage | Construction
4215 | 2003 | 10 | 6 | 0.35764 |  | 465 | 151 | 21 | Beaverbrook | 12/7.2kV | BBF2 | Part of transformer and cable replacement. Trans 3115 restored first and TX3057 restored 16:20. | Kanata | Scheduled Outage | Construction
9676 | 2006 | 11 | 17 | 0.074306 |  | 84 | 988 | 1104 | Beaverbrooke | 12/7.2kV | BBF2 | BBF2 tripped due to suspected cable fault between S26 and S295. Sectionalized to restore power. Note: BBF2 is carrying the SMF2, and SMF3 circuits as well. | Kanata | Defective Equipment
5922 | 2004 | 11 | 25 | 0.38125 |  | 126 | 44 | 21 | Beaverbrook | 12/7.2kV | BBF2 | Transformers TX2583 & TX3069 isolated to replace cable section. 23 Customers affected in power outage on Leacock st. | Kanata | Scheduled Outage | Repair
5926 | 2004 | 11 | 25 | 0.56736 |  | 76 | 16 | 13 | Beaverbrook | 12/7.2kV | BBF2 | Transformers 450 & 2517 isolated to allow crews to replace cables. Outage effected 13 customers on Leacock in Kanata. | Kanata | Scheduled Outage | Construction
15559 | 2009 | 12 | 27 | 0.015972 |  | 171 | 1154 | 405 | Beaverbrook | 12/7.2kV | BBF5 | Circuit opened and locked out. Circuit was patrolled no problems were found. Circuit was closed in via csada. All customers were restored at 03:14 | Kanata | Adverse Weather | Ice Storm
7290 | 2005 | 9 | 8 | 0.39514 |  | 2 | 3 | 100 |  | 12/7.2kV | BBF8 | Planned outage to isolate transformer 3764 on the BBF8, 10 transformers were interrupted due to out of phase condition. | Kanata | Scheduled Outage
7298 | 2005 | 9 | 9 | 0.37847 |  | 237 | 32 | 8 | Beaverbrook | 12/7.2kV | BBF8 | Isolation of transformer 3764 at 17 Beaufort St, Kanata to change transformer and clean up oil spill. | Kanata | Scheduled Outage
7331 | 2005 | 9 | 15 | 0.38958 |  | 519 | 112 | 13 | Beaverbrook | 12/7.2kV | BBF8 | Transformer # 4135 was isolated to all crews to change transformer & clean up oil spill.13 Customer effected by outage. | Kanata | Scheduled Outage | Repair
13394 | 2008 | 10 | 20 | 0.39375 |  | 109 | 20 | 11 | Beaverbrook | 12/7.2kV | BBF8 | TP5491 at 47 Bering isolated to allow crew change xfmr due to PCB. 11 customers | Kanata | Scheduled Outage | Preventive Maintenance
13405 | 2008 | 10 | 22 | 0.35625 |  | 251 | 54 | 13 | Beaverbrook | 8/4.8kV | BBF8 | TP5424 at 29 McClintock was isolated to replace PCB contaminated transformer | Kanata | Scheduled Outage | Construction
13422 | 2008 | 10 | 24 | 0.38194 |  | 140 | 23 | 10 | Beaverbrook | 13.2kV | BBF8 | TP5489 @ 66 McClintock way was isolated to allow the crew to change the transformer because it contains PCB. | Kanata | Scheduled Outage | Repair
7580 | 2005 | 11 | 8 | 0.40625 |  | 169 | 34 | 12 | BEVERBROOK | 12/7.2kV | BBF8 | ISOLATION OF XMER 3842 FROM HYDRO OTTAWA SOURCES TO CHANGE TRANSFORMER ON MCCLITION WAY. | Kanata | Scheduled Outage | Repair
13598 | 2008 | 11 | 12 | 0.38889 |  | 270 | 54 | 12 | Beaverbrook | 12/7.2kV | BBF8 | Transformers TP5507 @ 21 chimo and T5943 @ 5 Inuvik were isolated to replace both transformers. | Kanata | Scheduled Outage | Repair
6784 | 2005 | 6 | 23 | 0.23958 |  | 60 | 760 | 760 | Beaverbrook | 13.2kV | BBT2 | Squirrel contact caused Beaverbrook T2 transformer to open. | Kanata | Foreign Interference | Animal
16871 | 2010 | 9 | 4 | 0.43264 |  | 355 | 1211 | 260 | Bridlewood | 27.6/16kV | BDRF3 | A cable fault bet S12-3 W phase(78 Victor) and switch 681(4 Greer) in Stittsville | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
14049 | 2009 | 3 | 13 | 0.91528 |  | 295 | 17163 | 3965 | Beacon Hill | 8/4.8kV | Beacon Hill | Station fire caused failure of Beacon Hill MS. All load was recovered from outside stations | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13341 | 2008 | 10 | 8 | 0.48264 |  | 170 | 112 | 60 | 3F5 | 8/4.8kV | Beacon hill | white phase cable fault between TP3960 & TP3961 on 3F5 circuit @ 521 Rivershore Dr. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
13851 | 2009 | 1 | 9 | 0.41667 |  | 70 | 32 | 27 | BECKWITH | 27.6/16kV | Bechwith F2 | Transformer Switch S22563 located at Westleigh Blvd & Carlisle Circle isolated to allow for load transfer | Goulburn | Scheduled Outage | Load Shedding
4670 | 2004 | 1 | 3 | 0.48125 |  | 370 | 42 | 25 | Beckwith | 27.6/16kV | Beck F2 | Vehicle accident at 7510 Flewellyn Rd. | Goulburn | Foreign Interference | Vehicle
4835 | 2004 | 2 | 28 | 0.66806 |  | 63 | 2 | 2 | Beckwith | 27.6/16kV | beck F2 | Andy reports transformer #8080 on Fallowfield fuse found opened. Transformer was refused and closed. All load restored to normal. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
20107 | 2012 | 3 | 3 | 0.53889 |  | 311 | 1078 | 208 | Beckwith | 27.6/16kV | Beck F2 | Beckwith F2 W phase tripped, H - 1 crew to restore. FCI at entrance to Hydro - Ottawa service territiry clear indicating problem on H - 1 side. | Goulburn | Loss of Supply | HEPC Circuit Fault
20115 | 2012 | 3 | 3 | 0.54097 |  | 331 | 3360 | 609 | Beckwith | 27.6/16kV | Beck F2 | loss of supply on Beckwith F2 circuit. Hydro one crews made repairs and restored load. | Goulburn | Loss of Supply | HEPC Circuit Fault
6363 | 2005 | 4 | 4 | 0.55556 |  | 2 | 1 | 30 | Beckwith | 27.6/16kV | Beck F2 | When resetting RX2005 at Dwyer Hill & Flewelyn, the white phase tripped open, same was closed back in & held. | Goulburn | Human Element | Switching Errors
16021 | 2010 | 4 | 30 | 0.43333 |  | 95 | 100 | 63 | Beckwith | 27.6/16kV | Beck F2 | A defective arrestor at 8900 McLinton caused SW1500 fuse to blow & RX2024 white phase to open/reclose/lockout. Arrestor was replaced & all power restored. Customers on Dwyer Hill Rd, McCaffrey Trail, Copeland & McLinton were affected. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
10515 | 2007 | 6 | 2 | 0.73542 |  | 171 | 3 | 1 | BECKWITH | 27.6/16kV | BECK f2 | Transformer fuse found blown at 7928 Flewellyn. 24/7 replaced fuse all power restored. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
12548 | 2008 | 6 | 4 | 0.5625 |  | 160 | 3 | 1 | Beckwith | 27.6/16kV | Beck F2 | Defective Tx at 2586 Dwyer Hill rd isolated & replaced. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
16241 | 2010 | 6 | 10 | 0.18125 |  | 74 | 1 | 1 |  | 8/4.8kV | BECK F2 | 6736 Flewellyn reported no power, crew repaired broken switch and re-fused | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
5410 | 2004 | 6 | 30 | 0.74722 |  | 122 | 2 | 1 | Beckwith | 27.6/16kV | Beck F2 | Transformer 2070 at 2070 Munster Rd transformer fuse replaced. | Goulburn | Foreign Interference | Bird
14880 | 2009 | 7 | 29 | 0.92917 |  | 132 | 2 | 1 | Beckwith | 27.6/16kV | beck F2 | 24/7 reports fuse S22559 found opened at the road at 8490 Mcarton Rd. Transformer fuse replaced and closed all power restored. | Kanata | Unknown/Other | No Apparent Cause
5633 | 2004 | 8 | 10 | 0.44444 |  | 5 | 23 | 279 | Beckwith | 27.6/16kV | Beck F2 | Beckwith F2 feeder interrupted due to a trip of the Hydro One circuit feeding Beckwith DS. | Goulburn | Loss of Supply | HEPC Circuit Fault
11456 | 2007 | 10 | 3 | 0.55208 |  | 170 | 283 | 100 | Beckwith | 27.6/16kV | Beck F2 | W phase at H - 1 switch 34 supplying Hydro Ottawa section on BeckF2 blew. Hydro -Ottawa portion of line patrolled, no problems found. H - 1 found a tree on the line upstream of switch 34. Tree cleared & switch re-fused by H - 1. | Goulburn | Tree Contacts | Tree Limb Fallen
4239 | 2003 | 10 | 9 | 0.41667 |  | 1687 | 28 | 1 | beckwith | 27.6/16kV | beck F2 | Al Cooney reports private pole line pulled down dump truck at Cavanaugh construction. Dundas power to make repairs on Oct 10. | Kanata | Foreign Interference | Vehicle
4648 | 2003 | 12 | 22 | 0.85417 |  | 60 | 1 | 1 | Beckwith | 27.6/16kV | beck F2 | S. Cunningham reports fuse linkage had pulled apart. Fuse repalaced power restored. 1 customer affected in power outage. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
17468 | 2011 | 1 | 5 | 0.39583 |  | 115 | 4 | 2 | BECKWITH | 27.6/16kV | BECKF2 | isolated and replaced transformer X10975 at 8665 Flewellyn Rd | Goulburn | Scheduled Outage | Construction
13885 | 2009 | 1 | 22 | 0.45833 |  | 25 | 29 | 70 | Beckwith | 27.6/16kV | BeckF2 | A Cooney has moved S28075 from White phase to Blue phase on the BeckF2. Planned outage to approx 70 customers for 25min. In the Hwy7 & Westleigh area. | Goulburn | Scheduled Outage | Preventive Maintenance
15704 | 2010 | 2 | 3 | 0.4375 |  | 215 | 150 | 50 | Beckwith DS | 27.6/16kV | BECKF2 | A cracked arrester on McCaffrey Trail caused RX2024 White phase to open. Circuit was restored in sections to determine route cause. Arrester was replaced by 24/7 crew and all power restored. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
15902 | 2010 | 4 | 7 | 0.54167 |  | 30 | 1 | 1 | BECKWITH | 27.6/16kV | BECKF2 | Transformer X08615 at 3109 Ashton Station Rd isolated to allow for lightning arrestor change | Goulburn | Adverse Weather | Lightning
20413 | 2012 | 4 | 30 | 0.25417 |  | 144 | 12 | 5 | Beckwith | 27.6/16kV | BECKF2 | replaced blown fuse for transformer X32143 at 6 Sawgrass Cir primary bushing flashed over cause unknown (Crew cleaned primary transformer bushing and rerstored power) | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
18165 | 2011 | 5 | 16 | 0.79861 |  | 60 | 28 | 28 | Beckwith | 27.6/16kV | BECKF2 | RX2005 B phase opened due to a defective lightening arrestor on Hazeldean Rd. Crews cleared the defective equipment and restored the load to normal. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
14408 | 2009 | 5 | 25 | 0.3375 |  | 274 | 5 | 1 | Beckwith | 27.6/16kV | BeckF2 | Transformer #X11033 located at 8399 Mccaffrey Trail isolated due to squirrel contact, replaced switch | Goulburn | Foreign Interference | Animal
16341 | 2010 | 6 | 27 | 0.85694 |  | 120 | 4 | 2 | Beckwith | 27.6/16kV | BECKF2 | Dump truck has pulled down overhead conductor at transformer X08478at 1345 Ashton Station Rd which caused it to open. | Goulburn | Foreign Interference | Vehicle
14651 | 2009 | 6 | 30 | 0.72083 |  | 97 | 2 | 1 | Beckwith | 27.6/16kV | BeckF2 | Transformer #X32128 located at 7731 Fernbank isolated, cause unknown | Goulburn | Unknown/Other
16500 | 2010 | 7 | 20 | 0.39375 |  | 173 | 3 | 1 | Beckwith | 27.6/16kV | BeckF2 | Transformer #X11028 located at 8470 Mccaffrey Trail opened due to squirrel contact | Goulburn | Foreign Interference | Animal
16569 | 2010 | 7 | 27 | 0.37708 |  | 82 | 15 | 11 | Beckwith |  | BECKF2 | Bird came into contact with the overhead circuit on Abb rd in Goulburn caused the RX2038 to open, crew refused and closed all load restored. | Goulburn | Foreign Interference | Bird
18882 | 2011 | 8 | 4 | 0.60486 |  | 1 | 10 | 573 | Beckwith | 27.6/16kV | BECKF2 | Loss of supply from Hydro One. | Goulburn | Loss of Supply
16814 | 2010 | 8 | 25 | 0.76458 |  | 338 | 6 | 1 | Beckwith | 27.6/16kV | BECKF2 | S11042 fuse was found blown to customer line & O/H transformer at 1251 Ashton Station Rd. No obvious cause was found & switch was refused successfully restoring power. | Goulburn | Unknown/Other
15034 | 2009 | 8 | 31 | 0.275 |  | 114 | 8 | 4 | Beckwith | 27.6/16kV | BECKF2 | Transformer #X32127 located at 33 Sawgrass isolated due to bird contact | Goulburn | Foreign Interference | Bird
16914 | 2010 | 9 | 9 | 0.77292 |  | 253 | 8 | 2 | Beckwith | 27.6/16kV | BECKF2 | Transformer #X11633 located at 7262 Mansfield opened up due to squirrel contact | Goulburn | Foreign Interference | Animal
17007 | 2010 | 9 | 27 | 0.41458 |  | 78 | 1 | 1 | BECKWITH DS | 27.6/16kV | BECKF2 | Transformer X35734 at 8300 Flewellyn Rd refused due to squirrel contact | Goulburn | Foreign Interference | Animal
17013 | 2010 | 9 | 28 | 0.43264 |  | 113 | 8 | 4 | BECKWITH | 27.6/16kV | BECKF2 | Transformer X36419 at 16 Carlisle Circle isolated to allow for repairs to defective U/G | Goulburn | Scheduled Outage | Repair
19314 | 2011 | 10 | 3 | 0.50556 |  | 137 | 402 | 176 | Hydro 1 | 27.6/16kV | BECKF2 | Hydro 1 supply to BECKF2 red phase was interupted, no cause reported, Hydro Ottawa Crews patrolled and found nothing | Goulburn | Loss of Supply | HEPC Circuit Fault
9389 | 2006 | 10 | 5 | 0.40278 |  | 50 | 5 | 6 | Beckwith | 27.6/16kV | BECKF2 | Transformer #1840 located on Munster isolated to change insulators. PC10A #226 | Goulburn | Scheduled Outage | Preventive Maintenance
19346 | 2011 | 10 | 8 | 0.82292 |  | 330 | 6 | 1 | Beckwith | 8/4.8kV | BECKF2 | Customer line fuse blew due animal contact. Beckwith (BECKF2) ID#19346 | Goulburn | Foreign Interference | Animal
9410 | 2006 | 10 | 10 | 0.54167 |  | 55 | 7 | 8 | Beckwith | 27.6/16kV | BECKF2 | Transformer located at 345 Lucas Lane isolated for PCB transformer replacement. PC10A #1056 | Goulburn | Scheduled Outage | Preventive Maintenance
13410 | 2008 | 10 | 22 | 0.78333 |  | 141 | 42 | 19 | Beckwith | 27.6/16kV | BECKF2 | D Howat reported S28075 Blue phase barrel was burned up, did not have replacement barrel so they replaced the switch. 19 customers | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
15316 | 2009 | 10 | 27 | 0.40278 |  | 187 | 31 | 10 | BECKWITH | 27.6/16kV | BECKF2 | Transformer X11032 at 8420 McCaffrey isolated to allow for pole change | Goulburn | Scheduled Outage | Preventive Maintenance
13535 | 2008 | 10 | 30 | 0.56319 |  | 69 | 23 | 20 | Beckwith | 27.6/16kV | BECKF2 | MVA on Ashton Station just north of Copeland brought down the sinlge phase of BECKF2 fed by S21962, requiring that setion to be isolated for rescue and emergency repair | Goulburn | Foreign Interference | Vehicle
17270 | 2010 | 11 | 14 | 0.62917 |  | 129 | 2 | 1 | Beckwith | 27.6/16kV | BeckF2 | A broken switch that feeds transformer 36421. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
11800 | 2007 | 12 | 3 | 0.84028 |  | 430 | 255 | 54 | Beckwith | 27.6/16kV | BECKF2 | White phase at RX2005 opened. Line patrolled with no findings. SW1134 opened and RX2005 closed to restore some customers. Blown arrester found at TX8339 on Fernbank at Dwyer Hill. Lightening arrester cleared, section restored and TX8339 closed back in. All customers restored. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
11879 | 2007 | 12 | 24 | 0.027778 |  | 269 | 1706 | 400 | Beckwith | 27.6/16kV | BeckF2 | Loss of supply from Hydro One, tree on Hydro One's line caused white phase fuse to blow at their switch 258, initial patrol did not reveal any problems, after failed attempt to restore, tree was found and removed, and load was restored in stages to prevent overload. | Goulburn | Loss of Supply | HEPC Circuit Fault
15576 | 2009 | 12 | 26 | 0.70833 |  | 240 | 1696 | 424 | Beckwith | 27.6/16kV | BECKF2 | Hydro One reports loss of supply on the BECKF2 feeder to Hydro Ottawa customers due to continuing ice storm conditions. Repairs made and power restored. | Goulburn | Loss of Supply | HEPC Circuit Fault
15579 | 2009 | 12 | 27 | 0.99097 |  | 18 | 9 | 30 | Beckwith | 27.6/16kV | BECKF2 | Crew isolated overhead line on McCaffrey trail in order to install jumper around cut to restore customers who were out of power during tree removal. | Goulburn | Tree Contacts | Repair
15591 | 2009 | 12 | 29 | 0.5 |  | 270 | 4 | 1 | Beckwith | 27.6/16kV | BECKF2 | R. Carmeron reports tree on customer owned service. Customer removed tree and S19692 was refused & closed. | Goulburn | Tree Contacts | Tree Fallen
18330 | 2011 | 6 | 8 | 0.5625 |  | 20 | 16 | 47 | BECKWITH |  | BECKF3 | WX2017 Rabbit @ 7236 Flewellyn was open to allow crew to change voltage setting on load side. 47 customers were affected. Beckwith (BECKF3) | Goulburn | Scheduled Outage
11913 | 2008 | 1 | 9 | 0.44514 |  | 75 | 139 | 111 | Beckwith | 27.6/16kV | Beckwith F2 | A large tree fell on the O/H in the Westleigh Blvd/HWY 7 causing switch SW909 WB to open. | Goulburn | Tree Contacts | Tree Fallen
13850 | 2009 | 1 | 9 | 0.41667 |  | 62 | 28 | 27 | Beckwith | 27.6/16kV | Beckwith F2 | The crew completed a PC17 to balance load on the Blue and White phase in the Westleigh and HWY 7 area. | Goulburn | Scheduled Outage | Load Shedding
13852 | 2009 | 1 | 9 | 0.54167 |  | 5 | 1 | 17 | BECKWITH | 27.6/16kV | Beckwith F2 | Transformer switch S26916 at Fernbank Rd & Lucas Lane isolated to allow for load transfer | Goulburn | Scheduled Outage | Load Shedding
4745 | 2004 | 1 | 29 | 0.37431 |  | 91 | 2 | 1 | BECKWITH | 27.6/16kV | BECKWITH F2 | Transformer opened to re-arrang plant on primary. 1 Customer affected in power outage at 8715 Copeland Rd. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
13934 | 2009 | 2 | 4 | 0.77569 |  | 225 | 4 | 1 | Beckwith | 27.6/16kV | Beckwith F2 | Trans at 8586 COPELAND ROAD, GOU was re fused and power restored .. Cause was unknown | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
13981 | 2009 | 2 | 13 | 0.99097 |  | 541 | 63 | 7 | Beckwith | 27.6/16kV | Beckwith F2 | Transformer #X32139 located at 24 Sawgrass isolated due to defective cut out | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
17627 | 2011 | 2 | 20 | 0.57431 |  | 68 | 20 | 18 | Beckwith | 27.6/16kV | Beckwith F2 | RX2005 auto close when lightning arrester failed on Lucas Lane and S26918 fused switch open. Arrester changed and S26918 new fuse installed and closed. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
15899 | 2010 | 4 | 7 | 0.96319 |  | 163 | 105 | 69 | Beckwith | 27.6/16kV | Beckwith F2 | Blown fuse found at S10339. Patrolled nothing found new fuse installed and RX2024 opened, fuse blow. Recloser closed blown arrester cut clear and S10339 closed. | Goulburn | Lightning | Lightning Strike on Adjacent Circuit Flashed Over
10314 | 2007 | 4 | 23 | 0.96875 |  | 70 | 163 | 140 | Beckwith | 27.6/16kV | Beckwith F2 | While attempting to transfer 43F3 load to BeckwithF2 through rabbits at Dwyer Hill & Bleeks, the 43F3 was opened & SW424 supplying the rabbits failed to operate, 43F3 supply was restored to normal but 2 phases of Beckwith F2 opened on the attempted close of SW424. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
14213 | 2009 | 4 | 25 | 0.74722 |  | 8 | 67 | 500 | Beckwith | 27.6/16kV | Beckwith F2 | Hydro One reports loss of supply to Almonte TS which supplies Beckwith. No root cause reported. | Goulburn | Loss of Supply | HEPC Station Fault
8366 | 2006 | 5 | 29 | 0.079167 |  | 126 | 34 | 16 | Beckwith | 27.6/16kV | Beckwith F2 | The RX2005 recloser R phase opened when a thunderstorm went through the area. | Goulburn | Adverse Weather | Lightning
10557 | 2007 | 6 | 8 | 0.73125 |  | 2 | 50 | 1500 | Beckwith | 27.6/16kV | Beckwith F2 | Loss of supply to Beckwith station. Beckwith F2 customers affected in power outage. | Goulburn | Loss of Supply | HEPC Circuit Fault
10623 | 2007 | 6 | 13 | 0.68403 |  | 15 | 8 | 30 | Beckwith | 27.6/16kV | Beckwith F2 | While switching a lightning arrestor blew on the white phase causing 714 W to open, arrestor was cleared and recloser reset | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
10666 | 2007 | 6 | 19 | 0.65972 |  | 16 | 395 | 1480 | Beckwith | 27.6/16kV | Beckwith F2 | Hydro One M29C 230 Kv circuit had 3 auto trips while a thunderstorm had been passing over. | Goulburn | Loss of Supply | HEPC Circuit Fault
12714 | 2008 | 6 | 23 | 0.59028 |  | 50 | 135 | 162 | Beckwith | 27.6/16kV | Beckwith F2 | Customer calls indicated loss of W phase supply from H-1. When on call crew was able to check potential at metering unit (supply point from H - 1), all 3 phases were live & carrying load. H - 1 reported they experienced no problems with feeder, however, no problems were found on Hydro Ottawa portion. Customers reported power was off for about 50 min. | Goulburn | Loss of Supply | HEPC Circuit Fault
10736 | 2007 | 6 | 26 | 0.37917 |  | 31 | 3 | 6 | Beckwith | 27.6/16kV | Beckwith F2 | 6 customers on Ashton Station Rd fed from SW228 were interrupted to change phase to match Hydro One's supply from SW651. | Goulburn | Scheduled Outage
8629 | 2006 | 6 | 29 | 0.61528 |  | 168 | 526 | 188 | Beckwith | 27.6/16kV | Beckwith F2 | Hydro One Beckwith F2 W & b phase feeds to Hydro Ottawa interupted, Hydro One had numerous problems on their sections of the F2, all repairs completed and power restored, no problems on the Hydro Ottawa sections of the feeder. | Goulburn | Loss of Supply | HEPC Circuit Fault
10778 | 2007 | 7 | 3 | 0.45069 |  | 95 | 3 | 2 | Beckwith | 27.6/16kV | Beckwith F2 | Transformer located at 8767 Mccaffrey Trail isolated due to bird interference (a crow) | Goulburn | Foreign Interference | Bird
8663 | 2006 | 7 | 4 | 0.80556 |  | 345 | 748 | 130 | Beckwith | 27.6/16kV | Beckwith F2 | The Beckwith F2 W phase recloser opened due to many problems on the Hydro One side of the feeder, severe wind storm has caused heavy tree damage. | Goulburn | Loss of Supply | HEPC Circuit Fault
5480 | 2004 | 7 | 12 | 0.36806 |  | 180 | 3 | 1 | Beckwith | 27.6/16kV | Beckwith F2 | Transformer 8657 at 8657 McCaffrey Tr. was changed affecting one customer | Goulburn | Unknown/Other
12866 | 2008 | 7 | 16 | 0.25556 |  | 8 | 27 | 202 | Beckwith | 27.6/16kV | Beckwith F2 | Hydro one lost 230KV (M29C which interrupted Almonte T. S. which caused loss of power to beckwith and Wonderland stations. | Goulburn | Loss of Supply
8867 | 2006 | 7 | 29 | 0.375 |  | 93 | 170 | 110 | Beckwith | 27.6/16kV | Beckwith F2 | Reports of no power calls on Beckwith F2 Blue phase. 24/7 patrolled Hydro Ottawa owned Beckwith F2 and Hydro One patrolled their line and found Hydro One switch blown at 9th line and Hwy 15. Cause unknown. Hydro One refused switch and closed. All power restored. | Goulburn | Loss of Supply
10975 | 2007 | 8 | 1 | 0.9375 |  | 415 | 350 | 80 | Beckwith | 27.6/16kV | Beckwith F2 | Apparent defective lightning arrestor on the blue phase at 7 Lucas caused the outage, a defective recloser extended it. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
8929 | 2006 | 8 | 4 | 0.58264 |  | 396 | 7 | 1 | Beckwith | 27.6/16kV | Beckwith F2 | Line switch fuse to transformer 8028 at 8028 Flewellyn Rd was found blown due to defective transformer Transformer replaced and power restored | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
3890 | 2003 | 8 | 11 | 0.66667 |  | 10 | 0 | 1 | Beckwith | 27.6/16kV | Beckwith F2 | During drive by patrol, crew found fuse open at 10117 Flewelyn rd, Tx10117R10 feeding 1 customer. Not known when fuse opened, no apparent cause found. Fuse replaced & power restored. | Goulburn | Unknown/Other | No Apparent Cause
8984 | 2006 | 8 | 16 | 0.52083 |  | 25 | 1 | 3 | Beckwith | 27.6/16kV | Beckwith F2 | Transformer located at 62 Links Dr isolated to change lightning arrestor | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
11083 | 2007 | 8 | 16 | 0.65069 |  | 263 | 4 | 1 | Beckwith | 27.6/16kV | Beckwith F2 | Transformer located at 7928 Flewellyn Rd due to lightning & storm | Goulburn | Adverse Weather | Lightning
11107 | 2007 | 8 | 20 | 0.36458 |  | 80 | 1 | 1 | Beckwith | 27.6/16kV | Beckwith F2 | Transformer located at 8300 Flewellyn isolated due to animal interference | Goulburn | Foreign Interference | Animal
14978 | 2009 | 8 | 20 | 0.82292 |  | 58 | 464 | 480 | BECKWITH | 27.6/16kV | BECKWITH F2 | Hydro One lost the 230 Kv circuit feeding their stations due to severe thunderstorm affecting the Beckwith F2 and Wonderland F2 | Goulburn | Loss of Supply | HEPC Station Fault
9076 | 2006 | 8 | 28 | 0.38194 |  | 70 | 2 | 2 | Beckwith | 8/4.8kV | Beckwith F2 | AT 09:10 Trans 8704 at 8704 Copeland Rd isolated in order to upgrade insulators and arrestor | Goulburn | Scheduled Outage | Preventive Maintenance
3968 | 2003 | 8 | 29 | 0.61806 |  | 452 | 67 | 30 | Beckwith | 27.6/16kV | Beckwith F2 | White phase transfromer at 7315 Fernbank Rd General Dynamics Ltd. Tom McNealey of General Dynamics was notified of power out to Building and that we will be changing transformer. He has okayed power to stay off till Tuesday. Tom M Home # 864-0321 Work # 596-7109. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
9117 | 2006 | 9 | 4 | 0.28125 |  | 160 | 5 | 2 | Beckwith | 27.6/16kV | Beckwith F2 | Transformer located at 8455 Fallowfield isolated due to animal contact. Also, caused in-line switch #1261 to open. | Goulburn | Foreign Interference | Animal
9140 | 2006 | 9 | 7 | 0.42917 |  | 167 | 6 | 2 | Beckwith | 27.6/16kV | Beckwith F2 | 8 Kv O/H section at Copeland & Dwyer Hill isolated for construction of new line. | Goulburn | Scheduled Outage | Construction
15074 | 2009 | 9 | 9 | 0.32708 |  | 2 | 16 | 481 | BECKWITH | 27.6/16kV | BECKWITH F2 | Hydro One 230kv cct, M29C tripped, and the cause is being investigated. All load restored at 7:52. | Goulburn | Loss of Supply
13234 | 2008 | 9 | 15 | 0.15278 |  | 170 | 156 | 55 | Beckwith | 27.6/16kV | Beckwith F2 | Tree on wire at Canadian Golf course sub division of Hwy 7. Crews cleared overhead and refused S28975 on Westleigh Blvd. | Goulburn | Adverse Weather | Wind
15115 | 2009 | 9 | 17 | 0.375 |  | 173 | 23 | 8 |  | 27.6/16kV | Beckwith F2 | S21822 opened, to add 2 new phases to complete 3 phase line. 8 customers affected on Foster Rd. | Goulburn | Scheduled Outage
7343 | 2005 | 9 | 18 | 0.67708 |  | 55 | 1 | 1 | Beckwith | 27.6/16kV | Beckwith F2 | Bird contacted o/h line at 7296 Mansfield Dr. 24/7 Refused transformer 7296 to restore power. | Goulburn | Foreign Interference | Bird
4174 | 2003 | 9 | 28 | 0.94375 |  | 72 | 360 | 300 | Beckwith | 27.6/16kV | Beckwith F2 | Fire Department requested Hydro One to turn off power due to traffic Accident. 300 customers supplied from Beckwith F2 out. | Goulburn | Loss of Supply | Emergency Services Request
5861 | 2004 | 11 | 5 | 0.43403 |  | 139 | 70 | 30 |  | 27.6/16kV | Beckwith F2 | Peter Barr reports tree fallen, leaning on bell service. Recloser 714blue closed and holding | Goulburn | Tree Contacts | Tree Fallen
5868 | 2004 | 11 | 7 | 0.34653 |  | 53 | 1 | 1 | Beckwith | 27.6/16kV | Beckwith F2 | Transfomer at 8216 Fallowfield interrupted by squirrel. Transformer re-fused successfully. | Goulburn | Foreign Interference | Animal
9624 | 2006 | 11 | 9 | 0.52083 |  | 80 | 120 | 90 | Beckwith | 27.6/16kV | Beckwith F2 | Vehicle accident broken pole on Dwyer Hill at Fallowfield. Recloser 714 open to remove truck and make temporary pole repair. | Goulburn | Foreign Interference | Vehicle
15429 | 2009 | 11 | 27 | 0.62639 |  | 218 | 151 | 59 | Beckwith | 27.6/16kV | Beckwith F2 | RX2024 white phase tripped & locked out. Initial patrol did not reveal any obvious cause. RX2024 W was manually closed which caused S10339 fuse at Copeland & Dwyer Hill Rd to blow. The defective section was further sectionalized and patrolled in detail which revealed a defective arrestor on Ashton Station Rd. The arrestor was cut clear & all power restored. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
15504 | 2009 | 12 | 13 | 0.14583 |  | 263 | 456 | 424 | Beckwith | 27.6/16kV | Beckwith F2 | Customers from Beckwith F2 off loaded from and picked up from Alexander DS. H1 did not want to make and break parrallel. H1 adding bus pots at Almonte TS. 40 transfer customers at 8Kv out for the total duration. H1 had trouble with cold load pick up on the 40 transfer customers which delayed full restoration. | Goulburn | Scheduled Outage | Construction
6098 | 2004 | 12 | 25 | 0.61597 |  | 123 | 25 | 12 | Beckwith F2 | 27.6/16kV | Beckwith F2 | Blown arrester on transformer at 8283 Fernbank Rd, SW716W at Fernbank & Dwyer Hill opened. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
6099 | 2004 | 12 | 25 | 0.66667 |  | 50 | 42 | 50 | Beckwith F2 | 27.6/16kV | Beckwith F2 | Recloser RX2005 W phase opened during restoration attempts to restore O/H section on Fernbank Rd. | Goulburn | Defective Equipment
15588 | 2009 | 12 | 29 | 0.52431 |  | 145 | 140 | 58 | Beckwith F2 | 27.6/16kV | Beckwith F2 | RX2024 White phase reclosures highside fuse found blown. White phase reclosure bypass fused closed restoring load. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
6147 | 2005 | 1 | 22 | 0.7 |  | 322 | 268 | 50 | Beckwith | 27.6/16kV | Beckwith F3 | There was a vehicle accident that hit a pole at 8025 Fallowfield Rd which caused an insulator to break on the R phase. | Goulburn | Foreign Interference | Vehicle
6609 | 2005 | 5 | 26 | 0.73472 |  | 49 | 2 | 3 |  | 27.6/16kV | BeckwithF2 | Isolated o/h line on Jenkinson Side Road to repair broken insulator. | Goulburn | Defective Equipment
16337 | 2010 | 6 | 27 | 0.28819 |  | 365 | 122 | 20 | Beckwith | 27.6/16kV | BeckwithF2 | The O/H on Ashton Station rd was isolated to allow Hydro One crews and Ottawa Hydro crews convert the 4.8Kv to 27.6 | Goulburn | Scheduled Outage | Construction
16858 | 2010 | 9 | 3 | 0.65 |  | 77 | 335 | 261 | Beechwood | 4.16kV | Beechwood | UB04 circuit auto reclosed autoed, at the same time UB06 auto reclosed. 24/7 crew found a tree growing up thru circuits. Trimming was done to clear and remove branches. (St. Laurent /Arundel) | Ottawa | Tree Contacts | Inadequate Trimming
15510 | 2009 | 12 | 13 | 0.71875 |  | 39 | 6 | 10 | 47F4 | 8/4.8kV | Bells Corners | Transformer #X33014 @ the rear of 17 Quintall. Was opened to allow 24/7 to repair secondary covers. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
16800 | 2010 | 8 | 23 | 0.85417 |  | 116 | 2230 | 3717 | Beacon Hill | 8/4.8kV | BHTT1 | SCADA reports Gas Detected at BHTT1 & Hydro One reported 48M5 auto reclosed, crews found 2 high side fuses to T1 were blown. BHTT1-L is close to defective transformer, Hydro Ottawa Requested H1 to OPEN 48M5. BHTT1 isolated and all power restored | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5078 | 2004 | 4 | 30 | 0.44583 |  | 75 | 19 | 15 | 77M5 | 27.6/16kV | Billberry | TE3103 isolated to replace leaking transformer on Des Pruches st. All power restored at 11:57. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
13864 | 2009 | 1 | 14 | 0.047917 |  | 346 | 52 | 9 |  | 8/4.8kV | Black Corner F1 | Recloser 692 on Hydro 1 feeder opened affecting 9 transfer customers. | Goulburn | Loss of Supply | HEPC Circuit Fault
17329 | 2010 | 11 | 23 | 0.54167 |  | 180 | 18 | 6 | Blacks Corners | 8/4.8kV | Black Corner F1 | Hydro One reports S676 switch fall open nocause found. Switch was closed restoring power to 6 transfer customers in the area of 4195 Ashton Station Rd | Goulburn | Loss of Supply
3711 | 2003 | 7 | 9 | 0.86111 |  | 28 | 839 | 3161 | BLACKBRUN | 8/4.8kV | BLACKBURN | 48M3 CIRCUIT AUTO RECLOSED, Also 4F1,4F4 scada ind curcuits locked out. Hydro One opened 48M3 circuit due to large unbalance in load. 24/7 dispatched to Blackburn station. D. Hawett reports 4T1 fuse switch is damaged, and blown open. T1 transformer was isolated. Also 4F1 & 4F4 insulators found broken on overhaed but can be energized. All load restored as of 20:58. | Gloucester | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
15419 | 2009 | 11 | 24 | 0.97917 |  | 350 | 29 | 5 | Blacks Corners | 8/4.8kV | Blacks Cor. F1 | H - 1 rpts broken insulator @ Blacks corners DS, station isolated to make repairs. 5 Hydro Ottawa customers affected on Ashton Station rd. | Goulburn | Loss of Supply | HEPC Station Fault
3516 | 2003 | 6 | 4 | 0.53681 |  | 373 | 359 | 90 | Bridlewood | 27.6/16kV | BRD F1 | A defective U/G primary cable caused a switch in sectionalizer S39 to rupture. The crews, going on false assumptions from the fault indicators in the transformers showing them the wrong information isolated the wrong stretch of cable. When the stretch of transformers were re-energized it caused a larger outage by rupturing a fuse in sectionalizer S76 it also caused transformer#462 to go defective. The defective cable was then truly located and isolated. Some of the affected customers were re-energized, the defective transformer was changed and the remaining customers re-energized. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
9956 | 2007 | 1 | 22 | 0.3625 |  | 353 | 11449 | 5032 | Bridlewood | 27.6/16kV | BRD F2 | Defective cable section between S607-2 and Switch 86 caused the Bridlewood F1 to trip, which was also carrying the Bridlewood F2. During sectionalizing, the Bridlewood F1 tripped again due to another cable fault between S68 and S210. The Bridlewood F3 tripped once while attempting to restore the Bridlewood Faulted circuit. All power restored at 10:26 am. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
10357 | 2007 | 5 | 3 | 0.43403 |  | 35 | 1 | 2 | Bridlewood | 27.6/16kV | BRD F2 | Transformer #NP000166 located at 5044 Hope Side Rd isolated to reconnect after a fire | Kanata | Scheduled Outage | Construction
9957 | 2007 | 1 | 22 | 0.34514 |  | 1 | 12 | 700 | BRIDLEWOOD | 27.6/16kV | BRD F3 | The Bridlewood F3 tripped during sectionalizing of the Bridlewood F1 circuit. Defective cable was found between S86 and S607-2 | Kanata | Defective Equipment
4393 | 2003 | 11 | 5 | 0.38889 |  | 116 | 97 | 50 | Bridlewood | 27.6/16kV | Brd F4 | B. Seaman reports TX1187, 1190, 1191, 1192, 1193, & 1194 are now isolated to install 2 new transformer. 50 customers effected in this planned outage. All power was restored at 11:16. | Kanata | Scheduled Outage | Construction
15487 | 2009 | 12 | 8 | 0.375 |  | 275 | 32 | 7 | Bridlewood | 8/4.8kV | BRD F6 | Isolated transformer X06394 at 25 Country Lane for Maintenance work | Kanata | Scheduled Outage | Construction
3953 | 2003 | 8 | 20 | 0.75347 |  | 260 | 4 | 1 | Briddlewood | 27.6/16kV | BRD OCR2 | Cable feeding TE1533 was dug up by contractor insalling underground service for street lighting at Terry fox and Edgewater. One customer was affected. | Kanata | Foreign Interference | Dig-in
10027 | 2007 | 2 | 14 | 0.5625 |  | 5 | 333 | 4000 | Bridlewood | 27.6/16kV | BRD T1 | Outage on BRDT1 due to differential relay protection on BRDT2. Causing 605-S7M switcher & BRDT1 breaker to open. | Kanata | Human Element | Incorrect Protection Settings
3326 | 2003 | 4 | 9 | 0.38125 |  | 65 | 10 | 9 | Bridlewood |  | brd temp f1 | TX227 isolated to replace elbows & inserts. All customers notified of planned outage | Kanata | Scheduled Outage | Repair
3390 | 2003 | 4 | 30 | 0.39931 |  | 74 | 1850 | 1500 | Bridlewood | 27.6/16kV | BRD Temp F1 | During insulator washing, while the spray was directed at a switch, a lead came out of the top of the switch on the 27kv circuit and fell into the 8kv circuit below. Since this circuit was set on hold-off the circuit tripped to lockout. The lead was then cleared and the circuit was restored. A new lead was then installed on the defective switch and power was then restored to the last remaining transformer. This all happened at the corner of Micheal Copeland and Eagleson Roads in Kanata. | Kanata | Defective Equipment
19789 | 2012 | 1 | 5 | 0.42014 |  | 256 | 9 | 2 | Bridlewood MS | 27.6/16kV | BRDF1 | transformer 1143 at 85 Denzil Doyle was isolated so that it could be lifted off it's pad to allow an electrician pull in new secondary cable. | Kanata | Scheduled Outage | Construction
7900 | 2006 | 2 | 7 | 0.41667 |  | 128 | 85 | 40 | Bridlewood | 27.6/16kV | BRDF1 | Sectionalizer S391 on Grassy Plains Dr was isolated to make repairs. | Kanata | Scheduled Outage | Preventive Maintenance
4809 | 2004 | 2 | 20 | 0.56111 |  | 54 | 4 | 4 | Bridlewood | 27.6/16kV | BRDF1 | TX2282 isolate to replace leaking transformer at 70 Nighthawk. 4 Customers effected in power outage. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20039 | 2012 | 2 | 21 | 0.47639 |  | 10 | 657 | 3941 | Bridlewood | 27.6/16kV | BRDF1 | BRDF1 trip under hold off. Nothing reported to fire or police. Breaker closed. Al Cooney to check FCI's. Breaker flagged fault all 3 phases. FCI's lead to S393, noise comimg from inside switch gear. Gear to be isolated and inspected. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20041 | 2012 | 2 | 21 | 0.45833 |  | 90 | 15 | 10 | Bridlewood |  | BRDF1 | At 11h00 crews isolated TP3209 at 15 Inwood to change a defective transformer. 10 customers affected for 90 mins. Bridlewood BRDF1 ID# 20041 | Kanata | Scheduled Outage
3352 | 2003 | 4 | 16 | 0.54167 |  | 64 | 16 | 15 | Bridlewood | 27.6/16kV | BRDF1 | Transformers 1638 & 1473 isolated to replace 1638 with larger transformer. | Kanata | Scheduled Outage | Construction
6436 | 2005 | 4 | 21 | 0.38056 |  | 257 | 557 | 130 |  | 27.6/16kV | BRDF1 | Scheduled outage, to upgrade inserts and elbows. Shetland way, Bridlewood. | Kanata | Scheduled Outage
17980 | 2011 | 4 | 21 | 0.42083 |  | 66 | 10 | 9 | BDRF1 | 27.6/16kV | BRDF1 | TP6841 @ 174 Kinghaven was isolated to allow crew to replace dammaged transformer caused by developper. 9 customers were affected. Bridlewood (BRDF1) | Kanata | Scheduled Outage
6464 | 2005 | 4 | 26 | 0.38125 |  | 216 | 288 | 80 | Bridlewood | 27.6/16kV | BRDF1 | Planned outage to tx loop in Bridlewood for elbow and insert replacement. | Kanata | Scheduled Outage | Preventive Maintenance
5071 | 2004 | 4 | 29 | 0.64444 |  | 181 | 241 | 130 | Bridlewood | 27.6/16kV | BRDF1 | TX1035-1 elbow & insert blown caused s250-4 red phase fuse to blow. Transformer isolated to make temp repairs. A second outage will be required to complete the repairs. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6477 | 2005 | 4 | 29 | 0.38056 |  | 214 | 535 | 150 | Bridlewood | 27.6/16kV | BRDF1 | 12 white phase transformer insert and elbow replacement in Bridlewood F1 between S76-3 and 1723-2. | Kanata | Scheduled Outage | Repair
6489 | 2005 | 5 | 2 | 0.42361 |  | 274 | 785 | 172 |  | 27.6/16kV | BRDF1 | Planned outage for insert and elbow replacement in Kanata on Filion, Willowglen and Hawley Cres. | Kanata | Scheduled Outage
6493 | 2005 | 5 | 3 | 0.37778 |  | 216 | 259 | 72 | Bridlewood | 27.6/16kV | BRDF1 | Isolated 13 transformer in the Willow Glen Dr area Kanata to change elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
20460 | 2012 | 5 | 4 | 0.52778 |  | 95 | 14 | 9 | Bridlewood | 27.6/16kV | BRDF1 | TP2516 at 125 Palimino was isolated to repair broken insert. | Kanata | Scheduled Outage | Repair
20463 | 2012 | 5 | 4 | 0.53125 |  | 45 | 7 | 9 | Bridlewood | 8/4.8kV | BRDF1 | Isolated transformer TP2516 at 125 Plaomino Dr to replace broken insert. | Kanata | Scheduled Outage | Repair
20498 | 2012 | 5 | 10 | 0.70903 |  | 75 | 9 | 7 | Bridlewood | 27.6/16kV | BRDF1 | Transformer TP2544 at 22 Shetland was isolated to allow crew to replace leaking transformer | Kanata | Scheduled Outage | Repair
3429 | 2003 | 5 | 12 | 0.38056 |  | 207 | 518 | 150 | Bridlewood | 27.6/16kV | BRDF1 | 15 transformers isolated to replace elbows. Transformers located on Tamblyn Cres, & Drainie Dr. 150 customers affected in this outage. | Kanata | Scheduled Outage | Preventive Maintenance
14348 | 2009 | 5 | 13 | 0.63472 |  | 45 | 2339 | 3119 | Bridlewood | 27.6/16kV | BRDF1 | The BRDF1 breaker trip, a broken candle on the back of the breaker was found. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
16082 | 2010 | 5 | 13 | 0.22847 |  | 279 | 130 | 86 | Kanata MTS | 27.6/16kV | BRDF1 | S125-4 B phase fuse opened due to a defective insert at transformer 5678 at 80 Osprey. Transformer was isolated and repaired. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6556 | 2005 | 5 | 14 | 0.25694 |  | 146 | 5 | 2 | Bridlewood | 27.6/16kV | BRDF1 | TE755 & TE1474 isolated to allow crews to change elbows & inserts. | Kanata | Scheduled Outage | Preventive Maintenance
6567 | 2005 | 5 | 17 | 0.38472 |  | 214 | 535 | 150 |  | 27.6/16kV | BRDF1 | Scheduled outage for transformer and elbow replacement on the red phase in Bridlewood. | Kanata | Scheduled Outage
18168 | 2011 | 5 | 17 | 0.40208 |  | 101 | 44 | 26 |  | 27.6/16kV | BRDF1 | Transformer 1320W, 1321W, 1322W on Windfield Cresent were isolated to allow crew to replace leaking transformer and re-arrange elbows to facilitate switching. 26 Customer were affected. Bridlewood (BRDF1) | Kanata | Scheduled Outage
6569 | 2005 | 5 | 18 | 0.38125 |  | 185 | 462 | 150 |  | 27.6/16kV | BRDF1 | Planned outage in Bridlewood - elbow and insert replacement white phase. | Kanata | Scheduled Outage
6575 | 2005 | 5 | 19 | 0.37847 |  | 202 | 673 | 200 | Bridlewood | 27.6/16kV | BRDF1 | 20 transformers in kanata between S75-4 & 684-2 transformers isolated to allow crews to change elbows & inserts. 200 customers affected in planned outage. In the Steeplechase Dr area. | Kanata | Scheduled Outage | Preventive Maintenance
6580 | 2005 | 5 | 20 | 0.38889 |  | 195 | 325 | 100 | Bridlewood | 27.6/16kV | BRDF1 | B. Seaman reports all elbows & inserts have been replaced on white phase transformers on Yoho & Kokanee Gate area. 100 Customers affected in planned power outage. | Kanata | Scheduled Outage | Preventive Maintenance
6617 | 2005 | 5 | 30 | 0.37847 |  | 205 | 393 | 115 | Bridlewood | 27.6/16kV | BRDF1 | 15 transformers isolated in Kanata to allow crews to replace elbows & inserts. In the area of Cedarock, Hanover & Springtree Place. All power restored at 12:30. | Kanata | Scheduled Outage | Preventive Maintenance
12503 | 2008 | 5 | 30 | 0.61458 |  | 42 | 92 | 131 | Bridlewood | 27.6/16kV | BRDF1 | Cable elbow failed at transformer TP3228 while crew was performimg switching causing R phase fuse to open in sectionalizer S76. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6621 | 2005 | 5 | 31 | 0.54792 |  | 5 | 255 | 3061 | Bridlewood | 27.6/16kV | BRDF1 | while energizing bridlewood F1 cable section that was out for elbow and insert replacement an insert at TP2862 blew up causing circuit to open. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
6623 | 2005 | 5 | 31 | 0.37708 |  | 312 | 759 | 146 | BRD | 27.6/16kV | BRDF1 | 16 Tx's in Bridlewood area were isolated for planned elbow & insert upgrade. Saddlehorn, Equestrian, Rein & Stable Way. | Kanata | Scheduled Outage | Preventive Maintenance
18263 | 2011 | 5 | 31 | 0.35903 |  | 493 | 136 | 26 | Bridlewood | 27.6/16kV | BRDF1 | transformers 1320, 1321 and 1322 at 1 Martingale were isolated to allow crews to replace elbows and inserts then remediate the ground for at 1321 | Kanata | Scheduled Outage | Repair
20705 | 2012 | 6 | 7 | 0.37639 |  | 383 | 45 | 7 | Bridlewood | 27.6/16kV | BRDF1 | TP2544 at 22 Shetland isolated for remediation and new base/collar installation | Kanata | Scheduled Outage | Repair
20715 | 2012 | 6 | 8 | 0.17569 |  | 512 | 15535 | 9301 | Bridlewood | 27.6/16kV | BRDF1 | S76-1 Red phase found blown, R phase from S76-1 restored. Defective transformer at TP2544 on Shetland also caused S250-4 R phase to flash -over causing a second outage on BRDF1 which was also carrying BRDF2. Line was restored in sections, S250 isolated for repair & TP2544 replaced before all customers could be restored. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20757 | 2012 | 6 | 13 | 0.37153 |  | 34 | 6 | 10 | Bridlewood | 27.6/16kV | BRDF1 | TP2742R @ 83 Cedarock was isolated to relace broken inserts and elbows. | Kanata | Scheduled Outage | Repair
20758 | 2012 | 6 | 13 | 0.39583 |  | 41 | 5 | 7 | Bridlewood | 27.6/16kV | BRDF1 | Transformer TP2743 @ 5 Springtree was isolated to replace broken insert and elbow. | Kanata | Scheduled Outage | Repair
6746 | 2005 | 6 | 16 | 0.375 |  | 177 | 324 | 110 | Bridlewood | 27.6/16kV | BRDF1 | Isolate transformers and cable in Springwater,Steeplechase, Bridlewood area for elbow and insert replacement. | Kanata | Scheduled Outage | Preventive Maintenance
6780 | 2005 | 6 | 22 | 0.375 |  | 208 | 381 | 110 | Bridlewood | 27.6/16kV | BRDF1 | Insert and elbow replacement on Springwater Dr and Waterton Cres in Bridlewwod. 77 to 131 Springwater Dr odd only and 74 to 90 Springwater even only. All Waterton. | Kanata | Scheduled Outage | Preventive Maintenance
6787 | 2005 | 6 | 23 | 0.37917 |  | 234 | 566 | 145 | Bridlewood | 27.6/16kV | BRDF1 | 13 transformer isolated between Moresby Dr Springwater in Bridlewood area. To change elbows & replace inserts. | Kanata | Scheduled Outage | Preventive Maintenance
3609 | 2003 | 6 | 25 | 0.15069 |  | 395 | 186 | 50 | Bridlewood | 27.6/16kV | BRDF1 | Section of the BRDF1 seperated due to defective transformer 469W, load restored in sections. Transformer replaced and last customers restored. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20873 | 2012 | 6 | 26 | 0.39306 |  | 489 | 82 | 10 | Bridlewood | 27.6/16kV | BRDF1 | Transformer TP2555 at 42 Dartmoor was isolated to allow crew to replace leaking transformer and perform soil remidiation. | Kanata | Scheduled Outage | Repair
8700 | 2006 | 7 | 11 | 0.78611 |  | 231 | 4 | 1 | Bridlewood | 27.6/16kV | BRDF1 | Transformer 671 @ 99 Micheal Cowpland Dr was isolated because it was leaking and the elbows had to be replaced. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
5713 | 2004 | 8 | 24 | 0.4 |  | 524 | 1747 | 200 | Bridlewood | 27.6/16kV | BRDF1 | Transformers in the Palimino & Shetland area of Bridlewood isolated for elbow and insert replacement. | Kanata | Scheduled Outage | Preventive Maintenance
5714 | 2004 | 8 | 24 | 0.7875 |  | 45 | 8 | 10 | Bridlewood | 27.6/16kV | BRDF1 | Transformer TP2546R on Shetland in Bridlewood isolated to replace blown bennet fuse. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
16806 | 2010 | 8 | 24 | 0.66667 |  | 166 | 122 | 44 | Briddlewood | 27.6/16kV | BRDF1 | U/G cable fault from transformer 673-2 to 906-2. 44 customers affected for 166 minutes. | Kanata | Unknown/Other
5726 | 2004 | 8 | 26 | 0.38125 |  | 1 | 4 | 250 | Bridlewood | 27.6/16kV | BRDF1 | The open point pinned on the operating map was incorrect. The actual open point in the loop could not be located, thought to be closed. S76-1B opened and load lost for 1 min. then switch order closed by System. Open point located at T1770B-2 to 1768. | Kanata | Human Element | Incorrect Records
9074 | 2006 | 8 | 28 | 0.30486 |  | 41 | 11 | 16 | Bridlewood | 27.6/16kV | BRDF1 | transformers TP3500 and T1125 isolated to allow crew to correct phasing in BRDF1. | Kanata | Scheduled Outage | Preventive Maintenance
7233 | 2005 | 8 | 29 | 0.36528 |  | 364 | 85 | 50 | Bridlewood | 27.6/16kV | BRDF1 | Transformer TE240 at 500 Eagleson Rd faulted internally causing fire at tx, BRDF1 feeder auto/reclosed. Tx was replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5750 | 2004 | 8 | 30 | 0.37292 |  | 303 | 758 | 200 | BRDF1 | 27.6/16kV | BRDF1 | Planned outage to isolate transformers for upgrades to elbows and inserts. | Kanata | Scheduled Outage
5757 | 2004 | 9 | 1 | 0.39583 |  | 268 | 447 | 100 | Bridlewood | 27.6/16kV | BRDF1 | Isolate transformer on Shetland Way to replace elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
7374 | 2005 | 9 | 25 | 0.0069444 |  | 421 | 42 | 6 | Bridlewood | 27.6/16kV | BRDF1 | TX 240 at 500 Eagleson Rd out for oil spill clean-up. | Kanata | Scheduled Outage | Preventive Maintenance
19279 | 2011 | 9 | 28 | 0.72153 |  | 86 | 11587 | 9400 | Bridlewood |  | BRDF1 | At 17:19 SCADA indicated the BRDF1 breaker open. BRDF1 was also carrying the load from BRDF2 due a problem earlier in the week. Crew found a faulted cable section between the BRDF1 Breaker and SC3149 the first switching center from the station. Bridlewood BRDF1 ID# 19279 | Kanata | Defective Equipment
19586 | 2011 | 11 | 16 | 0.38542 |  | 162 | 62 | 23 | Bridlewood | 27.6/16kV | BRDF1 | At 9:15 crews isolated TP2867 at 8 Stable Way to replace a leaking transformer. Bridlewood BRDF1 ID#19586 | Kanata | Scheduled Outage | Repair
13675 | 2008 | 11 | 28 | 0.40972 |  | 40 | 867 | 1300 | Bridlewood | 27.6/16kV | BRDF1 | All load restore in the Stone heaven area caused found to be swicth SC4323-L2 was to be closed from PC14-22929 item #7 the previous day but was left open. | Kanata | Human Element | Switching Errors
17584 | 2011 | 2 | 15 | 0.375 |  | 260 | 26 | 6 | BRIDLEWOOD | 27.6/16kV | BRD-F1 | Transformer TP6842 at 240 Kinghaven isolated to pull in secondary | Kanata | Scheduled Outage | Construction
15604 | 2010 | 1 | 3 | 0.71875 |  | 98 | 3757 | 2300 | Bridlewood | 27.6/16kV | BRDF2 | BRDF2 breaker opened causing outage to approx 2300 customers . Cause maybe due to cable fault at S27699 to SC3149. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
7783 | 2006 | 1 | 8 | 0.37639 |  | 253 | 413 | 111 | Bridlewood | 27.6/16kV | BRDF2 | Scheduled outage on Equestrian,Trotting way Foxleigh,Bluegrass, in Bridlewood. Elbow insert replacement and switching for overhead outage. | Kanata | Scheduled Outage | Preventive Maintenance
19816 | 2012 | 1 | 11 | 0.36806 |  | 315 | 94 | 18 | Bridlewood | 27.6/16kV | BRDF2 | TP3730 at 101 Artesa Prvt was isolated to allow installation of secondary | Kanata | Scheduled Outage | Construction
7910 | 2006 | 2 | 13 | 0.41667 |  | 32 | 117 | 220 | Bridlewood | 27.6/16kV | BRDF2 | Outage to customers due to nonvented elbows. Load dropped for isolation on Switch342 repair. Stable Way,Pommel,Lane, Harness Crt, Stonehill Crt. | Kanata | Scheduled Outage | Repair
13972 | 2009 | 2 | 13 | 0.2125 |  | 110 | 22 | 12 | Bridlewood | 27.6/16kV | BRDF2 | TP5326 @ Michael Cowpland and Terrence Mathews was isolated for contractor to install new ducts. | Kanata | Scheduled Outage | Construction
20012 | 2012 | 2 | 14 | 0.55208 |  | 45 | 9 | 12 | Bridlewood | 27.6/16kV | BRDF2 | TP3295 at 8 Harness was isolated to replace defective insert. | Kanata | Scheduled Outage | Repair
15789 | 2010 | 3 | 11 | 0.60347 |  | 424 | 7 | 1 | BRIDLEWOOD | 27.6/16kV | BRDF2 | Bridlewood F2 circuit auto reclosed. All load recovered. Circuit to be patrolled. Patrol found S22324 at 5358 Fernbank found burnt at the load side, crews refused | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14047 | 2009 | 3 | 12 | 0.35 |  | 11 | 1043 | 7518 | Bridlewood | 27.6/16kV | BRDF2 | On closing S24796 to make parrallel between BRDF2 (F2 also carrying F1 load) and BRDF3 F2 recloser tripped. Only the red phase load on. In order to close the other 2 phase of switch S24796 safly BRDF3 was opend to drop red phase customers. When S24796 RWB were closed BRDF3 breaker was closed. | Kanata | Unknown/Other
8049 | 2006 | 3 | 21 | 0.40625 |  | 186 | 19 | 6 | Brdlewood | 27.6/16kV | BRDF2 | BRDF2 overhead line section at Terry Fox & Fernbank isolated to rearrange phasing. | Kanata | Scheduled Outage | Construction
8054 | 2006 | 3 | 23 | 0.42222 |  | 2 | 67 | 2000 | Bridlewood | 27.6/16kV | BRDF2 | The F2 tripped while Al Cooney was doing some swtching,there was a hold off inplace. For the final item on OTO 237-1-A the insulator at switch S902 broke while the switch was being open and flashed across. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20208 | 2012 | 3 | 23 | 0.39722 |  | 123 | 4 | 2 | Bridlewood | 27.6/16kV | BRDF2 | two customers on Fernbank were interrupted, for crew to re-sag line and install new switch. | Kanata | Scheduled Outage | Construction
8066 | 2006 | 3 | 25 | 0.67917 |  | 157 | 3 | 1 | Bridlewood | 27.6/16kV | BRDF2 | Reports of broken XMER switch, crew to remove XMER 3700 @ 5977 Hazeldean from service to repair switch. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20286 | 2012 | 4 | 5 | 0.79861 |  | 70 | 16 | 14 | Bridlewood | 27.6/16kV | BRDF2 | Transformer TP5440 @ 1466 Carronbridge was isolated to allow crew to replace a transformer that has been pushed off it's base. | Kanata | Scheduled Outage | Repair
10223 | 2007 | 4 | 8 | 0.98958 |  | 125 | 1676 | 2000 | Bridlewood | 27.6/16kV | BRDF2 | BRDF2 auto reclosed then opened and locked out, cable fault was traced to cable between S607-2 and switch 86 | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
15908 | 2010 | 4 | 8 | 0.38056 |  | 153 | 26 | 10 | Bridlewood | 27.6/16kV | BRDF2 | Transformer 130 @ 25 Gowrie was isolated to allow the crew to replace leaking transformer. | Kanata | Scheduled Outage | Repair
15936 | 2010 | 4 | 14 | 0.39583 |  | 463 | 77 | 10 | Bridlewood | 27.6/16kV | BRDF2 | Transformer 130 at 25 Gowrie was isolated to remediate soil as follow-up to oil spill | Kanata | Scheduled Outage | Repair
12289 | 2008 | 4 | 16 | 0.061806 |  | 111 | 17 | 9 | Bridlewood | 27.6/16kV | BRDF2 | Transformer 162R at 54 Rothesay was replaced by Oncall crew due to oil leak. 9 customers on Rothesay were interrupted. | Kanata | Defective Equipment
20346 | 2012 | 4 | 18 | 0.38889 |  | 295 | 1627 | 331 | Bridlewood | 27.6/16kV | BRDF2 | At 09:20 24 transformers in the Bridlewood area where isolated to allow crews to replace elbow and inserts. 331 customers were affected for 295 minutes. Bridlewood (BRDF2) ID#20346 | Kanata | Scheduled Outage | Preventive Maintenance
20454 | 2012 | 5 | 3 | 0.37847 |  | 360 | 222 | 37 | Bridllewood | 27.6/16kV | BRDF2 | transformer at 101 Artesa Pvt was isolated to allow contractor to install new secondary service. | Kanata | Scheduled Outage | Construction
16140 | 2010 | 5 | 25 | 0.65694 |  | 192 | 440 | 163 | Bridelwood | 13.2kV | BRDF2 | A defective transformer 192 at 11 Baneberry. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20621 | 2012 | 5 | 26 | 0.34792 |  | 561 | 898 | 96 | Bridlewood | 27.6/16kV | BRDF2 | A cable fault bet switch 342 and transformer TP3312 on the B phase on Equestrian Dr and Stable way, the outage took longer then normal because of night before strom and lack of man power. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
12485 | 2008 | 5 | 28 | 0.37847 |  | 327 | 109 | 20 | Bridlewood | 27.6/16kV | BRDF2 | Transformer 162 @ 80 Rothesay was isolated to clean up oil spill. | Kanata | Scheduled Outage | Repair
16162 | 2010 | 5 | 29 | 0.53611 |  | 13 | 0 | 1 | BRIDLEWOOD | 27.6/16kV | BRDF2 | Defective fuse barrel on XFMR X17945 was replaced feeding water control bldg rear of 362 Hillsboro | Kanata | Defective Equipment
20642 | 2012 | 5 | 30 | 0.37847 |  | 185 | 493 | 160 | Bridlewood | 27.6/16kV | BRDF2 | 17 R & W phase Tx's between 636 & 1042 in the Seabrooke / Gowrie area of Kanata South were isolated for elbow & insert upgrades. | Kanata | Scheduled Outage | Preventive Maintenance
18269 | 2011 | 6 | 1 | 0.60972 |  | 135 | 16 | 7 | Bridlewood | 27.6/16kV | BRDF2 | A tree bransch on the wires on Sisson caused the Switch 422 to open, 7 customers affected | Kanata | Tree Contacts | Tree Limb Fallen
12525 | 2008 | 6 | 2 | 0.29514 |  | 100 | 2 | 1 | Bridlewood | 27.6/16kV | BRDF2 | Two fuses were found blown on the overhead switchers feeding a 3-phase pad mount transformer at 480 Brigitta St | Kanata | Adverse Weather | Lightning
10562 | 2007 | 6 | 8 | 0.84722 |  | 199 | 50 | 15 | Bridlewood | 27.6/16kV | BRDF2 | Switch 422 on Scissons opened feeding five transformers. Also one of the transformer fuses was open as well. Crew cleared trees from overhead and refused transformer and switch. | Kanata | Tree Contacts
14525 | 2009 | 6 | 12 | 0.53472 |  | 80 | 5 | 4 | Bridlewood | 8/4.8kV | BRDF2 | Transformer #X06501 located at 168 Rothesay isolated to repair U/G service | Kanata | Scheduled Outage | Repair
6704 | 2005 | 6 | 13 | 0.375 |  | 265 | 486 | 110 | Bridlewood | 27.6/16kV | BRDF2 | Insert and elbow replacement on white phase cable section 2520 by 1819 in Bridlewood. | Kanata | Scheduled Outage | Preventive Maintenance
16269 | 2010 | 6 | 16 | 0.21667 |  | 118 | 14 | 7 | Bridlewood | 27.6/16kV | BRDF2 | BRDF2 auto re-closed and fuse 422 on Scissons Rd. blew. Overhead patroled and nothing found. 422 re-fused and closed. | Kanata | Unknown/Other | No Apparent Cause
8610 | 2006 | 6 | 27 | 0.73611 |  | 226 | 45 | 12 | BRIDLEWOOD | 27.6/16kV | BRDF2 | Crew found S422 ON Scessions Rd open due to tree contact. Crew trimmed trees and refused switch, and closed to pick up customers. | Kanata | Tree Contacts | Inadequate Trimming
8620 | 2006 | 6 | 29 | 0.19583 |  | 632 | 4531 | 2000 | Bridlewood | 27.6/16kV | BRDF2 | Bridlewood F2 feeder tripped due to a faulted sectionalizer S391 on Eagleview in Kanata, load restored in stages. Seactionalizer replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14662 | 2009 | 7 | 3 | 0.90972 |  | 697 | 221 | 19 | Bridlewood | 27.6/16kV | BRDF2 | TP5326 at 80 Micheal Cowpland was isolated to allow contractor to pull in new secondary into new electrical room in the new Home Hardware. | Kanata | Scheduled Outage | Construction
8666 | 2006 | 7 | 5 | 0.39375 |  | 160 | 267 | 100 | Bridlewood | 27.6/16kV | BRDF2 | Section of transformers on BRDF2 from 847B to TX700 out to allow crew to change elbow inserts. 100 customers. | Kanata | Scheduled Outage | Preventive Maintenance
8667 | 2006 | 7 | 5 | 0.54931 |  | 143 | 238 | 100 | Bridlewood | 27.6/16kV | BRDF2 | 8 Transformers isolated to replace connections in the Bridlewood area on the BRDF2 between switch S1068 R and TX700. | Kanata | Scheduled Outage | Preventive Maintenance
8669 | 2006 | 7 | 6 | 0.35625 |  | 168 | 252 | 90 | Bridlewood | 27.6/16kV | BRDF2 | Isolate the cables sect bet transformer 1102W and 700 to change elbows and insert in the Blue grass area. | Kanata | Scheduled Outage | Preventive Maintenance
14776 | 2009 | 7 | 17 | 0.91042 |  | 699 | 221 | 19 | Bridlewood | 27.6/16kV | BRDF2 | Transformer TP5326 at 80 Micheal Cowpland was isolated to allow a contractor to pull in new secondary cables. | Kanata | Scheduled Outage | Construction
8761 | 2006 | 7 | 18 | 0.37639 |  | 199 | 421 | 127 | Bridlewood | 27.6/16kV | BRDF2 | Insert Elbow reolacement Pommel, Harness Lane, Equestrian, Stonehill, Stonehaven. Bridlewwod. | Kanata | Scheduled Outage | Preventive Maintenance
8781 | 2006 | 7 | 19 | 0.375 |  | 200 | 320 | 96 | Bridlewood | 27.6/16kV | BRDF2 | Insert elbow replacement Equestrian and Stable Way Bridlewood area | Kanata | Scheduled Outage | Repair
19062 | 2011 | 8 | 31 | 0.3875 |  | 157 | 24 | 9 | Bridlewood | 27.6/16kV | BRDF2 | At 09:18 trasnformer TP5255 was isolated to allow crew to install new secondary cables. 9 customers were affected for 157 minutes. Bridlewood (BRDF2) ID#19062. | Kanata | Scheduled Outage
9300 | 2006 | 9 | 25 | 0.37847 |  | 271 | 547 | 121 | Bridlewood | 27.6/16kV | BRDF2 | Transformer in the Stonemeadow, Bridlepark area were isolated to allow the crew to change the elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
9303 | 2006 | 9 | 25 | 0.58125 |  | 142 | 286 | 121 | Bridlewood | 27.6/16kV | BRDF2 | Isolation of transformers bet switch 606R to transformer 675R on Huntsman and Equestrian Dr area to change elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
19254 | 2011 | 9 | 25 | 0.675 |  | 123 | 9833 | 5910 | Bridlewood | 27.6/16kV | BRDF2 | BRDF2 recloser failed (exploded) causing A9M1 to trip. Damaged structure @ Bridlewood isolated , A9M1 restored, BRDF2, F4 load restored via alternate supply | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19255 | 2011 | 9 | 25 | 0.675 |  | 102 | 8942 | 5260 | Bridlewood | 27.6/16kV | BRDF2 | BRDF2 recloser re-opened, and eventually blew up on the structure in the substation. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
9310 | 2006 | 9 | 26 | 0.37917 |  | 180 | 699 | 233 | Bridlewood | 27.6/16kV | BRDF2 | Bridlewood elbow insert replacement Huntsman Thunderbird Bridle Park | Kanata | Scheduled Outage | Preventive Maintenance
7478 | 2005 | 10 | 18 | 0.67083 |  | 18 | 540 | 1800 | Bridlewood | 27.6/16kV | BRDF2 | Dump truck contacted BRDF2 neutral. Circuit was on hold off, and no SCADA control. Closed manually. | Kanata | Foreign Interference | Vehicle
7553 | 2005 | 11 | 2 | 0.38194 |  | 195 | 520 | 160 | Bridlewood | 27.6/16kV | BRDF2 | B. Seaman reports RWB cable section between 5650R 2157w-2, 5648B to S3-24. Cable section were isolated to re-arrange plant. | Kanata | Scheduled Outage | Construction
7626 | 2005 | 11 | 16 | 0.70694 |  | 141 | 24 | 10 | Bridlewood | 27.6/16kV | BRDF2 | The transformer 2001 B phase @ 1 Spur was out of power during switching because it had wrong nomenclature. | Kanata | Human Element | Incorrect Records
19613 | 2011 | 11 | 21 | 0.39931 |  | 169 | 28 | 10 | Bridlewood | 27.6/16kV | BRDF2 | Transformer TP3294 @ 14 Pommell was isolated to allow crew to replace transformer. | Kanata | Scheduled Outage | Repair
11789 | 2007 | 11 | 29 | 0.56944 |  | 4 | 133 | 2000 | Bridlewood | 27.6/16kV | BRDF2 | While installing gang operated switch at Terry Fox and Hazeldean contact was made with the overhead circuit under hold-off. No injuries reported, crew and equipment confirmed clear, circuit closed and holding. | Kanata | Human Element | Incorrect Use of Equipment
19710 | 2011 | 12 | 9 | 0.38056 |  | 286 | 248 | 52 | Bridlewood | 27.6/16kV | BRDF2 | TP3726 @ 104 Artesa pvt, was isolated to allow removal of secondary service. | Kanata | Scheduled Outage | Repair
13818 | 2008 | 12 | 30 | 0.18889 |  | 14 | 467 | 2000 | Bridlewood | 27.6/16kV | BRDF2 | BRDF2 breaker A/R/A . Because of high winds and snow, and absense of high amp alarms breaker was closed from scada and held. Circuit to be patrolled during the day. | Kanata | Adverse Weather | Wind
16291 | 2010 | 6 | 25 | 0.42361 |  | 105 | 18 | 10 | Bridlewood | 8/4.8kV | BRD-F2 | Transformer #X6494 located at 116 Glamorgan Dr Kanata opened by crew for electrician to change panel | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
18892 | 2011 | 8 | 8 | 0.29167 |  | 270 | 40 | 9 | Bridlewood | 8/4.8kV | BRD-F2 | Isolated transformer X06399 rear of 39 Country Lane due to pole fire caused by leaking switch Temporary repairs made to the pole | Kanata | Defective Equipment | Equipment Deterioration Due to Age
19590 | 2011 | 11 | 17 | 0.41667 |  | 60 | 10 | 10 | Bridlewood | 27.6/16kV | BRD-F2 | Isolated and replaced transformer TP2155 at 68 Cedar Vally Dr due to oil leak | Kanata | Scheduled Outage | Preventive Maintenance
20792 | 2012 | 6 | 11 | 0.74097 |  | 1 | 96 | 5773 | Bridlewood |  | BRDF2 & F3 | RX2011 opened during switching to reduce loading on BRDT1 transformer. BRDF2 and BRDF3 load was interrupted for one minute. | Kanata | Human Element | Incorrect Protection Settings
15607 | 2010 | 1 | 4 | 0.40278 |  | 70 | 35 | 30 | Bridlewood | 27.6/16kV | BRDF3 | 5 Overhead transformers were opened to allow crews to tranfer overhead circuit from white phase to red phase @ switch 886.On Poole st in Stittsville | Kanata | Scheduled Outage | Repair
19820 | 2012 | 1 | 12 | 0.39097 |  | 252 | 34 | 8 | Bridlewood | 27.6/16kV | BRDF3 | At 09:23 transformer TP3677 at 375 Vendevale was isolated to allow contractor to install new secondary cables. 8 customers were affected for 252 minutes. Bridlewood (BRDF3) ID#19820 | Kanata | Scheduled Outage
17518 | 2011 | 1 | 24 | 0.52431 |  | 99 | 92 | 56 | Bridlewood | 27.6/16kV | BRDF3 | Broken isulator at 40 Fringewood in Stittswiville caused switch 886 B phase to open. Crews made repairs to the insulator and replaced a damaged cutout. All load was restored. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
19887 | 2012 | 1 | 24 | 0.48889 |  | 96 | 3 | 2 | Bridlewood | 27.6/16kV | BRDF3 | TP3677 @ 375 Vendevale was isolated to allow crews to replace secondary fuse in padmount transformer at this location. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6175 | 2005 | 2 | 3 | 0.36458 |  | 317 | 53 | 10 | Bridlewood | 27.6/16kV | BRDF3 | O/H transformer 3084 on Country Lane in Kanata isolated for relocation. | Kanata | Scheduled Outage | Construction
15744 | 2010 | 2 | 25 | 0.41528 |  | 91 | 167 | 110 | Briddlewood | 27.6/16kV | BRDF3 | at 9:58am, o/h sectione from TEMP80 &TEMP63 including 414 isolated to allow crews to string new conductor. 110 cutomers affected for 91 minutes. Briddlewood (BRDF3) ID#15744 | Kanata | Scheduled Outage
17696 | 2011 | 3 | 10 | 0.5 |  | 55 | 1 | 1 | Bridlewood | 27.6/16kV | BRDF3 | Replaced blown fuse at transformer X36338 at 3 Sweetnam Dr | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
8011 | 2006 | 3 | 11 | 0.56597 |  | 383 | 188 | 88 | Bridlewood | 27.6/16kV | BRDF3 | Burnt elbow and insert at transformer 263 at #1 DeCarlo caused the BRDF3 to autoreclose, and S59-3R blow. All customers restored at 13:35, with 8 remaining off until 18:15 hrs. On -call crew believed they could make repairs, but later found that the insert stud was broken and the transformer had to be replaced. | Kanata | Defective Equipment
10106 | 2007 | 3 | 11 | 0.40556 |  | 78 | 910 | 700 | Bridlewood | 27.6/16kV | BRDF3 | Bridlewood F3 opened. Patrolled and No cause found. Sectionalized and load restored. Patrolled again still no cause found. | Kanata | Unknown/Other | No Apparent Cause
6283 | 2005 | 3 | 15 | 0.52986 |  | 1232 | 58 | 3 | Bridlewood | 27.6/16kV | BrdF3 | Crew had problem identifying problem. One transformer had bad main fuse and the second transformer had blown current limiting fuse on the same phase. One transformer was replaced. At 08:50 trans #7779 was reisolated to connect the remaining 2 customers. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
15810 | 2010 | 3 | 16 | 0.59722 |  | 752 | 1128 | 570 | Briddlewood | 27.6/16kV | BRDF3 | Customers reported outage, crews found SC4281-CB3 open, & S59-3 BLUE Phase fuse blown. Further investigation found defective transfomer 296B at 32 Bujold. Transformer replaced by on-call crew | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
17743 | 2011 | 3 | 20 | 0.44792 |  | 173 | 236 | 110 | Bridlewood | 27.6/16kV | BRDF3 | Defective underground cable between SC9981 and 886 in the Fringewood area of Stittsville. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
17804 | 2011 | 3 | 30 | 0.42222 |  | 382 | 879 | 138 | Bridlewood | 27.6/16kV | BRDF3 | SC9981 on Fringewood North of Harry Douglas was isolated to allow crews to replace the defective switchgear. 15 radially fed transformers were interuppted . | Kanata | Scheduled Outage | Repair
14135 | 2009 | 4 | 2 | 0.53611 |  | 17 | 1 | 2 | Bridlewood | 27.6/16kV | BRDF3 | Transformer #X36344 located at 5 Lazy Nol Crt isolated for Broder to make repairs | Goulburn | Scheduled Outage | Repair
17970 | 2011 | 4 | 20 | 0.25 |  | 30 | 2 | 4 | Bridlewood | 27.6/16kV | BRDF3 | Transformer #7780 @ 6 Cedarow Crt was isolated for preventive maintenance. All power restored was restored as of 0630. | Kanata | Scheduled Outage | Preventive Maintenance
14200 | 2009 | 4 | 22 | 0.39514 |  | 323 | 65 | 12 | Bridlewood | 8/4.8kV | BRDF3 | TP6391 on Kathleen St. was isolated to allow Hydro Ottawa crews to replace a leaking transformer. | Ottawa | Scheduled Outage | Repair
6450 | 2005 | 4 | 23 | 0.58819 |  | 148 | 74 | 30 | Bridlewood | 12/7.2kV | BRDF3 | Switch 888R on brdf3 circuit opened. Oncall crews patrolled O/H section found no fault. Switch 888R closed restoring all load. | Kanata | Adverse Weather | Rain
10308 | 2007 | 4 | 23 | 0.99306 |  | 65 | 16 | 15 | Bridlewood | 27.6/16kV | BRDF3 | Wind storm damaged a single phase line on Second Line rd @ Murphy's road. | Kanata | Adverse Weather | Wind
3373 | 2003 | 4 | 24 | 0.38958 |  | 157 | 262 | 100 | Bridlewood | 27.6/16kV | BRDF3 | Planned outage to 11 transformers in the area around McCurdy & Castlefrank in Kanata to replace elbows with vented elbows. | Kanata | Scheduled Outage | Preventive Maintenance
14306 | 2009 | 5 | 5 | 0.40208 |  | 242 | 2207 | 600 | Bridlewood | 27.6/16kV | BRDF3 | A double parking stand @ S3 (springwood and trailway) blew up causing S23681 @ Stittsville and Hazeldeen to open. Crew removed defective parking stand and restored power. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
5138 | 2004 | 5 | 13 | 0.40625 |  | 126 | 44 | 21 | Bridlewood | 27.6/16kV | BRDF3 | John Brown isolated switch S198 & 4 transformer to relocate conductor on John Woods Dr. in Stittsville. | Goulburn | Scheduled Outage | Construction
14347 | 2009 | 5 | 13 | 0.63472 |  | 154 | 335 | 150 | Bridlewood | 27.6/16kV | BRDF3 | The BRDF3 (which was carrying the AlexF2 & F3)auto reclosed, then switch 463B blew, this was caused by a blown elbow on S1 B phase on Wintergreen Dr in Stittsville. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
18183 | 2011 | 5 | 19 | 0.37847 |  | 39 | 21 | 33 | Bridlewood |  | BRDF3 | At 09:05am crews isolated Bridlewood F3 section from switch 888 to end of line on Windwood Cres to allow contractors to perform tree removal. 33 customers affected for 39 mins. Bridlewood (BRDF3) ID # 18183 | Kanata | Scheduled Outage
16148 | 2010 | 5 | 26 | 0.42431 |  | 39 | 7 | 11 | Bridlewood | 27.6/16kV | BRDF3 | Transformer 227 at 102 Castlefrank was isolated to allow crews to replace it. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8406 | 2006 | 6 | 1 | 0.41667 |  | 300 | 10 | 2 | Bridlewood | 27.6/16kV | BRDF3 | Replaced defective 3 phase500 kva pad mount transformer 6757 at 83 Iber Rd due to a suspected lightning strike | Goulburn | Lightning | Direct Strike
18283 | 2011 | 6 | 2 | 0.64375 |  | 453 | 83 | 11 | Bridlewood |  | BRDF3 | At 15:27 crews isolated Transformer 7427 at 59 IBER rd to replace equipment. 11 customers affected for 453 mins. Bridlewood BRDF3 ID# 18283 | Kanata | Scheduled Outage
16186 | 2010 | 6 | 3 | 0.40278 |  | 450 | 90 | 12 | Bridlewood | 27.6/16kV | BRDF3 | Transformer 370 at 375 Pickford isolated to allow crews to change leaking transformer. | Kanata | Scheduled Outage | Repair
16203 | 2010 | 6 | 5 | 0.69306 |  | 209 | 3 | 1 | Bridlewood | 27.6/16kV | BRDF3 | Bell building at 5854 Hazeldean Rd has been complaing of low voltage with recent overhead line and transformer change due to road widening. Overhead wire was upgraded last night and still low voltage. This time transformers changed from 25kva to 50 kva. | Kanata | Defective Equipment
16204 | 2010 | 6 | 5 | 0.041667 |  | 210 | 4 | 1 | Bridlewood | 27.6/16kV | BRDF3 | 5854 Hazeldean Rd Bell Building has low voltage complaints. New transformer and triplex recently installed with road widening. Triplex size upgraded | Kanata | Defective Equipment
6829 | 2005 | 6 | 28 | 0.85417 |  | 350 | 2455 | 750 | Bridlewood | 27.6/16kV | BRDF3 | SC4281-CB3 was found tripped, B phase fault indicators found at some txs in tx loop fed by SC2481, all testing showed no faulted equipment, all equipment and customers restored. | Kanata | Unknown/Other
3799 | 2003 | 7 | 5 | 0.53194 |  | 152 | 25 | 10 | Bridlwood | 12/7.2kV | BRDF3 | Transformer 4348 on the BRDF3 was hit by lightning and had to be replaced | Kanata | Lightning | Direct Strike
8742 | 2006 | 7 | 17 | 0.39583 |  | 63 | 10 | 10 | Bridlewood | 27.6/16kV | BRDF3 | Isolated transformer 258 on Pickford to make repairs. | Kanata | Scheduled Outage | Repair
3826 | 2003 | 7 | 30 | 0.40556 |  | 1 | 2 | 90 | Bridlewood | 27.6/16kV | BRDF3 | Billy Seaman reports that at 9:44am, approximately 90 customers in the Bridlewood area of Kanata were interrupted due to an incorrect switch operation. All customers were restored at 9:45am Seaman states that while they were performing planned switching sw 636 R phase was opened instead of the B phase causing the 1 minute interuption. | Kanata | Human Element | Switching Errors
5715 | 2004 | 8 | 25 | 0.37153 |  | 167 | 284 | 102 | Bridlewood | 27.6/16kV | BRDF3 | Scheduled outage to isolate 8 txs on McDermot in Kanata for insert & elbow changes. | Kanata | Scheduled Outage | Preventive Maintenance
5716 | 2004 | 8 | 25 | 0.54514 |  | 89 | 67 | 45 | Bridlewood | 27.6/16kV | BRDF3 | Scheduled outage to isolate 4 txs on McDermot in Kanata for insert & elbow changes. | Kanata | Scheduled Outage | Preventive Maintenance
5756 | 2004 | 9 | 1 | 0.36597 |  | 118 | 167 | 85 | Bridlewood | 27.6/16kV | BRDF3 | Billy Seaman isolated transformers on Lightfoot to change elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
5760 | 2004 | 9 | 1 | 0.56319 |  | 68 | 39 | 34 | Bridlewood | 27.6/16kV | BRDF3 | Transformer 1732 & 1733 on McNeil Court isolated forelbows and insert changes. | Kanata | Scheduled Outage | Preventive Maintenance
9163 | 2006 | 9 | 8 | 0.7625 |  | 30 | 350 | 700 | BRIDLEWOOD | 27.6/16kV | BRDF3 | Severe Storm, caused BRDF3 breaker to trip. No SCADA Control, had to be closed manually. | Kanata | Adverse Weather | Wind
7348 | 2005 | 9 | 20 | 0.37917 |  | 100 | 17 | 10 | Bridlewood | 27.6/16kV | BRDF3 | Transformer TE7779 @ 8 Ceadrow Crt Stittsville was isolated to clean sand out of bottom fo well. | Kanata | Scheduled Outage | Construction
15135 | 2009 | 9 | 20 | 0.90278 |  | 520 | 9 | 1 | Bridlewood | 27.6/16kV | BRDF3 | Transformer at 5854 Hazeldean changed out due to defective 25kVA xfmr of 75kVA bank. Customer's breaker connection overheated due to loose connection, repaired by customer hired electrician. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19280 | 2011 | 9 | 28 | 0.67847 |  | 179 | 33 | 11 | Bridlewood | 27.6/16kV | BRDF3 | transformer at 76 Mclennan Way was isolated to allow crew to replace leaking transformer. | Kanata | Defective Equipment
19291 | 2011 | 9 | 29 | 0.86806 |  | 3 | 400 | 8000 | Bridlewood | 27.6/16kV | brdf3 | Brdf3 breaker opened due to human error. Cause under investagation. | Kanata | Human Element | Incorrect Use of Equipment
4205 | 2003 | 10 | 4 | 0.10972 |  | 230 | 8 | 2 | Bridlewood | 27.6/16kV | BRDF3 | Isolate TransformerT1135 & T1136 for maintenance | Kanata | Scheduled Outage | Repair
4301 | 2003 | 10 | 20 | 0.375 |  | 150 | 160 | 64 | Bridlewood | 27.6/16kV | BRDF3 | Changing transformer. | Kanata | Scheduled Outage | Repair
4323 | 2003 | 10 | 22 | 0.37014 |  | 88 | 73 | 50 | Bridlewood | 27.6/16kV | BRDF3 | Transformer maintenance | Kanata | Scheduled Outage | Preventive Maintenance
4325 | 2003 | 10 | 22 | 0.44514 |  | 114 | 152 | 80 | Bridlewood | 27.6/16kV | BRDF3 | Transformer maitenance to change elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
4330 | 2003 | 10 | 23 | 0.37153 |  | 125 | 156 | 75 | Bridlewood | 27.6/16kV | BRDF3 | Replacing elbows and Inserts on the transformer 773,774,775,776,777,778,779 | Kanata | Scheduled Outage | Preventive Maintenance
4399 | 2003 | 11 | 6 | 0.39583 |  | 199 | 332 | 100 | Bridlewood | 27.6/16kV | BRDF3 | Insert and elbow replacement between transformer 1350-1 and S69-2. | Kanata | Scheduled Outage | Preventive Maintenance
15361 | 2009 | 11 | 7 | 0.94931 |  | 68 | 5 | 4 | Bridlewood | 27.6/16kV | BRDF3 | A broken switch at transformer X37198 at 24 Fringewood. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
15407 | 2009 | 11 | 21 | 0.32292 |  | 485 | 32 | 4 | Bridlewood | 27.6/16kV | BRDF3 | Transformer TP5234 @ 200 Iber Rd was isolated to allow the crew to upgrade the transformer from 500KVA to 1000KVA. | Kanata | Scheduled Outage | Construction
11753 | 2007 | 11 | 22 | 0.93611 |  | 146 | 19 | 8 | Bridlewood |  | BRDF3 | Transformer 1136 at 420 Hazeldean Rd was leaking oil and replaced. | Kanata | Scheduled Outage | Repair
9711 | 2006 | 11 | 23 | 0.42431 |  | 95 | 22 | 16 | Bridlewood | 27.6/16kV | BRDF3 | A problem at customer own transformer 1012 @ the Kanata Rec. Complex-Walter Baker Pl causing to trip the circuit to trip at sectionalizer 44-3. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5938 | 2004 | 11 | 28 | 0.30556 |  | 92 | 3 | 2 | Bridlewood | 27.6/16kV | BRDF3 | Isolation of transformer 626 @ 100 Maple Grove for service. | Kanata | Scheduled Outage | Preventive Maintenance
15456 | 2009 | 12 | 2 | 0.55833 |  | 45 | 1184 | 1578 | Bridlewood | 27.6/16kV | BRDF3 | Vehicle hit bell messenger that wrapped itself in the BRDF3 primary at Hazeldeen and Terryfox. Crew cleared wires and re-energized circuit. | Kanata | Foreign Interference | Vehicle
9802 | 2006 | 12 | 6 | 0.37917 |  | 122 | 10 | 5 | Bridlewood | 27.6/16kV | BRDF3 | Isolation of T1400 and 1290 and S1012 to allow crew to rearrange cables in T1400. Terry Fox at Hazeldean. | Kanata | Scheduled Outage | Repair
7737 | 2005 | 12 | 15 | 0.71528 |  | 148 | 42 | 17 | Bridlewood | 27.6/16kV | BRDF3 | Cable dig in on Terry Fox at Hazeldean caused BRDF3 feeder to auto reclose and S44-2 switch to open to isolate faulted tx loop. Faulted cable isolated and customers restored. | Kanata | Foreign Interference | Dig-in
6089 | 2004 | 12 | 22 | 0.51389 |  | 55 | 642 | 700 | Bridlewood | 27.6/16kV | BRDF3 | Blown Arrester at S14135 on Hazaldean Road. Made repairs & closed BRDF3. | Kanata | Defective Equipment
15549 | 2009 | 12 | 25 | 0.54722 |  | 158 | 111 | 47 | Briddlewood |  | BRDF3 | Crews found S15922 RED phase OPEN @ 75 Harry Douglas Crews found 886 RED phase OPEN on Fringewood @ Poole Creek Crews Hi-pot'd RED PHASE from SC9981 to Xfrm'r 20114 - found dead short Crews Hi-pot'd RED PHASE from SC9981 to swtch 886 - found dead short EOL circuit on Poole Creek transferred to WHITE Phase to restore customers | Kanata | Unknown/Other
14424 | 2009 | 5 | 28 | 0.38681 |  | 23 | 4 | 10 |  |  | BRD-F3 | Xfmr 000238 at 70 Tamblyn Cres isolated to allow for reconnection of services | Kanata | Scheduled Outage | Repair
4764 | 2004 | 2 | 5 | 0.17847 |  | 438 | 2891 | 1100 | Bridlewood |  | BRDF3,HAZF4 | Cause determined to be defective S169 which caused the27 kv to fall into 8 kv HazF4. MDF - Investigation ongoing | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4799 | 2004 | 2 | 18 | 0.36458 |  | 25 | 2 | 6 | Bridlewood | 27.6/16kV | BRDF4 | Transformer 3728 at 133 Gray Cres isolated for transformer maintenance. | Kanata | Scheduled Outage
4845 | 2004 | 3 | 2 | 0.57986 |  | 51 | 85 | 100 | Bridlewood | 27.6/16kV | BRDF4 | Transformer TP4248 hit & damaged by vehicle had to replaced. Outage to 6 other R phase transformers required due to tx's being fed radially. | Kanata | Foreign Interference | Vehicle
4873 | 2004 | 3 | 10 | 0.61528 |  | 169 | 626 | 590 | Bridlewood | 27.6/16kV | BRDF4 | While swithing a catastrophic failer caused a large flash at an elbow at transformer 932 prompting emergency request from the crew involved for system to intrrup the BRDF4 feeder feeding that transformer. Gord Morris reports the switch at Transformer 259 indicated open but internally it wasn't which created the outage. MDF investigation ongoing with H&S into cause | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3413 | 2003 | 5 | 7 | 0.39792 |  | 57 | 190 | 200 | Bridlewood | 27.6/16kV | BRDF4 | Isolation to remove Tx 364 and install 4 new transformers. Outage to some customers due to out of phase switching. | Kanata | Scheduled Outage | Construction
12605 | 2008 | 6 | 11 | 0.65972 |  | 4 | 0 | 1 | BRIDLEWOOD | 27.6/16kV | BRDF4 | Switch 355 was burning up and could not be operated. Emergency switching performed to offload the switch, and one transformer 3994 was affected. | Kanata | Defective Equipment
12634 | 2008 | 6 | 15 | 0.725 |  | 159 | 1564 | 590 | Bridlewood | 27.6/16kV | BRDF4 | The BRDF4 tripped, because a pole fire and a broken insulator on the 44Kv it runs along Eagleson Rd along with the 200F1 and A9M1, lightning strike on the pole. | Kanata | Lightning | Lightening Srike on adjacent circuit
3798 | 2003 | 7 | 5 | 0.43056 |  | 220 | 37 | 10 | Bridlewood | 27.6/16kV | BRDF4 | transformer on Eagleson was replaced due to lightning restoral time is an approximation | Kanata | Lightning | Direct Strike
11034 | 2007 | 8 | 11 | 0.39583 |  | 100 | 3 | 2 | Bridlewood | 27.6/16kV | BRDF4 | Tx 626 @ 100 Maple Grove was isolated for planned customer maintenance. Due to Radial configuration, Tx 1487 supplying the Kingdom Hall was also off potential while the 4 way switch at Tx 626 was in the transformer off position. | Kanata | Scheduled Outage | Preventive Maintenance
4444 | 2003 | 11 | 13 | 0.65278 |  | 187 | 544 | 180 | Bridlewood | 27.6/16kV | BRDF4 | Broken Elbow at Trans. 3728 | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4495 | 2003 | 11 | 21 | 0.375 |  | 253 | 843 | 200 | Bridlewood | 27.6/16kV | BRDF4 | Transformers feeding Belleview and Vanstone St's in Kanata isolated to install ventied elbows. | Kanata | Scheduled Outage | Repair
4509 | 2003 | 11 | 24 | 0.42569 |  | 230 | 1020 | 266 | Bridlewood | 27.6/16kV | BRDF4 | 23 transformers were isolated to replace elbows & inserts in the Clarkson & Pickford area of Kanata. | Kanata | Scheduled Outage | Preventive Maintenance
15663 | 2010 | 1 | 17 | 0.23333 |  | 158 | 352 | 806 | Bridlewood | 8/4.8kV | BRDF5 | Cable fault between TP5410 and 2531 caused BRDF5 breaker to open, Dip switch S21647 blew when breaker closed. Section isolated and customers restored | Kanata | Defective Equipment | Imminent Equipment Failure Detected
17544 | 2011 | 2 | 1 | 0.40278 |  | 60 | 4 | 4 | Bridlewood | 8/4.8kV | BRDF5 | Transformer3138 at 146 Paddock Way isolated to replace broken insulator on live front transfomer. | Kanata | Scheduled Outage | Repair
19963 | 2012 | 2 | 5 | 0.22917 |  | 170 | 119 | 42 | Bridlewood | 8/4.8kV | BRDF5 | Fuse 302B opened due to cable fault betweek TP5409 and 3556HB blue phase affecting customers on Village Green, Country Lane and Carriage Crt. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19965 | 2012 | 2 | 5 | 0.31458 |  | 145 | 62 | 42 | Bridlewood | 8/4.8kV | BRDF5 | At 05:30am customers reported fuse 302B @ 51 Country Lane open. Crews identified a faulted cable section on the BRDF5 between 3556HB and TP5409 blue. 42 customers affected for 145 mins. Bridlewood BRDF5 ID# 19965 | Kanata | Defective Equipment | Equipment Deterioration Due to Age
15829 | 2010 | 3 | 21 | 0.88889 |  | 100 | 168 | 115 | Bridlewood | 8/4.8kV | BRDF5 | Cable fault between transformers TP5410R & 1645R caused S21647 fuse to blow interupting power to 13 transformers in the Country Lane/Abbey Hill/ Old Colony area of Kanata. Defective cable was isolated & power restored from both sides. | Kanata | Defective Equipment
12197 | 2008 | 3 | 28 | 0.68264 |  | 77 | 9 | 7 | Bridlewood |  | BrdF5 | Blown arrester found at 122 Glammorgan and transformer Tx 6494 fuse replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
12208 | 2008 | 3 | 31 | 0.39583 |  | 60 | 10 | 10 | BRIDLEWOOD | 8/4.8kV | BRDF5 | TRANSFORMER X06494 AT 122 GLAMORGAN ISOLATED TO ALLOW FOR O/H SERVICE CHANGE | Kanata | Scheduled Outage | Repair
14218 | 2009 | 4 | 25 | 0.70833 |  | 874 | 131 | 9 | Bridlewood | 27.6/16kV | BRDF5 | The fuse @ Transformer 5865B @ 13 Heathcliff blew around 17:00 on Saturday Apr 25, crews were on route when the storm went through the Ottawa area, then at 3:01 in the morning the BRDF5 AUTO reclosed and the crew found switch S10746 B phase open. Bob Cooper closed the normal open point back in to pick up the circuit and the transformer | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14219 | 2009 | 4 | 26 | 0.12569 |  | 273 | 1138 | 250 | Bridlewood | 8/4.8kV | BRDF5 | At 3:01 in the morning the BRDF5 AUTO reclosed and the crew found switch S10746 B phase open. Bob Cooper closed the normal open point back in to pick up the circuit and the transformer. | Nepean | Adverse Weather | Wind
14226 | 2009 | 4 | 26 | 0.12569 |  | 273 | 910 | 200 | Bridlewood | 27.6/16kV | BRDF5 | Fuse blew at transformer 5865 on Heathcliffe. BRDF5 auto reclosed at 3:01, and fuse S10746B blew. Transformer fuse replaced and power restore to 20 transformers. | Kanata | Defective Equipment
14318 | 2009 | 5 | 6 | 0.40903 |  | 293 | 39 | 8 | Bridlewood | 27.6/16kV | BRDF5 | Transformer TP5423 @ 101 Glamorgan was isolated for PCB transformer replacement program. | Kanata | Scheduled Outage | Repair
16062 | 2010 | 5 | 8 | 0.30069 |  | 302 | 544 | 115 | Bridlewood | 8/4.8kV | BRDF5 | cable fault between TP5410 and 1645 caused S21647 to blow inturrupting 115 customers on village green, country lane, old colony, paddock and abbyhill area. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14346 | 2009 | 5 | 12 | 0.36111 |  | 491 | 90 | 11 | Bridlewood | 8/4.8kV | BRDF5 | Transformer TP5413 @ 100 BANNING RD KANATA was isolated as part of PCB replacement program. | Kanata | Scheduled Outage | Preventive Maintenance
14349 | 2009 | 5 | 13 | 0.37569 |  | 449 | 90 | 12 | Bridlewood | 8/4.8kV | BRDF5 | At 9:01 transformer TP5413 at 108 Banning was isolated to allow crews to change transformer as part of the PCB program, 12 customers were affected and all power was resotred at 4:30pm. Bridlewood (BRDF5). ID#14349. | Kanata | Scheduled Outage | Construction
14392 | 2009 | 5 | 21 | 0.37778 |  | 416 | 69 | 10 | Bridllewood | 8/4.8kV | BRDF5 | Transformer TP5408 at 17 Carriage was isolated as part of the PCB replacement program. | Kanata | Scheduled Outage | Preventive Maintenance
10459 | 2007 | 5 | 24 | 0.77083 |  | 489 | 73 | 9 | Bridlewood | 8/4.8kV | BRDF5 | Transformer T5865 at 75 Glamorgan in Kanata failed and had to be replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14411 | 2009 | 5 | 25 | 0.375 |  | 564 | 150 | 16 | Bridlewood | 8/4.8kV | BRDF5 | TP5497 @ 52 Country Lane was isolated for replacement under the PCB replacment program. | Kanata | Scheduled Outage | Repair
14414 | 2009 | 5 | 26 | 0.40625 |  | 405 | 108 | 16 | Bridlewood | 8/4.8kV | BRDF5 | TP5414 at 31 Courtney Rd. was isolated to allow crews to replace the transformer as part of the PCB replacmetn program. | Ottawa | Scheduled Outage | Preventive Maintenance
16167 | 2010 | 5 | 31 | 0.46528 |  | 193 | 225 | 70 | Bridlewood | 8/4.8kV | BRDF5 | BRDF5 isolation required to repair a broken cross arm on a backyard pole on Glamorgan | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14438 | 2009 | 6 | 1 | 0.37847 |  | 116 | 17 | 9 | Bridlewood | 27.6/16kV | BRDF5 | Transformer 4406R at 188 Castlefrank was isolated to allow crew to repair a defective elbow. | Kanata | Scheduled Outage | Repair
14443 | 2009 | 6 | 2 | 0.375 |  | 345 | 34 | 6 | Bridlewood | 8/4.8kV | BRDF5 | TP5420 at 6 Glamorgan was isolated to allow crew to change out PCB transformer. 6 customers affected. | Kanata | Scheduled Outage | Preventive Maintenance
14450 | 2009 | 6 | 3 | 0.37778 |  | 422 | 84 | 12 | Bridlewood | 27.6/16kV | BRDF5 | TP5421 at 21 Glamorgan was isolated to allow crew to replace PCB transformer. | Kanata | Scheduled Outage | Preventive Maintenance
14520 | 2009 | 6 | 11 | 0.39236 |  | 645 | 86 | 8 | Bridlewood | 8/4.8kV | BRDF5 | TP5415 @ 119 Oakburn in Kanata was isolated to allow crews to replace transformer. | Kanata | Scheduled Outage | Preventive Maintenance
14537 | 2009 | 6 | 14 | 0.59514 |  | 161 | 416 | 435 | Bridlewood | 27.6/16kV | BRDF5 | BRDF5 breaker opened. S21647 found blown due to defective cable on the red phase between 1645R and TP5410. Cable isolated and all power restored. | Kanata | Defective Equipment
14825 | 2009 | 7 | 25 | 0.71875 |  | 1338 | 2208 | 176 | Bridlewood | 8/4.8kV | BRDF5 | Flooding in the bakyard of 163 Glamorgan caused transformer 5309 to short out which inturn caused the BRDF5 breaker to auto re-close and the red phase fuse to blow at S10746. At 15:18 crew closed S10746 red phase to energize all transformer except TE5909 R which remained isolated. All power was restored by 15:33. | Nepean | Adverse Environment | Flooding
14841 | 2009 | 7 | 25 | 0.77083 |  | 21 | 4 | 10 | Bridlewood | 8/4.8kV | BRDF5 | Transformer TE5873 was opened to allow crew to reconnect 35 Glamorgan. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
14964 | 2009 | 8 | 19 | 0.52778 |  | 10 | 2 | 12 | Bridlewood | 8/4.8kV | BRDF5 | Transformer 5871 at 46 Ballantrae Way in Kanata isolated to repair damaged barrier board. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
15017 | 2009 | 8 | 27 | 0.37708 |  | 535 | 107 | 12 | Bridlewood | 27.6/16kV | BRDF5 | transformer 5909 @ 167 Glamorgan was isolated fro oil redemption. | Kanata | Scheduled Outage | Repair
11501 | 2007 | 10 | 12 | 0.26528 |  | 287 | 500 | 150 | Bridlewood | 8/4.8kV | BRDF5 | Failed insulators at Tx 2568, 119 Oakburn caused S21647 to blow. The loop was sectionalized restoring 6 of 13 transformers, the defective transformer was then isolated & repairs made. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
13497 | 2008 | 10 | 29 | 0.010417 |  | 80 | 580 | 435 | BRIDLEWOOD | 27.6/16kV | BRDF5 | BRDF5 breaker opened, broken pole found at 90 Rothesay, temporarily repaired and breaker closed back in | Kanata | Adverse Weather | Snow
11633 | 2007 | 10 | 30 | 0.71181 |  | 121 | 156 | 130 | Bridlewood | 12/7.2kV | BRDF5 | Red phase cable fault between TE3556 & TE3138 in Glencairn. Outage response time was increased due to Radio communication failure during restoration efforts on BRDF5. Time MCI notified. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11636 | 2007 | 10 | 31 | 0.43333 |  | 26 | 2 | 4 | Bridlewood | 8/4.8kV | BRDF5 | Transformer T3138 @ 146 Paddock was isolated to make repairs from fault flashover. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
13560 | 2008 | 11 | 4 | 0.60972 |  | 62 | 207 | 200 | Bridlewood | 8/4.8kV | BRDF5 | During switching on the BRDF5 circuit between eagleson and terry Fox, customers reported out of power. Affecting 200 customers, there seems to be a mapping issue with rised pole S23484, believed to be in the incorrect location according to our maps. Crew will investigate tomorrow during daylight. | Kanata | Human Element
19549 | 2011 | 11 | 10 | 0.3875 |  | 251 | 59 | 14 | Bridlewood | 8/4.8kV | BRDF5 | Transformer 5512 at 224 Old Colony Rd was isolated to allow crew to replace transformer. | Kanata | Scheduled Outage | Preventive Maintenance
20011 | 2012 | 2 | 14 | 0.38958 |  | 146 | 34 | 14 | Bridlewood | 8/4.8kV | BRDF6 | Transformer 4071 @ 29 McKitrick was isolated to allow crews to replace defective transformer. | Kanata | Scheduled Outage | Repair
20159 | 2012 | 3 | 13 | 0.54236 |  | 20 | 4 | 13 | Bridlewood | 8/4.8kV | BRDF6 | Transformer 5699 at 70 Sheldrake Dr. isolated to disconnect service to defective U/G service at 64 Sheldrake. | Kanata | Scheduled Outage | Repair
12168 | 2008 | 3 | 22 | 0.74514 |  | 182 | 3 | 1 | Bridlewood | 8/4.8kV | BRDF6 | Defective underground to 130 Abbyhill repaired by On-call. Transformer 2672. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
10242 | 2007 | 4 | 11 | 0.58264 |  | 116 | 31 | 16 | Bridlewood | 8/4.8kV | BRDF6 | Transformer #002660 located at 201 Morrena Rd isolated due to a cable dig in | Kanata | Foreign Interference | Dig-in
10295 | 2007 | 4 | 22 | 0.93542 |  | 393 | 52 | 8 | BRIDLEWOOD | 8/4.8kV | BRDF6 | Defective transformer 2663R on 151 Abbottsford was replaced by Oncall. | Kanata | Defective Equipment
14259 | 2009 | 4 | 29 | 0.35278 |  | 4 | 1 | 13 | Bridlewood | 8/4.8kV | BRDF6 | Transformer #5863 located at 23 Ballantrae Way isolated for clearance | Kanata | Scheduled Outage | Preventive Maintenance
14494 | 2009 | 6 | 8 | 0.4 |  | 372 | 87 | 14 | Bridlewood | 8/4.8kV | BRDF6 | TP5411 at 36 Melanie was isolated for PCB transformer change | Kanata | Scheduled Outage | Construction
14559 | 2009 | 6 | 17 | 0.40764 |  | 457 | 0 | 12 | Bridlewood | 8/4.8kV | BRDF6 | Crew isolated TP5419 as part of PCB replacement program. | Kanata | Scheduled Outage | Preventive Maintenance
12822 | 2008 | 7 | 11 | 0.75347 |  | 265 | 71 | 16 | Bridlewood | 8/4.8kV | BRDF6 | transformer 4086 at 24 Seabrooke leaked most of its oil and required replacement | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19947 | 2012 | 2 | 1 | 0.78472 |  | 2 | 1 | 16 | Bridlewood | 8/4.8kV | BRDF7 | At 18:50, during switching to isolate a cable section for NRC cable testing, an incorrect device was operated causing a brief outage to TP5454 at 24 Seabrooke. 16 customers affected for 2 minutes. Bridlewood BRDF7. ID# 19947 | Kanata | Human Element | Switching Errors
14031 | 2009 | 3 | 8 | 0.67361 |  | 430 | 79 | 11 | Bridlewood | 8/4.8kV | BRDF7 | Transformer 3574R at 55 Morton Drive was defective and was replaced by the on call crew. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20330 | 2012 | 4 | 15 | 0.32292 |  | 414 | 14 | 2 | Bridlewood | 8/4.8kV | BRDF7 | At 07:45am crews isolated an overhead transformer to perform repairs. Kanata BRDF7 ID#20330 | Kanata | Scheduled Outage | Repair
14298 | 2009 | 5 | 4 | 0.37917 |  | 299 | 55 | 11 | Bridlewood | 27.6/16kV | BRDF7 | Transformer TP5418 was isolated to allow crew to change the transformer as part of a PCB replacement program in the west end. | Nepean | Scheduled Outage
14304 | 2009 | 5 | 5 | 0.375 |  | 333 | 94 | 17 | Bridlewood | 8/4.8kV | BRDF7 | Transformers TP5416 & TP5417 isolated for replacement affecting customers on Montebello & Morton. | Kanata | Scheduled Outage | Repair
14439 | 2009 | 6 | 1 | 0.55694 |  | 56 | 10 | 11 | Bridlewood | 27.6/16kV | BRDF7 | Transformer 3576B at 13 Montebello was isolated to repair a broken bushing. | Kanata | Scheduled Outage | Repair
14463 | 2009 | 6 | 4 | 0.41389 |  | 140 | 21 | 9 | Bridlewood | 8/4.8kV | BRDF7 | TP5406 at 56 Dunoon isolated for replacement under the PCB replacment program. | Ottawa | Scheduled Outage
13014 | 2008 | 8 | 7 | 0.38125 |  | 473 | 47 | 6 | Bridlewood | 8/4.8kV | BRDF7 | Transformer TP5454 @ 22 Seabrook was isolated to replace same and complete cleaning after oil spill. | Kanata | Scheduled Outage | Repair
14989 | 2009 | 8 | 21 | 0.5625 |  | 18 | 2 | 7 | Bridlewood | 8/4.8kV | BRDF7 | Transformer #5695 located at 97 Sheldrake Dr isolated for repairs | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
13192 | 2008 | 9 | 4 | 0.37153 |  | 720 | 120 | 16 | Bridlewood | 8/4.8kV | BRDF7 | TP5454 at 22 Seabrook was isolated for clean up of an oil spill | Kanata | Scheduled Outage | Repair
11766 | 2007 | 11 | 26 | 0.42569 |  | 127 | 19 | 9 | Bridlewood | 8/4.8kV | BRDF7 | Tx 3569 at 141 Morton was isolated to repair sagging barrier board in primary compartment. | Kanata | Scheduled Outage | Preventive Maintenance
18654 | 2011 | 7 | 13 | 0.91528 |  | 22 | 794 | 2165 | Bridlewood | 8/4.8kV | BRDT2 | The BRDT2 transformer high and low side breakers opened for no apparent reason load transfered to the BRDT3 crew to investigate tomorrow. Bridlewood ID#18654. Station Dept. Inspected transformer and found evidence of a raccoon contact on secondary bushing of transformer. | Kanata | Foreign Interference | Animal
3405 | 2003 | 5 | 5 | 0.38889 |  | 214 | 428 | 120 | Bridlewood | 27.6/16kV | BRDTF1 | Isolate Transfromer to install vent insert's. | Kanata | Scheduled Outage | Repair
4600 | 2003 | 12 | 14 | 0.75347 |  | 31 | 3358 | 6500 | Bridlewood | 27.6/16kV | Bridlewood | BRD-B1 breaker opened at bridlewood station. Causing outage to 6500 customers. Blue phase time on BRD-B1. Unable to close breakers via scada. S. Cunningham closed breaker manually to energize circuits. All load restored at 18:36. | Kanata | Human Element | Switching Errors
4601 | 2003 | 12 | 14 | 0.78194 |  | 189 | 6376 | 6500 | Bridlewood | 27.6/16kV | Bridlewood | BRD-B1 breaker opened cause unknown. S. Cunningham dispatched to station. Oncall R. Blair also dispatched to station. Scada ind. High-High amps on BRDF2 n. relay. Of 606 amps. BRD-B1 breaker restored and BRDF1, BRDF4 closed. R. Blair reports rwb fault ind is now flashing at riser pole 154. Circuit to be patrolled. Partial patrol ind no fault on O/H. Part of circuit restored @ 21:35. Sataion crews report BRD-B1 may have opened due to overload. Remaining part of BRDF2 energized. BRDF3 transferred to Campeau 310F1 All load restored at 21:55. MDF comments - Investigation showed station overloaded by load transferred to stn to do work & not returned to origonal supply, scada high amp alarms not programmed. | Kanata | Human Element | Switching Errors
11840 | 2007 | 12 | 13 | 0.42708 |  | 22 | 4 | 12 | Bridlewood | 8/4.8kV | Bridlewood F5 | Transformer #3122 located at 51 Rothesay isolated for electrician to re-attach meter base | Kanata | Scheduled Outage | Repair
3530 | 2003 | 6 | 6 | 0.57639 |  | 3 | 75 | 1500 | Bridlewood | 27.6/16kV | BridlewoodT1Bus | While testing the BRDF2 feeder for new scada connection the BRDT1-B1 tripped causing outage to BRDF4 BRDF3 BRDF1. | Kanata | Human Element | Incorrect Use of Equipment
17458 | 2010 | 12 | 29 | 0.51736 |  | 121 | 30 | 15 | SB10 | 4.16kV | Bronson | At 32 George Street West transformer X25676 was isolated to allow crew to replace defective transformer. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5519 | 2004 | 7 | 18 | 0.74028 |  | 19 | 1298 | 4100 | Hydro One | 230KV | C3S | Hydro One reports C3S circuit opened. Causing 624T1B1 breaker to open. C3S circuit closed as of 18:00 by Hydro One. All Kanata MTS power was restored as of 18:05. 4100 Customers affected in power outage. | Kanata | Loss of Supply | HEPC Circuit Fault
5553 | 2004 | 7 | 22 | 0.87708 |  | 6 | 400 | 4000 | Kanata MTS | 230KV | C3S | Hydro One circuit C3S tripped causing loss of supply to Kanata MTS. 4000 Customers affected in power outage all power was restored as of 21:09. Hydro One reports fault on different feeder at terminal station was picked up by protections on C3S, no actual fault on circuit. Protection relays on C3S being checked. | Kanata | Loss of Supply | HEPC Circuit Fault
4304 | 2003 | 10 | 21 | 0.038194 |  | 5 | 266 | 3186 | Kanata | 27.6/16kV | C3S | 230kv feed to Kanata MTS auto reclosed, 624T1B1 opened auto, same closed via scada after IMO approval given. | Kanata | Loss of Supply | HEPC Circuit Fault
4312 | 2003 | 10 | 21 | 0.14375 |  | 7 | 372 | 3186 | Kanata | 230kv | C3S | 230kv feed to Kanata MTS auto reclosed, 624T1B1 opened auto, same closed via scada after IMO approval given. | Kanata | Loss of Supply | HEPC Circuit Fault
14698 | 2009 | 7 | 11 | 0.35903 |  | 48 | 5600 | 7000 | QT84, QT89 | 8/4.8kV | C7B | outage at Manordale & Center Point due to C7B feeder tripped | Nepean | Loss of Supply | Lightning
17972 | 2011 | 4 | 20 | 0.29931 |  | 6 | 803 | 8032 | Manordale/Centerpoint | 115kV | C7BB | Loss of supply from Hydro One C7BM circuit due to heavy rain fall in the Ottawa Area. 8032 customer were affected for 6 Minutes. | Nepean | Loss of Supply
7980 | 2006 | 3 | 2 | 0.45278 |  | 109 | 24400 | 14000 | Nepean | 115kV | C7BM | Hydro One 115KV, C7BM circuit tripped under hold off as well as W3B circuit tripped on line protection. Hydro One crew was working on an isolated section of C7BM and sleeved a section of isolated line into a live section of line. C7BM was being backfed by B5QK, (115KV). The T2-B2 breaker at Lincoln tripped, causing an outage to the B2 Bus. Power was restored at Lincoln by the 24/7 crew at 10:52. | Nepean | Loss of Supply | HEPC Circuit Fault
8030 | 2006 | 3 | 15 | 0.43542 |  | 113 | 44508 | 37575 | Bridlewood | Yes | C7BM | Hydro 1 C7BM was compromised by a blasting mat on the 115kv overhead between Fitzroy Junction and L1C7BM-1. This occurred while F10MV was out of service causing the outage to be significantly more wide spread than normal configuration would have. Also lost Lincoln, Woodroofe, Marchwood, Mannerdale, Fallowfield, Richmond South, Limbank | Kanata | Loss of Supply | HEPC Circuit Fault
18048 | 2011 | 4 | 28 | 0.53958 |  | 43 | 5900 | 8232 | Centrepointe/Manordale | 44kV | C7BM | Loss of supply on the C7BM circuit cause Centrepointe and Manordale substation to be down. | Nepean | Loss of Supply | HEPC Circuit Fault
16030 | 2010 | 5 | 3 | 0.10417 |  | 11 | 3667 | 20000 | Merivale | 115kV | C7BM | Circuit fault on C7BM. Hydro One opened motor operated switch west of Manordale and all load restored to Hydro Ottawa customers. | Nepean | Loss of Supply | HEPC Circuit Fault
16065 | 2010 | 5 | 8 | 0.31181 |  | 30 | 4684 | 19572 | Merivale TS | 115kV | C7BM | C7BM auto-reclosed 3 times before staying off, interrupting power to Manordale, Centrepointe & Woodroffe TW. Circuit was sectionalized by H1 and all load restored to Hydro Ottawa. Woodroffe T2 & T4 transformers were isolated for scheduled work by H1, so outage was larger than it would have been had System been in normal setup. Hydro One later found defective dead end insulators at Chats, replaced them & restored the 115 kv circuit to normal. | Nepean | Loss of Supply
8392 | 2006 | 5 | 31 | 0.99653 |  | 10 | 1387 | 8324 | Centrepointe | 115kV | C7BM | H1 reported C7BM circuit tripped causing an interruption to Centrepoint and Manordale DS. H1 reports problem at their Chats Falls station. | Nepean | Loss of Supply | HEPC Circuit Fault
16324 | 2010 | 6 | 24 | 0.54306 |  | 19 | 3167 | 10000 | Manordale, Centerpointe | 115kV | C7BM | Hydro One 115kv C7BM Circuit tripped during rain and high winds, breaker fail at Barrett Chute.Hydro One restored from normal supply. Manordale 84F5 auto reclosed with inital loss of supply. | Nepean | Loss of Supply
12738 | 2008 | 6 | 26 | 0.64167 |  | 7 | 758 | 6500 | Merivale | 115kV | C7BM | C7BM circuit opened during lightning cause outage on Manordale & Centrepointe station. Hydro One closed circuit restoring lost load. | Nepean | Loss of Supply | Lightning
18548 | 2011 | 6 | 28 | 0.75417 |  | 5 | 674 | 8092 | HEPC | 115kV | C7BM | C7BM tripped during stormy weather, loss of supply to Centerpointe & Manordale stations. | Nepean | Loss of Supply | HEPC Circuit Fault
18556 | 2011 | 6 | 28 | 0.79306 |  | 30 | 4046 | 8092 | HEPC | 115kV | C7BM | Hydro One reports C7BM circuit failed to reclose dur to fault on circuit. C7BM cirucit was sectionized and power was restored to Centerpointe & Manordale. | Nepean | Loss of Supply | HEPC Circuit Fault
8660 | 2006 | 7 | 4 | 0.66319 |  | 6 | 900 | 9000 | Merivale |  | C7BM | C7BM opened due to lighting and adverse weather causing tree contacts and broken trees. | Hydro One | Loss of Supply | HEPC Circuit Fault
14774 | 2009 | 7 | 17 | 0.88611 |  | 2 | 257 | 7700 | MANORDALE/CENTREPOINTE | 115kV | C7BM | Hydro One C7BM circuit has auto tripped. Interruption to Manordale and Centrepoint substations. H1 have no apparent cause for trip. (7700 customers) | Nepean | Loss of Supply | HEPC Circuit Fault
8803 | 2006 | 7 | 23 | 0.22222 |  | 15 | 1738 | 6951 | Manordale | 115kV | C7BM | Hydro One loss of supply, reason unkown. Centrepoint, and Manordale. | Nepean | Loss of Supply | HEPC Circuit Fault
3813 | 2003 | 7 | 29 | 0.67361 |  | 47 | 6478 | 8589 | Hydro One | 115kV | C7BM | Hydro One Ckt. C7BM auto tripped interuptting Centre Point & Manordale stations, Centre Point 87F3 load restored from Woodroffe 170F2 at 16:10. Stations restored from H1 at 16:25. | Nepean | Loss of Supply | HEPC Circuit Fault
16665 | 2010 | 8 | 4 | 0.6125 |  | 4 | 667 | 10000 | Merivale Terminal | 115kV | C7BM | Hydro One reported trip on the C7BM circuit affecting Centrepointe, Woodroffe and Manordale. Major storm going through the Ottawa region. Circuit closed back in after 4 minutes by OGCC and held. | Ottawa | Loss of Supply
5634 | 2004 | 8 | 10 | 0.38889 |  | 3 | 350 | 7000 | Q84 & Q87 | 8/4.8kV | C7BM | Hydro One 115 Kv circuit C7BM trip due to lightening storm. | Nepean | Loss of Supply | HEPC Circuit Fault
3926 | 2003 | 8 | 21 | 0.96319 |  | 69 | 8511 | 8589 | Manordale, Centrepoint | 115kV | C7BM | Hydro One 115Kv circuit C7BM tripped interrupting Centrepoint and Manordale MS's. Centre Point 87F3 load restored from the 170F2 bkr at 2307. Manordale 84F6 load restored from the 160F2 at 23:11. Hydro One sectionalized their circuit and restored Manordale and Centre Point at 23:50 | Nepean | Loss of Supply | HEPC Circuit Fault
9030 | 2006 | 8 | 23 | 0.33264 |  | 18 | 711 | 2370 | Woodroffe | 115kV | C7BM | Hydro One Woodroffe 24T1 transformer tripped on differential protection which caused C7BM circuit to auto-reclose and a momentary interruption to Centrepoint & Manordale. All Q & Z bus load at Woodroffe was interrupted. 24T2, the companion transformer for T1, was unavailable & isolated for repairs. Load was restored at Woodroffe via Hydro Ottawa tie cables to the B & J busses. Differential trip was caused from a squirrel contact which damaged an insultor & lightning arrestor on secondary side. | Ottawa | Loss of Supply | HEPC Station Fault
15263 | 2009 | 10 | 15 | 0.32847 |  | 12 | 1874 | 9369 | Center Point & Manordale |  | C7BM | Hydro 1 loss of C7BM caused a loss of supply to Center Point, Manordale (and part of Woodroffe on transfer). Hydro 1 sectionalized and was able to restore the feed to our stations | Nepean | Loss of Supply | HEPC Circuit Fault
4477 | 2003 | 11 | 18 | 0.85069 |  | 6 | 1109 | 12845 | Hydro One | 115kV | C7BM | Loss of Hydro One supply to Manordale, Centrepoint, Woodroffe B & J busses and Lincoln T2. No load loss at Lincoln. Circuit failed to auto-reclose and was re-energized manually by Hydro One. | Ottawa | Loss of Supply | HEPC Circuit Fault
3387 | 2003 | 4 | 29 | 0.40278 |  | 140 | 152 | 65 | Campeau | 27.6/16kV | Camp F1 | Transformers were isolated to allow for the replacement of internal components, elbow and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
4550 | 2003 | 12 | 3 | 0.40347 |  | 49 | 65 | 80 | Campeau | 27.6/16kV | Camp F1 | During switching to install a new transformer when pulling the elbow at 754 to 2242 a flash over occurred. | Kanata | Defective Equipment
4581 | 2003 | 12 | 10 | 0.41875 |  | 93 | 37 | 24 | Campeau | 27.6/16kV | Camp F1 | 24 customers on Millman Crt interrupted to change elbows & inserts. | Kanata | Scheduled Outage | Preventive Maintenance
3497 | 2003 | 5 | 29 | 0.38681 |  | 133 | 244 | 110 | Campeau | 27.6/16kV | Camp Temp | Transformers isolated to replace elbows & insers.110 customers on Jackman Terrace & Aird Place affected. | Kanata | Scheduled Outage | Preventive Maintenance
4352 | 2003 | 10 | 28 | 0.375 |  | 199 | 464 | 140 | Camp Temp | 27.6/16kV | Camp Temp | Transformer shut down for maintence | Kanata | Scheduled Outage | Preventive Maintenance
3391 | 2003 | 4 | 30 | 0.38333 |  | 138 | 143 | 62 | Campeau | 27.6/16kV | Camp Temp F1 | Transformers #4347, 4348, 4349, 126, 128, 129 and 4351 were isolated to allow for the replacement of internal components, elbow and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
4114 | 2003 | 9 | 21 | 0.375 |  | 171 | 20 | 7 | Campeau | 27.6/16kV | CAMP TF1 | Transformer 4249B at McCurdy & Liessen in Kanata faulted internally and had to be replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4410 | 2003 | 11 | 7 | 0.55 |  | 69 | 1 | 1 | SM04 | 4.16kV | Carling | Transformer #5789 opened to allow crew change open wire service. 1 Customer affected in power outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9355 | 2006 | 10 | 1 | 0.29167 |  | 325 | 98 | 18 | CARP | 8/4.8kV | CARP | Planned outage from Carp DS as Hydro One replace deterorating insulators on CARP circuit. 18 transfer customers out. No indication from Hydro One that the outage was going on until our customers called. | Kanata | Scheduled Outage | Preventive Maintenance
17741 | 2011 | 3 | 19 | 0.97639 |  | 6 | 2 | 20 | Carp D.S. | 12/7.2kV | Carp F1 | customers report flickering lights. 24/7 found K634 (Hydro One owned switch) burning up. K634 was opened and fuse barrel replaced. All power was restored. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14193 | 2009 | 4 | 20 | 0.68403 |  | 63 | 2 | 2 | Carp TS (Hydro One) | 12/7.2kV | Carp F1 | On call crew replaced defective transformer #40127 at 1106 Huntmar Rd | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
18625 | 2011 | 7 | 8 | 0.91667 |  | 450 | 15 | 2 | Carp | 13.2kV | Carp F1 | Tree Fallen on Hydro One supply Carp F1which supplies2 customers from Hydro Ottawa on Old Carp Road. Tree removed and power restored. | Kanata | Tree Contacts | Tree Fallen
15245 | 2009 | 10 | 11 | 0.36111 |  | 120 | 20 | 10 | Carp D. S. | 8/4.8kV | Carp F1 | A tree contact caused the local fuse @ Carp rd. and Huntmar to open interrupting 10 of our transfer customers. Circuit belongs to H1 and they refused and closed. | Kanata | Tree Contacts | Tree Limb Fallen
12053 | 2008 | 2 | 17 | 0.80208 |  | 20 | 4 | 12 | Carp | 8/4.8kV | Carp F3 | A car accident in the Huntmar/Donald B. Munro area. | Ottawa | Foreign Interference | Vehicle
20123 | 2012 | 3 | 5 | 0.39236 |  | 185 | 12 | 4 | Carp DS | 8/4.8kV | Carp F3 | A section of o/h line on Old Carp rd from sw. 634 was isolated to re-insulate line. | Kanata | Scheduled Outage | Construction
16045 | 2010 | 5 | 5 | 0.85417 |  | 90 | 18 | 12 | Carp D.S. | 8/4.8kV | CarpF1 | transfer customers on Huntmar were interrupted due to problem on hydro one circuit. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
19393 | 2011 | 10 | 16 | 0.23958 |  | 405 | 135 | 20 | Carp | 12/7.2kV | CARPF1 | A9M3, A9M5 and a section of 624F1 circuits were isolated at Terry Fox and Richardson Side Rd to allow Hydro One to replace poles and move conductors and to allow Hydro Ottawa crews to remove A9M3-1 switch and install new VBM switches @ 76M3-1 and 76M3-2. Stations affected were Alexander, Carp, Beaverbrook, Janet King, Munster and Kanata. Most of the customers had been transfered prior to outage if possible. | Kanata | Scheduled Outage | Preventive Maintenance
20677 | 2012 | 6 | 2 | 0.28333 |  | 330 | 55 | 10 | Carp |  | CARPF3 | Hydro One owned fuse A675 on Old Carp Rd. opened due to a tree contact affecting LTC cusomters on Huntmar and Old Carp Rd. | Goulburn | Loss of Supply | HEPC Circuit Fault
5342 | 2004 | 6 | 20 | 0.64375 |  | 33 | 220 | 400 |  |  | Casselman F2 | Pieere reports 2 phases slapped together causing the circuit to open | Castleman | Adverse Weather | Wind
17461 | 2010 | 12 | 30 | 0.45972 |  | 118 | 2 | 1 | Carleton Place | 8/4.8kV | CPLF2 | At 11:02 transformer X36328 at 8664 Mcarton Road was isolated to allow crew to replace defective transformer. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
12727 | 2008 | 6 | 25 | 0.43125 |  | 69 | 1 | 1 | Carp | 8/4.8kV | CRPF1 | Transformer #X38133 located at 1756 Old Carp Rd isolated due to squirrel contact | Goulburn | Foreign Interference | Animal
20659 | 2012 | 5 | 29 | 0.22431 |  | 7 | 145 | 1244 | Cyrville | 27.6/16kV | CRYF2 | CYRF2 circuit opened during thunder storm. | Gloucester | Adverse Weather | Lightning
18117 | 2011 | 5 | 9 | 0.39444 |  | 184 | 205 | 67 | Cyrville | 12/7.2kV | CYR | Transformer TP7989, TP7988, TP7987, TP7986, TP7985, TP7984, TP7983 were isolated to allow crew to replace elbows and inserts on transfromer and to replace cut out at riser pole. | Gloucester | Scheduled Outage
19423 | 2011 | 10 | 20 | 0.2625 |  | 19 | 158 | 500 | Cyrville | 27.6/16kV | Cyr F2 | Ottawa police & Ottawa Fire called No reports of MVA. Breaker closed all load restored. | Gloucester | Adverse Weather | Rain
20415 | 2012 | 4 | 30 | 0.46181 |  | 209 | 767 | 1230 | Cyrville | 27.6/16kV | CYR F4 | One lead from G68 fell into the adjacent phase, causing the CYR F4 to trip, and two fuses to blow at G68. G68 isolated, and CYR F4 closed. Repairs made to G68, and closed restoring all customers | Gloucester | Defective Equipment
17770 | 2011 | 3 | 23 | 0.38403 |  | 285 | 392 | 124 | Cyrville | 27.6/16kV | CYRF1 | S25500 to S15980 on Sablewood Place was isolated to allow crews to Replace Switches, 124 customers affected. S25500 to TP8013 isolated to allow crews to replace elbow & inserts | Gloucester | Scheduled Outage | Preventive Maintenance
20233 | 2012 | 3 | 26 | 0.39792 |  | 262 | 22 | 5 | Cyrville | 27.6/16kV | CYRF1 | Hydro Ottawa crews isolated transformers TE2500 & TE2823 at 3080 Innes Rd sothat elbows & inserts could be replaced & nomenclatures changed & updated. | Gloucester | Scheduled Outage | Preventive Maintenance
17803 | 2011 | 3 | 30 | 0.4 |  | 267 | 258 | 58 | Cyrville | 27.6/16kV | CYRF1 | 4, 27kV transfromers on Loranger Crt. And Sablewood Pl. Were interrupted to allow crews to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
17852 | 2011 | 4 | 7 | 0.44514 |  | 199 | 159 | 48 | Cyrville | 27.6/16kV | CYRF1 | Transformers TP7999, TP7998 and TP7997 on Aspenview were isolated to allow crews to replace elbows and insert. | Gloucester | Scheduled Outage | Preventive Maintenance
17938 | 2011 | 4 | 15 | 0.26528 |  | 128 | 32 | 15 | Cyrville | 27.6/16kV | CYRF1 | G153 @ 1903 INNES RD was opened to allow crew to make repair to terminations at G153. 15 customers were affected for 128 mninutes. Cyrville (CYRF1) | Gloucester | Defective Equipment
17953 | 2011 | 4 | 18 | 0.39028 |  | 304 | 481 | 95 | Cyrville | 27.6/16kV | CYRF1 | 8 transformers on Aspenview Way were interrupted to allow crews to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
20353 | 2012 | 4 | 19 | 0.42222 |  | 323 | 183 | 34 | Cyrville | 27.6/16kV | CYRF1 | TP6902, TP6903, TP6905 and TP6899 on Eastboro Ave. Were isolated to allow a contractor to pull primary cable and energize 3 new transformers | Gloucester | Scheduled Outage | Construction
20437 | 2012 | 5 | 2 | 0.42569 |  | 72 | 2 | 2 | Cyrville | 27.6/16kV | CYRF1 | At 11:09am crews isolated TP6780 at 704 Morningstar Way to replace a damaged transformer. Cyrville CYRF1 ID# 20437 | Gloucester | Scheduled Outage | Repair
18096 | 2011 | 5 | 5 | 0.37778 |  | 208 | 184 | 53 | Cyrville | 12/7.2kV | CYRF1 | Transformers TP7981, TP7980, TP7979, TP7978, TP7977 and TP7976 Innes and Page were isolated to allow crews to change elbows and inserts to vented style | Gloucester | Scheduled Outage | Preventive Maintenance
18130 | 2011 | 5 | 11 | 0.39583 |  | 204 | 439 | 129 | Cyrville | 27.6/16kV | CYRF1 | Transformers TP7996, TP7995, TP7994, TP7993, TP7992, TP7991, TP7990 on Arbourwood Dr were isolated to allow crew to replace elbows and inserts in transfromers and cut out at riser pole | Gloucester | Scheduled Outage
20783 | 2012 | 6 | 17 | 0.24028 |  | 208 | 8651 | 4100 | Cyrville | 27.6/16kV | CYRF1 | CYRF1 A/R then RX2022 & CYRF1 tripped open. Cct sectionalized using CS17768. Fault indicators at SE13 led crew to isolate cable section between SE13 & SE23. CYRF1 closed & held for 4 min. Crew then found RX2022 had failed, same disconnected & by-pass switches closed, CYRF1 closed & held. Remainder of customers from SE13 then restored. Crew then found G613W blown. FCI's in loop indicated clear, cable from G613W hi-pooted, checked OK. G613W replaced & closed restoring all customers. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18730 | 2011 | 7 | 18 | 0.83333 |  | 1504 | 908 | 66 | Cyrville | 27.6/16kV | CYRF1 | Broken cross arm caused G852 and S28849 to blow. Cross arm repaired and switches closed to restore power. | Gloucester | Defective Equipment
16529 | 2010 | 7 | 21 | 0.89444 |  | 5 | 26 | 316 | Cyrville | 27.6/16kV | CYRF1 | SCADA indicated CYRF1 opened during lightning storm in area. No Auto Reclose. CYRF1 closed back in and holding. | Gloucester | Lightning
19004 | 2011 | 8 | 23 | 0.42917 |  | 320 | 267 | 50 | CYRVILLE | 27.6/16kV | CYRF1 | At 10:18 transformers TP7336,TP7334,TP7335,TP5722 and TP5719 were isolated to pull in new cable. Cyrville CYRF1 ID# 19004 | Gloucester | Scheduled Outage
19230 | 2011 | 9 | 21 | 0.65556 |  | 55 | 11 | 12 | Cyrville | 27.6/16kV | CYRF1 | TP8000 at 1761 Aspenview was isolated to move the transformer back onto its base after being knocked off. | Gloucester | Scheduled Outage | Repair
17546 | 2011 | 2 | 2 | 0.51458 |  | 10 | 6 | 34 | Cyrville | 27.6/16kV | CYRF2 | CYRF2 breaker tripped, no A/R, No Spike in load. RED & BLUE INST tagrgets flagged. Police and Fire have nothing reported. CYRF2 breaker closed and holding, load slowly restoring, crews found R&B Inline fuse blown at S19279, further patrol found no issues. Suspect snowplow contact with pole in city yard | Gloucester | Unknown/Other
15737 | 2010 | 2 | 23 | 0.32639 |  | 301 | 1383 | 285 | Cyrville | 27.6/16kV | CYRF2 | The pole at switch G502 @ 1471 Blair Rd caught on fire causing the CyrF2 circuit to trip, tempory repairs were made. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
17637 | 2011 | 2 | 23 | 0.13542 |  | 265 | 9 | 2 | Cyrville | 27.6/16kV | CYRF2 | OFD reported Pole fire, crews found defective Transformer X17879 at 1511 Innes, Replaced & customers restored at 7:40am, 2 customers affected for 265 minutes | Gloucester | Defective Equipment
18163 | 2011 | 5 | 16 | 0.35208 |  | 48 | 22 | 34 | Cyrville | 27.6/16kV | CYRF2 | Customer reported outage (Cyrville RTU down), Doug Baldock reports CYRF2 breaker open, Targets A & C flagged INST. Patrol fopund two fuses blown at S19279, third fuse openned and breaker closed, then S19279 refused, closed. | Gloucester | Unknown/Other
20550 | 2012 | 5 | 22 | 0.38125 |  | 25 | 4 | 10 | Cyrville | 27.6/16kV | CYRF2 | CYRF2 CB tripped and locked out, found dead squirrel at open point between 8F3 & CYRF2. | Gloucester | Foreign Interference | Animal
17993 | 2012 | 5 | 29 | 0.22431 |  | 7 | 473 | 4054 | Cyrville | 27.6/16kV | CYRF2 | CYRF2 circuit opened during thunder storm. Also CYRF4 & 48M5 circuit tripped at the same time. M3 load was transferred to 48M5 circuit at that time. | Gloucester | Adverse Weather | Lightning
20689 | 2012 | 6 | 4 | 0.36875 |  | 55 | 3 | 9 | CYRVILLE | 27.6/16kV | CYRF2 | CYRF2 breaker tripped due to bird contact at transformer X24262. Breaker closed and transformer refused to restore customers. | Gloucester | Foreign Interference | Bird
15269 | 2009 | 10 | 16 | 0.74792 |  | 92 | 452 | 295 | Cyrville | 27.6/16kV | CYRF2 | CYRF2 breaker auto-reclosed once at the same time as the CYRT2Q & CYRJQ breakers tripped clearing the Q bus, when the F2 breaker closed back in the bus was off. One attempt to energize caused the red phase fuse to blow at G865 allowing the remainder of circuit to be restored. Problem was determined to be a red phase cable fault between G865 & SC4908 at Telesat. Telesat was then restored to full power from alternate supply. | Gloucester | Defective Equipment
20620 | 2012 | 5 | 25 | 0.78819 |  | 1279 | 1045 | 49 | Cyrville | 27.6/16kV | CYRVLLE F1 | tree limb on pot Head switch G304. Limb removed and switch closed. | Gloucester | Tree Contacts | Tree Fallen
7820 | 2006 | 1 | 18 | 0.40972 |  | 507 | 8 | 1 | Casselman | 8/4.8kV | F1 | CUSTOMERS METER ISOLATED FOR REPLACEMENT FROM T139 THREE PHASE O/H TRANSFORMER. GORD MACDONALD OF SPROULE ISOLATED METER BASE. | Casselman | Adverse Weather | Rain
4737 | 2004 | 1 | 26 | 0.82292 |  | 11 | 2 | 9 | Casselman | 8/4.8kV | F1 | Transformer at 863 Principale interrupted to replace live line clamp. | Castleman | Defective Equipment | Equipment Deterioration Due to Age
3333 | 2003 | 4 | 11 | 0.76736 |  | 125 | 10 | 5 | Casselman | 12/7.2kV | F1 | Pierre Mercier reports Bird caused fuse (S108W @ 804 Principale) to blow. Fuse replaced all power restored to normal. | Castleman | Foreign Interference | Bird
6402 | 2005 | 4 | 12 | 0.39583 |  | 90 | 8 | 5 | Epworth | 4.16kV | F1 | Isolated Transformer # 1084 at 91 Chippewa to install new service | Ottawa | Scheduled Outage | Construction
6572 | 2005 | 5 | 18 | 0.46181 |  | 63 | 6 | 6 | Richmond South | 8/4.8kV | F1 | Isolated Trsansformer # 182 at 125 Hamilton in Richmond to repair a bad neutral | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7057 | 2005 | 8 | 3 | 0.51667 |  | 206 | 7 | 2 | Alexander | 27.6/16kV | F1 | Isolated Transformer # 17709 at 26 Canadian to change bad transformer | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9655 | 2006 | 11 | 14 | 0.30208 |  | 75 | 2 | 2 | CASSELMAN | 8/4.8kV | F1 | Isolated and replaced transformer 151 at 8 Racine St | Castleman | Scheduled Outage | Preventive Maintenance
9657 | 2006 | 11 | 14 | 0.39861 |  | 76 | 10 | 8 | CASSELMAN | 4.16kV | F1 | Changed trf. # 109 @ 21 Alice | Castleman | Scheduled Outage | Preventive Maintenance
9660 | 2006 | 11 | 14 | 0.53125 |  | 105 | 9 | 5 | CASSELMAN | 8/4.8kV | F1 | Isolated and replaced Transformer 110 at 27 Alice St | Castleman | Scheduled Outage | Preventive Maintenance
9661 | 2006 | 11 | 15 | 0.36458 |  | 105 | 14 | 8 | Casselman | 8/4.8kV | F1 | trf. @ 721 ST. ISISDORE WAS CHANGED AS PER MTCE. | Castleman | Scheduled Outage | Preventive Maintenance
9716 | 2006 | 11 | 23 | 0.35417 |  | 490 | 65 | 8 | Casselman | 8/4.8kV | F1 | Transformer #TP3376 located at 84 Lafleche Blvd isolated to install new conductor | Castleman | Scheduled Outage | Construction
7671 | 2005 | 12 | 1 | 0.39236 |  | 20 | 4 | 13 | Bridlewood | 27.6/16kV | F1 | Transformer #2527 located at 117 Country Lane isolated to disconnect a customer's service | Kanata | Scheduled Outage | Construction
7673 | 2005 | 12 | 1 | 0.59722 |  | 20 | 4 | 13 | Bridlewood | 27.6/16kV | F1 | Transformer #2527 located at 117 Country Lane isolated to disconnect a customer'r service | Kanata | Scheduled Outage | Construction
4451 | 2003 | 11 | 13 | 0.81667 |  | 254 | 12472 | 4354 | Bridlewood | 27.6/16kV | F1, F3 & F4 | Hydro One's W6MC circuit went out due to unknown causes. The transmission circuit was re-energized within minutes by Hydro One. Further investigation found that the BRD F4 breaker operated and went to lockout, the circuit switcher BRD-T1-B1, on the low side of the transformer BRD T1, also went to lockout aIong with the circuit switcher 605-W6MC on the high side of the transformer. So possible transformer damage was investigated and the power was restored when it was felt that there was no damage done. ID#4446 | Kanata | Adverse Weather | Wind
7789 | 2006 | 1 | 10 | 0.50903 |  | 58 | 9 | 9 | Beckwith | 8/4.8kV | F2 | SW649 opened to allow crew to move cbls from old pole to new pole, SW649 closed back in all customers restored. | Goulburn | Scheduled Outage | Repair
7906 | 2006 | 2 | 11 | 0.72708 |  | 197 | 3 | 1 | Beckwith | 27.6/16kV | F2 | A broken pole caused by a vehicle accident on Dwyerhill Rd. | Goulburn | Foreign Interference | Vehicle
12062 | 2008 | 2 | 19 | 0.54167 |  | 60 | 8 | 8 | Alexander | 8/4.8kV | F2 | At 13:00 trans at 511 Overland Dr was isolated in order to replace trans | Kanata | Scheduled Outage | Preventive Maintenance
6232 | 2005 | 2 | 24 | 0.61111 |  | 18 | 1 | 4 | Alexander | 27.6/16kV | F2 | Transformer 9687 isolated to change blown arrestor at 25 Carlyle | Ottawa | Defective Equipment
6234 | 2005 | 2 | 25 | 0.39236 |  | 20 | 15 | 44 | Alexander | 27.6/16kV | F2 | Planned outage to 3 txs for switching affecting customers on Bell St. | Ottawa | Scheduled Outage
6235 | 2005 | 2 | 25 | 0.5625 |  | 50 | 4 | 5 | Alexander | 27.6/16kV | F2 | Transformer 7842 isolated to repair a bad cutout | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12076 | 2008 | 2 | 25 | 0.41111 |  | 83 | 7 | 5 | Beckwith | 27.6/16kV | F2 | At 09:52 transformer at 8634 McLinton Rd was isolated in order to replace defective trans | Goulburn | Scheduled Outage | Preventive Maintenance
4844 | 2004 | 3 | 2 | 0.025694 |  | 198 | 13 | 4 | Richmond North | 8/4.8kV | F2 | Traffic accident involving a hydro pole at 1916 Stittsville Main St. Pole repaired by 24/ 7 & overtime crews. | Goulburn | Defective Equipment
8025 | 2006 | 3 | 14 | 0.9375 |  | 155 | 3 | 1 | Beckwith | 27.6/16kV | F2 | Blown fuse replaecd at 7910 Flewellyn Rd | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
6318 | 2005 | 3 | 24 | 0.42431 |  | 34 | 1 | 2 | Alexander | 27.6/16kV | F2 | Isolated Transformer # 2703 at 45 Neil Ave to repace downguy | Ottawa | Scheduled Outage | Preventive Maintenance
6323 | 2005 | 3 | 24 | 0.54236 |  | 34 | 1 | 2 | Beckwith | 27.6/16kV | F2 | Isolated Transformer # 6030 at 8960 Ormrod to replace blown arrestor | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8076 | 2006 | 3 | 29 | 0.39583 |  | 120 | 6 | 3 | Beckwith | 27.6/16kV | f2 | Transformer located at 27 Spruce Ridge Rd isolated to change over to new pole | Goulburn | Scheduled Outage | Construction
5001 | 2004 | 4 | 14 | 0.42431 |  | 137 | 5 | 2 | Munster | 8/4.8kV | F2 | Transformer 8472W25 at 8472 Franktown isolated to change cut -out switch. | Goulburn | Defective Equipment
5002 | 2004 | 4 | 14 | 0.58958 |  | 26 | 0 | 1 | Munster | 8/4.8kV | F2 | Transformer 7885R50 at 7885 Jocktrail isolated to change lightning arrestors. | Goulburn | Defective Equipment
6468 | 2005 | 4 | 27 | 0.55208 |  | 45 | 1 | 1 | Beckwith | 27.6/16kV | F2 | Transformer (# unknown) at 8283 Fernbank Rd isolated to change a blown lightning arrester | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
6524 | 2005 | 5 | 9 | 0.59028 |  | 21 | 0 | 1 | Munster | 8/4.8kV | F2 | Transformer at 8960 Purdy isolated to replace lightning arrester | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
6599 | 2005 | 5 | 24 | 0.76389 |  | 146 | 2 | 1 | Alexander | 27.6/16kV | F2 | Replaced fuse in Transformer at 8735 McCaffery Tr after tree branch caused fuse to blow | Ottawa | Tree Contacts
10465 | 2007 | 5 | 27 | 0.25 |  | 240 | 160 | 40 | Wonderland | 8/4.8kV | F2 | At approx 6:00am, Hydro One had a scheduled outage to Wonderland F2 for Hwy 7 expansion work. Approx 30 of our customers in the Ashton Station Rd area were affected until approx 10:00am. | Goulburn | Scheduled Outage | Construction
3527 | 2003 | 6 | 6 | 0.063194 |  | 110 | 2 | 1 | Beckwith | 27.6/16kV | F2 | M. Brown reports a racoon on hydro pole has cause transformer fuse to blow. Fuse was replaced restoring power to customer. | Goulburn | Foreign Interference | Animal
10855 | 2007 | 7 | 11 | 0.42986 |  | 94 | 16 | 10 | Alexander | 27.6/16kV | F2 | Transformer #8234 at 21-41 & 10 & 12 Kathleen Cres isolated to allow for emergency repairs | Goulburn | Scheduled Outage | Repair
3816 | 2003 | 7 | 29 | 0.71389 |  | 252 | 8 | 2 | Beckwith | 27.6/16kV | F2 | Transformer 8511 at 8511 Fallowfield in Goulbourn hit by lightning and was changed. | Goulburn | Lightning | Direct Strike
7137 | 2005 | 8 | 14 | 0.32639 |  | 81 | 1 | 1 | Beckwith | 27.6/16kV | F2 | Replaced broken switch to transformer #7635 at 7635 Fernbank Rd | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
9242 | 2006 | 9 | 18 | 0.38889 |  | 85 | 3 | 2 | Beckwith | 27.6/16kV | F2 | At 09:20 Trans # 2862 at Dwyer Hill / Bleeks Rd was isolated in order to replace transformer | Goulburn | Scheduled Outage
9244 | 2006 | 9 | 18 | 0.61806 |  | 100 | 13 | 3 | Beckwith | 27.6/16kV | F2 | At 14:50 trans at 2914 Dwyer Hill Rd was isolated in order to replace sec service | Goulburn | Scheduled Outage
9363 | 2006 | 10 | 2 | 0.79931 |  | 66 | 2 | 2 | Beckwith | 27.6/16kV | F2 | Fuse to transformer 7825 at 7825 Fallowfield Rd was found blown due to a squirrel contact | Goulburn | Foreign Interference | Animal
7518 | 2005 | 10 | 25 | 0.6875 |  | 254 | 13 | 3 | Beckwith | 27.6/16kV | F2 | Transformer #8475 located at 8511 Fallowfield isolated due to a blown transformer | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
9569 | 2006 | 10 | 31 | 0.8625 |  | 70 | 1 | 1 | Beckwith | 27.6/16kV | F2 | Fuse to Transformer 2070 at 2070 Munster Rd was found blown due to animal contact crew had to replace the switch and restored power | Goulburn | Foreign Interference | Animal
9599 | 2006 | 11 | 4 | 0.31875 |  | 96 | 6 | 4 | Beckwith | 27.6/16kV | F2 | Switch to transformer 7594 at 7594 Flewellyn Rd was found blown due to Squirrel. refused the switch and restored power | Goulburn | Foreign Interference | Animal
7594 | 2005 | 11 | 11 | 0.47014 |  | 178 | 3 | 1 | Munster | 8/4.8kV | F2 | Customer owned Primary line feeding transformer 7827 at 7827 Jock Trail Rd was isolated to remove tree and repair primary natural | Goulburn | Tree Contacts | Tree Fallen
7612 | 2005 | 11 | 14 | 0.56111 |  | 35 | 1 | 1 | Beckwith | 27.6/16kV | F2 | Isolated Transformer # 7466 at 7466 Fernbank to change a defective arrestor | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7613 | 2005 | 11 | 14 | 0.45139 |  | 25 | 2 | 4 | Munster | 8/4.8kV | F2 | Isolated Transformer # 7723 at Jock Trail to remove a branch off the Transformer | Ottawa | Tree Contacts | Tree Limb Fallen
9668 | 2006 | 11 | 16 | 0.36042 |  | 115 | 23 | 12 | casselman | 8/4.8kV | F2 | Trf. @ 685 Montcalm was change for mtce. | Castleman | Scheduled Outage | Preventive Maintenance
7676 | 2005 | 12 | 2 | 0.19444 |  | 30 | 2 | 5 | Beckwith | 27.6/16kV | F2 | A section of overhead line on Dwyer Hill Rd was isolated for 24/7 crew to clear broken guy wire & glass rod insulator away from circuit. Guywire & pole were broken by a vehicle accident. | Goulburn | Foreign Interference | Vehicle
7736 | 2005 | 12 | 15 | 0.57917 |  | 56 | 6 | 6 | Richmond North | 8/4.8kV | F2 | Transformer 212 at 34 Cockburn was isolated to splice secondary | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
3170 | 2003 | 2 | 6 | 0.51042 |  | 75 | 1162 | 930 | Alex F3 | 27.6/16kV | F3 | Received a call from outage desk reporting possible about an outage in Stittsville. Customers at 33 Mika ,28 Eilla & 9 Pool creek ct customers report all out, and 24/7 dispatched. Circuit was tagged hold off for B. Baker. B. Baker surrenders hold off protection, and reports his men are all clear. No contact the conductor by his work group. Hydro One notified to outage, and request promission to operate their reclosure at Alexander. 24/7 reports overhead clear. Al 24/7 closed Alex F3 Red phase reclosure once promission was received from Hydro One. All customer reports power restored. | Goulburn | Unknown/Other | No Apparent Cause
6195 | 2005 | 2 | 9 | 0.38542 |  | 74 | 1 | 1 | Marchwood | 8/4.8kV | F3 | Replaced broken cut out to transformer 000520 at 1620 Sixth line Rd Kanata | Kanata | Defective Equipment | Equipment Deterioration Due to Age
6339 | 2005 | 3 | 30 | 0.56736 |  | 65 | 1 | 1 | Janet King | 8/4.8kV | F3 | Isolated Transformer # 3166 at 6043 Hazeldean rd to replace bad arrestor | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6342 | 2005 | 3 | 31 | 0.625 |  | 60 | 3 | 3 | Marchwood | 27.6/16kV | F3 | Replaced broken switch for transformer #422 at 20 Grierson Lane | Kanata | Defective Equipment | Equipment Deterioration Due to Age
6377 | 2005 | 4 | 6 | 0.50208 |  | 97 | 3 | 2 | Marchwood | 27.6/16kV | F3 | Replaced switch for transformer 2344 at 3 Campbell Reid Dr | Kanata | Scheduled Outage | Preventive Maintenance
6404 | 2005 | 4 | 12 | 0.39583 |  | 30 | 2 | 5 | Marchwood | 27.6/16kV | F3 | Isolated Transformer # 479 at 2310 Dunrobin rd to replace cutout and arrestor | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6480 | 2005 | 4 | 29 | 0.67986 |  | 101 | 3 | 2 | Marchwood | 27.6/16kV | F3 | Transformer #455 isolated at 830 Berry Side Rd, Kanata, due to animal contact (squirrel) | Kanata | Foreign Interference | Animal
6522 | 2005 | 5 | 9 | 0.51458 |  | 30 | 0 | 1 | Munster | 8/4.8kV | F3 | At 12:21 Trans 7825 Bleeks Rd isolated to replace blown arresttor | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
8322 | 2006 | 5 | 19 | 0.39931 |  | 115 | 19 | 10 | Janet King | 8/4.8kV | F3 | Gary Coburn opened transformer 2956 at 25 Norway Spruce to hang a service | Goulburn | Scheduled Outage | Preventive Maintenance
8447 | 2006 | 6 | 7 | 0.66806 |  | 318 | 5 | 1 | Marchwood | 27.6/16kV | F3 | Transformer #2610 located at 2415 Marchurst isolated probably due to tree branches | Kanata | Tree Contacts | Inadequate Trimming
8448 | 2006 | 6 | 7 | 0.91667 |  | 50 | 1 | 1 | Marchwood | 27.6/16kV | F3 | Transformer #1447 located at Constance Lake Rd isolated to replace broken switch | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6815 | 2005 | 6 | 27 | 0.36806 |  | 52 | 4 | 5 | Blackburn | 8/4.8kV | F3 | Isolated Transformer at 2997 Navan rd to relocate same to new pole | Gloucester | Scheduled Outage | Preventive Maintenance
6875 | 2005 | 7 | 6 | 0.375 |  | 158 | 3 | 1 | Marchwood | 27.6/16kV | F3 | Isolated Transformer at 2705 5th line rd to repair bad UG service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6882 | 2005 | 7 | 7 | 0.46319 |  | 74 | 12 | 10 | Alexander | 27.6/16kV | F3 | Switch to transformer #2694 at 26 Johnwoods opened due to vines around the switch | Goulburn | Tree Contacts | Inadequate Trimming
10852 | 2007 | 7 | 11 | 0.69444 |  | 330 | 6 | 1 | Marchwood | 8/4.8kV | F3 | On call crew replaced blown arrester and switch on transformer at 1870 Sixth line Rd possible Lightning strike | Kanata | Adverse Weather | Lightning
10862 | 2007 | 7 | 12 | 0.47917 |  | 39 | 6 | 10 | Richmond |  | F3 | transformer#3859 at 36,24,22,19,17 Healey isolated to allow repairs to secondary connections which were heating up | Goulburn | Scheduled Outage | Repair
7185 | 2005 | 8 | 23 | 0.38542 |  | 38 | 1 | 1 | Richmond N | 8/4.8kV | F3 | Transformer 6922 at 6922 Flewellyn Rd was isolated to replace primary insulator on the pole | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
7203 | 2005 | 8 | 24 | 0.51042 |  | 45 | 4 | 5 | Marchwood | 27.6/16kV | F3 | Transformer 479 at 2310 Dunrobin Rd was isolated to replace service that was ripped down by truck | Kanata | Foreign Interference | Vehicle
3987 | 2003 | 9 | 1 | 0.29375 |  | 77 | 10 | 8 | Alexander | 27.6/16kV | F3 | Transformer #4831 was interrupted due to a squirrel coming into contact with the high voltage connections above the transformer. This cause the fuse to rupture. The fuse was replaced and power was restored. | Goulburn | Foreign Interference | Animal
9445 | 2006 | 10 | 17 | 0.32639 |  | 65 | 5 | 5 | Marchwood | 27.6/16kV | F3 | Fuse to Transformer 1532 at 1210 Old Caro Rd was found blown due to squirrel contact refused switch restored power | Kanata | Foreign Interference | Animal
7476 | 2005 | 10 | 18 | 0.52222 |  | 53 | 3 | 3 | Janet King | 8/4.8kV | F3 | Transformer 3079 at 28 Elm St was isolated to replace a service to 32 Elm St | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
4465 | 2003 | 11 | 16 | 0.20903 |  | 523 | 61 | 7 | Casselman | 8/4.8kV | F3 | Only 1 customer on Brebeuf had reported no power at 05:01 and was advised to get electrician. Further calls came in after 07:00 and one customer reported power had been off since about 01:00 but had not called it in. The transformer had a lot of old oil on it indicating probable leak for a while, but no fresh oil. The transformer was defective and replaced. 7 customers on Brebeuf were affected. | Castleman | Defective Equipment | Equipment Deterioration Due to Age
9703 | 2006 | 11 | 22 | 0.54167 |  | 15 | 0 | 2 | Jockvale | 8/4.8kV | F3 | Isolated transformer NP2524 at 3270 Cedarview Dr to repair neutral | Nepean | Scheduled Outage | Repair
6087 | 2004 | 12 | 22 | 0.30139 |  | 176 | 3 | 1 | Richmond South | 8/4.8kV | F3 | Repalced transformer #3946 W 10Kv front of 3946 McBean St Richmond | Goulburn | Unknown/Other | No Apparent Cause
7212 | 2005 | 8 | 25 | 0.41667 |  | 40 | 8 | 12 | Epworth | 8/4.8kV | F4 | Isolated Transformer #344 at 16 David st to disconnect a service | Ottawa | Scheduled Outage | Preventive Maintenance
3945 | 2003 | 8 | 26 | 0.90417 |  | 63 | 6 | 6 | Barhaven | 8/4.8kV | F4 | Switch # S204 on Cedarview north of Bankfield was opened to allow crews to safely remove a tree from the overhead line. | Nepean | Tree Contacts | Tree Fallen
4450 | 2003 | 11 | 13 | 0.81667 |  | 89 | 2703 | 1822 | Hazeldean | 8/4.8kV | F4, F5 & F6 | Hydro One's W6MC circuit went out due to unknown causes. The circuit was re-energized within minutes by Hydro One and all customers came back on. Further investigation found that the BRD F4 breaker operated and went to lockout, the circuit switcher BRD-T1-B1, on the low side of the transformer BRD T1, also went to lockout aIong with the circuit switcher 605-W6MC on the high side of the transformer. The transformer was isolated and the high side circuit switcher closed restoring power to the F4, F5 & F6 feeders. ID#4451 | Kanata | Adverse Weather | Wind
6405 | 2005 | 4 | 12 | 0.57639 |  | 35 | 6 | 11 | Hazeldean | 4.16kV | F5 | Isolated Transformer # 2522 at 135 Old Colony rd to repair a UG service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8321 | 2006 | 5 | 19 | 0.40625 |  | 20 | 3 | 10 | Epworth |  | F5 | Terry Dans had transformer NP000340 out to remove the service at 88 Palsen. | Nepean | Scheduled Outage
3986 | 2003 | 9 | 2 | 0.57014 |  | 16 | 2 | 8 | Hazeldean | 8/4.8kV | F5 | An overhead transformer had to be isolated in order to replace a defective lightning arrestor. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11439 | 2007 | 10 | 2 | 0.38542 |  | 125 | 8 | 4 | Merivale | 8/4.8kV | F5 | At 09:15 trans at 19 Largo was isolated in order to relocate the trans to a new pole | Nepean | Scheduled Outage | Preventive Maintenance
11769 | 2007 | 11 | 26 | 0.70139 |  | 10 | 1 | 8 | Hazeldean | 8/4.8kV | F5 | Isolated transformer 5915 at 135 Glemorgan Dr to reconnect service to address 137 | Kanata | Scheduled Outage | Emergency Services Request
11775 | 2007 | 11 | 27 | 0.45278 |  | 143 | 29 | 12 | Bridlewood | 8/4.8kV | F5 | Transformer T5870 @ 21 Glamorgan was isolated to replace sagging barrier boards. | Kanata | Scheduled Outage | Repair
11776 | 2007 | 11 | 27 | 0.5625 |  | 59 | 12 | 12 | Bridlewood | 8/4.8kV | F5 | Transformer T5909 @ 167 Glamorgan was isolated to replace sagging barrier boards. | Kanata | Scheduled Outage
11834 | 2007 | 12 | 12 | 0.40625 |  | 30 | 5 | 10 |  | 8/4.8kV | F5 | Isolated transformer 5868 at 22 Heathcliffe Crt for transformer repair | Kanata | Scheduled Outage | Repair
3947 | 2003 | 8 | 26 | 0.45486 |  | 25 | 2 | 5 | Bayshore | 8/4.8kV | F6 | Transformer #1275, at 29 Aero was isolated to allow for the relocation of a down guy. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
12240 | 2008 | 4 | 5 | 0.75347 |  | 480 | 8 | 1 | Greenland | 12/7.2kV | GNNF2 | Transformer 6021 was replaced by Hydro One to restore power to our transfer customer at 364 Thomas A. Dolan Pkwy. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19709 | 2011 | 12 | 9 | 0.097222 |  | 781 | 729 | 56 | Greenland | 27.6/16kV | GNRF2 | A car accident caused the wires down at Galetta side Rd affecting Hydro Ottawa transfer 56 customers, | Kanata | Loss of Supply | Vehicle
6749 | 2005 | 6 | 16 | 0.44792 |  | 173 | 282 | 100 | Moultan | 27.6/16kV | GR05 | A squirrel caused the fuse to blow at an O/H transformer, which caused the fuse to blow at G627W and at G628W on Massey and Rebecca. | Gloucester | Foreign Interference | Animal
3323 | 2003 | 4 | 8 | 0.43264 |  | 52 | 4 | 5 | Limebank | 27.6/16kV | GR1 | While isolating transformer T2585 four position switch failed to remain closed H1B at T2586. Causing power outage to 5 customers at 21 Monet cres. | Gloucester | Human Element | Switching Errors
3324 | 2003 | 4 | 8 | 0.45278 |  | 83 | 1 | 1 | Limebank | 27.6/16kV | GR1 | Transformer #2585 isolated to change leaking transformer. Customers notified April 7. | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
3353 | 2003 | 4 | 17 | 0.43194 |  | 118 | 20 | 10 | Leitrim | 27.6/16kV | GR1 | T667 isolated at 3691 Albion Rd to replace leaking transformer. | Gloucester | Scheduled Outage | Repair
3656 | 2003 | 6 | 30 | 0.85069 |  | 157 | 3 | 1 | Limebank | 27.6/16kV | GR1 | W. Reed reports flash burnt grounding strip off bracket also fuse holder had to be repaired. Cables meggered good transformer te2072 was restored to normal. | Gloucester | Foreign Interference | Bird
5450 | 2004 | 7 | 6 | 0.46528 |  | 4 | 212 | 3173 | Limebank | 27.6/16kV | GR1 | GR1 tripped while restoring TE1455 on Hunters point because new transformer was defective | Gloucester | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
5452 | 2004 | 7 | 6 | 0.39653 |  | 245 | 33 | 8 | Limebank | 27.6/16kV | GR1 | TE1455 was isolated to replace leaking transformer but when we went to restore new transformer the transformer fuse blew and tripped GR1 a new transformer was installed and power restored | Gloucester | Scheduled Outage | Imminent Equipment Failure Detected
6923 | 2005 | 7 | 13 | 0.95833 |  | 180 | 90 | 30 | Limebank | 27.6/16kV | GR1 | G489B switch was directly hit by lightning. Crew replaced switch | Gloucester | Adverse Weather | Lightning
6924 | 2005 | 7 | 13 | 0.97917 |  | 242 | 121 | 30 | LIMEBANK | 27.6/16kV | GR1 | Found 2 blown insulators at G329. Refused and closed. | Gloucester | Adverse Weather | Lightning
3942 | 2003 | 8 | 26 | 0.5 |  | 5 | 264 | 3173 | Limebank | 27.6/16kV | GR1 | The men patrolled the cct. and found nothing. There was a hold off in effect and was surrendered, the GR1 was reclosed and it held. | Gloucester | Unknown/Other | No Apparent Cause
9780 | 2006 | 12 | 2 | 0.44444 |  | 55 | 2658 | 2900 | Limebank | 27.6/16kV | GR1 | A tree fell onto a private O/H runoff that was tap onto the primary which trip the GR1 recloser on leitrim Rd. | Gloucester | Tree Contacts | Tree Fallen
6540 | 2005 | 5 | 11 | 0.40972 |  | 84 | 14 | 10 | Bilberry | 27.6/16kV | GR10 | D. Provost reports T1659 restored after elbows & inserts were replaced on Decarie st . | Gloucester | Scheduled Outage | Preventive Maintenance
5722 | 2004 | 8 | 26 | 0.10417 |  | 131 | 457 | 253 | Bilberry | 27.6/16kV | GR10 | Blue phase cable fault between T1139 & T1140 on Jeanne D'arc. Cause GR10 to auto reclose affecting power to 1304 customer. 453 Customers remained out of power until cable was isolated between T1139 & T1140. Power was restored to all customers by 04:41. | Gloucester | Defective Equipment
5798 | 2004 | 9 | 10 | 0.55556 |  | 76 | 13 | 10 | Billberry | 27.6/16kV | GR10 | Transformer 1139 @ 7869 Jeanne D'arc isolated to replace a previous leaking transformer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9596 | 2006 | 11 | 3 | 0.62778 |  | 319 | 53 | 10 | Bilberry | 27.6/16kV | GR10 | Replace transformer T1659 @ 7979 Decarie because of a defective transformer. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
11747 | 2007 | 11 | 21 | 0.375 |  | 705 | 12 | 1 | Richmond N | 8/4.8kV | GR1086 (29F3) | Transformer located at 2403 Conley Rd isolated due to A9M3 auto reclose with no cause found | Goulburn | Unknown/Other
3360 | 2003 | 4 | 20 | 0.046528 |  | 703 | 243 | 41 | Bilberry | 27.6/16kV | GR11 | Transformer TE1557 was stuck by a car and damaged beyond repair. New padmount had to be installed. | Gloucester | Foreign Interference | Vehicle
5183 | 2004 | 5 | 19 | 0.40278 |  | 407 | 75 | 11 | Bilberry | 27.6/16kV | GR11 | T1769 was isolated at 6464 Beause Jour to clean up oil. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
6618 | 2005 | 5 | 30 | 0.61944 |  | 68 | 16 | 14 | Bilberry | 27.6/16kV | GR11 | Lightning strike caused GR11 reclosure to auto. Also G279 rb fuses found opened. 14 customers fed off this switch . All power restored at 16:00. | Gloucester | Adverse Weather | Lightning
5244 | 2004 | 6 | 2 | 0.44306 |  | 64 | 11 | 10 | Bilberry |  | GR11 | TE1979 on Belcourt isolated due to an oil Leak | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
10869 | 2007 | 7 | 14 | 0.3 |  | 122 | 33 | 16 | BILBERRY | 27.6/16kV | GR11 | Fuse on transformer GL5921 at 6985 Notre Dame St was found blown due to contact with a bird (crow) | Gloucester | Foreign Interference | Bird
7048 | 2005 | 8 | 1 | 0.48958 |  | 70 | 6 | 5 | Bilberry | 27.6/16kV | GR11 | The GR11 auto reclosed crews dispatch to patrol, they found G279B fuse blown crow on the ground. | Gloucester | Foreign Interference | Bird
8952 | 2006 | 8 | 11 | 0.48264 |  | 61 | 405 | 800 | Bilberry | 27.6/16kV | GR11 | The Gr11 tripped under hold off, a dead bird was found at the O/H transformer @ 2231 Belcourt which caused the GR11 to trip and the fuse to blow at the transformer. | Gloucester | Foreign Interference | Bird
9008 | 2006 | 8 | 21 | 0.43403 |  | 179 | 30 | 10 | Bilberry | 27.6/16kV | GR11 | The transformer @ T2203 @ 1759 Silver Bark was isolated because it was leaking oil. | Gloucester | Scheduled Outage | Repair
5772 | 2004 | 9 | 3 | 0.68056 |  | 104 | 312 | 180 | Bilberry | 27.6/16kV | GR11 | Blown cable between transformer T1799W and T1891W on Ave Des Epinattes in Orleans. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6105 | 2004 | 12 | 28 | 0.93056 |  | 210 | 514 | 147 | Bilberry | 27.6/16kV | GR11 | After checking the fault indicators they found a blown cable between S709R to transformer 1864. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12872 | 2008 | 7 | 17 | 0.4375 |  | 1659 | 28 | 1 | Bilberry | 27.6/16kV | GR11 (77M6) | B phase cable at G268 supplying VE5, Cote school on Carrierre failed. VE5 isolated, cable to be repaired next day. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6426 | 2005 | 4 | 19 | 0.42847 |  | 164 | 22 | 8 | Bilberry | 27.6/16kV | GR12 | T2272W at 6243 Beausejour replaed with new transformer. | Gloucester | Scheduled Outage | Repair
6820 | 2005 | 6 | 27 | 0.84583 |  | 412 | 515 | 75 | Bilberry | 27.6/16kV | GR12 | Blue phase cable section failed between T2470b & T2471B on Tooney St. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5411 | 2004 | 7 | 1 | 0.30347 |  | 74 | 122 | 99 | Billberry | 27.6/16kV | GR12 | G552 B phase found blown at Boyer & Viseneau. Storm in the area. | Gloucester | Lightning | Direct Strike
7114 | 2005 | 8 | 10 | 0.75 |  | 165 | 165 | 60 | Billberry | 27.6/16kV | GR12 | S. Brakley reports W&B phase fuse replaced all load restored. In the Boyer & Meadowglen area in Orleans. | Gloucester | Adverse Weather | Lightning
9803 | 2006 | 12 | 6 | 0.85764 |  | 233 | 8 | 2 | Bilberry | 27.6/16kV | GR12 | Transformer TP3592 @ 2600 Mel Bleue was isolated to allow the eclectricain to pull in new cable. | Gloucester | Scheduled Outage | Preventive Maintenance
10025 | 2007 | 2 | 14 | 0.38194 |  | 175 | 88 | 30 | Blackbrun | 8/4.8kV | GR14 | 4F5 ciruit was isolated from GR14 to end of line. To allow Hydro one crews to remove 115KV conductor on Anderson Rd. | Gloucester | Scheduled Outage | Construction
8647 | 2006 | 7 | 2 | 0.75278 |  | 130 | 141 | 65 | Blackburn | 8/4.8kV | GR14 | Peter found a defective lead at the recloser GR14. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
7401 | 2005 | 9 | 29 | 0.59375 |  | 45 | 11 | 15 | Blackburn | 8/4.8kV | GR14 | Tree on the O/H on Anderson Rd caused the W phase to blow at GR14. | Gloucester | Adverse Weather | Wind
7664 | 2005 | 11 | 29 | 0.27083 |  | 477 | 368 | 60 | Blackburn | 8/4.8kV | GR14 | Two section of O/H in seperated loaction on the R phase on Anderson Rd were found laying on the ground and also there was a tree on the wires, and a broken switch on a run off. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6046 | 2004 | 12 | 11 | 0.25833 |  | 219 | 4 | 1 | Bilberry | 27.6/16kV | GR15 | Fused sw G732 feeding tx 959 at RCMP 1426 St Joseph found opened, heavy snow fall & high winds, same refused and closed. | Gloucester | Adverse Weather
8162 | 2006 | 4 | 19 | 0.50903 |  | 32 | 43 | 80 | BILBERRY | 27.6/16kV | GR16 | R. GRIZZEL REPORTS BROKEN INSULATOR FALLEN NEAR ENERGIZED PHASES. CREW OPENED G208 ON PAGE RD. TO REPAIR BROKEN INSULATOR. APROX. 80 CUSTOMERS OFF. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9867 | 2006 | 12 | 19 | 0.5 |  | 139 | 14 | 6 | Bilberry | 27.6/16kV | GR16 | Transformer #GLTE2423 located @1911 Heatherwood isolated to change transformer | Gloucester | Scheduled Outage | Construction
15556 | 2009 | 12 | 26 | 0.72222 |  | 38 | 19 | 30 | Bilberry | 27.6/16kV | GR16 | A tree fell onto the O/H on White Rd near Page causing the G373W to blow. | Gloucester | Tree Contacts | Tree Limb Fallen
12952 | 2008 | 7 | 26 | 0.55347 |  | 328 | 2411 | 441 | Bilberry | 27.6/16kV | GR16 (77M5) | GR16 at Page rd & Innis tripped while under H/O during thunderstorm. The cct supplying GR16, 77M5 also tripped & multiple attempts were made to restore supply. Once 77M5 was restored, it took some time to identify the remaining problem at GR16. There was also a delay contacting the holder of the H/O, H - 1 lines. | Gloucester | Lightning
7796 | 2006 | 1 | 11 | 0.45208 |  | 162 | 990 | 800 | Limbank | 27.6/16kV | GR2 | POLE FIRE AT 990 RIVER RD GLOU. CIRCUIT DUMPED FROM G2 SWITCH. CREW TO RE-DEAD END CABLE. | Gloucester | Unknown/Other | No Apparent Cause
4997 | 2004 | 4 | 13 | 0.5 |  | 155 | 3 | 1 | Limebank | 27.6/16kV | GR2 | Transformer GL245 at 752 River Rd out of service due to pole fire. Temp repairs made by Darcy P. | Gloucester | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
15965 | 2010 | 4 | 21 | 0.37847 |  | 199 | 786 | 237 | Limebank | 27.6/16kV | GR2 | Customers on Mclean, Hillcrest, Claire, Irene, Driscoll, Hartwell, Jean Park and Hilltop on the Manotick Island were iterrupted to allow crews to replace a pole. 237 customers were affected. | Gloucester | Scheduled Outage | Repair
5196 | 2004 | 5 | 22 | 0.19444 |  | 45 | 2 | 3 | Limebank | 27.6/16kV | GR2 | Switch 165W blew causing outage to 3 customers on River Rd. Re-fused and held. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14552 | 2009 | 6 | 17 | 0.28611 |  | 88 | 249 | 170 | Limebank | 27.6/16kV | GR2 | An animal made contact with the O/H in the Mclean Cres/Long Island Rd in Manotick witch caused the fuse to blow at S18183. | Gloucester | Foreign Interference | Animal
5357 | 2004 | 6 | 23 | 0.57639 |  | 102 | 137 | 95 | Limebank | 27.6/16kV | GR2 | Denis Martin found a blown arrestor at 5283 MacLean in Manotic. Causing the fuse to blow at G677W and G443W. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
12784 | 2008 | 7 | 3 | 0.45139 |  | 55 | 99 | 108 | Limebank | 27.6/16kV | GR2 | G166 on long island road was refused. No problem found that would cause outage, maybe the hard rain at the time or a tree contact perhaps. | Gloucester | Unknown/Other | No Apparent Cause
8670 | 2006 | 7 | 6 | 0.37778 |  | 243 | 61 | 15 | Limebank | 27.6/16kV | GR2 | Isolate the transformers T208,T209,T210 in the McLean Cres area in Manotick to replace transformers. | Gloucester | Scheduled Outage | Preventive Maintenance
6981 | 2005 | 7 | 16 | 0.78125 |  | 605 | 161 | 16 | Limebank | 27.6/16kV | GR2 | Lightning struck the O/H line on Spratt Rd which caused two switches to break and blow three others. | Gloucester | Adverse Weather | Lightning
5557 | 2004 | 7 | 23 | 0.46875 |  | 17 | 567 | 2000 | Limebank | 27.6/16kV | GR2 | On closeing and elbow the Red and White phases of GR2 opened under hold off. Cause thought to be energizing 3 phase transformer one phase at a time. Actual cause blown lightning arrester. See next outage # | Gloucester | Defective Equipment
5558 | 2004 | 7 | 23 | 0.50347 |  | 13 | 650 | 3000 | Limebank | 27.6/16kV | GR2 | On closing S32S28 the crew noticed a puff of smoke at and lights out. Cause was a blown lightning arrester on the white phase. | Gloucester | Defective Equipment
5570 | 2004 | 7 | 27 | 0.60694 |  | 45 | 208 | 277 | Leitrim | 27.6/16kV | GR2 | While energizing TE2374 @ 1111 Waterpark Place the elbow flashed over. | Ottawa | Human Element | Incorrect Use of Equipment
5571 | 2004 | 7 | 27 | 0.52153 |  | 123 | 37 | 4 | Leitrim | 12/7.2kV | GR2 | TE2374 was interupted to repair damage to pedastal by a vehicle accident. | Gloucester | Scheduled Outage | Repair
5599 | 2004 | 8 | 2 | 0.34722 |  | 60 | 39 | 42 | Limebank | 27.6/16kV | GR2 | Crow on transformer TX5866 cause G224R to blow. Crow removed and new fuse insalled. | Gloucester | Foreign Interference | Bird
5601 | 2004 | 8 | 2 | 0.39306 |  | 15 | 3 | 42 | Limebank | 27.6/16kV | GR2 | Tx switch 5866 broken. G224R opened to open TX switch 5866. Driscoll Dr Manotick. | Gloucester | Defective Equipment | Imminent Equipment Failure Detected
9723 | 2006 | 11 | 24 | 0.46389 |  | 72 | 32 | 27 | Manotick | 8/4.8kV | GR2 | Crew found SW G713 open at North Riverside Cres and North Riverside Dr. Crew patrolled the overhead no cause was found. Refused the switch and restored power | Gloucester | Unknown/Other | No Apparent Cause
19708 | 2011 | 12 | 8 | 0.6 |  | 487 | 199 | 68 | Limebank | 27.6/16kV | GR2 | Defective cable from switch S21533 @ 5287 HILLCREST DR RIDEAU | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
10958 | 2007 | 7 | 27 | 0.40278 |  | 64 | 3 | 3 | Limebank | 27.6/16kV | GR2/7F4 | Transformer #X13229 at 489 Rideau Rd. isolated to allow for broken switch replacement | Gloucester | Scheduled Outage | Repair
5606 | 2004 | 8 | 3 | 0.5125 |  | 41 | 683 | 1000 | Limebank | 27.6/16kV | GR2W | J. Streng reports Lightning strom in area. Caused GR2 W phase to open. D. Martin dispatched to GR2. J. Streng to check reports of loud bangs at customer locations. | Gloucester | Adverse Weather | Lightning
14801 | 2009 | 7 | 21 | 0.52847 |  | 117 | 68 | 35 | South Gloucester | 8/4.8kV | GR3 | Conductor fell on Mitch Owen east of Bank from GR3. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9978 | 2007 | 1 | 31 | 0.86528 |  | 2 | 1 | 30 | Blackburn | 8/4.8kV | GR4 | GR4 blue opened while crew was restoring recloser. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
7398 | 2005 | 9 | 29 | 0.44792 |  | 25 | 2 | 5 | LETRIUM | 27.6/16kV | GR4 | BLOWN FUSE AT G53 CAUSED BY DOWNED WHITE PHASE OVERHEAD. THE REMAINING TWO PHASES WERE OPENED TO MAKE REPAIRS. | Gloucester | Adverse Weather | Wind
7210 | 2005 | 8 | 25 | 0.39583 |  | 39 | 3 | 5 | Moulton | 27.6/16kV | GR5 | Isolated Transformer 1390 at 657 Blair rd to do pole testing | Ottawa | Scheduled Outage | Preventive Maintenance
5635 | 2004 | 8 | 10 | 0.38889 |  | 4 | 45 | 676 | leitrim | 27.6/16kV | GR6 | While setting a hold Off on the GR6 in line reclosers the reclosers tripped, same closed and circuit restored. | Gloucester | Human Element | Incorrect Use of Equipment
5678 | 2004 | 8 | 14 | 0.29861 |  | 109 | 54 | 30 | Leitrim | 27.6/16kV | GR6 | A squirrel made contact at transformer 4334 @ 4174 Farmers Way causing the fuse to blow at switch 540R. | Gloucester | Foreign Interference | Animal
3213 | 2003 | 2 | 26 | 0.47917 |  | 564 | 351 | 41 | LIMEBANK | 27.6/16kV | GR8 | G325R ON RIVER ROAD WAS FOUND BLOWN DUE TO A BLOWN ARRESTOR CREW MADE REPAIRS REFUSED AND CLOSED | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
3770 | 2003 | 7 | 22 | 0.69028 |  | 44 | 26 | 35 | Limebank | 27.6/16kV | GR8 | GR8 auto reclosed effecting 199 customers. 24/7 dispatched to patroll circuit. Reports of outage 17 Lennon transformer is blown. Crew reports G455W fuse switch found open. Crew refused switch restoring 30 customers. Crews report No Apparent Cause for transformer fuse to be blown at 17 Lennon. Transformer fuse replaced all load restored. | Gloucester | Unknown/Other | No Apparent Cause
4363 | 2003 | 10 | 31 | 0.58333 |  | 30 | 3 | 6 | Limebank | 27.6/16kV | GR8 | Replaced cracked insulator on GL5959 at 60 Mary Dr. | Gloucester | Defective Equipment
7804 | 2006 | 1 | 13 | 0.42361 |  | 210 | 10 | 3 | Moulton | 8/4.8kV | GR9 | Transformer #GL002286 located at 13 Cedar Rd isolated to change transformer | Gloucester | Scheduled Outage | Repair
7840 | 2006 | 1 | 21 | 0.625 |  | 166 | 58 | 21 | Moultan | 8/4.8kV | GR9 | Limb took down the triplex to 14 Kindle which also caused the primary switch 529R to blow. | Gloucester | Adverse Weather | Snow
8023 | 2006 | 3 | 14 | 0.50972 |  | 16 | 4 | 15 | Moulton | 27.6/16kV | GR9 | Broken switxh at 594 @ Miss Ottawa at Lerner. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
6731 | 2005 | 6 | 15 | 0.041667 |  | 430 | 287 | 40 | Limebank | 27.6/16kV | GR9 | Blown switch found at G247. Switch replaced all power restored to normal. | Gloucester | Adverse Weather | Lightning
4075 | 2003 | 9 | 16 | 0.41319 |  | 90 | 540 | 360 | Moulton | 27.6/16kV | GR9 | A balloon string crossed two phases of the circuit on Appleford in Gloucester causing switch G285R and G285W to rupture. The string was removed, fuses replaced and closed. Full power was restored. | Gloucester | Foreign Interference | Foreign Object
13942 | 2009 | 2 | 8 | 0.22778 |  | 122 | 20 | 10 | Greely | 8/4.8kV | Greely F3 | Hydro - 1 circuit Greely F3 supplying approx 10 transfer customer on Boundary rd tripped. (hydro one found no cause) | Gloucester | Loss of Supply
13963 | 2009 | 2 | 12 | 0.82431 |  | 372 | 62 | 10 | Greely |  | Greely F3 | Hydro - 1 circuit Greely F3 supplying approx 10 transfer customer on Boundary rd tripped. (hydro one found no cause) | Gloucester | Loss of Supply
19296 | 2011 | 10 | 1 | 0.0020833 |  | 122 | 10 | 5 | Greely | 8/4.8kV | Greely F3 | Inline fuse found blown on circuit all power restored. | Gloucester | Loss of Supply | HEPC Circuit Fault
5854 | 2004 | 11 | 4 | 0.87083 |  | 66 | 9 | 8 | Greely DS | 8/4.8kV | Greely F3 | An outage on Greely F3 circuit caused an outage to 8 transfer customers. Cause of outage was due to MVA and broken hydro pole. | Gloucester | Loss of Supply | HEPC Circuit Fault
12686 | 2008 | 6 | 18 | 0.069444 |  | 860 | 645 | 45 | Greenland | 8/4.8kV | Greenland F2 | Transfer customers on Thomas Dolan, Sixth Line & Neely were affected by loss of a 44kv feeder supplying Hydro - 1 Greenland MS. Several tree contacts on the 44 Kv and the underbuild. | Kanata | Loss of Supply | HEPC Circuit Fault
17312 | 2010 | 11 | 20 | 0.42431 |  | 126 | 52 | 25 |  | 8/4.8kV | Greenland F2 | Hydro One reports Arnprior 115KV M2 circuit tripped. Circuit feeds transfer customers out of Greenland DS. Hydro One advised there was a close in feeder fault at one of their 44kv stationsd (Woodlawn) which caused the M2 at Arnprior to trip. | Kanata | Loss of Supply
16395 | 2010 | 7 | 4 | 0.83264 |  | 221 | 4 | 1 | Greenland | 12/7.2kV | GRNF2 | Transformer X37023 @ 2665 Sixth Line Rd opened due to animal contact. 1 customer affected for 221 minutes. | Goulburn | Foreign Interference | Animal
12980 | 2008 | 7 | 31 | 0.38889 |  | 90 | 69 | 46 | GreenLand | 44kV | GRNF2 | Customers report no power on Thomas Dolan in the Carp area. Contacted Scott Collins from Hydro One and he reports a broken insulator required repair on the 44kV 61M2 fed from Arnprior TS. 46 customers affected, power restored at 10:50 am. Customers are fed from GRNF2 out of Greenland. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
15151 | 2009 | 9 | 22 | 0.73542 |  | 108 | 2 | 1 | Greenland | 12/7.2kV | GRNF2 | Transformer #X37023 located at 2665 Sixth Line Rd isolated, cause unknown | Kanata | Unknown/Other | No Apparent Cause
5028 | 2004 | 4 | 19 | 0.98889 |  | 493 | 123 | 15 |  | 115kV | H9A | Tap off of the 115kV circuit H9A feeding Navan D.S. caused loss of supply to our transfer customers on Mer Bleue. Hydro One reported most of their load transferred at 02:29, unable to confirm if single customer who had called on Mer Bleue restored. 06:30 customer on Mer Bleue still off. Hydro One reported Navan DS restored at 07:57 | Gloucester | Loss of Supply | HEPC Circuit Fault
12708 | 2008 | 6 | 20 | 0.86042 |  | 10 | 5 | 30 | Hawthorn | 115kV | H9A | Hydro One reported a loss of supply for the H9A. 30 load transfer customers in the cumberland area were without power for 10 minutes. | Gloucester | Loss of Supply
16640 | 2010 | 8 | 4 | 0.57292 |  | 127 | 33170 | 15671 | Billberry | 115kV | H9A | H1's H9A 115 kv circuit tripped during heavy rain & lightning interrupting all load at Bilberry due to 77T1B already opened for a control action for planned work at Hawthorne. Due to a DC failure and loss of station service H1 had no RTU indication or control of Bilberry station. Power could not be restored even after 115 kv circuit was restored until someone went to the station & restored the load locally. | Gloucester | Loss of Supply
11416 | 2007 | 9 | 30 | 0.30556 |  | 264 | 66 | 15 | Navan DS | 27.6/16kV | H9A | Hydro One isolated H9A circuit & Navan DS. 15 Load transfer customers were effected in outage. | Gloucester | Scheduled Outage | Preventive Maintenance
13715 | 2008 | 12 | 7 | 0.45833 |  | 550 | 128 | 14 | Wilhaven | 115kV | H9A | Two 115 kv conductors fell down through the underbuild affecting power to Navan & Wilhaven DS which affected 14 of our transfer customers. Repairs were made& power was restored by Hydro One. | Gloucester | Loss of Supply
10212 | 2007 | 4 | 4 | 0.84514 |  | 203 | 44706 | 15537 | Bilberry | 115kV | H9A & A2 | Hydro One Circuit Fault caused H9A & A2 115kv supply to trip, resulting in no power to the Bilberry Substation. Circuits were on single supply from Masson, as both H9A & A2 terminals at Hawthorne were isolated for work protection. | Gloucester | Loss of Supply | HEPC Circuit Fault
13713 | 2008 | 12 | 7 | 0.29167 |  | 225 | 52 | 14 |  | 115kV | H9A (H1) | Scheduled Hydro One Outage affecting 14 Hydro Ottawa transfer customers | Gloucester | Scheduled Outage | Preventive Maintenance
14191 | 2009 | 4 | 20 | 0.21111 |  | 435 | 53505 | 11720 | Hawthorne | 44kV | Hawthorne stn | Hydro One T7 transformer outage at Hawthorne TS caused by a blown lightening arrestor. T8 transformer out of service due to maintenance. Gloucester 8Kv stations affected were Startop, Blackburn & Beaconhill. Hydro One made reapairs on the T7 transformer and all power was restored. | Gloucester | Loss of Supply | HEPC Station Fault
3258 | 2003 | 3 | 16 | 0.33194 |  | 362 | 18 | 3 | Hazeldean | 8/4.8kV | Haz F4 | Scheduled customer outage due to construction of new overhead along Hazeldean Rd. | Kanata | Scheduled Outage | Construction
3248 | 2003 | 3 | 13 | 0.56389 |  | 3 | 3 | 60 | Hazdean | 12/7.2kV | HAZ F5 | Crew reports while restoring HAZF5 circuit to normal. Load was lost when parallel was broken. Crew reclosed 5913W-1 restoring all load to affected transformers. Outage was due to crew installing elbows at TX5859-2, but not closing switch on transformer. | Kanata | Human Element | Switching Errors
3389 | 2003 | 4 | 30 | 0.39931 |  | 32 | 640 | 1200 | Hazeldean | 8/4.8kV | HAZ F5 | During insulator washing, while the spray was directed at a switch, a lead came out of the top of the switch on the 27kv circuit and fell into the 8kv circuit below. Since this circuit was set on hold-off the circuit tripped to lockout. The lead was then cleared and the circuit was restored. A new lead was then installed on the defective switch and power was then restored to the last remaining transformer. This all happened at the corner of Micheal Copeland and Eagleson Roads in Kanata. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3520 | 2003 | 6 | 4 | 0.55208 |  | 100 | 7 | 4 | Hazeldean | 8/4.8kV | Haz F5 | Transformer at 130 Rothesay isolated to replace arrestor. Planned outage. | Kanata | Scheduled Outage | Repair
3897 | 2003 | 8 | 13 | 0.65278 |  | 145 | 290 | 120 | Hazeldean | 8/4.8kV | HAZ F6 | Switch at the corner of Abbeyhill and Castlefrank S36-4R was found ruptured. Tests and checks of fault indicators were made and found nothing. The fuse was replaced and closed restoring full power to all customers. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8053 | 2006 | 3 | 23 | 0.35417 |  | 54 | 1 | 1 | Hazeldean | 8/4.8kV | HAZF4 | Transformer #6009 located at 400 Hazeldean isolated to repair a blown fuse | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5163 | 2004 | 5 | 18 | 0.26319 |  | 5 | 49 | 590 | Hazeldean | 8/4.8kV | HazF4 | Breaker closed from SCADA. Had reports of wire down at Hazeldean at Irwin Gate from OC Transpo. There report was just the location of the strike. | Kanata | Adverse Weather | Lightning
3538 | 2003 | 6 | 8 | 0.4625 |  | 636 | 21 | 2 | Hazeldean | 8/4.8kV | HAZF4 | Transformers 609 & 3206 at Hazeldean & Eagleson isolated for reconfiguration. | Kanata | Scheduled Outage
5387 | 2004 | 6 | 27 | 0.19583 |  | 563 | 19 | 2 | Hazeldean | 8/4.8kV | HAZF4 | LCBO and Frisby Tire at on Eagleson at Hazeldean isolate for clearance for 44kv upgrade. | Kanata | Scheduled Outage | Construction
3797 | 2003 | 7 | 5 | 0.33333 |  | 360 | 60 | 10 | Hazeldean | 8/4.8kV | HAZF4 | Transformer on Hazeldean had to be replaced restoral time is an approximation | Kanata | Lightning | Direct Strike
3204 | 2003 | 2 | 19 | 0.92986 |  | 4 | 30 | 450 | Hazeldean | 8/4.8kV | HazF5 | While crew was fault finding Uxbridge, Heathcliffe,Ballantrae, & Courtney. HazF5 circuit opened and locked out. Circuit reclosed via scada. All load restored to circuit except 80 custumers in the Uxbridge, Heathcliffe Ballantrae, & Courtney area. | Kanata | Defective Equipment
3201 | 2003 | 2 | 20 | 0.9875 |  | 397 | 465 | 130 | Hazeldean | 8/4.8kV | HAZF5 | Crews found blown live front transformer # 5859. Transformer was isolated to change out. 7 customers affected in outage at this location. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3252 | 2003 | 3 | 14 | 0.38889 |  | 52 | 10 | 12 | Hazeldean | 8/4.8kV | HazF5 | TX5914 isolated for Preventive Maintenance at 115 Glamorgan in Kanata. All customers notified of outage. | Kanata | Scheduled Outage | Preventive Maintenance
7202 | 2005 | 8 | 24 | 0.4375 |  | 270 | 45 | 10 | Bridlewood | 12/7.2kV | HazF5 | Transformer 2616 was isolated to allow crews to clean up oil spill. | Kanata | Scheduled Outage | Repair
7561 | 2005 | 11 | 3 | 0.375 |  | 555 | 92 | 10 | Hazeldean | 8/4.8kV | HazF5 | Transformer 2616R @ 98 Abbyhill was isolated to clean up oil spill. | Kanata | Scheduled Outage | Repair
7564 | 2005 | 11 | 4 | 0.38194 |  | 65 | 11 | 10 | Hazldean | 8/4.8kV | HazF5 | Isolated transformer 2658W @ 204 Morenna dr in Kanata to upgrade to a 100KVA. | Kanata | Scheduled Outage | Preventive Maintenance
6786 | 2005 | 6 | 23 | 0.4625 |  | 289 | 48 | 10 | Briblewood | 8/4.8kV | HazF6 | TE4067 at Rickey Pl isolated to allow crews to repair leak. | Kanata | Scheduled Outage | Preventive Maintenance
18616 | 2011 | 7 | 8 | 0.74861 |  | 9 | 238 | 1588 | Castleman | 44kV | HEPC | Hydro One lost the 230 supply to their St Isidore station which cause power outage to Casselman. | Castleman | Loss of Supply | HEPC Circuit Fault
8116 | 2006 | 4 | 7 | 0.80556 |  | 854 | 41518 | 5011 | Hinchey | 13.2kV | Hinchey | Hydro 1 loss of Hinchey Q bus and then Z bus | Ottawa | Loss of Supply | HEPC Station Fault
3600 | 2003 | 6 | 23 | 0.69514 |  | 231 | 12113 | 5861 | Hinchey | 13.2kV | Hinchey | Hydro One 7T3Q breaker faulted. 7T3 and Q bus @ Hinchey cleared. 7T4 was off at the time and all Hinchey load was on T3. 7T4 could not be restored until Fire dep't was clear and damage checked. Switching was done to restore Bayswater T2 and Clifton T2 on lines from Carling. Hydro One restored 7T4 @ Hinchey and Z bus was restored. The rest of the load from Hinchey Q bus was restored using TH00 and circuits from Hinchey Z bus. | Ottawa | Loss of Supply | HEPC Station Fault
16930 | 2010 | 9 | 12 | 0.84167 |  | 20 | 4 | 11 | TH11 | 13.2kV | Hinchey | Transformer X30289 at 102 Merton was isolate by crew due to tracking across porcelain switch | Ottawa | Defective Equipment
17928 | 2011 | 4 | 14 | 0.43056 |  | 56 | 2 | 2 | GREELY | 8/4.8kV | HONI GRLYF3 | Transformer X20353 at 4192 Boundary Rd isolated for 16kV line conversion - Hydro Ottawa load transfer customer | Gloucester | Scheduled Outage | Construction
17931 | 2011 | 4 | 14 | 0.54861 |  | 80 | 4 | 3 | GREELY | 8/4.8kV | HONI GRLYF3 | Transformer X20356 at 4210 Boundary Rd isolated for 16kV line conversion - Hydro Ottawa load transfer customer | Gloucester | Scheduled Outage | Construction
4692 | 2004 | 1 | 11 | 0.71667 |  | 95 | 10 | 6 | Hydro One | 8/4.8kV | Hydro One | 6 customers on Boundary Rd. affected by Hydro One line outage. | Gloucester | Loss of Supply | HEPC Circuit Fault
7870 | 2006 | 1 | 29 | 0.73958 |  | 25 | 62 | 150 | Greenland | 12/7.2kV | Hydro one | Hydro One switch A466 white phase switch arcing. Circuit was isolated while crews jumpered switch out. Outage affected customers on Thomas Dolan Parkway. (Approx 150 customers) | Kanata | Loss of Supply | HEPC Circuit Fault
12241 | 2008 | 4 | 6 | 0.22917 |  | 172 | 40 | 14 | Wilhaven DS | 8/4.8kV | Hydro One | Hydro One planned outage that effected Hydro Ottawa customers in Mere Bleue Rd. | Gloucester | Scheduled Outage | Preventive Maintenance
4165 | 2003 | 9 | 27 | 0.36181 |  | 439 | 15 | 2 |  | 8/4.8kV | Hydro One | Hydro One reports a planned outage to 8 Kv circuit feeding transfer customers. The customer reports that they were not notified of the scheduled outage. They will be calling in to claims on Monday Sept. 29. | Castleman | Loss of Supply | Preventive Maintenance
7448 | 2005 | 10 | 12 | 0.42361 |  | 170 | 113 | 40 | Hydro One | 44kV | Hydro One | Power outage to Hydro Ottawa customers supplied from Hydro One. Pole fire on the 44 kv at Galetta. Repairs made by Hydro One. | Kanata | Loss of Supply | HEPC Circuit Fault
7543 | 2005 | 10 | 30 | 0.29167 |  | 268 | 223 | 50 | Hydro One | 44kV | Hydro One | Scheduled outage by Hydro One that caused outage to Hydro Ottawa transfer customers Along Thomas Dolan Parkway. | Kanata | Loss of Supply | Preventive Maintenance
4461 | 2003 | 11 | 15 | 0.85417 |  | 2120 | 448 | 15 |  | 12/7.2kV | Hydro One | Outage began with loss of supply from Hydro One feeder due to a tree on the feeder. When the feeder was returned it was discovered that a service in Hydro Ottawa equipment as well as a house fire at an other house was causing our runoff to remain o/s. The affected transformer was isolated and the other tx's restored. The final transformer was restored after the defective service was cut clear. We are unable to contact anyone at the service that remains off it is a cottage a distance off the road. Trees will have to be removed by the customer. | Kanata | Loss of Supply | HEPC Circuit Fault
3712 | 2003 | 7 | 10 | 0.0090278 |  | 72 | 5279 | 5310 | Overbrook | 13.2kV | J2 | J2 bus was removed from service automatically by Hydro One's bus differential protection. SC2 capacitor breaker is believed to have failed when automatically removing the capacitor from service. | Ottawa | Loss of Supply | HEPC Station Fault
20240 | 2012 | 3 | 27 | 0.42153 |  | 144 | 29 | 12 | Janet King | 27.6/16kV | JGKF4 | AT 10:07am crews isolated transformer 6930 at 31 Stittsville to replace a leaking transformer. 12 customers affected for 144mins. Janet King, JGKF4, ID# 20240 | Goulburn | Scheduled Outage
20276 | 2012 | 4 | 4 | 0.38611 |  | 271 | 632 | 140 | Janet King | 27.6/16kV | JKGF4 | Crews isolated the transformeers in the Johnathan Pack and Abbott area to replace the elboes and inserts. | Goulburn | Scheduled Outage | Preventive Maintenance
20509 | 2012 | 5 | 14 | 0.38542 |  | 237 | 249 | 63 | Janet King | 27.6/16kV | JKGF4 | Transformers on Johnathan Pack were isolated to allow crews to replace elbows and inserts and overhead switches. | Goulburn | Scheduled Outage | Preventive Maintenance
20513 | 2012 | 5 | 15 | 0.37917 |  | 193 | 42 | 13 | Janet King | 27.6/16kV | JKGF4 | 2 transformers were isolated on Jonathan Pack and Abbott to allow crews to perform elbows and inserts replacement. | Goulburn | Scheduled Outage | Preventive Maintenance
20720 | 2012 | 6 | 8 | 0.69792 |  | 98 | 7 | 4 | Janet King | 8/4.8kV | JKGF4 | transformer X36387 fuse cutout was blown due to animal contact. Outage prolonged due to lightning in the area. Janet King (JKGF4) ID #20720 | Goulburn | Foreign Interference | Animal
18841 | 2011 | 7 | 28 | 0.38056 |  | 95 | 32 | 20 | Janet king | 27.6/16kV | JkGF4 | TP2241 was isolated in a planned shut down to repair transformer graded issue at 184 Coyote Cres | Goulburn | Scheduled Outage | Construction
18871 | 2011 | 8 | 2 | 0.40694 |  | 266 | 355 | 80 | Janet King | 27.6/16kV | JKGF4 | Transformers 20005,20004,8934,8935,8055,8053,7500,7501 in the Carp Rd/McCooeye area were isolated to allow crews replace the elbows and inserts. | Goulburn | Scheduled Outage | Preventive Maintenance
18879 | 2011 | 8 | 4 | 0.37778 |  | 240 | 136 | 34 | Janet King | 27.6/16kV | JKGF4 | Blue phase transformers between switches 123 and 124 were isolated to allow crews to replace elbows and inserts and to install new nomenclature. | Goulburn | Scheduled Outage | Preventive Maintenance
19019 | 2011 | 8 | 26 | 0.4 |  | 223 | 7 | 2 | Janet King | 27.6/16kV | JKGF4 | TP7161 on Hobin St was isolated to allow crews to replace elbows and inserts. | Goulburn | Scheduled Outage | Preventive Maintenance
19151 | 2011 | 9 | 12 | 0.69792 |  | 113 | 28 | 15 | Janet King | 27.6/16kV | JKGF4 | Transformer 20031 at 6 Eliza isolated to change leaking transformer | Goulburn | Scheduled Outage
19394 | 2011 | 10 | 17 | 0.31181 |  | 365 | 2663 | 1100 | Janet King | 27.6/16kV | JKGF4 | A defective elbow in transformer 6692 caused switch S18704 Red phase to blow. An extra 450 customers were affected due to a Hydro One request for isolation over the weekend. | Goulburn | Defective Equipment
19578 | 2011 | 11 | 15 | 0.38472 |  | 214 | 535 | 150 | Janet King |  | JKGF4 | At 9:14 crews isolated a section of the Janet King JKGF4 for insert and elbow replacement on 12 transformers. Janet King JKGF4 ID# 19578 | Goulburn | Scheduled Outage | Preventive Maintenance
19585 | 2011 | 11 | 16 | 0.38194 |  | 240 | 600 | 150 | Janet King | 27.6/16kV | JKGF4 | 14 R phase transformer between S13985 & SC4528 in Stittsville were isolated for elbow & insert upgrades. | Goulburn | Scheduled Outage | Preventive Maintenance
19593 | 2011 | 11 | 18 | 0.37708 |  | 217 | 514 | 142 | Janet King | 27.6/16kV | JKGF4 | blue phase customers on Wintergreen, Hempel, Castlefield, oakfern, carbery and hedgerow, 12 transformers in total were isolated to allow crews to replace elbows and inserts. | Goulburn | Scheduled Outage | Preventive Maintenance
19649 | 2011 | 11 | 30 | 0.39028 |  | 526 | 132 | 15 | Janet King | 27.6/16kV | JKGF4 | TP9147 at 6 Eliza was isolated to allow crews to perform soil remediation | Goulburn | Scheduled Outage | Preventive Maintenance
20170 | 2012 | 3 | 15 | 0.71319 |  | 194 | 1087 | 745 | Janet King | 27.6/16kV | JKGF5 | During switching, Hydro Ottawa crews had an elbow pin fail at transformer 8945-2 causing the red phase fuse 50 to open. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
20339 | 2012 | 4 | 17 | 0.37778 |  | 246 | 467 | 114 | JANET KING | 27.6/16kV | JKGF5 | Transformers between S11121 and S12 on Victor were isolated to allow crew to replace elbows and inserts. | Goulburn | Scheduled Outage | Preventive Maintenance
20387 | 2012 | 4 | 25 | 0.375 |  | 151 | 126 | 50 | Janet King | 27.6/16kV | JKGF5 | 5 transformers between S12 & 631 on Greer & Savage in Stittsville were isolated for elbow & insert upgrades as well as switch maintenace. | Goulburn | Scheduled Outage | Preventive Maintenance
20395 | 2012 | 4 | 26 | 0.375 |  | 169 | 189 | 67 | Janet King | 27.6/16kV | JKGF5 | At 09:00 5 transformers on Eileen Crescent were affected to allow crews to replace elbows and inerts. 67 customers were affected for 169 minutes. Janet King (JKGF5) ID#20395 | Goulburn | Scheduled Outage | Preventive Maintenance
20512 | 2012 | 5 | 15 | 0.29306 |  | 40 | 12 | 18 | JANET KING | 8/4.8kV | JKGF5 | TP8621 at 5 Oakmont isolated to change elbows and insert. | Goulburn | Scheduled Outage | Preventive Maintenance
20540 | 2012 | 5 | 19 | 0.24653 |  | 72 | 12 | 10 | Janet King |  | JKGF5 | A squirrel made contact with transformer with X35229 at 7 Savage Dr. Causing the transformer to open. | Goulburn | Foreign Interference | Animal
19464 | 2011 | 10 | 25 | 0.44792 |  | 175 | 123 | 42 | Janet King | 27.6/16kV | JKGF5 | Transformers 4306, 4307, 4308, 4309, 4310 on Springbrook and Deer Moos Trail were isolated to allow crew to perform elbows and inserts replacement. | Goulburn | Scheduled Outage
19472 | 2011 | 10 | 26 | 0.37639 |  | 114 | 87 | 46 | Janet King | 27.6/16kV | JKGF5 | 4 transformers on Dunedin and River Oaks were isolated to allow crews to replace elbows and inserts. | Gloucester | Scheduled Outage | Preventive Maintenance
19480 | 2011 | 10 | 27 | 0.37639 |  | 175 | 219 | 75 | Janet King | 27.6/16kV | JKGF5 | 7 transformers isolated for elbow and insert replacement on Springbrook/Pebble area. | Goulburn | Scheduled Outage
19518 | 2011 | 11 | 2 | 0.37569 |  | 247 | 856 | 208 | Janet King | 27.6/16kV | JKGF5 | Red phase transformers at Springbrook and Hazeldean between S26333 and S39 were isolated to allow crews to replace elbows and inserts. | Goulburn | Scheduled Outage | Preventive Maintenance
19570 | 2011 | 11 | 13 | 0.69861 |  | 61 | 3 | 3 | Janet King | 27.6/16kV | JKGF5 | Squirrel contact caused overhead transformer X35227 @ 15 Sweetham to open. | Goulburn | Foreign Interference | Animal
9308 | 2006 | 9 | 25 | 0.77708 |  | 96 | 2 | 1 | Jockvale | 8/4.8kV | Jockvale F3 | Transformer #X34781 located at 3460 Twin Elm Rd isolated probably due to tree interference & wind | Nepean | Tree Contacts | Inadequate Trimming
6306 | 2005 | 3 | 21 | 0.46875 |  | 74 | 4 | 3 | Kanata MTS | 27.6/16kV | Kanata F2 | Transformer isolated to change a defective transformer, was wet on the side of the tank | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3465 | 2003 | 5 | 21 | 0.79236 |  | 279 | 2363 | 735 | Kanata | 27.6/16kV | KanF1 | Red phase cable faulted between switches 510 & 477 on the KanF1 circuit. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3463 | 2003 | 5 | 21 | 0.73264 |  | 61 | 44 | 43 | Kanata | 27.6/16kV | KanF2 | 624F2 Breaker tripped off when the 624F1 Breaker was closed while trying to isolate a fault. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3190 | 2003 | 2 | 14 | 0.51042 |  | 290 | 4375 | 1500 | Kan & MWD | 27.6/16kV | KanF2, MWDF4 | Red phase cable fault between Tx1149 & Tx890 on Terry Fox dr. caused KanF2 breaker to open, some load was also lost on the MWDF4 due to an abnormal tie condition. Load was picked up in sections as fault finding took place. Load loss & number of customers is an estimate. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3462 | 2003 | 5 | 21 | 0.73264 |  | 43 | 16 | 23 | Kanata | 27.6/16kV | KanF3 | 624F3 Circuit Breaker tripped when the 624F1 Circuit Breaker was closed while trying to isolate a cable fault. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5831 | 2004 | 10 | 8 | 0.55625 |  | 222 | 5940 | 2500 | Kanata MTS | 27.6/16kV | KANF3 | Cable fault on the KANF3 between S143 (March Rd. & Terry Fox) and S189 (Solant & Hines) The KANF3 was carrying the MWDF3 & MWDF4 circiuts at the time. Marchwood stn was unloaded for Hydro One | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
10637 | 2007 | 6 | 15 | 0.76875 |  | 177 | 728 | 250 | Kanata MTS | 27.6/16kV | KANF4 | A blue phase cable fault between T28B and T33B on Jarlan terrace caused the fuse at S51 to open. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
11826 | 2007 | 12 | 9 | 0.55486 |  | 7 | 583 | 5000 | Limebank | 115kV | L2M (H1) | Due to a problem at the Village of Russel DS, Hydro One had to dump the LM2 circuit which feeds Limebank and Gloucester South. Village Russel DS was isolated and circuit was restored. | Gloucester | Loss of Supply | HEPC Station Fault
18195 | 2011 | 5 | 20 | 0.87361 |  | 142 | 137 | 58 | Leitrim | 27.6/16kV | Leitrim | G212 red phase at 4505 Anderson Road was found blown crew patrolled line and found no issues, crew refused G212. Leitrim (249F2) ID# 18195 | Gloucester | Adverse Weather
5318 | 2004 | 6 | 16 | 0.52083 |  | 45 | 4 | 6 | 7F4 | 27.6/16kV | Limebank | To repair broken cut-out at 5258 Mclean . 6 Customers effected in power outage. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
4305 | 2003 | 10 | 21 | 0.011806 |  | 38 | 729 | 5835 | Limebank | 115kV | M1R | Hydro 1 115kv cct opened & was reclosed. GR8 tripped when station feed restored. Scada displays failed, GR8 was closed via scada once communication restored with GR8. | Gloucester | Loss of Supply
4310 | 2003 | 10 | 21 | 0.080556 |  | 4 | 214 | 5835 | Limebank | 115kV | M1R | Hydro 1 115kv cct opened & was reclosed. GR8 tripped when station feed restored. GR8 was closed via scada once communication restored with GR8. | Gloucester | Loss of Supply | HEPC Circuit Fault
4318 | 2003 | 10 | 21 | 0.31667 |  | 5 | 463 | 5556 | Limebank | 27.6/16kV | M1R | Loss of supply by Hydro One due to Lightning. | Gloucester | Loss of Supply | HEPC Circuit Fault
19605 | 2011 | 11 | 19 | 0.70556 |  | 4 | 790 | 11843 | Limebank MS | 27.6/16kV | M1R | Hydro One's M1R 115kV transmission circuit tripped causing an outage to Hydro Ottawa's Limebank MS. 11,843 customers were affected. | Gloucester | Loss of Supply | HEPC Circuit Fault
6710 | 2005 | 6 | 14 | 0.26389 |  | 10 | 47 | 280 | Beckwith | 44kV | M29C | Hydro One reports 230kv circuit M29C circuit to beckwith station opened. Circuit reclosed via Hydro One operator. | Goulburn | Loss of Supply | HEPC Circuit Fault
12641 | 2008 | 6 | 15 | 0.63681 |  | 3 | 300 | 6000 | Kanata | 230KV | M32S | Hydro One reports the M32S and the C3S auto reclosed because of lightning causing loss of supply to the 624T1 & T2. | Kanata | Loss of Supply | HEPC Circuit Fault
13258 | 2008 | 9 | 18 | 0.40139 |  | 16 | 6665 | 24993 | Nepean | 230 | M32S | Hydro One loss of supply on M32S complete supply to Nepean TS. Small delay on restoring load due to Kanata RTU down. | Nepean | Loss of Supply
15524 | 2009 | 12 | 16 | 0.54792 |  | 26 | 6813 | 15722 | Nepean TS | 230kV | M32S | Hydro Ottawa Stations crew working at Kanata MTS, performing transfer trip test with IESO inadvertanly tripped the M32S. All load restored in 26min, affecting 15722 customers. | Nepean | Human Element | Incorrect Use of Equipment
3270 | 2003 | 3 | 18 | 0.39514 |  | 61 | 712 | 700 | EPWORTH | 8/4.8kV | M4G | 3 FUSES WERE FOUND BLOWN ON THE HIGH SIDE OF THE 58T1 DUE TO A BLOWN ARRESTOR AND FLASHED OVER INSULATORS LOAD WAS TRANSFERRED TO THE 58T2. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
5782 | 2004 | 9 | 7 | 0.39583 |  | 338 | 113 | 20 | 84F6 | 8/4.8kV | Manodale | R. Blair reports all his work is now complete transformer are now replaced. | Nepean | Scheduled Outage | Construction
6230 | 2005 | 2 | 23 | 0.64306 |  | 129 | 54 | 25 | Marchwood | 27.6/16kV | Marchwood F2 | Replaced switch #128 at Second Line and Panandrick | Kanata | Defective Equipment | Equipment Deterioration Due to Age
12319 | 2008 | 4 | 22 | 0.16181 |  | 107 | 5 | 3 | Marchwood | 27.6/16kV | Marchwood F3 | Customers on Thomas A. Dolan reported loss of power, crew found a tree branch in contact with primary. Branch was removed and S67 at Thomas A. Dolan and Marchhurst was refused and customers restored. | Kanata | Tree Contacts | Tree Limb Fallen
10539 | 2007 | 6 | 5 | 0.61389 |  | 356 | 6 | 1 | Marchwood | 27.6/16kV | Marchwood F3 | Transformer #2610 located at 2415 Marchurst Rd isolated due to tree interference & also changed lightning arrestor | Kanata | Tree Contacts | Inadequate Trimming
11229 | 2007 | 9 | 2 | 0.32639 |  | 355 | 6 | 1 | Marchwood | 27.6/16kV | Marchwood F3 | Transformer #X07770 located at 1245 Murphy Side Rd isolated due to bird interference | Kanata | Foreign Interference | Bird
11427 | 2007 | 10 | 1 | 0.47917 |  | 10 | 0 | 3 | Marchwood | 27.6/16kV | Marchwood F3 | Transformer #52 located at 5 Panandrick View isolated for Bell Canada | Kanata | Scheduled Outage | Construction
11708 | 2007 | 11 | 15 | 0.34306 |  | 61 | 13 | 13 | Marchwood | 27.6/16kV | Marchwood F3 | Transformer #21 located at 1 Lillian Way isolated due to squirrel contact (crew refused 2 fuses) 106W found blown also. | Kanata | Foreign Interference | Animal
17994 | 2011 | 4 | 27 | 0.27986 |  | 112 | 38 | 25 | Marchwood | 27.6/16kV | MDWF3 | 24/7 crew found S88 opened @ 1902 Mc Cord due to broken cut out at transformer X39846 @ 1908 Mc Cord. 25 customer were affected. Marchwood MWDF3. | Kanata | Defective Equipment
8789 | 2006 | 7 | 19 | 0.97778 |  | 47 | 4 | 5 | Marchwood | 27.6/16kV | MDWF3 | An animal made contact to transformer 1696 on Riddle causeing the fuse to blow. | Kanata | Foreign Interference | Animal
5809 | 2004 | 9 | 15 | 0.38889 |  | 123 | 1264 | 900 | Merivale MS | 8/4.8kV | Merivale MS | Squirrel contact on 71B1-B2 bus tie switch @ Merivale MS. See Int # 5808 | Nepean | Foreign Interference | Animal
4625 | 2003 | 12 | 18 | 0.58333 |  | 95 | 2 | 1 | 8F3 | 27.6/16kV | Moulton | R. Barnett reports repairs and to secondary side of transformer.All power now restored. | Gloucester | Adverse Weather | Wind
10973 | 2007 | 7 | 31 | 0.69167 |  | 44 | 4 | 5 | Moulton | 27.6/16kV | Moulton F3 | Transformer #GL00831 located at 1359 Maxime isolated due to bird contact | Gloucester | Foreign Interference | Bird
16323 | 2010 | 6 | 23 | 0.59931 |  | 68 | 11860 | 16096 | Albion, Woodroffe, |  | Multiple | 15 Station Transformers tripped under gas surge protection due to earthquake which measured 5.7 on the Richter scale. UAT1, UWT1, UWT2, UWT4, SOT2, SOT3, SHT2, UXT1, UXT2, ADT1, ADT3, UJT1, UNT1, BRDT2, UBT2. | Ottawa | Adverse Environment | Vibration
3784 | 2003 | 7 | 25 | 0.875 |  | 83 | 1 | 1 | Munster | 8/4.8kV | mun f2 | 8286 Franktown Rd customer reports no power on farm. 24/7 dispatched and found fuse on TX8286 opened. Line patrolled no fault found on line. Transformer fuse replaced and closed all load restored. ( customer has been away for a week) | Kanata | Unknown/Other | No Apparent Cause
4442 | 2003 | 11 | 13 | 0.72986 |  | 492 | 323 | 300 | Munster | 8/4.8kV | MUNSTER | Crew replaced a defective transformer and one broken insulator (separate locations). | Goulburn | Adverse Weather | Wind
5046 | 2004 | 4 | 23 | 0.39236 |  | 125 | 4 | 2 | Munster | 12/7.2kV | Munster F2 | Outage at 7856 & 7861 Franktown RD. for maintenance. | Kanata | Scheduled Outage | Preventive Maintenance
10786 | 2007 | 7 | 3 | 0.74306 |  | 165 | 3 | 1 | Munster | 8/4.8kV | Munster F2 | Transformer located at 7195 Mansfield isolated due to squirrel contact | Goulburn | Foreign Interference | Animal
5670 | 2004 | 8 | 10 | 0.79167 |  | 1225 | 20 | 1 | Munster | 27.6/16kV | Munster F2 | Transformer at 7438 Jocktrail had to be replaced due to lightening strike. | Goulburn | Adverse Weather
4142 | 2003 | 9 | 24 | 0.11597 |  | 3 | 15 | 308 | Munster F2 |  | Munster F2 | Rabbits to Munster F2 opened due to the fact we could not parralell. | Goulburn | Foreign Interference | Vehicle
4624 | 2003 | 12 | 18 | 0.60278 |  | 75 | 16 | 25 | Munster | 8/4.8kV | Munster F2 | Tree found in O/H line on Jock Trail Rd. SW232 red fuse opened & SW1131 fuse refused and closed restoring load to 25 customers. G. Morrice to remove tree. | Kanata | Tree Contacts | Tree Fallen
3592 | 2003 | 6 | 22 | 0.37708 |  | 127 | 698 | 330 | Munster | 8/4.8kV | Munster F3 | Mark Brown reports Customer Dropped tree that fell on the line tree was cleared and power was restored. | Goulburn | Tree Contacts | Tree Fallen
4141 | 2003 | 9 | 24 | 0.10833 |  | 3 | 18 | 361 | Munster DS | 8/4.8kV | Munster F3 | Munster F3 was opened because we could not parralell with the rabbits to restore normal load to station. | Goulburn | Foreign Interference | Vehicle
4533 | 2003 | 11 | 28 | 0.92014 |  | 340 | 6 | 1 | Munster | 8/4.8kV | Munster F3 | Transformer #8282, at 8282 Bleek's Side Road in Munster Hamlet, was isolated to allow for the replacement of a customer owned meter base. ID#4533 | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
13388 | 2008 | 10 | 18 | 0.66042 |  | 83 | 270 | 480 | Munster | 8/4.8kV | Munster Station | Schedualled outage for Munster DS. System had to drop load at Munster in order to use the rabbits to pick up Munster load via Beckwith. | Goulburn | Scheduled Outage | Preventive Maintenance
14457 | 2009 | 6 | 4 | 0.50694 |  | 264 | 31 | 12 | Munster | 8/4.8kV | MUNSTERF2 | Red phase overhead circuit between S27677R and S28194R isolated to allow crews to transfer plant to new poles. | Ottawa | Scheduled Outage | Repair
14153 | 2009 | 4 | 8 | 0.50694 |  | 5 | 1 | 16 | Beaconhill MS | 8/4.8kV | MUSF1-BH5 | Isolated transformer TE0433 at 2147 Loyola Ave to disconnect defective U/G service | Gloucester | Scheduled Outage | Emergency Services Request
11118 | 2007 | 8 | 21 | 0.41667 |  | 80 | 3 | 2 | Marchwood | 27.6/16kV | MWD F3 | Transformer #000289 located at 2405 Second Line isolated for the Meter Dept | Kanata | Scheduled Outage | Construction
9221 | 2006 | 9 | 14 | 0.66181 |  | 133 | 7 | 3 | Marchwood | 27.6/16kV | MWD F3 | Vehicle hit a pole, broke the guy wire & caused the switch to open. 3 transformers were opened. All on Thomas A. Dolan Parkway | Kanata | Foreign Interference | Vehicle
4445 | 2003 | 11 | 13 | 0.77569 |  | 914 | 3783 | 1000 | Marchwood | 27.6/16kV | MWD F3 | A tree came down across the line near switch #1013 at the corner of March Road and Riddell Road. The tree was removed and power restored. ID#4445 | Kanata | Tree Contacts | Tree Fallen
4454 | 2003 | 11 | 14 | 0.13681 |  | 293 | 1547 | 1000 | Marchwood | 27.6/16kV | MWD F3 | The Marchwood F3 breaker opened up due to a tree falling down on the line. The tree fell clear of the line which allowed the breaker to be closed again but the line remained low to the ground and had to be repaired. ID#4454 Line was isolated at switch 1030 to preform other work | Kanata | Adverse Weather | Wind
3555 | 2003 | 6 | 12 | 0.48958 |  | 67 | 3015 | 2700 | Marchwood | 27.6/16kV | MWD F4 | While stringing a wire sleeve got caught in the travelling ground and caused it to break. This breakage caused the wire to swing into the live MWD F4 circuit causing it to trip to lockout as it was on hold-off already. Repairs were made and full power restored. | Kanata | Human Element | Incorrect Use of Equipment
3795 | 2003 | 7 | 28 | 0.40278 |  | 150 | 20 | 8 | Marchwood | 27.6/16kV | MWD F4 | Transformer 1713 was isolated to allow for the replacement of elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
20196 | 2012 | 3 | 22 | 0.22014 |  | 460 | 46 | 6 | Marchwood | 27.6/16kV | MWDF1 | Transformer 2177 @ 255 Kanata was replace due to oil leaking. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
20263 | 2012 | 3 | 31 | 0.7625 |  | 794 | 79 | 6 | Marchwood | 27.6/16kV | MWDF1 | Transformer TP9372 @ 255 Kanata was isolated to allow crew to perform soil remediation due to leaking transformer. | Kanata | Scheduled Outage | Repair
11895 | 2008 | 1 | 3 | 0.65972 |  | 200 | 833 | 250 | Marchwood | 27.6/16kV | MWDF2 | The blue phase lead to dip switch 63 on Maple Grove failed at connection to O/H line. Power restored from alternate source. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19901 | 2012 | 1 | 26 | 0.40833 |  | 100 | 30 | 18 | Marchwood | 27.6/16kV | MWDF2 | Transformer 209R at 400 Fenerty Crt changed out due to oil leak | Kanata | Scheduled Outage | Preventive Maintenance
19903 | 2012 | 1 | 26 | 0.40833 |  | 100 | 30 | 18 | Marchwood | 27.6/16kV | MWDF2 | Leaking transformer 209R at 400 Fenerty changed out. | Kanata | Scheduled Outage | Preventive Maintenance
17616 | 2011 | 2 | 19 | 0.1 |  | 18 | 230 | 768 | Marchwood | 27.6/16kV | MWDF2 | SCADA indicates MWDF2 tripped. High Winds. System closed MWDF2 breaker and held. | Kanata | Adverse Weather
17822 | 2011 | 4 | 2 | 0.35556 |  | 417 | 21 | 3 | Marchwood | 27.6/16kV | MWDF2 | Transformers 2373,2374 & 3038 @ 800 Palladium Dr were isolated for secondary maintenance | Kanata | Scheduled Outage | Preventive Maintenance
6380 | 2005 | 4 | 7 | 0.010417 |  | 705 | 3668 | 1000 | Marchwood | 27.6/16kV | MWDF2 | Burnt elbow found at TE914-2. Connection repaired and returned to service. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
12366 | 2008 | 4 | 30 | 0.46181 |  | 88 | 12 | 8 | Marchwood | 27.6/16kV | MWDF2 | transformer 775 at 51 Rowe Cres was isolated to replace a leaking transformer | Kanata | Scheduled Outage | Repair
20425 | 2012 | 4 | 30 | 0.91458 |  | 63 | 1 | 1 | Marchwood | 27.6/16kV | MWDF2 | Racoon caused X06653 @ 50 Lord Byng to open. | Kanata | Foreign Interference | Animal
14276 | 2009 | 5 | 1 | 0.21597 |  | 199 | 3 | 1 | Marchwood | 27.6/16kV | MWDF2 | Transformer #X06653 located at 50 Lord Byng isolated due to animal contact | Kanata | Foreign Interference | Animal
20439 | 2012 | 5 | 2 | 0.43681 |  | 226 | 467 | 124 | Marchwood | 27.6/16kV | MWDF2 | Elbow insert replacement on the white phase between S241 and S307-5 Waldon and Kimmins Streets | Kanata | Scheduled Outage | Preventive Maintenance
20450 | 2012 | 5 | 3 | 0.38333 |  | 188 | 445 | 142 | Marchwood | 27.6/16kV | MWDF2 | Customers in the Morgan Grant are were interupted to allow crew to replace elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
20451 | 2012 | 5 | 3 | 0.40764 |  | 80 | 1 | 1 | Marchwood | 27.6/16kV | MWDF2 | Replaced blown fuse feeding ttransformer X06653 at 50 Lord Byng (Crow) | Kanata | Foreign Interference | Bird
14329 | 2009 | 5 | 9 | 0.3625 |  | 40 | 1 | 1 | Marchwood | 27.6/16kV | MWDF2 | Transformer #X6653 located at 50 Lord Byng Way isolated due to animal contact | Kanata | Foreign Interference | Animal
18122 | 2011 | 5 | 9 | 0.59167 |  | 18 | 3 | 9 | Marchwood | 27.6/16kV | MWDF2 | Transformer 145R @ 40 Liston was isolated to allow crew to replace leaky transformer. 9 Customers were affected. Marchwood MWDF2 | Kanata | Scheduled Outage
18135 | 2011 | 5 | 12 | 0.36875 |  | 600 | 90 | 9 | Marchwood | 27.6/16kV | MWDF2 | Transformer at 40 Listen was isolated to allow crews to perform soil remediation after changing the leaking transformer. | Kanata | Scheduled Outage | Repair
20558 | 2012 | 5 | 23 | 0.38194 |  | 235 | 446 | 114 | Marchwood | 27.6/16kV | MWDF2 | At 09:10 12 transformers in Kanata Lakes were isolated to allow crews to replace elbows and inserts. 114 customers were affected for 235 minutes. Marchwood (MWDF2) ID#20558 | Kanata | Scheduled Outage
18317 | 2011 | 6 | 7 | 0.0027778 |  | 350 | 471 | 171 | Marchwood | 27.6/16kV | MWDF2 | A cable fault the R phase bet transformer 166 @ 45 Sundback and S38 @ 116 MCCLINTOCK WAY. While fault finding the crew broke two inserts at two seperate transformer 166 and 168. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
16365 | 2010 | 6 | 29 | 0.67639 |  | 116 | 244 | 127 | Marchwood | 27.6/16kV | MWDF2 | Switch 387 Red and Blue phase at 70 Aird Place Open due to animal contact in primary line. | Kanata | Foreign Interference | Bird
18575 | 2011 | 7 | 3 | 0.27083 |  | 44 | 2338 | 3188 | Marchwood |  | MWDF2 | At 6:30am MWDF2 breaker open. Crews patrolled circuit and did not find anything. All load was restored at 7:14. Marchwood MWDF2 ID# 18575 | Kanata | Unknown/Other
18592 | 2011 | 7 | 5 | 0.52361 |  | 84 | 3779 | 4570 | Marchwood | 27.6/16kV | MWDF2 | MWDF2 CB Auto-reclosed and locked out. Circuit was sectionalized and cable fault found between SC2260 and SC4565. Part of 624F1 circuit affected due to abnormal conditions. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
10887 | 2007 | 7 | 16 | 0.75833 |  | 305 | 1007 | 560 | MARCHWOOD | 27.6/16kV | MWDF2 | A vehicle ht a pole at 1625 Maple Grove causing the MWDF2 to trip, and the A9M3 auto reclose auto. The A9M3 was closed 1 minute later by Hydro One. | Kanata | Foreign Interference | Vehicle
18678 | 2011 | 7 | 17 | 0.80556 |  | 4 | 238 | 3572 | Marchwood | 27.6/16kV | MWDF2 | The Marchwood MWDF2 circuit opened during lightning storm. Closed via SCADA and no apparent cause was found. Marchwood MWDF2 | Kanata | Adverse Weather | Wind
18740 | 2011 | 7 | 17 | 0.80556 |  | 4 | 238 | 3572 | Marchwood | 27.6/16kV | MWDF2 | Marchwood MWDF2 Tripped due to adverse weather and was closed back in successfully. | Kanata | Adverse Weather
16504 | 2010 | 7 | 20 | 0.6 |  | 100 | 1081 | 856 | Marchwood | 27.6/16kV | MWDF2 | During switching S104-2 WHITE phase faulted, power restored and U/G section from S28 to S104 hipoted , crews reported WHITE Phase fault. Suspect at the termination of S104-2 | Kanata | Defective Equipment
8826 | 2006 | 7 | 25 | 0.36181 |  | 29 | 0 | 1 | Marchwood | 27.6/16kV | MWDF2 | Transformer #150 located at 1055 Klondike isolated due to animal interfence (racoon) | Kanata | Foreign Interference | Animal
11006 | 2007 | 8 | 7 | 0.47778 |  | 101 | 52 | 60 | Marchwood |  | MWDF2 | White phase fuse @ switch # 639 was found opened. White phase cable fault was located between TX259 & TX581. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5667 | 2004 | 8 | 11 | 0.49722 |  | 188 | 6 | 2 | Marchwood | 27.6/16kV | MWDF2 | Transformer at 351 Sandhill fuse opened due to squirrel contact. | Kanata | Foreign Interference | Animal
16765 | 2010 | 8 | 18 | 0.375 |  | 87 | 6 | 4 | Marchwood | 27.6/16kV | MWDF2 | Transformer 1278 @ 130 Goodman was isolated to allow the crews to change the elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
16770 | 2010 | 8 | 18 | 0.50972 |  | 102 | 7 | 4 | Marchwood | 27.6/16kV | MWDF2 | Transformer 1703 @ 1808 Rocklane was isolated to allow the crew to replace the elbows and insert changes. | Kanata | Scheduled Outage | Preventive Maintenance
18959 | 2011 | 8 | 18 | 0.55764 |  | 2 | 119 | 3573 | MARCHWOOD | 27.6/16kV | MWDF2 | MWDF2 TRIPPED & LOCKED OUT DUE TO HOLDOFF CLOSED AND HOLDING | Kanata | Lightning
14999 | 2009 | 8 | 24 | 0.35417 |  | 5 | 1 | 7 | Marchwood | 27.6/16kV | MWDF2 | Isolated transformer 1002 at 56 Hansen ave to disconnect service | Kanata | Scheduled Outage | Emergency Services Request
19057 | 2011 | 8 | 30 | 0.58681 |  | 35 | 1833 | 3880 | Marchwood | 27.6/16kV | MWDF2 | MWDF2 breaker opened due to faulted cable section and circuit was tried once while fault locating. Marchwood ID#19057 | Kanata | Defective Equipment
11222 | 2007 | 8 | 31 | 0.063889 |  | 93 | 1875 | 1500 | MARCHWOOD | 27.6/16kV | MWDF2 | SWITCH 387 & CABLE DIP FAILED AT 70 AIRD ST (KANATA WAVE POOL). CAUSING MWDF2 BREAKER TO OPEN. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
15071 | 2009 | 9 | 8 | 0.91458 |  | 72 | 192 | 160 | Marchwood | 27.6/16kV | MWDF2 | TP3681 at 233 Helm Circle defective and needed replacing. Outage to 22 transformer due to permit in effect and back-up cable unavailable. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
16905 | 2010 | 9 | 8 | 0.4875 |  | 158 | 18 | 7 | Marchwood | 27.6/16kV | MWDF2 | Transformer 206W at 122 McCurdy was isolated for crew to changeout leaking padmount transformer | Kanata | Scheduled Outage | Emergency Services Request
19198 | 2011 | 9 | 18 | 0.75139 |  | 148 | 2 | 1 | Marchwood | 27.6/16kV | MWDF2 | Blown transformer fuse at X06972. 24/7 crew refused and held. 1350 Old Carp Rd. | Kanata | Unknown/Other
19433 | 2011 | 10 | 21 | 0.052778 |  | 67 | 4239 | 3796 | MARCHWOOD DS | 27.6/16kV | MWDF2 | MWDF2 CB opened with B & W phase trip flags. No cause found. Daylight patrol required | Kanata | Unknown/Other | No Apparent Cause
19438 | 2011 | 10 | 21 | 0.79167 |  | 11 | 696 | 3796 | MARCHWOOD | 27.6/16kV | MWDF2 | MWDF2 Breaker opened. Circuit to be patrolled in daylight. | Kanata | Unknown/Other
17158 | 2010 | 10 | 22 | 0.027083 |  | 96 | 2359 | 3598 | Marchwood | 27.6/16kV | MWDF2 | MWDF2 CB A/R & tripped out (51-BLUE), SC2260-L4 opened & SC2260-L2 closed restoring 2831 customers. S307-1 & S307-2 FCI's flagged, S307-1 opened & MWDF2 CB closed, all power restored. Suspected cable fault. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19571 | 2011 | 11 | 14 | 0.41319 |  | 103 | 9 | 5 | Marchwood | 27.6/16kV | MWDF2 | Transformer 198R at 178 McCurdy was isolated for replacement | Kanata | Scheduled Outage | Preventive Maintenance
15440 | 2009 | 11 | 30 | 0.40833 |  | 107 | 11 | 6 | Marchwood | 27.6/16kV | MWDF2 | TP5010 at 139 Sonesta isolated to allow crew to install new collar under transformer. | Kanata | Scheduled Outage | Construction
15443 | 2009 | 11 | 30 | 0.39583 |  | 120 | 18 | 9 | MARCHWOOD DS | 27.6/16kV | MWDF2 | TP1050 at 139 Sonesta isolated to raise transformer | Goulburn | Scheduled Outage | Repair
15448 | 2009 | 12 | 1 | 0.47986 |  | 366 | 11 | 5 | Marchwood | 27.6/16kV | MWDF2 | crew cut incorrect cable causing S69-3 fuse to open interrupting 5 transformers on Palladium dr, on the MWDF2 circuit. 4 transformers were restored by refusing and closing at S69-3 and crew isolated the 627 transformer and repaired the cable, then energized. | Kanata | Human Element | Incorrect Construction
15452 | 2009 | 12 | 1 | 0.47986 |  | 366 | 6 | 1 | Marchwood | 27.6/16kV | MWDF2 | Hydro Ottawa crew inadvertently cut live undergound cable. | Kanata | Human Element | Incorrect Use of Equipment
19730 | 2011 | 12 | 16 | 0.59722 |  | 3 | 0 | 1 | Marchwood TS | 27.6/16kV | MWDF2 | Jim Lewandowski reports that his crew opened the wrong transformer isolating switch while performing PC17A 17-65819 accidentally dumping off TP4264 and causing a 3 minute outage to 1 customer. | Kanata | Human Element | Incorrect Use of Equipment
19736 | 2011 | 12 | 17 | 0.39722 |  | 363 | 12 | 2 | Marchwood | 27.6/16kV | MWDF2 | crew isolated transformers 626 and 1487 at 100 & 300 Maple grove to replace switch gear. | Kanata | Scheduled Outage | Construction
10886 | 2007 | 7 | 16 | 0.71319 |  | 1 | 74 | 4415 | SOUTH MARCH | 44kV | MWDF2 & A9M3 | A9M3 Tripped, reclosed tripped and was manually closed at 16:08 hours due to a truck hit a pole, at 1625 Maple Grove, causing the MWDF2 to trip and lock out. | Kanata | Foreign Interference | Vehicle
15629 | 2010 | 1 | 8 | 0.39931 |  | 110 | 22 | 12 | Marchwood | 27.6/16kV | MWDF3 | TP5114 isolated from Hydro Sources to change out transformer with damaged neutral bar | Kanata | Scheduled Outage
11927 | 2008 | 1 | 12 | 0.31667 |  | 59 | 12 | 12 | Marchwood | 27.6/16kV | MWDF3 | At 7:36am a squirell made contact to a transformer at 1060 Kerwin. 24-7 refused transformer, 12 customers affected for 59 min. ID#11927. | Kanata | Foreign Interference | Animal
11928 | 2008 | 1 | 12 | 0.31667 |  | 59 | 4 | 4 | Marchwood | 27.6/16kV | MWDF3 | Fuse on transformer #383 at 34 Ohara found blown, due to animal contact. | Kanata | Foreign Interference | Animal
13860 | 2009 | 1 | 13 | 0.59028 |  | 60 | 3 | 3 | MARCHWOOD | 27.6/16kV | MWDF3 | Transformer X40152 at 11 Wild Acre Lane isolated to allow for service upgrade | Goulburn | Scheduled Outage | Construction
7834 | 2006 | 1 | 21 | 0.41667 |  | 120 | 196 | 98 | Marchwood | 27.6/16kV | MWDF3 | A branch on a primary run off causing two fuses to blow. | Kanata | Adverse Weather | Snow
7836 | 2006 | 1 | 21 | 0.47986 |  | 59 | 1 | 1 | Marchwood | 27.6/16kV | MWDF3 | Transformer #1363 located at 11 Lillian Way isolated due to branch on primary private take off | Kanata | Tree Contacts | Tree Limb Fallen
7841 | 2006 | 1 | 21 | 0.74097 |  | 223 | 149 | 40 | Marchwood | 12/7.2kV | MWDF3 | Crew found step down transformer 502R blown. Crew patrolled circuit, nothing found. Refused and closed. | Kanata | Unknown/Other
11965 | 2008 | 1 | 21 | 0.55556 |  | 57 | 10 | 10 | Marchwood | 27.6/16kV | MWDF3 | Transformer TP3578 at 464 Celtic Ridge in Kanata isolated and replaced due to damage caused when it was hit by a vehicle. | Kanata | Foreign Interference | Vehicle
15675 | 2010 | 1 | 21 | 0.80972 |  | 180 | 18 | 22 | Marchwood | 27.6/16kV | MWDF3 | 1356R at 1403 Sheruby Way isolated from Hydro Sources to repair damaged transformer. | Kanata | Scheduled Outage | Repair
9964 | 2007 | 1 | 24 | 0.69792 |  | 50 | 1 | 1 | Marchwood | 8/4.8kV | MWDF3 | Replaced broken fuse in switch to transformer at 1620 Sixth Line Rd YMCA Outdoor Centre | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
19892 | 2012 | 1 | 25 | 0.39306 |  | 71 | 39 | 33 | MWDF3 | 27.6/16kV | MWDF3 | Broken Switch #109B located at 1 Grierson Lane repaired, re-fused and closed. All load restored. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
9970 | 2007 | 1 | 28 | 0.20833 |  | 66 | 855 | 1000 | Marchwood | 12/7.2kV | MWDF3 | Car hit a pole at 1770 Second Line Rd breaking an insulator and causing center phase to eventually fail and trip the feeder. Damaged conductor was secured, the feeder re-energized and RX2007 red and white phases were then reset to restore all customers | Kanata | Foreign Interference | Vehicle
6184 | 2005 | 2 | 7 | 0.98056 |  | 43 | 1 | 2 | Marchwood | 27.6/16kV | MWDF3 | TX#1909 @ 856March RD was opened to allow crews to repair downed neutral conductor. @ Customers effected in power outage. Neutral conductor down on school bus at this location. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6190 | 2005 | 2 | 8 | 0.47569 |  | 5 | 83 | 1000 | Marchwood | 27.6/16kV | MWDF3 | MWDF3 tripped open (recloseing off). Breaker closed from SCADA after 5 min. On line patrol switch 329 at 1299 Murphy Side Rd. was found defective and replaced. Station reclose showed white phase ground 2.1 Km from station. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
10008 | 2007 | 2 | 10 | 0.35625 |  | 170 | 57 | 20 | Marchwood | 27.6/16kV | MWDF3 | White phase cut out feeding Bathurst 238W blew refused | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
10009 | 2007 | 2 | 10 | 0.49375 |  | 90 | 30 | 20 | Marchwood | 27.6/16kV | MWDF3 | Squirrell in the switch to transformer 397W blew the fuse and damaged the switch | Kanata | Foreign Interference | Animal
13986 | 2009 | 2 | 16 | 0.57361 |  | 76 | 1 | 1 | Marchwood MS | 27.6/16kV | MWDF3 | Replaced broken switch feeding transformer X40081 at 5 Mowbray St | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6213 | 2005 | 2 | 17 | 0.44861 |  | 64 | 3 | 3 | Marchwood | 27.6/16kV | MWDF3 | Animal contact at 34 O'hara caused outage | Kanata | Foreign Interference | Animal
10056 | 2007 | 2 | 23 | 0.5 |  | 100 | 100 | 60 | Marchwood | 27.6/16kV | MWDF3 | Planned outage on 16 transformers in the area of Roycroft , Goodman area. To allow crews to change overhead switches. Balance feed loading on MWDF3 circuit. | Kanata | Scheduled Outage | Repair
10064 | 2007 | 2 | 26 | 0.43056 |  | 130 | 4 | 2 | Marchwood | 8/4.8kV | MWDF3 | Isolated transformer 2176 at 871 Berry Side Rd to transfer Hydro plant | Kanata | Scheduled Outage | Preventive Maintenance
4833 | 2004 | 2 | 28 | 0.37222 |  | 40 | 16 | 26 | Marchwood | 27.6/16kV | MWDF3 | Squirrel contacted at transformer #391 caused fuse to blow, Also s111 fuse to blow. Mike refused S111 at road restoring overhead line on Rochon & O' Hara. Transformer 391 checks ok. Fuse replaced and closed. | Kanata | Foreign Interference | Animal
7979 | 2006 | 3 | 2 | 0.39722 |  | 78 | 17 | 13 | Marchwood | 27.6/16kV | MWDF3 | Isolation of o/h line to replace defective transformer switches. 13 customers affected. | Kanata | Scheduled Outage
10086 | 2007 | 3 | 2 | 0.47083 |  | 72 | 2 | 2 | Marchwood | 8/4.8kV | MWDF3 | Switch to transformer 0091 at 18 Grierson Lane was found broken | Kanata | Adverse Weather | Wind
15767 | 2010 | 3 | 3 | 0.37778 |  | 286 | 48 | 10 | Kanata | 27.6/16kV | MWDF3 | Transformer 2031W at 7 Melmsdale replaced, required isolation to accomplish | Kanata | Scheduled Outage | Repair
6263 | 2005 | 3 | 11 | 0.40972 |  | 85 | 1317 | 1000 | Marchwood | 27.6/16kV | MWDF3 | While restoring MWDT1 transformer 624 B1-B2 tie switch failed to open propperly. Causing the tie switch to flash over. The MWD-CS1 & MWD-CS2 circuit switcher opened to clear the fault on C7M cirucit. Also Re-outage # 6261 & 6262, & 6263. | Kanata | Defective Equipment
3266 | 2003 | 3 | 17 | 0.55903 |  | 271 | 678 | 150 | Marchwood | 27.6/16kV | MWDF3 | Insulator failed causing pole fire on crossarm on Beachvale & Second Line Rd. Reclosure 909 White phase opened causing outage to approx 150 customers. | Kanata | Adverse Environment | Fire
20175 | 2012 | 3 | 18 | 0.65972 |  | 385 | 63 | 14 | Marchwood | 27.6/16kV | MWDF3 | customer reported outage, patrol found blown elblow and damaged insert at TP7889-H1A & defective insert at TP7096-H1B. ONCALL crew called in to replace both transformers. 8 customers affected. | Kanata | Defective Equipment
10173 | 2007 | 3 | 25 | 0.33611 |  | 97 | 18 | 11 | Marchwood | 27.6/16kV | MWDF3 | Lead to switch 242w burned off, switch isolated & lead repaired. Sixth line rd @ Thomas Dolan Pkwy. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14127 | 2009 | 3 | 31 | 0.4625 |  | 93 | 39 | 25 | Marchwood | 27.6/16kV | MWDF3 | Racoon caused a flash across the switch feeding transformer X40173 @ 1918 McCord, (which did not blow) but this caused S88 up the road to open. | Kanata | Foreign Interference | Animal
12223 | 2008 | 4 | 2 | 0.20625 |  | 439 | 734 | 102 | Marchwood | 27.6/16kV | MWDF3 | Recloser RX2009 open and switch 65B blown. Crew had difficulty locating defective cut out that cause outage. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8119 | 2006 | 4 | 8 | 0.56319 |  | 285 | 20 | 8 | MARCHWOOD | 27.6/16kV | MWDF3 | Crew checked out calls from the Thomas Fuller area. Found XMER 324 @ 5 Thomas Fuller had a bad insert. | Kanata | Unknown/Other
20301 | 2012 | 4 | 8 | 0.31667 |  | 62 | 26 | 25 | Marchwood | 27.6/16kV | MWDF3 | line fuse blown (88W) due to squirrel contact on McCord Dr. | Kanata | Foreign Interference | Animal
8125 | 2006 | 4 | 10 | 0.34028 |  | 38 | 158 | 250 | MARCHWOOD | 27.6/16kV | MWDF3 | FOUND SQURRIL AT XMER 388 ON O'HARA CAUSED FUSE TO BLOW AT XMER AND RX2009 TO OPEN. RX2009 WAS UNDER HOLD OFF. | Kanata | Foreign Interference | Animal
8164 | 2006 | 4 | 19 | 0.53819 |  | 75 | 2 | 2 | Marchwood | 27.6/16kV | MWDF3 | Isolated transformer 2358 at 1746 Marchurst Rd to relocate service to new pole | Kanata | Scheduled Outage | Preventive Maintenance
12311 | 2008 | 4 | 20 | 0.39375 |  | 78 | 3 | 2 | Marchwood | 27.6/16kV | MWDF3 | S129 at 840 Berry Side Rd was found blown, radial line was patrolled with no apparent cause found. S129 nomenclature was changed to S15431 and refused successfully. | Kanata | Unknown/Other
17971 | 2011 | 4 | 20 | 0.14583 |  | 170 | 332 | 117 | Marchwood | 27.6/16kV | MWDF3 | Tree Contact caused phase to come down on Grierson lane off of second line.RX2042 blue phase opened. Crews isolated radial and made temporary repairs. | Kanata | Tree Contacts
14253 | 2009 | 4 | 27 | 0.72986 |  | 136 | 3254 | 2095 | Marchwood | 27.6/16kV | MWDF3 | At the fire dept request the MWDF3 circuit had to be dump because of tree on the primary which was on fire which caused a grass fire. A portion of MWDF3 to S18419 was picked up. A section of the tree burned off & the remainder of the tree was removed from the vicinity of o/h lines by forestry crew before restoring Kanata north. | Kanata | Tree Contacts
10342 | 2007 | 4 | 30 | 0.16667 |  | 27 | 0 | 1 | Marchwood | 27.6/16kV | MWDF3 | At 2145 FIFTH LINE a raccoon caused damage on secondary of transformer # 1545. Repairs completed all power restored to normal. | Kanata | Foreign Interference | Animal
3394 | 2003 | 5 | 2 | 0.16319 |  | 80 | 33 | 25 | Marchwood | 27.6/16kV | MWDF3 | 24/7 reports overhead line checks ok. Reset line reclosure 696B. | Kanata | Unknown/Other | No Apparent Cause
5087 | 2004 | 5 | 2 | 0.20833 |  | 115 | 1917 | 1000 | Marchwood | 27.6/16kV | MWDF3 | The Marchwood F3 trip, while trying to find the problem they sectionlize at S312-1 and closed the F3 back in but trip again. Shawn was near the staion and seen sparks at switch 92 centre phase. Shawn determined it was a bad termination on the centre phase at that switch. The switch was opened and load restore from switch 256. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3434 | 2003 | 5 | 5 | 0.16319 |  | 80 | 33 | 25 | Marchwood | 27.6/16kV | MWDF3 | No power calls investigated. Overhead line recloser found open. No apparent damage found. Load restored OK. | Kanata | Unknown/Other | No Apparent Cause
8253 | 2006 | 5 | 8 | 0.65903 |  | 18 | 2 | 8 | Marchwood | 27.6/16kV | MWDF3 | Repaired broken switch 243 @ Marchbrook Circle at old Carp Rd. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
16073 | 2010 | 5 | 10 | 0.80833 |  | 176 | 1540 | 650 | Marchwood | 27.6/16kV | MWDF3 | Cable fault on cable section S251-4 to S394-1. Shirleys Brook Kanata. Red and white fuse were blown at S292 and HI pot of cable section showed cable bad on all 3 phases. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
12428 | 2008 | 5 | 11 | 0.87778 |  | 230 | 107 | 28 | Marchwood | 12/7.2kV | MWDF3 | Broken cutout on Load side of 792 B. Crew replaced switch and restored power. | Kanata | Defective Equipment
5144 | 2004 | 5 | 13 | 0.88125 |  | 227 | 4 | 1 | Marchwood | 27.6/16kV | MWDF3 | Customer reports transformer was hit by lightning. B. Seaman dispatched to 1670 Thomas Dolan Parkway. Crew reports transformer needs to be changed. | Kanata | Lightning | Direct Strike
20533 | 2012 | 5 | 17 | 0.375 |  | 181 | 513 | 170 | Marchwood | 27.6/16kV | MWDF3 | 18 transformer were isolated in the Bannock Cres and Morgan's Grant Way area to allow the crews to change the elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
5171 | 2004 | 5 | 18 | 0.48264 |  | 76 | 253 | 200 | Marchwood | 27.6/16kV | MWDF3 | Circuit patrolled and found switch to single transformer open. Nothing else found so switch 65 blue phase closed. | Kanata | Adverse Weather | Lightning
10442 | 2007 | 5 | 22 | 0.92431 |  | 129 | 2 | 1 | MARCHWOOD | 27.6/16kV | MWDF3 | Racoon cause the fuse to blow at transformer 150 @ 1055 Klondike. | Kanata | Foreign Interference | Animal
20572 | 2012 | 5 | 25 | 0.45556 |  | 76 | 317 | 250 | Marchwood | 27.6/16kV | MWDF3 | MWDF3 blue phase burnt clear at S92 Riser at station. Customers transferred to 624F1. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
12481 | 2008 | 5 | 26 | 0.96319 |  | 372 | 43 | 7 | Marchwood | 27.6/16kV | MWDF3 | 24/7 reported fuse 113W blown on March Valley and tree on primary overhead. On Call called to make repairs to pole top pin and to remove the tree. 113W and transformer cutout re-fused and the 7 affected customers restored. | Kanata | Adverse Weather | Wind
8367 | 2006 | 5 | 29 | 0.28472 |  | 95 | 119 | 100 | Marchwood | 27.6/16kV | MWDF3 | 144R on Old Carp Rd at March Rd. Overhead Patroled nothing found new fuse installed at 144. | Kanata | Unknown/Other | No Apparent Cause
12519 | 2008 | 5 | 31 | 0.82083 |  | 107 | 2 | 1 | Marchwood | 27.6/16kV | MWDF3 | Transformer 1476 at 1221 March rd. opened due to extreme lightning activity. (two other xfmrs on same o/h opened.) | Kanata | Adverse Weather
12520 | 2008 | 5 | 31 | 0.82083 |  | 128 | 2 | 1 | Marchwood | 27.6/16kV | MWDF3 | Transformer x37552 at 1210 March rd. opened due to extreme lightning activity. (two other xfmrs on same o/h opened.) | Kanata | Adverse Weather
12521 | 2008 | 5 | 31 | 0.82083 |  | 352 | 6 | 1 | Marchwood | 27.6/16kV | MWDF3 | Extreme lightning activity caused Transformer 7183 at 1194 March rd. to open. On call crew replaced the transformer. | Kanata | Adverse Weather | Lightning
12522 | 2008 | 5 | 31 | 0.82083 |  | 239 | 4 | 10 | Marchwood | 8/4.8kV | MWDF3 | crew replaced Switch 612 on 8kV o/h fed from rabbit WX2015. Fuses S14696 at the rabbit also opened. Crew refused both and restored power to customers on Riddel | Kanata | Adverse Weather
12524 | 2008 | 5 | 31 | 0.82083 |  | 613 | 235 | 23 | Marchwood | 8/4.8kV | MWDF3 | Red phase fuse at Switch S14696 was blown but remained closed refused and closed restoring power to red phase customers. When the crew restored the W phase all the calls were group together missing the R phase customers | Kanata | Adverse Weather | Lightning
14433 | 2009 | 5 | 31 | 0.37292 |  | 326 | 5 | 2 | Marchwood | 27.6/16kV | MWDF3 | 2990T1 and 2990T2 were isolated to allow contractors to perform maintenance on customer owned transformer and secondary equipment. | Kanata | Scheduled Outage | Preventive Maintenance
10567 | 2007 | 6 | 8 | 0.77569 |  | 420 | 7 | 1 | Marchwood | 27.6/16kV | MWDF3 | Tree contact caused Transformer feeding 2625 Marchhurst to open. | Kanata | Tree Contacts | Inadequate Trimming
12621 | 2008 | 6 | 13 | 0.32431 |  | 103 | 2 | 1 | Marchwood | 27.6/16kV | MWDF3 | Transformer #753 located at 1506 Second Line Rd isolated due to squirrel contact, had to change arrestor also. | Kanata | Foreign Interference | Animal
18428 | 2011 | 6 | 16 | 0.84653 |  | 73 | 3393 | 2789 | Marchwood |  | MWDF3 | Bird found at S20405, Terry Fox south west of Innovation, overhead clear. | Kanata | Foreign Interference | Bird
5334 | 2004 | 6 | 19 | 0.47917 |  | 222 | 4 | 1 | Marchwood | 27.6/16kV | MWDF3 | Transformer 5582 opened due to high winds causing tree contact. | Kanata | Adverse Weather | Wind
16311 | 2010 | 6 | 21 | 0.51944 |  | 92 | 6 | 4 | MARCHWOOD | 27.6/16kV | MWDF3 | Transformer at 1580 Monaghan was isoalted for elbow and insert replacment. | Kanata | Scheduled Outage
12711 | 2008 | 6 | 22 | 0.34097 |  | 52 | 1767 | 2039 | Marchwood | 27.6/16kV | MWDF3 | MWDF3 tripped, FCI 2000 indicator at Klondike & Second Line flagged. Station checked, no calls from police, circuit closed & held. Patrol found flashed arrestors at 1310 Second Line near Thomas Fuller. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18499 | 2011 | 6 | 24 | 0.85 |  | 78 | 3627 | 2790 | Marchwood | 27.6/16kV | MWDF3 | Lightning strick at S20405 caused lightning arrester to fail S11028 opened to allow MWDF3 breaker to be closed. | Kanata | Adverse Weather | Lightning
20852 | 2012 | 6 | 24 | 0.33333 |  | 237 | 4 | 1 | Marchwood | 27.6/16kV | MWDF3 | Switch 841 at 2015 Marchurts opened due to defective fuse holder - cuatomer owned line. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6794 | 2005 | 6 | 25 | 0.61597 |  | 8 | 133 | 1000 | Marchwood | 27.6/16kV | MWDF3 | MwdF3 opened because of storm, breaker was blocked, closed via scada. | Kanata | Adverse Weather | Lightning
6800 | 2005 | 6 | 25 | 0.64167 |  | 206 | 2245 | 1000 | Marchwood | 12/7.2kV | MWDF3 | MWDF3 reopened storm still in the area, Corey Ovington patrol circuit and found primary down on Riddle Rd, Line crews called in, Isolated the problem for repairs and closed in curcuit. | Kanata | Adverse Weather | Lightning
12739 | 2008 | 6 | 26 | 0.64653 |  | 10 | 167 | 1000 | Marchwood | 27.6/16kV | MWDF3 | MWDF3 customer reports lightning strike in area. MWDF3 circuit closed via scada all power restored. | Kanata | Adverse Weather | Lightning
12759 | 2008 | 6 | 26 | 0.94028 |  | 926 | 15 | 1 | Marchwood | 27.6/16kV | MWDF3 | Tree fell on customer owned line at 1835 Dunrobin. Crews put 10C protection into effect for contractor repair. Customer restored at 2pm. | Kanata | Tree Contacts | Tree Fallen
6814 | 2005 | 6 | 27 | 0.090278 |  | 410 | 68 | 10 | Marchwood | 27.6/16kV | MWDF3 | Found blown transformer fuse at 898B. Switching performed to isolate transformer 898 on Newcastle at Pepper | Kanata | Defective Equipment
16358 | 2010 | 6 | 29 | 0.41111 |  | 144 | 7 | 3 | Marchwood | 27.6/16kV | MWDF3 | Transformer 736 at 1810 Lahey was isolated to allow crew to replace inserts and elbows. 3 Customers on Lahey were affected. | Kanata | Scheduled Outage | Repair
16361 | 2010 | 6 | 29 | 0.375 |  | 185 | 9 | 3 | Marchwood | 27.6/16kV | MWDF3 | Isolated transformer 736 at 1810 Lahey Crt to replace primary elbows and inserts | Kanata | Scheduled Outage | Preventive Maintenance
16362 | 2010 | 6 | 29 | 0.51181 |  | 60 | 2 | 2 | Marchwood | 27.6/16kV | MWDF3 | Transformer 2483 at 1810 Lahey was isolated to allow crew to replace inserts and elbows. 2 Customers on Lahey were affected. | Kanata | Scheduled Outage | Repair
16369 | 2010 | 6 | 30 | 0.38889 |  | 90 | 4 | 3 | MARCHWOOD | 27.6/16kV | MWDF3 | Transformer 317 at 2 Sharne Lane was isolated to allow crew to ugrade elbows and inserts. Three customers on Sharne Lane were affected | Nepean | Scheduled Outage | Preventive Maintenance
16371 | 2010 | 6 | 30 | 0.36458 |  | 125 | 6 | 3 | Marchwood | 27.6/16kV | MWDF3 | Isolated transformer 317 at 1 Sharne Lane to replace primary elbows and inserts | Kanata | Scheduled Outage | Preventive Maintenance
16372 | 2010 | 6 | 30 | 0.5 |  | 72 | 5 | 4 | Marchwood | 27.6/16kV | MWDF3 | transformer 320 at 14 Rolston was isolated to allow crews to change elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
16375 | 2010 | 6 | 30 | 0.59306 |  | 101 | 2 | 1 | Marchwood | 27.6/16kV | MWDF3 | Transformer #753 located at 1506 Second Line Rd opened up due to tree contact | Kanata | Tree Contacts | Inadequate Trimming
6862 | 2005 | 7 | 1 | 0.75 |  | 2630 | 44 | 1 | Marchwood | 27.6/16kV | MWDF3 | Refused transformer at 530 Berry Side Rd. | Kanata | Adverse Weather | Lightning
14655 | 2009 | 7 | 2 | 0.98611 |  | 638 | 116 | 14 | Marchwood | 27.6/16kV | MWDF3 | Marchwood F3 circuit auto-reclosed due to defective transformer T401R @ 124 Beach Hieghts rd. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
3673 | 2003 | 7 | 5 | 0.25694 |  | 650 | 1741 | 485 | Marchwood | 27.6/16kV | MWDF3 | Crew reports found transformer at 2145 5TH line RD opened. Also found fuse blown at 65B on March Rd. 65B fuse refused and closed. Reclosure at 910B opened causing large outage on March RD. 65B re-fused R/C 910B closed . 792 B fuse closed restoring load to approx 250 customers. Transformer at 2145 5TH line rd. defective.Transformer has now been replaced | Kanata | Adverse Weather | Lightning
3676 | 2003 | 7 | 5 | 0.63611 |  | 14 | 105 | 450 | Marchwood | 27.6/16kV | MWDF3 | B. Seaman reports transformer at 2145 5TH line RD. Checks ok, and energized transformer with 8amp cutout fuse. Fuse blow and also tripped reclosure 910. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6869 | 2005 | 7 | 5 | 0.094444 |  | 68 | 2 | 2 | Marchwood | 27.6/16kV | MWDF3 | O/H transformer on Campbell Reid re-fused. Suspect lightning. | Kanata | Unknown/Other | No Apparent Cause
16403 | 2010 | 7 | 6 | 0.39792 |  | 102 | 8 | 5 | South March | 27.6/16kV | MWDF3 | Transformer #77 @ 17 Panandrick View Dr was isolated to upgrade elbow & inserts. | Kanata | Scheduled Outage | Preventive Maintenance
12797 | 2008 | 7 | 7 | 0.4375 |  | 20 | 1 | 2 | Marchwood | 27.6/16kV | MWDF3 | Isolated transformer X07300 at 1681 Dunrobin Rd to replace connections on the secondary | Goulburn | Scheduled Outage | Emergency Services Request
14683 | 2009 | 7 | 8 | 0.39236 |  | 321 | 107 | 20 | Marchwood | 27.6/16kV | mwdF3 | Te400 & TE401 were isolated to allow crews to install a new transformer TP3048 and cables. In the Beach Hieghts of Kanata | Kanata | Scheduled Outage | Construction
5472 | 2004 | 7 | 9 | 0.39583 |  | 100 | 7 | 4 | Marchwood | 27.6/16kV | MWDF3 | Te1705 was isolated to allow crews to remove sand from the base. 4 Customers affected in planned power outage. | Kanata | Scheduled Outage | Preventive Maintenance
10840 | 2007 | 7 | 10 | 0.42708 |  | 7 | 1 | 10 | Marchwood | 27.6/16kV | MWDF3 | An outage was required to restore an out of phase condition on the MWDF3 blue phase section to normal after new transformer were energized. | Kanata | Scheduled Outage | Repair
10854 | 2007 | 7 | 11 | 0.92708 |  | 121 | 2 | 1 | Marchwood | 27.6/16kV | MWDF3 | Overhead transformer at 2160 Sixth Line re-fused by Oncall. No obvious cause, suspect it may have been out since earlier lightning strike. | Kanata | Unknown/Other
3723 | 2003 | 7 | 12 | 0.30694 |  | 227 | 189 | 50 | Marchwood | 27.6/16kV | MWDF3 | Squirrel made contact with circuit causing in line fuse and a transformer fuse to fail. Switch was refused and closed to restore. | Kanata | Foreign Interference | Animal
6921 | 2005 | 7 | 13 | 0.88056 |  | 4 | 70 | 1050 | Marchwood | 27.6/16kV | MWDF3 | Severe Lightning storm caused MWDF3 to trip (recloser always blocked). | Kanata | Adverse Weather | Lightning
14760 | 2009 | 7 | 15 | 0.3875 |  | 320 | 75 | 14 | Marchwood | 27.6/16kV | MWDF3 | transformers 400 and 401 on beach heights in kanata were isolated to install new transformer TP3048. | Kanata | Scheduled Outage | Construction
12846 | 2008 | 7 | 16 | 0.32847 |  | 13 | 444 | 2050 | Marchwood | 27.6/16kV | MWDF3 | MWDF3 was restored manually from SCADA after no reports of problems were reported. Patrol did not reveal any obvious cause for trip. | Kanata | Unknown/Other
5511 | 2004 | 7 | 17 | 0.45556 |  | 39 | 1 | 1 | MARCHWOOD | 27.6/16kV | MWDF3 | Customer reports power outage at TX1554 @ 1913 MCCORD DR KANATA. Steve reports cut out blown caused by crow. Fuse replaced customer power restored as of 11:35. | Kanata | Foreign Interference | Bird
5516 | 2004 | 7 | 18 | 0.53472 |  | 150 | 2 | 1 | Marchwood | 27.6/16kV | MWDF3 | S. Muldon reports bird caused fuse on transformer to blow at 325 Didsbury RD North. | Kanata | Foreign Interference | Bird
12873 | 2008 | 7 | 18 | 0.16458 |  | 2 | 68 | 2050 | Marchwood | 27.6/16kV | MWDF3 | Thunderstorm in the area. | Kanata | Adverse Weather | Lightning
12890 | 2008 | 7 | 18 | 0.63056 |  | 105 | 1542 | 2051 | Marchwood | 27.6/16kV | MWDF3 | Lightning hit Sw. 131 at March & Huntmar causing cct to trip. Switch cleared from line, most customers restored. Sw. 131 R replaced restoring remaining customers. | Kanata | Lightning | Direct Strike
12893 | 2008 | 7 | 18 | 0.16458 |  | 1088 | 18 | 1 | Marchwood | 27.6/16kV | MWDF3 | Transformer #X40092 located at 2306 Marchurst isolated due to lighting storm early this morning. Customer clms he called three times. The only call in OMS for this address is at 19:03. | Kanata | Adverse Weather | Lightning
12894 | 2008 | 7 | 18 | 0.82986 |  | 189 | 3 | 1 | Marchwood | 27.6/16kV | MWDF3 | Transformer #X40088 located at 2290 Marchurst isolated due to lightning | Kanata | Adverse Weather | Lightning
8794 | 2006 | 7 | 21 | 0.48819 |  | 152 | 3 | 1 | Marchwood | 27.6/16kV | MWDF3 | Contractor dug up customer owned secondary at 2660 Marchurst Road. SX26449 opened to isolate transformer, while repairs were made. | Kanata | Foreign Interference | Dig-in
7025 | 2005 | 7 | 26 | 0.28889 |  | 90 | 28 | 19 |  | 27.6/16kV | MWDF3 | Animal Contact to transformer at 2140 Second Line caused S1739R to blow. Refused restoring load. | Kanata | Foreign Interference | Bird
12991 | 2008 | 8 | 2 | 0.40764 |  | 48 | 1 | 1 | Marchwood | 27.6/16kV | MWDF3 | Transformer #X07431 located at 971 Kerwin Rd isolated due to bird contact | Kanata | Foreign Interference | Bird
13003 | 2008 | 8 | 6 | 0.95417 |  | 186 | 29 | 17 | Marchwood | 27.6/16kV | MWDF3 | Tree contact at X39582 at 7 Lillian caused transformer cutout to open and S106W to blow open. Crews re-fused and closed switch, cleared tree limbs from O/H xfmr and closed cutout. All load restored. | Kanata | Tree Contacts | Inadequate Trimming
8937 | 2006 | 8 | 10 | 0.37222 |  | 94 | 3 | 2 | Marchwood | 8/4.8kV | MWDF3 | Transformer #746 located at 2215 Sixth Line Rd isolated due to squirrel contact | Kanata | Foreign Interference | Animal
16737 | 2010 | 8 | 15 | 0.52917 |  | 121 | 56 | 28 | Marchwood | 27.6/16kV | MWDF3 | Defective switch, possible lightning strike caused outage to 28 customers on Second line Rd in Kanata. | Kanata | Defective Equipment
11079 | 2007 | 8 | 16 | 0.58056 |  | 14 | 233 | 1000 | Marchwood | 27.6/16kV | MWDF3 | Motor Vehicle Accident (MVA) at Klondike and March, all Hydro is clear, circuit closed by SCADA load restored on all 3 phases | Kanata | Adverse Weather
13106 | 2008 | 8 | 18 | 0.66806 |  | 2 | 33 | 1000 | Marchwood | 27.6/16kV | MWDF3 | MWDF3 circuit opened due to storm activity. Recloser is always out of service, closed by scada. | Kanata | Adverse Weather | Lightning
16776 | 2010 | 8 | 19 | 0.38264 |  | 70 | 7 | 6 | Marchwood DS | 27.6/16kV | MWDF3 | Transformer 2557 at 6 Roycroft Way was isolated to allow crews to change defective elbows & inserts. | Kanata | Scheduled Outage | Repair
16778 | 2010 | 8 | 19 | 0.5 |  | 65 | 6 | 6 | Marchwood MS | 27.6/16kV | MWDF3 | Transformer 2561 at 50 Roycroft was isolated to allow crews to change defective elbows & inserts. | Kanata | Scheduled Outage
11137 | 2007 | 8 | 23 | 0.53472 |  | 110 | 4 | 2 | Marchwood | 27.6/16kV | MWDF3 | O/H transformer at 2741 Dunrobin Rd isolated to transfer secondary to new pole. | Kanata | Scheduled Outage | Construction
9041 | 2006 | 8 | 24 | 0.37153 |  | 105 | 7 | 4 | Marchwood | 27.6/16kV | MWDF3 | Transformer #945 located at 360 Berry Side Rd isolated due to squirrel contact | Kanata | Foreign Interference | Animal
16813 | 2010 | 8 | 25 | 0.81806 |  | 175 | 9 | 3 | Marchwood | 27.6/16kV | MWDF3 | Transformer #X07130 located at 1620 Marchurst opened up due to a broken cut out | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5743 | 2004 | 8 | 29 | 0.62361 |  | 62 | 103 | 100 | Marchwood | 27.6/16kV | MWDF3 | Heavy rain and Lightning in effect. S65Blue phase blown. Patrolled circuit refused and closed | Kanata | Adverse Weather
5748 | 2004 | 8 | 29 | 0.84514 |  | 467 | 121 | 40 | Marchwood | 27.6/16kV | MWDF3 | Heavy rain and Lightning in area. Tx 175 at 2205 Sixth Line faulted, 2 phases of sw 502 on Riddel opened. Switches refused and closed, tx 175 had to be replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
15032 | 2009 | 8 | 30 | 0.7125 |  | 319 | 90 | 17 | Marchwood | 27.6/16kV | MWDF3 | Broken insulatore at 178 John Aselford caused pole fire at location. Crews isolated from fusr at John Aselford and Marchurst to end of line to make temporary repairs and restore customers until permanent repairs can be made. 21 customers affected wer hydro one transfer customers. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
11227 | 2007 | 9 | 2 | 0.32639 |  | 4 | 67 | 1000 | Marchwood | 27.6/16kV | MWDF3 | MWDF3 breaker auto trip, breaker closed from SCADA. All load restored. Customer on murphy side rd. was out due to turkey vulture causing his transformer fuse to open. Fuse blew but cutout did not open. | Kanata | Unknown/Other
11231 | 2007 | 9 | 2 | 0.6875 |  | 100 | 47 | 28 | Marchwood | 27.6/16kV | MWDF3 | Crew replaced defective cutout at Switch S407. Huntmar and Weldale. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
19089 | 2011 | 9 | 4 | 0.14306 |  | 534 | 9 | 1 | Marchwood | 27.6/16kV | MWDF3 | Transformer X07680 at 1670 Thomas A. Dolan Parkway was hit by lightning. Customer also had electrician inspect further problems inside. Marchwood (MWDF3) ID# 19089 | Kanata | Lightning | Direct Strike
5780 | 2004 | 9 | 6 | 0.39236 |  | 45 | 750 | 1000 | Marchwood | 27.6/16kV | MWDF3 | MWDF3 tripped due to defective 909 recloser red phase. Approx 10 gallons of oil spray. Ministry called. All 3 phases isolated and bypass closed. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
11270 | 2007 | 9 | 7 | 0.72778 |  | 164 | 246 | 90 | Marchwood | 27.6/16kV | MWDF3 | Tree contact on 5th Line Rd caused fuse 65B to blow at March Rd & Kerwin. Tree was removed & 65B cutout replaced by Oncall. | Kanata | Tree Contacts | Tree Fallen
9148 | 2006 | 9 | 8 | 0.62153 |  | 110 | 37 | 20 | Marchwood | 27.6/16kV | MWDF3 | Single phase O/H section on Berry Side Rd from S239B to end of line isolated to clear last span and broken pole that was knocked over by a backhoe. | Kanata | Foreign Interference | Vehicle
16935 | 2010 | 9 | 13 | 0.875 |  | 35 | 19 | 32 | Marchwood | 27.6/16kV | MWDF3 | switch 109B was opened to remove tree from overhead at 11 Grierson. | Kanata | Tree Contacts | Tree Limb Fallen
16936 | 2010 | 9 | 13 | 0.94097 |  | 95 | 51 | 32 | Marchwood | 27.6/16kV | MWDF3 | switch 109B was opened to replace broken insulator on Grierson. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
13232 | 2008 | 9 | 15 | 0.11806 |  | 130 | 2383 | 1100 | Marchwood | 27.6/16kV | MWDF3 | Tree removed from overhead at March Rd west of second line, breaker closed from SCADA. | Kanata | Tree Contacts | Tree Fallen
13233 | 2008 | 9 | 15 | 0.097917 |  | 2 | 37 | 1100 | MWDF3 | 27.6/16kV | MWDF3 | Feeder tripped, breaker has no reclosing so breaker closed from SCADA and holding. Cause later determined to be tree on wires. | Kanata | Tree Contacts | Tree Fallen
4081 | 2003 | 9 | 17 | 0.36597 |  | 18 | 1 | 3 | Marchwood | 27.6/16kV | MWDF3 | Transformer isolated for pole testing with Bell Canada. | Kanata | Scheduled Outage
9238 | 2006 | 9 | 17 | 0.4375 |  | 259 | 8 | 3 | Marchwood | 27.6/16kV | MWDF3 | O/H transformer 3341at 1620 Thomas Dolan faulted and had to be replaced. In line switch at Marchhurst & Thomas Dolan also opened, interupting 2 other customers. | Kanata | Defective Equipment
9241 | 2006 | 9 | 18 | 0.49653 |  | 80 | 3 | 2 | Marchwood | 27.6/16kV | MWDF3 | At 11:55 transformer at 3 Campbell Rd was isolated in order to repalce secondary service | Kanata | Scheduled Outage | Preventive Maintenance
19201 | 2011 | 9 | 19 | 0.39861 |  | 249 | 187 | 45 | Marchwood | 27.6/16kV | MWDF3 | Crew isolated transformers 616R, 617R, 618R, 619R, 620R, 621R, 622R, 1356R, 1357R, 1358R, 1359R, 1360R, 1361R and 1362R at Weldale and Sherruby to for elbow and insert replacement. | Kanata | Scheduled Outage | Preventive Maintenance
19212 | 2011 | 9 | 20 | 0.39583 |  | 215 | 179 | 50 | Marchwood | 27.6/16kV | MWDF3 | 12 transformers were isolated to allow crew to replace elbows and inserts. Streets affected are: Marchvale, landel, maleylane, weatharly. | Kanata | Scheduled Outage | Preventive Maintenance
19228 | 2011 | 9 | 21 | 0.38333 |  | 263 | 158 | 36 | Marchwood | 27.6/16kV | MWDF3 | 11 transfomrer on Maley Ln and Landel Dr were isolated to allow crews to replace elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
19236 | 2011 | 9 | 22 | 0.39861 |  | 124 | 60 | 29 | Marchwood | 27.6/16kV | MWDF3 | Red phase transformers between S19411R and 468R were isolated to allow crews to replace elbows and inserts and to change nomenclature. | Kanata | Scheduled Outage | Preventive Maintenance
4170 | 2003 | 9 | 27 | 0.85417 |  | 595 | 40 | 4 | Marchwood | 27.6/16kV | MWDF3 | Customer reported big flash, loud bang suggested lightnig struck transformer due to storm in area. Crew reported no lightning strike just defective transformer. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4171 | 2003 | 9 | 28 | 0.14236 |  | 57 | 190 | 200 | Marchwood | 27.6/16kV | MWDF3 | On removing elbow from the parking stand, it flashed and caused recloser 909 red phase to open. Recloser was blocked for switching. Switching was completed and recloser closed. | Kanata | Defective Equipment
9347 | 2006 | 9 | 29 | 0.94444 |  | 35 | 2 | 4 | Marchwood | 27.6/16kV | MWDF3 | 871 Berry Side Rd transformer 2176 isolated due to arching. Switch stirup and LLC replaced. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
7416 | 2005 | 10 | 1 | 0.75417 |  | 123 | 410 | 200 | Marchwood | 27.6/16kV | MwdF3 | Temp repairs made to broken hydro pole. Police report # 279249. | Kanata | Foreign Interference | Vehicle
11420 | 2007 | 10 | 1 | 0.43056 |  | 9 | 0 | 10 | MARCHWOOD | 27.6/16kV | MWDF3 | Tranformer #X07959 at 2265 Sixth Line Rd isolated to allow for switch replacement | Goulburn | Scheduled Outage | Preventive Maintenance
19313 | 2011 | 10 | 3 | 0.37917 |  | 230 | 548 | 143 | Marchwood | 27.6/16kV | MWDF3 | Blue phase transformers on Halton Terr. between 1531 and S312 were isolated to allow crews to replace elbows, inserts and nomenclature. | Kanata | Scheduled Outage | Preventive Maintenance
19317 | 2011 | 10 | 4 | 0.37708 |  | 128 | 218 | 102 | Marchwood | 27.6/16kV | MWDF3 | red phase transformers on Halton Terr. between 1531 and S312 were isolated to allow crews to replace elbows, inserts and nomenclature. | Kanata | Scheduled Outage | Preventive Maintenance
19321 | 2011 | 10 | 5 | 0.37569 |  | 159 | 188 | 71 | Marchwood | 27.6/16kV | MWDF3 | White phase transformers on Halton Terr. between 1531 and S312 were isolated to allow crews to replace elbows, inserts and nomenclature. | Kanata | Scheduled Outage | Preventive Maintenance
19324 | 2011 | 10 | 5 | 0.51181 |  | 36 | 7 | 12 | Marchwood | 27.6/16kV | MWDF3 | Transformer TP8316B at 62 Beacon Way was isolated to allow crew to repair elbow/insert. | Kanata | Scheduled Outage | Repair
17084 | 2010 | 10 | 8 | 0.34653 |  | 61 | 1 | 1 | Marchwood | 27.6/16kV | MWDF3 | Bird contact cause transformer X26631 to open. | Kanata | Foreign Interference | Bird
17087 | 2010 | 10 | 8 | 0.56667 |  | 32 | 1 | 2 | Kanata MTS | 27.6/16kV | MWDF3 | Transformer X40166 at 26 Grierson Lane was isolated to replace defective cut out. | Kanata | Scheduled Outage
17100 | 2010 | 10 | 12 | 0.56597 |  | 60 | 2 | 2 | Marchwood | 27.6/16kV | MWDF3 | Transformer #X40174 located at 36 Grierson Lane opened by crew to replace broken cut out | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
9439 | 2006 | 10 | 16 | 0.53611 |  | 5 | 83 | 1000 | Marchwood | 27.6/16kV | MWDF3 | MWDF3 tripped open. Breaker dose not have reclosing. Switch 630 at Huntmar and Marchwood. Ground fault instanateous, breaker would not close from SCADA. Cloaed at station by Steve Arsenault. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5847 | 2004 | 10 | 20 | 0.67986 |  | 62 | 31 | 30 | Marchwood | 27.6/16kV | MWDF3 | the crew found a dead Squirrel at the the xfmr to 36 O'Hara Drive | Kanata | Foreign Interference | Animal
9507 | 2006 | 10 | 24 | 0.49236 |  | 126 | 8 | 4 | Marchwood | 27.6/16kV | MWDF3 | Transformer #495 located at 1870 Sixth Line Rd isolated due to a bird, had to re-fuse switch #495 | Kanata | Foreign Interference | Bird
13517 | 2008 | 10 | 29 | 0.16597 |  | 183 | 3050 | 1000 | MARCHWOOD | 27.6/16kV | MWDF3 | A.Cooney reports defective insulators replaced & should be clear to restore MWDF3 load, MWDF3 breaker closed & holding. | Kanata | Adverse Weather
9564 | 2006 | 10 | 30 | 0.65556 |  | 116 | 2 | 1 | Marchwood | 8/4.8kV | MWDF3 | Fuse was found blown at Sw363 at 1620 SIXTH LINE RD due to tree on the line | Kanata | Tree Contacts | Tree Fallen
15366 | 2009 | 11 | 8 | 0.54792 |  | 191 | 45 | 15 | Marchwood | 27.6/16kV | MWDF3 | A blown elbow at transformer 1358 @ 1411 Sherruby. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4480 | 2003 | 11 | 18 | 0.58333 |  | 7 | 0 | 2 | Marchwood | 27.6/16kV | MWDF3 | P. Barr reports cut out on transformer #554 opened to replace same. Outage affected 2 customers at 33 John Aselford cres. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4521 | 2003 | 11 | 26 | 0.47569 |  | 10 | 0 | 2 | Marchwood | 27.6/16kV | MWDF3 | Transformer #395 at 17 Bathurst interrupted to remove meter for the metering department. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
13685 | 2008 | 11 | 29 | 0.56944 |  | 87 | 84 | 58 | Marchwood | 27.6/16kV | MWDF3 | crew refused and closed 144R on old carp rd. o/h was patrolled and nothing was found. | Kanata | Unknown/Other | No Apparent Cause
9773 | 2006 | 12 | 1 | 0.65208 |  | 800 | 2577 | 1100 | Marchwood | 27.6/16kV | MWDF3 | A tree took down the O/H and broke a pole in behind Beacon Way. | Kanata | Adverse Weather | Ice Storm
5966 | 2004 | 12 | 2 | 0.39236 |  | 5 | 0 | 2 | Marchwood | 27.6/16kV | MWDF3 | Replace a bad meter at transformer 000395 @17 & 22 Bathurst | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
5979 | 2004 | 12 | 5 | 0.33333 |  | 60 | 3 | 3 | Marchwood | 27.6/16kV | MWDF3 | To allow crews to hook up new services. RX11 opened on MWDF3 circuit affecting power to 3 customers. Customers were notified by B. Baker before transformer was isolated. | Kanata | Scheduled Outage | Construction
19689 | 2011 | 12 | 6 | 0.38681 |  | 134 | 67 | 30 | Marchwood | 27.6/16kV | MWDF3 | 11 Transformers were isolated on Sharne Lane, Rolston Way & Thomas Fuller Dr to allow crews to replace elbows & inserts. | Kanata | Scheduled Outage | Preventive Maintenance
7703 | 2005 | 12 | 8 | 0.78681 |  | 398 | 27 | 4 | Marchwood | 27.6/16kV | MWDF3 | Transformer T1703 defective and replaced by on call crew. Rocklane Dr Kanata | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
13777 | 2008 | 12 | 18 | 0.42361 |  | 45 | 10 | 14 | Marchwood | 12/7.2kV | MWDF3 | Switch S13987 (old 792B) was opened to transfer customers on 6th line rd back to Hydro -Ottawa normal supply from H - 1 supply. | Kanata | Scheduled Outage | Repair
9873 | 2006 | 12 | 21 | 0.25833 |  | 308 | 51 | 10 | Marchwood | 27.6/16kV | MWDF3 | Replaced defective padmount transformer 2612 at 42 Newcastle Ave | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
13810 | 2008 | 12 | 28 | 0.48333 |  | 269 | 117 | 26 | Marchwood | 27.6/16kV | MWDF3 | Fallen tree limb at switch 89 on Rocklane to blow, and potentially causing the MWDCST2 outage. Crew removed tree limb and refused switch. | Kanata | Tree Contacts | Tree Limb Fallen
9907 | 2007 | 1 | 9 | 0.27431 |  | 132 | 22 | 10 | Marchwood | 27.6/16kV | MWDF4 | White phase fuse found opened at S25743 W on Rabbits on Riddell St. Circuit was patrolled on fault found. At 14:40 A. Cooney reports customer U/G cable is defective @ switch 2422. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
19823 | 2012 | 1 | 12 | 0.93958 |  | 114 | 4 | 2 | marchwood | 27.6/16kV | MWDF4 | TX 652 at 84 Heinz isolated to allow contractor to service customer mains. 2 customers affected for 114 minutes. | Kanata | Scheduled Outage | Repair
3113 | 2003 | 1 | 13 | 0.52431 |  | 50 | 6 | 7 | Marchwood | 27.6/16kV | MWDF4 | Planned Outage. Customers Notified. | Kanata | Scheduled Outage | Preventive Maintenance
6151 | 2005 | 1 | 24 | 0.4 |  | 219 | 73 | 20 | Marchwood | 27.6/16kV | MWDF4 | TP3320 and TP3321 isolate to allow new cable to be pulled in for addation of 2 new transformers. | Kanata | Scheduled Outage | Construction
9968 | 2007 | 1 | 25 | 0.59028 |  | 50 | 1 | 1 | Marchwood | 27.6/16kV | MWDF4 | Al Cooney isolated TRF. 1475 @ 2635 5th line to change TRF defective switch | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4785 | 2004 | 2 | 13 | 0.54514 |  | 74 | 9 | 7 | Marchwood | 27.6/16kV | MWDF4 | Transformer 3318 in Shirly Brook was isolated for the removal a defective transformer. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3205 | 2003 | 2 | 19 | 0.90556 |  | 296 | 10 | 2 | Marchwood | 27.6/16kV | MWDF4 | Fuse cutout & holder on private line found broken. On-call crew dispatched. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6262 | 2005 | 3 | 11 | 0.40972 |  | 40 | 733 | 1100 | Marchwood | 27.6/16kV | MWDF4 | While restoring MWDT1 transformer 624 B1-B2 tie switch failed to open propperly. Causing the tie switch to flash over. The MWD-CS1 & MWD-CS2 circuit switcher opened to clear the fault on C7M cirucit. Also Re-outage # 6261 & 6262, & 6263. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
14061 | 2009 | 3 | 16 | 0.86389 |  | 249 | 1541 | 525 | Marchwood | 27.6/16kV | MWDF4 | After an auto reclose S424-2 gas interuptor gang operated to open all 3 phases of MWDF4 section to clear a suspected white phase cable fault between transformers 4015 and 4016. The high pot tester showed the section good the first test and proved bad when energized causing the S424-2 to open again. | Kanata | Adverse Environment | Fire
14065 | 2009 | 3 | 16 | 0.60417 |  | 70 | 10 | 9 | Marchwood | 27.6/16kV | MWDF4 | Transformer 4016W @ 22 Whernside in Kanata was isolated to replace elbows and check transformer. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3351 | 2003 | 4 | 16 | 0.40556 |  | 48 | 80 | 100 | Marchwood | 27.6/16kV | MWDF4 | Radially fed transformers isolated to replace transformer 2599. | Kanata | Scheduled Outage | Construction
6446 | 2005 | 4 | 23 | 0.16458 |  | 63 | 42 | 40 | Marchwood | 27.6/16kV | MWDF4 | Customer at 1910 Dunrobin Rd reported hearing a loud bang as power went out. Crew could find nothing wrong. | Kanata | Unknown/Other | No Apparent Cause
6447 | 2005 | 4 | 23 | 0.33958 |  | 496 | 17 | 2 | Marchwood | 27.6/16kV | MWDF4 | Customer owned line at 1869 Dunrobin RD caused TX3196 fuse to blow due to Inadequate Trimming. Customer line isolated to allow tree trimming. | Kanata | Tree Contacts | Inadequate Trimming
3515 | 2003 | 6 | 3 | 0.42847 |  | 20 | 1 | 3 | Marchwood | 27.6/16kV | MWDF4 | Tranformer at 19 Mowbury isolated to make repairs. | Kanata | Defective Equipment
6796 | 2005 | 6 | 25 | 0.62014 |  | 3 | 55 | 1100 | Marchwood | 27.6/16kV | MWDF4 | MWDF4 curcuit opened because off the storm, closed via scada and holding. | Kanata | Adverse Weather
8726 | 2006 | 7 | 14 | 0.375 |  | 95 | 3 | 2 | Marchwood | 27.6/16kV | MWDF4 | Bill Seaman opened transformer 948 @ 16 Kanata Rockeries to do some work on the transformer | Kanata | Scheduled Outage | Preventive Maintenance
5550 | 2004 | 7 | 22 | 0.38542 |  | 162 | 81 | 30 | Marchwood | 27.6/16kV | MWDF4 | 3 transformers on Kinross Private out to move cable to new underground duct. | Kanata | Scheduled Outage | Construction
10952 | 2007 | 7 | 25 | 0.9375 |  | 60 | 7 | 7 | Marchwood | 27.6/16kV | MWDF4 | Transformer fuse found blown. Fuse replasced all power restored to normal. | Goulburn | Foreign Interference | Animal
3827 | 2003 | 8 | 1 | 0.38958 |  | 41 | 5 | 8 | Marchwood | 27.6/16kV | MWDF4 | G. Morrice reports elbow at TX1714 is now replaced. All customers were notified of outage on Monday. | Kanata | Scheduled Outage | Repair
3872 | 2003 | 8 | 7 | 0.55486 |  | 86 | 11 | 8 | Marchwood | 27.6/16kV | MWDF4 | Transformer isolated to replace it due to leaks. | Kanata | Defective Equipment | Imminent Equipment Failure Detected
7085 | 2005 | 8 | 8 | 0.37639 |  | 85 | 23 | 16 | Marchwood | 27.6/16kV | MWDF4 | TE4022 was isolated to allow crews to pull in new cable & make terminaties. Outage effected 16 customers in the Wernside Ter area. | Kanata | Scheduled Outage | Construction
4062 | 2003 | 9 | 13 | 0.29722 |  | 67 | 8 | 7 | Marchwood | 27.6/16kV | MWDF4 | D. Howett reports blown transformer fuse at this location. Outage effected 7 customers. Fuse on transformer blow due to squirrel contact. Fuse replaced all power restored @ 08:15 am. | Kanata | Foreign Interference | Animal
11356 | 2007 | 9 | 21 | 0.42986 |  | 134 | 9 | 4 | Marchwood | 27.6/16kV | MWDF4 | Transformer 3365 at 76 Walliston changed due to damaged neutral bus. | Kanata | Scheduled Outage | Repair
4143 | 2003 | 9 | 24 | 0.052083 |  | 214 | 86 | 24 | Marchwood | 27.6/16kV | MWDF4 | SW152B blown due to a defective cable between T1592-1B TO T171 cable was found by fault indicators cable isolated and power restored. | Kanata | Defective Equipment | Equipment Deterioration Due to Age
19262 | 2011 | 9 | 26 | 0.38403 |  | 205 | 957 | 280 | Marchwood | 27.6/16kV | MWDF4 | Transformers between TP2283 and S233 were isolated at Klondike and Famborough to allow crews to replace elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
19275 | 2011 | 9 | 27 | 0.39792 |  | 306 | 1122 | 220 | Marchwood | 27.6/16kV | MWDF4 | At 9:33 crews isolated 22 transformers on the Marchwood F4 for elbow and insert replacement. 220 customers affected for 306 mins. Marchwood MWDF4. | Kanata | Scheduled Outage
19293 | 2011 | 9 | 30 | 0.37708 |  | 216 | 713 | 198 | Marchwood | 27.6/16kV | MWDF4 | White phase transformers at Klondike and Flamborough between S233 and 1531 were isolated to allow crews to replace elbows and inserts and install new nomenclature. | Kanata | Scheduled Outage | Preventive Maintenance
19331 | 2011 | 10 | 6 | 0.375 |  | 195 | 757 | 233 | Marchwood |  | MWDF4 | At 9:00am crews isolated 19 Blue phase transformers for insert and elbow replacement. 233 customers affected for 195 mins. Marchwood MWDF4 ID# 19331 | Kanata | Scheduled Outage
9774 | 2006 | 12 | 1 | 0.75903 |  | 829 | 2578 | 1000 | Marchwood | 27.6/16kV | MWDF4 | A tree took down the O/H and broke a pole in behind Beacon Way. Heavy rain and wind | Kanata | Adverse Weather | Ice Storm
19697 | 2011 | 12 | 7 | 0.37778 |  | 98 | 103 | 63 | Marchwood | 27.6/16kV | MWDF4 | At 09:04 crews isolated 6 White phase transformers for elbow and insert replacement affecting 63 customers. Marchwood MWDF4 ID# 19697 | Kanata | Scheduled Outage
19702 | 2011 | 12 | 8 | 0.37639 |  | 75 | 75 | 60 | Marchwood | 27.6/16kV | MWDF4 | four blue phase transformer on Klondike and Wherside were isolated to allow crews to change elbows and inserts. | Kanata | Scheduled Outage | Preventive Maintenance
19706 | 2011 | 12 | 8 | 0.45972 |  | 70 | 33 | 28 | Kanata | 27.6/16kV | MWDF4 | MWDF4 red phase cable section between TP7145 and TP3016 was isolated for elbow and insert replacement, affection customers on Whernside, Beauly, and Halton Terrace. | Kanata | Scheduled Outage | Repair
17399 | 2010 | 12 | 10 | 0.10417 |  | 308 | 1731 | 634 | Marchwood | 27.6/16kV | MWDF4 | S233-2 tripped interrupting power to 63 transformers on the RWB phases. B & W phases were restored first and the red phase was sectionalized down to a suspected cable section between 1047R & 1048R. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6261 | 2005 | 3 | 11 | 0.44653 |  | 100 | 2033 | 2300 | Marchwood | 27.6/16kV | MWDF6 | While restoring MWDT1 transformer 624 B1-B2 tie switch failed to open propperly. Causing the tie switch to flash over. The MWD-CS1 & MWD-CS2 circuit switcher opened to clear the fault on C7m cirucit. MWDF6 circuit was also carring 624F1 load at the time of outage. S352-2 to the Nortel building opened. A. Cooney reports S352-2 is now closed storing all power at 11:30. Also Re-outage # 6261 & 6262, & 6263. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6797 | 2005 | 6 | 25 | 0.62222 |  | 1 | 7 | 400 | Marchwood | 27.6/16kV | MWDF6 | MWDF6 curcuit open because off storm,closed via scada and holding. | Kanata | Adverse Weather | Lightning
8722 | 2006 | 7 | 14 | 0.38472 |  | 94 | 3 | 2 | Marchwood | 27.6/16kV | MWDF6 | Transformer # 948R isolated to allow crew to replace transformer @ Kanata Rockeries Pvt. | Kanata | Scheduled Outage | Preventive Maintenance
13849 | 2009 | 1 | 9 | 0.43056 |  | 10 | 350 | 2100 | Marchwood | 27.6/16kV | MWDJQ-N | While the station crew were completing item # 3 MWDSS1-L-N for a close on PC17-26467 to energize the MWDSS1 and leave on potential the MWDJQ-N trip causing outages on the MWDF1,F3 circuits. | Kanata | Human Element | Incorrect Protection Settings
13807 | 2008 | 12 | 28 | 0.51875 |  | 169 | 11290 | 7100 | Marchwood | 27.6/16kV | MWDT2 | MWDCST2, MWDT2Q, MWDJQ, MWDF2 & MWDF4 tripped, during restoration of MWDF1 & F3 caused MWDCST2 to trip again, we restore load indivedually to MWDF1 & MWDF3, then offloaded MWDF2 to 624F4, had crew check FCI on MWDF4 nothing flagged, and picked up MWDF4 load with 624F6. | Kanata | Unknown/Other | No Apparent Cause
13815 | 2008 | 12 | 28 | 0.92847 |  | 128 | 4538 | 2600 | Marchwood | 27.6/16kV | MWDT2 | Tree contact on the MWDF3 caused the over trip of the bus and transformer. MWDF3 breaker appears the be going into breaker fail to quickly causing the overtrip. MWDF1 load restored first the F3 load restored through F3-F4 breaker. | Kanata | Tree Contacts | Tree Limb Fallen
14188 | 2009 | 4 | 19 | 0.0625 |  | 343 | 91 | 16 | Navan DS | 8/4.8kV | Navan DS F1 | Planned outage to H- 1 Navan DS for line repairs affecting transfer customers on Mer Bleue rd. Outage rescheduled from earlier date, no notification received. | Gloucester | Loss of Supply
16074 | 2010 | 5 | 10 | 0.76458 |  | 2 | 256 | 7669 | Nepean TS | 44kV | Nepean TS | Nepean TS J bus differemtial. 22M24 was unloaded for other work. M26 Parkwood Hills Borden Farms 4035 customers. M28 T2 Stafford and QCH DS 3634 customers. H1 reports flash marks on M28 insulators. | Nepean | Loss of Supply | HEPC Station Fault
13401 | 2008 | 10 | 21 | 0.44792 |  | 411 | 1844 | 4000 | Bridlewood | 27.6/16kV | OCR TF1 | transformer 8232 on Kathleen failed and required isolation for replacement. While switching to isolate the elbow at 8233 to 8232 flashed and tripped the OCR TF1 and damaged the elbow and bushing. Both 8232 and 8233 had to be isolated to allow for repair and replacement. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
12622 | 2008 | 6 | 13 | 0.625 |  | 335 | 17 | 3 | Bridlewood | 27.6/16kV | OCRTF1 | Tx 6757 @ 67 Iber rd isolated to transfer plant to new pole. | Kanata | Scheduled Outage | Construction
11154 | 2007 | 8 | 24 | 0.38333 |  | 301 | 1238 | 700 | Bridlewood | 27.6/16kV | OCRTF1 | Bushing at transformer T295B on Bujold Court in Kanata failed causing CB3 at SC4281 to open. Circuit sectionalized and customers restored in stages. Transformer T295B isolated and had to be replaced. | Kanata | Defective Equipment
13491 | 2008 | 10 | 28 | 0.95556 |  | 19 | 222 | 700 | Bridlewood | 27.6/16kV | OCRTF1 | Blown primary fuse on the BRDT4, OCRTF1 circuit fed from alternate source BRDF3. | Kanata | Adverse Weather
12475 | 2008 | 5 | 26 | 0.40972 |  | 30 | 2 | 3 | Bridlewood | 27.6/16kV | OCR-TF1 | Transformer #909 located at 651 Terry Fox isolated due to service disconnect for Arrears. | Kanata | Scheduled Outage | Construction
12582 | 2008 | 6 | 9 | 0.56944 |  | 20 | 1 | 3 | Bridlewood | 27.6/16kV | OCR-TF1 | Transformer #36349 located at 39 Lazy Nol Crt isolated to change arrestor & switch | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
11792 | 2007 | 11 | 30 | 0.69931 |  | 13 | 152 | 700 | Bridlewood | 27.6/16kV | OCR-TF1 | OCR-TF1 circuit breaker opened with no apparent cause. Fire and Police were called to see if any MVA's or fire reported. Circuit breaker closed in and holding. | Kanata | Unknown/Other | No Apparent Cause
6214 | 2005 | 2 | 17 | 0.61528 |  | 274 | 1529 | 1800 | Bridlewood | 27.6/16kV | OCRTF2 | Cable fault on the red phase cable between TE2925 & TE2355. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6351 | 2005 | 4 | 1 | 0.97569 |  | 196 | 33 | 10 | Bridlewood | 27.6/16kV | OCRTF2 | A blown fuse at transformer 1117W at 23 Bluegrass. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
6372 | 2005 | 4 | 5 | 0.86181 |  | 146 | 24 | 10 | Bridlewood | 27.6/16kV | OCRTF2 | Transformer fuse found blown at Tx 1117W, 23 Bluegrass, no cause found for open fuse, tx refused and restored. This is the second time this week, info passed onto Lines Reliability West. | Kanata | Defective Equipment
6379 | 2005 | 4 | 6 | 0.56181 |  | 150 | 20 | 8 |  | 27.6/16kV | OCRTF2 | Isolated T1117 on Bluegrass to change defective transformer | Kanata | Scheduled Outage
8375 | 2006 | 5 | 30 | 0.97222 |  | 555 | 918 | 100 | Bridlewood | 27.6/16kV | OCRTF2 | Switch S636W found open during patrol of 35F5 feeder. Bad cable found between 2214 and 699 on white phase. Section isolated and power restored. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8391 | 2006 | 5 | 31 | 0.82639 |  | 23 | 1941 | 5064 | Bridlewood | 27.6/16kV | OCRTF2 | OCRTF2 is carrying the load of BRDf1 and BRDF2 no metering or control of recloser. 24/7 closed recloser from local control and restored power to customers. | Kanata | Lightning
8423 | 2006 | 6 | 5 | 0.375 |  | 42 | 4 | 5 | Bridlewood | 27.6/16kV | OCRTF2 | Switch S422 on Richmond Rd found arcing and had to be replaced, O/H section fed from S422 isolated. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
8522 | 2006 | 6 | 19 | 0.77847 |  | 68 | 4533 | 4000 | Bridlewood | 27.6/16kV | OCRTF2 | Severe Lightning and Rain Storm caused the OCRTF2 to trip. No SCADA control. Doug McKay closed in Breaker, and held. | Kanata | Adverse Weather | Lightning
5477 | 2004 | 7 | 12 | 0.75 |  | 185 | 4692 | 2700 | Bridlewood temp | 27.6/16kV | OCRTF2 | A transformer blew at 53 Scissons and a fuse blew at 422 causing the OCRTF2 to trip. We sectionalize to pick the customers. | Kanata | Adverse Weather | Wind
5503 | 2004 | 7 | 15 | 0.51875 |  | 41 | 1230 | 1800 | Bridlewood | 27.6/16kV | OCRTF2 | MDF - Investigation determined cause determined to be Human Element. | Kanata | Human Element | Incorrect Use of Equipment
7139 | 2005 | 8 | 15 | 0.50694 |  | 366 | 556 | 3000 | Bridlewood | 27.6/16kV | OCRTF2 | Outage began on OCRTF2 - circuits then tied together (500 parallel) with BRDF3. Tripped both circuits (on Holdoff) due to isolated cables, were later determined not to be defective, as orignially suspected. All load was placed on BRDF3. During fault finding BRDF3 tripped again. Found dead short between TE1533W and TE104W. Various fault indicators were not working properly. Bad reading with meggar on original cable isolation. | Kanata | Defective Equipment
6241 | 2005 | 3 | 2 | 0.45833 |  | 10 | 28 | 170 | Bridlewood | 27.6/16kV | OCR-TF2 | Crews restored red phase cable section between TE2355 & TE2925. A planned outage was ranged by crews notifing customers at their door. Outage was required due to out of phase caution. | Kanata | Scheduled Outage | Repair
13555 | 2008 | 11 | 4 | 0.41528 |  | 1 | 126 | 7566 | Bridlewood | 27.6/16kV | OCR-TF2 | OCR-TF2 carrying BRDF1 & BRDF2 load, Steve Arseneault operated the wrong switch in S352 and dummped 7566 customers in the bridlewood area. Crew operated S352-2 instead of S352-3, after realizing the wrong switch was operated, crew closed in the S352-2 to pick up the load, caused OCR-TF2 to auto reclose due to the inrush of current. All customers picked up after 1 min. | Kanata | Human Element | Switching Errors
8978 | 2006 | 8 | 15 | 0.59375 |  | 65 | 5 | 5 | Queen | 4.16kV | OQ08 | Chris Williams opened transformer OTT417 @ 441 Billings to do a PCB transformer change. | Ottawa | Scheduled Outage | Preventive Maintenance
12042 | 2008 | 2 | 14 | 0.0375 |  | 86 | 4575 | 4500 | Albion | 13.2kV | Q Bus | 2210 line tripped due to a suspected cable fault causing the TABE breaker to trip because the Albion Q Bus was isolated for Hydro One. All load was restored and the defective cable isolated. | Ottawa | Defective Equipment
7958 | 2006 | 2 | 20 | 0.66736 |  | 127 | 1377 | 2203 | Lisgar | 12/7.2kV | Q BUS | Hydro One Lisgar Q Bus auto tripped due to a faulted capacitor breaker on their Q Bus. Breakers TLO1, TLO3. TLO5, TLO7, TLO9 & TL11 interupted. | Ottawa | Loss of Supply | HEPC Station Fault
3541 | 2003 | 6 | 9 | 0.035417 |  | 324 | 324 | 60 | Epworth | 8/4.8kV | Q.#58F1 | A tree contacted the line at 15 Starwood causing the 58F1 feeder to trip and reclose and the supply fuse at S205 to rupture. The tree was removed and, the line section was restored. | Nepean | Tree Contacts | Tree Fallen
3200 | 2003 | 2 | 19 | 0.475 |  | 51 | 5 | 6 | Merivale | 8/4.8kV | Q.#72 F7 | Truck backed into a down guy causing the circuit to auto-reclose and a transformer fuse to rupture. Complete repairs to be done at a later date but transformer was re-fused and closed. Full power was restored. | Nepean | Foreign Interference | Vehicle
4447 | 2003 | 11 | 13 | 0.89583 |  | 75 | 1430 | 1144 | Queensway Carleton | 8/4.8kV | Q.T.# 160 F3 | Line crews feel that the problem was a tree that fell across the line, at 60 Stinson in Bells Corners, and freed itself. The power was then restored by closing the breaker. This breaker also fed the Bells Corner F3 and F4 feeders. ID#4447 | Nepean | Adverse Weather | Wind
3787 | 2003 | 7 | 27 | 0.63542 |  | 70 | 58 | 50 | Woodroffe | 8/4.8kV | Q.T.# 170 F3 | The Woodroffe F3 breaker just auto-reclosed. It was switch S503 at the corner of Woodroffe and Vann that ruptured due to a tree contact at the corner of Rongal and Pineland. | Nepean | Tree Contacts | Tree Fallen
4388 | 2003 | 11 | 4 | 0.80903 |  | 105 | 350 | 200 | Woodroffe | 8/4.8kV | Q.T.# 170F4 | The live line lead feeding switch S987, at the corner of Woodfield and Lansfield, failed causing an outage to 7 transformers. ID#4388 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4178 | 2003 | 9 | 29 | 0.35 |  | 63 | 6 | 6 | Rideau Heights | 8/4.8kV | Q.T.# 180 | Broken fuse at transformer location #2823 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
3772 | 2003 | 7 | 22 | 0.72917 |  | 270 | 9 | 2 | Rideau Heights | 8/4.8kV | Q.T.# 180 F4 | Transformer TE1151 on Merivale Road had to be replaced due to leaking oil. | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4183 | 2003 | 9 | 30 | 0.69444 |  | 130 | 2 | 1 | Parkwood Hills | 8/4.8kV | Q.T.# 190 F2 | The service wire to 1404 Fisher Avenue in Nepean was severed due to a tree falling on it. Electrician to make repairs to service stack and meter base and ESA has to inspect it before the service is to be re-connected. Crew reconnected service & power restored at 18:50. | Nepean | Tree Contacts | Tree Fallen
4266 | 2003 | 10 | 15 | 0.75694 |  | 210 | 140 | 40 | Bell's Corners | 8/4.8kV | Q.T.# 47F4 | Tree on the line and is burning, switch SW214 was opened to allow for the tree to be removed and the power restored. | Nepean | Tree Contacts | Tree Limb Fallen
4265 | 2003 | 10 | 15 | 0.64583 |  | 125 | 417 | 200 | Epworth | 8/4.8kV | Q.T.# 58F1 | Tree on the line is responsible for the Q.T.# 58F1 circuit opening. Tree was removed and power was restored. | Nepean | Tree Contacts | Tree Fallen
3233 | 2003 | 3 | 8 | 0.70833 |  | 90 | 4 | 7 | Queenway | 8/4.8kV | Q.T.#160 F2 | Transformer TE278 on Abingdon in Nepean was isolated to allow for the disconnection of a pedestal. The pedestal was repaired and the transformer was again isolated to allow for its re-connection. | Nepean | Defective Equipment | Imminent Equipment Failure Detected
13665 | 2008 | 11 | 25 | 0.91736 |  | 1 | 42 | 2500 | Woodroffe | 13.2kV | Q/Z BUSES | While Hydro One has taking the Woodroffe Q Bus off potential their auto tranfer scheme operated interupting the Z Bus. The Q Bus load had been transferred to the Z Bus. | Ottawa | Loss of Supply
12215 | 2008 | 4 | 1 | 0.4375 |  | 120 | 2 | 1 | Uplands | 27.6/16kV | Q4801F7 | Overhead line to NRC at 2320 Lester Rd was isolated to replace 2 broken insulators. Defective insulators caused one fuse to blow at G656. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5164 | 2004 | 5 | 18 | 0.27778 |  | 2 | 0 | 15 | Uplands | 27.6/16kV | Q4801F7 | Breaker auto reclosed and locked out. F7 breaker closed from SCADA and held. Most of the load is Airport Services. | Gloucester | Adverse Weather | Lightning
19614 | 2011 | 11 | 21 | 0.51042 |  | 125 | 10 | 5 | Uplands | 27.6/16kV | Q4801F7 | Transformer #X13728 located at Uplands and Alert opened by crew to relocate transformer | Gloucester | Scheduled Outage | Construction
20927 | 2012 | 7 | 5 | 0.21667 |  | 48 | 55 | 69 | Uplands | 27.6/16kV | Q4801F8 | 24/7 reports G435R primary fuse found opened and transformer X14578 also found opened. Both fuses replaced all power restored. Cause unknown on Q4801F8 circuit. In the Atans Ave & Bank St area. | Gloucester | Unknown/Other | No Apparent Cause
12844 | 2008 | 7 | 15 | 0.33056 |  | 617 | 72 | 7 | Uplands | 27.6/16kV | Q4801F8 | Defective transformer TE655 at 3691 Albion Rd was replaced. | Gloucester | Defective Equipment
12912 | 2008 | 7 | 22 | 0.25972 |  | 131 | 17 | 8 | Uplands | 27.6/16kV | Q4801F8 | Transformer #X13513 located at 3582 Albion isolated due to bird contact. | Gloucester | Foreign Interference | Bird
12937 | 2008 | 7 | 24 | 0.84167 |  | 38 | 5 | 8 | Uplands | 27.6/16kV | Q4801F8 | Replaced blown fuse on switch feeding X13512 at 3568 Albion Rd (Cause Bird) | Gloucester | Foreign Interference | Bird
18865 | 2011 | 7 | 31 | 0.38958 |  | 149 | 12 | 5 | Uplands | 27.6/16kV | Q4801F8 | Transformer #X13512 located at 3568 Albion Rd opened up due to animal contact | Gloucester | Foreign Interference | Animal
15067 | 2009 | 9 | 8 | 0.55903 |  | 35 | 9 | 16 | Uplands | 27.6/16kV | Q4801F8 | Transformer #X13534 located at 3776 Albion Rd isolated to change blown arrestor due to animal contact | Gloucester | Foreign Interference | Animal
18210 | 2011 | 5 | 24 | 0.60903 |  | 121 | 12083 | 7580 | Uplands | 27.6/16kV | Q4801T3 | There was metal clade failure at Uplands on the Q4801T3Z, The Q4801F8 was carrying the 249F1 load at the time of the outage because the Leitrim station was out for servicing. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
5805 | 2004 | 9 | 16 | 0.61944 |  | 98 | 8 | 5 | Merivale | 8/4.8kV | Q72F5 | Heavy growth of Vines growing up the pole caused the transfomer fuse to blow | Nepean | Foreign Interference | Foreign Object
5817 | 2004 | 9 | 23 | 0.46042 |  | 59 | 18 | 18 | Manordale | 8/4.8kV | Q84F5 | Repairing Transformer at 110 MacLellan | Nepean | Scheduled Outage | Repair
6276 | 2005 | 3 | 13 | 0.38333 |  | 139 | 23 | 10 | Borden Farm | 8/4.8kV | QT130F1 | Isolated transformer TE4310 at 29 Kingsbury to repair secondary phase that had burnt off | Nepean | Defective Equipment | Equipment Deterioration Due to Age
6071 | 2004 | 12 | 17 | 0.27083 |  | 110 | 4 | 2 | Jockvale |  | QT145F3 | Replaced broken switch Transformer # 1525 at 55 Steeple Hill | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4861 | 2004 | 3 | 5 | 0.60833 |  | 332 | 778 | 323 | Queensway Carleton | 8/4.8kV | QT160 | Transformer TE 48 on the red phase under water blow S803 and 160T1 Hi side fuse. | Nepean | Adverse Weather | Rain
6200 | 2005 | 2 | 10 | 0.56111 |  | 77 | 8 | 6 | Woodroffe | 8/4.8kV | QT170F3 | Replaced broken Transformer switch #660 at the front of 60 Vaan | Nepean | Defective Equipment | Equipment Deterioration Due to Age
7632 | 2005 | 11 | 18 | 0.75972 |  | 151 | 5 | 2 | Rideau Hights | 8/4.8kV | QT180F4 | Replaced broken switch to transformer NP001557 at 2229 Prince of Wales Dr cause unknown | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
3767 | 2003 | 7 | 21 | 0.42708 |  | 45 | 4 | 6 | QT58 | 27.6/16kV | QT58F1 | At 10:15am on Monday, approximately 6 customers in the St. Helen Street area of Nepean were interrupted to allow for the replacement of a secondary service. Service was replaced and all customers were restored at 11:00am. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
6576 | 2005 | 5 | 19 | 0.38889 |  | 318 | 223 | 42 | Richmond North | 27.6/16kV | Rich F1 | A. Cooney reports TP2308 is now changed. All power restored to normal 14:38. 42 customers affected in power outage in richmond @ Shannonhouse | Kanata | Scheduled Outage | Preventive Maintenance
4057 | 2003 | 9 | 12 | 0.35208 |  | 31 | 23 | 45 | Richmond north | 8/4.8kV | Rich N F1 | Outage to transformers in the Dallaire Cr area of Richmond required to isolate cable section between TX106 & TX107 in Richmond to allow contractor to dig. | Goulburn | Scheduled Outage
4541 | 2003 | 12 | 1 | 0.51875 |  | 22 | 43 | 121 | Richmond S F1 | 27.6/16kV | Rich N F1 | Unscheduled outage required to overhead section from switch 336 to end of line to make repairs to overhead . Outage from switch 307 to 336 required to open switch 336. | Goulburn | Defective Equipment | Equipment Failure - Cause Unknown
4526 | 2003 | 11 | 27 | 0.37917 |  | 391 | 489 | 75 | Richmond north | 27.6/16kV | Rich N. F1 | Planed outage in Richmond to change transformer, and energize new switches. Outage effected 75 customers in the Richmond area | Kanata | Scheduled Outage | Construction
4592 | 2003 | 12 | 12 | 0.40278 |  | 158 | 26 | 10 | Richmond north | 27.6/16kV | Rich N. F1 | Transformer #100 isolated to remove tran# 93 from service. 10 Customers affected in power outage. | Kanata | Scheduled Outage | Construction
4034 | 2003 | 9 | 8 | 0.54167 |  | 100 | 5 | 3 | Richmond N | 27.6/16kV | Richmond F2 | J. Ryan reports transformer opened to change broken cross arm. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3969 | 2003 | 8 | 29 | 0.55694 |  | 33 | 72 | 130 | Richmond North | 8/4.8kV | Richmond N F1 | Lightning hit a pole on Perth St./Cockburn in Richmond, there was a Hold Off in effect on the Richmond N F1 circuit. The contractor surrended his Hold off and the circuit was closed back in and held. | Goulburn | Adverse Weather | Lightning
4584 | 2003 | 12 | 10 | 0.35972 |  | 177 | 35 | 12 | Richmond North | 27.6/16kV | Richmond N F1 | To isolate TX100 & TX101 to remove TX 100 from service. | Kanata | Scheduled Outage | Construction
4443 | 2003 | 11 | 13 | 0.68611 |  | 55 | 250 | 273 | Richmond R F3 | 8/4.8kV | Richmond N F3 | Tree fell on wires causing the W, R, Phase to open. The Bphase had to be open to removed the tree. | Goulburn | Adverse Weather | Wind
4631 | 2003 | 12 | 19 | 0.37153 |  | 180 | 15 | 15 | Richmond | 8/4.8kV | Richmond N. F1 | transformer 99 & TX95 isolated to disconnect secondary services. | Kanata | Scheduled Outage | Construction
7761 | 2005 | 12 | 24 | 0.49236 |  | 111 | 11 | 6 | Richmond North | 8/4.8kV | Richmond N. F3 | M. Brown reports transformer drop lead dective at replaced on TX2954 at 39 Norway Spruce st. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
4623 | 2003 | 12 | 18 | 0.38681 |  | 260 | 52 | 17 | Richmond N | 8/4.8kV | Richmond N-F1 | Transformer 96 was isolated for the replacement of pedestals and streetlights. 8 customers were affected to prevent out of phase. They were affected twice. | Goulburn | Scheduled Outage | Construction
7317 | 2005 | 9 | 12 | 0.40278 |  | 420 | 94 | 20 | 180F4 | 8/4.8kV | Rideau heights | TE554 & TE553 isolated to allow crews to replace transformers. 20 Customers affected by this outage. At 12:03 W. Ried reports TE554 energized. At 16:40 TE553 is now restored. | Nepean | Scheduled Outage | Construction
15680 | 2010 | 1 | 24 | 0.97917 |  | 45 | 65 | 87 | Limebank | 27.6/16kV | RX2001 | A hot line clamp let go and went into the O/H at 488 River Rd causing the RX2001 to trip. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15756 | 2010 | 3 | 1 | 0.40278 |  | 200 | 27 | 8 | Limebank | 27.6/16kV | RX2001 | Customers at 940 River rd were inturupted to allow crew to replace a pole. | Gloucester | Scheduled Outage | Preventive Maintenance
16412 | 2010 | 7 | 6 | 0.92639 |  | 402 | 72 | 24 | Limebank | 27.6/16kV | RX2001 | Defective transformer at 4120 Riverside caused RX2001 to auto reclose, load restored in sections. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
8890 | 2006 | 8 | 1 | 0.26389 |  | 122 | 244 | 120 | Limebank | 27.6/16kV | RX2001 | Lightning in the area causing the RX2001 to trip it was under hold off. | Gloucester | Adverse Weather | Lightning
8891 | 2006 | 8 | 1 | 0.26389 |  | 250 | 42 | 10 | Limebank | 27.6/16kV | RX2001 | Lightning in the area caused the switch G325R on River Rd to blow. | Gloucester | Adverse Weather | Lightning
15566 | 2009 | 12 | 27 | 0.54167 |  | 260 | 303 | 70 | Beckwith | 27.6/16kV | RX2005 | The RX2005 on Flewellyn Rd trip on the R & W phase, a tree at 7449 Flewellyn Rd fell on the O/H causing the phases to slap together. | Goulburn | Tree Contacts | Tree Fallen
7045 | 2005 | 7 | 31 | 0.53264 |  | 52 | 78 | 90 | Marchwood | 27.6/16kV | RX2009 | A car hit a pole on Kerwin Rd and broke it off. The recloser RX2009 had to be open to remove the remaining pole from the O/H. | Kanata | Foreign Interference | Vehicle
5094 | 2004 | 5 | 3 | 0.46875 |  | 57 | 47 | 49 | Limebank | 27.6/16kV | RX200X | A bushing at O/H transformer 2194 broke causing the R phase to blow at switch G460R. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16763 | 2010 | 8 | 17 | 0.65 |  | 370 | 9324 | 3000 | Alexander | 27.6/16kV | RX2010 | A broken B phase lead at switch 891 @ Johnwoods/Alon fell into the R phase causing the RX2010 to trip. When RX2010 was closed it was determined RX2013 on Fernbank was still open. RX2013 tripped again when a close was attempted after patrol did not reveal a problem. Single phase line fed from RX2013 was sectionalized & restored in sections. Suspect RX2013 trip settings but this has not been confirmed. | Goulburn | Defective Equipment
19602 | 2011 | 11 | 19 | 0.56458 |  | 20 | 912 | 2735 | Alexander | 27.6/16kV | RX2010 | RX2010 opened under hold-off during switching. Red phase elbow at S3-2 at 46 Trailway flashed over while crew attempted to open it tripping the RX2010. | Goulburn | Defective Equipment | Equipment Deterioration Due to Age
14446 | 2009 | 6 | 2 | 0.3875 |  | 102 | 339 | 1987 | Moulton | 27.6/16kV | RX2017 | 9:18 Scada indicated RX2017 auto reclosed, customer calls from Rothwell dr, G228, G617 and a transformer fuse at 15 Rothwell dr was found blown, dead squirrell was found at that address, when re-fusing G228, the RX2017 tripped under holdoff, restored holdoff and closed rx2017, crew then re-fused G617, then the transformer fuse. | Gloucester | Foreign Interference | Animal
14581 | 2009 | 6 | 20 | 0.76944 |  | 100 | 32 | 19 | Moulton | 27.6/16kV | RX2017 | The RX2017 auto reclosed which was caused by a crow that made contact with an O/H pail wich cause the fuse to blow at G884R @ 869 Mowat. | Gloucester | Foreign Interference | Animal
16330 | 2010 | 6 | 26 | 0.59375 |  | 134 | 159 | 71 | Moulton | 27.6/16kV | RX2017 | A defective R phase cable bet transformer T988(1246 Bethamy) and T919(1440 Beyhamy). | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16408 | 2010 | 7 | 6 | 0.72639 |  | 435 | 334 | 106 | Moulton | 27.6/16kV | RX2017 | RX2017 auto reclosed due to a defective overhead transformer at 14 Rothwell Dr. Load restored in sections. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16449 | 2010 | 7 | 9 | 0.85139 |  | 141 | 38 | 25 | Moulton | 8/4.8kV | RX2017 | Crews found G758B phase opened & transformer at 2050 Clovelly opened. Overhead fuse replaced and closed. | Gloucester | Adverse Weather | Lightning
16453 | 2010 | 7 | 10 | 0.62917 |  | 111 | 148 | 80 | Moulton | 27.6/16kV | RX2017 | SCADA indicates RX2017 on blair rd auto reclosed, cause to be crow contact on Rebecca causing G627 to blow. | Gloucester | Foreign Interference | Bird
15190 | 2009 | 9 | 30 | 0.32569 |  | 130 | 2 | 1 | Moulton | 27.6/16kV | RX2017 | The RX2017 auto reclosed on Blair because of the fuse blew at switch G732 @ the RCMP on Montreal Rd, the electrician found a problem on their side which caused the fuse to blow. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
14000 | 2009 | 2 | 23 | 0.56944 |  | 25 | 802 | 1925 | Moulton | 27.6/16kV | RX2017 (8F1) | RX2017 on Blair rd N. of Ogilvie tripped for no apparent reason. RX2017 was set on hold off at time of trip, crews cleared off H/O's, RX2017 closed & held. | Gloucester | Unknown/Other | No Apparent Cause
16804 | 2010 | 8 | 24 | 0.61736 |  | 2 | 66 | 1970 | Moulton MS | 27.6/16kV | RX2017(8F1) | RX2017 opened when crews attempted to energize new TP3984, causing a brief 2 minute outage. | Gloucester | Unknown/Other
14541 | 2009 | 6 | 16 | 0.26042 |  | 6 | 288 | 2879 | Bilberry Creek | 27.6/16kV | RX2020 | RX2020 at St. Joseph and Boyer tripped under holdoff protection, hold off was not issued, closed by System, crew to patrol in daylight. | Gloucester | Unknown/Other | No Apparent Cause
16541 | 2010 | 7 | 22 | 0.35208 |  | 156 | 3 | 1 | Bilberry | 27.6/16kV | RX2020 / 77M2 | A squirrel caused the cut-out to blow at 3897 Belcourt, Tx X19375 feeding a construction site.. This also caused RX2020 to A/R. | Gloucester | Foreign Interference | Animal
18241 | 2011 | 5 | 29 | 0.22083 |  | 52 | 6 | 7 | Bilberry | 27.6/16kV | RX2022 | A bird made contact with an O/H transformer causing the fuse to blow at transformer X18966 and the RX2022 to Auto reclose on Page Rd. | Gloucester | Foreign Interference | Bird
16043 | 2010 | 5 | 5 | 0.56597 |  | 182 | 361 | 119 | Blackburn | 8/4.8kV | RX2031 (4F3) | Crews found a defective insulator at 3237 Navan Rd. Insulator was repaired and power restored. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
16870 | 2010 | 9 | 4 | 0.36111 |  | 200 | 6042 | 2330 | Alexander |  | RX2039 | Switch gear S36 at 1251 STITTSVILLE MAIN ST has flashed over blades. | Goulburn | Defective Equipment | Imminent Equipment Failure Detected
3511 | 2003 | 5 | 29 | 0.35417 |  | 375 | 125 | 20 |  |  | s | K651, at 217 Rumulus, was isolated to allow for maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
11961 | 2008 | 1 | 19 | 0.64444 |  | 32 | 4 | 8 | Overbrook | 4.16kV | S002 | 4kV transformer feeding 8 customers on Dunbrak and telford, was opened to re-sleeve broken neutral on open wire service to 520 Dunbrak. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9366 | 2006 | 10 | 3 | 0.375 |  | 142 | 19 | 8 | Overbrook | 4.16kV | S002 | At 09:00 trans at 560 Queen Mary St was isolated for PCB replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9367 | 2006 | 10 | 3 | 0.38194 |  | 165 | 16 | 6 | Overbrook | 4.16kV | S002 | AT 09:10 trans at 568 Queen Mary was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
7446 | 2005 | 10 | 12 | 0.40278 |  | 35 | 6 | 11 | Overbrook | 4.16kV | S002 | Transformer #OTT3866 located at 467 Lawson isolated to change a service | Ottawa | Scheduled Outage | Construction
10052 | 2007 | 2 | 22 | 0.53125 |  | 100 | 25 | 15 | Overbrook | 4.16kV | S003 | At 12:45 trans at 242 Queen Mary Ave was isolated in order to replace a pole | Ottawa | Scheduled Outage | Repair
10072 | 2007 | 2 | 27 | 0.39583 |  | 270 | 32 | 7 | Overbrook | 4.16kV | S003 | At 09:30 trans OTT5168 at 216 Queen Mary was isolated in order to replace a transformer | Ottawa | Scheduled Outage | Repair
6434 | 2005 | 4 | 21 | 0.41667 |  | 120 | 8 | 4 | Overbrook | 4.16kV | S003 | Isolated Transformer # 5090 at 252 Queen Mary to replace bad xarm | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13178 | 2008 | 9 | 2 | 0.41111 |  | 158 | 21 | 8 | Overbrook | 4.16kV | S003 | At 09:52 trans at Vera St and St Patrick was isolated in order to transfer cond to new poles | Gloucester | Scheduled Outage | Construction
9615 | 2006 | 11 | 6 | 0.64653 |  | 57 | 14 | 15 | Overbrook | 4.16kV | S003 | At 15:31 trans at 240 Queen Mary was isolated in order to replace a pole | Ottawa | Scheduled Outage | Construction
11701 | 2007 | 11 | 13 | 0.48958 |  | 65 | 11 | 10 | Overbrook | 4.16kV | S003 | At 11:45 trans at 339 Presland Rd was isolated in order to replace seconday connecttors | Ottawa | Scheduled Outage | Repair
8191 | 2006 | 4 | 26 | 0.46875 |  | 130 | 6 | 3 | Overbrook | 4.16kV | S004 | Transformer #OTT6332 located at 1410 Triole isolated due to re-arranging of service | Ottawa | Scheduled Outage | Construction
12638 | 2008 | 6 | 15 | 0.72569 |  | 291 | 829 | 171 | Overbrook | 4.16kV | S004 | S004 circuit isolated due to S007 primary wire was laying on S004 circuit. S004 circuit autoreclosed at the same time S007 tripped. Primary repaired and breaker closed to restore load. Sever lightning storm in effect. | Ottawa | Adverse Weather | Lightning
9190 | 2006 | 9 | 11 | 0.35417 |  | 30 | 3 | 6 | Overbrook | 4.16kV | S004 | At 08:30 trans at 1483 Triole St was isolated in order to replace secondary service | Ottawa | Scheduled Outage | Preventive Maintenance
9259 | 2006 | 9 | 21 | 0.41667 |  | 104 | 21 | 12 | Overbrook | 4.16kV | S005 | Transformer located at 198 Presland isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
9268 | 2006 | 9 | 21 | 0.55903 |  | 50 | 7 | 8 | Overbrook | 4.16kV | S005 | Transformer located at 104 Presland isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
10043 | 2007 | 2 | 20 | 0.40069 |  | 187 | 37 | 12 | Overbrook | 4.16kV | S006 | At 09:37 trans OTT 5078 at 381 Prince Albert Ave was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
10858 | 2007 | 7 | 11 | 0.43056 |  | 35 | 4 | 6 | Coventry |  | S006 | Transformer #OTT5070 at 28 Queen Mary isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
12637 | 2008 | 6 | 15 | 0.65764 |  | 399 | 1416 | 213 | Overbrook | 4.16kV | S007 | S007 Breaker tripped, primary wire came down S004 overhead line on St. Laurent. S004 autoreclosed only. Wire repaired and breaker closed to restore power. Severe lightning storm in effect. | Ottawa | Adverse Weather
7054 | 2005 | 8 | 2 | 0.77083 |  | 32 | 4 | 8 | Overbrook | 4.16kV | S007 | Trans #OTT6731 located at 534 Donald St isolated to remove a span guy, touched against secondary & burnt it down | Ottawa | Adverse Weather | Rain
8907 | 2006 | 8 | 2 | 0.5 |  | 60 | 4 | 4 | Overbrook | 4.16kV | S007 | Isolated and removed from service transformer OTT1487 at 895 St Laurent Blvd 4 customers transfer to other transformer | Ottawa | Scheduled Outage | Construction
13182 | 2008 | 9 | 3 | 0.38611 |  | 78 | 13 | 10 | OVERBROOK | 13.2kV | S007 | Transformer X23764 at 606 Donald isolated to allow for transfer of plant | Ottawa | Scheduled Outage | Construction
14284 | 2009 | 5 | 1 | 0.61319 |  | 84 | 56 | 40 | Overbrook | 4.16kV | S010 | Defective lead at cutout to single phase line on Avenue R was replaced and switch closed to restore load to customers. | Ottawa | Defective Equipment
10669 | 2007 | 6 | 19 | 0.39583 |  | 27 | 5 | 12 | Overbrook | 4.16kV | S012 | Transformer #OTT5079 at 390 Prince Albert isolated to allow contractor to remove tree limb | Ottawa | Tree Contacts | Tree Limb Fallen
17552 | 2011 | 2 | 5 | 0.55764 |  | 11 | 3967 | 21638 | Merivale | 115kV | S7M | Hydro One crews at Manotick station was operating the T1-L when the switch did not operate correctly causing the switch to fail and flash, caused the S7M 115kV circuit to trip, affecting Hydro Ottawa's Fallowfield, Bridlewood T1 and T2, and Marchwood stations. 21638 customers affected. | Nepean | Loss of Supply | HEPC Station Fault
6227 | 2005 | 2 | 22 | 0.87222 |  | 449 | 299 | 40 | Hydro - One | 115kV | S7M | Hydro -One cct S7M (former W6MC) auto-reclosed due to a problem at H-1's Manotick DS causing a momentary loss of supply to Fallowfield, Bridlewood/Hazeldean, Marchwood & Richmond south stations. A number of transfer customers in the south west of Hydro - Ottawa's service territory remained out of power until Hydro - One made repairs at Manotick DS. | Nepean | Loss of Supply | HEPC Station Fault
14157 | 2009 | 4 | 9 | 0.095833 |  | 330 | 21712 | 18000 | Merivale TS | 115kV | S7M | Hydro One Supply S7M A/R/A interrupting power to Bridlewood DS, Marchwood DS, Fallowfield DS, Richmond S DS, and Manotick DS. Hydro One report a Skywire down at the Bridlewood Station Junction Point. | Ottawa | Loss of Supply
20456 | 2012 | 5 | 4 | 0.10139 |  | 139 | 35853 | 24583 | Marchwood | 115kV | S7M | Loss of supply from Hydro One circuit S7M affecting customers fed from Richmond South MS, Bridlewood DS, Marchwood DS and Fallowfield DS. Majority of load restored using alternate sources. Blown 115kV LA's found on Marchwood T1 transformer. | Kanata | Loss of Supply | HEPC Circuit Fault
20780 | 2012 | 6 | 15 | 0.55069 |  | 5 | 1771 | 21252 | Fallowfield | 115kV | S7M | Hydro One circuit S7M tripped affecting HOL stations (Fallowfield, Marchwood, Bridlewood-Half of Station, Richmond South - Offloaded). Truck contact. | Nepean | Loss of Supply | HEPC Circuit Fault
18489 | 2011 | 6 | 24 | 0.6625 |  | 66 | 2382 | 2165 | Bridlewood |  | S7M | At 15:54 the High and Low side Breakers of the Bridlewood T2 opened following an auto-reclose on the S7M line from Hydro One. All the load was transfered to Bridlewood T3. 2165 customers affected for 66mins. Bridlewood (BRDF5/BRDF6/BRDF7) ID# 18489 | Kanata | Loss of Supply
13161 | 2008 | 8 | 28 | 0.47014 |  | 4 | 1667 | 25000 |  | 115kV | S7M | Hydro One lost the S7M. No Apparent Cause. Affected Marchwood, Bridlewood, Fallowfield, Richmond S, Richmond North and Manotick DS. | Kanata | Loss of Supply
11329 | 2007 | 9 | 18 | 0.53681 |  | 10 | 6262 | 37575 | Bridlewood | 27.6/16kV | S7M | Hydro One circuit S7M auto tripped interrupting Bridlewood & Marchwood stations as well as Hydro Ottawa customers fed from Hydro One stations Fallowfield, Richmond South and Manotick DS's. It is suspected that a crane made contact with the 115 Kv circuit. | Kanata | Loss of Supply | HEPC Circuit Fault
17412 | 2010 | 12 | 12 | 0.4375 |  | 15 | 5411 | 21642 |  | 115kV | S7M | H1 loss of supply on the S7M circuit, Affecting marchwood - 4895 customers South Rich - 1215 customers Fallow Field - 8924 customers Briddlewood - 6608 customers | HYDRO ONE | Loss of Supply
17414 | 2010 | 12 | 12 | 0.46181 |  | 18 | 6493 | 21642 |  | 600/347 | S7M | H1 loss of supply on the S7M circuit, Affecting marchwood - 4895 customers South Rich - 1215 customers Fallow Field - 8924 customers Briddlewood - 6608 customers | HYDRO ONE | Loss of Supply
11140 | 2007 | 8 | 24 | 0.1875 |  | 8 | 5010 | 37575 | Hydro One | 115kV | S7M & W6CS | Hydro One reports S7M tripped when attempted to re-energize W6CS, power restored at 4:38 on the S7M, W6CS remains out of service due to a suspected permanent fault, | Kanata | Loss of Supply | HEPC Circuit Fault
11142 | 2007 | 8 | 24 | 0.16944 |  | 6 | 3758 | 37575 | Hydro One | 115kV | S7M & W6CS | Scada indicated loss of supply to Bridlewood and Marchwood, Hydro One (Lucky) reports S7M & W6CS both auto reclosed, and they manually attempted to close, W6CS is still off but no load is off, heavy lightning and rain in the area. | Kanata | Loss of Supply | HEPC Circuit Fault
10179 | 2007 | 3 | 26 | 0.91042 |  | 191 | 13 | 4 | SLATER |  | SA19 | Scheduled outage to 4 vaults affecting V151at 102 Bank, V53 at 109 Bank, TV54 at 119 Bank, and TV84 at Bank and Slater to remove Asbestos from V151 and V53. | Ottawa | Scheduled Outage
14616 | 2009 | 6 | 25 | 0.61111 |  | 35 | 1 | 1 | Slater | 4.16kV | SA19 | V151 at 102 Bank isolated to allow contractor to replace secondary main that was overheating. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17530 | 2011 | 1 | 27 | 0.47639 |  | 44 | 11 | 15 | Slater | 4.16kV | SA22 | Isolated transformer X30669 at 91 Nepean St for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
16027 | 2010 | 5 | 2 | 0.38681 |  | 463 | 77 | 10 | Slater | 4.16kV | SA22 | transformer at corner of Metcalfe east of somerset was opened for crew to change pole. | Ottawa | Scheduled Outage | Repair
5146 | 2004 | 5 | 14 | 0.29167 |  | 80 | 9 | 7 | SA | 4.16kV | SA22 | Tx OTT2795 isolated for replacement at 77 Gloucester. | Ottawa | Scheduled Outage | Repair
5499 | 2004 | 7 | 14 | 0.41458 |  | 70 | 16 | 14 | Slater | 4.16kV | SA22 | Transformer 4671 at 88 Nepean was isolated for the re-arrangement of secondary. | Ottawa | Scheduled Outage | Repair
3892 | 2003 | 8 | 12 | 0.64653 |  | 239 | 8 | 2 | Slater | 4.16kV | SA22 | Blown transformer 2794 at 150 Gloucester was replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11038 | 2007 | 8 | 12 | 0.49583 |  | 46 | 164 | 214 | Slater | 4.16kV | SA22 | At 11:54 a blown lightening arrestor at 315 Somerset caused SA22 to open. Arrestor cleared and circuit restored at 12:40 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17444 | 2010 | 12 | 21 | 0.38889 |  | 159 | 8 | 3 | Slater | 4.16kV | SA22 | Transformer #X30752 located at 150 Gloucester St opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
5145 | 2004 | 5 | 14 | 0.070139 |  | 139 | 42 | 18 | Slater | 4.16kV | SA23 | D. Howat reports broken switch at Dip pole #2 feeding V816 295 Gilmore St. V816 to be isolated to all crew replace defective switch. 18 Customers affected in power outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4022 | 2003 | 9 | 5 | 0.41319 |  | 83 | 7 | 5 | Albion | 8/4.8kV | SA23 | Transformer OTT2697 o/s to replace a sedondary service. | Ottawa | Scheduled Outage | Repair
20835 | 2012 | 6 | 23 | 0.081944 |  | 66 | 602 | 547 | Slater | 13.2kV | SAT1 | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
7881 | 2006 | 2 | 2 | 0.52431 |  | 30 | 5 | 10 | Bronson | 4.16kV | SB02 | Transformer 55D2D-0650 at 100 Paterson Dr was isolated to replace service | Ottawa | Scheduled Outage | Repair
7889 | 2006 | 2 | 4 | 0.88542 |  | 90 | 9 | 6 | Bronson | 4.16kV | SB02 | defective transformer switch on the overhead transformer at the corner of Pretoria and Queen Elizabeth. Crew replaced switch and closed in transformer. | Ottawa | Adverse Weather
6273 | 2005 | 3 | 13 | 0.06875 |  | 16 | 3 | 11 | Bronson | 4.16kV | SB02 | O/H xfmr on same pole as dip to P167 had to be interrupted to apply grounds in order to make cable repirs. 11 customers on Strathcona & Patterson were interrupted. | Ottawa | Unknown/Other
14064 | 2009 | 3 | 16 | 0.36806 |  | 30 | 3 | 6 | Bronson | 4.16kV | SB02 | Transformer #X30447 located at 26 Monkland Ave isolated to chg triplex from #4 to #2 | Ottawa | Scheduled Outage | Preventive Maintenance
10194 | 2007 | 3 | 28 | 0.43889 |  | 210 | 42 | 12 | Bronson | 4.16kV | SB02 | Tony Taylor isolated TRF. OTT 6116 @ 46 Stratcona for a pole change | Ottawa | Scheduled Outage | Preventive Maintenance
10204 | 2007 | 3 | 29 | 0.42708 |  | 225 | 22 | 6 | Bronson | 4.16kV | SB02 | AT 10:15 trans at 45 Strathcona was isolated for a pole change | Ottawa | Scheduled Outage | Repair
17844 | 2011 | 4 | 6 | 0.75833 |  | 31 | 258 | 499 | BRONSON | 4.16kV | SB02 | At 18:12 system opened SB02 breaker at Bronson to allow crew to safely repair fallen conductor on SB02 circuit in front of V420. 500 customers affected for 31 mins. A blown P/P/H was found at dip to V420. On call crew called in to repair defective P/P/H to V420 @ 64 Pretoria. Asbestos removal & cable replacement required, customer advised to obtain generator O/N. Bronson, SB02, ID# 17844 | Ottawa | Defective Equipment
10283 | 2007 | 4 | 19 | 0.41667 |  | 240 | 60 | 15 | Bronson | 4.16kV | SB02 | AT 10:00 trans at 40 Strathcona was isolated for pole and trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
5045 | 2004 | 4 | 23 | 0.42708 |  | 195 | 55 | 17 | slater | 4.16kV | SB02 | Outage at 493 Matcalfe St. for pole change. 17 Customers effected in power outage. | Ottawa | Scheduled Outage | Construction
18052 | 2011 | 4 | 28 | 0.56389 |  | 133 | 964 | 435 | Bronson | 4.16kV | SB02 | SB02 CB tripped during wind/lightning storm. Crews isolated small section to remove tree and restored power to remaining customers. | Ottawa | Tree Contacts | Tree Fallen
10343 | 2007 | 4 | 30 | 0.42014 |  | 150 | 25 | 10 | Bronson | 4.16kV | SB02 | Lee Piper isolated TRF. @ 70 Stratcona to change over plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
10347 | 2007 | 5 | 1 | 0.40625 |  | 135 | 18 | 8 | Bronson | 13.2kV | SB02 | transformer # X30064 located at 103 Strathcona, isolated to transfer hydro plant | Ottawa | Scheduled Outage | Preventive Maintenance
10358 | 2007 | 5 | 3 | 0.39583 |  | 315 | 178 | 34 | Bronson | 4.16kV | SB02 | Bill Edwards isolated TRF. 6117 & 6118 @ 99 & 103 Strathcona to install new secondary buss | Ottawa | Scheduled Outage | Preventive Maintenance
10385 | 2007 | 5 | 8 | 0.40625 |  | 172 | 34 | 12 | Bronson | 4.16kV | SB02 | Isolated P167 @ Pretoria Bridge to transfer the transformer to a new pole. | Ottawa | Scheduled Outage | Construction
12421 | 2008 | 5 | 9 | 0.39583 |  | 290 | 34 | 7 | Bronson | 4.16kV | SB02 | At 09:30 trans at 202 Pattereson Ave was isolated in order to replace a pole | Ottawa | Scheduled Outage | Preventive Maintenance
10427 | 2007 | 5 | 17 | 0.39583 |  | 210 | 35 | 10 | Bronson | 4.16kV | SB02 | Bill Edwards isolated TRF @ 46 stratcona to change over plant to new poles | Ottawa | Scheduled Outage | Preventive Maintenance
6585 | 2005 | 5 | 21 | 0.39306 |  | 56 | 8 | 9 | Bronson | 4.16kV | SB02 | Switch to Transformer OTT4111 at 29 Madawaska Dr was found blown due to animal contact (Squirrel) | Ottawa | Foreign Interference | Animal
10436 | 2007 | 5 | 22 | 0.39722 |  | 114 | 17 | 9 | Bronson | 4.16kV | SB02 | At 09:32 trans at 29 Monkland Ave was isolated in order to replace defective connections | Ottawa | Scheduled Outage | Preventive Maintenance
10448 | 2007 | 5 | 23 | 0.41667 |  | 180 | 36 | 12 | Bronson | 4.16kV | SB02 | At 10:00 trans at 75 Strathcona Ave was isolated in order to upgrade sec services | Ottawa | Scheduled Outage | Preventive Maintenance
10453 | 2007 | 5 | 24 | 0.44444 |  | 45 | 11 | 15 | Bronson | 4.16kV | SB02 | AT 10:00 trans at 19 Strathcona was isolated in order to replace spun buss | Ottawa | Scheduled Outage | Preventive Maintenance
10474 | 2007 | 5 | 29 | 0.41667 |  | 135 | 32 | 14 | Bronson | 4.16kV | SB02 | Transformer #OTT6115 located at 39 Strathcona Ave isolated to allow for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
10504 | 2007 | 6 | 1 | 0.39583 |  | 100 | 32 | 19 | Bronson | 4.16kV | SB02 | Transformer #X34425 located at 57 Strathcona isolated to install new pole | Ottawa | Scheduled Outage | Construction
5267 | 2004 | 6 | 8 | 0.41667 |  | 160 | 37 | 14 | Bronson | 4.16kV | SB02 | Transformer #4459 isolated to allow crews to complete pole changeover. 14 Customers effected in power outage. At Strathcona & Metcalfe. | Ottawa | Scheduled Outage | Construction
10832 | 2007 | 7 | 10 | 0.38333 |  | 105 | 21 | 12 | Bronson | 4.16kV | SB02 | O/H transformer at 489 Metcalf isolated for replacement. | Ottawa | Scheduled Outage | Repair
16474 | 2010 | 7 | 14 | 0.97778 |  | 47 | 1 | 1 | Bronson | 4.16kV | SB02 | Crew replaced defective cutouts feeding V420 at 26 Petoria (Loblaws) | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18742 | 2011 | 7 | 17 | 0.80694 |  | 230 | 1913 | 499 | Bronson | 4.16kV | SB02 | SBK2Y2 tripped carrying SB02 load, circuit closed back in with success | Ottawa | Adverse Weather
18788 | 2011 | 7 | 22 | 0.45139 |  | 100 | 30 | 18 | Bronson Sub | 4.16kV | SB02 | Crew isolated X31397 at 172 Patterson to change out transformer | Ottawa | Scheduled Outage
12941 | 2008 | 7 | 25 | 0.40278 |  | 205 | 17 | 5 | Bronson | 4.16kV | SB02 | Transformer #X30027 located at 28 Monkland isolated due to service upgrade. | Ottawa | Scheduled Outage | Preventive Maintenance
8851 | 2006 | 7 | 26 | 0.52083 |  | 60 | 12 | 12 | Bronson | 4.16kV | SB02 | Isolated transformer OTT2421 at 96 First Ave to replace secondary connections | Ottawa | Scheduled Outage | Repair
16686 | 2010 | 8 | 6 | 0.39792 |  | 269 | 161 | 36 | Bronson | 4.16kV | SB02 | Two Transformers were opened to disconnect single white phase local of SB02 overhead on pretoria between, Metcalfe, and O'Conner, To remove trees from overhead circuit. | Ottawa | Tree Contacts | Tree Limb Fallen
16713 | 2010 | 8 | 10 | 0.80764 |  | 160 | 51 | 19 | Bronson | 4.16kV | SB02 | broken switch caused overhead transformer X30430 on pretoria at Bank to open. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7247 | 2005 | 8 | 31 | 0.15208 |  | 61 | 30 | 30 | Bronson | 4.16kV | SB02 | Blown cut out and damaged switch to 200 Pretoria repaired and refused. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19161 | 2011 | 9 | 13 | 0.61944 |  | 368 | 1132 | 448 | Bronson | 4.16kV | SB02 | SB02 breaker opened during lightning storm due to SB00 circuit falling across it at Pretoria and O'Connor. SB00 was cut clear and breaker closed via SCADA and is holding. | Ottawa | Adverse Weather | Lightning
19184 | 2011 | 9 | 15 | 0.48611 |  | 20 | 6 | 18 | Bronson | 4.16kV | SB02 | Transformer #X31397 located at 172 Patterson Ave opened by crew to isolate buss for tree company | Ottawa | Tree Contacts | Inadequate Trimming
9289 | 2006 | 9 | 24 | 0.45833 |  | 118 | 232 | 118 | Bronson | 4.16kV | SB02 | With the high winds the SB02 slapped together at th intersection O'Connor & Strathcona | Ottawa | Adverse Weather | Wind
15215 | 2009 | 10 | 5 | 0.45417 |  | 36 | 4 | 7 | Bronson | 4.16kV | SB02 | Isolated transformer X30062 at 122 First Ave to replace triplex service | Ottawa | Scheduled Outage | Repair
17079 | 2010 | 10 | 7 | 0.63542 |  | 30 | 4 | 7 | Bronson | 4.16kV | SB02 | Transformer #X30457 located at 32 Pretoria opened by crew to connect new service | Ottawa | Scheduled Outage | Construction
4275 | 2003 | 10 | 15 | 0.96667 |  | 176 | 346 | 118 | Bronson | 4.16kV | SB02 | SB02 was taken out of service to put conductor on Pretoria west of O'Connor back up on poles. | Ottawa | Adverse Weather
13553 | 2008 | 11 | 3 | 0.6375 |  | 42 | 10 | 14 | BRONSON | 4.16kV | SB02 | Transformer # X30458 in front of 5 Pretoria isolated to replace connections at 214 Queen Elizabeth Driveway | Ottawa | Scheduled Outage | Repair
4457 | 2003 | 11 | 14 | 0.30556 |  | 93 | 183 | 118 | Bronson | 4.16kV | SB02 | SB02 breaker opened manually to repair a downed phase. | Ottawa | Adverse Weather | Wind
9769 | 2006 | 12 | 1 | 0.65 |  | 415 | 189 | 118 | Bronson | 4.16kV | SB02 | SB02 o/h circuit was opened via SCADA due to primary down. The damaged section from OConnor to Bank on Strathcona was isolated for repairs & the main circuit was restored while repairs were being made. The entire circuit was then isolated to reconnect the repaired section. | Ottawa | Adverse Weather | Ice Storm
4590 | 2003 | 12 | 12 | 0.083333 |  | 196 | 385 | 118 | Bronson | 4.16kV | SB02 | Possible high winds caused SB02 primary to come down at the intersection of Pretoria and O'Conner. | Ottawa | Adverse Weather | Wind
13945 | 2009 | 2 | 9 | 0.57986 |  | 50 | 7 | 8 | Bronson | 4.16kV | SB03 | O/H transformer at 263 First Ave isolated to repair defective service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20048 | 2012 | 2 | 23 | 0.45833 |  | 120 | 16 | 8 | Bronson | 4.16kV | SB03 | At 11:00am, transformer X30119 located at 33 powell was isolated for service. 8 customers affected for 120 minutes. Bronson (SB03) | Ottawa | Scheduled Outage
17957 | 2011 | 4 | 18 | 0.38889 |  | 45 | 8 | 10 | Bronson |  | SB03 | Isolated transformer X31376 at 126 Third Ave foe a swervice up-grade | Ottawa | Scheduled Outage | Repair
10372 | 2007 | 5 | 6 | 0.40208 |  | 124 | 562 | 272 | Bronson | 4.16kV | SB03 | A tree contractor dropped a limb on the SB03 o/h line at 683 Bronson. Limb cleared and circuit re-energized. | Ottawa | Foreign Interference | Foreign Object
12465 | 2008 | 5 | 23 | 0.22917 |  | 139 | 16 | 7 | Bronson | 4.16kV | SB03 | Transformer X25870 at 603 Bank opened to re-arrange Hydro plant. | Ottawa | Scheduled Outage | Construction
18334 | 2011 | 6 | 8 | 0.69028 |  | 227 | 409 | 536 | Bronson | 4.16kV | SB03 | Lightning storm, wires down. Circuit tripped ARA, restored from SCADA, then interrupted at the request of 24/7 crew on-site. Downed conductor cut clear & circuit restored. | Ottawa | Adverse Weather | Lightning
18335 | 2011 | 6 | 8 | 0.64236 |  | 263 | 447 | 536 | Bronson | 4.16kV | SB03 | SB03 auto reclosed. Crews found a live phase down behind 243 First Ave. The broken span was cut clear and the rest of the circuit picked up. On-call crews repaired the broken section and restored the remainder of the customers. | Ottawa | Tree Contacts | Tree Limb Fallen
16363 | 2010 | 6 | 29 | 0.625 |  | 20 | 0 | 1 | Bronson | 4.16kV | SB03 | Transformer #X31443 located at 54 Imperial Ave opened by crew to re-do connections at the transformer | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6876 | 2005 | 7 | 6 | 0.38542 |  | 91 | 15 | 10 | Bronson | 4.16kV | SB03 | Isolatre Transformer 749 at 120 Powell for D/R | Ottawa | Scheduled Outage | Preventive Maintenance
5497 | 2004 | 7 | 14 | 0.35417 |  | 270 | 40 | 9 | Bronson | 4.16kV | SB03 | Transformer 430 at rear of 93 Clemow was isolated for maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
5498 | 2004 | 7 | 14 | 0.33333 |  | 60 | 11 | 11 | Bronson | 4.16kV | SB03 | Transformer 431 at the rear of 97 Glede was isolated for maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
5579 | 2004 | 7 | 28 | 0.375 |  | 180 | 27 | 9 | Bronson | 4.16kV | SB03 | Transformer at 93 Clemow isolated to upgrade customer service. | Ottawa | Scheduled Outage | Construction
7053 | 2005 | 8 | 2 | 0.55139 |  | 60 | 14 | 14 | Bronson | 4.16kV | SB03 | Isolated Transformer #1558 at 5 Clemow to remove Vines of pole | Ottawa | Tree Contacts | Inadequate Trimming
3843 | 2003 | 8 | 4 | 0.45278 |  | 53 | 9 | 10 | Bronson | 4.16kV | SB03 | A squirrel caused the fuse at the transformer in the rear of 136 Glebe. The crew refused and restored power to approx. 10 customers on Glebe and First Ave. | Ottawa | Foreign Interference | Animal
13131 | 2008 | 8 | 21 | 0.5625 |  | 50 | 8 | 10 | SB03 | 4.16kV | SB03 | Transformer #X30108 located at 158 Glebe Ave isolated to change open wire service at transformer pole. | Ottawa | Scheduled Outage | Preventive Maintenance
11200 | 2007 | 8 | 29 | 0.92361 |  | 234 | 137 | 272 | Bronson | 4.16kV | SB03 | SB03 circuit opened to cut clear downed overhead conductor. 30 customers still out | Ottawa | Adverse Weather | Wind
4059 | 2003 | 9 | 12 | 0.33889 |  | 35 | 4 | 7 | Bronson | 4.16kV | SB03 | Squirrel contact opened transformer feeding 7 customers on Glebe and First fed from transformer at 136 glebe. | Ottawa | Foreign Interference | Animal
13235 | 2008 | 9 | 15 | 0.39583 |  | 20 | 1 | 2 | Bronson | 4.16kV | SB03 | Transformer #X31444 located at 655 Bronson Ave isolated to relocate transformer to another pole | Ottawa | Scheduled Outage | Preventive Maintenance
11393 | 2007 | 9 | 26 | 0.53125 |  | 105 | 21 | 12 | Bronson | 4.16kV | SB03 | Transformer #X31378 located at 137 Third Ave isolated to replace transformer for PCB change | Ottawa | Scheduled Outage
11452 | 2007 | 10 | 3 | 0.38194 |  | 164 | 25 | 9 | BRONSON | 4.16kV | SB03 | Transformer #X30101 at 64 Powell Ave isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
19530 | 2011 | 11 | 4 | 0.63542 |  | 25 | 2 | 5 | Bronson | 4.16kV | SB03 | Transformer #X43824 located at 243 First Ave opened by crew for Service work | Ottawa | Scheduled Outage | Construction
19543 | 2011 | 11 | 8 | 0.34722 |  | 10 | 1 | 5 | Bronson | 4.16kV | SB03 | Isolated transformer X43824 at 243 First Ave to disconnect service for an up-grade | Ottawa | Scheduled Outage | Emergency Services Request
9742 | 2006 | 11 | 28 | 0.35903 |  | 106 | 5 | 3 | Bronson | 4.16kV | SB03 | Isolated transformer at Bank/Strathcona to upgrade a service | Ottawa | Scheduled Outage | Preventive Maintenance
13706 | 2008 | 12 | 6 | 0.15486 |  | 282 | 52 | 11 | Bronson | 4.16kV | SB03 | Overhead transformer at Renfrew & Bronson was interrupted to disconnect power to building on fire at 659 Bronson. John Streng Disconnected service and removed triplex, restored transformer. Voltage good no damage to hydro plant. | Ottawa | Adverse Environment | Fire
19688 | 2011 | 12 | 6 | 0.40972 |  | 28 | 2 | 5 | Bronson | 4.16kV | SB03 | Transformer #X31344 located at 799 Lyon St S opened by crew for pole replacement | Ottawa | Scheduled Outage | Construction
19749 | 2011 | 12 | 20 | 0.52083 |  | 60 | 5 | 5 | Bronson | 4.16kV | SB03 | At 12h30 crews isolated transformer X31344 at 799 Lyon to transfer some service. 5 customers affected for 60 mins. Bronson SB03 ID# 19749 | Ottawa | Scheduled Outage
16011 | 2010 | 4 | 28 | 0.55208 |  | 75 | 30 | 24 | Bronson | 4.16kV | SB04 | Isolated transformer X25775 at 424 Cambridge St for service up-grade | Ottawa | Scheduled Outage | Repair
16017 | 2010 | 4 | 29 | 0.36944 |  | 218 | 22 | 6 | Bronson | 4.16kV | SB04 | SB04 B phase from Fredrick to Kippewa was isolated to allow working clearence for tree trimmers. | Ottawa | Scheduled Outage | Preventive Maintenance
20867 | 2012 | 6 | 25 | 0.44792 |  | 25 | 3 | 7 | Bronson | 4.16kV | SB04 | Isolated transformer X25771 at 448 Cambridge St for a service upgrade | Ottawa | Scheduled Outage | Emergency Services Request
5568 | 2004 | 7 | 26 | 0.5875 |  | 204 | 119 | 35 | SB | 4.16kV | SB04 | AS per dispatch, Tx 55D2C-0254 at 488 Cambridge off at 14:06 to replace defective transformer. 35 customers back on at 17:30 | Ottawa | Scheduled Outage | Repair
11819 | 2007 | 12 | 7 | 0.69792 |  | 15 | 2 | 7 | Bronson | 4.16kV | SB04 | Isolated transformer X25771 at 449 Cambridge St to cut service clear that had been pulled down by snow clearing equipment | Ottawa | Foreign Interference | Vehicle
15587 | 2009 | 12 | 29 | 0.49653 |  | 34 | 3 | 6 | Bronson | 4.16kV | SB04 | Transformer #X35005 located at 6 Frederick isolated for branch removal | Ottawa | Tree Contacts | Tree Limb Fallen
17605 | 2011 | 2 | 17 | 0.98264 |  | 270 | 284 | 63 | Bronson | 4.16kV | SB05 | At 23:35 vines on a pole at the rear of 296 First Ave caused a fuse to blow on the White phase of SB05. On Call crew removed vines a refused. 63 customers affected for 270 mins. Bronson SB05 ID#17605. | Ottawa | Tree Contacts
15764 | 2010 | 3 | 3 | 0.38194 |  | 50 | 12 | 14 | Bronson | 4.16kV | SB05 | Isolated transformer X37970 at 200 Glebe Ave for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
20120 | 2012 | 3 | 4 | 0.85069 |  | 10 | 3 | 20 | Bronson | 4.16kV | SB05 | crews found defective line clamp at 147 Fifth Ave, feeding K987, 20 customers affected for 10 minutes. Bronson (SB05) | Ottawa | Defective Equipment
20178 | 2012 | 3 | 19 | 0.33681 |  | 163 | 54 | 20 | Bronson | 4.16kV | SB05 | Transformer K987 @ 149 Fifth Ave was isolated by the crew to give them clearance to replace the pole. | Ottawa | Scheduled Outage | Construction
20194 | 2012 | 3 | 21 | 0.33681 |  | 329 | 411 | 75 | Bronson | 4.16kV | SB05 | Crew isolated P218 and white phase on holmwood to replace pole and transfer cables. Customers on holmwood and monk were interrupted. | Ottawa | Scheduled Outage | Construction
10232 | 2007 | 4 | 10 | 0.40625 |  | 265 | 31 | 7 | Bronson | 4.16kV | SB05 | Transformer #OTT4911 located at 535 Percy St isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
18090 | 2011 | 5 | 4 | 0.42917 |  | 46 | 8 | 10 | Bronson | 4.16kV | SB05 | Transformer @ 223 Fourth Ave was open to allow crew to replace O/H secondary cable to 378 Third Ave. 10 customer were affected. Bronson (SB05) | Ottawa | Defective Equipment
18092 | 2011 | 5 | 4 | 0.46944 |  | 60 | 6 | 6 | Bronson | 4.16kV | SB05 | Transformer X30005 was open to allow crew to upgrade service to 382 Third Ave. 6 customer were affected. Bronson SB05 | Ottawa | Scheduled Outage
20502 | 2012 | 5 | 11 | 0.43125 |  | 79 | 7 | 5 | Bronson | 4.16kV | SB05 | Transformer X29887 at 90 Fifth Ave. was isolated to string new service | Ottawa | Scheduled Outage | Construction
10456 | 2007 | 5 | 24 | 0.44444 |  | 80 | 20 | 15 | Bronson | 4.16kV | SB05 | At 10:40 trans at 7 Rupert was isolated for pole replacement | Ottawa | Scheduled Outage | Repair
8388 | 2006 | 5 | 31 | 0.43056 |  | 20 | 4 | 11 | Bronson | 4.16kV | SB05 | Isolated transformer OTT5272 at 8 Regent St to replace service | Ottawa | Scheduled Outage | Repair
18281 | 2011 | 6 | 2 | 0.375 |  | 15 | 4 | 17 | Bronson | 4.16kV | SB05 | Isolated transformer X31391 at 304 First Ave to replace triplex service | Ottawa | Scheduled Outage | Emergency Services Request
12777 | 2008 | 7 | 2 | 0.36806 |  | 80 | 21 | 16 | Bronson | 4.16kV | SB05 | Isolated transformer X29803 at 16 Regent St to replace a secondary service | Ottawa | Scheduled Outage | Repair
8693 | 2006 | 7 | 10 | 0.88056 |  | 97 | 24 | 15 | Bronson | 4.16kV | SB05 | Switch to transformer OTT2764 opened due to animal contact (Raccoon) refused switch restored power 190 Glebe | Ottawa | Foreign Interference | Animal
10835 | 2007 | 7 | 10 | 0.54653 |  | 143 | 24 | 11 | Bronson | 4.16kV | SB05 | Transformer #OTT5272 at 9 Regent St isolated to allow for PCB change | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10861 | 2007 | 7 | 11 | 0.52708 |  | 29 | 6 | 13 | Bronson | 4.16kV | SB05 | Transformer #29812 at 11 Clarey St isolated to allow for setting of new pole and changing buss | Ottawa | Scheduled Outage | Preventive Maintenance
7006 | 2005 | 7 | 22 | 0.25 |  | 110 | 16 | 9 | Bronson | 4.16kV | SB05 | Transformer #OTT2402 located at 288 Fifth Ave isolated due to bird contact | Ottawa | Foreign Interference | Bird
14820 | 2009 | 7 | 24 | 0.41667 |  | 30 | 4 | 8 | Bronson | 4.16kV | SB05 | Transformer #X27745 located across from 49 Adelaide St isolated due to running a new U/G service up a pole | Ottawa | Scheduled Outage | Construction
12988 | 2008 | 8 | 1 | 0.65625 |  | 32 | 7 | 14 | BRONSON | 4.16kV | SB05 | Transformer at pole X34831 ar 4 Regent isolated to allow for repairs | Ottawa | Scheduled Outage | Repair
7083 | 2005 | 8 | 7 | 0.47083 |  | 37 | 1 | 1 | Bronson | 4.16kV | SB05 | Tranformer at 900 Bank St isolated due to animal interference (The Beer Store) | Ottawa | Foreign Interference | Animal
11061 | 2007 | 8 | 15 | 0.42153 |  | 108 | 5 | 3 | Bronson | 4.16kV | SB05 | Transformer #OTT2538 located at 170 Fourth Ave isolated due to pole change | Ottawa | Scheduled Outage | Construction
11080 | 2007 | 8 | 16 | 0.54514 |  | 55 | 3 | 3 | Bronson | 4.16kV | SB05 | Transformer #OTT2538 located at 170 Fourth Ave isolated to change pole | Ottawa | Scheduled Outage | Construction
11087 | 2007 | 8 | 17 | 0.60069 |  | 65 | 13 | 12 | Bronson | 4.16kV | SB05 | Isolated transformer X31332 at 186 Fourth Ave to reconnect service | Ottawa | Scheduled Outage | Emergency Services Request
9024 | 2006 | 8 | 22 | 0.62153 |  | 125 | 27 | 13 | Bronson | 4.16kV | SB05 | At 14:55 trans OTT2542 at 188 Fourth Ave was isolated in order to replace open wire service with tplx | Ottawa | Scheduled Outage | Preventive Maintenance
19077 | 2011 | 9 | 2 | 0.38542 |  | 48 | 11 | 14 | BRONSON | 4.16kV | SB05 | Transformer X27743 at 16 Rupert St. Isolated for service change | Ottawa | Scheduled Outage | Construction
7295 | 2005 | 9 | 8 | 0.84722 |  | 174 | 26 | 9 | Bronson | 4.16kV | SB05 | Cable dig in at 147 Fifth required isolation for repair. | Ottawa | Foreign Interference | Dig-in
9294 | 2006 | 9 | 24 | 0.59861 |  | 11 | 53 | 287 | Bronson | 4.16kV | SB05 | Circuit was incorrectly identified by System on drawings when overhead crew requested and emergency trip of circuit due to primary conductor down | Ottawa | Human Element | Switching Errors
11433 | 2007 | 10 | 1 | 0.54861 |  | 100 | 12 | 7 | Bronson | 4.16kV | SB05 | Isolated and replaced transformer OTT4908 at 545 Percy St (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
11443 | 2007 | 10 | 2 | 0.55208 |  | 155 | 36 | 14 | Bronson | 4.16kV | SB05 | Isolated and removed transformer OTT6853 at 39 Adelaide St and transformer OTT6854 at 25 Adelaide St Installed one new transformer to replace the two that were removed | Ottawa | Scheduled Outage | Construction
11463 | 2007 | 10 | 4 | 0.375 |  | 145 | 17 | 7 | Bronson | 4.16kV | SB05 | Transformer #55D4A-0173 located at 236 Fourth Ave isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
19432 | 2011 | 10 | 20 | 0.81458 |  | 71 | 83 | 70 | Bronson DS |  | SB05 | Crew established PC10A# 4388 to isolate a single phase radial line to clear a tree that had fallen on the lines. | Ottawa | Tree Contacts | Tree Fallen
11640 | 2007 | 11 | 1 | 0.1125 |  | 283 | 104 | 22 | Bronson | 4.16kV | SB05 | Fallen tree took down primary & secondary conductors between 1st & 2nd Aves west of Percy during high winds. Oncall crews repaired circuit and restored power. | Ottawa | Tree Contacts | Tree Fallen
19537 | 2011 | 11 | 7 | 0.47222 |  | 13 | 2 | 10 | Bronson | 4.16kV | SB05 | Transfromer #X31393 located at 266 Second Ave opened by crew to remove a service | Ottawa | Scheduled Outage | Construction
17249 | 2010 | 11 | 9 | 0.44792 |  | 25 | 6 | 14 | Bronson | 4.16kV | SB05 | Transformer #X37970 located at 311 First opened by crew for a change over | Ottawa | Scheduled Outage | Construction
4514 | 2003 | 11 | 24 | 0.88264 |  | 51 | 17 | 20 | SB | 4.16kV | SB05 | Tx OTT3296 @ 3 Howick st was opened to clear tree limb from wires | Ottawa | Tree Contacts | Tree Limb Fallen
15417 | 2009 | 11 | 24 | 0.26667 |  | 251 | 167 | 40 | Bronson |  | SB05 | Cable section between S14343 & S28051 isolated to splice new section at Dip1 & Dip2. Bronson (SB05). ID#15417 | Ottawa | Scheduled Outage
6013 | 2004 | 12 | 11 | 0.086806 |  | 80 | 383 | 287 | Bronson | 4.16kV | SB05 | Opened circuit for crew to repair downed primary on Adelaide. | Ottawa | Adverse Weather
19714 | 2011 | 12 | 12 | 0.54514 |  | 95 | 8 | 5 | Bronson | 4.16kV | SB05 | At 13:05 crews isolated transformer in front of 197 Fourth Ave to rearrange some secondary. 5 customers affected for 95 mins. Bronson SB05 ID# 19714 | Ottawa | Scheduled Outage
6097 | 2004 | 12 | 25 | 0.043056 |  | 290 | 1387 | 287 | Bronson | 4.16kV | SB05 | SB05 line was opened by SCADA at request of Fire Dep't to fight a fire at 60 Fifth Ave. Power was restored when fire brought under control and ice cleared off the line. | Ottawa | Adverse Environment | Fire
15633 | 2010 | 1 | 8 | 0.69444 |  | 30 | 4 | 9 | Bronson | 4.16kV | SB06 | Isolated transformer X31309 at 36 Fouth Ave to replace connections on a secondary service | Ottawa | Scheduled Outage | Emergency Services Request
7791 | 2006 | 1 | 10 | 0.52778 |  | 95 | 17 | 11 | Bronson | 4.16kV | SB06 | Transformer #OTT6265 located at 46 Third Ave isolated due to re-arranging secondary | Ottawa | Scheduled Outage | Repair
15666 | 2010 | 1 | 18 | 0.60486 |  | 470 | 673 | 90 | Bronson | 4.16kV | SB06 | SB06 red and white phase local feeding customers on First ave. and Glebe ave was opened for fire dept to fight fire at 114 glebe. | Ottawa | Adverse Environment | Fire
10131 | 2007 | 3 | 14 | 0.54514 |  | 25 | 148 | 356 | Bronson | 13.2kV | SB06 | Tree Limb caused SB06 breaker to trip and SB02 breaker to auto reclose. Limb Cleared and power restored on SB06 line | Ottawa | Tree Contacts | Tree Limb Fallen
12148 | 2008 | 3 | 17 | 0.42014 |  | 55 | 3 | 3 | BRONSON | 4.16kV | SB06 | Transformer #X30069 isolated to allow for transfer of services to another transformer. Transformer to be removed. | Ottawa | Scheduled Outage | Construction
17913 | 2011 | 4 | 12 | 0.54167 |  | 21 | 5 | 13 | Bronson | 4.16kV | SB06 | Transformer X31310 at 17 Fourth Ave isolated for relocation of plant for pole change | Ottawa | Scheduled Outage | Construction
17914 | 2011 | 4 | 12 | 0.55208 |  | 50 | 7 | 8 | Bronson | 4.16kV | SB06 | Transformer X29982 at 607 O'Connor St. Isolated for relocation of plant for pole change | Ottawa | Scheduled Outage | Construction
17939 | 2011 | 4 | 15 | 0.375 |  | 135 | 7 | 3 | Bronson | 4.16kV | SB06 | Transformer X29984 at 19 Fifth Ave isolated by Doug McKay for rearrangement of plant | Ottawa | Scheduled Outage | Construction
20422 | 2012 | 4 | 30 | 0.71111 |  | 47 | 9 | 11 | Bronson | 4.16kV | SB06 | Transformer X31304 at 46 Third Ave. isolated by on-call crew to complete service upgrade | Ottawa | Scheduled Outage
20432 | 2012 | 5 | 1 | 0.72917 |  | 41 | 8 | 11 | Bronson | 4.16kV | SB06 | Transformer X31304 at 46 Third Ave. isolated for contractor renovations | Ottawa | Scheduled Outage
18106 | 2011 | 5 | 6 | 0.39583 |  | 120 | 18 | 9 | Bronson | 4.16kV | SB06 | Isolated transformer X31316 at 23 Fourth Ave to re-arrange the hydro plant | Ottawa | Scheduled Outage | Construction
18138 | 2011 | 5 | 12 | 0.42014 |  | 39 | 6 | 9 | Bronson | 4.16kV | SB06 | Transformer X31316 at 23 Fourth Ave was open to allow crew to replace broken pole. 9 customers were affected. Bronson (SB06) | Ottawa | Scheduled Outage
3531 | 2003 | 6 | 6 | 0.6875 |  | 136 | 18 | 8 | Bronson | 4.16kV | SB06 | defective transformer cut-out replaced. Transformer checked OK. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18308 | 2011 | 6 | 6 | 0.43056 |  | 270 | 58 | 13 | Bronson | 4.16kV | SB06 | Transformer X31310 at 15 Fourth Ave was opened to allow crews to re-configure the primary. | Ottawa | Scheduled Outage | Construction
18344 | 2011 | 6 | 8 | 0.74236 |  | 391 | 528 | 81 | Bronson | 4.16kV | SB06 | Fallen trees in the rear of 171 First Ave. Took down a span of primary conductor. The affected overhead section was isolated and repaired. | Ottawa | Tree Contacts | Tree Limb Fallen
18383 | 2011 | 6 | 10 | 0.54514 |  | 85 | 18 | 13 | BRONSON | 4.16kV | SB06 | X31302 at 34 Third Ave. Isolated to cut away existing pole to make room for new one | Ottawa | Scheduled Outage | Construction
18569 | 2011 | 7 | 1 | 0.49028 |  | 44 | 59 | 81 | Bronson | 4.16kV | SB06 | Customer reported tree limb that was broken in wind storm a few weeks ago fell out of the tree causing 2 phases to be pushed together and open 2 line switches at 171 First Ave | Ottawa | Tree Contacts | Tree Limb Fallen
14823 | 2009 | 7 | 24 | 0.46875 |  | 40 | 10 | 15 | Bronson | 4.16kV | SB06 | Transformer #X30454 located at 109 First isolated to remove a service | Ottawa | Scheduled Outage | Construction
11060 | 2007 | 8 | 15 | 0.38542 |  | 245 | 225 | 55 | Bronson | 8/4.8kV | SB06 | At 1st Ave. & Glebe Ave. between Bank and O'Connor a red phase switch and a white phase switch was isolated to install a pole and transfer plant. | Ottawa | Scheduled Outage | Construction
11076 | 2007 | 8 | 16 | 0.37014 |  | 194 | 26 | 8 | Bronson | 4.16kV | SB06 | At 08:53 trans at 114 Glebe Ave was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
8994 | 2006 | 8 | 17 | 0.52708 |  | 481 | 80 | 10 | Bronson | 4.16kV | SB06 | Transformer #P288 located at 724 Bank St isolated:insert was defective & transformer was replaced | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18958 | 2011 | 8 | 18 | 0.39931 |  | 65 | 36 | 33 | Bronson | 4.16kV | SB06 | Transformer #X34696 located at 157 First Ave opened by crew for a disconnect/reconnect | Ottawa | Scheduled Outage | Construction
18994 | 2011 | 8 | 22 | 0.52083 |  | 70 | 15 | 13 | Bronson | 4.16kV | SB06 | Isolated transformer X31310 at 15 Fourth Ave to transfer hydro plant | Ottawa | Scheduled Outage | Construction
19054 | 2011 | 8 | 30 | 0.4375 |  | 150 | 28 | 11 | BRONSON | 4.16kV | SB06 | Transformers X29984/X29976/X29982 removed and new one installed | Ottawa | Scheduled Outage | Construction
19076 | 2011 | 9 | 2 | 0.375 |  | 143 | 31 | 13 | BRONSON | 4.16kV | SB06 | Transformer X31310 at 17 Fourth Ave isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
19100 | 2011 | 9 | 6 | 0.38194 |  | 120 | 16 | 8 | Bronson | 4.16kV | SB06 | Transformer #X31323 located at 20 Third opened by crew due to transferring plant | Ottawa | Scheduled Outage | Construction
19102 | 2011 | 9 | 6 | 0.53819 |  | 55 | 12 | 13 | Bronson | 4.16kV | SB06 | Transformer #X31302 located at 39 Third opened by crew due to transferring plant | Ottawa | Scheduled Outage | Construction
19107 | 2011 | 9 | 7 | 0.40972 |  | 134 | 18 | 8 | Bronson | 4.16kV | SB06 | Transformer #X31303 located at 28 third Ave opened by crew due to pole change | Ottawa | Scheduled Outage | Construction
19128 | 2011 | 9 | 9 | 0.39931 |  | 175 | 23 | 8 | Bronson | 4.16kV | SB06 | Trans X31306 was isolated in order to replace the exisitng transformer with a new one | Ottawa | Scheduled Outage | Preventive Maintenance
19143 | 2011 | 9 | 12 | 0.39931 |  | 115 | 15 | 8 | Bronson | 4.16kV | SB06 | Transformer #X31306 located at 1 Third Ave opened by crew to transfer plant for a pole change | Ottawa | Scheduled Outage | Construction
19187 | 2011 | 9 | 16 | 0.375 |  | 110 | 15 | 8 | Bronson | 4.16kV | SB06 | Transformer #X31323 located at 20 Third Ave opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
11335 | 2007 | 9 | 19 | 0.55 |  | 120 | 22 | 11 | Bronson | 4.16kV | SB06 | At 13:12 trans at 52 Fourth Ave was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
19206 | 2011 | 9 | 19 | 0.375 |  | 345 | 46 | 8 | Bronson | 4.16kV | SB06 | Transformer #X31303 located at 28 Third Ave opened by crew to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
9290 | 2006 | 9 | 24 | 0.45833 |  | 120 | 712 | 356 | Bronson | 4.16kV | SB06 | With the high winds the SB06 slapped together at th intersection O'Connor & Strathcona | Ottawa | Adverse Weather | Wind
11378 | 2007 | 9 | 25 | 0.048611 |  | 10 | 1 | 8 | Bronson | 4.16kV | SB06 | Transformer in front of #15 Fourth Ave opened to repair hot line ctamp connection | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11391 | 2007 | 9 | 26 | 0.4375 |  | 60 | 10 | 10 | Bronson | 4.16kV | SB06 | Transformer #OTT4749 located at 606 O'Connor St isolated due to transformer replacement | Ottawa | Scheduled Outage
11392 | 2007 | 9 | 26 | 0.38194 |  | 55 | 6 | 7 | Bronson | 4.16kV | SB06 | Transformer #OTT2544 located at 28 Fourth Ave isolated due to transformer replacement | Ottawa | Scheduled Outage
11424 | 2007 | 10 | 1 | 0.39583 |  | 120 | 34 | 17 | Bronson | 4.16kV | SB06 | Transformer #OTT2425 located at 170 First Ave isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
13382 | 2008 | 10 | 17 | 0.70833 |  | 30 | 2 | 5 | Bronson | 4.16kV | SB06 | Isolated transformer X31309 at 44 Fourth Ave to replace service | Ottawa | Scheduled Outage | Emergency Services Request
15280 | 2009 | 10 | 20 | 0.36806 |  | 15 | 8 | 33 | Bronson | 4.16kV | SB06 | Isolated transformer X34696 at 163 First Ave for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
4376 | 2003 | 11 | 3 | 0.48264 |  | 55 | 12 | 13 | Bronson | 4.16kV | SB06 | Transformer #6272, at 64 Third Avenue in Ottawa, was isolated to allow for the replacement on an open wire service. ID#4376 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4426 | 2003 | 11 | 11 | 0.44444 |  | 15 | 1 | 3 | Bronson | 4.16kV | SB06 | 1-3-7 Third Ave to install new service. | Ottawa | Scheduled Outage | Construction
11921 | 2008 | 1 | 10 | 0.40833 |  | 206 | 21 | 6 | BRONSON | 4.16kV | SB07 | Tranformer #25541 located at 246 Breezehill Ave isolated to allow for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11941 | 2008 | 1 | 16 | 0.42361 |  | 130 | 13 | 6 | Bronson | 4.16kV | SB07 | Isolated and replaced transformer at 169 Beech St | Ottawa | Scheduled Outage | Preventive Maintenance
11948 | 2008 | 1 | 17 | 0.40278 |  | 60 | 6 | 6 | Bronson | 4.16kV | SB07 | Isolated transformer 55D2C-0170 at 279 Breezehill Ave to re-arrange the hydro plant to install new pole | Ottawa | Scheduled Outage | Construction
11949 | 2008 | 1 | 17 | 0.52083 |  | 110 | 11 | 6 | Bronson | 4.16kV | SB07 | Isolated transformer 55D2C-0170 at 272 Breezehill Ave to replace pole | Ottawa | Scheduled Outage | Construction
4717 | 2004 | 1 | 20 | 0.39792 |  | 84 | 4 | 3 | BRONSON | 4.16kV | SB07 | AT TRANSFORMER #55D2C-0688 ONE LEG OF TRANSFORMER HAD BURNT OFF. TRANSFORMER ISOLATED TO ALLOW CREWS TO REPAIR SAME. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9958 | 2007 | 1 | 22 | 0.51736 |  | 45 | 1 | 1 | Bronson | 4.16kV | SB07 | Mark Brown isolated P 130 to replace broken lead to TRF. Switch @ 60 Beech | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11980 | 2008 | 1 | 25 | 0.39583 |  | 94 | 6 | 4 | Bronson | 4.16kV | SB07 | Transformer #X25538 located at 292 Breezehill isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
11985 | 2008 | 1 | 28 | 0.42014 |  | 205 | 34 | 10 | Bronson | 4.16kV | SB07 | Transformer X25541 at 270 Breezhill Ave was isolated to replace the pole | Ottawa | Scheduled Outage | Construction
11998 | 2008 | 1 | 31 | 0.38056 |  | 244 | 33 | 8 | Bronson | 4.16kV | SB07 | At 09:08 trans at 275 Breezehill Ave was isolated in order for a pole change | Ottawa | Scheduled Outage | Preventive Maintenance
15928 | 2010 | 4 | 13 | 0.28125 |  | 225 | 60 | 16 | Bronson | 4.16kV | SB07 | At 06:45 ..Trans at 167 Hickory St Ott failed ,, crew replaced with a new one , power restored at 10:30 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3385 | 2003 | 4 | 28 | 0.75139 |  | 28 | 0 | 1 | Bronson | 4.16kV | SB07 | P130 at 60 Beech isolated to replace a burnt lead. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18026 | 2011 | 4 | 28 | 0.57569 |  | 234 | 1665 | 427 | Bronson | 4.16kV | SB07 | SB07 auto-reclosed during wind/lightning storm and locked out. Close VIA scada and held. | Ottawa | Adverse Weather | Wind
8316 | 2006 | 5 | 18 | 0.49306 |  | 65 | 13 | 12 | Bronson | 4.16kV | SB07 | Scott Barkley opened transformer 55D2C-0107 at 88 Beech to do a transformer upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
10546 | 2007 | 6 | 7 | 0.41667 |  | 70 | 14 | 12 | BRONSON | 4.16kV | SB07 | Transformer #55D2C-0172 at 282 Breezehill Ave isolated to allow for transformer replacement | Ottawa | Scheduled Outage | Preventive Maintenance
10547 | 2007 | 6 | 7 | 0.375 |  | 48 | 3 | 4 | Bronson | 4.16kV | SB07 | Transformer #55D2C-0174 at 290 Breezhill isolated to allow for transformer change | Ottawa | Scheduled Outage | Preventive Maintenance
5355 | 2004 | 6 | 22 | 0.79167 |  | 227 | 26 | 7 | SB | 4.16kV | SB07 | Tx 55D2C-0465 & Tx X17704 at Carling & Loretta were opened to re-arrange wires for construction. | Ottawa | Scheduled Outage | Construction
10797 | 2007 | 7 | 5 | 0.41667 |  | 70 | 9 | 8 | Bronson | 4.16kV | SB07 | At 10:00 trans at 42 Bolton was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
10799 | 2007 | 7 | 5 | 0.4375 |  | 90 | 14 | 9 | Bronson | 4.16kV | SB07 | At 10:30 trans at 180 Beech was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Repair
18744 | 2011 | 7 | 17 | 0.80764 |  | 9 | 64 | 428 | Bronson | 4.16kV | SB07 | SB07 tripped during lightening storm. Closed back in 9 minutes later and held | Ottawa | Lightning
11221 | 2007 | 8 | 31 | 0.026389 |  | 25 | 2 | 5 | Bronson | 4.16kV | SB07 | Transformer at 238 Breeehill isolated to repair neutral wire. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13315 | 2008 | 10 | 3 | 0.48611 |  | 128 | 132 | 203 | Bronson | 4.16kV | SB07 | Scada indicated SB07 breaker opened, 24-7 crews dispatched to investigate. Vic Schnob reports that Pumper truck back swung boom of cement truck into Primary SB07 overhead section on Loretta Avenue between Carling and Hickory. John Streng of 24-7 opened a set of temp switches north on Loretta of S29596 and hung a PC10A # 4769 to make repairs to the overhead conductor on the ground that burnt off from contact. SBO7 re-energized through closing in breaker and picked up 188 customers of the 203 customers, 15 customers still remain out. PC10A#4769 surrendered all men and grounds are complete and system can restore back to normal. John Streng reports all power restored to the 15 customers on the SB07 circuit. | Ottawa | Foreign Interference | Vehicle
13421 | 2008 | 10 | 24 | 0.3125 |  | 115 | 12 | 6 | BRONSON | 4.16kV | SB07 | Isolated transformer X31610 at 234 Breezhill Ave for maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
19634 | 2011 | 11 | 25 | 0.47917 |  | 50 | 4 | 5 | Bronson | 4.16kV | SB07 | Transformer X34848 at 64 Young St. isolated to connect a service to a new house | Ottawa | Scheduled Outage | Construction
7687 | 2005 | 12 | 5 | 0.44444 |  | 30 | 5 | 10 | Bronson | 4.16kV | SB07 | Transformer 55DZC-0301 at 60 Champagne was isolated to install new service | Ottawa | Scheduled Outage | Construction
13768 | 2008 | 12 | 17 | 0.43056 |  | 70 | 20 | 17 | BRONSON | 4.16kV | SB07 | Transformer #TP5027 at 200 Lindenpark Pvt isolated to allow for new service installation | Ottawa | Scheduled Outage | Construction
13770 | 2008 | 12 | 17 | 0.48611 |  | 91 | 38 | 25 | BRONSON | 4.16kV | SB07 | Transformer # X25537 at 306 Breezehill isolated to allow for service upgrade | Ottawa | Scheduled Outage | Repair
19800 | 2012 | 1 | 8 | 0.71875 |  | 248 | 21 | 5 | Bronson | 4.16kV | SB09 | Transformer X26077 at 395 Third Avenue was isloated to allow crew to replace defective cut out Bronson (SB09) ID#19800 | Ottawa | Defective Equipment
8148 | 2006 | 4 | 13 | 0.48958 |  | 30 | 2 | 4 | Bronson | 4.16kV | SB09 | Dave Jones opened transformer at Second and Percy to replace connections; interrupting power to 4 customers. | Ottawa | Unknown/Other
12406 | 2008 | 5 | 7 | 0.375 |  | 30 | 4 | 7 | Bronson | 4.16kV | SB09 | Isolated transfomer X30037 at 50 CHRYSLER ST to install a new service | Ottawa | Scheduled Outage | Emergency Services Request
16071 | 2010 | 5 | 10 | 0.39583 |  | 15 | 3 | 13 | BRONSON | 4.16kV | SB09 | Transformer X30044 across from 818 Bronson Ave isolated to move services | Ottawa | Scheduled Outage | Construction
6536 | 2005 | 5 | 11 | 0.16597 |  | 121 | 4 | 10 | Bronson | 4.16kV | SB09 | Broken cutout feeding transformer at 365 First ave. opened transformer. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20545 | 2012 | 5 | 20 | 0.70972 |  | 185 | 9 | 3 | Bronson | 13.2kV | SB09 | Crew replaced defective Transformer at 780 Bronson | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5229 | 2004 | 5 | 31 | 0.54861 |  | 15 | 2 | 6 |  | 4.16kV | SB09 | Transformer at 260 Fourth Ave. was opened to allow load transfer. | Ottawa | Scheduled Outage | Construction
3806 | 2003 | 7 | 23 | 0.53125 |  | 45 | 3 | 4 | Bronson | 4.16kV | SB09 | The transformer at 400 Third Ave. was taken out of service to change an open wire secondary service. 4 customers were affected and restored at 13:30 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16598 | 2010 | 8 | 1 | 0.62847 |  | 63 | 8 | 8 | Bronson | 4.16kV | SB09 | Transformer #X30043 located at 375 Third opened by crew to replace switch and arrestor | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18993 | 2011 | 8 | 22 | 0.44444 |  | 65 | 10 | 9 | Bronson | 4.16kV | SB09 | Isolated transformer X30010 at 369 Thired Ave for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
19118 | 2011 | 9 | 8 | 0.40278 |  | 30 | 4 | 8 | Bronson | 4.16kV | SB09 | Trans at 375 Third Ave was isolated in order to remove tree limb | Ottawa | Tree Contacts | Tree Limb Fallen
9295 | 2006 | 9 | 24 | 0.60764 |  | 256 | 546 | 128 | Bronson | 4.16kV | SB09 | SB09 interupted due to primary wires down on Bronson | Ottawa | Tree Contacts | Tree Fallen
17050 | 2010 | 10 | 4 | 0.69931 |  | 24 | 4 | 11 | BRONSON | 4.16kV | SB09 | Transformer X30016 at 364 First Ave. Isolated to renew the primary connection and also check connections | Ottawa | Scheduled Outage | Repair
5853 | 2004 | 11 | 4 | 0.0069444 |  | 128 | 17 | 8 | Bronson | 4.16kV | SB09 | Fire Dep't reported service wire down across Bronson at second Ave area. 24/7 crew in Nepean for outage. J. Kelly called as on call supervisor and he went to check. Meterbase ripped off wall to 810 Bronson and transformer fuse blown at 55D2C-0219 affecting 8 customers on Bronson and Second Ave. Jim cut wire clear and rolled off road. 24/7 sent when done in Nepean and cleared service from transformer, then refused. | Ottawa | Foreign Interference | Vehicle
17328 | 2010 | 11 | 23 | 0.55556 |  | 45 | 9 | 12 | BRONSON | 4.16kV | SB09 | Transformer X29989 at 865 Bronson Ave isolated to repair live secondary | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19920 | 2012 | 1 | 30 | 0.33194 |  | 10 | 64 | 381 | Bronson | 4.16kV | SB10 | Patrol found no cause, breaker flagged on the blue phase instantaneous | Ottawa | Unknown/Other | No Apparent Cause
20036 | 2012 | 2 | 19 | 0.35417 |  | 20 | 3 | 9 | Bronson | 4.16kV | SB10 | Isolated transformer X25684 at 67 Aberdeen St to isolate secondary service feeding Giovannis Restaurant | Ottawa | Scheduled Outage | Repair
7973 | 2006 | 2 | 28 | 0.59167 |  | 168 | 3 | 1 | Bronson | 4.16kV | SB10 | Balloons made contact with o/h lines at dip pole to P498 @ 845 Carling ave. ( Dow Honda ). 2 blown lightning arrestors & 2 damaged cut-outs were replaced. | Ottawa | Foreign Interference | Foreign Object
14033 | 2009 | 3 | 10 | 0.47917 |  | 29 | 13 | 27 | BRONSON | 4.16kV | SB10 | transformer #X25745 at 69 Pamilla St. isolated to allow for re-arrangement of plant on pole | Ottawa | Scheduled Outage | Preventive Maintenance
12277 | 2008 | 4 | 14 | 0.26042 |  | 242 | 28 | 7 | BAYSWATER | 4.16kV | SB10 | Transformer X25523 across from 338 Preston St isolated to allow for pole change | Ottawa | Scheduled Outage | Repair
8170 | 2006 | 4 | 20 | 0.20486 |  | 195 | 81 | 25 | Bronson | 4.16kV | SB10 | The 3 phase overhead transformer at Preston & Beech was upgaded to a larger model. The 25 affected customers were on Preston, Beech & Norman. | Ottawa | Scheduled Outage | Preventive Maintenance
16037 | 2010 | 5 | 4 | 0.66875 |  | 37 | 12 | 20 | Bronson | 4.16kV | SB10 | A broken lead that feeds primary takeoff down Pamilla St. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20462 | 2012 | 5 | 4 | 0.375 |  | 120 | 34 | 17 | Bronson | 4.16kV | SB10 | Isolated transformer X25857 at 116 Pamilla St and X25858 at 120 Pamilla St to replace open wire secondary buss with triplex conductor for safety due to scaffolding that has been set up for work on the building on the corner of Pamilla St and Preston St | Ottawa | Scheduled Outage | Construction
14893 | 2009 | 8 | 3 | 0.22917 |  | 177 | 784 | 382 | BRONSON | 4.16kV | SB10 | Transformer blew open due to fire at 357 Preston, causing outage to 15 customers. SB10 circuit opened for OFD. | Ottawa | Adverse Environment | Fire
14894 | 2009 | 8 | 3 | 0.26806 |  | 131 | 520 | 238 | Bronson | 4.16kV | SB10 | SB10 circuit was opened for working clearance for fire dept. for fire at 357 Preston. | Ottawa | Scheduled Outage | Emergency Services Request
11504 | 2007 | 10 | 12 | 0.29167 |  | 105 | 42 | 24 | Bronson | 4.16kV | SB10 | Isolated and replaced transformer 55D2C-0519 at 54 Norman St (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9679 | 2006 | 11 | 17 | 0.46042 |  | 22 | 3 | 7 | Bronson | 4.16kV | SB10 | Isolated transformer OTT4850 at 128 Pamilla St to replace hot line clamp | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9733 | 2006 | 11 | 26 | 0.86181 |  | 14 | 1 | 6 | Bronson | 4.16kV | SB10 | 24/7 opened a transformer to renew connection at transformer. Customers were complaining of voltage surges. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7660 | 2005 | 11 | 28 | 0.39583 |  | 45 | 7 | 9 | Bronson | 4.16kV | SB10 | Transformer #55D2C-0603 located at 354 Preston St isolated to re-arrange some wiring | Ottawa | Scheduled Outage | Construction
7666 | 2005 | 11 | 30 | 0.27778 |  | 215 | 32 | 9 | Bronson | 4.16kV | SB10 | At 06:40 Trans at 367 Preston isolated to upgrade trans | Ottawa | Scheduled Outage | Preventive Maintenance
17560 | 2011 | 2 | 7 | 0.38889 |  | 60 | 11 | 11 | Bronson | 4.16kV | SB11 | Isolated transformer X30118 at 169 Powell Ave for service up-grade to 173 Powell Ave | Ottawa | Scheduled Outage | Emergency Services Request
20026 | 2012 | 2 | 16 | 0.94792 |  | 50 | 9 | 11 | Bronson |  | SB11 | crews found broken standoff pin at X30023, repaired then refused. 11 customers affected for 50 minutes. Bronson (SB11) | Ottawa | Defective Equipment
12209 | 2008 | 3 | 31 | 0.44514 |  | 14 | 2 | 10 | BRONSON | 4.16kV | SB11 | TRANSFORMER X25872 ISOLATED TO ALLOW CITY TO PERFORM A BREAKER CHANGE | Ottawa | Scheduled Outage
3398 | 2003 | 5 | 2 | 0.61458 |  | 15 | 1 | 4 | Bronson | 4.16kV | SB11 | Opened transformer at 322 clemow to allow disconnection of cutomer in arrears. | Ottawa | Scheduled Outage | Load Shedding
3447 | 2003 | 5 | 15 | 0.42361 |  | 70 | 14 | 12 | Bronson | 4.16kV | SB11 | Transformer feeding 12 customers was opened to replace service at 48 Renfrew. | Ottawa | Scheduled Outage
5217 | 2004 | 5 | 29 | 0.17917 |  | 14 | 46 | 195 | Bronson | 4.16kV | SB11 | Circuit SB11 manually opened to allow for the removal of a dead tree which is very close to the circuit. | Ottawa | Adverse Environment
3560 | 2003 | 6 | 12 | 0.81944 |  | 124 | 10 | 5 | Bronson | 4.16kV | SB11 | Transformer 5024 at 272 Powell ave in Ottawa was replaced due to oil leaks. | Ottawa | Scheduled Outage | Equipment Failure - Cause Unknown
14954 | 2009 | 8 | 17 | 0.41667 |  | 90 | 27 | 18 | Bronson | 4.16kV | SB11 | Transformer #X30084 located at 26 Renfrew isolated to replace transformer | Ottawa | Scheduled Outage | Construction
5785 | 2004 | 9 | 7 | 0.5 |  | 74 | 2 | 2 | Bronson | 4.16kV | SB11 | The transformer at 68 Chamberlain was take out of service to replace a defective connection. 2 customers at 68 & 72 Chamberlain were affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11397 | 2007 | 9 | 27 | 0.52639 |  | 97 | 11 | 7 | Bronson | 4.16kV | SB11 | At 12:38 trans OTT2773 was isolated in order to replace PCB trans | Ottawa | Scheduled Outage | Preventive Maintenance
17037 | 2010 | 10 | 1 | 0.46528 |  | 107 | 12 | 7 | Bronson | 4.16kV | SB11 | Transformer #X30049 located at 66 Glendale opened by crew to re-do connections | Ottawa | Scheduled Outage | Construction
9364 | 2006 | 10 | 2 | 0.41667 |  | 35 | 5 | 9 | Bronson | 4.16kV | SB11 | Isolated transformer 55D2D-0751 at 129 Powell Ave to replace connections on the service | Ottawa | Scheduled Outage | Repair
11440 | 2007 | 10 | 2 | 0.375 |  | 130 | 11 | 5 | Bronson | 4.16kV | SB11 | At 09:00 trans at 302 Clemow was isolated for PCB trans replacement | Ottawa | Scheduled Outage
4245 | 2003 | 10 | 11 | 0.54931 |  | 94 | 17 | 11 | Bronson | 4.16kV | SB11 | Defective switch on transformer at 83 Renfrew St. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6054 | 2004 | 12 | 12 | 0.38542 |  | 240 | 32 | 8 | Bronson | 4.16kV | SB11 | Planned outage to transformer at 30 Chamberlain, isolated to replace a pole. | Ottawa | Scheduled Outage | Repair
19729 | 2011 | 12 | 16 | 0.54861 |  | 35 | 2 | 4 | Bronson | 4.16kV | SB11 | At 13:10 crews isolated transformer at 320 Clemow Ave for service up-grade. Bronson SB11 ID# 19729 | Ottawa | Scheduled Outage
19900 | 2012 | 1 | 26 | 0.375 |  | 135 | 61 | 27 | Bronson | 4.16kV | SB12 | SB12 circuit at the rear of Merritt was isolated to allow crew to replace poles. | Ottawa | Scheduled Outage | Construction
19923 | 2012 | 1 | 30 | 0.375 |  | 135 | 32 | 14 | Bronson | 4.16kV | SB12 | Transformer X29908 at 217 McGillivray St. isolated by Black & Mac to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
15933 | 2010 | 4 | 14 | 0.5625 |  | 40 | 7 | 10 | BRONSON | 4.16kV | SB12 | Transformer X31321 at 55 Fourth Ave. isolated to allow for new service | Ottawa | Scheduled Outage | Construction
18818 | 2011 | 7 | 25 | 0.86111 |  | 11 | 2 | 9 | Bronson | 4.16kV | SB12 | Transformer #X26689 located at 86 Fourth Ave opened by crew to replace hot line clamp | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18901 | 2011 | 8 | 10 | 0.38542 |  | 45 | 7 | 9 | Bronson | 4.16kV | SB12 | Transformer #X26689 located at 86 Fourth opened by crew to replace all connections | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
18920 | 2011 | 8 | 13 | 0.65417 |  | 68 | 6 | 5 | BRONSON | 4.16kV | SB12 | Transformer X29977 at 17 Fifth Ave. Opened due to defective switch. | Ottawa | Defective Equipment
18953 | 2011 | 8 | 17 | 0.39583 |  | 145 | 22 | 9 | Bronson | 4.16kV | SB12 | Transformer X31309 at 41 Fourth Ave. was isolated to allow crew to transfer plant to a new pole. | Ottawa | Scheduled Outage | Construction
19515 | 2011 | 11 | 2 | 0.375 |  | 5 | 3 | 31 | Bronson | 4.16kV | SB12 | At 9:00am crew opened S25232 White phase at 20 Clegg to transfer the customers temporarly to the Red Phase. 31 customers affected for 5 mins. Bronson SB12 ID# 19515 | Ottawa | Scheduled Outage | Construction
17214 | 2010 | 11 | 3 | 0.375 |  | 265 | 62 | 14 | Bronson | 4.16kV | SB12 | Trans outage at 75 FOURTH AVE OTTAWA for pole change // transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
19546 | 2011 | 11 | 9 | 0.35417 |  | 68 | 12 | 11 | Bronson | 4.16kV | SB12 | Transformer #X29901 located at 16 Clegg opened by crew to replace pole | Ottawa | Scheduled Outage | Construction
19583 | 2011 | 11 | 15 | 0.60417 |  | 15 | 18 | 72 | Bronson | 4.16kV | SB12 | Isolated S25232 at 20 Clegg St for pole replacment | Ottawa | Scheduled Outage | Construction
13635 | 2008 | 11 | 18 | 0.39236 |  | 110 | 13 | 7 | BRONSON | 4.16kV | SB12 | Isolated and replaced transformer X31319 at 46 Fourth Ave | Ottawa | Scheduled Outage | Preventive Maintenance
11896 | 2008 | 1 | 4 | 0.26389 |  | 10 | 33 | 200 | Bronson | 4.16kV | SB13 | Failed lightning arrester at 319 Powell. Breaker opened and locked out. No police or fire calls breaker closed from SCADA. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9920 | 2007 | 1 | 12 | 0.84375 |  | 10 | 4 | 22 | Bronson | 4.16kV | SB13 | Isolated transformer OTT2177 at 205 Plymouth St and replaced hot line clamp | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8117 | 2006 | 4 | 7 | 0.58472 |  | 43 | 10 | 14 | Bronson | 4.16kV | SB13 | Fuse to transformer OTT5286 at 123 Renfrew Ave opened due to squirrel | Ottawa | Foreign Interference | Animal
16272 | 2010 | 6 | 16 | 0.69792 |  | 15 | 3 | 11 | Bronson | 4.16kV | SB13 | Isolated transformer X25772 at the corner of Bell St and Plymouth St to replace secondary connections | Ottawa | Scheduled Outage | Preventive Maintenance
20829 | 2012 | 6 | 22 | 0.375 |  | 85 | 35 | 25 | Bronson | 4.16kV | SB13 | Transformer #X34732 located at 319 Lebreton St opened by crew to install new wire | Ottawa | Scheduled Outage | Construction
5417 | 2004 | 7 | 1 | 0.62292 |  | 95 | 317 | 200 | Bronson | 4.16kV | SB13 | Neutral and 1 phase tangled on Bronson, cleared and re-energized by SCADA | Ottawa | Adverse Weather | Wind
6985 | 2005 | 7 | 17 | 0.86458 |  | 92 | 14 | 9 | Bronson | 4.16kV | SB13 | Replaced transformer secondary connection for at 12 Orangeville. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18842 | 2011 | 7 | 28 | 0.36806 |  | 25 | 6 | 15 | Bronson | 4.16kV | SB13 | Isolated transformer X25762 at 13 Henry St for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
18873 | 2011 | 8 | 3 | 0.39583 |  | 38 | 6 | 9 | Bronson | 4.16kV | SB13 | Trans X25759 at 326 Powell Ave was isolated in order to change over a secondary service | Ottawa | Scheduled Outage | Preventive Maintenance
5915 | 2004 | 11 | 22 | 0.46181 |  | 25 | 10 | 24 | Bronson | 4.16kV | SB13 | Transformer 979 @ 690 Bronson isolated for service. | Ottawa | Scheduled Outage | Preventive Maintenance
20187 | 2012 | 3 | 21 | 0.27361 |  | 39 | 315 | 484 | Bronson | 4.16kV | SB14 | Ottawa fire requested the SB14 line in front of 266 Rochester to be isolated due to fire. Bronson ID#20187 | Ottawa | Adverse Environment | Fire
17811 | 2011 | 3 | 31 | 0.47222 |  | 127 | 32 | 15 | Bronson |  | SB14 | K527 at 301 Rochester was opened at the request of the customer | Ottawa | Scheduled Outage | Repair
17816 | 2011 | 4 | 1 | 0.38889 |  | 90 | 28 | 19 | Bronson | 4.16kV | SB14 | K452 at 817 Gladstone was opened at customer's request | Ottawa | Scheduled Outage | Preventive Maintenance
17832 | 2011 | 4 | 5 | 0.42014 |  | 63 | 9 | 9 | Bronson | 4.16kV | SB14 | Kisok K528 at 498 Booth St was open to allow contractor to replace customer main disonnect. 9 customers were affected for 63 minutes. | Ottawa | Scheduled Outage
4975 | 2004 | 4 | 6 | 0.5 |  | 85 | 24 | 17 | Bronson | 4.16kV | SB14 | O/H transformer at 86 Poplar interrupted to replace service. | Ottawa | Scheduled Outage | Repair
17857 | 2011 | 4 | 8 | 0.44792 |  | 105 | 63 | 36 | Bronson | 4.16kV | SB14 | Kiosk K00448 at 71 Raymond was isolated for electrician to perform planned work. Fed from SB14, 4.16 kV. 36 customer were affected | Ottawa | Scheduled Outage
17881 | 2011 | 4 | 11 | 0.39792 |  | 122 | 16 | 8 | Bronson | 4.16kV | SB14 | Transformer X31701 at 32 Balsam St isolated to allow contractor to do maintenance work | Ottawa | Scheduled Outage | Preventive Maintenance
17920 | 2011 | 4 | 13 | 0.35417 |  | 73 | 19 | 16 | Bronson | 4.16kV | SB14 | Trans K449 at 498 Booth St was isolated for elec to make repairs | Ottawa | Scheduled Outage | Preventive Maintenance
14413 | 2009 | 5 | 26 | 0.44792 |  | 12 | 3 | 16 | Bronson | 4.16kV | SB14 | Transformer #K449 located at 353 Rochester isolated for crew to get a PCB oil sample | Ottawa | Scheduled Outage | Preventive Maintenance
10488 | 2007 | 5 | 31 | 0.42917 |  | 107 | 14 | 8 | BRONSON |  | SB14 | Transformer #OTT128 located at 70 Anderson Street isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
10781 | 2007 | 7 | 3 | 0.42639 |  | 332 | 66 | 12 | Bronson | 4.16kV | SB14 | K452 @ 34 Balsam Ave isolated to allow City contractor to excavate around transformer. | Ottawa | Scheduled Outage | Construction
11167 | 2007 | 8 | 28 | 0.38542 |  | 125 | 25 | 12 | Bronson | 4.16kV | SB14 | Isolated and replaced transformer 55D2A-0570 at 76 Poplar St (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
19155 | 2011 | 9 | 13 | 0.49306 |  | 136 | 79 | 35 | Bronson | 4.16kV | SB14 | Transformer K448 at 71 Raymond was isolated to allow contractor to excavate near transformer. | Ottawa | Scheduled Outage | Construction
13307 | 2008 | 10 | 1 | 0.44583 |  | 93 | 56 | 36 | BRONSON | 4.16kV | SB14 | Transformer # X31779 at 90 Willow St. isolated to allow for panel upgrade | Ottawa | Scheduled Outage | Construction
11470 | 2007 | 10 | 5 | 0.29514 |  | 105 | 10 | 6 | Bronson | 4.16kV | SB14 | Transformer #55D2A-0180 located at 388 Booth St isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
4289 | 2003 | 10 | 17 | 0.41667 |  | 15 | 5 | 20 | Bronson | 4.16kV | SB14 | Transformer at Willow and rochester was opened to replace a hot line clamp on o/h at 119 Willow. | Ottawa | Defective Equipment
4557 | 2003 | 12 | 4 | 0.38542 |  | 125 | 79 | 38 | SB | 4.16kV | SB14 | K448 @ 69 Raymond was opened to replace pole. | Ottawa | Defective Equipment
4566 | 2003 | 12 | 5 | 0.45139 |  | 44 | 28 | 38 | Bronson | 4.16kV | SB14 | Transformer 448 at 69 Raymond transfer over to new equipment. | Ottawa | Scheduled Outage | Construction
4577 | 2003 | 12 | 8 | 0.375 |  | 146 | 92 | 38 | Bronson | 4.16kV | SB14 | Transformer relocated to a new pole in the rear of 69 Raymond. ID#4577 | Ottawa | Scheduled Outage | Construction
4578 | 2003 | 12 | 8 | 0.375 |  | 146 | 32 | 13 | Bronson | 4.16kV | SB14 | Transformer relocated to a new pole at 534 Booth. ID#4578 | Ottawa | Scheduled Outage | Construction
4588 | 2003 | 12 | 10 | 0.41667 |  | 120 | 20 | 10 | Bronson | 4.16kV | SB14 | Transformer opposite 437 Booth was opened to transfer plant to new pole. 10 cust. | Ottawa | Scheduled Outage
11893 | 2007 | 12 | 31 | 0.60069 |  | 65 | 25 | 23 | Bronson | 4.16kV | SB14 | Broken switch to transformer on pole location number X25589 at 169 Rochester St | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4771 | 2004 | 2 | 8 | 0.94097 |  | 15 | 1 | 4 | Bronson | 4.16kV | SB16 | Defective cutout on transformer 245649 at 201 Third Av. At Percy | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10126 | 2007 | 3 | 14 | 0.37708 |  | 47 | 9 | 12 | Bronson | 4.16kV | SB16 | Jeff MaGee isolated TRF. @ 220 3rd Ave. to do a service upgrade | Ottawa | Scheduled Outage | Repair
20237 | 2012 | 3 | 27 | 0.20833 |  | 90 | 10 | 7 | Bronson | 4.16kV | SB16 | Transformer X31390 at 166 Second was isolated to allow crew to transfer plant to new pole | Ottawa | Scheduled Outage
20337 | 2012 | 4 | 17 | 0.35417 |  | 240 | 96 | 24 | Bronson | 4.16kV | SB16 | Transformer #X26241 located at 64 Second Ave opened by crew for pole replacement | Ottawa | Scheduled Outage | Construction
20338 | 2012 | 4 | 17 | 0.35417 |  | 240 | 80 | 20 | Bronson | 4.16kV | SB16 | Transformer #X31314 located at 80 Second Ave opened by crew for pole replacement | Ottawa | Scheduled Outage
20347 | 2012 | 4 | 18 | 0.35417 |  | 240 | 56 | 14 | Bronson | 4.16kV | SB16 | Transformer X30071 at 38 Second Ave. isolated to allow for pole change | Ottawa | Scheduled Outage | Construction
20348 | 2012 | 4 | 18 | 0.35417 |  | 240 | 20 | 5 | Bronson | 4.16kV | SB16 | Transformer #X30052 located at 30 Second Ave opened by crew for a pole replacement | Ottawa | Scheduled Outage | Construction
20349 | 2012 | 4 | 18 | 0.35417 |  | 240 | 36 | 9 | Bronson | 4.16kV | SB16 | Transformer #X30061 located at 46 Second Ave opened by crew for a pole replacement | Ottawa | Scheduled Outage | Construction
20382 | 2012 | 4 | 24 | 0.54167 |  | 180 | 42 | 14 | Bronson | 4.16kV | SB16 | Isolated transformer X30068 at 330 Queen Elizabeth Dr to transfer Hydro plant | Ottawa | Scheduled Outage | Construction
20383 | 2012 | 4 | 24 | 0.54167 |  | 180 | 27 | 9 | Bronson | 4.16kV | SB16 | Isolated transformer X30072 at 22 Second Ave to transfer Hydro Plant | Ottawa | Scheduled Outage | Construction
16075 | 2010 | 5 | 11 | 0.40278 |  | 61 | 12 | 12 | Bronson | 4.16kV | SB16 | Transfomer X31375 at 184 Second Ave isolated for service upgrade | Ottawa | Scheduled Outage | Construction
14631 | 2009 | 6 | 27 | 0.83681 |  | 50 | 0 | 14 | Bronson | 4.16kV | SB16 | At 20:05 transformer X30071 at 38 Second Ave had a deffective cut out switch. 14 customers were affected for 50 minutes. | Nepean | Defective Equipment
16647 | 2010 | 8 | 4 | 0.65347 |  | 62 | 1 | 1 | Bronson | 4.16kV | SB16 | SB16 breaker tripped during heavy rain & lightning. Breaker closed manually from SCADA. | Ottawa | Unknown/Other
13180 | 2008 | 9 | 2 | 0.75 |  | 15 | 2 | 7 | Bronson | 4.16kV | SB16 | Isolated transformer X31394 At 233 Third Ave to cut service clear feeding 529 Percy St | Ottawa | Scheduled Outage | Repair
13186 | 2008 | 9 | 3 | 0.57708 |  | 37 | 4 | 7 | BRONSON | 4.16kV | SB16 | transformer X31394 at 529 Percy isolated to allow for repairs to service damaged by a contractor | Ottawa | Scheduled Outage | Repair
11387 | 2007 | 9 | 26 | 0.375 |  | 205 | 14 | 4 | Bronson | 4.16kV | SB16 | The SB16 B O/H line on Glebe at Lyon was isolated to allow contractor to trim the trees. | Ottawa | Scheduled Outage | Preventive Maintenance
11398 | 2007 | 9 | 27 | 0.39931 |  | 99 | 5 | 3 | Bronson | 120/240 | SB16 | At 09:35 trans at 819 Lyon St was isolated in order for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15225 | 2009 | 10 | 7 | 0.35139 |  | 89 | 7 | 5 | Bronson | 4.16kV | SB16 | Transformer #X31348 located at 187 Third Ave isolated due to defective switch | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19647 | 2011 | 11 | 28 | 0.54861 |  | 85 | 7 | 5 | Bronson | 4.16kV | SB16 | Isolated transformer X31348 at 191 Third Ave to replace pole | Ottawa | Scheduled Outage | Construction
15542 | 2009 | 12 | 22 | 0.375 |  | 60 | 13 | 13 | Bronson | 4.16kV | SB16 | At 09:00 trans at 173 Second Ave was isolated to replace sec service | Ottawa | Scheduled Outage | Preventive Maintenance
15601 | 2010 | 1 | 2 | 0.60556 |  | 268 | 4 | 1 | Bronson | 4.16kV | SBO2 | crew replaced defective cutout at 200 Isabella feeding V421. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9966 | 2007 | 1 | 24 | 0.91458 |  | 473 | 95 | 12 | Albion | 13.2kV | SC1001 | A defective transformer KT210 at 1027 Karsh Drive was replaced. There was no access in the customer yard due to a swimming pool. A crane was called in to assist the crew. | Ottawa | Defective Equipment
6702 | 2005 | 6 | 12 | 0.60208 |  | 133 | 33 | 15 | Albion | 13.2kV | SC1001/2206 | Transformer #KT335 at 6 Southland isolated due to a blown transformer fuse (cause unknown) | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8074 | 2006 | 3 | 29 | 0.42014 |  | 60 | 21 | 21 | Albion | 13.2kV | SC1002 | KT347 at 19 Horsdal was isolated to reposition the kiosk back on the pad properly. Kiosk had been recently involved in a vehicle accident. The 21 customers affected were on Horsdal & Ted Grant in the Hunt Club Park area of the city. | Ottawa | Scheduled Outage | Repair
8237 | 2006 | 5 | 5 | 0.7375 |  | 51 | 41 | 48 | Russell | 13.2kV | SC101 | Normal open point at KT49 96-2570 Southvale Cres insulator found broken. Causing cable section to go to ground, blowning fuse at riser pole. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19762 | 2011 | 12 | 25 | 0.84236 |  | 308 | 149 | 62 | Russell | 13.2kV | SC101 | A flash over insulators at Transformer KT54 @ 2610 Southvale. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16666 | 2010 | 8 | 4 | 0.65903 |  | 471 | 1546 | 197 | Russell | 13.2kV | SC101/5310 | W & B phases of SC101 were found blown after stormy weather passed through the area. Area affected: Russell rd / Southvale Cr. | Ottawa | Adverse Weather | Lightning
4669 | 2004 | 1 | 1 | 0.13333 |  | 393 | 96 | 27 | Russell | 13.2kV | SC102 | The remaining 7 customers were restored one at a time between 8:05 & 9:45. The cause was determined to be from mice, which caused a flash in SW190 at 951 Ages. The resulting flash caused a total of 6 fuses to blow. | Ottawa | Foreign Interference | Animal
9639 | 2006 | 11 | 11 | 0.39931 |  | 390 | 72 | 11 | Russell | 13.2kV | SC102 | PT118 at 2413 Stevenage was isolated for contractor to install new secondary conductor. Only the 1 apt bldg was affected. | Ottawa | Scheduled Outage | Construction
9562 | 2006 | 10 | 30 | 0.6875 |  | 30 | 12 | 25 | Russell | 13.2kV | SC102 (5310) | During switching to restore SC102 to normal, the blue phase fuse of SC102 blew when parrallel was made between Albion & Russell. A small number of single phase customers were affected as well as many 3 phase customers (part-out). | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5495 | 2004 | 7 | 14 | 0.38819 |  | 31 | 3 | 6 | Albion | 13.2kV | SC1101 | Transformer KT363 at the rear of 7 Depper was isolated to upgrade its service. | Ottawa | Scheduled Outage | Preventive Maintenance
3231 | 2003 | 3 | 7 | 0.49653 |  | 312 | 176 | 80 | Albion | 13.2kV | SC1202 | SC1202-F red phase fuse blew due to a defective termination to the secondary at KT303. 8 kiosks were affected in Dosseter. Pittaway, Notman & Blohm area. Fault indicators were checked, crew opened cable to KT303 at KT302 and refused and closed SC1202-F to pick up 5 kiosks. The remainig kiosks and cable sections were checked and the crew found a defective termination at KT303 to the secondary of the xfmr. They opened at KT303 and restored the remaining 2 kiosks. When repairs were made KT303 was restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6268 | 2005 | 3 | 11 | 0.61111 |  | 489 | 394 | 126 | Albion | 13.2kV | SC1502 | White phase fuse blew at SC15 interrupting power to 18 kiosks. The cause was determined to be a broken barrier board in KT7 which caused a flashover in the kiosk. Power was restored to 17 of the 18 kiosks at 17:30 and repairs were made to KT7. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11780 | 2007 | 11 | 28 | 0.38333 |  | 52 | 10 | 11 | ALBION | 13.2kV | SC1502 | Transformer #KT11 at 109 Country Club isolated to allow for maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
16880 | 2010 | 9 | 6 | 0.54861 |  | 100 | 2 | 1 | Woodroffe TW | 13.2kV | SC1572-01 | PT11feeding 2740 Queensview was isolated to make repairs to defective elbow & insert. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3748 | 2003 | 7 | 16 | 0.41667 |  | 80 | 16 | 12 | TR | 13.2kV | SC1576 | B.Kerfoot reports SC1576 Cable Red Phase restored to normal. 3 new transformers (MT1768, MT1769, MT1770) have been added to circuit between MT1684 to MT1685. | Ottawa | Scheduled Outage | Construction
16019 | 2010 | 4 | 29 | 0.63264 |  | 26 | 5 | 12 | Albion | 13.2kV | SC157801 | MT1655 at 76 Inverkip isolated to repair defective elbow & insert. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
15002 | 2009 | 8 | 24 | 0.62153 |  | 795 | 13 | 1 | Albion | 13.2kV | SC1601 | Defective primary cable to VT660 at 280 Hunt Club, Nav Canada caused all 3 phases to blow at supply dip S19420. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7342 | 2005 | 9 | 18 | 0.36528 |  | 78 | 130 | 100 | Albion | 13.2kV | SC1601 | Burnt cable terminations at SC1601-F caused 2 fuses to blow at SC2501F-SC1601. Approx 100 customers were interrupted in the Huntclub / Riverside area. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7510 | 2005 | 10 | 24 | 0.95833 |  | 584 | 37 | 11 | Albion | 13.2kV | SC1601 | Fuse blown to 220 Hunt Club & KT379. Suspect defective cable between the two place. Power was restored to KT379, but due to no access at 220 Hunt Club power restoration had to wait until dayshift for 220 Hunt Club. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6833 | 2005 | 6 | 30 | 0.40694 |  | 77 | 77 | 60 | Albion | 13.2kV | SC1602 | 13 kv kiosks KT160, 161, 162, 163, 164 & 165 in Hunt Club Woods were isolated to repair elbows. | Ottawa | Scheduled Outage | Repair
3693 | 2003 | 7 | 8 | 0.20625 |  | 253 | 122 | 29 |  | 13.2kV | SC1602 | Padmount transformer failed and needed replacing. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3750 | 2003 | 7 | 16 | 0.80208 |  | 31 | 5 | 9 | TA | 13.2kV | SC1602 (2207) | KT16 @ 11 Masters Dr was opened twice to repair U/G cable to pedestal & then again to repair loose connections at the pedestal. The first interruption was from 19:15 to 19:20, the second from 19:29 to 19:46. 9 customers on Uplands Dr & Masters Dr affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6330 | 2005 | 3 | 27 | 0.45903 |  | 34 | 10 | 18 | Riverdale | 13.2kV | SC2002 | Pole Switch for KT0269 at 1161 Rockingham Ave opened due to animal contact (squirrel) | Ottawa | Foreign Interference | Animal
14145 | 2009 | 4 | 4 | 0.88194 |  | 79 | 13 | 10 | Kilborn | 13.2kV | SC201 | Excessive vines caused transformer OTT1773 at 2242 Alta Vista to open. | Ottawa | Tree Contacts | Inadequate Trimming
5311 | 2004 | 6 | 15 | 0.4375 |  | 50 | 13 | 16 | Riverdale | 13.2kV | SC201 | Re- fused O/H transfomer at 178 Dahlia. | Ottawa | Tree Contacts
14601 | 2009 | 6 | 24 | 0.078472 |  | 56 | 10 | 11 | Riverdale | 13.2kV | SC201 | overhead transformer X28164 @ 1281 Cheverton opened for no apparent reason. | Ottawa | Unknown/Other | No Apparent Cause
12750 | 2008 | 6 | 26 | 0.74653 |  | 404 | 94 | 14 | Albion | 13.2kV | SC201 | At 5:55pm customers in the area of Kilborn and Essex were without power, 14 customers were affected by a tree hitting the overhead circuit, crews cleared the tree and power was restored at 1:33am on Friday morning. ID#12750. | Ottawa | Adverse Weather | Wind
12891 | 2008 | 7 | 18 | 0.24931 |  | 307 | 72 | 14 | Riverdale | 13.2kV | SC201 | Lightning strike at Beaver north of Livingston caused a single white phase switch to burn up. Switch was replaced and load restored. Normal feed to SC2 is 505. | Ottawa | Adverse Weather | Lightning
14824 | 2009 | 7 | 24 | 0.64514 |  | 56 | 7 | 8 | Riverdale | 13.2kV | SC201 | Replaced blown fuse feeding transformer X27482 (squirrel contact) | Ottawa | Foreign Interference | Animal
3900 | 2003 | 8 | 13 | 0.60069 |  | 35 | 4 | 6 | Albion | 4.16kV | SC201 | P. McEwan reports trans # 3958 isolated to replace deffective triplex st 2241 Lilac Lane. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18921 | 2011 | 8 | 13 | 0.65833 |  | 107 | 18 | 10 | Riverdale | 4.16kV | SC201 | Transformer X28229 had a defective termination on the cut out. Riverdale SC201) ID#188921 | Ottawa | Defective Equipment
4188 | 2003 | 9 | 30 | 0.38542 |  | 81 | 8 | 6 | Riverdale | 13.2kV | SC201 | Transformer #OTT6717 at 132 Winther in Ottawa was isolated due to an inadvertant contact by a squirrel. | Ottawa | Foreign Interference | Animal
11612 | 2007 | 10 | 28 | 0.059028 |  | 110 | 33 | 18 | Riverdale | 13.2kV | SC201 | crew replaced broken cutout to O/H transformer at 1304 kilborn. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11641 | 2007 | 11 | 1 | 0.28472 |  | 195 | 65 | 20 | Riverdale | 13.2kV | SC201 | Fallen tree pulled down primary single phase conductor in the back yard of 1255 Randall opening the fuse at Randall & Beaver. Two transformers interrupted. | Ottawa | Tree Contacts | Tree Fallen
7649 | 2005 | 11 | 23 | 0.38194 |  | 350 | 41 | 7 | Riverdale | 12/7.2kV | SC201 | Replaced defective transformer OTT130 at 2224 Alta Vista Dr | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9753 | 2006 | 11 | 30 | 0.19722 |  | 76 | 11 | 9 | Riverdale | 13.2kV | SC201 | Crew replaced broken cutout on transformer feeding customers on Livingstone & Randall. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17661 | 2011 | 3 | 2 | 0.38194 |  | 19 | 4 | 12 | Riverdale | 13.2kV | SC201/505 | Transformer #X28198 located at 1331 Essex isolted by crew to remove a branch off the buss | Ottawa | Tree Contacts | Tree Limb Fallen
16297 | 2010 | 6 | 25 | 0.475 |  | 56 | 12 | 13 | Riverdale | 13.2kV | SC201/505 | Transformer #X27820 located at 1377 Micmac opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
16354 | 2010 | 6 | 28 | 0.80069 |  | 142 | 19 | 8 | Riverdale | 13.2kV | SC201/505 | Transformer #X28233 located at 1227 Randall Ave opened up due to tree interference | Ottawa | Tree Contacts | Inadequate Trimming
8649 | 2006 | 7 | 2 | 0.75486 |  | 156 | 36 | 14 | Riverdale | 13.2kV | SC201/505 | Trees in backyard contacted and caused transformer cut out to open | Ottawa | Tree Contacts | Inadequate Trimming
8754 | 2006 | 7 | 18 | 0.98403 |  | 743 | 639 | 350 | Riverdale | 13.2kV | SC201/505 | SC201-L circuit was opened to allow crews to refuse overhead circuit. The cause of the blown fuse was later found at KT274, 2093 Lamira. The cable elbow had blown off the transformer. | Ottawa | Adverse Weather | Lightning
8856 | 2006 | 7 | 26 | 0.60972 |  | 72 | 14 | 12 | Riverdale | 12/7.2kV | SC201/505 | Trans at 1401 Micmac St islolated in order replace trans | Ottawa | Scheduled Outage | Preventive Maintenance
8908 | 2006 | 8 | 2 | 0.61458 |  | 70 | 9 | 8 | Riverdale | 13.2kV | SC201/505 | Transformer #KT181 located at 1472 Clementine isolated due to transormer replacement for PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
18204 | 2011 | 5 | 24 | 0.39028 |  | 170 | 167 | 59 | Riverdale | 13.2kV | SC202 | VT719 @ 1161 Belanger was isolated to allow contractor to perform vault maintenance. 59 customers were affetced. Riverdale (SC202) | Ottawa | Scheduled Outage
3528 | 2003 | 6 | 6 | 0.3625 |  | 74 | 42 | 34 | Riverdale | 13.2kV | SC202 | One line switch & one transformer switch found blown. Dead squirrel also on the ground. | Ottawa | Foreign Interference | Animal
14565 | 2009 | 6 | 18 | 0.50694 |  | 80 | 11 | 8 | Riverdale | 4.16kV | SC202 | Replaced blown fuse on transformer switch at 1498 Laselle St Squirrel contact | Ottawa | Foreign Interference | Animal
14571 | 2009 | 6 | 19 | 0.29375 |  | 67 | 18 | 16 | Riverdale | 4.16kV | SC202 | Refused swich feeding transformer OTT1514 at 1053 Secord Ave (Blown fuse due to tree branch) | Ottawa | Tree Contacts | Inadequate Trimming
7136 | 2005 | 8 | 14 | 0.475 |  | 31 | 4 | 8 | Riverdale | 13.2kV | SC202 | Switch to transformer OTT3827 at 1045 Apolydor Ave opened due to bird contact | Ottawa | Foreign Interference | Bird
19197 | 2011 | 9 | 18 | 0.47917 |  | 227 | 170 | 45 | Riverdale TS | 13.2kV | SC202 | A tree limb took down primary conductor on the SC202 blue phase run off. Riverdale TS ID# 19197 | Ottawa | Tree Contacts | Tree Limb Fallen
7350 | 2005 | 9 | 20 | 0.33333 |  | 125 | 10 | 5 | Riverdale | 4.16kV | SC202 | Transformer OTT5499 at 1184 Rockingham was isolated to relocate to new pole | Ottawa | Scheduled Outage | Construction
9314 | 2006 | 9 | 26 | 0.325 |  | 52 | 5 | 6 | Riverdale | 4.16kV | SC202 | Fuse to transformer OTT1513 at 1502 Clementine Blvd was found blown due to a crow | Ottawa | Foreign Interference | Bird
7441 | 2005 | 10 | 10 | 0.076389 |  | 120 | 56 | 28 | Riverdale | 13.2kV | SC202 | Combination of wind and trees caused a section of neutral conductor to fall down. 3 transformers E of Clementine, between Aldea & Guertin had to be interrupted to clear trees & repair neutral. | Ottawa | Adverse Weather | Wind
7865 | 2006 | 1 | 27 | 0.43056 |  | 140 | 26 | 11 | Riverdale | 13.2kV | SC202/505 | Transformer #OTT2668 located at 1570 Gilles isolated due to pole change | Ottawa | Scheduled Outage | Construction
13904 | 2009 | 1 | 29 | 0.30069 |  | 92 | 28 | 18 | Riverdale | 13.2kV | SC202/505 | Transformer #OTT5310 located at 1116 Richard Ave isolated due to squirrel interference | Ottawa | Foreign Interference | Animal
17706 | 2011 | 3 | 12 | 0.33125 |  | 48 | 10 | 12 | Riverdale | 13.2kV | SC202/505 | Transformer #X28244 located at 1111 Guertin opened up due to animal contact | Ottawa | Foreign Interference | Animal
19452 | 2011 | 10 | 23 | 0.66042 |  | 52 | 6 | 7 | Riverdale | 13.2kV | SC202/505 | Transformer #X21686 located at 1123 Aldea opened up due to squirrel interference | Ottawa | Foreign Interference | Animal
7702 | 2005 | 12 | 8 | 0.93056 |  | 70 | 12 | 10 | Riverdale | 13.2kV | SC202/505 | Transformer #OTT53 located at 1059 Aldea Ave isolated to re-do connections on the secondary | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15516 | 2009 | 12 | 15 | 0.39375 |  | 99 | 28 | 17 | Riverdale | 13.2kV | SC202R | PC10a #9048 completed by G.Schwartz & issued to J Petrachuck, S28427 opened to Isolated SC202-R to EOL. For tree trimming | Ottawa | Scheduled Outage
3580 | 2003 | 6 | 21 | 0.38542 |  | 125 | 417 | 200 | CARLING | 13.2kV | SC2101 | Lightning arrestor blown @ Rideau View Terrace & Pr.Of Wales also blown cut-out | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14624 | 2009 | 6 | 26 | 0.75694 |  | 155 | 13 | 5 | Carling TS | 13.2kV | SC2101 | The R & B phases of SC2101 blew during a storm, line patrolled & fuses replaced. | Ottawa | Adverse Weather | Rain
14628 | 2009 | 6 | 27 | 0.070833 |  | 544 | 725 | 80 | Albion | 13.2kV | SC2101 | car hit a pole at Prince of wales and Baseline breaking the pole and bringing down the overhead wires. This made it necessary to isolate SC2101 to make repairs. | Ottawa | Foreign Interference | Vehicle
7617 | 2005 | 11 | 15 | 0.52292 |  | 49 | 4 | 5 | Carling | 13.2kV | SC2101 | Transformer switch OTT2520 at 70 Forest Hill Ave opened due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
16879 | 2010 | 9 | 6 | 0.59375 |  | 85 | 10 | 15 | Russell TB | 13.2kV | SC2301-F | After A/R of TB22, a blown R phase fuse was found at SC24 supplying 15 SW's in the Walkley, Don Reid / Conroy area. There was a breif outage to all customers to sectionalize the loop & the last 6 customers were restored in stages as the crew tested cables during power restoration. All switchgear was inspected & cables hi-potted but no defective equipment was found. | Ottawa | Unknown/Other | No Apparent Cause
4608 | 2003 | 12 | 16 | 0.57153 |  | 32 | 5 | 9 | Albion | 13.2kV | SC2601 | Kiosk KT227 was opened to reconnect new secondary service cable that was replaced feeding 4 Trellis court. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3208 | 2003 | 2 | 24 | 0.013889 |  | 60 | 100 | 100 | ALBION | 13.2kV | SC2702 | REPAIRED ONE PHASE OF O/H CIRCUIT | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7873 | 2006 | 1 | 31 | 0.96875 |  | 110 | 26 | 14 | Albion | 13.2kV | SC2801 | Burnt secondary cable and bus bar at KT576 at 150 Hunterswood required repairs by oncall crew. | Ottawa | Defective Equipment
3477 | 2003 | 5 | 21 | 0.40972 |  | 60 | 20 | 20 | Albion | 12/7.2kV | SC2801 | Transformer repairs to KT563 on Jessica St. | Ottawa | Scheduled Outage
18245 | 2011 | 5 | 30 | 0.10764 |  | 105 | 21 | 12 | Albion TA | 13.2kV | SC2801 (2206) | found blown fuse at KT572, 210 Hunterswood cr. due to fallen barrier board. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3705 | 2003 | 7 | 8 | 0.42153 |  | 68 | 20 | 18 | TA | 13.2kV | SC401 | KT150 at 414 Sandham was opened to make repairs to a defective U/G service. Even numbered homes from 400 to 434 Sandham were affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8257 | 2006 | 5 | 9 | 0.30278 |  | 169 | 6 | 2 | Lisgar | 13.2kV | SC5928 | Replaced defective transformer OTT4494 at 156 Middle St | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4991 | 2004 | 4 | 11 | 0.47847 |  | 356 | 225 | 61 | Overbrook | 13.2kV | SC6202 | Power was restored to KT519 picking up 30 customers. After testing KT516 showed no sign of a fault, an attempt to re-energize KT516 kocked off power to KT519 again. Power was quickly restored to KT519 and KT516 was re-assessed. Defective cable between fuse & transformer and fuse holder were replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7056 | 2005 | 8 | 2 | 0.77083 |  | 100 | 42 | 25 | King Edward | 13.2kV | SC66901 | Local open at 466 Cloverdale & broken cutout due to weather | Ottawa | Adverse Weather | Equipment Failure - Cause Unknown
17792 | 2011 | 3 | 28 | 0.5 |  | 3 | 1 | 17 | Albion | 13.2kV | SC7802/2204 | Transformer #MT0025 located at 43 Folison St opened by crew for electrician to make repairs to jaws of meter base. | Ottawa | Scheduled Outage | Construction
15818 | 2010 | 3 | 18 | 0.39792 |  | 129 | 45 | 21 | Carling | 13.2kV | SC8101 | transformer TP5085 @ 42 Jenscott was isolated to allow crew to re- train secondary cable. | Ottawa | Scheduled Outage | Repair
7183 | 2005 | 8 | 23 | 0.35764 |  | 19 | 1 | 2 | Carling | 13.2kV | SC8101 | Digging, construction and amintenance scheduled for 110 Central Park requiring isolation of secondary cables from PT1688, secondary cables disconnected and PT1688 re-energized. | Ottawa | Scheduled Outage | Construction
3386 | 2003 | 4 | 29 | 0.38889 |  | 80 | 11 | 8 | Carling |  | SC8102 | MT1369 on Central Park Ave isolated to replace it with a new one due to an oil leak. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18720 | 2011 | 7 | 17 | 0.80903 |  | 1376 | 13508 | 589 | Riverdale | 13.2kV | SC8233 | High winds knock down a tree onto the O/H on Aylmer fed out of SC8233-CA4 which is the TR3UY circuit. | Ottawa | Adverse Weather | Wind
19351 | 2011 | 10 | 10 | 0.40486 |  | 61 | 95 | 114 | Riverdale | 13.2kV | SC8233 | Animal contact on Hopewell Ave. caused S27755 adn S10183 to open. | Ottawa | Foreign Interference | Animal
17311 | 2010 | 11 | 20 | 0.41319 |  | 130 | 1445 | 667 | Riverdale | 13.2kV | SC8233 CA4 | A broken tree top fell on the 3 phase primary at 59 Aylmer and caused it to trip at SC8233 | Ottawa | Tree Contacts | Tree Limb Fallen
4911 | 2004 | 3 | 17 | 0.51389 |  | 720 | 444 | 37 | Albion | 13.2kV | SC901 | SW89 white phase fuse blew due to cable fault from SW89 to PT52 at 2100 Thurston. The red & blue phases were opened to isolate PT52 from Ottawa Hydro sources, contractor brought in to dig splice pit and cable spliced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6513 | 2005 | 5 | 5 | 0.37847 |  | 155 | 36 | 14 | King Edward | 13.2kV | SCV6601 (TK2AC) | Transformer #OTT5150 at 2280 Prospect isolated due to transferring plant | Ottawa | Scheduled Outage | Construction
8445 | 2006 | 6 | 7 | 0.59792 |  | 234 | 20 | 1 | King Edward | 13.2kV | SCV66901 | Transformer located at 200 Howick St isolated due to inadequate tree trimming | Ottawa | Tree Contacts | Inadequate Trimming
18373 | 2011 | 6 | 8 | 0.70625 |  | 778 | 2399 | 185 | King Edward | 13.2kV | SCV66901 | SCV66901 white and blue fuses were found open during the lightning storm due to a tree falling one the overhead conductors. | Ottawa | Tree Contacts | Tree Fallen
18374 | 2011 | 6 | 8 | 0.70625 |  | 778 | 2399 | 185 | King Edward | 13.2kV | SCV66901 | SCV66901 white and blue phase fuses were found open due to tree fallen on overhead conductors | Ottawa | Tree Contacts | Tree Fallen
16240 | 2010 | 6 | 10 | 0.7125 |  | 167 | 14 | 5 | King Edward | 13.2kV | SCV66901 | tree contacts caused overhead transformer X23047 @ 495 Lansdowne to open. | Ottawa | Tree Contacts | Inadequate Trimming
5432 | 2004 | 7 | 1 | 0.62292 |  | 656 | 3280 | 300 | TK | 13.2kV | SCV66901 | Cct opened during storm. Patrol removed tree limb from O/H, W & B phases re-fused & power restored. Red phase was off breifly to allow replacement of blown fuses in VT669. | Ottawa | Adverse Weather | Lightning
16458 | 2010 | 7 | 12 | 0.33681 |  | 191 | 16 | 5 | King Edward | 13.2kV | SCV66901 | tree contact caused fuse to blow at Mariposa and Acacia, crew re-fused. | Ottawa | Tree Contacts | Inadequate Trimming
8741 | 2006 | 7 | 16 | 0.89861 |  | 111 | 2 | 1 | King Edward | 13.2kV | SCV66901 | Transformer at 446 Cloverdale refused successfully. Suspect animal contact. Customer may have been out of power longer but he was away for 4 days. | Ottawa | Foreign Interference | Animal
13031 | 2008 | 8 | 9 | 0.59375 |  | 20 | 2 | 7 | King Edward | 4.16kV | SCV66901 | Isolated transformer at the rear of 176 Acacia Ave to re-sag open wire secondary buss | Ottawa | Scheduled Outage | Emergency Services Request
5669 | 2004 | 8 | 11 | 0.75 |  | 70 | 10 | 9 | King Edward | 12/7.2kV | SCV66901 | Transformer at 456 Landsdown Rd in Rockcliffe fuse opened due to lightening. | Ottawa | Adverse Weather
7168 | 2005 | 8 | 19 | 0.36458 |  | 55 | 2 | 2 | King Edward | 4.16kV | SCV66901 | Switch opened to overhead transformer at 560 Hillsdale rd due to squirrel contact | Ottawa | Foreign Interference | Animal
7169 | 2005 | 8 | 19 | 0.425 |  | 58 | 6 | 6 | King Edward | 4.16kV | SCV66901 | Opened switch to overhead transformer at 427 Cloverdale to replace arrester and switch | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
4072 | 2003 | 9 | 15 | 0.56597 |  | 218 | 22 | 6 | King Edward | 12/7.2kV | SCV66901 | Contractor isolated transformer for pole replacement. | Ottawa | Scheduled Outage | Construction
7394 | 2005 | 9 | 29 | 0.3125 |  | 270 | 900 | 200 | King Edward | 13.2kV | SCV66901 | Appears tree contacts caused fuses to blow in VT669, patrolled and no cause found. | Ottawa | Unknown/Other | No Apparent Cause
9423 | 2006 | 10 | 13 | 0.31667 |  | 79 | 11 | 8 | King Edward | 4.16kV | SCV66901 | Transformer fuse was found blown at 191 Howick st due to contact with a squirrel | Ottawa | Foreign Interference | Animal
9807 | 2006 | 12 | 7 | 0.55972 |  | 157 | 18 | 7 | King Edward | 13.2kV | SCV66901 | Tree fell over & knocked down single phase line on Acacia, 1 span north of Wood. Crew cut damaged section clear, installed a new switch & re-energized. Temp switch was then sleeved out. | Ottawa | Tree Contacts | Tree Fallen
4667 | 2003 | 12 | 31 | 0.78194 |  | 64 | 19 | 18 | King Edward | 13.2kV | SCV66901 | Defective transformer switch caused supply fuse to single phase runoff to blow. Crews replaced defective switch & re-fused circuit. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9872 | 2006 | 12 | 21 | 0.47014 |  | 78 | 4 | 3 | King Edward | 13.2kV | SCV66901(TK2AC) | Fuse to transformer at the rear of 403 Wood Ave was found blown due to an animal contact (squirrel) | Ottawa | Foreign Interference | Animal
7201 | 2005 | 8 | 24 | 0.38542 |  | 10 | 0 | 3 | King Edward | 13.2kV | SCV6801/TK2AC | Transformer located at 159 Coltrin Rd isolated to disconnect the service for a demolition | Ottawa | Scheduled Outage | Construction
9939 | 2007 | 1 | 17 | 0.56597 |  | 137 | 2 | 1 | Holland | 4.16kV | SH02 | Two phases of the SH02 o/h feeding V405 @ 476 holland opened due to suspected frost intrusion. | Ottawa | Adverse Weather | Frost
17617 | 2011 | 2 | 18 | 0.89375 |  | 393 | 46 | 7 | Holland | 4.16kV | SH02 | Leads to transformer X35024, at 351 Holland, came off | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17670 | 2011 | 3 | 5 | 0.54583 |  | 24 | 2 | 5 | Carling | 4.16kV | SH02 | --- Transformer, X35161, 105 RUSKIN ST refused after small branch made contact with secondary bushings | Ottawa | Tree Contacts | Tree Limb Fallen
3475 | 2003 | 5 | 22 | 0.39931 |  | 95 | 16 | 10 | Hinchey | 4.16kV | SH02 | Planned outage for transformer 573 at 332 Sherwood for replacement. | Ottawa | Scheduled Outage
12643 | 2008 | 6 | 15 | 0.59514 |  | 1553 | 471 | 171 | Holland | 4.16kV | SH02 | SH02 Breaker tripped. Severe lightning storm in effect. SH02 Breaker closed via Scada, 30 amps missing on white phase. 24/7 found wire down on Hinton & Sherwood, feeding 3 o/h transformers. No one available until the following day to make repairs. | Ottawa | Adverse Weather | Lightning
12656 | 2008 | 6 | 15 | 0.59653 |  | 834 | 283 | 171 | Holland | 4.16kV | SH02 | 4kv O/H Primary down at Sherwood and Hinton. Restoration delayed due to not enough man power. Changed insulators, brackets, and sleeved in conductor. Also replaced O/H Transformer in front of 353 Hinton. | Ottawa | Adverse Weather | Lightning
10653 | 2007 | 6 | 18 | 0.63542 |  | 55 | 6 | 7 | Holland | 4.16kV | SH02 | Transformer #OTT6479 at 1170 Carling isolated to allong for replacement of main disconnect | Ottawa | Scheduled Outage | Repair
11934 | 2008 | 1 | 14 | 0.42708 |  | 60 | 5 | 5 | Holland | 4.16kV | SH04 | Isolated and replaced transformer 55D1D-0528 at 88 Ruskin St | Ottawa | Scheduled Outage | Preventive Maintenance
12285 | 2008 | 4 | 15 | 0.52222 |  | 116 | 8 | 4 | Hollanda | 4.16kV | SH04 | At 12:32 trasn at 132 Kenilworth St was isoalted for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
18369 | 2011 | 6 | 8 | 0.78403 |  | 240 | 32 | 8 | Holland | 4.16kV | SH04 | Tree fell on primary causeing S13169 to open. Tree removed by tree crew and line restored | Ottawa | Tree Contacts | Tree Limb Fallen
3717 | 2003 | 7 | 10 | 0.41736 |  | 192 | 32 | 10 | Holland | 4.16kV | SH04 | Crews opened transformers at the rear of Reid st. To make repairs at this location. All customers were notified to outage. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6901 | 2005 | 7 | 11 | 0.40972 |  | 160 | 11 | 4 | Holland | 4.16kV | SH04 | Transformer #OTT768 located at 10 Barrie isolated due to running a new secondary & to run a new service to a house | Ottawa | Scheduled Outage | Construction
12960 | 2008 | 7 | 29 | 0.43403 |  | 65 | 4 | 4 | Holland | 4.16kV | SH04 | Isolated transformer X25551 at 33 Warwick Ave to relocate secondary services | Ottawa | Scheduled Outage | Construction
12967 | 2008 | 7 | 29 | 0.43403 |  | 65 | 4 | 4 | HOLLAND |  | SH04 | Transformer #X25551 at 33 Warwick Place isolated to allow for transfer of plant | Ottawa | Scheduled Outage | Preventive Maintenance
16642 | 2010 | 8 | 4 | 0.65069 |  | 14 | 74 | 318 | Holland | 4.16kV | SH04 | SH04 breaker tripped during heavy rain & lightning. Breaker closed manually from SCADA. | Ottawa | Unknown/Other
13050 | 2008 | 8 | 13 | 0.375 |  | 90 | 8 | 5 | Holland | 4.16kV | SH04 | Transformer #55D1D-0355 located at 222 Sherwood Dr isolated due to tree trimming | Ottawa | Scheduled Outage | Preventive Maintenance
9031 | 2006 | 8 | 23 | 0.55208 |  | 69 | 10 | 9 | Holland | 4.16kV | SH04 | Single phase overhead line section between Kenilworth & Orrin was isolated by K-Line in order to transfer it to a different circuit in preparation for pole line relocation. All customers were advised in advance. | Ottawa | Scheduled Outage | Construction
9210 | 2006 | 9 | 13 | 0.60764 |  | 54 | 21 | 30 | Holland | 13.2kV | SH04 | 2 locals were open to allow crews to transfer new plant to new hydro poles on Parkdale Ave. | Ottawa | Scheduled Outage | Construction
17141 | 2010 | 10 | 19 | 0.74653 |  | 70 | 8 | 7 | Holland | 4.16kV | SH04 | Transformer #X35163 located at 359 Huron Ave S opened by crew twice to replace connections. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7577 | 2005 | 11 | 7 | 0.39722 |  | 4 | 15 | 231 | Holland | 4.16kV | SH04 | Cutout at 230 Sherwood broke and the live lead wrapped around the primary feed. Circuit was opened for crew to untangle lead. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11700 | 2007 | 11 | 13 | 0.44097 |  | 225 | 34 | 9 | Holland | 4.16kV | SH04 | At 10:35 trans at 55 Reid Ave was isolated in order for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
17332 | 2010 | 11 | 24 | 0.375 |  | 135 | 29 | 13 | Holland | 4.16kV | SH04 | Trans at 290 SHERWOOD DR OTTAWA isolated for tree timming | Ottawa | Tree Contacts | Inadequate Trimming
15528 | 2009 | 12 | 18 | 0.36042 |  | 190 | 48 | 15 | Holland | 4.16kV | SH04 | At 08:39am, switch S18254 to end of line was isolated to allow tree contractors to trim trees close to primary conductors. 15 customers were affected for 190 minutes. Holland (SH04) ID#15528. | Ottawa | Scheduled Outage | Preventive Maintenance
4935 | 2004 | 3 | 24 | 0.36806 |  | 100 | 23 | 14 | Holland | 4.16kV | SH05 | Transformer at 479 Parkdale Ave o/s to change transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20228 | 2012 | 3 | 26 | 0.16667 |  | 310 | 41 | 8 | Holland | 4.16kV | SH05 | Transformer #X33702 located at 146 Holland Ave opened up due to broken cutout | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17963 | 2011 | 4 | 19 | 0.36111 |  | 33 | 6 | 11 | Holland | 4.16kV | SH05 | Transformer #X21509 located at 126 Hinton Ave opened by crew for a change over. | Ottawa | Scheduled Outage | Construction
5252 | 2004 | 6 | 3 | 0.53472 |  | 95 | 19 | 12 | Holland | 4.16kV | SH05 | A transformer on Hinton was taken out of service to change the service and fix a broken rack at 163 Hinton. 12 Customers on Hinton affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20767 | 2012 | 6 | 13 | 0.58333 |  | 25 | 3 | 8 | Holland | 4.16kV | SH05 | Transformer X33711 at 205 Holland Ave isolated to allow for service upgrade at 202 Holland | Ottawa | Scheduled Outage | Repair
20768 | 2012 | 6 | 13 | 0.60417 |  | 30 | 4 | 8 | Holland | 4.16kV | SH05 | Transformer X33675 at 212 Holland Ave isolated to allow for service upgrade at 206 Holland Ave. | Ottawa | Scheduled Outage | Repair
3972 | 2003 | 8 | 29 | 0.15833 |  | 39 | 4 | 6 | Holland | 4.16kV | sh05 | A squirral made contact causing the fuse to blow. | Ottawa | Foreign Interference | Animal
19369 | 2011 | 10 | 13 | 0.52083 |  | 40 | 5 | 7 | Holland | 4.16kV | SH05 | Transformer X25666 at 114 Hamilton Ave isolated to make repairs to 2 services (the other service is a 36 (Tyndall) | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7689 | 2005 | 12 | 5 | 0.62153 |  | 40 | 8 | 12 | Holland | 4.16kV | SH05 | Transformer 55D-IB0779 at 34 Simmes was isolated to replace pole | Ottawa | Scheduled Outage | Construction
17415 | 2010 | 12 | 12 | 0.59167 |  | 88 | 16 | 11 | Holland | 4.16kV | SH05 | Trans at 125 HINTON Ave N was isolated in order to make repairs to the service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15526 | 2009 | 12 | 17 | 0.5 |  | 10 | 3 | 20 | Holland | 4.16kV | SH05 | Isolated transformer X26652 at 195 Hinton Ave for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
7746 | 2005 | 12 | 19 | 0.39583 |  | 48 | 14 | 17 | Holland | 4.16kV | SH05 | Isolated transformer 5501B-0779 AT 34 Sims to relocate the primary conductor | Ottawa | Scheduled Outage | Construction
7787 | 2006 | 1 | 9 | 0.39236 |  | 215 | 125 | 35 | Holland | 4.16kV | SH07 | K-Line opened 3 single phase transformers and one bank @ Piccadilly and Island park affecting 35 customers to do a voltage conversion from 4kv to 13.8kv. No transformer number available. | Ottawa | Scheduled Outage | Preventive Maintenance
7858 | 2006 | 1 | 25 | 0.54514 |  | 247 | 123 | 30 | Holland | 4.16kV | SH07 | A section of SH07 on Richmond rd @ Mayfair was isolated to rebuild a corner pole. | Ottawa | Scheduled Outage | Construction
6386 | 2005 | 4 | 7 | 0.91944 |  | 26 | 3 | 7 | Holland | 4.16kV | SH07 | Opened switch to transformer OTT3218 at 140 Holland Ave to repaire connection on the primary neutral | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6539 | 2005 | 5 | 11 | 0.39583 |  | 109 | 22 | 12 | Holland | 4.16kV | SH07 | Isolated Transformer # 4918 at 375 Piccadilly to change the Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
6582 | 2005 | 5 | 20 | 0.39583 |  | 234 | 43 | 11 | Holland | 4.16kV | SH07 | Isolated Transformer at 375 Island Park to change transformer | Ottawa | Scheduled Outage | Preventive Maintenance
20553 | 2012 | 5 | 22 | 0.39583 |  | 49 | 6 | 7 | Holland | 4.16kV | SH07 | Transformer #X34082 located at 12 Hampton Ave opened by crew for a disconnect/reconnect | Ottawa | Scheduled Outage | Emergency Services Request
14747 | 2009 | 7 | 14 | 0.44097 |  | 85 | 3 | 2 | Holland | 4.16kV | SH07 | Transformer #X34061 located at 425 Mayfair isolated to install new service | Ottawa | Scheduled Outage | Construction
7031 | 2005 | 7 | 27 | 0.30208 |  | 55 | 15 | 16 | Holland | 4.16kV | SH07 | Trucked backed into the driveway at 57 Hampton and made contact with the open wire service causing the fuse to blow to transformer OTT2970 | Ottawa | Foreign Interference | Vehicle
3878 | 2003 | 8 | 8 | 0.93125 |  | 56 | 15 | 16 | Holland | 4.16kV | SH07 | Crew opened transformer at 383 Mayfair to repair pole that had broken at the base and was leaning badly. Crew reports pole had been reported leaning July 11, and that yesterday a new triplex was installed and that caused the pole to further collapse. | Ottawa | Scheduled Outage
5804 | 2004 | 9 | 16 | 0.83194 |  | 50 | 7 | 8 | HOLLAND | 4.16kV | SH07 | Crew connected new service | Ottawa | Scheduled Outage | Construction
17014 | 2010 | 9 | 28 | 0.53819 |  | 31 | 4 | 8 | Holland DS | 4.16kV | SH07 | Transformer X34076 at 15 Julian Ave. was opened under PC10A# 1684, to allow crews to trim excess branches. | Ottawa | Tree Contacts | Inadequate Trimming
17016 | 2010 | 9 | 28 | 0.53125 |  | 41 | 4 | 6 | HOLLAND | 4.16kV | SH07 | Transformer X26017 at 29 Julian Ave isolated to remove fallen tree limb from primary | Ottawa | Tree Contacts | Tree Limb Fallen
11487 | 2007 | 10 | 9 | 0.5625 |  | 88 | 10 | 7 | HOLLAND | 4.16kV | SH07 | Transformer #OTT3334 at 183 Huron Ave isoloated to allow for PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
5974 | 2004 | 12 | 4 | 0.80694 |  | 60 | 6 | 6 | SH | 4.16kV | SH07 | Defective fused cut out replaced at Tx OTT2970, 58 Hampton. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4789 | 2004 | 2 | 15 | 0.50347 |  | 1 | 0 | 2 | Hinchey | 13.2kV | SH3UJ | VT310 & VT225 were interrupted during an isolation at hinchey sub for maintenance. | Ottawa | Human Element | Switching Errors
17272 | 2010 | 11 | 14 | 0.94653 |  | 68 | 106 | 641 | Holland | 4.16kV | SHK1Y1 | The holland SHK1Y1 breaker, which was carrying SH02, and SH05 load, opened due to burnt switch and bad arrestor on transformer X21510 at 129 Hinton ave on the SH05 circuit. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17820 | 2011 | 4 | 2 | 0.42778 |  | 64 | 549 | 642 | Holland SH | 4.16kV | SHT2 | Holland SHT2 tripped, no apparent cause. No spikes in load prior to trip. Gas alarm came in & cleared at same time as trip, but no flags found at station. 4kv brekers also showed no flags. Attempted to restore load to all cuatomers via SHK1Y1 (SH02, 05), however very high combined load was picked up on W phase. K1Y1 opened & only SH05 restored via SHK1Y1. Additional switching performed to restore SH02 via Carling SM00. Load readings now normal. | Ottawa | Unknown/Other | No Apparent Cause
17221 | 2010 | 11 | 4 | 0.77014 |  | 44 | 470 | 641 | Holland | 4.16kV | SHT2 | SHT2 breaker opened interrupting power to SH02, SH05 & SH00N feeders. Load restored from alternate bank, SHT1. Cause is still under investigation. | Ottawa | Unknown/Other
10466 | 2007 | 5 | 28 | 0.3 |  | 73 | 4 | 3 | King Edward | 4.16kV | SK03 | Glen Carswell isolated TRF. @ 110 Parent for a TRF upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
5617 | 2004 | 8 | 5 | 0.53264 |  | 73 | 24 | 20 | SK | 4.16kV | SK06 | K996 @ 186 Boetler was opened to re-arrange plant. As per dispatch. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11983 | 2008 | 1 | 28 | 0.35417 |  | 15 | 2 | 6 | King Edward | 4.16kV | SK09 | Isolated transformer X26541 at 80 St Andrew St to disconnect and remove triplex service for clearance for Crane | Ottawa | Scheduled Outage | Construction
12365 | 2008 | 4 | 30 | 0.28819 |  | 10 | 1 | 8 | King Edward | 4.16kV | SK09 | Isolated transformer X26541 at 84 St Andrew St to disconnect two service to give a Crane clearances from two overhead services feeding 75 and 79 St Andrew St | Ottawa | Scheduled Outage | Emergency Services Request
12552 | 2008 | 6 | 5 | 0.41667 |  | 90 | 15 | 10 | King Edward | 4.16kV | SK09 | Isolated transformer X30602 at 45 St Andrew St to install new pole | Ottawa | Scheduled Outage | Construction
8683 | 2006 | 7 | 9 | 0.77917 |  | 48 | 10 | 12 | King Edward | 4.16kV | SK09 | 24/7 reports transformer # OTT5932 fuse found opened due to tree contact. Tree trimmed transformer fuse replaced all power restored. | Ottawa | Tree Contacts | Inadequate Trimming
10882 | 2007 | 7 | 16 | 0.38889 |  | 42 | 10 | 15 | King Edward | 4.16kV | SK09 | At 09:20 trans at 273 St Patrick was isolated for trans PCB replacement | Ottawa | Scheduled Outage | Preventive Maintenance
12986 | 2008 | 8 | 1 | 0.39583 |  | 135 | 18 | 8 | King Edward | 4.16kV | SK09 | Isolated transformer X26541 at 86 St Andrew St to replace service | Ottawa | Scheduled Outage | Emergency Services Request
13002 | 2008 | 8 | 5 | 0.47361 |  | 28 | 4 | 8 | KING EDWARD | 4.16kV | SK09 | Transformer located at 86 St. Andrew isolated to allow for new service connection | Ottawa | Scheduled Outage | Construction
11051 | 2007 | 8 | 14 | 0.89931 |  | 107 | 34 | 19 | King Edward | 4.16kV | SK09 | 229 St Patrick transformer # OTT6099, fuse opened due to broken switch, 24/7 replaced broken switch and refused, | Ottawa | Defective Equipment
9157 | 2006 | 9 | 8 | 0.73958 |  | 120 | 514 | 257 | King Edward | 4.16kV | SK09 | SK09 circuit auto-reclosed auto and locked out. opened due to storm conditions. Was tried once via scada 10 minutes after and re-opened. Then it was patrolled and nothing was found. Closed again by scada and Held. Runs beside SK16 on King Edward. | Ottawa | Adverse Weather | Wind
13207 | 2008 | 9 | 8 | 0.63542 |  | 159 | 41 | 257 | King Edward | 4.16kV | SK09 | SK09 breaker auto-reclose-auto at the same time as SK16 tripped, apparently from phases making contact at King Edward & St Patrick. High winds and rain storm happening at the time. Breaker was closed successfully from SCADA. CB1 main vault breaker tripped at V438 (256 King Edward) apparently from the surge of trips. | Ottawa | Adverse Weather | Rain
15123 | 2009 | 9 | 18 | 0.47292 |  | 10 | 66 | 397 | King Edward | 4.16kV | SK09 | Crew was re-arranging a section of an NIU Line which came in contact with SK09 and tripped the breaker. Conductor cleared, and breaker closed to restore power. | Ottawa | Human Element
5844 | 2004 | 10 | 13 | 0.89583 |  | 27 | 116 | 257 | King Edward |  | SK09 | a live line clamp burnt clear causing one phase to fall to the ground. Circuit opened for the crew to do repairs | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17981 | 2011 | 4 | 21 | 0.375 |  | 320 | 421 | 79 | King Edward | 4.16kV | SK10 | Transformer #X30997 located at 162 Daly Ave opened by crew to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
5101 | 2004 | 5 | 4 | 0.29444 |  | 74 | 247 | 200 | King Edward | 4.16kV | SK10 | Lead to the switch to transformer OTT5984 at 139 Stewart let go. Lead replaced and power restored | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20581 | 2012 | 5 | 25 | 0.78542 |  | 8 | 112 | 837 | King Edward | 4.16kV | SK10 | Lightning storm and high winds caused circuit to open. King Edward ID#20581 | Ottawa | Adverse Weather | Wind
10838 | 2007 | 7 | 10 | 0.37847 |  | 100 | 18 | 11 | King Edward | 4.16kV | SK10 | Transformer #65CIA-0583 at 93 Stewart St. isolated to allow for pcb TX change | Ottawa | Scheduled Outage | Preventive Maintenance
3807 | 2003 | 7 | 23 | 0.57292 |  | 50 | 3 | 4 | King Edward | 4.16kV | SK10 | The transformer at 25 Daly was taken out of service to replace the cutout. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15019 | 2009 | 8 | 28 | 0.38264 |  | 60 | 758 | 758 | King Edward | 4.16kV | SK10 | SK10 circuit auto trip due to cable dig in at Rideau & King Edward. | Ottawa | Foreign Interference | Dig-in
7262 | 2005 | 9 | 2 | 0.56597 |  | 26 | 11 | 25 | King Edward | 4.16kV | SK10 | Transformer OTT1823 at 133 Daly Ave was isolated to repair service | Ottawa | Tree Contacts | Tree Limb Fallen
7300 | 2005 | 9 | 9 | 0.375 |  | 210 | 21 | 6 | King edward | 4.16kV | SK10 | Isolated Transformer # 1826 at 222 Daly to do a service change | Ottawa | Scheduled Outage | Preventive Maintenance
19636 | 2011 | 11 | 25 | 0.44306 |  | 160 | 48 | 18 | SK10 | 4.16kV | SK10 | Transformer #X30908 located at 72 Daly Ave opened up due to defective transformer switch | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11796 | 2007 | 12 | 1 | 0.18542 |  | 8 | 2 | 13 | King Edward | 4.16kV | SK10 | Transformer at 219 Daly isolated to disconnected service due to fire. | Ottawa | Adverse Environment | Fire
13698 | 2008 | 12 | 3 | 0.68403 |  | 107 | 141 | 79 | King Edward | 4.16kV | SK10 | Transformer #X30997 located at 162 Daly isolated due to defective cut out | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6130 | 2005 | 1 | 13 | 0.55903 |  | 15 | 0 | 2 | SK | 4.16kV | SK11 | D Jones rpts opened o/h Tx at 189 Laurier E ( Angolan Embassy ) to replace switch & connections. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3202 | 2003 | 2 | 18 | 0.87708 |  | 867 | 881 | 61 | King Edward | 4.16kV | SK11 | 2 phases of an underground cable faulted, supplying vault V778 at 225 Wilbrod St.. Customer rented a generator during the outage. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17750 | 2011 | 3 | 22 | 0.40972 |  | 55 | 7 | 8 | King Edward | 4.16kV | SK11 | Transformer #X30942 located at 193 Wilbrod St opened by crew to relocate conductor. | Ottawa | Scheduled Outage | Construction
17756 | 2011 | 3 | 22 | 0.51944 |  | 84 | 11 | 8 | King Edward | 4.16kV | SK11 | Transformer #X30942 located at 193 Wilbrod St opened by crew for an upgrade | Ottawa | Scheduled Outage | Construction
17769 | 2011 | 3 | 23 | 0.39583 |  | 143 | 19 | 8 | King Edward | 4.16kV | SK11 | Transformer #X30942 located at 193 Wilbrod St opened by crew for a wire upgrade | Ottawa | Scheduled Outage | Construction
17777 | 2011 | 3 | 24 | 0.40972 |  | 140 | 28 | 12 | King Edward | 4.16kV | SK11 | Transformer at 205 Wilbrod was upgraded, 12 customers affected | Ottawa | Scheduled Outage
17788 | 2011 | 3 | 28 | 0.29167 |  | 46 | 6 | 8 | King Edward | 4.16kV | SK11 | Transformer #X30942 located at 193 Wilbrod St opened by crew due to upgrade on wires and switch | Ottawa | Scheduled Outage | Construction
8079 | 2006 | 3 | 29 | 0.55069 |  | 47 | 4 | 5 | King Edward | 4.16kV | SK11 | Transfromer #OTT1691 located at 4 Cornwall isolated to take a vine off the pole | Ottawa | Tree Contacts | Tree Limb Fallen
17842 | 2011 | 4 | 6 | 0.375 |  | 310 | 258 | 50 | King Edward | 4.16kV | SK11 | Jamie Leblanc, line maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
17843 | 2011 | 4 | 6 | 0.375 |  | 330 | 550 | 100 | king Edward | 4.16kV | SK11 | A section of of SK11 circuit was isolated and transferred to SK10 circuit on Daly street. | Ottawa | Scheduled Outage | Construction
3347 | 2003 | 4 | 15 | 0.44306 |  | 1102 | 367 | 20 | King Edward Sub | 4.16kV | SK11 | A defective transformer at 292 Besserer was changed. 20 customer at 173 Daly were affected. The cause is supected to be lightning | Ottawa | Lightning | Direct Strike
6703 | 2005 | 6 | 13 | 0.375 |  | 193 | 45 | 14 | King Edward | 4.16kV | SK11 | Isolated Transformer at 112 Daly Ave to change the transformer# | Ottawa | Scheduled Outage | Preventive Maintenance
10730 | 2007 | 6 | 25 | 0.54167 |  | 100 | 22 | 13 | King Edward | 4.16kV | SK11 | Transformer #OTT4653 located at 230 Nelson isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10743 | 2007 | 6 | 27 | 0.375 |  | 107 | 21 | 12 | King Edward | 4.16kV | SK11 | Isolated X34678 transformer at 85 Stewart St. for PCB Change. | Ottawa | Scheduled Outage | Preventive Maintenance
10753 | 2007 | 6 | 28 | 0.41667 |  | 90 | 32 | 21 | King Edward Sub | 4.16kV | SK11 | Interrupted transformer P00273 at 201 Laurier for PCB change. | Ottawa | Scheduled Outage | Preventive Maintenance
5508 | 2004 | 7 | 16 | 0.42222 |  | 7 | 1 | 11 | King Edward | 4.16kV | SK11 | Transformer OTT6643 opened to 165 Laurier to trim a tree. | Ottawa | Tree Contacts | Inadequate Trimming
8893 | 2006 | 8 | 1 | 0.64375 |  | 118 | 161 | 82 | King Edward | 4.16kV | SK11 | Transformer #V00741 located at 110 Stewart St isolated due to lightning (broken cut out) | Ottawa | Lightning | Direct Strike
4041 | 2003 | 9 | 9 | 0.48958 |  | 113 | 19 | 10 | King Edward | 4.16kV | SK11 | Dave Stevens reports transformer open for maintenance. 10 customers effected power outage. | Ottawa | Scheduled Outage | Preventive Maintenance
4054 | 2003 | 9 | 11 | 0.40278 |  | 130 | 39 | 18 | King Edward | 4.16kV | Sk11 | Replacement of broken pole at 2 Cornwall transformer 1691 | Ottawa | Scheduled Outage | Preventive Maintenance
17477 | 2011 | 1 | 10 | 0.74306 |  | 70 | 26 | 22 | King Edward | 4.16kV | SK12 | Mole set was burnt up and crew isolated TV188 and replaced mole set. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20632 | 2012 | 5 | 31 | 0.36181 |  | 459 | 130 | 17 | King Edward | 4.16kV | SK12 | TV185 on York was isolated to allow crew to replace sidewalk transformer to a padmount. | Ottawa | Scheduled Outage | Construction
6628 | 2005 | 6 | 1 | 0.39722 |  | 466 | 381 | 49 | King Edward | 4.16kV | SK12 | TV187 was isolated to change transformers and remodel vault. | Ottawa | Scheduled Outage | Preventive Maintenance
14452 | 2009 | 6 | 3 | 0.36111 |  | 610 | 274 | 27 | King Edward SK | 4.16kV | SK12 | TV186 at 300 Clarence was isolated to replace submersible Tx with new turtle style Tx. | Ottawa | Scheduled Outage | Preventive Maintenance
6912 | 2005 | 7 | 12 | 0.88333 |  | 300 | 290 | 58 | SK | 4.16kV | SK12 | SK12 A/R, problem reported by customers supplied from TV191 @ 272 Bruyere, on-call crew found blown elbow & mole at K1015, cable section isolated & power restored to TV191. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6958 | 2005 | 7 | 15 | 0.39931 |  | 261 | 44 | 10 | King Edward | 4.16kV | SK12 | Kiosk#K01015 at 244 Bruyere St isolated to make repairs to the kiosk | Ottawa | Scheduled Outage | Repair
7329 | 2005 | 9 | 15 | 0.41458 |  | 495 | 380 | 46 | SK | 4.16kV | SK12 | TV91 @ 331 Clarence was isolated for planned replacement. | Ottawa | Scheduled Outage | Construction
15136 | 2009 | 9 | 21 | 0.4375 |  | 40 | 7 | 10 | King Edward | 4.16kV | SK12 | UG crew reports that while performing PC17A 17-34141 at TV191 (272 Bruyere) he inadvertantly parked a live elbow on a grounding bushing thinking it was a parking stand. This caused the blue phase fuse at SC6701 to open and an outage to K1015 at 244 Bruyere. | Ottawa | Human Element | Switching Errors
19576 | 2011 | 11 | 15 | 0.37708 |  | 553 | 240 | 26 | King Edward | 4.16kV | SK12 | TV188 @ 272 Murray St was isolated by the crew for transformer replacement | Ottawa | Scheduled Outage | Preventive Maintenance
19704 | 2011 | 12 | 8 | 0.42708 |  | 65 | 11 | 10 | King Edward | 4.16kV | SK12 | At 10h15 crews isolated K01015 at 244 Bruyere st for service repairs. King Edward SK12 ID# 19704 | Ottawa | Scheduled Outage
15708 | 2010 | 2 | 7 | 0.86806 |  | 332 | 83 | 15 | King Edward | 4.16kV | SK13 | tree contact caused overhead transformer X30606 on Bruyere to open. Two legs burnt down in front of 25 bruyere and on service to 30 the neutral burnt off. | Ottawa | Tree Contacts | Inadequate Trimming
12259 | 2008 | 4 | 9 | 0.41667 |  | 60 | 10 | 10 | KING EDWARD | 4.16kV | SK13 | 2 Transformers at 203 & 205 St. Andrew isolated to allow for re-arranging of one transformer & removal of one. No transformer numbers available. | Ottawa | Scheduled Outage | Construction
12467 | 2008 | 5 | 23 | 0.40625 |  | 135 | 63 | 28 | King Edward | 4.16kV | SK13 | Isolated 3 transformers X27978, X27977, and X27976 on Bruyere St between King Edward and Cumberland for pole changers | Ottawa | Scheduled Outage | Construction
14636 | 2009 | 6 | 28 | 0.90556 |  | 13 | 2 | 7 | King Edward | 4.16kV | SK13 | Hot line clamp to transformer X30548 at 61 Parent was sparking, transformer opened to replace the live line clamp. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10776 | 2007 | 7 | 3 | 0.38542 |  | 110 | 16 | 9 | King Edward | 4.16kV | SK13 | Transformer #X30623 located at 166 Bruyere St isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
8668 | 2006 | 7 | 5 | 0.81667 |  | 49 | 13 | 16 | King Edward | 4.16kV | SK13 | Transformer #65A3C-0364 located at 205 Dalhousie isolated due to defective equipment | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10884 | 2007 | 7 | 16 | 0.54167 |  | 108 | 16 | 9 | King Edward | 4.16kV | SK13 | Transformer #30622 at 141 Bruyere St isolated to allow for replacement of transformer for pcb oil | Ottawa | Scheduled Outage | Preventive Maintenance
10906 | 2007 | 7 | 18 | 0.54167 |  | 90 | 8 | 5 | King Edward | 4.16kV | SK13 | Transformer located at 61 Parent isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10909 | 2007 | 7 | 19 | 0.36111 |  | 195 | 65 | 20 | King Edward | 4.16kV | SK13 | At 08:40 trans at 240 Guigues was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
12958 | 2008 | 7 | 28 | 0.52083 |  | 150 | 38 | 15 | King Edward | 4.16kV | SK13 | Transformer #X30904 located at 169 Guigues Ave isolated for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
12964 | 2008 | 7 | 29 | 0.38542 |  | 195 | 52 | 16 | KING EDWARD | 4.16kV | SK13 | Tranformer #X30905 at 181 Guigues Ave isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
13047 | 2008 | 8 | 12 | 0.38542 |  | 318 | 80 | 15 | KING EDWARD | 4.16kV | SK13 | Transformer X30904 at 17o1 Guigues Ave isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
13048 | 2008 | 8 | 13 | 0.38542 |  | 69 | 14 | 12 | King Edward | 4.16kV | SK13 | Transformer #X34484 located at 139 Guigues Ave isolated for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
13072 | 2008 | 8 | 18 | 0.38542 |  | 135 | 45 | 20 | King Edward | 4.16kV | SK13 | Transformer #X30920 located at 233 Guigues isolated to transfer hydro plant off pole. | Ottawa | Scheduled Outage | Preventive Maintenance
13147 | 2008 | 8 | 25 | 0.53819 |  | 40 | 10 | 15 | King Edward | 4.16kV | SK13 | Transformer #X30904 located at 166 Guigues isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
13154 | 2008 | 8 | 27 | 0.40278 |  | 216 | 216 | 60 | King Edward | 4.16kV | SK13 | A section on SK13 circuit was isolated from Temp#91 to end of line on Guigues & King Edward. To allow crews to replace conductor. | Ottawa | Scheduled Outage | Construction
11347 | 2007 | 9 | 20 | 0.38194 |  | 135 | 25 | 11 | KING EDWARD | 4.16kV | SK13 | Transformer #OTT1018 at 18 Bruyere ST isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
6370 | 2005 | 4 | 5 | 0.38889 |  | 130 | 20 | 9 | King Edward | 4.16kV | SK16 | K00996 at 194 Boteler St out for Maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
14234 | 2009 | 4 | 25 | 0.80833 |  | 116 | 543 | 281 | King Edward | 4.16kV | SK16 | SK16 breaker tripped (A/R/A) during high winds, heavy rain & lightning. No permanent problem was found. | Ottawa | Adverse Weather | Wind
10397 | 2007 | 5 | 9 | 0.79583 |  | 127 | 17 | 8 | King Edward | 4.16kV | SK16 | Transformer M1452 on Boteler was replaced due to a defective secondary bushing. | Ottawa | Defective Equipment
10412 | 2007 | 5 | 13 | 0.77083 |  | 15 | 0 | 2 | King Edward | 4.16kV | SK16 | Customers complaining of flickering lights. Ott251 114 and 116 Boteler | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12453 | 2008 | 5 | 20 | 0.4375 |  | 66 | 6 | 5 | King Edward | 4.16kV | SK16 | At 10:30 trans at 221 Bruyere was isolated in order to relocate plant | Ottawa | Scheduled Outage | Preventive Maintenance
12461 | 2008 | 5 | 22 | 0.46875 |  | 75 | 40 | 32 | King Edward | 4.16kV | SK16 | Isolated two transformers X27984 at 170 Cathcart and X30923 at 200 Cathcart St to re-arrange the hydro plant | Ottawa | Scheduled Outage | Construction
12483 | 2008 | 5 | 27 | 0.5625 |  | 40 | 23 | 35 | King Edward | 4.16kV | SK16 | 2 transformer isolated at 190 & 216 Cathcart (#X30923 & X30902) due to re-arranging plant | Ottawa | Scheduled Outage | Preventive Maintenance
8364 | 2006 | 5 | 28 | 0.8625 |  | 186 | 6 | 2 | King Edward | 4.16kV | SK16 | SK16 blue phase cable faulted between K949 and M1453 while same loop was isolated between M1891 and M1451. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12488 | 2008 | 5 | 28 | 0.39583 |  | 70 | 13 | 11 | King Edward | 4.16kV | SK16 | Transformer #X27984 located at 178 Cathcart isolated due to re-arranging plant | Ottawa | Scheduled Outage | Preventive Maintenance
12489 | 2008 | 5 | 28 | 0.40278 |  | 125 | 17 | 8 | King Edward | 4.16kV | SK16 | Transformer #X30922 located at 240 Cathcart isolated due to re-arranging plant | Ottawa | Scheduled Outage | Preventive Maintenance
3545 | 2003 | 6 | 9 | 0.88472 |  | 2 | 9 | 281 | King Edward | 4.16kV | sk16 | Vehicle hit a hydro pole at King Edward and Cathcart causing circuit to open. Recloser was out of service. Closed in via scada. Accident caused damage to NCC traffic plant. | Ottawa | Foreign Interference | Vehicle
12715 | 2008 | 6 | 24 | 0.42014 |  | 70 | 54 | 46 | King Edward | 4.16kV | SK16 | Crew isolated 3 transformers between Dalhousie and Cumberland on Cathart to install new conductor | Ottawa | Scheduled Outage | Construction
12728 | 2008 | 6 | 25 | 0.42153 |  | 153 | 82 | 32 | King Edward | 4.16kV | SK16 | 2 transformers isolated at 177 & 195 Cathcart (X27984 & X30923) due to changing conductor. | Ottawa | Scheduled Outage | Preventive Maintenance
10780 | 2007 | 7 | 3 | 0.52083 |  | 105 | 9 | 5 | King Edward | 4.16kV | SK16 | Transforner #OTT1262 located at 65 Cathcart isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10790 | 2007 | 7 | 4 | 0.54167 |  | 115 | 31 | 16 | King Edward | 4.16kV | SK16 | Transformer #OTT4858 located at 66 Parent isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10791 | 2007 | 7 | 4 | 0.37153 |  | 170 | 6 | 2 | King Edward | 4.16kV | SK16 | Transformer #OTT4856 located at 23 Parent isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
18746 | 2011 | 7 | 17 | 0.80764 |  | 8 | 48 | 359 | King Edward Sub | 4.16kV | SK16 | SK16 Circuit tripped during lightening storm. Circuit was closed back in with success 8 minutes later. | Ottawa | Adverse Weather | Lightning
10907 | 2007 | 7 | 18 | 0.25 |  | 210 | 63 | 18 | King Edward | 4.16kV | SK16 | Transformer #OTT1257 located at 174 Cathcart isolated to set a new pole & re-locate transformer, service, open wire buss & 3 phase primary over to new pole | Ottawa | Scheduled Outage | Construction
5526 | 2004 | 7 | 19 | 0.54167 |  | 45 | 14 | 19 | King Edward | 4.16kV | SK16 | 2 overhead transformers on Bolton St were isolated to rearrange secondary services. | Ottawa | Scheduled Outage
5534 | 2004 | 7 | 20 | 0.42708 |  | 30 | 4 | 7 | King Edward | 4.16kV | SK16 | O/H transformer at 233 Bolton isolated to repair secondary service. | Ottawa | Scheduled Outage | Repair
5546 | 2004 | 7 | 21 | 0.40625 |  | 60 | 7 | 7 | King Edward | 4.16kV | SK16 | Scheduled outage to transformer OTT493 at 233 Bolton to re-arrange services | Ottawa | Scheduled Outage | Preventive Maintenance
5562 | 2004 | 7 | 23 | 0.44583 |  | 68 | 11 | 10 |  | 27.6/16kV | SK16 | Transformer OTT 399 isolated to transfer to a new supply. | Ottawa | Scheduled Outage
5583 | 2004 | 7 | 29 | 0.44792 |  | 105 | 18 | 10 | King Edward | 4.16kV | SK16 | O/H transformer at 180 Bolton isolated to replace pole. | Ottawa | Scheduled Outage | Repair
5627 | 2004 | 8 | 9 | 0.51389 |  | 40 | 7 | 10 | KingEdward | 4.16kV | SK16 | Replace transformer 494 at 237 Bolton. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5629 | 2004 | 8 | 9 | 0.51389 |  | 40 | 5 | 8 | King Edward | 4.16kV | SK16 | Replace transformer 496 @ 257 Bolton. | Ottawa | Scheduled Outage | Emergency Services Request
11064 | 2007 | 8 | 15 | 0.33333 |  | 300 | 70 | 14 | King Edward | 4.16kV | SK16 | Transformer #OTT1012 & OTT1013 located at 201 & 215 Bruyere isolated due to setting new poles & transferring plant to the new poles | Ottawa | Scheduled Outage | Construction
11071 | 2007 | 8 | 15 | 0.64583 |  | 95 | 8 | 5 | KING EDWARD | 4.16kV | SK16 | Transformer isolated at 240 Cathcart to allow for relocating wire to new pole | Ottawa | Scheduled Outage | Construction
3922 | 2003 | 8 | 20 | 0.39444 |  | 67 | 6 | 5 | King Edward | 4.16kV | SK16 | Transformer 3621 isolated to make repairs to a defective service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11121 | 2007 | 8 | 22 | 0.33333 |  | 65 | 20 | 18 | King Edward | 4.16kV | SK16 | Transformer #OTT3633 located at 90 King Edward isolated due to relocating to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
11124 | 2007 | 8 | 22 | 0.40625 |  | 90 | 8 | 5 | King Edward | 4.16kV | SK16 | Transformer #OTT497 located at 56 Bolton isolated due to service upgrades | Ottawa | Scheduled Outage | Preventive Maintenance
11125 | 2007 | 8 | 22 | 0.40625 |  | 164 | 25 | 9 | King Edward | 4.16kV | SK16 | Transformer #OTT498 located at 70 Bolton isolated due to service upgrades | Ottawa | Scheduled Outage | Preventive Maintenance
11128 | 2007 | 8 | 22 | 0.33333 |  | 330 | 99 | 18 | King Edward | 4.16kV | SK16 | Transformer #OTT495 located at 251 Bolton isolated due to relocating to new pole | Ottawa | Scheduled Outage | Construction
11129 | 2007 | 8 | 22 | 0.33333 |  | 330 | 28 | 5 | King Edward | 4.16kV | SK16 | Transformer #OTT493 located at 243 Bolton isolated due to relocating new pole | Ottawa | Scheduled Outage
5720 | 2004 | 8 | 25 | 0.55208 |  | 75 | 12 | 10 | King Edward | 4.16kV | SK16 | P. McEwan reports transformer# 492 isolated to allow crews to transfer transformer to new pole. Planned outage on Sk16 at 186 Bolton st outage affected power to 10 customers. | Ottawa | Scheduled Outage | Construction
9158 | 2006 | 9 | 8 | 0.73958 |  | 120 | 562 | 281 | King Edward | 4.16kV | SK16 | SK16 circuit opened due to storm conditions. Circuit auto-reclosed auto and locked out. Circuit was patrolled and nothing was found. Closed by scada and held. Runs parallel with SK09 down King Edward. | Ottawa | Adverse Weather | Wind
13206 | 2008 | 9 | 8 | 0.63542 |  | 8 | 37 | 281 | King Edward | 4.16kV | SK16 | SK16 breaker tripped at the same time as SK09 tripped, apparently from phases making contact at King Edward & St Patrick. High winds and rain storm happening at the time. Breaker was closed successfully from SCADA. Reclosure was blocked for H.O. at the time of trip. | Ottawa | Adverse Weather | Rain
15068 | 2009 | 9 | 8 | 0.54861 |  | 49 | 15 | 18 | King Edward | 4.16kV | SK16 | Transformer #X37578 located at 257 Bolton St isolated to re-arrange plant | Ottawa | Scheduled Outage | Construction
15117 | 2009 | 9 | 17 | 0.4375 |  | 110 | 33 | 18 | King Edward | 4.16kV | SK16 | Transformer #X37579 located at 243 Bolton St isolated to re-arrange plant | Ottawa | Scheduled Outage | Construction
11685 | 2007 | 11 | 9 | 0.39444 |  | 28 | 115 | 246 | King Edward | 4.16kV | SK16 | An aluminum balloon made contact with O/H causing it to trip. | Ottawa | Foreign Interference | Foreign Object
19604 | 2011 | 11 | 19 | 0.36458 |  | 272 | 45 | 10 | King Edward DS | 4.16kV | SK16 | M1452 was isolated to allow crews to re-locate the mini-pad. | Ottawa | Scheduled Outage | Construction
9829 | 2006 | 12 | 12 | 0.34375 |  | 325 | 65 | 12 | Carling | 4.16kV | SM 12 | Sam Baird isolated TRF. Behind 12 larchwood to remove large tree by crane | Ottawa | Scheduled Outage | Preventive Maintenance
17472 | 2011 | 1 | 7 | 0.62292 |  | 218 | 290 | 381 | Carling Sub | 4.16kV | SM01 | At 14:57 SM01 breaker opened due to vehicle accident that caused two phases to fall at Archibald Street and Thames. Crew cut taps to to allow breaker to be closed back in with 10 customers to be affected. SM01 breaker had to be reopened to allow crew to make final repairs to avoid single phasing customers. | Ottawa | Foreign Interference | Vehicle
11935 | 2008 | 1 | 14 | 0.4375 |  | 140 | 30 | 13 | Carling | 4.16kV | SM01 | Isolated and replaced transformer OTT6242 at 1354 Thames St | Ottawa | Scheduled Outage | Preventive Maintenance
11940 | 2008 | 1 | 15 | 0.40625 |  | 85 | 8 | 6 | Carling | 4.16kV | SM01 | Isolated and replaced transformer OTT6240 at 1316 Thames St | Ottawa | Scheduled Outage | Preventive Maintenance
9982 | 2007 | 2 | 2 | 0.44792 |  | 75 | 14 | 11 | Carling | 13.2kV | SM01 | Isolated and relocated transformer OTT132 to new pole at 64 Anna Ave | Ottawa | Scheduled Outage | Construction
10122 | 2007 | 3 | 13 | 0.63194 |  | 56 | 14 | 15 | Carling | 4.16kV | SM01 | Brian Brooks isolated TRF. 6475 to change a TRF. switch | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10273 | 2007 | 4 | 18 | 0.35625 |  | 242 | 202 | 50 | Carling |  | SM01 | S18711 opened to isolate overhead line on Veteran Ave. to restring conductor. | Ottawa | Scheduled Outage | Construction
12324 | 2008 | 4 | 22 | 0.55625 |  | 64 | 9 | 8 | Carling | 13.2kV | SM01 | Transformer #X29964 located at 1331 Leaside Ave isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10317 | 2007 | 4 | 24 | 0.375 |  | 157 | 39 | 15 | Carling | 4.16kV | SM01 | Transformer #OTT6475 located at 61 Viscount isolated to install new conductor | Ottawa | Scheduled Outage | Construction
10354 | 2007 | 5 | 2 | 0.35417 |  | 270 | 72 | 16 | Carling | 13.2kV | SM01 | Transformer #OTT3019 located at 73 Harrold Place isolated to transfer hydro plant | Ottawa | Scheduled Outage | Construction
10439 | 2007 | 5 | 22 | 0.57639 |  | 85 | 7 | 5 | Carling | 4.16kV | SM01 | Transformer located at 164 Admiral isolated to transfer plant | Ottawa | Scheduled Outage | Construction
10447 | 2007 | 5 | 23 | 0.35417 |  | 210 | 52 | 15 | Carling | 4.16kV | SM01 | At 08:30 trans at 73 Anna Ave was isolated in order to replace trans and sec buss | Ottawa | Scheduled Outage | Preventive Maintenance
6640 | 2005 | 6 | 1 | 0.79653 |  | 298 | 40 | 8 | Carling SM | 4.16kV | SM01 | Crew found transformer deffective at 42 Viscount Ave. Transformer secondary jumpered . All power restored . | Ottawa | Adverse Weather
10530 | 2007 | 6 | 5 | 0.35417 |  | 195 | 49 | 7 | Carling | 4.16kV | SM01 | Brian Brooks isolated TRF. OTT 5981 @ 37 stevenson for a TRF upgrade and service relocated to new buss | Ottawa | Scheduled Outage | Preventive Maintenance
10531 | 2007 | 6 | 5 | 0.35417 |  | 195 | 23 | 7 | Carling | 4.16kV | SM01 | Brian Brooks isolated & removed TRF OTT 5977 @ 43 Stevenson for a buss upgrade and customers energized from TRF OTT 5981 | Ottawa | Scheduled Outage
10648 | 2007 | 6 | 18 | 0.35417 |  | 240 | 32 | 8 | Carling | 4.16kV | SM01 | replaced transformer OTT3020 at 173 Crerar | Ottawa | Scheduled Outage | Construction
10682 | 2007 | 6 | 20 | 0.35417 |  | 240 | 36 | 9 | Carling | 4.16kV | SM01 | Transformer #OTT3018 located at 145 Crerar isolated to relocate buss | Ottawa | Scheduled Outage | Construction
18484 | 2011 | 6 | 24 | 0.53472 |  | 70 | 18 | 15 | Carling | 4.16kV | SM01 | Transformer #X34942 located at 90 Viscount Ave opened by crew to change connections in transformer | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10729 | 2007 | 6 | 25 | 0.35417 |  | 180 | 24 | 8 | Carling | 4.16kV | SM01 | Transformer #OTT1739 located at 129 Crerar isolated due to changing service & transformer over to new pole | Ottawa | Scheduled Outage | Construction
10738 | 2007 | 6 | 26 | 0.375 |  | 225 | 22 | 6 | Carling | 4.16kV | SM01 | Isolated transformer OTT1742 at 113 Crerar Ave for transformer re-location. | Ottawa | Scheduled Outage | Construction
8608 | 2006 | 6 | 27 | 0.40278 |  | 20 | 3 | 9 | CARLING | 4.16kV | SM01 | Isolated transformer OTT6477 at 26 Viscount Ave to replace triplex service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12867 | 2008 | 7 | 17 | 0.39583 |  | 85 | 7 | 5 | Carling | 13.2kV | SM01 | At 09:30 trans at 1337 Laperriere Ave was isolated for replacement | Ottawa | Scheduled Outage | Preventive Maintenance
12919 | 2008 | 7 | 22 | 0.53819 |  | 110 | 26 | 14 | Carling | 4.16kV | SM01 | Transformer #X29955 located at 1345 Laperierre Ave isolated due to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
16873 | 2010 | 9 | 4 | 0.86458 |  | 7 | 44 | 380 | Carling | 4.16kV | SM01 | SM01 breaker opened with no attempt to auto reclose, no reports from OFD or OPD, System Office closed in breaker and held, all load apears to have been picked up. On Tuesday, Sept 7 a blown arrestor was found at 1243 Thames & it was replaced. | Ottawa | Unknown/Other | No Apparent Cause
13261 | 2008 | 9 | 18 | 0.77083 |  | 195 | 32 | 10 | Carling | 13.2kV | SM01 | Isolated and replaced transformer X31283 at 1299 Laperriere Ave (PCB Oil) | Ottawa | Scheduled Outage | Preventive Maintenance
16993 | 2010 | 9 | 25 | 0.065278 |  | 386 | 1284 | 381 | Carling | 4.16kV | SM01 | Two phases down at Thames and Archbald caused the SM01 breaker to open. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4402 | 2003 | 11 | 7 | 0.49306 |  | 9 | 38 | 252 | Carling Sub | 4.16kV | SM01 | A tree was threatening to bring down a TV antenna on SM01 circuit in rear of a lot between Harrold & Crerar. The crew requested SM01 taken out of service to safely remove it. SM01 breaker was opened by SCADA & closed again after crew cleared the tree.252 customers in area of Laperriere in S, Kenzie in W., Carling in N & Anna in E. | Ottawa | Tree Contacts | Tree Fallen
11859 | 2007 | 12 | 17 | 0.35833 |  | 643 | 11 | 1 | Carling Sub | 4.16kV | SM01 | At 8:36am, vault V236 at 1296 Carling reported a power outage. Crew responded and discovered two broken cut-outs and flooding in the vault. Customer was issued a PC10C to due repairs and vault was restored to normal. One customer was affected for 643 min. ID#11859. | Ottawa | Unknown/Other
17658 | 2011 | 3 | 1 | 0.64583 |  | 15 | 29 | 115 | Carling | 4.16kV | SM02 | At the rear of 915 Merivale Rd a section of overhead conductor was made NIU to allow a contractor to replace the roof on Ethiopian church. SM02 overhead section was temp. transferred to AD06 circuit. While repairs are being made to church. | Ottawa | Scheduled Outage | Construction
10390 | 2007 | 5 | 8 | 0.5625 |  | 90 | 18 | 12 | Carling | 4.16kV | SM02 | Trans #OTT6869 & OTT1743 located at 164 & 128 Crerar isolated due to pole & secondary buss change | Ottawa | Scheduled Outage | Construction
18339 | 2011 | 6 | 8 | 0.69931 |  | 23 | 94 | 244 | Carling | 4.16kV | SM02 | Circuit opened due to storm activity, no cause reported yet, closed in via scada. | Ottawa | Adverse Weather | Lightning
10608 | 2007 | 6 | 12 | 0.35417 |  | 270 | 40 | 9 | Carling | 4.16kV | SM02 | Transformer #OTT2631 located at 125 General isolated by Brian Brooks to allow for setting of poles | Ottawa | Scheduled Outage | Construction
10716 | 2007 | 6 | 23 | 0.82639 |  | 15 | 2 | 10 | Carling | 4.16kV | SM02 | Transformer in the rear of 79 Crown Ott1788 was arcing due to inadequate tree trimming. Transformer was opened tree was trimmed all power restored. | Ottawa | Tree Contacts | Inadequate Trimming
16850 | 2010 | 9 | 2 | 0.37847 |  | 26 | 3 | 6 | CARLING SM | 4.16kV | SM02 | Transformer X39189 at 60 Crown Cres isolated to allow for clearing of secondary service | Ottawa | Scheduled Outage | Preventive Maintenance
9206 | 2006 | 9 | 12 | 0.46875 |  | 150 | 10 | 4 | Carling | 4.16kV | SM02 | At 11:15 trans OTT4260 at 58 Marshall Ave was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15335 | 2009 | 10 | 31 | 0.47917 |  | 67 | 17 | 15 | Carling | 4.16kV | SM02 | 174 Anna St transformer was opened to repair open secondary bus. | Ottawa | Adverse Weather
13573 | 2008 | 11 | 6 | 0.53472 |  | 57 | 6 | 6 | Carling | 4.16kV | SM02 | At 12:50 trans at 166 ANNA AVE OTTAWA was isoalted in order to repair a defective sec service | Ottawa | Scheduled Outage | Repair
13620 | 2008 | 11 | 16 | 0.66806 |  | 63 | 6 | 6 | Carling Sub | 4.16kV | SM02 | Transformer OTT1750-25Bat 232 Crerar St, customers called to report outage Live Line Clamp repaired | Ottawa | Defective Equipment
13673 | 2008 | 11 | 27 | 0.45 |  | 42 | 4 | 5 | Carling | 4.16kV | SM02 | Transformer #OTT132 located at 120 Anna isolated for tree trimming | Ottawa | Scheduled Outage | Preventive Maintenance
17591 | 2011 | 2 | 16 | 0.47222 |  | 44 | 4 | 5 | Caling | 4.16kV | SM03 | Lee Piper isolated trans / adding 2 meters for new units /5 custs / affected 124 CLARENDON AVE OTT | Ottawa | Scheduled Outage | Repair
6251 | 2005 | 3 | 6 | 0.86597 |  | 98 | 343 | 210 | Carling SM | 4.16kV | SM03 | Circuit was isolated from station to allow crew to make repairs to SM05 circuit. Phase from SM05 fell between phases of SM03. See Outage ID#6249 for SM05 outage. | Ottawa | Scheduled Outage | Repair
6532 | 2005 | 5 | 10 | 0.39375 |  | 155 | 70 | 27 | Carling | 4.16kV | SM03 | Isolated transformer # 4920 at 420 Piccadily st to change transformer | Ottawa | Scheduled Outage | Preventive Maintenance
3662 | 2003 | 7 | 2 | 0.57986 |  | 75 | 16 | 13 | Carling | 4.16kV | SM03 | Blown arrester changed and pole cleaned up. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16398 | 2010 | 7 | 5 | 0.51389 |  | 92 | 21 | 14 | Carling | 4.16kV | SM03 | A tree fell on the Bell wires in the rear of 511 Picadillly and was putting enough pressure on the shared poles that it was feared the poles would fail bringing down red phase primary on SM03. Emergency isolating was required, 2 transformers affected X34245 and X34246. | Ottawa | Tree Contacts | Tree Fallen
7023 | 2005 | 7 | 25 | 0.4125 |  | 35 | 3 | 5 | Carling | 4.16kV | SM03 | isolated Transformer # 2124 at 27 Edina to install new service | Ottawa | Scheduled Outage
18948 | 2011 | 8 | 16 | 0.52431 |  | 93 | 8 | 5 | Carling | 4.16kV | SM03 | Transformer X34000 @ 28 Byron was opened to allow crew to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
13156 | 2008 | 8 | 27 | 0.59375 |  | 99 | 26 | 16 | CARLING SM | 4.16kV | SM03 | Transformer X33694 at 77 Java isolated to allow for repairs | Ottawa | Scheduled Outage | Construction
13170 | 2008 | 8 | 29 | 0.59097 |  | 9 | 32 | 210 | Carling | 4.16kV | SM03 | SM03 was interrupted to remove defective cable from service & restore customers from an alternate feed. | Ottawa | Defective Equipment
15100 | 2009 | 9 | 14 | 0.38194 |  | 28 | 4 | 8 | CARLING | 4.16kV | SM03 | Transformer X21666 at 58 Harmer Ave isolated to allow for new service | Ottawa | Scheduled Outage | Construction
5843 | 2004 | 10 | 13 | 0.55139 |  | 37 | 2 | 4 | Carling | 4.16kV | SM03 | Transformer opened to connect new service. | Ottawa | Scheduled Outage | Construction
11547 | 2007 | 10 | 18 | 0.375 |  | 115 | 29 | 15 | Carling | 4.16kV | SM03 | 2 transformers, #OTT3379 & OTT3371 located at 17 & 25 Iona isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
4483 | 2003 | 11 | 19 | 0.38889 |  | 62 | 9 | 9 | Carling | 4.16kV | SM03 | Crew opened transformer at 519 Piccadilly for clearance to change secondary service. | Ottawa | Scheduled Outage | Repair
17338 | 2010 | 11 | 24 | 0.69792 |  | 50 | 5 | 6 | Carling | 4.16kV | SM03 | Isolated transformer X34608 at 482 Mayfair Ave to replace triplex service | Ottawa | Scheduled Outage | Emergency Services Request
9814 | 2006 | 12 | 8 | 0.71181 |  | 70 | 7 | 6 | Carling | 4.16kV | SM03 | Mark isolated TRF. # 4928 @ 498 Mayfair to change tpx. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17480 | 2011 | 1 | 12 | 0.39583 |  | 15 | 2 | 9 | Carling | 4.16kV | SM05 | Isolated transformer X33696 at 139 Faraday Sy for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
6249 | 2005 | 3 | 6 | 0.73958 |  | 280 | 565 | 121 | Carling SM | 4.16kV | SM05 | Conductor failed midspan at Helena & Clarendon causing circuit to trip, reclose then go to lockout. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8269 | 2006 | 5 | 10 | 0.5 |  | 45 | 7 | 9 | Carling | 4.16kV | SM05 | Isolated transformer OTT 2854 at 20 Grenville Ave to repaire primary overhead conductor (Burnt off at the dead end) | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6639 | 2005 | 6 | 1 | 0.69444 |  | 370 | 92 | 15 | Carling SM | 4.16kV | SM05 | Crew replaced 2 x 37.5 kva transformers with 1 x 75kva Transformers found deffective after lightening storm. | Ottawa | Adverse Weather | Lightning
17344 | 2010 | 11 | 25 | 0.41667 |  | 66 | 9 | 8 | CARLING | 4.16kV | SM05 | Transformer X33728 at 141 Faraday isolated to install new service | Ottawa | Scheduled Outage | Construction
19957 | 2012 | 2 | 3 | 0.55208 |  | 24 | 3 | 7 | Carling | 4.16kV | SM06 | Transformer X33890 at 481 Island Park Dr isolated to allow for tree trimming at the rear of 477 Island Park. | Ottawa | Tree Contacts | Inadequate Trimming
6250 | 2005 | 3 | 6 | 0.86597 |  | 98 | 287 | 176 | Carling SM | 4.16kV | SM06 | Circuit was isolated from station to allow crew to make repairs to SM05. Conductor from SM05 fell between the phases of SM06. See Outage ID# 6249 for SM05 | Ottawa | Scheduled Outage | Repair
4123 | 2003 | 9 | 22 | 0.41181 |  | 12 | 1 | 4 | Clifton | 4.16kV | SM06 | Transformer at 575 Island park dr. was opened to allow Bell Canada to perform testing. | Ottawa | Scheduled Outage | Preventive Maintenance
9339 | 2006 | 9 | 29 | 0.40278 |  | 50 | 4 | 5 | Carling | 4.16kV | SM06 | Transformer #OTT4925 located at 469 Island Park Dr isolated to replace triplex service. PC10A#1500 | Ottawa | Scheduled Outage | Repair
11554 | 2007 | 10 | 18 | 0.5625 |  | 85 | 10 | 7 | CARLING | 13.2kV | SM06 | Isolated and replaced transformer OTT4922 at 435 Island park Dr (PCB OIL) | Ottawa | Scheduled Outage | Preventive Maintenance
17382 | 2010 | 12 | 5 | 0.39583 |  | 50 | 6 | 7 | Carling | 4.16kV | SM06 | Overhead transformer at 19 Edina was isolated to repair defective service to 20 Edina. 7 customers on Edina were affected. | Ottawa | Defective Equipment
9771 | 2006 | 12 | 1 | 0.51528 |  | 51 | 2 | 2 | Carling | 4.16kV | SM09 | SM09 circuit tripped when a truck hit a guy wire into TM3UC and SM09 o/h. | Ottawa | Foreign Interference | Vehicle
15606 | 2010 | 1 | 4 | 0.3625 |  | 26 | 5 | 12 | CARLING SM | 4.16kV | SM10 | Transformer X35022 at 42 Inglewood Place isolated to swing over new service | Ottawa | Scheduled Outage | Construction
19819 | 2012 | 1 | 12 | 0.35417 |  | 70 | 12 | 10 | Carling | 4.16kV | SM10 | Isolated transformer X35021 at 403 Huron Ave to upgrade secondary service to 414 Holand Ave | Ottawa | Scheduled Outage | Emergency Services Request
12245 | 2008 | 4 | 7 | 0.4375 |  | 110 | 22 | 12 | Carling | 4.16kV | SM10 | Isolated and replaced transformer OTT5591 at 144 Ruskin St (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
12408 | 2008 | 5 | 7 | 0.44792 |  | 80 | 15 | 11 | Carling | 4.16kV | SM10 | Isolated and replaced transformer X35006 at 267 Harmer Ave (PCB Oil) | Ottawa | Scheduled Outage | Preventive Maintenance
12415 | 2008 | 5 | 7 | 0.44792 |  | 80 | 15 | 11 | Carling | 4.16kV | SM10 | Transformer #X35006 located at 267 Harmer isolated due to transformer replacement for PCB | Ottawa | Scheduled Outage | Preventive Maintenance
8362 | 2006 | 5 | 27 | 0.65417 |  | 43 | 138 | 192 | Carling | 4.16kV | SM10 | SM10 cable P/P/H failed, load was transferred to SM00. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18299 | 2011 | 6 | 5 | 0.59028 |  | 71 | 14 | 12 | Carling | 4.16kV | SM10 | Transformer X35022 at 423 Huron was found with a blown fuse crew replaced fuse. | Ottawa | Defective Equipment
18300 | 2011 | 6 | 5 | 0.64792 |  | 287 | 57 | 12 | Carling | 4.16kV | SM10 | Defective transformer X35022 at 423 Huron was isolated and replaced due to fuse blowing a second time. | Ottawa | Defective Equipment
8760 | 2006 | 7 | 17 | 0.98403 |  | 653 | 2090 | 192 | Carling | 4.16kV | SM10 | SM10 cct tripped due to a large tree pulling down primary conductor on Ruskin ave. A severe thunder storm was passing through the area at the time. A tree contractor was called in to assist Hydro crews. | Ottawa | Tree Contacts | Tree Fallen
14812 | 2009 | 7 | 23 | 0.38889 |  | 60 | 11 | 11 | Carling | 4.16kV | SM10 | Transformer #X35006 located at 267 Harmer Ave S isolated for a service upgrade | Ottawa | Scheduled Outage | Construction
7157 | 2005 | 8 | 18 | 0.29028 |  | 82 | 15 | 11 | Carling |  | SM10 | Switch to transformer OTT 3237 at 412 Holland Ave opened due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
9088 | 2006 | 8 | 29 | 0.43056 |  | 60 | 4 | 4 | Carling | 4.16kV | SM10 | Scott Dickson opened transformer OTT3415 at 650 Island Park to do a secondary transfer | Ottawa | Scheduled Outage | Preventive Maintenance
16927 | 2010 | 9 | 12 | 0.57014 |  | 134 | 74 | 33 | CARLING | 4.16kV | SM10 | Tree fell on primary behind 715 Island Park Dr., Line isolated to clear tree and make repairs to primary. On-call crew called in to make repairs to secondary service. | Ottawa | Tree Contacts | Tree Fallen
15150 | 2009 | 9 | 22 | 0.47569 |  | 5 | 8 | 102 | Carling | 4.16kV | SM10 | Lee Piper called to ask if we could dump SM10 to allow them to remove a tree limb on all three phases at the rear of 400 Holland. | Ottawa | Tree Contacts | Tree Limb Fallen
11388 | 2007 | 9 | 26 | 0.54167 |  | 60 | 4 | 4 | Carling | 4.16kV | SM10 | Isolated and replaced transformer OTT5588 at 115 Ruskin St (Up-grade) | Ottawa | Scheduled Outage | Construction
11395 | 2007 | 9 | 27 | 0.43958 |  | 122 | 14 | 7 | Carling | 4.16kV | SM10 | At 10:33 trans at 393 Huron was isolated in order to replace a pcb trans | Ottawa | Scheduled Outage | Preventive Maintenance
19365 | 2011 | 10 | 12 | 0.625 |  | 60 | 4 | 4 | Carling | 4.16kV | SM10 | Isolated transformer X35168 at 232 Harmer Ave for a service up-grade | Ottawa | Scheduled Outage | Repair
11956 | 2008 | 1 | 18 | 0.52431 |  | 100 | 15 | 9 | Carling | 4.16kV | SM11 | Isolated transformer's OTT582 and 55D2C-0174 at 288 and 293 Breezehill Ave to replace two poles | Ottawa | Scheduled Outage | Construction
11955 | 2008 | 1 | 18 | 0.38889 |  | 83 | 6 | 4 |  | 4.16kV | SM12 | Isolated transformer 55D2C-0174 at 288 Breezehill Ave to replace the pole | Ottawa | Scheduled Outage | Construction
11973 | 2008 | 1 | 23 | 0.40486 |  | 187 | 31 | 10 | Carling | 4.16kV | SM12 | At 09:43 trans at 288 Breezehill Ave in order to replace a pole | Ottawa | Scheduled Outage | Repair
11976 | 2008 | 1 | 24 | 0.56944 |  | 25 | 2 | 6 | Carling | 4.16kV | SM12 | Transformer #X25526 located at 246 Bayswater isolated due to replacing O/H service | Ottawa | Scheduled Outage | Preventive Maintenance
11987 | 2008 | 1 | 29 | 0.52083 |  | 60 | 8 | 8 | Carling Sub | 13.2kV | SM12 | At 12:30 trans at Breezehill/Hickory was isolated in order to re-arrange cond on new poles | Ottawa | Scheduled Outage | Preventive Maintenance
6172 | 2005 | 2 | 3 | 0.39583 |  | 200 | 40 | 12 | Carling | 4.16kV | SM12 | Trans OTT583 isolated at 306 Breezehill Ave to relocate equip | Ottawa | Scheduled Outage | Preventive Maintenance
7996 | 2006 | 3 | 9 | 0.44444 |  | 30 | 2 | 5 | Carling | 4.16kV | SM12 | Mike Byers opened transformer OTT6824 at the rear of 19 Galt to change a service | Ottawa | Unknown/Other
20185 | 2012 | 3 | 20 | 0.375 |  | 30 | 2 | 3 | Carling | 4.16kV | SM12 | Trans X25534 at 157 Hickory St was isolated for secondary service work | Ottawa | Scheduled Outage | Construction
20416 | 2012 | 4 | 30 | 0.375 |  | 180 | 18 | 6 | Carling | 4.16kV | SM12 | Isolated transformer X25560 at 2 Ruskin St for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
3425 | 2003 | 5 | 11 | 0.73264 |  | 65 | 4 | 4 | Carling Sub | 4.16kV | SM12 | A lightning strike caused the fuse to blow at xfmr OTT2916 affecting 4 customers on Gwynne. The crew refused and restored power | Ottawa | Lightning | Direct Strike
14354 | 2009 | 5 | 14 | 0.54861 |  | 15 | 1 | 5 | Carling | 4.16kV | SM12 | Transformer #55D1D-0099 located at 332 Fairmont isolated due to removal of branch from triplex | Ottawa | Tree Contacts | Tree Limb Fallen
10452 | 2007 | 5 | 24 | 0.42639 |  | 30 | 6 | 12 | Carling | 4.16kV | SM12 | At 10:14 trans at 189 Hichory St was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Repair
10471 | 2007 | 5 | 28 | 0.52778 |  | 120 | 24 | 12 | CARLING | 4.16kV | SM12 | Mike Anderson isolated tranformer at Beech & Breezehill Ave to relocate plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
10658 | 2007 | 6 | 19 | 0.40278 |  | 130 | 130 | 60 | Carling | 4.16kV | SM12 | At 09:40 trans at 238 Breezehill was isolated to relocate trans to new pole | Ottawa | Scheduled Outage
10806 | 2007 | 7 | 6 | 0.42847 |  | 115 | 54 | 28 | Carling | 4.16kV | SM12 | At 10:07 trans at 306 Breezhill was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Repair
6940 | 2005 | 7 | 13 | 0.89306 |  | 2 | 11 | 338 | LincolnCarling SM | 4.16kV | SM12 | Circuit opened during lightening storm.Recloser was blocked at time of outage. Circuit closed back in via scada. | Ottawa | Adverse Weather | Lightning
8850 | 2006 | 7 | 26 | 0.4375 |  | 88 | 13 | 9 | Carling | 4.16kV | SM12 | Isolated and replaced transformer OTT5773 at 16 Larchwood Ave | Ottawa | Scheduled Outage | Construction
12961 | 2008 | 7 | 29 | 0.38542 |  | 147 | 10 | 4 | Carling | 4.16kV | SM12 | Isolated transformer OTT846 at 318 Bayswater Ave for tree contractor to trim trees | Ottawa | Scheduled Outage | Construction
16886 | 2010 | 9 | 7 | 0.79167 |  | 395 | 1853 | 316 | Carling | 4.16kV | SM12 | SCADA SM12 A/R & locked out. 24/7 crew reported primary down at 236 Baywater, Crews cut damaged wire at fern Ave & circuit energized while crews wait out storm. Reisolated to repair down white phase cable. Transformer feeding School at 207 Baywater is also damaged. Transformer, cutouts replaced, requires ODCSB electrician to check phasing before restoring to normal | Ottawa | Adverse Weather
11454 | 2007 | 10 | 3 | 0.53472 |  | 132 | 15 | 7 | Carling | 4.16kV | SM12 | At 12:50 trans at 304 Fairmont was isolated in order to replace PCB trans | Ottawa | Scheduled Outage | Preventive Maintenance
11467 | 2007 | 10 | 4 | 0.54167 |  | 125 | 10 | 5 | Carling | 4.16kV | SM12 | Transformer located at 29 Gwynne isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
11484 | 2007 | 10 | 9 | 0.35486 |  | 174 | 23 | 8 | Carling | 4.16kV | SM12 | At 8:31 trans at 32 Fern was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11891 | 2007 | 12 | 28 | 0.40625 |  | 45 | 5 | 7 | CARLING SM |  | SM12 | Transformer #OTT848 at 288 Bayswater isolated to allow for replacement of cut-out | Ottawa | Scheduled Outage | Repair
6108 | 2004 | 12 | 30 | 0.50347 |  | 87 | 9 | 6 | Carling | 4.16kV | SM12 | Crew opened transformer to replace defective triplex at 172 young st. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7808 | 2006 | 1 | 14 | 0.92014 |  | 10 | 2 | 10 | Carling | 4.16kV | SM13 | 24/7 reports Ott3684 opened to repair secondary connection to 39 Kinnear St, and trim same tree branches. | Ottawa | Tree Contacts | Inadequate Trimming
9953 | 2007 | 1 | 19 | 0.54861 |  | 50 | 8 | 10 | Carling | 4.16kV | SM13 | At 13:10 trans at Kinnear/Fairmount was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
7893 | 2006 | 2 | 5 | 0.51042 |  | 15 | 4 | 14 | Carling | 4.16kV | SM13 | Changed secondary connections for overhead transformer at 39 Kinnear. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10063 | 2007 | 2 | 26 | 0.42569 |  | 164 | 16 | 6 | Carling | 4.16kV | SM13 | At 10:13 trans OTT3682 at 15 Kinnear St was isolated in order to replace a pole | Ottawa | Scheduled Outage | Preventive Maintenance
5018 | 2004 | 4 | 19 | 0.70208 |  | 6 | 10 | 96 | SM | 4.16kV | SM13 | SM13 opened during windstorm. Hold offs cleared & cct closed via scada. Line was patrolled Apr 20th and nothing obvious found. R & W inst. Relays reset. | Ottawa | Adverse Weather | Wind
12349 | 2008 | 4 | 26 | 0.4375 |  | 67 | 8 | 7 | CARLING | 4.16kV | SM13 | Transformer X31759 at 39 Kinnear isolated to change connections at pole for 39 & 41 Kinnear | Ottawa | Scheduled Outage | Repair
20565 | 2012 | 5 | 24 | 0.39583 |  | 25 | 4 | 10 | Carling | 4.16kV | SM13 | Transformer #X31619 located at 35 Fuller St opened by crew for a change over | Ottawa | Scheduled Outage | Construction
6941 | 2005 | 7 | 13 | 0.89306 |  | 2 | 3 | 96 | Carling SM | 4.16kV | SM13 | Circuit opened during lightening storm.Recloser was blocked at time of outage. Circuit closed back in via scada. | Ottawa | Adverse Weather | Lightning
7170 | 2005 | 8 | 19 | 0.45139 |  | 50 | 7 | 8 | Carling | 4.16kV | SM13 | Opened transformer OTT6829 at 202 Young St to replace connections on triplex service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5789 | 2004 | 9 | 9 | 0.45903 |  | 178 | 285 | 96 | Carling | 4.16kV | SM13 | SB13 cable between Carling and pole #1 faulted. Circuit transferred to SM00. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19199 | 2011 | 9 | 19 | 0.40625 |  | 70 | 9 | 8 | Carling | 4.16kV | SM13 | Isolated transformer X39184 at 328 Fairmont Ave for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
15184 | 2009 | 9 | 28 | 0.4125 |  | 141 | 24 | 10 | CARLING SM | 13.2kV | SM13 | transformer OTT6831 isolated to allow for transformer change due to leaker | Ottawa | Scheduled Outage | Repair
4391 | 2003 | 11 | 4 | 0.52778 |  | 55 | 6 | 7 | Carling | 4.16kV | SM13 | Transformer OTT6829 in Ottawa was isolated to allow for secondary connections to be re-done as they were heating up. ID#4391 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7773 | 2006 | 1 | 3 | 0.46875 |  | 53 | 6 | 7 | Carling | 4.16kV | SM15 | Transformer #OTT6595 located at 257 Westhaven isolated to hook up 2 new homes | Ottawa | Scheduled Outage | Construction
19810 | 2012 | 1 | 10 | 0.6125 |  | 38 | 290 | 458 | Carling | 4.16kV | SM15 | SM15 Overhead circuit was isolated to make emergency repairs to a broken insulator. | Ottawa | Scheduled Outage | Repair
7981 | 2006 | 3 | 2 | 0.39583 |  | 240 | 76 | 19 | Carling | 4.16kV | SM15 | Trans OTT916 isolated at 538 Broadhead Ave to replace 4 poles and transfer spun buss | Gloucester | Scheduled Outage | Preventive Maintenance
7986 | 2006 | 3 | 3 | 0.42361 |  | 124 | 23 | 11 | Carling | 4.16kV | SM15 | Isolated transformer OTT916 at 526 Broadhead St to install spun buss | Ottawa | Scheduled Outage | Construction
7992 | 2006 | 3 | 7 | 0.42708 |  | 135 | 25 | 11 | Carling | 4.16kV | SM15 | Transformer #OTT916 located at 525 Broadhead isolated to transfer secondary plant to new pole. | Ottawa | Scheduled Outage | Construction
17686 | 2011 | 3 | 8 | 0.81181 |  | 21 | 2 | 6 | Carling | 4.16kV | SM15 | Transformer #X21651 located at 212 Westhaven opened by crew to replace connections at house and pole | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8069 | 2006 | 3 | 28 | 0.38889 |  | 185 | 34 | 11 | Carling | 4.16kV | SM15 | Trans at 544 Laderoute Ave was isolated in order to transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
12194 | 2008 | 3 | 28 | 0.64583 |  | 15 | 2 | 10 | Carling | 4.16kV | SM15 | Transformer #X32162 located at 226 Westhaven isolated to repair service damaged by ice. | Ottawa | Foreign Interference | Foreign Object
10229 | 2007 | 4 | 9 | 0.42708 |  | 10 | 3 | 16 | Carling | 8/4.8kV | SM15 | At 10:15 trans OTT6593 was isolated at 162 Westhaven Cres to remove a raccoon | Ottawa | Scheduled Outage | Repair
8712 | 2006 | 7 | 13 | 0.39931 |  | 125 | 21 | 10 | Carling | 4.16kV | SM15 | Lee Piper opened transformer OTT4880 to transfer plant | Ottawa | Scheduled Outage
16581 | 2010 | 7 | 29 | 0.36806 |  | 22 | 2 | 6 | Carling | 13.2kV | SM15 | Isolated transformer X34230 at 543 Hilson Ave for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
8878 | 2006 | 7 | 31 | 0.54167 |  | 55 | 9 | 10 | Carling | 4.16kV | SM15 | Trans at 633 Parkview Rd isolated in order to replace secondary service | Ottawa | Scheduled Outage | Preventive Maintenance
16681 | 2010 | 8 | 5 | 0.6625 |  | 8 | 1 | 11 | Carling | 4.16kV | SM15 | crew opened 4kv overhead transformer X26064 @ 148 clare to disconnect service for tree removal. | Ottawa | Tree Contacts
18938 | 2011 | 8 | 15 | 0.54028 |  | 17 | 10 | 35 | Carling Sub | 4.16kV | SM15 | Crew isolated blue phase overhead section at S24530 at 218 Clare Street to allow contractor to remove trees. 35 customers were affected for 17 minutes. Carling (SM15) ID#18938 | Ottawa | Tree Contacts
9137 | 2006 | 9 | 7 | 0.51389 |  | 65 | 11 | 10 | Carling | 4.16kV | SM15 | Peter Broren opened transformer #QT3372 at 255 Iona and replaced all connections | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11524 | 2007 | 10 | 15 | 0.53472 |  | 83 | 14 | 10 | Carling | 4.16kV | SM15 | Transformer #OTT6614 located at 600 Westview isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
11570 | 2007 | 10 | 22 | 0.38194 |  | 140 | 12 | 5 | Carling | 4.16kV | SM15 | At 09:10 trans at 483 Kirkwood was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11574 | 2007 | 10 | 22 | 0.54167 |  | 100 | 10 | 6 | Carling | 4.16kV | SM15 | Transformer #OTT3698 located at 565 Kirkwood isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
17383 | 2010 | 12 | 6 | 0.080556 |  | 138 | 115 | 50 | Carling | 4.16kV | SM15 | A 4 Kv vault V492 @ 198 Macy Blvb was isolated to allow the crews to repair a burnt switch and test the transformers. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18878 | 2011 | 8 | 4 | 0.35139 |  | 114 | 1746 | 919 | Carling SM | 4.16kV | SM15 & SM16 | Cable dig in at 1309 Carling caused SM15 and SM16 circuits to trip. Carling Sub ID#18878 | Ottawa | Foreign Interference | Dig-in
11902 | 2008 | 1 | 7 | 0.47569 |  | 25 | 5 | 12 | Carling | 4.16kV | SM16 | Transformer #OTT2003 located at 180 Dovercourt isolated for service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
5247 | 2004 | 6 | 2 | 0.36458 |  | 45 | 9 | 12 | Carling | 4.16kV | SM16 | Transformer OTT 6370 at 540 Tweedsmuir isolated for tree removal. | Ottawa | Scheduled Outage | Preventive Maintenance
8412 | 2006 | 6 | 2 | 0.375 |  | 320 | 133 | 25 | Carling | 4.16kV | SM16 | Mike Maclellan opened a 4 transformers between 674-682 Tweedsmuir to do transformer maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
8432 | 2006 | 6 | 6 | 0.45694 |  | 27 | 10 | 22 | Carling | 4.16kV | SM16 | Isolated transformers OTT6380, OTT6384, OTT6381, OTT6385 to re-lash the spun buss between 674 and 682 Tweedsmuir Ave | Ottawa | Scheduled Outage | Construction
16388 | 2010 | 7 | 3 | 0.70694 |  | 326 | 33 | 6 | Craling | 4.16kV | SM16 | Transformer X33641@ 264 Clare St was isolated to allow crew to replace defective transformer. 6 Customer were affected. | Ottawa | Defective Equipment
14806 | 2009 | 7 | 22 | 0.81944 |  | 30 | 1 | 2 | Carling | 4.16kV | SM16 | At 19:40 trans at 185 Switzer Ave was isolated in order to replace a defective LLC | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14862 | 2009 | 7 | 28 | 0.45486 |  | 60 | 12 | 12 | Carling | 4.16kV | SM16 | At 10:55am, transformer K1032 at 30 Molenaar was isolated to allow crews to replace transformer to comply with PCB regulations, 12 customers were affected and power was restored at 11:55am. Carling (SM16). ID#14862. | Ottawa | Scheduled Outage | Construction
16615 | 2010 | 8 | 3 | 0.55556 |  | 95 | 16 | 10 | Carling | 4.16kV | SM16 | Crews isolated Kiosk K1035 at 601 Tweedsmuir to reset the cables after dig-in pulled at them. | Ottawa | Scheduled Outage | Repair
4067 | 2003 | 9 | 14 | 0.4625 |  | 184 | 12 | 4 | Carling | 4.16kV | SM16 | D. Howet reports fuse blown & defective barrel. Fuse barrel and fuse blown replaced, and power restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13237 | 2008 | 9 | 15 | 0.29306 |  | 118 | 10 | 5 | Carling | 4.16kV | SM16 | Transformer No.33602 at 714 TweedsmuirAve, Cut out broken at Pole, Repaired by Jeff MaGee. | Ottawa | Adverse Weather | Wind
19182 | 2011 | 9 | 15 | 0.41667 |  | 138 | 9 | 4 | Carling | 4.16kV | SM16 | Transformer #X33641 located at 264 Clare St opened by crew to install new pole | Ottawa | Scheduled Outage | Construction
19242 | 2011 | 9 | 23 | 0.38889 |  | 110 | 22 | 12 | Carling | 4.16kV | SM16 | Isolated transformer X33622 at 547 Tweedsmuir Ave to transfer hydro plant | Ottawa | Scheduled Outage | Construction
19259 | 2011 | 9 | 26 | 0.39583 |  | 76 | 5 | 4 | Carling | 4.16kV | SM16 | Transformer #X33641 located at 264 Clare St opened by crew to install new secondary buss | Ottawa | Scheduled Outage | Construction
19260 | 2011 | 9 | 26 | 0.38542 |  | 75 | 15 | 12 | Carling | 4.16kV | SM16 | Transformer #X33622 located at 547 Tweedsmuir opened by crew to install new secondary buss | Ottawa | Scheduled Outage | Construction
17017 | 2010 | 9 | 28 | 0.59444 |  | 10 | 1 | 8 | Carling | 4.16kV | SM16 | K1035 at 600 Tweedmuir was isolated to allow crews to replace Live Line Clamp, 8 Customers affected | Ottawa | Defective Equipment
19355 | 2011 | 10 | 11 | 0.40625 |  | 70 | 5 | 4 | Carling | 4.16kV | SM16 | Isolated transformer X33641 at 264 Clare St for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
11516 | 2007 | 10 | 15 | 0.38194 |  | 80 | 8 | 6 | Carling | 4.16kV | SM16 | Transformer #OTT1894 located at 199 Devonshire isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
11519 | 2007 | 10 | 15 | 0.4375 |  | 103 | 22 | 13 | Carling | 4.16kV | SM16 | Transformer #55D1C-0138 located at 190 Devonshire isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
5939 | 2004 | 11 | 28 | 0.35694 |  | 25 | 115 | 277 | Carling SM | 4.16kV | SM16 | SM16 open via SCADA to allow crew to repair downed phase. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19675 | 2011 | 12 | 4 | 0.375 |  | 200 | 20 | 6 | Vaughan | 4.16kV | SM16 | Transformers X24927 and X24926 Kilborn Ave at Reeves Cres isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
5999 | 2004 | 12 | 9 | 0.70833 |  | 130 | 35 | 1 |  |  | SM16 | Replaced the conections at the pole and at the stand pipe on the triplex service Tansformer #OTT2686 front of 523 Gilmour St | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14912 | 2009 | 8 | 5 | 0.60139 |  | 797 | 4428 | 481 | Carling, Clyde, Clifton | 4.16kV | SM16,UC00,UL06 | At 2:26pm, a severe storm in the area caused a tree to fall into the overhead at Dovercourt at Tweedsmuir which caused the SM16, UC00 & UL06 circuits to open and lock out. Crews called in to isolate and make repairs and power was restored on Wednesday morning at 3:43am . Carling, Clyde, Clifton (SM16, UC00, UL06). ID#14912. | Ottawa | Tree Contacts | Tree Fallen
6870 | 2005 | 7 | 5 | 0.52986 |  | 43 | 7 | 10 | Carling | 4.16kV | SM6 | Isolated Transformer at 205 Switzer to connect new services | Ottawa | Scheduled Outage | Preventive Maintenance
4827 | 2004 | 2 | 26 | 0.87361 |  | 32 | 5 | 40 | Southmarch | 8/4.8kV | SMF3 | Ian Burnett has been notified about the secondary cable fault at transformer 2551B. To isolate this secondary cable safely the transformer secondary switch cannot be operated safely without knocking off seven other transformer because they are live front transformer. There will be a momentary outage to isolate the cable as per Ian Burnett. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
7276 | 2005 | 9 | 4 | 0.28403 |  | 479 | 299 | 70 | Southmarch | 8/4.8kV | SMF3 | A cable fault bet transf 2540R (26 Milne Cr) & T2544R(21D Varley) in Kanata. To restore the other side a permit which was out for a contractor for excavation was terminated, those cables bet TE2546R(48 Pellan Cr) & TE2547R(31 Pellan) were meger and Hi potted was also found faulted. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
7488 | 2005 | 10 | 20 | 0.36042 |  | 489 | 204 | 25 | SOUTHMARCH | 13.2kV | SMF3 | Transformers 2546 & 2547 on Phelan Dr in Kanata isolated for replacement. | Kanata | Scheduled Outage | Construction
17615 | 2011 | 2 | 19 | 0.1 |  | 17 | 118 | 418 | South March | 12/7.2kV | SMH F3 | South March F3 feeder tripped and locked out, wind was high at the time, no reports of problems or accidents, feeders were closed by SCADA, no crews available for patrol | Kanata | Unknown/Other | No Apparent Cause
5801 | 2004 | 9 | 13 | 0.55764 |  | 122 | 800 | 600 | Carling Sub | 4.16kV | SMT3 | Cable riser termination failure overtripped into SMT3 & X3 bus. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19856 | 2012 | 1 | 18 | 0.39861 |  | 101 | 7 | 4 | Carling | 4.16kV | SN12 | S11929 at 1045 Sherwood was opened to allow contractor to perform tree trimming. 4 customers were affected | Ottawa | Scheduled Outage | Preventive Maintenance
7792 | 2006 | 1 | 10 | 0.36806 |  | 231 | 8 | 2 | Overbrook | 4.16kV | SO02 | Faulty hot line clamp caused a phase of SO02 circuit to come down at 1052 St. Laurent. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7793 | 2006 | 1 | 10 | 0.46944 |  | 85 | 71 | 50 | Overbrook | 4.16kV | SO02 | A Local at Lawson and Francais had to be opened to isolate the phase at 1052 St. Laurent to allow crew to make repairs. The crew requested the circuit to be opened to open the local because of its bad location. | Ottawa | Defective Equipment
7794 | 2006 | 1 | 10 | 0.46944 |  | 7 | 27 | 229 | Overbrook | 4.16kV | SO02 | The crew requested the circuit to be opened to open the local at Francis & Lawson to isolate the downed phase at 1052 St. Laurent.Because of its bad location and Obstruction this was nessessary. | Ottawa | Defective Equipment
7795 | 2006 | 1 | 10 | 0.52292 |  | 8 | 31 | 229 | OVERBROOK | 4.16kV | SO02 | The crew requested the circuit to be opened to open the local at Francis & Lawson to isolate the downed phase at 1052 St. Laurent.Because of its bad location and Obstruction this was nessessary. | Ottawa | Defective Equipment
17509 | 2011 | 1 | 22 | 0.72569 |  | 70 | 117 | 100 | Overbrook | 4.16kV | SO02 | Blown B phase fuse found at Francess St. N of King George cause found to be defective cut-out. Re-fused and all power restored. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7974 | 2006 | 2 | 28 | 0.88542 |  | 30 | 7 | 14 | Overbrook | 4.16kV | SO02 | John Streng opened transformer OTT5095 in the rear of 344 Queen Mary to replace a triplex. | Ottawa | Tree Contacts | Inadequate Trimming
17900 | 2011 | 4 | 11 | 0.64653 |  | 308 | 612 | 549 | Overbrook | 4.16kV | SO02 | Tree fell on the overhead at 530 Alesther, causing the circuit to trip, lateral overhead disconnected at Telford to allow the main portion of the feeder to be restored while trees where clearded | Ottawa | Tree Contacts | Tree Limb Fallen
20600 | 2012 | 5 | 26 | 0.80833 |  | 428 | 549 | 77 | Overbrook | 4.16kV | SO02 | S20249 Red phase @ 1015 Frances opened. No cause was found. | Ottawa | Adverse Weather | Wind
16296 | 2010 | 6 | 19 | 0.69375 |  | 296 | 44 | 9 | Overbrook | 4.16kV | SO02 | Vines on Transformer X23704 as well as primary and secondary conductor. | Ottawa | Foreign Interference | Foreign Object
18476 | 2011 | 6 | 23 | 0.90278 |  | 378 | 133 | 101 | Overbrook | 4.16kV | SO02 | Customer reports of lightening strike in the rear of 667 Alesther makes us suspect that caused the outage, blue phase fuse at Frances and King George was found open and transformer X23755 was found to be defective in the rear of 667 Alethster | Ottawa | Adverse Weather | Lightning
3603 | 2003 | 6 | 24 | 0.85764 |  | 60 | 24 | 24 | Overbrook | 4.16kV | SO02 | A defective switch caused an outage to K669 at 550 Straby affecting 24 customers. The cable to the switch was isolated and K669 restored by closing the normal open point at K669. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6953 | 2005 | 7 | 14 | 0.25417 |  | 74 | 282 | 229 | Overbrook | 4.16kV | SO02 | Storm activity caused AM03 circuit to open which in turn caused AM02 circuit to open. No problems were found on the AM02 circuit. | Ottawa | Adverse Weather
5676 | 2004 | 8 | 13 | 0.86736 |  | 51 | 5 | 6 | Overbrook | 4.16kV | SO02 | O/H transfomer at 693 Alesther St was interrupted to make repairs. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8974 | 2006 | 8 | 15 | 0.49028 |  | 181 | 270 | 114 | Overbrook | 4.16kV | SO02 | A rotten spruce tree fell on to the overhead circuit behind Queen Mary Public School blowing 2 fuses at Frances & King George. At 11:46 the 3rd phase was opened in order to isolate all 3 phase of line section for tree removal by Asplund. | Ottawa | Tree Contacts | Tree Fallen
13275 | 2008 | 9 | 22 | 0.52431 |  | 85 | 8 | 6 | Overbrook | 4.16kV | SO02 | Transformer #X29698 located at Frances/King George isolated to transfer load to new transformer | Ottawa | Scheduled Outage | Preventive Maintenance
7404 | 2005 | 9 | 29 | 0.60347 |  | 155 | 592 | 229 | Overbrook | 4.16kV | SO02 | Apparent cable fault on SO02 from the station transferred to SO00 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9346 | 2006 | 9 | 29 | 0.55208 |  | 89 | 6 | 4 | Overbrook | 4.16kV | SO02 | Transformer #OTT3646 located at 492 Lawson isolated to replace transformer (PCB oil). PC10A#1136 | Ottawa | Scheduled Outage | Preventive Maintenance
9395 | 2006 | 10 | 6 | 0.40625 |  | 90 | 9 | 6 | Overbrook | 4.16kV | SO02 | Transformer #OTT6725 located at 516 Wolffdale was isolated for PCB transformer replacement. PC10A #1101 | Ottawa | Scheduled Outage | Preventive Maintenance
9435 | 2006 | 10 | 16 | 0.40278 |  | 135 | 16 | 7 | Overbrook | 4.16kV | SO02 | Transformer #OTT5795 located at 532 Straby isolated to change transformer due to PCB as per PC10A#1186 | Ottawa | Scheduled Outage | Preventive Maintenance
15540 | 2009 | 12 | 21 | 0.50278 |  | 66 | 9 | 8 | Overbrook | 4.16kV | SO02 | transformer X23573 at rear of 531 Dunbrak was opened to replace secondary service. | Ottawa | Defective Equipment
10003 | 2007 | 2 | 8 | 0.43403 |  | 103 | 21 | 12 | Overbrook | 4.16kV | SO03 | Bob Rolland isolated TRF.5078 @ 381 Prince Albert to relocate TRF to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
13999 | 2009 | 2 | 23 | 0.44792 |  | 25 | 5 | 13 | Overbrook | 4.16kV | SO03 | Isolated transformer X24840 at 238 Prince Albert St to replace primary stand-off insulator | Ottawa | Scheduled Outage | Repair
17849 | 2011 | 4 | 7 | 0.52431 |  | 130 | 20 | 9 | Overbrook Sub | 4.16kV | SO03 | Transformer X29685 at 255 Prince Albert was isolated to allow crew to replace defective connection. 9 customers were affected for 130 minutes. Overbrook Sub (SO03) ID# 17849 | Ottawa | Defective Equipment
8177 | 2006 | 4 | 22 | 0.48611 |  | 64 | 85 | 80 | Overbrook | 4.16kV | SO03 | An in-line blue phase fuse opened at Queen Mary & Francis. Line was patrolled & found clear. New fuse installed & customers restored. Load beyond fuse may exceed installed capacity, to be confirmed. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14609 | 2009 | 6 | 24 | 0.45833 |  | 11 | 2 | 12 | Overbrook | 4.16kV | SO03 | Transformer #X29682 located at 280 Prince Albert St isolated to trim trees | Ottawa | Tree Contacts | Inadequate Trimming
14610 | 2009 | 6 | 24 | 0.53472 |  | 30 | 6 | 12 | Overbrook | 4.16kV | SO03 | Transformer #X29682 isolated at 280 Prince Albert to reconnect services | Ottawa | Scheduled Outage | Construction
6952 | 2005 | 7 | 14 | 0.44444 |  | 15 | 57 | 228 | Overbrook | 4.16kV | SO03 | SO03 circuit was opened to re-attach primary at francis and Prince Albert that was brought down by the storm. | Ottawa | Adverse Weather
6954 | 2005 | 7 | 14 | 0.25417 |  | 74 | 281 | 228 | Overbrook | 4.16kV | SO03 | Storm conditions caused a phase of SO03 to come down. Crew cut downed phase clear and we picked up circuit. Crews will repair phase later. | Ottawa | Adverse Weather
5501 | 2004 | 7 | 15 | 0.28125 |  | 113 | 121 | 75 | Overbrook | 4.16kV | SO03 | Apparent cause of outage was contact by secondary wires from O/H xfmr at 287 Prince Albert, however cut out to xfmr was not blown. Circuit fuse was replaced & then secondary wires repaired & last xfmr restored. | Ottawa | Unknown/Other
3755 | 2003 | 7 | 17 | 0.45486 |  | 70 | 8 | 7 | SO | 4.16kV | SO03 | Tx OTT3639 at 158 King George was isolated for re location of Tx. | Ottawa | Scheduled Outage | Construction
9312 | 2006 | 9 | 26 | 0.39236 |  | 173 | 26 | 9 | Overbrook | 4.16kV | SO03 | Isolated and replaced transformer Ott5074 at 277 Prince Albert due to PCB oil | Ottawa | Scheduled Outage | Preventive Maintenance
9313 | 2006 | 9 | 26 | 0.41319 |  | 118 | 4 | 2 | Overbrook | 4.16kV | SO03 | Isolated and replaced transformer OTT5075 at 286 Prince Albert ( PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9315 | 2006 | 9 | 26 | 0.54167 |  | 77 | 6 | 5 | Overbrook | 4.16kV | SO03 | Isolated and replaced transformer OTT5034 at 328 Princ Albert St (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9322 | 2006 | 9 | 27 | 0.39236 |  | 115 | 23 | 12 | Overbrook | 4.16kV | SO03 | Chris Willliams isolated xfmr OTT5067 at 164 Prince Albert to do a pcb change. Used tag PC10A # 1126 | Ottawa | Scheduled Outage | Preventive Maintenance
9325 | 2006 | 9 | 27 | 0.52431 |  | 120 | 8 | 4 | Overbrook | 4.16kV | SO03 | Mike Gruich isolated xfmr OTT 6638 to do a pcb change at 223 Whitton. Used tag PC10A#1196 | Ottawa | Scheduled Outage | Preventive Maintenance
9326 | 2006 | 9 | 27 | 0.51736 |  | 65 | 4 | 4 | Overbrook | 4.16kV | SO03 | Chris Williams isolated xfmr OTT6639 @ 226 Whitton to do a pcb change. Used tag PC10A# 1053 | Ottawa | Scheduled Outage
4175 | 2003 | 9 | 29 | 0.052778 |  | 82 | 82 | 60 | Overbrook |  | SO03 | Cutout at Frances & Queen Mary found blown. Patrol found no obvious cause. Cutout was refused. | Ottawa | Unknown/Other | No Apparent Cause
9344 | 2006 | 9 | 29 | 0.44792 |  | 41 | 6 | 9 | Overbrook | 4.16kV | SO03 | Transformer #OTT5097 located at 348 Prince Albert St isolated to replace triplex service. PC10A#1654 | Ottawa | Scheduled Outage | Repair
9383 | 2006 | 10 | 5 | 0.375 |  | 125 | 12 | 6 | Overbrook | 4.16kV | SO03 | Transformer located at 263 King George isolated for PCB transformer replacement. PC10A #1102 | Ottawa | Scheduled Outage | Preventive Maintenance
19385 | 2011 | 10 | 16 | 0.15486 |  | 7 | 2 | 16 | Overbrook SO | 4.16kV | SO03 | Tx X29678 at rear of 300 Prince Albert opened to replace defective hot line clamp. | Ottawa | Defective Equipment
9616 | 2006 | 11 | 7 | 0.41667 |  | 85 | 11 | 8 | Overbrook | 4.16kV | SO03 | Bob Rolland isolated Transformer at 381 Prince Albert to install a pole | Ottawa | Scheduled Outage | Preventive Maintenance
3135 | 2003 | 1 | 22 | 0.39931 |  | 44 | 125 | 171 | Overbrook | 4.16kV | SO04 | L. Piper reports white phase down on the ground at ST. Laurent Blvd. / North of the Queens Way. Request circuit to be isolated to repair phase. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3245 | 2003 | 3 | 13 | 0.22917 |  | 110 | 11 | 6 | Overbrook | 4.16kV | SO04 | 4 kv K685 isolated for McGowan Electric to core drill & install new cable. | Ottawa | Scheduled Outage | Construction
16495 | 2010 | 7 | 19 | 0.79514 |  | 19 | 23 | 74 | Overbrook | 4.16kV | SO04 | SO04 circuit at S15516 supply to K685 1179 St Laurent overhead conductor burning through. Circuit opened from SCADA to prevent conductor from falling on sidewalk. Repairs made and power restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4411 | 2003 | 11 | 7 | 0.475 |  | 10 | 3 | 20 | Overbrook | 4.16kV | SO04 | Crew opened transformer #1472 to repair defective secondary. 20 Customers were affected in power outage. | Ottawa | Defective Equipment
17285 | 2010 | 11 | 17 | 0.077083 |  | 214 | 160 | 72 | Overbrook | 4.16kV | SO04 | SO04 Breaker opened by System, to allow crew to safely isolate low sparking wire at 417 and St. Laurent. Wire isolated, repairs made. Breaker opened by System to allow crew to close in their Dip, and SO04 breaker auto reclosed tripped. Dip re-opened and breaker closed to restore up to Dip. Crew found a hole in the cable guard, and report defective cable. Cable isolated, alternate cable available to restore customers. | Ottawa | Defective Equipment
17293 | 2010 | 11 | 17 | 0.55139 |  | 144 | 106 | 44 | Overbrook | 13.2kV | SO04 | SO04 breaker auto-reclosed twice before locking out. Cause was determined to be a cable fault on St Laurent at dip under Queensway. Power was restored up to Queensway until alternate cable could be tested & placed back in service restoring power to southside of Queensway. | Ottawa | Defective Equipment
7633 | 2005 | 11 | 19 | 0.33333 |  | 121 | 353 | 175 | OVERBROOK | 4.16kV | SO04 | CABLE FAILURE BETWEEN DIP 1 @ POLE 13 & DIP 4 @ POLE 10 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4974 | 2004 | 4 | 6 | 0.42361 |  | 88 | 21 | 14 | Overbrook | 4.16kV | SO05 | O/H transformer at 352 Prince Albert interrupted to install new service. | Ottawa | Scheduled Outage | Construction
3417 | 2003 | 5 | 8 | 0.81667 |  | 112 | 22 | 12 | Overbrooke | 4.16kV | SO05 | Fused dip to transformer K1126 failed, same isolated and replaced. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12558 | 2008 | 6 | 6 | 0.39583 |  | 107 | 21 | 12 | Overbrook |  | SO05 | KT1117 at 208 Prestland PCB transformer replaced . | Ottawa | Scheduled Outage | Preventive Maintenance
12559 | 2008 | 6 | 6 | 0.40625 |  | 90 | 15 | 10 | Overbrook | 4.16kV | SO05 | Isolated and replaced transformer K1117 at 208 Presland Rd (PCB Oil) | Ottawa | Scheduled Outage | Preventive Maintenance
14793 | 2009 | 7 | 20 | 0.55556 |  | 15 | 3 | 12 | Overbrook | 4.16kV | SO05 | Transformer #K1033 located at 225 Presland isolated for a PCB sample | Ottawa | Scheduled Outage | Construction
3346 | 2003 | 4 | 15 | 0.98403 |  | 3 | 17 | 340 | Overbrook Sub | 4.16kV | SO05 & SO06 | SO05 & SO06 opened by SCADA to allow the Fire Dep't to use water to put out a pole fire on Vanier Parkway across from Coventry. Both circuits were restored by SCADA once fire was out. | Ottawa | Adverse Weather | Rain
13869 | 2009 | 1 | 15 | 0.081944 |  | 60 | 14 | 14 | Overbrook | 4.16kV | SO06 | A loader from the city while clearing snow caught the guy wire at 48 Prince Albert causing it to break a blowing the transformer fuse, 14 customers affected. | Ottawa | Foreign Interference | Vehicle
4777 | 2004 | 2 | 10 | 0.42917 |  | 42 | 3 | 4 | Overbrook | 4.16kV | SO06 | Transformer at 1043 North River Rd isolated to replace a defective pole. | Ottawa | Defective Equipment
10031 | 2007 | 2 | 16 | 0.52153 |  | 59 | 12 | 12 | Overbrook | 4.16kV | SO06 | Isolated Transformer #5078 at 381 Prince Albert to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
20083 | 2012 | 3 | 1 | 0.41667 |  | 85 | 17 | 12 | Overbrook | 4.16kV | SO06 | Transformer #X23629 located at 72 Drouin Ave opened by crew for a service upgrade | Ottawa | Scheduled Outage | Construction
10687 | 2007 | 6 | 20 | 0.99653 |  | 85 | 8 | 6 | Overbrook | 4.16kV | SO06 | Triplex service at 384 and 386 restored. Transformer open to make new connections | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13020 | 2008 | 8 | 8 | 0.44097 |  | 40 | 3 | 4 | Overbrook | 4.16kV | SO06 | Transformer #X23636 located at 1089 North River Rd Vanier isolated in order to energize 2 homes. | Ottawa | Scheduled Outage | Preventive Maintenance
14981 | 2009 | 8 | 21 | 0.077778 |  | 261 | 52 | 12 | OVERBROOK | 8/4.8kV | SO06 | Crews report Transformer X23647 at 44 Queen Mary is defective, oncall required to replace Xfrm'r | Ottawa | Defective Equipment
9316 | 2006 | 9 | 26 | 0.54167 |  | 77 | 8 | 6 | Overbrook | 4.16kV | SO06 | Isolated and replaced transformer OTT5080 at 4 Prince Albert St (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9341 | 2006 | 9 | 29 | 0.42708 |  | 90 | 14 | 9 | Overbrook | 4.16kV | SO06 | Transformer #OTT5077 located at 38 Prince Albert St isolated to replace transformer (PCB oil). PC10A#1054 | Ottawa | Scheduled Outage | Preventive Maintenance
12143 | 2008 | 3 | 15 | 0.63958 |  | 16 | 57 | 213 | Overbrook | 4.16kV | SO07 | SO07 tripped at the same time as SO04 tripped & reclosed twice.(see ID #12144) Oncall crew found blown arrestor on SO04 blown, lead from arrestor fell down & flashed insulator on SO07. Both arrestor & insulator were replaced. SO07 reclosure was blocked at the time of trip. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5239 | 2004 | 6 | 1 | 0.53472 |  | 20 | 3 | 8 | Overbrook | 4.16kV | SO07 | Transformer P126 at 425 McArthur isolated to replace broken switch. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18370 | 2011 | 6 | 8 | 0.70347 |  | 387 | 645 | 100 | Overbrook | 4.16kV | SO07 | Phase down on St Laurent & Coventry caused circuit to open. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16498 | 2010 | 7 | 20 | 0.40972 |  | 62 | 8 | 8 | Overbrook | 4.16kV | SO07 | Isolated transformer X23753 at 534 Donald St for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
9387 | 2006 | 10 | 5 | 0.48958 |  | 80 | 8 | 6 | Overbrook | 4.16kV | SO07 | Transformer located at 433 McArthur isolated for PCB transformer replacement. PC10A #1151 | Ottawa | Scheduled Outage | Preventive Maintenance
9427 | 2006 | 10 | 13 | 0.54167 |  | 65 | 8 | 7 | Overbrook | 4.16kV | SO07 | Transformer #OTT4317 located at 419 McArthur isolated for PCB transformer replacement. PC10A #1154 | Ottawa | Scheduled Outage | Preventive Maintenance
4766 | 2004 | 2 | 5 | 0.58333 |  | 60 | 3 | 3 | Overbrook | 4.16kV | SO10 | Transformer interrupted to repair defective service. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7923 | 2006 | 2 | 17 | 0.40139 |  | 158 | 516 | 196 | Overbrook | 4.16kV | SO10 | Wires came down at Tremblay and Avenue P causing the circuit to A/R and lock out | Ottawa | Adverse Weather | Wind
4863 | 2004 | 3 | 5 | 0.87153 |  | 35 | 5 | 9 | Overbrook | 4.16kV | SO10 | Transformer OTT6312 isolated to replace defective hotline clamp. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6307 | 2005 | 3 | 21 | 0.52431 |  | 100 | 10 | 6 | Overbrook | 4.16kV | SO10 | Transformer OTT6312 isolated to change a pole at 1309 Avenue O | Ottawa | Scheduled Outage | Preventive Maintenance
14103 | 2009 | 3 | 26 | 0.89028 |  | 198 | 33 | 10 | Overbrook | 4.16kV | SO10 | Replace the defective O/H transformer X29609 at 1325 Avenue Q | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18342 | 2011 | 6 | 8 | 0.70347 |  | 19 | 91 | 286 | Overbrook | 4.16kV | SO10 | Circuit opened due to storm activity, no cause reported yet, closed in via scada. | Ottawa | Adverse Weather
5275 | 2004 | 6 | 10 | 0.36667 |  | 75 | 245 | 196 | Overbrook | 4.16kV | SO10 | Public reported seeing kids pulling & jumping on guywire prior to outage. Flash marks on 2 phases right above guywire indicate that 2 phases came in contact with each other. Guywire re-tensioned and no permanent damage to phases. | Ottawa | Foreign Interference | Vandalism
7016 | 2005 | 7 | 24 | 0.42083 |  | 44 | 13 | 18 | Overbrook | 4.16kV | SO10 | Squirrel contact caused transformer OTT611 to open feeding customers at Tremblay and ave's P & Q | Ottawa | Foreign Interference | Animal
4434 | 2003 | 11 | 12 | 0.86458 |  | 35 | 4 | 6 | Overbrook | 4.16kV | SO10 | Transformer #6312 at 360 Tremblay Road was isolated to allow for the repair of defective connections. ID#4434 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4519 | 2003 | 11 | 26 | 0.4625 |  | 203 | 30 | 9 | Overbrook | 4.16kV | SO10 | Transformer #OTT6312 at 360 Tremblay isolated to repair ground strap & open wire secondary service. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15434 | 2009 | 11 | 28 | 0.43333 |  | 576 | 115 | 12 | Overbrook | 4.16kV | SO10 | At 10:24am kiosk, K1208 at 2016 was knocked off it's based due to vehicular collison, 12 customers were affected and power was resotred at 20:00. Overbrook (SO10). ID#15434. | Ottawa | Foreign Interference | Vehicle
12118 | 2008 | 3 | 10 | 0.17431 |  | 258 | 542 | 126 | Overbrook Sub | 4.16kV | SO11 | At 4:11am Ottawa Fire reports that a vehicle has hit and taken down 3 primary overhead conductors, 24-7 crews established isolation and 4 oncall crew memebers called in to make repairs. O/H line repaired by on call. Stations replaced blown close coil fuse on SO11 breaker. | Ottawa | Foreign Interference | Vehicle
12340 | 2008 | 4 | 23 | 0.76736 |  | 307 | 5 | 1 | OVERBROOKE | 4.16kV | SO11 | V316 at 455 Coventry Rd, was isolated to repair defective primary cable. | Ottawa | Defective Equipment
5303 | 2004 | 6 | 14 | 0.61458 |  | 35 | 1 | 1 | Overbrook Sub | 4.16kV | SO11 | Mains opened at V316, 455 Coventry, to change a broken cutout at pole. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13838 | 2009 | 1 | 5 | 0.41319 |  | 150 | 32 | 13 | Overbrook | 4.16kV | SO12 | Transformer #X29699 located at 391 King George St isolated to install new 400 amp service. | Ottawa | Scheduled Outage | Preventive Maintenance
14090 | 2009 | 3 | 24 | 0.40625 |  | 115 | 56 | 29 | Overbrook | 4.16kV | SO12 | J Pertachuck established PC10A on switch S29815, to remove tree from overhead circuit, 4 overhead transformers affected, affecting 29 customers on Beaudry and Eve St. | Ottawa | Tree Contacts | Tree Limb Fallen
10278 | 2007 | 4 | 18 | 0.50417 |  | 44 | 7 | 9 | Overbrook | 4.16kV | SO12 | Graham Schwartz isolated TRF 5076 @ 388 Queen Mary to install new service triplex | Ottawa | Scheduled Outage | Repair
16015 | 2010 | 4 | 29 | 0.43056 |  | 40 | 5 | 8 | Overbrook | 4.16kV | SO12 | Transformer #X29480 located at 961 Beaudry St opened by crew to re-locate service | Ottawa | Scheduled Outage | Construction
8330 | 2006 | 5 | 20 | 0.53125 |  | 30 | 4 | 9 | Overbrook | 4.16kV | SO12 | Isolated transformer OTT4888 at 1015 Du Pere Charlebois Ave to replace triplex service and trim tree | Ottawa | Tree Contacts | Inadequate Trimming
10551 | 2007 | 6 | 7 | 0.48611 |  | 92 | 14 | 9 | Overbrook | 4.16kV | SO12 | At 11:40 trans at 387 Vincent Massey was isolated in order to upgrade a sec service | Ottawa | Scheduled Outage | Preventive Maintenance
10552 | 2007 | 6 | 7 | 0.40972 |  | 110 | 18 | 10 | Overbrook | 4.16kV | SO12 | At 09:50 trans at 409 Vincent Massey was isolated iin order to upgrade sec service | Ottawa | Scheduled Outage | Repair
18372 | 2011 | 6 | 8 | 0.77292 |  | 671 | 6218 | 556 | Overbrook | 4.16kV | SO12 | At 370 Fullerton three phase conductors fell down due to wind storm. | Ottawa | Adverse Weather | Wind
10607 | 2007 | 6 | 12 | 0.45139 |  | 40 | 4 | 6 | Overbrook | 4.16kV | SO12 | At 10:30 trans at 410 AVE. MONSEIGNEUR LEMIEUX AVE was isolated in order to install a new service | Gloucester | Scheduled Outage | Repair
14818 | 2009 | 7 | 24 | 0.28958 |  | 83 | 12 | 9 | Overbrook | 4.16kV | SO12 | Transformer #X23073 located 475 Prince Albert St isolated due to vine contact | Ottawa | Tree Contacts | Inadequate Trimming
7140 | 2005 | 8 | 15 | 0.98819 |  | 55 | 7 | 8 | SO | 4.16kV | SO12 | Tx OTT4893 at 1015 Paul Emile Lamarche was found open, possible tree or animal contact. Tx re-fused & closed. | Ottawa | Foreign Interference | Foreign Object
3982 | 2003 | 9 | 2 | 0.76042 |  | 20 | 5 | 16 | King Edward | 4.16kV | SO12 | Transformer OTT3644 on King George was opened to remove 2 triplex services affected by a structure fire. | Ottawa | Adverse Environment | Fire
15098 | 2009 | 9 | 14 | 0.38819 |  | 110 | 1018 | 555 | Overbrook Sub | 4.16kV | SO12 | At 396 Donald a backhoe hit the down guy and pole to break causing the neutral to break and wrap around the phases. | Ottawa | Foreign Interference | Vehicle
9283 | 2006 | 9 | 22 | 0.5625 |  | 65 | 26 | 24 | Overbrook | 4.16kV | SO12 | Transformer #OTT1948 located at 330 Donald isolated due for PCB change. PC10 #1133. | Ottawa | Scheduled Outage | Preventive Maintenance
9425 | 2006 | 10 | 13 | 0.39931 |  | 120 | 20 | 10 | Overbrook | 4.16kV | SO12 | Transformer #OTT6466 located at 410 Monseigneur Lemieux Ave isolated to allow PCB transformer replacement. PC10A #1153. | Ottawa | Scheduled Outage | Preventive Maintenance
17143 | 2010 | 10 | 19 | 0.96667 |  | 298 | 70 | 14 | Overbrook | 4.16kV | SO12 | Crew replaced defective tranformer X34630 at rear of Paul Emile Lamarche. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9510 | 2006 | 10 | 25 | 0.38194 |  | 246 | 33 | 8 | Overbrook | 4.16kV | SO12 | Transf. 29695 was changed as / PCB program @ 397 Prince Albert | Ottawa | Scheduled Outage | Preventive Maintenance
19632 | 2011 | 11 | 24 | 0.53958 |  | 94 | 14 | 9 | Overbrook | 4.16kV | SO12 | Transformer #X29452 located at 382 Vincent Massey Ave opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
9797 | 2006 | 12 | 5 | 0.53472 |  | 55 | 8 | 9 | Overbrook | 4.16kV | SO12 | Rick isolated TRF. 1952 @ 388 Donald for contractors to clear trees | Ottawa | Foreign Interference | Foreign Object
13817 | 2008 | 12 | 29 | 0.59375 |  | 10 | 1 | 8 | Overbrook | 4.16kV | SO12 | Isolated transformer X29450 at 405 Vincent Massey Dr to install new triplex service | Ottawa | Scheduled Outage | Repair
6118 | 2005 | 1 | 5 | 0.72222 |  | 30 | 2 | 5 | SO | 4.16kV | SO13 | D Howatt rpts P292 at 505 Industrial opened at 17:20 to repair burning hot line clamp, power restored to 5 customers at 17:50. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7924 | 2006 | 2 | 17 | 0.41528 |  | 147 | 419 | 171 | Overbrook | 4.16kV | SO13 | Circuit patrolled and no problem found | Ottawa | Adverse Weather | Wind
4875 | 2004 | 3 | 10 | 0.47917 |  | 56 | 8 | 9 | Overbrook | 4.16kV | SO13 | Transformer at 125 King George was interrupted to replace defective switch. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16758 | 2010 | 8 | 17 | 0.375 |  | 70 | 1 | 1 | Overbrook DS | 4.16kV | SO13 | OMS rceived a call regarding a downed conductor acroos the road. Crews had to replace the live line clamps. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10977 | 2007 | 8 | 1 | 0.083333 |  | 210 | 32 | 9 | South Gloucester | 8/4.8kV | South Glouc F4 | Transformer 678 at 5401 Bank failed and caused very high voltages to approx. 9 customers in a trailer park. Transformer was isolated and replaced | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
3183 | 2003 | 2 | 11 | 0.875 |  | 110 | 310 | 300 | SMF2 | 12/7.2kV | South March | While isolating cable section between TX2506R and TX2502. To repair broken water main. 24/7 crew closed normal open point on oto to make parell between SMF2 & BBF1. Switch failed to be closed properly at TX2577-1. Causing switch to flash over while breaking parell at 2506-2. This caused outage on SMF2 red phase reclosure, and S2-4 red phase fuse to blow. | Kanata | Human Element | Incorrect Use of Equipment
17294 | 2010 | 11 | 17 | 0.72222 |  | 154 | 13757 | 6383 | Alexander | 44kV | South March M5 | At 15:10 the A9M5 tripped off and Hydro One closed it back it at 15:15, all customers were restored but tripped out again at 15:20. Hydro One dispatched crew and found a blown insulator on the 44KV near Alexander. Crews closed S22403 at 17:20 and picked up the Alex F3. Crews closed S12799 at 17:49 and picked up Alex F2 and all load was restored. South March A9M5 | Goulburn | Loss of Supply | HEPC Circuit Fault
15879 | 2010 | 4 | 1 | 0.72778 |  | 8 | 2467 | 18500 | South March MS | 44kV | South March TS | Hydro One operator (Steve) reports a bird made contact with the Y buss at Southmarch TS causing a complete station outage. Loss of supply to South March, Alexander, Beaverbrook, Janet King, Munster, Richmond North, stations and 10 large customers off the A9M2 & A9M4 circuits. | Kanata | Loss of Supply
19787 | 2012 | 1 | 5 | 0.47222 |  | 63 | 9 | 9 | Riverdale | 4.16kV | SR01 | Transformer #X21501 located at 15 Chestnut opened by crew for an upgrade | Ottawa | Scheduled Outage | Construction
13920 | 2009 | 2 | 2 | 0.43056 |  | 28 | 7 | 16 | RIVERDALE | 4.16kV | SR01 | Xfmr X27568 at 141 Concord St. S isolated to replace triplex at #135 Concord | Ottawa | Scheduled Outage | Construction
10016 | 2007 | 2 | 12 | 0.44792 |  | 142 | 17 | 7 | Riverdale | 4.16kV | SR01 | Glen Carswell isolated OTT2251 @ 60 Evelyn to change a pole | Ottawa | Scheduled Outage | Preventive Maintenance
10020 | 2007 | 2 | 13 | 0.42639 |  | 31 | 4 | 8 | Riverdale | 4.16kV | SR01 | Isolated transformer at 248 Evrlyn St to connect new service | Ottawa | Scheduled Outage | Repair
20017 | 2012 | 2 | 14 | 0.44375 |  | 61 | 10 | 10 | Riverdale | 4.16kV | SR01 | Isolated transformer X31102at 44 Chestnut St to transfer hydro plant | Ottawa | Scheduled Outage | Construction
7918 | 2006 | 2 | 15 | 0.42361 |  | 30 | 8 | 16 | Riverdale | 4.16kV | SR01 | Transformer #OTT3046 located at 168 Hawthorne Ave isolated to replace service | Ottawa | Scheduled Outage | Repair
10057 | 2007 | 2 | 23 | 0.41042 |  | 159 | 19 | 7 | Riverdale | 4.16kV | SR01 | AT 09:51 trans at 60 Evelyn Ave was isolated in order to replace a defective pole | Ottawa | Scheduled Outage | Repair
10112 | 2007 | 3 | 12 | 0.43542 |  | 58 | 10 | 10 | Riverdale | 4.16kV | SR01 | At 10:27 trans at 192 Hawthorne Ave was isolated for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
20156 | 2012 | 3 | 13 | 0.42361 |  | 50 | 9 | 11 | Riverdale | 4.16kV | SR01 | Transformer K1059 at 143 Evelyn Ave was isolated in oder to work on secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
20157 | 2012 | 3 | 13 | 0.45833 |  | 90 | 15 | 10 | Riverdale | 4.16kV | SR01 | Trans X31102 at 44 Chestnut St was isolated in order to upgrade secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
20210 | 2012 | 3 | 23 | 0.54167 |  | 90 | 32 | 21 | Riverdale | 4.16kV | SR01 | Transformer #X30792 located at 48A Simcoe opened by crew to repair neutral | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17915 | 2011 | 4 | 12 | 0.71875 |  | 45 | 6 | 8 | Riverdale | 4.16kV | SR01 | Isolated transformer X30888 at 113 Concord St to replace defective secondary service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6761 | 2005 | 6 | 19 | 0.47639 |  | 34 | 5 | 9 | Riverdale | 4.16kV | SR01 | Interrupted power to Transformer OTT1639 at 167 Hawthorne Ave to replace connection on the secondary bushing | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5336 | 2004 | 6 | 20 | 0.021528 |  | 58 | 8 | 8 | Riverdale | 4.16kV | SR01 | Crew opened transformer at 56 Evelyn to replace defective service and trim trees. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
12755 | 2008 | 6 | 27 | 0.056944 |  | 44 | 314 | 428 | Riverdale Sub | 4.16kV | SR01 | At 1:22am SR01 circuit was isolated to allow crews to repair a downed overhead primary conductor, 428 customers were affected and power was restored at 2:06am. Riverdale (SR01). ID#12755. | Ottawa | Adverse Weather | Wind
18798 | 2011 | 7 | 22 | 0.79514 |  | 45 | 14 | 18 | RIVERDALE | 4.16kV | SR01 | ISOLATED TRANSFORMER X31100 AT 68 ROSEMERE AVE TO REMOVE TREE BRANCH FROM SECONDARY OPEN BUSS | Ottawa | Tree Contacts | Tree Limb Fallen
7027 | 2005 | 7 | 26 | 0.375 |  | 20 | 5 | 15 | Riverdale | 4.16kV | SR01 | Power interruption to transformer OTT 1641 at 137 Concord to connect new service | Ottawa | Scheduled Outage | Construction
7065 | 2005 | 8 | 4 | 0.82153 |  | 503 | 84 | 10 | RIVERDALE | 4.16kV | SR01 | SR01 autoreclosed. White phase span on Concord S. of Evelyn down due to lightning strike. Wire put back up and spliced in. | Ottawa | Lightning | Direct Strike
9449 | 2006 | 10 | 17 | 0.42708 |  | 103 | 12 | 7 | Riverdale | 4.16kV | SR01 | Isolated transformer OTT2251 at 60 Evelyn Ave to transfer services | Ottawa | Scheduled Outage | Construction
9475 | 2006 | 10 | 20 | 0.39236 |  | 145 | 17 | 7 | Riverdale | 4.16kV | SR01 | Transformer #OTT2251 located at 60 Evelyn isolated re-arrange for crane set-up. PC10A #40 | Ottawa | Scheduled Outage | Preventive Maintenance
4440 | 2003 | 11 | 13 | 0.54792 |  | 101 | 502 | 298 | Riverdale | 4.16kV | SR01 | SR01 breaker was opened manually to remove circuit from service. Circuit had 2 energized 4 kv phases on the ground. Repairs were made & circuit re-energized. | Ottawa | Adverse Weather | Wind
17301 | 2010 | 11 | 18 | 0.4375 |  | 35 | 2 | 4 | Riverdale | 4.16kV | SR01 | Isolated transformer X37956 at 27 Graham ave for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
19821 | 2012 | 1 | 12 | 0.375 |  | 434 | 130 | 18 | Riverdale | 4.16kV | SR02 | single red phase of SR02 circuit between Mason teerace and Mount Pleasant was isolated to upgrade overhead line, install switches, and change transformer. | Ottawa | Scheduled Outage | Preventive Maintenance
19846 | 2012 | 1 | 17 | 0.51458 |  | 219 | 44 | 12 | Riverdale | 4.16kV | SR02 | Isolated transformer X31685 at 38 Mason Terr to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Construction
19858 | 2012 | 1 | 18 | 0.35417 |  | 270 | 27 | 6 | Riverdale | 4.16kV | SR02 | Transformer in rear of 41 mount Pleasasant was upgraded. 6 customers affected for 270 minutes | Ottawa | Scheduled Outage | Construction
19869 | 2012 | 1 | 20 | 0.52431 |  | 115 | 17 | 9 | Riverdale SR | 4.16kV | SR02 | Sproule powerline opened transformer X31950 at 669 Echo to transfer plant to new pole. | Ottawa | Scheduled Outage | Construction
19908 | 2012 | 1 | 26 | 0.38542 |  | 362 | 278 | 46 | Riverdale | 4.16kV | SR02 | S26318 open to isolate overhead to allow Sproule to install new poles along Merrit Ave and Main St | Ottawa | Scheduled Outage | Construction
19926 | 2012 | 1 | 30 | 0.52083 |  | 120 | 26 | 13 | Riverdale | 4.16kV | SR02 | Transformer #X29917 located at 26 Merritt Ave opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
19937 | 2012 | 1 | 31 | 0.52083 |  | 170 | 40 | 14 | Riverdale | 4.16kV | SR02 | Trans at 49 Bower St was isolated in odrer to tranfer plant to new pole | Ottawa | Scheduled Outage | Construction
19951 | 2012 | 2 | 2 | 0.35417 |  | 165 | 38 | 14 | Riverdale | 4.16kV | SR02 | Transformer 55D4B-0460 at 49 Bower St. isolated to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
19952 | 2012 | 2 | 2 | 0.53264 |  | 118 | 26 | 13 | Riverdale | 4.16kV | SR02 | Transformer X29917 at 26 Merritt Ave. isolated for transfer of plant | Ottawa | Scheduled Outage | Construction
4877 | 2004 | 3 | 11 | 0.47083 |  | 32 | 2 | 3 | Riverdale | 4.16kV | SR02 | Transformer OTT4630 at 16 Mutchmore interrupted to upgrade service. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
4950 | 2004 | 3 | 31 | 0.40972 |  | 20 | 6 | 17 | Riverdale | 4.16kV | SR02 | Transformer OTT4630 at 16 Mutchmore was isolated for relocate of overhead services. | Ottawa | Unknown/Other | No Apparent Cause
4951 | 2004 | 3 | 31 | 0.4375 |  | 95 | 13 | 8 | Riverdale | 4.16kV | SR02 | Transformer OTT4629 @ 7 Mutchmor was isolated for relocating services. | Ottawa | Unknown/Other
4962 | 2004 | 4 | 2 | 0.39931 |  | 85 | 11 | 8 | Riverdale | 4.16kV | SR02 | Transfer services at transformer Ott531 located at 16 Bower St. | Ottawa | Scheduled Outage | Construction
20267 | 2012 | 4 | 3 | 0.42778 |  | 66 | 14 | 363 | Riverdale | 4.16kV | SR02 | An old proclin cut out at transformer X29766 @ 56 ONSLOW CRES was burning up and the crew could not open it up and requested the SR02 breaker for them to cut it clear. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
4973 | 2004 | 4 | 6 | 0.39306 |  | 157 | 44 | 17 | Riverdale | 4.16kV | SR02 | O/H transformaer at 16 Mutchmor Rd interrupted to replace pole. | Ottawa | Scheduled Outage | Repair
4976 | 2004 | 4 | 6 | 0.5625 |  | 15 | 3 | 12 | Riverdale | 4.16kV | SR02 | O/H transformer at 115 Mason Terrace interrupted to relocate service. | Ottawa | Scheduled Outage | Preventive Maintenance
12284 | 2008 | 4 | 15 | 0.38542 |  | 165 | 22 | 8 | Riverdale | 4.16kV | SR02 | At 09:15 trans at 106 Clegg Ave was isolated for a pole change | Ottawa | Scheduled Outage | Repair
5157 | 2004 | 5 | 17 | 0.55208 |  | 65 | 9 | 8 | SR | 4.16kV | SR02 | B Kerfoot via dispatch rpts Tx OTT4629 was opened at 13:15 & restored at 14:20 to change pole T.E. to new line. 8 customers affected on Mutchmor, Marret & Bower. | Ottawa | Scheduled Outage | Construction
5184 | 2004 | 5 | 19 | 0.41319 |  | 175 | 23 | 8 | Riverdale | 4.16kV | SR02 | Transformer at 7 Mutchmor isolated to transfer plant. 8 customers affected on Bower, McGillvary & Merritt. | Ottawa | Unknown/Other
10816 | 2007 | 7 | 8 | 0.38125 |  | 116 | 29 | 15 | Riverdale | 4.16kV | SR02 | Transformer #OTT4619 located at 34 Riverdale Ave isolated due to broken cut out (cause unknown) | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6902 | 2005 | 7 | 11 | 0.60903 |  | 218 | 109 | 30 | Riverdale | 4.16kV | SR02 | Crew responded to a call from the Fire Dept of a wire down at 645 Echo Dr. When the crew arrived they found that a Hiab boom truck had made contact with the open wire buss running down Echo Dr and the primary neutral was on the ground Power to three transformers on Riverdale,Mount Pleasant, Echo, and Brown st was interrupted for 2 hours for repairs to be made | Ottawa | Foreign Interference | Vehicle
5509 | 2004 | 7 | 16 | 0.56597 |  | 80 | 48 | 36 | Riverdale | 4.16kV | SR02 | White phase local on Belgrave was opened feeding 4 transformers to clear a burning tree. | Ottawa | Tree Contacts | Inadequate Trimming
18857 | 2011 | 7 | 30 | 0.11319 |  | 256 | 883 | 362 | Riverdale | 4.16kV | SR02 | Switch S27599 blue phase was found with lead off switch. Circuit was isolated to allow crew to make repairs. Riverdale (SR02) ID#18857 | Ottawa | Defective Equipment
14945 | 2009 | 8 | 14 | 0.51597 |  | 67 | 13 | 12 | Riverdale | 4.16kV | SR02 | Transformer #X31684 located at 19 Mount Pleasant Ave isolated to connect a new service | Ottawa | Scheduled Outage | Construction
11075 | 2007 | 8 | 16 | 0.40625 |  | 66 | 8 | 7 | Riverdale | 4.16kV | SR02 | At 09:45 trans at 28 Mason was isolated to repair a primary neutral | Ottawa | Scheduled Outage | Repair
9396 | 2006 | 10 | 6 | 0.43056 |  | 138 | 16 | 7 | Riverdale | 4.16kV | SR02 | Transformer #OTT4629 located at 26 Merritt isolated for removal. PC10A #841 | Ottawa | Scheduled Outage | Preventive Maintenance
15376 | 2009 | 11 | 10 | 0.70833 |  | 54 | 4 | 5 | Riverdale | 4.16kV | SR02 | Transformer #X29757 located at 16 Belgrave isolated to hook up new service | Ottawa | Scheduled Outage | Construction
6006 | 2004 | 12 | 10 | 0.46528 |  | 32 | 4 | 7 | Riverdale | 4.16kV | SR02 | Replaced the triplex service at 70 Merritt in Ottawa. | Ottawa | Defective Equipment | Repair
17470 | 2011 | 1 | 6 | 0.375 |  | 254 | 51 | 12 | Riverdale | 4.16kV | SR03 | Transformer #X29778 located at 139 McGillivray St opened by crew to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
17486 | 2011 | 1 | 13 | 0.375 |  | 252 | 50 | 12 | Riverdale | 4.16kV | SR03 | At 09:00 trans isolated at 167 MCGILLIVRAY ST OTTAWA in order to replace a pole | Ottawa | Scheduled Outage | Repair
15660 | 2010 | 1 | 16 | 0.57639 |  | 10 | 1 | 6 | Riverdale | 4.16kV | SR03 | Transformer #X29775 located at 179 Mcgillivray isolated to change arrestor | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17875 | 2011 | 4 | 11 | 0.26667 |  | 384 | 32 | 5 | Riverdale | 4.16kV | SR03 | Transformer X29795 at Main Street - defective transformer | Ottawa | Lightning | Direct Strike
17888 | 2011 | 4 | 11 | 0.26667 |  | 250 | 21 | 5 | Riverdale | 4.16kV | SR03 | Cutout replaced at transformer X29795 located at 141 Main Street - lightning strike | Ottawa | Lightning | Lightening Strike on adjacent circuit
5051 | 2004 | 4 | 24 | 0.67778 |  | 35 | 8 | 14 | Riverdale | 4.16kV | SR03 | Main lead for cutout to transformer at 202 Main let go. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20653 | 2012 | 5 | 29 | 0.11806 |  | 1 | 5 | 278 | Riverdale | 4.16kV | SR03 | SR03 breaker tripped, due to lightning storm in area | Ottawa | Adverse Weather | Lightning
20654 | 2012 | 5 | 29 | 0.62708 |  | 102 | 12 | 7 | Riverdale | 4.16kV | SR03 | Transformer X29974 at 199 Keehoe St. refused due to branch contact | Ottawa | Tree Contacts | Tree Limb Fallen
18274 | 2011 | 6 | 1 | 0.70139 |  | 9 | 41 | 275 | Riverdale | 4.16kV | SR03 | SR03 tripped at the same time as SR00N. SR03 closed and held via SCADA. All load restored. SR00N to be patrolled trpped again. | Ottawa | Adverse Weather | Wind
10826 | 2007 | 7 | 9 | 0.45833 |  | 219 | 47 | 13 | Riverdale | 4.16kV | SR03 | Isolated transformer OTT2017 at 127 Drummond St to replace services | Ottawa | Scheduled Outage | Construction
10929 | 2007 | 7 | 23 | 0.37569 |  | 139 | 32 | 14 | RIVERDALE | 4.16kV | SR03 | Transformer #OTT3883 at 60 Lees Ave isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
10933 | 2007 | 7 | 23 | 0.55208 |  | 93 | 8 | 5 | Riverdale | 4.16kV | SR03 | Transformer #K1058 at 118 Lees Ave isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
19140 | 2011 | 9 | 12 | 0.45833 |  | 50 | 3 | 4 | Riverdale | 4.16kV | SR03 | Transformer #X29904 located at 47 Clegg St opened by crew to replace transformer. | Ottawa | Scheduled Outage | Construction
19185 | 2011 | 9 | 15 | 0.38194 |  | 170 | 20 | 7 | Riverdale | 4.16kV | SR03 | Transformer #X26089 located at 143 Drummond St opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
19188 | 2011 | 9 | 16 | 0.37847 |  | 175 | 26 | 9 | Riverdale | 4.16kV | SR03 | Isolated transformer X34828 at 175 Drummond St to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Construction
11434 | 2007 | 10 | 1 | 0.83958 |  | 15 | 2 | 10 | Riverdale | 4.16kV | SR03 | At 8:09pm a transformer at 196 Main Street was isolated to replace a hotline clamp, 10 customers were affected for 15min. ID 11434. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7430 | 2005 | 10 | 6 | 0.47708 |  | 63 | 10 | 10 | Riverdale | 4.16kV | SR03 | Isolated Transfomer at 32 Herridge to install new service | Ottawa | Scheduled Outage | Preventive Maintenance
19340 | 2011 | 10 | 7 | 0.48611 |  | 39 | 3 | 5 | RIVERDALE | 4.16kV | SR03 | Trans X27996 at 139 Glenora St was isolated in order to upgrade sec services | Ottawa | Scheduled Outage | Preventive Maintenance
19360 | 2011 | 10 | 12 | 0.35417 |  | 218 | 15 | 4 | Riverdale | 4.16kV | SR03 | Transformer #X27999 located at 169 Glenora St opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
17308 | 2010 | 11 | 19 | 0.375 |  | 210 | 38 | 11 | Riverdale | 4.16kV | SR03 | overhead transformer X26287 at 167 McGillvary was opened to replace pole. | Ottawa | Scheduled Outage | Preventive Maintenance
9795 | 2006 | 12 | 5 | 0.36806 |  | 175 | 23 | 8 | Riverdale | 4.16kV | SR03 | At 08:50 Trans OTT4339 at 153 McGillivray St was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
17437 | 2010 | 12 | 20 | 0.43403 |  | 35 | 5 | 8 | Riverdale | 4.16kV | SR03 | Transformer #X29776 located at 160 Mcgillivray opened by crew due to re-insulating | Ottawa | Scheduled Outage | Construction
19751 | 2011 | 12 | 20 | 0.33333 |  | 165 | 44 | 16 | RIVERDALE | 4.16kV | SR03 | Transformer X29794 at 415 Echo Drive isolated to allow for transfer of plant | Ottawa | Scheduled Outage | Preventive Maintenance
19754 | 2011 | 12 | 21 | 0.33333 |  | 240 | 44 | 11 | RIVERDALE | 4.16kV | SR03 | Transformer X21533 at 33 Herridge St. Isolated to allow transfer of plant | Ottawa | Scheduled Outage | Construction
12180 | 2008 | 3 | 27 | 0.41667 |  | 55 | 16 | 17 | Riverdale | 4.16kV | SR04 | Isolated transformer X21654 at 12 Letchworth Rd to replace pole | Ottawa | Scheduled Outage | Construction
12181 | 2008 | 3 | 27 | 0.41667 |  | 55 | 16 | 17 | Riverdale | 4.16kV | SR04 | Isolated transformer X21654 at 12 Letchworth Rd to replace pole | Ottawa | Scheduled Outage | Construction
12189 | 2008 | 3 | 28 | 0.52083 |  | 85 | 24 | 17 | Riverdale | 4.16kV | SR04 | isolated transformer X21554 at 12 Letchworth Rd to install new pole | Ottawa | Scheduled Outage | Construction
12235 | 2008 | 4 | 4 | 0.40278 |  | 105 | 21 | 12 | RIVERDALE | 13.2kV | SR04 | Transformer #X34437 at 7 Burnham isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
12250 | 2008 | 4 | 8 | 0.40278 |  | 25 | 7 | 17 | Riverdale | 4.16kV | SR04 | Isolated transformer X21654 at 12 Letchworth Rd to replace the pole | Ottawa | Scheduled Outage | Construction
12251 | 2008 | 4 | 8 | 0.4375 |  | 30 | 6 | 11 | Riverdale | 4.16kV | SR04 | Isolated transformer X29764 at 21 Burnham Rd to replace the pole | Ottawa | Scheduled Outage | Construction
12301 | 2008 | 4 | 17 | 0.39792 |  | 153 | 26 | 10 | RIVERDALE | 4.16kV | SR04 | Transformer at 12 Letchworth Rd isolated to allow for pole change | Ottawa | Scheduled Outage
14412 | 2009 | 5 | 26 | 0.39583 |  | 5 | 1 | 10 | Riverdale | 4.16kV | SR04 | Transformer #X29780 located at 125 Glenora St isolated for crew to get oil sample | Ottawa | Scheduled Outage | Preventive Maintenance
10894 | 2007 | 7 | 17 | 0.375 |  | 95 | 17 | 11 | Riverdale | 4.16kV | SR04 | Transformer #OTT2775 located at 60 Glengarry isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10895 | 2007 | 7 | 17 | 0.375 |  | 85 | 20 | 14 | Riverdale | 4.16kV | SR04 | Transformer #OTT2774 located at 42 Glengarry isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10896 | 2007 | 7 | 17 | 0.45139 |  | 70 | 8 | 7 | Riverdale | 4.16kV | SR04 | Transformer #OTT4768 located at 88 Onslow isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10899 | 2007 | 7 | 17 | 0.54167 |  | 120 | 26 | 13 | RIVERDALE | 4.16kV | SR04 | Transformer #OTT1034 at 7 Burnham isolated to allow for PCB transformer change | Ottawa | Scheduled Outage | Preventive Maintenance
7470 | 2005 | 10 | 16 | 0.95972 |  | 43 | 121 | 169 | SR | 4.16kV | SR04 | Primary conductor brought down by tree contact between Rideau Garden & Bullock. | Ottawa | Tree Contacts | Tree Limb Fallen
4364 | 2003 | 10 | 31 | 0.52847 |  | 99 | 21 | 13 | Riverside | 4.16kV | SR04 | Replace connections and repair 2 services. | Ottawa | Defective Equipment
17225 | 2010 | 11 | 5 | 0.40278 |  | 45 | 9 | 12 | Riverdale | 4.16kV | SR04 | At 09:40 transformer X29784 was isolated to allow crew to install new service. 12 customers were affected for 45 minutes. Riverdale (SR04) ID# 17225 | Ottawa | Scheduled Outage
17243 | 2010 | 11 | 8 | 0.48056 |  | 58 | 12 | 12 | RIVERDALE | 4.16kV | SR04 | Transformer X29784 at 33 Hazel St. Isolated to connect a new service | Ottawa | Scheduled Outage | Construction
19742 | 2011 | 12 | 19 | 0.52778 |  | 155 | 18 | 7 | Riverdale | 4.16kV | SR04 | Isolated transformer X29788 at 413 Echo Dr and X29789 at 409 Echo Dr to replace pole's | Ottawa | Scheduled Outage | Construction
4752 | 2004 | 2 | 2 | 0.42361 |  | 150 | 35 | 14 | SR | 4.16kV | SR06 | Tx336 @ 44 Bellwood was opened to change the Tx. 14 customers affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7903 | 2006 | 2 | 8 | 0.51389 |  | 8 | 1 | 9 | Riverdale | 4.16kV | SR06 | Isolated transformer OTT5426 at 414 Riverdale to replace live line clamp | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
12083 | 2008 | 2 | 27 | 0.45833 |  | 109 | 18 | 10 | Riverdale | 4.16kV | SR06 | Transformer #X30380 located at 360 Sunnyside Ave isolated to repair defective mole. | Ottawa | Scheduled Outage | Repair
12135 | 2008 | 3 | 12 | 0.38542 |  | 210 | 35 | 10 | RIVERDALE | 13.2kV | SR06 | TRANSFORMER #X30384 AT 410 SUNNYSIDE ISOLATED TO ALLOW FOR POLE REPLACEMENT | Ottawa | Scheduled Outage | Preventive Maintenance
12136 | 2008 | 3 | 12 | 0.54167 |  | 149 | 25 | 10 | RIVERDALE | 13.2kV | SR06 | TRANSFORMER #X36459 AT 427 SUNNYSIDE ISOLATED TO ALLOW FOR POLE REPLACEMENT | Ottawa | Scheduled Outage | Construction
12149 | 2008 | 3 | 17 | 0.39167 |  | 126 | 32 | 15 | RIVERDALE SR | 4.16kV | SR06 | Transformer #X30387 at 451 Sunnyside isolated to allow for pole change. | Ottawa | Scheduled Outage | Construction
12151 | 2008 | 3 | 18 | 0.40278 |  | 125 | 19 | 9 | Sunnyside | 4.16kV | SR06 | At 09:40 trans at 481 Sunnyside was isolated in order for a pole change | Ottawa | Scheduled Outage | Repair
4928 | 2004 | 3 | 23 | 0.68056 |  | 25 | 4 | 10 | Riverdale | 4.16kV | SR06 | Transformer P136 at 1255 Bank was interrupted to repair defective switch. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15853 | 2010 | 3 | 26 | 0.38889 |  | 268 | 152 | 34 | Riverdale SR | 4.16kV | SR06 | Crew isolated an O/H section of SR06 to allow crews to upgrade cunductor and transfer plant to new poles. | Ottawa | Scheduled Outage | Construction
8113 | 2006 | 4 | 6 | 0.38194 |  | 40 | 7 | 11 | Riverdale | 4.16kV | SR06 | Transformer #OTT6151 located at 367 Sunnyside isolated due to a change over of service | Ottawa | Scheduled Outage | Construction
6534 | 2005 | 5 | 11 | 0.091667 |  | 120 | 16 | 8 | Riverdale | 4.16kV | SR06 | leaking transformer at 155 belmont was replaced. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16122 | 2010 | 5 | 22 | 0.12639 |  | 172 | 32 | 11 | Riverdale | 4.16kV | SR06 | fire at 377 Sunnyside caused secondary bus to come down. Transformer X30382 was opened to make repairs. | Ottawa | Adverse Environment | Fire
6590 | 2005 | 5 | 24 | 0.28819 |  | 80 | 85 | 332 | SR | 4.16kV | SR06 | Muldoon rpts ampact connection failed on red phase at Leonard & Sunnyside, cct opened via SCADA to make repairs. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10553 | 2007 | 6 | 7 | 0.60833 |  | 137 | 14 | 6 | Riverdale | 4.16kV | SR06 | At 14:36 trans at 165 Cameron Rd was isolated in order to relocate primary conductor | Ottawa | Scheduled Outage | Repair
10631 | 2007 | 6 | 14 | 0.5 |  | 50 | 8 | 10 | Riverdale | 4.16kV | SR06 | Transformer #OTT1123 located at 111 Cameron isolated due to lowering existing 4kv on to new pole | Ottawa | Scheduled Outage | Construction
10646 | 2007 | 6 | 18 | 0.39722 |  | 173 | 12 | 4 | Riverdale | 4.16kV | SR06 | isolated transformer OTT1121 at 74 Cameron Ave. to replace pole | Ottawa | Scheduled Outage | Construction
10691 | 2007 | 6 | 21 | 0.41319 |  | 155 | 52 | 20 | Riverdale | 4.16kV | SR06 | Isolated K544 @ 21 Pentry to transfer cables to new pole. | Ottawa | Scheduled Outage | Construction
10696 | 2007 | 6 | 21 | 0.40625 |  | 206 | 82 | 24 | Riverdale | 4.16kV | SR06 | At 09:45 trans at 1 Pentry was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Repair
10747 | 2007 | 6 | 27 | 0.38889 |  | 100 | 27 | 16 | Riverdale | 4.16kV | SR06 | Interrupted transformer OTT3028 at 50 Harvard Ave. for pole change. | Ottawa | Scheduled Outage | Construction
18540 | 2011 | 6 | 28 | 0.25 |  | 185 | 46 | 15 | Riverdale | 4.16kV | SR06 | X30396 at 1103 Bank St was isolated to string triplex thru open conductor | Ottawa | Scheduled Outage | Emergency Services Request
10762 | 2007 | 6 | 29 | 0.38194 |  | 215 | 25 | 7 | Riverdale | 4.16kV | SR06 | Transformer #OTT5227 located at 9 Raleigh isolated due to voltage conversion & new pole construction | Ottawa | Scheduled Outage | Construction
10863 | 2007 | 7 | 12 | 0.39583 |  | 170 | 23 | 8 | Riverdale |  | SR06 | Transformer #OTT4797 at 12 Osborne isolated to allow for pole replacement | Ottawa | Scheduled Outage | Construction
16472 | 2010 | 7 | 14 | 0.39583 |  | 280 | 70 | 15 | Riverdale | 4.16kV | SR06 | Transformer #X31633 located at 21 Willard opened by crew to transfer U/G service | Ottawa | Scheduled Outage | Construction
3792 | 2003 | 7 | 27 | 0.93681 |  | 31 | 4 | 7 | Riverdale | 4.16kV | SR06 | Transformer #6147 at 383 Sunnyside was interrupted to replace defective cutout switch. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10979 | 2007 | 8 | 1 | 0.375 |  | 215 | 14 | 4 | Riverdale | 4.16kV | SR06 | Transformer #OTT1116 located at 167 Cameron Ave isolated due to transformer conversion | Ottawa | Scheduled Outage | Construction
16674 | 2010 | 8 | 5 | 0.375 |  | 225 | 56 | 15 | Riverdale | 4.16kV | SR06 | Transformer X31633 @ 19 willard opened due to storm. | Ottawa | Adverse Weather
16680 | 2010 | 8 | 5 | 0.35417 |  | 280 | 84 | 18 | Riverdale | 4.16kV | SR06 | crew opened 4kv overhead transformer X34440 at reat of 29 Willard to remove tree. | Ottawa | Tree Contacts | Tree Limb Fallen
11005 | 2007 | 8 | 7 | 0.44306 |  | 140 | 30 | 13 | Riverdale | 4.16kV | SR06 | At 10:38 trans at 354 Sunnyside Ave was isolated for trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11041 | 2007 | 8 | 13 | 0.43056 |  | 40 | 7 | 10 | Sunnyside | 4.16kV | SR06 | At 10:20 trans OTT1123 was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
14943 | 2009 | 8 | 13 | 0.67708 |  | 23 | 5 | 13 | Riverdale | 4.16kV | SR06 | Transformer #X30398 located at 1113 Bank St isolated to change triplex service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11063 | 2007 | 8 | 15 | 0.375 |  | 220 | 11 | 3 | Sunnyside | 4.16kV | SR06 | Transformer #OTT3910 located at 115 Leonard Ave isolated to install pole | Ottawa | Scheduled Outage | Construction
11109 | 2007 | 8 | 20 | 0.53472 |  | 150 | 28 | 11 | Riverdale | 4.16kV | SR06 | At 12:50 trans OTT6692 at 6 Windsor Ave was isoalted in order to transfer plant | Ottawa | Scheduled Outage | Repair
11113 | 2007 | 8 | 21 | 0.41667 |  | 40 | 3 | 5 | Riverdale | 4.16kV | SR06 | Transformer located at 150 Cameron isolated due to upgrading transformer | Ottawa | Scheduled Outage | Preventive Maintenance
11164 | 2007 | 8 | 27 | 0.40278 |  | 140 | 14 | 6 | Sunnyside | 4.16kV | SR06 | Isolated transformer OTT1114 at 154 Cameron Ave to replace pole | Ottawa | Scheduled Outage | Construction
11168 | 2007 | 8 | 28 | 0.38542 |  | 150 | 25 | 10 | Riverdale | 4.16kV | SR06 | Isolated transformer OTT1123 at 111 Cameron Ave to replace pole | Ottawa | Scheduled Outage | Construction
11224 | 2007 | 8 | 31 | 0.37153 |  | 175 | 29 | 10 | Riverdale | 4.16kV | SR06 | Isolated transformer OTT1121 at 71 Cameron Ave to replace the pole | Ottawa | Scheduled Outage | Construction
11260 | 2007 | 9 | 6 | 0.375 |  | 210 | 66 | 19 | RIVERDALE | 13.2kV | SR06 | TRANSFORMER #OTT4206 - X31910 AT 1 MARCO LANE ISOLATED TO ALLOW FOR POLE REPLACEMENT | Ottawa | Scheduled Outage | Construction
16901 | 2010 | 9 | 8 | 0.40347 |  | 255 | 64 | 15 | Riverdale DS | 4.16kV | SR06 | Transformer X31633 at 14 Fairburn was opened to alllow crews to relocate conductor. | Ottawa | Scheduled Outage | Construction
11343 | 2007 | 9 | 20 | 0.31389 |  | 118 | 197 | 100 | Riverdale | 4.16kV | SR06 | Voltage conversion on Wendover Chelsey and Warrington from 4kv to 13 kv | Ottawa | Scheduled Outage | Construction
11348 | 2007 | 9 | 20 | 0.54861 |  | 80 | 19 | 14 | Riverdale | 4.16kV | SR06 | Transformer #OTT6576 at 92 Cameron isolated to allow for pole replacement | Ottawa | Scheduled Outage | Construction
11357 | 2007 | 9 | 21 | 0.38056 |  | 57 | 21 | 22 | Riverdale | 4.16kV | SR06 | V00223 at 18 Rideau River Lane isolated to allow for voltage conversion | Ottawa | Scheduled Outage | Construction
11374 | 2007 | 9 | 24 | 0.54514 |  | 42 | 31 | 45 | Riverdale | 4.16kV | SR06 | K544 isolated to allow crew to convert line section from 4kv to 13kv. Units 1 to 45 on Pentry were affected. | Ottawa | Scheduled Outage
11394 | 2007 | 9 | 27 | 0.39583 |  | 60 | 15 | 15 | Riverdale | 13.2kV | SR06 | At 09:30 trans 11 Osborne Ave was isolated to upgrade plant | Ottawa | Scheduled Outage | Preventive Maintenance
11400 | 2007 | 9 | 27 | 0.39583 |  | 62 | 31 | 30 | Riverdale | 4.16kV | SR06 | Circuit SR06 O/H section and transformer TP4760 on Ssborne St in Ottawa isolated for conversion from 4 Kv to 13 Kv. | Ottawa | Scheduled Outage | Construction
11551 | 2007 | 10 | 18 | 0.40625 |  | 225 | 34 | 9 | Riverdale | 4.16kV | SR06 | Transformer #OTT651 located at 112 Aylmer isolated due to stringing in new primary | Ottawa | Scheduled Outage | Construction
9495 | 2006 | 10 | 23 | 0.42361 |  | 77 | 17 | 13 | Riverdale | 4.16kV | SR06 | Transformer was replaced under the pcb program @ 24 Leonard | Ottawa | Scheduled Outage | Preventive Maintenance
11634 | 2007 | 10 | 31 | 0.36458 |  | 205 | 154 | 45 | Riverdale | 4.16kV | SR06 | The O/H on Leonard & Sunnyside was isolated for 4Kv to 13Kv conversion. | Ottawa | Scheduled Outage | Construction
15427 | 2009 | 11 | 26 | 0.39236 |  | 212 | 141 | 40 | Riverdale | 4.16kV | SR06 | SR06 blue phase run off at 220 Sunny was isolated to replace 3 poles | Ottawa | Scheduled Outage
7693 | 2005 | 12 | 6 | 0.45972 |  | 103 | 12 | 7 | Riverdale | 4.16kV | SR06 | Transformer #OTT1391 located at 5 Chesley St isolated due to a broken cut out | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11829 | 2007 | 12 | 11 | 0.45833 |  | 60 | 14 | 14 | Riverdale | 4.16kV | SR06 | Isolated transformer OTT6152 at 399 Sunnyside Ave to transfer hydro plant | Ottawa | Scheduled Outage | Construction
15619 | 2010 | 1 | 6 | 0.45486 |  | 8 | 1 | 10 | Riverdale | 4.16kV | SR07 | Isolated transformer X26270 at 121 Fentiman Ave to repair service | Ottawa | Scheduled Outage | Emergency Services Request
5096 | 2004 | 5 | 4 | 0.47708 |  | 68 | 216 | 191 | SR | 4.16kV | SR07 | Crew found defective connection at corner pole allowing pat to fall into other phase at Riverdale & Belmont. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5371 | 2004 | 6 | 24 | 0.78194 |  | 437 | 138 | 19 | Riverdale | 4.16kV | SR07 | Fuse to O/H transformer at 223 Sunnyside found blown from tree contact due to heavy wind storm. Restoration was delayed due to a parked car preventing access for tree removal. | Ottawa | Tree Contacts
18581 | 2011 | 7 | 4 | 0.60069 |  | 30 | 4 | 8 | Riverdale | 4.16kV | SR07 | Isolated transformer X31654 at 93 Fentiman Ave to remove vines from around the switch and the transformer | Ottawa | Scheduled Outage | Preventive Maintenance
10913 | 2007 | 7 | 19 | 0.55903 |  | 140 | 9 | 4 | Riverdale | 4.16kV | SR07 | Transformer #OTT2346 located at 107 Fentiman isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10939 | 2007 | 7 | 24 | 0.375 |  | 145 | 14 | 6 | Riverdale | 4.16kV | SR07 | Transformer #OTT5429 located at 478 Riverdale isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
7038 | 2005 | 7 | 28 | 0.36528 |  | 28 | 5 | 10 | Riverdale | 13.2kV | SR07 | Isolated transformer # 2347 at 121 Fentiman to install new service | Ottawa | Scheduled Outage
16650 | 2010 | 8 | 4 | 0.65417 |  | 6 | 31 | 308 | Riverdale | 4.16kV | SR07 | SR07 auto-reclosed-auto and stayed off during heavy rain & lightning. Breaker closed manually from SCADA. | Ottawa | Unknown/Other
15210 | 2009 | 10 | 4 | 0.33819 |  | 247 | 1260 | 306 | Riverdale | 13.2kV | SR07 | At 7:54am, customers called in to reports a downed overhead conductor. System & 24-7 isolated to allow crews to make repairs to overhead circuit, 306 customers were affected and power was restored at 12:14pm. Riverdale Substation (SR07). ID#15210. | Ottawa | Defective Equipment
17099 | 2010 | 10 | 12 | 0.52431 |  | 65 | 18 | 17 | Riverdale | 4.16kV | SR07 | Transformer #X31639 located at 223 Sunnyside opened by Sproule to change triplex | Ottawa | Scheduled Outage | Construction
4676 | 2004 | 1 | 5 | 0.49792 |  | 117 | 351 | 180 | SR | 4.16kV | SR08 | O/H was patrolled, cable to riser was tested, all OK. Breaker closed via scada, electrical & mechanical indicators checked at station showed breaker operating but no potential at cable riser to O/H. Load transferred to SR00S & SR08 cable isolated. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12055 | 2008 | 2 | 18 | 0.22222 |  | 145 | 19 | 8 | Riverdale Sub | 4.16kV | SR08 | At 5:20am PC10A# 000332 issued to Lindsay LeFaivre to make repairs in manhole on Bank St near Cameron, Mole water seal failed in Manhole , 8 customers afffeted for …min. ID#12055. | Ottawa | Adverse Weather | Rain
5231 | 2004 | 5 | 31 | 0.82292 |  | 37 | 3 | 5 | RIVERDALE | 4.16kV | SR08 | Isotate transformer OTT 335 at 21 Bellwood to repair secondary service with tree on service. | Ottawa | Tree Contacts | Tree Fallen
18371 | 2011 | 6 | 8 | 0.76667 |  | 351 | 1989 | 340 | Riverdale | 4.16kV | SR08 | phase of SR00S came down into SR08 circuit. SR08, and SR00S were isolated. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20719 | 2012 | 6 | 8 | 0.71944 |  | 724 | 1338 | 412 | Riverdale | 4.16kV | SR08 | OFD reports wires down and wires sparking at Brighton and Bristol, S Cunningham request to dump circuit apon arrival. | Ottawa | Tree Contacts | Tree Limb Fallen
20723 | 2012 | 6 | 8 | 0.73056 |  | 708 | 1015 | 86 | Riverdale | 4.16kV | SR08 | During thunder storm a tree fall on Brighton causing the overhead conductor to break at 4 spans. It also damaged an overhead transformer at 89 Brighton, and pulled both customer services off the homes at 89 & 91 Brighton. | Ottawa | Tree Contacts | Tree Fallen
20725 | 2012 | 6 | 9 | 0.73056 |  | 876 | 1064 | 412 | Rverdale | 4.16kV | SR08 | Tree fall during thunder storm pulling down 4 spans of overhead conductor and damaged a overhead transformer 89 Brighton. Also both customer services at 91 & 89 Brighton were pulled off the homes. | Ottawa | Tree Contacts | Tree Fallen
10633 | 2007 | 6 | 15 | 0.3125 |  | 30 | 8 | 15 | Riverdale | 4.16kV | SR08 | Transformer #55D4D-0211 located at 55 Cameron isolated to put new transformer on new pole | Ottawa | Scheduled Outage | Construction
18721 | 2011 | 7 | 18 | 0.80069 |  | 260 | 129 | 340 | Riverdale | 4.16kV | SR08 | 1 phase of a 3 phase lateral brought down required SR08 breaker opened to allow for live line cut of the phase, secured for construction crew to respond and repair. | Ottawa | Tree Contacts | Tree Fallen
10946 | 2007 | 7 | 24 | 0.54167 |  | 120 | 14 | 7 | Riverdale | 4.16kV | SR08 | At 13:00 trans at 418 Riverdale was isolated in order for a PCB trans change | Gloucester | Scheduled Outage | Preventive Maintenance
16651 | 2010 | 8 | 4 | 0.65417 |  | 6 | 32 | 322 | Riverdale |  | SR08 | SR08 auto-reclosed-auto and stayed off during heavy rain & lightning. Breaker closed manually from SCADA. | Ottawa | Unknown/Other
19060 | 2011 | 8 | 31 | 0.52431 |  | 11 | 2 | 10 | Riverdale | 4.16kV | SR08 | Transformer X31697 at 29 Brighton Ave isolated to remove vines from wires | Ottawa | Tree Contacts | Tree Limb Fallen
16910 | 2010 | 9 | 9 | 0.21181 |  | 28 | 5 | 11 | Riverdale SR | 4.16kV | SR08 | Trnasformer X31667 @ 105 Bellwood was opened to disconnect 2 services damaged by a fallen tree limb.. (101 & 103 Bellwood) | Ottawa | Tree Contacts | Tree Limb Fallen
16913 | 2010 | 9 | 9 | 0.86111 |  | 36 | 7 | 11 | Riverdale | 4.16kV | SR08 | Transformer #X31667 located at 101 Bellwood opened by crew to reconnect service after damages from tree contact repaired | Ottawa | Tree Contacts | Tree Fallen
9413 | 2006 | 10 | 10 | 0.4375 |  | 90 | 15 | 10 | Riverdale | 4.16kV | SR08 | Transformer #OTT2765 located at 111 Riverdale was isolated for service upgrade. PC10A #1736 | Ottawa | Scheduled Outage | Preventive Maintenance
9559 | 2006 | 10 | 30 | 0.46875 |  | 30 | 4 | 8 | Riverdale | 4.16kV | SR08 | Transformer located at 99 Fourth Ave isolated to allow new service. PC10A #1773 | Ottawa | Scheduled Outage | Preventive Maintenance
17404 | 2010 | 12 | 10 | 0.39583 |  | 158 | 29 | 11 | Riverdale | 4.16kV | SR08 | Transformer #X31663 located at 41 Brighton opened by crew for clearance for contractor doing eavestroughing | Ottawa | Scheduled Outage | Construction
7715 | 2005 | 12 | 12 | 0.49028 |  | 152 | 20 | 8 |  | 4.16kV | SR08 | Pole change at 99 Bellwood by Bruce Kerfoot |  | Unknown/Other
9884 | 2006 | 12 | 26 | 0.61667 |  | 75 | 225 | 180 | RIVERDALE | 4.16kV | SR08 | SR08 circuit opened due to possible P/P/H failure. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15646 | 2010 | 1 | 13 | 0.38194 |  | 131 | 98 | 45 | Riverdale | 4.16kV | SR09 | S 17138 on Southern Ave at Toronto St opened to allow tree removal. | Ottawa | Scheduled Outage | Preventive Maintenance
19948 | 2012 | 2 | 2 | 0.32361 |  | 113 | 17 | 9 | Riverdale | 4.16kV | SR09 | Transformer #X37960 located at 92 Southern opened due to squirrel contact | Ottawa | Foreign Interference | Animal
14016 | 2009 | 3 | 2 | 0.48611 |  | 35 | 5 | 8 | RIVERDALE | 4.16kV | SR09 | transformer X31691 at 51 Glencairn isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
14019 | 2009 | 3 | 3 | 0.59236 |  | 110 | 64 | 35 | Riverdale | 4.16kV | SR09 | A broken switch at 433 Main at Dip3 in the Elliot/Centennial area, | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17959 | 2011 | 4 | 18 | 0.83056 |  | 67 | 19 | 17 | Riverdale | 4.16kV | SR09 | Defective cutout at transformer X31965 at 124 Southern Dr - repaired by 24/7 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17974 | 2011 | 4 | 20 | 0.34306 |  | 126 | 17 | 8 | Riverdale | 4.16kV | SR09 | Transformer #X31695 located at 30 Southern opened up due to defective switch | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20374 | 2012 | 4 | 24 | 0.35417 |  | 115 | 38 | 20 | Riverdale | 4.16kV | SR09 | Transformer X31953 isolated by contractor for pole change at Riverside and Glenview | Ottawa | Scheduled Outage
18054 | 2011 | 4 | 28 | 0.59444 |  | 1385 | 8864 | 384 | Riverdale | 4.16kV | SR09 | SR09 tripped during wind/lightning storm. Crews repaired line and restored power. | Ottawa | Adverse Weather | Wind
20429 | 2012 | 5 | 1 | 0.33333 |  | 480 | 176 | 22 | Riverdale |  | SR09 | At 8:00 crews isolated a section of SR09 from S29864 to end of line. 22 customers affected. Riverdale SR09 ID# 20429 | Ottawa | Scheduled Outage | Construction
20447 | 2012 | 5 | 2 | 0.33333 |  | 390 | 403 | 62 | Riverdale | 4.16kV | SR09 | SR09 Blue phase section was isolated from S29864 to EOL to allow crew to replace poles. | Ottawa | Scheduled Outage | Construction
16041 | 2010 | 5 | 5 | 0.54931 |  | 94 | 17 | 11 | Riverdale | 4.16kV | SR09 | Transformer #X34843 located at 33 Toronto St opened by crew to relocate service | Ottawa | Scheduled Outage | Construction
20475 | 2012 | 5 | 7 | 0.35417 |  | 245 | 33 | 8 | Riverdale | 4.16kV | SR09 | At 08:30, transformer X31954 was isolated to allow crews to change poles & transfer plant. 8 customers affected for 245 minutes. Riverdale DS (SR09) ID #20475 | Ottawa | Scheduled Outage
20485 | 2012 | 5 | 9 | 0.33333 |  | 390 | 150 | 23 | Riverdale | 4.16kV | SR09 | SR09 W phase section from S14804 to EOL on Glencairn was isolated to allow crew to perform pole replacement | Ottawa | Scheduled Outage | Construction
18185 | 2011 | 5 | 19 | 0.50486 |  | 33 | 5 | 9 | Riverdale | 4.16kV | SR09 | Transformer X31954 @ 67 Glencairn was open to allow crew to remove branch on SR09 circuit. 9 customers were affected. Riverdale (SR09) | Ottawa | Scheduled Outage
12553 | 2008 | 6 | 5 | 0.40278 |  | 260 | 43 | 10 | BRONSON | 4.16kV | SR09 | Transformer at Bronson & Holmwood Ave isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
3563 | 2003 | 6 | 13 | 0.81875 |  | 391 | 26 | 8 | Riverdale Sub | 4.16kV | SR09 | Atree came down on the triplex secondaries at 135 Riverdale. The crew took 2 xfmrs out of service to make repairs. 2 temporary services were installed for 2 homes requiring standpipe repair. | Ottawa | Tree Contacts | Tree Fallen
5317 | 2004 | 6 | 16 | 0.5625 |  | 36 | 6 | 10 | Riverdale | 4.16kV | SR09 | To repair & replace buss at Main & Bullock st. 10 Customers effected in power outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
18425 | 2011 | 6 | 16 | 0.42917 |  | 92 | 15 | 10 | Riverdale | 4.16kV | SR09 | Transformer X31664 @ 147 Sunnyside was opened to allow crew to replace transformer. 10 cusotmers were affected. Riverdale (SR09) | Ottawa | Scheduled Outage
16332 | 2010 | 6 | 26 | 0.79444 |  | 90 | 14 | 9 | Riverdale | 4.16kV | SR09 | Tree contact to open bus during tree trimming cause transformer X37960 at 92 Southern to open. | Ottawa | Tree Contacts | Tree Limb Fallen
10805 | 2007 | 7 | 6 | 0.375 |  | 121 | 40 | 20 | Riverdale | 4.16kV | SR09 | At 09:00 trans at 39 Marco Lane was isoalted for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
14831 | 2009 | 7 | 24 | 0.79167 |  | 300 | 125 | 25 | Riverdale | 4.16kV | SR09 | At 400 Main Street Ottawa.the single phase run off condutor burnt off at the conector and wire fell. | Nepean | Defective Equipment
10950 | 2007 | 7 | 25 | 0.375 |  | 130 | 15 | 7 | RIVERDALE | 4.16kV | SR09 | Crew isolated and replaced transformer OTT2767 at 25 Glencairn Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
16564 | 2010 | 7 | 26 | 0.46875 |  | 60 | 19 | 19 | Riverdale | 4.16kV | SR09 | Isolated transformer X31694 at 10 Bristol for a service Up-grade | Ottawa | Scheduled Outage
18866 | 2011 | 7 | 31 | 0.59375 |  | 15 | 1 | 4 | Riverdale | 4.16kV | SR09 | Transformer #X29949 located at 49 Toronto St opened by crew to put the service back up | Ottawa | Scheduled Outage | Construction
11104 | 2007 | 8 | 20 | 0.38542 |  | 45 | 4 | 6 | Riverdale | 4.16kV | SR09 | Transformer #OTT2769 located at 38 Glencairn isolated due to service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
16908 | 2010 | 9 | 8 | 0.55208 |  | 50 | 8 | 10 | RIVERDALE | 4.16kV | SR09 | Transformer X31686 at 55 Avenue Rd isolated to connect a new service | Ottawa | Scheduled Outage
15158 | 2009 | 9 | 23 | 0.83333 |  | 120 | 22 | 11 | Riverdale | 4.16kV | SR09 | Transformer at 101 Sunnyside X31625 was isolated to renew primary connections | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
4173 | 2003 | 9 | 28 | 0.83333 |  | 205 | 38 | 11 | Riverdale |  | SR09 | Broken cutout at transformer 2771 in rear of 55 Glencairn was replaced. 11 customers on Glencairn & Riverdale affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17025 | 2010 | 9 | 29 | 0.40972 |  | 300 | 60 | 12 | RIVERDALE SR | 4.16kV | SR09 | Transformer X31969 at 151 Riverdale isolated to allow a crane to remove tree | Ottawa | Scheduled Outage | Preventive Maintenance
17026 | 2010 | 9 | 29 | 0.40972 |  | 301 | 60 | 12 | RIVERDALE SR | 4.16kV | SR09 | Transformer X31969 at 151 Riverdale Ave isolated to allow a crane to remove a tree | Ottawa | Scheduled Outage | Preventive Maintenance
19328 | 2011 | 10 | 5 | 0.38542 |  | 283 | 245 | 52 | Riverdale | 4.16kV | SR09 | SR09 from Temp 147 to EOL at 67 Glencairn was isolated to allow forestry crew to remove tree with a crane. | Ottawa | Scheduled Outage | Construction
19582 | 2011 | 11 | 15 | 0.38889 |  | 50 | 11 | 13 | Riverdale | 4.16kV | SR09 | Isolated transformer X31958 at 110 Glenview Ave for a service up-grade | Ottawa | Scheduled Outage | Preventive Maintenance
4515 | 2003 | 11 | 25 | 0.48403 |  | 133 | 11 | 5 | SR | 4.16kV | SR09 | Tx OTT618 @ 15 Avenue st was replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9786 | 2006 | 12 | 3 | 0.20139 |  | 5 | 1 | 10 | Riverdale | 4.16kV | SR09 | O/H Transformer opened to disconnect secondary service at 96 Southern. | Ottawa | Adverse Weather | Ice Storm
9826 | 2006 | 12 | 11 | 0.48264 |  | 110 | 9 | 5 | Riverdale | 4.16kV | SR09 | Isolated Transformer at 171 First Avnue to change a triplex service | Ottawa | Scheduled Outage | Preventive Maintenance
9827 | 2006 | 12 | 11 | 0.40417 |  | 38 | 8 | 12 | Riverdale | 4.16kV | SR09 | Isolated Transformer at 390 First Avenue to replace the triplex service | Ottawa | Scheduled Outage | Preventive Maintenance
7264 | 2005 | 9 | 2 | 0.60069 |  | 50 | 125 | 150 | RIVERSIDE | 4.16kV | SRO3 | SR03 OPENED & LOCKED OUT DUE TO WIND STORM. CIRCUIT WAS PATROLLED NO FAULT FOUND. CIRCUIT CLOSED VIA SCADA. | Ottawa | Adverse Weather | Wind
3100 | 2003 | 1 | 9 | 0.87083 |  | 66 | 1 | 1 | Stafford Rd DS | 8/4.8kV | Stafford RD F2 | RCMP Connaught Range at Shirleys Bay reported no power. Blown transformer fuse replace by 24/7 | Nepean | Unknown/Other
3163 | 2003 | 2 | 4 | 0.90625 |  | 25 | 0 | 1 | Stafford RD | 8/4.8kV | Stafford Rd F6 | Sparking reported at 126 Robertson Rd. (McDonalds) 24/7 reports that the problem is a burning line clamp.Arrangments made with McDonalds for a short interruption to make repairs. | Nepean | Defective Equipment | Equipment Failure - Cause Unknown
9886 | 2006 | 12 | 27 | 0.39583 |  | 125 | 2 | 1 | Startop | 8/4.8kV | Startop F4 | Transformer #GLTE2376 located at 1418 Michael St isolated to change elbow & switches | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
15757 | 2010 | 3 | 2 | 0.14583 |  | 30 | 989 | 1978 | Startop | 8/4.8kV | Startop station | Control panel at S29028 was found opened & no lock on door. | Gloucester | Human Element | Sabotage
10661 | 2007 | 6 | 19 | 0.69792 |  | 20 | 439 | 3432 | Albion | 13.2kV | TA J Bus | Load at Hydro One Albion TS manually interupted due to emergency overlaoding of the Hydro One 84T1 transformer. They had a planned outage to the 84T2 at the time. Hydro Ottawa interupted the TA2AF circuit at 16:43 to relieve load, then Hydro One dumped the J Bus at 16:45. The TA2AF circuit and J Bus were restored at 16:50 with the TA11/UAT1 remaining O/S. The UAT1 was restored via Riverdale at 17:03. | Ottawa | Loss of Supply | HEPC Load Shedding
16464 | 2010 | 7 | 13 | 0.53472 |  | 75 | 12 | 10 | Albion | 13.2kV | TA02 | Transformer #KT244 located at 23 Thornhedge Crt opened by crew to relocate sec U/G | Ottawa | Adverse Environment | Construction
13630 | 2008 | 11 | 17 | 0.57222 |  | 30 | 237 | 474 | Albion | 13.2kV | TA04 | A garbage truck left it's box up and has broken a pole and another pole is leaning at the corner of Kitchener and Bank. A guy wire also was broken off sitting on the secondary. No wires down. Premises cleared and breaker closed to retore circuit to normal. Follow-0up required to make pole repairs. | Ottawa | Foreign Interference | Vehicle
14826 | 2009 | 7 | 24 | 0.99653 |  | 4 | 2 | 25 | Albion TA | 13.2kV | TA05 | TA05, TA06 and TA10 circuits all tripped at the same time one minute later Ottawa fire reports lightning strikes in that area. All breakers were closed and held on first attempt. | Nepean | Lightning
13088 | 2008 | 8 | 18 | 0.68472 |  | 3 | 24 | 470 | ALBION | 13.2kV | TA05 | BREAKER OPENED DUE TO STORM, CLOSED VIA SCADA | Ottawa | Adverse Weather | Lightning
17859 | 2011 | 4 | 8 | 0.54931 |  | 49 | 1432 | 1803 | Albion | 13.2kV | TA06 | TA06 circuit breaker tripped open. Load restored in stages. No cause found. | Ottawa | Unknown/Other | No Apparent Cause
10575 | 2007 | 6 | 8 | 0.82986 |  | 1 | 5 | 279 | Albion | 13.2kV | TA06 | Albion TA06 breaker 2201 & 2205 circuits auto tripped, closed via SCADA. Circuit to be patrolled later. | Ottawa | Adverse Weather | Wind
8585 | 2006 | 6 | 23 | 0.77778 |  | 215 | 64 | 18 | ALBION | 13.2kV | TA06 | Fuse on transformer KT124 at 21 Somero Priv was found broken crew replaced the fuse and restored power | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14827 | 2009 | 7 | 24 | 0.99653 |  | 4 | 107 | 1610 | Albion TA | 13.2kV | TA06 | TA05, TA06 and TA10 circuits all tripped at the same time one minute later Ottawa fire reports lightning strikes in that area. All breakers were closed and held on first attempt. | Nepean | Lightning
19148 | 2011 | 9 | 12 | 0.68819 |  | 7 | 211 | 1807 | Albion TS | 13.2kV | TA06 | TA06 tripped during Lightening Storm. Fire and Police checked clear and breaker was closed back in successfully | Ottawa | Adverse Weather | Lightning
20070 | 2012 | 2 | 28 | 0.42917 |  | 147 | 17 | 7 | Albion | 13.2kV | TA07 | Transformer KT7 @ 10 Ratan was isolated to allow the crew to change heated primary terminations. | Ottawa | Scheduled Outage | Preventive Maintenance
13086 | 2008 | 8 | 18 | 0.68472 |  | 1 | 14 | 848 | ALBION | 13.2kV | TA07 | BREAKER OPENED DUE TO STORM, CLOSED VIA SCADA | Ottawa | Adverse Weather | Lightning
13464 | 2008 | 10 | 29 | 0.045139 |  | 597 | 1168 | 575 | ALBION | 13.2kV | TA07 | TA07 breaker opened from tree on 5102 overhead line section on Bowesville Rd. TA2QZ section was restored up to 5102 line which was left out of service for tree removal. 5102 line & SC1601 lines were both isolated for work protection at 9:55am to remove tree. | Ottawa | Adverse Weather
18517 | 2011 | 6 | 24 | 0.68472 |  | 644 | 5547 | 3416 | Albion | 12/7.2kV | TA09 | SC1504 was struck by lightning and was isolated to allow crew to replace defective switch. Albion (TA09) ID#18517 | Ottawa | Lightning | Direct Strike
16329 | 2010 | 6 | 26 | 0.46389 |  | 89 | 24 | 16 | Albion | 13.2kV | TA09 | Trans KT277 trans fuse failed causing trans outage to 16 custs ,,, trans refused power restored no apparent reason for fuse failure | Ottawa | Unknown/Other | No Apparent Cause
14828 | 2009 | 7 | 24 | 0.99653 |  | 4 | 126 | 1897 | Albion TA | 13.2kV | TA10 | TA05, TA06 and TA10 circuits all tripped at the same time one minute later Ottawa fire reports lightning strikes in that area. All breakers were closed and held on first attempt. | Nepean | Lightning
13087 | 2008 | 8 | 18 | 0.68472 |  | 1 | 32 | 1903 | ALBION | 13.2kV | TA10 | BREAKER OPENED DUE TO STORM, CLOSED VIA SCADA | Ottawa | Adverse Weather | Lightning
14832 | 2009 | 7 | 25 | 0.13125 |  | 34 | 1 | 1 | Albion | 13.2kV | TA13 | The 2209 cable that feeds VT16 trip at the Central heating plant. | Ottawa | Unknown/Other
13629 | 2008 | 11 | 17 | 0.57222 |  | 29 | 509 | 1054 | Albion | 13.2kV | TA15 | Garbage truck left it's box up and has broken a pole and another pole is leaning at the corner of Kitchener and Bank. A guy wire also was broken off sitting on the secondary. No wires down. Premises cleared and breaker closed to restore circuit to normal. Follow up require to make pole repairs. | Ottawa | Foreign Interference | Vehicle
16891 | 2010 | 9 | 7 | 0.8125 |  | 12 | 135 | 673 | Albion |  | TA17 | SCADA indicates TA17 CB A/R & locked out, closed by sytems, affected cahill Sub | Ottawa | Adverse Weather
12287 | 2008 | 4 | 15 | 0.50417 |  | 109 | 7 | 4 | Albion | 4.16kV | TA18 | Isolated transformer KT288 at 213 Twyford St to open Ped Live front to replace connections | Ottawa | Scheduled Outage | Repair
18100 | 2011 | 5 | 5 | 0.83333 |  | 15 | 4 | 18 | Albion | 13.2kV | TA18 | 13kV transaformer KT30 at 16 Archer was isolated to allow crews to remove a broken barrier board. | Ottawa | Scheduled Outage | Repair
17471 | 2011 | 1 | 7 | 0.40208 |  | 52 | 3 | 3 | Albion TS | 13.2kV | TA1AF | At 09:39 TA1AF circuit auto reclosed due to cable fault in MH-3918. 3 customers were affected for for 52 minutes. ID #17471 | Ottawa | Defective Equipment
6644 | 2005 | 6 | 2 | 0.65347 |  | 59 | 769 | 782 | TA | 13.2kV | TA1AF | TA1AF line tripped off when the p/p/h at the riser pole from TA failed. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5271 | 2004 | 6 | 9 | 0.73264 |  | 50 | 652 | 782 | Albion | 13.2kV | TA1AF | TA1AF, TA2AF, TA3AF, & TA1UZ all tripped at the same time for no apparent reason, fire balls reported on hydro lines at 1300 Kitchener and the intersection of Brookfield and Kaladar. | Ottawa | Unknown/Other | No Apparent Cause
9150 | 2006 | 9 | 8 | 0.74028 |  | 4 | 52 | 782 | ALBION | 13.2kV | TA1AF | TA1AF circuit opened due to storm activity. Was closed by scada and held. | Ottawa | Adverse Weather | Lightning
17298 | 2010 | 11 | 18 | 0.0034722 |  | 145 | 2 | 1 | Albion TA | 13.2kV | TA1AF | SW119 including PT149 isolated for repair due to an internal flash @ SW119 @ 1170 Bank st (Canadian Tire) . | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10769 | 2007 | 7 | 1 | 0.46944 |  | 121 | 530 | 977 | Albion | 13.2kV | TA1AF & TA2AF | (TA1AF) TA04 breaker and (TA2AF) TA15 breaker interupted they feed all 6 4kv feeders at Brookfield DS and 7 direct customers on 13kv vaults. All load restored patrols done nothing found, TA2AF TA15 breaker left off. | Ottawa | Unknown/Other | No Apparent Cause
17704 | 2011 | 3 | 11 | 0.64306 |  | 52 | 589 | 778 | Albion | 13.2kV | TA1AN | At 15:26 TA14 CB auto reclosed and then locked out. Crews first restored Cahill station followed by the vaults. 778 customer affected for 52 mins. Cause is still unknown at this time trouble crews are investigating. Albion TA14 ID# 17704 | Ottawa | Unknown/Other | No Apparent Cause
3264 | 2003 | 3 | 17 | 0.42639 |  | 46 | 393 | 583 | Albion | 13.2kV | TA1AN | TA1AN (TA14 ACB) tripped affecting 583 customers in the area of Hunt Club, Cahill & Albion Rds. All customers were restored on TA2AN and 2204. A report of a pole hit on Johnston near Albion was investigated and no damage found. The rest of the line was patrolled and nothing found. TA14 breaker was tried and tripped free. The line was isolated to test the cable. | Ottawa | Unknown/Other
3291 | 2003 | 3 | 23 | 0.13611 |  | 36 | 350 | 583 | Albion | 13.2kV | TA1AN | Defective lightning arrestor caused circuit to open. MDF See outage 3290 - same outage on diff cct. | Ottawa | Defective Equipment
18518 | 2011 | 6 | 24 | 0.90486 |  | 239 | 4 | 1 | Albion | 13.2kV | TA1AN | VT765 had blown fuse in Reyroll gear crew replaced fuses and tested transformers and cables. Albion (TA09) ID#18518 | Ottawa | Lightning
14622 | 2009 | 6 | 26 | 0.79514 |  | 456 | 1573 | 750 | Albion | 13.2kV | TA1AN | KT450 at 199 Southport barrier board became soaked with water, sagged into primary connections and caused flash to ground, primary connections replaced | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8885 | 2006 | 8 | 1 | 0.079861 |  | 108 | 870 | 583 | Albion | 13.2kV | TA1AN | Circuit tripped during heavy storm along with adjacent cct, 2206, | Ottawa | Adverse Weather | Lightning
8913 | 2006 | 8 | 2 | 0.93889 |  | 21 | 35 | 100 | Albion | 13.2kV | TA1AN | Circuit tripped during thunderstorm at the same time as 2204 & AN06 tripped. All 3 circuits run together. Reclosure was in service however SCADA Event Summary does not show breaker attempted a reclose. Breaker was closed manually from SCADA after the area was confirmed clear of emergency calls. TA1AN was partially isolated at the time which reduced the normal customer count. | Ottawa | Adverse Weather | Lightning
7153 | 2005 | 8 | 17 | 0.54722 |  | 6 | 1 | 9 | Albion | 13.2kV | TA1AN | Transformer KT229 located at 55 Rosegarden isolated to open live front pedestal | Ottawa | Scheduled Outage | Repair
7333 | 2005 | 9 | 16 | 0.10417 |  | 80 | 595 | 600 | Albion | 13.2kV | TA1AN | TA1AN & 2206 overhead circuit tripped. TA1AN load was transferred to TA2AN & 2204 circuits. Overhead circuit to be patrolled. | Ottawa | Unknown/Other
4199 | 2003 | 10 | 2 | 0.67639 |  | 8 | 78 | 583 | Albion | 13.2kV | TA1AN | blown lightning arrestors on 2206 o/h line at SC12 on Esson caused TA1AN the adjacent circuit to open. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
5825 | 2004 | 10 | 4 | 0.41528 |  | 47 | 451 | 583 | ALBION | 13.2kV | TA1AN | A mouse in SC1360 caused a phase to phase fault. | Ottawa | Foreign Interference | Animal
5072 | 2004 | 4 | 29 | 0.56944 |  | 81 | 1341 | 1385 | Albion | 13.2kV | TA1AN &TA2AN | TA1An circuit tripped due to an arrester at SW161 blown. TA1AN line was carring the load of TA2An line at the time of the outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8435 | 2006 | 6 | 6 | 0.62153 |  | 33 | 362 | 659 | Albion | 13.2kV | TA1AQ | TA1AQ opened fault. Circuit sectionalized and all customers restored @ 15:28. Section of circuit to be patrolled and fault loacted. Suspected cable fault. | Ottawa | Unknown/Other | No Apparent Cause
5518 | 2004 | 7 | 18 | 0.74514 |  | 82 | 705 | 659 | Albion | 13.2kV | TA1AQ | TA1AQ tripped affecting 659 customers. McArthy T1 load transferred to 5101/TA2QZ line restoring 651 customers. No cause at this time but line was sectionalized & breaker closed to test cable at Albion TS and O/H line to TA1AQ-L3 @ SC29 and it tripped again indicated it is faulted. Remaining customers restored from McArthy when faulted section determined. Patrol later found broken wart style insulator. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18823 | 2011 | 7 | 26 | 0.5125 |  | 5 | 95 | 1144 | Albion | 13.2kV | TA1AQ | TA08 (TA1AQ) circuit opened during lightning storm. Closed back in via SCADA and held. | Ottawa | Adverse Weather | Lightning
8232 | 2006 | 5 | 4 | 0.66736 |  | 4 | 78 | 1175 | Albion | 13.2kV | TA1UZ | TA10 (TA1UZ) circuit opened during lightning storm. Ottawa fire & police reports NO MVA or reports of wires down in the area. Circuit closed via scada all load picked back up. Crew found a blown Pothead on TA1UZ going into Walkey Sub | Ottawa | Adverse Weather | Lightning
5274 | 2004 | 6 | 9 | 0.73264 |  | 53 | 1038 | 1175 | Albion | 13.2kV | TA1UZ | TA1AF, TA2AF, TA3AF, & TA1UZ all tripped at the same time for no apparent reason, fire balls reported on hydro lines at 1300 Kitchener and the intersection of Brookfield and Kaladar. | Ottawa | Unknown/Other | No Apparent Cause
3858 | 2003 | 8 | 6 | 0.59097 |  | 28 | 473 | 1013 | TA & UZ | 13.2kV | TA1UZ | Scada indicates TA1UZ circuit opened. Cleared H/O's and closed TA1UZ via SCADA. Circuit Held. Lightning storm in area. | Ottawa | Adverse Weather | Lightning
11190 | 2007 | 8 | 29 | 0.73889 |  | 16 | 280 | 1050 | Albion | 13.2kV | TA1UZ | TA10 circuit opened and locked out due to adverse weather, circuit closed via SCADA and holding | Ottawa | Adverse Weather
17296 | 2010 | 11 | 17 | 0.78889 |  | 21 | 745 | 2129 | Albion TA | 13.2kV | TA1UZ, TA2AF | An internal flash @ SW119 @ 1170 Bank st (Canadian Tire) caused TA2AF & TA1UZ to trip. Customers reported flashes & explosions as far as Bank & Walkley where the lines intersect. Lines were abnormal at this time for other planned work. TA3AF also A/R at this time. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20283 | 2012 | 4 | 5 | 0.15486 |  | 10 | 20 | 118 | Albion | 13.2kV | TA21 | TA21 breaker opened and crew suspects that SC6 flahed over. Albion ID# 20283 | Ottawa | Unknown/Other
5272 | 2004 | 6 | 9 | 0.73264 |  | 51 | 577 | 679 | Albion | 13.2kV | TA2AF | TA1AF, TA2AF, TA3AF, & TA1UZ all tripped at the same time for no apparent reason, fire balls reported on hydro lines at 1300 Kitchener and the intersection of Brookfield and Kaladar. | Ottawa | Unknown/Other | No Apparent Cause
9151 | 2006 | 9 | 8 | 0.74028 |  | 3 | 34 | 679 | ALBION | 13.2kV | TA2AF | TA2AF circuit opened due to storm activity. Was closed by scada and held. | Ottawa | Adverse Weather
11660 | 2007 | 11 | 5 | 0.49028 |  | 28 | 280 | 600 | Albion | 13.2kV | TA2AF | TA2AF outage due to possible cable fault. TA2AF circuits load transferred to TA1AF, Crews have found bad Blue Phase cable termination at TA2AF run-off to SW141. Crews will continue patrol Tuesday November 6th 2007. ID # 11660. | Ottawa | Unknown/Other | No Apparent Cause
18508 | 2011 | 6 | 24 | 0.68472 |  | 87 | 977 | 674 | Albion | 27.6/16kV | TA2AN | TA2AN circuit opened during lightening storm. | Ottawa | Adverse Weather | Lightning
18650 | 2011 | 7 | 13 | 0.58125 |  | 4 | 45 | 674 | Albion | 13.2kV | TA2AN | TA17 breaker for TA2AN circuit tripped and System Office closed from scada to restore all load | Ottawa | Adverse Weather
7230 | 2005 | 8 | 28 | 0.56458 |  | 3 | 40 | 802 | Albion | 13.2kV | TA2AN | TA2AN opened , and was closed via scada. No cause found as of yet. Circuit to be patrolled. | Ottawa | Unknown/Other
6689 | 2005 | 6 | 10 | 0.090278 |  | 38 | 570 | 900 | Albion | 13.2kV | TA2QZ | All of TA2QZ normal load plus SC18, SC19 & VT352 were interrupted. Cause was determined to be a pole fire / broken pole on the private 13 kv line on Lindberg Lane. The Caravan Airport Service & The Ottawa Flying Club are still without power until repairs can be made to their line. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12694 | 2008 | 6 | 19 | 0.59097 |  | 72 | 307 | 675 | Albion | 13.2kV | TA2QZ | Boom truck pulled down O/H private line, poles & transformers at Lindberg Pvt causing TA07 breaker to open. TA07 was carrying extra customers due to outage on SC16. After area of problem was determined, power was restored up to switch 5102-B at McCarthy. Line crew cut private line clear of our circuits and the remainder of customers were restored. Private line was rebuilt by Hydro Ottawa at the request of customer, new switch S24772 installed at tap off. | Ottawa | Foreign Interference | Vehicle
18661 | 2011 | 7 | 14 | 0.91667 |  | 119 | 412 | 725 | Albion | 13.2kV | TA2QZ | The TA07(TA2QZ circuit) trip sectionalize the circuit and found nothing, require patrolling in the daylight. | Ottawa | Unknown/Other
18825 | 2011 | 7 | 26 | 0.55903 |  | 77 | 618 | 851 | Albion | 13.2kV | TA2QZ | TA07 (TA2QZ) opened during lightning storm. Attemps to close via SCADA were unsuccessful and was determined that a cable dip was found to be blown at the station. Customers were restored in stages. | Ottawa | Lightning | Direct Strike
3857 | 2003 | 8 | 6 | 0.59097 |  | 27 | 296 | 658 | TA & QZ | 13.2kV | TA2QZ | Scada indicated TA2QZ circuit opened. Lightning storm was in the area. Cleared H/O's and closed TA2QZ via SCADA. Circuit Held. | Ottawa | Adverse Weather | Lightning
14333 | 2009 | 5 | 9 | 0.73611 |  | 160 | 142 | 67 | Albion | 13.2kV | TA3AE | Cause unknown, o/h to be patrol and u/g to be tested. Customers power restored from alternate circuits. | Ottawa | Unknown/Other
12735 | 2008 | 6 | 26 | 0.68125 |  | 91 | 1623 | 1070 | Albion | 13.2kV | TA3AE | SC7 was hit by lightning causing flash on overhead circuit. | Ottawa | Adverse Weather | Lightning
12756 | 2008 | 6 | 27 | 0.42361 |  | 201 | 3 | 1 | Albion | 13.2kV | TA3AE | 2100 Walkley reports 1 phase off in VT318. Mike reports white phase terminations on R1-F have failed, white phase fuse found blown in R1-F switch gear. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14629 | 2009 | 6 | 27 | 0.125 |  | 142 | 142 | 67 | Albion TS | 13.2kV | TA3AE | TA3AE cct tripped, cause unknown, load transferred to alternate sources, to be patrolled. | Ottawa | Unknown/Other
9129 | 2006 | 9 | 6 | 0.70833 |  | 260 | 9 | 2 | Albion | 13.2kV | TA3AE | SW89 isolated to install new cable, PT52 interupted | Ottawa | Scheduled Outage | Construction
16898 | 2010 | 9 | 8 | 0.081944 |  | 252 | 25 | 16 | Albion | 13.2kV | TA3AE | White phase cable fault found on SC601 between VT674 and VT685 and defective switch feeding SC8 S-157 tracking between phases. Fault isolated and 2 customers being fed thru faulty switch until repairs can be made. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13691 | 2008 | 12 | 1 | 0.076389 |  | 17 | 20 | 72 | Albion | 13.2kV | TA3AE | Circuit tripped during heavy rain storm. No calls from Police or Fire, circuit tried & held. | Ottawa | Adverse Weather | Rain
15558 | 2009 | 12 | 26 | 0.97222 |  | 15 | 17 | 67 | Albion | 13.2kV | TA3AE | TA3AE (TA12) tripped. Circuit was closed back in via scada. All customers restored, | Ottawa | Adverse Weather | Ice Storm
19873 | 2012 | 1 | 22 | 0.45 |  | 69 | 22 | 19 | Albion | 13.2kV | TA3AF | Replaced blown fuse feeding transformer X28173 at 1108 Richard St due to squirrel contact | Ottawa | Foreign Interference | Animal
4868 | 2004 | 3 | 8 | 0.54167 |  | 107 | 690 | 387 | Albion | 13.2kV | TA3AF | TA3AF line tripped due to a transition splice failure on red phase between VT354 & SW118. About 387 customers in Walkley & Heron area affected. MDF - fault was on transition splice from 3-ph PILC to single phase XLPE per J. Kelly | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8180 | 2006 | 4 | 22 | 0.95833 |  | 194 | 52 | 16 | Albion | 13.2kV | TA3AF | Vines caused transformer cut out to blow feeding 75kva transformer OTT5705, on call crew refused | Ottawa | Foreign Interference | Foreign Object
8395 | 2006 | 5 | 31 | 0.73958 |  | 48 | 608 | 760 | Albion | 13.2kV | TA3AF | TA05 breaker tripped during a thunder storm, lightning reported in area at time of trip, circuit patrolled & no problem found, breaker closed & held. Circuit was carrying part of TA1AF load at time of trip | Ottawa | Adverse Weather | Lightning
5273 | 2004 | 6 | 9 | 0.73264 |  | 52 | 335 | 387 | Albion | 13.2kV | TA3AF | TA1AF, TA2AF, TA3AF, & TA1UZ all tripped at the same time for no apparent reason, fire balls reported on hydro lines at 1300 Kitchener and the intersection of Brookfield and Kaladar. | Ottawa | Unknown/Other | No Apparent Cause
15001 | 2009 | 8 | 24 | 0.57014 |  | 77 | 32 | 25 | Albion | 13.2kV | TA3AF | TA05 breaker tripped and did not attempt to reclose, after a patrol, nothing was found, breaker would not close via Scada and had to be manually closed at the station. | Ottawa | Unknown/Other | No Apparent Cause
11189 | 2007 | 8 | 29 | 0.73889 |  | 16 | 103 | 387 | Albion | 13.2kV | TA3AF | TA05 circuit opened and locked out due to adverse weather. Circuit closed back in and holding | Ottawa | Adverse Weather
15351 | 2009 | 11 | 3 | 0.38194 |  | 44 | 1 | 1 | Albion | 13.2kV | TA3AF | At 9:10am vault VT773 was isolated to allow crews to open the R1-F switch to replace a blown fuse, no apparent cause to why reyrolle fuses failed. Fuse replaced and vault restored at 9:54am. Albion (TA3AF). ID#15351. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5892 | 2004 | 11 | 16 | 0.55069 |  | 57 | 368 | 387 | Albion | 13.2kV | TA3AF | TA3AF tripped on Grd Inst. Fault. Hole found in base of pothead to VT158 at Charlebois HS, 2525 Alta Vista | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20896 | 2012 | 6 | 28 | 0.25833 |  | 84 | 843 | 804 | Albion | 13.2kV | TA3AQ | TA3AQ circuit opened due to cable fault between SW182 and Albion Stn. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7039 | 2005 | 7 | 29 | 0.075694 |  | 66 | 269 | 457 | Albion | 13.2kV | TA3AQ | TA3AQ - TA01 opened due to suspected cable fault between SW182 and station TA. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19804 | 2012 | 1 | 10 | 0.39931 |  | 141 | 16 | 7 | Albion | 13.2kV | TA3UA | Transformer KT22 at 38 Rich Little was isolated for HOL crew to make repairs to the primary connections. | Ottawa | Scheduled Outage | Preventive Maintenance
19984 | 2012 | 2 | 8 | 0.39792 |  | 104 | 17 | 10 | Albion | 13.2kV | TA3UA | Transformer KT643 at 59 Rhapsody was isolated to allow crew to replace primary connections. | Ottawa | Scheduled Outage | Preventive Maintenance
9670 | 2006 | 11 | 16 | 0.40625 |  | 245 | 82 | 20 | ALBION | 13.2kV | TAIAN | KT405 @ #2 ASHPARK HIT BY CAR. XFMR REPLACED | Ottawa | Foreign Interference | Vehicle
3501 | 2003 | 5 | 30 | 0.48611 |  | 66 | 2590 | 2700 | RUSSELL | 13.2kV | TB - Q | A fault on H-1's A3RM feeder at Merivale M.S tripped the TB T1, relaying then cleared all supply to the Q bus & opened all feeder breakers. Some load was restored outside the station while most of the load was restored via the transfer bus after the station was inspected. H-1 relay coordination is suspected as the cause of loss of supply to the Q bus. | Ottawa | Loss of Supply | HEPC Station Fault
16518 | 2010 | 7 | 21 | 0.88819 |  | 5 | 168 | 2022 | Russell | 13.2kV | TB01 | At 21:19 the Russell TB01 breaker tripped open during the heavy rain and lightning. 2022 customer were affected. | Ottawa | Unknown/Other
16152 | 2010 | 5 | 26 | 0.90069 |  | 73 | 445 | 2022 | RUSSELL TS | 13.2kV | TB01 & TB17 | TB01 & TB17 tripped. Emergency switching was performed and all load was restored. TB1AL was patrolled from Bantree Sub to the dead end at St Laurent Blvd. And nothing was found. Crews to patrol in daylight. Thunderstorms were indicated at the time of outage. | Ottawa | Unknown/Other
5412 | 2004 | 7 | 1 | 0.32708 |  | 24 | 1 | 3 | Russell | 13.2kV | TB02 | TB02 in the Russell, Belfast, Industrial area open under Hold Off, removed hold off and closed and held | Ottawa | Adverse Weather | Lightning
19773 | 2011 | 12 | 31 | 0.94583 |  | 52 | 193 | 223 | Ruussel TS | 13.2kV | TB03 | MVA at 2495 Lancaster caused the TB03 circuit to auto reclose. The circuit had to opened at 22:42 for safety purposes due to the TB03 wires being low at the accident scene. Emergency switching was performed to isolate the section at the accident scene. | Ottawa | Foreign Interference | Vehicle
7811 | 2006 | 1 | 16 | 0.58333 |  | 45 | 9 | 12 | Russell | 12/7.2kV | TB06 | Trans # OTT5211 isolated at 836 Quinland to make repairs to sec overhead buss | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9938 | 2007 | 1 | 17 | 0.47014 |  | 53 | 10 | 11 | Russell | 4.16kV | TB06 | Fuse to transformer OTT1341 at 2001 Haig Dr was found blown due to a squirrel contact | Ottawa | Foreign Interference | Animal
19857 | 2012 | 1 | 18 | 0.43056 |  | 65 | 6 | 6 | Russell | 13.2kV | TB06 | X27071 was isolated to allow crews to repair defective tripel at 808 Chapman. 6 customers affected for 65 minutes. Russell (TB06) ID #19857 | Ottawa | Unknown/Other
19867 | 2012 | 1 | 19 | 0.94444 |  | 52 | 10 | 12 | Russell | 13.2kV | TB06 | Trans at 2050 Palmer Pl was isolated in order to replace defective trans ,, was only putting out 120 volt | Gloucester | Defective Equipment | Equipment Deterioration Due to Age
19991 | 2012 | 2 | 8 | 0.46875 |  | 95 | 13 | 8 | Russell | 13.2kV | TB06 | Isolated transformer X40554 at 211 Cunningham Ave for tree trimming | Ottawa | Scheduled Outage | Preventive Maintenance
10013 | 2007 | 2 | 11 | 0.35694 |  | 31 | 6 | 12 | Russell | 4.16kV | TB06 | At 08:34 trans OTT6848 at 763 Adams St opened due to squirrel contact ,12 custs were affected | Ottawa | Foreign Interference | Animal
17578 | 2011 | 2 | 14 | 0.080556 |  | 64 | 18 | 17 | Russel | 13.2kV | TB06 | A blown transformer fuse at transformerX27326 @ 974 Chapmen. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14017 | 2009 | 3 | 3 | 0.52083 |  | 104 | 73 | 42 | Russell | 13.2kV | TB06 | The TB06 autoreclosed TB06 circuit to auto reclosed, Crew found center fuse open at switch TB06-S2, Patrol found no cause to the fault. Russell (TB06) ID# 14017. | Ottawa | Unknown/Other
8045 | 2006 | 3 | 19 | 0.5625 |  | 40 | 8 | 12 | Russell | 13.2kV | TB06 | Transformer #OTT4996 located at 794 Pleasant Park Rd isolated due to animal contact | Ottawa | Foreign Interference | Animal
12170 | 2008 | 3 | 25 | 0.42708 |  | 20 | 1 | 3 | Russell | 13.2kV | TB06 | Transformer #OTT2194 located at 2007 Oxbow isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
12171 | 2008 | 3 | 25 | 0.45833 |  | 75 | 6 | 5 | Russell | 13.2kV | TB06 | Transformer #X27346 located at 580 Pleasant Park isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
12174 | 2008 | 3 | 26 | 0.38542 |  | 150 | 12 | 5 | Russell | 13.2kV | TB06 | Transformer #X27346 located at 580 Pleasant Park isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
10356 | 2007 | 5 | 2 | 0.80208 |  | 41 | 342 | 500 | Russell | 13.2kV | TB06 | Partially isolated TB06 to allow crew work protection to make temporary repairs to pole. | Ottawa | Foreign Interference | Vehicle
6512 | 2005 | 5 | 5 | 0.43403 |  | 45 | 4 | 5 | Russell | 13.2kV | TB06 | Transformer #OTT3270 at Rear of 2164 Arch St isolated to tie a triplex service to another house | Ottawa | Scheduled Outage | Construction
14337 | 2009 | 5 | 9 | 0.91528 |  | 117 | 23 | 12 | Russell | 13.2kV | TB06 | Crew refused and closed transformer at rear of 966 Weston that opened due to tree contact. | Ottawa | Tree Contacts | Inadequate Trimming
10438 | 2007 | 5 | 22 | 0.48611 |  | 60 | 4 | 4 | Russell | 12/7.2kV | TB06 | At 11:40 trans at 699 Sandra Ave was isolated in order to transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
14407 | 2009 | 5 | 24 | 0.69097 |  | 53 | 14 | 16 | Russell | 13.2kV | TB06 | Squirrel opened 13kv overhead transformer X27326 @ 971 Weston. Crew refused and closed. | Ottawa | Foreign Interference | Animal
20606 | 2012 | 5 | 26 | 0.80069 |  | 1145 | 754 | 45 | Russell | 13.2kV | TB06 | S13376 on Marshall Cres opened due to tree contact on O/H at rear of 2080 Palmer. | Ottawa | Tree Contacts | Tree Fallen
6613 | 2005 | 5 | 28 | 0.39167 |  | 109 | 13 | 7 | Russell | 13.2kV | TB06 | Transformer fuse to transformer OTT4083 @ 1982 Oxbow found open. Refused transformer and restored power to customers. Apparent squirel contact. | Ottawa | Foreign Interference | Animal
12486 | 2008 | 5 | 28 | 0.35139 |  | 57 | 14 | 15 | Russell | 4.16kV | TB06 | Fuse to Transformer X27327 at 927 Weston Dr was found blown due to squirrel contact | Ottawa | Foreign Interference | Animal
20629 | 2012 | 5 | 28 | 0.69792 |  | 95 | 16 | 10 | Russell | 13.2kV | TB06 | Transformer #X27191 located at 895 Chapman Blvd opened up due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
8368 | 2006 | 5 | 29 | 0.42361 |  | 50 | 4 | 5 | Russell | 13.2kV | TB06 | Transformer #OTT3266 located at 2115 Haig Dr isolated for planned outage to make repairs to broken pole | Ottawa | Scheduled Outage | Repair
20651 | 2012 | 5 | 29 | 0.45833 |  | 48 | 27 | 34 | Russell | 13.2kV | TB06 | Customers on Rachel and Mountbatten interrupted to allow crew to transfer customers from one phase to another. | Ottawa | Scheduled Outage | Construction
8378 | 2006 | 5 | 30 | 0.40278 |  | 130 | 32 | 15 | Russell | 13.2kV | TB06 | 3 transformers located at 2115 Haig isolated to replace broken pole | Ottawa | Scheduled Outage | Repair
8387 | 2006 | 5 | 31 | 0.40625 |  | 190 | 32 | 10 | Russell | 13.2kV | TB06 | Transformer located at 2115 Haig isolated to transfer secondary over from broken pole | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18293 | 2011 | 6 | 4 | 0.375 |  | 115 | 21 | 11 | Russell | 13.2kV | TB06 | Transformer #X27345 located at 663 Chapman Blvd opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
12568 | 2008 | 6 | 7 | 0.35417 |  | 120 | 20 | 10 | Russell | 13.2kV | TB06 | Fuse blown at transformer X27191 located at 895 Chapman from squirrel contact. Crew refused transformer & restored power to all 10 customers. | Ottawa | Foreign Interference | Animal
16236 | 2010 | 6 | 9 | 0.70208 |  | 99 | 16 | 10 | Russell | 13.2kV | TB06 | Replaced blown fuse at transformer OTT6623 at 972 Weston Ave (caused by tree contact ) | Ottawa | Tree Contacts | Inadequate Trimming
20787 | 2012 | 6 | 18 | 0.25 |  | 135 | 16 | 7 | Russell | 13.2kV | TB06 | Transformer #X27344 located at 603 Pleasant Park Rd opened up due to animal contact | Ottawa | Foreign Interference | Animal
6769 | 2005 | 6 | 21 | 0.41597 |  | 100 | 357 | 507 | Russell | 13.2kV | TB06 | Elmvale Acres area. Circuit was picked up from SCADA after a fuse was found blown at TB06-S2. 24/7 patrolled & found a blown arrestor between Wingate & Chapman. Arrestor cut clear & 2 fuses were replaced at TB06-S2 restoring power to the remaining customers. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20853 | 2012 | 6 | 24 | 0.37778 |  | 175 | 23 | 8 | Russell | 13.2kV | TB06 | Transformer X27698 at 388 Summit opened due to animal contact | Ottawa | Foreign Interference | Animal
18530 | 2011 | 6 | 26 | 0.74583 |  | 281 | 28 | 6 | Russell | 12/7.2kV | TB06 | Transformer X26763 cut out was blowns due to animal contact. Russell (TB06) ID#18530 | Ottawa | Foreign Interference
20894 | 2012 | 6 | 27 | 0.6375 |  | 168 | 34 | 12 | Russell | 13.2kV | TB06 | Transformer #X26240 located at 1999 Lynda Lane opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
5476 | 2004 | 7 | 11 | 0.48194 |  | 41 | 8 | 11 | Russell | 13.2kV | TB06 | O/H transformer OTT2926 at 1959 Haig re-fused after a contact with squirrel. | Ottawa | Foreign Interference | Animal
12840 | 2008 | 7 | 14 | 0.93333 |  | 205 | 34 | 10 | Russell | 13.2kV | TB06 | Transformer fuse found blown at 794 Adams, crew patrolled,no apparent cause. Transformer refused & all power restored. | Ottawa | Unknown/Other
18669 | 2011 | 7 | 16 | 0.28056 |  | 86 | 46 | 32 | Russell | 13.2kV | TB06 | The TB06 auto reclosed becuaes of a squirrel making contact with transformer #40534 @ 350 Cunningham and alos switch S27654 blew on on montpatten no cause was found there. | Ottawa | Foreign Interference | Animal
18750 | 2011 | 7 | 17 | 0.80903 |  | 1277 | 33670 | 1582 | Russell | 13.2kV | TB06 | TB06 tripped during the storm. Multiple trees and Limbs cleared off several locations of this circuit, power restored the following day after attemps to restore. | Ottawa | Tree Contacts | Tree Limb Fallen
8773 | 2006 | 7 | 18 | 0.27778 |  | 128 | 26 | 12 | Russell | 13.2kV | TB06 | Rick Grisel had xfmr OTT6613 off to remove a tree from the line at 972 Weston | Ottawa | Foreign Interference
18716 | 2011 | 7 | 18 | 0.89444 |  | 1605 | 24240 | 1582 | Russell | 13.2kV | TB06 | High winds caused trees to fall into the O/H and break conductor in the Cunningham/Pleasant Park area. | Ottawa | Adverse Weather | Wind
10928 | 2007 | 7 | 23 | 0.03125 |  | 44 | 6 | 8 | Russell | 13.2kV | TB06 | A Raccoon cause the fuse to blow at transformer 2192 @ 1993 Oxbow. | Ottawa | Foreign Interference | Animal
8829 | 2006 | 7 | 25 | 0.39167 |  | 111 | 22 | 12 | Russell | 13.2kV | TB06 | Transformer #OTT4033 located at 1982 Oxbow isolated due to tree interference | Ottawa | Tree Contacts | Inadequate Trimming
16575 | 2010 | 7 | 28 | 0.4375 |  | 80 | 23 | 17 | Russell | 13.2kV | TB06 | Squirrel opened transformer X27326 at 967 Weston. | Ottawa | Foreign Interference | Animal
16588 | 2010 | 7 | 29 | 0.43958 |  | 122 | 35 | 17 | Russell | 4.16kV | TB06 | Replaced blown fuse feeding transformer X27326 at 967 Weston Dr ( Squirrel contact ) | Ottawa | Foreign Interference | Animal
14889 | 2009 | 8 | 1 | 0.20417 |  | 279 | 18 | 11 | Russell | 13.2kV | TB06 | A Raccoon caused transformer OTT2194 @ 599 Pleasant park to open. Transformer was leaking oil, so crew connected load to transformer OTT2192, whick required opening same transformer. Transformer OTT2194 was removed. | Ottawa | Foreign Interference | Animal
14890 | 2009 | 8 | 1 | 0.56042 |  | 93 | 17 | 11 | Russel | 13.2kV | TB06 | O/H section of the TB06 circuit on Pleasant Park isolated to remove leaking transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8904 | 2006 | 8 | 2 | 0.29514 |  | 240 | 28 | 7 | Russell | 13.2kV | TB06 | Isolated and replaced defective transformer OTT4988 at 2005 Norway Cres | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16652 | 2010 | 8 | 5 | 0.45347 |  | 1180 | 9507 | 522 | Russell | 13.2kV | TB06 | heavy rain & lightning caused extensive damage to three phase at rear of 682 pleasant park causing fuses at S19554 at haig and weston to open , and tree brought down overhead at rear of 730 chapman, which caused S2 at Haig and Weston to open. | Ottawa | Adverse Weather | Lightning
18931 | 2011 | 8 | 14 | 0.90972 |  | 15 | 2 | 10 | Russell | 13.2kV | TB06 | 13kv O/H transformer X29233 at 807 Chapman opened to repair primary connection | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16752 | 2010 | 8 | 16 | 0.37708 |  | 97 | 27 | 17 | Russell | 13.2kV | TB06 | Transformer #X27326 located at 971 Weston opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
7179 | 2005 | 8 | 21 | 0.90069 |  | 58 | 9 | 9 | Russell | 13.2kV | TB06 | Transformer OTT6694 taken out of service to connect new triplex service to 816 Wingate. 9 customers on Arch, Wingate and Chapman affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13172 | 2008 | 8 | 31 | 0.40625 |  | 55 | 5 | 5 | Russell | 13.2kV | TB06 | Transformer #X27069 located at 800 Chapman Blvd isolated due to animal contact | Ottawa | Foreign Interference | Animal
5776 | 2004 | 9 | 4 | 0.64931 |  | 340 | 877 | 507 | TB | 13.2kV | TB06 | A home owner cutting a tree at Arch & Weston caused the red & white phase of TB06-S2 fuses to open. The circuit was opened by Scada as the tree was burning in the energized blue phase. 24/7 opened the blue phase fuse & the majority of customers were restored. Repairs then were made to the damaged section of O/H. | Ottawa | Foreign Interference | Foreign Object
13200 | 2008 | 9 | 6 | 0.42361 |  | 170 | 11 | 4 | Russell | 4.16kV | TB06 | Replaced blown fuse at switch feeding transformer OTT2178 at 709 Sandra Ave | Ottawa | Adverse Weather | Rain
16885 | 2010 | 9 | 7 | 0.79583 |  | 269 | 76 | 17 | Russell | 13.2kV | TB06 | SCADA indicates TB06 A/R, suspect due to storm rolling through region. Customer reported outage, White phase fuse blown at 1695 dorval Crews replaced damaged cutout | Ottawa | Adverse Weather
19112 | 2011 | 9 | 7 | 0.76667 |  | 11 | 3 | 14 | Russell | 13.2kV | TB06 | Transformer X26886 at 821 Quinlan Rd isolated to reconnect secondary after tree trimming | Ottawa | Tree Contacts | Inadequate Trimming
5795 | 2004 | 9 | 10 | 0.14167 |  | 61 | 10 | 10 | Russell | 4.16kV | tb06 | Tree contact with overhead. Limbs need removal rear of 862 Chapman. | Ottawa | Tree Contacts | Inadequate Trimming
5821 | 2004 | 9 | 30 | 0.37431 |  | 86 | 29 | 20 | Russell TS | 13.2kV | TB06 | Crew responded to all-out with customer reporting loud bang. Squirrel contact discovered & cutout refused. | Ottawa | Foreign Interference | Animal
11418 | 2007 | 10 | 1 | 0.37153 |  | 34 | 6 | 10 | Russell | 13.2kV | TB06 | Transformer #OTT6694 at 803 Chapmand isolated to change triplex | Ottawa | Scheduled Outage | Repair
13338 | 2008 | 10 | 8 | 0.41181 |  | 107 | 18 | 10 | Russell | 13.2kV | TB06 | Transformer #X26761 located at 747 Pleasant Park Rd isolated due to bird contact | Ottawa | Foreign Interference | Bird
19366 | 2011 | 10 | 12 | 0.68125 |  | 261 | 1228 | 1395 | Russell TB | 13.2kV | TB06 | TB06 tripped under H/O. After clearing h/o's & checking with fire & police, TB06 was closed in at 16:30. 24/7 responded to a report of wires down & found a cement truck had pulled down O/H wires at 346 Cunningham. TB06 opened due to live wire on the ground, line sectionalized at S11681 & most customers restored. On call crew required to repair downed conductor. | Ottawa | Foreign Interference | Vehicle
19421 | 2011 | 10 | 20 | 0.16528 |  | 452 | 2637 | 350 | Russell | 13.2kV | TB06 | TB06 auto-reclosed during storm. S19554 R at haig & Chapman was found blown. Tree trimming crew required to trim trees in backyards on Arch st before power restored | Ottawa | Adverse Weather | Wind
11746 | 2007 | 11 | 21 | 0.66042 |  | 69 | 17 | 15 | Russell | 13.2kV | TB06 | Transformer #27327 located at 940 Chapman isolated due to animal interference | Ottawa | Foreign Interference | Animal
17350 | 2010 | 11 | 27 | 0.33958 |  | 407 | 563 | 83 | Russell | 13.2kV | TB06 | overhead section of TB06 circuit from temp 52 switches to end of line was isolated to change overhead conductor on pleasant park. | Ottawa | Scheduled Outage | Construction
15432 | 2009 | 11 | 28 | 0.37917 |  | 38 | 12 | 19 | Russell | 13.2kV | TB06 | Replaced blown fuse feeding transformer X27182 at 887 Pleasant Park Rd (Squirrel contact) | Ottawa | Foreign Interference | Animal
11795 | 2007 | 12 | 1 | 0.8625 |  | 235 | 473 | 250 | Russel | 13.2kV | TB06 | Centre phase conductor of circuit TB06 in the back of 818 Pleasant Park failed with the load side falling to the ground. 3 phase switches S19554 opened to isolate the circuit for repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17387 | 2010 | 12 | 7 | 0.375 |  | 180 | 51 | 17 | Russell | 13.2kV | TB06 | Transformer #X27176 located at 805 Pleasant Park Rd opened by crew to install new switches | Ottawa | Scheduled Outage | Construction
17400 | 2010 | 12 | 10 | 0.38542 |  | 200 | 167 | 50 | Russell | 13.2kV | TB06 | The O/H line bet Chapman Blvd and Weston was isolated to allow crews to re string new conductor. | Ottawa | Scheduled Outage | Preventive Maintenance
17405 | 2010 | 12 | 10 | 0.47778 |  | 30 | 8 | 17 | Russell | 13.2kV | TB06 | Transformer #X27326 located at 967 Weston opened due to squirrel contact | Ottawa | Foreign Interference | Animal
17427 | 2010 | 12 | 16 | 0.375 |  | 140 | 40 | 17 | Russell | 13.2kV | TB06 | Isolated transformer X27176 at 805 Pleasant Park Dr for new pole instalation | Ottawa | Scheduled Outage | Construction
11903 | 2008 | 1 | 7 | 0.5 |  | 21 | 1 | 4 | RUSSELL | 13.2kV | TB07 | PPH Switches to PT211 were opened to allow crew to replace fuses at transformer. | Ottawa | Defective Equipment
13996 | 2009 | 2 | 20 | 0.42014 |  | 365 | 18 | 3 | Russell | 13.2kV | TB07 | PT144 at 1575 St Laurent was interrupted at the request of the Ottawa Fire Department due to fire damage in 2 units. Power was restored after approval of ESA, OFD & the onsite electrician. | Ottawa | Adverse Environment | Fire
20053 | 2012 | 2 | 25 | 0.13889 |  | 285 | 289 | 1307 | Russell | 13.2kV | TB07 | TB07 CB was open to allow crew to isolate section of TB07 O/H on Micheal St due to pole fire, repair pole and was opened again to restore TB07 O/H to normal. | Ottawa | Scheduled Outage | Repair
20121 | 2012 | 3 | 5 | 0.28125 |  | 95 | 5 | 3 | Russell | 13.2kV | TB07 | Replaced broken live line lead feeding transformer X24981 at 1211 Newmarket St | Ottawa | Adverse Weather | Wind
14249 | 2009 | 4 | 26 | 0.58194 |  | 374 | 6 | 1 | Russell | 13.2kV | TB07 | PT170 at 911 Industrial was isolated due to pole fire and cable damage. Only the 1 customer, City of Ottawa Yard, was affected. Repairs were made by cable crew & overhead crew and power restored. | Ottawa | Defective Equipment
18034 | 2011 | 4 | 28 | 0.58125 |  | 580 | 1808 | 187 | Russell | 13.2kV | TB07 | TB07 auto-reclosed and locked out during wind/lightning storm. Crews repaired broken conductors and power was restored. | Ottawa | Adverse Weather | Wind
14400 | 2009 | 5 | 23 | 0.35694 |  | 126 | 6 | 3 | RUSSELL | 13.2kV | TB07 | Transformer X29029 at 1515 St. Laurent Blvd isolated to allow for transformer upgrade | Ottawa | Scheduled Outage | Construction
18350 | 2011 | 6 | 8 | 0.70556 |  | 229 | 718 | 188 | Russell | 13.2kV | TB07 | Blown blue phase fuse @ PT189 @ 1145 newmarket, and defective bushing at transformer feeding 1445 Michel caused TB07 circuit to open. | Ottawa | Adverse Weather
14536 | 2009 | 6 | 14 | 0.47431 |  | 152 | 15 | 6 | Russell | 13.2kV | TB07 | Replaced blown fuse at transformer OTT3995 at 1570 Liverpool Court due to squirrel contact | Ottawa | Foreign Interference | Animal
18436 | 2011 | 6 | 19 | 0.36458 |  | 45 | 1 | 1 | Russell | 13.2kV | TB07 | Defective blue phase switch feeding P194 was blown. Switch replaced and closed to restore power on Michael St. | Ottawa | Defective Equipment
5431 | 2004 | 7 | 1 | 0.66944 |  | 444 | 7105 | 1000 | TB | 13.2kV | TB07 | Cct opened during storm. TB07 was also carrying TB14 load due to isolation of TB14 section for Hydro - One. Primary lines down Belfast/ St Laurent & Michael st area. Section of TB07 was on after an O/H switch was opened at 17:25, cct was opened to close this switch after repairs made. | Ottawa | Adverse Weather | Lightning
14923 | 2009 | 8 | 9 | 0.37361 |  | 42 | 1 | 2 | Russell |  | TB07 | Replaced blown fuse at switch for transformer OTT4469 at 1572 Michael St Squirrel contact | Ottawa | Foreign Interference | Animal
19384 | 2011 | 10 | 16 | 0.125 |  | 340 | 11 | 2 | Russell TB | 13.2kV | TB07 | Termination burning up at dip to PT144, 1575 St Laurent. Switch opened by 24/7, on - call crew required to complerte repairs. On call repaired lead and replaced K-mate fuse. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13521 | 2008 | 10 | 29 | 0.60208 |  | 36 | 1 | 1 | Russell | 13.2kV | TB07 | At 1525 Micheal Street, Adrien Henry reports secondary lead burnt off. PC10A#4385 established and all power restored after reparis at 3:03pm. 1 Customer affected for 36 min. Lincoln Heights (TD07). ID#13521. | Ottawa | Adverse Weather | Snow
4653 | 2003 | 12 | 25 | 0.50972 |  | 28 | 177 | 380 | TB | 13.2kV | TB07 | 24/7 found 2 phases wrapped on Michael st S. of Belfast. No apparent cause. | Ottawa | Unknown/Other
5413 | 2004 | 7 | 1 | 0.32708 |  | 24 | 3 | 8 | Russell | 13.2kV | TB09 | TB09 in the Russell Belfast Industrial area open under Hold Off, removed hold off and close and held. | Ottawa | Adverse Weather
17020 | 2010 | 9 | 28 | 0.82292 |  | 17 | 10 | 35 | Russel | 13.2kV | TB09 | While performing OTO 17-47426, S-247 at VT50 failed causing TB09 to trip. VT50 was isolated from the circuit and TB09 picked up. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12071 | 2008 | 2 | 22 | 0.15139 |  | 87 | 6 | 4 | Russell | 13.2kV | TB09 / TB02 | At 3:38am TB02 Breaker autoreclosed and locked out and TB09 auto reclosed. Crews dispatched to investigate. 24-7 crews restored power to the 4 customers that were left without power for 87min. Crews are currently still investigating what caused the fault. ID#12071. | Ottawa | Unknown/Other | No Apparent Cause
18037 | 2011 | 4 | 28 | 0.59306 |  | 289 | 828 | 172 | Russell | 13.2kV | TB10 | TB10 circuit breaker auto-reclosed and locked out during wind/lightning storm. Closed via scada and held. | Ottawa | Adverse Weather | Wind
16517 | 2010 | 7 | 21 | 0.8875 |  | 65 | 2400 | 2215 | Russell | 13.2kV | TB13 | At 21:18 the Russell TB13 breaker tripped open during the heavy rain and lightning. 2215 customer were affected. | Ottawa | Unknown/Other
11957 | 2008 | 1 | 18 | 0.67431 |  | 84 | 25 | 18 | RUSSELL | 13.2kV | TB14 | Transformer #OTT5627 at 1684 Russell Rd isolated to allow for repair to connections at pole | Ottawa | Scheduled Outage | Repair
9952 | 2007 | 1 | 19 | 0.53125 |  | 35 | 6 | 10 | Russell | 4.16kV | TB14 | At 12:45 trans at 520 Braydon was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
13886 | 2009 | 1 | 22 | 0.44097 |  | 80 | 9 | 7 | Russell | 13.2kV | TB14 | Transformer #OTT1401 located at 1473 Chomley Cres isolated to repair secodary service due to Guy Wire contact | Ottawa | Tree Contacts | Tree Limb Fallen
9995 | 2007 | 2 | 6 | 0.53125 |  | 95 | 36 | 23 | Russell | 4.16kV | TB14 | Isolated transformers OTT 602 and OTT 601 at 495 and 513 Braydon Ave to replace poles | Ottawa | Scheduled Outage | Construction
19992 | 2012 | 2 | 8 | 0.62083 |  | 106 | 7 | 4 | Russell | 13.2kV | TB14 | Transformer #X27269 located at 516 Browning Ave opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
20059 | 2012 | 2 | 27 | 0.46875 |  | 45 | 12 | 16 | Russell | 13.2kV | TB14 | Transformer X27108 at 1621 Dixie St. isolated to Installed new triplex at 1622 Pullen and replaced connections at transformer | Ottawa | Scheduled Outage | Repair
15773 | 2010 | 3 | 5 | 0.51736 |  | 50 | 9 | 11 | Russell | 13.2kV | TB14 | Transformer #X27100 located at 1584 Pullen isolated to change O/H switch | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15828 | 2010 | 3 | 21 | 0.3875 |  | 40 | 5 | 8 | Russell | 13.2kV | TB14 | Squirell contact at the rear of 599 Browning caused the cut out to blow on transformer X27117. Refused and closed successfully, squirell did not make it | Ottawa | Foreign Interference | Animal
10182 | 2007 | 3 | 27 | 0.375 |  | 174 | 41 | 14 | Russell | 13.2kV | TB14 | Transformer #OTT1303 located at 670 Coronation isolated due to change open wire service | Ottawa | Scheduled Outage | Preventive Maintenance
17806 | 2011 | 3 | 30 | 0.54097 |  | 210 | 420 | 243 | Russell | 13.2kV | TB14 | tree contractor dropped a tree on the overhead circuit in the rear of 1543 Botsford, caused TB14 breaker to auto reclose then caused S13095 blue phase fuse to blow, crew cut the citcuit clear where the tree is located, refused the S13095 and repaired the o/H conductor. | Ottawa | Tree Contacts | Tree Limb Fallen
20302 | 2012 | 4 | 10 | 0.69375 |  | 69 | 8 | 7 | Russell | 13.2kV | TB14 | Replaced Primary lead that had broken from cut-out. Feeding transformer X39331 at 1591 Devon St | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6531 | 2005 | 5 | 10 | 0.44792 |  | 55 | 6 | 6 | Russell | 13.2kV | TB14 | Isolated Transformer #1301 at 624 Chadburn to replace the service wires. | Ottawa | Scheduled Outage | Preventive Maintenance
16087 | 2010 | 5 | 14 | 0.98542 |  | 172 | 75 | 26 | Russell | 13.2kV | TB14 | Temporary repairs made to burnt pole at 617 Browning. New pole is required asap. All load restored. | Ottawa | Defective Equipment
18192 | 2011 | 5 | 20 | 0.60208 |  | 118 | 16 | 8 | Russell | 13.2kV | TB14 | Transformer #X24848 located at 1513 Mimosa Ave opened up due to defective hot line clamp and lead. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20673 | 2012 | 6 | 2 | 0.2375 |  | 284 | 52 | 11 | Russell | 13.2kV | TB14 | Tranformer #X27100 located at 1585 Dixie St opened up, crew could not find cause. | Ottawa | Unknown/Other | No Apparent Cause
16225 | 2010 | 6 | 8 | 0.37083 |  | 71 | 154 | 130 | Russell | 13.2kV | TB14 | Squirrel contact at rear of 1480 Caverley caused circuit to A/R & SMD20 B phase fuse on Russell N. Of Shelley to blow. B phase fuse replaced & all power restored. | Ottawa | Foreign Interference | Animal
6687 | 2005 | 6 | 9 | 0.59236 |  | 546 | 9 | 1 | Russell | 13.2kV | TB14 | Defective 13 kv padmount PT41 at 855 Industrial was replaced with a new one. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16233 | 2010 | 6 | 9 | 0.40625 |  | 40 | 5 | 7 | Russell TS | 13.2kV | TB14 | Transformer # X21685 located at499 Penhill was opened to allow crews to replace an O/H service. | Ottawa | Scheduled Outage | Repair
8470 | 2006 | 6 | 12 | 0.16042 |  | 68 | 15 | 13 | Russell | 13.2kV | TB14 | One O/H transformer at 517 Braydon was interrupted due to a line clamp burning off, the line clamp was replaced & power was restored to the 13 customers on Avalon, Balena & Braydon. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10612 | 2007 | 6 | 12 | 0.86458 |  | 95 | 22 | 14 | Russell | 4.16kV | TB14 | Isolated transformer OTT1303 at 662 Coranation Ave to trim trees and repair open wire secondary | Ottawa | Tree Contacts | Tree Limb Fallen
16278 | 2010 | 6 | 17 | 0.38194 |  | 458 | 172 | 26 | Russell | 13.2kV | TB14 | A section of TB14 o/h line between Digby & Dixie was cut away to allow crew to replace burned pole. Line section was energized restoring Tx"s X27101 & X27121 before completing at Tx X27110 at rear of 617 Browning. | Ottawa | Scheduled Outage | Repair
5347 | 2004 | 6 | 21 | 0.5375 |  | 56 | 9 | 10 | TB | 13.2kV | TB14 | TxOTT5630 at 1698 Russell rd opened due to a squirrel contact. | Ottawa | Foreign Interference | Animal
8579 | 2006 | 6 | 22 | 0.375 |  | 45 | 8 | 10 | Russell | 13.2kV | TB14 | Transformer #OTT5630 located at 1633 Pullen isolated to put up a service | Ottawa | Scheduled Outage | Construction
3620 | 2003 | 6 | 28 | 0.71111 |  | 40 | 4 | 6 | Russel | 12/7.2kV | TB14 | Bird contact caused transformer fuse to rupture at 617 Bathurst Ave in Ottawa. | Ottawa | Foreign Interference | Animal
16345 | 2010 | 6 | 28 | 0.60694 |  | 144 | 2813 | 1172 | Russell | 13.2kV | TB14 | TB14 A/ R at 14:31 then went through A/R/A cycle & locked out when wind caused primary conductor to come in contact with a 600V service at 755 Industrial. The primary line was partially burned through and was isolated to allow crew to make repairs. The 600 V service required furhter repairs as well. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3631 | 2003 | 6 | 29 | 0.53611 |  | 53 | 6 | 7 | Russell | 13.2kV | TB14 | Vines caused the fuse to blow to the transformer in rear of 1587 Devon. 7 customers on Devon, Orchid & Shelley affected. | Ottawa | Foreign Interference | Foreign Object
10759 | 2007 | 6 | 29 | 0.37361 |  | 77 | 17 | 13 | Russell | 4.16kV | TB14 | Transformer #OTT1401 located at 1499 Chomley isolated due to animal contact | Ottawa | Foreign Interference | Animal
5408 | 2004 | 6 | 30 | 0.48542 |  | 41 | 7 | 10 | Russell | 12/7.2kV | TB14 | Ott5630 at 1698 Russel Rd transformer fuse replaced due to squirrel contact. | Ottawa | Foreign Interference | Animal
10809 | 2007 | 7 | 7 | 0.73958 |  | 60 | 10 | 10 | RUSSELL | 13.2kV | TB14 | Bird caused transformer fuse to blow at OTT5630. Fuse replaced all power restored at 1633 Pullen St. | Ottawa | Foreign Interference | Bird
8776 | 2006 | 7 | 18 | 0.29306 |  | 458 | 53 | 7 | Russell | 13.2kV | TB14 | Frank Bols had xfmr at 1462 Chomley open to change it. Xfmr blew during the storm | Ottawa | Adverse Weather | Lightning
18779 | 2011 | 7 | 20 | 0.44444 |  | 30 | 6 | 11 | Russell | 13.2kV | TB14 | Transformer #X26009 located at 499 Braydon opened by crew to re-establish triplex service | Ottawa | Tree Contacts | Tree Limb Fallen
8802 | 2006 | 7 | 22 | 0.8125 |  | 75 | 14 | 11 | Russel | 13.2kV | TB14 | Bird contact at 483 Braydon caused transformer OTT602 to open. Fuse replaced. | Ottawa | Foreign Interference | Bird
10955 | 2007 | 7 | 26 | 0.55556 |  | 50 | 2 | 2 | Russell | 13.2kV | TB14 | Transformer #000395 at 17 Bathurst isolated to allow for new service connection | Ottawa | Scheduled Outage | Construction
18830 | 2011 | 7 | 26 | 0.70556 |  | 348 | 151 | 26 | Russell | 13.2kV | TB14 | Tree contact in the rear of 1591 Digby caused TB14 breaker to auto reclose and S28447 fuse to blow. Crew later discovered a tree contractor dropped a large tree limb on the overhead circuit. Russell ID#18830. | Ottawa | Tree Contacts | Tree Fallen
3788 | 2003 | 7 | 27 | 0.6875 |  | 51 | 21 | 25 | Russell | 13.2kV | TB14 | Replaced blown transformer fuse. No obvious cause for blown fuse. | Ottawa | Unknown/Other | No Apparent Cause
11036 | 2007 | 8 | 11 | 0.91667 |  | 10 | 0 | 1 | Russell | 13.2kV | TB14 | Transformer at 700 Coronation which was feeding partial power was interrupted to tighten a live line clamp. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
18979 | 2011 | 8 | 19 | 0.44097 |  | 11 | 1 | 6 | Russell | 13.2kV | TB14 | Transformer #X26916 located at 1526 Caverley opened by crew to remove section of tree from secondary and re sag. | Ottawa | Tree Contacts | Tree Limb Fallen
16827 | 2010 | 8 | 28 | 0.51736 |  | 59 | 1137 | 1156 | Russell | 13.2kV | TB14 | TB14 circuit auto & locked out. Overhead circuit was patrolled no fault found. TB14 circuit closed and holding. Allload restored to normal. | Ottawa | Unknown/Other | No Apparent Cause
15080 | 2009 | 9 | 9 | 0.70833 |  | 385 | 64 | 10 | RUSSELL | 13.2kV | TB14 | Transformer at Russell Rd & Industrial Ave isolated to allow for transfer of temporary feed | Ottawa | Scheduled Outage | Construction
13368 | 2008 | 10 | 15 | 0.39583 |  | 55 | 8 | 9 | Russell | 4.16kV | TB14 | Isolated TFR X27083 @1480 Caverley St for a service upgrade | Ottawa | Scheduled Outage | Repair
15274 | 2009 | 10 | 18 | 0.19514 |  | 9 | 1 | 7 | Russell | 13.2kV | TB14 | Transformer in the rear of 495 Penhill was opened to allow crew to disconnect service due to fire. | Ottawa | Adverse Environment | Fire
15303 | 2009 | 10 | 26 | 0.40625 |  | 22 | 2 | 5 | Russell | 13.2kV | TB14 | Transformer #OTT5612 located at 1662 Russell Ave isolated to install new 400 amp U/G service | Ottawa | Scheduled Outage | Construction
9591 | 2006 | 11 | 3 | 0.32708 |  | 144 | 2 | 1 | Russell | 4.16kV | TB14 | Transformer #OTT575 located at 480 Avalon isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
9612 | 2006 | 11 | 6 | 0.50694 |  | 150 | 32 | 13 | Russell | 13.2kV | TB14 | Bob Rolland isolated trf.601 to install new pole @ 507 Braydon | Ottawa | Scheduled Outage | Construction
9613 | 2006 | 11 | 6 | 0.55 |  | 88 | 22 | 15 | Russell | 13.2kV | TB14 | Bob Willis isolated trf. @540 Braydon to install new pole | Ottawa | Scheduled Outage | Construction
15365 | 2009 | 11 | 8 | 0.53819 |  | 151 | 2866 | 1139 | Russell | 13.2kV | TB14 | 24/7 reports a ground on isolated 5307 overhead found wrapped in TB14 blue phase conductor @ 755 Industrial Rd. Also 2 conductors of the new construction of 5307 & 5306 found wrapped in TB14 blue phase @ 820 Belfast Rd. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13594 | 2008 | 11 | 12 | 0.49306 |  | 50 | 2 | 2 | Russell | 13.2kV | TB14 | Transformer #PT144 located at 1555 St. Laurent isolated due to service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
7638 | 2005 | 11 | 16 | 0.44236 |  | 271 | 271 | 60 | TB | 13.2kV | TB14 | TR10 (TR1JP = TB2JP) & TR04 ( TR1UQ=TB1UQ) tripped due to a broken wart style insulator on the center phase of TB2JP along HEPC right of way. The flash caused the adjacent circuit to open as well as blowing a red phase fuse on TB14 underbuild. A road had to be opened to allow access to the broken insulator before TB14 could be re-fused. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9683 | 2006 | 11 | 19 | 0.625 |  | 22 | 20 | 55 | Russell | 13.2kV | TB14 | AT 15:00 trans KT144 was isolated at 707 Coronation Ave in order to replace defective sec connection on T3 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19629 | 2011 | 11 | 24 | 0.38889 |  | 43 | 11 | 16 | Russell | 13.2kV | TB14 | Transformers #X26909 and X26900 located at 625 and 637 Bathurst opened by crew to install a new service | Ottawa | Scheduled Outage | Construction
5949 | 2004 | 11 | 29 | 0.38542 |  | 25 | 2 | 5 | Russell | 13.2kV | TB14 | House service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
19653 | 2011 | 11 | 30 | 0.70347 |  | 6 | 1 | 6 | RUSSELL | 13.2kV | TB14 | Transformer X26916 at 1526 Caverley St. Isolated to remove fallen tree limb | Ottawa | Tree Contacts | Tree Limb Fallen
17362 | 2010 | 12 | 1 | 0.55069 |  | 132 | 1377 | 626 | Russell | 13.2kV | TB14 | At 13:13 crews isolated TB14 overhead from S25488 to brace a burnt pole top at the rear of 533 Browing. 626 customers affected for 132 mins. Russell (TB14) ID# 17362 | Ottawa | Unknown/Other
15534 | 2009 | 12 | 20 | 0.55556 |  | 55 | 6 | 7 | Russell | 13.2kV | TB14 | A squirrel contact caused the transformer at the rear of 540 Browning to open. | Ottawa | Foreign Interference | Animal
15546 | 2009 | 12 | 23 | 0.77083 |  | 255 | 8 | 2 | Russel | 13.2kV | TB14 | Transformer PT38 at 831 Industrial Rd isolated to transfer plant to new pole. | Ottawa | Scheduled Outage | Construction
17462 | 2010 | 12 | 31 | 0.26458 |  | 94 | 16 | 10 | Russell | 13.2kV | TB14 | Replaced blown fuse at transformer X39346 at 639 Chadburn Ave due to vines around transformer primary bushing | Ottawa | Tree Contacts | Inadequate Trimming
7955 | 2006 | 2 | 20 | 0.51319 |  | 86 | 22 | 15 | Russell | 13.2kV | TB15 | Transformer #OTT1353 located at 2001 Saunderson isolated due to animal contact | Ottawa | Foreign Interference | Animal
12067 | 2008 | 2 | 20 | 0.97222 |  | 219 | 1624 | 445 | Russell TS | 13.2kV | TB15 | At 11:20pm, Scada indicates TB15 has opened. D. Guy reports phase came down N.W corner of 1854 Haig Drive when 24/7 was trying to repair a loose connection, 445 customers affected for 219min. ID#12067. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20125 | 2012 | 3 | 5 | 0.6875 |  | 18 | 3 | 9 | Russell | 13.2kV | TB15 | Transformer #X21688 located at 1858 Haig Dr opened by crew to replace broken switch | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6255 | 2005 | 3 | 9 | 0.72014 |  | 103 | 14 | 8 | Russell | 13.2kV | TB15 | Transformer KT609 at 1920 Russell rd. was opened for crew to replace live line clamp on Overhead switch. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
15795 | 2010 | 3 | 13 | 0.46944 |  | 89 | 18 | 12 | Russell | 13.2kV | TB15 | Transformer #X27645 located at 678 Hastings opened due to squirrel | Ottawa | Foreign Interference | Animal
8027 | 2006 | 3 | 15 | 0.39722 |  | 7 | 1 | 9 | Russell | 13.2kV | TB15 | Jeff Meek had transformer OTT5817 for a pole change @ 917 Smyth | Ottawa | Unknown/Other
8028 | 2006 | 3 | 15 | 0.52222 |  | 140 | 21 | 9 | Russell | 13.2kV | TB15 | Jeff Meek took off transformer OTT5817 to do a pole change at 907 Smyth. | Ottawa | Unknown/Other
20168 | 2012 | 3 | 15 | 0.47569 |  | 74 | 10 | 8 | Russell | 13.2kV | TB15 | Transformer #X27160 located at 1750 Russell Rd opened by crew to install a new service | Ottawa | Scheduled Outage | Construction
8048 | 2006 | 3 | 20 | 0.52083 |  | 80 | 12 | 9 | Russell | 13.2kV | TB15 | Mike Gruich opened transformer OTT5817 feeding 7 customers to do a pole transfer | Ottawa | Scheduled Outage | Construction
8095 | 2006 | 4 | 2 | 0.83264 |  | 191 | 105 | 34 | Russell | 13.2kV | TB15 | Fire Department requested power shut off to 1797 Russell Units E, F, G & H. KT108 was interrupted first to remove power from Units F, G & H, no access to 108P1 pedestal due to proximity of fire. Then KT109 was then interrupted to remove power to Unit E. All units A to I remain disconnected at the Fire Department's request & power was then restored to the remaining 26 units. 108P1 was not disconnected at KT108 due to a broken handle, 108P1 was disconnected right at the pedestal on the supply side. Units A to E were disconnected at KT109. | Ottawa | Adverse Environment | Fire
20270 | 2012 | 4 | 3 | 0.45833 |  | 60 | 10 | 10 | Russell | 13.2kV | TB15 | Transformer X21514 at 1799 Saunderson Dr isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
6552 | 2005 | 5 | 13 | 0.42917 |  | 87 | 13 | 9 | Russell | 13.2kV | TB15 | Replaced blown fuse to Transformer OTT3346 at 1839 Hutton Ave Outage caused by squirrel | Ottawa | Foreign Interference | Animal
18152 | 2011 | 5 | 14 | 0.56597 |  | 20 | 0 | 1 | RUSSELL | 13.2kV | TB15 | Defective lead at S23634, 1825 Russell Road was replaced. | Ottawa | Defective Equipment
20643 | 2012 | 5 | 30 | 0.38542 |  | 226 | 26 | 7 | Russell | 13.2kV | TB15 | Transformer X26883 at 701 Smyth Rd. isolated to allow for tree removal by private contractor | Ottawa | Tree Contacts
18285 | 2011 | 6 | 3 | 0.32083 |  | 108 | 22 | 12 | Russell | 4.16kV | TB15 | Replaced blown fuse in switch feeding transformer X27168 at 1832 Haig Dr (Removed vines) | Ottawa | Tree Contacts | Inadequate Trimming
12556 | 2008 | 6 | 6 | 0.24583 |  | 136 | 20 | 9 | Russell | 4.16kV | TB15 | Blown fuse on transformer X27337 at 1972 Naples Ave due to a squirrel contact | Ottawa | Foreign Interference | Animal
14523 | 2009 | 6 | 12 | 0.275 |  | 129 | 28 | 13 | Russell | 13.2kV | TB15 | Transformer #X26921 located 1917 Dauphin Rd isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
5340 | 2004 | 6 | 19 | 0.66389 |  | 129 | 32 | 15 | Russell | 13.2kV | TB15 | Winds caused tree damage. Crew repaired secondary bus and refused transformer at 1966 Olympia. | Ottawa | Adverse Weather | Wind
16304 | 2010 | 6 | 21 | 0.37014 |  | 506 | 290 | 44 | Russell |  | TB15 | Tree limb fallan damaging primary and secondary conductors and an o/h transformer. | Ottawa | Tree Contacts | Tree Limb Fallen
16334 | 2010 | 6 | 26 | 0.875 |  | 56 | 7 | 8 | Russell | 13.2kV | TB15 | Fuses at transformer X26242 @ 1953 Olympia blown for no apparent reason. | Ottawa | Unknown/Other | No Apparent Cause
12767 | 2008 | 6 | 29 | 0.61736 |  | 323 | 86 | 16 | Russel | 13.2kV | TB15 | O/H transformer at 2025 Olympia Cr failed and was replaced by On Call. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10811 | 2007 | 7 | 7 | 0.79028 |  | 77 | 51 | 40 | Russell | 13.2kV | TB15 | Animal contact at transfromer caused transformer and line fuse to blow. S26818 white phase found blown. | Ottawa | Foreign Interference | Animal
18632 | 2011 | 7 | 9 | 0.58333 |  | 65 | 44 | 41 | Russell | 13.2kV | TB15 | Defective insulator, line switch and hot line clamp at 1835 Hutton were replaced. Russell (TB15) ID#18632 | Ottawa | Defective Equipment
5475 | 2004 | 7 | 11 | 0.42639 |  | 40 | 9 | 13 | Russell | 13.2kV | TB15 | O/H transformer OTT1859 at 1913 Dauphin re-fused after contact a with squirrel. | Ottawa | Foreign Interference | Animal
6936 | 2005 | 7 | 13 | 0.88403 |  | 8 | 59 | 445 | Russell | 13.2kV | TB15 | TB15 breaker tripped-reclosed & tripped. Breaker was closed manually from SCADA. Problem was later determined to be primary conductor down on Haig north of Smythe. | Ottawa | Adverse Weather | Lightning
16462 | 2010 | 7 | 13 | 0.31597 |  | 80 | 9 | 7 | Russell | 13.2kV | TB15 | Transformer #X29124 located at 1845 Hutton opened up due to tree interference | Ottawa | Tree Contacts | Inadequate Trimming
6931 | 2005 | 7 | 14 | 0.054167 |  | 235 | 1743 | 445 | Russell | 13.2kV | TB15 | Circuit was interrupted manually from SCADA due to primary wires on the ground. Circuit had tripped earlier as well. | Ottawa | Adverse Weather | Lightning
6957 | 2005 | 7 | 14 | 0.82639 |  | 73 | 486 | 445 | Russell | 13.2kV | TB15 | TB15 ACB opened from SCADA to lift pats at Haig & Raglan in order to repair downed conductor from this morning's storm. No customers were without power from the downed caonductor as the load side of conductor broke with no customers after the break. TB15 ACB was reopened from SCADA in order to reconnect the pats. | Ottawa | Adverse Weather | Lightning
18735 | 2011 | 7 | 19 | 0.24167 |  | 1192 | 3568 | 186 | Russell | 13.2kV | TB15 | S21380 in the rear of 806 Smyth found open, then transformer cut out found open in the rear of 1010 Haig with primary cunductor down. | Ottawa | Tree Contacts | Tree Limb Fallen
7024 | 2005 | 7 | 25 | 0.83333 |  | 68 | 7 | 6 | Lincoln | 4.16kV | TB15 | At 21:08 Trans @ 802 Raglan Ave refused due to animal contact | Ottawa | Foreign Interference | Animal
14835 | 2009 | 7 | 25 | 0.31042 |  | 282 | 52 | 11 | Russel | 13.2kV | TB15 | Crew found switch at transformer in the rear of 2018 Olympia blown. No apparent cause found. Same refused and closed to restore power. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16594 | 2010 | 7 | 30 | 0.87153 |  | 30 | 4 | 9 | Russell | 13.2kV | TB15 | Racoon opened transformer X21514 @ rear of 1772 Hutton caused TB15 circuit to auto-reclose. | Ottawa | Foreign Interference | Animal
14927 | 2009 | 8 | 9 | 0.93819 |  | 113 | 46 | 29 | Russell | 13.2kV | TB15 | Transformer cut-out fuse blew at 1843 Saunderson & also line fuse blew at 1787 Haig interrupting power to customers on Haig, Hutton & Saunderson in the Elmvale Acres area. Line fuse was closed first restoring power to 2 transformers and then thr transformer was refused successfully. | Ottawa | Unknown/Other
8976 | 2006 | 8 | 15 | 0.63889 |  | 367 | 420 | 70 | Russell | 13.2kV | TB15 | Two single phase overhead line sections in the Smythe & Othello area were isolated for K-Line to replace poles. During restoration S22538 would not close & had to be replaced. | Ottawa | Scheduled Outage | Preventive Maintenance
11059 | 2007 | 8 | 15 | 0.14028 |  | 104 | 12 | 7 | Russell | 13.2kV | TB15 | 917 Hamlet transformer fuse blew due to vines growing up the pole, crew cleared vines and re-fused transformer. | Ottawa | Tree Contacts | Inadequate Trimming
8983 | 2006 | 8 | 16 | 0.35903 |  | 386 | 397 | 70 | Russell | 13.2kV | TB15 | Two single phase overhead line sections in the Smythe & Othello area were isolated for K-Line to replace poles. At 12:23, the line section fed from S17223 was restored. | Ottawa | Scheduled Outage | Preventive Maintenance
9078 | 2006 | 8 | 28 | 0.38889 |  | 220 | 37 | 10 | Russell | 4.16kV | TB15 | At 09:20 trans at 2025 Olympia Cres was isolated iin order to transfer trans and equip to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
11166 | 2007 | 8 | 28 | 0.38194 |  | 40 | 9 | 14 | Russell | 13.2kV | TB15 | Isolated transformer OTT5816 at 883 Smyth Rd to replace service | Ottawa | Scheduled Outage | Preventive Maintenance
9085 | 2006 | 8 | 29 | 0.37153 |  | 109 | 18 | 10 | Russell | 13.2kV | TB15 | Isolated and removed from service transformer OTT4764 at 2001 Olympia Cres | Ottawa | Scheduled Outage | Construction
9096 | 2006 | 8 | 30 | 0.39583 |  | 235 | 43 | 11 | Russell | 13.2kV | TB15 | Isolated transformer OTT4642 at 1989 Naples Ave to replace pole | Ottawa | Scheduled Outage | Construction
11213 | 2007 | 8 | 30 | 0.32083 |  | 41 | 1 | 1 | Russell | 13.2kV | TB15 | To repair a broken switch S17642 at PT206 @ Vincent Massey school 745 Smyth Rd | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15046 | 2009 | 9 | 1 | 0.88889 |  | 69 | 6 | 5 | Russell | 13.2kV | TB15 | Refused blown switch feeding transformer OTT5668 at the rear of 1782 Haig Dr | Ottawa | Tree Contacts | Inadequate Trimming
4020 | 2003 | 9 | 5 | 0.52431 |  | 13 | 3 | 15 | TB | 13.2kV | TB15 | KT110 at 1781 Russel was opened to reconnect unit E (arrears disconnect) | Ottawa | Scheduled Outage
9121 | 2006 | 9 | 5 | 0.38542 |  | 150 | 18 | 7 | Russell | 4.16kV | TB15 | At 09:15 trans OTT4640 at 1969 Naples Ave was isolated for trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9145 | 2006 | 9 | 8 | 0.1875 |  | 105 | 12 | 7 | Russell | 13.2kV | TB15 | O/H transformer at 1845 Hutton was isolated to replace triplex & connections. | Ottawa | Defective Equipment
11282 | 2007 | 9 | 10 | 0.72222 |  | 159 | 19 | 7 | Russell | 13.2kV | TB15 | Transformer #OTT2963 at 864 Smyth Rd isolated to allow for repairs to customer service | Ottawa | Human Element | Incorrect Use of Equipment
9246 | 2006 | 9 | 18 | 0.375 |  | 100 | 8 | 5 | Russell | 12/7.2kV | TB15 | At 09:00 trans at 930 Wingate Dr in order to relocate secondary service | Ottawa | Scheduled Outage
15183 | 2009 | 9 | 28 | 0.54167 |  | 55 | 30 | 33 | Russell | 13.2kV | TB15 | TB15 line section fed from S21753 isolated to repair broken conductor on Portage Ave at dip pole to VT448. TB15 breaker auto-reclosed once when conductor sleeve let go, see ID #15181. Customers affected on Portage, Haig, Dauphin, Tweed & Hamlet including Hillcrest H.S. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11422 | 2007 | 10 | 1 | 0.38542 |  | 10 | 4 | 22 | Russell | 13.2kV | TB15 | Transformer #KT0107 at 1779 Russell Rd isolated to do disconnect for arrears | Ottawa | Scheduled Outage | Construction
17036 | 2010 | 10 | 1 | 0.38194 |  | 55 | 9 | 10 | Russell | 13.2kV | TB15 | Transformer #X26881 located at 1846 Russell opened by crew to install new O/H service | Ottawa | Scheduled Outage | Construction
17088 | 2010 | 10 | 9 | 0.10278 |  | 51 | 667 | 785 | Russell | 13.2kV | TB15 | Vehicle hit stub pole in front of 1806 Haig dr. That caused circuit to lock out. | Ottawa | Foreign Interference | Vehicle
17165 | 2010 | 10 | 24 | 0.78333 |  | 127 | 106 | 50 | Russell | 13.2kV | TB15 | Overhead transformer fused switch failed at 1970 Naples Ave. Causing line switch S17223 to open. Outage effected 50 customers in the area of Naples & Windgate area. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4369 | 2003 | 11 | 2 | 0.94583 |  | 26 | 3 | 7 | Russell | 12/7.2kV | TB15 | Call from customer that sparking is coming from transformer in back yard of 1818 Saunderson | Ottawa | Defective Equipment
15345 | 2009 | 11 | 2 | 0.47153 |  | 110 | 52 | 30 | Russell | 13.2kV | TB15 | Squirrel contact at O/H transformer caused both the transformer cutout fuse & the supply fuse to radial line to blow. O/H line was refused first & then power was restored to the single O/H transformer. Customers interrupted were on Hutton Ave & Russell Rd. | Ottawa | Foreign Interference | Animal
17207 | 2010 | 11 | 2 | 0.38889 |  | 190 | 22 | 7 | Russell | 13.2kV | TB15 | Transformer #X29124 located at 1845 Hutton opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
11663 | 2007 | 11 | 5 | 0.65625 |  | 44 | 8 | 11 | Russel | 13.2kV | TB15 | Transformer OTT2951 isolated to disconnect customer at 908 Smyth Rd so customer can complete repairs on their equipment. | Ottawa | Defective Equipment
15374 | 2009 | 11 | 9 | 0.43194 |  | 78 | 13 | 10 | RUSSELL | 13.2kV | TB15 | Transformer X34465 at 1960 Haig Drive isolated to change open wire service | Ottawa | Scheduled Outage | Construction
4453 | 2003 | 11 | 14 | 0.078472 |  | 505 | 907 | 400 | Russell | 13.2kV | TB15 | A large spruce tree in the rear of 875 Hamlet fell on TB15 overhead blowing all 3 phases of TB15-S2 and damaging the white phase cutout requiring isolation to effect emergency repairs. Tree removal; continued with TB15-S2 being a point of isolation allowing the restoration of the rest of TB15 circuit. Upon completion of tree removal the rest of TB15 was restored by closing the TB15-S2. | Ottawa | Adverse Weather | Wind
15395 | 2009 | 11 | 17 | 0.38194 |  | 26 | 8 | 18 | RUSSELL | 13.2kV | TB15 | Transformer KT104 at 1761 Russell Rd isolated to allow for disconnect for Revenue Dept | Ottawa | Scheduled Outage | Construction
4479 | 2003 | 11 | 18 | 0.54167 |  | 20 | 2 | 7 | Russell | 13.2kV | TB15 | J. Petrachuk reports transformer #2920 isolated to remove tree. 7 Customers affected in power outage at 1768 Haig. | Ottawa | Tree Contacts | Tree Fallen
5947 | 2004 | 11 | 29 | 0.091667 |  | 45 | 10 | 14 | Russell | 13.2kV | TB15 | O/H transformer at 1812 Haig re-fused, suspect tree contact due to high wind. | Ottawa | Tree Contacts | Inadequate Trimming
15523 | 2009 | 12 | 16 | 0.46875 |  | 30 | 5 | 10 | Russell | 13.2kV | TB15 | Transformer #X26881 located at 1831 Hutton isolated to renew connections at the pole | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4626 | 2003 | 12 | 18 | 0.49306 |  | 47 | 1410 | 1978 | Russell | 13.2kV | TB15, TB2JP | Circuits were both patrolled with no sign of a fault or cause for outage. AJT1, AJT2 & UPT2 transformers were removed from service with TB2JP. | Ottawa | Adverse Weather | Snow
3730 | 2003 | 7 | 13 | 0.21389 |  | 27 | 1598 | 3550 | Russell | 13.2kV | TB15,TB2AL | After consulting Hyrdo OnE control room and being advised we should transfer the load to our own transfer breakers Hydro One operator decided that we should not use the Q bus for this purpose and insisted that we interupt the load again. This was done until Hydro One operator determined that it was OK to close the 36QZ breaker restoring the load on the Russell Q bus. | Ottawa | Loss of Supply | HEPC Station Fault
16377 | 2010 | 7 | 1 | 0.49931 |  | 39 | 107 | 222 | Russell | 13.2kV | TB1AL | AL02 auto-reclosed causing TB17 (TB1AL) to open due to overhead wires slapped together at the Science and Technology parking lot. | Ottawa | Foreign Interference
16503 | 2010 | 7 | 20 | 0.52778 |  | 409 | 273 | 341 | Russell | 13.2kV | TB1AL | Cable dig-in cable at 1730 St. Laurent blvd. At 12:49 AlT1 load was restored at Bantree substation. VT445 & VT168 as restored at 13:14. VT701 @ 1730 St. Laurent Blvd all power restored. | Ottawa | Foreign Interference | Dig-in
16542 | 2010 | 7 | 22 | 0.76944 |  | 158 | 5 | 2 | Russell | 13.2kV | TB1AL | VT701 at 1730 ST Laurent Rd was isolated to allow crews to repair dammaged cable. 2 customers were affected. Russell (TB1AL). | Ottawa | Scheduled Outage
16664 | 2010 | 8 | 4 | 0.65903 |  | 11 | 61 | 334 | Russell | 13.2kV | TB1AL | TB17 breaker tripped during heavy rain & lightning. Breaker closed manually from SCADA. | Ottawa | Unknown/Other
15124 | 2009 | 9 | 18 | 0.62708 |  | 127 | 454 | 332 | RUSSELL | 13.2kV | TB1AL | TB1AL tripped, inturupting customers on St Laurent, Gladwin, and T1 at Bantree Sub. All load restored from an alternate source, overhead portion was patrolled and nothing was found, suspected underground fault. | Ottawa | Unknown/Other
4096 | 2003 | 9 | 19 | 0.70556 |  | 15 | 158 | 635 | TB | 13.2kV | TB1AL | SCADA reported TB1AL tripped & at the same time SCADA indicated AL02 & AL04 auto-reclosed. Very windy day. TB1AL was reclosed by S.O. which held but then ALT1 tripped. After checking tripping sequences ALT1 was closed and AL03, AL04, & AL02 were picked in that order up and held. | Ottawa | Adverse Weather | Wind
4129 | 2003 | 9 | 23 | 0.69236 |  | 4 | 42 | 635 | TB | 13.2kV | TB1AL | TB1AL & TB3LE both tripped at the same time. Very windy out, and both circuits run O/H & parrallel to each other. Neither cct has R/C, so circuits were closed and both held. | Ottawa | Adverse Weather | Wind
15185 | 2009 | 9 | 28 | 0.62153 |  | 17 | 213 | 774 | Russell | 13.2kV | TB1AL | TB17 breaker tripped at the same time as 4 kv underbuild AL02 auto-reclosed.TB1AL circuit feeds 3 vaults and ALT1 transformer at Bantree. Circuit was re-energized first restoring power to the 3 vaults & then ALT1 load was restored. | Ottawa | Unknown/Other
17323 | 2010 | 11 | 22 | 0.50764 |  | 6 | 33 | 334 | Russell | 13.2kV | TB1AL | Tree trimmers Charlie Godwin of Tamarack had a falling tree cause an unintentional contact made between 2 circuits. Interupting TB3LE (TB01) TB1AL (TB17) and AL02 | Ottawa | Tree Contacts | Tree Fallen
15560 | 2009 | 12 | 27 | 0.12847 |  | 39 | 209 | 322 | Russell | 13.2kV | TB1AL | TB17 (TB1AL) tripped and locked out. Circuit was patrolled and no problems were found. Circuit was closed via scada. All customer restored. | Ottawa | Adverse Weather | Ice Storm
7073 | 2005 | 8 | 5 | 0.75486 |  | 76 | 1030 | 1442 | TB | 13.2kV | TB1AL, TB3LE | TB1AL & TB3LE lines tripped, o/h was patrolled before restoring TB3LE & TB1AL load was transferred to alternate supply. Note: T1 @ AE was o/s at the time, reducing the number of customers affected. Patrol & hi-pot of TB1AL found no problems, line placed on pot before restoring to normal. | Ottawa | Unknown/Other
20870 | 2012 | 6 | 26 | 0.34444 |  | 95 | 16 | 10 | Albion | 13.2kV | TB1UQ | SC2402 at Don Reid and Walkley was found tripped. Circuit was sectionalized and restored. No cause was found. | Ottawa | Unknown/Other | No Apparent Cause
19531 | 2011 | 11 | 5 | 0.021528 |  | 107 | 811 | 534 | Russell | 13.2kV | TB1UQ | TB22 breaker at Russell Sub auto-reclosed and locked out. Crews restored power to affected customers and isolated circuit. No cause has been found as of yet. | Ottawa | Unknown/Other | No Apparent Cause
7623 | 2005 | 11 | 16 | 0.48264 |  | 108 | 2324 | 2130 | TR | 13.2kV | TB1UQ, TB2JP | TR10 (TR1JP = TB2JP) & TR04 ( TR1UQ=TB1UQ) tripped due to a broken wart style insulator on the center phase of TB2JP along HEPC right of way. The flash caused the adjacent circuit to open as well as blowing a red phase fuse on TB14 underbuild. A road had to be opened to allow access to the broken insulator before TB14 could be re-fused. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14112 | 2009 | 3 | 29 | 0.77569 |  | 458 | 1053 | 704 | Russell | 13.2kV | TB1UQ/TA1JP | Circuit tripped after attempting to restore, possible defective insulators or wet weather. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15552 | 2009 | 12 | 26 | 0.35139 |  | 67 | 136 | 122 | Russell | 13.2kV | TB20 | At 08:26am breaker TB20 opened due to defective switch (vegas) at 1867 St. Laurent crews opened swiches and circuit was then pick back up. 122 customers were affected for 67 minutes. Russell (TB20) ID#15552. | Gloucester | Defective Equipment
15715 | 2010 | 2 | 10 | 0.80278 |  | 164 | 319 | 428 | Russell TB | 13.2kV | TB2AL | TB24 breaker (TB2AL cct) tripped A/R/A. All load transferred to alternate source. Access issues at VT301 & equipment issues at SC6131 delayed final restoration of last 2 customers. Cause of trip to be investigated. | Ottawa | Unknown/Other | No Apparent Cause
15728 | 2010 | 2 | 18 | 0.72222 |  | 44 | 4 | 5 | Russell | 13.2kV | TB2AL | SW133 at 1881 Bantree isolated to repair terminations. 5 commercial customers affected. | Ottawa | Scheduled Outage | Repair
10154 | 2007 | 3 | 21 | 0.65694 |  | 114 | 4 | 2 | RUSSELL | 13.2kV | TB2AL | At 201 Innes Parkay SC10002 CB3 and CB4 where found tripped. Equipment checked nothing found, power restored. | Ottawa | Unknown/Other | No Apparent Cause
10287 | 2007 | 4 | 20 | 0.30208 |  | 95 | 2 | 300 | Russell | 13.2kV | TB2AL | All customers were restored from their alternate supply. Problem was later determined to be a burnt cable termination in SW147. Repairs were completed by On-call on Saturday, April 21st. | Ottawa | Unknown/Other | No Apparent Cause
14660 | 2009 | 7 | 3 | 0.46042 |  | 123 | 320 | 156 | Russell | 13.2kV | TB2AL | TB24 breaker at Russell auto reclosed the same time as TB20, AL10, TB03 and ALK1Y1 breakers tripped, no apparent cause was found during patrol. When TB2AL reclosed AL10 at Bantree remained open with 2 phases wrapped together at the station, AL10 was isolated for repairs and inspection. | Ottawa | Unknown/Other | No Apparent Cause
19776 | 2011 | 12 | 31 | 0.99236 |  | 2 | 17 | 497 | Russell TS | 13.2kV | TB2AL | TB24 carrying TB2AL had to be opened during emergency switching to allow crews to close single blade switches. | Ottawa | Foreign Interference | Vehicle
6521 | 2005 | 5 | 8 | 0.52639 |  | 127 | 1102 | 1533 | TB | 13.2kV | TB2JP | TB13 breaker tripped, all load transferred to alternate supply. Patrol found broken wart style insulator on o/h line. | Ottawa | Defective Equipment
18268 | 2011 | 6 | 1 | 0.59028 |  | 9 | 355 | 2365 | Russell | 13.2kV | TB2JP | High winds caused TB2JP (TB13) to trip. Affecting transformers at Playfair T2 and Kilborn T2 as well as Playfair Towers and Rosemeadow Condos. Breaker closed all load restored. | Ottawa | Adverse Weather | Wind
18273 | 2011 | 6 | 1 | 0.69236 |  | 8 | 315 | 2365 | Russell | 13.2kV | TB2JP | TB13 TB2JP tripped for a second time, no calls and no apparent reason, closed by SCADA | Ottawa | Unknown/Other | No Apparent Cause
7314 | 2005 | 9 | 10 | 0.37153 |  | 159 | 1702 | 1600 | Russell | 13.2kV | TB2JP | Part of TB1UQ line being carried on TB2JB cable. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10225 | 2007 | 4 | 8 | 0.49653 |  | 48 | 1099 | 1374 | Russell | 13.2kV | TB3LE | TB3LE tripped with load loss at Urbandale. 24/7 coming in from Munster RD and Fernbank. Blown Arrester found at 2064 St Laurent Rd Porclien Arrester. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5061 | 2004 | 4 | 27 | 0.12778 |  | 20 | 235 | 1374 | Russell | 13.2kV | TB3LE | TB3LE tripped on TB01 breaker causing the loss of load on AET1 and AET2 transformers. | Ottawa | Unknown/Other | No Apparent Cause
18051 | 2011 | 4 | 28 | 0.56736 |  | 36 | 1214 | 2024 | Russell | 13.2kV | TB3LE | TB01 circuit auto-reclosed and locked out. Circuit feeding Urbandale T1 and T2. Crews transfered load and restored power. | Ottawa | Defective Equipment
6642 | 2005 | 6 | 2 | 0.46597 |  | 14 | 585 | 2509 | TB | 13.2kV | TB3LE | TB01 breaker tripped, station crew was on site for a different job & reported trip setting on TB01 breaker was at 400A, as there is a double cable on this cct, the setting was changed to 720A before closing the breaker. There was approx 380A on breaker when it tripped. No other problems reported. | Ottawa | Human Element | Incorrect Protection Settings
12532 | 2008 | 6 | 2 | 0.67847 |  | 108 | 1328 | 1373 | Russell | 13.2kV | TB3LE | Ottawa fire reports flash on pole at 1917 St. Laurent Blvd. S. Barkley dispatched. M. Brown reports AE load restored VIA TA2AE circuit. VT168 @ 2267 Galdwin mains off due to defective switch in vault. TB01 breaker closed restoring TB3LE circuit. Crews report no problems found on overhead circuit. | Ottawa | Adverse Weather | Lightning
6783 | 2005 | 6 | 22 | 0.59097 |  | 116 | 2227 | 2053 | Russell | 13.2kV | TB3LE | AE01 & AE06 circuits wrapped together in several locations. Cause for wrapping is unknown. The wrapping tripped two 4 kv circuits at Urbandale as well as the 13 kv supply cct to Urbandale which happened to be carrying 5303 at the time. Most power was restored when the situation was identified, and the remainder (AE01 & AE06) was restored after the detangling. | Ottawa | Unknown/Other | No Apparent Cause
8595 | 2006 | 6 | 26 | 0.60069 |  | 292 | 1972 | 1374 | Russell | 13.2kV | TB3LE | TB3LE, AE01 & AE06 ccts tripped at the same time. Crew found AE01 & AE06 ccts tangled together where all 3 circuits run together on St. Laurent. Power was restored to the 13 kv cct TB3LE and all load was restored at Urbandale except AE01 & AE06. At 14:51 5303 auto-reclosed while attempting to restore AET1 load when AE01 breaker closed & opened. AE01 & AE06 circuits were isolated for work protection & detangled. AE06 was restored at 16:45, however AE01 still would not hold. Circuit was patrolled again by 24/7 & On-call and no sign of a problem was found. AE01 cable between station & P/P/H was energized to confirm its integrity & it held. Circuit was re-energized with crews spread out to detect problem & the circuit held. | Ottawa | Defective Equipment
16656 | 2010 | 8 | 4 | 0.65903 |  | 15 | 506 | 2022 | Russell | 13.2kV | TB3LE | TB01 breaker tripped during heavy rain & lightning. Breaker closed manually from SCADA. | Ottawa | Unknown/Other
7162 | 2005 | 8 | 18 | 0.69306 |  | 5 | 114 | 1374 | Russell | 13.2kV | TB3LE | A patio umbrella from the Fat Alberts at the corner of Smyth & ST. Laurent took flight into the o/h opening two circuits. | Ottawa | Foreign Interference | Foreign Object
11235 | 2007 | 9 | 4 | 0.24444 |  | 53 | 624 | 706 | Russell | 13.2kV | TB3LE | A blown lightning arrestor on the AL04 under build which flash up into the the 13 KV which cause it to trip in the St Laurent Gladwin area. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4095 | 2003 | 9 | 19 | 0.70556 |  | 1 | 23 | 1374 | Russell | 13.2kV | TB3LE | Due to wind storm TB3LE circuit opened. Circuit has no recloser. Closed by scada and held. Feeds all Urbandale sub. | Ottawa | Adverse Weather | Wind
4130 | 2003 | 9 | 23 | 0.69236 |  | 4 | 92 | 1374 | TB | 13.2kV | TB3LE | TB1AL & TB3LE both tripped at the same time. Very windy out, and both circuits run O/H & parallel to each other. Neither cct has R/C, so circuits were closed and both held. | Ottawa | Adverse Weather | Wind
9472 | 2006 | 10 | 20 | 0.054861 |  | 39 | 893 | 1374 | Russell | 13.2kV | TB3LE | TB3LE tripped due to a possible defective cable at dip to VT274. Both switches of the dual radial supply at VT274 were found closed which caused the normal feed (5303) to trip also. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4338 | 2003 | 10 | 25 | 0.16528 |  | 143 | 5 | 2 | Russell | 13.2kV | TB3LE | VT168 @2261 Gladwin was isolated to repair TB3LE-L3 and maintain the vault | Ottawa | Scheduled Outage | Repair
17322 | 2010 | 11 | 22 | 0.50764 |  | 5 | 169 | 2024 | Russell | 13.2kV | TB3LE | Tree trimmers Charlie Godwin of Tamarack had a falling tree cause an unintentional contact made between 2 circuits. Interupting TB3LE (TB01) TB1AL (TB17) and AL02 | Ottawa | Tree Contacts | Tree Fallen
15319 | 2009 | 10 | 28 | 0.38194 |  | 310 | 129 | 25 | russell | 13.2kV | tbo5 | R phase local of the TB14 circuit on Bloor Ave isolated to remove large tree at 475 Bloor. | Ottawa | Scheduled Outage
20543 | 2012 | 5 | 20 | 0.20972 |  | 178 | 3 | 1 | Lisgar | 13.2kV | TC3TL | The lisgar TL15 CB breaker tripped due to cable fault at MH29 on the TC3TL circuit causing the generation to trip at Chaudiere GS. On call crew called in to make repairs | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
19727 | 2011 | 12 | 16 | 0.51528 |  | 6 | 0 | 1 | Chaudiere | 13.2kV | TCT2 | While performing switching to transfer 4G1 & TC2GS Gens to TC3TL supply @ Chaudiere, when parallel was made between TC3TL and TC1TL the TCT2 breaker tripped knocking TC4G2 generator offline. | Ottawa | Human Element | Incorrect Protection Settings
17469 | 2011 | 1 | 6 | 0.35764 |  | 75 | 12 | 10 | Lincoln Heights | 13.2kV | TD01 | Transformer #X35464 located at 526 Fraser Ave opened by crew due to putting up a new service | Ottawa | Scheduled Outage | Construction
9919 | 2007 | 1 | 12 | 0.70833 |  | 15 | 2 | 8 | Linclon Heights | 13.2kV | TD01 | Isolated transformer 55C2D-0725 at 684 Gainsborough Ave and replaced hot line clamp | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
19834 | 2012 | 1 | 15 | 0.16319 |  | 18 | 3 | 10 | Lincoln Heights | 13.2kV | TD01 | Crews interrupted power to transformer behind 446 Fraser to perform emergency disconnect of service to 446 Fraser. Transformer was re-energized after an 18 minute outage. | Ottawa | Scheduled Outage | Emergency Services Request
19897 | 2012 | 1 | 26 | 0.38056 |  | 51 | 8 | 9 | Lincoln Heights | 13.2kV | TD01 | X32577 at 552 Courtenay was isolated to allow crews to install new service | Ottawa | Scheduled Outage | Construction
7895 | 2006 | 2 | 5 | 0.79236 |  | 170 | 14 | 5 | Lincoln | 13.2kV | TD01 | A combination of Winds and excesive trees, opened transformer at 460 Westminster. Tree trimming will have to be done in future. Crew cleared, refused and closed. | Ottawa | Tree Contacts | Inadequate Trimming
19983 | 2012 | 2 | 7 | 0.72708 |  | 44 | 7 | 9 | Lincoln | 13.2kV | TD01 | Transformer #X35469 located at 683 Windermere opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
19990 | 2012 | 2 | 8 | 0.34375 |  | 32 | 4 | 7 | Lincoln | 13.2kV | TD01 | Transformer X34270 at 1856 Carling Ave isolated to allow for repairs - voltage issue | Ottawa | Scheduled Outage | Repair
20013 | 2012 | 2 | 14 | 0.56042 |  | 78 | 13 | 10 | Lincoln | 13.2kV | TD01 | Replaced blown fuse feeding transformer X35314 at 595 Wavell Ave due to squirrel contact | Ottawa | Foreign Interference | Animal
12059 | 2008 | 2 | 18 | 0.73889 |  | 41 | 4 | 6 | Lincoln Heights | 13.2kV | TD01 | Replaced broken fuse to transformer 55C2D-0734 at 611 WINDERMERE AVE | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4820 | 2004 | 2 | 24 | 0.62986 |  | 53 | 9 | 10 | lincoln heights | 13.2kV | TD01 | Cut out broken on transformer #594. Cut out replaced power restored. 10 Customers affected in power outage at 565 Brierwood AV. | Ottawa | Defective Equipment
6237 | 2005 | 2 | 26 | 0.46528 |  | 100 | 17 | 10 | TD | 13.2kV | TD01 | A squirrell caused the cut-out to blow at an O/H transformer at 680 Westminster. | Ottawa | Foreign Interference | Animal
17648 | 2011 | 2 | 27 | 0.55833 |  | 81 | 8 | 6 | Lincoln Heights | 13.2kV | TD01 | Transformer X 34270 at 815 Maitland refused due to animal contact - squirrel | Ottawa | Foreign Interference | Animal
17650 | 2011 | 2 | 28 | 0.39931 |  | 5 | 112 | 1343 | Lincoln Heights | 13.2kV | TD01 | TD01 Breaker Openeed to allow crews to install jumper at S-195 RED Phase. Located at Byron & Courtenay, 1343 customers affected for 5 minutes. Lincoln Heights (TD01) Crews repaired switch & removed jumper using Live Line Techniques | Ottawa | Defective Equipment
17653 | 2011 | 2 | 28 | 0.62708 |  | 13 | 0 | 1 | Lincoln Heights | 13.2kV | TD01 | Transformer X32105 at 607 Richmond Rd isolated to disconnect streetlight pole caused by MVA | Ottawa | Foreign Interference | Vehicle
4842 | 2004 | 3 | 1 | 0.46528 |  | 35 | 6 | 10 | Lincoln | 13.2kV | TD01 | Transformer at 597 Fraser interrupted to repair secondary service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17663 | 2011 | 3 | 3 | 0.4375 |  | 30 | 4 | 8 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32587 located at 657 Rowanwood isolated by crew for an upgrade | Ottawa | Scheduled Outage | Construction
17667 | 2011 | 3 | 4 | 0.61111 |  | 37 | 5 | 8 | Lincoln Heights | 13.2kV | TD01 | Crew isolated X32515 at 651 Wavel to install a new service, 8 customers affected on Wavel, Gainsborough and Dovercourt | Ottawa | Scheduled Outage | Construction
7999 | 2006 | 3 | 9 | 0.66736 |  | 54 | 5 | 6 | Lincoln | 13.2kV | TD01 | Switch to transformer 55C2B-0149 at 630 Crossfield Ave opened due to a broken tree branch | Ottawa | Tree Contacts | Tree Limb Fallen
8021 | 2006 | 3 | 14 | 0.33194 |  | 18 | 278 | 926 | Lincoln | 13.2kV | TD01 | Recloser blocked, closed by SCADA after clhold offs cleared, police and fire contacted. To be patrolled | Ottawa | Unknown/Other | No Apparent Cause
12172 | 2008 | 3 | 25 | 0.54514 |  | 85 | 34 | 24 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32513 & X35314 at 609 Wavell etc isolated due to cutout needed to be replaced due to animal contact (squirrel) | Ottawa | Foreign Interference | Animal
3302 | 2003 | 3 | 26 | 0.27778 |  | 80 | 21 | 16 | Lincoln | 13.2kV | TD01 | Local opened up feeding two transformers on Wavell and Gainsboro. | Ottawa | Foreign Interference | Animal
12191 | 2008 | 3 | 28 | 0.51389 |  | 60 | 9 | 9 | Lincoln Heights | 13.2kV | TD01 | Isolated transformer X32578 at 563 Redwood Ave to repair services | Ottawa | Scheduled Outage | Repair
8126 | 2006 | 4 | 10 | 0.42014 |  | 5 | 0 | 5 | Licoln Heights | 13.2kV | TD01 | Isolated transformer at 675 Westminster to remove overhead service to house that is being demolished | Ottawa | Scheduled Outage | Emergency Services Request
6415 | 2005 | 4 | 15 | 0.375 |  | 320 | 48 | 9 | Lincoln Heights | 13.2kV | TD01 | IsolatedTransformer at 42 Gould to transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
10286 | 2007 | 4 | 19 | 0.58681 |  | 160 | 404 | 926 | Lincoln Heights | 13.2kV | TD01 | A truck made contact with circuit TD01 and had to be opened from SCADA. | Ottawa | Foreign Interference | Vehicle
6457 | 2005 | 4 | 25 | 0.35417 |  | 46 | 7 | 9 | Lincoln Heights | 13.2kV | TD01 | Switch feeding transformer #925-15 at 480 Denbury Ave opened due to animal contact (Squirrel) refused the switch-restored power | Ottawa | Foreign Interference | Animal
6463 | 2005 | 4 | 26 | 0.41667 |  | 12 | 2 | 12 | Lincoln | 13.2kV | TD01 | Transformer location #A1704-7 isolated at 688 Denbury for removal of a service for demolition | Ottawa | Scheduled Outage | Construction
12358 | 2008 | 4 | 29 | 0.36111 |  | 15 | 2 | 9 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32578 located at 571 Redwood isolated due to relocating plant | Ottawa | Scheduled Outage | Preventive Maintenance
18067 | 2011 | 4 | 30 | 0.54028 |  | 62 | 19 | 18 | Lincoln | 12/7.2kV | TD01 | Switch S12497 was isolated to allow crew to repair radial line and remove trees. 18 customers were affected for 62 minutes. Lincoln (TD01) ID# 18067 | Ottawa | Adverse Weather | Wind
18074 | 2011 | 4 | 30 | 0.92778 |  | 192 | 58 | 18 | LINCOLN | 4.16kV | TD01 | Tree fell on secondary service causing S12497 to blow. S12497 refused and power restored. | Ottawa | Tree Contacts
18079 | 2011 | 5 | 1 | 0.79653 |  | 25 | 19 | 46 | Lincoln | 13.2kV | TD01 | Tree fell on Primary causing S20585. Tree removed, and S20585 refused. | Ottawa | Tree Contacts
10417 | 2007 | 5 | 14 | 0.53958 |  | 173 | 29 | 10 | Lincoln Heights | 13.2kV | TD01 | Fuse to transformer X35459 at 629 Mansfield was found blown due to tree limbs grown around open wire buss Trimmed trees and restored power | Ottawa | Tree Contacts | Inadequate Trimming
8327 | 2006 | 5 | 20 | 0.29167 |  | 75 | 5 | 4 | Lincoln | 13.2kV | TD01 | Fuse to Transformer 55C2D-0333 at 680 Dovercourt Ave opened due to tree branch contact | Ottawa | Tree Contacts | Inadequate Trimming
8329 | 2006 | 5 | 20 | 0.41319 |  | 63 | 10 | 10 | Lincoln | 13.2kV | TD01 | Fuse to transformer 55C2B-0441 at 852 Byron Ave opened due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
8333 | 2006 | 5 | 20 | 0.77917 |  | 120 | 20 | 10 | Lincoln | 13.2kV | TD01 | Fuse to transformer 55C2B-0441 at 852 Byron Ave opened, suspect either tree contact or wind had blown neutal conection into open wire bus. Some branches cleared and neutral wire shortened. | Ottawa | Tree Contacts | Inadequate Trimming
3460 | 2003 | 5 | 21 | 0.43125 |  | 44 | 7 | 10 | Lincoln Hts |  | TD01 | A squirrel caused the fuse to blow at a transformer on Dovercourt. | Ottawa | Foreign Interference | Animal
3478 | 2003 | 5 | 21 | 0.50694 |  | 65 | 3 | 3 | Lincoln Heights | 12/7.2kV | TD01 | Planned outage to transformer 148 at 2130 Wayne Ave to replace customer triplex. | Ottawa | Scheduled Outage
6584 | 2005 | 5 | 21 | 0.28611 |  | 61 | 8 | 8 | Lincoln Heights | 13.2kV | TD01 | Transformer switch at 604 Westminster St was found blown due to tree branch making contact with the primary bushing | Ottawa | Tree Contacts | Inadequate Trimming
10434 | 2007 | 5 | 21 | 0.39097 |  | 46 | 8 | 10 | Lincoln Heights | 13.2kV | TD01 | Transformer fuse to 55C2D-0558 at 587 Dovercourt was found blown no apparent cause | Ottawa | Unknown/Other | No Apparent Cause
16119 | 2010 | 5 | 21 | 0.45833 |  | 78 | 6 | 5 | Lincoln Heights | 13.2kV | TD01 | At 11:00 trans at 600 Windermere was isolated in order to relocate a seconday service | Ottawa | Scheduled Outage | Preventive Maintenance
10443 | 2007 | 5 | 23 | 0.39583 |  | 54 | 10 | 11 | Lincoln Heights | 13.2kV | TD01 | At 09:30 trans at 680 Dovercourt was isolated in order to make repairs to services and guy wires | Ottawa | Scheduled Outage | Repair
10444 | 2007 | 5 | 23 | 0.39583 |  | 70 | 12 | 10 | Lincoln Fields | 13.2kV | TD01 | At 09:30 trans at 656 Wavell Ave was isolated in order to make repairs to sec services | Ottawa | Scheduled Outage | Repair
16131 | 2010 | 5 | 25 | 0.2875 |  | 81 | 12 | 9 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32410 located at 2121 Rice Ave opened up, crew could not find cause. | Ottawa | Unknown/Other | No Apparent Cause
20599 | 2012 | 5 | 25 | 0.79097 |  | 271 | 122 | 27 | Lincoln Heights | 13.2kV | TD01 | Tree contact cause S28235 @ 732 Byron to open. | Ottawa | Adverse Weather | Wind
8389 | 2006 | 5 | 31 | 0.49583 |  | 65 | 8 | 7 | Lincoln | 13.2kV | TD01 | Fuse found blown on switch to transformer OTT3168 at 685 Hillcrest Ave due to a squirrel contact | Ottawa | Foreign Interference | Animal
16170 | 2010 | 6 | 1 | 0.22569 |  | 55 | 8 | 9 | Lincoln Heights | 13.2kV | TD01 | Plant contact caused transformer X35465 at 504 Fraser to open. | Ottawa | Tree Contacts | Inadequate Trimming
20688 | 2012 | 6 | 3 | 0.5625 |  | 57 | 4 | 4 | Lincoln | 13.2kV | TD01 | Transformer #X32279 located at 455 Westminster Ave opened up due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
20692 | 2012 | 6 | 4 | 0.56389 |  | 99 | 130 | 79 | Lincoln | 13.2kV | TD01 | Hydro Ottawa crews isolated a radial section of the TD01 circuit to allow forestry crews to clear a tree limb that had fallen onto the conductor. | Ottawa | Tree Contacts | Tree Limb Fallen
10537 | 2007 | 6 | 5 | 0.80208 |  | 48 | 5 | 6 | Lincoln | 13.2kV | TD01 | Transformer #55C2D-0300 located at 669 Denbury Ave isolated due to tree interference | Ottawa | Tree Contacts | Inadequate Trimming
6674 | 2005 | 6 | 7 | 0.38611 |  | 44 | 7 | 10 | Lincoln | 13.2kV | TD01 | Replaced transformer fuse at 595 Fraser avenue caused by tree outage | Ottawa | Tree Contacts | Inadequate Trimming
6678 | 2005 | 6 | 7 | 0.725 |  | 41 | 5 | 8 | Lincoln | 13.2kV | TD01 | Transformer at 508 Windermere isolated due to animal interference (squirrel) | Ottawa | Foreign Interference | Animal
12578 | 2008 | 6 | 8 | 0.64653 |  | 74 | 12 | 10 | Lincoln Heights | 13.2kV | TD01 | Transformer #OTT5305 located at 851 Maitland Ave isolated due to broken cutout. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3546 | 2003 | 6 | 9 | 0.76319 |  | 56 | 6 | 6 | Lincoln | 13.2kV | TD01 | The transformer fuse at 2208 Deschenes blew due to a squirrel. | Ottawa | Foreign Interference | Animal
16237 | 2010 | 6 | 9 | 0.69792 |  | 53 | 7 | 8 | Linclon Heights | 13.2kV | TD01 | Replaced blown fuse for transformer X35465 at 505 Mansfield Ave (Caused by tree contact) | Ottawa | Tree Contacts | Inadequate Trimming
16238 | 2010 | 6 | 9 | 0.8 |  | 53 | 6 | 7 | Lincoln Heights | 13.2kV | TD01 | Replaced blown fuse for transformer X32510 at 513 Gainsborough Ave (Squirrel Contact) | Ottawa | Foreign Interference | Animal
5277 | 2004 | 6 | 10 | 0.53889 |  | 44 | 7 | 10 | Lincolin | 13.2kV | TD01 | A squirrel made contact at transformer S5C2D-0295 at 597 Fraser. | Ottawa | Foreign Interference | Animal
16242 | 2010 | 6 | 10 | 0.42639 |  | 58 | 6 | 6 | LINCOLN HEIGHTS | 13.2kV | TD01 | Transformer X32192 at 669 Denbury Ave isolated to allow for tree trimming | Ottawa | Scheduled Outage | Preventive Maintenance
16246 | 2010 | 6 | 10 | 0.47917 |  | 45 | 3 | 4 | LINCOLN HTS | 13.2kV | TD01 | Transformer X32523 at 603 Gainsborough isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
20748 | 2012 | 6 | 12 | 0.425 |  | 78 | 13 | 10 | Lincoln | 13.2kV | TD01 | Transformer #X32282 located at 449 Mansfield Ave opened up due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
14529 | 2009 | 6 | 13 | 0.90694 |  | 20 | 2 | 6 | Lincoln | 13.2kV | TD01 | Raccon caused the transformer X32192 at 669 Denbury to open. | Ottawa | Foreign Interference | Animal
6715 | 2005 | 6 | 14 | 0.62917 |  | 106 | 14 | 8 | Lincoln Hights | 13.2kV | TD01 | Refused switch to transformer at 2011 BLACK FRIARS Rd outage caused by squirrel | Ottawa | Foreign Interference | Animal
18402 | 2011 | 6 | 14 | 0.35764 |  | 45 | 3 | 4 | Lincoln Heights | 13.2kV | TD01 | Transformer #X35317 located at 692 Dovercourt opened by crew for a change over | Ottawa | Scheduled Outage | Construction
14544 | 2009 | 6 | 16 | 0.43819 |  | 29 | 4 | 8 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32510 located at 513 Gainsborough isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
6754 | 2005 | 6 | 17 | 0.51944 |  | 47 | 7 | 9 | Lincoln | 13.2kV | TD01 | Transformer at 504 Fraser Ave isolated, cause was possibly a tree branch | Ottawa | Foreign Interference | Foreign Object
8500 | 2006 | 6 | 17 | 0.20556 |  | 74 | 12 | 10 | Lincoln | 13.2kV | TD01 | Tree contact caused transformer 55C2C-0496 on Keenan at Redwood to open. | Ottawa | Tree Contacts | Inadequate Trimming
8510 | 2006 | 6 | 18 | 0.72569 |  | 50 | 8 | 10 | Lincoln | 13.2kV | TD01 | 24/7 reports tree contact caused fuse on transformer at 529 Rowanwood to open. Tree trimming complete and transformer fuse replaced. All power restored to customers. | Ottawa | Tree Contacts | Inadequate Trimming
5338 | 2004 | 6 | 19 | 0.69653 |  | 161 | 32 | 12 | Lincoln | 4.16kV | TD01 | Transformer at 597 Fraser Ave opened due to high wind causing tree branches to contact sercondary. Refused and power restored. | Ottawa | Adverse Weather | Wind
10681 | 2007 | 6 | 20 | 0.61736 |  | 91 | 14 | 9 | Lincoln Heights | 13.2kV | TD01 | Transformer #55C2D-0760 located at 601 Dovercourt isolated due to animal contact | Ottawa | Foreign Interference | Animal
8573 | 2006 | 6 | 22 | 0.60764 |  | 51 | 12 | 14 | Lincoln | 13.2kV | TD01 | A Blue phase run off between Wavell & Courtney N. of Dovercourt was opened to remove a large tree limb from the primary wire. | Ottawa | Tree Contacts | Tree Limb Fallen
8576 | 2006 | 6 | 22 | 0.50486 |  | 411 | 688 | 926 | Lincoln | 13.2kV | TD01 | Tree limbs brought down a primary conductor between Westminster & Windermere n. of Keenan ave. The cct A/R allowing R & W phase SMD20 fuses on Byron @ Gainsborough to clear. The cct was opened to allow the 24/7 crew to cut clear corner taps at Byron & Westminster. R & W phase SMD20 fuses on Byron @ Gainsborough were closed leaving only the isolated section off. Tree limbs were cleared & conductor repaired, R W& B phase SMD20 fuses on Byron @ Gainsborough were opened to replace the taps at Byron & Westminster, the cct was opened to allow the O/H crew to close R W& B phase SMD20 fuses on Byron @ Gainsborough. | Ottawa | Tree Contacts | Inadequate Trimming
14595 | 2009 | 6 | 22 | 0.4375 |  | 70 | 12 | 10 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32182 located at 597 Fraser isolated due to relocating service | Ottawa | Scheduled Outage | Preventive Maintenance
14596 | 2009 | 6 | 22 | 0.4375 |  | 60 | 10 | 10 | LINCOLN | 13.2kV | TD01 | Transformer X32182 at 597 Fraser isolated to relocate service | Ottawa | Scheduled Outage | Repair
16314 | 2010 | 6 | 25 | 0.54167 |  | 41 | 3 | 4 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32350 located at 2205 Deschenes St opened by crew for a new service | Ottawa | Scheduled Outage | Construction
20865 | 2012 | 6 | 25 | 0.30347 |  | 123 | 33 | 16 | Lincoln | 13.2kV | TD01 | replaced blown fuse feeding ttransformer X32419 at 86 Pooler Ave (Squirrel contact) | Ottawa | Foreign Interference | Animal
18552 | 2011 | 6 | 28 | 0.83889 |  | 135 | 22 | 10 | Lincoln Heights | 13.2kV | TD01 | Transformer #X35466 located at 489 Mansfield opened up due to lightning. | Ottawa | Adverse Weather | Lightning
20903 | 2012 | 6 | 29 | 0.61458 |  | 105 | 16 | 9 | Lincoln Heights | 13.2kV | TD01 | Transformer X35469 at 683 Windermere Ave. refused due to animal contact - squirrell | Ottawa | Foreign Interference | Animal
8650 | 2006 | 7 | 2 | 0.75903 |  | 155 | 36 | 14 | Lincoln Heights | 13.2kV | TD01 | Tree in wires | Ottawa | Tree Contacts | Inadequate Trimming
10775 | 2007 | 7 | 2 | 0.81111 |  | 70 | 9 | 8 | Lincoln Heights | 13.2kV | TD01 | Transformer #55C2D-0734 located at 604 Westminster Ave isolated due to animal contact | Ottawa | Foreign Interference | Animal
12793 | 2008 | 7 | 6 | 0.33264 |  | 91 | 15 | 10 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32178 located at 464 Denbury Ave isolated due to squirrel contact, crew installed animal guard on transformer | Ottawa | Foreign Interference | Animal
5478 | 2004 | 7 | 12 | 0.775 |  | 98 | 15 | 9 | Lincoln Hts | 13.2kV | TD01 | Fuse blew at transformer 55C2C-0505 at 635 Rowanwood due to lightning storm. Crew refused to restore 9 customers on Courtenay, Rowanwood & Dovercourt. | Ottawa | Adverse Weather | Lightning
8707 | 2006 | 7 | 12 | 0.90972 |  | 20 | 3 | 9 | Lincoln Heigths | 13.2kV | TD01 | Isolalated transformer 55C2B-0461 at 491 Westminster Ave to replace hot line clamp | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14773 | 2009 | 7 | 17 | 0.73333 |  | 134 | 7 | 3 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32403 located at 81 Aylen isolated due to animal contact. | Ottawa | Foreign Interference | Animal
3764 | 2003 | 7 | 19 | 0.58264 |  | 96 | 18 | 11 | Lincoln Hts | 13.2kV | TD01 | The transformer fuse blew in the rear of 568 Denbury affecting 11 customers on Denbury, Fraser & Keenan. 24/7 crew cleared some tree limbs and refused. | Ottawa | Tree Contacts | Inadequate Trimming
18774 | 2011 | 7 | 19 | 0.69792 |  | 5 | 113 | 1358 | Lincoln heights | 13.2kV | TD01 | TD01 circuit was opened to allow crews to reconnect line taps at X40738. | Ottawa | Tree Contacts | Tree Fallen
5563 | 2004 | 7 | 24 | 0.28403 |  | 65 | 11 | 10 | Lincoln | 12/7.2kV | TD01 | Transformer fuse blew at 683 Windermere due to squirrel contact. | Ottawa | Foreign Interference | Animal
10956 | 2007 | 7 | 26 | 0.76597 |  | 101 | 24 | 40 | Linclon Heights | 13.2kV | TD01 | A blown cable bet KT627 and PPH switches at pole 20 at 655 Richmond Rd. While fault finding the R phase fuse flashed across causing the W phase at pole 20 to blow and the S24350 RW phase down stream to also blow. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3790 | 2003 | 7 | 27 | 0.86111 |  | 9 | 0 | 2 | Lincoln | 13.2kV | TD01 | Overhead transformer interrupted to replace a defective line clamp. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7043 | 2005 | 7 | 30 | 0.77431 |  | 53 | 7 | 8 | Lincoln | 13.2kV | TD01 | Overhead transformer interrupted by a squirrel. Transformer refused successfully. 8 customers on Westminster & Windermere were affected. | Ottawa | Foreign Interference | Animal
10970 | 2007 | 7 | 30 | 0.43403 |  | 275 | 9 | 2 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32416 located at 10 Cleary Ave isolated due to pole change | Ottawa | Scheduled Outage | Construction
8877 | 2006 | 7 | 31 | 0.44792 |  | 93 | 8 | 5 | Lincoln Heights | 13.2kV | TD01 | Isolated transformer 55C2D-0769 at 673 Westminster to install new services | Ottawa | Scheduled Outage | Construction
8905 | 2006 | 8 | 2 | 0.51875 |  | 48 | 8 | 10 | Lincoln Heights | 13.2kV | TD01 | Switch to Transformer 55C2D-0558 at 577 Dovercourt Ave opened due to tree branch contact refused the switch and restored power | Ottawa | Tree Contacts | Inadequate Trimming
12996 | 2008 | 8 | 3 | 0.3875 |  | 31 | 4 | 8 | TD01 | 13.2kV | TD01 | Transformer #X35462 located at 562 Fraser isolated due to squirrel contact. | Ottawa | Foreign Interference | Animal
7071 | 2005 | 8 | 5 | 0.34028 |  | 10 | 1 | 8 | Lincoln Heights | 13.2kV | TD01 | Power outage to transformer at the rear of 684 Gainsborough Ave to disconnect service to 680 Gainsborough | Ottawa | Tree Contacts | Tree Fallen
3849 | 2003 | 8 | 6 | 0.26528 |  | 218 | 18 | 5 | Lincoln | 13.2kV | TD01 | Blown bushing on transformer caused by lightning strike caused interruption to 5 customers on Dovercourt, Windermiere,and Westmintster. | Ottawa | Adverse Weather | Lightning
7078 | 2005 | 8 | 6 | 0.28681 |  | 127 | 19 | 9 | Lincoln | 13.2kV | TD01 | Transformer isolated at 493 Mansfield due to animal interference (squirrel) | Ottawa | Foreign Interference | Animal
7102 | 2005 | 8 | 10 | 0.65208 |  | 110 | 1698 | 926 | Lincoln | 13.2kV | TD01 | one half of circuit picked up blown SMU 20 fuse @ Keenan & Courtney | Ottawa | Adverse Weather | Lightning
14930 | 2009 | 8 | 11 | 0.37639 |  | 61 | 6 | 6 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32350 located at 2216 Deschenes St isolated due to animal contact | Ottawa | Foreign Interference | Animal
14936 | 2009 | 8 | 12 | 0.46806 |  | 76 | 4 | 3 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32403 located at 2129 Saunders Ave isolated due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
8971 | 2006 | 8 | 15 | 0.44444 |  | 55 | 7 | 8 | Lincoln Heights | 4.16kV | TD01 | Trans at 580 Rowanwood isolated in order top install new service | Ottawa | Scheduled Outage | Preventive Maintenance
11085 | 2007 | 8 | 16 | 0.84931 |  | 117 | 16 | 8 | Lincoln Heights | 13.2kV | TD01 | Transformer #55C2B-0199 located at 509 Gainsborough isolated due to animal contact | Ottawa | Foreign Interference | Animal
9006 | 2006 | 8 | 20 | 0.85139 |  | 9 | 0 | 3 | Lincoln Heights | 13.2kV | TD01 | KT623 was opened to allow crew to disconnect defective underground from pedestal to 685 Richmond. Temporary jumper installed from 683 Richmond to 685. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9010 | 2006 | 8 | 21 | 0.44444 |  | 20 | 1 | 3 | Lincoln Heights | 13.2kV | TD01 | Transformer #KT623 located at 685 Richmond isolated to find out what the problem was from last night (bad U/G) | Ottawa | Scheduled Outage | Repair
14982 | 2009 | 8 | 21 | 0.26875 |  | 111 | 11 | 6 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32192 located at 669 Denbury Ave isolated due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
18997 | 2011 | 8 | 22 | 0.58819 |  | 93 | 40 | 33 | Lincoln | 13.2kV | TD01 | X32581 was opened to replace triplex at 854 Byron. TD01 B phase conductor from S11338 at Byron & Courtney came down when crew removed defective hot line clamp at X32581. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9032 | 2006 | 8 | 23 | 0.51181 |  | 83 | 11 | 8 | Lincoln Heights |  | TD01 | Transformer #55C2B-0199 located at the rear of 509 Gainsborough isolated due to squirrel contact | Ottawa | Scheduled Outage | Preventive Maintenance
19018 | 2011 | 8 | 26 | 0.41667 |  | 80 | 13 | 10 | Lincoln Heights | 13.2kV | TD01 | Isolated transformer X35314 at 595 Wavell Ave for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
13169 | 2008 | 8 | 29 | 0.46806 |  | 76 | 3 | 2 | Lincoln Heights | 13.2kV | TD01 | Refused switch to transformer X32416 at 793 Richmond Rd | Ottawa | Unknown/Other | No Apparent Cause
7256 | 2005 | 8 | 31 | 0.78333 |  | 41 | 5 | 7 | Lincoln | 13.2kV | TD01 | Transformer #OTT1162 located at 1850 Carling Ave isolated due to tree interference | Ottawa | Tree Contacts | Inadequate Trimming
5761 | 2004 | 9 | 2 | 0.064583 |  | 47 | 9 | 11 | Lincoln | 13.2kV | TD01 | Re-fused O/H transformer at the rear of 635 Mansfield. Suspect contact by racoon. | Ottawa | Foreign Interference | Animal
7274 | 2005 | 9 | 2 | 0.60069 |  | 73 | 1127 | 926 | Lincoln | 13.2kV | TD01 | Circuit tripped during windstorm, circuit picked up after patrol revealed no problems. | Ottawa | Adverse Weather | Wind
4017 | 2003 | 9 | 5 | 0.46944 |  | 11 | 170 | 926 | Lincoln | 13.2kV | TD01 | Circuit was under a hold off for ongoing live line work on the circuit. While lengthening leads to a cut out, a lead pulled out of the cutout & into the live TD01, no personnel injuries occurred. The circuit was re-energized after men and equipment were confirmed clear of the circuit and that no damage ocurred. | Ottawa | Human Element | Incorrect Installation
15061 | 2009 | 9 | 7 | 0.3125 |  | 330 | 66 | 12 | Lincoln | 13.2kV | TD01 | At 13:00 hrs the trans at 662 Windrmere was renergized after being replaced for failure | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19108 | 2011 | 9 | 7 | 0.375 |  | 190 | 32 | 10 | Lincoln Heights | 13.2kV | TD01 | Transformer #X35314 located at 595 Wavell Ave opened by crew due to transferring plant to new poles | Ottawa | Scheduled Outage
19109 | 2011 | 9 | 7 | 0.375 |  | 190 | 25 | 8 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32513 located at 605 Wavell Ave opened by crew due to transferring plant to new poles | Ottawa | Scheduled Outage
19121 | 2011 | 9 | 8 | 0.69792 |  | 35 | 6 | 10 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32586 located at 684 Courtenay Ave opened due to bird contact. Crew refused, power restored. | Ottawa | Foreign Interference | Bird
9202 | 2006 | 9 | 12 | 0.35417 |  | 225 | 30 | 8 | Lincoln Heights | 4.16kV | TD01 | At 08:30 trans at 433 Fraser Ave was isolated in order to trim trees from the overhead lines | Ottawa | Scheduled Outage | Preventive Maintenance
19139 | 2011 | 9 | 12 | 0.45486 |  | 45 | 6 | 8 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32520 located at 629 Gainsborough opened by crew for a service upgrade | Ottawa | Scheduled Outage | Construction
13256 | 2008 | 9 | 18 | 0.44792 |  | 35 | 5 | 9 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32282 located at 445 Mansfield Ave isolated to replace O/H service | Ottawa | Scheduled Outage | Preventive Maintenance
4100 | 2003 | 9 | 19 | 0.68819 |  | 144 | 22 | 9 | Lincoln | 4.16kV | TD01 | Transformer 55C2D-0760, at 630 Mansfield in Ottawa, had to be isolated to allow for the repair of secondary wired downed by a fallen tree. Wires were repaired and power was restored. | Ottawa | Tree Contacts | Tree Fallen
9249 | 2006 | 9 | 19 | 0.55208 |  | 47 | 5 | 7 | Lincoln Heights | 13.2kV | TD01 | Isolated transformer 55C2B-0456 at 449 Westminster Ave to replace service | Ottawa | Scheduled Outage | Repair
11331 | 2007 | 9 | 19 | 0.076389 |  | 42 | 8 | 11 | Lincoln Heights | 12/7.2kV | TD01 | Transformer at 559 Courtenay opened due to raccon contact, crew re-fused transformer and restored power. | Ottawa | Foreign Interference | Animal
15137 | 2009 | 9 | 21 | 0.48611 |  | 40 | 5 | 8 | Lincoln Heights | 13.2kV | TD01 | Isolated transformer X35468 at 680 Mansfield Ave to replace defective service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19222 | 2011 | 9 | 21 | 0.35972 |  | 207 | 21 | 6 | Lincoln Heights | 13.2kV | TD01 | 4kV transformer X32584 at the rear of 595 Wavell was isolated to allow crews to re-arrange plant | Ottawa | Scheduled Outage | Preventive Maintenance
9277 | 2006 | 9 | 22 | 0.37083 |  | 41 | 9 | 13 | Lincoln Heights | 13.2kV | TD01 | Transformer #55C2A-0079 located at 2202 Deschenes isolated due to bird contact | Ottawa | Foreign Interference | Bird
4135 | 2003 | 9 | 23 | 0.39583 |  | 15 | 1 | 4 | Lincoln | 13.2kV | TD01 | Transformer at 573 Westminster was opened to allow Bell Canada to perform pole testing | Ottawa | Scheduled Outage | Preventive Maintenance
4136 | 2003 | 9 | 23 | 0.41667 |  | 15 | 1 | 4 | Licoln | 13.2kV | TD01 | Transformer at 577 Windermere was opened to allow Bell Canada to perform pole testing | Ottawa | Scheduled Outage
19252 | 2011 | 9 | 25 | 0.49583 |  | 41 | 5 | 8 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32500 located at 607 Windermere opened up due to squirrel interference | Ottawa | Foreign Interference | Animal
13293 | 2008 | 9 | 26 | 0.46528 |  | 103 | 17 | 10 | Lincoln |  | TD01 | Transformer X35471 (656) at 656 Mansfield Ave isolated to allow for repairs | Ottawa | Scheduled Outage | Repair
9352 | 2006 | 9 | 30 | 0.48472 |  | 212 | 14 | 4 | Lincoln | 4.16kV | TD01 | Transformer #55C2D-0333 located at 692 Dovercourt isolated due to the pole was hit with a fibre packing tool | Ottawa | Foreign Interference | Foreign Object
19304 | 2011 | 10 | 2 | 0.31528 |  | 28 | 3 | 7 | Lincoln Heights | 13.2kV | TD01 | Replaced blown fuse feeding transformer X38557, at 667 WINDERMERE AVE (squirrel) | Ottawa | Foreign Interference | Animal
4220 | 2003 | 10 | 7 | 0.61111 |  | 305 | 46 | 9 | Lincoln Heights | 13.2kV | TD01 | Defective transformer, 55C2D-0405, in rear of 614 Windemere changed. 9 customers on Windemere & Gainsborough affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13339 | 2008 | 10 | 8 | 0.46111 |  | 86 | 11 | 8 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32094 located at 567 Fraser Ave isolated due to animal contact | Ottawa | Foreign Interference | Animal
11478 | 2007 | 10 | 9 | 0.023611 |  | 44 | 2 | 3 | Lincoln Heights | 13.2kV | TD01 | A burnt hot line clamp had to be change at 2122 SAUNDERS AVE OTTAWA | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15243 | 2009 | 10 | 10 | 0.40278 |  | 19 | 2 | 6 | LINCOLN HTS | 13.2kV | TD01 | Transformer X32418 at 2206 Elder Street isolated to allow for repairs to service connection | Ottawa | Scheduled Outage | Repair
4258 | 2003 | 10 | 15 | 0.055556 |  | 13 | 0 | 1 | Lincoln hieghts | 13.2kV | TD01 | Transformer # 6506148 at 809 Wavell opened to repair arcing hot line clamp. | Ottawa | Adverse Weather | Rain
11530 | 2007 | 10 | 16 | 0.54514 |  | 30 | 5 | 10 | Lincoln | 13.2kV | TD01 | Transformer #55C2A-0094 located at 2161 Rice isolated due to defective cut out change | Ottawa | Scheduled Outage | Repair
13397 | 2008 | 10 | 21 | 0.11111 |  | 58 | 10 | 10 | Lincoln | 13.2kV | TD01 | Overhead tranformer at 598 Rowanwood Ave isolated to replace triplex to 597 Redwood that had burnt off. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15287 | 2009 | 10 | 21 | 0.64167 |  | 56 | 12 | 13 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32504 located at 509 Windermere isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
9492 | 2006 | 10 | 23 | 0.46181 |  | 110 | 16 | 9 | Lincoln Heights | 13.2kV | TD01 | Isolated transformer 55C2B-0322 at 449 Mansfield Ave to relocate hydro plant | Ottawa | Scheduled Outage | Construction
15302 | 2009 | 10 | 26 | 0.38542 |  | 45 | 8 | 11 | LINCOLN HEIGHTS | 13.2kV | TD01 | Trnasformer X35466 at 492 Fraser Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
7523 | 2005 | 10 | 27 | 0.39583 |  | 230 | 27 | 7 | Lincoln Heights | 13.2kV | TD01 | Isolated Transformer at 2131 Saunders Ave to relocate same to new pole | Ottawa | Scheduled Outage | Construction
9530 | 2006 | 10 | 28 | 0.83264 |  | 514 | 238 | 90 | Lincoln Heights | 13.2kV | TD01 | The top of a riser pole broke supplying VT493 at 20 Cleary, causing 2 fuses to blow at Byron and Woodroffe. Suspected defective switches on pole caused fire, and damaged red phase riser cable. Section isolated for repairs, and top of pole cut off and circuitry moved down on existing pole. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11613 | 2007 | 10 | 28 | 0.1125 |  | 66 | 12 | 11 | Lincoln | 13.2kV | TD01 | Crew closed cutout to transformer at 884 Byron that fell open for no apparent reason. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11638 | 2007 | 11 | 1 | 0.050694 |  | 67 | 12 | 11 | Lincoln | 13.2kV | TD01 | High winds, caused tree branches to blow transformer fuse in the rear of 571 Fraser Ave. Tree Branches trimmed, transformer refused and power restored. | Ottawa | Tree Contacts
4374 | 2003 | 11 | 3 | 0.61111 |  | 40 | 8 | 12 | Lincoln | 13.2kV | TD01 | Transformer KT0623, at 9-655 Richmond Road in Ottawa, was isolated to allow for the repair of a meter base at 12-655 Richmond Road. ID#4373 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4390 | 2003 | 11 | 4 | 0.43542 |  | 43 | 8 | 11 | Lincoln | 13.2kV | TD01 | Transformer 55C2D-0293 in Ottawa was inadvertently isolated due to a possible animal contact. ID#4390 | Ottawa | Foreign Interference | Animal
11669 | 2007 | 11 | 5 | 0.95139 |  | 74 | 10 | 8 | LINCOLN | 13.2kV | TD01 | Tree contact caused transformer fuse to open on transformer feeding customers on westminster and Windermere | Ottawa | Tree Contacts | Inadequate Trimming
4409 | 2003 | 11 | 7 | 0.57083 |  | 63 | 9 | 9 | Llincoln Heights | 13.2kV | TD01 | Transformer opened to replace open wire service. 9 Customers affected in this power outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15360 | 2009 | 11 | 7 | 0.5625 |  | 141 | 33 | 14 | Lincoln Heights | 13.2kV | TD01 | At 13:30 customers call to report they had no power. Crews replaced a broker cutout at transformer X34026 (842 Maitland) all power was restored at 15:51. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19550 | 2011 | 11 | 10 | 0.39236 |  | 58 | 9 | 9 | Lincoln Heights | 13.2kV | TD01 | Transformer #X39482 located at 633 Fraser Ave opened by crew for a new service | Ottawa | Scheduled Outage | Construction
7591 | 2005 | 11 | 11 | 0.45139 |  | 35 | 6 | 10 | Lincoln Heights | 13.2kV | TD01 | Transformer 55C2C-0148 at 684 Cortney was isolated to repair service | Ottawa | Scheduled Outage | Repair
19556 | 2011 | 11 | 11 | 0.41667 |  | 45 | 7 | 9 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32577 located at 555 Rowanwood Ave opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
7624 | 2005 | 11 | 16 | 0.43403 |  | 42 | 6 | 9 | Lincoln Heights | 13.2kV | TD01 | Tree branch caused fuse to blow on Transformer 55C20-0327 at 521 Mansfield crew trimmed tree refused switch restored power | Ottawa | Tree Contacts | Inadequate Trimming
7625 | 2005 | 11 | 16 | 0.43403 |  | 42 | 6 | 9 | Lincoln Heights | 13.2kV | TD01 | Switch to transformer 55C20-0327 at 521 Mansfield opened due to tree branch | Ottawa | Tree Contacts | Inadequate Trimming
9792 | 2006 | 12 | 3 | 0.88194 |  | 304 | 203 | 40 | Lincoln Heights | 13.2kV | TD01 | Fuse opened on south lateral from Dovercourt between Gainsborough & Wavell due to neutral conductor down on ground. Approx 5 xfrms interrupted. Repairs passed on to Oncall crews. | Ottawa | Adverse Weather | Ice Storm
19682 | 2011 | 12 | 5 | 0.325 |  | 67 | 11 | 10 | Lincoln Heights | 13.2kV | TD01 | Transformer #X32586 located at 601 Sherbourne Rd opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
4579 | 2003 | 12 | 9 | 0.44931 |  | 38 | 6 | 10 | Lincoln | 13.2kV | TD01 | A squirrel got into it with a transformer in the rear of 634 Gaineborough causing a blown fuse. ID#4579 | Ottawa | Foreign Interference | Animal
9839 | 2006 | 12 | 14 | 0.66528 |  | 82 | 12 | 9 | lincoln Heights | 13.2kV | TD01 | Transformer switch 55C20-0760 at 630 Mansfield Ave was found blown due to a squirrel contact refused the switch and restored power | Ottawa | Foreign Interference | Animal
11850 | 2007 | 12 | 14 | 0.67708 |  | 65 | 11 | 10 | Lincoln Heights | 13.2kV | TD01 | At 4:15pm customers in the area of Lockhart and Algonquin Avenue called in with no power calls. 24-7 reports squirel contact and refused secondary transformer, 10 customers affected for 65 min. ID#11850. | Ottawa | Foreign Interference | Animal
4633 | 2003 | 12 | 19 | 0.38681 |  | 93 | 6 | 4 | Lincoln | 12/7.2kV | TD01 | Transformer at 680 Dovercourt isolated for reconnection of a service. | Ottawa | Defective Equipment
6090 | 2004 | 12 | 23 | 0.25764 |  | 130 | 15 | 7 | Lincoln Heights | 13.2kV | TD01 | Replaced broken cutout on tansformer 55C2A-0044 at 2194 Elder St | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9883 | 2006 | 12 | 24 | 0.59097 |  | 69 | 12 | 10 | Lincoln | 13.2kV | TD01 | Outage @ 735 Fraser was caused by squirrell | Ottawa | Foreign Interference | Animal
13792 | 2008 | 12 | 25 | 0.066667 |  | 291 | 632 | 256 | LINCON HEIGHTS | 13.2kV | TD01 | Primary conductor fell down at 565 Windermere causing 1 fuse to blow at S24350. At 5:10 the other 2 phases of S24350 were opened for Oncall crew to make repairs. | Ottawa | Defective Equipment
11835 | 2007 | 12 | 12 | 0.48958 |  | 27 | 3 | 6 | Lincoln Heights | 13.2kV | TD010 | Isolated transformer 55C2B-0453 at 571 Wavell Ave for a service up-grade | Ottawa | Scheduled Outage | Preventive Maintenance
13842 | 2009 | 1 | 6 | 0.45208 |  | 129 | 19 | 9 | Lincoln Heights | 13.2kV | TD05 | Refused blown switch feeding transformer X33112 at 972 Gold Crers (Caused by squirrel contact) | Ottawa | Foreign Interference | Animal
3108 | 2003 | 1 | 12 | 0.4375 |  | 140 | 9 | 4 | Lincoln TS | 13.2kV | TD05 | 24/7 and Crew refused transformer at rear of 959 Arkell, opened by squirrel.Transformer feeding four addresses. | Ottawa | Foreign Interference | Animal
19850 | 2012 | 1 | 18 | 0.029167 |  | 117 | 883 | 453 | Lincoln Fields | 13.2kV | TD05 | A tree fell accoss TD05 line near S21518, crew removed tree limb and is re-fused S21518. Lincoln Heights (TD05) ID#19850 | Ottawa | Tree Contacts
3133 | 2003 | 1 | 21 | 0.875 |  | 205 | 27 | 8 | Lincoln TS | 13.2kV | TD05 | Leed came free from fused cutout feeding transformer at 2790 fallis. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11967 | 2008 | 1 | 21 | 0.69792 |  | 45 | 6 | 8 | Lincoln Heights | 13.2kV | TD05 | Isolated trtansformer at the rear of 2715 Kelly Ave to replace triplex service | Ottawa | Scheduled Outage | Emergency Services Request
19893 | 2012 | 1 | 25 | 0.45139 |  | 50 | 9 | 11 | Lincoln Heights | 13.2kV | TD05 | Transformer #X33281 located at 963 Alpine opened by crew for a service change | Ottawa | Scheduled Outage | Construction
3142 | 2003 | 1 | 26 | 0.46528 |  | 63 | 7 | 7 | Lincoln TS | 13.2kV | TD05 | Refused 50 kva transformer that was opened by squirrel. | Ottawa | Foreign Interference | Animal
7866 | 2006 | 1 | 28 | 0.4625 |  | 59 | 4 | 4 | Lincoln | 13.2kV | TD05 | Switch to transformer 55C3B-0024 at 2592 Chambers Ave opened due to bird contact | Ottawa | Foreign Interference | Bird
7894 | 2006 | 2 | 5 | 0.86042 |  | 53 | 6 | 7 | Lincoln | 13.2kV | TD05 | High winds probable cause of transformer at 814 Alpine opening. Crew refused and closed. | Ottawa | Adverse Weather | Wind
15716 | 2010 | 2 | 11 | 0.375 |  | 213 | 174 | 49 | Lincoln Fields | 13.2kV | TD05 | Circuit feeding Alpine Street was isolated by Hydro Crew for contractor to conduct tree trimming | Ottawa | Scheduled Outage | Preventive Maintenance
20032 | 2012 | 2 | 17 | 0.68681 |  | 16 | 4 | 14 | Lincoln | 13.2kV | TD05 | Transformer X33472 at 2519 isolated to replace secondary service connections | Ottawa | Scheduled Outage | Repair
3217 | 2003 | 2 | 28 | 0.84028 |  | 15 | 2 | 6 | Lincoln Hts | 13.2kV | TD05 | Xfmr taken out of service for service repair at 2566 Hopkins. 6 customers on Hopkins & Roman were affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20087 | 2012 | 3 | 1 | 0.69306 |  | 262 | 57 | 13 | Lincoln | 13.2kV | TD05 | Transformer X36083 at the rear of 2526 Roman was found to be defective and primary bushing was burnt and cracked at the end. Crews replaced transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20091 | 2012 | 3 | 2 | 0.45139 |  | 70 | 13 | 11 | Lincoln | 13.2kV | TD05 | Transformer #X32945 located at 847 Connaught Ave opened by crew to put up a service | Ottawa | Scheduled Outage | Construction
12106 | 2008 | 3 | 5 | 0.82292 |  | 11 | 2 | 12 | Lincoln | 13.2kV | TD05 | TO05 switch 18662 at Sackville @ Connaught hot line clamp burning. Switch open to replace clamp | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20145 | 2012 | 3 | 9 | 0.50556 |  | 180 | 12 | 4 | Lincoln | 13.2kV | TD05 | Transformer X33474 at 899 Tavistock isolated to rearange plant | Ottawa | Scheduled Outage | Construction
14042 | 2009 | 3 | 11 | 0.87361 |  | 83 | 18 | 13 | Lincoln Heights | 13.2kV | TD05 | Replaced blown fuse feeding transformer X33143 at 2739 Kelly Ave | Ottawa | Adverse Weather | Wind
10170 | 2007 | 3 | 23 | 0.54861 |  | 80 | 9 | 7 | Lincoln Heights | 13.2kV | TD05 | Peter Bishop isolated TRF 55C3B-0060 @ 889 Connaught to allow elctrician to change meter base @ 865 Connaught | Ottawa | Scheduled Outage | Repair
20241 | 2012 | 3 | 27 | 0.52083 |  | 60 | 7 | 7 | Lincoln | 13.2kV | TD05 | Isolated transformer X32944 at 889 Connaught Ave to transfer hydro plant | Ottawa | Scheduled Outage | Construction
4944 | 2004 | 3 | 29 | 0.23333 |  | 29 | 4 | 8 | Lincoln | 13.2kV | TD05 | Blown fuse from squirrel contact interrupted customers on Alpine & Forest. Re-fused transformer. | Ottawa | Foreign Interference | Animal
17825 | 2011 | 4 | 3 | 0.37708 |  | 121 | 28 | 14 | Lincoln Fields | 13.2kV | TD05 | Trans X36091 at :819 TAVISTOCK RD: was refused after brid made conatct ,, power restored | Ottawa | Foreign Interference | Bird
12275 | 2008 | 4 | 14 | 0.024306 |  | 40 | 9 | 14 | Lincoln Heights | 13.2kV | TD05 | At 12:35am, transformer OTT3432 at 840 Ivanhoe Drive, was opened in order to allow crews to make repair to connection at transformer, power restored at 1:15am. Lincoln Heights (TD05-B). ID#12275 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3363 | 2003 | 4 | 21 | 0.66528 |  | 42 | 6 | 9 | Lincoln Hts | 13.2kV | TD05 | A squirrel caused the fuse to blow to xfmr in backyard at 2697 Moncton affecting 9 customers on Moncton & Kelly. Reliability refused and restored power | Ottawa | Foreign Interference | Animal
5074 | 2004 | 4 | 29 | 0.63889 |  | 95 | 24 | 15 | Lincoln | 12/7.2kV | TD05 | Lead to switch had burnt off to transformer at 986 Mossdale St. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18062 | 2011 | 4 | 30 | 0.40833 |  | 44 | 36 | 49 | Lincoln | 12/7.2kV | TD05 | At 09:48 switch S28520 was isolated to allow crew to repair blue phase radial on Forest Street. 49 customers were affected for 44 minutes. Lincoln (TD05) ID# 18062 | Ottawa | Adverse Weather | Wind
10348 | 2007 | 5 | 1 | 0.45278 |  | 18 | 4 | 13 | Lincoln Heights | 13.2kV | TD05 | Transformer #55C3B-0314 at 2522 Roman Ave, to replace hot line clamp. | Ottawa | Scheduled Outage | Repair
6498 | 2005 | 5 | 3 | 0.94861 |  | 128 | 9 | 4 | Lincoln | 13.2kV | TD05 | Animal contact opened transformer at 2738 Kelly in Ottawa west. Crew refused and closed. (crew was delayed in responding due to fire call.) | Ottawa | Foreign Interference | Animal
8228 | 2006 | 5 | 4 | 0.375 |  | 60 | 13 | 13 | Lincoln | 13.2kV | TD05 | Transformer #55C3B-0344 located at the rear of 2556 Severn isolated due to installing a new conductor | Ottawa | Scheduled Outage | Construction
10364 | 2007 | 5 | 4 | 0.41667 |  | 119 | 26 | 13 | Lincoln Heights | 13.2kV | TD05 | John Streng isolated TRF @ 2526 Roman to replace all connections at the TRF and on all the on the services hooked up to the buss | Ottawa | Scheduled Outage | Preventive Maintenance
12387 | 2008 | 5 | 4 | 0.36458 |  | 123 | 86 | 42 | Lincoln | 13.2kV | TD05 | B phase O/H section of the TD05 circuit isolated to remove tree. | Ottawa | Tree Contacts | Tree Fallen
5107 | 2004 | 5 | 5 | 0.5625 |  | 50 | 5 | 6 | Lincoln | 13.2kV | TD05 | Isolate 55C3B-0319 transformer at 2570 Roman Ave to replace connection's service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10407 | 2007 | 5 | 11 | 0.45 |  | 64 | 79 | 74 | Lincoln Heights | 13.2kV | TD05 | Tree limb fell onto primary causing 2 phases of switch at Connaught & Severne to open. | Ottawa | Tree Contacts | Tree Limb Fallen
5148 | 2004 | 5 | 14 | 0.73264 |  | 45 | 675 | 900 | TD | 13.2kV | TD05 | TD05 acb opened via scada at request of G Bell to make emergency repairs to burned pole on Severn | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6594 | 2005 | 5 | 24 | 0.55903 |  | 47 | 9 | 11 | Lincoln | 13.2kV | TD05 | Isolated Transformer at 1035 Hindley to remove trees from secondary | Ottawa | Tree Contacts | Tree Fallen
12476 | 2008 | 5 | 26 | 0.43125 |  | 39 | 5 | 8 | Lincoln Heights | 13.2kV | TD05 | Transformer #TD05 located at 2715 Kelly Ave isolated due to squirrel interference | Ottawa | Foreign Interference | Animal
20655 | 2012 | 5 | 29 | 0.6375 |  | 247 | 1626 | 454 | Lincoln Heights | 13.2kV | TD05 | Two fuses open at 21516 due to downed conductor. Denis Martin crew established work protection to make repairs | Ottawa | Tree Contacts | Tree Limb Fallen
3506 | 2003 | 6 | 1 | 0.45417 |  | 102 | 15 | 9 | Lincoln | 13.2kV | TD05 | Cut out blown to overhead transformer at the rear of 2583 Chambers. Dead squirrel found in the vicinity. Transformer refused & power restored to the 9 affected customers on Henley, Chambers & Arkell streets. | Ottawa | Foreign Interference | Animal
10523 | 2007 | 6 | 4 | 0.49792 |  | 68 | 10 | 9 | Lincoln Heights | 13.2kV | TD05 | Refused switch for transformer 55C3B-0201 at 2698 Kelly Ave that was found blown due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
8429 | 2006 | 6 | 5 | 0.70139 |  | 27 | 4 | 10 | Lincoln | 13.2kV | TD05 | faulty Switch S27453 on the TD05 overhead on Ivanhoe in Ottawa west was replaced. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10559 | 2007 | 6 | 8 | 0.925 |  | 40 | 1 | 1 | Lincoln Heights | 13.2kV | TD05 | A lead came off one phase of TD05 p/p/h switches feeding VT879* at 1065 carling. Crew isolated vault reconnected lead and restored power. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
12574 | 2008 | 6 | 8 | 0.30764 |  | 167 | 19 | 7 | Lincoln Heights | 13.2kV | TD05 | Transformer #X32614 located at 989 Watson St isolated, no cause was found. | Ottawa | Unknown/Other
5278 | 2004 | 6 | 10 | 0.84792 |  | 56 | 4 | 4 | Lincoln | 13.2kV | TD05 | A squirrel made contact at 1022 Pine Wood Cres causing the fus to blow. | Ottawa | Foreign Interference | Animal
8466 | 2006 | 6 | 11 | 0.05 |  | 50 | 11 | 13 | Lincoln | 13.2kV | TD05 | One O/H transformer at 1035 Connaught was interrupted in order to replace a burning line clamp. 13 customers on Connaught, Hanlon & Hopkins were interrupted. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8482 | 2006 | 6 | 13 | 0.75486 |  | 128 | 15 | 7 | Lincoln | 13.2kV | TD05 | Switch to transformer 55C3B-0122 at 862 Ivenhoe Av was found broken and was replaced | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5310 | 2004 | 6 | 15 | 0.36042 |  | 88 | 23 | 16 | Lincoln | 13.2kV | TD05 | Re- fused O/H transfomer at 847 Alpine. | Ottawa | Unknown/Other | No Apparent Cause
20798 | 2012 | 6 | 19 | 0.32708 |  | 109 | 49 | 27 | Lincoln | 13.2kV | TD05 | Transformer #X33200 located at 833 Norton Ave opened up due to animal contact | Ottawa | Foreign Interference | Animal
8554 | 2006 | 6 | 20 | 0.52917 |  | 96 | 14 | 9 | Lincoln | 13.2kV | TD05 | Transformer #OTT5188 located at 2091 Queensgrove isolated due to animal contact | Ottawa | Foreign Interference | Animal
20823 | 2012 | 6 | 21 | 0.84375 |  | 65 | 21 | 19 | Lincoln | 13.2kV | TD05 | Isolated transformer X35533 at 895 Dundee Ave to disconnect two services that had been damaged due to tree falling on the secondary service | Ottawa | Tree Contacts | Tree Fallen
6798 | 2005 | 6 | 25 | 0.62847 |  | 1 | 17 | 1018 | Lincoln | 12/7.2kV | TD05 | TD05 open because of storm, closed via scada and holding | Ottawa | Adverse Weather | Lightning
6805 | 2005 | 6 | 25 | 0.63542 |  | 502 | 8517 | 1018 | Lincoln | 13.2kV | TD05 | Direct lighteneing strike at rear of 2656 Moncton broke pole. Conductors on 5408 & TD05 came togeather | Ottawa | Lightning | Direct Strike
18550 | 2011 | 6 | 28 | 0.83542 |  | 162 | 8 | 3 | Lincoln Heights | 13.2kV | TD05 | Transformer #X33116 located at 2728 Moncton opened up due to lightning storm, vines had to be trimmed | Ottawa | Adverse Weather | Lightning
8641 | 2006 | 7 | 2 | 0.36736 |  | 86 | 14 | 10 | Lincoln Heights | 4.16kV | TD05 | Broken trans cut out replaced at 1038 Hindley St. .. power restored to 10 custs | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12788 | 2008 | 7 | 4 | 0.38194 |  | 65 | 4 | 4 | Lincoln Heights | 13.2kV | TD05 | Isolated transformer X32941 at 862 Maplewood Ave to replace a secondary service | Ottawa | Scheduled Outage | Repair
8689 | 2006 | 7 | 10 | 0.42361 |  | 15 | 1 | 4 | Lincoln Heights | 13.2kV | TD05 | Bob Rolland opened transformer (location number 6160-24) to do streetlight repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14710 | 2009 | 7 | 11 | 0.59097 |  | 199 | 150 | 75 | Lincoln | 13.2kV | TD05 | S25697 RWB opened to isolate blown blue phase fuse and transformer at 2509 Roman, local re-energized after bad O/H transformer was cleared from the primary, transformer replaced | Ottawa | Lightning | Direct Strike
5484 | 2004 | 7 | 12 | 0.51458 |  | 114 | 21 | 11 | Lincoln Hts | 13.2kV | TD05 | Leaking transformer 55C3B-0185 at 1063 Hindley was changed. | Ottawa | Scheduled Outage | Repair
6919 | 2005 | 7 | 13 | 0.65208 |  | 206 | 3435 | 1018 | Lincoln Hts | 13.2kV | TD05 | Crane pulled down middle phase and damaged bottom phase of TD05 at Connaught & Elmhurst causing TD05 to trip and lockout. Reclosing was in service. Queensview was picked up from SC1572, repairs made and line restored. | Ottawa | Foreign Interference | Vehicle
3739 | 2003 | 7 | 14 | 0.29861 |  | 318 | 69 | 13 | TD | 13.2kV | TD05 | O/H Tx 55C3A-0102 at 906 Pinecrest failed affecting 13 customers from 883 to 913 Pinecrest. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10902 | 2007 | 7 | 18 | 0.41181 |  | 57 | 6 | 6 | Lincoln Heights | 13.2kV | TD05 | Transformer #55C1D-0004 located at 810 Alpine isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
12884 | 2008 | 7 | 18 | 0.19722 |  | 206 | 1112 | 324 | Lincoln | 13.2kV | TD05 | In line fuses at Connaught and Elmhusrst found blown. | Ottawa | Adverse Weather | Lightning
5539 | 2004 | 7 | 20 | 0.90347 |  | 84 | 14 | 10 | Lincoln | 13.2kV | TD05 | O/H transformer at 1021 Pinewood was re-fused after contact by racoon. | Ottawa | Foreign Interference | Animal
7037 | 2005 | 7 | 28 | 0.55694 |  | 35 | 9 | 16 | Lincoln Heights | 13.2kV | TD05 | Isolated transformer # 647 at 1060 Ramsey to change a Pedestal cover | Ottawa | Scheduled Outage | Preventive Maintenance
3835 | 2003 | 8 | 3 | 0.95139 |  | 85 | 8 | 6 | TD | 13.2kV | TD05 | Tx 55C3B-0195 at 2570 Hopkins opened during a lightning storm. The fuse was replaced & power restored to 6 Customers on Hopkins ave & Roman rd. | Ottawa | Adverse Weather | Lightning
13010 | 2008 | 8 | 6 | 0.95139 |  | 103 | 41 | 24 | Lincoln | 13.2kV | TD05 | Tree fell on line between Alpine & Forest, north of Elmhurst. Tree broke conductor & caused single phase fuse S28520 to blow at 2612 Elmhurst. 24/7 repaired conductor & refused line successfully. | Ottawa | Tree Contacts | Tree Fallen
16698 | 2010 | 8 | 9 | 0.38681 |  | 53 | 15 | 17 | Lincoln Heights TD | 13.2kV | TD05 | replaced blown fuse feeding transformer X32609 due to a bird contact | Ottawa | Foreign Interference | Bird
7101 | 2005 | 8 | 10 | 0.73333 |  | 148 | 2168 | 1018 | Lincoln | 13.2kV | TD05 | Circuit opened , recloser was out of service. Cleared h/o and closed circuit, circuit reopened. Tried circuit later at approx 17:00 circuit opened again. At 17:36 opened SMU 20 fuses at Connaught and Hanlon and circuit held. Patrolled downstream of fuses and found nothing. Closed in SMU fuses one at a time and all load recovered. | Ottawa | Adverse Weather
8939 | 2006 | 8 | 10 | 0.37847 |  | 45 | 764 | 1018 | Lincoln Heights | 13.2kV | TD05 | Suspected cable fault between Lincoln and first riser | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11040 | 2007 | 8 | 12 | 0.89931 |  | 121 | 26 | 40 | Lincoln Heights | 13.2kV | TD05 | Animal contact caused XFMR 55C1D-0358 at 813 Norton to blow a fuse also causing damage to white phase switch 16738 hot line clamp. Switch was opened to repair the hot line clamp. Transformer was re-fused and the customers have been restored. | Ottawa | Foreign Interference | Animal
5680 | 2004 | 8 | 14 | 0.053472 |  | 93 | 19 | 12 | Lincoln | 13.2kV | TD05 | Branches cleared & O/H transformer at 2586 Henley re-fused. | Ottawa | Tree Contacts | Inadequate Trimming
11053 | 2007 | 8 | 14 | 0.99167 |  | 76 | 4 | 3 | Lincoln Heights | 13.2kV | TD05 | 882 Tavistock Ave transformer fuse opened due to vines growing up guy wire, crew cleared vines and re-fused transformer. | Ottawa | Defective Equipment
16775 | 2010 | 8 | 19 | 0.39236 |  | 123 | 25 | 12 | Lincoln Heights | 13.2kV | TD05 | Transformer #X33390 located at 868 Tavistock opened by crew for new services | Ottawa | Scheduled Outage | Construction
14985 | 2009 | 8 | 21 | 0.43403 |  | 15 | 3 | 13 | Lincoln Heights | 13.2kV | TD05 | Transformer #KT425 located at 844 Rob Roy isolated to isolate a service out of ped | Ottawa | Scheduled Outage | Construction
14990 | 2009 | 8 | 21 | 0.57639 |  | 9 | 2 | 13 | Lincoln Heights | 13.2kV | TD05 | Transformer #KT425 located at 844 Rob Roy isolated to re-energize service | Ottawa | Scheduled Outage | Construction
3930 | 2003 | 8 | 23 | 0.73958 |  | 65 | 8 | 7 | Lincoln Heights | 13.2kV | TD05 | A connection burnt off on the transformer at 2522 Roman. Repair made and power restored | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9053 | 2006 | 8 | 24 | 0.66389 |  | 94 | 16 | 10 | Lincoln Heights | 13.2kV | TD05 | Power outage to transformer OTT4193 846 Maplewood Ave due to squirrel contact | Ottawa | Foreign Interference | Animal
16831 | 2010 | 8 | 29 | 0.34514 |  | 58 | 7 | 7 | Lincoln Heights | 13.2kV | TD05 | Transformer #X32643 located at 1000 Watson opened up due to vine contact around the transformer | Ottawa | Tree Contacts | Inadequate Trimming
11225 | 2007 | 8 | 31 | 0.55208 |  | 64 | 13 | 12 | Lincoln Heights | 13.2kV | TD05 | Isolated transformer 55C3B-0006 at 852 Forest St to repair service | Ottawa | Scheduled Outage | Preventive Maintenance
19068 | 2011 | 9 | 1 | 0.375 |  | 150 | 30 | 12 | Lincoln Heights | 13.2kV | TD05 | Rick Wallace isolated X32945 at 847 Connaught to relocate plant | Ottawa | Scheduled Outage | Construction
19069 | 2011 | 9 | 1 | 0.50694 |  | 20 | 4 | 12 | Lincoln Heights | 13.2kV | TD05 | Transformer X33390 at 867 Norton Ave isolated to remove vines from transformer and replace hotline clamp | Ottawa | Tree Contacts | Inadequate Trimming
7279 | 2005 | 9 | 4 | 0.60069 |  | 44 | 4 | 5 | Lincoln | 13.2kV | TD05 | Transformer located rear of 836 Norton isolated due to animal interference (squirrel) | Ottawa | Foreign Interference | Animal
16934 | 2010 | 9 | 13 | 0.90625 |  | 28 | 4 | 8 | Lincoln Heights | 13.2kV | TD05 | Trans at 2715 KELLY AVE OTTAWA was isolated in order to replace a defective LLC | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19178 | 2011 | 9 | 14 | 0.54167 |  | 57 | 16 | 17 | Lincoln Heights | 13.2kV | TD05 | Transformer X36093 at 845 Alpine on the TD05 Blue Phase was removed from service for crew to replace service. | Ottawa | Scheduled Outage
5814 | 2004 | 9 | 18 | 0.84375 |  | 25 | 2 | 5 | Lincoln Hts. | 13.2kV | TD05 | Burning hot-line clamp at the rear of 2570 Roman Ave. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11334 | 2007 | 9 | 19 | 0.54861 |  | 83 | 14 | 10 | Lincoln Heights | 13.2kV | TD05 | At 13:10 trans at 824 Alpine St was isolated in order to replace the sec service | Ottawa | Scheduled Outage | Preventive Maintenance
13311 | 2008 | 10 | 2 | 0.53194 |  | 59 | 7 | 7 | Lincoln Heights | 13.2kV | TD05 | Transformer #X33291 located at 996 Pinewood isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
19370 | 2011 | 10 | 13 | 0.48194 |  | 86 | 75 | 52 | Lincoln | 13.2kV | TD05 | At 11:34 swtich S16738 at 839 Travistock opened due to squirrel contact. Crew refused and restored power. Lincoln Heights TD05,19370 | Ottawa | Foreign Interference | Animal
17150 | 2010 | 10 | 21 | 0.39583 |  | 80 | 11 | 8 | Lincoln | 13.2kV | TD05 | Trans at 958 Farrell St Ott for a service upgrrade | Ottawa | Scheduled Outage | Preventive Maintenance
13417 | 2008 | 10 | 23 | 0.53264 |  | 113 | 11 | 6 | Lincoln Heights | 13.2kV | TD05 | At 12:47 trans at 820 Forest St was isolated in order to install a new service | Ottawa | Scheduled Outage | Preventive Maintenance
9527 | 2006 | 10 | 27 | 0.67986 |  | 116 | 23 | 12 | Lincoln Heights | 13.2kV | TD05 | Fuse on switch to transformer 55C1D-0002 at 811 Alpine Ave was found blown due to squirrel contact | Ottawa | Foreign Interference | Animal
19490 | 2011 | 10 | 28 | 0.43889 |  | 28 | 3 | 7 | Lincoln Heights | 13.2kV | TD05 | Transformer #X33137 located at 960 Gold Cres opened by crew for a change over | Ottawa | Scheduled Outage | Construction
15341 | 2009 | 10 | 31 | 0.70347 |  | 259 | 35 | 8 | Lincoln | 13.2kV | TD05 | Transformer switch failed for tx at 950 Farrel. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7581 | 2005 | 11 | 8 | 0.375 |  | 180 | 60 | 20 | Lincoln | 13.2kV | TD05 | Transformer located at rear of 2660 Moncton isolated due to transferring U/G to new pole | Ottawa | Scheduled Outage | Construction
7583 | 2005 | 11 | 8 | 0.54167 |  | 180 | 30 | 10 | Lincoln | 13.2kV | TD05 | Transformer located at the rear of 2654 Moncton isolated due to transferring of U/G to new pole | Ottawa | Scheduled Outage | Construction
7585 | 2005 | 11 | 9 | 0.35417 |  | 105 | 10 | 6 | Lincoln | 13.2kV | TD05 | Transformer located at the rear of 2642 Moncton isolated to transfer U/G to new pole | Ottawa | Scheduled Outage | Construction
9647 | 2006 | 11 | 13 | 0.39583 |  | 35 | 7 | 12 | Lincoln Heights | 13.2kV | TD05 | trf. 55c1d-0002 was isolated to change a service @ 811 alpine | Ottawa | Scheduled Outage | Preventive Maintenance
4471 | 2003 | 11 | 17 | 0.49861 |  | 21 | 7 | 19 | Lincoln Heights | 13.2kV | TD05 | P. Barr reports transformer # KT654 opened to reconnect defective secondary service. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9695 | 2006 | 11 | 21 | 0.37708 |  | 77 | 5 | 4 | Lincoln | 13.2kV | TD05 | Fuse on transformer switch 55C3A-0128 at 1018 Pinewood was found blown due to squirrel | Ottawa | Foreign Interference | Animal
13677 | 2008 | 11 | 28 | 0.54028 |  | 59 | 3 | 3 | Lincoln Heights | 13.2kV | TD05 | Transformer #X33392 located at 831 Alpine isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
15522 | 2009 | 12 | 16 | 0.098611 |  | 30 | 1 | 2 | Lincoln | 13.2kV | TD05 | o/h transformer was opened to disconnect Service feeding 2678 henley that burnt off at house due to fire. | Ottawa | Adverse Environment | Fire
17436 | 2010 | 12 | 20 | 0.44444 |  | 48 | 9 | 11 | Lincoln Heights | 13.2kV | TD05 | Transformer #X33117 located at 2678 Moncton opened by crew to re-arrange service | Ottawa | Scheduled Outage | Construction
11885 | 2007 | 12 | 26 | 0.61667 |  | 72 | 20 | 17 | Lincoln Heights | 13.2kV | TD05 | Blown fuse on switch feeding transformer at 858 Forest St due to a squirrel contact | Ottawa | Foreign Interference | Animal
17453 | 2010 | 12 | 26 | 0.51597 |  | 49 | 7 | 8 | Lincoln Heights | 13.2kV | TD05 | Replaced blown fuse feeding transformer X33129 at 2697 Moncton Rd due to a squirrel contact | Ottawa | Foreign Interference | Animal
15570 | 2009 | 12 | 27 | 0.14167 |  | 182 | 389 | 162 | Lincoln | 13.2kV | TD05 | Primary conductor down at 2528 Hopkins caused 2 fuses to blow at S25697, the remaining phase was opened to isolate the line section for repairs. Power was restored to all 3 phases following repairs. Affected customers were in the Hopkins, Roman, Connaught area. | Ottawa | Adverse Weather | Ice Storm
13809 | 2008 | 12 | 28 | 0.47569 |  | 513 | 205 | 24 | Lincoln Heights | 13.2kV | TD05 | Primary conductor broken at the corner of Hindley & Hanlon. | Ottawa | Adverse Weather | Wind
19781 | 2012 | 1 | 3 | 0.84375 |  | 109 | 67 | 37 | Lincoln Heights | 13.2kV | TD06 | A defective lightning arrestor at 486 Woodland cause the outage | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6122 | 2005 | 1 | 7 | 0.38056 |  | 289 | 2738 | 1126 | Lincoln | 13.2kV | TD06 | Conductor broke apart & fell to the ground at 2095 Knightsbridge. Conductor broke underneath a clamp. A set of SMD20 fuses were opened to take downed conductor off potential & prevent affected customers from experiencing abnormal voltage. The outage was again expanded after the crews were set-up in order to re-attach the conduct. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19874 | 2012 | 1 | 22 | 0.54583 |  | 79 | 12 | 9 | Lincoln Heights | 13.2kV | TD06 | replaced blown fuse feeding transformer X35792 at 2099 Prince Charles Rd due to squirrel contact | Ottawa | Foreign Interference | Animal
15687 | 2010 | 1 | 27 | 0.09375 |  | 185 | 3 | 1 | Lincoln Heights | 13.2kV | TD06 | TD06 auto-reclosed, crews found single phase wire down at 993 Richmond. O/H section repaired and customer restored | Ottawa | Defective Equipment
9986 | 2007 | 2 | 3 | 0.71528 |  | 38 | 1 | 1 | Lincoln Heights | 13.2kV | TD06 | red squirrel opened O/H blue phase fuse on three phase feeding PT006 at 809 Richmond rd. | Ottawa | Foreign Interference | Animal
3168 | 2003 | 2 | 5 | 0.77083 |  | 432 | 2532 | 1050 | Lincoln TS | 13.2kV | TD06 | PRIMARY O/H LINE DOWN IN BACK YARD ON BROMLEY AVE. COULD NOT FIND FAULT FOR OVER 2 HRS. THEN OPENED WRONG SMU FUSES. WHEN RIGHT FUSES WERE OPENED THE CIRCUIT OPENED & RECLOSED. CIRCUIT WAS OPENED BY SCADA TO CLOSE FUSES. CIRCUIT WOULD NOT PICK UP FROM STATION KEPT TRIPPING BREAKER. SMU FUSES REOPENED & PART OF CIRCUIT PICKED UP BY SCADA. WHEN FIRST FUSE CLOSED THE CIRCUIT OPENED & RECLOSED. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20005 | 2012 | 2 | 13 | 0.46736 |  | 48 | 9 | 11 | Lincoln | 4.16kV | TD06 | Transformer X38564 at 2296 Lawn Ave. isolated to allow for connection of new service | Ottawa | Scheduled Outage | Construction
14026 | 2009 | 3 | 6 | 0.79653 |  | 43 | 9 | 13 | Linclon Heights | 13.2kV | TD06 | Replaced blown fuse at transformer X35794 at the rear of 2062 Knightsbridge Rd | Ottawa | Tree Contacts | Inadequate Trimming
8001 | 2006 | 3 | 9 | 0.69583 |  | 118 | 49 | 25 | Lincoln | 13.2kV | TD06 | Hot line clamp failed at Holt & Adams st. 2 transformers affected in power outage. | Ottawa | Adverse Weather | Ice Storm
12129 | 2008 | 3 | 11 | 0.825 |  | 132 | 18 | 8 | Lincoln Heights | 13.2kV | TD06 | Transformer #X35319 located at 1856 Bromley isolated due to animal contact (racoon) | Ottawa | Foreign Interference | Animal
6284 | 2005 | 3 | 15 | 0.32986 |  | 275 | 472 | 1126 | TD | 13.2kV | TD06 | B phase SMD20 fuse at Knightsbridge found blown, 1 span of primary down at 1889 Lauder, TD06 RWB L/C's at 1955 Wembly opened & while closing B phase SMD20 fuse at Knightsbridge, B & W phase flashed over, TD06 breaker opened. B & W SMD re-fused & closed, TD06 breaker closed via scada. All customers restored except approx 35 on Lauder & Wembly. Squirrel contact caused flash damaging o/h conductor. | Ottawa | Foreign Interference | Animal
20218 | 2012 | 3 | 24 | 0.75417 |  | 37 | 6 | 10 | Lincoln | 13.2kV | TD06 | Animal contact caused fuse to blow at X35088. | Ottawa | Foreign Interference | Animal
15848 | 2010 | 3 | 25 | 0.84375 |  | 50 | 14 | 17 | Lincoln Heights | 13.2kV | TD06 | Transformer #X32381 located at 2206 Anthony isolated due to vines around the transformer | Ottawa | Tree Contacts | Inadequate Trimming
14102 | 2009 | 3 | 26 | 0.5 |  | 10 | 2 | 13 | Lincoln Heights | 13.2kV | TD06 | Issolated transformer X35904 at 2035 Neepawa Ave for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
3314 | 2003 | 4 | 2 | 0.88889 |  | 60 | 10 | 10 | TD | 13.2kV | TD06 | 24/7 opened xfmr 55C2C-0199 @ 2303 Fox to make repairs to the secondary bus | Ottawa | Scheduled Outage | Repair
15888 | 2010 | 4 | 3 | 0.27778 |  | 160 | 29 | 11 | Lincoln Heights | 13.2kV | TD06 | TD06 DIP1 at Woodland and Halldon white fuse blew, crew completed a quick patrol and found nothing, switch re-fused and holding. | Ottawa | Unknown/Other | No Apparent Cause
4969 | 2004 | 4 | 5 | 0.017361 |  | 370 | 31 | 5 | TD | 13.2kV | TD06 | 24/7 found broken primary drop to Tx 55C2C-0376 at 2001 Neepawa. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12266 | 2008 | 4 | 10 | 0.41389 |  | 74 | 2 | 2 | LINCOLN HTS | 4.16kV | TD06 | Transformer #X32367 at 1000 Byron Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Repair
12269 | 2008 | 4 | 10 | 0.41389 |  | 74 | 2 | 2 | LINCOLN HTS | 4.16kV | TD06 | Transformer #32767 at 1000 Byron Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage
5088 | 2004 | 5 | 2 | 0.64931 |  | 347 | 1928 | 1200 | Lincoln | 13.2kV | TD06 | Faulted P/P/H switches to VT823 2045 Carling caused SMD20 200A fuses to blow at 2095 Knightsbridge. Attempts to refuse and pick up the load on TD06 breaker failed and the load had to be restored by closing the fuses in live after the circuit was thoroughly patrolled. VT823 isolated to repair TD06 P/P/H switches to VT823. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10377 | 2007 | 5 | 7 | 0.37639 |  | 88 | 1 | 1 | Lincoln Heights | 13.2kV | TD06 | Power outage to transformer OTT125 @ 2207 Carling Avenue, due to squirrel contact. | Ottawa | Foreign Interference | Animal
20470 | 2012 | 5 | 7 | 0.43958 |  | 7 | 1 | 11 | Lincoln | 13.2kV | TD06 | Transformer X34429 at 2117 Prince Charles Rd. isolated to remove streetlight feed | Ottawa | Scheduled Outage | Construction
3423 | 2003 | 5 | 11 | 0.54167 |  | 46 | 5 | 7 | LINCOLN | 13.2kV | TD06 | A squirrel building a nest at the transformer @ 2089 Dovercourt Ave. blew the fuse. | Ottawa | Foreign Interference | Animal
8292 | 2006 | 5 | 13 | 0.8125 |  | 40 | 17 | 25 | Lincoln | 13.2kV | TD06 | O/C crew isolated 2 phase run-off between Bromley & Lauder to remove limb from primary, | Ottawa | Tree Contacts | Tree Limb Fallen
18153 | 2011 | 5 | 14 | 0.61458 |  | 49 | 10 | 12 | Lincoln Heights | 13.2kV | TD06 | Replaced broken fuse feeding transformer X35791 | Ottawa | Unknown/Other | No Apparent Cause
6561 | 2005 | 5 | 15 | 0.52083 |  | 50 | 3 | 4 | Lincoln | 13.2kV | TD06 | crew isolated three phase transformer bank on overhead to repair broken cutout. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8309 | 2006 | 5 | 17 | 0.21389 |  | 47 | 31 | 39 | Lincoln | 13.2kV | TD06 | 13 kv O/H transformer OTT3271 at Byron & Honeywell was interrupted by a tree branch making contact with the primary bushing. Tree branch cleared & transformer refused successfully. | Ottawa | Tree Contacts | Inadequate Trimming
6581 | 2005 | 5 | 20 | 0.375 |  | 43 | 3 | 4 | Lincoln | 13.2kV | TD06 | Isolated Transformer #0432 at 2131 Neepawa to do a service change | Ottawa | Scheduled Outage | Preventive Maintenance
16113 | 2010 | 5 | 20 | 0.84375 |  | 357 | 2310 | 499 | Lincoln Heights | 13.2kV | TD06 | 24/7 reports wires down in the backyard @ 1969 Broomley. S17634 fuses opened for public safety outage to 499 customers in the Carling, Bromley & Knights Bridge area. On-call crew dispatched to repair overhead conductor. | Ottawa | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
8335 | 2006 | 5 | 21 | 0.81597 |  | 40 | 5 | 8 | Lincoln | 13.2kV | TD06 | Crew cleared trees and refused transformer feeding customers on Knightsbridge. Lackhart and Black Friers. | Ottawa | Tree Contacts | Inadequate Trimming
20605 | 2012 | 5 | 25 | 0.78819 |  | 869 | 58 | 4 | Lincoln Heights | 13.2kV | TD06 | A blown switch caused by the high winds at transformer X32526 at 1985 Neepawa Ave | Ottawa | Adverse Weather | Wind
3489 | 2003 | 5 | 26 | 0.78472 |  | 20 | 1 | 3 | Lincoln Hieghts | 13.2kV | TD06 | Crew reports transformer opened to repair hot line clamp. 3 Customers affected in power outage. Customers at 2102,2104 & 2110 knightsbridge. While crew replaced hot line clamp. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18235 | 2011 | 5 | 28 | 0.70833 |  | 50 | 9 | 11 | LINCOLN HEIGHTS | 13.2kV | TD06 | At 17:00 customers report a blown transformer fuse at X38564 on TD06 White phase. Crews arrived on site and found a blown fuse with no apparent cause. 11 customers affected for 50 mins. Lincoln Heights (TD06) ID# 18235 | Ottawa | Unknown/Other
5226 | 2004 | 5 | 30 | 0.70486 |  | 88 | 21 | 14 | Lincoln | 13.2kV | TD06 | Crew refused transformer at 704 sherbourne that was opened by a squirrel. | Ottawa | Foreign Interference | Animal
18246 | 2011 | 5 | 30 | 0.38542 |  | 45 | 5 | 7 | Lincoln Heights | 13.2kV | TD06 | Isolated transformer X35799 at 2098 Honeywell Ave to replace defective switch | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20675 | 2012 | 6 | 2 | 0.425 |  | 91 | 18 | 12 | Lincoln | 13.2kV | TD06 | Transformer #X32528 located at 751 Courtenay Ave opened up due to tree contact. | Ottawa | Tree Contacts | Inadequate Trimming
18306 | 2011 | 6 | 6 | 0.40625 |  | 25 | 3 | 7 | Lincoln TS | 13.2kV | TD06 | Transformer X35799 at 2098 Honeywell was opened to allow forestry crews to clear tree limbs off the primary. | Ottawa | Tree Contacts | Inadequate Trimming
18310 | 2011 | 6 | 6 | 0.45486 |  | 30 | 2 | 5 | Lincoln TS | 13.2kV | TD06 | Transformer X32573 at 418 Halldon had to be opened to allow forestry crews to clear limbs from the primary. | Ottawa | Tree Contacts | Inadequate Trimming
18315 | 2011 | 6 | 6 | 0.45486 |  | 30 | 2 | 5 | Lincoln TS |  | TD06 | Transformer X32573 at 418 Halldon had to be opened to allow forestry crews to clear branches off the primary. | Ottawa | Tree Contacts
10574 | 2007 | 6 | 8 | 0.95833 |  | 90 | 2 | 1 | Lincoln Heights | 13.2kV | TD06 | crew isolated vault VT824* at 2055 Carling to replace Burnt TD06 p/p/h switch. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3542 | 2003 | 6 | 9 | 0.088194 |  | 183 | 366 | 120 | Russell | 13.2kV | TD06 | Tree limbs were blowing into the circuit and caused the fuse to rupture at the switch behind 974 Weston. | Ottawa | Tree Contacts | Inadequate Trimming
12617 | 2008 | 6 | 12 | 0.3875 |  | 242 | 20 | 5 | Lincoln Heights | 13.2kV | TD06 | Transformer #X32573 located at 422 Halldon isolated for tree removal/trimming. | Ottawa | Scheduled Outage | Preventive Maintenance
5294 | 2004 | 6 | 13 | 0.28333 |  | 17 | 4 | 13 | Lincoln Heights | 13.2kV | TD06 | Squirrel caused fuse on transformer to blow. Transformer refused restoring power to all customers 723 MANITOU DR area. | Ottawa | Foreign Interference | Animal
12628 | 2008 | 6 | 14 | 0.93889 |  | 428 | 100 | 14 | Lincoln | 13.2kV | TD06 | Tree Fallen behind 236 New Orchard causing the secondary bushings to come out and several service wires are down, as well as open wire bus needed replacing. Damaged transformer changed & power restored. | Ottawa | Tree Contacts | Tree Fallen
6756 | 2005 | 6 | 17 | 0.63264 |  | 69 | 8 | 7 | Lincoln | 13.2kV | TD06 | Transformer located at 483 Sherbourne was isolated due to lightning | Ottawa | Adverse Weather | Lightning
8581 | 2006 | 6 | 22 | 0.88194 |  | 10 | 3 | 17 | LINCOLN | 13.2kV | TD06 | Isolated transformer 55C2C-0588 at 220 WOODROFFE AVE to trim the tree branches that was in the open wire buss | Ottawa | Tree Contacts | Inadequate Trimming
16360 | 2010 | 6 | 29 | 0.40278 |  | 218 | 84 | 23 | Lincoln Heights | 13.2kV | TD06 | 23 Customers were affected in a planned outage in the area of 1965 Broley. To allow tree trimming crew to remove several tree in the overhead circuit. | Ottawa | Scheduled Outage | Preventive Maintenance
10817 | 2007 | 7 | 8 | 0.48125 |  | 75 | 9 | 7 | Lincoln Heights | 13.2kV | TD06 | Transformer #55C2C-0378 located at 1965 Bromley isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
18747 | 2011 | 7 | 17 | 0.80764 |  | 414 | 16277 | 2359 | Lincoln Heights | 13.2kV | TD06 | TD06 tripped during lightening storm. Closed back in and circuit held | Ottawa | Adverse Weather | Lightning
10910 | 2007 | 7 | 19 | 0.42778 |  | 49 | 5 | 6 | LINCOLN HEIGHTS | 13.2kV | TD06 | Crew found blown fuse on Transformer 55C2C-0361 at 2128 Knights Bridge due to a bird contact | Ottawa | Foreign Interference | Bird
16490 | 2010 | 7 | 19 | 0.2875 |  | 104 | 17 | 10 | Lincoln Heights | 13.2kV | TD06 | Transformer #X32574 located at 445 Halldon opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
10938 | 2007 | 7 | 24 | 0.35208 |  | 113 | 15 | 8 | Lincoln Heights | 13.2kV | TD06 | Transformer #55C2C-0579 located at 153 Woodroffe Ave isolated due to animal contact | Ottawa | Foreign Interference | Animal
12931 | 2008 | 7 | 24 | 0.40972 |  | 40 | 8 | 12 | Lincoln Heights | 13.2kV | TD06 | Transformer #X32356 located at 950 Byron isolated due to service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
14854 | 2009 | 7 | 27 | 0.35556 |  | 126 | 348 | 1126 | Lincoln Heights | 13.2kV | TD06 | S17634 at 2095 Kinghts Bridge Road, customer called in declaring a phase opened. Fuse opened due to Lightining and/ or heavy rain fall. Lincoln Heights (TD06). ID#14854 (for more information on duration of outage, please see log for the day details) | Ottawa | Adverse Weather | Lightning
8868 | 2006 | 7 | 29 | 0.47083 |  | 58 | 1088 | 1126 | Lincoln | 13.2kV | TD06 | Bird contact with circuit at Woodland & Byron damaged an insulator & arrestor. Damaged insulator & arrestor were both replaced & power restored to all customers. | Ottawa | Foreign Interference | Animal
3822 | 2003 | 7 | 30 | 0.94375 |  | 80 | 1500 | 1125 | Lincoln | 13.2kV | TD06 | A blown pot head on 5409 caused by a racoon occurred the same time as this interuption indicating it may be related. The circuit was closed by SCADA and reopened at 23:05 for no apparent reason | Ottawa | Foreign Interference | No Apparent Cause
16627 | 2010 | 8 | 3 | 0.68056 |  | 41 | 379 | 555 | Lincoln | 13.2kV | TD06 | Lightning in the area of Knightsbridge and Carling open S17634 Blue Phase, Crews re-fused and closed successfully restoring all load. | Ottawa | Adverse Weather | Lightning
11001 | 2007 | 8 | 6 | 0.38125 |  | 41 | 9 | 13 | Lincoln Heights | 13.2kV | TD06 | Transformer #55C2C-0163 located at 2074 Knightsbridge isolated due to animal contact | Ottawa | Foreign Interference | Animal
14922 | 2009 | 8 | 9 | 0.0041667 |  | 92 | 43 | 28 | Lincoln | 13.2kV | TD06 | 2 overhead transformers on Sherbourne were interrupted to make repairs to damaged insulators, broken neutral conductor and burnt guy wires at 722 Sherbourne. Suspect damage was caused from a previous lightning strike. Repairs were made by 24/7 & Oncall crew. Customers on Wembley & Sherbourne were affected. | Ottawa | Defective Equipment
8964 | 2006 | 8 | 14 | 0.52292 |  | 47 | 8 | 10 | Lincoln Heights | 13.2kV | TD06 | Fuse to transformer 55C2C-0460 at 2106 Black Friars Cres was found blown due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
18977 | 2011 | 8 | 18 | 0.58333 |  | 535 | 571 | 64 | Linclon Heights | 12/7.2kV | TD06 | During lightning strom tree limb fell on lines, lines down. | Ottawa | Tree Contacts | Tree Limb Fallen
13148 | 2008 | 8 | 26 | 0.38542 |  | 49 | 8 | 10 | LINCOLN HEIGHTS | 13.2kV | TD06 | Transformer #X32595 at 650 Tillbury isolated to allow for service upgrade | Nepean | Scheduled Outage | Construction
11174 | 2007 | 8 | 28 | 0.60417 |  | 330 | 50 | 9 | Lincoln Heights | 13.2kV | TD06 | Transformer #55C2C-0587 located at 244 Woodroffe Ave isolated due to pothead compound clean-up | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
13174 | 2008 | 8 | 31 | 0.89375 |  | 33 | 4 | 7 | Lincoln Heights | 13.2kV | TD06 | Transformer fuse replaced @ 1893 LAUDER DR. Outage was caused by racoon found at bottom of pole. All customers restored. | Ottawa | Foreign Interference | Animal
15037 | 2009 | 8 | 31 | 0.44444 |  | 45 | 3 | 4 | Lincoln Heights | 13.2kV | TD06 | Transformer #X32535 located at 1973 Bromley isolated to replace connections at the pole | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4044 | 2003 | 9 | 10 | 0.72361 |  | 53 | 4 | 4 | Lincoln Heights | 13.2kV | TD06 | A squirrel caused the fuse to blow at the transformer in the rear of 1973 Bromley. 4 customers on Manitou and Bromley were affected. Power restored at 18:15 | Ottawa | Foreign Interference | Animal
13223 | 2008 | 9 | 12 | 0.58333 |  | 100 | 424 | 425 | Lincoln | 13.2kV | TD06 | Jeff Magee reports that the W phase load side conductor to switch S18680 at Dovercourt has burnt off and is on the ground and the W phase switch is also broken. S17634 opened to isolated same for repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11311 | 2007 | 9 | 14 | 0.89583 |  | 60 | 8 | 8 | Lincoln Heights | 13.2kV | TD06 | Tree contact caused transformer 55C2C at 1983 Bromley to open. Refused and customers restored | Ottawa | Tree Contacts | Inadequate Trimming
13229 | 2008 | 9 | 14 | 0.82639 |  | 213 | 4 | 1 | Lincoln | 13.2kV | TD06 | VT 596 at 2001 Carling blown fuse at dip pole. Cause was defective termiation at vault switch. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19223 | 2011 | 9 | 21 | 0.41042 |  | 156 | 174 | 67 | Lincoln Heights | 13.2kV | TD06 | 13kV vault VT597 at 2019 Carling was isolated to allow contractor to perform maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
9311 | 2006 | 9 | 26 | 0.49306 |  | 55 | 8 | 9 | Lincoln Heights | 13.2kV | TD06 | Fuse to transformer 55C2C-0398 at 2300 Midway was found blown due to tree branch | Ottawa | Tree Contacts | Inadequate Trimming
15174 | 2009 | 9 | 27 | 0.12292 |  | 53 | 5 | 6 | Lincoln | 13.2kV | TD06 | Crew refused transformer @ 1959 Bromley. No cause was found. | Ottawa | Unknown/Other | No Apparent Cause
4213 | 2003 | 10 | 6 | 0.39792 |  | 285 | 1311 | 276 | Lincoln | 13.2kV | TD06 | Scheduled isolation of VT823 @ 2045 Carling for routine vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
4214 | 2003 | 10 | 6 | 0.43542 |  | 255 | 1173 | 276 | Lincoln | 13.2kV | TD06 | Scheduled isolation of VT824 @ 2055 Carling for routine vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
17093 | 2010 | 10 | 12 | 0.41389 |  | 54 | 12 | 13 | Lincoln Heights | 13.2kV | TD06 | Transformer #X35790 located at 2122 Honeywell opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
15268 | 2009 | 10 | 16 | 0.55208 |  | 50 | 5 | 6 | LINCOLN HEIGHTS | 13.2kV | TD06 | TRANSFORMER x32526 AT 1959 NEEPEWA ISOLATED TO ALLOW FOR NEW SERVICE FOR INSTALLATION OF STREETLIGHT FEED | Ottawa | Scheduled Outage | Construction
19437 | 2011 | 10 | 21 | 0.47917 |  | 129 | 19 | 9 | Lincoln Heights | 13.2kV | TD06 | Isolated transformer X35793 at 2105 Neepawa Ave for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
11571 | 2007 | 10 | 22 | 0.48958 |  | 75 | 18 | 14 | Lincoln Heights | 13.2kV | TD06 | Isolated transformer 55C2D-0680 at 695 Sherbourn Rd to replace primary top pin and secondary service | Ottawa | Scheduled Outage | Preventive Maintenance
13409 | 2008 | 10 | 22 | 0.58819 |  | 55 | 6 | 6 | Lincoln Heights | 13.2kV | TD06 | Refused switch feeding transformer X35783 at 2051 KNIGHTSBRIDGE ROAD | Ottawa | Unknown/Other | No Apparent Cause
19460 | 2011 | 10 | 24 | 0.58611 |  | 61 | 7 | 7 | Lincoln Heights | 13.2kV | TD06 | Transformer #X32538 located at 1897 Lauder opened up due to squirrel interference | Ottawa | Foreign Interference | Animal
17185 | 2010 | 10 | 27 | 0.70833 |  | 60 | 6 | 6 | Lincoln TD | 13.2kV | TD06 | Primary cable to KT617 at 316 Woodroffe failed, defective cable disconnected & power restored via spare cable. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15336 | 2009 | 10 | 31 | 0.4125 |  | 131 | 17 | 8 | Lincoln Heights | 13.2kV | TD06 | Refused blown switch feeding transformer X38567 at the rear of 171 Lockhart Ave | Ottawa | Adverse Weather | Wind
5865 | 2004 | 11 | 6 | 0.58958 |  | 44 | 10 | 14 | Lincoln | 13.2kV | TD06 | Transfomer at 2258 Lawn interrupted due to a defective fuse. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11679 | 2007 | 11 | 7 | 0.92361 |  | 10 | 2 | 12 | LINCOLN HEIGHTS | 13.2kV | TD06 | Transformer at 175 Woodroffe Ave was isolated while crews repair hot line clamp. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7582 | 2005 | 11 | 8 | 0.39931 |  | 145 | 24 | 10 | Lincoln | 13.2kV | TD06 | Transformer located at rear of 2268 Carling Ave isolated due to a pole change | Ottawa | Scheduled Outage | Construction
19577 | 2011 | 11 | 15 | 0.39097 |  | 307 | 1126 | 220 |  | 13.2kV | TD06 | PT208 @ 2090 Neepawe was shut down to allow the contractor to preform secondarty maintence | Ottawa | Scheduled Outage | Preventive Maintenance
4564 | 2003 | 12 | 5 | 0.41319 |  | 40 | 4 | 6 | Linclon | 13.2kV | TD06 | 2047 Knightsbridge service replaced | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11816 | 2007 | 12 | 5 | 0.52778 |  | 130 | 22 | 10 | Lincoln Heights | 13.2kV | TD06 | Transformer #55C2D-0677 located at 650 Tillbury isolated due to working fire | Ottawa | Adverse Environment | Fire
15490 | 2009 | 12 | 9 | 0.56597 |  | 51 | 17 | 20 | Lincoln Heights | 13.2kV | TD06 | At 13:35 overhead line at 2286 Carling was isolated to allow crews to repair broken red phase conductor. 20 customers were affected for 51 minutes. Lincoln Heights (TD06) ID#15490. | Nepean | Defective Equipment
15494 | 2009 | 12 | 10 | 0.53542 |  | 92 | 12 | 8 | Lincoln Heights | 13.2kV | TD06 | Transformer #X32525 located at 2001 Neepawa isolated due to broken primary lead | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17417 | 2010 | 12 | 13 | 0.38542 |  | 36 | 3 | 5 | Lincoln | 13.2kV | TD06 | At 09:15 transformer KT617 at 320 Woodroffe was isolated to allow crew to remove defective cable. 5 customers were affected for 36 minutes. Lincoln (TD06) ID #17417 | Ottawa | Scheduled Outage
15717 | 2010 | 2 | 11 | 0.41458 |  | 59 | 10 | 10 | Lincoln Heights | 13.2kV | TD07 | Replaced blown fuse for transformer X38560 at 2407 Rosewood Ave (Squirrel contact) | Ottawa | Foreign Interference | Animal
14039 | 2009 | 3 | 11 | 0.73542 |  | 56 | 24 | 26 | Lincoln Heights |  | TD07 | Replaced broken switch at the corner of Lawn Ave and Hartleigh Ave feeding two overhead transformers | Ottawa | Adverse Weather | Wind
10145 | 2007 | 3 | 18 | 0.63403 |  | 57 | 16 | 17 | Lincoln Heights | 13.2kV | TD07 | Transformer #55C1D-0380 located at 485 Wentworth Ave isolated due to broken riser to the cut out. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6309 | 2005 | 3 | 21 | 0.66319 |  | 54 | 13 | 14 | Lincoln Heights | 13.2kV | TD07 | Refused switch to transformer 0360 at 831 Edgeworth cause of outage unknown | Ottawa | Unknown/Other | No Apparent Cause
20288 | 2012 | 4 | 6 | 0.3125 |  | 142 | 19 | 8 | Lincoln | 13.2kV | TD07 | Transfomer PT13 at 2355 Carling was isolated to allow crew to replace dammaged transformer. 8 customers were affected for 142 minutes. Lincoln (TD07). ID# 20288 | Ottawa | Scheduled Outage | Preventive Maintenance
12294 | 2008 | 4 | 17 | 0.25 |  | 132 | 18 | 8 | Lincoln | 13.2kV | TD07 | Transformer X34684 at Carling & Richardson opened to allow crew to replace pole & transfer plant. | Ottawa | Scheduled Outage | Construction
14222 | 2009 | 4 | 26 | 0.91667 |  | 1059 | 2120 | 254 | Lincoln Heights | 13.2kV | TD07 | A tree on on the primary on Georgina and Rose wood caused two phases to open at S27571, TD07 was open via scada to allow the crew to close the three SMD200 fuses safetly. | Ottawa | Adverse Weather | Wind
12386 | 2008 | 5 | 4 | 0.11111 |  | 105 | 14 | 15 | Lincoln | 13.2kV | TD07 | Transformer on TD07 55C3B-0326 failed, customers were transferred to 55C3B-0328 also interupted to allow cut over | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5103 | 2004 | 5 | 5 | 0.4375 |  | 125 | 71 | 45 | TD | 13.2kV | TD07 | A hot line clamp at the dip to VT517 burned through the o/h conductor causing an outage to customers on that phase. Further repairs were required to the dip to VT517 after most customers were restored. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5104 | 2004 | 5 | 5 | 0.49167 |  | 15 | 127 | 507 | TD | 13.2kV | TD07 | A hot line clamp at the dip to VT517 burned through the o/h conductor requiring the cct to be opened to allow repairs to damaged conductor. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3455 | 2003 | 5 | 19 | 0.81736 |  | 78 | 4 | 3 | Lincoln Hts | 13.2kV | TD07 | A squirrel caused the fuse to blow at a xfmr affecting customers on Midway & Richardson | Ottawa | Foreign Interference | Animal
5181 | 2004 | 5 | 19 | 0.58264 |  | 46 | 1 | 1 | Lincoln Hts | 13.2kV | TD07 | VT521 13KV xfmr bus isolated to change a defective transformer in the vault. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20624 | 2012 | 5 | 27 | 0.625 |  | 5 | 1 | 11 | Lincoln | 13.2kV | TD07 | At 15:00, transformeer X26664 located at 235 Richardson Ave was openned up to allow crews to clear downed street light due to MVC. 11 customers affected for 5 minutes. Linconl Heights (TD07) ID #20624 | Ottawa | Foreign Interference | Vehicle
14481 | 2009 | 6 | 7 | 0.32292 |  | 142 | 17 | 7 | Lincoln Heights | 13.2kV | TD07 | Transformer #55C3B-0326 located at 2419 Georgina isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
12697 | 2008 | 6 | 19 | 0.59167 |  | 247 | 12 | 3 | Lincoln Heights | 13.2kV | TD07 | Transformer #55C2C-0280 located at 509 Hartleigh isolated due to bird contact | Ottawa | Foreign Interference | Bird
7008 | 2005 | 7 | 22 | 0.88056 |  | 112 | 13 | 7 | Lincoln | 4.16kV | TD07 | At Trans at 2394 Rosewood was refused due to squirrel contact power was restored | Ottawa | Foreign Interference | Animal
16604 | 2010 | 8 | 2 | 0.35833 |  | 52 | 9 | 10 | Lincoln Heights | 13.2kV | TD07 | Transformer X33075 at 61 McEwan refused due to animal contact - squirrel | Ottawa | Scheduled Outage | Repair
13039 | 2008 | 8 | 12 | 0.41319 |  | 5 | 1 | 8 | Lincoln Heights | 13.2kV | TD07 | Transformer #55C2C-0469 located at 405 Richardson Ave isolated to disconnect 2 O/H services. | Ottawa | Scheduled Outage | Preventive Maintenance
18941 | 2011 | 8 | 16 | 0.375 |  | 46 | 2 | 3 | Lincoln Heights | 13.2kV | TD07 | Transformer X33083 @ 513 Hartley was opened to allow crew to replace a service | Ottawa | Scheduled Outage | Preventive Maintenance
14995 | 2009 | 8 | 22 | 0.45 |  | 64 | 10 | 9 | Lincoln Heights | 13.2kV | TD07 | Trans at 429 Richardson ave was refused after Bird contact | Ottawa | Foreign Interference | Bird
19053 | 2011 | 8 | 30 | 0.43333 |  | 49 | 12 | 15 | LINCOLN | 13.2kV | TD07 | S21120 at the rear of 2443 Rosewood was opened to allow crew to remove limb from primary at 2408 Rosewood - 2 transformers interrupted | Ottawa | Tree Contacts | Tree Limb Fallen
16921 | 2010 | 9 | 10 | 0.68958 |  | 76 | 1 | 1 | Lincoln | 13.2kV | TD07 | Squirrel caused 2 transformers of three phase bank to open at 1290 Richmond. | Ottawa | Foreign Interference | Animal
7336 | 2005 | 9 | 16 | 0.48819 |  | 222 | 4 | 1 | TD | 13.2kV | TD07 | VT533 at 525 Wentworth was isolated for the customer to make emergency repairs to the secondary main switch | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16983 | 2010 | 9 | 22 | 0.58472 |  | 57 | 5 | 5 | Lincoln Heights | 13.2kV | TD07 | Transformer #X32925 located at 2440 Georgina opened by squirrel contact | Ottawa | Foreign Interference | Animal
16994 | 2010 | 9 | 24 | 0.80208 |  | 327 | 1506 | 330 | Lincoln Heights | 13.2kV | TD07 | Two phases fell at 2455 Rosewood causing switch S27571 to open. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16998 | 2010 | 9 | 25 | 0.42847 |  | 1083 | 18 | 1 | Lincoln | 13.2kV | TD07 | Defective PT1566 at 920 Parkhaven replaced by Oncall crew. Only the 1 customer, Whitehaven Public School, was affected. | Ottawa | Defective Equipment
17074 | 2010 | 10 | 7 | 0.38542 |  | 173 | 225 | 78 | Lincoln | 13.2kV | TD07 | A squirell contact on the primary overhead caused the white phase fuse of S27347 to blow and damaged 2 insulators | Ottawa | Foreign Interference | Animal
7438 | 2005 | 10 | 8 | 0.31389 |  | 51 | 6 | 7 | Lincoln Heights | 13.2kV | TD07 | Transformer switch at 2380 Georgina Dr opened due to tree branch contact | Ottawa | Tree Contacts | Inadequate Trimming
7439 | 2005 | 10 | 8 | 0.38194 |  | 95 | 11 | 7 | Lincoln Heights | 13.2kV | TD07 | Transformer switch at 2380 Georgina Dr opened due to defective fuse | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9417 | 2006 | 10 | 12 | 0.42361 |  | 25 | 3 | 8 | Lincoln Heights | 4.16kV | TD07 | Isolated transformer at 475 Richardson Rd for a service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
7464 | 2005 | 10 | 16 | 0.29236 |  | 99 | 16 | 10 | Lincoln Heights | 13.2kV | TD07 | Refused transformer at 2048 Knightsbridge .Outage was caused by Squirrel | Ottawa | Tree Contacts | Inadequate Trimming
17246 | 2010 | 11 | 8 | 0.77431 |  | 11 | 0 | 1 | Lincoln Heights | 13.2kV | TD07 | Crew opened the Reyrolle at VT517 to refuse dips to vault. | Ottawa | Unknown/Other
9653 | 2006 | 11 | 13 | 0.44722 |  | 231 | 81 | 21 | Lincoln Heights | 13.2kV | TD07 | Trf. # TP2883 located @ Edgeworth & mayflower for a service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
17274 | 2010 | 11 | 15 | 0.46042 |  | 67 | 11 | 10 | Lincoln Heights | 13.2kV | TD07 | Replaced blown fuse feeding transformer X33081 at 2318 Lawn Ave (Squirrel Contact) | Ottawa | Foreign Interference | Animal
19631 | 2011 | 11 | 24 | 0.49583 |  | 46 | 8 | 10 | Lincoln Heights | 13.2kV | TD07 | Transformer #X32927 located at 895 Dresden Cres opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
7680 | 2005 | 12 | 2 | 0.72569 |  | 173 | 288 | 100 | Lincoln | 13.2kV | TD07 | 150 E SMU20 fuses, 2 phases blew for no apparent reason, patrolled and refused | Ottawa | Unknown/Other | No Apparent Cause
7696 | 2005 | 12 | 7 | 0.41667 |  | 140 | 14 | 6 | Lincoln | 13.2kV | TD07 | Transformer #55C1D-0209 located opposite of 437 Edgeworth isolated to re-arrange plant | Ottawa | Scheduled Outage | Construction
15580 | 2009 | 12 | 28 | 0.010417 |  | 42 | 1 | 1 | Woodroffe | 13.2kV | TD07 | VT523 at 2410 Georgina was interrupted when S10698 was opened to reconnect lead to the overhead. Only the one customer, Woodroffe H.S., was affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6106 | 2004 | 12 | 29 | 0.41319 |  | 2 | 0 | 11 | Lincoln Heights | 13.2kV | TD07 | Disconnect customers service on transformer #55C1D-0080 At the rear of 2407 Rosewood | Ottawa | Scheduled Outage | Emergency Services Request
14829 | 2009 | 7 | 25 | 0.033333 |  | 8 | 105 | 784 | Lincoln | 13.2kV | TD08 | TD08 & TD12 circuits both tripped due to adverse weather. After calling Police and Fire no reports of anything in that area, closed both breakers and both held. | Nepean | Lightning
15866 | 2010 | 3 | 29 | 0.15347 |  | 109 | 18 | 10 | Lincoln Heights | 13.2kV | TD09 | Transformer fuse found opened on transformer # X35689. Fuse closed restoring all load | Ottawa | Unknown/Other | No Apparent Cause
11922 | 2008 | 1 | 10 | 0.45486 |  | 33 | 6 | 10 |  |  | TD12 | Transformer #KT0680 located at 3142 Dumaurier isolated to allow electrician to perform repairs | Ottawa | Scheduled Outage | Repair
15640 | 2010 | 1 | 10 | 0.30278 |  | 340 | 79 | 14 | Lincoln | 13.2kV | TD12 | KT527 transformer at 231 High was faulty and had to be isolated for replacement by on call crew | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17500 | 2011 | 1 | 20 | 0.67708 |  | 15 | 1 | 5 | Lincoln Heights | 13.2kV | TD12 | Trans at 954 ALENMEDE CRES: was isoloted in order to connect a new service | Ottawa | Scheduled Outage | Preventive Maintenance
4746 | 2004 | 1 | 30 | 0.21111 |  | 81 | 20 | 15 | Lincoln Heights | 13.2kV | TD12 | 24/7 Crews isolated KT548 due to a working fire at units 14,16, & 18 @ 2950 Pennys Dr. Crews reports secondary disconnected to units 14,16, & 18. Outage affected 15 customers. KT548 restored to normal after services disconnected to 14,16, & 18. | Ottawa | Adverse Environment | Fire
4759 | 2004 | 2 | 3 | 0.87847 |  | 25 | 6 | 15 | TD | 13.2kV | TD12 | KT548 at 2950 Penny was opened to make repairs to secondary connections. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6204 | 2005 | 2 | 12 | 0.56597 |  | 33 | 11 | 20 | Lincoln Hieghts | 13.2kV | TD12 | Streng reports squirel found to base of transformer. Fuse reports all power restored. | Ottawa | Foreign Interference | Animal
10019 | 2007 | 2 | 13 | 0.375 |  | 13 | 3 | 12 | Lincoln Heights | 13.2kV | TD12 | Isolated transformer KT0669 at 1064 Alenmede Cres to disconnect service to grow house | Ottawa | Foreign Interference | Vandalism
12054 | 2008 | 2 | 18 | 0.98681 |  | 150 | 96 | 48 | Linclon Heights | 13.2kV | TD12 | 4 transformer out on Alenmede cresent and Barwell Avenue. Bad underground cable from PPH to KT674. Staged restoration. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12066 | 2008 | 2 | 20 | 0.46528 |  | 157 | 37 | 14 | Lincoln | 13.2kV | TD12 | Customers on Alanmede cr fed from KT668 callied in after crew performed switching to isolate a cable section from KT668 to riser pole. It was later found that the cables in KT668 were incorrectly identified ( nomenclature reversed ). | Ottawa | Human Element | Commissioning Errors
10062 | 2007 | 2 | 26 | 0.42361 |  | 15 | 4 | 14 | Lincoln Heights | 13.2kV | TD12 | Isolated KT 677 at 977 Barwell Dr to replace blown fuse in live front ped 677P2 for underground service to 800 Torsa Court | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12082 | 2008 | 2 | 27 | 0.44792 |  | 75 | 14 | 11 | Lincoln Heights | 13.2kV | TD12 | Transformer #KT686 located at 19 Noren Ave isolated to replace defective secondary mole | Ottawa | Scheduled Outage | Repair
20075 | 2012 | 2 | 28 | 0.65 |  | 409 | 143 | 41 | Lincoln | 13.2kV | TD12 | A flash barrier board at transformer KT662 @ 3076 DUMAURIER AVE caused switch S28265 to blow causing outages to three transformers. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15755 | 2010 | 3 | 1 | 0.34167 |  | 36 | 5 | 8 | LINCOLN HEIGHTS | 13.2kV | TD12 | Transformer X32734 at rear of 2917 Highland Cres isolated to allow for removal of tree limb | Ottawa | Tree Contacts | Tree Limb Fallen
4864 | 2004 | 3 | 5 | 0.36458 |  | 15 | 4 | 18 | LINCOLN | 13.2kV | TD12 | TRANSFORMER K551 WAS OPENED TO DISCONNECT METER BASE AT 108 PENNY DR. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
4865 | 2004 | 3 | 5 | 0.47917 |  | 15 | 4 | 18 | LINCOLN | 13.2kV | TD12 | TRANSFORMER K551 WAS OPENED TO RECONNECT METER BASE AT 108 PENNY DR. | Ottawa | Defective Equipment
8010 | 2006 | 3 | 10 | 0.82986 |  | 68 | 1 | 1 | Lincoln | 13.2kV | TD12 | Crew isolated 13kv distribution vault VT877 at 838 pinecrest to replace defective overhead switch. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6272 | 2005 | 3 | 12 | 0.65208 |  | 47 | 7 | 9 | Lincoln Heights | 13.2kV | TD12 | A squirrel took out the fuse that feeds transformer OTT3140 @ 2966 Richmond Rd. | Ottawa | Foreign Interference | Animal
8040 | 2006 | 3 | 17 | 0.25833 |  | 8 | 114 | 854 | Lincoln | 13.2kV | TD12 | TD12 circuit tripped, reclosure was out of service. Breaker closed manually from SCADA. Blown Lightning arrestor at 2929 carling feeding PT180 caused the outage. | Ottawa | Unknown/Other
8041 | 2006 | 3 | 17 | 0.38542 |  | 25 | 0 | 1 | Lincoln | 13.2kV | TD12 | Blown Lightning arrestor at 2929 carling feeding PT180 was replaced. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
12167 | 2008 | 3 | 22 | 0.31458 |  | 91 | 12 | 8 | Lincoln Heights | 13.2kV | TD12 | At 7:33am, customers at transformer KT681 on Richmond Rd, called in reports of no power. 24-7 dispatched and discovered a broken cutout at pole #41. Crews repaired broken cutout and all power restored to the 8 customers affected for 91mins. ID#12167. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6328 | 2005 | 3 | 26 | 0.46806 |  | 119 | 2 | 1 | Lincoln | 13.2kV | TD12 | 13 kv vault VT805 at 2929 Carling interrupted to remove squirrels from vault, inspect equipment & refuse Reyrolle. | Ottawa | Foreign Interference | Animal
4948 | 2004 | 3 | 30 | 0.53125 |  | 15 | 5 | 21 | Lincoln Heights | 13.2kV | TD12 | KT0547 at 2949 Penny Dr. was isolated to allow crew to replace lid on KT. | Ottawa | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
14140 | 2009 | 4 | 3 | 0.375 |  | 12 | 1 | 5 | Lincoln Heights | 13.2kV | TD12 | Transformer #X35367 located at 2868 Haughton isolated for a service removal | Ottawa | Scheduled Outage | Preventive Maintenance
12276 | 2008 | 4 | 14 | 0.39583 |  | 11 | 1 | 4 | LINCOLN HEIGHTS | 13.2kV | TD12 | Transformer #X35695 at 37 Boyce isolated to allow for new service | Ottawa | Scheduled Outage | Construction
14247 | 2009 | 4 | 26 | 0.70347 |  | 1341 | 2817 | 854 | Lincoln | 13.2kV | TD12 | TD12 breaker was opened manually from SCADA due to a report of a transformer fire on Scrivens, hanging wires on Scrivens and lines down & sparking on Croft. 2 damaged line sections were isolated from the main line on Croft and circuit was re-energized. Repairs were made later to remove trees and repair downed conductor. | Ottawa | Adverse Weather | Wind
18107 | 2011 | 5 | 6 | 0.375 |  | 80 | 21 | 16 | Lincoln Heights | 13.2kV | TD12 | Isolated transformer X35632 at 111 Scrivens St to replace secondary service | Ottawa | Scheduled Outage | Emergency Services Request
5116 | 2004 | 5 | 7 | 0.57292 |  | 15 | 5 | 19 | Lincolin | 13.2kV | TD12 | Transformer KT543 isolated to reconnect arrears for unit 3 at 111 Ritchie. | Ottawa | Unknown/Other | No Apparent Cause
5125 | 2004 | 5 | 10 | 0.40625 |  | 5 | 2 | 21 | Lincoln | 13.2kV | TD12 | Transformer at 117 Ritchie interrupted to reconnect to service to Unit #1 | Ottawa | Scheduled Outage | Construction
8279 | 2006 | 5 | 11 | 0.67708 |  | 10 | 3 | 20 | Lincoln | 13.2kV | TD12 | Transformer was opened to transfer plant to 3 new poles | Ottawa | Scheduled Outage | Construction
6548 | 2005 | 5 | 12 | 0.32569 |  | 266 | 27 | 6 | Lincoln Heights | 13.2kV | TD12 | Isolated Transformer # 690 at 1112 Grenon to replace the transformer | Ottawa | Scheduled Outage | Preventive Maintenance
14376 | 2009 | 5 | 19 | 0.42708 |  | 15 | 6 | 26 | Lincoln Heights | 13.2kV | TD12 | Transformer #KT543 located at 109 Ritchie St isolated for arrears disconnect | Ottawa | Unknown/Other | Construction
14377 | 2009 | 5 | 19 | 0.44444 |  | 10 | 3 | 18 | Lincoln Heights | 13.2kV | TD12 | Transformer #KT538 located at 103 Ritchie St isolated for an arrears disconnect | Ottawa | Unknown/Other | Construction
14378 | 2009 | 5 | 19 | 0.46528 |  | 9 | 3 | 17 | Lincoln Heights | 13.2kV | TD12 | Transformer #KT535 located at 77 Ritchie isolated for an arrears disconnect. | Ottawa | Unknown/Other | Construction
5207 | 2004 | 5 | 25 | 0.46875 |  | 111 | 30 | 16 | Lincoln Hts | 13.2kV | TD12 | KT540 on Ritchie St was hit by a vehicle and shifted on its pad. KT535 was found to be arcing from primary to enclosure when crew went there to isolate KT540. Both KT535 & KT540 were isolated for repairs affecting 16 customers on Ritchie. Customers who were home were advised prior to shut down. | Ottawa | Foreign Interference | Vehicle
8352 | 2006 | 5 | 25 | 0.65278 |  | 11 | 3 | 16 | Lincoln Heights | 13.2kV | TD12 | Isolated transformer KT528 at 855 Grenon Ave to access live front Ped PT528 to repaire underground service | Ottawa | Scheduled Outage | Repair
8357 | 2006 | 5 | 26 | 0.58125 |  | 48 | 7 | 9 | Lincoln | 13.2kV | TD12 | Transformer #OTT3140 located at 943 Lovitt isolated probably due to animal contact | Ottawa | Foreign Interference | Animal
20676 | 2012 | 6 | 2 | 0.375 |  | 212 | 21 | 6 | Lincoln | 13.2kV | TD12 | Transformer #KT738 located at 2949 Richmond Rd opened up due to broken drop lead. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3649 | 2003 | 6 | 9 | 0.53472 |  | 10 | 0 | 10 | Lincoln Heights | 13.2kV | TD12 | At 12:50pm the transformer at 19 Noreen Street in West Ottawa was opened to make repairs. 10 customers were interrupted, power was restored at 1:00pm. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12583 | 2008 | 6 | 9 | 0.57569 |  | 56 | 37 | 40 | Lincoln | 13.2kV | TD12 | TD12 curcuit auto/reclosed due to faulted cable termination, switch and arrestor on the B phase cable at 109 Ritchie. Switch burnt and txs KT443 & KT549 had to be back fed through tx loop. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16248 | 2010 | 6 | 11 | 0.14375 |  | 133 | 29 | 13 | Lincoln Heights | 13.2kV | TD12 | Switch S26100 @ Carling/Oakley was opened to allow on-call crews to make temporary repairs to pole @ 53 Oakley damaged by pole fire. | Ottawa | Scheduled Outage | Repair
18387 | 2011 | 6 | 11 | 0.33333 |  | 85 | 7 | 5 | Lincoln Heights | 13.2kV | TD12 | Replaced blown fuse for transformer X35649 at 18 Wylie Ave (squirrel contact) | Ottawa | Foreign Interference | Animal
8471 | 2006 | 6 | 12 | 0.29514 |  | 119 | 18 | 9 | Lincoln | 13.2kV | TD12 | Transformer #OTT3140 located at 2927 Highfield isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
20751 | 2012 | 6 | 12 | 0.95972 |  | 626 | 2594 | 1575 | Lincoln | 13.2kV | TD12 | Pole fire at 3009 Carling Ave caused significant damage to the pole and dip to PT138. TD12 breaker had to be opened twice to allow crews to establish their work permit safely. | Ottawa | Adverse Environment | Fire
20761 | 2012 | 6 | 13 | 0.40625 |  | 239 | 120 | 33 | Lincoln | 13.2kV | TD12 | customer reported outage, crews found defective switch at DIP feeding KT679 & repaired. Upon restore Fuse blew, crews hipoted cable and found defective cable from KT677 to KT680. cable section isolated and all power restored | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12624 | 2008 | 6 | 14 | 0.28403 |  | 76 | 9 | 7 | Lincoln Heights | 13.2kV | TD12 | Replaced blown fuse on transformer X6814 at 22 Wylie Ave cause of outage Squrrel contact | Ottawa | Foreign Interference | Animal
14553 | 2009 | 6 | 17 | 0.25278 |  | 153 | 13 | 5 | TD12 | 13.2kV | TD12 | Transformer #X35392 located 2855 Ahearn isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
18461 | 2011 | 6 | 22 | 0.40208 |  | 51 | 6 | 7 | Lincoln Heights | 13.2kV | TD12 | Transformer #X35381 located at 2828 Grandeur Ave opened up due to branch contact on h1 bushing. | Ottawa | Tree Contacts | Tree Limb Fallen
20868 | 2012 | 6 | 25 | 0.54514 |  | 105 | 10 | 6 | Lincoln | 13.2kV | TD12 | Isolated transformer KT0738 at 2949 Richmond Rd for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
8591 | 2006 | 6 | 26 | 0.27778 |  | 130 | 20 | 9 | Lincoln | 13.2kV | TD12 | Transformer #OTT3140 located at 2911 Highfield isolated due to squirrel interference. | Ottawa | Foreign Interference | Animal
16350 | 2010 | 6 | 28 | 0.70486 |  | 182 | 124 | 41 | Lincoln | 13.2kV | TD12 | Broken cutout at S28265 was replaced on Alenmede. | Ottawa | Defective Equipment
14667 | 2009 | 7 | 4 | 0.8 |  | 84 | 14 | 10 | Lincoln |  | TD12 | Squirrel contact caused transformer fuse to blow at 2911 Highfield. Transformer refused successfully. | Ottawa | Foreign Interference | Animal
6877 | 2005 | 7 | 6 | 0.47917 |  | 43 | 612 | 854 | Lincoln | 13.2kV | TD12 | Tree at Richmond rd. and Grenon caused the phases on the overhead circuit to slap together and opened the TD12 circuit. Also fuses on adjacent pole feeding a lateral opened. | Ottawa | Tree Contacts | Tree Fallen
10807 | 2007 | 7 | 6 | 0.39583 |  | 132 | 139 | 63 | Lincoln Heights | 12/7.2kV | TD12 | At 09:30 trans at 2950 Penny Dr was isolated in order to make repairs to sec connections | Ottawa | Scheduled Outage
5461 | 2004 | 7 | 7 | 0.74236 |  | 50 | 8 | 9 | Lincoln | 13.2kV | TD12 | Squirrel caused transformer at 2995 walters to open feeding 9 customers. | Ottawa | Foreign Interference | Animal
6883 | 2005 | 7 | 7 | 0.26389 |  | 108 | 16 | 9 | Lincoln Heights | 13.2kV | TD12 | Switch to transformer OTT3140 at 2927 Highfield Cres opened due to squirrel contact | Ottawa | Foreign Interference | Animal
3716 | 2003 | 7 | 10 | 0.40486 |  | 10 | 3 | 19 | Lincoln Heights | 13.2kV | TD12 | KT551 was isolated by crew to make repairs. 19 customers affected in outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6927 | 2005 | 7 | 14 | 0.06875 |  | 57 | 811 | 854 | Lincoln | 13.2kV | TD12 | 5407, 5408 & TD12 circuits were interrupted in order to remove skywire that had fallen between the circuits. See ID #6926 for 5407 & 5408. TD12 white phase fuse blew on Richmond Rd at Marielle. | Ottawa | Adverse Weather | Lightning
12833 | 2008 | 7 | 14 | 0.3 |  | 88 | 10 | 7 | Lincoln Heights | 27.6/16kV | TD12 | At 08:40 trans at 128 Doane was refused and power restored due to squirrel contact | Ottawa | Foreign Interference | Animal
6975 | 2005 | 7 | 16 | 0.78681 |  | 907 | 702 | 300 | Lincoln Hts | 13.2kV | TD12 | Lightning caused fuses to blow on all 3 phases on Richmond Rd. and 2 phases at Richmond & Grennon. Transformer behind 16 Noren defective with broken bushing. Main line refused, transformer cleared and 2 phases refused at Grennon. Transformer left for replacement later due to other calls. | Ottawa | Lightning | Direct Strike
12913 | 2008 | 7 | 22 | 0.39097 |  | 20 | 7 | 20 | Lincoln Heights | 13.2kV | TD12 | Transformer #KT661 located at 2969 Richmond Rd isolated due to disconnecting service | Ottawa | Scheduled Outage | Construction
3802 | 2003 | 7 | 23 | 0.38611 |  | 89 | 12 | 8 | Lincoln Hts | 13.2kV | TD12 | Fuse blew due to a bird at transformer @ 2589 Ahearn affecting 8 customers. | Ottawa | Foreign Interference | Bird
12938 | 2008 | 7 | 25 | 0.38889 |  | 90 | 6 | 4 | Lincoln Heights | 4.16kV | TD12 | Transformer #X32638 located at the corner of Richmond Rd & Lovitt Rd isolated to transfer load. | Ottawa | Scheduled Outage | Preventive Maintenance
14830 | 2009 | 7 | 25 | 0.033333 |  | 8 | 153 | 1149 | Lincoln | 13.2kV | TD12 | TD08 & TD12 circuits both tripped due to adverse weather. After calling Police and Fire no reports of anything in that area, closed both breakers and both held. | Nepean | Lightning
14866 | 2009 | 7 | 28 | 0.18403 |  | 95 | 13 | 8 | Lincoln | 13.2kV | TD12 | Tree limb brought down neutral on secondary bus and open wire service @ corner of Ritchie and Ahearn. | Ottawa | Tree Contacts | Tree Limb Fallen
3820 | 2003 | 7 | 30 | 0.94375 |  | 5 | 71 | 850 | Lincoln | 13.2kV | TD12 | A blown pot head on 5409 caused by a racoon occurred the same time as this interuption indicating it may be related. | Ottawa | Foreign Interference | Animal
12995 | 2008 | 8 | 3 | 0.34375 |  | 652 | 78 | 16 | Lincoln | 13.2kV | TD12 | KT538 at 100 Ritchie was interrupted to disconnect secondary cables and pedestals P1 & P2 to make repairs to damaged cables. At 15:34, KT538 was interrupted to restore all but the remaining 2 damaged services out of P1 (87 Unit 1 & 100 Unit 3) . After repairs were made KT538 was interrupted again to reconnect these 2 services. | Ottawa | Foreign Interference | Dig-in
16766 | 2010 | 8 | 18 | 0.39722 |  | 64 | 5 | 5 | Lincoln TS | 13.2kV | TD12 | KT456 at 45 Oakley Ave. Was isolated to allow crews to repair a defective insulator. | Ottawa | Scheduled Outage | Repair
7211 | 2005 | 8 | 25 | 0.5 |  | 54 | 5 | 6 | Lincoln Heights | 13.2kV | TD12 | Isolated Transformer # 2848 at 2884 Grandeur to change a service | Ottawa | Scheduled Outage | Preventive Maintenance
16807 | 2010 | 8 | 25 | 0.38333 |  | 66 | 10 | 9 | Lincoln TS | 13.2kV | TD12 | KT 531 at 878 Grenon Ave was isolated to allow crews to replace broken insulators. | Ottawa | Scheduled Outage | Repair
15012 | 2009 | 8 | 26 | 0.69444 |  | 25 | 3 | 8 | Lincoln Heights | 13.2kV | TD12 | Transformer #KT548 located at 2950 Penny Dr isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
5737 | 2004 | 8 | 28 | 0.46458 |  | 211 | 4 | 1 | Lincoln | 13.2kV | TD12 | Crew found 1fuse blown to 3 phase 13 kv padmount PT180 at 2930 Carling (Swiss Chalet). Cable & transfomer checked out OK and transfomer was refused successfully. Cause for blown fuse unknown. Crew had to be re-routed while retrieving a fuse from Carling due to Fire Call at 267 O'Connor. ID # | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16947 | 2010 | 9 | 15 | 0.45486 |  | 68 | 15 | 13 | Lincoln heights | 13.2kV | TD12 | KT691 isolated from all Hydro Ottawa sources to allow crews to replace defective cable. | Ottawa | Scheduled Outage | Repair
4137 | 2003 | 9 | 23 | 0.47569 |  | 30 | 4 | 7 | Lincoln |  | TD12 | Transformer at 2583 Ahearn was opened to allow Bell Canada to perform pole testing | Ottawa | Scheduled Outage
4138 | 2003 | 9 | 23 | 0.49306 |  | 15 | 2 | 8 | Lincoln | 13.2kV | TD12 | Transformer at 2589 Ahearn was opened to allow Bell Canada to perform pole testing | Ottawa | Scheduled Outage
11415 | 2007 | 9 | 28 | 0.73472 |  | 12 | 2 | 10 | Lincoln Hieghts | 13.2kV | TD12 | Transformer #KT00543 at 109 Ritchie St. isolated to allow for reconnection for Revenue Dept | Ottawa | Scheduled Outage | Repair
11468 | 2007 | 10 | 4 | 0.50208 |  | 12 | 4 | 20 | Lincoln Heights | 13.2kV | TD12 | Transformer #KT0535 located at 77 Ritchie St isolated to reconnect service for arrears | Ottawa | Scheduled Outage | Construction
11482 | 2007 | 10 | 9 | 0.40139 |  | 85 | 31 | 22 | Lincoln Heights | 13.2kV | TD12 | PC10A# 1772 issued by Jeff Magee on Ahearn, Croft and Haughton St. to check if poles are rotten with Bell Canada. | Ottawa | Unknown/Other
9474 | 2006 | 10 | 20 | 0.34444 |  | 84 | 13 | 9 | Lincoln Heights | 13.2kV | TD12 | Transformer #OTT3140 located at 943 Lovitt Rd was isolated by squirrel contact. | Ottawa | Foreign Interference | Animal
15282 | 2009 | 10 | 20 | 0.63194 |  | 10 | 3 | 17 | Lincoln Heights | 13.2kV | TD12 | Transformer #KT535 located at 79 Ritchie St isolated to reconnect unit #6 (was disc for non pymt) | Ottawa | Unknown/Other | No Apparent Cause
15283 | 2009 | 10 | 20 | 0.66667 |  | 10 | 3 | 18 | Lincoln Heights | 13.2kV | TD12 | Transformer #KT538 located at 103 Ritchie St isolated to reconnect Unit #3 that was disconnected for non pymt | Ottawa | Unknown/Other | No Apparent Cause
15290 | 2009 | 10 | 22 | 0.99167 |  | 114 | 304 | 190 | Lincoln Heights | 13.2kV | TD12 | At 23:48 dip pole switches KT544 & KT548 at 2958 Michele Drive were found blown and broken. Crews isolated at S12240 which affected 60 more customers. Lincoln Heights (TD12) ID#15290 | Nepean | Defective Equipment | Equipment Deterioration Due to Age
4345 | 2003 | 10 | 26 | 0.59722 |  | 30 | 2 | 4 | TD | 13.2kV | TD12 | Tx 6818 @ 70 Wylie was opened to repair a leaking cut -out after a pole fire. 4 customers affected at Carling & Wylie. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7530 | 2005 | 10 | 27 | 0.78403 |  | 157 | 21 | 8 | Lincoln | 13.2kV | TD12 | 24/7 crew report either bad elbow or bad bus bar in KT0679 at 1120 Grenon Ave. Isolated for future repairs and power restored. | Ottawa | Defective Equipment
11621 | 2007 | 10 | 29 | 0.54514 |  | 5 | 0 | 6 | Lincoln Heights | 13.2kV | TD12 | Isolated transformer KT661 at 2965 Richmond Rd to disconnect service | Ottawa | Scheduled Outage | Emergency Services Request
9563 | 2006 | 10 | 30 | 0.39583 |  | 118 | 2 | 1 | Lincoln Heights | 13.2kV | TD12 | A blown W phase fuse was found in the reyrolle switch at VT805, 2929 Carling. The fuse was found in pieces inside the switch. There was no apparent cause for the fuse to fail. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7593 | 2005 | 11 | 11 | 0.50694 |  | 100 | 10 | 6 | Lincoln Heights | 13.2kV | TD12 | Transformer KT690 at 1112 Grenon was isolated to replace elbows | Ottawa | Scheduled Outage | Repair
11730 | 2007 | 11 | 16 | 0.90208 |  | 126 | 40 | 19 | LINCOLN | 13.2kV | TD12 | PPH Switch feeding KT661 blew, due to tree branches engulfed around cable and switch. Tree branches trimmed and power restored. | Ottawa | Tree Contacts
13636 | 2008 | 11 | 18 | 0.42708 |  | 160 | 43 | 16 | Lincoln Heights | 13.2kV | TD12 | Isolated transformer X32745 at 926 Pinewood Cres for pole replacement | Ottawa | Scheduled Outage | Construction
9697 | 2006 | 11 | 21 | 0.57431 |  | 76 | 39 | 38 | Lincoln Heights | 13.2kV | TD12 | 3 Kiosk KT668, KT662 & KT678 reports power outage. M. Irven reports KT668 transformer maybe defective. KT 668 secondary opened, and KT668 fuse at pole # 36 closed restoring KT662 & KT678. Transformer @ KT668 tested and no fault found on transformer at KT668. KT668 secondary fuse closed restoing all load @ 14:10. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17351 | 2010 | 11 | 28 | 0.39306 |  | 296 | 455 | 454 | Lincoln TS |  | TD12 | TD 12 circuit, blue phase opened up at S22871 on Richmond Rd. Upon patrolling the O/H line, it was found that S28265 blue phase was also opened. Crews found this switch to be burned up. The cause was found to be a blown insulator on the blue phase at KT662 located at the rear of 1037 Barwell Cres. 24/7 made repairs to O/H switch S28265, isolated KT662 & restored power. On call crews were brought in to make repairs to KT662. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17376 | 2010 | 12 | 3 | 0.73958 |  | 245 | 8 | 2 | Lincoln Heights | 13.2kV | TD12 | At 17:45 crews isolated PT177 at 46 Farrow to change at transformer hit by a car. 2 customers affected for 245mins. Lincoln Heights TD12 ID# 17376 | Ottawa | Foreign Interference | Vehicle
6093 | 2004 | 12 | 23 | 0.96875 |  | 760 | 714 | 75 | TD | 13.2kV | TD12 | Internal flash at kt664 at 1077 Barwell caused dip switch to open, 7 transformers off. Cables hi-potted & transformers picked up one at a time. Defective barrier board found at kt664, same removed. Also replaced blown fuse at KT664 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15586 | 2009 | 12 | 29 | 0.2875 |  | 121 | 24 | 12 | Lincoln | 13.2kV | TD12 | I. McEwan reports fuse found opened at S27355 which feeds KT526 @ 18 Moore St.. Fuse replaced and all power restored. | Ottawa | Adverse Weather | Wind
17457 | 2010 | 12 | 29 | 0.39792 |  | 62 | 4 | 16 | Lincoln | 13.2kV | TD12 | Transformer X32745 at 878 Pinewood Cresent was isolated to allow crew to replace defective cut out. | Ottawa | Defective Equipment
15594 | 2009 | 12 | 30 | 0.1875 |  | 55 | 10 | 11 | Lincoln Heights | 13.2kV | TD12 | Customers report sparking wires, Crews report S29529 defective and replaced on Scrivens at Haughton.Lincoln Hieghts, (TD12) ID #15594 | Ottawa | Defective Equipment
15595 | 2009 | 12 | 30 | 0.34167 |  | 88 | 10 | 7 | Lincoln Heights | 13.2kV | TD12 | S27355 re-fused after crew found and replaced a leaking arrestor. 7 customers affected on Moore Ave. TD12 circuit. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7814 | 2006 | 1 | 17 | 0.41528 |  | 122 | 20 | 10 | Lincoln | 13.2kV | TD14 | Tony Taylor had a transformer (no #) out to relocate a secondary service in the rear of 347 Zepher | Nepean | Scheduled Outage | Repair
19853 | 2012 | 1 | 18 | 0.027083 |  | 706 | 471 | 40 | Lincoln Heights | 13.2kV | TD14 | S16295 O/H fuse opened due to a tree falling on the O/H wires and breaking a pole at 2708 Violet. | Ottawa | Tree Contacts | Tree Fallen
19859 | 2012 | 1 | 18 | 0.55903 |  | 25 | 4 | 10 | Lincoln Heights | 13.2kV | TD14 | transformer in rear of 2679 Regina was isolated to make repaires to service wires. 10 customers affected for 25 minutes | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7871 | 2006 | 1 | 30 | 0.41667 |  | 70 | 12 | 10 | Lincoln | 13.2kV | TD14 | Transformer KT0703 at 18 Richlin Cres was isolated to do maitenance work | Ottawa | Scheduled Outage | Preventive Maintenance
7882 | 2006 | 2 | 2 | 0.40278 |  | 70 | 12 | 10 | Lincoln | 13.2kV | TD14 | Transformer KT0703 at 160 Lincoln Heights was isolated to restore service to normal | Ottawa | Scheduled Outage
17555 | 2011 | 2 | 5 | 0.53542 |  | 187 | 87 | 28 | Lincoln Heights | 13.2kV | TD14 | Squirrel contact caused switch S21991 on Don st. To open. Switch fed 3 blue phase overhead transformers feeding customers on Zephyr, Howe and Britannia | Ottawa | Foreign Interference | Animal
19996 | 2012 | 2 | 9 | 0.88125 |  | 46 | 11 | 14 | Lincoln | 13.2kV | TD14 | Transformer X34675 at 2711 Marie St. refused - animal contact | Ottawa | Foreign Interference | Animal
13949 | 2009 | 2 | 11 | 0.32639 |  | 47 | 8 | 10 | LINCOLN HEIGHTS | 13.2kV | TD14 | xfmr located between 343 Zephyr & 352 Britannia Rd refused due to animal contact - squirrel | Ottawa | Foreign Interference | Animal
20001 | 2012 | 2 | 11 | 0.70833 |  | 15 | 4 | 14 | Lincoln | 13.2kV | TD14 | Transformer # X34675 @ 2711 Marie St was isolated to allow crews to replace hot line clamp. Customer were complaining of flickering lights. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3185 | 2003 | 2 | 12 | 0.99306 |  | 188 | 2533 | 880 | Lincoln Hieghts | 13.2kV | TD14 | TD14 circuit found opened at station. Possible cable fault between Dip#1 & Dip#2 on Carling ave. Cable section opened, and TD14 acb closed energizing circuit from station TD to Dip #1. TD00W closed at SC73 energizing overhead section to dip#2 on Carling. | Ottawa | Unknown/Other | No Apparent Cause
20023 | 2012 | 2 | 15 | 0.38194 |  | 45 | 10 | 14 | Lincoln | 13.2kV | TD14 | At 09:10am crew isolated Transformer X34675 to perform repairs on the transformer connections. 14 customers affected for 45mins. Lincoln Heights TD14 ID# 20023 | Ottawa | Scheduled Outage | Repair
17606 | 2011 | 2 | 18 | 0.42083 |  | 39 | 14 | 22 | Lincoln Heights | 13.2kV | TD14 | Jim Yeldon isolated transformer X35397 at 2712 Howe St. for a service upgrade | Ottawa | Scheduled Outage | Construction
20043 | 2012 | 2 | 21 | 0.40625 |  | 320 | 53 | 10 | Lincoln | 13.2kV | TD14 | Transformer #KT0709 located at 64 Winthrop Pvt opened by crew for electrician to replace main disconnect. | Ottawa | Scheduled Outage | Construction
14013 | 2009 | 2 | 27 | 0.36458 |  | 86 | 7 | 5 | Lincoln Heights | 13.2kV | TD14 | At 08:45 trans at 333 ZEPHYR AVE OTTAWA was isolated in order to replace a service | Ottawa | Scheduled Outage | Preventive Maintenance
20136 | 2012 | 3 | 7 | 0.37847 |  | 340 | 227 | 40 | Lincoln | 13.2kV | TD14 | An O/H section of TD14 red phase was opened to allow Hydro Ottawa crews to chang a pole that was broken in the windstorm on March 3, 2012 | Ottawa | Scheduled Outage | Repair
14101 | 2009 | 3 | 26 | 0.4375 |  | 120 | 8 | 4 | Russell | 13.2kV | TD14 | At 12:30 trans at 1662 Russell Rd was isolated in order to replace a trans | Ottawa | Scheduled Outage | Preventive Maintenance
12219 | 2008 | 4 | 1 | 0.87014 |  | 112 | 58 | 31 | Lincoln | 13.2kV | TD14 | Connection replaced on Jamieson. White phase S18861 replaced and fuse closed at Brittania and Rowatt. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8114 | 2006 | 4 | 6 | 0.46181 |  | 48 | 15 | 19 | Lincoln Heights | 13.2kV | TD14 | Transformer #55C1D-0186 located at 2700 Don St isolated to make secondary repairs | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15927 | 2010 | 4 | 12 | 0.4375 |  | 52 | 13 | 15 | LINCOLN HEIGHTS | 13.2kV | TD14 | Transformer X31944 at 2639 Priscilla St isolated to change triplex | Ottawa | Scheduled Outage | Repair
15938 | 2010 | 4 | 15 | 0.040278 |  | 32 | 4 | 8 | Lincoln Heights | 13.2kV | TD14 | 24/7 reports Racoon caused transformer fuse to blow at 2705 Don st. | Ottawa | Foreign Interference | Animal
12293 | 2008 | 4 | 17 | 0.20347 |  | 45 | 10 | 14 | Lincoln | 13.2kV | TD14 | Animal contact in the rear of 2711 Marie caused the fused cut out of the transformer X34675 to blow. TD14 out of Lincoln | Ottawa | Foreign Interference | Animal
12320 | 2008 | 4 | 22 | 0.40208 |  | 230 | 4 | 1 | Lincoln Heights | 13.2kV | TD14 | Replace a leaking transformer PT257 @ 2575 Bond St. | Ottawa | Defective Equipment
17987 | 2011 | 4 | 23 | 0.54931 |  | 71 | 14 | 12 | LINCOLN HEIGHTS | 13.2kV | TD14 | Refused transformer X35386 at 2711 Regina St. - squirrel contact | Ottawa | Foreign Interference | Animal
15990 | 2010 | 4 | 24 | 0.95625 |  | 78 | 21 | 16 | Lincoln | 13.2kV | TD14 | The overhead transformer at rear of 2696 Marie in Britannia was refused successfully. No positive cause was found, suspect animal contact. 16 customers on Marie St were affected. | Ottawa | Unknown/Other
14230 | 2009 | 4 | 25 | 0.92986 |  | 231 | 3003 | 780 | Lincoln | 13.2kV | TD14 | Downed primary lines, and trees on multiple circuits. Breaker opened by SCADA until runoffs isolated. | Ottawa | Adverse Weather
6475 | 2005 | 4 | 28 | 0.86458 |  | 43 | 9 | 13 | Lincoln | 13.2kV | TD14 | Transformer isolated at rear of 2712 Violet St due to animal contact (racoon) | Ottawa | Foreign Interference | Animal
16028 | 2010 | 5 | 2 | 0.68958 |  | 51 | 14 | 16 | Lincoln | 13.2kV | TD14 | crew refused transformer at 2696 Marie, cause unkown. | Ottawa | Unknown/Other
20541 | 2012 | 5 | 19 | 0.75 |  | 483 | 56 | 7 | Lincoln | 13.2kV | TD14 | Transformer X29974 was found defective on Salina, Kehoe and Cascades. Hydro Ottawa on call crews had to replace the transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5219 | 2004 | 5 | 29 | 0.53681 |  | 52 | 5 | 6 | Lincoln | 13.2kV | TD14 | Probable animal contact caused transformer at 2688 Violet to open. | Ottawa | Foreign Interference | Animal
12494 | 2008 | 5 | 29 | 0.375 |  | 40 | 3 | 4 | Lincoln Heights | 13.2kV | TD14 | Transformer #X31949 located at 335 Zephyr isolated for service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
14427 | 2009 | 5 | 29 | 0.49931 |  | 71 | 21 | 18 | Lincoln Heights | 13.2kV | TD14 | Transformer #X31929 located rear of 2703 Conn isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
14434 | 2009 | 5 | 31 | 0.84028 |  | 70 | 5 | 4 | LINCOLN | 4.16kV | TD14 | Defective transformer switch at 244 Brittania. Switch replaced and power restored. | Ottawa | Defective Equipment
20672 | 2012 | 6 | 2 | 0.10486 |  | 197 | 82 | 25 | Lincoln | 13.2kV | TD14 | X31941 at 2647 Priscilla fuse blew for no apeart reason, crew re-fused. | Ottawa | Unknown/Other | No Apparent Cause
3521 | 2003 | 6 | 4 | 0.34306 |  | 144 | 14 | 6 | Lincoln Heights | 13.2kV | TD14 | Squirrel cause fuse to blow at 2047 Knightsbridge. Transformer was refused restoring power to all customers. | Ottawa | Foreign Interference | Animal
6673 | 2005 | 6 | 7 | 0.42569 |  | 54 | 7 | 8 | Lincoln Heights | 13.2kV | TD14 | Switch to Transformer at 2643 Priscilla opened due to tree contact on the secondary | Ottawa | Tree Contacts | Inadequate Trimming
20733 | 2012 | 6 | 10 | 0.36111 |  | 86 | 14 | 10 | Lincoln Heights | 13.2kV | TD14 | Replaced blown fuse feeding transformer X35375 at 2720 Rigina St (Squirrel contact) | Ottawa | Foreign Interference | Animal
20745 | 2012 | 6 | 12 | 0.325 |  | 82 | 10 | 7 | Lincoln | 13.2kV | TD14 | Transformer #X29961 located at 159 Kehoe St opened up due to squirrel interference | Ottawa | Foreign Interference | Animal
5331 | 2004 | 6 | 19 | 0.37431 |  | 51 | 9 | 11 | Lincoln | 13.2kV | TD14 | O/H transformer at 2696 Violet re-fused. Suspect tree may have contacted transfomer due to gusts of wind. | Ottawa | Foreign Interference | Animal
5332 | 2004 | 6 | 19 | 0.4125 |  | 38 | 7 | 11 | Lincoln | 13.2kV | TD14 | Suspect tree may have contacted transfomer due to gusts of wind. Tree branches close to circuit were trimmed & O/H transformer at 2696 Violet was re-fused a second time (see ID #5331). | Ottawa | Tree Contacts | Inadequate Trimming
16298 | 2010 | 6 | 19 | 0.75903 |  | 249 | 29 | 7 | Lincoln | 13.2kV | TD14 | A squirell contacted transformer X35683 causing fuse to blow. | Ottawa | Foreign Interference | Animal
20828 | 2012 | 6 | 22 | 0.30208 |  | 126 | 36 | 17 | Lincoln | 13.2kV | TD14 | Transformer #X31940 located at 2637 Don St opened up due to animal contact, animal guard installed | Ottawa | Foreign Interference | Animal
6806 | 2005 | 6 | 25 | 0.66319 |  | 980 | 490 | 30 | Lincoln | 13.2kV | TD14 | Large Tree limb fell across overhead at 2696 Marie taking out local fuse at Marie & Poulin. Were unable to contact Aspulnd. Crew had to remove tree. Crew removed enough to restore power by 08:15 | Ottawa | Tree Contacts | Tree Fallen
8590 | 2006 | 6 | 25 | 0.92361 |  | 55 | 10 | 11 | Lincoln | 13.2kV | TD14 | Racoon caused overhead transformer to open feeding customers on Don, Regina and Brittania. | Ottawa | Foreign Interference | Animal
12722 | 2008 | 6 | 25 | 0.29514 |  | 38 | 1 | 2 | Lincoln | 13.2kV | TD14 | Transformer PT258 isolated to disconnect service to 2583 Carling Ave. | Ottawa | Scheduled Outage
20869 | 2012 | 6 | 25 | 0.62153 |  | 157 | 701 | 268 | Lincoln |  | TD14 | The Lincoln TD14 Dip 1 W phase at 360 Croydon opened due to defective terminator | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10754 | 2007 | 6 | 28 | 0.42014 |  | 160 | 27 | 10 | Lincoln Heights | 13.2kV | TD14 | Isolated transformer 55C1B-0010 at 186 Bradford St to transfer services to new pole | Ottawa | Scheduled Outage | Construction
5438 | 2004 | 7 | 2 | 0.96528 |  | 15 | 2 | 10 | Lincoln Hts | 13.2kV | TD14 | Transformer 55CID-0396 at the rear of 300 britannia was taken out of service to replace a connection. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10773 | 2007 | 7 | 2 | 0.275 |  | 79 | 12 | 9 | Lincoln Heights | 13.2kV | TD14 | Fuse to Transformer 55C1B-0045 at 96 Britannia Rd was found blown due to squirrel contact | Ottawa | Foreign Interference | Animal
6880 | 2005 | 7 | 7 | 0.13472 |  | 81 | 18 | 13 | Lincoln Hts | 13.2kV | TD14 | Squirrel caused fuse to blow at transformer 55CID-0364, 2708 Regina affecting 13 customers on Britannia, Regina & Violet. Crew refused and restored power. | Ottawa | Foreign Interference | Animal
18605 | 2011 | 7 | 7 | 0.15486 |  | 62 | 10 | 10 | Lincon Heights | 13.2kV | TD14 | Fuse cut out found blown on transformer at 2730 Marie St due to animal contact. Fuse was replaced all power restored. | Ottawa | Foreign Interference | Animal
6895 | 2005 | 7 | 10 | 0.34722 |  | 20 | 1 | 2 | Lincoln Heights | 13.2kV | TD14 | Transformer located at 2765 Salina St isolated due to animal interference (bird) | Ottawa | Foreign Interference | Bird
16470 | 2010 | 7 | 14 | 0.50347 |  | 110 | 16 | 9 | Lincoln Heights | 13.2kV | TD14 | Transformers #X31948 and X31927 located at 396 and 404 Britannia opened by crew to make repairs, open buss was down | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8738 | 2006 | 7 | 16 | 0.28611 |  | 83 | 21 | 15 | Lincoln Heights | 13.2kV | TD14 | Fuse toTransformer 55C1B-0005 at 136 Bradford St was found blown due to a bird contact | Ottawa | Foreign Interference | Bird
5538 | 2004 | 7 | 20 | 0.79236 |  | 35 | 7 | 12 | Lincoln | 13.2kV | TD14 | O/H transfomer at 2707 Conn was re-fused. Suspect tree contact due to high winds. | Ottawa | Adverse Weather | Wind
10918 | 2007 | 7 | 20 | 0.47292 |  | 54 | 5 | 6 | Lincoln Heights | 13.2kV | TD14 | Crew found fuse blown on transformer 55C1B-0069 at 156 Kehoe St due to animal contact (Squirrel) | Ottawa | Foreign Interference | Animal
8809 | 2006 | 7 | 24 | 0.21458 |  | 66 | 28 | 25 | Lincoln Heights | 13.2kV | TD14 | A squirrel caused a line fuse & a transformer fuse at Marie & Brittania to open, fuse replaced | Ottawa | Foreign Interference | Animal
18811 | 2011 | 7 | 24 | 0.75625 |  | 117 | 21 | 11 | Lincoln Heights | 13.2kV | TD14 | Cuttout blown at transformer X35697 rear of 288 Britannia. No apparent cause. Refused and customers restored. | Ottawa | Unknown/Other | No Apparent Cause
12944 | 2008 | 7 | 25 | 0.82847 |  | 37 | 9 | 15 | LINCOLN HEIGHTS | 13.2kV | TD14 | Transformer fuse found blown @ transformer # X35683 at 87 Kirby st due to animal contact. | Ottawa | Foreign Interference | Animal
16579 | 2010 | 7 | 29 | 0.31528 |  | 36 | 8 | 13 | Lincoln Heights | 13.2kV | TD14 | Replaced blown fuse at the transformer X35675 at 142 Britannia Rd (Squirrel contact) | Ottawa | Foreign Interference | Animal
18855 | 2011 | 7 | 29 | 0.97153 |  | 276 | 28 | 6 | Lincoln Hieghts | 13.2kV | TD14 | Tree contact caused the cut out on transformer X24654 to blow. Lincoln (TD14) ID#18855. | Ottawa | Tree Contacts
5597 | 2004 | 8 | 1 | 0.29375 |  | 141 | 38 | 16 | TD | 13.2kV | TD14 | A squirrel caused the transformer fuse to open at 233 Britannia, | Ottawa | Foreign Interference | Animal
5603 | 2004 | 8 | 2 | 0.80556 |  | 38 | 18 | 28 | Lincoln | 13.2kV | TD14 | Tree contacted the transformer at 2649 Don st. | Ottawa | Tree Contacts | Inadequate Trimming
16750 | 2010 | 8 | 16 | 0.31667 |  | 73 | 1 | 1 | LINCOLN HEIGHTS | 13.2kV | TD14 | replaced fuses on red and white phase at PT0256 located at 2475 Regina Street | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3925 | 2003 | 8 | 21 | 0.99583 |  | 131 | 22 | 10 | TD | 13.2kV | TD14 | Tx OTT1657 at the rear of 2652 Don st opened during a storm. The fuse was replaced & load restored. | Ottawa | Adverse Weather | Rain
14984 | 2009 | 8 | 21 | 0.34861 |  | 88 | 7 | 5 | Lincoln Heights | 13.2kV | TD14 | Transformer #X32601 located at 42 Richlin isolated probably due to animal contact. | Ottawa | Foreign Interference | Animal
18992 | 2011 | 8 | 22 | 0.375 |  | 60 | 21 | 21 | Lincoln Heights | 13.2kV | TD14 | Isolated transformer X35397 at 2709 Violet St for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
11151 | 2007 | 8 | 24 | 0.44236 |  | 191 | 3 | 1 | Lincoln Heights | 13.2kV | TD14 | 3 phase dip pole switches to PT259 at 2475 Regina St in Ottawa found open, no apparent problems found, thunderstorm in the area. Switch refused and closed to restore. | Ottawa | Defective Equipment
3957 | 2003 | 8 | 27 | 0.61111 |  | 50 | 1 | 1 | lincoln | 13.2kV | TD14 | Opened 3 phase bank at 1451 richmond rd to replace a secondary wire that fell out of bushing on transformer.One customer interrupted. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16830 | 2010 | 8 | 28 | 0.775 |  | 104 | 42 | 24 | Lincoln |  | TD14 | Broken cutout feeding KT711 was replaced and power restored. | Ottawa | Defective Equipment
4011 | 2003 | 9 | 4 | 0.45486 |  | 55 | 11 | 12 | Lincoln | 13.2kV | TD14 | transformer opened on Priscilla to replaced connections at the transformer, unplanned repair. | Ottawa | Scheduled Outage | Repair
4012 | 2003 | 9 | 4 | 0.53125 |  | 15 | 0 | 2 | Lincoln | 13.2kV | TD14 | Transformer opened on Conn to perform planned maintenance on the transformer. | Ottawa | Scheduled Outage | Preventive Maintenance
4013 | 2003 | 9 | 4 | 0.49653 |  | 47 | 2 | 2 | Lincoln | 13.2kV | TD14 | Transformer was opened on Conn to perform planned maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
4049 | 2003 | 9 | 10 | 0.56944 |  | 20 | 4 | 12 | Lincoln Heights | 13.2kV | TD14 | Transformer KT0697 in rear of 213 Lincoln Hts was taken out of service due to a defective underground service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11281 | 2007 | 9 | 10 | 0.61458 |  | 57 | 10 | 10 | Lincoln Heights | 13.2kV | TD14 | The O/H from switch S16295 in behind 2699 Regina had to be isolated to remove a large tree that fell on the O/H | Ottawa | Tree Contacts | Tree Fallen
13278 | 2008 | 9 | 23 | 0.38542 |  | 42 | 7 | 10 | Lincon Hieghts | 13.2kV | TD14 | Refused switch feeding X29958 at 136 Bradford Street. | Ottawa | Foreign Interference | Bird
16987 | 2010 | 9 | 23 | 0.5625 |  | 30 | 2 | 5 | Lincoln Heights | 13.2kV | TD14 | Isolated transformer X31945 at 2704 Priscilla St to replace service | Ottawa | Scheduled Outage | Emergency Services Request
9334 | 2006 | 9 | 28 | 0.43264 |  | 47 | 16 | 20 | Lincoln Heights | 13.2kV | TD14 | Isolated transformer 55C1D-0176 at 2632 Don St to replace triplex service | Ottawa | Scheduled Outage | Repair
11457 | 2007 | 10 | 4 | 0.37153 |  | 21 | 5 | 15 | LINCOLN HEIGHTS | 13.2kV | TD14 | Transformer #x29958 (55C1B-0005) at 136 Bradford isolated for refusing of transformer due to bird interferrence | Ottawa | Foreign Interference | Bird
13340 | 2008 | 10 | 8 | 0.55208 |  | 79 | 17 | 13 | LINCOLN HEIGHTS | 13.2kV | TD14 | transformer #31942 located in the rear of 2692 Priscilla isolated to allow for repairs | Nepean | Scheduled Outage | Repair
15232 | 2009 | 10 | 8 | 0.39583 |  | 36 | 6 | 10 | Lincoln Heights | 13.2kV | TD14 | At 09:30 Trans KT699 at 284 LINCOLN HEIGHT was isolated for mmeter base repairs | Ottawa | Scheduled Outage | Repair
4250 | 2003 | 10 | 12 | 0.56806 |  | 47 | 9 | 12 | Lincoln | 13.2kV | TD14 | Blown transformer fuse due to squirrel contact. | Ottawa | Foreign Interference | Animal
4255 | 2003 | 10 | 14 | 0.86319 |  | 62 | 13 | 13 | Lincoln | 13.2kV | TD14 | Transformer at 2637 Don St refused restoring power to 13 customers, cause of outage was a racoon contact. | Ottawa | Foreign Interference | Animal
19441 | 2011 | 10 | 22 | 0.4 |  | 154 | 39 | 15 | Lincoln Heights | 13.2kV | TD14 | Transformer #X35679 located at 233 Britannia opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
13413 | 2008 | 10 | 23 | 0.17014 |  | 135 | 2 | 1 | Lincoln heights | 13.2kV | TD14 | PT259 @ 1545 Carling Ave was isolated to all crews to replace defective transformer | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17193 | 2010 | 10 | 30 | 0.5625 |  | 50 | 15 | 18 | Lincoln Heights | 13.2kV | TD14 | Replaced blown fuse feeding transformer X31946 at 2548 Regina St (squirrel contact) | Ottawa | Foreign Interference | Animal
19507 | 2011 | 10 | 31 | 0.38333 |  | 62 | 17 | 16 | Lincoln Heights | 13.2kV | TD14 | Replaced blown fuse in switch feeding transformer X32634 at 2696 Marie St (Cause unknown) | Ottawa | Unknown/Other | No Apparent Cause
9637 | 2006 | 11 | 10 | 0.57986 |  | 35 | 7 | 12 | Lincoln Heights | 12/7.2kV | TD14 | At 13:55 trans KT701 at 72 Lincoln Heights was isolated in order to reconnect sec / u/g service and remove cab tire | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5897 | 2004 | 11 | 17 | 0.43333 |  | 98 | 24 | 15 | Lincoln | 13.2kV | TD14 | Squirrel conatct at 55C1B-0005 at 138 Bradford | Ottawa | Foreign Interference | Animal
9784 | 2006 | 12 | 2 | 0.98958 |  | 13 | 3 | 15 | Lincoln Heights | 13.2kV | TD14 | O/H transformer was interrupted to disconnect service to 237 Britannia due to working fire. | Ottawa | Adverse Environment | Fire
19671 | 2011 | 12 | 3 | 0.63194 |  | 273 | 5 | 1 | Lincoln Heights | 13.2kV | TD14 | Transformer PT256 at 2475 Regina was isolated to allow crew to repalce defective transformer. 1 customer was affected for 273 minutes. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9815 | 2006 | 12 | 8 | 0.80556 |  | 46 | 8 | 11 | Lincoln Heights | 13.2kV | TD14 | John isolated TRF.#KT734 @ 73 Winthrop under PC10C # 751 to change sec. Main in building | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19711 | 2011 | 12 | 9 | 0.9625 |  | 49 | 15 | 18 | Lincoln Heights | 13.2kV | TD14 | Transformer X31933 @ 1290 Richmond opened due to tree contact. | Ottawa | Tree Contacts
9889 | 2006 | 12 | 28 | 0.58333 |  | 30 | 0 | 1 | Lincoln | 13.2kV | TD14 | Transformer #PT0259 located at 2545 Carling Ave isolated to change broken switch | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12589 | 2008 | 6 | 10 | 0.70556 |  | 34 | 4 | 7 | LINCOLN | 13.2kV | TD15 | 5401 circuit (TD15) tripped due to tree coming down at 31 McEwen 2 spans E of S18001. 5409 circuit also tripped, both lines run together. Tree cleared itself and breaker closed in to restore power. | Ottawa | Tree Contacts
18471 | 2011 | 6 | 23 | 0.39931 |  | 194 | 828 | 256 | Lincoln Hieghts | 13.2kV | TD15 | Vault VT513 @ 1071 Ambleside was isolated to allow contractor to perform customer vault maintenance. 256 customers were affected. Lincoln (TD15) | Ottawa | Scheduled Outage
17657 | 2011 | 3 | 1 | 0.51389 |  | 65 | 2 | 2 | Lincoln Heights | 13.2kV | TD17 | Isolated 3 phase pad mount transformer PT0019 at 2670 Queensview Dr to replace broken switch | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18465 | 2011 | 6 | 22 | 0.73611 |  | 56 | 63 | 69 | Lincoln Heights | 12/7.2kV | TD17 | TD17 breaker opend due to a bird in lines. 70 customers were affected for 54 minutes. 1 customer was affected for 2 minutes while crew trasfered to back up lin. | Ottawa | Foreign Interference | Animal
6799 | 2005 | 6 | 25 | 0.62917 |  | 2 | 2 | 62 | Lincoln | 12/7.2kV | TD17 | TD17 open storm in the area,closed via scada and holding. | Ottawa | Adverse Weather | Lightning
5307 | 2004 | 6 | 15 | 0.30486 |  | 26 | 1 | 3 | Woodroffe | 13.2kV | TD1TW | A squirrel caused a flashover at the riser pole for the overhead section on TD1TW circuit. | Ottawa | Foreign Interference | Animal
17894 | 2011 | 4 | 11 | 0.22292 |  | 16 | 265 | 993 | Lincoln |  | TD22 | At 5:21 AM TD22 CB tripped open cause remains unknown. Suppect bad weather due to strom blowing in the Ottawa area | Ottawa | Adverse Weather | Rain
17895 | 2011 | 4 | 11 | 0.22292 |  | 16 | 265 | 993 | Lincoln | 13.2kV | TD22 | At 5:21 AM TD22 tripped open. Cause remains unknown, suspect weather due to storm bowing trough Ottawa area | Ottawa | Adverse Weather | Rain
3937 | 2003 | 8 | 25 | 0.57361 |  | 46 | 6 | 8 |  |  | TD3 | Transformer OTT#4282 was isolated to allow for the repairs to a vault. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6101 | 2004 | 12 | 26 | 0.53819 |  | 25 | 5 | 11 | Lincoln | 12/7.2kV | TDO5 | Transformer at 2550 Hopkins isolated to replace defective triplex. | Ottawa | Defective Equipment
3341 | 2003 | 4 | 14 | 0.78125 |  | 105 | 1563 | 1250 | Bridlewood & Hazeldean | 27.6/16kV | Temp F1, 35F5 | A tree fell on the line along the propose extension on the south end of Terry Fox. Tree was removed and the circuit was restored locally at the station as it is not on the Scada system yet. | Kanata | Tree Contacts | Tree Fallen
8524 | 2006 | 6 | 20 | 0.79028 |  | 376 | 4248 | 2220 | Hinchey | 13.2kV | TH00, TH2UJ | TH12 breaker was caryying TH01 & TH11 feeders due to Hinchey Q bus outage. Breaker was closed manually from SCADA at 19:16. Later 3 fuses were found blown on TH11 at Scott & Pinhey due to a tree knocking a phase to the ground & resting on the other two. TH12 breaker was reopened form SCADA at 23:58 in an attempt to get fuses closed. Fuses would still not close & then the breaker wouldn't close from SCADA. Breaker was closed locally from the station & fuses were repaired & closed. | Ottawa | Lightning | Direct Strike
13843 | 2009 | 1 | 7 | 0.40278 |  | 35 | 2 | 3 | TH01 | 13.2kV | TH01 | Transformer #X33690 located at 337 Carleton Ave isolated to run new secondary | Ottawa | Scheduled Outage | Preventive Maintenance
17505 | 2011 | 1 | 21 | 0.44792 |  | 60 | 8 | 8 | HINCHEY | 13.2kV | TH01 | Transformer X34050 at 37 Western Ave. Isolated to allow for installation of new service | Ottawa | Scheduled Outage | Construction
19905 | 2012 | 1 | 26 | 0.54306 |  | 36 | 4 | 6 | Hinchey | 13.2kV | TH01 | X34144 at 30 Clearview isolated to allow crews to install new service. | Ottawa | Scheduled Outage | Construction
7868 | 2006 | 1 | 29 | 0.29861 |  | 135 | 146 | 65 | Hinchey | 13.2kV | TH01 | TH01 circuit auto reclosed. 24/7 report animal contact cause local fuse & switch to fail. | Ottawa | Foreign Interference | Animal
13912 | 2009 | 2 | 1 | 0.33681 |  | 158 | 16 | 6 | Hinchey | 13.2kV | TH01 | At 8:05am customers in the area of Oakdale & Island Park Drive called in with no power call, squirell contact, transformer refused and closed, power restored at 10:43am. Hinchey (TH01) ID#13912. | Ottawa | Foreign Interference | Animal
17573 | 2011 | 2 | 12 | 0.62292 |  | 58 | 11 | 11 | Hinchey | 13.2kV | TH01 | Transformer #X34232 at 395 Island Park Dr opened up due to squirell contact | Ottawa | Foreign Interference | Animal
15741 | 2010 | 2 | 24 | 0.36667 |  | 297 | 64 | 13 | Hinchey | 13.2kV | TH01 | The O/H line on Patirica was isolated by the crew to allow safe work area for the tree contractor. | Ottawa | Scheduled Outage | Preventive Maintenance
3275 | 2003 | 3 | 20 | 0.90347 |  | 448 | 4704 | 630 | Hinchey |  | TH01 | TH01 line tripped due to a pole fire on Scott at Rockhurst | Ottawa | Adverse Environment | Salt Spray
3289 | 2003 | 3 | 21 | 0.72917 |  | 30 | 4 | 7 | hinchey | 13.2kV | TH01 | Transformer opened @ 2 Caroline to make repairs to secondary. | Ottawa | Scheduled Outage
17749 | 2011 | 3 | 22 | 0.38542 |  | 85 | 8 | 6 | Hinchey | 13.2kV | TH01 | Transformer #X30495 located at 99 Gilchrist opened by crew for a service change over | Ottawa | Scheduled Outage | Construction
17766 | 2011 | 3 | 23 | 0.4375 |  | 10 | 1 | 6 | Hinchey | 13.2kV | TH01 | Transformer #X34143 located at 61 Clearview Ave opened by crew for removal of service | Ottawa | Scheduled Outage | Construction
10202 | 2007 | 3 | 28 | 0.56944 |  | 140 | 14 | 6 | Hinchey | 4.16kV | TH01 | Glen Carswell isolated TRF. @ 27 Grange Ave. for pole change | Ottawa | Scheduled Outage | Equipment Deterioration Due to Age
8100 | 2006 | 4 | 3 | 0.35417 |  | 28 | 0 | 1 | Hinchey | 4.16kV | TH01 | Dave Jones had tranformer off at 211 Patricia to change bad connections in the transformer | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20271 | 2012 | 4 | 3 | 0.47917 |  | 37 | 2 | 4 | Hinchey | 13.2kV | TH01 | Transformer X33692 at 332 Oakdale Ave. isolated to allow for rearranging of plant | Ottawa | Scheduled Outage | Construction
16056 | 2010 | 5 | 7 | 0.57986 |  | 71 | 8 | 7 | HINCHEY | 13.2kV | TH01 | Transformer X34110 at Pontiac St & Northwestern Ave. isolated to straighten pole | Ottawa | Scheduled Outage | Preventive Maintenance
14341 | 2009 | 5 | 11 | 0.39583 |  | 143 | 24 | 10 | HINCHEY | 13.2kV | TH01 | transformer OTT5352 at rear of 375 Island Park Drive isolated to allow for relocation of services | Ottawa | Scheduled Outage | Preventive Maintenance
8281 | 2006 | 5 | 12 | 0.16319 |  | 365 | 36 | 6 | Hinchey | 13.2kV | TH01 | A tree has fallen on the O/H service at 197 Cowley causing the TH01 to auto reclose and blew the transformer fuse on Cowley at Clearview. Defective service disconnected and transformer refused. | Ottawa | Tree Contacts | Tree Fallen
8294 | 2006 | 5 | 14 | 0.37708 |  | 57 | 11 | 12 | Hinchey | 13.2kV | TH01 | Transformer fuse 55D1B-0993 at the rear of 69 Huron Ave was found open due to tree contact on the open wire buss Trimmed trees and restored power | Ottawa | Tree Contacts | Inadequate Trimming
5158 | 2004 | 5 | 18 | 0.030556 |  | 60 | 4 | 4 | TH | 13.2kV | TH01 | Racoon caused Tx 55D1B-0134 fuse to open at 121 Caroline , 4 customers affected. Fuse replaced & power restored. | Ottawa | Foreign Interference | Animal
12454 | 2008 | 5 | 20 | 0.37847 |  | 19 | 2 | 6 | Hinchey | 13.2kV | TH01 | At 09:05 trana at 100 Grange Ave was isolated in order for service replacement | Ottawa | Scheduled Outage | Repair
6586 | 2005 | 5 | 22 | 0.51389 |  | 74 | 9 | 7 | Hinchey | 12/7.2kV | TH01 | A squirrel caused the fuse to blow to the transformer 900-76 that feeds customers on Caroline. | Ottawa | Foreign Interference | Animal
18207 | 2011 | 5 | 24 | 0.49514 |  | 111 | 9 | 5 | Hinchey | 13.2kV | TH01 | Transformer #X34122 located at 236 Cowley opened up, crew could not find the cause | Ottawa | Unknown/Other | No Apparent Cause
6638 | 2005 | 6 | 1 | 0.82917 |  | 145 | 17 | 7 | Hinchey | 13.2kV | TH01 | Crew found transformer fuse blown at 1818 Scott. Transformer refused. Power restored at 2219 | Ottawa | Unknown/Other | No Apparent Cause
20695 | 2012 | 6 | 5 | 0.28958 |  | 111 | 30 | 16 | Hinchey | 13.2kV | TH01 | At 6:57, transformer X30484 opnned duer to animal contact. 16 customers affected for 111 minutes. Hinchey (TH01). ID #20695 | Ottawa | Foreign Interference | Animal
20702 | 2012 | 6 | 5 | 0.69236 |  | 68 | 8 | 7 | Lincoln | 13.2kV | TH01 | Replaced blown fuse feeding transformer X21505 at 87 Clearview Ave (Squirrel contact) | Ottawa | Foreign Interference | Animal
14524 | 2009 | 6 | 12 | 0.3 |  | 100 | 8 | 5 | Hinchey | 13.2kV | TH01 | Transformer #X31461 located at 59 Grange isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
12625 | 2008 | 6 | 14 | 0.33958 |  | 41 | 3 | 5 | Hinchey | 13.2kV | TH01 | Refused switch to transformer X31461 at 59 Grange Ave | Ottawa | Unknown/Other | No Apparent Cause
8495 | 2006 | 6 | 15 | 0.61458 |  | 75 | 6 | 5 | Hinchey | 13.2kV | TH01 | Transformer #55D1B-0291 located at 54 Grange isolated due to tree interference | Ottawa | Tree Contacts | Inadequate Trimming
12676 | 2008 | 6 | 16 | 0.99722 |  | 59 | 10 | 10 | Hinchey | 13.2kV | TH01 | Crew opened transformer X33857 in front of 37 Huron to replace defective line clamp, switch & arrestor. | Ottawa | Adverse Weather | Lightning
8520 | 2006 | 6 | 19 | 0.35486 |  | 55 | 5 | 5 | HINCHEY | 4.16kV | TH01 | Fused switch to transformer 55D1A-0512 at 335 Island Park Dr opened due to squirrel contact | Ottawa | Foreign Interference | Animal
12696 | 2008 | 6 | 19 | 0.66806 |  | 88 | 7 | 5 | Hinchey | 13.2kV | TH01 | Transformer #55D1A-0507 located at 298 Oakdale isolated due to squirrel interference | Ottawa | Foreign Interference | Animal
14578 | 2009 | 6 | 20 | 0.35972 |  | 193 | 139 | 955 | Hinchey | 13.2kV | TH01 | Squirell contact on Oakdale caused TH01 breaker to open due to the fact the reclosing was not in service. Once Fire and Police were contacted and clear system tried TH01 Breaker. TH01 held and transformer X33692 at 345 Island Park was found to be left open.(Hinchey) TH01. ID#14578. | Ottawa | Foreign Interference | Animal
10705 | 2007 | 6 | 21 | 0.78681 |  | 114 | 17 | 9 | Hinchey | 13.2kV | TH01 | Transformer #55B3C-0199 located at 199 Patricia isolated-transformer checked okay, re-installed barrell & closed, cause unknown | Ottawa | Unknown/Other | No Apparent Cause
12761 | 2008 | 6 | 27 | 0.85347 |  | 58 | 4 | 4 | Hinchey | 13.2kV | TH01 | Replaced broken switch at transformer X34124 at 137 Keyworth Ave | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5396 | 2004 | 6 | 29 | 0.68056 |  | 75 | 312 | 250 | Hinchey | 13.2kV | TH01 | A tree contractor dropped a limb across red & white phases of TH01 at Sunnymede & Patricia causing the line to autoreclose and 2 fuses to blow at SMD20 switch on Carleton at Premiere. Crew removed branch and switch was refused and closed | Ottawa | Foreign Interference | Foreign Object
6845 | 2005 | 7 | 1 | 0.72569 |  | 26 | 504 | 1162 | TH | 13.2kV | th01 | TH01 was opened to allow the crew to close a set of in-line fuses at Holland/Spencer, the breaker tripped when it was closed, the fuses were opened, the breaker tripped again. The fuses were closed & the line patrolled. No problems were found & when the breaker was tried again it held. | Ottawa | Adverse Weather | Lightning
8652 | 2006 | 7 | 2 | 0.89583 |  | 55 | 10 | 11 | Hinchey | 13.2kV | TH01 | TH01 transformer opened to clear large limb from the overhead | Ottawa | Tree Contacts | Inadequate Trimming
12778 | 2008 | 7 | 2 | 0.85417 |  | 25 | 2 | 6 | Hinchey | 13.2kV | TH01 | Transformer #X26685 located at 303 Island Park Dr isolated to replace connections | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18635 | 2011 | 7 | 10 | 0.28542 |  | 384 | 70 | 11 | Hinchey | 13.2kV | TH01 | Defective transformer X33705 at 70 Holland Ave was replaced due to flashed over insulator (Squirrel contact) | Ottawa | Foreign Interference | Animal
6909 | 2005 | 7 | 12 | 0.42014 |  | 37 | 6 | 10 | Hinchey | 13.2kV | TH01 | Interrupted power to Transformer G7044-28 at 258 Cowley Ave to relocate services | Ottawa | Scheduled Outage | Construction
10871 | 2007 | 7 | 14 | 0.75972 |  | 102 | 29 | 17 | Hinchey | 4.16kV | TH01 | TH01 circuit reclosed due to squirrell contact. At 1806 Scott Street, a fuse at the switch and a lateral feed transformer fuse opened. Replaced fuses, closed in switches and power has been restored to normal. | Ottawa | Foreign Interference | Animal
16487 | 2010 | 7 | 17 | 0.82292 |  | 85 | 17 | 12 | Hinchey | 13.2kV | TH01 | A tree limb had fallen on the triplex that feedds 184 Carleton , the transformer fuse at X34104 was open to make repairs. | Ottawa | Tree Contacts | Tree Limb Fallen
7010 | 2005 | 7 | 23 | 0.31944 |  | 135 | 14 | 6 | Hinchey | 13.2kV | TH01 | Transformer at 194 Cowley opened due to Bird contact. Also caused TH01 circuit to auto. | Ottawa | Foreign Interference | Bird
14817 | 2009 | 7 | 24 | 0.27292 |  | 107 | 7 | 4 | Hinchey | 13.2kV | TH01 | Transformer #X33692 located at 345 Island Park Dr isolated due to animal contact | Ottawa | Foreign Interference | Animal
8831 | 2006 | 7 | 25 | 0.33889 |  | 262 | 70 | 16 | Hinchey | 13.2kV | TH01 | Transformer #55D1B-0799 located at 68 Smirle isolated due to defective transformer (was replaced) | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16563 | 2010 | 7 | 26 | 0.4375 |  | 42 | 8 | 12 | Hinchey | 4.16kV | TH01 | Isolated transformer X33874 at 135 Huron St for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
10963 | 2007 | 7 | 29 | 0.73472 |  | 65 | 8 | 7 | Hinchey | 13.2kV | TH01 | Hinchey TH01 circuit auto/reclosed when the fuse to transformer opened due to squirrel contact. | Ottawa | Foreign Interference | Animal
7049 | 2005 | 8 | 2 | 0.40694 |  | 64 | 7 | 7 |  | 13.2kV | TH01 | Power interruption to transformer at 74 Ross st to do maintenance work on the pole | Ottawa | Scheduled Outage | Preventive Maintenance
7077 | 2005 | 8 | 6 | 0.24861 |  | 67 | 7 | 6 | Hinchey | 13.2kV | TH01 | Transformer isolated at 194 Cowley Ave due to animal interference (squirrel) | Ottawa | Foreign Interference | Animal
13052 | 2008 | 8 | 13 | 0.43403 |  | 10 | 3 | 19 | Hinchey | 13.2kV | TH01 | Transformer #X30497 located at 83 Gilchrist isolated to cut down 2 triplex services. | Ottawa | Scheduled Outage | Preventive Maintenance
16730 | 2010 | 8 | 13 | 0.28125 |  | 105 | 2 | 1 | Hinchey | 13.2kV | TH01 | 13kV Vault at 345 Carleton was isolated from Hydro Ottawa Sources for Hydro Ottawa Crew to change out defective Blue Phase 50kVA transformer. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
18944 | 2011 | 8 | 16 | 0.41667 |  | 126 | 13 | 6 | Hinchey | 13.2kV | TH01 | Transformer X34143 @ 65 Clearview was isolated to allow crew to install new service | Ottawa | Scheduled Outage | Construction
18974 | 2011 | 8 | 18 | 0.375 |  | 330 | 44 | 8 | Hinchey | 13.2kV | TH01 | Transformer #X34147 located at 73 Sunnymede Ave opened by crew for a pole replacement | Ottawa | Scheduled Outage | Construction
14965 | 2009 | 8 | 19 | 0.52986 |  | 32 | 3 | 5 | Hinchey | 13.2kV | TH01 | Transformer #55D1A-0502 located at 241 Northwestern Ave isolated due to animal contact | Ottawa | Foreign Interference | Animal
16780 | 2010 | 8 | 19 | 0.5 |  | 190 | 35 | 11 | Hinchey | 13.2kV | TH01 | Isolated transformer X34129 at 260 Keyworth Ave for new pole installation | Ottawa | Scheduled Outage | Emergency Services Request
14973 | 2009 | 8 | 20 | 0.40972 |  | 15 | 1 | 5 | Hinchey | 13.2kV | TH01 | Transformer #X34085 located at 316 Oakdale isolated to drop a service for tree removal | Ottawa | Scheduled Outage | Construction
9037 | 2006 | 8 | 24 | 0.29722 |  | 52 | 7 | 8 | Hinchey | 4.16kV | TH01 | Transformer #55B3C-0183 located at 181 Northwestern Ave isolated due to bird contact | Ottawa | Foreign Interference | Bird
9082 | 2006 | 8 | 28 | 0.73611 |  | 10 | 3 | 16 | Hinchey | 13.2kV | TH01 | Transformer #OTT266 located at 303 Kirchoffer isolated to get squirrel off the open secondary wire | Ottawa | Foreign Interference | Animal
15021 | 2009 | 8 | 28 | 0.62083 |  | 51 | 8 | 10 | HINCHEY | 13.2kV | TH01 | Transformer X21540 at 400 Piccadilly isolated to allow for u/g service connection | Ottawa | Scheduled Outage | Construction
19106 | 2011 | 9 | 7 | 0.43056 |  | 84 | 8 | 6 | Hinchey | 13.2kV | TH01 | Trans X26658 at 198 Cowley Ave was isolated for secondary service work | Ottawa | Scheduled Outage | Preventive Maintenance
5815 | 2004 | 9 | 20 | 0.38542 |  | 15 | 2 | 7 | HINCHEY | 13.2kV | TH01 | Service upgrade to 97 Gilcrest | Goulburn | Scheduled Outage | Construction
4139 | 2003 | 9 | 23 | 0.58681 |  | 15 | 4 | 15 | Hinchey | 13.2kV | TH01 | Transformer at 151 Hinton was opened to allow Bell Canada to perform pole testing | Ottawa | Scheduled Outage
11366 | 2007 | 9 | 23 | 0.59236 |  | 68 | 6 | 5 | Hinchey | 13.2kV | TH01 | At 14:13 trans cut out at 300 Oakvale Ave blew due to a bird contact cut out refuse power restored | Ottawa | Foreign Interference | Bird
4179 | 2003 | 9 | 29 | 0.56944 |  | 15 | 4 | 16 | Hinchey | 13.2kV | TH01 | Pole testing at 151 Hinton | Ottawa | Scheduled Outage | Preventive Maintenance
4181 | 2003 | 9 | 29 | 0.55208 |  | 15 | 2 | 10 | Hinchey | 13.2kV | TH01 | pole testing at 177 Hinton | Ottawa | Scheduled Outage | Preventive Maintenance
4182 | 2003 | 9 | 29 | 0.55208 |  | 15 | 3 | 11 | Hinchey | 13.2kV | TH01 | Pole Testing at 161 Hinton | Ottawa | Scheduled Outage | Preventive Maintenance
17024 | 2010 | 9 | 29 | 0.40972 |  | 23 | 2 | 6 | HINCHEY | 13.2kV | TH01 | Transformer X33690 at 21 Garrison St isolated to allow for rearranging of secondary | Ottawa | Scheduled Outage | Construction
11485 | 2007 | 10 | 9 | 0.44583 |  | 38 | 4 | 7 | Hinchey | 13.2kV | TH01 | Transformer #55D1B-0982 located at 30 Holland isolated due to animal contact | Ottawa | Foreign Interference | Animal
19373 | 2011 | 10 | 14 | 0.375 |  | 69 | 14 | 12 | Hinchey | 13.2kV | TH01 | Transformer #X30498 located at 13 Gilchrist opened up due to squirrel interference | Ottawa | Foreign Interference | Animal
9471 | 2006 | 10 | 19 | 0.62153 |  | 40 | 5 | 8 | Hinchey | 4.16kV | TH01 | Switch to transformer 55D1A-0795 at 37 Western Ave was found blown due to a squirrel contact refused switch power restored | Ottawa | Foreign Interference | Animal
17170 | 2010 | 10 | 25 | 0.375 |  | 170 | 23 | 8 | Hinchey | 13.2kV | TH01 | Crew opened transformer at corner of Carleton and Wellinton to re-arrange overhead plant. | Ottawa | Scheduled Outage
15305 | 2009 | 10 | 26 | 0.42708 |  | 45 | 5 | 7 | Hinchey | 13.2kV | TH01 | Transformer #X34106 located at 213 Carleton Ave isolated to install new service | Ottawa | Scheduled Outage | Construction
15328 | 2009 | 10 | 29 | 0.41667 |  | 301 | 65 | 13 | Hinchey | 13.2kV | TH01 | Transformer #X34108 located at 248 Carleton Ave isolated to plant a new pole | Ottawa | Scheduled Outage | Construction
19517 | 2011 | 11 | 2 | 0.37014 |  | 177 | 86 | 29 | Hinchey TS | 13.2kV | TH01 | PC10A# 3736 established on S10276 to allow forrestry crews to clear limbs from this section TH01 O/H line. | Ottawa | Scheduled Outage | Preventive Maintenance
17290 | 2010 | 11 | 17 | 0.41319 |  | 145 | 5 | 2 | Hinchey | 13.2kV | TH01 | Section of TH01 line between Ross & Grange isolated to repair burnt pole top at dip to PT197. 2 commercial buildings, PT197 at 1319 Wellington and VT594 at 119 Ross interrupted. Pole to be replaced at later date. | Ottawa | Defective Equipment
13692 | 2008 | 12 | 1 | 0.12222 |  | 59 | 8 | 8 | Hinchey | 13.2kV | TH01 | Cut out broken on transformer X30499 at 58 Western Ave. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15444 | 2009 | 12 | 1 | 0.375 |  | 199 | 27 | 8 | Hinchey | 13.2kV | TH01 | Transformer #X33856 located at 5 Huron Ave N isolated to install new pole | Ottawa | Scheduled Outage | Construction
15449 | 2009 | 12 | 1 | 0.54167 |  | 55 | 9 | 10 | Hinchey | 13.2kV | TH01 | Transformer #X33688 located at 280 Spencer St isolated to replace some services | Ottawa | Scheduled Outage | Construction
4549 | 2003 | 12 | 3 | 0.39167 |  | 100 | 70 | 42 | HINCHEY | 13.2kV | TH01 | Scheduled outage to MT1748, MT1749 & MT1750 on Banknote Prv & West Village Prv off Scott St. to straighten the transformers. | Ottawa | Scheduled Outage | Repair
4551 | 2003 | 12 | 3 | 0.47222 |  | 68 | 11 | 10 | Hinchey | 13.2kV | TH01 | Scheduled outage to MT1742 to straighten the transformer. | Ottawa | Scheduled Outage | Repair
15493 | 2009 | 12 | 10 | 0.52778 |  | 75 | 51 | 41 | Hinchey | 13.2kV | TH01 | Transformer #X31473 located at 1285 Wellington St isolated for an upgrade | Ottawa | Scheduled Outage | Construction
19724 | 2011 | 12 | 15 | 0.40625 |  | 22 | 2 | 6 | Hinchey | 4.16kV | TH01 | Isolated transformer X30489 at 109 Smirle Ave for a service up-grade | Ottawa | Scheduled Outage | Preventive Maintenance
13800 | 2008 | 12 | 27 | 0.60347 |  | 431 | 72 | 10 | Hinchey | 13.2kV | TH01 | Transfomer at 1335 Wellington defective and replaced. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15569 | 2009 | 12 | 27 | 0.071528 |  | 98 | 42 | 26 | Hinchey | 13.2kV | TH01 | Radial fuse on Scott between Island Park & Oakdale was opened to isolate line section for repairs to primary conductor taken down by a fallen tree. | Ottawa | Adverse Weather | Ice Storm
14819 | 2009 | 7 | 24 | 0.33056 |  | 39 | 4 | 6 | Hinchey | 13.2kV | TH02 | Transformer #X34132 located 229 Daniel Ave isolated due to animal contact | Ottawa | Foreign Interference | Animal
18755 | 2011 | 7 | 17 | 0.81042 |  | 7 | 21 | 181 | Hinchey TS | 13.2kV | TH03 | TH03 Tripped during severe storm. Closed back in and held 7 minutes later | Ottawa | Adverse Weather | Wind
13469 | 2008 | 10 | 29 | 0.053472 |  | 268 | 13 | 3 | HINCHEY | 13.2kV | TH03/04 | Richard Barnett found the neutral down, the phases at Scott and OC transpo. | Ottawa | Adverse Weather
16606 | 2010 | 8 | 2 | 0.62361 |  | 61 | 39 | 45 | Hinchey | 13.2kV | TH05 | A squirrel made contact inside the PHM switch gear SC32 at Tunneys Pasture causing it to flash over. | Ottawa | Foreign Interference | Animal
3159 | 2003 | 2 | 4 | 0.60972 |  | 187 | 3428 | 1100 | Hinchey TS | 13.2kV | TH06 | Cct dumped due to pole fire at Scott & Parkdale | Ottawa | Adverse Weather | Rain
12217 | 2008 | 4 | 1 | 0.71528 |  | 532 | 9 | 1 | Hinchey | 13.2kV | TH06 | PT234 @ 383 Parkdale blown arrester replaced by Howat. Transformer replaced by on call crew. Power restored. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15903 | 2010 | 4 | 7 | 0.71458 |  | 3 | 64 | 1286 | Hinchey | 13.2kV | TH06 | TH06 breaker opened by System at the request of the 24/7. Crew reports while opening the transformer cutout the supporting insulator let go and caused the live switch to come in proximity of the grounding bracket threatning to trip TH06 cct. | Ottawa | Defective Equipment
15905 | 2010 | 4 | 7 | 0.70139 |  | 40 | 12 | 18 | Hinchey | 13.2kV | TH06 | Transformer #X30298 located at 75 Hinton Ave N opened to replace broken cutout | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8130 | 2006 | 4 | 11 | 0.45833 |  | 120 | 16 | 8 | Hinchey | 13.2kV | TH06 | Isolated transformer OTT1024 at 11 Bullman to upgrade service | Ottawa | Scheduled Outage | Preventive Maintenance
17954 | 2011 | 4 | 18 | 0.36458 |  | 47 | 1 | 1 | Hinchey | 13.2kV | TH06 | one phase of three feeding 13kv distribution vault VT850 @ 300 Parkdale opened due to defective insulators. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
12318 | 2008 | 4 | 21 | 0.75625 |  | 351 | 6 | 1 | Hinchey | 13.2kV | TH06 | At 6:09pm PT234 at 383 Parkdale Avenue, customers called in to report poor power out of the 3 Phase 347/600V transformer. 24-7 made replaced one fuse and two K-Links and power was restored to customers at 12:00am. Hinchey (TH06). ID#12318. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20508 | 2012 | 5 | 12 | 0.40625 |  | 160 | 43 | 16 | Hinchey | 13.2kV | TH06 | 45 PT234 and 3 overhead transformers isolated on Grant to were isolated to allow crews to reconfigure secondary bus | Ottawa | Scheduled Outage | Construction
6558 | 2005 | 5 | 15 | 0.28611 |  | 1 | 14 | 854 | Hinchey | 13.2kV | TH06 | transformer at 163 Parkdale opened due to squirrel, also causing TH06 circuit to open. | Ottawa | Foreign Interference | Animal
6559 | 2005 | 5 | 15 | 0.28611 |  | 63 | 4 | 4 | Hinchey | 13.2kV | TH06 | transformer at 163 Parkdale opened due to squirrel, also causing TH06 circuit to open. | Ottawa | Foreign Interference
12449 | 2008 | 5 | 18 | 0.36597 |  | 46 | 8 | 10 | Hinchey | 13.2kV | TH06 | TH06 auto reclosed, overhead transformer at 10 Oxford was found with a blown cutout suspect the dead squirrel caused the trip. | Ottawa | Foreign Interference | Animal
14442 | 2009 | 6 | 1 | 0.84028 |  | 55 | 1 | 1 | HINCHEY | 13.2kV | TH06 | At 8:10pm Ottawa Fire notified Dispatch of a pole fire located at 215 Parkdale, Crews report cracked switch caused pole fire. Switch was opened to repair and replaced all 3 switches and 3 Live Line Clamps.1 Customer was affected for 55min and power was restored at 9:05pm. (Hinchey TH06). ID#14442. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16176 | 2010 | 6 | 2 | 0.42917 |  | 42 | 13 | 18 | Hinchey | 13.2kV | TH06 | replaced blown fuse at transformer X30299 at 78 Hinton Ave due to squirel contact | Ottawa | Foreign Interference | Animal
8426 | 2006 | 6 | 5 | 0.36528 |  | 46 | 5 | 6 | Hinchey | 13.2kV | TH06 | Switch to Transformer OTT1213 at 112 Carruthers St opened due to animal contact (Squirrel) | Ottawa | Foreign Interference | Animal
8549 | 2006 | 6 | 20 | 0.35694 |  | 96 | 2 | 1 | Hinchey | 13.2kV | TH06 | severe storm condition caused the blue phase fuse to open feeding the 13kv transformer PT114 @ 159 Forward ave. Crew opened transformer to investigate for possible problems. None found. | Ottawa | Adverse Weather | Lightning
16454 | 2010 | 7 | 11 | 0.35417 |  | 40 | 12 | 18 | Hinchey | 13.2kV | TH06 | Squirrel opened overhead transformer X30299 @ 81 Hinton ave. North. | Ottawa | Foreign Interference | Animal
12829 | 2008 | 7 | 13 | 0.11458 |  | 21 | 350 | 1000 | Hinchey | 13.2kV | TH06 | TH06 cut out to VT853 at 395 Parkdale one broken phase was arcing, isolation required to safely open cut out. | Ottawa | Scheduled Outage | Emergency Services Request
14750 | 2009 | 7 | 15 | 0.37847 |  | 29 | 1 | 2 | Hinchey | 13.2kV | TH06 | Transformer #X27831 located at 20 Grant isolated to install new service | Ottawa | Scheduled Outage | Construction
8810 | 2006 | 7 | 24 | 0.27292 |  | 122 | 16 | 8 | Hinchey | 13.2kV | TH06 | Transformer #OTT2528 located at 146 Forward Ave isolated caused by a bird interference | Ottawa | Foreign Interference | Bird
7033 | 2005 | 7 | 27 | 0.64514 |  | 53 | 16 | 18 | Hinchey | 13.2kV | TH06 | Auto reclose on TH06. Problem was later determined to be a squirrel contact at an overhead transformer on Hinton Ave. Transformer was refused successfully. | Ottawa | Foreign Interference | Animal
16602 | 2010 | 8 | 2 | 0.28056 |  | 101 | 35 | 21 | Hinchey | 13.2kV | TH06 | Transformer #X23885 located at 107 Parkdale opened up due to bird contact | Ottawa | Foreign Interference | Bird
3923 | 2003 | 8 | 20 | 0.74167 |  | 332 | 138 | 25 | TH | 13.2kV | TH06 | A customer that had been disconnected for non payment attempted to reconnect his service, this made the neutral conductor live and damaged 3 spans of O/H primary conductor. 2 O/H transformers were off at Hinchey/Scott/ Carruthers area while the crew made repairs to downed wires. | Ottawa | Foreign Interference | Vandalism
4060 | 2003 | 9 | 12 | 0.55694 |  | 33 | 2 | 3 | Hinchey | 13.2kV | TH06 | Bird contact opened transformer feeding 3 customers on Parkdale fed from transformer at 205 Parkdale.. | Ottawa | Foreign Interference
4180 | 2003 | 9 | 29 | 0.59028 |  | 15 | 4 | 16 | Hinchey | 13.2kV | TH06 | Pole testing at 83 Hinton | Ottawa | Scheduled Outage | Preventive Maintenance
17069 | 2010 | 10 | 6 | 0.89514 |  | 66 | 14 | 13 | HINCHEY | 13.2kV | TH06 | Replaced broken cutout at transformer X27907 located at 191 Armstrong St. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4249 | 2003 | 10 | 12 | 0.50208 |  | 57 | 3 | 3 | Hinchey | 13.2kV | TH06 | Bird contact resulted in blown fuse. | Ottawa | Foreign Interference | Bird
11782 | 2007 | 11 | 28 | 0.46875 |  | 215 | 4 | 1 | Hinchey | 13.2kV | TH06 | Hinchey TH06 breaker auto/reclose, 2 phases of switch S20720 at VT830 found open due to failed stress cone at the cable dip S20720 to VT830. Vault isolated and cable repaired. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7670 | 2005 | 12 | 1 | 0.21875 |  | 295 | 25 | 5 | Hinchey | 13.2kV | TH06 | PT1438 at 1217 Wellington was upgraded from a 150 kva to a 225 kva to allow for temporary construction services. | Ottawa | Scheduled Outage | Construction
15467 | 2009 | 12 | 3 | 0.89375 |  | 103 | 2 | 1 | Hinchey | 13.2kV | TH06 | VT853 at 395 Parkdale Ave reported outage, crews found a cutout was burnt up. Openned VT853 R1-F, replace cutout, meggered cable, and vault restored. | Ottawa | Defective Equipment
11815 | 2007 | 12 | 5 | 0.39583 |  | 395 | 118 | 18 | Hinchey | 13.2kV | TH06 | Transformer #MT0035 located at 2 Craftsman isolated to change transformer due to leaker | Ottawa | Scheduled Outage | Preventive Maintenance
13079 | 2008 | 8 | 18 | 0.67917 |  | 3 | 30 | 603 | HINCHEY | 13.2kV | TH08 | BREAKER OPENED, DUE TO STORM, CLOSED VIA SCADA | Ottawa | Adverse Weather | Lightning
13078 | 2008 | 8 | 18 | 0.67917 |  | 3 | 35 | 694 | HINCHEY | 13.2kV | TH09 | BREAKER OPENED, DUE TO STORM, CLOSED VIA SCADA | Ottawa | Adverse Weather | Lightning
13882 | 2009 | 1 | 20 | 0.74514 |  | 468 | 39 | 5 | HINCHEY | 13.2kV | TH11 | Section of TH11 circuit isolated to allow crew to transfer plant to new line at Bayview and Scott area. | Ottawa | Scheduled Outage
17503 | 2011 | 1 | 21 | 0.40972 |  | 30 | 5 | 10 | HINCHEY | 13.2kV | TH11 | Transformer X31477 at 15 Elm Street isolated to allow for changeover | Ottawa | Scheduled Outage | Construction
7854 | 2006 | 1 | 25 | 0.5625 |  | 60 | 13 | 13 | HINCHEY | 4.16kV | TH11 | TRANSFORMER OUT TO REPLACE OPEN fuse @ 373 greenview ave. transformer 55c1c-0189 | Ottawa | Scheduled Outage | Repair
9972 | 2007 | 1 | 29 | 0.51389 |  | 26 | 7 | 16 | Hinchey | 13.2kV | TH11 | Isolated transformer 55D2A-0387 at 27 Elm St to replace broken switch | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3155 | 2003 | 2 | 3 | 0.54861 |  | 205 | 743 | 1058 | Hinchey TS | 13.2kV | TH11 | FIRST OUTAGE WAS CAUSED BY DEFECTIVE XFMR @ 15 ELM ST. CAUSING SMU20 RED PHASE FUSE TO BLOW. SECOND OUTAGE WAS CAUSED BY DEFECTIVE LIGHTNING ARRESTOR @ VT491 CAUSING THE TH11 CIRCUIT TO OPEN FAULT. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7914 | 2006 | 2 | 14 | 0.52431 |  | 30 | 2 | 3 | Hinchey | 13.2kV | TH11 | Isolated transformer OTT5684 at 1370 Scott St to replace service | Ottawa | Scheduled Outage | Preventive Maintenance
7919 | 2006 | 2 | 15 | 0.4375 |  | 266 | 13 | 3 | Hinchey | 13.2kV | TH11 | Transformer #OTT5684 located at 1372 Scott St isolated to relocate services | Ottawa | Scheduled Outage | Construction
3197 | 2003 | 2 | 17 | 0.83681 |  | 15 | 2 | 8 | TH | 13.2kV | TH11 | O/H xfmr was opened at 10 Manchester to replace defective hot line clamp. Customers were notified. | Ottawa | Scheduled Outage | Repair
12058 | 2008 | 2 | 18 | 0.61806 |  | 110 | 33 | 18 | Hinchey | 4.16kV | TH11 | Isolated two transformers at 188 Primrose Ave to relocated two mid span services | Ottawa | Foreign Interference | Foreign Object
17610 | 2011 | 2 | 18 | 0.87639 |  | 168 | 680 | 243 | Hinchey |  | TH11 | SMU-20 fuse blew (one phase) at City Center and Scott, causing interuption to customers on Primrose, Elm, Spruce, Rochester. After quick patrol nothing found crew re-fused. | Ottawa | Adverse Weather | Wind
17621 | 2011 | 2 | 19 | 0.21667 |  | 121 | 1003 | 1847 | Hinchey | 13.2kV | TH11 | SMU-20 fuse blew (two phases) at City Center and Scott, causing interuption to customers on Primrose, Elm, Spruce, Rochester. Crew installed new switches and TH11 breaker was opened to allow crew to close in fuses. TH11 breaker was closed in with four crews set up to watch the o/h while it was being re-energized via SCADA, crews report that they didn't see any issues and TH11 stayed on. | Ottawa | Adverse Weather | Wind
8046 | 2006 | 3 | 20 | 0.42639 |  | 131 | 26 | 12 | Hinchey | 13.2kV | TH11 | Transformer #55D2A-0786 located at 29 Spruce isolated due to transferring plant. | Ottawa | Scheduled Outage | Construction
3279 | 2003 | 3 | 21 | 0.04375 |  | 66 | 1035 | 941 | Hinchey | 13.2kV | TH11 | TH11 taken out of service for repairs to a pole on Scott at Bayview due to a pole fire. | Ottawa | Adverse Environment | Salt Spray
17758 | 2011 | 3 | 22 | 0.42708 |  | 45 | 2 | 2 | Hinchey | 13.2kV | TH11 | Transformer #X31718 located at 146 Elm St opened by crew to install new service | Ottawa | Scheduled Outage | Construction
3295 | 2003 | 3 | 23 | 0.86458 |  | 90 | 750 | 500 | Hinchey | 13.2kV | TH11 | Bad lightning arrestor at 21 preston feeding KT555 caused the blue phase SMU fuse at Champagne and Wellington to blow. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20223 | 2012 | 3 | 26 | 0.1125 |  | 76 | 823 | 1870 | Hinchey | 13.2kV | TH11 | TH11 tripped during windy weather, RW phases of S17297 were found blown. TH11 closed, remainder of cct patrolled, no problem found. S17297 RW fuses replaced restoring remaining customers. | Ottawa | Adverse Weather | Wind
20225 | 2012 | 3 | 26 | 0.175 |  | 401 | 4297 | 1870 | Hinchey | 13.2kV | TH11 | TH11 tripped again during windy conditions, S17297 RW found open again, TH11 closed & tripped. Patrol found broken insulator on Scott st, insulator replaced, TH11 closed & held. Broken Conductor found on Spruce St. Down the line from S17297. While trying to open the B phase at S17297 to isolate the broken conductor, the switch fell apart and tripped TH11 CB. Switch was cut clear and TH11 picked up to S17297. Switches were replaced and broken conductor repaired. | Ottawa | Adverse Weather | Wind
6365 | 2005 | 4 | 5 | 0.083333 |  | 13 | 229 | 1058 | Hinchey | 13.2kV | TH11 | TH11 was opened for fire at 807 somerset but a field check confirmed that it was not nessesary. Circuit was picked back up. | Ottawa | Adverse Environment | Fire
8136 | 2006 | 4 | 11 | 0.60208 |  | 318 | 37 | 7 | Hinchey | 13.2kV | TH11 | Transformer #OTT1216 located at 190 Carruthers isolated due to a broken switch | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17908 | 2011 | 4 | 11 | 0.74653 |  | 241 | 4602 | 1845 | Hinchey | 13.2kV | TH11 | TH11 opened due to downed phase and blown insulator on Scott between Phiney, and Stirling. When circuit was picked up that caused two phases of S17297 to open. Crew patrolled found no cause for fuses blowing, refused and closed. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10250 | 2007 | 4 | 13 | 0.46111 |  | 56 | 9 | 10 | Hinchey | 13.2kV | TH11 | At 11:04 trans at 147 Primrose was isolated in order to upgrade the trans | Ottawa | Scheduled Outage | Preventive Maintenance
20367 | 2012 | 4 | 21 | 0.85069 |  | 268 | 4531 | 1870 | Hinchey | 13.2kV | TH11 | TH11 breaker was opened due to a pole fire at the corner of Armstrong Street and Pinhey Street. Once the affected section was isolated load was restored to the unaffected areas. Hinchey ID#20367 | Ottawa | Adverse Environment | Fire
14336 | 2009 | 5 | 9 | 0.90069 |  | 83 | 1 | 1 | Hinchey | 13.2kV | TH11 | Crew refused and closed at transformer bank feeding the O-train yard at Bayview and Scott. No apparent cause found. | Ottawa | Unknown/Other | No Apparent Cause
10401 | 2007 | 5 | 10 | 0.58472 |  | 116 | 340 | 176 | Hinchey | 13.2kV | TH11 | The white phase of in line fuse at S17297 opened due to a failed arrestor. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6555 | 2005 | 5 | 13 | 0.69097 |  | 8 | 141 | 1058 | Hinchey | 13.2kV | TH11 | Scada indicates TH11 opened fault. No indication as to reason for fault on data window on scada or from relay at station. 1058 customers affected. Circuit to be patrolled. | Ottawa | Unknown/Other | No Apparent Cause
6564 | 2005 | 5 | 17 | 0.39583 |  | 60 | 0 | 8 | Hinchey | 13.2kV | TH11 | At 09:30 transformer at 52 Garland isolated for replacement | Ottawa | Scheduled Outage | Repair
3483 | 2003 | 5 | 25 | 0.96181 |  | 45 | 16 | 22 | TH | 13.2kV | TH11 | KT612 @ 45 Rochester was opened to repair a defective primary lead. | Ottawa | Scheduled Outage | Repair
14440 | 2009 | 6 | 1 | 0.73125 |  | 28 | 6 | 12 | Hinchey | 13.2kV | TH11 | Transformer #OTT5052 located at 60 Preston St isolated to reconnect service | Ottawa | Scheduled Outage | Repair
10545 | 2007 | 6 | 6 | 0.67014 |  | 20 | 1 | 4 | hinchey | 13.2kV | TH11 | Mike Byers isolated TRF @ 935 Wellington to remove broken guy wire | Ottawa | Scheduled Outage | Preventive Maintenance
14472 | 2009 | 6 | 6 | 0.32292 |  | 62 | 13 | 13 | Hinchey | 13.2kV | TH11 | Transformer #X31711 located at 70 Preston St isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
18325 | 2011 | 6 | 8 | 0.23611 |  | 40 | 4 | 6 | Hinchey TH | 13.2kV | TH11 | squirrel caused cut-out to blow @ X23892, 70 Pinehurst @ Scott | Ottawa | Foreign Interference | Animal
20726 | 2012 | 6 | 9 | 0.21528 |  | 226 | 1022 | 1901 | Hinchey |  | TH11 | A pole fire at 6 Lowrey caused a forced outage to TH11 circuit to allow crews to make repairs to a burnt transformer pole. Hinchey TH11 | Ottawa | Adverse Environment | Fire
20747 | 2012 | 6 | 12 | 0.44097 |  | 29 | 6 | 13 | Hinchey | 13.2kV | TH11 | Transformer #X25226 located at 79 Preston St opened up by crew for a change over | Ottawa | Scheduled Outage | Construction
14538 | 2009 | 6 | 14 | 0.80208 |  | 38 | 8 | 13 | Hinchey | 13.2kV | TH11 | Squirrel caused transformer X31711 @ Preston and Elm to open. | Ottawa | Foreign Interference | Animal
5306 | 2004 | 6 | 15 | 0.22569 |  | 240 | 76 | 19 | Hinchey | 13.2kV | TH11 | Transfomer at 12 Merton had to be interrupted due to wires down & a working fire at 7 Merton. | Ottawa | Adverse Environment | Fire
6740 | 2005 | 6 | 15 | 0.63194 |  | 176 | 880 | 300 | TH | 13.2kV | TH11 | TH11 cct auto reclosed when fuses at Wellington & Champagne opened. Repairs made & fuses replaced. | Ottawa | Adverse Weather | Lightning
8589 | 2006 | 6 | 25 | 0.56111 |  | 68 | 167 | 175 | Hinchey | 13.2kV | TH11 | TH11 circuit auto-reclosed once. 24/7 crew found the white phase fuse blown at Scott & Pinhey and the white phase fuse to PT139 both blown. Power was restored to the line section first & then to PT139 after the cause was determined to be from a bird contact flashing over the switch & arrestor to PT139. | Ottawa | Foreign Interference | Animal
8626 | 2006 | 6 | 29 | 0.54444 |  | 89 | 1569 | 1058 | Hinchey | 13.2kV | TH11 | Extreme weather caused a Skywire at parkdale & Scott to open circuit. Initially TH11 stayed on until skywire flashed over from circuit TH2UL. | Ottawa | Adverse Weather
5404 | 2004 | 6 | 30 | 0.33194 |  | 77 | 1 | 1 | Hinchey | 13.2kV | TH11 | A squirrel caused a fuse to blow to a xfmr feeding a City pumphouse at Bayswater & Bayview. The TH11 circuit autorclosed when the fuse blew. | Ottawa | Foreign Interference
5418 | 2004 | 7 | 1 | 0.62292 |  | 408 | 2040 | 300 | TH | 13.2kV | TH11 | Cct reclosed during thunder storm, tree limb was found on primary on Stirling ave which caused R & W SMD fuses at Scott & Pinhey to open. | Ottawa | Tree Contacts | Tree Limb Fallen
5439 | 2004 | 7 | 3 | 0.5 |  | 50 | 9 | 11 | Hinchey |  | TH11 | Transformer 55D2A-0349 at 142 Elm was taken out of service to remove a large tree on the service. | Ottawa | Tree Contacts | Tree Fallen
8658 | 2006 | 7 | 4 | 0.23958 |  | 30 | 6 | 12 | Hinchey | 13.2kV | TH11 | Squirrel caused transformer to open feeding customers on lowery and Garland. | Ottawa | Foreign Interference | Animal
10796 | 2007 | 7 | 5 | 0.375 |  | 30 | 8 | 15 | Hinchey | 12/7.2kV | TH11 | At 09:00 trans at 51 Spruce was isolated in order to relocate a sec service | Gloucester | Scheduled Outage | Repair
12795 | 2008 | 7 | 6 | 0.58611 |  | 165 | 21 | 8 | Hinchey | 13.2kV | TH11 | White phase cable fault between P/P/H switch @ pole #38 to KT615 @ 30 Rochester St. Caused outage on KT615 & KT618. Cable section was isolated and all power restored. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8680 | 2006 | 7 | 8 | 0.33333 |  | 100 | 8 | 5 | Hinchey | 13.2kV | TH11 | Transfomer isolated at 145 Elm St due to squirrel contact | Ottawa | Foreign Interference | Animal
6984 | 2005 | 7 | 17 | 0.64514 |  | 117 | 2 | 1 | Hinchey | 13.2kV | TH11 | 45 Rochester lightening arrestor and fuse to KT612 blew due to apparent lightening strike which caused auto reclose on TH11. | Ottawa | Adverse Weather | Lightning
12868 | 2008 | 7 | 17 | 0.43056 |  | 125 | 10 | 5 | Hinchey | 13.2kV | TH11 | At 10:20 trans at 138 CARRUTHERS AVE was isolated for service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
18694 | 2011 | 7 | 18 | 0.80694 |  | 976 | 30109 | 1851 | Hinchey | 13.2kV | TH11 | TH11 circuit opened during the wind storm due to downed conductors. Several attempts were made to close in breaker unsuccessfully. | Ottawa | Adverse Weather | Wind
16491 | 2010 | 7 | 19 | 0.30417 |  | 76 | 33 | 26 | Hinchey | 13.2kV | TH11 | Transformer #X27974 locate at 40 Stirling opened up due to bird contact | Ottawa | Foreign Interference | Bird
14798 | 2009 | 7 | 21 | 0.32292 |  | 90 | 3 | 2 | Hinchey | 13.2kV | TH11 | Transformer #X31534 located at 47 Breezehill isolated due to animal contact | Ottawa | Foreign Interference | Animal
7026 | 2005 | 7 | 26 | 0.37639 |  | 256 | 183 | 43 | Hinchey | 13.2kV | TH11 | 13 kv transformer KT458 isolated by K-Line to transfer it to new cables. 43 customers at 110 & 120 Walnut were affected. | Ottawa | Scheduled Outage | Construction
3809 | 2003 | 7 | 28 | 0.76736 |  | 97 | 126 | 80 | Hinchey | 13.2kV | TH11 | An arrestor failed at switch on Albert to KT613 causing the fuse to blow at this switch plus white phase SMU 220-E fuse at Champagne & Scott. The arrestor was replaced, switch refused at Champagne & Scott and then switch to KT613 refused restoring all power. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14882 | 2009 | 7 | 30 | 0.42083 |  | 99 | 13 | 8 | Hinchey |  | TH11 | Replaced connection at primary bushing on Transformer X31546 at 83 Spruce St | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
18869 | 2011 | 8 | 2 | 0.55208 |  | 82 | 23 | 17 | HINCHEY | 13.2kV | TH11 | Transformer X31542 at 57 Preston St. Isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
16649 | 2010 | 8 | 4 | 0.65556 |  | 378 | 11573 | 1837 | Hinchey | 13.2kV | TH11 | The 4301 O/H at Scott and Bayview conductor fell into the TH11 circuit | Ottawa | Adverse Weather | Wind
3846 | 2003 | 8 | 5 | 0.52083 |  | 25 | 5 | 12 | Hinchey | 13.2kV | TH11 | Crew opened 13kV transformer KT458 to replace defective arrestor affecting 12 customers on Walnut court. | Ottawa | Scheduled Outage | Repair
16668 | 2010 | 8 | 5 | 0.66667 |  | 610 | 7438 | 1837 | Hinchey | 13.2kV | TH11 | 3 SMU fuses at S17297 on Albert & City Park were blown because off lightning, to close them safely the TH11 breaker was open. | Ottawa | Adverse Weather | Rain
16746 | 2010 | 8 | 16 | 0.1875 |  | 245 | 1102 | 270 | Hinchey | 13.2kV | TH11 | lightning caused damage to neutral and two connections to circuit at Preston and Spruce. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11093 | 2007 | 8 | 18 | 0.65278 |  | 75 | 8 | 6 | Hinchey | 13.2kV | TH11 | broken transformer switch at 56 Stonehurst, Doug Mckay replaced and re-fused switch. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16782 | 2010 | 8 | 19 | 0.825 |  | 76 | 14 | 11 | Hinchey | 13.2kV | TH11 | Squirrel contact caused transformer X25696 @ 10 Garland to open | Ottawa | Foreign Interference | Animal
19017 | 2011 | 8 | 25 | 0.69583 |  | 14 | 1 | 5 | Hinchey | 13.2kV | TH11 | Transformer X23889 at 52 Carruthers isolated to trim trees at 56 & 58 Carrusthers - crew also renewed services there | Ottawa | Scheduled Outage | Repair
15073 | 2009 | 9 | 9 | 0.35764 |  | 65 | 9 | 8 | Hinchey | 13.2kV | TH11 | at 08:35 trans at 32 LOWREY ST OTTAWA was isolated for a service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
7341 | 2005 | 9 | 18 | 0.29792 |  | 55 | 23 | 25 | Hinchey | 13.2kV | TH11 | TH11 breaker auto-reclosed causing a momentary outage in the Hintonburg area. Cause was later determined to be a bird contact with the overhead transformer at 8 Lowrey. Transformer was re-fused successfully restoring power to 25 customers on Lowrey. | Ottawa | Foreign Interference | Animal
16964 | 2010 | 9 | 18 | 0.69236 |  | 47 | 23 | 29 | HINCHEY | 13.2kV | TH11 | Crews opened transformer X31543 @ 196 Primrose to change fuse in pedestal SP30 feeding the same address. | Ottawa | Defective Equipment | Repair
13274 | 2008 | 9 | 22 | 0.46181 |  | 60 | 8 | 8 | Hinchey | 13.2kV | TH11 | Isolated transformer X27844 at 266 Carruthers Ave to replace service | Ottawa | Scheduled Outage | Preventive Maintenance
15180 | 2009 | 9 | 28 | 0.46875 |  | 17 | 2 | 6 | HINCHEY | 13.2kV | TH11 | transformer X23897 at 52 Stonehurst Ave isolated to make temporary repairs to customer's point of attachment and allow crew to trim vines from around transformer | Ottawa | Scheduled Outage | Repair
13351 | 2008 | 10 | 9 | 0.72917 |  | 110 | 9 | 5 | Hinchey | 13.2kV | TH11 | Transformer #55D1B-0358 located at 7 Hilda isolated to replace a leaking transformer | Ottawa | Scheduled Outage | Repair
17090 | 2010 | 10 | 10 | 0.64722 |  | 54 | 5 | 6 | HINCHEY | 13.2kV | TH11 | Transformer X31711 at 70 Preston street refused after squirrel contact | Ottawa | Foreign Interference | Animal
7516 | 2005 | 10 | 25 | 0.68889 |  | 328 | 2401 | 1058 | Hinchey | 13.2kV | TH11 | Pole fire on Armstrong and Hilda burnt the pole thru requiring the circuit to be opened for safety. Section affected was isolated, for repair, restoring most of the customers. Remaining customers restored after repairs completed. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4373 | 2003 | 11 | 3 | 0.86458 |  | 12 | 3 | 17 | Hinchey | 13.2kV | TH11 | The switch at transformer 55D2A-0387, at 27 Elm Street in Ottawa, went defective and was replaced. ID#4373 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9652 | 2006 | 11 | 13 | 0.5625 |  | 54 | 5 | 6 | Hinchey | 13.2kV | TH11 | Trf. Located @ 18 Ladouceur isolated for service mtce. | Ottawa | Scheduled Outage | Preventive Maintenance
17374 | 2010 | 12 | 3 | 0.56667 |  | 124 | 21 | 10 | Hinchey | 13.2kV | TH11 | Transformer #X31549 located at 41 Spruce opened due to squirrel contact. Crew replaced cracked switch | Ottawa | Foreign Interference | Animal
5995 | 2004 | 12 | 8 | 0.89167 |  | 19 | 5 | 17 | Hinchey | 13.2kV | TH11 | Customer at 65 Rochester reported sparking on pole. Crew replaced fused cutout at xfmr 55D2A-0671. 16 customers on Rochester & 1 on Primrose affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9813 | 2006 | 12 | 8 | 0.57292 |  | 10 | 2 | 14 | Hinchey | 13.2kV | TH11 | Transformer #OTT2622 located at 41 Hilda isolated due to re-arranging the service | Ottawa | Scheduled Outage | Construction
4652 | 2003 | 12 | 25 | 0.35069 |  | 49 | 343 | 1058 | TH | 13.2kV | TH11 | TH11 breaker opened due to a faulty arrestor on Pinhey at Scott st. The red phase fuse supplying this lateral opened also, but with reclosing out of service the breaker stayed open until reclosing status was checked at the station. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13816 | 2008 | 12 | 29 | 0.45833 |  | 30 | 6 | 11 | Hinchey | 13.2kV | TH11 | At 11:00 trans at 9 Merton was isolated in order to replace defective sec conections | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8625 | 2006 | 6 | 29 | 0.54444 |  | 65 | 776 | 716 | Hinchey | 13.2kV | TH12 | Extreme weather caused a Skywire at Parkdale & Scott to fall and open circuit. | Ottawa | Adverse Weather | Lightning
7433 | 2005 | 10 | 7 | 0.23264 |  | 94 | 4 | 3 | Hinchey | 13.2kV | TH1SH,4304 | Cable fault caused 4304 and TH1SH to Trip. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3160 | 2003 | 2 | 4 | 0.62153 |  | 175 | 3 | 1 | Hinchey TS | 13.2kV | TH1UL | Pole fire at Scott & Parkdale, all load transferred except Canadian Bank Note, VT48, 145 Richmond rd | Ottawa | Adverse Weather | Rain
3280 | 2003 | 3 | 21 | 0.093056 |  | 175 | 3 | 1 | Hinchey | 13.2kV | TH1UL | TH1UL taken out of service after transferring all customers except Canadian Banknote at VT48 due to a pole fire on Scott at Rockhurst. Pole was temporarily repaired and line restored. | Ottawa | Adverse Environment | Salt Spray
3365 | 2003 | 4 | 13 | 0.48611 |  | 298 | 3397 | 687 | Hinchey | 13.2kV | TH1UL | While isolating TH1UL line complete. TH1UL-L switch at Clifton sub-station failed. Causing fire in Clifton station. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18483 | 2011 | 6 | 24 | 0.15972 |  | 557 | 9 | 1 | Hinchey | 13.2kV | TH1UL | Vault VT48 @ 145 Richmond Rd was isolated to allow contractor to make repair on transformer bus and main bus to correct tracking issue. 1 customer was afffected. Hinchey (TH1UL) | Ottawa | Foreign Interference
8627 | 2006 | 6 | 29 | 0.54444 |  | 139 | 412 | 602 | Hinchey | 13.2kV | TH1UL | Extreme weather caused a Skywire at Parkdale & Scott to fall and open circuit. | Ottawa | Adverse Weather | Wind
4131 | 2003 | 9 | 23 | 0.048611 |  | 655 | 11 | 1 | Hinchey | 13.2kV | TH1UL | 13KV OCB at VT48, Canada Banknote, tripped and would not close. Crew reported noise heard when tried to close. Customer advised to get an electrical contractor and vault main & transformer buses were isolated. Contractor reported our metering CT found burned. Metering advised and sent. Blue phase CT changed and bus repaired. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15551 | 2009 | 12 | 26 | 0.35972 |  | 65 | 589 | 883 | Hinchey | 13.2kV | TH1UL | A blown pot head at the corner of Scott and Lanark caused the TH1UL to trip. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4033 | 2003 | 9 | 8 | 0.83333 |  | 117 | 8 | 6 | Hinchey | 13.2kV | TH1UL,4301,4304 | Power was restored one vault at a time as they were transferred to alternate feeds. Customers affected included part of Tunney's Pasture Central Heating Plant, part of Lemieux Island, Canadian Bank Note, Loblaws, Tom Brown Arena and an Apartment Building. Cable crew located a fault on the red phase of 4304 circuit. No fault indicated by Hi-pot test on TH1UL, cause of trip is still to be determined. | Ottawa | Unknown/Other | No Apparent Cause
8938 | 2006 | 8 | 10 | 0.29861 |  | 70 | 4 | 5 | Hinchey | 13.2kV | TH2SH & 4305 | Squirell contacted between 2 LA's at TH2SH P/P/H to VT310 (-L2) | Ottawa | Foreign Interference | Animal
11273 | 2007 | 9 | 8 | 0.35417 |  | 77 | 2 | 3 | Hinchey | 13.2kV | TH2SH-4305 | A squirrel made contact at the run off SH3UJ to VT310 at Gladestone and Lorretta burning the connection and the insulators | Ottawa | Foreign Interference | Animal
5902 | 2004 | 11 | 19 | 0.14583 |  | 30 | 350 | 700 | Hinchey | 13.2kV | TH2UJ | Circuit TH2UJ auto tripped, Bayswater T2 load interupted, load transferred to the Bayswater T1. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3161 | 2003 | 2 | 4 | 0.625 |  | 5 | 0 | 1 | Hinchey TS | 13.2kV | TH2UL | Pole fire at Scott & Parkdale, all load transferred before dumping cct except VT65 on Lanark ave. 24/7 crew transferred VT65 to alternate supply shortly after TH2UL dumped. | Ottawa | Adverse Weather | Rain
3287 | 2003 | 3 | 21 | 0.48264 |  | 160 | 8 | 3 | Hinchey | 4.16kV | TH2UL | Three customers were dumped to effect repairs to overhead, as of result of pole fires caused by weather conditions. | Ottawa | Scheduled Outage | Repair
8628 | 2006 | 6 | 29 | 0.61319 |  | 134 | 321 | 463 | Hinchey | 13.2kV | TH2UL | Extreme weather caused a Skywire at Parkdale & Scott to fall and open circuit. | Ottawa | Adverse Weather | Lightning
16567 | 2010 | 7 | 27 | 0.3375 |  | 68 | 701 | 1090 | Hinchey | 13.2kV | TH2UL | Blown pothead at vault VT65 @ 250 Lanark caused circuit breaker TH09 (TH2UL) @ Hinchey to open. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15157 | 2009 | 9 | 23 | 0.59583 |  | 82 | 1 | 1 | Hinchey | 13.2kV | TH2UL | The CB1 Breaker at vault VT75 195 Clearview found open, txs tested, equipment inspected no problem found. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4538 | 2003 | 11 | 29 | 0.65417 |  | 351 | 6 | 1 | Hinchey | 13.2kV | TH2UL | VT65 T2 red phase fuse found blown caused by a flash over of the 13kv transformer bus at a support insulator. CB1 opened to interrupt vault supply by 24/7, station crew called in to make emergency repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6331 | 2005 | 3 | 27 | 0.79097 |  | 168 | 4 | 2 | Hinchey | 12/7.2kV | TH3SH | Circuit TH3SH tripped due to faulted cable. Circuit sectionalized to restore customers. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20728 | 2012 | 6 | 9 | 0.33889 |  | 300 | 225 | 45 | Hinchey | 13.2kV | TH3SH | Vault VT630 transformer bus at 99 Holland was isolated to allow crews to replace leaking transformers. | Ottawa | Scheduled Outage | Preventive Maintenance
15134 | 2009 | 9 | 20 | 0.77917 |  | 64 | 11 | 10 | King Edward | 13.2kV | TK06 | Squirrel contact caused transformer fuse to open on Howick St. Refused and power restored. | Ottawa | Foreign Interference | Animal
16484 | 2010 | 7 | 17 | 0.60139 |  | 184 | 3 | 1 | King Edward | 13.2kV | TK09 | Customer at 55 Byward was isolated to allow electrician to replace defective breaker. 1 Customer affected | Ottawa | Defective Equipment
5718 | 2004 | 8 | 25 | 0.87778 |  | 22 | 147 | 400 | King Edward | 13.2kV | TK1AC | TK1AC (TK19) tripped on grd fault. Dagmar T4 xfmr affected and was transferred to TO3AC supply. TK1AC was isolated. 400 customers in Vanier were afected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3976 | 2003 | 8 | 31 | 0.53472 |  | 42 | 293 | 418 | King Edward | 13.2kV | TK1AC | TK1AC cable indicated ground fault on TK19 breaker. Cable isolated load restored via alternate supply. | Ottawa | Unknown/Other | No Apparent Cause
10116 | 2007 | 3 | 13 | 0.35 |  | 56 | 1 | 1 | King Edward | 13.2kV | TK24 | Blown arrester at VT691 caused fuse to blow at Ashbury College. Arrester replaced and power restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13879 | 2009 | 1 | 19 | 0.56111 |  | 32 | 3 | 5 | KING EDWARD | 4.16kV | TK26 | Isolated transformer 65A1D-0055 at 467 Cloverdale Rd to restore power to Pedestal SP26 that had to be replaced after being hit by a snowplough | Ottawa | Scheduled Outage | Repair
7728 | 2005 | 12 | 15 | 0.42014 |  | 10 | 1 | 8 | King Edward | 13.2kV | TK26 | Transformer located at Rockcliffe Way/Rock Ave isolated due to upgrading services | Ottawa | Scheduled Outage | Construction
7729 | 2005 | 12 | 15 | 0.42014 |  | 10 | 1 | 8 | King Edward | 13.2kV | TK26 | Transformer located at Rock Ave/Rockcliffe Way isolated due to upgrading services | Ottawa | Scheduled Outage | Construction
9902 | 2007 | 1 | 4 | 0.46875 |  | 79 | 4 | 3 | King Edward | 13.2kV | TK2AC | Transformer located at 429 N Lansdowne isolated due to animal contact | Ottawa | Foreign Interference | Animal
19842 | 2012 | 1 | 17 | 0.45347 |  | 22 | 2 | 5 | KING EDWARD | 13.2kV | TK2AC | Transformer X23042 isolated at pedestal SP26 to disconnect the service | Ottawa | Scheduled Outage | Repair
19862 | 2012 | 1 | 19 | 0.39583 |  | 175 | 15 | 5 | King Edward | 13.2kV | TK2AC | Transformer #X23042 located at 467 Cloverdale Rd opnened by crew for secondary pedestal replacement. | Ottawa | Scheduled Outage | Construction
20109 | 2012 | 3 | 3 | 0.725 |  | 169 | 386 | 406 | King Edward | 13.2kV | TK2AC | Wind storm at the time S17134 on Mariposa 2 phases found open and SCV66901-F 2 phases also found open, no spare fuses available, S17134 jumpered, crews did not want to operate in VT669 nor VT670, TK26 (TK2AC) opened by SCADA to allow closing in of SCV66901 fuses from remote loaction. | Ottawa | Adverse Weather | Wind
8002 | 2006 | 3 | 9 | 0.70486 |  | 95 | 2 | 1 | King Edward | 4.16kV | TK2AC | Tree branch broke and hit transformer switch at 320 Cloverdale Rd and caused the fuse to blow | Ottawa | Tree Contacts | Tree Limb Fallen
17719 | 2011 | 3 | 16 | 0.45972 |  | 39397 | 16423 | 75 | King Edward TK | 13.2kV | TK2AC | VT728 at 29 Mackay was isolated at request of OFD due to working firre. VT539 at 20 Charlevoix & VT498 at 40 Landry were briefly affected during switching to isolate VT728. | Ottawa | Adverse Environment | Fire
20231 | 2012 | 3 | 26 | 0.46181 |  | 26 | 3 | 7 | King Edward | 13.2kV | TK2AC | Transformer #X21697 located at 143 Acacia opened by crew to make repairs for streetlights. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14223 | 2009 | 4 | 26 | 0.83333 |  | 1296 | 1035 | 290 | King Edward | 13.2kV | TK2AC | A tree fell on the O/H at 195 Acacia which caused two fuses to blow at SCV66901 in VT669 which is located at 21 Durham. The TK26 circuit that feeds that vault had to be open because of saftey reason in that vault. | Ottawa | Adverse Weather | Wind
18159 | 2011 | 5 | 15 | 0.49861 |  | 52 | 4 | 5 | King Edward | 4.16kV | TK2AC | Replaced blown fuse at transformer X23366 at 404 Cloverdale Rd (squirrel contact) | Ottawa | Foreign Interference | Animal
18535 | 2011 | 6 | 27 | 0.5625 |  | 10 | 0 | 2 | King Edward |  | TK2AC | Isolated transformer X29421 at 198 Lisgar Rd to replaced secondary connections | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7173 | 2005 | 8 | 20 | 0.2875 |  | 157 | 1047 | 400 | TK | 13.2kV | TK2AC | TK26 breaker tripped on ground time, line sectionalized & last section of cable to normal open point isolated. Manual FCI indicators at VT669, VT807 & VT728 all flagged, unknown when last re-set. RTU failure @ TK extended length of outage. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16787 | 2010 | 8 | 20 | 0.45139 |  | 10 | 3 | 20 | King Edward | 13.2kV | TK2AC | Hot line clamp at the corner of Cloverdale and Old Prospect needed repairs resulting in short outage to customers. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11201 | 2007 | 8 | 30 | 0.057639 |  | 415 | 1397 | 600 | King Edward | 13.2kV | TK2AC | SCV66901 WB fuses open due to limb contact. TK26 (TK2AC) open to prevent possible fuse flash to close to line man in Vault | Ottawa | Tree Contacts | Tree Limb Fallen
11271 | 2007 | 9 | 7 | 0.76458 |  | 249 | 1308 | 599 | King Edward | 13.2kV | TK2AC | SCV66901-F Blue phase blew due to multiple branches on o/h circuit, and switch and arrester were replaced on Fairview. When 24/7 crew closed SCV66901-F Blue phase it flashed over, and caused TK2AC (TK26) to trip. SCV66901-F isolated and power restored. Email sent to advised on damage at VT669. | Ottawa | Tree Contacts | Tree Limb Fallen
19244 | 2011 | 9 | 23 | 0.42708 |  | 210 | 35 | 10 | King Edward | 4.16kV | TK2AC | Isolated transformer X39470 at 290 Mariposa Ave to replace pole | Ottawa | Scheduled Outage | Construction
19257 | 2011 | 9 | 26 | 0.39583 |  | 285 | 19 | 4 | KING EDWARD | 13.2kV | TK2AC | Transformer X39470 at 290 Mariposa Ave isolated to allow for pole change | Ottawa | Scheduled Outage | Construction
11404 | 2007 | 9 | 27 | 0.86458 |  | 25 | 0 | 10 | King Edward | 13.2kV | TK2AC | Transformer #OTT6837 at 150 Acacia Ave isolated to allow for repairs to hot line clamp & broken mid-span bracket | Ottawa | Scheduled Outage | Repair
19496 | 2011 | 10 | 29 | 0.45 |  | 57 | 6 | 6 | King Edward |  | TK2AC | Replaced blown fuse feeding transformer X23269 at 403 Wood Ave (Squirrel contact) | Ottawa | Foreign Interference | Animal
11119 | 2007 | 8 | 21 | 0.42014 |  | 115 | 10 | 5 | King Edward | 13.2kV | TK2AC (SCV66901 | Transformer located at 580 Old Prospect isolated due to service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
18763 | 2011 | 7 | 18 | 0.8125 |  | 308 | 1106 | 3202 | King Edward TS | 13.2kV | TK2AC (TK26) | 2 fuses found blown at SCV66901 on the TK2AC circuit. Circuit was patrolled. TK26 breaker was opened for crew to safely refuse the SC and Breaker closed and held. | Ottawa | Adverse Weather | Wind
11212 | 2007 | 8 | 30 | 0.24861 |  | 103 | 687 | 400 | King Edward | 13.2kV | TK2AC SCV669001 | To repair down wire on Springfield north of Buena Vista found one blown fuse found in Vault VT 669 @ 21 Durham, lightning and heavey rain | Ottawa | Adverse Weather | Rain
11216 | 2007 | 8 | 30 | 0.20347 |  | 362 | 60 | 10 | King Edward | 13.2kV | TK2AC SCV669001 | Replaced defective transformer at 464 Springfield. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11052 | 2007 | 8 | 14 | 0.78056 |  | 66 | 220 | 200 | King Edward | 4.16kV | TK2AC SCV66901 | Tree on the o/h conductor on Springfield Drive, was burning and crew was concerned the conductor may break. SCV66901 circuit isolated for crew to remove tree. | Ottawa | Tree Contacts
7817 | 2006 | 1 | 18 | 0.29167 |  | 26 | 351 | 809 | King Edward | 13.2kV | TK3UG | Fault was later determined to be in TK15 metalclad due to a water leak from building roof. | Ottawa | Adverse Environment | Flooding
10010 | 2007 | 2 | 10 | 0.45833 |  | 360 | 6 | 1 | King Edward | 13.2kV | TK4TS | At VT430 @ 30 Nicholas the R1-L trip because of a burnt connection at the transformer caused by water leaking onto the connection. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4417 | 2003 | 11 | 9 | 0.15972 |  | 145 | 208 | 86 | King Edward | 13.2kV | TK5TS | 13 kv vault VT786 at 141 Clarence isolated for Globe Electric to perform routine maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
13709 | 2008 | 12 | 7 | 0.21875 |  | 113 | 2 | 10 | KING EDWARD | 12/7.2kV | TK5TS | VT787 at 141 Clarence was isolated to allow construction of safe work area for future cable work PC10a #5184 established | Ottawa | Scheduled Outage | Construction
20845 | 2012 | 6 | 23 | 0.081944 |  | 181 | 519 | 172 | Slater |  | TK6TS | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
18486 | 2011 | 6 | 24 | 0.42569 |  | 351 | 6 | 1 | KING EDWARD |  | TK6TS | At 10:13am crews isolated VT408 at 80 Rideau because the ceiling was coming down on the equipment in the vault. 1 customer affected for 351 mins. King Edward TK6TS ( ID # 18486) | Ottawa | Adverse Environment
6107 | 2004 | 12 | 30 | 0.52569 |  | 141 | 85 | 36 | Slater | 13.2kV | TK6TS | TK6TS line tripped due to cable fault between VT9 & VT84. Line was sectionalized to find faulted section and power on & off as breaker was used to test cable sections. Rideau Centre and Chateau Laurier were part of outage. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17463 | 2011 | 1 | 2 | 0.13889 |  | 58 | 598 | 686 | Lisgar | 13.2kV | TL12 | A flood at 395 Somerset Street West (VT239) cause TL12 breaker to open. 686 customers affected for 32 minutes and 536 affected for 26 minutes. VT239 remains isolated until vault is repaired. | Ottawa | Foreign Interference
13215 | 2008 | 9 | 10 | 0.34722 |  | 97 | 10 | 6 | Lisgar | 13.2kV | TL13 | TL13 Breaker tripped due to Vault at VT268, 255 Albert faulting due to water leakage. All customers restored except for VT268, which will be repaired and placed back into service on Friday. | Ottawa | Defective Equipment
15386 | 2009 | 11 | 13 | 0.78125 |  | 1785 | 60 | 2 | Lisgar | 13.2kV | TL13 | Vault VT268 at 255 Albert was isolated to allow contractor to perform customer maintenance. | Ottawa | Scheduled Outage
13797 | 2008 | 12 | 26 | 0.55417 |  | 512 | 10 | 5 | Lisgar | 13.2kV | TL13 | TL13 CB tripped at the station. Crews report that CB1 at VT268 (255 Albert, Kent Square) had tripped on all 3 phases. Crews isolated VT268 and the remaining customers where restored. Customer owned secondary insulator flashed in the vault. | Ottawa | Foreign Interference | Imminent Equipment Failure Detected
5151 | 2004 | 5 | 15 | 0.48819 |  | 43 | 401 | 559 | Lisgar | 13.2kV | TL1SB | TL1SB cable was automatically removed from service. Bronson T2 transfomer and SB06 & SB07 feeders were interrupted. All load restored on an alternate supply. Suspected cable fault. | Ottawa | Defective Equipment
12642 | 2008 | 6 | 15 | 0.78333 |  | 10 | 120 | 722 | Lisgar | 13.2kV | TL2SB | Severe lightining storm in effect. TL18 Breaker tripped. Breaker closed by SCADA and held. | Ottawa | Adverse Weather | Lightning
7418 | 2005 | 10 | 3 | 0.069444 |  | 34 | 439 | 775 | Lisgar | 13.2kV | TL2SB | TL18 (TL2SB) breaker opened, causing an outage to T4 bank at Bronson substation. | Ottawa | Unknown/Other | No Apparent Cause
20604 | 2012 | 5 | 26 | 0.23542 |  | 637 | 32 | 3 | Lisgar | 13.2kV | TL2TS | Vault VT124 @ 365 Laurier was isolated to allow contractor to perform vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
4415 | 2003 | 11 | 8 | 0.43056 |  | 296 | 10 | 2 | Lisgar | 13.2kV | TL2TS | VT569 13kv main and transformer busses isolated at 221 Lyon St. to perform standard vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
3094 | 2003 | 1 | 2 | 0.55903 |  | 77 | 1 | 1 | Lisgar TS | 13.2kV | TL3SB | Vault was isolated at request of customer to replace 600 volt switch. Switch on the 9th floor was arcing. Vault had to be isolated to replace unit. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5559 | 2004 | 7 | 24 | 0.45208 |  | 201 | 3 | 1 | Lisgar | 13.2kV | TL3SB | PT connection repaired in VT289 (265 Carling), fuse in R1-F replaced and power restored. Call originally came in at 10:51am as a customer problem (2 floors out of power in an apatment building). Call came back in at 12:26pm as no power to complete building. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15338 | 2009 | 10 | 31 | 0.49514 |  | 279 | 9 | 2 | Lisgar | 13.2kV | TL3SB | TVM2855 at 17 Aberdeen was isolated today to allow contractor to perform customer owned maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
19563 | 2011 | 11 | 12 | 0.45486 |  | 172 | 9 | 3 | Lisgar | 13.2kV | TL3SB | Vault TVM2855CHZ at 333 Preston was isolated to allow contractor (Carelton Electric) to perform customer vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
13615 | 2008 | 11 | 15 | 0.43056 |  | 260 | 9 | 2 | Lisgar | 13.2kV | TL3SB | 13 kv vault TVM2855CHZ at 333 Preston & TNS2779CZZ were isolated together for routine maintenance by Carleton Electric & pothead repair by Hydro Ottawa cable crew. | Ottawa | Scheduled Outage | Preventive Maintenance
17310 | 2010 | 11 | 20 | 0.41667 |  | 255 | 8 | 2 | Lisgar | 13.2kV | TL3SB | TVM2855CHZ and TV3652 at 453 Preston were isolated to allow the customer's contractor to perform standard vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
7832 | 2006 | 1 | 20 | 0.625 |  | 863 | 28 | 8 | Lisgar | 13.2kV | TL3TS | Suspected cable fault on TL5TS between VT507 and VT61. Crews checked cable and found no problem. Cause of trip was later determined to be a fault in the vault VT25, at 200 Kent St. VT25 was not restored as previously thought due to the vault breaker being tripped. The circuits tripped again while attempting to energize VT25, see outage report #7833. Defective CT's were replaced by Schneider Electric and vault was re-energized on Jan 22nd, however building was supplied by generators sinceJjan 21st. | Ottawa | Defective Equipment
7833 | 2006 | 1 | 20 | 0.86806 |  | 2 | 0 | 4 | Lisgar | 13.2kV | TL3TS | TL21 breaker tripped while attempting to restore power to VT25 at 200 Kent. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9779 | 2006 | 12 | 2 | 0.21042 |  | 31 | 1 | 1 | Lisgar | 13.2kV | TL4SB | TL08 breaker tripped, circuit which would normally be on pot was carrying 1 vault, VT195 (Glebe H.S.) due to the TR1FB outage. Circuit was sectionalized via SCADA. cable fault on 202 cable. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20732 | 2012 | 6 | 10 | 0.38889 |  | 195 | 32 | 10 | Lisgar | 13.2kV | TL4TS | At 9:20 am, vault VT452 transformer bus at 234 Laurier was isolated to allow contractor to take measurements for future isolation. 10 customers were affected. | Ottawa | Scheduled Outage | Construction
19734 | 2011 | 12 | 17 | 0.51944 |  | 128 | 21 | 10 | Lisgar | 13.2kV | TL4TS | Vault VT452 at 234 Laurier was isolated to allow contractor to perform vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
7752 | 2005 | 12 | 21 | 0.46111 |  | 333 | 188 | 173 | TS | 13.2kV | TL4TS | A contractor broke into the primary cable duct & caused a cable fault in the basement of 188 Bank st, VT571. Power was restored to all customers except VT571. VT571 was isolated to identify damaged cable before power could be restored.. | Ottawa | Foreign Interference | Dig-in
7818 | 2006 | 1 | 18 | 0.55972 |  | 400 | 7 | 1 | Lisgar | 13.2kV | TL5TS | CB1 breaker tripped, vault was filled with smoke when 24/7 arrived. Vault was isolated from Hydro Ottawa system to allow crew to investigate. No possible cause was found. | Ottawa | Unknown/Other
8005 | 2006 | 3 | 10 | 0.11389 |  | 356 | 7 | 2 | LISGAR | 13.2kV | TL5TS | 150 & 180 MACLAREN OUT OF POWER. VT82 & VT68 RESPECTIVLY. CT'S @ VT 82 FOUND FLASHED, FAULT CURRENT CAUSED CB1 BREAKER @ VT68 TO OPEN. CREW RESTORED VT68 AND VT82 was isolated. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20837 | 2012 | 6 | 23 | 0.081944 |  | 117 | 716 | 367 | Slater |  | TL5TS | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
20846 | 2012 | 6 | 23 | 0.081944 |  | 286 | 521 | 172 | Slater |  | TL6TS | Due to the Slater TS T3 transformer failure, VT68 at 180 Maclaren had their CB1 trip. It wasn't until OPD called that we knew this customer was still without power. | Ottawa | Loss of Supply | HEPC Station Fault
19739 | 2011 | 12 | 18 | 0.34792 |  | 245 | 20 | 5 | Lisgar | 13.2kV | TL6TS | Vault VT 612 at 202 Laurier was isolated to allow contractor perform grounding repair and arc proofing incomming cables. | Ottawa | Scheduled Outage | Repair
17464 | 2011 | 1 | 2 | 0.11667 |  | 792 | 29 | 20 | Lisgar | 13.2kV | TL7TS | Water from floor above leaked into 13kv vault VT239 @ 395 Somerset, causing the TL12 breaker at lisgar to trip. 13kv Vault VT239 was repaired and serviced. | Ottawa | Adverse Environment | Flooding
14453 | 2009 | 6 | 3 | 0.40764 |  | 166 | 385 | 139 | Lisgar | 13.2kV | TL7TS | VT886 at 453 Cooper was isolated for planned customer maintenance. Note: customer count as per OMS. VT886 feeds town houses on Lisgar from customer owned secondary supply. | Ottawa | Scheduled Outage | Preventive Maintenance
5752 | 2004 | 8 | 31 | 0.40833 |  | 122 | 22 | 11 | Lisgar | 13.2kV | TL7TS | Customer vault shut down for routine maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
11883 | 2007 | 12 | 25 | 0.6625 |  | 425 | 31 | 19 | LISGAR | 13.2kV | TL7TS | Insulators on the 13kV transformer bus flashed at VT239, 395 Somerset. The main Breaker in the vault tripped as well as TL12 breaker at Lisgar. All customers were restored except for 395 Somerset. It remained off until repairs in vault were completed. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5724 | 2004 | 8 | 26 | 0.58403 |  | 1 | 10 | 600 | TL & TS | 13.2kV | TLS1UF | When transfering load from Lisgar TS to Slater at Hydro One's request due to load levels exceeding the 10 day LTR a parallel was made between TL & TS. When the parallel was made both TL06 & TS66 opened on overcurrent. There was a transformer out of service at Lisgar at the time the transfer was to be made so we had Hydro One remove T1 at Slater TS from service. The voltages were then matched and the parallel was made. | Ottawa | Unknown/Other
5415 | 2004 | 7 | 1 | 0.36111 |  | 76 | 1380 | 1200 | Lisgar | 13.2kV | TLS1UF & TLS2FB | Lightening strike at Lyon and Somerset caused concertic neutral damage on TLS1UF cable dip to Nepean affecting TLS2FB. TLS1UF line isolated and load restored on TLS2FB at Florence. | Ottawa | Lightning | Direct Strike
11910 | 2008 | 1 | 9 | 0.27917 |  | 37 | 1850 | 3000 | Carling TM | 115kV | TM Y Bus | When Hydro One closed in there SC2Y Bus Capacitor Bank, it tripped out the Carling TM Y Bus on differential. Approximately 3000 customers affected for Crews restored power to all customers at 7:19am. | Ottawa | Loss of Supply | HEPC Station Fault
11197 | 2007 | 8 | 29 | 0.77361 |  | 13 | 0 | 2 | Carling | 13.2kV | TM05 | TM05 opened and locked out, circuit closed in via SCADA and holding | Ottawa | Adverse Weather
15800 | 2010 | 3 | 15 | 0.37153 |  | 18 | 0 | 1 | CALRING TM | 13.2kV | TM19 | transformer 1638 Carling isolated to allow for repairs to riser wire | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5160 | 2004 | 5 | 18 | 0.54514 |  | 178 | 285 | 252 | Carling | 13.2kV | TM1AH | Lightening strike burned through the span guys north of Kenwood on Churchill and came in contact with the overhead causing damage to insulators, cross arm and jumpers. Circuit isolated with load transferred. | Ottawa | Lightning | Direct Strike
6945 | 2005 | 7 | 13 | 0.91944 |  | 2 | 23 | 679 | Carling TM | 13.2kV | TM1AH | Circuit opened during lightening storm.Circuit has no recloser. Circuit closed back in via scada. | Ottawa | Adverse Weather | Lightning
19028 | 2011 | 8 | 27 | 0.73889 |  | 306 | 10 | 2 | Carling | 13.2kV | TM1AH | VT1812 & VT1824 @ 861 Clyde Ave were isolated to contractor to complete secondary work in customer vaults. | Ottawa | Scheduled Outage | Preventive Maintenance
11196 | 2007 | 8 | 29 | 0.77361 |  | 13 | 55 | 252 | Carling | 13.2kV | TM1AH | TM23 opened and locked out, circuit closed back in via SCADA and holding | Ottawa | Adverse Weather
11704 | 2007 | 11 | 13 | 0.53542 |  | 95 | 104 | 256 | Carling | 13.2kV | TM1AH | TM1AH circuit tripped interrupting 250 customers out of Hillcrest Sub and 6 comercial vaults. Suspect cable fault but still undetermined at this time. | Ottawa | Unknown/Other
6739 | 2005 | 6 | 15 | 0.62639 |  | 43 | 186 | 260 | TM | 13.2kV | TM1AH, TM3UC | The customers switchgear at VT549, 495 Richmond rd failed causing TM1AH & UL1AH ( TM3UC ) cct's to open. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19861 | 2012 | 1 | 19 | 0.48056 |  | 293 | 857 | 1764 | Carling | 13.2kV | TM1AK | A back hoe doing snow removal damaged the AK04 overhead at 962 Dynes causing the AK04 breaker to open and TM07 (TM1AK) breaker to open also. The damaged section was isolated and customers remained off while repairs were performed. | Ottawa | Foreign Interference | Vehicle
7839 | 2006 | 1 | 21 | 0.54514 |  | 7 | 87 | 920 | Carling | 13.2kV | TM1AK | AK03 and AK04 breakers operated apparently taking out TM1AK from Carling. Switching by SCADA to restore load. To be patrolled at a later time. | Ottawa | Unknown/Other | No Apparent Cause
3269 | 2003 | 3 | 18 | 0.27361 |  | 30 | 460 | 920 | Carling | 13.2kV | TM1AK | Cable fault on TM1AK line between Fisher and Carling sub. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14179 | 2009 | 4 | 15 | 0.76875 |  | 68 | 9 | 8 | Carling | 13.2kV | TM1AK | 24/7 reports broken switch @ 1093 Arnot Rd. Switch replaced all power restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6629 | 2005 | 6 | 1 | 0.69583 |  | 2 | 20 | 600 | Carling | 13.2kV | TM1AK | lightning caused AK03 circuit to open whick appears to have opened TM1AK. TM1AK is the direct feed for the T1 bank at Fisher. | Ottawa | Adverse Weather | Lightning
3800 | 2003 | 7 | 5 | 0.21528 |  | 50 | 721 | 865 | Carling | 13.2kV | TM1AK | TM1AK line tripped during lightning storm all load picked up via TM1DK | Ottawa | Lightning | Direct Strike
8888 | 2006 | 8 | 1 | 0.13264 |  | 68 | 1043 | 920 | Carling | 13.2kV | TM1AK | TM1AK tripped at the same time as AK04 & AK07, AK03 also A/R. Station was checked & all feeders restored. | Ottawa | Adverse Weather | Lightning
13108 | 2008 | 8 | 18 | 0.5875 |  | 90 | 1733 | 2162 | Carling | 13.2kV | TM1AK | A tree fell onto AK07 circuit at Prince of Wales and Normandy. Other circuits overtripped, reason remains undetermined. | Ottawa | Tree Contacts | Tree Fallen
18983 | 2011 | 8 | 20 | 0.54236 |  | 67 | 1965 | 1760 | Carling | 13.2kV | TM1AK | A bird made contact with 303 & TM1DK o/h lines outside of Fisher sub. The flash caused TM1DK to trip (no customers), 303 to A/R & AK04 to trip. The AK04 trip apparently went past the AKT1 CB & caused TM07 (TM1AK) cable to trip. The multiple breaker trips at TM appear to have caused a fire alarm at the station. H - 1 dispatched a crew & the fire dept. No problem was found at TM, Damaged arrestors were cleared from o/h lines & all power restored. There were also some damaged insulators on the 4kv underbuild. | Ottawa | Foreign Interference | Bird
6011 | 2004 | 12 | 10 | 0.99375 |  | 1 | 15 | 920 | Carling | 13.2kV | TM1AK | TM1AK circuit opened in conjuntion with AK04 and AK06 circuits auto reclosing. Circuit was closed via Scada and held.Circuit feeds AKT1 and AKT3 transformers. Which caused interruption to 5 circuits | Ottawa | Adverse Weather
15998 | 2010 | 4 | 26 | 0.40486 |  | 165 | 28 | 10 | Carling | 13.2kV | TM1DK | TP5036 on Jenscott was isolated to to re train secondary cables in the base of TP5036. | Ottawa | Scheduled Outage
5081 | 2004 | 4 | 30 | 0.6125 |  | 54 | 494 | 644 | Carling | 13.2kV | TM1UJ | TM1UJ (TM21 breaker) line tripped due to a defective pothead at VT310, 175 Loretta. UJT1 at bayswater and two vaults, City garage at 175 Loretta, & VT225, British Bank Note at 975 Gladstone affected. Cable section between VT310 & VT225 was isolated and all customers restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6615 | 2005 | 5 | 29 | 0.35694 |  | 46 | 498 | 650 | Carling TM | 13.2kV | TM1UJ | 08:34 scada indicate TM21 (TM1UJ) opened fault. Customers restored @ 09:20 via TH2UJ circuit. Suspected cable fault between Carling TM and Bayswater Sub. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7397 | 2005 | 9 | 29 | 0.53472 |  | 60 | 515 | 644 | Carling | 13.2kV | TM1UJ | tree limb on SH3UJ at bayswater and Laurel. | Ottawa | Tree Contacts | Tree Limb Fallen
17289 | 2010 | 11 | 17 | 0.67222 |  | 63 | 752 | 716 | Carling | 13.2kV | TM2AK | TM2AK line opened out of Carling. Suspected cable between Fisher and Carling on TM2AK. Section isolated and customers restored via alternate feed. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14374 | 2009 | 5 | 18 | 0.95972 |  | 135 | 13 | 10 | Carling | 13.2kV | TM2SB | A cable fault on the TM2SB cable bet VT857 and VT538 in the Carling/Irving St area. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10685 | 2007 | 6 | 20 | 0.74097 |  | 246 | 8 | 2 | Carling | 13.2kV | TM2SB | VT266 at 785 Carling and VT202 at 560 Rochester isolated for contractotr to perform vault maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
4115 | 2003 | 9 | 21 | 0.37847 |  | 305 | 10 | 2 | TM | 13.2kV | TM2SB | Planned outage for customer routine maintenance @ VT266 & VT202 | Ottawa | Scheduled Outage | Preventive Maintenance
9349 | 2006 | 9 | 30 | 0.34931 |  | 200 | 7 | 2 | Carling | 13.2kV | TM2SB | VT857 & VT857W1 was isolated to allow contractor to preform maintenance on vaults. | Ottawa | Scheduled Outage | Preventive Maintenance
3698 | 2003 | 7 | 7 | 0.46319 |  | 8 | 42 | 316 | TM | 13.2kV | TM2SH | TM30 GCB tripped due to a bird contact at the SH3UJ P/P/H on Gladstone. The circuit was feeding SHT2, UJT3 (on pot only ) & VT225 & VT310. The line was sectionalized via scada & all load was restored in 8 minutes. | Ottawa | Foreign Interference | Bird
11908 | 2008 | 1 | 8 | 0.56042 |  | 68 | 5 | 6 | Carling | 13.2kV | TM2UC | At 12:52pm TM19 circuit breaker opened. 1725 Woodward Avenue, a blown pothead was found to have caused the outage. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3214 | 2003 | 2 | 26 | 0.48958 |  | 100 | 4 | 6 | Carling | 13.2kV | TM2UC | TM2UC tripped on ground timed relay due to a cable fault in blue phase cable section between TM2UC P/P/H and S-381 @ SW1361, Hillel Lodge. 7 vaults in Carling & Clyde area were affected. Custromers were transferred to TM3UC and Hillel Lodge to TW1UC to restore. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12706 | 2008 | 6 | 21 | 0.43681 |  | 455 | 15 | 2 | Carling | 13.2kV | TM2UC | At 10:29am, vaults VT202 (560 Rochester) and VT266 ( 785 Carling) was isolated to allow a contractor to perform customer vault maintenance, 2 customers were affected and power was restored at 6:04pm. Carling (TM2UC). ID#12706. | Ottawa | Scheduled Outage | Preventive Maintenance
18813 | 2011 | 7 | 25 | 0.28056 |  | 126 | 65 | 31 | Carling | 13.2kV | TM2UC | Blown pothead on TM3UC going to VT393 due to crow contact caused UC06, TM19 and TM28 to open. | Ottawa | Foreign Interference | Animal
13841 | 2009 | 1 | 6 | 0.37639 |  | 80 | 5 | 4 | CARLING | 13.2kV | TM3UC | Cable dig in at 269 Avondale caused TM3UC Line to trip. Line isolated and customers transferred. | Ottawa | Foreign Interference | Dig-in
20097 | 2012 | 3 | 3 | 0.37014 |  | 31 | 3 | 5 | Carling | 13.2kV | TM3UC | TM28 breaker opened interupting TM3UC circuit, calls to fire and police made and customer calls checked, no reports, feeder closed back in by SCADA, patrol to take place later, high winds and multiple outages going on at the time. | Ottawa | Adverse Weather | Wind
20100 | 2012 | 3 | 3 | 0.54653 |  | 28 | 2 | 5 | Carling | 13.2kV | TM3UC | Previously reported lightening arrestor was observed by the crew just arrived to repair coming in contact with the neutral on the TM3UC cable dip. | Ottawa | Adverse Weather | Wind
17829 | 2011 | 4 | 4 | 0.71042 |  | 33 | 3 | 5 | CARLING | 13.2kV | TM3UC | TM3UC line, TM28 Breaker tripped due to Pole fire at Kenwood and Broadview. Circuit sectionalized and power restored. | Ottawa | Defective Equipment
3366 | 2003 | 4 | 13 | 0.48611 |  | 21 | 69 | 196 | Carling | 13.2kV | TM3UC | While isolating TH1UL line complete. TH1UL-L switch at Clifton substation failed. Causing a Fire in sub-station. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3367 | 2003 | 4 | 13 | 0.69306 |  | 2 | 7 | 500 | Carling | 13.2kV | TM3UC | While restoring power to Clifton sub-station. TM3UC-UL1AH switch failed to operate propperly circuit was opened, and TM3UC-UL1AH switch was closed. All load restored to on TM3UC as well as restoration of the Clifton UL02, UL03, UL04, and UL14 circuits for the first time. | Ottawa | Defective Equipment
3554 | 2003 | 6 | 12 | 0.40278 |  | 1 | 0 | 1 | Carling | 13.2kV | TM3UC | Interruption was required in order to restore power to VT640 (Turpin Auto Body). Vault was being feed from TM3UC line which blew a O/H pothead. Vault was switched over to TM2UC line to restore power, then the TM3UC line was isolated for repairs. Outage was for 1 min when TM3UC-L3, was opened and TM2UC-L3 closed. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6946 | 2005 | 7 | 13 | 0.91944 |  | 2 | 7 | 196 | Carling TM | 13.2kV | TM3UC | Circuit opened during lightening storm.Circuit has no reclosing. Circuit closed back in via scada. | Ottawa | Adverse Weather | Lightning
10920 | 2007 | 7 | 21 | 0.16389 |  | 124 | 4 | 4 | Carling | 13.2kV | TM3UC | TM28 breaker at Carling opened interupting TM3UC, switching performed to restore 3 of 4 customers affected, no access to VT395 at West Gate SC. | Ottawa | Unknown/Other | No Apparent Cause
18814 | 2011 | 7 | 25 | 0.28056 |  | 126 | 8 | 4 | Carling | 13.2kV | TM3UC | Blown pothead on TM3UC going to VT393 due to crow contact caused UC06, TM19 and TM28 to open. | Ottawa | Foreign Interference | Animal
16727 | 2010 | 8 | 12 | 0.8125 |  | 580 | 10 | 1 | Carling | 13.2kV | TM3UC | VT395 at 2171 carling was Isolated to allow crews to Inspect 13 kv transformer bus and test transformers after a flash over due to falling cieling debris. S/G also issued to Shaun Lauzon of seimens to allow for clean and torque of vault equipment | Ottawa | Foreign Interference | Foreign Object
9455 | 2006 | 10 | 18 | 0.4 |  | 19 | 1 | 4 | CARLING | 13.2kV | TM3UC | While partially isolating VT75 195 Clearview switch # s27056 was opened to provide isolation on a section of UL1Ah line as per OTO 17-1321 in Job#1289. This switch was the dip pole to SC17647. Not the in-line switch for UL1AH circuit. Which had no nomenclature on system board or in the field. Contractor applied a set of portable ground on a live switch at VT75 195 clearview causing outage on TM3UC circuit. | Ottawa | Human Element | Incorrect Records
9770 | 2006 | 12 | 1 | 0.51528 |  | 33 | 3 | 5 | Carling | 13.2kV | TM3UC | TM3UC o/h circuit tripped due to a truck hitting a guy-wire into TM3UC and TM09 circuits. | Ottawa | Foreign Interference | Vehicle
20094 | 2012 | 3 | 3 | 0.23889 |  | 173 | 6 | 2 | Carling | 13.2kV | TM4SB | VT29 at 588 Booth was planned isolation to allow customer's contractor to install new cables in metalclad in VT29, due to improper nomenclature the neighbouring vault TV7760 at 808 Bronson was included in the isolation. TV7760 was restored when the mistake was discovered. | Ottawa | Scheduled Outage | Preventive Maintenance
16134 | 2010 | 5 | 25 | 0.41319 |  | 33 | 0 | 12 | Carling | 13.2kV | TM4SB | The TM06(TM4SB) circuit trip, while closing the TM06 fault finding the TM04(TM2SB) also trip, The TM04 close back in via scada and held. A cable fault bet VT29(588 Booth) and station TM. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5488 | 2004 | 7 | 13 | 0.64583 |  | 60 | 814 | 814 | TM | 13.2kV | TM4SB | TM4SB cable faulted, customers 13kv loop breaker @ VT29 was found tripped, main OCB closed, but after fault finding, no problem was found with customer equipment. Cable was sectionalized & put on pot from TM & held but after further sectionalizing, fault proved to be in first section of cable. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17019 | 2010 | 9 | 28 | 0.81458 |  | 474 | 17013 | 4505 | Overbrook | 13.2kV | TO Q1 | at 16:21 SCADA indicated Overbrook TS Q1 BUS was all out (NOTE: TO44 CB indicated Open Close and OPEN) TO44 (T01UT) feeding Eastview - 182 customers restored at 20:20 & 1521 Customers restored at 20:49 TO46 (TO2UB) feeding beechwood - 841 customers restored at 18:20 & 897 customers restored at 00:15 TO48 (1802) - 93 cutomers affected, restored at 21:10 (NOTE: crews experienced a Flash during switching at VT50) TO50 (TR02UQ) - 66 Customers affected, restored at 19:33 TO52 (SOT2) - feeding Overbrook DS, 894 customers affected, restored at 17:30 TO54 (SOT4) - feeding Overbrook DS, 11 customers affected, restored at 17:46 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8198 | 2006 | 4 | 28 | 0.13194 |  | 115 | 647 | 1206 | Overbrook | 13.2kV | TO1UB | TO1UB circuit (TO32) tripped, load transferred to alternate supply & line isolated. Cause unknown at this time. Crew on site @ VT812 waited for on-call from High school to give access. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3614 | 2003 | 6 | 26 | 0.85417 |  | 70 | 700 | 600 | Beechwood | 13.2kV | TO1UB | B.Cowtan reported the UBT1 xfmr off load & the S-439 @ sc1437 found open which feeds the UBT1 xfmr | Ottawa | Unknown/Other | No Apparent Cause
14421 | 2009 | 5 | 28 | 0.18194 |  | 47 | 1115 | 1424 | Overbrooke | 13.2kV | TO1UT | TO1UT circuit trip interupted the load to the Eastview UTT1 & UTT2 transformers. Circuit isolated and load restored via the TO2UT circuit. | Ottawa | Defective Equipment
10035 | 2007 | 2 | 18 | 0.44444 |  | 120 | 24 | 12 | Overbrook | 12/7.2kV | TO2UB | KT521 struck by vehicle and transformer isolated to repostion unit on base. 1 Provender Ave. | Ottawa | Foreign Interference | Vehicle
17700 | 2011 | 3 | 11 | 0.21181 |  | 85 | 4 | 3 | Overbrook |  | TO2UB | SW1716 at 400 Den Haag was isolated to allow Station crew to repair the faulty gas gauge. | Ottawa | Scheduled Outage | Repair
17701 | 2011 | 3 | 11 | 0.21181 |  | 85 | 4 | 3 | Overbrook | 13.2kV | TO2UB | SW1716 at 400 Den Haag was isolated to allow the Station Crew to repair a defective gas pressure gauge on the switch gear | Ottawa | Scheduled Outage | Repair
12214 | 2008 | 4 | 1 | 0.14167 |  | 174 | 229 | 608 | Overbrook | 13.2kV | TO2UB | There was a pole fire on the TO2UB circuit just north of 500 St Laurent.SW162,SC4239,SW1716 and SC62 had to be shoveled out causing the delay or restoration | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12382 | 2008 | 5 | 3 | 0.093056 |  | 44 | 892 | 1216 | Overbrook | 13.2kV | TO2UB | TO1UB (TO32) auto reclosed, TO2UB (TO46) opened, crew patrolled and found nothing, breaker was closed by SCADA and held | Ottawa | Unknown/Other | No Apparent Cause
3491 | 2003 | 5 | 27 | 0.14583 |  | 70 | 1125 | 1326 | Overbrook |  | TO2UB | TO2UB & TO2AP circuits tripped after Lightning arresters at 906 Montreal Rd blow on overhead. UB05 &07 circuits where transferred via scada to To3ub circuit. At 03:35 A.M. approx 300 customers power restored. Unable to close UB06 circuit via scada or at the station. UB06 circuit transferred to UB K1Y1 breaker. Approx 210 customers load restored at 04:11 AM. 24/7 reports 3 blown lightning arrester found blown clear at 906 Montreal Rd. To2UB load restored 04:40 AM. | Ottawa | Defective Equipment
14620 | 2009 | 6 | 26 | 0.75278 |  | 45 | 7 | 1751 | Overbrook | 13.2kV | TO2UB | At 18:04pm TO2UB and TO2AP circuit breaker opened. Customer reported lighting hit a transformer X23392 in front of McDonalds on Montreal Rd. Transformer is on UB03 and TO2UB, TP2AP are above it on the pole. Crews patrol line and found blown fuse at 800 Montreal Rd. Beechwood T2 load was restored by switching feed from TO2UB to TO4ACB. | Ottawa | Lightning | Lightening Strike on adjacent circuit
5424 | 2004 | 7 | 1 | 0.62292 |  | 126 | 1680 | 800 | TO | 13.2kV | TO2UB | Cct opened during storm. Customer count does not include UBT2, separate rpt made. Cct closed after patrol. | Ottawa | Adverse Weather | Lightning
8637 | 2006 | 7 | 2 | 0.029167 |  | 18 | 183 | 610 | Overbrook | 13.2kV | TO2UB | 24/7 patrolled and found nothing, daytime patrol for Tuesday | Ottawa | Lightning | Direct Strike
8644 | 2006 | 7 | 2 | 0.48264 |  | 94 | 139 | 608 | Overbrook | 13.2kV | TO2UB | A tree in the o/h line near Beechwood sub caused TO2UB to trip & TO1UB to A/R. Began transferring load to alternate supply, tree was removed & feeder restored. | Ottawa | Tree Contacts | Inadequate Trimming
12782 | 2008 | 7 | 3 | 0.45625 |  | 255 | 60 | 14 | Overbrooke | 13.2kV | TO2UB | Transformer KT523 at 126 Provender isolated for replacement and soil removal. | Ottawa | Scheduled Outage | Repair
16690 | 2010 | 8 | 8 | 0.17361 |  | 980 | 212 | 13 | Overbrook | 13.2kV | TO2UB | Vault VT186 at 568 Montreal Rd transformer bus isolated to allow crew to replace PCB transformer. When re-energization was attempted one of the new transformers blew, requiring isolation to be expanded to entire vault. Repairs made, equipment checked ok and re-energized successfullty. | Ottawa | Scheduled Outage | Repair
9075 | 2006 | 8 | 28 | 0.42153 |  | 18 | 396 | 1321 | Overbrook | 13.2kV | TO2UB | TO2UB circuit tripped @ 10:07. Ottawa Police & Ottawa Fire reports NO calls. Circuit was closed via scada all load restored. No fault found on patrol of TO2UB line. | Ottawa | Unknown/Other | No Apparent Cause
20130 | 2012 | 3 | 6 | 0.56181 |  | 132 | 229 | 196 | Overbrook | 13.2kV | TO2UT | Blown Pothead On Vanier Parkway behind Eastview Sub caused TO2UT (TO43 Breaker) to trip. Pot head isolated and power restored. | Ottawa | Defective Equipment
8359 | 2006 | 5 | 26 | 0.81667 |  | 66 | 1387 | 1261 | Overbrook | 13.2kV | TO2UT | P/H to VT712 on Presland found flashed after reports of sparking wires. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14928 | 2009 | 8 | 10 | 0.6125 |  | 294 | 10 | 2 | Overbrook | 13.2kV | TO2UT | VT761 at 282 Depuis, Ottawa Police reported Human Contact on Customer 600V secondary. Crews dispatched and reported that 290 Dupuis also without power and R1-F had blown. Received ESA to re-energize, 282 Dupuis Secondaries to remain open until repairs are complete. | Ottawa | Foreign Interference | Foreign Object
9767 | 2006 | 12 | 1 | 0.62014 |  | 8 | 160 | 1200 | Overbrook | 12/7.2kV | TO2UT | The TO43 breaker tripped under hold off, called police and fire dept they had nothing, closed in and holding. Later patrol did not reveal any obvious problems. | Ottawa | Adverse Weather | Ice Storm
7748 | 2005 | 12 | 19 | 0.74306 |  | 175 | 3678 | 1261 | Overbrook | 13.2kV | TO2UT | Blown pothead @ pole feeding VT.227 @ Mcarthur High School. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3345 | 2003 | 4 | 16 | 0.96389 |  | 236 | 7795 | 2578 | Overbrook | 13.2kV | TO2UT & TO3UT | TO2UT & TO3UT circuits were opened by SCADA due to a pole fire on Vanier Parkway across from Coventry. The on call crew were called in to brace the pole top. Switching was done to restore as many customers as possible. The remaining customers were restored when bracing completed and lines restored. | Ottawa | Adverse Weather | Rain
15693 | 2010 | 1 | 30 | 0.39583 |  | 8 | 141 | 1058 | Dagmar | 4.16kV | TO3AC | While restoring TO3AC line to normal at Dagmar station ACT1 & ACT2 load was interrupted. Outage to 1058 customers in the Vanier area. | Ottawa | Human Element | Switching Errors
8438 | 2006 | 6 | 7 | 0.36528 |  | 63 | 693 | 1020 | Overbrook | 13.2kV | TO3AC | Squirrel was found in overhead circuits of TO3AC & TO4ACB @ 485 Donald st. The squirrel made contact on the TO4ACB circuit which then flashed over to the TO3AC | Ottawa | Foreign Interference | Animal
18663 | 2011 | 7 | 15 | 0.45833 |  | 109 | 1834 | 2892 | Overbrooke | 13.2kV | TO3AC | TO4ACB (TO31 and TO3AC (TO49) tripped at the same time. Circuit sectionalized to restore power. 24/7 crew found defective pothead blown on TO4ACB at 358 Montford. TO3AC (TO31) on the same pole has flashed insulators and burnt lightning arrester. | Ottawa | Defective Equipment
8751 | 2006 | 7 | 17 | 0.98403 |  | 46 | 1150 | 1500 | Overbrook | 13.2kV | TO3AC | TO3AC circuit is on the same pole as AA05 P/P/H which was hit by lightning. | Ottawa | Adverse Weather | Lightning
13118 | 2008 | 8 | 19 | 0.29514 |  | 28 | 590 | 1265 | Overbrook | 13.2kV | TO3AC | TO3AC line tripped at the same time as TO4ACB. Load was restored from SCADA. Later patrol did not reveal a cause for trip. | Ottawa | Unknown/Other
19335 | 2011 | 10 | 7 | 0.37778 |  | 26 | 1222 | 2821 | Overbrook | 13.2kV | TO3AC | TO3AC & TO4ACB circuits tripped circuits patrolled found no problem. | Ottawa | Unknown/Other | No Apparent Cause
19700 | 2011 | 12 | 8 | 0.22153 |  | 55 | 1241 | 2755 | Overbrook | 13.2kV | TO3AC | TO49 breaker tripped and load was transfered to TO4ACB line. Crew to investigate problem. Overbrook ID#19700 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17478 | 2011 | 1 | 11 | 0.38194 |  | 45 | 10 | 14 | Overbrook | 13.2kV | TO3AP | MT1475 at 194 Borealis was isolated to reposition transformer on to pad. | Ottawa | Scheduled Outage
6229 | 2005 | 2 | 23 | 0.44028 |  | 222 | 698 | 623 | Overbrooke | 13.2kV | TO3AP | TO3AP pothead in VT229 failed causing feeder breaker to trip. Circuir sectionalized,399 customers restored @ 11:35 . VT229 isolated, 223 customers restored @ 11:52. VT229 remaind off untill repairs made. Vault restored at 14:16 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6277 | 2005 | 3 | 13 | 0.58333 |  | 237 | 40 | 10 | Overbrooke | 13.2kV | TO3AP | Defective transformer M1478 was isolated and changed by the on-call crew. Transformer had fluctuating voltage and was making excessive noise. Sparks were seen by 24/7 coming from transformer | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10408 | 2007 | 5 | 11 | 0.57431 |  | 145 | 948 | 623 | Overbrook | 13.2kV | TO3AP | Circuit TO3AP tripped due to faulted cable in section between VT363 and VT648. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5548 | 2004 | 7 | 22 | 0.27569 |  | 48 | 498 | 623 | TO | 13.2kV | TO3AP | TO47 GCB feeding TO3AP cable tripped due to a cable fault between substation & VT363. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13036 | 2008 | 8 | 11 | 0.28264 |  | 80 | 857 | 643 | Overbrook | 13.2kV | TO3AP | Scada indicates TO47 breaker opened. 24-7 dispatched to help restore lost load. At VT363 (522 Montreal Rd.) Mark Brown reports that there is smoke and cause of fault is at this vault. Mark dispatched to adjacent vault and TO47 as isolation. John Streng, Mark Brown and system completed OTO# AUG-11-08-SP-TR to isolate VT363 and restore power to TO3AP line VIA through TO1AP. TO47 Breaker targets read RED & WHITE PHASE on time. ID# 13036. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9338 | 2006 | 9 | 29 | 0.97778 |  | 152 | 1120 | 623 | Overbrook | 13.2kV | TO3AP | TO3AP sectionalized suspected cable fault between VT648 and VT363 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13552 | 2008 | 11 | 3 | 0.85069 |  | 56 | 497 | 532 | Overbrook | 13.2kV | TO3AP | Primary cable failed in customer vault, VT363 @ 522 Montreal rd. Defective cable isolated & power restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13564 | 2008 | 11 | 4 | 0.97222 |  | 144 | 24 | 10 | Overbrook | 13.2kV | TO3AP | VT363 @ 522 Montreal rd was isolated by cable crew to install plywood barrier in transformer enclosure. The barrier will provide a safe work area for repair of damaged TO3AP cable. | Ottawa | Scheduled Outage | Repair
4545 | 2003 | 12 | 2 | 0.38125 |  | 157 | 489 | 187 | OVERBROOK | 13.2kV | TO3UB | VT811 AT 520 ST. LAURENT ISOLATED FOR ROUTINE MAINTENANCE AFFECTING 187 CUSTOMERS | Ottawa | Scheduled Outage | Preventive Maintenance
8003 | 2006 | 3 | 9 | 0.80625 |  | 974 | 32 | 2 | Overbrook | 13.2kV | TO3UT | Red phase fuse found blown in VT 540. All transformers check ok in vault @ 318 Savard. Found insulation failure on R phase cable supplying Xfmr bus. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6381 | 2005 | 4 | 6 | 0.65625 |  | 160 | 2150 | 1317 | TO | 13.2kV | TO3UT | Hydro -1 T3 at station tripped off on diferential fault, squirrel found under transformer, no load loss. TO30 breaker opened at the same time. Load was transferred & line sectionalized, no fault found. | Ottawa | Loss of Supply | HEPC Circuit Fault
5486 | 2004 | 7 | 13 | 0.0034722 |  | 191 | 38 | 12 | Overbrook | 13.2kV | TO3UT | Scheduled outage to 13KV xfmr bus at VT402, 355 Montreal Rd, for routine maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
4120 | 2003 | 9 | 22 | 0.52431 |  | 93 | 1737 | 1317 | TO | 13.2kV | TO3UT | TO3UT overhead line (TO30) tripped when 3 arrestors blew outside by the Hurdman Pumping Station (VT180). | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15164 | 2009 | 9 | 24 | 0.97708 |  | 99 | 696 | 573 | Overbrook | 13.2kV | TO3UT | At 22:07 TO30 tripped. Crews dispatched and circuit TO3UT was sectionalized and customers restored via circuit transfers. | Ottawa | Unknown/Other
13804 | 2008 | 12 | 28 | 0.37639 |  | 58 | 571 | 591 | Overbrook | 13.2kV | TO3UT | Due to skywire falling down into 13kV & 4kV underbuild caused UTT1 breaker and TO30 (TO3UT) breaker to trip, and UT03 auto reclosed. Crew cut skywire clear. 1875 customers affected, 1284 customers affected from UTT1, and 591 customers affected from TO30 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8390 | 2006 | 5 | 31 | 0.69931 |  | 2 | 42 | 1261 | Overbrook | 13.2kV | TO4ACB | TO31 GCB tripped when an isolated section of TO2UT line was placed on potential as per OTO. Customers interrupted were from TO2UT line which was being carried on TO4ACB. TO2UT line was re-isolated & breaker closed successfully restoring power to all customers. A quick patrol did not reveal any obvious problem but it will require a more detailed investigation. | Ottawa | Unknown/Other
8439 | 2006 | 6 | 7 | 0.36528 |  | 63 | 525 | 500 | Overbrook | 13.2kV | TO4ACB | Squirrel was found in overhead circuits of TO3AC & TO4ACB @ 485 Donald st.TO4ACB also was carrying TO2UT circuit. | Ottawa | Foreign Interference | Animal
18615 | 2011 | 7 | 8 | 0.43472 |  | 419 | 7 | 1 | Overbrook | 13.2kV | TO5UB | While restoring VT286 @ 1 Sandridge from the first shut down the insulator flashed over in the vault. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14269 | 2009 | 4 | 30 | 0.60069 |  | 10 | 2 | 12 | Beaverbrook | 12/7.2kV | TP6152 | Transformer #TP6152 located at 34 Tiffany isolated for clearance | Kanata | Scheduled Outage | Preventive Maintenance
20727 | 2012 | 6 | 9 | 0.26319 |  | 121 | 26 | 13 | Riverdale | 4.16kV | TR02 | Replaced blown fuse feeding transformer X31958 at 110 Glenview Ave (Squirrel contact) | Ottawa | Foreign Interference | Animal
8337 | 2006 | 5 | 22 | 0.95833 |  | 85 | 3 | 2 | Riverdale | 12/7.2kV | TR02UQ | Switch TR-05 at Hurdman Station, lock has been removed and switch opened causing loss of supply to RCMP Headquartes and Hurdman Pumping Station. Vandulism reported to Ottawa Police, case # 06-134879. | Ottawa | Foreign Interference | Vandalism
16799 | 2010 | 8 | 23 | 0.60278 |  | 71 | 1938 | 3700 | Riverdale | 13.2kV | TR02UQ | Contractor working at RCMP @ 1200 Vanier PKWY cut into cable | Ottawa | Foreign Interference
18004 | 2011 | 4 | 28 | 0.059722 |  | 124 | 525 | 1205 | Riverdale | 13.2kV | TR05 | At 1:26 TR05 breaker at Riverdale tripped. TR1FB was also suppling the SBT1 load. System swtiching restored the load at Bronson.The 5 customers on the 13KV were transferred to TR2FB supply. No cause has been found at this time. Riverdale TR05. No Access to Glebe High school. Crew onsite until after hour contact could open door to building. | Ottawa | Unknown/Other
5933 | 2004 | 11 | 26 | 0.62778 |  | 101 | 42 | 25 | Riverside | 13.2kV | TR07 | Cutout at transformer OTT5431 replaced. 25 customers on Riverside & Bank affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7799 | 2006 | 1 | 12 | 0.35347 |  | 106 | 11 | 6 | Riverdale | 12/7.2kV | TR09 | Transformer #OTT2413 located at 20 Findlay Ave isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
11947 | 2008 | 1 | 17 | 0.37847 |  | 110 | 28 | 15 | Riverdale | 4.16kV | TR09 | Isolated and replaced transformer OTT3246 at 186 Holmwood Ave | Ottawa | Scheduled Outage | Preventive Maintenance
19844 | 2012 | 1 | 17 | 0.37569 |  | 85 | 11 | 8 | RIVERDALE | 13.2kV | TR09 | Transformer X29991 at 8 Madawska Dr isolated to allow for service upgrade | Ottawa | Scheduled Outage
3123 | 2003 | 1 | 18 | 0.33333 |  | 60 | 9 | 9 | Riverdale TS | 13.2kV | TR09 | 24/7 refused cut-out at 27 Lakeside av. After removing dead squirel. | Ottawa | Foreign Interference | Animal
11966 | 2008 | 1 | 21 | 0.60417 |  | 75 | 9 | 7 | Riverdale | 13.2kV | TR09 | Transformer #OTT959 located at 544 Queen Elizabeth isolated due to service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
19883 | 2012 | 1 | 24 | 0.42014 |  | 55 | 9 | 10 | Riverdale | 13.2kV | TR09 | Transformer #X21663 located at 248 Fifth Ave opened by crew to re-arrange plant for pole change | Ottawa | Scheduled Outage | Construction
19885 | 2012 | 1 | 24 | 0.50764 |  | 46 | 13 | 17 | Riverdale | 13.2kV | TR09 | X29834 at 234 Fifth Ave. was isolated to rearrange plant | Ottawa | Scheduled Outage | Preventive Maintenance
15688 | 2010 | 1 | 27 | 0.41667 |  | 25 | 6 | 14 | Riverdale | 13.2kV | TR09 | Transformer #X29854 located at Broadway and Torrington isolated to install new triplex service | Ottawa | Scheduled Outage | Construction
13938 | 2009 | 2 | 6 | 0.56111 |  | 60 | 5 | 5 | RIVERDALE | 4.16kV | TR09 | xfmr X29840 at 12 Morris isolated to allow for service change | Ottawa | Scheduled Outage | Construction
4788 | 2004 | 2 | 13 | 0.54861 |  | 34 | 1 | 1 | Riverdale | 13.2kV | TR09 | Transformer # 953 isolated to replace defective equipment. 1 Customer affected in power outage at 90 Broadway. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12061 | 2008 | 2 | 19 | 0.41458 |  | 53 | 7 | 8 | Riverdale | 12/7.2kV | TR09 | At 09:57 trans at 224 Holmwood Ave in order to change a service | Ottawa | Scheduled Outage
17649 | 2011 | 2 | 27 | 0.34722 |  | 568 | 9 | 1 | Riverdale | 13.2kV | TR09 | A bad cable bet the main switch R1-F to the transformers at VT820 @ 860 Thronton. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20138 | 2012 | 3 | 7 | 0.38889 |  | 130 | 37 | 17 | Riverdale | 13.2kV | TR09 | At 09:20 transformer X29834 at 238 Fifth Avenue was isolated to allow crew to replace pole. 17 customers were affected for 130 minutes. Riverdale (TR09) ID#20138 | Ottawa | Scheduled Outage
15788 | 2010 | 3 | 11 | 0.4375 |  | 30 | 3 | 6 | Riverdale | 13.2kV | TR09 | Isolated transformer X29804 at 38 Morris St to re-locate triplex service | Ottawa | Scheduled Outage | Emergency Services Request
15808 | 2010 | 3 | 16 | 0.38542 |  | 35 | 6 | 10 | RIVERDALE TR | 13.2kV | TR09 | Transformer X27727 at 14 Woodlawn isolated to allow for transformer change (per Jamie Lawlor) | Ottawa | Scheduled Outage | Construction
17730 | 2011 | 3 | 18 | 0.40278 |  | 123 | 18 | 9 | Riverdale | 13.2kV | TR09 | Transformer X27740 at 21 Oakland Ave. Isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
20195 | 2012 | 3 | 21 | 0.71319 |  | 2 | 50 | 1489 | Riverdale | 13.2kV | TR09 | Controlled outage to make repairs to broken line tap at Fifth and Ralph | Ottawa | Scheduled Outage
17751 | 2011 | 3 | 22 | 0.375 |  | 115 | 21 | 11 | Riverdale | 13.2kV | TR09 | Transformer #X27749 located at 37 Woodlawn opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
17771 | 2011 | 3 | 23 | 0.53125 |  | 69 | 12 | 10 | Riverdale | 13.2kV | TR09 | Transformer #X27740 located at 25 Oakland Ave opened by crew to relocate transformer to different pole | Ottawa | Scheduled Outage | Construction
15860 | 2010 | 3 | 27 | 0.32639 |  | 436 | 174 | 24 | Riverdale | 13.2kV | TR09 | crew opened two transformers and disconnected a single phase local for fire dept for clearance for fire trucks. | Ottawa | Scheduled Outage | Emergency Services Request
17790 | 2011 | 3 | 28 | 0.40278 |  | 250 | 54 | 13 | Riverdale | 13.2kV | TR09 | Transformer X27749 at 37 Woodlawn Ave isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
17802 | 2011 | 3 | 29 | 0.40278 |  | 110 | 24 | 13 | Riverdale | 4.16kV | TR09 | isolated transformer X27729 at 496 Queen Elizabeth Dr for pole change | Ottawa | Scheduled Outage | Construction
4965 | 2004 | 4 | 4 | 0.4125 |  | 42 | 6 | 8 | Riverdale | 13.2kV | TR09 | Vines caused fuse to blow at transformer 55D4B-0579. Cleared vines & transformer switch refused to restore 8 customers 0n Melgund & Ralph. | Ottawa | Foreign Interference | Foreign Object
17836 | 2011 | 4 | 6 | 0.4 |  | 113 | 15 | 8 |  |  | TR09 | TP3840 at 19 Ralph Street isolated to relocate transformer for pole change | Ottawa | Scheduled Outage | Construction
17841 | 2011 | 4 | 6 | 0.54514 |  | 76 | 11 | 9 | Riverdale | 4.16kV | TR09 | X29833 at 25 Thornton Ave isolated for transformer change | Ottawa | Scheduled Outage | Construction
17850 | 2011 | 4 | 7 | 0.40625 |  | 195 | 29 | 9 | RIVERDALE | 13.2kV | TR09 | TRANSFORMER AT x27740, 21 OAKLAND AVE, OUT TO ALLOW CREWS TO INSTALL NEW POLE | Ottawa | Scheduled Outage | Construction
17898 | 2011 | 4 | 11 | 0.53542 |  | 63 | 12 | 11 | Riverdale | 13.2kV | TR09 | Transformer #X29826 located at 19 Thornton Ave opened by crew to re-arrange plant for future pole replacement. | Ottawa | Scheduled Outage | Construction
17910 | 2011 | 4 | 12 | 0.38194 |  | 259 | 39 | 9 | Riverdale | 13.2kV | TR09 | Transformer X29833 at 27 Thornton isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
8144 | 2006 | 4 | 13 | 0.36806 |  | 50 | 14 | 17 | Riverdale | 13.2kV | TR09 | Isolated transformer 55D4B-0474 at 34 Melgund St due to pole fire | Ottawa | Adverse Weather | Rain
17918 | 2011 | 4 | 13 | 0.40625 |  | 120 | 16 | 8 | Riverdale | 13.2kV | TR09 | Transformer X29898 at 35 Thornton isolated for pole change | Ottawa | Scheduled Outage | Construction
17921 | 2011 | 4 | 13 | 0.375 |  | 150 | 25 | 10 | Riverdale | 12/7.2kV | TR09 | Trans at 25 Oakland Ave was isolated in order to change a pole | Ottawa | Scheduled Outage
17932 | 2011 | 4 | 14 | 0.39444 |  | 222 | 22 | 6 | Riverdale | 13.2kV | TR09 | Transformer X29822 at 15 Monk St. Isolated for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
17955 | 2011 | 4 | 18 | 0.39583 |  | 135 | 29 | 13 | Riverdale | 13.2kV | TR09 | Trans X27729 at 496 Popes Lane was isolated in order to set a new pole | Ottawa | Scheduled Outage | Construction
6435 | 2005 | 4 | 21 | 0.44097 |  | 181 | 15 | 5 | Riverdale | 13.2kV | TR09 | Isolated Transformer # 0381 at 819 Lyon to repair service | Ottawa | Scheduled Outage | Preventive Maintenance
15969 | 2010 | 4 | 21 | 0.34931 |  | 37 | 2 | 4 | RIVERDALE | 13.2kV | TR09 | Transformer X29849 opened @ 4 Thornton for a service upgrade | Ottawa | Scheduled Outage | Construction
18002 | 2011 | 4 | 27 | 0.53472 |  | 100 | 18 | 11 | Riverdale | 13.2kV | TR09 | Isolated transformer X29826 at 19 Thornton Ave to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Construction
20420 | 2012 | 4 | 30 | 0.4875 |  | 122 | 22 | 11 | Riverdale | 4.16kV | TR09 | Tree branch came in contact with transformer bushing X29882 at 288 Fifth Ave Trimmed tree and sleeved out bad area in 4/0 solid primary concuctor. | Ottawa | Tree Contacts | Tree Limb Fallen
14280 | 2009 | 5 | 1 | 0.44097 |  | 20 | 2 | 5 | Riverdale | 13.2kV | TR09 | Transformer #X29991 located at 15 Crescent Hts isolated for a service removal | Ottawa | Scheduled Outage | Preventive Maintenance
18093 | 2011 | 5 | 4 | 0.54444 |  | 69 | 13 | 11 | Riverdale | 13.2kV | TR09 | Transformer X29826 @19 Thornton ave was open to allow crew to upgrade secodary service at 15 Thornton. 1 customer were affected. Riverdale TR19 | Ottawa | Scheduled Outage
14324 | 2009 | 5 | 7 | 0.72222 |  | 315 | 1162 | 679 | Riverdale | 13.2kV | TR09 | Pole fire on the pole to VT820 at Bank and Thorton caused 3 phases of TR09 overhead to come down at Monk and Thorton. Recloser was blocked when reports of a pole fire came in so the next fault caused the breaker to open and stay open. Overhead was sectionalized at Ralph and Thorton, for isolation, and most of the customers picked up while repairs were made. Apon re-energization of O/H, crew requested TR09 breaker to be opened to untangle phases. Breaker closed after 3 min. | Ottawa | Adverse Environment | Fire
10404 | 2007 | 5 | 11 | 0.46667 |  | 68 | 18 | 16 | Riverdale | 13.2kV | TR09 | Fuse blew due to squirrel on line. | Ottawa | Foreign Interference | Animal
18136 | 2011 | 5 | 12 | 0.40139 |  | 112 | 11 | 6 | Riverdale | 13.2kV | TR09 | Transformer X29825 at 9 Thornton isolated to allow for transfer of secondary | Ottawa | Scheduled Outage | Construction
18141 | 2011 | 5 | 12 | 0.51389 |  | 86 | 6 | 4 | Riverdale | 13.2kV | TR09 | Transformer X29849 was open to allow crew to trasnfer plant @ 1 Thornton. 4 customers were affected. Riverdale (TR09) | Ottawa | Scheduled Outage
8286 | 2006 | 5 | 13 | 0.28611 |  | 93 | 6 | 4 | Riverdale | 13.2kV | TR09 | Transformer #OTT6689 located at 380 Queen Elizabeth isolated due to tree interference | Ottawa | Tree Contacts | Inadequate Trimming
14373 | 2009 | 5 | 17 | 0.39861 |  | 51 | 3 | 4 | Riverdale | 13.2kV | TR09 | Due to squirrel contact, transformer fuse at 1 Oakland blew, crew re-fused. Riverdale (TR09) ID#14373 | Ottawa | Foreign Interference | Animal
18173 | 2011 | 5 | 18 | 0.39167 |  | 210 | 238 | 68 | Riverdale | 13.2kV | TR09 | Temp switch at Broadway and Craig St was open to allow tree trimmers to remove tree at rear of Broadway Ave using crane. 68 customers were affected. Riverdale (TR09) | Ottawa | Scheduled Outage
18175 | 2011 | 5 | 18 | 0.39583 |  | 120 | 8 | 4 | Riverdale | 13.2kV | TR09 | Transformer #X29849 located at 3 Thornton Ave opened by crew to transfer service | Ottawa | Scheduled Outage | Construction
18178 | 2011 | 5 | 18 | 0.70833 |  | 186 | 25 | 8 | Riverdale | 13.2kV | TR09 | Transformer X29822 at 16 Monk St isolated to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
5194 | 2004 | 5 | 21 | 0.40625 |  | 80 | 20 | 15 | RIVERSIDE | 12/7.2kV | TR09 | Isolation of transformer at 5 Monk St to relocate services. | Ottawa | Scheduled Outage | Construction
8336 | 2006 | 5 | 21 | 0.84722 |  | 70 | 10 | 9 | Riverdale | 13.2kV | TR09 | Crew has cleared trees and refused transformer feeding customers on Fifth ave. | Ottawa | Tree Contacts | Inadequate Trimming
12493 | 2008 | 5 | 29 | 0.37639 |  | 108 | 20 | 11 | Riverdale | 13.2kV | TR09 | Transformer #55D4B-0579 located 43 Melgund isolated due to vine interference | Ottawa | Tree Contacts | Inadequate Trimming
5227 | 2004 | 5 | 30 | 0.86528 |  | 35 | 7 | 12 | Riverdale | 13.2kV | TR09 | Fuse blew at transformer OTT2411 at 316 Fifth Ave. due to a squirrell. 12 customers on Fifth were affected. Crew refused and restored. | Ottawa | Foreign Interference | Animal
16171 | 2010 | 6 | 1 | 0.37847 |  | 25 | 5 | 11 | Riverdale | 4.16kV | TR09 | Isolated transformer X29895 at 42 Craig St for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
10519 | 2007 | 6 | 3 | 0.32847 |  | 52 | 1 | 1 | Riverdale | 13.2kV | TR09 | At 07:43 trans at 23 Monk St opened due to squirrel contact.. Refused and power restored | Ottawa | Foreign Interference | Animal
6681 | 2005 | 6 | 8 | 0.31389 |  | 58 | 2 | 2 | Riverdale | 13.2kV | TR09 | Replaced Transformer fuse at Transformer #0102 at 3 Craig st because of squirrell | Ottawa | Foreign Interference | Animal
8461 | 2006 | 6 | 10 | 0.33472 |  | 90 | 9 | 6 | Riverdale | 13.2kV | TR09 | Transformer #OTT951 located at 582 Queen Elizabeth Driveway isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
12595 | 2008 | 6 | 10 | 0.67986 |  | 131 | 17 | 8 | Riverdale | 4.16kV | TR09 | refused blown fuse on transformer 55D4A-0122 at 5 Ella St | Ottawa | Adverse Weather | Lightning
18415 | 2011 | 6 | 15 | 0.26667 |  | 101 | 8 | 5 | Riverdale | 13.2kV | TR09 | Transformer #X29882 located at 288 Fifth opened up due to animal contact | Ottawa | Foreign Interference | Animal
20779 | 2012 | 6 | 15 | 0.36736 |  | 61 | 9 | 9 | Riverdale | 4.16kV | TR09 | replaced broken switch feeding transformer X29821 at 2 Capital Park | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6751 | 2005 | 6 | 16 | 0.28194 |  | 61 | 7 | 7 | Riverdale | 13.2kV | TR09 | Transformer #6689 located at 374 Queen Elizabeth isolated due to animal interference (squirrel) | Ottawa | Foreign Interference | Animal
8505 | 2006 | 6 | 18 | 0.25694 |  | 130 | 30 | 14 | Riverdale | 13.2kV | TR09 | Fuse on transformer 55D4D-0519 at 20 Morris St opened due to an animal contact (squirrel) | Ottawa | Foreign Interference | Animal
8558 | 2006 | 6 | 20 | 0.61181 |  | 194 | 39 | 12 | Riverdale | 13.2kV | TR09 | Transformer #OTT3758 located at 54 Sunset Blvd isolated due to animal contact | Ottawa | Foreign Interference | Animal
8648 | 2006 | 7 | 2 | 0.94167 |  | 23 | 4 | 11 | Riverdale | 13.2kV | TR09 | Squirell in the overhead caused a transfomer cutout to open | Ottawa | Foreign Interference | Animal
8651 | 2006 | 7 | 2 | 0.86111 |  | 45 | 10 | 12 | Riverdale | 13.2kV | TR09 | Tangled services required transformer to be opened for repairs | Ottawa | Tree Contacts | Inadequate Trimming
12783 | 2008 | 7 | 3 | 0.45833 |  | 135 | 22 | 10 | Riverdale | 13.2kV | TR09 | Cut out feeding O/H transformer at 92 Broadway Ave in Ottawa opened due to tree branch contact. | Ottawa | Tree Contacts | Inadequate Trimming
3808 | 2003 | 7 | 5 | 0.1875 |  | 173 | 72 | 25 | Riverdale | 13.2kV | TR09 | 2 fuses on TR09 line at Madawaska area due to lighning. Crew patrolled and refused. | Ottawa | Lightning | Direct Strike
8672 | 2006 | 7 | 6 | 0.47222 |  | 130 | 20 | 9 | Riverdale | 13.2kV | TR09 | Isolated transformer OTT3259 at 266 Holmwood Dr to install new pole | Ottawa | Scheduled Outage | Construction
10820 | 2007 | 7 | 8 | 0.90764 |  | 73 | 12 | 10 | Riverdale | 13.2kV | TR09 | Transformer OTT6167 at 25 Lakeside blew its fuse, cause unknown. Re-fused transformer, all customers restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10827 | 2007 | 7 | 9 | 0.65139 |  | 52 | 4 | 5 | Riverdale | 4.16kV | TR09 | Fuse was found blown on transformer OTT4774 at 27 Dows Lake Rd due contact with a squirrel | Ottawa | Foreign Interference | Animal
16434 | 2010 | 7 | 9 | 0.5 |  | 463 | 8 | 1 | Riverdale | 13.2kV | TR09 | VT656 at 315 Holmwood was isolated from Hydro Ottawa at the customer's request to repair their defective secondary main. Routine maintenacne was performed by Schneider Electricr at the same time. | Ottawa | Defective Equipment
12824 | 2008 | 7 | 12 | 0.28264 |  | 28 | 5 | 10 | Riverdale | 4.16kV | TR09 | Replaced blown fuse at switch feeding transformer X27748 at 3 Oakland Ave (Squirrel contact ) | Ottawa | Foreign Interference | Animal
18754 | 2011 | 7 | 17 | 0.81181 |  | 14 | 346 | 1485 | Riverdale | 13.2kV | TR09 | TR09 Tripped during severe storm, closed back in 14 minutes later | Ottawa | Adverse Weather | Wind
18769 | 2011 | 7 | 17 | 0.82569 |  | 153 | 3787 | 1485 | Riverdale TS | 13.2kV | TR09 | TR09 Tripped again, crew cut clear some damaged equipment in order to get the breaker closed. | Ottawa | Adverse Weather | Wind
18723 | 2011 | 7 | 18 | 0.82778 |  | 187 | 34 | 11 | Riverdale | 13.2kV | TR09 | Tree down at 957 Bronson, crew isolated from S23955 to remove tree and restore power. | Ottawa | Tree Contacts
18732 | 2011 | 7 | 18 | 0.82778 |  | 162 | 30 | 11 | Riverdale | 13.2kV | TR09 | S239554 isolated to remove fallen tree. 11 customers affected and power restored. | Ottawa | Tree Contacts
5537 | 2004 | 7 | 20 | 0.83333 |  | 15 | 1 | 5 | Riverdale | 13.2kV | TR09 | O/H transformer at 51 Sunset interrupted to repair connections. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14790 | 2009 | 7 | 20 | 0.49931 |  | 21 | 2 | 5 | Riverdale | 13.2kV | TR09 | Transformer #X29862 located at 580 Queen Elizabeth Driveway isolated due to animal contact | Ottawa | Foreign Interference | Animal
18787 | 2011 | 7 | 21 | 0.42083 |  | 22 | 26 | 72 | Riverdale |  | TR09 | S10936 blew due to tree branches falling on the circuit. Crew cleared the trees and refused the switch. Affecting customers on Broadway, sidney cook, george watts lane. | Ottawa | Tree Contacts | Tree Limb Fallen
16536 | 2010 | 7 | 22 | 0.34792 |  | 53 | 4 | 5 | Riverdale | 13.2kV | TR09 | Transformer X39476 located at 49 Dow's Lake Rd opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
10999 | 2007 | 8 | 5 | 0.34792 |  | 44 | 9 | 12 | Riverdale | 13.2kV | TR09 | Transformer #OTT3758 located at 34 Sunset Blvd isolated due to animal contact | Ottawa | Foreign Interference | Animal
14916 | 2009 | 8 | 5 | 0.52778 |  | 46 | 5 | 6 | Riverdale | 4.16kV | TR09 | Isolated transformer X29840 at 13 Morris St to replace service | Ottawa | Scheduled Outage | Emergency Services Request
18886 | 2011 | 8 | 7 | 0.33194 |  | 44 | 12 | 17 | Riverdale | 13.2kV | TR09 | Replaced blown fuse at transformer X29888 at 44 Muriel St (Squirrel contact) | Ottawa | Foreign Interference | Animal
11114 | 2007 | 8 | 21 | 0.38056 |  | 47 | 7 | 9 | Riverdale | 13.2kV | TR09 | Transformer #OTT4111 located at 20 Kippewa Dr isolated due to animal contact | Ottawa | Foreign Interference | Animal
9017 | 2006 | 8 | 22 | 0.29097 |  | 91 | 17 | 11 | Riverdale | 4.16kV | TR09 | Fused switch to transformer 55D4A-0202 at 13 Gordon St was found blown due to squirrel contact | Ottawa | Foreign Interference | Animal
19012 | 2011 | 8 | 25 | 0.090278 |  | 50 | 9 | 11 | Riverdale TR | 13.2kV | TR09 | Transformer X29882 at 288 Fifth opened due to tree contact. Branch cleared & transformer fuse replaced. | Ottawa | Tree Contacts | Tree Limb Fallen
9083 | 2006 | 8 | 29 | 0.33681 |  | 65 | 3 | 3 | Riverdale | 13.2kV | TR09 | Mano Della Vedova opened xfmr OTT3252 at 237 Holmwood to put in a new service | Ottawa | Scheduled Outage | Preventive Maintenance
16839 | 2010 | 8 | 30 | 0.39583 |  | 90 | 14 | 9 | Riverdale | 13.2kV | TR09 | Isolated transformer X29881 at 30 Morris St for a pole change | Ottawa | Scheduled Outage | Construction
16848 | 2010 | 9 | 1 | 0.33333 |  | 90 | 21 | 14 | RIVERDALE | 4.16kV | TR09 | Transformer X29805 @ 22 Morris St isolated for pole change | Ottawa | Scheduled Outage | Repair
19080 | 2011 | 9 | 3 | 0.2875 |  | 91 | 11 | 7 | Riverdale | 4.16kV | TR09 | Replaced blown fuse feeding transformer X29864 at 94 Broadway Ave (Squirrel contact) | Ottawa | Foreign Interference | Animal
4027 | 2003 | 9 | 6 | 0.83333 |  | 50 | 8 | 9 | Riverdale | 13.2kV | TR09 | Squirrel caused transformer at 45 Melgund to open. 9 customers interrupted. Crew refused transformer. | Ottawa | Foreign Interference | Animal
4117 | 2003 | 9 | 21 | 0.46597 |  | 46 | 6 | 8 | Riverdale | 13.2kV | TR09 | Cleared and refused restoring load. | Ottawa | Foreign Interference | Animal
9264 | 2006 | 9 | 21 | 0.46597 |  | 74 | 20 | 16 | Riverdale | 13.2kV | TR09 | Transformer #OTT3245 located at 183 Holmwood isolated due to transformer upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
9270 | 2006 | 9 | 21 | 0.41319 |  | 125 | 65 | 31 | Riverdale | 4.16kV | TR09 | Isolated two transformers at 256 and 275 Holmwood Dr to replace pole's | Ottawa | Scheduled Outage | Construction
11385 | 2007 | 9 | 25 | 0.61597 |  | 28 | 5 | 10 | Riverdale | 13.2kV | TR09 | Transformer #29876 at 278 Holmwood isolated to allow for repairs to secondary at 57 Gordon, triplex spliced, Damage to Plant done | Ottawa | Scheduled Outage | Construction
4217 | 2003 | 10 | 6 | 0.52431 |  | 150 | 20 | 8 | Riverdale | 4.16kV | TR09 | To repair switch at K139 transformer 952 rear of 142 Broadway. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17138 | 2010 | 10 | 19 | 0.375 |  | 160 | 61 | 23 | Riverdale | 4.16kV | TR09 | Isolated two transformers X29881 at 28 Morris St and X29805 at 22 Morris St for pole change | Ottawa | Scheduled Outage | Construction
19436 | 2011 | 10 | 21 | 0.41875 |  | 70 | 15 | 13 | Riverdale | 4.16kV | TR09 | Replaced blown fuse for transformer X26264 at 594 Queen Elizabeth Dr (Squirrel contact) | Ottawa | Foreign Interference | Animal
15295 | 2009 | 10 | 22 | 0.46181 |  | 80 | 5 | 4 | Riverside | 13.2kV | TR09 | Isolated transformer X29991 at 11 Crescent Hts to connect new services | Ottawa | Scheduled Outage | Preventive Maintenance
13419 | 2008 | 10 | 23 | 0.40139 |  | 102 | 51 | 30 | Riverdale | 13.2kV | TR09 | Suspected vehicle bump to pole caused S20715 at the corner of Bronson and Fifth to open. Line patrolled and switch closed back in restoring 30 customers downstream of switch. | Ottawa | Foreign Interference | Vehicle
13428 | 2008 | 10 | 25 | 0.65972 |  | 470 | 43 | 22 | Riverdale | 13.2kV | TR09 | A single phase run -off at the SE corner of Bronson & Fifth ave was isolated to make repairs to a broken cut out & bracket at Tx X29993, rear of 25 Crescent Heights. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17175 | 2010 | 10 | 26 | 0.37083 |  | 216 | 50 | 14 | RIVERDALE | 4.16kV | TR09 | Transformer X29805 at 20 Morris isolated to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
17182 | 2010 | 10 | 27 | 0.375 |  | 240 | 40 | 10 | RIVERDALE | 4.16kV | TR09 | Transformer X26018 at 8 Morris St. Isolated to tranfer plant to new pole | Ottawa | Scheduled Outage | Construction
13467 | 2008 | 10 | 29 | 0.078472 |  | 19 | 228 | 719 | RIVERDALE | 4.16kV | TR09 | 1:53am - TR09 has trip A/R/A flagged RWB 2:12am - closed back in and holding | Ottawa | Adverse Weather
13541 | 2008 | 10 | 31 | 0.85556 |  | 202 | 112 | 719 | Riverdale | 13.2kV | TR09 | TR09 breaker opened from SCADA to allow 24/7 to disconnect single phase line in front of 13 Morris for the Fire Department. | Ottawa | Adverse Environment | Fire
15337 | 2009 | 10 | 31 | 0.56111 |  | 112 | 17 | 9 | Riverdale | 4.16kV | TR09 | Replaced blown fuse at switch feeding transformer X29999 at 31 Madawaska Dr | Ottawa | Adverse Weather | Wind
11694 | 2007 | 11 | 11 | 0.69653 |  | 60 | 67 | 84 | RIVERDALE TS | 13.2kV | TR09 | At 3:57pm transformer OTT943 fuse at 135 Broadway Avenue opened up due to squirrel contact. S10936 fuse also opened and was refused to pick up majority of customers. Transformer OTT943 fuse was replaced and remaining twelve customers were restored, 84 customers were affected for 60 min. ID 11694. | Ottawa | Foreign Interference | Animal
15382 | 2009 | 11 | 12 | 0.55208 |  | 27 | 3 | 7 | RIVERDALE TR | 13.2kV | TR09 | transformer X29897 at 59 Ralph isolated to allow for adjustment of taps | Ottawa | Scheduled Outage | Construction
17327 | 2010 | 11 | 23 | 0.49583 |  | 71 | 69 | 58 | Riverdale | 13.2kV | TR09 | S20715 R,W at Bronson and Madawaska Dr opened due to vehecile contact (hit and Run) Fused switches just open not blown. | Ottawa | Foreign Interference | Vehicle
4552 | 2003 | 12 | 3 | 0.49097 |  | 53 | 7 | 8 | Riverdale | 13.2kV | TR09 | Squirrel contact caused fuse to blow at transformer OTT4111 at 31 Madaska. 8 customers on Kippewa & Madaska were affected. Crew refused and restored. | Ottawa | Foreign Interference | Animal
7682 | 2005 | 12 | 3 | 0.6875 |  | 20 | 2 | 5 | Riverdale | 13.2kV | TR09 | Transformer OTT6168 at 23 Crescent Hights was isolated to replace connections on the service | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
15597 | 2009 | 12 | 30 | 0.59097 |  | 44 | 7 | 10 | TR09 | 13.2kV | TR09 | Transformer #X29833 located at 25 Thornton Ave opened for crew to run new triplex to reconnect after a fire. | Ottawa | Adverse Environment | Fire
18036 | 2011 | 4 | 28 | 0.59306 |  | 34 | 951 | 1679 | Riverdale | 13.2kV | TR13 | TR13 circuit breaker tripped during wind/lightning storm. Closed via scada and held. | Ottawa | Adverse Weather | Wind
13771 | 2008 | 12 | 17 | 0.44444 |  | 157 | 44 | 17 | RIVERDALE | 4.16kV | TR13 | Transformer #MT0023 at 13 Kings Landing Pvt isolated to allow for contractor repairs | Ottawa | Scheduled Outage
14467 | 2009 | 6 | 5 | 0.35764 |  | 40 | 14 | 21 | Riverdale | 13.2kV | TR15 | Replaced blown fuse at transformer X39342 at 197 Hopewell Ave due to Squirrel contact | Ottawa | Foreign Interference | Animal
15967 | 2010 | 4 | 21 | 0.46806 |  | 94 | 28 | 18 | RIVERDALE | 13.2kV | TR17 | Transformer # KT0269 located at 1153 Rockingham opened due to squirrel contact | Ottawa | Foreign Interference | Animal
14478 | 2009 | 6 | 6 | 0.64306 |  | 103 | 17 | 10 | Riverdale | 13.2kV | TR17 | At 3:26pm a transformer OTT1773 at 2244 Alta Vista opened due to contact with vines, 10 customers were affected and power was restored at 5:09pm. (Riverdale TR17). ID#14478. | Ottawa | Tree Contacts | Inadequate Trimming
15401 | 2009 | 11 | 19 | 0.42361 |  | 25 | 5 | 13 | Riverdale | 13.2kV | TR17 | Isolated and replaced broken switch feeding transformer X27493 at 1497 Brule Ave | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7209 | 2005 | 8 | 25 | 0.45694 |  | 26 | 663 | 1530 | Riverdale | 13.2kV | TR1JP | TR10 breker (TR1JP & TR1UY tripped due to a blown arrestor at 477 Sunnysde on TR1UY dip to VT8 (Carelton U.). | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7636 | 2005 | 11 | 16 | 0.44236 |  | 108 | 1383 | 1530 | TR | 13.2kV | TR1JP/TB2JP | TR10 (TR1JP = TB2JP) & TR04 ( TR1UQ=TB1UQ) tripped due to a broken wart style insulator on the center phase of TB2JP along HEPC right of way. The flash caused the adjacent circuit to open as well as blowing a red phase fuse on TB14 underbuild. A road had to be opened to allow access to the broken insulator before TB14 could be re-fused. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13844 | 2009 | 1 | 7 | 0.41319 |  | 60 | 55 | 55 | Riverdale | 13.2kV | TR1UN | S19459 at Lees and Hurdman was defective. Switch isolated and power restored to customers. | Ottawa | Defective Equipment
13867 | 2009 | 1 | 14 | 0.46528 |  | 10 | 2 | 14 | RIVERDALE | 13.2kV | TR1UN | Isolated transformer X31239 at 73 Harvey St to replace hotline clamp | Ottawa | Scheduled Outage | Repair
20352 | 2012 | 4 | 18 | 0.85764 |  | 168 | 87 | 31 | Riverdale | 13.2kV | TR1UN | At 20:35 crews replaced a leaking transformer PT191 at 21 HURDMAN RD. 31 customers affected for 168 mins. Riverdale TR1UN ID# 20352 | Ottawa | Scheduled Outage | Repair
18032 | 2011 | 4 | 29 | 0.27778 |  | 169 | 493 | 175 | Riverdale | 13.2kV | TR1UN | SC6601 @ 6 Hurdman was isolated to allow crew to reapair broken condoctor. 175 customer were affected. Riverdale TR1UN | Ottawa | Adverse Weather | Wind
20419 | 2012 | 4 | 30 | 0.45833 |  | 30 | 7 | 14 | Riverdale |  | TR1UN | Isolated transformer X30724 at 17 Robinson Ave for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
5367 | 2004 | 6 | 24 | 0.76528 |  | 674 | 4149 | 1563 | RIVERDALE | 13.2kV | TR1UN | TR13 circuit tripped due to pole coming down feeding the City Yard at 29 Hurdman. SC6601 circuit was isolated and TR1UN circuit was energized at 18:22. Approx 300 customers on Sc6601 remained out until repairs were made. | Ottawa | Adverse Weather | Wind
10721 | 2007 | 6 | 24 | 0.71875 |  | 180 | 18 | 6 | Riverdale | 13.2kV | TR1UN | Squirrel contact caused the transformer fuse to open at 14 Montcalm. Fuse replaced. | Ottawa | Foreign Interference | Animal
10723 | 2007 | 6 | 25 | 0.25 |  | 32 | 3 | 6 | Riverdale | 13.2kV | TR1UN | Squirrel contact caused the transformer fuse to open at 14 Montcalm. Fuse replaced. 2nd time in 12 hours. | Ottawa | Foreign Interference | Animal
4989 | 2004 | 4 | 9 | 0.44792 |  | 15 | 2 | 6 | TR | 13.2kV | TR1UN (SC6601) | Squirrel caused transformer fuse to open at 37 Robinson, Tx A1045-49. Fuse replaced. | Ottawa | Foreign Interference | Animal
7637 | 2005 | 11 | 16 | 0.44236 |  | 47 | 470 | 600 | TR | 13.2kV | TR1UQ/TB1UQ | TR10 (TR1JP = TB2JP) & TR04 ( TR1UQ=TB1UQ) tripped due to a broken wart style insulator on the center phase of TB2JP along HEPC right of way. The flash caused the adjacent circuit to open as well as blowing a red phase fuse on TB14 underbuild. A road had to be opened to allow access to the broken insulator before TB14 could be re-fused. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17854 | 2011 | 4 | 7 | 0.82292 |  | 50 | 371 | 889 | Riverdale TR | 13.2kV | TR1UX | TR22 breaker tripped due to a suspected cable fault on TR1UX cable. Part of the load was transferred to alternate sources & the cable sectionalized to isolate faulted section. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11930 | 2008 | 1 | 13 | 0.49861 |  | 125 | 1248 | 1700 | Riverdale |  | TR1UY | 1/2 of Carleton normal supply TR2UY isolated for WP overhead work on Sunnyside. When TR1UY tripped grounds had to be removed and circuit returned to service.Sunnyside T2, Playfair T1,T2 and Kilborn T2, 2 apts and 1/2 Carleton U. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12098 | 2008 | 3 | 4 | 0.52083 |  | 120 | 20 | 10 | Riverdale | 4.16kV | TR1UY | Transformer #X30385 located at 423 Sunnyside isolated due to transferring plant | Ottawa | Scheduled Outage | Preventive Maintenance
10433 | 2007 | 5 | 20 | 0.95139 |  | 25 | 625 | 1500 | Riverdale | 13.2kV | TR1UY | Cable fault on TR1UY (TR10) going into Carleton University - Load restored on the TB13. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11518 | 2007 | 10 | 15 | 0.44306 |  | 64 | 1484 | 2063 | Riverdale | 13.2kV | TR1UY | While isolating the TR3UY cable sect bet Sunnyside sub,& VT900 the TR3UY-L did not operat properly it remained closed despite the operating mechanism being operated to the open position. This caused an outage when the Reyrolle switch was placed in the earth position at VT900 on TR1UY and TR2UY. | Ottawa | Human Element | Switching Errors
17877 | 2011 | 4 | 11 | 0.30486 |  | 249 | 17 | 4 | Riverdale | 13.2kV | TR23 | Transformer X38073 at 115 Leonard Ave replaced due to lightning strike | Ottawa | Lightning | Direct Strike
16382 | 2010 | 7 | 2 | 0.35208 |  | 48 | 6 | 8 | Riverdale | 4.16kV | TR23 | Replaced blown fuse feeding transformer X38062 at 8 Osborne St (Squirrel contact) | Ottawa | Foreign Interference | Animal
16591 | 2010 | 7 | 30 | 0.3125 |  | 55 | 6 | 6 | Riverdale | 4.16kV | TR23 | Reolaced blown fuse feeding transformer X38031 at 150 Cameron Ave (Squirrel contact) | Ottawa | Foreign Interference | Animal
16629 | 2010 | 8 | 3 | 0.69792 |  | 45 | 14 | 18 | Riverdale | 13.2kV | TR23 | 2 overhead transformers at Wendover and Chesley were isolated for crew to make repairs to single phase overhead damaged by high winds during storm. | Ottawa | Adverse Weather | Wind
5414 | 2004 | 7 | 1 | 0.31667 |  | 54 | 3 | 3 | Riverdale | 13.2kV | TR2FB | Lightening strike on the sky wire at 150 Fourth Ave. caused a ground trip on TR20 breaker feeding TR2FB. Circuit patrolled and reclosed by SCADA | Ottawa | Lightning | Direct Strike
13420 | 2008 | 10 | 23 | 0.91806 |  | 16 | 0 | 1 | Slater | 13.2kV | TR2TS | Power was shut off at VT89 @ 180 Argyle St YMCA during switching to partially isolation 460 O'Conner St. (due to the poor condition of switchgear at the YMCA Hydro Ottawa will not operate switch gear while energized) | Ottawa | Adverse Environment | Corrosion
13427 | 2008 | 10 | 25 | 0.75 |  | 1 | 0 | 1 | Riverdale | 13.2kV | TR2TS | Due to a mapping error, while switching to isolate VT279 at 460 O'Connor, when the crew opened TV3656-L1, 100 Isabella to complete the isolation of VT279, power went out at TV3656. The crew closed the switch restoring power. It was found that nomenclature at TV3656 did not agree with system map. | Ottawa | Human Element | Incorrect Records
4503 | 2003 | 11 | 22 | 0.1125 |  | 243 | 405 | 100 | Riverdale | 13.2kV | TR2TS | VT24 at 255 Metcalfe isolated for Hydro Ottawa to perform routine maintenance for the customer. | Ottawa | Scheduled Outage | Preventive Maintenance
13361 | 2008 | 10 | 13 | 0.16389 |  | 449 | 7 | 1 | Riverdale | 13.2kV | TR2UY | CB2 @ VT8 tripped, Carelten U closed in CB2 and tripped TR03 breaker (TR2UY). Customer insepcted own equiptent and found trouble with customer owned switch, power was restored from alternate source. | Ottawa | Foreign Interference | Foreign Object
4968 | 2004 | 4 | 5 | 0.0083333 |  | 91 | 248 | 633 | TR | 13.2kV | TR3UQ | TR14 acb tripped due to a faulted cable between VT282 & VT213 on Riverside dr. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3397 | 2003 | 5 | 2 | 0.47361 |  | 98 | 588 | 700 | RIVERDALE | 13.2kV | TR3UQ | POTHEAD ON O/H LINE BETWEEN VT282 & VT213 FAILED TRIPING OFF CURCUIT TR3UQ BY BREAKER TR14 AT RIVERSIDE TERMINAL. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7499 | 2005 | 10 | 21 | 0.92014 |  | 359 | 1836 | 633 | Riverside | 13.2kV | TR3UQ | A single phase(white) of 13kv TR3UQ circuit came down on 4kV circuit UQ07 at 1785 Riverside dr. TR3UQ, UQ05, and UQ08 were energized by 22:35, UQ07 remained out until crew could remove phase of TR3UQ nad repair. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20335 | 2012 | 4 | 16 | 0.83472 |  | 146 | 219 | 90 | Riverdale | 13.2kV | TR3UY | At 20:02, crews established PC10a #9021 at S20344 to isolate TR3UY O/H section to allow emergency tree trimming at 77 Glen Ave. Tree is split & is threating to fall on house, with in limits of O/H circuit. | Ottawa | Tree Contacts | Tree Limb Fallen
18305 | 2011 | 6 | 6 | 0.32917 |  | 91 | 38 | 25 | Riverdale | 13.2kV | TR3UY | Transformer #X43570 located at 79 Fulton opened up due to squirrel contact. Bird guard installed. | Ottawa | Foreign Interference | Animal
16212 | 2010 | 6 | 7 | 0.3625 |  | 58 | 17 | 18 | Riverdale | 13.2kV | TR3UY | Transformer #X35425 located at 34 Euclid opened up due to squirrel contact Riverdale | Ottawa | Foreign Interference | Animal
14528 | 2009 | 6 | 13 | 0.74097 |  | 92 | 28 | 18 | Riverdale | 13.2kV | TR3UY | Squirrel caused transformer at 30 Euclid to open. | Ottawa | Foreign Interference | Animal
18439 | 2011 | 6 | 20 | 0.30139 |  | 139 | 32 | 14 | Riverdale | 13.2kV | TR3UY | Transformer #X43856 located at 14 Rosedale opened up due to squirrel contact. | Ottawa | Foreign Interference | Animal
20886 | 2012 | 6 | 26 | 0.86806 |  | 55 | 24 | 26 | Riverdale | 13.2kV | TR3UY | at 20:50, transformer X43926 on Glen Ave openned due to animal contact, crews refused cutout and power restored. 26 Customers affected for 55 minutes. Riverdale (TR3UY) ID #20886 | Ottawa | Foreign Interference | Animal
18572 | 2011 | 7 | 2 | 0.37708 |  | 37 | 2 | 3 | Riverdale | 13.2kV | TR3UY | Jason Walkden reports transformer #X43886 opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
14794 | 2009 | 7 | 21 | 0.25833 |  | 108 | 25 | 14 | Riverdale | 13.2kV | TR3UY | Transformer #X43553 located at 1087 Bronson Pl isolated due to animal contact | Ottawa | Foreign Interference | Animal
12911 | 2008 | 7 | 22 | 0.27222 |  | 103 | 31 | 18 | Riverdale | 13.2kV | TR3UY | Transformer #X35425 located at 30 Euclid isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
16590 | 2010 | 7 | 29 | 0.84306 |  | 67 | 23 | 21 | Riverdale | 13.2kV | TR3UY | Transformer #X39342 located at 197 Hopewell opened by squirrel contact | Ottawa | Foreign Interference | Animal
18910 | 2011 | 8 | 11 | 0.43056 |  | 80 | 19 | 14 | Riverdale | 13.2kV | TR3UY | Transformer #X43590 located at 25 Roslyn opened by crew to replace transformer | Ottawa | Scheduled Outage | Construction
14956 | 2009 | 8 | 17 | 0.71389 |  | 392 | 3367 | 673 | Riverdale | 13.2kV | TR3UY | Conductor failed at Sunnyside & Leonard which caused SC8233-CB4 to trip when 1 phase fell onto other phases. Suspect excessive sag in conductors combined with load and wind caused phases to make contact and break. One 3 phase transformer at Galt & Aylmer also had a fuse blown. Temporary repairs to circuit were made by Oncall crew and then the 3 phase transformer was tested & restored after inspection. | Ottawa | Defective Equipment
14983 | 2009 | 8 | 21 | 0.27292 |  | 112 | 21 | 11 | Riverdale | 13.2kV | TR3UY | Transformer #X35436 located at 49 Leonard Ave isolated due to animal contact. | Ottawa | Foreign Interference | Animal
16864 | 2010 | 9 | 3 | 0.74167 |  | 230 | 2580 | 673 | Riverdale | 13.2kV | TR3UY | Overhead wires at 47 Leonard were tangled together caused SC8233-CB4 to trip, crews untangled and closed to restore power. | Ottawa | Defective Equipment
19136 | 2011 | 9 | 12 | 0.30694 |  | 78 | 27 | 21 | Riverdale | 13.2kV | TR3UY | Transformer #X39342 located at 197 Hopewell opened up due to squirrel interference | Ottawa | Foreign Interference | Animal
19177 | 2011 | 9 | 14 | 0.525 |  | 24 | 8 | 21 | Riverdale | 4.16kV | TR3UY | Replaced blown fuse feeding transformer X39342 at 197 Hopewell Ave due to Squirrel | Ottawa | Foreign Interference | Animal
13273 | 2008 | 9 | 22 | 0.33819 |  | 41 | 5 | 7 | Sunnyside | 13.2kV | TR3UY | Refused switch feeding transformer X35431 at 6 Barton St. | Ottawa | Foreign Interference | Animal
4167 | 2003 | 9 | 28 | 0.10069 |  | 257 | 4 | 67 | Riverdale |  | TR3UY | VT819 @ 774 Echo was shutdown for cleaning and torquing. | Ottawa | Scheduled Outage | Preventive Maintenance
13545 | 2008 | 11 | 1 | 0.56944 |  | 25 | 8 | 18 | SUNNYSIDE | 4.16kV | TR3UY | Refused switch feeding transforner X35425 at 30 Euclid Ave Due to squirrel contact | Ottawa | Foreign Interference | Animal
17208 | 2010 | 11 | 2 | 0.53542 |  | 84 | 20 | 14 | Riverdale | 13.2kV | TR3UY | Transformer #X43861 located at 59 Rosedale opened due to squirrel contact | Ottawa | Foreign Interference | Animal
19756 | 2011 | 12 | 21 | 0.86597 |  | 67 | 748 | 670 | Riverdale | 13.2kV | TR3UY | The SC8233-CB4 at 459 Sunnyside tripped opened due to snow plow accidentally hitting the down guy wire at 43 Dunbarton (Senior Residence). Riverdale (TR3UY). | Ottawa | Foreign Interference | Vehicle
15065 | 2009 | 9 | 8 | 0.48611 |  | 30 | 6 | 11 | Riverdale | 13.2kV | TR3UY (SC8233) | Transformer #X43865 located at 16 Grosvenor Ave isolated to install new service. | Ottawa | Scheduled Outage | Construction
5095 | 2004 | 5 | 4 | 0.39167 |  | 194 | 181 | 56 | TO | 13.2kV | TRO2UQ | VT319 @ 305 Presland was isolated for planned maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
19343 | 2011 | 10 | 8 | 0.19097 |  | 152 | 154 | 66 | Overbrook | 13.2kV | TRO2UQ | TO50 breaker opened due to a suspected cable fault between SW166 and VT319. Overbrook (TRO2UQ) ID#19343 | Ottawa | Defective Equipment
8072 | 2006 | 3 | 29 | 0.10486 |  | 220 | 4925 | 3000 | Slater | 13.2kV | TS J1 & J2 bus | Hydro 1 fault on the J1J2 tie breaker caused the loss of supply to Hydro Ottawa J1 and J2 busses at Slater | Ottawa | Loss of Supply | HEPC Station Fault
20833 | 2012 | 6 | 23 | 0.081944 |  | 28 | 542 | 1161 | Slater | 13.2kV | TS2UX | Slater T3 forced out of service due to gassing, circuit transferred to alternate supply. | Ottawa | Loss of Supply | HEPC Station Fault
19113 | 2011 | 9 | 7 | 0.9125 |  | 6 | 37 | 371 | Slater | 13.2kV | TS54 | TS54 Inadvertent Load Dump due to bypass switch not being closed. Breaker closed back in and bypass closed. | Ottawa | Human Element | Switching Errors
19114 | 2011 | 9 | 7 | 0.9125 |  | 6 | 74 | 742 | Slater TS | 13.2kV | TS56 | TS56 Inadvertent Load dump due to bypass switch not being closed. Breaker closed back in and bypass closed. | Ottawa | Human Element | Switching Errors
19115 | 2011 | 9 | 7 | 0.9125 |  | 6 | 13 | 130 | Slater | 13.2kV | TS58 | TS58 Inadvertent Load Dump due to bypass switch not being closed. Breaker closed back in and bypass closed. | Ottawa | Human Element | Switching Errors
18311 | 2011 | 6 | 6 | 0.44375 |  | 734 | 17 | 7 | Slater TS | 13.2kV | TS70 | VT452 at 234 Laurier was isolated due to a water leaking into the metalclad. Customers were picked up in two stages as system isolated VT452. | Ottawa | Foreign Interference
15207 | 2009 | 10 | 4 | 0.055556 |  | 690 | 18 | 11 | Slater TS | 13.2kV | TS75 | At 00:40 while switching VT543 at 155 Queens back after customer maintenance our crew had the 602-L14 at VT142 blow up, which caused the TS75 breaker to open. | Ottawa | Defective Equipment
13734 | 2008 | 12 | 11 | 0.31528 |  | 97 | 1126 | 1131 | Woodroffe TS | 13.2kV | TW J Bus | TW20 breaker faulted causing a J bus differential. Load was interrupted to 2804, TW22 & TW2UC (UCT3) circuits which were restored from alternate sources. Roof leak caused water to build up in TW20's arc chute causing breaker to fault. | Ottawa | Loss of Supply | HEPC Station Fault
12635 | 2008 | 6 | 15 | 0.79722 |  | 16 | 3 | 10 | Woodroffe | 13.2kV | TW07 | SCADA indicates TW07 breaker tripped, and at the same time TW08 breaker tripped. Severe Lightning storm in affect. Breaker closed and holding. | Ottawa | Adverse Weather | Lightning
16896 | 2010 | 9 | 7 | 0.91875 |  | 23 | 165 | 430 | Woodroffe TS | 13.2kV | TW07 | SCADA indicates TW07 CB opened, Systems closed & holding... | Ottawa | Adverse Weather
10128 | 2007 | 3 | 14 | 0.54028 |  | 1 | 12 | 750 | WOODROFFE | 13.2kV | TW13 | TW13 tripped due toa tree limb, which also tripped UW03 . TW13 closed to restore load. The tree limb was at 1243 Major Street. | Ottawa | Tree Contacts | Tree Limb Fallen
14846 | 2009 | 7 | 27 | 0.34861 |  | 2 | 17 | 750 | Woodroffe | 13.2kV | TW13 | At 8:21am, Severe weather in area, lightning and heavy rain. UWT3 CB opened, verified weather in area and closed back in circuits accordingly. 750 customers out originally and all power restored at 8:23am. Woodroffe (TW13, UW01, UW02, UW03, UW04, UWK1Y1, UW06). ID#14846. | Ottawa | Adverse Weather | Lightning
16862 | 2010 | 9 | 3 | 0.75625 |  | 360 | 2079 | 761 | WOODROFFE | 13.2kV | TW13 | SCADA indicated TW13 and UW03 breaker tripped. OMS Reports tree on line at UW03, on Field Street. TW13 Closed to restore UW01, UW02, UW04. Tree was cleared and crew found 3 phases wrapped together at Woodroffe and Iris. | Ottawa | Tree Contacts | Tree Fallen
16991 | 2010 | 9 | 24 | 0.79861 |  | 10 | 78 | 465 | Woodroffe | 13.2kV | TW13 | The TW13 breaker which feeds the UWT1 transformer and the UW01,UW02,UW03 & UW04 breakers trip because a branch fell on the O/H and a tap also burnt off on the UW03 circuit. The UW03 breaker did not open. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12718 | 2008 | 6 | 25 | 0.11736 |  | 8 | 153 | 1144 | Woodroffe | 13.2kV | TW1UC | TW21 Breaker tripped, which was carrying UCT2 load, and UCT3 load at Clyde. System isolated suspected defective cable, and overhead circuit between Clyde and Woodroffe. Circuit to be patrolled in morning. Woodward, Clyde, Queensway N. area. | Ottawa | Unknown/Other
11141 | 2007 | 8 | 24 | 0.19097 |  | 7 | 51 | 441 | Woodroffe | 13.2kV | TW1UC | Lightning storm in effect, causing TW21 to trip. System closed TW21 to restore load | Ottawa | Adverse Weather | Lightning
11193 | 2007 | 8 | 29 | 0.76389 |  | 12 | 88 | 441 | Woodroffe | 13.2kV | TW1UC | TW1UC opened and locked out, circuit closed back in via SCADA and holding | Ottawa | Adverse Weather
20162 | 2012 | 3 | 13 | 0.86389 |  | 3 | 38 | 750 | Woodroffe TS | 13.2kV | TW1UV | While preforming a switching operation the crew in the field accidently put the switch in the earth position instead of the close position in the Iris/Pinecrest area. | Ottawa | Human Element | Switching Errors
15453 | 2009 | 12 | 2 | 0.40972 |  | 35 | 6 | 10 | Woodroffe | 13.2kV | TW21 | Transformer #OTT5192 located at 2132 Queensgrove isolated to change connections | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15600 | 2010 | 1 | 1 | 0.48125 |  | 53 | 53 | 615 | Woodroffe | 13.2kV | TW22 | S13369 Red phase found defective. TW22 breaker opened, to allow crew to install a jumper to make temporary repairs. TW22 Breaker closed to restore all power. | Ottawa | Defective Equipment
15628 | 2010 | 1 | 8 | 0.44444 |  | 40 | 3 | 5 | Woodroffe | 13.2kV | TW22 | Transformer #X32674 located at 886 Winnington isolated to install new service | Ottawa | Scheduled Outage | Construction
11914 | 2008 | 1 | 9 | 0.43681 |  | 191 | 159 | 50 | Woodroffe | 13.2kV | TW22 | At 10:29am trees made contact to overhead wires causing two fuses to open up switch located at Lenester at Dunlevie Avenue, 50 customers affected for 191min. ID#11914. | Ottawa | Tree Contacts | Inadequate Trimming
13868 | 2009 | 1 | 14 | 0.54167 |  | 20 | 4 | 12 | WOODROFFE TW | 13.2kV | TW22 | Isolated transformer OTT5191 at 2137 Queensgrove Rd to replace the service to 2129 Queensgrove | Ottawa | Scheduled Outage | Emergency Services Request
15662 | 2010 | 1 | 16 | 0.95486 |  | 80 | 13 | 10 | Woodroffe |  | TW22 | Customers reported outage and Sparks in back yard, Crews found Ice from the roof of 876 Woodroffe damaged the service and cuased the fuse to X33406 to blow. Crews report Service to 876 Wooroffe has been secured temperarily and notified customer to have electrician to repair properly. | Ottawa | Foreign Interference | Foreign Object
7835 | 2006 | 1 | 21 | 0.46528 |  | 220 | 92 | 25 | Woodroffe | 13.2kV | TW22 | Tree in wires at 2121 Westbourne blew 80 amp fuse at Strathmore east of Inswood and 80 amp fuse on Lenester east of Fairlawn. | Ottawa | Tree Contacts | Tree Limb Fallen
15677 | 2010 | 1 | 22 | 0.83333 |  | 210 | 364 | 163 | Woodroffe | 13.2kV | TW22 | S13369 RWB on Georgina W. of Woodroffe opened to make repairs to primary line at tap to S12502, defective hot line clamp caused R phase primary conductor to fail. All 3 phases opened to complete repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17513 | 2011 | 1 | 24 | 0.13472 |  | 25 | 5 | 13 | Woodroffe | 13.2kV | TW22 | Crew opened transformer X33763 at rear of 969 Hare to remove tree from primary. | Ottawa | Tree Contacts | Tree Limb Fallen
11988 | 2008 | 1 | 29 | 0.55833 |  | 66 | 11 | 10 | WOOODROFFE | 13.2kV | TW22 | transformer #33756 located at 908 Killeen isolated to install a service up a pole | Ottawa | Scheduled Outage | Construction
19918 | 2012 | 1 | 29 | 0.89583 |  | 60 | 77 | 77 | Woodroffe | 13.2kV | TW22 | patrol found S21976 white phase blown, further patrol on O/H found nothing. Refused closed and holding | Ottawa | Unknown/Other
6157 | 2005 | 1 | 30 | 0.43194 |  | 33 | 6 | 10 | Woodroffe | 13.2kV | TW22 | Squirrel caused fuse to blow on transformer OTT3664 at the rear of 975 Kingsmere Ave interrupting power to 10 customers | Ottawa | Foreign Interference | Animal
9979 | 2007 | 2 | 1 | 0.41667 |  | 120 | 14 | 7 | Woodroffe | 13.2kV | TW22 | Isolated transformer OTT3658 at 817 Kingsmere Ave to relocate secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
13922 | 2009 | 2 | 2 | 0.54444 |  | 36 | 4 | 6 | TW22 | 13.2kV | TW22 | Transformer #X24049 located at 957 Muskoka Ave isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
9993 | 2007 | 2 | 6 | 0.36042 |  | 40 | 4 | 6 | Woodroffe | 13.2kV | TW22 | Fuse to transformer OTT4417 at 840 Melwood Ave was found blown due to an animal contact (Squirrel) | Ottawa | Foreign Interference | Animal
17559 | 2011 | 2 | 6 | 0.625 |  | 30 | 4 | 9 | Woodroofe | 13.2kV | TW22 | At 15:00 trans at 956 WINNINGTON AVE OTTAWA was isolated in oder to isolate defeective sec u/g | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17625 | 2011 | 2 | 19 | 0.94583 |  | 48 | 6 | 7 | WOODROFFE TS | 13.2kV | TW22 | Transformer 35323 and 35322 opened to repair broken neutral and sleeve in new conductor at the rear of 908 Fairlawn. | Ottawa | Defective Equipment
10055 | 2007 | 2 | 23 | 0.35069 |  | 25 | 3 | 8 | Woodroffe | 4.16kV | TW22 | Mike Irven isolated TRF. 3660 @ 832 Iroquois to change secondary connections on the service feeding 832 Iroquois | Ottawa | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
20056 | 2012 | 2 | 27 | 0.43403 |  | 33 | 1 | 2 | Woodroffe TS | 13.2kV | TW22 | Transformer #X34221 located at 816 Hare Ave opened by crew to replace service | Ottawa | Scheduled Outage | Construction
10076 | 2007 | 2 | 28 | 0.41667 |  | 212 | 35 | 10 | Woodroffe | 4.16kV | TW22 | AT 10:00 trans at 2332 Rembrandt Rd was isolated in order to replace a pole | Ottawa | Scheduled Outage | Repair
10083 | 2007 | 3 | 2 | 0.098611 |  | 88 | 43 | 29 | WOODROFFE | 13.2kV | TW22 | A Gazebo blew into the secondary service at 868 Duberry causing the line fuse to blow, at Fox and Duberry. Secondary service removed and closed in fuse to restore power. (868 Duberry will remain out of power until standpipe repaired, and service replaced.) | Ottawa | Foreign Interference | Foreign Object
12092 | 2008 | 3 | 3 | 0.41667 |  | 15 | 2 | 6 | WOODROFFE | 13.2kV | TW22 | Transformer at 2032 Killarney isolated to allow for repairs to service connection | Ottawa | Scheduled Outage | Repair
6247 | 2005 | 3 | 6 | 0.28819 |  | 50 | 4 | 5 | Woodroffe | 13.2kV | TW22 | Squirrel opened the transformer at 975 Kingsmere. | Ottawa | Foreign Interference | Animal
14025 | 2009 | 3 | 6 | 0.54167 |  | 85 | 13 | 9 | Woodroffe | 13.2kV | TW22 | Isolated transformer X31508 at 816 Melwood Ave to transfer secondary services | Ottawa | Scheduled Outage | Construction
6254 | 2005 | 3 | 9 | 0.015278 |  | 38 | 10 | 16 | Lincoln | 13.2kV | TW22 | Power was interupted to 20 customers on Hare ST to replace broken cutout at pole # 9 on TW22 circuit | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17689 | 2011 | 3 | 9 | 0.41319 |  | 88 | 13 | 9 | Woodroffe TS | 13.2kV | TW22 | Isolated transformer X32804 at 964 Winnington Ave to install new service | Ottawa | Scheduled Outage | Emergency Services Request
14043 | 2009 | 3 | 11 | 0.8375 |  | 194 | 29 | 9 | Woodroffe | 13.2kV | TW22 | Refused switch feeding transformer X32432 at 933 Parkhurst Blvd | Ottawa | Adverse Weather | Wind
6281 | 2005 | 3 | 14 | 0.51389 |  | 85 | 4 | 3 | Woodroffe | 13.2kV | TW22 | Transformer #OTT5189 isolated at 2088 Queensgrove for transformer replacement | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10152 | 2007 | 3 | 21 | 0.40972 |  | 142 | 9 | 4 | Woodroffe | 4.16kV | TW22 | At 09:50 trans @ 805 Hare Avewas isolated in order to install a new conductor | Ottawa | Scheduled Outage | Repair
3283 | 2003 | 3 | 22 | 0.32569 |  | 71 | 13 | 11 | Woodroffe | 13.2kV | TW22 | 24/7 reports transformer fuse blown at the rear of 848 Duberry st in Ottawa. 24/7 reports vines found on the secondary side of the transformer cleared. No other apparent cause in this outage. | Ottawa | Unknown/Other | No Apparent Cause
10166 | 2007 | 3 | 23 | 0.42708 |  | 104 | 17 | 10 | Woodroffe | 13.2kV | TW22 | Lee Piper isolated TRF. @ 814 Hare to remove niu conductor | Ottawa | Scheduled Outage
8093 | 2006 | 4 | 1 | 0.84931 |  | 50 | 46 | 55 | Woodroffe | 13.2kV | TW22 | Broken cutout to KT169. Switch replaced & closed restoring power to all customers. The 55 affected customers were on Lenester, Esterlawn & Aaron. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12236 | 2008 | 4 | 5 | 0.074306 |  | 11 | 3 | 16 | Woodroffe | 13.2kV | TW22 | Ottawa Fire Dept, requested Hydro Ottawa to disconnect service due to working fire at 2365 Georgina St. Ottawa. Transformer OTT3605 opened to disconnect customer. | Ottawa | Adverse Environment | Fire
17855 | 2011 | 4 | 8 | 0.27431 |  | 165 | 30 | 11 | Woodroffe | 4.16kV | TW22 | Replaced broken switch feeding transformer X33897 at 899 KINGSMERE AVE | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17941 | 2011 | 4 | 16 | 0.41111 |  | 83 | 6 | 4 | Woodroffe TW | 13.2kV | TW22 | Isolated transformer X35528 at the rear of 2188 QUEENSGROVE RD to replace secondary paddles at the transformer | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20386 | 2012 | 4 | 25 | 0.27083 |  | 120 | 12 | 6 | Woodroffe | 13.2kV | TW22 | Transformer #X28377 located at 2332 Rembrandt opened up due to wire from switch to H1 bushing was disconnected. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14229 | 2009 | 4 | 26 | 0.83958 |  | 696 | 4693 | 868 | WOODROFFE | 13.2kV | TW22 | Multiple calls concerning trees and wires down on TW22 Circuit. Breaker opened by System. Trees cleared, and circuits repaired. | Ottawa | Tree Contacts
10350 | 2007 | 5 | 2 | 0.5 |  | 90 | 12 | 8 | Woodroffe | 13.2kV | TW22 | Single phase runoff isolated for tree trimming affecting customers on Aaron & Iroquois. | Ottawa | Scheduled Outage | Preventive Maintenance
12379 | 2008 | 5 | 2 | 0.83333 |  | 15 | 1 | 4 | Woodroffe | 13.2kV | TW22 | Isolated transformer X35454 at 2168 Queensgrove Rd to repair overhead service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20441 | 2012 | 5 | 2 | 0.42014 |  | 60 | 5 | 5 | Woodroffe TS | 4.16kV | TW22 | Isolated transformer X33668 at 963 Killeen Ave to replace connections at the transformer | Ottawa | Scheduled Outage | Emergency Services Request
10363 | 2007 | 5 | 4 | 0.40972 |  | 25 | 5 | 13 | Woodroffe | 13.2kV | TW22 | Steve Driscoll isolated TRF. OTT4624 @ 899 Muskoka to remove triplex service | Ottawa | Scheduled Outage | Preventive Maintenance
10365 | 2007 | 5 | 4 | 0.68056 |  | 30 | 4 | 9 | Woodroffe | 13.2kV | TW22 | Isolated transformer OTT4624 at 899 Muskoka to reconnect triplex service that had been disconnected for a tree removal | Ottawa | Scheduled Outage | Emergency Services Request
16060 | 2010 | 5 | 8 | 0.325 |  | 177 | 83 | 28 | Woodroffe | 13.2kV | TW22 | Tree fell on to primary in the rear of 968 Kingsmere, crew isolated and replaced 1 span of primary | Ottawa | Tree Contacts | Tree Limb Fallen
18134 | 2011 | 5 | 11 | 0.51944 |  | 112 | 116 | 62 | Woodroffe | 13.2kV | TW22 | Crews isolated TW22 3 phase run South from 2242 Georgina to assist in crane removal of tree in the backyard overhead circuit. | Ottawa | Scheduled Outage
16086 | 2010 | 5 | 14 | 0.56319 |  | 29 | 6 | 13 | Woodroffe | 13.2kV | TW22 | Transformer X32439 at 2174 Rushton Rd isolated to remove service. Customer upgrading service in futur. House vacant. Branch fell on service wire pull out the hit and broke standpipe. | Ottawa | Foreign Interference | Foreign Object
5162 | 2004 | 5 | 18 | 0.29861 |  | 145 | 121 | 50 | Woodroffe | 13.2kV | TW22 | Lightening strike caused a flash over and a fuse to blow on a blue phase single lateral on Kilarney. | Ottawa | Lightning | Direct Strike
16100 | 2010 | 5 | 19 | 0.34375 |  | 56 | 5 | 5 | Woodroffe | 13.2kV | TW22 | Transformer #OTT5188 located at 1008 Parkhurst opened up due to a broken transformer fuse | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5199 | 2004 | 5 | 23 | 0.28125 |  | 125 | 12 | 6 | TW | 13.2kV | TW22 | 24/7 found open cut-out at Tx3609, 3032 Kilarney, due to squirel contact. Fuse replaced & power restored to 6 customers. | Ottawa | Foreign Interference | Animal
20608 | 2012 | 5 | 25 | 0.82431 |  | 918 | 107 | 7 | Woodroffe | 13.2kV | TW22 | Transfomrer X35189 at 849 Maplecrest opened due to burnt neutral connection. | Ottawa | Adverse Weather | Lightning
20612 | 2012 | 5 | 25 | 0.78819 |  | 1093 | 674 | 37 | Woodroffe | 13.2kV | TW22 | S11177 at 2322 Georgina opened due to treee contact with O/H on Saddler. Crew remove tree and power was restored | Ottawa | Adverse Weather
14420 | 2009 | 5 | 27 | 0.85417 |  | 365 | 30 | 5 | Woodroffe | 13.2kV | TW22 | Secondary bushing of transformer X33660 failed at 2104 Killarney, transformer was isolated and replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18259 | 2011 | 5 | 31 | 0.26875 |  | 88 | 13 | 9 | Woodroffe | 4.16kV | TW22 | Replaced blown fuse feeding transformer X31773, at 933 FAIRLAWN AVE (squirrel contact) | Ottawa | Foreign Interference | Animal
5255 | 2004 | 6 | 4 | 0.40764 |  | 112 | 9 | 5 | Woodroffe | 13.2kV | TW22 | Transfomer #OTT3611 at 2104 Kilarny replaced with new one. | Ottawa | Scheduled Outage
14469 | 2009 | 6 | 5 | 0.40625 |  | 55 | 9 | 10 | Woodroffe | 13.2kV | TW22 | Isolated transformer X33771 at 2117 Westbourne Ave to relocate secondary services to new poles | Ottawa | Scheduled Outage | Construction
18303 | 2011 | 6 | 6 | 0.24792 |  | 37 | 7 | 12 | Woodroffe | 13.2kV | TW22 | Transformer X32805 fuse blew due to no apparent cause. Crew refused and held. TW22. | Ottawa | Unknown/Other
18307 | 2011 | 6 | 6 | 0.39931 |  | 60 | 13 | 13 | Woodroffe TS | 13.2kV | TW22 | Transformer X32442 at 816 Iroquois was opened to allow crews to change out the transformer. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16211 | 2010 | 6 | 7 | 0.08125 |  | 83 | 14 | 10 | Woodroffe | 13.2kV | TW22 | Customer reports transformer fuse blown on transfomer # X33762. 24/7 reports animal caused fuse to blow. Transformer refused and closed. | Ottawa | Foreign Interference | Animal
14488 | 2009 | 6 | 8 | 0.36111 |  | 62 | 6 | 6 | Woodroffe TW | 13.2kV | TW22 | Transformer #X33762 located at 920 Muskoka Ave isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
18389 | 2011 | 6 | 11 | 0.90278 |  | 65 | 11 | 10 | Woodroffe | 13.2kV | TW22 | crew opened transformer X3367 at 2032 killarney to replace burnt 110 tap. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16256 | 2010 | 6 | 13 | 0.15833 |  | 62 | 11 | 11 | WOODROFFE TS | 13.2kV | TW22 | Transformer #X26050 at the rear of 904 Aaron Ave opened up due to animal contact. Crew refused transformer and restored power. | Ottawa | Foreign Interference | Animal
14533 | 2009 | 6 | 14 | 0.53403 |  | 177 | 18 | 6 | Woodroffe | 4.16kV | TW22 | Replaced blown fuse at transformer OTT3612 at the rear of 851 Killeen Ave due to squirrel contact | Ottawa | Foreign Interference | Animal
18407 | 2011 | 6 | 14 | 0.44167 |  | 137 | 5 | 2 | Woodroffe | 13.2kV | TW22 | Transformer #X34221 located at 820 Hare Ave opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
5309 | 2004 | 6 | 15 | 0.29931 |  | 57 | 6 | 6 | Woodroffe | 13.2kV | TW22 | Re- fused O/H transfomer at 860 Killen. Suspect squirrel contact. | Ottawa | Unknown/Other | No Apparent Cause
12657 | 2008 | 6 | 15 | 0.59514 |  | 912 | 304 | 20 | Woodroffe | 13.2kV | TW22 | S20908 was blown but still closed. Crew found switch to be defective, and needed replacing. Restoration time delayed, many outages throughout city. Severe Lightning storm in effect. Possible lightning strike. | Ottawa | Adverse Weather | Lightning
20786 | 2012 | 6 | 17 | 0.75 |  | 45 | 6 | 8 | Woodroffe | 13.2kV | TW22 | A squirrel cause the fuse to open at transformer X31506 @ 2015 Lenester. | Ottawa | Foreign Interference | Animal
6758 | 2005 | 6 | 18 | 0.30417 |  | 51 | 5 | 6 | Woodroffe | 13.2kV | TW22 | Transformer Switch OTT4623 at 914 Muskoka opened due to tree branch contact | Ottawa | Tree Contacts | Inadequate Trimming
12689 | 2008 | 6 | 18 | 0.80625 |  | 57 | 4 | 4 | WOODROFFE | 13.2kV | TW22 | Tranformer X35454 at 2168 Queensgrove isolated to allow for repairs to service connections at 2172 Queensgrove | Nepean | Scheduled Outage | Repair
16283 | 2010 | 6 | 18 | 0.079167 |  | 30 | 6 | 11 | Woodroffe | 13.2kV | TW22 | Racoon contact caused fuse to blow, at 885 Ridley, crew re-fused. | Ottawa | Foreign Interference | Animal
6760 | 2005 | 6 | 19 | 0.38472 |  | 84 | 10 | 7 | Woodroffe | 13.2kV | TW22 | Switch to Transformer OTT489 at 986 Parkhurst opened due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
16302 | 2010 | 6 | 20 | 0.75625 |  | 139 | 14 | 6 | Woodroffe | 13.2kV | TW22 | Squirell contacted with transformer X34049 causing transformer fuse to blow | Ottawa | Foreign Interference | Animal
18438 | 2011 | 6 | 20 | 0.11667 |  | 53 | 10 | 11 | Woodroffe | 13.2kV | TW22 | Racoon caused fuse to blow at transformer X26050 at 885 Ridley. | Ottawa | Foreign Interference | Animal
6775 | 2005 | 6 | 22 | 0.13542 |  | 45 | 8 | 10 | Woodruff | 12/7.2kV | TW22 | Branches caused the transformer fuse to blow at the rear of 992 Hare St. | Ottawa | Tree Contacts | Inadequate Trimming
12712 | 2008 | 6 | 22 | 0.79861 |  | 60 | 12 | 12 | Woodroffe | 13.2kV | TW22 | Transformer # X31503 fuse found blown at the rear of 2060 Carling Ave. Fuse replaced all power restored. | Ottawa | Tree Contacts | Inadequate Trimming
18469 | 2011 | 6 | 23 | 0.22083 |  | 54 | 6 | 7 | Woodroffe |  | TW22 | A racoon caused transformer X34409 to blow on Winnington Ave. Transformer refused and closed | Ottawa | Foreign Interference | Animal
5370 | 2004 | 6 | 24 | 0.74097 |  | 506 | 51 | 6 | Woodroffe | 13.2kV | TW22 | Fuse to O/H transformer at 886 Winnington found blown from tree contact due to heavy wind storm. All secondary services were taken down and tangled up with tree. Extensive clean up required to clear tree & restore services, it was then determined transfomer was defective also. Customers were jumpered to transfomer at 2286 Fox. | Ottawa | Tree Contacts
5372 | 2004 | 6 | 25 | 0.073611 |  | 27 | 3 | 6 | Woodroffe | 13.2kV | TW22 | O/H transfomer at 2286 Fox interrrupted in order to jumper customers from transformer at 886 Winnington. | Ottawa | Adverse Weather | Wind
5375 | 2004 | 6 | 25 | 0.86111 |  | 39 | 8 | 12 | Woodroffe | 13.2kV | TW22 | Transformer opened to replace the service to 886 Duberry | Ottawa | Adverse Weather | Wind
12724 | 2008 | 6 | 25 | 0.43472 |  | 34 | 2 | 4 | Woodroffe | 13.2kV | TW22 | Transformer #X34220 located at 2052 Carling Ave isolated due to possible animal interference | Ottawa | Foreign Interference | Animal
16289 | 2010 | 6 | 25 | 0.39028 |  | 164 | 41 | 15 | Woodroffe | 13.2kV | TW22 | TW22 white phase overhead section on Parkhurst was isolated at S12475 to allow for tree trimming at 969 Parkhurst | Ottawa | Scheduled Outage | Preventive Maintenance
16294 | 2010 | 6 | 25 | 0.31389 |  | 81 | 14 | 10 | Woodroffe | 13.2kV | TW22 | Transformer #X35527 located at 2059 Benjamin opened up due to squirrel contact | Ottawa | Foreign Interference | Animal
14623 | 2009 | 6 | 26 | 0.81319 |  | 173 | 43 | 43 | Woodroffe TS | 13.2kV | TW22 | A section of primary line on Fox Crescent burned down at live line connection, section of line was isolated from S14621 to make repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20890 | 2012 | 6 | 27 | 0.46389 |  | 197 | 190 | 58 | Woodroffe |  | TW22 | crew isolated TW22 overhead circuit on Riddell to replace defective hydro pole. | Ottawa | Scheduled Outage | Repair
6834 | 2005 | 6 | 30 | 0.79792 |  | 50 | 9 | 11 | Woodroffe | 13.2kV | TW22 | Switch was found blown to transformer OTT5585 at 2149 Benjamin Ave due to Squirrel contact | Ottawa | Foreign Interference | Animal
16368 | 2010 | 6 | 30 | 0.30278 |  | 59 | 8 | 8 | Woodroffe | 4.16kV | TW22 | Replaced blown fuse at transformer X31506 at 2021 Lenester Ave Squirrel contact | Ottawa | Foreign Interference | Animal
8640 | 2006 | 7 | 2 | 0.35556 |  | 58 | 11 | 11 | Woodroffe | 4.16kV | TW22 | Trans OTT4186 refused after trees made contact with secondary buss | Ottawa | Adverse Weather | Wind
8656 | 2006 | 7 | 3 | 0.85694 |  | 221 | 29 | 8 | Woodroffe | 13.2kV | TW22 | Adverse weather caused transformer at 1964 lenester to open. | Ottawa | Adverse Weather | Wind
20923 | 2012 | 7 | 4 | 0.40556 |  | 63 | 6 | 6 | Woodroffe TW | 13.2kV | TW22 | Transformer X33762 at 905 Hare Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage
10853 | 2007 | 7 | 11 | 0.70486 |  | 270 | 54 | 12 | WOODROFFE | 4.16kV | TW22 | Fuse was found blown on transformer OTT5191 at 2125 Queensgrove due to a squirrel contact | Ottawa | Foreign Interference | Animal
5482 | 2004 | 7 | 12 | 0.40278 |  | 32 | 3 | 6 | Woodroffe | 13.2kV | TW22 | Transformer OTT4595 at rear of 859 Mountainview was taken out of service to move a service around | Ottawa | Unknown/Other
5492 | 2004 | 7 | 14 | 0.81458 |  | 62 | 6 | 6 | Woodroff | 13.2kV | TW22 | A squirrel made contact with transformer OTT6629 at 2362 Whtehaven Cres which made the fuse to blow. | Ottawa | Foreign Interference | Animal
18657 | 2011 | 7 | 14 | 0.5625 |  | 45 | 6 | 8 | Woodroffe | 13.2kV | TW22 | Transformer #X33664 located at 2128 Queensgrove opened up by crew to replace all connections at transformer pats. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6962 | 2005 | 7 | 16 | 0.24722 |  | 69 | 707 | 615 | Woodroffe | 13.2kV | TW22 | TW22 cable from TW to TW22 P/P/H to TW faulted and circuit load was restored on TW00. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8774 | 2006 | 7 | 17 | 0.95833 |  | 600 | 90 | 9 | Woodroffe | 13.2kV | TW22 | Mark Brown opened xfmr OTT4558 at 945 Muskoka to fix a switch that opened during the storm | Ottawa | Adverse Weather | Lightning
8775 | 2006 | 7 | 17 | 0.95833 |  | 600 | 40 | 4 | Woodroofe | 13.2kV | TW22 | Mark Brown had xfmr OTT4625 at 925 Muskoka open because the main line switch opened during the storm | Ottawa | Adverse Weather | Lightning
8757 | 2006 | 7 | 18 | 0.98403 |  | 552 | 235 | 30 | Woodroffe | 13.2kV | TW22 | A transformer fuse was found open at 848 duberry. Fuse was replaced & closed. At 929 Muskoka Ave crews found a broken switch on a local. 24/7 crew had to go to Carling to find a new switch. | Ottawa | Adverse Weather | Lightning
18726 | 2011 | 7 | 19 | 0.050694 |  | 393 | 265 | 50 | Woodroffe | 13.2kV | TW22 | Large tree down on Lenester required a crane to remove, overhead isolated for clearance | Ottawa | Tree Contacts | Tree Fallen
12935 | 2008 | 7 | 24 | 0.50347 |  | 49 | 8 | 10 | Woodroffe | 13.2kV | TW22 | Transformer #OTT4187 located at 820 Maplecrest Ave isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
7022 | 2005 | 7 | 25 | 0.47222 |  | 87 | 17 | 12 | Woodroffe | 13.2kV | TW22 | Isolated Transformer 2026 at 832 Fairlawn to install new service | Ottawa | Scheduled Outage
7029 | 2005 | 7 | 26 | 0.94792 |  | 20 | 0 | 1 | Woodroffe | 13.2kV | TW22 | Trans OTT357 at 2191 Benjamin Ave isolated to repair defective LLC | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16589 | 2010 | 7 | 29 | 0.41667 |  | 455 | 46 | 6 | Woodroffe | 13.2kV | TW22 | KT616 at 2080 Carling was isolated to replace a leaking transformer. | Ottawa | Scheduled Outage | Repair
18847 | 2011 | 7 | 29 | 0.52778 |  | 120 | 8 | 4 | Woodroffe | 13.2kV | TW22 | Isolated transformer X33898 at 818 Riddell Ave for service up-grade | Ottawa | Scheduled Outage | Construction
18861 | 2011 | 7 | 30 | 0.26458 |  | 113 | 17 | 9 | Woodroffe | 13.2kV | TW22 | Transformer #X34048 located at 941 Muskoka opened up due to animal contact | Ottawa | Foreign Interference | Animal
11026 | 2007 | 8 | 9 | 0.38333 |  | 193 | 39 | 12 | Woodroffe | 13.2kV | TW22 | Transformer #55C4B-0338 located at 877 Killeen isolated due to tree contact. | Ottawa | Tree Contacts | Inadequate Trimming
16755 | 2010 | 8 | 16 | 0.55556 |  | 143 | 17 | 7 | WOODROFFE | 13.2kV | TW22 | Transformer X33661 at 2100 Queensgrove Rd isolated to allow for | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7149 | 2005 | 8 | 17 | 0.25556 |  | 32 | 6 | 12 | TW | 13.2kV | TW22 | Probable animal contact at Tx OTT2028, 853 Duberry. Re-fused & closed. | Ottawa | Foreign Interference | Animal
7171 | 2005 | 8 | 19 | 0.52708 |  | 72 | 10 | 8 | Woodroffe | 13.2kV | TW22 | Switch to transformer OTT3898 at 1977 Shron St opened due to vines on the pole | Ottawa | Tree Contacts | Inadequate Trimming
11100 | 2007 | 8 | 19 | 0.67222 |  | 237 | 16 | 4 | Woodroffe | 13.2kV | TW22 | Transformer OTT5193 at 2168 Queensgrove Dr in Ottawa replaced due to oil leak. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7184 | 2005 | 8 | 23 | 0.36875 |  | 29 | 6 | 13 | Woodroffe | 13.2kV | TW22 | Transformer OTT5587 at 2165 Benjamin Ave was isolated to replace triplex service | Ottawa | Scheduled Outage | Repair
7219 | 2005 | 8 | 26 | 0.42569 |  | 54 | 9 | 10 | Woodroffe | 13.2kV | TW22 | Isolated Transformer at 840 Duberry to remove vines and install a new service | Ottawa | Scheduled Outage | Preventive Maintenance
15018 | 2009 | 8 | 28 | 0.16458 |  | 138 | 23 | 10 | WOODROFFE | 13.2kV | TW22 | Transformer X31504 fuse blew, due to suspected animal contact. Transformer refused and held. | Ottawa | Unknown/Other
11195 | 2007 | 8 | 29 | 0.76389 |  | 250 | 2562 | 615 | Woodroffe | 13.2kV | TW22 | TW22 auto reclosed due to blown fuses on line, circuit repaired and all customers restored | Ottawa | Adverse Weather | Lightning
15026 | 2009 | 8 | 29 | 0.18681 |  | 551 | 772 | 87 | Woodroffe Teminal | 13.2kV | TW22 | Blue & White fuses found blown at switch S21976 at 2050 Lenester Ave. Crews patrolled and found a possible tree that might have made contact with the high winds this morning located at 988 Hare Avenue.Crew tried to close switxches back in and held for sometime, then re-opened. Work protection put into place and Yves Mercier from Asplund trimmed trees away from overhead conductors, 87 customers were affected and all power was restored at 2:12pm. Woddroffe (TW22). ID#15026 | Nepean | Tree Contacts | Inadequate Trimming
7277 | 2005 | 9 | 4 | 0.32778 |  | 217 | 14 | 4 | Woodroffe | 13.2kV | TW22 | Transformer #OTT3609 located rear of 2032 Killarney isolated due to a defective switch | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19097 | 2011 | 9 | 6 | 0.47917 |  | 40 | 3 | 5 | Woodroffe | 13.2kV | TW22 | Transformer X35188 at 1940 Carling was opened to allow crews to make repairs. | Ottawa | Scheduled Outage | Repair
11278 | 2007 | 9 | 9 | 0.38611 |  | 118 | 12 | 6 | Woodroffe | 13.2kV | TW22 | Refused transformer OTT4623 at 920 Muskoka Ave (Squirrel Contact) | Ottawa | Foreign Interference | Animal
11279 | 2007 | 9 | 9 | 0.56736 |  | 42 | 4 | 6 | Woodroffe | 13.2kV | TW22 | Refused transformer OTT3613 at 581 Dunlevie Ave (Squirrel contact) | Ottawa | Foreign Interference | Animal
16966 | 2010 | 9 | 19 | 0.72361 |  | 57 | 8 | 8 | Woodroffe | 13.2kV | TW22 | Squirrel contact cause transformer X31506 at 2006 Lenester to open. | Ottawa | Foreign Interference | Animal
9276 | 2006 | 9 | 22 | 0.37083 |  | 51 | 10 | 12 | Woodroffe | 13.2kV | TW22 | Transformer #OTT5194 located at 2164 Benjamin isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
16979 | 2010 | 9 | 22 | 0.39167 |  | 52 | 28 | 32 | Woodroffe | 4.16kV | TW22 | Line switch at 2220 Fox Cres opened due to vines in the overhead line crew removed the vines, re-fused the switch and restored the power. | Ottawa | Tree Contacts | Inadequate Trimming
13281 | 2008 | 9 | 23 | 0.70625 |  | 28 | 4 | 9 | Woodroffe | 13.2kV | TW22 | Transformer X31503, located at 814 Hare isolated due to animal contact, Squirrel. Refused and all good | Ottawa | Foreign Interference | Animal
16999 | 2010 | 9 | 25 | 0.70139 |  | 82 | 4 | 3 | Woodroffe | 13.2kV | TW22 | Transformer X32446 at 2207 Fox isolated for crew to make repairs to burnt secondary | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13313 | 2008 | 10 | 2 | 0.56389 |  | 67 | 10 | 9 | Woodroffe | 13.2kV | TW22 | Transformer #X31503 located at 2052 Carling Ave isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
17057 | 2010 | 10 | 5 | 0.54167 |  | 35 | 6 | 11 | Woodroffe | 13.2kV | TW22 | Transformer #X33406 located at 875 Winnington opened by crew to connect new service for the Serv Dept | Ottawa | Scheduled Outage | Construction
13348 | 2008 | 10 | 9 | 0.14028 |  | 718 | 121 | 60 | Woodroffe | 13.2kV | TW22 | Suspected lightening at Woodroffe and Fox (TW22) caused the top of the pole to break off bringing two phases of primary conductor down across Woodroffe. Isolation established to clear downed conductor. Section rebuilt and all customers restored. | Ottawa | Lightning | Direct Strike
15247 | 2009 | 10 | 11 | 0.57986 |  | 103 | 15 | 9 | Woodroffe | 13.2kV | TW22 | animal contact caused transformer X32432 @ rear of 933 parkhurst to open. | Ottawa | Foreign Interference | Animal
15258 | 2009 | 10 | 14 | 0.40625 |  | 65 | 2 | 2 | Woodroffe | 13.2kV | TW22 | Isolated transformer X32445 at 2228 Fox Cres for service up-grade | Ottawa | Scheduled Outage | Preventive Maintenance
4279 | 2003 | 10 | 15 | 0.73472 |  | 62 | 10 | 10 | Woodroffe | 12/7.2kV | TW22 | Transformer 4601 at the rear of 976 Mountainview. Tree down. | Ottawa | Adverse Weather | Wind
13370 | 2008 | 10 | 15 | 0.52847 |  | 72 | 16 | 13 | Woodroffe | 13.2kV | TW22 | REFUSED SWITCH FEEDING THE TFR X32929 @ 2373 WHITEHAVEN. CAUSE OF OUTAGE SQUIRREL CONTACT | Ottawa | Foreign Interference | Animal
19429 | 2011 | 10 | 20 | 0.40278 |  | 305 | 391 | 77 | Woodroffe TW | 13.2kV | TW22 | Stormy weather caused S21976 W & B to blow. Crew trimmed trees before repairing downed conductor. Kingsmere / Queensgrove area. | Ottawa | Adverse Weather | Wind
13544 | 2008 | 11 | 1 | 0.47083 |  | 72 | 7 | 6 | WOODROFFE | 13.2kV | TW22 | Refused blown fuse feeding transformer X33762 at 905 Hare Ave | Ottawa | Foreign Interference | Animal
17206 | 2010 | 11 | 2 | 0.39583 |  | 75 | 16 | 13 | Woodroffe | 13.2kV | TW22 | Transformer #X32430 located at 907 Iroquois opened by crew to change a service | Ottawa | Scheduled Outage | Construction
17211 | 2010 | 11 | 3 | 0.39583 |  | 40 | 7 | 11 | Woodroffe | 13.2kV | TW22 | Transformer #X33773 located at 2171 Rushton opened by crew to install a new service | Ottawa | Scheduled Outage | Construction
17213 | 2010 | 11 | 3 | 0.47083 |  | 46 | 8 | 11 | Woodroffe | 13.2kV | TW22 | Transformer #X33759 located at 889 Aaron Ave opened due to squirrel interference. | Ottawa | Foreign Interference | Animal
4392 | 2003 | 11 | 4 | 0.875 |  | 50 | 6 | 7 | Woodroffe | 13.2kV | TW22 | Transformer OTT5276 in Ottawa was isolated to allow for re-connection of a secondary service wire that was taken down by a tree limb ID#4392 | Ottawa | Tree Contacts | Tree Limb Fallen
19538 | 2011 | 11 | 7 | 0.50417 |  | 59 | 7 | 7 | Woodroffe | 13.2kV | TW22 | Transformer X32930 at 2291 Whitehaven Cres refused after animal contact - squirrel | Ottawa | Foreign Interference | Animal
13618 | 2008 | 11 | 15 | 0.625 |  | 60 | 11 | 11 | Woodroffe | 13.2kV | TW22 | At 15:00 trans at 863 Duberry St was isolated to make repairs to defective connections | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5894 | 2004 | 11 | 16 | 0.37847 |  | 55 | 3 | 3 | Woodroffe | 4.16kV | TW22 | Transformer fuse at OTT489 opened due to squirrel contact. | Ottawa | Foreign Interference | Animal
4500 | 2003 | 11 | 21 | 0.50694 |  | 50 | 6 | 7 | Woodroffe | 13.2kV | TW22 | Transformer at 2100 Queensgrove was opened to change leaking pothead. 7 customers on queensgrove were interrupted. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
13662 | 2008 | 11 | 24 | 0.44514 |  | 49 | 8 | 10 | WOODROFFE | 13.2kV | TW22 | Transformer #X32929 at 2371 Georgina Dr isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
5929 | 2004 | 11 | 26 | 0.45833 |  | 65 | 9 | 8 | Woodroffe | 13.2kV | TW22 | Transformer OTT2278 at 1008 Fairlawn taken out of service to redo secondary connections. 8 customers on Benjamin & Fairlawn affected. Customers at home were advised. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19643 | 2011 | 11 | 27 | 0.99028 |  | 29 | 17 | 36 | Woodroffe | 13.2kV | TW22 | Live Line clamp was burning up at S17988 . Crew opened switch to make repairs. Benjamin & Rushton streets affected. | Ottawa | Defective Equipment
17354 | 2010 | 11 | 29 | 0.38333 |  | 164 | 104 | 38 | Woodroffe | 13.2kV | tw22 | S29439 to end of line on TW22 circuit isolated on Riddell, Killeen and Dunlevie to allow crews to remove 1 span of overhead near Carling. | Ottawa | Scheduled Outage | Construction
13769 | 2008 | 12 | 17 | 0.54028 |  | 42 | 6 | 9 | Woodroffe | 4.16kV | TW22 | Refused blown switch at transformer X31503 at 814 Hare Ave (squirrel contact) | Ottawa | Foreign Interference | Animal
17434 | 2010 | 12 | 19 | 0.62292 |  | 33 | 5 | 9 | Woodroffe | 13.2kV | TW22 | Transformer #X33769 located at 2145 Rushton Rd opened due to animal contact | Ottawa | Foreign Interference | Animal
17447 | 2010 | 12 | 22 | 0.39931 |  | 55 | 3 | 3 | WOODROFFE | 13.2kV | TW22 | Transformer X33663 @ 2088 Queensgrove Rd isolated for changeover | Ottawa | Scheduled Outage | Construction
15568 | 2009 | 12 | 27 | 0.18681 |  | 241 | 1460 | 615 | Woodrfoffe | 13.2kV | TW22 | TW22 breaker was opened manually from SCADA due to live primary down & sparking at rear of 2200 Carling. The downed conductor was cut clear for repairs, as well as an O/H xfmr on Kingsmere was opened for a separate problem of downed neautral conductor and then the main circuit was restored. Reapirs were made to both problems & all power restored. | Ottawa | Adverse Weather
15585 | 2009 | 12 | 29 | 0.069444 |  | 467 | 608 | 176 | Woodroffe | 13.2kV | TW22 | TW22 auto reclosed, crews report Single fuse Open at S13369, patroled RED phase circuits west of Woodroffe. Crews found 1 span of primary down. Repairs done and all power restored at 9:27am . Woodroffe (TW22). ID#15585. | Ottawa | Adverse Weather | Wind
3114 | 2003 | 1 | 13 | 0.53819 |  | 25 | 214 | 513 | Woodroffe TS | 13.2kV | TW2UC | TW2UC-Z blue phase insulator blew off the structure at clyde causing loss of power to the T3 bank. Power was restored to the T3 bank using the TW1UC circuit. The configuration of the station was abnormal for an isolation for a contractor. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11143 | 2007 | 8 | 24 | 0.19097 |  | 7 | 60 | 513 | Woodroffe | 13.2kV | TW2UC | Severe Lightning Storm in effect caused TW16 breaker to open. TW16 closed by System and holding | Ottawa | Lightning
11192 | 2007 | 8 | 29 | 0.76389 |  | 12 | 103 | 513 | Woodroffe | 13.2kV | TW2UC | TW2UC circuit opened and locked out due to adverse weather, circuit closed in via SCADA and holding | Ottawa | Adverse Weather
3487 | 2003 | 5 | 26 | 0.64583 |  | 68 | 495 | 658 | WOODROFFE | 13.2kV | TW2UV | TW2UV TRIPPED ON GRD FAULT. CUSTOMERS REPORTED FLASH IN THE AREA OF IRIS & ADIRONDACK. LOAD TRANSFERRED TO TW1UC AND TW2UC ISOLATED. PATROL OF O/H DID NOT FIND AN OBVIOUS CAUSE. ON CALL CREW WAS CALLED IN TO DISCONNECT P/P/H'S AND HIGH POT CABLE. | Ottawa | Unknown/Other
3551 | 2003 | 6 | 11 | 0.27778 |  | 115 | 1068 | 830 | WOODROFFE | 13.2kV | TW2UV | TW02 (TW2UV) tripped. The line had just been restored about midnight after insulator changes due to previous trip. TM1UV had been isolated for insulator changes and TM2UV was carrying some of its load. The load was restored on TW1UV & TW3UV and the line isolated. A patrol found no obvious cause. After line was tested by sticks the crew requested an OF14 to test by energizing. At 14:30 the breaker was closed to try to put TW2UV on pot, but it tripped free. The line was re-isolated for further checking NOTE: They believe the cause was more defective insulators and replaced more. Nothing definite. | Ottawa | Unknown/Other
11858 | 2007 | 12 | 17 | 0.55556 |  | 25 | 4 | 9 | Woodroffe | 4.16kV | TW32 | Isolated transformer OTT4624 at 912 Mooney Ave to up-grade service | Ottawa | Scheduled Outage | Preventive Maintenance
12636 | 2008 | 6 | 15 | 0.79722 |  | 16 | 0 | 1 | Woodroffe | 13.2kV | TW3UV | SCADA indicates TW07 Breaker tripped, due to severe lightning storm in effect. TW08 Breaker tripped at the same time. Breaker closed and holding. | Ottawa | Adverse Weather | Lightning
7550 | 2005 | 11 | 1 | 0.38889 |  | 38 | 1 | 1 | WOODROFFE | 13.2kV | TW3UV | Squirrel contact caused circuit TW3UV to open. | Ottawa | Foreign Interference | Animal
4894 | 2004 | 3 | 15 | 0.4125 |  | 156 | 122 | 47 | UA | 4.16kV | UA02 | K396 & K397 on Nootka cr were isolated for planned cable maintenance. | Ottawa | Scheduled Outage | Preventive Maintenance
8154 | 2006 | 4 | 15 | 0.63194 |  | 120 | 2 | 1 | Albion | 4.16kV | UA02 | Vault V11 at 2995 Albion was isolated for the Oncall crew to replace a broken bushing on the 600 V bank. Only the one apartment building was affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18272 | 2011 | 6 | 1 | 0.67986 |  | 46 | 127 | 165 | Albion | 4.16kV | UA02 | Patrol revealed no apparent cause, closed by SCADA | Ottawa | Unknown/Other | No Apparent Cause
12542 | 2008 | 6 | 4 | 0.39931 |  | 110 | 38 | 21 | Albion | 4.16kV | UA02 | Isolated and replaced transformer K400 at 1456 Heatherington Rd (pcb oil) | Ottawa | Scheduled Outage | Preventive Maintenance
16413 | 2010 | 7 | 6 | 0.97917 |  | 8 | 0 | 1 | Albion | 13.2kV | UA02 | Opened 3 phase transformer X28017 at the rear of 2677 Ayers Ave to remove dead racoon | Ottawa | Foreign Interference | Animal
14871 | 2009 | 7 | 29 | 0.54931 |  | 1 | 4 | 223 | Albion | 4.16kV | UA02 | Storm in the area and the UA02 and UAK1Y1 trip, close via scada and holding in Albion and Walkley area. | Ottawa | Adverse Weather | Lightning
13365 | 2008 | 10 | 14 | 0.58472 |  | 358 | 6 | 1 | Albion Sub | 4.16kV | UA02 | V11 at 2995 Albion was interrupted to repair defective customer owned circuit breaker in the vault. 1 Customer affected and power was restored at 08:00pm | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7482 | 2005 | 10 | 19 | 0.40139 |  | 53 | 17 | 19 | Albion | 4.16kV | UA02 | Transformer #K00392 located at 1454 G Heatherington isolated due to meter base change over to one of the units. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7587 | 2005 | 11 | 9 | 0.77083 |  | 63 | 12 | 11 | Albion | 4.16kV | UA02 | V763 at 1436 walkley was isolated to replace faulty transformer. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9737 | 2006 | 11 | 27 | 0.40556 |  | 129 | 6 | 3 | albion | 4.16kV | UA02 | M Gruich isolated trf. # 650 @ 2663 Ayers for PCB trf. Change | Ottawa | Scheduled Outage | Preventive Maintenance
9739 | 2006 | 11 | 27 | 0.54861 |  | 71 | 4 | 3 | Albion | 4.16kV | UA02 | Isolated Transformer at 2659 Ayers to replace Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
18448 | 2011 | 6 | 21 | 0.25 |  | 95 | 3 | 2 | Albion Sub | 4.16kV | UA03 | At 06:00 P97 was isolated to allow crew to transfer plant to new pole. 2 customers were affected for 95 minutes. Albion Sub (UA03) ID#18448 | Ottawa | Scheduled Outage
8587 | 2006 | 6 | 25 | 0.0013889 |  | 58 | 1 | 1 | Albion | 4.16kV | UA03 | V86 @ 1729 bank was isolated to change defective switch on three phase O/H bank. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16325 | 2010 | 6 | 25 | 0.5625 |  | 25 | 6 | 15 | Albion | 4.16kV | UA03 | Isolated Transformer K653 at 1225 Ledbury Ave to disconnect service | Ottawa | Scheduled Outage | Emergency Services Request
18536 | 2011 | 6 | 27 | 0.50694 |  | 30 | 5 | 10 | Albion | 4.16kV | UA03 | Isolated transformer K658 to identify the address for secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
18537 | 2011 | 6 | 27 | 0.53125 |  | 60 | 10 | 10 | Albion | 4.16kV | UA03 | Isolated transformer K657 to identify the address for secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
3668 | 2003 | 7 | 3 | 0.54583 |  | 15 | 4 | 15 | Albion | 4.16kV | UA03 | Reason was listed as reconnect for arrears, nothing listed in causes to cover that. K659 at 1281 Ledbury Ave | Ottawa | Foreign Interference
16486 | 2010 | 7 | 17 | 0.8125 |  | 86 | 17 | 12 | Albion | 4.16kV | UA03 | A tree limb had fallen on the triplex that feedds 1224 Surrey, the transformer fuse at X27297 was open to make repairs | Ottawa | Tree Contacts | Tree Limb Fallen
16506 | 2010 | 7 | 21 | 0.41528 |  | 130 | 37 | 17 | Albion | 4.16kV | UA03 | K653 @ 1225 Ledbury was isolated for all Hydro Ottawa sources to allow crews to replace defective insulators. | Ottawa | Scheduled Outage | Preventive Maintenance
5611 | 2004 | 8 | 4 | 0.71528 |  | 5 | 2 | 18 | UA | 4.16kV | UA03 | As per dispatch, K661 opened at 17:10 to lift lid on live front pedestal. 18 customers restored at 17:15. Customers defective service caused fuse to blow at pedestal. | Ottawa | Foreign Interference | Equipment Failure - Cause Unknown
11376 | 2007 | 9 | 24 | 0.56528 |  | 11 | 2 | 12 | Albion | 4.16kV | UA03 | Isolated transformer K654 at 1285 Ledbury Ave to open live front Ped to disconnect service | Ottawa | Scheduled Outage | Emergency Services Request
15237 | 2009 | 10 | 8 | 0.34722 |  | 610 | 214 | 21 | Albion | 4.16kV | UA03 | Transformer #K659 located at 1275 Ledbury Ave isolated for Marcel Elec to make repairs | Ottawa | Scheduled Outage | Construction
15252 | 2009 | 10 | 13 | 0.38542 |  | 20 | 5 | 16 | Albion | 4.16kV | UA03 | Isolated transformer K657 at 1250 Ledbury Ave to disconnect Ped 657P1 feeding 3 customers for contractor digging near secondary services | Ottawa | Scheduled Outage | Construction
4400 | 2003 | 11 | 6 | 0.79514 |  | 15 | 5 | 20 | Albion | 4.16kV | UA03 | A possibloe loose connection on the current limiter board in Kiosk 656 caused secondary current limit fuse to blow and board to flash over. Crew made temporary repairs because of lack of proper parts. Customers at 1225 and 1235 ledbury were interrupted. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
4408 | 2003 | 11 | 7 | 0.56944 |  | 105 | 35 | 20 | Albion | 4.16kV | UA03 | Transformer K00656 on circuit UA03 was opened to do repairs. 20 Customers affected in power outage. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13628 | 2008 | 11 | 17 | 0.57431 |  | 78 | 269 | 623 | Albion | 4.16kV | UA03 | A Garbage truck left it's box up and has broken a pole and another pole is leaning at the corner of Kitchener and Bank. A guy wire also was broken off sitting on the secondary. No wires down. Premises cleared and breaker closed to restore circuit to normal. Follow-up required to make pole repairs. One o/h transformer was left off to remove guy wire off secondary bus. Wire removed and transformer closed to restore power. | Ottawa | Foreign Interference | Vehicle
19592 | 2011 | 11 | 18 | 0.35556 |  | 178 | 6 | 2 | Albion | 4.16kV | UA03 | TP7025 at 1910 Bank was isolated to allow contractor to pull in new secondary cables. | Ottawa | Scheduled Outage | Construction
19788 | 2012 | 1 | 5 | 0.51736 |  | 25 | 4 | 10 | Albion | 4.16kV | UA04 | Transformer #K404 located at 1485 Heatherington opened by crew to make repairs burnt leg on U/G service | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
19839 | 2012 | 1 | 17 | 0.072222 |  | 26 | 0 | 1 | Albion | 4.16kV | UA04 | Crew opened 4kv transformer P261 @ 2429 Holley lane to replace defective overhead switch. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
12015 | 2008 | 2 | 6 | 0.375 |  | 135 | 27 | 12 | Albion | 4.16kV | UA04 | Isolated K404 at 1485 Heatherington Rd to repair service at the Ped P404 | Ottawa | Scheduled Outage | Repair
7915 | 2006 | 2 | 14 | 0.91667 |  | 5 | 2 | 22 | ALBION | 4.16kV | UA04 | 4KV KIOSK k404 AT 1485 Heatherington was opened to test for possible defective secondary underground service to unit 88. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7916 | 2006 | 2 | 14 | 0.93194 |  | 23 | 8 | 22 | Albion | 4.16kV | UA04 | 4KV KIOSK k404 AT 1485 Heatherington was opened to replace defective current limiting fuse feeding secondary underground service to unit 88 fed from pedestal 2. | Ottawa | Defective Equipment
20014 | 2012 | 2 | 14 | 0.38472 |  | 121 | 44 | 22 | Albion | 4.16kV | UA04 | K239 at 41 Corley was isolated for HOL crew to make insulator repairs to the kiosk | Ottawa | Scheduled Outage
14277 | 2009 | 5 | 1 | 0.39028 |  | 163 | 33 | 12 | Albion | 4.16kV | UA04 | K570 at 1776 Featherstone was isolated to replace transformer, insulators, etc and remove asbestos. 12 customers on Featherstone, Wyndale & Haddington were affected. | Ottawa | Scheduled Outage | Preventive Maintenance
5176 | 2004 | 5 | 18 | 0.83889 |  | 87 | 28 | 19 | UA | 4.16kV | UA04 | UA04 red phase dip to K405 blown, K405 checks OK, K405 to pole opened & K405 to K409 closed restoring power to 19 customers. Possible defective cable. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10934 | 2007 | 7 | 23 | 0.38472 |  | 369 | 338 | 55 | Albion Sub | 4.16kV | UA04 | S15963 to end of line 2400 Virgina Ave isolated to allow re-string of overhaed conductor. | Ottawa | Scheduled Outage | Construction
14996 | 2009 | 8 | 22 | 0.74375 |  | 309 | 62 | 12 | Albion | 4.16kV | UA04 | Holder for tx fuse at K570 at 1776 Featherstone failed and required replacing. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9058 | 2006 | 8 | 25 | 0.62778 |  | 137 | 78 | 34 | ALBION | 4.16kV | UA04 | 34 Customers at 1485 Heatherington were interrupted due to a defective cable between K403 and K404. | Ottawa | Defective Equipment
9105 | 2006 | 8 | 31 | 0.53472 |  | 45 | 13 | 17 | Albion | 4.16kV | UA04 | K404 at 1485 Heatherington was isolated to allow crew to locate defective primary cable. | Ottawa | Scheduled Outage | Repair
9119 | 2006 | 9 | 5 | 0.375 |  | 105 | 19 | 11 | Albion | 4.16kV | UA04 | At 09:00 trans K569 at 2364 Haddington Cres was isolated for trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9169 | 2006 | 9 | 9 | 0.28472 |  | 340 | 193 | 34 | Albion | 4.16kV | UA04 | A defective U/G cable between K404 & K403 @ 1485 Heatherington was found. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13212 | 2008 | 9 | 10 | 0.37708 |  | 251 | 63 | 15 | Albion | 4.16kV | UA04 | K407 at 1535 Heatherington isolated to allow cable splice between K406 and K407. | Ottawa | Scheduled Outage | Construction
9269 | 2006 | 9 | 21 | 0.52083 |  | 70 | 13 | 11 | Albion | 4.16kV | UA04 | Isolated and replaced transformer K00568 at 2378 Haddington (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
15149 | 2009 | 9 | 22 | 0.72222 |  | 9 | 0 | 1 | Albion | 4.16kV | UA04 | Transformer #X29055 located at 2376 Jefferson to isolate secondary due to knob pulled out of house | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15152 | 2009 | 9 | 22 | 0.86458 |  | 40 | 1 | 1 | Albion | 4.16kV | UA04 | Transformer #X29055 located at 2376 Jefferson isolated to reconnect service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11624 | 2007 | 10 | 29 | 0.45139 |  | 105 | 7 | 4 | ALBION | 4.16kV | UA04 | Transformer #X26986 at 2460 Wyndale isolated to allow contractor to make service repairs | Ottawa | Scheduled Outage | Repair
15471 | 2009 | 12 | 4 | 0.39236 |  | 91 | 30 | 20 | Albion | 4.16kV | UA04 | To install proper meter base & cables @ K244 3054 Fairlea cres. | Ottawa | Scheduled Outage | Construction
9804 | 2006 | 12 | 7 | 0.22917 |  | 347 | 6 | 1 | Albion | 4.16kV | UA04 | White phase cable fault on dip to 4 kv vault V756 at 2400 Virginia caused fuse to blow a P/P/H switches. CB1 breaker was opened by 24/7 to find fault & make repairs. The faulted cable was replaced with the spare cable. Only the 1 apartment bldg was affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11867 | 2007 | 12 | 22 | 0.53472 |  | 30 | 10 | 20 | Albion | 4.16kV | UA04 | Transformer #K404 located at 1485 Heatherington Rd isolated to disconnect service for unit 70 due to ice damage (knocked the meter off the wall) | Ottawa | Adverse Weather
11871 | 2007 | 12 | 22 | 0.77431 |  | 6 | 1 | 19 | Albion | 4.16kV | UA04 | Transformer K404 located at 1485 Heatherington Rd isolated to reconnect service for unit 70 after repairs from ice damage (knocked the meter off the wall) | Ottawa | Adverse Environment
9778 | 2006 | 12 | 2 | 0.0034722 |  | 91 | 1474 | 972 | Albion | 13 & 4 kV | UA04, 2203 | UA04 & TA21 breakers opened at the same time, both circuits run together from Albion Station to Walkley & Heron. The common section was patrolled with no obvious problem found. Both circuits were then energized successfully. An extra 288 customers were interrupted due to early problem on 5308/TA1JP. | Ottawa | Adverse Weather | Ice Storm
7921 | 2006 | 2 | 16 | 0.65972 |  | 370 | 148 | 24 | Albion | 4.16kV | UA05 | K1080 supplying units 38 to 84 at 3019 Fairlea failed. An on-call crew was called in to change the defective transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14362 | 2009 | 5 | 15 | 0.39097 |  | 143 | 21 | 9 | Albion | 4.16kV | UA05 | Transformer K563 at 1681 Amberdale isolated for replacement. | Ottawa | Scheduled Outage | Repair
3624 | 2003 | 6 | 20 | 0.46875 |  | 95 | 6 | 4 | UA | 4.16kV | UA05 | K562 at 1692 Featherstone was opened for planned service work affecting 1684, 1692, 1700, 1708 Featherstone dr. | Ottawa | Scheduled Outage | Preventive Maintenance
10848 | 2007 | 7 | 11 | 0.55139 |  | 71 | 15 | 13 | Albion | 4.16kV | UA05 | Planned outage to replace transformer K814 at 1565 Heron Rd. | Ottawa | Scheduled Outage | Repair
18790 | 2011 | 7 | 21 | 0.51806 |  | 74 | 113 | 92 | Albion | 4.16kV | UA05 | J Magee had a forced outage on Finn cres due to low voltages, crew transfered load and restored. | Ottawa | Scheduled Outage
9099 | 2006 | 8 | 30 | 0.58333 |  | 80 | 19 | 14 | Albion | 4.16kV | UA05 | Mike Gruich opened K1093 at 127 Gable to do a pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
9100 | 2006 | 8 | 30 | 0.58333 |  | 80 | 20 | 15 | Albion | 4.16kV | UA05 | Mike Gruich opened K1092 at 120 Gable to do a transformer pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
9101 | 2006 | 8 | 30 | 0.63889 |  | 40 | 8 | 12 | Albion | 4.16kV | UA05 | Mike Gruich opened K01099 at 48 Paddington to do a pcb trans change | Ottawa | Scheduled Outage | Preventive Maintenance
5755 | 2004 | 8 | 31 | 0.77431 |  | 430 | 64 | 9 | UA | 4.16kV | UA05 | A defective transformer, K313 at 12 Garand place was replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9253 | 2006 | 9 | 20 | 0.37153 |  | 110 | 11 | 6 | Albion | 13.2kV | UA05 | Isolated and replaced transformer K564 at 1705 Amberdale Cres (PCB OIL) | Ottawa | Scheduled Outage | Preventive Maintenance
9279 | 2006 | 9 | 22 | 0.39583 |  | 85 | 11 | 8 | Albion | 4.16kV | UA05 | Transformer #K00314 located at 15 Garand isolated due to a PCB change. PC10 #1052 | Ottawa | Scheduled Outage | Preventive Maintenance
4435 | 2003 | 11 | 12 | 0.50347 |  | 112 | 22 | 12 | Albion | 4.16kV | UA05 | Transformer #5767 at 1233 Sherman Drive was isolated to allow for the repair of a defective service wire. ID#4435 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4448 | 2003 | 11 | 13 | 0.79861 |  | 50 | 42 | 50 | Albion | 4.16kV | UA05 | White phase switch to K582 at pole #12 on UA05 was flashing with wind gusts and was opened by the crew to eliminate flashing. | Ottawa | Adverse Weather | Wind
7765 | 2005 | 12 | 29 | 0.55903 |  | 30 | 8 | 16 | Albion | 4.16kV | UA05 | Transformer #OTT3105 located at 1647 Heron Rd isolated-pole was knocked down on Fri, transformer was hanging by conductors.Pole was replaced & they hung a new transformer. Had to jump one side of secondary over to another. Trans opened to energize the other ones. | Ottawa | Scheduled Outage | Repair
6915 | 2005 | 7 | 13 | 0.43542 |  | 36 | 292 | 486 | Albion Sub | 4.16kV | UA05 & UA07 | UAK1Y1 breaker tripped on red ph inst. Fault. Load of UA05 & UA07 on K1Y1 at time due to UA06 cable fault and UAT2 gas accumulation trip earlier. Report of high hoe on Banff off Kitchener checked with no apparent cause. Lightning activity in distance reported. No apparent cause at this time. | Ottawa | Unknown/Other | No Apparent Cause
6123 | 2005 | 1 | 7 | 0.47361 |  | 167 | 50 | 18 | Albion | 4.16kV | UA06 | K595 at 2884 Cedarwood was isolated for Hydro Ottawa to make repairs & prep for upcomnig additions. | Ottawa | Scheduled Outage | Repair
11950 | 2008 | 1 | 17 | 0.57361 |  | 997 | 704 | 198 | Albion | 13.2kV | UA06 | From V123 White phase cable to PPH and red phase cable to V121 fault. V123 to arrange emergency generator. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11958 | 2008 | 1 | 18 | 0.72917 |  | 261 | 4 | 1 | Albion | 4.16kV | UA06 | From V123 White phase cable to PPH and red phase cable to V121 fault. Customer @ V123 on generator supply, generator removed at 17:30. Cables repaired & Hydro supply available as of 19:34, customer electrician damaged 600V secondary main while disconnecting generator. Customer completed repairs on 600V secondary main & ESA approval received before V123 finally energized. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15681 | 2010 | 1 | 25 | 0.27292 |  | 212 | 375 | 116 | Albion | 4.16kV | UA06 | Cable fault between S17116 and K597 caused an outage to 116 customers in the Walkley, Cedarwood and Collistor area. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12039 | 2008 | 2 | 13 | 0.39722 |  | 60 | 16 | 16 | UA | 4.16kV | UA06 | TP3496 at 500 Reardon isolated for insert and elbow replacement. 500 to 530 Reardon Private, 16 customers | Ottawa | Scheduled Outage | Construction
17956 | 2011 | 4 | 18 | 0.50694 |  | 85 | 1 | 1 | Albion | 4.16kV | UA06 | A burnt live line stirrup caused one phase of UA06 overhead line at Holley lane to come down, feeding V408. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
3589 | 2003 | 6 | 18 | 0.36806 |  | 375 | 75 | 12 | Albion | 4.16kV | UA06 | K00588 2882 Sandalwood took outage to replace transformer | Ottawa | Scheduled Outage | Construction
6913 | 2005 | 7 | 13 | 0.19097 |  | 84 | 409 | 684 | UA | 4.16kV | UA06 | UA06 tripped due to a cable fault, during fault finding, the UAT2 tripped on a gas accumulation alarm. UA05, 07 load now lost. UA06 was transferred to UA00 & UA05, 07 were put on by-pass at UA. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12971 | 2008 | 7 | 30 | 0.41667 |  | 146 | 2 | 1 | Albion | 4.16kV | UA06 | Vault V407 at 2379 Holly Lane isolated to replace a defective transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16821 | 2010 | 8 | 28 | 0.21875 |  | 125 | 191 | 126 | Albion | 4.16kV | UA06 | White phase cable fault between S17116 & K597. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9132 | 2006 | 9 | 7 | 0.32986 |  | 90 | 15 | 10 | Albion | 4.16kV | UA06 | Chris Williams opened xfmr at 2380 Holly to do a pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
11375 | 2007 | 9 | 24 | 0.58681 |  | 15 | 3 | 11 | Albion | 4.16kV | UA06 | Isolated transformer K401 at 1462 Heatherington Rd to open live front Ped to disconnect service | Ottawa | Scheduled Outage | Emergency Services Request
9317 | 2006 | 9 | 26 | 0.5625 |  | 20 | 7 | 20 | Albion | 4.16kV | UA06 | Denis Martin isolated xfmr K597 at 2882 Cedarwood to connect a secondary service. He used tag PC10A#125 | Ottawa | Scheduled Outage
19338 | 2011 | 10 | 7 | 0.39375 |  | 138 | 46 | 20 | Albion | 4.16kV | UA06 | K596 was isolated to all crews to cut underground loop over to new switch S20018 on AU06 circuit at Ceaderwood & Walkley | Ottawa | Scheduled Outage | Construction
19354 | 2011 | 10 | 11 | 0.42361 |  | 247 | 148 | 36 | Albion UA | 4.16kV | UA06 | K597 @ 1446 Walkley was isolated to reconfigure primary cables | Ottawa | Scheduled Outage | Construction
19358 | 2011 | 10 | 12 | 0.38889 |  | 260 | 260 | 60 | Albion UA | 4.16kV | UA06 | Transformer K590, K591 & K592 on Cedarwood & Baycrest were isolated to reconfigure primary cables. | Ottawa | Scheduled Outage | Construction
11729 | 2007 | 11 | 16 | 0.6125 |  | 261 | 550 | 330 | ALBION | 4.16kV | UA06 | UA06 breaker tripped due to defective cable between V121 and V123 on Baycrest. Cable section isolated and customers restored in sections. | Ottawa | Defective Equipment
19849 | 2012 | 1 | 18 | 0.017361 |  | 5 | 0 | 6 | Abion | 27.6/16kV | UA07 | 4kv transformer X27419 at rear of 1220 St. Paul was opened to allow crew to untangle secondary. | Ottawa | Adverse Weather | Wind
19880 | 2012 | 1 | 23 | 0.94792 |  | 74 | 10 | 8 | Albion UA | 4.16kV | UA07 | Replaced defective cut out at Tx X27285, 1937 Banff ave. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4806 | 2004 | 2 | 19 | 0.61458 |  | 20 | 3 | 9 | Albion |  | UA07 | Transformer K1199 at 1979 Jasper ave was opened to replace defective underground secondary service. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17717 | 2011 | 3 | 15 | 0.57292 |  | 45 | 6 | 8 | Albion | 4.16kV | UA07 | Trans at 1335 Kitchener Ave was isolated in order to make repairs to Sec Service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4927 | 2004 | 3 | 23 | 0.49792 |  | 58 | 14 | 15 | Albion | 4.16kV | UA07 | Replaced O/H transformer #3719 at 1227 Kitchener due to an oil leak. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14590 | 2009 | 6 | 21 | 0.93472 |  | 47 | 3 | 4 | Albion | 4.16kV | UA07 | a racoon made contact with transformer X27415 @ the rear of 1242 Foxbar causing the fuse to blow. | Ottawa | Foreign Interference | Animal
20831 | 2012 | 6 | 22 | 0.48264 |  | 65 | 3 | 3 | Albion | 4.16kV | UA07 | Transformer #X27442 located at 1215 St. Paul Ave opened up due to aluminum balloon contact | Ottawa | Foreign Interference | Foreign Object
16482 | 2010 | 7 | 17 | 0.57847 |  | 277 | 55 | 14 | Albion | 4.16kV | UA07 | K1198 opened due to squirel contact on Over head Switche. K1199 fuse was opened to allow crews to make repairs to dammaged Over head switche at 1362 Notting Hill. Customer on Jasper St and Paardeburg Ave were affected. | Ottawa | Foreign Interference | Animal
3906 | 2003 | 8 | 14 | 0.37083 |  | 26 | 3 | 6 | Albion | 4.16kV | UA07 | Transformer isolated to make repairs to customer service. | Ottawa | Defective Equipment
13188 | 2008 | 9 | 3 | 0.75347 |  | 15 | 0 | 2 | Albion | 4.16kV | UA07 | Isolated transformer X27445 at 1915 Bank St to replace hot line clamp | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
19103 | 2011 | 9 | 6 | 0.57639 |  | 24 | 1 | 3 | Albion | 4.16kV | UA07 | Transformer #X27442 located at 1214 Foxbar opened by crew due to tree contact, brought down secondary service and stand pipe and knob pulled away, crew disconnected service. | Ottawa | Tree Contacts | Tree Fallen
13272 | 2008 | 9 | 21 | 0.64583 |  | 10 | 1 | 4 | Albion | 4.16kV | UA07 | Overhead transformer at 1242 Fozbar Ave in Ottawa isolated to remove live cat from top of tx. | Ottawa | Foreign Interference | Animal
19378 | 2011 | 10 | 15 | 0.44444 |  | 40 | 2 | 3 | Albion | 4.16kV | UA07 | Trans X27442 at 1215 ST. PAUL AVENUE, OTT was isolated in order to install new sec service conductor | Gloucester | Scheduled Outage | Repair
13622 | 2008 | 11 | 17 | 0.038194 |  | 20 | 1 | 3 | Albion | 4.16kV | UA07 | Fire dept. reported there was a flashing transformer X27442 at 1215 St. Paul. Crews responeded, isolated the transformer and replaced a deffective live line clamp. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9768 | 2006 | 12 | 1 | 0.64375 |  | 50 | 83 | 100 | Albion | 4.16kV | UA07 | UA07 circuit opened via scada to remove tree from overhead. | Ottawa | Adverse Weather | Ice Storm
13704 | 2008 | 12 | 5 | 0.75 |  | 15 | 0 | 2 | Albion | 4.16kV | UA07 | Transformer #X27445 located at 1915 Bank St isolated to replace a burnt piece of wire between the U/G pyro & the buss wire & changed the neutral connection | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11986 | 2008 | 1 | 29 | 0.43056 |  | 40 | 2 | 3 | Albion Sub | 4.16kV | UA11 | At 10:20am, transformer TP3499 at 1512 Walkley, was isolated to allow crews to re-terminated red phase cable in to transformer, 3 customers affected for 40 min. ID#11986. | Ottawa | Scheduled Outage | Construction
13968 | 2009 | 2 | 12 | 0.34583 |  | 47 | 1 | 1 | Albion | 4.16kV | UA11 | P14 feeding 1610 and 1620 Walkley was isolated to repair damaged fused cutout | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17754 | 2011 | 3 | 22 | 0.38542 |  | 60 | 7 | 7 | Albion | 4.16kV | UA11 | Transformer #X27277 located at 1341 Kitchener opened by crew to put a new service up the pole | Ottawa | Scheduled Outage | Construction
6333 | 2005 | 3 | 28 | 0.64792 |  | 701 | 285 | 163 | UA | 4.16kV | UA11 | UA11 blue phase to V139 opened due to defective cable. Faulted cable section difficult to locate, entire circuit tripped twice during sectionalizing attempts. At 20:00 all customers were back except 2861 Baycrest, V139, only 2 phases feeding. On call crew still found cables to & from V139 testing faulted. Cable from K581 to V139 tried & held restoring V139. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3577 | 2003 | 6 | 18 | 0.38194 |  | 360 | 90 | 15 | Albion | 4.16kV | UA11 | Defective K588 replaced with new M588. | Ottawa | Scheduled Outage | Repair
20796 | 2012 | 6 | 18 | 0.67917 |  | 187 | 56 | 18 | Albion | 4.16kV | UA11 | UA11 White phase switch at Albion and Kitchener was found open and broken. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3721 | 2003 | 7 | 12 | 0.25347 |  | 145 | 505 | 209 | UA | 4.16kV | UA11 | the lead to K384 dip switch @ pole 15 from the blue phase made contact with the UA11 white phase on a lower cross arm. This tripped the feeder breaker & slightly damaged the O/H conductor. There is a stand-off pin on the drop lead but the lead was still able to contact the white phase. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3724 | 2003 | 7 | 12 | 0.53333 |  | 22 | 2 | 6 | UA | 4.16kV | UA11 | During switching to isolate B phase dip to K384, a defective lightning arrestor was found at K391. 6 customers at 2925 to 2935 Fairlea were notified & K391 was isolated & the arrestor replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10900 | 2007 | 7 | 18 | 0.375 |  | 20 | 7 | 20 | Walkley | 4.16kV | UA11 | K589 @ the rear of 1159 Walkley was isolated to repair secondary connections | Ottawa | Scheduled Outage | Repair
10904 | 2007 | 7 | 18 | 0.54167 |  | 62 | 21 | 20 | Albion | 4.16kV | UA11 | Isolated K587 @ 1559 Walkley to repair secondary connection. | Ottawa | Scheduled Outage | Repair
16694 | 2010 | 8 | 8 | 0.63542 |  | 150 | 122 | 63 | Albion | 4.16kV | UA11 | UA11 blue phase cable on Baycrest faulted between K580 and K579, restored in stages while fault finding | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16777 | 2010 | 8 | 19 | 0.53056 |  | 54 | 16 | 18 | Albion | 4.16kV | UA11 | K579 at 1556 Heron Rd isolated to allow new terminations to completed for new cable | Ottawa | Scheduled Outage | Repair
19149 | 2011 | 9 | 12 | 0.68819 |  | 304 | 2819 | 580 | Albion Sub | 4.16kV | UA11 | Lighning storm caused UA11 circuit to fall down. 580 customers were affected. Albion ID# 19149 | Ottawa | Adverse Weather
12111 | 2008 | 3 | 7 | 0.52431 |  | 91 | 15 | 10 | ALBION | 13.2kV | UACB2 | TRANSFORMER #KT0024 AT 22 FOXHUNT ISOLATED TO ALLOW FOR CABLE REPAIR | Ottawa | Scheduled Outage | Repair
15496 | 2009 | 12 | 11 | 0.43403 |  | 20 | 4 | 13 | Albion | 13.2kV | UACB2 | Transformer #KT44 located at 59 Vanhurst isolated for electrician to make repairs | Ottawa | Scheduled Outage | Construction
7998 | 2006 | 3 | 9 | 0.66667 |  | 80 | 27 | 20 | Beechwood | 4.16kV | UB02 | UB02 cct A/R due to a squirrel making contact with primary line at dip to K1182 supplying 118 to 176 Dunbarton. Fuse & arrestor replaced. | Ottawa | Foreign Interference | Animal
11915 | 2008 | 1 | 9 | 0.53819 |  | 332 | 56 | 234 | Beechwood | 4.16kV | UB03 | UB03 circuit opened due to overhead circuit conductors slapping together. UB03 circuit breaker operated after 13 minutes to see if it would hold. UB03 breaker holding and 1 customer still reported out. Darcy Provost confirmed customer at V687 CB opened. Customer told to contact High Voltage contractor to investigate vault before CB can be closed. Contractor said vault was ok, and closed in breaker. All load restored. Darcy Provost did mention that water is starting to enter vault, will need to be monitored. | Ottawa | Adverse Weather | Wind
12161 | 2008 | 3 | 20 | 0.3125 |  | 160 | 27 | 10 | BEECHWOOD | 4.16kV | UB03 | Transformer at Montreal Rd & St. Laurent Blvd isolated to change leaking transformer | Ottawa | Scheduled Outage | Repair
6334 | 2005 | 3 | 29 | 0.40278 |  | 140 | 28 | 12 | Beechwood | 4.16kV | UB03 | Isolated tranformer # 5479 at 421 Appltree to relocate service wires | Ottawa | Scheduled Outage | Preventive Maintenance
12228 | 2008 | 4 | 3 | 0.36111 |  | 60 | 2 | 2 | Beechwood | 4.16kV | UB03 | Transformer #OTT4546 located at 550 Montreal Rd isolated to change 600 V service | Ottawa | Scheduled Outage | Preventive Maintenance
10240 | 2007 | 4 | 11 | 0.44931 |  | 78 | 1 | 1 | Beechwood | 4.16kV | UB03 | Transformer #P00098 located at 551 Montreal Rd isolated due to broken switch feeding the U/G | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20379 | 2012 | 4 | 24 | 0.47222 |  | 70 | 8 | 7 | Beechwood | 4.16kV | UB03 | Isolated transformer X38993 at 1071 Riviera Dr for tree removal | Ottawa | Scheduled Outage | Preventive Maintenance
18010 | 2011 | 4 | 28 | 0.5625 |  | 80 | 736 | 552 | Beechwood | 4.16kV | UB03 | UB03 circuit breaker auto-reclosed twice and locked out the second time during wind/lightning storm. Breaker was closed VIA scada and held. | Ottawa | Adverse Weather | Wind
6517 | 2005 | 5 | 6 | 0.39583 |  | 170 | 40 | 14 | Beechwood | 4.16kV | UB03 | Transformer #OTT158 at Rear of 396 Apple Tree Lane isolated to change a defective transformer | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8403 | 2006 | 6 | 1 | 0.52431 |  | 115 | 15 | 8 | Beechwood | 4.16kV | UB03 | Isolated transformer # OTT4381 at 426 Meadow Park to re-sag secondary service and trim tree. | Ottawa | Tree Contacts | Inadequate Trimming
14913 | 2009 | 8 | 4 | 0.86528 |  | 101 | 970 | 576 | Beechwood | 4.16kV | UB03 | At 8:46pm UB03 circuit auto reclosed and auto lockouted. 24-7 crews arrived on site and patrolled main trunk overhead and informed system all clear. System tried UB03 breaker with recloser in service and all power restored at 10:27pm. Beechwood (UB03). ID#14913. | Ottawa | Adverse Weather | Wind
5631 | 2004 | 8 | 10 | 0.17778 |  | 343 | 86 | 15 | Beechwood | 4.16kV | UB03 | fuse to transformer # OTT1210 at 424 Carpenter Way blew for no apparent reason | Ottawa | Unknown/Other | No Apparent Cause
3983 | 2003 | 9 | 2 | 0.5875 |  | 6 | 1 | 12 | Beechwood | 4.16kV | UB03 | Transformer OTT0912 on Brittany was opened to replace a damaged lightening arrester. | Ottawa | Adverse Weather | Lightning
7474 | 2005 | 10 | 18 | 0.43056 |  | 14 | 6 | 26 | Beechwood | 4.16kV | UB03 | Transformer OTT 5480 at 410 Bangs St was isolated to trim tree | Ottawa | Scheduled Outage | Preventive Maintenance
4329 | 2003 | 10 | 22 | 0.54861 |  | 80 | 8 | 6 | Beechwood | 4.16kV | UB03 | Transformer at the rear of 407 Meadow Dr was isolated to repair secondary service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17242 | 2010 | 11 | 8 | 0.53472 |  | 78 | 30 | 23 | BEECHWOOD | 4.16kV | UB03 | Transformer X24950 at 261 Britanny Dr. Isolated to allow for service repairs | Ottawa | Scheduled Outage | Repair
9662 | 2006 | 11 | 15 | 0.37569 |  | 169 | 45 | 16 | beechwood | 4.16kV | UB03 | Trf. # 4890 located @ 1028 meadow park isolated to change PCB trf. | Ottawa | Scheduled Outage | Preventive Maintenance
19589 | 2011 | 11 | 16 | 0.35417 |  | 120 | 30 | 15 | Beechwood | 4.16kV | UB03 | Transformer X23400 at 499 Brittany Dr isolated by Denis Gray of Black and Mac for pole replacement | Ottawa | Scheduled Outage | Construction
9702 | 2006 | 11 | 22 | 0.38194 |  | 175 | 18 | 6 | Beechwood | 4.16kV | UB03 | Transformer #OTT4380 located at 417 Meadow Park Pl isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
19648 | 2011 | 11 | 29 | 0.35417 |  | 315 | 467 | 89 | Beechwood | 4.16kV | UB03 | UB03 O/H section between Temp 13 and Temp 14 on Brittany Dr was isolated to allow crew to install new poles. 89 customers were affected for | Ottawa | Scheduled Outage | Construction
19651 | 2011 | 11 | 30 | 0.52917 |  | 233 | 132 | 34 | Beechwood | 4.16kV | UB03 | Switch S25870 @ 343 Brittany was open to allow crew to perform pole replacement. Beechwood SB03 | Ottawa | Scheduled Outage | Construction
13865 | 2009 | 1 | 14 | 0.076389 |  | 305 | 86 | 17 | Beechwood | 4.16kV | UB04 | Transformer X23619 at 233 Barclay failed. On call crew called in to replace transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6141 | 2005 | 1 | 17 | 0.46528 |  | 30 | 3 | 6 | beachwood | 4.16kV | UB04 | Trans OTT2328 at 16 Arundel to repair service | Ottawa | Scheduled Outage | Preventive Maintenance
6166 | 2005 | 2 | 2 | 0.47917 |  | 80 | 16 | 12 | Beechwood | 4.16kV | UB04 | Power interruption to transformer #OTT3480 at the rear of 12 Jeffrey Ave to replace pole | Ottawa | Scheduled Outage | Construction
6197 | 2005 | 2 | 9 | 0.4375 |  | 120 | 24 | 12 | Beechwood |  | UB04 | Open transformer OTT3480 at the rear of 12 Jeffrey Ave for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
14056 | 2009 | 3 | 15 | 0.23125 |  | 401 | 100 | 15 | Beechwood | 4.16kV | UB04 | tree came down on primary at rear of 164 St. Laurent blvd. Crew isolated secondary run for tree contractor to remove tree. | Ottawa | Tree Contacts | Tree Fallen
6507 | 2005 | 5 | 4 | 0.34722 |  | 60 | 8 | 8 | Beechwood | 4.16kV | UB04 | Replaced broken switch to transformer OTT2328 at 16 Killbury Cres | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6523 | 2005 | 5 | 9 | 0.375 |  | 395 | 151 | 23 | Beechwood | 4.16kV | UB04 | 3 Transformers, #OTT239, OTT4444, & OTT6019 isolated on Sandridge, Merriman & Arundel to re-locate transformers to new poles. | Ottawa | Scheduled Outage | Construction
6541 | 2005 | 5 | 11 | 0.375 |  | 228 | 15 | 4 | Beechwood | 4.16kV | UB04 | Isolated Transformer # 4444 at 25 Arundel to relocate same to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
5345 | 2004 | 6 | 21 | 0.44028 |  | 90 | 26 | 17 | UB | 4.16kV | UB04 | Tx OTT6041 at 304 St Laurent was opened to relocate the transformer. | Ottawa | Scheduled Outage | Preventive Maintenance
16351 | 2010 | 6 | 28 | 0.7875 |  | 67 | 291 | 261 | Beechwood | 4.16kV | UB04 | A lightening strike at Hemlock and St. Laurent apparently caused UB00, UB04 and UB06 breakers to Auto reclose and then trip again. | Ottawa | Lightning | Direct Strike
5423 | 2004 | 7 | 1 | 0.62292 |  | 558 | 1632 | 234 | UB | 4.16kV | UB04 | Cct opened during storm. A single phase conductor was cut clear & had to be repaired on Bedford ave. | Ottawa | Adverse Weather | Lightning
5483 | 2004 | 7 | 12 | 0.53681 |  | 47 | 1 | 1 | Beechwood | 4.16kV | UB04 | Transformer OTT6045 at 400 St. Laurent wa taken out of service to relocate the service. Our Lady of Mount carmel church was only customer affected. | Ottawa | Unknown/Other
18843 | 2011 | 7 | 28 | 0.35417 |  | 349 | 35 | 6 | BEECHWOOD | 4.16kV | UB04 | Transformer X23611 isolated to allow for removal of tree limb | Ottawa | Tree Contacts | Tree Limb Fallen
5787 | 2004 | 9 | 9 | 0.35556 |  | 62 | 242 | 234 | Beechwood | 4.16kV | UB04 | UB04 breaker locked out when a branch brought all 3 phases together at St. Laurent and Sandridge, | Ottawa | Tree Contacts | Tree Limb Fallen
4099 | 2003 | 9 | 19 | 0.70486 |  | 30 | 2 | 4 | Beechwood | 4.16kV | UB04 | Transformer OTT#3578, at 18 Farnham Street in Ottawa, had to be isolated to allow for the repair of secondary wired downed by a fallen tree. Wires were repaired and power was restored. | Ottawa | Tree Contacts | Tree Fallen
9329 | 2006 | 9 | 27 | 0.70833 |  | 45 | 10 | 13 | Beechwood | 4.16kV | UB04 | Transformer #OTT3480 located behind 210 Barclay isolated to clear trees off the open buss, PC10A#2699 | Ottawa | Tree Contacts | Inadequate Trimming
9594 | 2006 | 11 | 3 | 0.52083 |  | 97 | 23 | 14 | Beechwood | 4.16kV | UB04 | Isolated Transformer at 837 Eastbourne to change PCB Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
9714 | 2006 | 11 | 23 | 0.36806 |  | 198 | 26 | 8 | Beechwood | 4.16kV | UB04 | Isolated and replaced the transformer OTT 2328 at 13 Farnham St (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9722 | 2006 | 11 | 24 | 0.36111 |  | 150 | 28 | 11 | Beechwood | 4.16kV | UB04 | Isolated and replaced transformer OTT2329 at 27 Farnham Cres (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
17419 | 2010 | 12 | 14 | 0.46181 |  | 40 | 8 | 12 | BEECHWOOD | 4.16kV | UB04 | Transformer X23411 at 32 Sandridge Rd isolated to allow for repairs to transformer | Ottawa | Scheduled Outage | Repair
3522 | 2003 | 6 | 5 | 0.42361 |  | 440 | 81 | 11 | Beechwood | 4.16kV | UB05 | V803 @ 65 Whitrmarl was shutdown to change secondary cable and clean vault. | Ottawa | Scheduled Outage | Construction
5957 | 2004 | 12 | 1 | 0.50208 |  | 47 | 1 | 1 | UB | 4.16kV | UB05 | V803 at 65 Whitemarl was isolated for emergency repairs to a burning hot line clamp | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6270 | 2005 | 3 | 12 | 0.020833 |  | 248 | 265 | 64 | Beechwood | 4.16kV | UB06 | K1165 at 31 Sheba was interrupted to disconnect secondary cables for DanCan to replace 800 amp main. Verbal Esa approval rec'd from J.Wilkenson. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6304 | 2005 | 3 | 19 | 0.77569 |  | 99 | 16 | 10 | UB | 4.16kV | UB06 | Fused secondary connections at 112 Camelia caused the Tx at 132 Camelia to open. Connections repaired & Tx restored. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6444 | 2005 | 4 | 22 | 0.375 |  | 420 | 70 | 10 | Beechwood | 4.16kV | UB06 | Jeremy from Dundas isolated Transformer #OTT1099 from 165-177 Camelia to re-wire (modify) secondary service | Ottawa | Scheduled Outage | Repair
12414 | 2008 | 5 | 7 | 0.45694 |  | 122 | 18 | 9 | Vaughan | 4.16kV | UB06 | Transformer #X4737 located at 172 Laval isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
5147 | 2004 | 5 | 14 | 0.43333 |  | 53 | 57 | 64 | UB | 4.16kV | UB06 | K1165 on Sheba Pvt isolated for change - out, casing leaking. | Ottawa | Scheduled Outage | Repair
10451 | 2007 | 5 | 23 | 0.74792 |  | 176 | 769 | 595 | Beechwood | 4.16kV | UB06 | Overhead conductor of the UB06 broke and conductor fell to the ground. The UB06 breaker did not open causing the S-227 to open at Beechwood to intterupt the UBT2 transformer and circuits UB05, UB06 & UB07. | Ottawa | Defective Equipment
3626 | 2003 | 6 | 28 | 0.96042 |  | 27 | 8 | 17 | Beechwood | 4.16kV | UB06 | Transformer at 304 St Laurent Blvd had to be isolated to replace the fused dip. Fused sw had been arcing. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16352 | 2010 | 6 | 28 | 0.7875 |  | 69 | 618 | 537 | Beechwood | 4.16kV | UB06 | A lightening strike at Hemlock and St. Laurent apparently caused UB00, UB04 and UB06 breakers to Auto reclose and then trip again. | Ottawa | Lightning | Direct Strike
14834 | 2009 | 7 | 24 | 0.69375 |  | 741 | 259 | 21 | Beechwood | 4.16kV | UB06 | At transfomer X17542 at 274 St. Laurent Blvd. was isolated to allow crew to replace defective transformer. | Nepean | Defective Equipment
5602 | 2004 | 8 | 2 | 0.74306 |  | 9 | 33 | 220 | UB | 4.16kV | UB06 | Customer report of lightning strike at 243 St Laurent, Hold - offs cleared & circuit closed via scada. | Ottawa | Adverse Weather | Lightning
14958 | 2009 | 8 | 17 | 0.78958 |  | 333 | 44 | 8 | Beechwood | 4.16kV | UB06 | Single phase primary down at 1045 Blasdell. Repairs made and power restored UB06 cct. | Ottawa | Defective Equipment
15040 | 2009 | 8 | 31 | 0.44444 |  | 200 | 30 | 9 | Beechwood | 4.16kV | UB06 | Transformer #X23405 located at 184 Wingham Pl isolated to change open wire service | Ottawa | Scheduled Outage | Construction
15720 | 2010 | 2 | 11 | 0.63056 |  | 72 | 10 | 8 | BEECHWOOD | 4.16kV | UB07 | Transformer X23661 located at rear of 717 Hemlock Rd isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
14359 | 2009 | 5 | 14 | 0.62083 |  | 56 | 203 | 217 | Beechwood | 4.16kV | UB07 | UB07 breaker auto tripped, circuit patrolled in area were customer reported hearing loud bang, no problem found. Breaker closed via SCADA to restore circuit. | Ottawa | Unknown/Other | No Apparent Cause
20614 | 2012 | 5 | 26 | 0.78819 |  | 1188 | 2879 | 362 | Beechwood | 4.16kV | UB07 | Tree limb on 2 phases of UB07 in rear of 80 Blenheim Dr. UB07 complete overhead isolated to make repairs. | Ottawa | Adverse Weather | Wind
6647 | 2005 | 6 | 2 | 0.52083 |  | 223 | 15 | 4 | Beechwood | 4.16kV | UB07 | Relocate transformer OTT4011 at 729 Lonsdale to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
18343 | 2011 | 6 | 8 | 0.70417 |  | 260 | 1564 | 361 | Beechwood | 4.16kV | UB07 | circuit opened due to blown station station pothead, crew transfered circuit to UB00. | Ottawa | Adverse Weather
14561 | 2009 | 6 | 18 | 0.38889 |  | 199 | 20 | 6 | Beechwood | 4.16kV | UB07 | UB07 R phase backyard runoff between Placel & Lakeway isolated to trim trees. | Ottawa | Scheduled Outage | Preventive Maintenance
8566 | 2006 | 6 | 21 | 0.52431 |  | 60 | 1 | 1 | Beechwood | 4.16kV | UB07 | Transformer #OTT4954 located at rear of 40 Lakeway isolated due to trees on wires | Ottawa | Tree Contacts | Inadequate Trimming
18479 | 2011 | 6 | 24 | 0.88472 |  | 511 | 51 | 6 | Beechwood | 4.16kV | UB07 | Transformer X38351 defective. Transformer X38550 opened to allow customers from X38351 to be connected. Pole at X38351 needs to be re-built. | Ottawa | Defective Equipment
18480 | 2011 | 6 | 24 | 0.88472 |  | 561 | 62 | 12 | Beechwood | 4.16kV | UB07 | Transformer X38351 defective, Transformer at X38550 opened to allow customers from X38351 to be connected on Hemlock. | Ottawa | Defective Equipment
12821 | 2008 | 7 | 11 | 0.92222 |  | 383 | 311 | 206 | Beechwood | 4.16kV | UB07 | At 3:50pm customers in the area of Dunvegan & Sandridge Road, a tree limb had taken down a phase on the UB07 circuit. On call crews called in to make repairs, all power restored at 10:13pm. Beechwood (UB07). ID#12821. | Ottawa | Tree Contacts | Tree Limb Fallen
6964 | 2005 | 7 | 16 | 0.58333 |  | 30 | 103 | 206 | Beechwood | 4.16kV | UB07 | UB07 white phase overhead in the backyard of 737 Lonsdale came down into the trees and required isolation for repair. | Ottawa | Unknown/Other | No Apparent Cause
8834 | 2006 | 7 | 25 | 0.4375 |  | 215 | 47 | 13 | Beechwood | 4.16kV | UB07 | Isoalted and replaced transformer 23653 at 731 Eastbourne Ave | Ottawa | Scheduled Outage | Construction
11069 | 2007 | 8 | 15 | 0.77431 |  | 280 | 107 | 206 | Beechwood | 4.16kV | UB07 | Beechwood UB07 circuit auto/reclose/auto trip. Crew found transformer cutout blown and tree branches burnt at 50 Dunvegan. Tree limbs trimed and transformer refused and closed. | Ottawa | Tree Contacts | Inadequate Trimming
11226 | 2007 | 9 | 1 | 0.50278 |  | 151 | 33 | 13 | Beechwood | 4.16kV | UB07 | Transformer #OTT2069 located at 50 Dunvegan Rd isolated due to tree contact | Ottawa | Tree Contacts | Inadequate Trimming
9203 | 2006 | 9 | 12 | 0.38194 |  | 170 | 34 | 12 | Beechwood | 4.16kV | UB07 | At 09:10 trans OTT422 at 75 Birch Ave was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
13230 | 2008 | 9 | 15 | 0.036806 |  | 91 | 312 | 206 | Beechwood | 4.16kV | UB07 | In the Hemlock/Dunvegun area the O/H was patrolled and found nothing, a little storm went through the area. | Ottawa | Adverse Weather | Wind
7335 | 2005 | 9 | 16 | 0.5125 |  | 117 | 12 | 6 | UB | 4.16kV | UB07 | Transformer #OTT2082 located at 767 Eastbourne isolated due to tree interference. | Ottawa | Tree Contacts | Inadequate Trimming
19213 | 2011 | 9 | 20 | 0.54167 |  | 50 | 5 | 6 | Beechwood | 4.16kV | UB07 | Isolated transformer X23652 at 57 Kilbarry Cres for a sevice up-grade | Ottawa | Scheduled Outage | Emergency Services Request
19329 | 2011 | 10 | 5 | 0.375 |  | 240 | 84 | 21 | Beechwood | 4.16kV | UB07 | At 09:00 red phase run off was isolated to allow tree and crane contractors to remove trees. 21 customers were affected for 240 minutes. Beechwood (UB07) ID#19329 | Ottawa | Scheduled Outage | Preventive Maintenance
7431 | 2005 | 10 | 6 | 0.55208 |  | 42 | 7 | 10 | Beechwood | 4.16kV | UB07 | Isolated Transformer at 111 Blenheim to replace service wires | Ottawa | Scheduled Outage | Preventive Maintenance
11590 | 2007 | 10 | 25 | 0.39236 |  | 146 | 29 | 12 | Beechwood | 4.16kV | UB07 | 12 customers on Lakeway Dr isolated to provide claerance for tree removal near overhead line. | Ottawa | Scheduled Outage | Preventive Maintenance
15380 | 2009 | 11 | 11 | 0.44792 |  | 25 | 2 | 5 | Beechwood | 4.16kV | UB07 | Transformer #X23673 located at 95 Lyttleton Gdns isolated for clearances for a reconnect | Ottawa | Scheduled Outage | Construction
13610 | 2008 | 11 | 14 | 0.58333 |  | 30 | 3 | 6 | BEECHWOOD | 4.16kV | UB07 | Isolated transformer X23674 at 270 Sandridge Rd for service up-grade | Ottawa | Scheduled Outage | Repair
7639 | 2005 | 11 | 21 | 0.36458 |  | 30 | 2 | 4 | Beechwood | 4.16kV | UB07 | Trans OTT424 @ 26 Dunvegan isolated to replace secondary service | Ottawa | Scheduled Outage | Preventive Maintenance
13658 | 2008 | 11 | 24 | 0.4375 |  | 28 | 5 | 10 | Beachwood | 4.16kV | UB07 | 4KV transformer at 270 Sandridge was open to allow crews to remove coverup from overhead. | Ottawa | Scheduled Outage | Preventive Maintenance
17420 | 2010 | 12 | 14 | 0.52014 |  | 43 | 7 | 10 | BEECHWOOD | 4.16kV | UB07 | Transformer X17547 at 195 Lakeway Drive Rockcliffe isolated to allow for transformer repairs | Ottawa | Scheduled Outage
5360 | 2004 | 6 | 23 | 0.40625 |  | 125 | 23 | 11 | Beechwood | 4.16kV | UB11 | O/H transformer at 906 Glasgow interrupted to change pole. | Ottawa | Scheduled Outage | Repair
5573 | 2004 | 7 | 27 | 0.41667 |  | 164 | 30 | 11 | UB | 4.16kV | UB12 | Tx 65a4c-0102 @ 208 Granville st was opened to transfer services to new pole. | Ottawa | Scheduled Outage | Construction
3664 | 2003 | 7 | 3 | 0.54306 |  | 4 | 33 | 500 | Beechwood | 13.2kV | UBT1 | Scada indicated S-439 @ UB opened feeding UBT1 - load loss equals 1800 KW. Power restored to UBT1 by closing S-439 @ UB. No fault found, no cause for trip apparent. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3665 | 2003 | 7 | 3 | 0.54653 |  | 15 | 125 | 500 | Beechwood | 13.2kV | UBT1 | 13:07- S-439 @ UB tripped again after holding for about 45 seconds causing load loss of 1800 KW. Stations crew on site suspect a control wiring problem. At 13:12 S-439 @ UB closed, but trips again instantly. Plans to up-pick load with UBT2 have started. Power restored through UBT2 at 13:22. | Ottawa | Human Element | Incorrect Installation
3666 | 2003 | 7 | 3 | 0.54306 |  | 4 | 33 | 500 | UB | 4.16kV | UBT1 | S-439 feeding UBT1 tripped open for no apparent reason while a stations crew was working on SCADA & RTU indications at UB. The switch opened again (see report #3665) and faulty control wiring is suspected by Stations crew. This has been an ongoing problem with this switchgear and actual problem with the wiring not known. | Ottawa | Human Element | Equipment Failure - Cause Unknown
8931 | 2006 | 8 | 7 | 0.0875 |  | 340 | 810 | 479 | Beechwood | 4.16kV | UBT1 | Blown LA, two phases of UB04 primary cunductor burned, one burned down the other badly flashed, caused a surge past the UBT1 transformer causing an interuption on the UBT1 transformer. Isolation required of UB04 to affect repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7551 | 2005 | 11 | 2 | 0.090278 |  | 168 | 2800 | 1000 | Beechwood | 4.16kV | UBT1 & UBT2 | All circuits fed from Beechwood substation were isolated for maintenance on bus disconnects. | Ottawa | Scheduled Outage | Preventive Maintenance
5422 | 2004 | 7 | 1 | 0.62292 |  | 398 | 3046 | 571 | UB | 4.16kV | UBT2 | UBT2 supply opened during storm, UB06 reclosed multiple times. Transformer was checked & placed on pot before restoring UB05, 07. UB06 was restored after patrol. | Ottawa | Adverse Weather | Lightning
14023 | 2009 | 3 | 5 | 0.45486 |  | 68 | 12 | 11 | CLYDE | 4.16kV | UC01 | Transformer X32083 isolated to allow for new service at 255 Currell Ave. | Ottawa | Scheduled Outage | Construction
17732 | 2011 | 3 | 18 | 0.38194 |  | 71 | 12 | 10 | Clyde | 4.16kV | UC01 | Vault V242 at 1570 Carling Ave. Isolated to replace switches and leeds | Ottawa | Scheduled Outage | Repair
15850 | 2010 | 3 | 25 | 0.96181 |  | 7 | 1 | 5 | Clyde | 4.16kV | UC01 | Transformer #OTT1436 located at 703 Churchill isolated by crew to cut triplex at stand pipe for Fire Dept | Ottawa | Adverse Environment | Fire
8120 | 2006 | 4 | 8 | 0.61319 |  | 60 | 3 | 3 | Clyde | 4.16kV | UC01 | At 14:43 24/7 replaced defective cutout at OTT1156 at 1619 Carling Ave | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8157 | 2006 | 4 | 18 | 0.375 |  | 135 | 18 | 8 | Clyde | 4.16kV | UC01 | At 09:00 trans at 709 Churchill ave Ott was isolated for upgrade to plant | Ottawa | Scheduled Outage | Preventive Maintenance
18070 | 2011 | 4 | 30 | 0.71597 |  | 3 | 15 | 299 | CLYDE | 4.16kV | UC01 | UC01 was interrupted to isolate UC02 and UC03 for emergency repairs on UC00. UCT1 is isolated. | Ottawa | Defective Equipment
18073 | 2011 | 4 | 30 | 0.85556 |  | 1 | 5 | 299 | Clyde | 4.16kV | UC01 | UC01 was interrupted to restore circuits UC02 and UC03 to normal. UCT1 isolated. | Ottawa | Defective Equipment
16224 | 2010 | 6 | 8 | 0.375 |  | 30 | 4 | 9 | Clyde | 4.16kV | UC01 | Transformer X32085 at 296 Currell was disconnected to allow an electrician to upgrade a customers panel. | Ottawa | Scheduled Outage | Repair
14508 | 2009 | 6 | 10 | 0.43056 |  | 100 | 23 | 14 | Clyde | 4.16kV | UC01 | At 12:00 trans at 365 Tillbury was isolated in order for a pole change | Ottawa | Scheduled Outage | Repair
16285 | 2010 | 6 | 18 | 0.45833 |  | 40 | 11 | 17 | Clyde | 4.16kV | UC01 | Isolated and relocated transformer X30252 at 682 Churchill Ave to new pole | Ottawa | Scheduled Outage | Construction
11543 | 2007 | 10 | 17 | 0.53819 |  | 147 | 32 | 13 | Clyde | 4.16kV | UC01 | At 12:55 trans at 300 Dovercourt was isolated for PCB trans change | Ottawa | Scheduled Outage | Preventive Maintenance
11545 | 2007 | 10 | 17 | 0.53472 |  | 105 | 32 | 18 | Clyde | 4.16kV | UC01 | At 12:50 trans at 274 Westhill was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15294 | 2009 | 10 | 22 | 0.40625 |  | 30 | 6 | 11 | Clyde | 4.16kV | UC01 | Isolated transformer X30272 at 726 Edison Ave to re-arrange hydro plant | Ottawa | Scheduled Outage | Repair
15307 | 2009 | 10 | 26 | 0.45347 |  | 11 | 2 | 11 | CLYDE | 4.16kV | UC01 | Transformer X30272 at 726 Edison Ave isolated to allow for rearanging of plant | Ottawa | Scheduled Outage | Construction
18028 | 2011 | 4 | 28 | 0.58611 |  | 426 | 4608 | 1161 | Clyde | 4.16kV | UC01, 02, 03 | UCK2Y2 CB tripped during wind/lightning storm which was carrying UC01, 02 and 03 load. Field crews reported that the UC00 line had fallen into the UC02 line. UC01 and 03 were restored and UC02 was restored after repairs were made. | Ottawa | Adverse Weather | Wind
20088 | 2012 | 3 | 1 | 0.90972 |  | 228 | 80 | 21 | Clyde | 4.16kV | UC02 | UC02 O/H circuit on Clyde road between Doobie and Carling was isolated to allow crew to repair a pole that broke off due to a fire. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20204 | 2012 | 3 | 22 | 0.70486 |  | 4 | 0 | 4 | Clyde | 4.16kV | UC02 | Transformer #X32005 located at 302 Westhill Ave opened by crew to replace bad connections. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18071 | 2011 | 4 | 30 | 0.71806 |  | 199 | 1201 | 362 | CLYDE | 4.16kV | UC02 | UC02 breaker was isolated for emergency repairs. | Ottawa | Defective Equipment
14283 | 2009 | 5 | 1 | 0.54167 |  | 92 | 9 | 6 | Clyde | 4.16kV | UC02 | Transformer #X31828 located at 656 Edison isolated due to re-arranging for new poles to be installed | Ottawa | Scheduled Outage | Preventive Maintenance
20442 | 2012 | 5 | 2 | 0.58333 |  | 15 | 2 | 7 | Clyde | 4.16kV | UC02 | Isolated transformer X37912 at 528 Highcroft Ave for a service upgrade | Ottawa | Scheduled Outage | Emergency Services Request
20448 | 2012 | 5 | 2 | 0.36181 |  | 19 | 2 | 7 | Clyde | 4.16kV | UC02 | Transformer #X37912 located at 519 Churchill Ave N opened by crew for a disc/rec for contractor | Ottawa | Scheduled Outage | Construction
20546 | 2012 | 5 | 21 | 0.034722 |  | 84 | 8 | 6 | Clyde | 4.16kV | UC02 | An electircal panel fire at 874 Clyde caused a 600V secondary service to burn off of the overhead. 4kV transformer X33753 at 856 Clyde Ave. was opened by crews to disconnect the affected service. | Ottawa | Adverse Environment | Fire
14470 | 2009 | 6 | 5 | 0.44444 |  | 83 | 18 | 13 | Clyde | 4.16kV | UC02 | Isolated transformer X30274 at 704 Edison Ave to transfer secondary services to new pole | Ottawa | Scheduled Outage | Construction
14491 | 2009 | 6 | 8 | 0.43194 |  | 23 | 6 | 16 | CLYDE | 4.16kV | UC02 | Transformer X30273 at 716 Edison was isolated to allow crew to install new pole. | Nepean | Scheduled Outage
14496 | 2009 | 6 | 8 | 0.54861 |  | 100 | 27 | 16 | Clyde | 4.16kV | UC02 | Transformer X30273 at 708 Edison was isolated to allow crew to replace pole. | Nepean | Scheduled Outage | Preventive Maintenance
12786 | 2008 | 7 | 3 | 0.54167 |  | 70 | 10 | 9 | Clyde | 4.16kV | UC02 | Transformer at 654 Churchhill isolated to replace broken insulator at tx switch. | Ottawa | Scheduled Outage | Repair
16386 | 2010 | 7 | 3 | 0.69444 |  | 230 | 12 | 6 | Clyde | 4.16kV | UC02 | Open wire bus crossing Churchill from X30250 at 556 Churchill had a downed leg, transformer opened to cut the bus clear. Oncall repaired secondary bus & ran new triplex. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14870 | 2009 | 7 | 29 | 0.37778 |  | 234 | 39 | 10 | CLYDE | 4.16kV | UC02 | Transformer X31828 at 656 Edison isolated to allow for pole changes | Ottawa | Scheduled Outage | Preventive Maintenance
18864 | 2011 | 7 | 31 | 0.30208 |  | 102 | 36 | 21 | Clyde | 4.16kV | UC02 | Transformer #X32024 located at 673 Churchill opened up due to bird contact. | Ottawa | Foreign Interference | Bird
7360 | 2005 | 9 | 21 | 0.61042 |  | 9 | 3 | 17 | Clyde | 4.16kV | UC02 | Transformer OTT2145 at 707 Edison Ave was isolated to install service | Ottawa | Scheduled Outage | Construction
11412 | 2007 | 9 | 28 | 0.54514 |  | 40 | 5 | 8 | Clyde | 4.16kV | UC02 | Isolated transformer OTT2047 at 324 Duncairn Ave to replace service | Ottawa | Scheduled Outage | Preventive Maintenance
11528 | 2007 | 10 | 16 | 0.36458 |  | 150 | 20 | 8 | Clyde | 4.16kV | UC02 | Transformer #OTT2141 located at 674 Edison isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
15308 | 2009 | 10 | 26 | 0.46181 |  | 12 | 2 | 11 | CLYDE | 4.16kV | UC02 | Transformer X30274 at 700 Edison isolated to alloe for rearranging of plant | Ottawa | Scheduled Outage | Construction
15309 | 2009 | 10 | 26 | 0.47014 |  | 16 | 3 | 11 | CLYDE | 4.16kV | UC02 | Transformer X31827 at 674 Edison Ave isolated to allow for rearranging of plant | Ottawa | Scheduled Outage
11630 | 2007 | 10 | 30 | 0.38542 |  | 140 | 12 | 5 | Clyde | 4.16kV | UC02 | Isolated and replaced transformer OTT2820 at 674 Cole Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
11631 | 2007 | 10 | 30 | 0.53125 |  | 82 | 11 | 8 | Clyde | 4.16kV | UC02 | Isolated and replaced transformer OTT1426 at 578 Churchill Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
11632 | 2007 | 10 | 30 | 0.49306 |  | 30 | 2 | 5 | Clyde | 4.16kV | UC02 | Isolated transformer OTT637 at 415 Avondale to repair service | Ottawa | Scheduled Outage | Emergency Services Request
11637 | 2007 | 10 | 31 | 0.375 |  | 150 | 38 | 15 | Clude | 4.16kV | UC02 | At 09:00 trans at 716 Cole was isolated for PCB trans replacement | Ottawa | Scheduled Outage
19505 | 2011 | 10 | 31 | 0.39583 |  | 65 | 4 | 4 | Clyde | 4.16kV | UC02 | Isolated transformer X32020 at 298 Westhill Ave for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
13863 | 2009 | 1 | 13 | 0.87917 |  | 116 | 10 | 5 | Clyde | 4.16kV | UC03 | Secondary conductors made contact causing fuse to blow at transformer X33671, 870 Campbell. Note: this transformer also supplies station service for Clyde sub. | Ottawa | Adverse Weather | Wind
14041 | 2009 | 3 | 11 | 0.78681 |  | 142 | 24 | 10 | Clyde | 4.16kV | UC03 | Replaced blown fuse in switch feeding transformer X34214 at 895 Rex Ave | Ottawa | Adverse Weather | Wind
17846 | 2011 | 4 | 7 | 0.35417 |  | 45 | 8 | 10 | CLYDE | 4.16kV | UC03 | transformer X32314, at 387 Greenwood was replaced | Ottawa | Scheduled Outage
15989 | 2010 | 4 | 24 | 0.95486 |  | 20 | 3 | 8 | Clyde | 4.16kV | UC03 | The overhead transformer at rear of 854 Broadview was isolated to replace defective triplex connections to 850 Broadview. 6 customers on Broadview & 2 on Denison were affected. | Ottawa | Defective Equipment
14246 | 2009 | 4 | 26 | 0.86042 |  | 214 | 1234 | 346 | Clyde | 4.16kV | UC03 | UC03 breaker was opened manually from SCADA due to a report of fire and tree on lines on Denison. Damaged section was isolated and power restored to all but section damaged by trees pending repairs by lines & forestry crews. | Ottawa | Adverse Weather
15997 | 2010 | 4 | 26 | 0.47222 |  | 14 | 2 | 8 | Clyde | 4.16kV | UC03 | Transformer #X33875 located at 854 Broadview opened by crew to disconnect services damaged by fire that happened on Saturday per ESA's request | Ottawa | Adverse Environment | Fire
18072 | 2011 | 4 | 30 | 0.71806 |  | 199 | 1658 | 500 | CLYDE | 4.16kV | UC03 | UC03 Breaker was isolated for emergency repair. | Ottawa | Defective Equipment
8256 | 2006 | 5 | 8 | 0.66667 |  | 34 | 4 | 7 | Clyde | 4.16kV | UC03 | Transformer #OTT2002 located at 651 Golden Ave isolated to remove old wire | Ottawa | Scheduled Outage | Construction
5190 | 2004 | 5 | 20 | 0.59306 |  | 526 | 9 | 1 | Clyde | 4.16kV | UC03 | 4 kv vault V850 at 850 Campbell was isolated to replace defective transformers in the vault. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14422 | 2009 | 5 | 28 | 0.33681 |  | 280 | 270 | 475 | Clyde | 4.16kV | UC03 | Circuit A/R when trees brought down 3 phase primary line between Dennison & Broadview S. of Carling. Circuit was opened to allow crew to isolate damaged section. Trees were trimmed & line repaired. | Ottawa | Tree Contacts | Inadequate Trimming
20738 | 2012 | 6 | 11 | 0.51042 |  | 35 | 5 | 9 | Clifton | 4.16kV | UC03 | transformer X37913 openned to allow crews clearence to disconnect service to 725 Golden Ave. Clyde (UC03) ID #20738 | Ottawa | Foreign Interference | Dig-in
20743 | 2012 | 6 | 11 | 0.69236 |  | 30 | 5 | 10 | Clyde | 4.16kV | UC03 | Transformer X37913 @ 435 Tillbury was disconnect to make repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18417 | 2011 | 6 | 15 | 0.57847 |  | 22 | 1 | 4 | Clyde | 4.16kV | UC03 | Transformer #X32311 located at 463 Avondale opened by crew to hook up a service | Ottawa | Scheduled Outage | Construction
20900 | 2012 | 6 | 28 | 0.41667 |  | 46 | 8 | 10 | Clyde | 4.16kV | UC03 | Transformer X33731 at 1817 Ernest Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
16729 | 2010 | 8 | 13 | 0.375 |  | 45 | 16 | 21 | Clyde | 4.16kV | UC03 | Clyde UC03 White phase overhead was isolated to end of line on Denison Crt. so that Hydro Ottawa Crew could remove tree from the line. | Ottawa | Scheduled Outage
8973 | 2006 | 8 | 15 | 0.38194 |  | 155 | 13 | 5 | Clyde | 4.16kV | UC03 | Transformer #OTT637 located at 415 Avondale isolated due to re-arranging plant | Ottawa | Scheduled Outage | Preventive Maintenance
13128 | 2008 | 8 | 20 | 0.47222 |  | 100 | 25 | 15 | Clyde | 4.16kV | UC03 | Isolated two transformers X35182 and X34208 at 834 and 844 Broadview Ave to relocate secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
14977 | 2009 | 8 | 20 | 0.52431 |  | 130 | 22 | 10 | Clyde | 4.16kV | UC03 | Transformer #X33731 located at 896 Broadview Ave isolated to hook up a new service mid span, re-sag neutral & then had to replace switch | Ottawa | Scheduled Outage | Construction
11155 | 2007 | 8 | 24 | 0.20208 |  | 565 | 565 | 60 | Clyde | 4.16kV | UC03 | UC03 circuit was affected by the thunderstorm in the Ottawa area. Andy Laneville reports wires down between Carling and Kerr between Denison and Broadview. There is no switches on Boyd to isolate UC03. Andy Laneville reports wires are cut clear on Broadview, Carling, Denison & Kerr area. Mike Anderson and crews fixed the lines affected by the thunderstorm and restored load to the customers on the UC03 circuit. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5784 | 2004 | 9 | 7 | 0.58333 |  | 38 | 13 | 20 | Clyde | 4.16kV | UC03 | Transformer OTT1585 at 584 Cole was taken out of service to balance load. 20 customers on Cole & Avondale were affected. | Ottawa | Human Element | Incorrect Use of Equipment
9211 | 2006 | 9 | 14 | 0.375 |  | 75 | 10 | 8 | Clyde | 4.16kV | UC03 | At 09:00 trans OTT1588 at 715 Cole Ave isolated in order to replace secondary service | Ottawa | Scheduled Outage | Preventive Maintenance
13251 | 2008 | 9 | 16 | 0.70833 |  | 120 | 10 | 5 | Clyde | 4.16kV | UC03 | At 17:00 trans at 866 Campbell Ave was isolated for PCB trans replacement | Ottawa | Scheduled Outage
13335 | 2008 | 10 | 7 | 0.72569 |  | 65 | 1 | 1 | Clyde | 4.16kV | UC03 | Vault V850 at 850 Campbell Ave isolated to replace defective hotline clamp. | Ottawa | Defective Equipment
11505 | 2007 | 10 | 12 | 0.4375 |  | 90 | 12 | 8 | Clyde | 4.16kV | UC03 | Transformer located at 648 Clyde isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
7651 | 2005 | 11 | 24 | 0.375 |  | 15 | 2 | 9 | Clyde | 4.16kV | UC03 | At 09:00 trans OTT1589 isolated to repair Live line clamp | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11774 | 2007 | 11 | 27 | 0.28403 |  | 38 | 3 | 5 | Clyde | 4.16kV | UC03 | Overhead transformer at 1820 Carling isolated for replacement. | Ottawa | Scheduled Outage | Repair
5984 | 2004 | 12 | 5 | 0.59028 |  | 65 | 8 | 7 | Clyde | 4.16kV | UC03 | Refused the switch Transformer Number OTT2002 446 DOVERCOURT | Ottawa | Unknown/Other | No Apparent Cause
7747 | 2005 | 12 | 19 | 0.46181 |  | 55 | 7 | 8 | Clyde | 4.16kV | UC03 | Isolated transformer OTT2869 at 392 Greenwood to replace triplex service | Ottawa | Scheduled Outage | Preventive Maintenance
8227 | 2006 | 5 | 4 | 0.35764 |  | 45 | 5 | 7 | Clyde | 4.16kV | UC04 | Transformer #OTT4629 located at 30 Merritt isolated due to putting in a new service | Ottawa | Scheduled Outage | Construction
15826 | 2010 | 3 | 20 | 0.69306 |  | 80 | 1 | 1 | Clyde | 4.16kV | UC05 | Defective switch burnt up at V783, 1733 Woodward. Crew replaced switch and restored power. | Ottawa | Defective Equipment
20205 | 2012 | 3 | 22 | 0.63542 |  | 70 | 97 | 83 | Clyde | 4.16kV | UC05 | At 15:15 UC05 overhead section was isolated to end of line to allow crew to replace defective transformer. 83 customers were affected for 70 minutes. Clyde (UC05) ID#20205 | Ottawa | Scheduled Outage | Preventive Maintenance
17798 | 2011 | 3 | 29 | 0.375 |  | 190 | 44 | 14 | Clyde | 4.16kV | UC05 | Transformer #X32683 located at 1153 Greyrock opened by crew due to tree trimming | Ottawa | Tree Contacts | Inadequate Trimming
17799 | 2011 | 3 | 29 | 0.375 |  | 190 | 16 | 5 | Clyde | 4.16kV | UC05 | Transformer #X37922 located at 1173 Greyrock opened by crew due to tree trimming. | Ottawa | Tree Contacts | Inadequate Trimming
12329 | 2008 | 4 | 23 | 0.43611 |  | 52 | 6 | 7 | Clyde | 4.16kV | UC05 | At 10:28 trans at 1085 Castle Hill was isolated in order to replace a pcb trans .. | Ottawa | Scheduled Outage | Preventive Maintenance
14227 | 2009 | 4 | 25 | 0.80694 |  | 104 | 324 | 187 | Clyde | 4.16kV | UC05 | UC05 breaker tripped during high winds, heavy rain & lightning. No permanent problem was found. | Ottawa | Adverse Weather
18023 | 2011 | 4 | 28 | 0.57986 |  | 72 | 360 | 300 | Clyde | 4.16kV | UC05 | UC05 circuit breaker tripped during wind/lightning storm. Closed via SCADA and held. | Ottawa | Adverse Weather | Wind
14295 | 2009 | 5 | 4 | 0.54167 |  | 120 | 10 | 5 | Clyde | 4.16kV | UC05 | At 13:00 trans at 9012 Clyde was isolated to make repairs to service | Ottawa | Scheduled Outage | Preventive Maintenance
6553 | 2005 | 5 | 13 | 0.39236 |  | 86 | 20 | 14 | Clyde | 4.16kV | UC05 | Power interrupted to Transformer OTT2878 at 1236 Bonnie cr for service upgrade | Ottawa | Scheduled Outage | Construction
16279 | 2010 | 6 | 17 | 0.36944 |  | 183 | 76 | 25 | Clyde | 4.16kV | UC05 | Primary neutral burnt down due to tree contact on the open wire buss transformer X37921 at 1193 Maitland Ave and X32053 at 1177 Maitland Ave opened to make repairs | Ottawa | Tree Contacts | Inadequate Trimming
5368 | 2004 | 6 | 25 | 0.99931 |  | 226 | 211 | 187 | Clyde | 4.16kV | UC05 | UC05 was interupted from SCADA to allow O/H crew to cut damaged section free of circuit in order to make repairs. 2 phases were knocked down by the high winds. See A/R at 17:35, ID #5364. Circuit was again interrupted in order to reconnect repaired section. | Ottawa | Adverse Weather | Wind
18709 | 2011 | 7 | 17 | 0.80903 |  | 1115 | 5575 | 300 | Clyde | 4.16kV | UC05 | With high wind caused the UC05 circuit to trip in the CastlHill area. | Ottawa | Adverse Weather | Wind
6994 | 2005 | 7 | 19 | 0.75 |  | 181 | 6 | 2 | Clyde | 4.16kV | UC05 | Isolated Transformer # 6783 at 1771 Woodward to replace a leaking Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
12993 | 2008 | 8 | 2 | 0.58542 |  | 1220 | 61 | 3 | Clyde | 4.16kV | UC05 | UC00 line and a section of UC05 line were isolated to replace the Queensway bridge at Clyde Ave. One 3 phase O/H transformer was interrupted to 3 commercial customers on Clyde Ave. | Ottawa | Scheduled Outage | Construction
5626 | 2004 | 8 | 8 | 0.89028 |  | 166 | 17 | 6 | Clyde | 4.16kV | UC05 | A squirrel cause the fuse to blow at transformer OTT2875 at 1145 Greyrock. The switch broke while crew was trying to restore and was replaced. 6 customers on Bonnie, Greyrock and Castle Hill were affected. | Ottawa | Foreign Interference | Animal
19033 | 2011 | 8 | 28 | 0.66181 |  | 37 | 185 | 300 | Clyde | 4.16kV | UC05 | UC05 breaker tripped, at the same time as UC10 breaker auto reclosed and tripped. 24/7 crew patrolled and nothing found. UC05 closed and holding. | Ottawa | Unknown/Other | No Apparent Cause
7280 | 2005 | 9 | 5 | 0.32639 |  | 259 | 78 | 18 | Clyde | 4.16kV | UC05 | Car accident on Woodward broke a pole requiring these customers to be interupted for repairs. | Ottawa | Scheduled Outage | Repair
19219 | 2011 | 9 | 21 | 0.34722 |  | 85 | 7 | 5 | Clyde | 4.16kV | UC05 | Isolated transformer X30221 at 1273 Grarock Cres for a service up-grade | Ottawa | Scheduled Outage | Construction
11462 | 2007 | 10 | 4 | 0.40972 |  | 120 | 28 | 14 | Clyde | 4.16kV | UC05 | Transformer #OTT5373 located at 993 Riddell isolated for maintenance | Ottawa | Scheduled Outage
15910 | 2010 | 4 | 8 | 0.81597 |  | 60 | 6 | 6 | CLYDE | 4.16kV | UC06 | Transformer X32057 at 1801 Woodward Drive replaced due to leaking transformer | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17962 | 2011 | 4 | 19 | 0.090278 |  | 49 | 3 | 4 | CLYDE |  | UC06 | A car accident at 1805 Woodward caused an outage to 4 customer for 49 mins. Crews made repairs to fallen secondary cables. Clyde UC06 ID # 17962 | Ottawa | Foreign Interference | Vehicle
8312 | 2006 | 5 | 17 | 0.55556 |  | 40 | 1 | 1 | Clyde | 4.16kV | UC06 | P239 @ 1701 Woodward dr. was isolated from Hydro Ottawa sources to repair sparking hot line clamps. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18440 | 2011 | 6 | 20 | 0.35417 |  | 55 | 7 | 8 | Clyde | 4.16kV | UC06 | Transformer #X31597 located at 1240 Clyde opened up by crew to upgrade a sevice | Ottawa | Scheduled Outage | Construction
18794 | 2011 | 7 | 22 | 0.4375 |  | 20 | 2 | 5 | Clyde | 4.16kV | UC06 | Transformer #X32058 located at 1771 Woodward opened by crew to check pressure of transformer | Ottawa | Scheduled Outage | Construction
18812 | 2011 | 7 | 25 | 0.28056 |  | 125 | 302 | 145 | Clyde | 4.16kV | UC06 | Blown pothead on TM3UC going to VT393 due to crow contact caused UC06, TM19 and TM28 to open. | Ottawa | Foreign Interference | Animal
8966 | 2006 | 8 | 15 | 0.35417 |  | 40 | 7 | 11 | Clyde | 4.16kV | UC06 | Transformer #OTT1109 located at 1116 Clyde isolated due to maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
8068 | 2006 | 3 | 27 | 0.4375 |  | 300 | 0 | 1 | Clyde | 4.16kV | UC07 | water leaking into the customer main breaker caused the customer to request emergency 4kv vault isolation. | Ottawa | Adverse Environment | Flooding
12770 | 2008 | 6 | 30 | 0.38542 |  | 75 | 2 | 2 | Clyde | 4.16kV | UC07 | Crew isolated 3 phase transformer bank X32123 at 1594 Laperriere Ave for service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
10833 | 2007 | 7 | 10 | 0.39722 |  | 68 | 11 | 10 | Clyde | 4.16kV | UC07 | Transformer K1225 at 155 Lebrun St isolated for replacement. | Ottawa | Scheduled Outage | Repair
17081 | 2010 | 10 | 7 | 0.65625 |  | 107 | 2 | 1 | Clyde | 4.16kV | UC07 | V446 was isolated due to 2 blown phases on the dip from UC07 to V446 at 880 Lady Ellen Pl. Investigation revealed no reported cause | Ottawa | Unknown/Other | No Apparent Cause
13408 | 2008 | 10 | 22 | 0.75347 |  | 45 | 1 | 1 | CLYDE | 4.16kV | UC07 | 4kv breaker tripped in V452 at 1523 LAPERRIERE AVENUE cause unknown | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17216 | 2010 | 11 | 3 | 0.7375 |  | 60 | 43 | 43 | CLYDE | 4.16kV | UC07 | Defective white phase cable below the pothead on the riser of the UC07 at Clyde. Section isolated and power restored on the UC00. | Ottawa | Defective Equipment
17217 | 2010 | 11 | 3 | 0.7375 |  | 60 | 43 | 43 | Clyde | 4.16kV | UC07 | Cause was determined to be a UC07 cable fault between the station & overhead. Load was restored from UC00. | Ottawa | Defective Equipment
19668 | 2011 | 12 | 3 | 0.35903 |  | 394 | 66 | 10 | Clyde | 4.16kV | UC07 | The transformer at Lady Ellen & Carling was isolated for transformer replacement. | Ottawa | Scheduled Outage | Preventive Maintenance
11936 | 2008 | 1 | 14 | 0.52431 |  | 75 | 28 | 22 | Clyde | 4.16kV | UC08 | Isolated and replaced transformer OTT3714 at 888 Kirkwood Dr | Ottawa | Scheduled Outage | Preventive Maintenance
17626 | 2011 | 2 | 20 | 0.38194 |  | 10 | 1 | 3 | Clyde | 4.16kV | UC08 | Isolated transformer OTT3716 at the rear of 905 Kirkwood Ave to replace connections on secondary service | Ottawa | Scheduled Outage | Emergency Services Request
20042 | 2012 | 2 | 21 | 0.54167 |  | 75 | 9 | 7 | Clyde | 4.16kV | UC08 | Trans X30258 at 913 Cavan St was isolated to upgrade secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
20069 | 2012 | 2 | 28 | 0.40278 |  | 177 | 118 | 40 | Clyde | 4.16kV | UC08 | The O/H crew isolated the O/H on Laperrier Ave at Merivale to allow them to transfer the W phase customers on AD05 circuit over to the R phase UC08 circuit. | Ottawa | Scheduled Outage | Construction
6358 | 2005 | 4 | 3 | 0.33542 |  | 17 | 2 | 6 | Clyde | 4.16kV | UC08 | Isolated Transformer # 1567 at 1381 Coldrey Ave to replace bad connector | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12268 | 2008 | 4 | 10 | 0.41042 |  | 129 | 17 | 8 | CLYDE | 4.16kV | UC08 | Transformer #34739 at 1397 Coldrey Ave isolated for transformer change (PCB) | Ottawa | Scheduled Outage | Repair
12286 | 2008 | 4 | 15 | 0.375 |  | 150 | 18 | 7 | Woodroffe | 4.16kV | UC08 | Isolated and replaced transformer X31523 at 1381 Coldrey Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
20744 | 2012 | 6 | 12 | 0.37292 |  | 83 | 8 | 6 | Clyde | 4.16kV | UC08 | Transformer #X37917 located at 908 Kirkwood Ave opened up due to lead burnt off switch | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16293 | 2010 | 6 | 25 | 0.45486 |  | 10 | 1 | 7 | Clyde | 4.16kV | UC08 | Transformer #X32303 located at 1442 Laperriere opened by crew for Revenue Dept to disconnect a service | Ottawa | Scheduled Outage | Construction
18639 | 2011 | 7 | 11 | 0.51389 |  | 30 | 3 | 6 | Clyde | 4.16kV | UC08 | Trans X31517 at 1281 Coldrey was isolated in order to remove a tree from the secondary service | Ottawa | Tree Contacts | Tree Fallen
11284 | 2007 | 9 | 10 | 0.36806 |  | 70 | 4 | 3 | Clyde | 4.16kV | UC08 | Transformer #OTT314 at 1577 Laperriere isolated to allow refusing of TX switch | Ottawa | Scheduled Outage | Repair
11285 | 2007 | 9 | 10 | 0.375 |  | 80 | 9 | 7 | Clyde | 13.2kV | UC08 | Transformer #X35482 at 812 Kirwood isolated to allow for transfer of plant | Ottawa | Scheduled Outage | Construction
13260 | 2008 | 9 | 18 | 0.70833 |  | 135 | 22 | 10 | Clyde | 4.16kV | UC08 | Isolated and replaced transformer X35617 at 1550 Laperriere Ave (PCB Oil) | Ottawa | Scheduled Outage | Preventive Maintenance
17144 | 2010 | 10 | 20 | 0.32361 |  | 299 | 60 | 12 | CLYDE | 4.16kV | UC08 | Transformer X32304 at rear of 1400 Laperriere defective and replaced | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17146 | 2010 | 10 | 20 | 0.32361 |  | 284 | 57 | 12 | Clyde | 4.16kV | UC08 | Replaced defective transformer X32304 at 1400 Laperriere Ave | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19946 | 2012 | 2 | 1 | 0.40694 |  | 302 | 60 | 12 | Clyde | 4.16kV | UC10 | O/H crews opened 2 O/H transformers, X35138 & X31589 and performed a primary cut to isolate a section of the UC10 white phase to allow crews to remove trees in the rear of 1045 Castle Hill. | Ottawa | Tree Contacts | Inadequate Trimming
15709 | 2010 | 2 | 8 | 0.41667 |  | 45 | 6 | 6 | Clyde | 4.16kV | UC10 | At 10:00 trans at 1182 Greyrock Cres was isolated for a sec service mtec repair | Ottawa | Scheduled Outage | Preventive Maintenance
7951 | 2006 | 2 | 19 | 0.89583 |  | 30 | 0 | 1 | Clyde | 4.16kV | UC10 | Switch to V310 @ 1750 courtwood found burning up. 4KV vault main opened switch replaced. All power restored to normal. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
12370 | 2008 | 5 | 1 | 0.39861 |  | 100 | 5 | 3 | Clyde | 4.16kV | UC10 | 4kV transformer X35143 at 1048 Castlehill was isolated for PCB change. | Ottawa | Scheduled Outage
14326 | 2009 | 5 | 8 | 0.39236 |  | 45 | 2 | 3 | Clyde | 4.16kV | UC10 | Isolated transformer X33432 at 1151 Bonnie Dr for service up-grade | Ottawa | Scheduled Outage | Construction
16069 | 2010 | 5 | 9 | 0.061111 |  | 32 | 123 | 230 | Clyde | 4.16kV | UC10 | Dump trucks in the city yard at 1683 Woodward caught fire. Hydro Ottawa crews determined that the circuit tripped due to Ottawa fire spraying water through the conductors in an attempt to extinguish the fire. UC10 breaker was closed back in and held. | Ottawa | Adverse Environment | Fire
10587 | 2007 | 6 | 10 | 0.66042 |  | 157 | 8 | 3 | Clyde | 4.16kV | UC10 | Oncall crew replaced defective O/H transformer at 1151 Bonnie. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18594 | 2011 | 7 | 6 | 0 |  | 155 | 8 | 3 | Clyde | 4.16kV | UC10 | Transformer X35143 at 1066 Castle Hill was isolated to allow crew to remove branch from secondary. Clyde (UC10) ID#18594 | Ottawa | Tree Contacts | Tree Limb Fallen
18719 | 2011 | 7 | 17 | 0.80903 |  | 1387 | 5317 | 230 | Clyde | 4.16kV | UC10 | Wind caused a tree to fall onto the UC10 O/H causing the circuit to trip. | Ottawa | Adverse Weather | Wind
8833 | 2006 | 7 | 25 | 0.4375 |  | 110 | 29 | 16 | Clyde | 4.16kV | UC10 | Isolated transformer OTT1243 at 1161 Castle Hill Cres for service work | Ottawa | Scheduled Outage | Repair
19030 | 2011 | 8 | 28 | 0.66181 |  | 318 | 717 | 230 | Clyde | 4.16kV | UC10 | UC10 Breaker tripped. High winds in the area at the time. Report of branches on wire, crew found nothing. UC10 closed and held for 4 minutes. Cover-up installed at one location where it was suspected the phases might be coming together and the circuit was restored. Customers still calling wit no power. Eventually found red phase down in the rear of 1042 Castle Hill. | Ottawa | Adverse Weather | Wind
7415 | 2005 | 10 | 1 | 0.61111 |  | 25 | 5 | 11 | Clyde | 4.16kV | UC10 | Transformer #OTT28 located at 1275 Albany isolated to make repairs due to 3 phase primary down due to a fallen tree | Ottawa | Tree Contacts | Tree Fallen
11889 | 2007 | 12 | 27 | 0.47917 |  | 700 | 12 | 1 | Clyde | 4.16kV | UC10 | P62 at 1755 Courtwood isolated to repair defective cable, 1 customer affected for 700min. ID#11889. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15589 | 2009 | 12 | 29 | 0.59097 |  | 57 | 10 | 10 | Clyde | 4.16kV | UC10 | At 2:11pm transformer X32824 was opened and a PC10#7895 was established to allow contractor tree trimming crew to cut down tree leaning on the 3 phase overhead section, 10 customers affected and all power was restored at 3:08pm. Clyde (UC10). ID#15589. | Ottawa | Scheduled Outage | Preventive Maintenance
13822 | 2008 | 12 | 30 | 0.51389 |  | 110 | 2 | 1 | Clyde | 4.16kV | UC10 | Lead pulled out of 1 phase fused cut-out at dip to V788, 1827 Woodward Dr. V788 isolated from Hydro sources to make repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18973 | 2011 | 8 | 18 | 0.62986 |  | 128 | 177 | 1165 | Clyde | 4.16kV | UCK2Y2 | UCK1Y1 carrying UC01, 02, 03 was opened for crews to cut clear downed primary at 707 Cole, customers out during repair. | Ottawa | Adverse Weather | Lightning
18553 | 2011 | 6 | 28 | 0.79583 |  | 32 | 360 | 675 | Clyde | 4.16kV | UCT3 | UCT3 transformer tripped during lightening storm. Causing outage to UC08 circuit & UC10 circuit. | Ottawa | Adverse Weather | Lightning
18849 | 2011 | 7 | 29 | 0.94444 |  | 175 | 1594 | 1950 | Clyde | 4.16kV | UCT3 | Lightning storm caused the UCT1 and the UC05 breaker to open. Customer reported wires down on UC03 circuit, crew found service wires down. Crew then patrolled UC10 circuit and found one phase resting on a span guy. Clyde ID#18849 | Ottawa | Lightning
18209 | 2011 | 5 | 24 | 0.42014 |  | 605 | 91 | 9 | Augusta | 4.16kV | UD01 | TV142 at 500 Clarence was isolated for planned transformer repalcement. | Ottawa | Scheduled Outage | Construction
7562 | 2005 | 11 | 3 | 0.39861 |  | 469 | 94 | 12 | Augusta | 4.16kV | UD01 | TV139 @ 468 Clarence was isolated for rebuilding of TV139 | Ottawa | Scheduled Outage | Construction
12089 | 2008 | 2 | 29 | 0.67847 |  | 47 | 1 | 1 | Gladstone | 4.16kV | UD02 | V166 pole dip base damaged due to vehicle contact exposing primary. Crew isolated radial vault feed and repaired exposed cable. Shopping Plaza affected at 604 Rideau St. | Ottawa | Foreign Interference | Vehicle
16190 | 2010 | 6 | 3 | 0.57569 |  | 21 | 1 | 2 | Augusta | 4.16kV | UD02 | Transformer X30746 at 418 Rideau St was isolated to replace service wire. | Ottawa | Defective Equipment
20892 | 2012 | 6 | 27 | 0.33333 |  | 180 | 15 | 5 | Augusta | 4.16kV | UD02 | Transformer X30954 at 227 Wurtemburg St. isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
20905 | 2012 | 7 | 1 | 0.62083 |  | 122 | 283 | 139 | Augusta | 4.16kV | UD02 | UD02 & UD00 breaker triped and locked out, James Rice onsite and reports metal ballon hanging from wires, suspect cause of fault. Closed UD02 and breaker A/R, additional patrol found wires wraped at 428 Rideau. 24/7 onsite and unwrapped wires, UD02 closed, UD00 closed & UD02 breaker tripped, UD00 indicates 60 amps on blue phase. UD00 breaker openned viqa SCADA, further patrol found wrapped wires east of chapel. Wrapped, UD02 & UD00 breakers closed | Ottawa | Foreign Interference | Foreign Object
10783 | 2007 | 7 | 3 | 0.59375 |  | 125 | 23 | 11 | Augusta | 4.16kV | UD02 | Transformer #OTT5396 located at 535 Besserer St isolated to do major tree trimming with assistance of Asplundh | Ottawa | Tree Contacts | Inadequate Trimming
19796 | 2012 | 1 | 6 | 0.47569 |  | 82 | 8 | 6 | Augusta | 4.16kV | UD04 | Isolated transformer X30734 at 603 Besserer St to install new service | Ottawa | Scheduled Outage | Repair
6139 | 2005 | 1 | 16 | 0.70139 |  | 15 | 6 | 25 | Augusta | 4.16kV | UD04 | Defective switch to P367 at 247 Rideau replaced. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12081 | 2008 | 2 | 27 | 0.4375 |  | 40 | 13 | 19 | Augusta | 4.16kV | UD04 | Transformer #X30947 located at 425 Daly isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
12084 | 2008 | 2 | 27 | 0.54167 |  | 65 | 15 | 14 | Augusta | 4.16kV | UD04 | Transformer #V283 located at 207 Charlotte isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
8108 | 2006 | 4 | 5 | 0.41667 |  | 55 | 21 | 23 | Augusta | 4.16kV | UD04 | Transformer #OTT1357 located at 184 Charlotte isolated due to re-arranging hydro plant | Ottawa | Scheduled Outage | Construction
5027 | 2004 | 4 | 19 | 0.85347 |  | 128 | 41 | 19 | Augusta | 4.16kV | UD04 | Hot line clamp burnt off, feeding the transformer at 508 Besserer. | Ottawa | Defective Equipment
16121 | 2010 | 5 | 21 | 0.85417 |  | 30 | 8 | 16 | Augusta | 4.16kV | UD04 | Transformer #X30728 located at 530 Rideau St opened for crew to make repairs to triplex service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20791 | 2012 | 6 | 18 | 0.4375 |  | 60 | 11 | 11 | Augusta | 4.16kV | UD04 | Transformer #X30736 located at 168 Charlotte St opened by crew to hook up a service | Ottawa | Scheduled Outage | Construction
20811 | 2012 | 6 | 20 | 0.33333 |  | 210 | 70 | 20 | Augusta | 4.16kV | UD04 | Transformer #X30948 located at 401 Daly Ave opened by crew to relocate plant | Ottawa | Scheduled Outage | Construction
10695 | 2007 | 6 | 21 | 0.48611 |  | 19 | 3 | 8 | Augusta | 4.16kV | UD04 | At 11:40 trans at 351 Stewart was isolated in order to replace a broken cutout | Ottawa | Scheduled Outage | Repair
10697 | 2007 | 6 | 21 | 0.48611 |  | 19 | 3 | 8 | Augusta | 4.16kV | UD04 | At 11:40 trans at 351 Stewart was isolated in order to replace defective cutout | Ottawa | Scheduled Outage | Repair
10752 | 2007 | 6 | 28 | 0.38194 |  | 108 | 34 | 19 | Augusta | 4.16kV | UD04 | Transformer #OTT1839 located at 430 Daly isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
20895 | 2012 | 6 | 28 | 0.37778 |  | 329 | 66 | 12 | Augusta | 4.16kV | UD04 | 4kV cable dip from S22954 at 419 Daly was isolated to allow crews to transfer the dip to a new pole. | Ottawa | Scheduled Outage | Construction
10830 | 2007 | 7 | 10 | 0.03125 |  | 36 | 3 | 5 | Augusta | 4.16kV | UD04 | Transformer at 347 Stewart St was arcing. 24/7 replaced LLC, and restored power to transformer. | Ottawa | Defective Equipment
10836 | 2007 | 7 | 10 | 0.54583 |  | 114 | 21 | 11 | Augusta | 4.16kV | UD04 | Transformer #OTT5396 at 535 Besserer St isolated to allow for pcb transformer change | Ottawa | Scheduled Outage | Preventive Maintenance
16501 | 2010 | 7 | 20 | 0.375 |  | 192 | 80 | 25 | Augusta | 4.16kV | UD04 | Isolated transformer X30730 at 535 Besserer St for contractor to remove tree | Ottawa | Scheduled Outage | Preventive Maintenance
8991 | 2006 | 8 | 17 | 0.43056 |  | 87 | 6 | 4 | Augusta | 4.16kV | UD04 | At 10:20 Trans OTT1835 at 214 Cobourg St was isolated for replacement , 4 cust affected | Ottawa | Scheduled Outage | Preventive Maintenance
15011 | 2009 | 8 | 26 | 0.58333 |  | 114 | 21 | 11 | AUGUSTA | 4.16kV | UD04 | Transformer X31095 at 183 Augusta isolated to allow for service upgrade | Ottawa | Scheduled Outage | Repair
15050 | 2009 | 9 | 3 | 0.40069 |  | 16 | 3 | 10 | Augusta | 4.16kV | UD04 | K1056 @ 419 Daley was isolated by the crew under the PCB transformer replacement progam | Ottawa | Scheduled Outage | Preventive Maintenance
11548 | 2007 | 10 | 18 | 0.46181 |  | 65 | 18 | 17 | Augusta | 4.16kV | UD04 | Transformer #65A3D-0178 located at 229 Charlotte isolated for customer to take down scaffolding safely | Ottawa | Scheduled Outage | Preventive Maintenance
11605 | 2007 | 10 | 26 | 0.38542 |  | 170 | 28 | 10 | Augusta | 4.16kV | UD04 | Isolated transformer OTT5994 at 351 Stewart St to transfer hydro plant | Ottawa | Scheduled Outage | Construction
11649 | 2007 | 11 | 2 | 0.43194 |  | 53 | 14 | 16 | Augusta | 4.16kV | UD04 | Transformer #OTT1835 located at 368 Daly Ave isolated due to squirrel contact | Ottawa | Foreign Interference | Animal
15753 | 2010 | 2 | 28 | 0.78125 |  | 660 | 287 | 40 | Augusta | 4.16kV | UD05 | Transformer TV192 @ 346 Bruyere is defective which caused the fuses to blow at the distribution vault V184 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20556 | 2012 | 5 | 23 | 0.36806 |  | 548 | 247 | 27 | Augusta | 4.16kV | UD05 | TV193 at 335 St Andrew was isolated & replaced with new TP9392. | Ottawa | Scheduled Outage | Construction
16510 | 2010 | 7 | 21 | 0.6875 |  | 14 | 4 | 17 | Augusta | 4.16kV | UD05 | A transformer @ V184 @ 500 old St. Patrick Rd to allow crews to replace PCB transformer | Ottawa | Scheduled Outage | Preventive Maintenance
3780 | 2003 | 7 | 24 | 0.37014 |  | 361 | 217 | 36 | UD | 4.16kV | UD05 | VT179 on St. Patrick was isolated to replace existing transformer with the new turtle. | Ottawa | Scheduled Outage | Construction
10953 | 2007 | 7 | 26 | 0.055556 |  | 184 | 43 | 14 | Augusta | 4.16kV | UD05 | Asbestos removal from V184 at 500 St Patrick St | Ottawa | Scheduled Outage | Preventive Maintenance
16919 | 2010 | 9 | 10 | 0.61667 |  | 41 | 7 | 10 | Augusta | 4.16kV | UD05 | 4kv Transformer K1015 at 244 Bruyere was opened to allow crew to disconnect bad service to 248 Bruyere. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16923 | 2010 | 9 | 10 | 0.84722 |  | 4 | 1 | 10 | Augusta | 4.16kV | UD05 | Transformer #K1015 located at 244 Bruyere St opened by crew to reconnect service at 248 Bruyere | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
19504 | 2011 | 10 | 31 | 0.38333 |  | 458 | 115 | 15 | Augusta | 4.16kV | UD05 | TV183 at 20 Patro was isolated for replacement. | Ottawa | Scheduled Outage | Preventive Maintenance
13969 | 2009 | 2 | 12 | 0.27917 |  | 2323 | 39 | 1 | Augusta | 4.16kV | UD08 | V126 at 151 Chapel was isolated due to flooding in the vault, to maintain vault, repair damage from water and remove asbestos. | Ottawa | Adverse Environment | Flooding
3304 | 2003 | 3 | 26 | 0.81528 |  | 746 | 749 | 192 | Augusta | 4.16kV | UD08 | Augusta UD08 4 kv circuit tripped causing an interruption to customers in the downtown area of King Edward & Murray Streets. Customers were restored in stages with all customers restored by 10:46pm except the 35 residential customers fed from the faulted transformer. The transformer was replaced and customers restored at 08:00 am | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6604 | 2005 | 5 | 25 | 0.40972 |  | 410 | 273 | 40 | UD | 4.16kV | UD08 | TV90 supplying 126 Beausoliel was isolated for planned replacement. | Ottawa | Scheduled Outage | Preventive Maintenance
6683 | 2005 | 6 | 8 | 0.45347 |  | 473 | 441 | 56 | Gloucester | 4.16kV | UD08 | 4 kv vault TV121 isolated for Hydro Ottawa to replace transformers & remodel vault. 56 customers on Clarence, Cobourg & Heney were affected. | Ottawa | Scheduled Outage | Preventive Maintenance
5454 | 2004 | 7 | 6 | 0.39792 |  | 388 | 6 | 31 | Augusta | 4.16kV | UD08 | TV113 at 190 Beausoleil was isolated to upgrade from 75 kva to 100 kva transformer. | Ottawa | Scheduled Outage | Repair
19218 | 2011 | 9 | 21 | 0.38125 |  | 414 | 166 | 24 | Augusta | 4.16kV | UD08 | 4kV sidewalk vault TV120 at 20 Heney St. Was isolated to allow crews to replace transformers | Ottawa | Scheduled Outage | Preventive Maintenance
19266 | 2011 | 9 | 27 | 0.40139 |  | 186 | 192 | 62 | Augusta | 4.16kV | UD08 | TV121 @ 23 Heney was isolated to allow crews to replace defective "turtle" transformer in sidewalk vault. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19268 | 2011 | 9 | 27 | 0.41667 |  | 170 | 28 | 10 | Augusta | 4.16kV | UD08 | Trans at 74 Cobourg St was isolated in order to replace the transformer | Ottawa | Scheduled Outage | Preventive Maintenance
7487 | 2005 | 10 | 20 | 0.03125 |  | 370 | 432 | 196 | Augusta | 4.16kV | UD08 | Blue phase cable fault on circuit SC7202 line out of SC72. | Ottawa | Defective Equipment
7489 | 2005 | 10 | 20 | 0.39931 |  | 509 | 382 | 45 | UD | 4.16kV | UD08 | TV92 @ 360 Murray isolated for planned replacement. | Ottawa | Scheduled Outage | Construction
15286 | 2009 | 10 | 21 | 0.39028 |  | 195 | 78 | 24 | Augusta | 4.16kV | UD08 | At 9:22am transformers K186 & K187 at 72 Cobourgh were isolated to allow crews toremove asbestos board, upgrade insulators and upgrade terminations, 24 customers were affected and power was restored at . Augusta (UD08). ID#15286. | Ottawa | Scheduled Outage | Preventive Maintenance
13576 | 2008 | 11 | 7 | 0.42708 |  | 70 | 23 | 20 | Augusta | 4.16kV | UD08 | At 180 Beausoleil Drive transformer isolated for maintenance at 10:15am and restored at 11:25am. | Ottawa | Scheduled Outage | Repair
13982 | 2009 | 2 | 14 | 0.42639 |  | 33 | 220 | 400 | Augusta | 4.16kV | UDT2 | The pothead termination blew that feeds the primary side of the transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9712 | 2006 | 11 | 23 | 0.56042 |  | 6 | 95 | 950 | Augusta | 13.2kV | UDT2 | Augusta T1 transformer was transferred to T2 for testing of the T1 assosiated apparatus when the T2 was operated in error. The opperator was under the impression that the UDT1 breaker was selected while the UDT2 breaker was in fact selected. This caused a total loss of Augusta load. Approximatly 2.8 MW | Ottawa | Human Element | Commissioning Errors
4791 | 2004 | 2 | 13 | 0.40625 |  | 105 | 24 | 14 | Florence | 4.16kV | UF01 | Transformer OTT195 at 364 Arlington isolated to transfer customers to new supply. | Ottawa | Scheduled Outage | Construction
4520 | 2003 | 11 | 26 | 0.47431 |  | 37 | 11 | 18 | Florence | 4.16kV | UF01 | Transformer *OTT192 at 278 Arlington interrupted to redo connections on secondary service. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11962 | 2008 | 1 | 19 | 0.74653 |  | 63 | 21 | 20 | Flourence | 4.16kV | UF04 | Corner od Gilmour and Lyon, UF04 line fuse blew causing outage of 2 transformers. Single phase run off re-fused and all 20 customers restored. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7913 | 2006 | 2 | 14 | 0.45833 |  | 36 | 10 | 16 | Florence | 4.16kV | UF04 | Isolated transformer OTT2685 at 513 Gilmour St to replace the connections on the secondary buss | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17808 | 2011 | 3 | 31 | 0.42222 |  | 236 | 269 | 271 | Florence | 4.16kV | UF04 | UF04 3 phase run off on MacLaren east of Kent, large truck contacted plant at the dip to V491 causing all 3 phases to burn down at the dip pole. Run off isolated for repairs remainder of UF04 closed in. | Ottawa | Foreign Interference | Vehicle
20481 | 2012 | 5 | 8 | 0.39583 |  | 160 | 397 | 149 | Florence | 4.16kV | UF04 | at 09:10, 4KV vault V380 at 420 Gilmour was isolated under PC10a #3698 established by glen carswell to allow crews to replace PCB transformers. 149 customers affected for 10 minutes. Florence (UF04). ID #20481. Intial isolation cancelled due to resident stuck in elevating device. at 09:30, 4KV vault V380 at 420 Gilmour was isolated under PC10a #3699 established by glen carswell to allow crews to replace PCB transformers. 149 customers affected for 150 minutes. Florence (UF04). ID #20481. | Ottawa | Scheduled Outage
20714 | 2012 | 6 | 8 | 0.11458 |  | 75 | 66 | 53 | Florence | 4.16kV | UF04 | UF04 cct isolated from S28407 to EOL due to requrest of Ottawa Fire Dept, wires were on fire. 24/7 crew found damaged cables at V491, 386 MacLaren. All customers restored except for V491, which will require mtce, and inspection. | Ottawa | Adverse Environment | Fire
12651 | 2008 | 6 | 15 | 0.88333 |  | 356 | 119 | 20 | Florence | 4.16kV | UF04 | A section of O/h line was isolated on McClaren, because Pole was leaning on house, and one phase of primary was down. Repairs made and switch closed. | Ottawa | Adverse Weather | Lightning
11359 | 2007 | 9 | 21 | 0.62708 |  | 113 | 15 | 8 | Flourence | 4.16kV | UF04 | PCB transformer at 412 MacLaren replaced with new can non PCB. | Ottawa | Scheduled Outage | Repair
13276 | 2008 | 9 | 22 | 0.70833 |  | 185 | 25 | 8 | Florence | 4.16kV | UF04 | Transformer #X30516 located at 430 Maclaren isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
13288 | 2008 | 9 | 24 | 0.70833 |  | 180 | 39 | 13 | Florence | 4.16kV | UF04 | Transformer #X30324 located at 412 Maclaren insolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
17397 | 2010 | 12 | 9 | 0.46528 |  | 80 | 25 | 19 | Florence | 4.16kV | UF04 | Transformer #X31871 located at 84 Florence opened by crew due to primary re-arranging | Ottawa | Scheduled Outage | Construction
15701 | 2010 | 2 | 3 | 0.40625 |  | 15 | 2 | 9 | Florence | 4.16kV | UF05 | Transformer #X30659 located at 547 Gilmour St isolated to reconnect building after fire. | Ottawa | Scheduled Outage | Fire
12940 | 2008 | 7 | 25 | 0.41667 |  | 15 | 3 | 13 | Florence | 4.16kV | UF05 | Transformer #X30518 located at 471 Maclaren St isolated due to pole transfer | Ottawa | Scheduled Outage | Preventive Maintenance
5816 | 2004 | 9 | 23 | 0.42708 |  | 45 | 2 | 2 | UF | 4.16kV | UF05 | To repair the Secondary Service to 555 Gilmore | Ottawa | Scheduled Outage | Repair
15300 | 2009 | 10 | 25 | 0.26458 |  | 149 | 37 | 15 | Florence | 4.16kV | UF05 | Transformer #X31049 located at 102 James St isolated due to wire burnt off the drop lead | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14122 | 2009 | 3 | 31 | 0.066667 |  | 259 | 1157 | 268 | Florence | 4.16kV | UF06 | UF06 breaker opened manually from SCADA due to the proximity to fire at 464 Bank on the corner of McLeod & Bank Streets. Damaged services were disconnected, primary line was inspected & power restored to all but the damaged services. | Ottawa | Adverse Environment | Fire
12229 | 2008 | 4 | 3 | 0.41667 |  | 60 | 18 | 18 | Florence | 4.16kV | UF06 | Transformer #X31037 located at 129 Catherine St isolated to transfer customers | Ottawa | Scheduled Outage | Preventive Maintenance
16051 | 2010 | 5 | 6 | 0.625 |  | 84 | 1 | 1 | Florence | 4.16kV | UF06 | Crew reports broken cutout switch at p/p/h to V67 410 Bank St. bSwitch was replaced and power restored to building. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
18129 | 2011 | 5 | 10 | 0.95833 |  | 235 | 70 | 18 | FLORENCE | 4.16kV | UF06 | Transformer X31036 at 127 Catherine St. Ottawa was isolated to replace defective transformer. | Ottawa | Defective Equipment
16217 | 2010 | 6 | 7 | 0.37708 |  | 320 | 485 | 150 | Kilborn | 4.16kV | UF06 | UP06 circuit load was transfered to UP07 circuit. This required an outage. | Ottawa | Scheduled Outage | Construction
8518 | 2006 | 6 | 19 | 0.35417 |  | 45 | 10 | 14 | FLORENCE | 4.16kV | UF06 | Isolated transformer OTT2505 at 100 Florence St for service upgrade | Ottawa | Scheduled Outage | Repair
20803 | 2012 | 6 | 19 | 0.47222 |  | 45 | 10 | 14 | Florence | 4.16kV | UF06 | Transformer #X31190 located at 414 Mcleod St opened up by crew to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
20883 | 2012 | 6 | 26 | 0.37847 |  | 113 | 9 | 5 | Florence | 4.16kV | UF06 | Isolated transformer X42450 at 400 Mcleod St for service upgrade | Ottawa | Scheduled Outage | Emergency Services Request
7260 | 2005 | 9 | 1 | 0.29861 |  | 100 | 2 | 1 | Florence | 4.16kV | UF06 | Transformer at 464 Bank St was isolated and replaced due to an oil leak | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11303 | 2007 | 9 | 13 | 0.73264 |  | 175 | 6 | 2 | Florence | 4.16kV | UF06 | Transformer #X30320 located at 490 Kent isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
11304 | 2007 | 9 | 13 | 0.73264 |  | 175 | 38 | 13 | Florence | 4.16kV | UF06 | Transformer #OTT2474 located at 114 Flora isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
15226 | 2009 | 10 | 7 | 0.45139 |  | 83 | 26 | 19 | Florence | 4.16kV | UF06 | Transformer #X31189 located at 404 Mcleod isolated for crew to re-energize with a new service | Ottawa | Scheduled Outage | Construction
19414 | 2011 | 10 | 20 | 0.043056 |  | 5 | 24 | 291 | Florence DS | 4.16kV | UF06 | Af06 breaker opened up. No apparent cause. | Ottawa | Unknown/Other | No Apparent Cause
9498 | 2006 | 10 | 23 | 0.78125 |  | 260 | 4 | 1 | Florence | 4.16kV | UF06 | V273 @270 Cathrine was interupted by a broken cutout which was isolated for repairs | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11937 | 2008 | 1 | 14 | 0.59375 |  | 40 | 7 | 11 | Florence | 4.16kV | UF07 | Transformer #OTT190 located at 264 Arlington Ave isolated to replace triplex service | Ottawa | Scheduled Outage | Preventive Maintenance
4712 | 2004 | 1 | 18 | 0.68611 |  | 760 | 559 | 214 | Florence | 4.16kV | UF07 | UF07 circuit interrupted at the request of the Ottawa F.D. in order to gain access with ladder truck to 308 Flora. Taps were cut & circuit was picked back up with all customers except Flora St between Percy & Bronson. When the Fire Department completed their work the circuit was again interrupted in order to restore Flora St customers. | Ottawa | Adverse Environment | Fire
9944 | 2007 | 1 | 18 | 0.40278 |  | 200 | 113 | 34 | Florence | 4.16kV | UF07 | Transformer #OTT3451 located at 196 James isolated due to installing new services | Ottawa | Scheduled Outage | Construction
4867 | 2004 | 3 | 7 | 0.3125 |  | 150 | 18 | 7 | Florence | 4.16kV | UF07 | Replaced overhead 3 phase transformer at Bronson & Arlington. | Ottawa | Scheduled Outage | Repair
4880 | 2004 | 3 | 12 | 0.39583 |  | 75 | 9 | 7 | Florence | 4.16kV | UF07 | Isolation of transformer OTT975 at 542 Bronson to upgrade new pole and relocate transformer | Ottawa | Scheduled Outage | Construction
4884 | 2004 | 3 | 13 | 0.21875 |  | 143 | 5 | 2 | Florence | 4.16kV | UF07 | P495 at Bronson and Arlington was isolated to transfer hardware. | Ottawa | Scheduled Outage | Construction
20433 | 2012 | 5 | 1 | 0.62292 |  | 18 | 2 | 6 | Florence | 4.16kV | UF07 | Transformer X31862 at 196 Arlington Ave. isolated to change overhead switch and arrestor | Ottawa | Scheduled Outage | Preventive Maintenance
10387 | 2007 | 5 | 8 | 0.53819 |  | 34 | 10 | 18 | Florence | 4.16kV | UF07 | Isolated Transformer OTT3453 at 197 James for service on secondary. | Ottawa | Scheduled Outage | Repair
20759 | 2012 | 6 | 13 | 0.32639 |  | 75 | 15 | 12 | Florence | 4.16kV | UF07 | Transformer #X31866 located at 243 Percy St opened up by crew to remove large tree limb from wires. | Ottawa | Tree Contacts | Tree Limb Fallen
20769 | 2012 | 6 | 13 | 0.64236 |  | 35 | 7 | 12 | Florence | 4.16kV | UF07 | Transformer X31866 at 243 Percy St. isolated to allow for reconnect after repairs required due to tree limb falling on service | Ottawa | Tree Contacts | Tree Limb Fallen
20775 | 2012 | 6 | 14 | 0.4375 |  | 20 | 4 | 12 | Florence | 4.16kV | UF07 | Isolated transformer X31529 at 254 Arlington Ave for a service upgrade | Ottawa | Scheduled Outage | Construction
19016 | 2011 | 8 | 25 | 0.39931 |  | 10 | 2 | 13 | Florence | 4.16kV | UF07 | Isolated transformer X30305 at 306 Flora St foe service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
11182 | 2007 | 8 | 29 | 0.57292 |  | 35 | 12 | 21 | Florence | 4.16kV | UF07 | Transformer #OTT837 located at 544 Bay St isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
9116 | 2006 | 9 | 3 | 0.73681 |  | 314 | 147 | 28 | Florence | 4.16kV | UF07 | defective 50kva transformer at 542 Maclaren was replaced. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11258 | 2007 | 9 | 6 | 0.38194 |  | 115 | 25 | 13 | FLORENCE | 13.2kV | UF07 | TRANSFORMER #X31151 AT 560 BAY ST ISOLATED TO ALLOW FOR PCB CHANGE | Ottawa | Scheduled Outage | Preventive Maintenance
9649 | 2006 | 11 | 13 | 0.47847 |  | 6 | 0 | 2 | Florence | 4.16kV | UF07 | Glenn Carswell opened Transformer at 540 McLaren to relocate Transformer to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
9796 | 2006 | 12 | 5 | 0.42361 |  | 120 | 20 | 10 | Florence | 4.16kV | UF07 | Lee Piper isolated TRF. # 3457 @ 333 James to work on sec. Buss | Ottawa | Scheduled Outage | Preventive Maintenance
9808 | 2006 | 12 | 7 | 0.38889 |  | 26 | 3 | 7 | Florence | 4.16kV | UF07 | Isolated transformer OTT0185 at 190 Arlington Ave to replace triplex service | Ottawa | Scheduled Outage | Preventive Maintenance
4695 | 2004 | 1 | 12 | 0.38819 |  | 122 | 4 | 2 | Florence | 4.16kV | UF08 | connections renewed on a triangle at 505 Gladstone ID #4842 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7815 | 2006 | 1 | 17 | 0.42569 |  | 49 | 20 | 25 | Florence | 4.16kV | UF08 | Mano had a transformer out at 442 Mcleod to remove the old transformer | Ottawa | Scheduled Outage | Repair
7874 | 2006 | 2 | 1 | 0.39583 |  | 30 | 2 | 3 | Florence | 4.16kV | UF08 | Trans OTT1832 isolated at 320 Daly St in order to change over plant | Ottawa | Scheduled Outage | Preventive Maintenance
10024 | 2007 | 2 | 13 | 0.71875 |  | 75 | 11 | 9 | Florence | 4.16kV | UF08 | Mark Brown isolated TRF.4363 @ 487 mcleod to install new triplex | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6282 | 2005 | 3 | 15 | 0.034722 |  | 40 | 7 | 11 | Flourence | 4.16kV | UF08 | Transformer cut out replaced for supply to 546 Gladstone. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14060 | 2009 | 3 | 15 | 0.91667 |  | 40 | 3 | 5 | Florence | 4.16kV | UF08 | Tx X30315 at 187 Flora was opened to make repairs to defective secondary conductors. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12157 | 2008 | 3 | 19 | 0.84583 |  | 87 | 13 | 9 | Florence | 4.16kV | UF08 | Fuses in the transformer & at the street found blown on K1075 @ 309 Frank St. Due to snow & ice falling off the roof of the building. | Ottawa | Adverse Weather | Snow
15833 | 2010 | 3 | 23 | 0.58333 |  | 57 | 8 | 8 | FLORENCE | 4.16kV | UF08 | Transformer X30331 at 604 Gladstone Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
4937 | 2004 | 3 | 25 | 0.67014 |  | 75 | 44 | 35 | Florence | 4.16kV | UF08 | The UF08 cable pole fuse at Gladstone and Bank on white phase blew due a blown arrestor at the cable riser at Frank & Bank. The cable was meggered OK, arrestor replaced and switch refused to restore. Approx 25 customers on Frank East of bank affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6384 | 2005 | 4 | 7 | 0.55069 |  | 15 | 45 | 180 | Florence | 4.16kV | UF08 | Circuit was opened to allow crew to make emergency repairs to overhead. Hot line clamp was holding conductor togeather at Bank and Frank. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16046 | 2010 | 5 | 5 | 0.93958 |  | 19 | 1 | 3 | Florence | 4.16kV | UF08 | Crew opened overhead transformer X31042 @ 437 Catherine to repair sparking hotline clamp. | Ottawa | Defective Equipment
18104 | 2011 | 5 | 6 | 0.46042 |  | 67 | 42 | 38 | Florence | 4.16kV | UF08 | Transformer bus at TV3906 @ 457 Mceaod was isolated to allow contractor to perform Fire pump breaker maintenance. 38 customers were affected. Florence (UF08) | Ottawa | Scheduled Outage
20511 | 2012 | 5 | 14 | 0.85833 |  | 226 | 1086 | 851 | Florence | 4.16kV | UF08 | At 19:27 System Operators dumped UF08 breaker via SCADA at the request of the Ottawa Fire Chief due to proximity of flames to conductor. 851 customers affected for 69 mins and 41 remained off for an additional 157 mins. Florence UF08 ID# 20511 | Ottawa | Adverse Environment | Fire
20908 | 2012 | 7 | 2 | 0.42292 |  | 112 | 4 | 2 | Florence | 4.16kV | UF08 | Transformer #X30309 located at 273 Flora St opened up due to defective switch | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
7161 | 2005 | 8 | 18 | 0.60069 |  | 25 | 8 | 20 | Florence | 4.16kV | UF08 | Transformer #OTT4358 located at 442 Mcleod isolated due to replacing a service for an upgrade | Ottawa | Scheduled Outage | Construction
11103 | 2007 | 8 | 20 | 0.42014 |  | 25 | 8 | 18 | Florence | 4.16kV | UF08 | Transformer #OTT4367 located at 520 Mcleod isolated due to triplex changed from #4 to 1/0 | Ottawa | Scheduled Outage | Preventive Maintenance
15102 | 2009 | 9 | 14 | 0.47917 |  | 36 | 14 | 24 | FLORENCE | 4.16kV | UF08 | Transformer X31862 across from 85 Arling Ave isolated to allow for connection of a new service | Ottawa | Scheduled Outage
15182 | 2009 | 9 | 28 | 0.38889 |  | 145 | 24 | 10 | FLORENCE | 4.16kV | UF08 | transformer X31852 at 99 Arlington isolated to allow for transformer upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
4288 | 2003 | 10 | 17 | 0.39167 |  | 81 | 24 | 18 | Florence | 4.16kV | UF08 | Transformer at Lyon & Gladstone was opened to check connections on service feeding 505 gladstone. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
15346 | 2009 | 11 | 2 | 0.63958 |  | 35 | 1 | 1 | Florence | 4.16kV | UF08 | 4 kv vault V372 at 360 Frank isolated to confirm cause of 2 dip fuses blowing was a squirrel contact. 4 kv supply cables meggared good & the vault was restored. | Ottawa | Foreign Interference | Animal
13441 | 2008 | 10 | 28 | 0.75486 |  | 15 | 50 | 198 | Florence | 4.16kV | UF10 | Adverse Weather - High winds and blowing snow Gladstone, O'Connor and MacLaren area | Ottawa | Adverse Weather | Snow
13443 | 2008 | 10 | 29 | 0.82292 |  | 310 | 66 | 226 | Florence | 4.16kV | UF10 | There is a signal phase down on Maclaren, so to make repairs the UF10 circuit had to be open and isolated to make repairs. | Ottawa | Adverse Weather | Wind
4420 | 2003 | 11 | 9 | 0.40069 |  | 193 | 16 | 5 | Florence | 4.16kV | UF10 | P390 at 340 MacLaren was isolated to transfer plant to new pole. | Ottawa | Scheduled Outage | Construction
11723 | 2007 | 11 | 16 | 0.50347 |  | 25 | 5 | 11 | Florence | 4.16kV | UF10 | Transformer #OTT4075 located at 275 Maclaren isolated due to pole transfer | Ottawa | Scheduled Outage | Construction
5980 | 2004 | 12 | 5 | 0.39028 |  | 118 | 4 | 2 | Florence | 4.16kV | UF10 | V490 at 335 MacLaren & P390 at 340 MacLaren were taken out of service on a scheduled outage to relocate the line back to normal at the pole. | Ottawa | Scheduled Outage | Construction
16093 | 2010 | 5 | 17 | 0.39861 |  | 42 | 840 | 1200 | Florence | 4.16kV | UFT2 | S360 to UFT2 transfomer opened causing outage to UF05, UF06 & UF08 circuits cause unknown at this time. | Ottawa | Unknown/Other | No Apparent Cause
19722 | 2011 | 12 | 15 | 0.39444 |  | 14 | 342 | 1464 | Florence | 4.16kV | UFT2 | S-230 feeding UFT2 transfomer at Florence Sub was tripped inadvertently due to incorrect wiring at the T2 gas reset push button. | Ottawa | Unknown/Other | No Apparent Cause
7845 | 2006 | 1 | 23 | 0.68403 |  | 31 | 5 | 9 | Vaughan | 4.16kV | UG02 | Isolated transformer 65A3A-0017 at 160 Crichton St to reconnect triplex service | Ottawa | Scheduled Outage | Repair
4881 | 2004 | 3 | 12 | 0.70486 |  | 59 | 2 | 2 | Vaughan | 4.16kV | UG02 | Isolation of transformer OTT4068 at 55 Mackay St to replace connections on service. | Ottawa | Scheduled Outage | Repair
14092 | 2009 | 3 | 24 | 0.36875 |  | 142 | 12 | 5 | Vaughan | 4.16kV | UG02 | At 8:51 trans at 166 Chrichton St failed due to a defective trans cutout.. It was replaced and power restored | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14093 | 2009 | 3 | 24 | 0.98333 |  | 34 | 3 | 6 | Vaughn | 4.16kV | UG02 | Transformer X29629 supplying customers on Crichton, Avon & McKay was opened to install a temporary service to supply a secondary pedastal in the rear of 170 Crichton. Defective U/G service will be replaced at a later time. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14095 | 2009 | 3 | 24 | 0.98333 |  | 34 | 6 | 10 | VAUGHAN | 4.16kV | UG02 | Transformer X29269 at 170 Crichton St isolated to allow for installation of a temp service | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8115 | 2006 | 4 | 6 | 0.5 |  | 45 | 6 | 8 | Vaughan | 4.16kV | UG02 | Transformers OTT2036, OTT2038 & OTT1766 located behind 200 Crichton (Avon Lane & Dufferin) isolated due to transferring plant. | Ottawa | Scheduled Outage | Construction
15946 | 2010 | 4 | 16 | 0.36458 |  | 42 | 7 | 10 | VAUGHAN | 4.16kV | UG02 | Transformer X24657 at 35 MacKay isolated to disconnect/reconnect service to 11 Rideau Gate | Ottawa | Scheduled Outage | Construction
14207 | 2009 | 4 | 24 | 0.44444 |  | 50 | 4 | 5 | Vaughan | 4.16kV | UG02 | Isolated transformer X29269 at 1614 Avon Lane for service up-grade | Ottawa | Scheduled Outage | Construction
8220 | 2006 | 5 | 3 | 0.45486 |  | 70 | 4 | 3 | Vaughan | 4.16kV | UG02 | Isolated transformer OTT 6836 at 135 Acacia Ave to replace triplex services | Ottawa | Scheduled Outage | Preventive Maintenance
10643 | 2007 | 6 | 17 | 0.74514 |  | 5 | 0 | 3 | Vaughan | 4.16kV | UG02 | Transformer at cormer on Mackey and Thomas opened to allow replacement of hot line clamp | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6929 | 2005 | 7 | 14 | 0.0625 |  | 20 | 67 | 201 | Vaughan | 4.16kV | UG02 | UG02 & UG03 both tripped, reclosed & tripped again. Patrol revealed no evident problem. | Ottawa | Adverse Weather | Lightning
6949 | 2005 | 7 | 14 | 0.0625 |  | 20 | 67 | 201 | Vaughan | 4.16kV | UG02 | Circuit opened during lightening storm. Circuit went through reclose sequence. No reports of any problems. Circuit closed back in via scada. | Ottawa | Adverse Weather | Lightning
16467 | 2010 | 7 | 14 | 0.375 |  | 95 | 10 | 6 | Vaughan | 4.16kV | UG02 | Transformer #X29552 located at 14 Crichton St opened by crew to replace triplex | Ottawa | Scheduled Outage | Construction
16768 | 2010 | 8 | 18 | 0.48958 |  | 20 | 8 | 23 | Vaughan | 4.16kV | UG02 | Isolated transformer X29284 at 372 MacKay St for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
11218 | 2007 | 8 | 30 | 0.36597 |  | 85 | 4 | 3 | Vaughan | 4.16kV | UG02 | Replaced switch to transformer OTT4065 at 187 MacKay St | Ottawa | Adverse Weather | Lightning
16963 | 2010 | 9 | 18 | 0.64167 |  | 101 | 12 | 7 | Vaughan | 4.16kV | UG02 | defective hotline clamp caused transformer X29551 to open at School lane at rear of 79 McKay. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
4193 | 2003 | 10 | 1 | 0.48194 |  | 19 | 108 | 341 | Augusta |  | UG02 | Transformer at 227 Wurtemburg was opened to remove conductor. | Ottawa | Scheduled Outage | Preventive Maintenance
7755 | 2005 | 12 | 22 | 0.98403 |  | 303 | 15 | 3 | Vaughan | 4.16kV | UG02 | Blown transformer at Rideau Gate and Thomas | Ottawa | Unknown/Other | No Apparent Cause
19907 | 2012 | 1 | 26 | 0.53125 |  | 62 | 4 | 4 | Vaughan | 4.16kV | UG03 | S22162 at 160 Dufferin was opened to allow crew to repair load break elbow. | Ottawa | Scheduled Outage | Repair
4931 | 2004 | 3 | 23 | 0.92222 |  | 92 | 18 | 12 | Vaughan | 4.16kV | UG03 | Blown cut-out caused outages on Dufferin Rd. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8099 | 2006 | 4 | 3 | 0.39583 |  | 20 | 0 | 1 | Vaughan | 4.16kV | UG03 | Rick Wallace had a transformer out at 64 Dufferin , OTT2037 to set up for a pole change | Ottawa | Unknown/Other | Preventive Maintenance
15955 | 2010 | 4 | 19 | 0.4375 |  | 39 | 4 | 6 | Vaughan | 4.16kV | UG03 | K696 @ 172 Dufferin Rd Isolated @ 10:30 for secondary service work | Ottawa | Scheduled Outage | Preventive Maintenance
14237 | 2009 | 4 | 25 | 0.80903 |  | 125 | 383 | 184 | Vaughan | 4.16kV | UG03 | UG03 breaker tripped during high winds, heavy rain & lightning. No permanent problem was found. UG05, UG06 & UG00 tripped at same time. | Ottawa | Adverse Weather
20582 | 2012 | 5 | 25 | 0.78542 |  | 39 | 194 | 299 | Vaughn | 4.16kV | UG03 | Lightning storm and high winds caused circuit to open. Vaughn (UG03) ID#20582 | Ottawa | Adverse Weather | Wind
5419 | 2004 | 7 | 1 | 0.62292 |  | 298 | 914 | 184 | UG | 4.16kV | UG03 | Cct opened during storm, patrol found no problems. | Ottawa | Adverse Weather | Lightning
6930 | 2005 | 7 | 14 | 0.0625 |  | 128 | 393 | 184 | Vaughan | 4.16kV | UG03 | UG02 & UG03 both tripped, reclosed & tripped again. Patrol revealed no evident problem. | Ottawa | Adverse Weather | Lightning
6950 | 2005 | 7 | 14 | 0.0625 |  | 128 | 390 | 183 | Vaughan | 4.16kV | UG03 | Circuit opened during lightening storm.. Circuit closed back in via scada.Circuit re-opened due to low amp readings on R&W phases.Circuit was patrolled with no problems found. Circuit closed back in all customers restored. | Ottawa | Adverse Weather
9161 | 2006 | 9 | 8 | 0.7375 |  | 245 | 751 | 184 | Langs | 4.16kV | UG03 | Lightening strike on overhead caused original outage, suspected cable fault caused UG03 breaker to be unable to close, transferred to UG00 | Ottawa | Lightning | Direct Strike
13205 | 2008 | 9 | 8 | 0.63611 |  | 10 | 31 | 184 | Vaughan | 4.16kV | UG03 | UG03 circuit Auto tripped. Rain and High wind storm in effect. Breaker closed by system and held. | Ottawa | Adverse Weather | Rain
9847 | 2006 | 12 | 15 | 0.39583 |  | 113 | 9 | 5 | Vaughan | 4.16kV | UG03 | Transformer located at 28 Lisgar Rd in Rockcliffe isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
12031 | 2008 | 2 | 10 | 0.20278 |  | 106 | 2 | 1 | VAUGHAN | 4.16kV | UG04 | Broken switch insulator found at 90 Julianna Rd. Crew repaired switch & restored power to 1 affected customer. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20016 | 2012 | 2 | 14 | 0.54167 |  | 210 | 49 | 14 | Vaughan | 4.16kV | UG04 | Isolated transformer X23593 at 9 Jolliet Ave to transfer hydro plant | Ottawa | Scheduled Outage | Construction
17592 | 2011 | 2 | 16 | 0.45694 |  | 17 | 9 | 31 | VAUGHAN | 4.16kV | UG04 | Transformer X24727 at 22 Ste. Cecile St isolated to move transformer and move 2 services (at #22 & #24) | Ottawa | Scheduled Outage | Construction
14182 | 2009 | 4 | 16 | 0.42083 |  | 24 | 4 | 10 | VAUGHAN | 4.16kV | UG04 | transf X23577 at 457 Oakhill Rd isolated to allow for a service upgrade | Ottawa | Scheduled Outage | Repair
14242 | 2009 | 4 | 26 | 0.12014 |  | 189 | 734 | 233 | Vaughan | 4.16kV | UG04 | UG04 circuit was isolated along with UG00 & UG06 to make temporary repairs to pole at NE corner of Mackay & Beechwood. | Ottawa | Defective Equipment
18999 | 2011 | 8 | 22 | 0.35417 |  | 210 | 56 | 16 | Vaughan | 4.16kV | UG04 | Transformer #X23110 located at 7 Acacia Ave opened by crew due to pole change | Ottawa | Scheduled Outage | Construction
19000 | 2011 | 8 | 22 | 0.35417 |  | 210 | 21 | 6 | Vaughan | 4.16kV | UG04 | Transformer #X23588 located at 17 Acacia Ave opened by crew due to pole change | Ottawa | Scheduled Outage | Construction
19003 | 2011 | 8 | 23 | 0.35417 |  | 150 | 28 | 11 | Vaughan | 4.16kV | UG04 | Isolated transformer X23586 at 37 Acacia Ave to replace pole | Ottawa | Scheduled Outage | Construction
19005 | 2011 | 8 | 24 | 0.35417 |  | 220 | 48 | 13 | Vaughan | 4.16kV | UG04 | At 8:30 S25330 was open to allow black and Mac to perform work. 13 customers were affected for 220 mins. Vaughan UG04 ID# 19005 | Ottawa | Scheduled Outage
4028 | 2003 | 9 | 6 | 0.77222 |  | 218 | 18 | 5 | UG | 4.16kV | UG04 | TP2101 supplying a strip mall @ 160 Beechwood was isolated for upgrade from 150 to 225kva & for replacement of secondary conductors. | Ottawa | Scheduled Outage | Construction
19284 | 2011 | 9 | 29 | 0.29167 |  | 10 | 0 | 3 | Vaughan | 4.16kV | UG04 | Transformer #X24726 located at 12 Ste. Cecile opened by crew due to re-framing the poles | Ottawa | Scheduled Outage | Construction
19285 | 2011 | 9 | 29 | 0.29861 |  | 20 | 9 | 26 | Vaughan | 4.16kV | UG04 | Transformer #X24727 located at 34 Ste. Cecile opened by crew due to re-framing the poles | Ottawa | Scheduled Outage
19286 | 2011 | 9 | 29 | 0.29861 |  | 20 | 1 | 4 | Vaughan | 4.16kV | UG04 | Transformer #X24728 located at 44 Ste. Cecile opened by crew due to re-framing the poles | Ottawa | Scheduled Outage
19311 | 2011 | 10 | 3 | 0.35417 |  | 235 | 51 | 13 | Vaughan | 4.16kV | UG04 | Transformers X23587 @ 12 Acacia and X23585 @ 451 Green were isolated to allow crew to rearrange plant. | Ottawa | Scheduled Outage | Construction
19312 | 2011 | 10 | 3 | 0.36111 |  | 30 | 2 | 3 | Vaughan | 4.16kV | UG04 | Transformers X24743 @ 208 Beechwood and X24741 @ 204 beechwood were isolated to allow crew to rearrange plant. | Ottawa | Scheduled Outage | Construction
9715 | 2006 | 11 | 23 | 0.42708 |  | 35 | 9 | 16 | Vaughan | 4.16kV | UG04 | Isolated and replaced transformer 65A3D-0156 at 105 Beechwood Ave (PVB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
19677 | 2011 | 12 | 4 | 0.375 |  | 260 | 39 | 9 | VAUGHAN | 4.16kV | UG04 | Transformers X24926 on Kilborn Ave at Reeves Cres isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
19679 | 2011 | 12 | 4 | 0.375 |  | 90 | 4 | 3 | Vaughan | 4.16kV | UG04 | Transformer X21673 on Kilborn Ave. at Reeves Cres. isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
19680 | 2011 | 12 | 4 | 0.375 |  | 390 | 39 | 6 | Vaughan | 4.16kV | UG04 | Transformers X29370 on Kilborn Ave at Reeves Cres isolated to allow for pole change | Ottawa | Scheduled Outage
9835 | 2006 | 12 | 13 | 0.41319 |  | 60 | 8 | 8 | Vaughan | 4.16kV | UG04 | Isolated and replaced transformer at 241 Beechwood (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
20102 | 2012 | 3 | 3 | 0.57431 |  | 92 | 239 | 156 | Vaughan | 4.16kV | UG05 | Branch across 3 phases at 470 Acacia caused the UG05 breaker to auto reclose then trip. | Ottawa | Adverse Weather | Wind
15805 | 2010 | 3 | 16 | 0.20833 |  | 202 | 57 | 35 | Vaughan | 4.16kV | UG05 | Switch feeding K1295 was defective. Switch feeding K1299 was opened for working clearance. | Ottawa | Defective Equipment
6414 | 2005 | 4 | 15 | 0.41667 |  | 45 | 2 | 3 | Vaughan | 4.16kV | UG05 | Trans at 771 Acacia Lane replaced due to leaking | Ottawa | Scheduled Outage | Repair
8167 | 2006 | 4 | 19 | 0.59653 |  | 43 | 6 | 8 | Vaughan | 4.16kV | UG05 | Primary connection on the switch to transformer 65A3D-0719 at 7 Springfield burnt off causing an outage to 8 customers | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14238 | 2009 | 4 | 25 | 0.80903 |  | 625 | 1875 | 180 | Vaughan | 4.16kV | UG05 | UG05 breaker tripped during high winds, heavy rain & lightning. Circuit was left off pending investiagtion of wire down report on Acacia which turned out to be Bell wires. Patrol did not reveal any problems. UG03, UG06 & UG00 tripped at same time. | Ottawa | Adverse Weather
5246 | 2004 | 6 | 2 | 0.30556 |  | 80 | 3 | 2 | Vaughan | 4.16kV | UG05 | Squirrel contact caused transformer at 444 Springfield to open. | Ottawa | Foreign Interference | Animal
6744 | 2005 | 6 | 15 | 0.85417 |  | 450 | 30 | 4 | UG | 4.16kV | UG05 | A transformer at 300 Acacia ave was replaced after it was damaged by lightning. | Ottawa | Lightning | Direct Strike
5420 | 2004 | 7 | 1 | 0.62292 |  | 263 | 1148 | 262 | UG | 4.16kV | UG05 | 2 phases of primary came down on Beechwood ave. | Ottawa | Adverse Weather | Lightning
3783 | 2003 | 7 | 25 | 0.45833 |  | 33 | 9 | 16 | Vaughan | 4.16kV | UG05 | K1295 at 20 Springfield was isolated to make repairs to a faulted underground service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10960 | 2007 | 7 | 28 | 0.65208 |  | 126 | 40 | 19 | Vaughan | 4.16kV | UG05 | Crew replaced Broken switch on UG05 o/h feeding K1299 @ 24 Springfield. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
12999 | 2008 | 8 | 4 | 0.88611 |  | 74 | 1 | 1 | Vaughan | 4.16kV | UG05 | Replaced broken switch feeding transformer X23147 at 11 Crescent Rd | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11194 | 2007 | 8 | 29 | 0.76319 |  | 187 | 561 | 180 | Vaughan | 4.16kV | UG05 | UG05 opened via SCADA, wires knocked down due to fallen tree, circuit isolated, repaired by on-call crews and restored. | Ottawa | Tree Contacts | Tree Limb Fallen
4102 | 2003 | 9 | 19 | 0.93056 |  | 3 | 9 | 180 | Vaugan | 4.16kV | UG05 | Circuit was momentarily interupted by SCADA to clear a tree from the primary overhead. | Ottawa | Adverse Weather | Wind
9288 | 2006 | 9 | 24 | 0.44583 |  | 117 | 351 | 180 | Vaughan | 4.16kV | UG05 | With high winds the UG05 O/H circuit in the vaughan area slapped together, circuit patrolled nothing found,breaker closed via scada. | Ottawa | Adverse Weather | Wind
4757 | 2004 | 2 | 3 | 0.35972 |  | 172 | 29 | 10 | UG | 4.16kV | UG06 | An o/h Tx was opened for tree removal by the City at 457 Oakhill | Ottawa | Tree Contacts
12242 | 2008 | 4 | 6 | 0.83958 |  | 62 | 18 | 17 | Vaughan | 4.16kV | UG06 | LargeTree Limbs fallen on secondary bus at 158 Laval St. Transformer 24736 opened to clear Limbs off secondary bus, very close to primary | Ottawa | Tree Contacts | Tree Limb Fallen
12243 | 2008 | 4 | 6 | 0.91319 |  | 14 | 4 | 17 | Vaughn | 4.16kV | UG06 | Transformer 24736 opened to allow City of Ottawa crew to remove limb off secondary bus. | Ottawa | Tree Contacts | Tree Limb Fallen
14239 | 2009 | 4 | 25 | 0.80903 |  | 119 | 520 | 262 | Vaughan | 4.16kV | UG06 | UG06 breaker tripped during high winds, heavy rain & lightning.Problem was determined to be a broken pole at Mackay & Beechwood. Circuit was re-energized until pole repairs could be made and circuit had to be isolated. UG03, UG05 & UG00 tripped at same time. | Ottawa | Adverse Weather
14240 | 2009 | 4 | 26 | 0.12014 |  | 194 | 847 | 262 | Vaughan | 4.16kV | UG06 | UG06 circuit was isolated along with UG00 & UG04 to make temporary repairs to pole at NE corner of Mackay & Beechwood. | Ottawa | Defective Equipment
12367 | 2008 | 4 | 30 | 0.58333 |  | 120 | 12 | 6 | Vaughan | 4.16kV | UG06 | Isolated transformer X24737 at 172 Laval St to install a new pole | Ottawa | Scheduled Outage | Construction
18066 | 2011 | 4 | 30 | 0.55486 |  | 139 | 28 | 12 | Vaughan | 4.16kV | UG06 | White phase overhead radial line section was isolated to allow crew to remove a tree. 12 customers were affected for minutes. Vaughan (UG06) ID# 18066 | Ottawa | Adverse Weather | Wind
12402 | 2008 | 5 | 6 | 0.37847 |  | 105 | 44 | 25 | VAUGHAN | 4.16kV | UG06 | Transformer X24933 at 70 Laval isolated to allow for a pole change | Ottawa | Scheduled Outage | Preventive Maintenance
12403 | 2008 | 5 | 6 | 0.49653 |  | 139 | 25 | 11 | VAUGHAN | 4.16kV | UG06 | TRANSFORMER X24738 AT 130 LAVAL ST ISOLATED TO ALLOW FOR POLE CHANGE | Ottawa | Scheduled Outage | Preventive Maintenance
12404 | 2008 | 5 | 6 | 0.62361 |  | 47 | 16 | 21 | VAUGHAN | 4.16kV | UG06 | TRTANSFORMER #X24932 AT 74 LAVAL ISOLATED TO ALLOW FOR POLE CHANGE | Ottawa | Scheduled Outage
12413 | 2008 | 5 | 7 | 0.40833 |  | 68 | 31 | 27 | VAUGHAN | 4.16kV | UG06 | TRANSFORMER #X24735 AT 163 LAVAL ISOLATED TO ALLOW FOR POLE CHANGE | Ottawa | Scheduled Outage | Preventive Maintenance
18242 | 2011 | 5 | 29 | 0.27014 |  | 161 | 13 | 5 | Vaughan | 4.16kV | UG06 | HOL Crews isolated TP4229 at 16 Beechwood to transfer primary feed to a new pole | Ottawa | Scheduled Outage
18243 | 2011 | 5 | 29 | 0.42361 |  | 105 | 9 | 5 | Vaughan | 4.16kV | UG06 | Crews isolated transformer X24936 as part of pole replacement project | Ottawa | Scheduled Outage
12537 | 2008 | 6 | 3 | 0.37361 |  | 212 | 32 | 9 | Kilborn | 4.16kV | UG06 | Transformer #27699 at 621 Thessaly Circ isolated to allow for transformer change | Ottawa | Scheduled Outage | Repair
12538 | 2008 | 6 | 3 | 0.375 |  | 60 | 14 | 14 | Vaughan | 4.16kV | UG06 | Transformer X24739 at 145 Laval St isolated to allow for pole change | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12539 | 2008 | 6 | 3 | 0.57292 |  | 79 | 18 | 14 | VAUGHAN | 4.16kV | UG06 | Transformer # X24739 at 145 Laval isolated a second time to allow completion of pole replacement | Ottawa | Scheduled Outage | Repair
12544 | 2008 | 6 | 4 | 0.38889 |  | 160 | 72 | 27 | VAUGHAN | 4.16kV | UG06 | Transformer # 24735 at 158 Laval isolated to allow for system upgrade | Ottawa | Scheduled Outage | Construction
12545 | 2008 | 6 | 4 | 0.57708 |  | 84 | 38 | 27 | VAUGHAN | 4.16kV | UG06 | Transformer X24735 at 174 Laval isolated to allow for system upgrade | Ottawa | Scheduled Outage | Construction
12546 | 2008 | 6 | 4 | 0.57708 |  | 84 | 25 | 18 | VAUGHAN | 4.16kV | UG06 | Transformer X24736 at 181 Laval isolated to allow for system upgrade | Ottawa | Scheduled Outage | Construction
12615 | 2008 | 6 | 12 | 0.41667 |  | 60 | 18 | 18 | Vaughan | 4.16kV | UG06 | Transformer #X24736 located at 184 Laval St isolated for an upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
20764 | 2012 | 6 | 13 | 0.33333 |  | 220 | 26 | 7 | Vaughan | 4.16kV | UG06 | Transformer X24508 at 9 Coupal Street isolated to allow for pole change | Ottawa | Scheduled Outage | Construction
20765 | 2012 | 6 | 13 | 0.33333 |  | 220 | 37 | 10 | Vaughan | 4.16kV | UG06 | Transformer X65A3D-0485 (X29287) at 16 Lenore Place isolated to allow for pole change | Ottawa | Scheduled Outage | Repair
20766 | 2012 | 6 | 13 | 0.33333 |  | 220 | 44 | 12 | Vaughan | 4.16kV | UG06 | Transformer K00943 at 20 Lenore Place isolated to allow for pole change | Ottawa | Scheduled Outage | Repair
3595 | 2003 | 6 | 22 | 0.91042 |  | 123 | 61 | 30 | Vaughan | 4.16kV | UG06 | Lead to a fused cutout was burnt off at Coupal & Lenore . 24/7 repaired lead and restored all customers. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18542 | 2011 | 6 | 28 | 0.375 |  | 215 | 108 | 30 | Vaughn UG | 4.16kV | UG06 | A section of o/h line on Coupal & Lenore was isolated to upgrade plant. | Ottawa | Scheduled Outage | Construction
18778 | 2011 | 7 | 20 | 0.40625 |  | 76 | 13 | 10 | Vaughan | 4.16kV | UG06 | Transformer isolated on Waylings to remove trees on lines. | Ottawa | Tree Contacts | Inadequate Trimming
8894 | 2006 | 8 | 1 | 0.64583 |  | 150 | 125 | 50 | Vaughan | 4.16kV | UG06 | Transformer isolated at 9 Lenore Place due to lightning (broken cut out) | Ottawa | Lightning | Direct Strike
16749 | 2010 | 8 | 16 | 0.39236 |  | 31 | 2 | 3 | VAUGHAN | 4.16kV | UG06 | Transformer X24359 at 203 North River Rd isolated to connect new u/g service | Gloucester | Scheduled Outage | Construction
19134 | 2011 | 9 | 11 | 0.625 |  | 257 | 47 | 11 | Vaughan | 4.16kV | UG06 | Transformer X24937 at 8 Beechwood Ave isolated for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
19138 | 2011 | 9 | 12 | 0.35417 |  | 208 | 24 | 7 | Vaughan | 4.16kV | UG06 | Transformer #X23277 located at 43 Landry St opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
9497 | 2006 | 10 | 23 | 0.75694 |  | 325 | 108 | 20 | Vaughan | 4.16kV | UG06 | Transformer #P00347 located at 16 Beechwood isolated to replace a leaker as per PC10A#101 | Ottawa | Scheduled Outage | Repair
9567 | 2006 | 10 | 31 | 0.46597 |  | 103 | 12 | 7 | Vaughan | 4.16kV | UG06 | Transformer located at 178 Laval isolated for PCB transformer replacement. PC10A #1179. | Ottawa | Scheduled Outage | Preventive Maintenance
9579 | 2006 | 11 | 1 | 0.53819 |  | 84 | 8 | 6 | Vaughan | 4.16kV | UG06 | Isolated and replaced transformer 23588 at 19 Acacia (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
10050 | 2007 | 2 | 22 | 0.40625 |  | 223 | 59 | 16 | Vaughn | 4.16kV | UG07 | Interruption on Acacia to all removal of tree from overhead, Petrachuck | Ottawa | Scheduled Outage | Preventive Maintenance
4832 | 2004 | 2 | 27 | 0.67014 |  | 70 | 13 | 11 | UG | 4.16kV | UG07 | A broken cut-out was replaced feeding Tx OTT5913 at 169 Springfield | Ottawa | Defective Equipment
10183 | 2007 | 3 | 27 | 0.39583 |  | 154 | 18 | 7 | Vaughan | 4.16kV | UG07 | At 09:30 trans at 269 Roger Ave in order to transfer sec cond to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
8138 | 2006 | 4 | 12 | 0.375 |  | 105 | 24 | 14 | Vaughan | 4.16kV | UG07 | Removed transformer OTT5913 at the rear of 169 Springfield from service and installed new transformer in front of this address | Ottawa | Scheduled Outage | Construction
8212 | 2006 | 5 | 1 | 0.375 |  | 270 | 50 | 11 | Vaughan | 4.16kV | UG07 | Transformer #OTT3961 located at 12 Lindenlea isolated due to installing a new pole | Ottawa | Scheduled Outage | Construction
10422 | 2007 | 5 | 15 | 0.73264 |  | 130 | 4 | 2 | Vaughn | 13.2kV | UG07 | UG07 cables section from S15065 to V500 and V728 on Maple Lane isolated to replace V500 with new TP4270. | Ottawa | Scheduled Outage | Construction
9700 | 2006 | 11 | 22 | 0.375 |  | 190 | 28 | 9 | Vaughan | 4.16kV | UG07 | Transformer #OTT5492 located at 25 Rockcliffe isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
9701 | 2006 | 11 | 22 | 0.375 |  | 190 | 28 | 9 | Vaughan | 4.16kV | UG07 | Transformer #OTT5492 located at 25 Rockcliffe isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
9789 | 2006 | 12 | 3 | 0.52431 |  | 255 | 8 | 2 | Vaughan | 4.16kV | UG07 | V500 at 50 Maple and V728 at 140 Springfield was isolated for a contractor to replace a customer ownwed pole on primary line feeding both premises | Ottawa | Scheduled Outage | Construction
19863 | 2012 | 1 | 19 | 0.4375 |  | 45 | 9 | 12 | Vaughn UG | 4.16kV | UG09 | Transformer X23266 at 94 Maple Lane isolated to allow for tree trimming | Ottawa | Scheduled Outage | Preventive Maintenance
19865 | 2012 | 1 | 19 | 0.65764 |  | 103 | 21 | 12 | Vaughan | 4.16kV | UG09 | Trans X23266 at 94 Maple Ln was isolated in order to trim trees | Ottawa | Tree Contacts | Tree Limb Fallen
6378 | 2005 | 4 | 6 | 0.39236 |  | 125 | 10 | 5 | Vaughan | 4.16kV | UG09 | Opened transformer OTT3775 at 24 Lambton Ave to allow removal of a tree | Ottawa | Scheduled Outage | Preventive Maintenance
8477 | 2006 | 6 | 12 | 0.87847 |  | 35 | 3 | 5 | Vaughan | 4.16kV | UG09 | Isolated transformer OTT 2187 at 17 Elmdale Ave to replace connections on the secondary services | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8497 | 2006 | 6 | 16 | 0.46875 |  | 100 | 8 | 5 | Vaughan | 4.16kV | UG09 | Transformer #OTT2187 located at 17 Elmdale isolated to change all connections on the pole | Ottawa | Scheduled Outage | Repair
18856 | 2011 | 7 | 29 | 0.95139 |  | 345 | 29 | 5 | Vaughn | 4.16kV | UG09 | Tree contact caused the cut out on transformer X23581 to blow. Lincoln (TD14) ID#18856. | Ottawa | Tree Contacts
9098 | 2006 | 8 | 30 | 0.54861 |  | 50 | 5 | 6 | Vaughn | 4.16kV | UG09 | Denis Martin opened xfmr OTT2188 at 5 Elmdale to reinstall a service that had been ripped down by a tree | Ottawa | Loss of Supply
19276 | 2011 | 9 | 28 | 0.41806 |  | 158 | 79 | 30 | Vaughan | 4.16kV | UG09 | S25813 red phase switch was isolated to allow tree trimmers to remove trees from primary services | Ottawa | Scheduled Outage | Preventive Maintenance
9397 | 2006 | 10 | 6 | 0.47917 |  | 35 | 5 | 8 | Vaughan | 4.16kV | UG09 | Transformer #OTT2188 located at 5 Elmdale Ave was isolated to run a new triplex service. PC10A #126 | Ottawa | Scheduled Outage | Preventive Maintenance
15230 | 2009 | 10 | 7 | 0.84028 |  | 36 | 0 | 9 | VAUGHAN | 4.16kV | UG09 | Transformer at 236 Rideau Terrace isolated to make repairs to broken lead on white phase | Ottawa | Scheduled Outage | Repair
11514 | 2007 | 10 | 14 | 0.64653 |  | 45 | 5 | 7 | Vaughan | 4.16kV | UG09 | Replace a burnt hot line clamp at transformer OTT2185 at 11 ELMDALE. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9589 | 2006 | 11 | 2 | 0.52083 |  | 58 | 7 | 7 | Vaughan | 4.16kV | UG09 | Mike Gruich isolated trf. K613 to change PCB trf. @ 14 Maple Lane | Ottawa | Scheduled Outage
9693 | 2006 | 11 | 21 | 0.39931 |  | 135 | 18 | 8 | Vaughan | 4.16kV | UG09 | Transformer #OTT2185 located at 5 Ashbury isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
15627 | 2010 | 1 | 7 | 0.53819 |  | 40 | 11 | 16 | Vaughan | 4.16kV | UG10 | Transformer #X29239 located at 280 Crichton isolated to install 2 new triplex services | Ottawa | Scheduled Outage | Construction
15924 | 2010 | 4 | 11 | 0.81528 |  | 98 | 21 | 13 | VAUGHAN | 4.16kV | UG10 | Defective switch on transformer X29242 was replaced. | Ottawa | Defective Equipment
14297 | 2009 | 5 | 4 | 0.70139 |  | 7 | 1 | 5 | Vaughan | 4.16kV | UG10 | Transformer #X29564 located at 58 Queen Victoria St isolated to replace hot line clamp | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14387 | 2009 | 5 | 21 | 0.38542 |  | 45 | 12 | 16 | Vaughan | 4.16kV | UG10 | At 09:30 trans at 284 CRICHTON ST OTTAWA was isolated in order to upgrade sec service | Ottawa | Scheduled Outage | Preventive Maintenance
14409 | 2009 | 5 | 25 | 0.49653 |  | 60 | 5 | 5 | VAUGHAN | 4.16kV | UG10 | Transformer X29559 at 70 Union Street isolated to install new 400 amp service | Ottawa | Scheduled Outage | Construction
20610 | 2012 | 5 | 25 | 0.8 |  | 1052 | 228 | 13 |  | 4.16kV | UG10 | Transformer X29242 at 169 Chrichton opened due to tree contact caused by wind storm on May 25, 2012 | Ottawa | Tree Contacts | Tree Fallen
3561 | 2003 | 6 | 12 | 0.40764 |  | 88 | 6 | 4 | Vaughan | 4.16kV | UG10 | Tree fell into a service off of the transformer at 62 John St in Ottawa dumping the transformer. | Ottawa | Tree Contacts | Tree Fallen
10772 | 2007 | 7 | 1 | 0.90278 |  | 92 | 368 | 240 | Vaughn | 4.16kV | UG10 | UG10 Breaker opened by System to make repairs to primary wires down on Stanley at Union. | Ottawa | Defective Equipment
8714 | 2006 | 7 | 13 | 0.38889 |  | 55 | 9 | 10 | Vaughn | 4.16kV | UG10 | Mano Della Vadova disconnected transformer A2288-11 to install a new service | Ottawa | Scheduled Outage | Repair
5587 | 2004 | 7 | 31 | 0.23056 |  | 337 | 592 | 240 | Vaughan | 4.16kV | UG10 | Vehicle accident broke a guy wire causing UG10 wires to come down and UG10 to open and lock out. Damaged area cut clear to restore power to most customers. | Ottawa | Foreign Interference | Vehicle
7069 | 2005 | 8 | 5 | 0.91875 |  | 294 | 511 | 240 | Vaughan | 4.16kV | UG10 | UG10 tripped when vehicle hit guy wire at Vanier Pkwy & St Patrick. Phases wrapped around each other at Beechwood & Vanier Pkwy. Section isolated with switches at Beechwood and main line restored. One 600V xfmr off until new pieces sleeved in. | Ottawa | Foreign Interference | Vehicle
7214 | 2005 | 8 | 25 | 0.67431 |  | 26 | 5 | 12 | Vaughn | 4.16kV | UG10 | Transformer at 105 Stanley was isolated to reconnect triplex service | Ottawa | Scheduled Outage | Repair
13157 | 2008 | 8 | 27 | 0.38889 |  | 19 | 7 | 23 | VAUGHAN | 4.16kV | UG10 | Transformer K941 located at Thomas St & Stanley Ave isolated to allow for meter base repairs | Ottawa | Scheduled Outage | Construction
19124 | 2011 | 9 | 9 | 0.44097 |  | 15 | 2 | 10 | Vaughan | 4.16kV | UG10 | At 10:35 crews isolated Transformers X24656 and X29265 at 120 Keffer St to straighten leaning pole. Vaughan UG10 ID# 19124 | Ottawa | Scheduled Outage
15177 | 2009 | 9 | 27 | 0.96319 |  | 8 | 20 | 151 | Vaughan | 4.16kV | UG10 | Vaughan UG10 feeder auto trip when vehicle hit a pole at Beechwood and Vanier Pkwy. | Ottawa | Foreign Interference | Vehicle
13403 | 2008 | 10 | 21 | 0.5625 |  | 25 | 1 | 3 | VAUGHAN | 4.16kV | UG10 | Transformer X29559 at 44 Crichton St isolated to allow for load transfer | Ottawa | Scheduled Outage | Preventive Maintenance
9525 | 2006 | 10 | 27 | 0.50347 |  | 100 | 17 | 10 | Vaughan | 4.16kV | UG10 | At 12:05 trans at 158 Stanley St was isolated in order to replace trans for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9526 | 2006 | 10 | 27 | 0.51389 |  | 89 | 16 | 11 | Vaughan | 4.16kV | UG10 | At 12:20 trans at 133 Stanley St was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
4613 | 2003 | 12 | 17 | 0.44861 |  | 40 | 10 | 15 | Vaughn | 4.16kV | UG10 | transformer @ 280 Crichton open to replace connections at transformer.15 customers interrupted. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10114 | 2007 | 3 | 12 | 0.52778 |  | 50 | 10 | 12 | Vaughan | 4.16kV | UG11 | At 12:40 trans OTT3444 at 61 Ivy Cres was isolated for pole change | Ottawa | Scheduled Outage | Repair
10165 | 2007 | 3 | 23 | 0.38958 |  | 174 | 58 | 20 | Vaughan | 4.16kV | UG11 | Bruce Kerfoot isolated 2 TRF.'s @ 133 to 159 Ivy to install new poles | Ottawa | Scheduled Outage | Preventive Maintenance
10184 | 2007 | 3 | 27 | 0.38542 |  | 150 | 22 | 9 | Vaughan | 4.16kV | UG11 | Transformer #OTT3437 located at 145 Ivy isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
7068 | 2005 | 8 | 4 | 0.91875 |  | 71 | 114 | 96 | Vaughan | 4.16kV | UG11 | Tripped when vehicle hit guy wire at Vanier Pkwy & St Patrick. Patrolled and restored | Ottawa | Foreign Interference | Vehicle
18902 | 2011 | 8 | 10 | 0.40625 |  | 145 | 60 | 25 | Vaughn UG | 4.16kV | UG11 | A section of UG11 o/h line on Crichton & Electric ave was isolated to replace a pole. | Ottawa | Scheduled Outage | Construction
18937 | 2011 | 8 | 15 | 0.35417 |  | 210 | 42 | 12 | Vaughn | 4.16kV | UG11 | Transformer at 12 and 14 Electric St isolate to transfer services from old line and transformers to new Hydro plant. | Ottawa | Scheduled Outage | Construction
19484 | 2011 | 10 | 27 | 0.4375 |  | 200 | 83 | 25 | Vaughan | 4.16kV | UG11 | Trans X29236 at 211 Ivy Crescent was isolated in order to transfer plants due to upgrades | Ottawa | Scheduled Outage | Preventive Maintenance
9646 | 2006 | 11 | 13 | 0.37778 |  | 120 | 34 | 17 | Vaughan | 4.16kV | UG11 | PCB trf. Change @29 Ivy trf. # 3442 | Ottawa | Scheduled Outage | Preventive Maintenance
9980 | 2007 | 2 | 1 | 0.41667 |  | 77 | 10 | 8 | Vaughan | 13.2kV | UG12 | Isolated and replaced transformer at 116 Park Rd (PCB oil) | Ottawa | Scheduled Outage
12068 | 2008 | 2 | 21 | 0.14028 |  | 228 | 11 | 3 | Vaughan | 4.16kV | UG12 | At 3:22am, customer at 255 Soper Drive called in reporting no power. 24-7 crew dispatched to discover that K01231 at 247 Soper Drive had blown. On call crew dispatched to replace transformer, 3 customers affected for 288 min. ID#12068. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6292 | 2005 | 3 | 16 | 0.39583 |  | 75 | 12 | 10 |  | 4.16kV | UG12 | Tony Taylor had transformer out at 324 Manor to change a pole | Ottawa | Scheduled Outage | Preventive Maintenance
14243 | 2009 | 4 | 26 | 0.20208 |  | 1354 | 4326 | 250 | Vaughan | 4.16kV | UG12 | UG12 brekaer tripped (A/R/A) for trees on primary & taking primary down on Lisgar Rd & Manor Ave. Damaged sections were cut free & part of the circuit was restored. Forestry & line crews completed repairs to damaged sections later in the day. | Ottawa | Adverse Weather
14355 | 2009 | 5 | 14 | 0.52917 |  | 82 | 5 | 4 | Vaughan | 4.16kV | UG12 | Transformer #K1296 located at 771 Acacia Lane isolated due to inadequate tree trimming | Ottawa | Tree Contacts | Inadequate Trimming
14740 | 2009 | 7 | 13 | 0.56667 |  | 117 | 14 | 7 | Vaughan | 4.16kV | UG12 | S25179 white phase failed apparently due to blown lightning arrestor at transformer pole X29217. Arrestor cleared and circuit re-energized from S25179 at Lisgar and Buena Vista, Rockcliffe area | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3933 | 2003 | 8 | 24 | 0.30556 |  | 76 | 4 | 3 | Vaughn | 4.16kV | UG12 | Squirrel caused transformer to open feeding three customers on Spring field and Beauna vista. | Ottawa | Foreign Interference | Animal
11211 | 2007 | 8 | 29 | 0.76389 |  | 720 | 360 | 30 | Vaughn | 4.16kV | UG12 | Lisgar Rd North of Buena Vista tree has been removed from overhead wire and repairs made to 2 poles power restored. Single phase white fuse blown. | Ottawa | Tree Contacts | Tree Limb Fallen
15060 | 2009 | 9 | 6 | 0.29792 |  | 211 | 21 | 6 | Vaughan | 4.16kV | UG12 | Replaced broken switch feeding transformer X29406 at 294 Manor Ave | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4035 | 2003 | 9 | 8 | 0.48611 |  | 135 | 9 | 4 | Vaughan | 4.16kV | UG12 | Steve Fisher from Black & McDonald reports a transformer at 125 Kinua isolated , and same replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4051 | 2003 | 9 | 11 | 0.33333 |  | 150 | 2 | 1 | Vaughn | 4.16kV | UG12 | Pole replaced by Contractor Black and MacDonald. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4076 | 2003 | 9 | 16 | 0.54167 |  | 197 | 13 | 4 | UG | 4.16kV | UG12 | An o/h Tx @ 39 Buena Vista was opened while pole replacement work took place. | Ottawa | Scheduled Outage | Construction
11410 | 2007 | 9 | 28 | 0.30069 |  | 92 | 6 | 4 | Vaughan | 4.16kV | UG12 | Crew found fuse blown at transformer OTT4505 at 170 Minto Pl caused by squirrel | Ottawa | Foreign Interference | Animal
4192 | 2003 | 10 | 1 | 0.57778 |  | 14 | 58 | 250 | UG | 4.16kV | UG12 | Scada indicated cct. UG12 tripped. Circuit was patrolled & L.Piper reports pigeon found dead outside Vaughan Sub under the overhead. Reclosure was blocked with H/O. H/O was cleared with crew, and circuit breaker UG12 was closed and circuit held. | Ottawa | Foreign Interference | Bird
11451 | 2007 | 10 | 3 | 0.40417 |  | 180 | 12 | 4 | Vaughan | 4.16kV | UG12 | At 09:42 trans at 375 Minto Place was isolated to upgrade the service | Ottawa | Scheduled Outage | Preventive Maintenance
15525 | 2009 | 12 | 17 | 0.47569 |  | 20 | 2 | 5 | Vaughan | 4.16kV | UG12 | Isolated transformer X23352 at 80 Mackinnon Rd for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
8182 | 2006 | 4 | 23 | 0.09375 |  | 105 | 1187 | 809 | Vaughan | 4.16kV | UGT3 | Pole hit at Vanier Parkway and Beechwood caused guys to contact circuits, UG06, UG10, and UG11 A/R, UGT3 tripped, UG10 opened and locked out | Ottawa | Foreign Interference | Vehicle
5905 | 2004 | 11 | 19 | 0.59236 |  | 189 | 885 | 836 | Vaughan | 13.2kV | UGT3 | UG12 auto reclosed under fault wich caused UGT3 breaker to open. UG09, UG10, UG11, UG12 acb's were opened. UGT3 was closed and then UG09, UG10, UG11 circuiits were restoered. UG12 was left out until cause of outage was determined. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4532 | 2003 | 11 | 28 | 0.92569 |  | 257 | 1826 | 810 | Vaughan | 4.16kV | UGT3 | Vehicle accident at the corner of Vanier Parkway and Beechwood Ave. hitting a guy pole on the south west corner breaking the span guys which tangled with UG10 overhead. UG10 was isolated for repairs and UG09, UG11, and UG12 loads were restored when the vehicle was cleared. | Ottawa | Foreign Interference | Vehicle
17847 | 2011 | 4 | 7 | 0.35972 |  | 202 | 44 | 13 | Bayswater | 4.16kV | UJ02 | At 08:38 transformer X31566 at 17 Fairmont Avenue was isolated to allow crew to reconfigure plant. 13 customers were affected for 202 minutes. Bayswater (UJ02) ID# 17847 | Ottawa | Scheduled Outage
17848 | 2011 | 4 | 7 | 0.35972 |  | 187 | 6 | 2 | Bayswater | 4.16kV | UJ02 | At 08:38 transformer X31728 at 31 Fairmont Avenue was isolated to allow crew to reconfigure plant. 2 customers were affected for 187 minutes. Bayswater (UJ02) ID# 17848 | Ottawa | Scheduled Outage
18098 | 2011 | 5 | 5 | 0.35417 |  | 261 | 57 | 13 | Bayswater | 4.16kV | UJ02 | Isolated transformer X31566 at 20 Fairmont for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
16193 | 2010 | 6 | 4 | 0.37778 |  | 303 | 146 | 29 | Bayswater | 4.16kV | UJ02 | P217 at 29 Spadina isolated to allow crew to replace leaking transformer. | Ottawa | Scheduled Outage | Preventive Maintenance
16245 | 2010 | 6 | 10 | 0.5 |  | 35 | 9 | 15 | BAYSWATER | 4.16kV | UJ02 | Transformer X30186 at 166 Bayswater isolated to allow for tree trimming | Ottawa | Scheduled Outage | Preventive Maintenance
11180 | 2007 | 8 | 29 | 0.38542 |  | 120 | 56 | 28 | Bayswater | 4.16kV | UJ02 | Isolated and replaced transformer OTT2297 at 45 Fairmont Ave | Ottawa | Scheduled Outage | Preventive Maintenance
11181 | 2007 | 8 | 29 | 0.38194 |  | 110 | 11 | 6 | Bayswater | 4.16kV | UJ02 | Isolated and replaced transformer OTT2287 at 120 Fairmont Ave | Ottawa | Scheduled Outage | Preventive Maintenance
9133 | 2006 | 9 | 7 | 0.4375 |  | 45 | 10 | 14 | Bayswater | 4.16kV | UJ02 | Bill Edwards opened xfmr @ 82 Irving to transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
9139 | 2006 | 9 | 7 | 0.53819 |  | 95 | 6 | 4 | Bayswater | 4.16kV | UJ02 | Bill Edwards opened transformer #55D1B-0490 at 36 Irving and changed a delta. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9282 | 2006 | 9 | 22 | 0.41458 |  | 153 | 20 | 8 | Bayswater | 4.16kV | UJ02 | Transformer located at 56 Irving isolated for a pole change. PC10 #804 | Ottawa | Scheduled Outage | Repair
9359 | 2006 | 10 | 2 | 0.44444 |  | 110 | 9 | 5 | Bayswater | 4.16kV | UJ02 | Transformer located at 38 Irving Ave isolated to allow for pole change. PC10A#807 | Ottawa | Scheduled Outage | Construction
9393 | 2006 | 10 | 5 | 0.6875 |  | 170 | 17 | 6 | Bayswater | 4.16kV | UJ02 | AT 16:30 trans at 37 Irvine St was isolated in order to replace pole | Ottawa | Scheduled Outage | Preventive Maintenance
9424 | 2006 | 10 | 13 | 0.41667 |  | 122 | 69 | 34 | Bayswater | 4.16kV | UJ02 | Isolated transformer 55D1B-0820at 22 Spadina Ave to install new pole | Ottawa | Scheduled Outage | Construction
9446 | 2006 | 10 | 17 | 0.375 |  | 62 | 14 | 14 | Bayswater | 4.16kV | UJ02 | Transformer #54D1B-0205 located at 82 Fairmont isolated to transfer secondary | Ottawa | Scheduled Outage | Construction
5920 | 2004 | 11 | 23 | 0.38611 |  | 229 | 57 | 15 | Bayswater | 4.16kV | UJ02 | Transformer P217 @ 29 Spadina was isolated for the transfer of hydro plant. | Ottawa | Scheduled Outage | Repair
13710 | 2008 | 12 | 7 | 0.27014 |  | 4520 | 301 | 4 | BAYSWATER | 4.16kV | UJ02 | Pole mount Transformer was isoalted due to 2nd alarm fire at 72 Spadina. Transformer located on pole X30191 ESA require prior to power being restored, Caution Tag on transformer | Ottawa | Adverse Environment | Fire
6067 | 2004 | 12 | 16 | 0.52083 |  | 90 | 36 | 24 | Bayswater | 4.16kV | UJ02 | Transferred overhead services at 62 Bayswater | Ottawa | Scheduled Outage | Preventive Maintenance
11887 | 2007 | 12 | 27 | 0.2 |  | 117 | 23 | 12 | Bayswater | 4.16kV | UJ02 | Fuse fell open at 228 Bayswater Dr, Ottawa. Patrolled circuit, nothing found. Closed back in and holding. | Ottawa | Unknown/Other
15651 | 2010 | 1 | 14 | 0.19097 |  | 53 | 12 | 46 | Bayswater |  | UJ03 | Smoke from the fire at 173 Preston made it difficult to see which was the transformer cut out to X26296, a single phase line switch was opened along with the cutout and reclosed when the cutout was verified. | Ottawa | Adverse Environment | Fire
19881 | 2012 | 1 | 24 | 0.36458 |  | 15 | 7 | 27 | Bayswater | 4.16kV | UJ03 | Transformers #X30588 and X26675 located at 890 and 880 Somerset St W opened by crew to put new taps on the transformers. | Ottawa | Scheduled Outage | Construction
19919 | 2012 | 1 | 30 | 0.31597 |  | 60 | 4 | 4 | Bayswater | 4.16kV | UJ03 | At 07:35 transformer X30591 at 838 Somerset Street West was isolated for the pole replacement program. 4 customers were affected for 60 minutes. Bayswater (UJ03) ID#19919 | Ottawa | Scheduled Outage
19975 | 2012 | 2 | 7 | 0.29167 |  | 230 | 115 | 30 | Baywater | 4.16kV | UJ03 | Isolated 3 transformers X30592 at 834 Somerset X30590 at 850 Somerset and X26675 at 880 Somerset St to replace poles | Ottawa | Scheduled Outage | Construction
20004 | 2012 | 2 | 13 | 0.47014 |  | 200 | 185 | 464 | Bayswater | 4.16kV | UJ03 | Transformer X34829 at 814 Somerset St W isolated for transfer of plant. While energizing transformer, UJ03 circuit opened due to faulty arrestors. | Ottawa | Scheduled Outage | Construction
20006 | 2012 | 2 | 13 | 0.64583 |  | 15 | 2 | 8 | Bayswater | 4.16kV | UJ03 | Isolated transformer X25591 at 91 Anderson St to install new pole | Ottawa | Scheduled Outage | Construction
20010 | 2012 | 2 | 14 | 0.33333 |  | 105 | 18 | 10 | Bayswater | 4.16kV | UJ03 | Transformer X30594 at 790 1/2 Somserset St W isolated by Black and Mac to transfer plant | Ottawa | Scheduled Outage | Construction
17722 | 2011 | 3 | 17 | 0.36875 |  | 349 | 12 | 2 | Bayswater | 4.16kV | UJ03 | Transformer X30596 at 765 Somerset St W isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
4930 | 2004 | 3 | 23 | 0.38194 |  | 116 | 4 | 2 | Bayswater | 4.16kV | UJ03 | 129 & 131 Loretta was interupted for transformer installation. | Ottawa | Unknown/Other | No Apparent Cause
8087 | 2006 | 3 | 31 | 0.42708 |  | 135 | 20 | 9 | Bayswater | 4.16kV | UJ03 | Isolated transformer 55D2A-0466 at 48 Laurel ave to replace pole | Ottawa | Scheduled Outage | Construction
20264 | 2012 | 4 | 2 | 0.40278 |  | 30 | 2 | 4 | Bayswater | 4.16kV | UJ03 | Isolated transformer X31803 at 125 Preston St to disconnect the service to 121 Preston St | Ottawa | Scheduled Outage | Emergency Services Request
20265 | 2012 | 4 | 2 | 0.40278 |  | 30 | 2 | 3 | Bayswater |  | UJ03 | Isolated 3 phase transformer X31804 at 121 Preston St to disconnect the 600v service to 121 Preston St | Ottawa | Scheduled Outage | Emergency Services Request
6368 | 2005 | 4 | 5 | 0 |  | 290 | 1334 | 276 | Bayswater | 4.16kV | UJ03 | UJ03 circuit was opened for the fire dept to fight fires at 807 and 876 Somerset. | Ottawa | Adverse Environment | Fire
20291 | 2012 | 4 | 6 | 0.48958 |  | 150 | 75 | 30 | Bayswater | 4.16kV | UJ03 | Trans X31802 at130 Anderson St was isolated in order to replace trans to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
15962 | 2010 | 4 | 20 | 0.38333 |  | 35 | 6 | 10 | BAYSWATER | 4.16kV | UJ03 | Transformer X26675 @ 882 Somerset opened @ 9:12 for secondary servicing | Ottawa | Scheduled Outage | Preventive Maintenance
5089 | 2004 | 5 | 2 | 0.61111 |  | 30 | 4 | 9 | Bayswater | 4.16kV | UJ03 | O/H transformer at 35 Laurel interrupted to repair defective 600 V service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8215 | 2006 | 5 | 2 | 0.38542 |  | 130 | 17 | 8 | Bayswater | 4.16kV | UJ03 | Transformer OTT 685 at 131 Balsam St was isolated and replaced due to being defective and causing part out to all the customers fed from it | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6510 | 2005 | 5 | 4 | 0.79167 |  | 285 | 86 | 18 | Bayswater | 4.16kV | UJ03 | Trans OTT5862 at 812 Somerset isolated to relocate equip to new poles | Ottawa | Scheduled Outage | Repair
16132 | 2010 | 5 | 25 | 0.38542 |  | 15 | 2 | 9 | Bayswater | 4.16kV | UJ03 | Isolated transformer X31807 at 25 Laurel St to replace connections on a secondary service | Ottawa | Scheduled Outage | Emergency Services Request
16164 | 2010 | 5 | 30 | 0.45486 |  | 69 | 7 | 6 | Bayswater | 4.16kV | UJ03 | Transformer X30597 opened to repair broken switch and down ground | Ottawa | Defective Equipment
16215 | 2010 | 6 | 7 | 0.44444 |  | 125 | 19 | 9 | Bayswater |  | UJ03 | Transformer #X31807 located at 22 Oak St opened by crew to change the cut out and re-do connections | Ottawa | Scheduled Outage | Construction
10897 | 2007 | 7 | 17 | 0.29167 |  | 110 | 28 | 15 | Bayswater | 4.16kV | UJ03 | At 07:00 trans at 153 Preston St was isolated in order to replace leaking trans | Ottawa | Scheduled Outage | Repair
8921 | 2006 | 8 | 3 | 0.63194 |  | 60 | 1 | 1 | Bayswater | 4.16kV | UJ03 | 4KV vault V723 @ 1050 somerset was isolated to change defective transformer. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11241 | 2007 | 9 | 4 | 0.39583 |  | 110 | 13 | 7 | BAYSWATER | 13.2kV | UJ03 | Transformer #OTT6677 AT 119 Willow isolated to allow for pcb change | Ottawa | Scheduled Outage | Construction
9127 | 2006 | 9 | 6 | 0.43056 |  | 145 | 19 | 8 | Bayswater |  | UJ03 | Lee Piper opened xfmr OTT686 at 133 Palsen to transfer plant | Ottawa | Scheduled Outage | Construction
4094 | 2003 | 9 | 19 | 0.52569 |  | 5 | 23 | 276 | UJ | 4.16kV | UJ03 | Scada indicated UJ03 circuit opened 4127kw load loss. Phoned police, they report all clear and closed UJ03 via scada and circuit held. It is a very windy day. Hurricane Isabelle hit mainland yesterday. | Ottawa | Adverse Weather | Wind
17239 | 2010 | 11 | 7 | 0.86111 |  | 12 | 8 | 40 | Bayswater | 4.16kV | UJ03 | Crew reported switch at the corner of Preston and Oak burning up and had to change it. | Ottawa | Defective Equipment
5879 | 2004 | 11 | 12 | 0.66597 |  | 361 | 132 | 22 | Bayswater | 4.16kV | UJ03 | The fire department requested the transformer 5011 be opened at 27 Poplar street because of fire at 15 Poplar. | Ottawa | Adverse Environment | Fire
9690 | 2006 | 11 | 20 | 0.4375 |  | 60 | 9 | 9 | Bayswater | 4.16kV | UJ03 | Isolated transformer 55D2A-0466 at 124 Breezhill Ave to replace service | Ottawa | Scheduled Outage | Preventive Maintenance
9846 | 2006 | 12 | 15 | 0.41181 |  | 97 | 11 | 7 | Bayswater | 4.16kV | UJ03 | Grg McMillan isolated Transformer at 50 Laurel to replace the transformer | Ottawa | Scheduled Outage | Preventive Maintenance
9897 | 2007 | 1 | 3 | 0.39583 |  | 222 | 44 | 12 | Bayswater | 4.16kV | UJ04 | At 09:30 trans at 109 Bayswater Ave was isolated in order to transfer plant on pole | Ottawa | Scheduled Outage | Preventive Maintenance
3219 | 2003 | 3 | 1 | 0.5 |  | 140 | 30 | 13 | Bayswater | 4.16kV | UJ04 | Broken cutout opened on transformer at 138 Bayswater. Reliability changed cutout and repired same. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6467 | 2005 | 4 | 26 | 0.66111 |  | 330 | 202 | 112 | Bayswater | 4.16kV | UJ04 | The UJ04 circuit was opened for a severe fire at 930 Gladstone. Crew installed overhead cuts and most of the circuit was picked up with the exclusion of four transformers. They were energized later after the fire dept was clear. The customer at 930 will remain out as bldg will probably be demolished. | Ottawa | Adverse Environment | Fire
5083 | 2004 | 5 | 1 | 0.38194 |  | 20 | 0 | 1 | Bayswater | 4.16kV | UJ04 | Overhead transformer at 950 Gladstone interrupted to repair underground service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6518 | 2005 | 5 | 6 | 0.91319 |  | 59 | 10 | 10 | Bayswater | 4.16kV | UJ04 | Switch to transfromer at the rear of 109 Bayswater was found broken crew replaced the switch and restored power | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16832 | 2010 | 8 | 29 | 0.67708 |  | 85 | 7 | 5 | Bayswater | 4.16kV | UJ04 | X31485 at 970 Gladstone was Isolated to allow crews to trim trees. 5 customers affected for 85 mintes. Bayswater (UJ04) ID #16832 | Ottawa | Tree Contacts | Inadequate Trimming
11261 | 2007 | 9 | 6 | 0.36111 |  | 201 | 37 | 11 | BAYSWATER | 13.2kV | UJ04 | TRANSFORMER #55D2A-0419 (X31486) AT 970 GLADSTONE AVE ISOLATED TO ALLOW FOR PCB CHANGE | Ottawa | Scheduled Outage | Preventive Maintenance
9411 | 2006 | 10 | 10 | 0.55208 |  | 60 | 8 | 8 | Bayswater | 4.16kV | UJ04 | Transformer located at 119 Gladstone isolated to allow pole change. PC10A #817 | Ottawa | Scheduled Outage
13380 | 2008 | 10 | 17 | 0.55833 |  | 3 | 2 | 50 | Bayswater | 4.16kV | UJ04 | While performing switching to transfer the UJ03 feeder to new 4 Kv metalclad breaker at Bayswater sub the UJK1Y1 breaker tripped interupting the UJ04 feeder. | Ottawa | Unknown/Other | No Apparent Cause
9479 | 2006 | 10 | 20 | 0.44444 |  | 60 | 9 | 9 | Bayswater | 4.16kV | UJ04 | Transformer located at 48 Laurel isolated to allow pole change. PC10A #816 | Ottawa | Scheduled Outage | Preventive Maintenance
9626 | 2006 | 11 | 9 | 0.44792 |  | 90 | 12 | 8 | Bayswater | 4.16kV | UJ04 | Isolated trf. To install new pole | Ottawa | Scheduled Outage | Preventive Maintenance
9632 | 2006 | 11 | 10 | 0.40972 |  | 55 | 18 | 20 | Bayswater | 4.16kV | UJ04 | At 09:50 trans at 142 Breezehill Ln was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
9634 | 2006 | 11 | 10 | 0.54167 |  | 39 | 5 | 8 | Bayswater | 4.16kV | UJ04 | At 13:00 trans at 141 Bayswater was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
9724 | 2006 | 11 | 24 | 0.50694 |  | 44 | 5 | 7 | Bayswater | 4.16kV | UJ04 | Isolated transformer 55D2A-0421 at 1008 Gladstone Ave for a service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
9854 | 2006 | 12 | 18 | 0.46528 |  | 105 | 35 | 20 | Bayswater | 4.16kV | UJ04 | Transformer #55D2A-0104 located at 127 Bayswater isolated due to pole changes | Ottawa | Scheduled Outage | Construction
15754 | 2010 | 2 | 27 | 0.92361 |  | 340 | 227 | 40 | Bayswater | 4.16kV | UJ05 | Scheduled outage. Crews required isolation on UJ05 to re-string 5 spans of O/H conductor and install switch S20218 | Ottawa | Scheduled Outage | Construction
15768 | 2010 | 3 | 4 | 0.35417 |  | 225 | 180 | 48 | Bayswater | 4.16kV | UJ05 | Transformer #X25496 located at 33 Rosemount Ave isolated for a conductor replacement job | Ottawa | Scheduled Outage | Construction
15783 | 2010 | 3 | 9 | 0.4375 |  | 140 | 112 | 48 | Bayswater | 4.16kV | UJ05 | isolated transformer X25496 at 33 Rosemount Ave to replace primary conductor | Ottawa | Scheduled Outage | Construction
8315 | 2006 | 5 | 18 | 0.47917 |  | 45 | 8 | 10 | Bayswater | 4.16kV | UJ05 | Glen opened transformer OTT5903 at 12 Spadina to put in a new pole. | Ottawa | Scheduled Outage | Construction
10498 | 2007 | 5 | 31 | 0.93056 |  | 90 | 346 | 231 | Bayswater | 4.16kV | UJ05 | Lightening strike on an overhead transformer at Wellington and Spadina caused a trip on the circuit, lightening arrestor blown and cut clear, transformer cut out refused, circuit re-energized | Ottawa | Lightning | Direct Strike
6959 | 2005 | 7 | 15 | 0.71736 |  | 23 | 89 | 231 | Bayswater | 4.16kV | UJ05 | Opened UJ05 circuit to allow crew to reserect downed primary at 1149 Gladstone. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6960 | 2005 | 7 | 15 | 0.73889 |  | 11 | 7 | 36 | Bayswater | 4.16kV | UJ05 | Trans OTT5555 isolated at 41 Rosemount to replace defective Sw and LLC | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14878 | 2009 | 7 | 29 | 0.71667 |  | 108 | 691 | 384 | Bayswater | 4.16kV | UJ05 | A tree has fallen on the O/H at 1161 Wellington taking down the O/H. | Ottawa | Tree Contacts | Tree Fallen
13046 | 2008 | 8 | 12 | 0.38889 |  | 298 | 79 | 16 | BAYSWATER | 4.16kV | UJ05 | Transformer X33863 at 28 Melrose Ave isolated to allow for installation of new secondary buss | Ottawa | Scheduled Outage | Repair
5721 | 2004 | 8 | 25 | 0.83333 |  | 155 | 8 | 1 | Playfiar | 4.16kV | UJ05 | Crews isolated 3 phase transformers at 453 Parkdale Ave. Outage affected 3 customers while crews replaced transformers. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11171 | 2007 | 8 | 28 | 0.53819 |  | 115 | 27 | 14 | Bayswater | 4.16kV | UJ05 | Isolated and replaced transformer OTT4412 at 61 Melrose Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
4140 | 2003 | 9 | 23 | 0.625 |  | 15 | 10 | 38 | Bayswater |  | UJ05 | Transformer at 37 Rosemount was opened to allow Bell Canada to perform pole testing | Ottawa | Scheduled Outage | Preventive Maintenance
9327 | 2006 | 9 | 27 | 0.5625 |  | 45 | 10 | 14 | Bayswater | 4.16kV | UJ05 | Transformer #OTT5903 located at 20 Spadina isolated due to pole change, PC10A#806 | Ottawa | Scheduled Outage | Construction
9384 | 2006 | 10 | 5 | 0.41667 |  | 120 | 12 | 6 | Bayswater | 4.16kV | UJ05 | Transformer located at 12 Spadina isolated to allow a pole change. PC10A #810 | Ottawa | Scheduled Outage | Preventive Maintenance
9440 | 2006 | 10 | 16 | 0.42708 |  | 135 | 16 | 7 | Bayswater | 4.16kV | UJ05 | Transformer located at 16 Spadina isolated to allow pole change. PC10A #819 | Ottawa | Scheduled Outage | Preventive Maintenance
7797 | 2006 | 1 | 11 | 0.6 |  | 56 | 13 | 14 | Bayswater | 4.16kV | UJ06 | Ice fell and pulled service down,trans OTT321 at 4 Eccles St opened up. Service cut clear, trans re-energized | Ottawa | Foreign Interference | Foreign Object
7798 | 2006 | 1 | 11 | 0.33333 |  | 20 | 5 | 14 | Bayswater | 4.16kV | UJ06 | Transformer OTT321 at 4 Eccles St was isolated to re-install triplex service | Ottawa | Scheduled Outage | Emergency Services Request
12099 | 2008 | 3 | 4 | 0.57986 |  | 20 | 3 | 10 | Bayswater | 4.16kV | UJ06 | Transformer #X31408 located at 10 Eccles isolated for repairs | Goulburn | Scheduled Outage | Repair
6369 | 2005 | 4 | 5 | 0 |  | 290 | 1208 | 250 | Bayswater | 4.16kV | UJ06 | UJ06 circuit was opened for fire dept to fight fire at 876 Somerset. | Ottawa | Adverse Environment | Fire
20323 | 2012 | 4 | 13 | 0.75347 |  | 114 | 2 | 1 | Bayswater | 4.16kV | UJ06 | V140 at 52 Bayswater Drive was isolated to allow crew to replace defective transformer in Vault. 1 customer affected. | Ottawa | Defective Equipment
10335 | 2007 | 4 | 26 | 0.41667 |  | 140 | 44 | 19 | Bayswater | 4.16kV | UJ06 | Isolated transformer 55D2A-0652 at 85 Eccles St to transfer hydro plant | Ottawa | Scheduled Outage | Preventive Maintenance
12369 | 2008 | 5 | 1 | 0.26042 |  | 195 | 26 | 8 | Bayswater | 4.16kV | UJ06 | Transformer X25503 at 14 Lebretton St, Ottawa isolated for pole replacement | Ottawa | Scheduled Outage
6707 | 2005 | 6 | 13 | 0.4375 |  | 413 | 7 | 1 | UJ | 4.16kV | UJ06 | P40 supplying 1040 Somerset was isolated to make repairs to a defective primary cable. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13621 | 2008 | 11 | 16 | 0.80417 |  | 145 | 179 | 209 | Bayswater | 13.2kV | UJ06 | UJ06 auto tripped due to a broken conductor on Louisa St. Crews responded and isolated the section of broken conductor at that time the UJ06 was picked back up. 1 transformer remained isolated while crews repaired the broken cable section. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4518 | 2003 | 11 | 26 | 0.42708 |  | 195 | 23 | 7 | Bayswater | 4.16kV | UJ06 | Transformer at 218 Lebreton transferred to a new pole. | Ottawa | Scheduled Outage | Construction
4528 | 2003 | 11 | 27 | 0.41667 |  | 105 | 12 | 7 | Bayswater | 4.16kV | UJ06 | Transformer at 218 Lebreton interrupted to install a new 600 V service. | Ottawa | Scheduled Outage | Construction
4568 | 2003 | 12 | 5 | 0.52778 |  | 110 | 42 | 23 | Bayswater | 4.16kV | UJ06 | Transfromer 55D2C-0488 at 48 Louisa to transfer everything to new pole. | Ottawa | Scheduled Outage | Construction
7756 | 2005 | 12 | 23 | 0.14653 |  | 103 | 9 | 5 | Bayswater | 4.16kV | UJ06 | Blown transformer fuse on Bell and Eccles, refused and held | Ottawa | Unknown/Other | No Apparent Cause
11874 | 2007 | 12 | 23 | 0.61042 |  | 281 | 36 | 10 | Bayswater | 4.16kV | UJ06 | At 2:39pm, UJ06 Red phase amps climbed up to 289.3A (HIGH STATE). Ottawa Fire department called in with a wire down on ground. 24-7 dispatched and John Streng reports triplex infront of 10 Eccles has burnt to ground from transformer, leaving 5 customers without power. On-Call crew called in to repair secondary service. 5-10 customers were affected . ID#11874. | Ottawa | Adverse Weather | Ice Storm
13911 | 2009 | 2 | 1 | 0.027083 |  | 62 | 11 | 11 | Bayswater | 4.16kV | UJ07 | A defective fuse that feeds transformer X24480 @ 18 Westmount. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15698 | 2010 | 2 | 2 | 0.38542 |  | 165 | 55 | 20 | Bayswater | 4.16kV | UJ07 | Transformer #X25494 located at 78 Rosemount Ave Ottawa isolated to prepare for conductor job | Ottawa | Scheduled Outage | Construction
12027 | 2008 | 2 | 8 | 0.91736 |  | 82 | 1 | 1 | Bayswater | 4.16kV | UJ07 | A City of Ottawa snow plow hit hydro pole and damaged cable feeding transformer K700 at 99 Rosemount in Ottawa. | Ottawa | Foreign Interference | Vehicle
17608 | 2011 | 2 | 18 | 0.87917 |  | 372 | 4656 | 751 | Bayswater | 4.16kV | UJ07 | Wires came down on Irving at Laurel on UJ07 also involving UJ00 | Ottawa | Adverse Weather | Wind
14010 | 2009 | 2 | 26 | 0.76736 |  | 10 | 1 | 6 | Bayswater | 4.16kV | UJ07 | Transformer #X30582 located at 1106 Somerset St W isolated to disc secondary dip at trans, damaged by snow plow | Ottawa | Foreign Interference | Vehicle
14048 | 2009 | 3 | 13 | 0.41806 |  | 28 | 3 | 6 | BAYSWATER | 4.16kV | UJ07 | transformer X30582 at 1106 Somerset isolated to allow for reconnect after repairs | Ottawa | Scheduled Outage | Repair
17858 | 2011 | 4 | 8 | 0.48125 |  | 72 | 2 | 2 | Bayswater | 4.16kV | UJ07 | 24/7 Crew Replaced defective switch at TX25479 at 27 Westmount Ave. 2 customers were affected for 72 minutes. Bayswater UJ07, 4.16 kV | Ottawa | Defective Equipment
17863 | 2011 | 4 | 9 | 0.55417 |  | 47 | 1 | 1 | Bayswater | 4.16kV | UJ07 | Transformer #X25479 located at 24 Westmount opened by crew to replace connections at pipe and pail. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8258 | 2006 | 5 | 9 | 0.53472 |  | 35 | 12 | 20 | Bayswater | 4.16kV | UJ07 | Isolated transformer 55D1B-0269 at 98 Rosemount to locate cable fault | Ottawa | Scheduled Outage | Repair
18140 | 2011 | 5 | 12 | 0.44444 |  | 35 | 5 | 9 | Bayswater | 4.16kV | UJ07 | Transformer X24480 @ 18 Westmount was isolated and put NIU by crew due to age of transformer. Customers fed off transfromer X24480 were transfered to transformer X25479. | Ottawa | Scheduled Outage
12593 | 2008 | 6 | 10 | 0.73333 |  | 92 | 423 | 276 | Bayswater | 4.16kV | UJ07 | High winds caused wires to slap and wrap. Wire unwrapped and breaker closed. | Ottawa | Adverse Weather | Wind
12609 | 2008 | 6 | 11 | 0.46667 |  | 1020 | 714 | 42 | Bayswater | 4.16kV | UJ07 | Transformer X31744 has failed; crew replaced 75KVA transformer. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12652 | 2008 | 6 | 15 | 0.82847 |  | 378 | 1739 | 276 | Bayswater | 4.16kV | UJ07 | 200 feet of Primary came down on Laurel between Irving and Spadina. Delays in restoration time, due to not having enough manpower. Primary replaced. UJ07 Breaker closed. | Ottawa | Adverse Weather | Lightning
16276 | 2010 | 6 | 17 | 0.37153 |  | 30 | 6 | 12 | Bayswater | 4.16kV | UJ07 | Replaced defective switch feeding transformer X30199 at 38 Spadina Ave | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
8607 | 2006 | 6 | 27 | 0.46181 |  | 55 | 10 | 11 | Bayswater | 4.16kV | UJ07 | Isolated transformer 55D1B-0247 at 1074 Gladstone Ave to replace triplex service | Ottawa | Foreign Interference | Vehicle
18677 | 2011 | 7 | 17 | 0.80903 |  | 894 | 11205 | 752 | Bayswater | 4.16kV | UJ07 | UJ07 O/H line that runs from Laurel to Somerset came down with the high winds causing UJ07 breaker to trip. | Ottawa | Adverse Weather | Wind
18766 | 2011 | 7 | 17 | 0.80694 |  | 178 | 2231 | 752 | Bayswater Sub | 4.16kV | UJ07 | UJ07 Tripped and was closed with success. | Ottawa | Adverse Weather | Wind
8895 | 2006 | 8 | 1 | 0.63542 |  | 175 | 32 | 11 | Bayswater | 4.16kV | UJ07 | Transformer #OTT2287 located at 123 Fairmont isolated due to broken cut out (lightning) | Ottawa | Lightning | Direct Strike
10983 | 2007 | 8 | 1 | 0.375 |  | 120 | 30 | 15 | Bayswater | 4.16kV | UJ07 | Transformer #55D1B-0485 located at 161 Irving Ave isolated to set new poles & transfer plant | Ottawa | Scheduled Outage | Construction
10984 | 2007 | 8 | 1 | 0.54375 |  | 207 | 52 | 15 | Bayswater | 4.16kV | UJ07 | Transformer #55D1B-0485 located at 161 Irving Ave isolated to set new poles & transfer plant | Ottawa | Scheduled Outage | Construction
16644 | 2010 | 8 | 4 | 0.65069 |  | 378 | 4265 | 677 | Bayswater | 4.16kV | UJ07 | UJ07 & UJ00 tripped during heavy rain & lightning. Conductor came down on both circuits in several places. Oncall made repairs to both circuits and restored power. | Ottawa | Lightning
9028 | 2006 | 8 | 23 | 0.24653 |  | 35 | 5 | 8 | Bayswater | 4.16kV | UJ07 | M. Byers reports transformer infront of 1109 Gladstone Ave, for fire department. | Ottawa | Adverse Environment | Fire
15253 | 2009 | 10 | 13 | 0.44444 |  | 30 | 5 | 10 | Bayswater | 4.16kV | uj07 | Isolated transformer X30284 at 172 Irving Ave for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
17364 | 2010 | 12 | 2 | 0.375 |  | 60 | 11 | 11 | Bayswater | 27.6/16kV | UJ07 | At 09:00 trans at 116 Fairmont Ave was isolated in order to install a new secondary service | Ottawa | Scheduled Outage | Preventive Maintenance
7719 | 2005 | 12 | 13 | 0.54653 |  | 123 | 12 | 6 | Bayswater | 4.16kV | UJ07 | Trans OTT2531 at 465 Parkdale Ave isolated in order to relocate trans to new pole | Ottawa | Scheduled Outage | Repair
13791 | 2008 | 12 | 24 | 0.72153 |  | 125 | 19 | 9 | Bayswater | 4.16kV | UJ07 | Circuit auto-reclosed once during freezing rain. Cause was determined to be a broken arrestor lead which made contact with an overhead transformer switch at 124 Fairmont. Arrestor was repaired & transformer refused. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13964 | 2009 | 2 | 12 | 0.023611 |  | 248 | 62 | 15 | Clifton | 4.16kV | UL02 | A Squirrels nest that was soaked from the rain caused transformer X35175 @ 249 Remic to open. | Ottawa | Foreign Interference | Foreign Object
15809 | 2010 | 3 | 16 | 0.44792 |  | 60 | 11 | 11 | CLIFTON | 4.16kV | UL02 | Transformer X33729 at 260 Remic Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
10181 | 2007 | 3 | 27 | 0.38542 |  | 45 | 4 | 5 | Clifton | 4.16kV | UL02 | Transformer located at 257 Remic isolated due to new service | Ottawa | Scheduled Outage | Construction
8187 | 2006 | 4 | 25 | 0.5625 |  | 40 | 8 | 12 | Clifton | 4.16kV | UL02 | Transformer #OTT2620 located at 10 Garland isolated to change connections at the pole & stand pipe | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20630 | 2012 | 5 | 28 | 0.91667 |  | 30 | 4 | 8 | Clifton | 4.16kV | UL02 | Transformer #X33893 located at 235 Latchford Rd opened by crew to re-sag wire. Secondary buss slapping together in the wind | Ottawa | Scheduled Outage | Construction
12616 | 2008 | 6 | 12 | 0.38194 |  | 170 | 17 | 6 | Clifton | 4.16kV | UL02 | Transformer #X34210 located at 204 Latchford isolated due to transferring plant. | Ottawa | Scheduled Outage | Preventive Maintenance
16607 | 2010 | 8 | 2 | 0.80556 |  | 150 | 2 | 1 | Clifton | 4.16kV | UL02 | V291 at 185 Clearview isolated at main breaker to allow contractor to replace defective fire pump feed outside of vault. | Ottawa | Defective Equipment
16932 | 2010 | 9 | 13 | 0.42014 |  | 57 | 10 | 10 | Clifton | 4.16kV | UL02 | Transformer #X34212 located at 283 Remic opened by crew for a streetlighting service | Ottawa | Scheduled Outage | Construction
11527 | 2007 | 10 | 16 | 0.375 |  | 125 | 21 | 10 | Clifton | 4.16kV | UL02 | Transformer #OTT5285 located at 125 Lanark isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
4149 | 2003 | 9 | 25 | 0.32639 |  | 2 | 20 | 600 | Clifton | 4.16kV | UL02,UL03,UL04 | Lighning strike caused ULK1Y1 breaker at clifton sub to open. UL02,UL03,UL04 circuit were on transfer on the ULK1Y1 breaker. ULK1Y1 has no recloser, and was closed by scada. | Ottawa | Lightning
14046 | 2009 | 3 | 12 | 0.34375 |  | 50 | 8 | 10 | CLIFTON | 4.16kV | UL03 | Transformer at 111 Patricia isolated to allow for transfer of plant | Ottawa | Scheduled Outage
4904 | 2004 | 3 | 16 | 0.34375 |  | 30 | 5 | 10 | Clifton | 4.16kV | UL03 | Transformer @ 368 Tweedsmuir was opened to change secondary services. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
6341 | 2005 | 3 | 31 | 0.36458 |  | 80 | 1 | 1 | Clifton | 4.16kV | UL03 | Replaced three switchers on dip pole for Transfomer #337 at 256 Richmond Rd | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14151 | 2009 | 4 | 7 | 0.58333 |  | 25 | 4 | 10 | CLIFTON | 4.16kV | UL03 | Transformer X33647 at 440 Evered Ave isolated to allow for repairs to blown arrestor | Ottawa | Scheduled Outage | Repair
8152 | 2006 | 4 | 14 | 0.39722 |  | 193 | 48 | 15 | Clifton | 4.16kV | UL03 | A section of UL03 o/h line on Patricia ave N. of Richmond rd was isolated to transfer plant to new poles. Customers were notified in advance. | Ottawa | Scheduled Outage | Construction
8208 | 2006 | 4 | 30 | 0.125 |  | 257 | 150 | 35 | Clifton | 4.16kV | UL03 | 3 single phase transformers & two 3 phase transformers were opened as scheduled to install new quadraplex service. Approx 35 customers in the Richmond Rd area of Westboro were interrupted, all customers were advised last week. | Ottawa | Scheduled Outage | Construction
5132 | 2004 | 5 | 11 | 0.57986 |  | 15 | 2 | 8 | Clifton | 4.16kV | UL03 | Transformer at 318 Richmond Rd interrupted to prepare for upcoming outage. | Ottawa | Scheduled Outage
5136 | 2004 | 5 | 13 | 0.27083 |  | 95 | 8 | 5 | UL | 4.16kV | UL03 | V633 @ 205 richmond rd was removed from service & new TP2357 at same location now in service. | Ottawa | Scheduled Outage | Construction
5180 | 2004 | 5 | 19 | 0.44514 |  | 5 | 0 | 1 | Clifton | 4.16kV | UL03 | The cable dip to Winks Store to P337 at 256 Richmond Rd was transferred from the road side circuit, UL03 , to field side, UL05. Crew was installing new pole and road is washing away around old pole. Needed more clearance to get new pole in quickly before they lose old pole. | Ottawa | Adverse Environment | Flooding
18336 | 2011 | 6 | 8 | 0.69861 |  | 181 | 688 | 228 | Clifton | 4.16kV | UL03 | UL03 circuit opened due to very Large tree on UL03 overhead at Clifton and Wilber. | Ottawa | Tree Contacts | Tree Fallen
8528 | 2006 | 6 | 19 | 0.79097 |  | 11 | 40 | 219 | Clifton | 4.16kV | UL03 | UL03 auto-reclosed twice before locking out. Breaker was closed manually from SCADA. | Ottawa | Lightning
18909 | 2011 | 8 | 11 | 0.41667 |  | 45 | 3 | 4 | Clifton | 4.16kV | UL03 | Transformer #X33562 located at 312 Parnell opened by crew for a service upgrade | Ottawa | Scheduled Outage | Construction
19234 | 2011 | 9 | 22 | 0.39583 |  | 165 | 28 | 10 | Clifton | 4.16kV | UL03 | Isolated transformer X33644 at 306 Clare St to install new secondary spun buss | Ottawa | Scheduled Outage | Construction
19278 | 2011 | 9 | 28 | 0.39583 |  | 170 | 28 | 10 | Clifton | 4.16kV | UL03 | Trans at 306 Clare St was isolated in order to transfer plant and sec conductors,, | Ottawa | Scheduled Outage | Preventive Maintenance
11536 | 2007 | 10 | 16 | 0.54167 |  | 112 | 22 | 12 | Clyde | 4.16kV | UL03 | At 13:00 trans at 656 Melbourne was isolated for PCB trans change | Ottawa | Scheduled Outage | Preventive Maintenance
15278 | 2009 | 10 | 20 | 0.25 |  | 136 | 23 | 10 | Cliffton | 4.16kV | UL03 | X34699 at 366 Tweedmuir isolated for Xfrm'r upgrade. 10 customers affected. Cliffton (UL03) ID #15278 | Ottawa | Scheduled Outage
12006 | 2008 | 2 | 4 | 0.55903 |  | 35 | 6 | 11 | Clifton | 4.16kV | UL04 | Transformer #OTT3890 located at 422 Island Park Dr isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
12014 | 2008 | 2 | 6 | 0.5 |  | 105 | 14 | 8 | Clifton | 4.16kV | UL04 | Transformer X34905 at 409 Leighton Terr was isolated to replace the pole | Ottawa | Scheduled Outage | Construction
12038 | 2008 | 2 | 12 | 0.57292 |  | 25 | 3 | 8 | Clifton | 4.16kV | UL04 | Isolated transformer X34905 at 409 Leighton Terr to replace the pole | Ottawa | Scheduled Outage | Construction
10022 | 2007 | 2 | 13 | 0.3125 |  | 340 | 227 | 40 | Clifton | 4.16kV | UL04 | Radial line on Mulvihill St isolated for pole replacement. | Ottawa | Scheduled Outage | Preventive Maintenance
17585 | 2011 | 2 | 15 | 0.44097 |  | 25 | 3 | 8 | Clifton | 4.16kV | UL04 | xfmr X32169 AT 474 Dawson open for approx. 45 mins to allow for service upgrade - all custs notified - will also take in some houses on Bevan | Ottawa | Scheduled Outage | Construction
10071 | 2007 | 2 | 27 | 0.41667 |  | 168 | 11 | 4 | Cliton | 4.16kV | UL04 | At 10:00 trans OTT4031 at 153 Mulvihill Ave was isolated in order to transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
10075 | 2007 | 2 | 28 | 0.41667 |  | 197 | 13 | 4 | Clifton | 4.16kV | UL04 | AT 10:00 trans OTT4031 at 149 Mulvihill Ave in order to transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
18025 | 2011 | 4 | 29 | 0.45694 |  | 7 | 3 | 22 | Clifton | 4.16kV | UL04 | S13987 @ 226 Byron was opened by crew by error, human element. 22 customer were affected. Clifton UL04. | Ottawa | Human Element | Switching Errors
18337 | 2011 | 6 | 8 | 0.69861 |  | 181 | 1252 | 415 | Clifton | 4.16kV | UL04 | UL04 circuit opened due to very Large tree on UL04 overhead at Clifton and Wilber. | Ottawa | Tree Contacts
8532 | 2006 | 6 | 19 | 0.79097 |  | 11 | 45 | 248 | Clifton | 4.16kV | UL04 | UL04 auto-reclosed twice before locking out. Breaker was closed manually from SCADA. | Ottawa | Lightning
11245 | 2007 | 9 | 4 | 0.82847 |  | 72 | 10 | 8 | Clifton | 4.16kV | UL04 | Replaced broken fuse on transformer OTT4696 at 485 Kirkwood Ave | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11313 | 2007 | 9 | 15 | 0.23056 |  | 48 | 6 | 8 | Clifton | 4.16kV | UL04 | Squirell contact caused a blown cutout at transformer OTT4696 located at 161 Nora St. Transformer refused and 8 customers restored. | Ottawa | Foreign Interference | Animal
13255 | 2008 | 9 | 18 | 0.40278 |  | 25 | 2 | 6 | Clifton | 4.16kV | UL04 | Transformer #OTT3426 located at 451 Brennan isolated to replace blown lightning arrestor | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4124 | 2003 | 9 | 22 | 0.44792 |  | 15 | 1 | 5 | Clifton | 4.16kV | UL04 | Transformer at 502 Bevan was opened to allow Bell Canada to perform testing. | Ottawa | Scheduled Outage
4125 | 2003 | 9 | 22 | 0.47222 |  | 15 | 2 | 8 | Clifton | 4.16kV | UL04 | Transformer at 501 Bevan was opened to allow Bell Canada to perform testing. | Ottawa | Scheduled Outage
4126 | 2003 | 9 | 22 | 0.47222 |  | 15 | 1 | 5 | Clifton | 4.16kV | UL04 | Transformer at 494 Dawson was opened to allow Bell Canada to perform testing. | Ottawa | Scheduled Outage
9332 | 2006 | 9 | 28 | 0.33681 |  | 105 | 26 | 15 | Clifton | 4.16kV | UL04 | Isolated transformer OTT6578 at 118 Wesley Ave to install new pole | Ottawa | Scheduled Outage | Construction
9357 | 2006 | 10 | 2 | 0.46181 |  | 25 | 4 | 9 | Clifton | 4.16kV | UL04 | Transformer #OTT6579 located at 126 Wesley isolated to allow relocation of primary. | Ottawa | Scheduled Outage | Construction
11471 | 2007 | 10 | 5 | 0.35764 |  | 60 | 5 | 5 | Clifton | 4.16kV | UL04 | Transformer #OTT1861 located at 493 Bevan isolated due to change over | Ottawa | Scheduled Outage | Preventive Maintenance
9419 | 2006 | 10 | 12 | 0.34375 |  | 135 | 22 | 10 | Clifton | 4.16kV | UL04 | At 08:15 trans OTT6580 at 153 Wesley Ave in order to relocate trans to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
13362 | 2008 | 10 | 14 | 0.45833 |  | 60 | 5 | 5 | Clifton | 4.16kV | UL04 | Isolated transformer X32171 at 44 Bevan Ave to replace the pole | Ottawa | Scheduled Outage | Construction
11517 | 2007 | 10 | 15 | 0.375 |  | 105 | 23 | 13 | Clifton | 4.16kV | UL04 | Transformer #OTT3183 located at 158 Geoffrey isolated due to PCB change | Ottawa | Scheduled Outage
11523 | 2007 | 10 | 15 | 0.45833 |  | 105 | 16 | 9 | Clifton | 4.16kV | UL04 | Transformer #OTT3179 located at 501 Hilson isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
11525 | 2007 | 10 | 15 | 0.54167 |  | 85 | 14 | 10 | Clifton | 4.16kV | UL04 | Transformer located at 220 Iona isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
13374 | 2008 | 10 | 16 | 0.375 |  | 150 | 20 | 8 | CLIFTON | 4.16kV | UL04 | Transformer #32171 at 219 Wesley Ave isolated to allow for pole change | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11553 | 2007 | 10 | 18 | 0.52083 |  | 90 | 8 | 5 | CLIFTON | 4.16kV | UL04 | Isolated and replaced transformer OTT 3543 at 439 Kensington St (PCB OIL) | Ottawa | Scheduled Outage | Preventive Maintenance
9468 | 2006 | 10 | 19 | 0.3125 |  | 210 | 108 | 31 | Clifton | 4.16kV | UL04 | 3 transformers isolated at 444 Dawson to change a pole | Ottawa | Scheduled Outage | Construction
9580 | 2006 | 11 | 1 | 0.56042 |  | 189 | 47 | 15 | Clifton | 4.16kV | UL04 | Isolated transformer OTT6578 at 117 Wesley to relocate services | Ottawa | Scheduled Outage | Construction
9583 | 2006 | 11 | 2 | 0.29861 |  | 218 | 29 | 8 | Clifton | 4.16kV | UL04 | Isolated TRANSFORMER AT 126 Wesley to change Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
9650 | 2006 | 11 | 13 | 0.5625 |  | 33 | 4 | 8 | Clifton | 4.16kV | UL04 | Black and Macdonald Isolated a Transformer at 159 Norah st to relocate transformer | Ottawa | Scheduled Outage | Preventive Maintenance
9659 | 2006 | 11 | 14 | 0.35417 |  | 180 | 24 | 8 | CLIFTON | 4.16kV | UL04 | Isolated transformer OTT 4696 at 159 Nora to relocate primary conductor | Ottawa | Scheduled Outage | Construction
9665 | 2006 | 11 | 15 | 0.52083 |  | 117 | 16 | 8 | Clifton | 4.16kV | UL04 | Isolated transformer OTT4696 at 1598 Nora St to relocate hydro plante to new pole | Ottawa | Scheduled Outage | Construction
9705 | 2006 | 11 | 22 | 0.3125 |  | 270 | 45 | 10 | Clifton | 4.16kV | UL04 | Isolated and replaced transformer OTT1044 at 306 Byron Ave | Ottawa | Scheduled Outage | Preventive Maintenance
17385 | 2010 | 12 | 6 | 0.39931 |  | 37 | 4 | 6 | CLIFTON | 4.16kV | UL04 | Transformer X34150 at 457 Brennan Ave isolated for service upgrade | Ottawa | Scheduled Outage | Construction
19690 | 2011 | 12 | 6 | 0.46528 |  | 30 | 3 | 6 | Clifton | 4.16kV | UL04 | Transformer #X34151 located at 451 Brennan Ave opened by crew for a service upgrade | Ottawa | Scheduled Outage | Construction
7730 | 2005 | 12 | 15 | 0.4375 |  | 28 | 4 | 9 | Clifton | 4.16kV | UL04 | Transformer #OTT584 isolated at 445 Kensington to replace service | Ottawa | Scheduled Outage | Preventive Maintenance
6127 | 2005 | 1 | 12 | 0.4125 |  | 78 | 16 | 12 | Clifton | 4.16kV | UL05 | Replaced Switch for Transformer OTT254 at 476 Athlone Ave | Ottawa | Unknown/Other | No Apparent Cause
19939 | 2012 | 2 | 1 | 0.4375 |  | 30 | 5 | 10 | Clifton | 4.16kV | UL05 | At 10:30 transformer X21502 at 455 Highcroft Avenue was isolated to allow crew to upgrade service. 10 customers were affected for 30 minutes. Clifton (UL05) ID#19939. | Ottawa | Scheduled Outage | Construction
10049 | 2007 | 2 | 22 | 0.41667 |  | 106 | 42 | 24 | Cliffton | 4.16kV | UL05 | Tony Taylor isolated TRF. @ 393 Leighton For pole Change | Ottawa | Scheduled Outage | Preventive Maintenance
4909 | 2004 | 3 | 17 | 0.45139 |  | 47 | 9 | 11 | Clifton | 4.16kV | UL05 | Xfmr OTT3890 in rear of 419 Leighton taken O.O.S. to replace switch and repair x-arm. 11 customers on Island Park & Leighton affected. Customers who were home were advised. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17876 | 2011 | 4 | 11 | 0.3375 |  | 107 | 20 | 11 | CLIFTON | 4.16kV | UL05 | Transformer X26276 at 484 Highcroft - replaced insulator and drop lead | Ottawa | Adverse Weather | Rain
12331 | 2008 | 4 | 23 | 0.66597 |  | 80 | 337 | 253 | Clifton | 4.16kV | UL05 | The UL05 circuit trip because of a blown pothead. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18338 | 2011 | 6 | 8 | 0.69861 |  | 181 | 1092 | 362 | Clifton | 4.16kV | UL05 | UL05 circuit opened due to very Large tree on UL05 overhead at Clifton and Wilber. | Ottawa | Tree Contacts
10578 | 2007 | 6 | 9 | 0.039583 |  | 68 | 8 | 7 | Clifton | 4.16kV | UL05 | Crew opened transformer to reconnect customers service that was taken down by a tree. | Ottawa | Tree Contacts | Tree Limb Fallen
20760 | 2012 | 6 | 13 | 0.39236 |  | 45 | 2 | 2 | Clifton | 4.16kV | UL05 | Transformer #X22444 located at 72 Richmond Rd opened by crew to re-arrange plant | Ottawa | Scheduled Outage | Construction
10792 | 2007 | 7 | 4 | 0.64583 |  | 163 | 49 | 18 | Clifton | 4.16kV | UL05 | Transformer #OTT1416 located at 414 Churchill Ave N isolated to replace a leaking transformer | Ottawa | Scheduled Outage | Repair
12877 | 2008 | 7 | 18 | 0.37153 |  | 326 | 275 | 252 | Clifton | 4.16kV | UL05 | Thunderstorm in the area. Primary phase burnt down on highcroft, circuit isolated for repair | Ottawa | Adverse Weather | Lightning
18722 | 2011 | 7 | 18 | 0.80139 |  | 38 | 229 | 362 | Clifton | 4.16kV | UL05 | Tree on the wires at 460 Athalone required UL05 circuit opened to allow crews to isolate and remove tree | Ottawa | Tree Contacts | Tree Fallen
12918 | 2008 | 7 | 22 | 0.57292 |  | 30 | 6 | 13 | Clifton | 4.16kV | UL05 | Transformer #X26282 located at 309 Lincoln isolated due to pole transfer. | Ottawa | Scheduled Outage | Preventive Maintenance
4148 | 2003 | 9 | 25 | 0.32639 |  | 100 | 40 | 40 | CLIFTON | 4.16kV | UL05 | UL05 circuit auto reclosed due to lightning strike which also caused two locals to open feeding 40 customers. | Ottawa | Lightning | Direct Strike
19277 | 2011 | 9 | 28 | 0.40625 |  | 60 | 4 | 4 | Clifton | 4.16kV | UL05 | Trans X32092 at 231 Wesley Ave was isolated in order to connect a new service | Ottawa | Scheduled Outage | Construction
5832 | 2004 | 10 | 9 | 0.41528 |  | 81 | 302 | 224 | Clifton | 4.16kV | UL05 | Garbage Truck hit a pole at 441 Highcroft. Wires down | Ottawa | Foreign Interference | Vehicle
11506 | 2007 | 10 | 12 | 0.71528 |  | 35 | 2 | 4 | Clifton | 4.16kV | UL05 | Transformer #OTT6581 located at 229 Wesley Ave isolated to change serv & connections were replaced at both ends | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7471 | 2005 | 10 | 17 | 0.60417 |  | 30 | 5 | 10 | Clifton | 4.16kV | UL05 | Isolated Transformer # 3132 at 484 Highcroft to install service1 | Ottawa | Scheduled Outage | Preventive Maintenance
4337 | 2003 | 10 | 24 | 0.49653 |  | 10 | 37 | 224 | Clifton | 4.16kV | UL05 | Vehicle hit pole at 356 Kirkwood caused UL05 circuit to open .recloser out of service Circuit closed by scada and held. | Ottawa | Foreign Interference | Vehicle
19508 | 2011 | 11 | 1 | 0.375 |  | 75 | 16 | 13 | Clifton | 4.16kV | UL05 | 3 transformers (#X34237, X34234 and X34233) located at 392, 408 and 422 Leighton, opened by crew to re-arrange O/H | Ottawa | Scheduled Outage | Construction
5885 | 2004 | 11 | 15 | 0.29375 |  | 194 | 65 | 20 | UL | 4.16kV | UL05 | V635 at 311 Richmond rd isolated for planned primary cable upgrade. | Ottawa | Scheduled Outage | Construction
19581 | 2011 | 11 | 15 | 0.54167 |  | 40 | 7 | 11 | Clifton UL | 4.16kV | UL05 | Tx X35032 at 94 Mailes opened to remove NIU secondary. | Ottawa | Scheduled Outage | Construction
7686 | 2005 | 12 | 5 | 0.55625 |  | 64 | 6 | 6 | Clifton | 4.16kV | UL05 | Transformer OTT3130 at 441 Highcroft was isolated to relocate service | Ottawa | Scheduled Outage | Preventive Maintenance
6064 | 2004 | 12 | 15 | 0.87153 |  | 72 | 26 | 22 | Clifton | 4.16kV | UL05 | Cut-out replaced to single phase O/H line section on Leighton Ave. Suspect fused cut-out deteriorated due to age. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9863 | 2006 | 12 | 19 | 0.39583 |  | 120 | 18 | 9 | Clifton | 4.16kV | UL05 | Transformer #OTT3140 located @ 2966 Richmond Rd isolated due to service upgrade | Ottawa | Scheduled Outage | Construction
5811 | 2004 | 9 | 17 | 0.4625 |  | 39 | 215 | 433 | Clifton Sub | 4.16kV | UL05 & UL06 | Transport truck hit the pole twice. No damage to circuit. | Ottawa | Foreign Interference | Vehicle
4841 | 2004 | 3 | 1 | 0.40625 |  | 5 | 0 | 1 | Clifton | 4.16kV | UL06 | P234 at Scott & Tweedsmuir interrupted to replace arrestor. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
15971 | 2010 | 4 | 21 | 0.24653 |  | 35 | 7 | 12 | Clifton | 4.16kV | UL06 | transformer on Churchill was interrupted to allow crews to temporarily move it to a new location to allow crews to install new poles. | Ottawa | Scheduled Outage | Construction
8486 | 2006 | 6 | 14 | 0.81042 |  | 94 | 13 | 8 | Clifton | 4.16kV | UL06 | Tree limbs made contact to O/H line which caused the fuse to blow at transformer OTT4393 @ 633 Melbourne. | Ottawa | Tree Contacts | Inadequate Trimming
8934 | 2006 | 8 | 8 | 0.84167 |  | 63 | 9 | 9 | Clifton | 4.16kV | UL06 | Power outage to transformer OTT2000 at 317 Divercourt Ave due to broken switch | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11445 | 2007 | 10 | 2 | 0.85069 |  | 40 | 4 | 6 | Clifton | 4.16kV | UL06 | Isolated transformer OTT2044 at 288 Duncairn Ave to reconnect service | Ottawa | Scheduled Outage | Emergency Services Request
17083 | 2010 | 10 | 7 | 0.97222 |  | 372 | 81 | 13 |  | 13.2kV | UL06 | X34198 at 334 Richmond was opened to allow an electrician to make new secondary connections. | Ottawa | Scheduled Outage | Repair
19374 | 2011 | 10 | 14 | 0.44444 |  | 13 | 1 | 6 | CLIFTON | 4.16kV | UL06 | Steve Driscoll isolated X32002 to allow for new service | Ottawa | Scheduled Outage | Construction
11549 | 2007 | 10 | 18 | 0.45833 |  | 85 | 6 | 4 | Clifton | 4.16kV | UL06 | Transformer #OTT3430 located at 509 Island Park isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
11581 | 2007 | 10 | 24 | 0.375 |  | 155 | 28 | 11 | CLIFTON | 4.16kV | UL06 | Transformer #X32011 at 293 Duncairnn isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
17167 | 2010 | 10 | 25 | 0.45 |  | 32 | 6 | 12 | Clifton | 4.16kV | UL06 | Transformer #X30203 located at 484 Churchill opened by crew to change a service | Ottawa | Scheduled Outage | Construction
17548 | 2011 | 2 | 3 | 0.42014 |  | 31 | 8 | 15 | Clifton | 4.16kV | UL14 | Transformer #X33818 located at 310 Beechgrove opened by crew to install new service | Ottawa | Scheduled Outage | Construction
17600 | 2011 | 2 | 17 | 0.37639 |  | 59 | 9 | 9 | Clifton | 4.16kV | UL14 | Transformer #X34200 located at 330 Beechgrove opened by crew for a new service | Ottawa | Scheduled Outage | Construction
20044 | 2012 | 2 | 22 | 0.38889 |  | 160 | 19 | 7 | Clifton | 4.16kV | UL14 | Transformer #X33940 located at 289 Selby Ave opened by crew to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
12905 | 2008 | 7 | 21 | 0.38542 |  | 55 | 6 | 7 | Clifton | 4.16kV | UL14 | Transformer #X34213 located at 303 Atlantis isolated for service upgrade. | Ottawa | Scheduled Outage | Construction
7042 | 2005 | 7 | 29 | 0.51667 |  | 43 | 4 | 5 | Clifton | 4.16kV | UL14 | Isolated transformer # 26 at 236 Royal to make repairs to UG service | Ottawa | Scheduled Outage | Preventive Maintenance
4127 | 2003 | 9 | 22 | 0.50694 |  | 20 | 3 | 9 | Clifton | 4.16kV | UL14 | Transformer at 234 Churchill was opened to allow Bell Canada to perform testing. | Ottawa | Scheduled Outage
11491 | 2007 | 10 | 10 | 0.375 |  | 184 | 28 | 9 | Clifton | 4.16kV | UL14 | At 09:00 trans at 342 Lanark Ave was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11495 | 2007 | 10 | 10 | 0.58681 |  | 91 | 15 | 10 | CLIFTON | 4.16kV | UL14 | Transformer #OTT2359 at 283 Ferndale removed; went from 2 transformers to 1 AT 294 Ferndale - see interruption for 294 Ferndale | Ottawa | Scheduled Outage | Construction
11496 | 2007 | 10 | 10 | 0.54167 |  | 156 | 10 | 4 | Clifton | 4.16kV | UL14 | Transformer #OTT2360 at 294 Ferndale isolated to allow for PCB change | Ottawa | Scheduled Outage | Construction
11535 | 2007 | 10 | 16 | 0.54167 |  | 146 | 17 | 7 | Clifton | 4.16kV | UL14 | At 13:00 trans at 360 Whitby was isolated for PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
11772 | 2007 | 11 | 27 | 0.43403 |  | 81 | 19 | 14 | Clifton | 4.16kV | UL14 | Transformer #X35178 at 270 Royal isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
4993 | 2004 | 4 | 13 | 0.18472 |  | 33 | 238 | 433 | UL | 4.16kV | ULK1Y1 | UL05 & UL06 being fed from ULK1Y1 breaker due to ULT2 out of service for oil clean - up. Circuits patrolled & no problem found. Poor weather at time of trip. | Ottawa | Unknown/Other
4994 | 2004 | 4 | 13 | 0.28403 |  | 97 | 547 | 782 | UL | 4.16kV | ULK1Y1 | UL05 & UL06 being fed from ULK1Y1 breaker due to ULT2 out of service for oil clean - up. Circuits patrolled & no problem found. Poor weather at time of trip. UL05 patrolled, picked up only UL05 & crew saw flash. UL06 picked up & patrol continued on UL05. At Scott and Tweedsmuir span guy found in overhead 13kv TH2UL, interupted UL02, UL14, and UL06 for working clearances while crew removed the broken span guy and effected minor repair. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14008 | 2009 | 2 | 26 | 0.41667 |  | 20 | 4 | 11 | Henderson | 4.16kV | UN03 | Isolated transformer K01178 at 332 Wilbrod St to repair secondary service | Ottawa | Scheduled Outage | Repair
3356 | 2003 | 4 | 18 | 0.56528 |  | 266 | 27 | 6 | Henderson | 4.16kV | UN03 | 50 KVA single phase transformer supplying 173 Daly was faulted (xfmr located across from 296 Besserer at the corner of Nelson). Transformer replaced with a new one by 24/7 crew. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18169 | 2011 | 5 | 17 | 0.44444 |  | 100 | 7 | 4 | Henderson | 4.16kV | UN03 | G Carswell isolated trans X31094 at 335 Laurier Ave in order to transfer plant to new poles | Ottawa | Scheduled Outage | Construction
18191 | 2011 | 5 | 20 | 0.39236 |  | 203 | 14 | 4 | Henderson | 4.16kV | UN03 | Transformer X31094 @ 335 Laurier was isolated to allow crew to perform service upgrade. 4 customers were affected for 203 minutes. Henderson (UN03) | Ottawa | Scheduled Outage
10728 | 2007 | 6 | 25 | 0.41319 |  | 95 | 6 | 4 | Henderson | 4.16kV | UN03 | Transformer #OTT4655 located at 275 Nelson St isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
4223 | 2003 | 10 | 7 | 0.5625 |  | 38 | 6 | 10 | UN03 | 4.16kV | UN03 | Transformer OTT372 taken out of service for maintenance. 10 customers on Besserer affected. | Ottawa | Scheduled Outage | Preventive Maintenance
17497 | 2011 | 1 | 20 | 0.4375 |  | 60 | 5 | 5 | Henderson | 4.16kV | UN04 | Transformer #X27581 located at 105 Blackburn opened by crew due to transferring plant | Ottawa | Scheduled Outage | Construction
17596 | 2011 | 2 | 16 | 0.54792 |  | 108 | 29 | 16 | Henderson | 4.16kV | UN04 | Peter Bishop isolated trans for service work | Ottawa | Scheduled Outage
6253 | 2005 | 3 | 8 | 0.50347 |  | 38 | 11 | 17 | Henderson | 4.16kV | UN04 | O/H transformer OTT1328 at 588 Chapel isolated in order to repair secondary connections to 429 Chapel. Customers were notified door to door. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20163 | 2012 | 3 | 14 | 0.35417 |  | 210 | 35 | 10 | Henderson | 4.16kV | UN04 | Transformer X27609 at Templeton and Chapel was isolated to transfer plant to new transformer and pole | Ottawa | Scheduled Outage
6403 | 2005 | 4 | 12 | 0.45833 |  | 46 | 13 | 17 | Henderson | 4.16kV | UN04 | Isolated Transformer # 1328 at 588 Chapel to clean connections | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6406 | 2005 | 4 | 12 | 0.75833 |  | 38 | 11 | 17 | Henderson | 4.16kV | UN04 | Transformer #OTT1328 located at frt of 588 Chapel St isolated to change whole triplex service at 429 Chapel | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15926 | 2010 | 4 | 12 | 0.45556 |  | 24 | 8 | 20 | HENDERSON | 4.16kV | UN04 | Transformer X30880 at 172 Marlborough isolated for service upgrade | Ottawa | Scheduled Outage | Construction
14175 | 2009 | 4 | 15 | 0.42153 |  | 208 | 459 | 538 | Henderson | 4.16kV | UN04 | Fire at Somerset and Blackburn required fire dept. to spray on and close to Hydro overhead plant, request UN04 and UN11 off potential. UN11 and UN04 re-energized however services to 320 and 318 Somerset presented a hazard to fire dept, could not be removed until fire was completely out transformer, X27619 opened to provide isolation until fire dept clear. UG service to 322 Somerset and 100 Blackburn disconnected from X27581 all 4 premises destroyed | Ottawa | Scheduled Outage | Emergency Services Request
14296 | 2009 | 5 | 4 | 0.65625 |  | 30 | 8 | 15 | Henderson | 4.16kV | UN04 | Transformer #X27619 located at 322 Somerset St isolated to reconnect serv, had to put up 2 new services | Ottawa | Scheduled Outage | Repair
20503 | 2012 | 5 | 11 | 0.33333 |  | 377 | 44 | 7 | Henderson | 4.16kV | UN04 | X30826 at 88 Range Rd. was isolated to allow the crew to transfer plant | Ottawa | Scheduled Outage | Construction
6554 | 2005 | 5 | 13 | 0.52639 |  | 102 | 29 | 17 | Henderson | 4.16kV | UN04 | Power interrupted to transformer OTT1328 at 588 Chapel St to replace connections on the secondary services and install new triplex service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20510 | 2012 | 5 | 14 | 0.33333 |  | 150 | 15 | 6 | Henderson | 4.16kV | UN04 | Isolated transformer X27555 at 76 Range Rd to transfer hydro plant | Ottawa | Scheduled Outage | Preventive Maintenance
20520 | 2012 | 5 | 15 | 0.375 |  | 448 | 112 | 15 | Henderson | 4.16kV | UN04 | Transformer X30829 at 98 Range Rd. isolated for pole changes | Ottawa | Scheduled Outage | Construction
20647 | 2012 | 5 | 29 | 0.33333 |  | 150 | 28 | 11 | Henderson | 4.16kV | UN04 | Transformer X27581 at 100 Blackburn Ave. isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
20640 | 2012 | 5 | 30 | 0.33333 |  | 180 | 18 | 6 | Henderson | 4.16kV | UN04 | Transformer X27580 at 120 Blackburn Ave isolated to transfer plant | Ottawa | Scheduled Outage
20634 | 2012 | 5 | 31 | 0.33333 |  | 180 | 30 | 10 | Henderson | 4.16kV | UN04 | Isolated transformer X27579 at 136 Blackburn Ave to transfer hydro plant | Ottawa | Scheduled Outage | Construction
10856 | 2007 | 7 | 11 | 0.37986 |  | 162 | 27 | 10 | HENDERSON | 4.16kV | UN04 | Transformers isolated on Goulburn Ave, Templeton & Marlborough to allow for pcb change and rearanging of primary | Ottawa | Scheduled Outage | Preventive Maintenance
5616 | 2004 | 8 | 5 | 0.52083 |  | 130 | 22 | 10 | UN | 4.16kV | UN04 | Tx OTT4247 @ 219 Goulburn was opened to remove tree from conductor. As per dispatch. | Ottawa | Tree Contacts | Tree Limb Fallen
15214 | 2009 | 10 | 5 | 0.45833 |  | 11 | 4 | 20 | Henderson | 4.16kV | UN04 | At 11:00 trans in the rear of 172 Marlbourough was isloated in order to make repairs to the sec service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13689 | 2008 | 11 | 30 | 0.33333 |  | 310 | 83 | 16 | Henderson | 4.16kV | UN04 | At 08:00 trans at 300 SOMERSET ST E OTTAWA was isolated for trans PCB replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15481 | 2009 | 12 | 7 | 0.42361 |  | 70 | 23 | 20 | Henderson | 4.16kV | UN04 | Transformer #X30880 located at 172 Marlborough isolated to hook up a new service | Ottawa | Scheduled Outage | Construction
13989 | 2009 | 2 | 17 | 0.40278 |  | 45 | 2 | 3 | HENDERSON | 4.16kV | UN05 | xfmr X30713 at 24 Russell isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
20122 | 2012 | 3 | 5 | 0.35417 |  | 45 | 2 | 3 | Henderson | 4.16kV | UN05 | Isolated transformer X26257 at 324 Laurier Ave to re-arrange hydro plant | Ottawa | Scheduled Outage | Construction
20209 | 2012 | 3 | 23 | 0.35417 |  | 190 | 10 | 3 | Henderson | 4.16kV | UN05 | Transformer #X26257 located at 324 Laurier Ave E opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
20232 | 2012 | 3 | 26 | 0.39583 |  | 60 | 8 | 8 | Henderson | 4.16kV | UN05 | Transformer #X30525 located at 336 Chapel opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
20519 | 2012 | 5 | 15 | 0.72569 |  | 12 | 3 | 16 | Henderson | 4.16kV | UN05 | Transformer X27594 at 94 Sweetland isolated to disconnect hazardous service per ESA | Ottawa | Scheduled Outage | Emergency Services Request
10499 | 2007 | 5 | 31 | 0.95139 |  | 175 | 852 | 292 | Henderson | 4.16kV | UN05 | No problem found on patrol, breaker closed by SCADA and held. Lightning storm in the area | Ottawa | Adverse Weather | Lightning
10865 | 2007 | 7 | 13 | 0.12986 |  | 90 | 6 | 4 | Henderson | 4.16kV | UN05 | Transformer was opened to disconnect customer at 122 osgoode, and for clearance for working fire. | Ottawa | Scheduled Outage | Emergency Services Request
16577 | 2010 | 7 | 28 | 0.70486 |  | 54 | 9 | 10 | Henderson | 4.16kV | UN05 | Transformer #X30931 located at 29 Sweetland opened by crew to change triplex | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8898 | 2006 | 8 | 1 | 0.58333 |  | 139 | 2 | 1 | Henderson | 4.16kV | UN05 | Customer vault V796 was isolated to allow contractor to make emergency repais to breaker. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18932 | 2011 | 8 | 14 | 0.97847 |  | 124 | 8 | 4 | Henderson | 4.16kV | UN05 | V454 at 228 Laurier was isolated to allow the customer's contractor to perform standard vault maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
19070 | 2011 | 9 | 1 | 0.39861 |  | 56 | 22 | 24 | Henderson | 4.16kV | UN05 | Transformer X30930 at 48 Sweetland isolated for a changeover | Ottawa | Scheduled Outage | Construction
11338 | 2007 | 9 | 19 | 0.69097 |  | 420 | 70 | 10 | Henderson | 4.16kV | UN05 | Defective O/H transformer replaced by on -call crew at 96 Russell | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15321 | 2009 | 10 | 29 | 0.37153 |  | 35 | 3 | 5 | Henderson | 4.16kV | UN05 | Transformer #X30967 located at 30 Russell Ave isolated for a service upgrade | Ottawa | Scheduled Outage | Construction
17282 | 2010 | 11 | 16 | 0.72917 |  | 116 | 2 | 1 | Henderson | 4.16kV | UN05 | V396 at 27 Henderson isolated to determine cause of blown transformer fuse in vault. Old and undersized fuse feeding one of the transformers that was not upgraded with the other 2 where. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5981 | 2004 | 12 | 5 | 0.46181 |  | 60 | 27 | 27 | Henderson | 4.16kV | UN05 | Pole replacment | Ottawa | Scheduled Outage | Construction
5982 | 2004 | 12 | 5 | 0.46181 |  | 55 | 25 | 27 | Henderson | 4.16kV | UN05 | Pole Replacement | Ottawa | Scheduled Outage | Construction
19793 | 2012 | 1 | 6 | 0.49306 |  | 15 | 1 | 5 | Henderson | 4.16kV | UN06 | Transformer #X17741 located at 300 Osgoode St opened by crew to re-sag triplex | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20147 | 2012 | 3 | 9 | 0.52083 |  | 240 | 24 | 6 | Henderson | 4.16kV | UN06 | Trans X27602 at 372 Chapel St was isolated in order to transfer plant to new poles | Ottawa | Scheduled Outage | Construction
20183 | 2012 | 3 | 20 | 0.375 |  | 90 | 9 | 6 | Henderson | 4.16kV | UN06 | Trans X 27603 at 386 Chapel St was isolated in order to replace poles | Ottawa | Scheduled Outage | Preventive Maintenance
20255 | 2012 | 3 | 29 | 0.35417 |  | 165 | 14 | 5 | Henderson | 4.16kV | UN06 | Transformer #X27602 located at 372 Chapel St opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
20256 | 2012 | 3 | 29 | 0.52083 |  | 165 | 151 | 55 | Henderson | 4.16kV | UN06 | Isolated trtansformer X27600 at 343 Chapel St to transfer hydro plant | Ottawa | Scheduled Outage | Construction
20259 | 2012 | 3 | 30 | 0.35417 |  | 150 | 12 | 5 | Henderson | 4.16kV | UN06 | Transformer #X30601 located at 350 Chapel St opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
20424 | 2012 | 4 | 30 | 0.52083 |  | 206 | 31 | 9 | Henderson | 4.16kV | UN06 | Transformer X27585 at 66 Blackburn Ave. isolated to allow for pole replacement | Ottawa | Scheduled Outage | Construction
20426 | 2012 | 5 | 1 | 0.35417 |  | 210 | 24 | 7 | Henderson | 4.16kV | UN06 | Transformer X27586 at 76 Blackburn Ave. isolated to transfer plant | Ottawa | Scheduled Outage | Construction
20444 | 2012 | 5 | 2 | 0.52083 |  | 150 | 8 | 3 | Henderson | 4.16kV | UN06 | Transformer #X27587 located at 44 Blackburn Ave opened by crew to transfer Hydro plant | Ottawa | Scheduled Outage | Construction
20445 | 2012 | 5 | 2 | 0.52083 |  | 150 | 15 | 6 | Henderson | 4.16kV | UN06 | Transformer #X27588 located at 38 Blackburn Ave opened by crew to transfer Hydro plant | Ottawa | Scheduled Outage | Construction
20471 | 2012 | 5 | 7 | 0.30208 |  | 165 | 11 | 4 | Henderson | 4.16kV | UN06 | Transformer X27589 at 18 Blackburn Ave. isolated to transfer plant | Ottawa | Scheduled Outage
20713 | 2012 | 6 | 7 | 0.54167 |  | 180 | 42 | 14 | Henderson | 4.16kV | UN06 | Transformer X31230 at 82 Goulburn Ave. isolated to allow for transfer of plant | Ottawa | Scheduled Outage | Construction
10737 | 2007 | 6 | 26 | 0.40625 |  | 110 | 13 | 7 | Henderson | 4.16kV | UN06 | Isolated and replaced transformer OTT436 at 76 Blackburn due to PCB | Ottawa | Scheduled Outage | Preventive Maintenance
10901 | 2007 | 7 | 18 | 0.38889 |  | 115 | 15 | 8 | Henderson | 4.16kV | UN06 | Transformer #OTT4245 located at 5 Marlborough isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
11177 | 2007 | 8 | 28 | 0.85764 |  | 284 | 66 | 14 | Henderson | 4.16kV | UN06 | crew replaced leaking transformer at 82 Goulburn | Ottawa | Defective Equipment
11448 | 2007 | 10 | 3 | 0.38542 |  | 16 | 3 | 10 | HENDERSON | 4.16kV | UN06 | TRANSFORMER #65C1A-0439 AT 4 RANGE RD ISOLATED TO ALLOW FOR REPAIRS TO A BAD CONNECTION AT KIOSK | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
9754 | 2006 | 11 | 30 | 0.36806 |  | 45 | 4 | 6 | Henderson | 4.16kV | UN06 | Mark Rushton isolated trf. # 1321 for a service upgrade @ 336 Chapel | Ottawa | Scheduled Outage | Preventive Maintenance
17671 | 2011 | 3 | 5 | 0.58681 |  | 32 | 2 | 3 | Henderson | 4.16kV | UN07 | Trans at 238 Laurier Ave was isolatedin order to replace a defective cutout | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20699 | 2012 | 6 | 5 | 0.375 |  | 300 | 415 | 83 | Henderson | 4.16kV | UN07 | Transformer P01324 at 10 Goulburn Ave. isolated to allow for transfer of plant | Ottawa | Scheduled Outage | Construction
6942 | 2005 | 7 | 13 | 0.90625 |  | 3 | 14 | 276 | Henderson | 4.16kV | UN07 | Circuit opened during lightening storm.Circuit has no recloser. Circuit closed back in via scada. | Ottawa | Adverse Weather | Lightning
5719 | 2004 | 8 | 25 | 0.70139 |  | 157 | 44 | 17 | Henderson | 4.16kV | UN07 | Transformer # 3847 isolated to all crews to replace defective unit. Outage affected power to 17 customers on un07 circuit. | Ottawa | Scheduled Outage | Repair
9500 | 2006 | 10 | 24 | 0.42014 |  | 70 | 9 | 8 | Henderson | 4.16kV | UN07 | Isolated transformer OTT5990 at 289 Stewart St to replace triplex service | Ottawa | Scheduled Outage | Repair
15313 | 2009 | 10 | 26 | 0.57431 |  | 73 | 26 | 21 | Henderson | 4.16kV | UN07 | Transformer #X30984 located at 386 Wilbrod St isolated for pole change | Ottawa | Scheduled Outage | Construction
15608 | 2010 | 1 | 4 | 0.38125 |  | 46 | 25 | 32 | HENDERSON | 4.16kV | UN10 | Transformer X34846 at 170 Russell Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage
20331 | 2012 | 4 | 16 | 0.38194 |  | 10 | 4 | 21 | Henderson | 4.16kV | UN10 | Isolated transformer X30961 at 478 Nelson st to disconnect service to 488 Nelson St | Ottawa | Scheduled Outage | Emergency Services Request
16006 | 2010 | 4 | 28 | 0.13889 |  | 98 | 18 | 11 | Henderson | 4.16kV | UN10 | A blown arrestor on the transformer X30834 at Templeton and Russell caused UN10 circuit to auto-reclose, and transformer to open. Crew made repairs, and refused transformer. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14460 | 2009 | 6 | 4 | 0.45833 |  | 30 | 4 | 9 | Henderson | 4.16kV | UN10 | Isolated transformer X30715 at 178 Russell Ave for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
10535 | 2007 | 6 | 5 | 0.40625 |  | 345 | 69 | 12 | henderson | 4.16kV | UN10 | Peter Bishop isolated TRF. OTT 5822 @ 216 Somerset to allow contractors to work in the vicinity of our lines | Ottawa | Scheduled Outage | Emergency Services Request
10536 | 2007 | 6 | 5 | 0.40625 |  | 345 | 69 | 12 | henderson | 4.16kV | UN10 | Peter Bishop established a PC 10 C 3496 to Serge [ contractor ] @ TRF. 5822 @ 216 somerset to allow contractor to work near our lines | Ottawa | Scheduled Outage
10746 | 2007 | 6 | 27 | 0.375 |  | 156 | 34 | 13 | Henderson | 4.16kV | UN10 | Interrupted transformer 65C1A-0658 at 204 Russel Road for PCB change. | Ottawa | Scheduled Outage | Preventive Maintenance
10857 | 2007 | 7 | 12 | 0.375 |  | 120 | 46 | 23 | Henderson | 4.16kV | UN10 | K1164 Transformer #30963 at 391 Nelson ST isolated to allow for PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
16483 | 2010 | 7 | 17 | 0.77083 |  | 29 | 2 | 4 | Henderson | 4.16kV | UN10 | Overhead transformer at 75 Mann interrupted to disconnect dammaged service and stand pipe to 75 Mann and replace blown arrestor at pole | Ottawa | Tree Contacts | Tree Limb Fallen
7028 | 2005 | 7 | 26 | 0.88194 |  | 30 | 4 | 9 | Henderson | 4.16kV | UN10 | Trans OTT6189 @ 141 Sweetland Ave isolated to repair broken sec neutral caused by fallien tree branch | Ottawa | Tree Contacts | Tree Limb Fallen
7248 | 2005 | 8 | 31 | 0.29167 |  | 76 | 147 | 186 | Henderson | 4.16kV | UN10 | Tree fell on seconday wires at 155 Russell Ave causing primary to slap together. Circuit was re-energized from SCADA with the exception of the one affected O/H transformer. Crew later repaired secondary & re-energized the last transformer. 186 customers affected were in the Sandy Hill area (Mann, Sweetland, Russell, Somerset) | Ottawa | Tree Contacts | Tree Limb Fallen
17358 | 2010 | 11 | 30 | 0.39236 |  | 30 | 4 | 7 | Henderson | 4.16kV | UN10 | Transformer #X27615 located at Nelson and Somerset opened by crew to install new Bell Box. | Ottawa | Scheduled Outage | Construction
4595 | 2003 | 12 | 12 | 0.54167 |  | 27 | 7 | 15 | Henderson | 4.16kV | UN10 | Transformer opened to redo connections at 66 Havelock. 15 Customers effected in power outage. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17586 | 2011 | 2 | 15 | 0.52083 |  | 105 | 23 | 13 | HENDERSON | 4.16kV | UN11 | Transformer X27605 at 304 Somerset St E open to string primary | Ottawa | Scheduled Outage | Construction
14174 | 2009 | 4 | 15 | 0.38681 |  | 50 | 218 | 261 | Henderson | 4.16kV | UN11 | Fire at Somerset and Blackburn required fire dept. to spray on and close to Hydro overhead plant, request UN04 and UN11 off potential. | Ottawa | Scheduled Outage | Emergency Services Request
20711 | 2012 | 6 | 7 | 0.33333 |  | 180 | 69 | 23 | Henderson | 4.16kV | UN11 | Transformer X31231 at 120 Goulburn Ave. isolated to allow for transfer of plant | Ottawa | Scheduled Outage | Construction
11267 | 2007 | 9 | 7 | 0.12083 |  | 61 | 12 | 12 | Henderson | 8/4.8kV | UN11 | Mark Brown reports transformer at 95 Henderson on Pole #2 on the UM11 circuit was opened to isolate the feed to the apartments and a PC10A#004819 was issued. Isolation was required due to fire. | Ottawa | Adverse Environment | Fire
13257 | 2008 | 9 | 18 | 0.43403 |  | 14 | 5 | 22 | Henderson | 4.16kV | UN11 | Transformer #X30892 located at 158 Goulburn isolated to disconnect O/H service for someone worling on the house | Ottawa | Scheduled Outage | Preventive Maintenance
13263 | 2008 | 9 | 19 | 0.4375 |  | 20 | 7 | 22 | Henderson | 4.16kV | UN11 | Transformer #X30892 located at 158 Goulburn Ave isolated to reconnect a serv that was disconnected yesterday | Ottawa | Scheduled Outage | Preventive Maintenance
20022 | 2012 | 2 | 15 | 0.46181 |  | 87 | 26 | 18 | Henderson | 4.16kV | UN12 | At 11:05 crews isolated Transformer X30837 on Henderson to rearrange the transformer feeds. 18 customers affected for 87mins. Henderson, UN12 ID# 20022 | Ottawa | Scheduled Outage | Construction
3236 | 2003 | 3 | 9 | 0.23403 |  | 11 | 18 | 56 | Henderson | 4.16kV | UN12 | Clamp burnt off to K1190 & primary down. Circuit was unloaded, primary sleeved thru & clamp repaired. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3420 | 2003 | 5 | 9 | 0.5625 |  | 80 | 9 | 7 | Henderson | 4.16kV | UN13 | TX 18923 at 1307 Highgate disconnected to repair service . 7 customers affected . Dispatch . | Ottawa | Scheduled Outage | Repair
3140 | 2003 | 1 | 25 | 0.52153 |  | 329 | 219 | 102 | Kilborn | 4.16kV | UP02 | Blue phase cable fault between K559 and K560 caused UP02 to open and Cable come out from blue phase cutout. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
19891 | 2012 | 1 | 25 | 0.37222 |  | 69 | 12 | 10 | Kilborn | 4.16kV | UP02 | K546 at 1592 Featherston was isolated to allow crews to change the secondary connections | Ottawa | Scheduled Outage | Repair
3145 | 2003 | 1 | 29 | 0.47361 |  | 83 | 14 | 10 | Kilborn | 4.16kV | UP02 | K560 Isolated by crew to repair bad cable in pit of transfer. All customers notified by crew the day of outage. All load restored to normal at 12:45 p.m. | Ottawa | Scheduled Outage | Repair
3196 | 2003 | 2 | 17 | 0.67014 |  | 69 | 11 | 9 | Kilborn | 4.16kV | UP02 | Short notice outage, all customers notified. First outage to open secondary from K557 in order to remove cover from pedestal in order to make repairs to 1945 Camborne. Second outage was to connect a temporary supply from K557 to pedestal. | Ottawa | Scheduled Outage | Repair
14338 | 2009 | 5 | 10 | 0.73125 |  | 14 | 3 | 11 | Kilborn | 4.16kV | UP02 | K560 at 1880 Ferncroft was interrupted to replace current limiter. Due to some customers experiencing intermittent power problems. 11 customers on Featherstone & Ferncroft were affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3606 | 2003 | 6 | 24 | 0.39167 |  | 146 | 24 | 10 | Kilborn | 4.16kV | UP02 | Electrician to fix main. | Ottawa | Scheduled Outage | Preventive Maintenance
14603 | 2009 | 6 | 24 | 0.40278 |  | 8 | 1 | 9 | Kilborn | 4.16kV | UP02 | Transformer #K554 located at 1868 Camborne Cres isolated for crew to take a PCB oil sample | Ottawa | Scheduled Outage | Construction
13019 | 2008 | 8 | 8 | 0.38889 |  | 15 | 2 | 9 | KILBORN | 4.16kV | UP02 | Transformer #K00554 at 1862 Camborne isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
4222 | 2003 | 10 | 6 | 0.40972 |  | 35 | 5 | 8 | Kilborn | 4.16kV | UP02 | Transformer K547 at 1865 Fairmeadow taken out of service to repair defective switch. 8 customers on Fairmeadow affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4243 | 2003 | 10 | 11 | 0.55417 |  | 28 | 5 | 11 | Kilborn | 4.16kV | UP02 | To repair U/G secondary connections. | Ottawa | Scheduled Outage | Repair
19808 | 2012 | 1 | 10 | 0.53125 |  | 70 | 5 | 4 | Kilborn | 4.16kV | UP03 | Isolated transformer X28039 at 1226 Willowdale Ave to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Construction
15643 | 2010 | 1 | 12 | 0.57986 |  | 54 | 10 | 11 | KILBORN | 4.16kV | UP03 | Transformer X34472 at 1293 Ridgemont isolated to allow for tree removal | Ottawa | Scheduled Outage | Preventive Maintenance
17481 | 2011 | 1 | 12 | 0.41667 |  | 30 | 3 | 6 | Kilborn | 4.16kV | UP03 | Isolated transformer X28187 at 1292 Willowdale Ave to replace open wire service feeding 2356 Ridgecrest Place | Ottawa | Scheduled Outage | Emergency Services Request
17485 | 2011 | 1 | 13 | 0.375 |  | 210 | 18 | 5 | Kilborn | 4.16kV | UP03 | Isolated transformer X28095 at 2307 Alta Vista Dr to replace pole | Ottawa | Scheduled Outage | Construction
17488 | 2011 | 1 | 14 | 0.37847 |  | 140 | 12 | 5 | KILBORN | 4.16kV | UP03 | Transformer X28095 at 2303 Alta Vista Dr isolated for secondary buss work | Ottawa | Scheduled Outage | Construction
11951 | 2008 | 1 | 17 | 0.50556 |  | 3 | 12 | 231 | Kilborn | 4.16kV | UP03 | On restoring UA06 load to V123 a switch at V121 was closed and second cable fault located. This one on the red phase. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11952 | 2008 | 1 | 17 | 0.60486 |  | 1 | 4 | 231 | Kilborn | 4.16kV | UP03 | UP03 tripped on trying to pick up cables only. Last attempt was cables bus and allload in V123. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19884 | 2012 | 1 | 24 | 0.375 |  | 157 | 16 | 6 | Kilborn | 4.16kV | UP03 | Transformer #X28187 located at 1292 Willowdale opened by crew to upgrade plant | Ottawa | Scheduled Outage | Construction
19886 | 2012 | 1 | 24 | 0.54167 |  | 108 | 18 | 10 | Kilborn | 4.16kV | UP03 | X28238 at 1303 Chattaway was isolated for plant upgrade. | Ottawa | Scheduled Outage | Construction
19890 | 2012 | 1 | 25 | 0.375 |  | 192 | 42 | 13 | Kilborn | 4.16kV | UP03 | X39133 and X28042 in the rear of 1242 Willowdale were isolated to allow crews to upgrade plant. | Ottawa | Scheduled Outage | Construction
19894 | 2012 | 1 | 25 | 0.54167 |  | 72 | 6 | 5 | Kilborn | 4.16kV | UP03 | X28039 at 1216 Willowdale was isolated to allow crews to upgrade plant. | Ottawa | Scheduled Outage | Construction
4735 | 2004 | 1 | 26 | 0.55486 |  | 21 | 3 | 8 | Kilborn | 4.16kV | UP03 | Transformer #5405 at 2369 Ridgecrest interrupted to replace a secondary connection. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19904 | 2012 | 1 | 26 | 0.52083 |  | 128 | 13 | 6 | Kilborn |  | UP03 | X28183 at 1284 Wesmar was isolated to allow crews to upgrade plant. | Ottawa | Scheduled Outage | Construction
19941 | 2012 | 2 | 1 | 0.41667 |  | 90 | 8 | 5 | Kilborn | 4.16kV | UP03 | Isolated transformer X28184 at 1298 Wesmar Dr to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Construction
19954 | 2012 | 2 | 3 | 0.39583 |  | 77 | 13 | 10 | Kilborn | 4.16kV | UP03 | Transformer 54B2D-0161B at 1217 Willowdale Ave isolated to allow for repairs to service at 1294 Chattaway | Ottawa | Scheduled Outage | Repair
19956 | 2012 | 2 | 3 | 0.375 |  | 90 | 8 | 5 | Kilborn | 4.16kV | UP03 | Transformer X39134 at 1545 Bank St. isolated to allow for reinsulating | Ottawa | Scheduled Outage | Preventive Maintenance
19970 | 2012 | 2 | 6 | 0.375 |  | 180 | 123 | 41 | Kilborn | 4.16kV | UP03 | Switch S12025 at 1287 Willowdale Ave was opened to allow crew to re-insulate primary and relocate single phase run off. | Ottawa | Scheduled Outage | Preventive Maintenance
19974 | 2012 | 2 | 7 | 0.375 |  | 90 | 8 | 5 | Kilborn | 4.16kV | UP03 | Isolated transformer X28045 at 2377 Evans Pl to replace pole | Ottawa | Scheduled Outage | Construction
19978 | 2012 | 2 | 7 | 0.46528 |  | 95 | 8 | 5 | Kilborn | 4.16kV | UP03 | Transformer #X28045 located at 2377 Evans Pl opened by crew for a pole replacement | Ottawa | Scheduled Outage | Construction
20002 | 2012 | 2 | 12 | 0.38542 |  | 258 | 43 | 10 | Kilborn | 4.16kV | UP03 | Overhead crew reports a section of UP03 overhead circuit has now been removed, and customer load transferred to a new padmount transformer. | Ottawa | Scheduled Outage | Construction
20024 | 2012 | 2 | 16 | 0.52083 |  | 100 | 8 | 5 | Kilborn | 4.16kV | UP03 | Transformer X28039 at 1226 Willowdale Ave. isolated to remove and replace a 75kVA transformer for future conversion | Ottawa | Scheduled Outage | Construction
20040 | 2012 | 2 | 21 | 0.39931 |  | 176 | 29 | 10 | Kilborn | 4.16kV | UP03 | Trans X39132 at 1237 Willowdale Ave was isolated in order to upgrade secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
20062 | 2012 | 2 | 27 | 0.45833 |  | 118 | 10 | 5 | Kilborn | 4.16kV | UP03 | Transformer 54B20D-0537B isolated to install new transformer for future conversion | Ottawa | Scheduled Outage | Construction
20081 | 2012 | 2 | 29 | 0.375 |  | 295 | 98 | 20 | Kilborn | 4.16kV | UP03 | Isolated transformer X28238 at 1309 Chattaway Ave and transformer 54B2D-0161B at 1217 Willowdale Ave for future conversion | Ottawa | Scheduled Outage | Construction
20124 | 2012 | 3 | 5 | 0.375 |  | 235 | 86 | 22 | Kilborn | 4.16kV | UP03 | Isolated and replaced 3 transformers X28183 at 1284 Wesmar Dr X39135 at 1285 Evans Blvd and X28087 at 1271 Wesmar Dr for upcoming primary line conversion from 4.16kv to 13.2kv | Ottawa | Scheduled Outage | Construction
20131 | 2012 | 3 | 6 | 0.375 |  | 225 | 22 | 6 | Kilborn | 4.16kV | UP03 | Transformer X28183 at 1284 Wesmar Dr. isolated to change transformer for future conversion | Ottawa | Scheduled Outage | Construction
20140 | 2012 | 3 | 7 | 0.375 |  | 295 | 64 | 13 | Kilborn | 4.16kV | UP03 | Isolated and replaced transformers X39133 at 1243 Evans Blvd and X28042 at 2360 Renfield Rd for primary conversion from 4.16kv to 13.2kv | Ottawa | Scheduled Outage | Construction
17683 | 2011 | 3 | 8 | 0.41667 |  | 142 | 12 | 5 | Kilborn | 4.16kV | UP03 | Isolated transformer X34474 at 1291 Willowdale Ave for service up-grade | Ottawa | Scheduled Outage | Preventive Maintenance
17714 | 2011 | 3 | 15 | 0.43056 |  | 150 | 25 | 10 | Kilborn | 4.16kV | UP03 | Trans at 1309 Chattaway Ave was isolated in order to re insulate the pole | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17723 | 2011 | 3 | 17 | 0.39583 |  | 195 | 26 | 8 | Kilborn | 4.16kV | UP03 | Transformer X28240 at 1217 Willowdale isolated for insulator & crossarm change | Ottawa | Scheduled Outage | Preventive Maintenance
17724 | 2011 | 3 | 17 | 0.39583 |  | 120 | 20 | 10 | Kilborn | 4.16kV | UP03 | Transformer X39132 at 1233 Willowdale isolated for insulator & crossarm change | Ottawa | Scheduled Outage | Preventive Maintenance
20174 | 2012 | 3 | 18 | 0.29167 |  | 375 | 250 | 40 | Kilborn | 4.16kV | UP03 | The O/H in the Alta Vista,Chattaway area was converted from 4Kv to 13Kv. | Ottawa | Scheduled Outage | Construction
17755 | 2011 | 3 | 22 | 0.375 |  | 155 | 16 | 6 | Kilborn | 4.16kV | UP03 | Transformer #X28081 located at 1267 Willowdale opened by crew for an insulator change | Ottawa | Scheduled Outage | Construction
17768 | 2011 | 3 | 23 | 0.375 |  | 150 | 12 | 5 | Kilborn | 4.16kV | UP03 | Trans at 1279 Willow dale Ave was isloated in order to replace insulators and switch | Ottawa | Scheduled Outage | Preventive Maintenance
17778 | 2011 | 3 | 24 | 0.375 |  | 190 | 41 | 13 | Kilborn | 4.16kV | UP03 | Transformer isolated to allow crews to repaire Insulators. 13 customers affected | Ottawa | Scheduled Outage
20254 | 2012 | 3 | 29 | 0.46181 |  | 55 | 5 | 5 | Kilborn | 4.16kV | UP03 | Transformer #X27817 located at 1448 Kilborn Ave opened by crew to transfer plant | Ottawa | Scheduled Outage | Construction
20260 | 2012 | 3 | 30 | 0.39583 |  | 195 | 16 | 5 | Kilborn | 4.16kV | UP03 | Transformer #X27817 located at 1448 Kilborn Ave opened by crew to transfer a transformer. | Ottawa | Scheduled Outage | Construction
17838 | 2011 | 4 | 6 | 0.39583 |  | 347 | 58 | 10 | Kilborn | 4.16kV | UP03 | X27538 at 1458 Kilborn Ave isolated to allow for pole change | Ottawa | Scheduled Outage | Construction
17839 | 2011 | 4 | 6 | 0.39583 |  | 152 | 10 | 4 | Kilborn | 4.16kV | UP03 | X27816 at 2291 Alta Vista Drive isolated to allow for pole change | Ottawa | Scheduled Outage
17845 | 2011 | 4 | 7 | 0.375 |  | 300 | 110 | 22 | Kilborn | 4.16kV | UP03 | At 09:00 three transformers at 1679 Grasmere Crescent were isolated to allow crew to install poles. 22 customers were affected for minutes. Kilborn (UP03) ID# 17845. | Ottawa | Scheduled Outage
10351 | 2007 | 5 | 2 | 0.48264 |  | 35 | 4 | 7 | Kilborn | 4.16kV | UP03 | Transformer OTT6584 at 1284 Wesmar Dr was issolated to replace cut out | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10353 | 2007 | 5 | 2 | 0.44792 |  | 45 | 4 | 5 | Kilborn | 4.16kV | UP03 | Transformer OTT2246 at 1260 Wesmar Dr was isolated to to repair open wire service | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18084 | 2011 | 5 | 2 | 0.9375 |  | 55 | 8 | 9 | Kilborn | 4.16kV | UP03 | Transformer #X28184 opened by crew to repair 3 services and remove tree from an open buss at 1308 Wesmar | Ottawa | Tree Contacts | Tree Fallen
16099 | 2010 | 5 | 18 | 0.83194 |  | 29 | 2 | 5 | Kilborn |  | UP03 | Transformer X28227 at the rear of 1282 Chattaway Cres had to be opened due to a pole fire. A squirrels nest near the pyro street light cable caused the fire. | Ottawa | Unknown/Other
18282 | 2011 | 6 | 2 | 0.36458 |  | 210 | 18 | 5 | Killborn | 4.16kV | UP03 | Isolated transformer X28095 at 2307 Alta Vista Dr to re-arrange Hydro plant | Ottawa | Scheduled Outage | Construction
14573 | 2009 | 6 | 19 | 0.56944 |  | 30 | 2 | 5 | Kilborn | 4.16kV | UP03 | Isolated and replaced transformer X39134 at the rear of 1207 Evans Blvd due to oil leak | Ottawa | Scheduled Outage | Preventive Maintenance
18445 | 2011 | 6 | 20 | 0.39583 |  | 347 | 29 | 5 | Kilborn | 4.16kV | UP03 | Transformer X28095 at 2299 Alta Vista Drive isolated for conversion | Ottawa | Scheduled Outage | Construction
18457 | 2011 | 6 | 21 | 0.40972 |  | 328 | 22 | 4 | Kilborn | 4.16kV | UP03 | Trans X27816 at 2291 Alta Vista was isolated for voltage conversion | Gloucester | Scheduled Outage | Preventive Maintenance
18645 | 2011 | 7 | 12 | 0.375 |  | 270 | 58 | 13 | Kilborn | 4.16kV | UP03 | Trans at 1339 Ridgecrest Pl was isolated for upgrade to plant | Ottawa | Scheduled Outage
12923 | 2008 | 7 | 23 | 0.43056 |  | 130 | 13 | 6 | Kilborn | 4.16kV | UP03 | Transformer #X27824 located at 2335 Alta Vista isolated to replace transformer | Ottawa | Scheduled Outage | Preventive Maintenance
18891 | 2011 | 8 | 8 | 0.95139 |  | 130 | 13 | 6 | Kilborn | 4.16kV | UP03 | P70 at 1525 Bank & xfmr at rear of 1282 Chataway were isolated for xfmr upgrade & to re-arrange plant. P70 now TP8910. | Ottawa | Scheduled Outage | Construction
18935 | 2011 | 8 | 15 | 0.42361 |  | 45 | 4 | 5 | Kilborn | 4.16kV | UP03 | Crews isolated X28185 for voltage conversion at 1312 Wesmar Drive | Ottawa | Scheduled Outage
18946 | 2011 | 8 | 16 | 0.375 |  | 237 | 20 | 5 | Kilborne | 4.16kV | UP03 | Transformer X34474 @ 1291 Willowdale was isolated to allow for conversion. | Ottawa | Scheduled Outage | Construction
19040 | 2011 | 8 | 29 | 0.375 |  | 330 | 38 | 7 | KILBORN | 4.16kV | UP03 | Transformer X28186 at 2369 Ridgecrest isolated - conversion area | Ottawa | Scheduled Outage | Construction
19045 | 2011 | 8 | 29 | 0.58333 |  | 270 | 31 | 7 | Kilborn | 4.16kV | UP03 | At 9: 00 am transformer X28186 was opened to allow crew to clear branch of O/H.7 customers affected for 224 minutes. | Ottawa | Tree Contacts | Tree Limb Fallen
13236 | 2008 | 9 | 15 | 0.30347 |  | 83 | 7 | 5 | KILBORN | 4.16kV | UP03 | Transformer No. 39134 located at 1207 Evans Boul. Isolated, crew replaced lead on top of cut out, possible weather | Ottawa | Adverse Weather | Wind
19425 | 2011 | 10 | 20 | 0.32639 |  | 190 | 1172 | 370 | Kilborn | 4.16kV | UP03 | UP03 line was isolated to repair downed conductor at Heron & Alta Vista. | Ottawa | Adverse Weather | Wind
19428 | 2011 | 10 | 20 | 0.32639 |  | 192 | 1178 | 368 | Kilborn | 4.16kV | UP03 | The UP03 circuit was isolated to allow the crews reinstall down conductor at the corner heron and Alt vista. | Ottawa | Adverse Weather | Wind
9713 | 2006 | 11 | 23 | 0.54167 |  | 57 | 4 | 4 | Kilborn | 4.16kV | UP03 | Isolated and replaced transformer OTT 87 at 2291 Alta Vista Dr (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
19639 | 2011 | 11 | 26 | 0.41667 |  | 390 | 84 | 13 | Kilborn | 4.16kV | UP03 | Isolated transformer X28083 at 2339 Ridgecrest Pl to replace pole | Ottawa | Scheduled Outage | Construction
19640 | 2011 | 11 | 26 | 0.52083 |  | 240 | 20 | 5 | Kilborn | 4.16kV | UP03 | Isolated transformer X28185 at 1312 Wesmar Dr to replace pole | Ottawa | Scheduled Outage | Construction
17646 | 2011 | 2 | 25 | 0.375 |  | 270 | 698 | 155 | Kilborn | 4.16kV | UP04 | A portion of UP04 circuit was isolated to convert it to 13.2kv and was restored on TB06 out of Russell | Ottawa | Scheduled Outage | Construction
17666 | 2011 | 3 | 4 | 0.39583 |  | 20 | 3 | 10 | Kilborn | 4.16kV | UP04 | Transformer #X40308 located at 1471 Cavendish isolated by crew to make repairs | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10101 | 2007 | 3 | 9 | 0.41667 |  | 96 | 13 | 8 | Killborn | 4.16kV | UP04 | Rick Wallace isolated TRF. @ 315 Nelson to install new pole | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12121 | 2008 | 3 | 10 | 0.58333 |  | 70 | 14 | 12 | Kilborn | 4.16kV | UP04 | Transformer #OTT4985 located at 488 Pleasant Park Rd isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
12141 | 2008 | 3 | 14 | 0.38542 |  | 155 | 16 | 6 | Kilborn | 4.16kV | UP04 | At 09:22 trans at 422 Pleasant Park was isolated for pole replacement | Ottawa | Scheduled Outage
6298 | 2005 | 3 | 16 | 0.83611 |  | 70 | 7 | 6 | Kilborn | 4.16kV | UP04 | Transformer 5017 H2 bushing deffective, customer transferred to transformer 5016. See outage report 6299 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6299 | 2005 | 3 | 16 | 0.87847 |  | 9 | 2 | 13 | Kilborn | 4.16kV | UP04 | Transformer 5017 opened to allow 24/7 crew to transfer customers on transformer 5016 to transformer 5017. See outage report 6298 | Ottawa | Scheduled Outage | Repair
12150 | 2008 | 3 | 17 | 0.40556 |  | 106 | 7 | 4 | KILBORN | 4.16kV | UP04 | Transformer #X27800 at 476 Pleasant Park isolated to allow for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15870 | 2010 | 3 | 30 | 0.37847 |  | 373 | 249 | 40 | Kilborn | 4.16kV | UP04 | B phase run-off between Rachael & Mountbatten N. Of Cavendish from S25781 isolated for pole replacement & to transfer plant. | Ottawa | Scheduled Outage | Construction
12230 | 2008 | 4 | 3 | 0.38889 |  | 90 | 16 | 11 | Kilborn | 4.16kV | UP04 | Transformer #X27901 located at 453 Pleasant Park isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
12234 | 2008 | 4 | 3 | 0.57292 |  | 55 | 6 | 6 | Kilborn | 4.16kV | UP04 | Transformer #X27902 located at 494 Pleasant Park isolated due to upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
12267 | 2008 | 4 | 10 | 0.375 |  | 180 | 18 | 6 | Kilborn | 4.16kV | UP04 | At 09:00 trans at 448 Pleasant Park was isolated in order to replace adefective pole | Ottawa | Scheduled Outage | Repair
12271 | 2008 | 4 | 10 | 0.50625 |  | 171 | 17 | 6 | Kilborn | 4.16kV | UP04 | Isolated transformer X27902 at 476 Pleasant Park Rd for pole change | Ottawa | Scheduled Outage | Construction
12278 | 2008 | 4 | 14 | 0.39583 |  | 180 | 33 | 11 | KILBORN | 4.16kV | UP04 | Transformer X27901 at 470 Pleasant Park isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
10284 | 2007 | 4 | 19 | 0.57292 |  | 65 | 6 | 6 | Kilborn | 4.16kV | UP04 | At 14:52 trans at 353 McArthur for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15964 | 2010 | 4 | 20 | 0.375 |  | 330 | 50 | 9 | KILBORN | 4.16kV | UP04 | Transformer X27535 at 218 Cunningham isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
15968 | 2010 | 4 | 21 | 0.375 |  | 240 | 32 | 8 | KILBORN | 4.16kV | UP04 | Transformer X26279 @ 404 Pleasant Park opened @ 9AM, to transfer transformer to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
16016 | 2010 | 4 | 29 | 0.375 |  | 275 | 28 | 6 | Kilborn | 4.16kV | UP04 | Transformer #X27781 located at 1990 Fairbanks opened by crew for service upgrade | Ottawa | Scheduled Outage | Construction
16096 | 2010 | 5 | 18 | 0.44444 |  | 135 | 18 | 8 | Kilborn | 4.16kV | UP04 | Transformer #X27251 located at 201 Rachael Ave opened by crew for pole replacement | Ottawa | Scheduled Outage | Construction
18405 | 2011 | 6 | 14 | 0.4375 |  | 91 | 5 | 3 |  | 4.16kV | UP04 | Trans X29141 at 2239 Alta Vista was isolated in order to replace a new pole | Ottawa | Scheduled Outage | Preventive Maintenance
18411 | 2011 | 6 | 14 | 0.5625 |  | 95 | 5 | 3 | Kilborn | 4.16kV | UP04 | Transformer #X29142 located at 2205 Alta Vista opened by crew due to a conversion | Ottawa | Scheduled Outage | Construction
16420 | 2010 | 7 | 7 | 0.375 |  | 15 | 1 | 4 | Kilborn | 4.16kV | UP04 | Isolated transformer X27778 at 327 Pleasant Park Rd to relocate switch to new pole | Ottawa | Scheduled Outage | Construction
18659 | 2011 | 7 | 14 | 0.60417 |  | 100 | 5 | 3 | Kilborn | 4.16kV | UP04 | Transformer #X29141 located at 2239 Alta Vista opened by crew due to rearranging plant to install new poles | Ottawa | Scheduled Outage | Construction
18660 | 2011 | 7 | 14 | 0.67361 |  | 130 | 6 | 3 | Kilborn | 4.16kV | UP04 | Transformer #X29142 located at 2205 Alta Vista opened by crew due to rearranging plant to install new poles | Ottawa | Scheduled Outage | Construction
8852 | 2006 | 7 | 26 | 0.58333 |  | 87 | 17 | 12 | Kilborn | 4.16kV | UP04 | Isolated and replaced transformer OTT4603 at 220 Mountbatten Ave | Ottawa | Scheduled Outage | Construction
8860 | 2006 | 7 | 27 | 0.61111 |  | 50 | 6 | 7 | Kilbourn | 4.16kV | UP04 | Chris Williams opened xfmr OTT6253 to change a pcb transformer | Ottawa | Scheduled Outage
16571 | 2010 | 7 | 27 | 0.39583 |  | 150 | 20 | 8 | Kilborn | 4.16kV | UP04 | Isolated transformer X27788 at 346 PLEASANT PARK RD to replace pole | Ottawa | Scheduled Outage | Construction
16587 | 2010 | 7 | 29 | 0.39931 |  | 195 | 650 | 200 | Kilborn | 4.16kV | UP04 | Over head section of UP04 on Pleasant Park was isolated to allow Hydro crews to replace the conductor with larger conductor | Ottawa | Scheduled Outage | Construction
5595 | 2004 | 8 | 1 | 0.29375 |  | 107 | 9 | 5 | UP | 4.16kV | UP04 | A squirrel caused the transformer fuse to open at 2145 Alta Vista, TxOTT100. | Ottawa | Foreign Interference | Animal
8896 | 2006 | 8 | 1 | 0.375 |  | 50 | 2 | 3 | Kilborn | 4.16kV | UP04 | Transformer #OTT3588 located at 1606 Kilborn isolated due to transformer change for high PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
8920 | 2006 | 8 | 3 | 0.55208 |  | 108 | 11 | 6 | Kilborn | 4.16kV | UP04 | Transformer at 274 Pleasant Park in Ottawa isolated for replacement. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16613 | 2010 | 8 | 3 | 0.49653 |  | 100 | 8 | 5 | KILBORN | 4.16kV | UP04 | Transformer X27779 at 338 Pleasant Park isolated to remove transformer & run new secondary | Ottawa | Scheduled Outage | Construction
7058 | 2005 | 8 | 4 | 0.35417 |  | 40 | 5 | 7 | Kilborn | 4.16kV | UP04 | Power interrupted to Transformer OTT1284 at 1426 Portal St to replace service | Ottawa | Scheduled Outage | Repair
16716 | 2010 | 8 | 11 | 0.36667 |  | 386 | 225 | 35 | Playfair DS | 4.16kV | UP04 | Crews isolated a section of UP04 Blue phase from S10445 to end of line in order to install new poles. | Ottawa | Scheduled Outage | Construction
8968 | 2006 | 8 | 15 | 0.36458 |  | 80 | 8 | 6 | Kilborn | 4.16kV | UP04 | Transformer #OTT4970 located at 374 Pleasant Park Rd isolated due to transformer change due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
16809 | 2010 | 8 | 25 | 0.37917 |  | 79 | 5 | 4 | Kilborn | 4.16kV | UP04 | S10445 at 1390 Cavendish was isolated to allow crews to transfer conductor to new poles. | Ottawa | Scheduled Outage | Construction
11178 | 2007 | 8 | 29 | 0.38542 |  | 25 | 2 | 5 | Kilborn | 4.16kV | UP04 | Isolated transformer OTT4982 at 364 Pleasant Park Dr for service up-grade | Ottawa | Scheduled Outage | Preventive Maintenance
16838 | 2010 | 8 | 30 | 0.37847 |  | 235 | 20 | 5 | KILBORN | 4.16kV | UP04 | Transformer X34402 @ 1450 Cavendish isolated to allow for pole change | Ottawa | Scheduled Outage | Repair
16887 | 2010 | 9 | 7 | 0.79444 |  | 140 | 359 | 154 | Kilborn | 4.16kV | UP04 | SCADA indicates UP04 A/R & locked out, Patroll found did not find issues | Ottawa | Adverse Weather
16894 | 2010 | 9 | 7 | 0.79444 |  | 138 | 354 | 154 | Kilborn | 4.16kV | UP04 | UP04 A/R/A, circuit patrolled nothing found, closed via SCADA and holding. Severe lightning storm in effect. | Ottawa | Adverse Weather
16933 | 2010 | 9 | 13 | 0.40625 |  | 135 | 22 | 10 | Kilborn | 4.16kV | UP04 | Transformer #X27258 located at 1453 Portal opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
16943 | 2010 | 9 | 14 | 0.37708 |  | 297 | 35 | 7 | Kilborn | 4.16kV | UP04 | Trans at 152 MOUNTBATTEN AVE OTT was isolated in order to replace a pole | Ottawa | Scheduled Outage | Preventive Maintenance
16945 | 2010 | 9 | 14 | 0.37708 |  | 297 | 35 | 7 | Kilborn | 4.16kV | UP04 | Isolated transformer X28211 at 152 Mountbatten Ave to replace pole | Ottawa | Scheduled Outage | Construction
16952 | 2010 | 9 | 16 | 0.38542 |  | 205 | 14 | 4 | Kilborn | 4.16kV | UP04 | Transformer #X27250 located at 156 Mountbatten opened by crew to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
19302 | 2011 | 10 | 1 | 0.36597 |  | 403 | 302 | 45 | KILBORN | 4.16kV | UP04 | UP04 and UP07 overhead cct were isolated from Reeves Cr West on Kilborn to remove conductor and transfer UP04 load to UP03 cct. | Ottawa | Scheduled Outage
17051 | 2010 | 10 | 4 | 0.375 |  | 454 | 61 | 8 | Kilborn | 4.16kV | UP04 | Transformer X27251 at 201 Rachel Ave isolated to allow for pole change | Ottawa | Scheduled Outage | Construction
17056 | 2010 | 10 | 5 | 0.375 |  | 195 | 23 | 7 | Kilborn | 4.16kV | UP04 | Transformer #X28211 located at 156 Mountbatten opened by crew to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
17110 | 2010 | 10 | 13 | 0.375 |  | 302 | 161 | 32 | Kilbourn | 4.16kV | UP04 | UP04 backyard overhead from Cavendish to Mountbatten was isolated for crews to install new poles and transfer plant. | Ottawa | Scheduled Outage | Construction
17151 | 2010 | 10 | 21 | 0.36458 |  | 195 | 20 | 6 | Kilborn | 4.16kV | UP04 | UP04 radial feed from S19280 at 279 Pleasant Park was isolated by Hydro Crew for pole replacement. | Ottawa | Scheduled Outage | Construction
17157 | 2010 | 10 | 21 | 0.375 |  | 180 | 15 | 5 | KILBORN | 4.16kV | UP04 | Transformer X27916 at 279 Pleasant Park Rd isolated to allow for pole replacement | Ottawa | Scheduled Outage | Construction
4328 | 2003 | 10 | 22 | 0.42014 |  | 70 | 6 | 5 | KILBORN | 4.16kV | UP04 | Transformer at the rear of 225 Mountbatten was isolated to change pole. Outage effected 5 customers on Pleasant Park & Alta Vista. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17197 | 2010 | 10 | 30 | 0.90972 |  | 310 | 46 | 9 | Kilborn | 4.16kV | UP04 | transformer X 27335 at 218 Cavendish opened when branches damaged open wire secondaries. | Ottawa | Tree Contacts | Tree Limb Fallen
17218 | 2010 | 11 | 4 | 0.39236 |  | 200 | 20 | 6 | Kilborn UP | 4.16kV | UP04 | S19280 was opened isolating a section of UP04 O/H to transfer plant to new poles. Alta Vista / Pleasant Park / Billings ave. | Ottawa | Scheduled Outage | Construction
9608 | 2006 | 11 | 6 | 0.46319 |  | 53 | 7 | 8 | Kilborn | 4.16kV | UP04 | Bob Rolland installing new ploe @ 269 Fernbank | Ottawa | Scheduled Outage | Construction
13589 | 2008 | 11 | 10 | 0.38542 |  | 245 | 16 | 4 | Kilborn | 4.16kV | UP04 | Transformer #X27668 located at 2041 Alta Vista Dr isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
11719 | 2007 | 11 | 15 | 0.64583 |  | 45 | 3 | 4 | Killborn | 4.16kV | UP04 | Transformer OTT522 at 167 Rachael Ave was isolated to replace split bolt connections on the secondary services | Ottawa | Scheduled Outage | Repair
17280 | 2010 | 11 | 16 | 0.375 |  | 185 | 12 | 4 | Kilborn | 4.16kV | UP04 | Isolated transformer X27916 at 2015 Alta Vista dr for a pole change | Ottawa | Scheduled Outage | Construction
17303 | 2010 | 11 | 18 | 0.38194 |  | 115 | 17 | 9 | Kilborn | 4.16kV | UP04 | Isolated transformer X27535 at 218 Cunningham Ave for a tree contractor to remove a tree | Ottawa | Scheduled Outage | Emergency Services Request
19879 | 2012 | 1 | 23 | 0.69236 |  | 97 | 8 | 5 | Kilborn | 4.16kV | UP05 | On-call refused transformer 54B2D-0398 at 2322 Hillary Ave. | Ottawa | Adverse Weather | Rain
13928 | 2009 | 2 | 3 | 0.375 |  | 315 | 68 | 13 | Kilborn | 4.16kV | UP05 | Isolated transformer X26937 at 2202 Prospect Ave to replace pole | Ottawa | Scheduled Outage | Construction
9998 | 2007 | 2 | 7 | 0.43056 |  | 175 | 18 | 6 | Kilborn | 4.16kV | UP05 | Chuck Barton isolated TRF. # 564 @ 2215 Braeside to chageover plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
19976 | 2012 | 2 | 7 | 0.42708 |  | 105 | 26 | 15 | Kilborn | 4.16kV | UP05 | Isolated transformer X27515 at 1477 Farnsworth Ave to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Construction
19989 | 2012 | 2 | 8 | 0.38542 |  | 150 | 18 | 7 | Kilborn | 4.16kV | UP05 | Isolated transformer X27519 at 1515 Farnsworth Ave to transfer hydro plant to new transformer X45602 | Ottawa | Scheduled Outage | Construction
19998 | 2012 | 2 | 10 | 0.375 |  | 75 | 20 | 16 | Kilborn | 4.16kV | UP05 | Trans X27518 at 1509 Grace St was isolated in order to work on secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
20165 | 2012 | 3 | 15 | 0.38056 |  | 222 | 56 | 15 | Kilborn | 4.16kV | UP05 | 4kV Overhead circuit on Quinn Cres. Was isolated to allow crews to trim trees and install new insulators for furture voltage conversion. Kilborn (UP05) | Ottawa | Scheduled Outage | Construction
20188 | 2012 | 3 | 21 | 0.375 |  | 170 | 23 | 8 | Kilborn | 4.16kV | UP05 | Transformer #X27512 located at 1510 Orchard Ave opened by crew for 13KV conversion | Ottawa | Scheduled Outage | Construction
20193 | 2012 | 3 | 21 | 0.41667 |  | 220 | 59 | 16 | Kilborn | 4.16kV | UP05 | Transformer #X27516 located at 1464 Farnsworth Ave opened by crew for secondary upgrades | Ottawa | Scheduled Outage | Construction
20198 | 2012 | 3 | 22 | 0.38542 |  | 295 | 79 | 16 | Kilborn | 4.16kV | UP05 | At 09:15 transformers X275186 and X27518 in the rear of Farnsworth Avenue were isolated to allow crew to install new transformers. 16 customers were affected for 295 minutes. Kilborn (UP05) ID#20198 | Ottawa | Scheduled Outage | Construction
20299 | 2012 | 4 | 10 | 0.55972 |  | 39 | 4 | 6 | Kilborn | 4.16kV | UP05 | Transformer X26360 at 2216 Hillary Ave. isolated for future conversion | Ottawa | Scheduled Outage | Construction
20305 | 2012 | 4 | 11 | 0.38889 |  | 80 | 8 | 6 | Kilborn | 4.16kV | UP05 | Transformer X26360 isolated to allow for prep work for conversion | Ottawa | Scheduled Outage | Construction
20306 | 2012 | 4 | 11 | 0.38889 |  | 80 | 21 | 16 | Kilborn | 4.16kV | UP05 | Transformer X27532 isolated to allow for prep work for conversion | Ottawa | Scheduled Outage | Construction
20314 | 2012 | 4 | 12 | 0.375 |  | 567 | 359 | 38 | Kilborn | 4.16kV | UP05 | UP05 O/H from S27916 to EOL was isolated to allow crews to install new poles. 38 customers affected for 596 minutes. Kilborn (UP05) | Ottawa | Scheduled Outage
8146 | 2006 | 4 | 13 | 0.48611 |  | 30 | 3 | 6 | Kilborn | 4.16kV | UP05 | Isolated tranmsformer OTT564 at 2215 Braeside Ave to trim trees | Ottawa | Tree Contacts | Inadequate Trimming
20423 | 2012 | 4 | 30 | 0.41667 |  | 360 | 30 | 5 | Kilborn | 4.16kV | UP05 | Transformer X27685 at 2247 Courtice Ave. isolated to allow for transformer upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
20453 | 2012 | 5 | 3 | 0.52569 |  | 105 | 14 | 8 | Kilborn | 4.16kV | UP05 | UP05-B phase from tap to EOL at 1437 Palen was isolated to allow crew to removed tree from O/H circuit. | Ottawa | Tree Contacts | Inadequate Trimming
6506 | 2005 | 5 | 4 | 0.37708 |  | 147 | 17 | 7 | Kilborn | 4.16kV | UP05 | Opened transformer OTT1717 at 2285 Courtice to disconnect service | Ottawa | Scheduled Outage | Repair
5159 | 2004 | 5 | 18 | 0.34375 |  | 280 | 920 | 206 | Kilborn | 4.16kV | UP05 | UP05 3 phases down across Palen and one phase down in the rear of Hillary, curcuit tripped and locked out. Isolation was required for repair. | Ottawa | Lightning | Direct Strike
20568 | 2012 | 5 | 24 | 0.39931 |  | 127 | 25 | 12 | Kilborn | 4.16kV | UP05 | Transformer #X26937 located at 2210 Prospect Ave opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
20569 | 2012 | 5 | 25 | 0.84583 |  | 862 | 1767 | 123 | Kilborn | 4.16kV | UP05 | S19657 opened due to wires down at 1427 Denver. | Ottawa | Adverse Weather | Construction
20594 | 2012 | 5 | 25 | 0.7875 |  | 99 | 424 | 257 | Kilborn | 4.16kV | UP05 | UP05 CB auto-reclosed and locked out during storm. Crew found downed wires @ 1427 Denver. Crew opened S19657 to repair. | Ottawa | Adverse Weather | Wind
20648 | 2012 | 5 | 29 | 0.375 |  | 311 | 26 | 5 | Kilborn | 4.16kV | UP05 | Transformer X27685 at 2247 Courtice was isolated to allow for pole change | Ottawa | Scheduled Outage
20649 | 2012 | 5 | 29 | 0.42708 |  | 30 | 2 | 5 | Kilborn | 4.16kV | UP05 | Transformer X27687 at 2233 Courtice Ave. isolated to allow for transfer of hydro plant. | Ottawa | Scheduled Outage
20637 | 2012 | 5 | 30 | 0.45278 |  | 110 | 22 | 12 | Kilborn | 4.16kV | UP05 | Transformer X27505 at 2240 Prospect Ave. isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
20644 | 2012 | 5 | 30 | 0.45278 |  | 110 | 68 | 37 | Kilborn | 4.16kV | UP05 | Transformer X27505 at 2240 Prospect Ave. isolated a second time to allow continued transfer of plant | Ottawa | Scheduled Outage | Construction
20631 | 2012 | 5 | 31 | 0.32153 |  | 52 | 10 | 12 | Kilborn | 4.16kV | UP05 | Replaced blown fuse feeding transformer X26937 at 2210 Prospect Ave (Cause unknown) | Ottawa | Unknown/Other | No Apparent Cause
20709 | 2012 | 6 | 7 | 0.38889 |  | 225 | 34 | 9 | Kilborn | 4.16kV | UP05 | Transformer X26085 at 2215 Courtice Ave. isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
20710 | 2012 | 6 | 7 | 0.375 |  | 245 | 20 | 5 | Kilborn | 4.16kV | UP05 | Transformer X27687 at 2233 Courtice Ave. isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
20736 | 2012 | 6 | 11 | 0.38194 |  | 135 | 4 | 2 | Kilborn | 4.16kV | UP05 | Isolated and removed from service transformer X27683 at 1520 Orchard St | Ottawa | Scheduled Outage | Construction
20739 | 2012 | 6 | 11 | 0.38889 |  | 205 | 24 | 7 | Kilborn | 4.16kV | UP05 | transformer X27686 openned to allow crews to transfer plant. 7 customers affected for 205 minutes. Kilborn (UP05) ID #20739 | Ottawa | Scheduled Outage | Construction
20741 | 2012 | 6 | 11 | 0.64931 |  | 26 | 4 | 10 | Kilborn | 4.16kV | UP05 | Transaformer X28178 @ 1388 Wesmar was disconnect to make repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20763 | 2012 | 6 | 13 | 0.375 |  | 200 | 50 | 15 | Kilborn | 4.16kV | UP05 | Transformer X27515 at 1468 Orchard Ave. isolated to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
20770 | 2012 | 6 | 13 | 0.53125 |  | 298 | 20 | 4 | Kilborn | 4.16kV | UP05 | Transformer X28180 isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
20771 | 2012 | 6 | 13 | 0.53125 |  | 298 | 35 | 7 | Kilborn | 4.16kV | UP05 | Transformer X28189 at 2364 Tampa Ave. isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
20773 | 2012 | 6 | 14 | 0.56111 |  | 455 | 288 | 49 | Kilborn | 4.16kV | UP05 | UP05 red and white phase from S10727 to EOL on Tampa was isolated by crews to replace insulator for voltage conversion. | Ottawa | Scheduled Outage | Construction
20808 | 2012 | 6 | 19 | 0.52431 |  | 210 | 14 | 4 | Kilborn | 4.16kV | UP05 | Transformer #X27520 located at 2321 Hillary Ave opened by crew to replace transformer for future conversion | Ottawa | Scheduled Outage
20875 | 2012 | 6 | 26 | 0.38889 |  | 440 | 147 | 20 | Kilborn | 4.16kV | UP05 | At 09:20 three transformers fed from S15844 at 1443 Palen Avenue was isolated to allow crew to replace insulators for 13KV conversion. 20 customers were affected for 440 minutes. Kilborn (UP05) ID#20875. | Ottawa | Scheduled Outage | Construction
20880 | 2012 | 6 | 26 | 0.38194 |  | 465 | 62 | 8 | Kilborn | 4.16kV | UP05 | Isolated transformer X27523 at 1433 Palen Ave to re-insulate primary for conversion from 4.16kv to 13kv | Ottawa | Scheduled Outage | Construction
20891 | 2012 | 6 | 27 | 0.54861 |  | 149 | 25 | 10 | Kilborn | 4.16kV | UP05 | Transformer X45771 at 2276 Hillary Ave. isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
20893 | 2012 | 6 | 27 | 0.375 |  | 442 | 88 | 12 | Kilborn | 4.16kV | UP05 | Transformer X45629 at 2258 Hillary Ave. isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage
18680 | 2011 | 7 | 17 | 0.80903 |  | 938 | 4174 | 267 | Kilborn | 4.16kV | UP05 | UP05 circuit trip beacuse limbs fell on the O/H because of high winds. | Ottawa | Adverse Weather | Wind
18753 | 2011 | 7 | 17 | 0.80972 |  | 937 | 4170 | 267 | Kilborn | 4.16kV | UP05 | UP05 Tripped during severe stor. Circuit was patrolled for problems and then restored. | Ottawa | Adverse Weather | Wind
18955 | 2011 | 8 | 17 | 0.54861 |  | 47 | 5 | 7 | Kilborn | 4.16kV | UP05 | Transformer #X28189 located at 2364 Tampa opened by crew for tree removal | Ottawa | Tree Contacts | Tree Limb Fallen
9022 | 2006 | 8 | 22 | 0.54514 |  | 70 | 6 | 5 | Kilborn | 4.16kV | UP05 | Isolated and replaced transformer OTT1716 at 2247 Courtice Ave due to contaminated oil (PCB) | Ottawa | Scheduled Outage | Preventive Maintenance
19164 | 2011 | 9 | 13 | 0.72917 |  | 590 | 2537 | 258 | KILBORN | 4.16kV | UP05 | UP05 breaker opened due to tree falling onto wire breaking conductor. Kilborn (UP05) ID# 19164 | Ottawa | Adverse Weather | Lightning
13265 | 2008 | 9 | 19 | 0.54167 |  | 50 | 2 | 3 | Kilborn | 4.16kV | UP05 | Transformer #X28180 located at 2471 Alta Vista Dr isolated to connect a cable to the primary line | Ottawa | Scheduled Outage | Preventive Maintenance
4290 | 2003 | 10 | 17 | 0.43611 |  | 49 | 11 | 14 | Kilborn | 4.16kV | UP05 | Transformer at Braeside & Woodcrest was opened to remove tree limb from o/h at 2184 Braeside. | Ottawa | Tree Contacts | Tree Limb Fallen
11671 | 2007 | 11 | 6 | 0.44097 |  | 20 | 4 | 12 | Kilborn | 4.16kV | UP05 | Transformer #27516 located at 1489 Grace St isolated to make repairs | Ottawa | Scheduled Outage | Repair
17320 | 2010 | 11 | 22 | 0.4375 |  | 158 | 34 | 13 | KILBORN | 4.16kV | UP05 | Transformer OTT3166 isolated to allow for the installation of a new transformer | Ottawa | Scheduled Outage | Construction
19696 | 2011 | 12 | 7 | 0.39583 |  | 319 | 21 | 4 | Kilborn | 4.16kV | UP05 | At 9:30 crew remove taps for a UP05 Red phase run off at 2322 Hillary for tree removal affecting 4 customer on transformer X27520. Kilborn UP05 | Ottawa | Scheduled Outage | Construction
15557 | 2009 | 12 | 27 | 0.90764 |  | 357 | 1242 | 295 | Kilborn | 4.16kV | UP05 | Broken tree limb took down primary conductor at rear of 1364 Wesmar, damaged section was cut clear for repairs and power restored to main line. Crew repaired overhead then circuit was opened to allow crew to reconnect line clamp. Alll power was restored at 03:44 | Ottawa | Adverse Weather | Ice Storm
11925 | 2008 | 1 | 11 | 0.71875 |  | 65 | 11 | 10 | Kilborn | 4.16kV | UP06 | Isolated white phase local between Baffin & Thessaly circle for Aspen to remove tree from primary. | Ottawa | Tree Contacts | Tree Fallen
15736 | 2010 | 2 | 22 | 0.52083 |  | 90 | 15 | 10 | Kilborn | 4.16kV | UP06 | Isolated and replaced transformer X27539 at 351 Marshall Crt | Ottawa | Scheduled Outage | Preventive Maintenance
15802 | 2010 | 3 | 15 | 0.4375 |  | 18 | 1 | 2 | Kilborn | 4.16kV | UP06 | Transformer #X27682 located at 386 Cunningham isolated due to re-arranging plant | Ottawa | Scheduled Outage | Construction
15941 | 2010 | 4 | 15 | 0.47847 |  | 50 | 2 | 2 | KILBORN | 4.16kV | UP06 | Transformer X27682 at 386 Cunningham isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
10349 | 2007 | 5 | 2 | 0.36736 |  | 44 | 22 | 30 | Kilborn | 4.16kV | UP06 | Single phase runoff isolated for tree trimming affecting customers on Fairbanks & Thorn. | Ottawa | Scheduled Outage | Preventive Maintenance
6544 | 2005 | 5 | 11 | 0.54792 |  | 76 | 48 | 38 | KILBORN | 4.16kV | UP06 | BRANCH FROM TREE FELL ON WHITE PHASE OF UP06 CIRCUITCAUSING FUSE TO BLOW.. | Ottawa | Tree Contacts | Tree Limb Fallen
16078 | 2010 | 5 | 12 | 0.37847 |  | 115 | 15 | 8 | KILBORN | 4.16kV | UP06 | Transformer X27539 at 367 Marshall Crt isolated for pole change | Ottawa | Scheduled Outage | Construction
16083 | 2010 | 5 | 13 | 0.36042 |  | 222 | 37 | 10 | Kilborn | 4.16kV | UP06 | Transformer X27504 at Cunningham and Palmer Isolateed for maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
16136 | 2010 | 5 | 25 | 0.36458 |  | 195 | 23 | 7 | Kilborn | 4.16kV | UP06 | Transformer #X27540 located at 334 Cunningham opened by crew for pole change | Ottawa | Scheduled Outage | Construction
16137 | 2010 | 5 | 25 | 0.48611 |  | 20 | 2 | 6 | Kilborn | 4.16kV | UP06 | Transformer #X27695 located at 350 Cunningham opened by crew for pole change | Ottawa | Scheduled Outage | Construction
14466 | 2009 | 6 | 5 | 0.36458 |  | 45 | 2 | 2 | Kilborn | 4.16kV | UP06 | Isolated transformer X27682 at 392 Cunningham Ave to connect new underground service | Ottawa | Scheduled Outage | Emergency Services Request
3629 | 2003 | 6 | 28 | 0.87708 |  | 27 | 2 | 4 | UP | 4.16kV | UP06 | An o/h xfmr was opened at 539 Thessaly to repair secondary connnections. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14638 | 2009 | 6 | 29 | 0.027778 |  | 180 | 24 | 8 | Kilborn | 4.16kV | UP06 | transformer X27696 at 2089 Palmer leaking oil and required isolation for replacement | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10898 | 2007 | 7 | 17 | 0.35417 |  | 120 | 22 | 11 | Kilborn | 4.16kV | UP06 | At 08:30 trans at 384 Crestview was isolated in order to transfer services | Ottawa | Scheduled Outage
8901 | 2006 | 8 | 2 | 0.070833 |  | 188 | 47 | 15 | Kilborn | 4.16kV | UP06 | A fallen tree limb brought down a single phase primary wire on Thessaly at Baffin. 24/7 & O/C crew removed branch & repaired broken conductor. | Ottawa | Tree Contacts | Tree Limb Fallen
8961 | 2006 | 8 | 14 | 0.38194 |  | 110 | 13 | 7 | Kilborn | 4.16kV | UP06 | Transformer OTT1804 at 358 Cunningham Ave isolated to replace secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
8989 | 2006 | 8 | 16 | 0.60417 |  | 115 | 19 | 10 | Kilborn | 4.16kV | UP06 | Transformer #OTT2264 located at 1944 Fairbanks isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
9023 | 2006 | 8 | 22 | 0.59722 |  | 94 | 9 | 6 | Kilborn | 4.16kV | UP06 | Isolated and replaced transformer OTT6547 at 2245 Webster Ave due to contaminated oil (PCB) | Ottawa | Scheduled Outage | Preventive Maintenance
9059 | 2006 | 8 | 25 | 0.84722 |  | 45 | 6 | 8 | Kilborn | 4.16kV | UP06 | Isolated transformer OTT664 at 2055 Thorne Ave to replace triplex service | Ottawa | Scheduled Outage | Repair
15727 | 2010 | 2 | 18 | 0.375 |  | 250 | 75 | 18 | Kilborn | 4.16kV | UP07 | Radial line on Summit Ave fed from S15418 isolated to replace insulators & one O/H transformer. 16 customers on Summit & 2 on Palmer were affected. | Ottawa | Scheduled Outage | Preventive Maintenance
7953 | 2006 | 2 | 20 | 0.375 |  | 120 | 16 | 8 | Kilbourn | 4.16kV | UP07 | Jeff Meek opened transformer OTT101 at 261 Cunningham for a pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
7954 | 2006 | 2 | 20 | 0.375 |  | 120 | 16 | 8 | Kilbourn | 4.16kV | UP07 | Jeff Meek opened transformer OTT101 at 261 Cunningham to do a pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
7956 | 2006 | 2 | 20 | 0.52431 |  | 140 | 19 | 8 | Kilborn | 4.16kV | UP07 | Transformer #OTT101 located at 261 Cunningham isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
7960 | 2006 | 2 | 21 | 0.375 |  | 150 | 28 | 11 | Kilborn | 4.16kV | UP07 | At 09:00 trans OTT101 at 261 Cunningham Ave was isolated in order to replace pole | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15766 | 2010 | 3 | 3 | 0.375 |  | 210 | 10 | 3 | Kilborn | 4.16kV | UP07 | Transformer #X27675 located at 1466 Tedder Ave isolated for an upgrade | Ottawa | Scheduled Outage | Construction
15806 | 2010 | 3 | 16 | 0.35208 |  | 355 | 95 | 16 | Kilborn | 4.16kV | UP07 | S18186 opened by R Longpre to allow for poles to be changed on Tedder, 16 customers affected. | Ottawa | Scheduled Outage | Construction
15807 | 2010 | 3 | 16 | 0.37569 |  | 62 | 3 | 3 | KILBORN | 4.16kV | UP07 | Transformer X27528 at 277 Cunningham isolated to allow for pole change | Ottawa | Scheduled Outage | Construction
20180 | 2012 | 3 | 19 | 0.45833 |  | 60 | 3 | 3 | Kilborn | 4.16kV | UP07 | Trans X45767 at 1462 Kilborn Ave was isolted in order to replace the transformer pole | Ottawa | Scheduled Outage | Preventive Maintenance
20182 | 2012 | 3 | 20 | 0.37847 |  | 300 | 105 | 21 | Kilborn | 4.16kV | UP07 | A section of UP07 from S23847 isolated for tree trimming, pole & insulator replacement affecting customers on Woodcrest & Quinn. | Ottawa | Scheduled Outage | Repair
20189 | 2012 | 3 | 21 | 0.45833 |  | 40 | 3 | 5 | Kilborn | 4.16kV | UP07 | Transformer #X40855 located at 2221 Alta Vista Dr opened by crew for voltage conversion | Ottawa | Scheduled Outage | Construction
17762 | 2011 | 3 | 22 | 0.56597 |  | 80 | 8 | 6 | Kilborn | 4.16kV | UP07 | Transformer #X27688 located at 2233 Webster Ave opened by crew due to a pole change | Ottawa | Scheduled Outage | Construction
17767 | 2011 | 3 | 23 | 0.36458 |  | 160 | 11 | 4 | Kilborn | 4.16kV | UP07 | Trans X27547 at 2213 Webster Ave was isolated in order to tranfer planrt to new poles | Ottawa | Scheduled Outage | Construction
20242 | 2012 | 3 | 27 | 0.35764 |  | 390 | 136 | 21 | Kilborn | 4.16kV | UP07 | UP07 W phase section from S23847 to EOL on Woodcrest and Quinn was isolated to allow crew to reinsulate and install new poles. | Ottawa | Scheduled Outage
17801 | 2011 | 3 | 29 | 0.375 |  | 330 | 33 | 6 | Kilborn | 4.16kV | UP07 | Isolated transformer X27689 at 2245 Webster Ave to replace pole | Ottawa | Scheduled Outage | Construction
15875 | 2010 | 3 | 31 | 0.35833 |  | 374 | 810 | 130 | Kilborn | 4.16kV | UP07 | A section of UP07 from temp 175 was isolated to allow crews to rearrange plant. Customers on Teddar, Summit, Palmer, Alta Vista & Mountbatten were affected. | Ottawa | Scheduled Outage | Construction
6388 | 2005 | 4 | 8 | 0.41667 |  | 133 | 16 | 7 | Kilborn | 4.16kV | UP07 | Transformer #5016 isolated at 240 Mountbatten to change transformer | Ottawa | Scheduled Outage | Preventive Maintenance
17924 | 2011 | 4 | 14 | 0.375 |  | 240 | 52 | 13 | Kilborn | 4.16kV | UP07 | Crew isolated transformer X29138 at 2105 Woodcrest for a pole change. | Ottawa | Scheduled Outage | Preventive Maintenance
17933 | 2011 | 4 | 14 | 0.375 |  | 240 | 52 | 13 | Kilborn | 4.16kV | UP07 | Trans at 2105 Woodcrest Rd was isolated in order to replace pole and tranfer planrt | Ottawa | Scheduled Outage | Construction
15956 | 2010 | 4 | 19 | 0.4 |  | 180 | 12 | 4 | Kilborn | 4.16kV | UP07 | X27528 @ 277 Cunningham isolated @ 9:36 for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
17966 | 2011 | 4 | 19 | 0.375 |  | 380 | 19 | 3 | Kilborn | 4.16kV | UP07 | Transformer #X29133 located at 1525 Caton St opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
17967 | 2011 | 4 | 19 | 0.375 |  | 380 | 44 | 7 | Kilborn | 4.16kV | UP07 | Transformer #X29132 located at 1531 Caton St opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
20378 | 2012 | 4 | 24 | 0.35417 |  | 255 | 17 | 4 | Kilborn | 4.16kV | UP07 | Isolated transformer X27530 at 2044 Woodcrest Rd to transfer hydro plant | Ottawa | Scheduled Outage | Construction
20394 | 2012 | 4 | 25 | 0.35417 |  | 495 | 66 | 8 | Kilborn | 4.16kV | UP07 | Isolated and replaced transformer X27527 at 2010 Woodcrest Rd for primary conversion from 4.16kv to 13kv | Ottawa | Scheduled Outage | Construction
20398 | 2012 | 4 | 26 | 0.375 |  | 345 | 23 | 4 | Kilborn | 4.16kV | UP07 | Isolated transformer X27530 at 2044 Woodcrest Rd for tree trimming | Ottawa | Scheduled Outage | Construction
17999 | 2011 | 4 | 27 | 0.47917 |  | 65 | 11 | 10 | Kilborn | 4.16kV | UP07 | Transformer #X29135 located at 1496 Caton opened by crew due to a pole change | Ottawa | Scheduled Outage | Construction
18003 | 2011 | 4 | 27 | 0.56597 |  | 130 | 9 | 4 | Kilborn | 4.16kV | UP07 | Trans X29137 at 2150 Braeside was isolated in order to install a new pole | Gloucester | Scheduled Outage | Preventive Maintenance
16012 | 2010 | 4 | 28 | 0.55208 |  | 247 | 58 | 14 | Kilborn | 4.16kV | UP07 | At 13:35 trans at 1439 TEDDER AVE OTTAWA was isolated for Transformer replacement | Ottawa | Scheduled Outage | Preventive Maintenance
18120 | 2011 | 5 | 9 | 0.50347 |  | 36 | 14 | 23 | KILBORN | 4.16kV | UP07 | Transformer X29135 at 1504 Caton, X29132 at 1533 Caton and X29135 at 1496 Caton isolated for load transfer | Ottawa | Scheduled Outage | Construction
16070 | 2010 | 5 | 10 | 0.39583 |  | 393 | 105 | 16 | Kilborn | 4.16kV | UP07 | UP07 red phase radial line on Tedder was isolated to replace conductor. | Ottawa | Scheduled Outage | Preventive Maintenance
18124 | 2011 | 5 | 10 | 0.375 |  | 233 | 23 | 6 | Kilborn | 4.16kV | UP07 | At 09:00 transformer X29134 at 1510 Caton was isolated to allow crew to preform service upgrade. 6 customers were aftected for minutes. Kilborn (UP07) ID#18124. | Ottawa | Scheduled Outage
18137 | 2011 | 5 | 12 | 0.37153 |  | 371 | 43 | 7 | Kilborn | 4.16kV | UP07 | Transformer X29140 was open to allow crew to perform transformer upgrade. 7 customer were affected. Kilborn UP07 | Ottawa | Scheduled Outage
16079 | 2010 | 5 | 13 | 0.375 |  | 280 | 56 | 12 | Kilborn | 4.16kV | UP07 | O/h crew isolated the O/H on Reeves Cres to allow the tree contractor to preform tre trimming. | Ottawa | Scheduled Outage
14372 | 2009 | 5 | 17 | 0.31319 |  | 76 | 48 | 38 | Kilborn | 4.16kV | UP07 | Tree contact caused a radial fuse to blow on Tedder affecting customers on Summit. Crew trimmed tree and refused. Kilborn (UP07) ID#14372. | Ottawa | Tree Contacts | Inadequate Trimming
18177 | 2011 | 5 | 18 | 0.375 |  | 60 | 4 | 4 | Kilborn | 4.16kV | UP07 | Transformer #X29137 located at 2150 Braeside Ave opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
18205 | 2011 | 5 | 24 | 0.37986 |  | 193 | 872 | 476 | Kilborn | 4.16kV | UP07 | UP07 tripped due to a fallen tree at rear of 486 Thessaly damaging primary line. The damaged section was isolated & most customers restored. Tree removed from line & repairs completed before restoring remaining customers. | Ottawa | Tree Contacts | Tree Fallen
18316 | 2011 | 6 | 6 | 0.52083 |  | 215 | 43 | 12 | Kilborn | 4.16kV | UP07 | Transformer #X27662 located at 2233 Reeves Cres opened by crew due to a conversion | Ottawa | Scheduled Outage | Construction
18323 | 2011 | 6 | 7 | 0.27083 |  | 325 | 1625 | 300 | Kilborn | 4.16kV | UP07 | 25 overhead transformers in the Cunningham and Pleasent Park area were interrupted to allow crews to perform a voltage conversion on the circuit. | Ottawa | Scheduled Outage | Construction
16230 | 2010 | 6 | 9 | 0.39583 |  | 270 | 72 | 16 | Kilborn | 4.16kV | UP07 | A section of UP07 between Thorne & Baffin from S18618 was isolated for planned insulator & transformer replacement. | Ottawa | Scheduled Outage | Construction
18422 | 2011 | 6 | 16 | 0.375 |  | 380 | 76 | 12 | Killborn | 4.16kV | UP07 | Transformer X27662 @ 2233 Reeves was opened to allow crew to replace pole. 12 customers were affected. Killborn (UP07) | Ottawa | Scheduled Outage
18462 | 2011 | 6 | 22 | 0.375 |  | 305 | 51 | 10 | Kilborn | 4.16kV | UP07 | Transformer #64A1A-0228H located at 2221 Reeves opened up by crew due to conversion area. | Ottawa | Scheduled Outage | Construction
18582 | 2011 | 7 | 4 | 0.38889 |  | 155 | 31 | 12 | Kilborn | 4.16kV | UP07 | Isolated transformer X27662 at 2233 Reeves Cres for primary conversion from 4.16 kv to 13.2 kv | Ottawa | Scheduled Outage | Construction
8903 | 2006 | 8 | 2 | 0.36458 |  | 80 | 4 | 3 | Kilborn | 4.16kV | UP07 | Isolated and replaced transformer OTT6220 at 1475 Tedder Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
16667 | 2010 | 8 | 5 | 0.73889 |  | 426 | 254 | 352 | Kilborn | 4.16kV | UP07 | The UP07 breaker open via scada at Darcey Provest request to allow his crew to connect the O/H lead at Tedder and Cunningham | Ottawa | Adverse Weather | Rain
8962 | 2006 | 8 | 14 | 0.375 |  | 130 | 15 | 7 | Kilborn | 4.16kV | UP07 | Trans OTT6135 isolated at 308 Summit Ave in order to replace secondary services | Ottawa | Scheduled Outage | Preventive Maintenance
8977 | 2006 | 8 | 15 | 0.56597 |  | 95 | 3 | 2 | Kilbourn | 4.16kV | UP07 | Mike Gruich opened a transformer OTT4609 at 379 Mountbatton to do a PCB transformer change. | Ottawa | Scheduled Outage | Preventive Maintenance
16771 | 2010 | 8 | 18 | 0.33681 |  | 565 | 188 | 20 | Kilborn | 4.16kV | UP07 | Customers on Mountbatten and summit were isolated to allow crews to replace poles in the backyards with a crane. | Ottawa | Scheduled Outage | Construction
16772 | 2010 | 8 | 18 | 0.80903 |  | 355 | 83 | 14 | Kilborn | 4.16kV | UP07 | Problems on the secondary services cause transformer X2768 at 317 Summit to open. | Ottawa | Defective Equipment
9035 | 2006 | 8 | 23 | 0.36458 |  | 150 | 15 | 6 | Kilborn | 4.16kV | UP07 | Isolated and replaced transformer OTT4846 at 2040 Palmer Pl due to contaminated oil (PCB) | Ottawa | Scheduled Outage | Preventive Maintenance
9095 | 2006 | 8 | 30 | 0.39583 |  | 150 | 12 | 5 | Kilborn | 4.16kV | UP07 | Isolated and replaced transformer OTT4775 at 1471 Farnsworth Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
19163 | 2011 | 9 | 13 | 0.72708 |  | 76 | 194 | 153 | KILBORN | 4.16kV | UP07 | Line patrolled and nothing found lightning storm at the time of the outage. Kilborn (UP07) ID#19163 | Ottawa | Adverse Weather
16974 | 2010 | 9 | 21 | 0.40278 |  | 482 | 201 | 25 | Kilborn DS | 4.16kV | UP07 | UP07 isolated beteen S27654 to EOL at Alta Vista & Mountbatten to allow crews to change poles. | Ottawa | Scheduled Outage | Construction
19289 | 2011 | 9 | 29 | 0.46389 |  | 117 | 23 | 12 | Kilborn | 4.16kV | UP07 | Transformer #X29129 located at 1533 Kilborn Ave opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
19292 | 2011 | 9 | 30 | 0.45139 |  | 90 | 18 | 12 | Kilborn | 4.16kV | UP07 | Transformer #X29129 located at 2201 Reeves Cres opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
19298 | 2011 | 10 | 1 | 0.36528 |  | 431 | 862 | 120 | Kilborn | 4.16kV | UP07 | Removing UP04 & UP07 conductor | Ottawa | Scheduled Outage
19299 | 2011 | 10 | 1 | 0.36597 |  | 403 | 336 | 50 | Kilborn | 4.16kV | UP07 | UP07 and UP04 overhead isolated from Reeves Cr West on Kilborn to remove conductor and transfer UP07 load to the UP03 circuit. | Ottawa | Scheduled Outage
17112 | 2010 | 10 | 14 | 0.375 |  | 260 | 22 | 5 | Kilborn | 4.16kV | UP07 | Transformer X27678 at 325 Summit isolated to allow for pole replacement | Ottawa | Scheduled Outage | Construction
17115 | 2010 | 10 | 14 | 0.375 |  | 260 | 22 | 5 | Kilborn | 4.16kV | UP07 | Transformer X27678 isolated for pole replacement. | Ottawa | Scheduled Outage | Construction
17130 | 2010 | 10 | 17 | 0.64167 |  | 121 | 16 | 8 | Kilborn | 4.16kV | UP07 | X27508 was openned up to allow crews to tighten connections on Secondary bus. 8 customers affected for 121 minutes, Kilborn (up07) | Ottawa | Defective Equipment
17147 | 2010 | 10 | 20 | 0.375 |  | 290 | 48 | 10 | Kilborn | 4.16kV | UP07 | Isolated transformer X27678 at 327 Summit Ave to replace pole | Ottawa | Scheduled Outage | Construction
17169 | 2010 | 10 | 25 | 0.375 |  | 169 | 28 | 10 | Kilborn | 4.16kV | UP07 | X347471 Transformer at 293 Summit was opened to transfer plant to new pole. | Ottawa | Scheduled Outage
17171 | 2010 | 10 | 25 | 0.49236 |  | 99 | 23 | 14 | Kilborn | 4.16kV | UP07 | X27678 transformer at 315 Summit was opened to transfer plant to new pole. | Ottawa | Scheduled Outage
17173 | 2010 | 10 | 25 | 0.45139 |  | 325 | 54 | 10 | KILBORN | 4.16kV | UP07 | crew opened two transformers X 27506 and X27270 between Thessaly and Baffin for service upgrades. | Ottawa | Scheduled Outage | Construction
17176 | 2010 | 10 | 26 | 0.375 |  | 310 | 52 | 10 | KILBORN | 4.16kV | UP07 | Transformer X34471 at 293 Summit isolated to allow for service upgrade | Ottawa | Scheduled Outage | Repair
17177 | 2010 | 10 | 26 | 0.38889 |  | 204 | 10 | 3 | KILBORN | 4.16kV | UP07 | Transformer X39130 at 518 Thessaly isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
17189 | 2010 | 10 | 28 | 0.375 |  | 266 | 133 | 30 | Kilborn | 4.16kV | UP07 | At 09:00 switch S27654 at Plesant Park and Alta Vista was isolated to allow crew to crane poles into back yards. 30 customers were affected for 226 minutes. Kilborn (UP07) ID #17189 | Ottawa | Scheduled Outage
17201 | 2010 | 11 | 1 | 0.41667 |  | 202 | 54 | 16 | Kilborn | 4.16kV | UP07 | Crew isolated single phase overhead section between Baffin and Thorne to re-arrange secondary connections | Ottawa | Scheduled Outage | Construction
17210 | 2010 | 11 | 3 | 0.37847 |  | 305 | 127 | 25 | Kilborn | 4.16kV | UP07 | S27654 at Alta Vista and Mountbatten opened to isolate UP07 red phase section for tree trimming | Ottawa | Scheduled Outage | Construction
17212 | 2010 | 11 | 3 | 0.39583 |  | 150 | 22 | 9 | Kilborn | 4.16kV | UP07 | Isolated transformer at 621 THESSALY CIR OTTAWA for trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
17227 | 2010 | 11 | 5 | 0.4 |  | 64 | 10 | 9 | Kiborn | 4.16kV | UP07 | At 09:36 transformer X27254 was isolated to allow crew to install new service. 9 customers were affected for minutes. Kilborn (UP07) ID# 17227 | Ottawa | Scheduled Outage
17252 | 2010 | 11 | 9 | 0.41667 |  | 210 | 38 | 11 | Kilborn | 4.16kV | UP07 | Transformer #X27502 located at 2042 Thorne opened by crew to replace transformer | Ottawa | Scheduled Outage | Construction
17259 | 2010 | 11 | 11 | 0.35417 |  | 284 | 47 | 10 | Kilborn | 4.16kV | UP07 | Transformer #X26762 located at 424 Thessaly opened by crew and was replaced by X40802 | Ottawa | Scheduled Outage | Construction
17305 | 2010 | 11 | 18 | 0.57639 |  | 119 | 10 | 5 | Kilborn | 4.16kV | UP07 | Transformer #X39131 located at 548 Thessaly Cir opened by crew for a pole change | Ottawa | Scheduled Outage | Construction
19601 | 2011 | 11 | 19 | 0.375 |  | 245 | 49 | 12 | Kilborn | 4.16kV | UP07 | Transformer #X29129 located at 2201 Reeves Cres opened by crew to install new poles | Ottawa | Scheduled Outage | Construction
17334 | 2010 | 11 | 24 | 0.375 |  | 215 | 36 | 10 | KILBORN | 4.16kV | UP07 | Transformer X27253 at 2101 Alta Vista Dr isolated to allow for plant upgrade | Ottawa | Scheduled Outage | Construction
17335 | 2010 | 11 | 24 | 0.5 |  | 35 | 6 | 10 | KILBORN | 4.16kV | UP07 | Transformer X34471 at 280 Mountbatten Ave isolated to upgrade plant | Ottawa | Scheduled Outage
17337 | 2010 | 11 | 24 | 0.61458 |  | 45 | 6 | 8 | Kilborn | 4.16kV | UP07 | Isolated transformer X26762 at 418 Thessaly Dr to repair damaged secondary due to tree branch falling on open wire buss | Ottawa | Foreign Interference | Foreign Object
15430 | 2009 | 11 | 27 | 0.64931 |  | 25 | 2 | 4 | Kilborn | 4.16kV | UP07 | Transformer #X27776 located at 359 Mountbatten Ave isolated for streetlighting work | Ottawa | Scheduled Outage | Construction
19667 | 2011 | 12 | 3 | 0.37153 |  | 215 | 43 | 12 | Kilborn | 4.16kV | UP07 | Transformer X29129 at 2201 Reeves Cres. isolated for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
19674 | 2011 | 12 | 4 | 0.375 |  | 375 | 150 | 24 | KILBORN | 4.16kV | UP07 | Transformers X29128, X27529 and X29129 near the intersection of Kilborn Ave and Reeves isolated to allow for transformer upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
6057 | 2004 | 12 | 13 | 0.95833 |  | 20 | 20 | 60 | Kilborn | 4.16kV | UP07 | J. Streng reports Local fuse opened at Alta Vista & Mountbatten to isolate overhead circuit at the rear of 331 Mountbatten. To make temp repairs for the night. | Ottawa | Tree Contacts | Tree Fallen
17431 | 2010 | 12 | 17 | 0.38542 |  | 115 | 56 | 29 | KILBORN | 4.16kV | UP07 | UP07 R phase cct from S27654 was isolated to allow crew to re-arrange primary. Mt. Batten Pleasant Park area. | Ottawa | Scheduled Outage
7768 | 2005 | 12 | 29 | 0.92153 |  | 203 | 135 | 40 | Kilbourn | 4.16kV | UP07 | Red phase phase opened by oncall crew, to allow tree trimmers to remove a tree on primary circuit at the rear 338 Pleasant Park. | Ottawa | Tree Contacts | Tree Fallen
12152 | 2008 | 3 | 18 | 0.49722 |  | 126 | 21 | 10 | QUEENS | 4.16kV | UQ02 | Transformer at 1880 Logan Ave isolated to allow for transformer change due to leak | Ottawa | Scheduled Outage | Repair
8444 | 2006 | 6 | 7 | 0.6 |  | 98 | 8 | 5 | Queens | 4.16kV | UQ02 | Transfomers #OTT5505 & OTT5507 located at 141 Rodney Cres & 172 Crestview isolated due to changing connections around on the transformer | Ottawa | Scheduled Outage | Construction
10860 | 2007 | 7 | 11 | 0.47917 |  | 30 | 2 | 5 | Queens | 4.16kV | UQ02 | Transformer #OTT684 at Rear 172 Balmoral isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
18664 | 2011 | 7 | 15 | 0.46875 |  | 40 | 3 | 4 | Queens | 4.16kV | UQ02 | Trans X27658 at 173 Heath St was isolated for secondary service upgrades | Ottawa | Scheduled Outage | Preventive Maintenance
8858 | 2006 | 7 | 27 | 0.42014 |  | 140 | 14 | 6 | Queens | 4.16kV | UQ02 | Chris Williams opened xfmr OTT3064 at 159 Rogers to change a transformer with pcbs | Ottawa | Scheduled Outage
13063 | 2008 | 8 | 15 | 0.575 |  | 262 | 4 | 1 | Queens | 4.16kV | UQ02 | Contractor broke cable duct at 1635 Riverside Dr. V670 isolated to allow Greely to inspect cabl;e. Cable okay duct repaired power restored. | Ottawa | Foreign Interference | Dig-in
9019 | 2006 | 8 | 22 | 0.375 |  | 120 | 12 | 6 | Queens | 4.16kV | UQ02 | Transformer #OTT5514 located at the rear of 165 Roger Rd isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
7268 | 2005 | 9 | 2 | 0.64931 |  | 307 | 895 | 175 | QUEENS | 4.16kV | UQ02 | OTTAWA POLICE REPORTS WIRES DOWN AT 1785 OLD RIVERSIDE DR. J. MAGEE REPORTS UQ02 & UQ03 CIRCUITS ON THE GROUND. | Ottawa | Adverse Weather | Wind
15246 | 2009 | 10 | 11 | 0.56875 |  | 67 | 19 | 17 | Queens | 4.16kV | UQ02 | the single white phase tap on the UQ02 overhead at the rear of 170 Heath separated from the overhead connection, crew opened two downstream transformers, and reconnected tap to overhead. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
19359 | 2011 | 10 | 12 | 0.42014 |  | 15 | 5 | 18 | Queens | 4.16kV | UQ02 | Isolated transformer K1264 at 13 San Remo Pvt to replace connections on the secondary | Ottawa | Scheduled Outage | Repair
15348 | 2009 | 11 | 3 | 0.54861 |  | 85 | 13 | 9 | Queens | 4.16kV | UQ02 | Transformer #X27655 located at 160 Balmoral isolated to put up a back yard span guy | Ottawa | Scheduled Outage | Construction
19672 | 2011 | 12 | 4 | 0.53056 |  | 102 | 592 | 375 | Queens | 4.16kV | UQ02 | Possible bad cable/pot head on Old Riverside Dr at Balmoral on UQ02. Cable isolated and power restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7959 | 2006 | 2 | 20 | 0.62986 |  | 683 | 114 | 10 | Queens | 4.16kV | UQ03 | Blown pole mounted transformer replaced | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7977 | 2006 | 3 | 1 | 0.62847 |  | 45 | 6 | 8 | Queens | 4.16kV | UQ03 | Transformer #OTT4979 isolated at 194 Pleasant Park to replace broken arrestor & switch. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8472 | 2006 | 6 | 12 | 0.38542 |  | 25 | 8 | 20 | Queens | 4.16kV | UQ03 | 2 transformers at Billings Ave & Rodney (one is #OTT410) isolated due to changing connections | Ottawa | Scheduled Outage | Construction
10628 | 2007 | 6 | 14 | 0.375 |  | 223 | 15 | 4 | Queens | 4.16kV | UQ03 | Transformer #OTT5507 located at 178 Crestview isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
12626 | 2008 | 6 | 14 | 0.69792 |  | 266 | 94 | 25 | Queens | 4.16kV | UQ03 | A tree fell onto the R phase in the back yard of 187 Mount Batton causing the fuse to blow. | Ottawa | Tree Contacts | Tree Fallen
10740 | 2007 | 6 | 26 | 0.63194 |  | 830 | 14 | 1 | Queens | 4.16kV | UQ03 | A cable fault that feeds V671 @ 1725 Riverside. | Gloucester | Defective Equipment | Equipment Failure - Cause Unknown
18626 | 2011 | 7 | 9 | 0.30208 |  | 799 | 132 | 15 | Queens |  | UQ03 | Very large tree in the rear of 135 Mountbatten came down and took an open wire secondary bus down at transformer X28209. | Ottawa | Tree Contacts | Tree Fallen
7269 | 2005 | 9 | 2 | 0.64931 |  | 307 | 1049 | 205 | QUEENS | 4.16kV | UQ03 | OTTAWA POLICE REPORTS WIRES DOWN AT 1785 OLD RIVERSIDE DR. J. MAGEE REPORTS UQ02 & UQ03 CIRCUITS ON THE GROUND. REPAIRS MADE AND ALL POWER RESTORED. | Ottawa | Adverse Weather | Wind
17002 | 2010 | 9 | 26 | 0.67361 |  | 342 | 40 | 7 | Queens | 4.16kV | UQ03 | Rosemarie Leclair reported to Jeff Meek that a there is a tree on the wires in front of her home at 2087 Riverside Dr. 24/7 Steve Muldoon reported tree interfering with the open buss. ONCALL Doug Mackay isolated Transformer X28207 @ 2077 Riverside to allow (DAVEY) tree contractor to remove tree on secondary wire going to 2087 Riverside. | Ottawa | Tree Contacts | Tree Fallen
17579 | 2011 | 2 | 14 | 0.19167 |  | 104 | 2 | 1 | Queens | 4.16kV | UQ04 | Tree contact at the rear of 1758 Alta Vista caused fused switch to open S26916. jeff reports tree has been removed and will close S26916. | Ottawa | Tree Contacts | Tree Fallen
8302 | 2006 | 5 | 16 | 0.71389 |  | 7 | 7 | 57 | Queens | 4.16kV | UQ04 | UQ04 circuit was opened to enable crew to isolate faulty UQ04 load was restored using the UQ00 circuit. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18393 | 2011 | 6 | 12 | 0.70139 |  | 390 | 32 | 5 | Queens | 4.16kV | UQ04 | A section of primary line at rear of 1598 Abbey rd was isolated to remove a broken tree from the line. | Ottawa | Tree Contacts | Tree Limb Fallen
18675 | 2011 | 7 | 17 | 0.80903 |  | 753 | 1130 | 90 | Queens | 4.16kV | UQ04 | A tree fell from the high winds on the O/H at 1602 Abbey causing the breaker to trip. | Ottawa | Adverse Weather | Wind
9012 | 2006 | 8 | 21 | 0.375 |  | 170 | 14 | 5 | Queens | 4.16kV | UQ04 | Transformer #OTT2244 located at 1594 Abbey isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
9014 | 2006 | 8 | 21 | 0.54167 |  | 110 | 11 | 6 | Queens | 4.16kV | UQ04 | Mike Gruich opened transformer OTT2611 at 1658 Abbey to do a pcb transformer change | Ottawa | Scheduled Outage | Preventive Maintenance
12345 | 2008 | 4 | 25 | 0.41667 |  | 120 | 16 | 8 | Queens | 4.16kV | UQ05 | Isolated transformer OTT449 at 511 Blair St to replace the pole | Ottawa | Scheduled Outage | Construction
5076 | 2004 | 4 | 29 | 0.39583 |  | 225 | 15 | 4 | Queens | 4.16kV | UQ05 | Replace defective kiosk. | Ottawa | Scheduled Outage | Repair
20486 | 2012 | 5 | 9 | 0.67708 |  | 15 | 2 | 6 | Queens | 4.16kV | UQ05 | Isolated transformer X29731 at 1624 Alta Vista dr to repair secondary service | Ottawa | Scheduled Outage | Emergency Services Request
5129 | 2004 | 5 | 11 | 0.39583 |  | 20 | 7 | 22 | Queens | 4.16kV | UQ05 | Transformer K616 at 1490 Station Rd interrupted to change arrestor. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5210 | 2004 | 5 | 27 | 0.39306 |  | 55 | 197 | 215 | Queens | 4.16kV | UQ05 | Truck hit a pole at 1561 Alta Vista bringing down primary wires, circuit opened by request of crew. | Ottawa | Foreign Interference | Vehicle
12501 | 2008 | 5 | 29 | 0.85903 |  | 443 | 74 | 10 | Queens | 4.16kV | UQ05 | Defective O/H transformer at 1611 Dorion was replaced by oncall crew. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18345 | 2011 | 6 | 8 | 0.70417 |  | 11 | 76 | 415 | Queens | 4.16kV | UQ05 | Circuit opened due to storm activity, no cause reported yet, closed in via scada. | Ottawa | Adverse Weather
8727 | 2006 | 7 | 14 | 0.35417 |  | 90 | 12 | 8 | Queens | 4.16kV | UQ05 | Mano Della vedova opened transformer OTT3969 @ 321 Lindsay to install an u/g service | Ottawa | Scheduled Outage
16496 | 2010 | 7 | 20 | 0.42361 |  | 44 | 3 | 4 | Queens | 4.16kV | UQ05 | Transformer #X24828 located at 1572 Dorion opened by crew to replace a service | Ottawa | Scheduled Outage | Construction
8836 | 2006 | 7 | 25 | 0.61111 |  | 126 | 15 | 7 | Queens | 4.16kV | UQ05 | Isolated transformer OTT3732 at 339 Acton St to relocate services | Ottawa | Scheduled Outage | Preventive Maintenance
18853 | 2011 | 7 | 29 | 0.96875 |  | 7 | 48 | 415 | Queens | 4.16kV | UQ05 | Lightning caused the UQ05 breaker to open circuit closed back in. Leitrim ID#18850 | Ottawa | Lightning
8876 | 2006 | 7 | 31 | 0.39583 |  | 195 | 29 | 9 | Queens | 4.16kV | UQ05 | Isolated and replaced transformer OTT3906 at 209 Knox Cres due to contaminated oil (PCB) | Ottawa | Scheduled Outage | Preventive Maintenance
3877 | 2003 | 8 | 8 | 0.75694 |  | 64 | 6 | 6 | Queens | 4.16kV | UQ05 | Crew refused transformer at 349 lindsay, no apparent cause was found to cause outage. | Ottawa | Unknown/Other
7144 | 2005 | 8 | 16 | 0.47569 |  | 100 | 5 | 3 | Queens | 4.16kV | UQ05 | Transformer located at 1163 Station Blvd isolated to change the transformer | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9124 | 2006 | 9 | 6 | 0.375 |  | 75 | 269 | 215 | Queens | 4.16kV | UQ05 | UQ05 tripped due to broken pole on Knox near a construction sight on Knox near Dorion | Ottawa | Foreign Interference | Vehicle
9194 | 2006 | 9 | 11 | 0.39583 |  | 170 | 37 | 13 | QUEEN | 4.16kV | UQ05 | Isolated and replaced transformer OTT3709 at 262 Lennox Park (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
7408 | 2005 | 9 | 29 | 0.82778 |  | 5 | 18 | 215 | UQ | 4.16kV | UQ05 | UQ05 opened to install hot line clamp after repairs made to O/H line. | Ottawa | Tree Contacts | Tree Limb Fallen
13432 | 2008 | 10 | 26 | 0.42431 |  | 67 | 4 | 4 | QUEENS | 4.16kV | UQ05 | Refused switch feeding transformer X24828 at 253 Lennox park ave (Squirrel contact) | Ottawa | Foreign Interference | Animal
17247 | 2010 | 11 | 8 | 0.85486 |  | 25 | 4 | 9 | Queens | 4.16kV | UQ05 | Crews isolated transformer X29743 to change switch feeding transformer X29743 because it was burning up. | Ottawa | Defective Equipment
13617 | 2008 | 11 | 15 | 0.52778 |  | 20 | 2 | 5 | Queens Sub | 4.16kV | UQ05 | at 13:00 trans at 487 BLAIR ST OTTAWA was isolated in order to reomove trees from sec buss | Ottawa | Tree Contacts | Inadequate Trimming
7643 | 2005 | 11 | 21 | 0.99444 |  | 22 | 14 | 215 | Queens | 4.16kV | UQ05 | UQ05 breaker opened by System Operator to allow 24/7 crew to open defective cutout at 1617 Alta Vista. 24/7 crew suspected if they attempted to open the switch, it would break and cause a flash which would trip the cct. Repairs were made and the 1 affected transfomer was restored. | Ottawa | Defective Equipment
9734 | 2006 | 11 | 27 | 0.36806 |  | 50 | 8 | 9 | Queens | 4.16kV | UQ05 | M Rushton isolated trf.# 451 @ 504 Blair for a service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
19768 | 2011 | 12 | 28 | 0.47917 |  | 90 | 12 | 8 | Queens |  | UQ05 | Transformer X29743 at 194 Cluny St. Isolated to renew connections | Ottawa | Scheduled Outage | Repair
15612 | 2010 | 1 | 5 | 0.46181 |  | 70 | 4 | 3 | Queens | 4.16kV | UQ07 | Transformer #X27364 located at 165 Rodney Cres isolated to install new 200 am U/G serv up the pole | Ottawa | Scheduled Outage | Construction
11946 | 2008 | 1 | 17 | 0.40764 |  | 68 | 10 | 9 | Queens | 4.16kV | UQ07 | At 09:47 trans at 1903 Broadmoor Ave was isoalted in order to connect a new service | Ottawa | Scheduled Outage | Construction
11991 | 2008 | 1 | 30 | 0.10694 |  | 326 | 48 | 235 | Queens | 4.16kV | UQ07 | UQ07 opened to isolate damaged section of line. All customer back on at 2:45 except 411 Smyth, Rotel. | Ottawa | Foreign Interference | Vehicle
12064 | 2008 | 2 | 20 | 0.35833 |  | 67 | 9 | 8 | QUEENS | 4.16kV | UQ07 | TRANSFORMER #X27670 AT 171 BILLINGS ISOLATED TO ALLOW FOR REPLACEMENT OF TRIPLEX | Ottawa | Scheduled Outage | Repair
20246 | 2012 | 3 | 27 | 0.67014 |  | 122 | 6 | 3 | Queens | 4.16kV | UQ07 | Trans X27214 at 371 Crestview Rd was isolater in order to install a new pole | Ottawa | Scheduled Outage | Preventive Maintenance
8137 | 2006 | 4 | 11 | 0.99306 |  | 135 | 9 | 4 | Queens | 4.16kV | UQ07 | The overhead transformer fuse had blown due to the secondary service wires getting tangled, open wire service Untangled & tightened wires, transformer refused successfully. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18033 | 2011 | 4 | 28 | 0.59167 |  | 1231 | 6504 | 317 | Queens | 4.16kV | UQ07 | UQ07 circuit breaker auto-reclosed during wind/lightning storm and locked out. Tree fell into over head. Crew cleared trees and circuit was restored to most. | Ottawa | Tree Contacts | Tree Fallen
18059 | 2011 | 4 | 30 | 0.059722 |  | 74 | 21 | 17 | Queens | 4.16kV | UQ07 | 17 customers interrupted on Crestview, Briar and Highridge to clear downed wire in trees. UQ07 cct. | Ottawa | Adverse Weather | Wind
18060 | 2011 | 4 | 30 | 0.059722 |  | 74 | 21 | 17 | Queens | 4.16kV | UQ07 | Temp 199 W opened to isolate section of UQ07 on Crestview to remove downed line in trees and make repair to system neutral. | Ottawa | Defective Equipment
20483 | 2012 | 5 | 9 | 0.40972 |  | 85 | 6 | 4 | Queens | 4.16kV | UQ07 | Transformer X27350 at 1880 Highland Terrace isolated for transformer change | Ottawa | Scheduled Outage | Repair
8345 | 2006 | 5 | 24 | 0.55625 |  | 302 | 151 | 30 | Queens | 4.16kV | UQ07 | 3 overhead transformer isolated on UQ07 section for pole replacement project | Ottawa | Scheduled Outage | Construction
12566 | 2008 | 6 | 6 | 0.725 |  | 220 | 862 | 235 | Queens | 4.16kV | UQ07 | cable dip 2 on UQ07 at Riverside and Smyth, cable on the pole blew. 1 min outage was required on UQ02 to recover load through UQ07-UQ02 tie switches. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10610 | 2007 | 6 | 12 | 0.375 |  | 186 | 46 | 15 | Queen | 4.16kV | UQ07 | Transformer #OTT587 located at 416 Briar isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
10615 | 2007 | 6 | 13 | 0.375 |  | 170 | 23 | 8 | QUEENS | 4.16kV | UQ07 | Transformer #OTT407 at 454 Briar isolated to allow for PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
8516 | 2006 | 6 | 19 | 0.39931 |  | 53 | 2 | 2 | QUEENS | 4.16kV | UQ07 | Isolated transformer OTT4720 at 1922 Norwood Ave to relocate services | Ottawa | Scheduled Outage | Construction
10694 | 2007 | 6 | 21 | 0.375 |  | 161 | 19 | 7 | Overbrook | 4.16kV | UQ07 | At 09:00 trans at 1891 Barnhurst was isolated for PCB trans replacement | Ottawa | Scheduled Outage
16356 | 2010 | 6 | 28 | 0.97569 |  | 23 | 6 | 15 | Queens | 4.16kV | UQ07 | Transformer #X27229 located at 420 Crestview Rd opened by crew to remove branches from secondary buss | Ottawa | Tree Contacts | Tree Limb Fallen
10766 | 2007 | 6 | 30 | 0.57361 |  | 51 | 200 | 235 | Queens | 4.16kV | UQ07 | Vehicle accident on Smyth and Broadmoor broke a pole off, pole cleared and circuit re-energized. | Ottawa | Foreign Interference | Vehicle
10784 | 2007 | 7 | 3 | 0.34722 |  | 501 | 92 | 11 | Queens | 4.16kV | UQ07 | Transformer #OTT5522 located at 384 Crestview isolated due to pole replacement. PC10A#E07870 surrendered | Ottawa | Scheduled Outage | Construction
5547 | 2004 | 7 | 21 | 0.56944 |  | 80 | 8 | 6 | Queens | 4.16kV | UQ07 | Transformer OTT4720 at 1904 Norwood taken out of service to replace the open wire secondary | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16547 | 2010 | 7 | 23 | 0.38194 |  | 55 | 2 | 2 | Queens | 4.16kV | UQ07 | Transformer #X27351 located at 1899 Highland opened by crew to remove service for demolition and also replaced broken cut out | Ottawa | Scheduled Outage | Construction
8992 | 2006 | 8 | 17 | 0.375 |  | 190 | 25 | 8 | Queens | 4.16kV | UQ07 | At 09:00 trans OTT5518 at 380 Roger Rd was isolated for trans replacement ,, 8 custs affected | Ottawa | Scheduled Outage
7198 | 2005 | 8 | 24 | 0.38889 |  | 25 | 1 | 3 | Queens | 4.16kV | UQ07 | Transformer OTT1754 at 348 Roger Rd isolated to relocate services | Ottawa | Scheduled Outage | Construction
9089 | 2006 | 8 | 29 | 0.35417 |  | 170 | 20 | 7 | Queens | 4.16kV | UQ07 | Mike Gruich opened trans OTT5888 to do a pcb transformer change | Ottawa | Scheduled Outage
13193 | 2008 | 9 | 4 | 0.30556 |  | 178 | 36 | 12 | Queens | 4.16kV | UQ07 | Customers in the area of Billings Avenue and Highridge Road called in with no power, crews found a blown transformer fuse had opened due to raccoon contact. Queens UQ07. ID#13193 | Ottawa | Foreign Interference | Animal
16981 | 2010 | 9 | 22 | 0.57431 |  | 2 | 11 | 318 | Queens DS | 4.16kV | UQ07 | UQ07 CB had to be opened to allow 24/7 crews to clear a branch that had fallen on the 3 phase line. Once the circuit was off potential, crews cleared the branch with an insulated stick. | Ottawa | Tree Contacts | Tree Limb Fallen
19265 | 2011 | 9 | 27 | 0.39583 |  | 184 | 18 | 6 | Queens | 4.16kV | UQ07 | Trans X45596 at 1899 Highlanad Terr was isolated in order to transfer plant to new pole | Gloucester | Scheduled Outage | Preventive Maintenance
17023 | 2010 | 9 | 29 | 0.3875 |  | 212 | 32 | 9 | Queens DS | 4.16kV | UQ07 | S14555 at 1929 Highridge was opened to allow crews to complete tree trimming. | Ottawa | Tree Contacts | Tree Limb Fallen
9622 | 2006 | 11 | 8 | 0.42361 |  | 258 | 26 | 6 | Queens | 4.16kV | UQ07 | trf. @ 195 Rodney isolated for pole replacement | Ottawa | Scheduled Outage | Construction
15465 | 2009 | 12 | 3 | 0.60208 |  | 63 | 4 | 4 | Queens | 4.16kV | UQ07 | Transformer #X27220 located at 440 Smyth Rd isolated to install new feed and connect | Ottawa | Scheduled Outage | Construction
13819 | 2008 | 12 | 30 | 0.17361 |  | 110 | 22 | 12 | Queens | 4.16kV | UQ07 | Crew replaced defective cutout on overhead transformer TX27700 at rear of 218 rogers rd. Ottawa. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10078 | 2007 | 3 | 1 | 0.375 |  | 290 | 34 | 7 | QUEENS | 4.16kV | UQ08 | Isolated transformer 65C3C-0100 at 269 Roger Rd to relocate Hydro plante | Ottawa | Scheduled Outage | Construction
17708 | 2011 | 3 | 12 | 0.89306 |  | 39 | 5 | 7 | Queens | 4.16kV | UQ08 | Transformer X27782 at 371 Billings was isolated to allow crew to remove tree that had grown into the secondary conductors. 7 customers were affected for 39 minutes. | Ottawa | Tree Contacts
17757 | 2011 | 3 | 22 | 0.51736 |  | 89 | 3 | 2 | Queens | 4.16kV | UQ08 | Transformer #X27797 located at 1873 Fairbanks Ave opened by crew to install new service | Ottawa | Scheduled Outage | Construction
18076 | 2011 | 5 | 1 | 0.46875 |  | 17 | 2 | 6 | Queens | 4.16kV | UQ08 | A section of o/h line was isolated to allow crew to repair low saging conductors. 6 customers were affected for 17 minutes. Queens (UQ08) ID#18076 | Ottawa | Adverse Weather | Wind
8411 | 2006 | 6 | 2 | 0.41667 |  | 65 | 8 | 7 | Queens | 4.16kV | UQ08 | isolated transformer @ 309 Frost to connect new service | Ottawa | Scheduled Outage | Construction
16177 | 2010 | 6 | 2 | 0.46528 |  | 20 | 2 | 7 | Queens | 4.16kV | UQ08 | Isolated transformer X34756 at 269 Roger Rd to replace secondary service | Ottawa | Scheduled Outage | Emergency Services Request
18585 | 2011 | 7 | 5 | 0.40833 |  | 62 | 16 | 15 | Queens | 4.16kV | UQ08 | Single phase section of UQ08 in the rear of 260 Faircrest was isolated to allow crews to remove a tree. | Ottawa | Tree Contacts | Tree Fallen
8849 | 2006 | 7 | 26 | 0.39583 |  | 102 | 15 | 9 | Queens | 4.16kV | UQ08 | Isolated and replaced transformer OTT1758 at 315 Crestview Ave | Ottawa | Scheduled Outage | Construction
13018 | 2008 | 8 | 7 | 0.74306 |  | 555 | 65 | 7 | Queens | 4.16kV | UQ08 | O/H transformer at the rear of 257 Roger had to be replaced by the Oncall crew due to damage from lightning strike. | Ottawa | Lightning
8972 | 2006 | 8 | 15 | 0.42569 |  | 127 | 17 | 8 | Queens | 4.16kV | UQ08 | Trans OTT411 at 367 Billings Ave isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
8985 | 2006 | 8 | 16 | 0.4375 |  | 120 | 14 | 7 | Queens | 4.16kV | UQ08 | Trans at 267 Rogers Rd isolated to upgrade plant on pole | Ottawa | Scheduled Outage | Preventive Maintenance
8986 | 2006 | 8 | 16 | 0.39722 |  | 178 | 21 | 7 | Queens | 4.16kV | UQ08 | Trans at 264 Faircrest Rd isolated in order to replace PCB trans | Ottawa | Scheduled Outage | Preventive Maintenance
9087 | 2006 | 8 | 29 | 0.51389 |  | 55 | 10 | 11 | Queens | 4.16kV | UQ08 | Mike Gruich opened transformer OTT404 at 275 Billings to change a leaking transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19152 | 2011 | 9 | 13 | 0.375 |  | 19 | 4 | 13 | Queens | 4.16kV | UQ08 | Transformer #X40381 located at 336 Crestview Rd opened by crew to install a new service | Ottawa | Scheduled Outage | Construction
13285 | 2008 | 9 | 24 | 0.56597 |  | 40 | 8 | 12 | QUEENS | 4.16kV | UQ08 | Isolated transformer X27923 at 298 Crestview Rd to remove secondary service | Ottawa | Scheduled Outage | Emergency Services Request
9513 | 2006 | 10 | 25 | 0.68958 |  | 71 | 209 | 177 | Queens | 4.16kV | UQ08 | Dig-in by Greely at 1700 Alta Vista (at Balfour) caused circuit to trip. Damaged section was isolated & power restored. | Ottawa | Foreign Interference | Incorrect Construction
9645 | 2006 | 11 | 13 | 0.43611 |  | 30 | 1 | 2 | Queens | 4.16kV | UQ08 | Mark Rushton opened Transformer at 1881 Fairbanks to disconnect a service | Ottawa | Scheduled Outage | Preventive Maintenance
15396 | 2009 | 11 | 17 | 0.40625 |  | 202 | 40 | 12 | Queens | 4.16kV | UQ08 | At 9:45am 24-7 isolated an overhead section on the UQ08 circuit taking out X34756 at 264 Faircrest to allow the forestry crews to clear away branches, 12 customers were affected and power was restored at 13:07 . Queens (UQ08). ID#15396 | Ottawa | Scheduled Outage | Preventive Maintenance
15562 | 2009 | 12 | 27 | 0.3875 |  | 446 | 632 | 145 | Queens | 4.16kV | UQ08 | Broken tree limb took down primary conductor at 298 Frost, damaged section was cut clear for repairs and power restored to main line. Crew repaired overhead then circuit was opened to allow crew to reconnect line clamp. | Ottawa | Tree Contacts | Tree Limb Fallen
18612 | 2011 | 7 | 8 | 0.4375 |  | 5 | 62 | 744 | Queens | 4.16kV | UQT1 | While working on RTU at Queens sub, the RTU caused UQT1 to trip, relays were verified to be clear & UQT1 closed back in. | Ottawa | Human Element | Commissioning Errors
3812 | 2003 | 7 | 29 | 0.66458 |  | 49 | 512 | 627 | UQ |  | UQT2 | UQT2 tripped, causing outage on circuits UQ05, UQ07, UQ08. SCADA indicated that UQ05 tried to reclose and did not hold. UQ07, UQ08 had reclosing blocked. A.Henry reports circuit UQ05 tripped INST on R W & B phases. | Ottawa | Unknown/Other
20428 | 2012 | 5 | 1 | 0.50347 |  | 3 | 70 | 1400 | Eastview | 4.16kV | UT T1 | While performing switching for the isolation of the Eastview UTT1 the UTX1K1-N breaker was opened causing X1 bus to lose supply. Circuits affected were UT02, UT03, UT04 | Ottawa | Human Element | Switching Errors
12205 | 2008 | 3 | 30 | 0.79167 |  | 60 | 6 | 6 | Eastview | 4.16kV | UT02 | Transformer 65C1B-0123 at 401 Dollard had a blown cutout, crew replaced cutout and customers restored | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14129 | 2009 | 4 | 1 | 0.41319 |  | 10 | 3 | 17 | Eastview | 4.16kV | UT02 | Transformer #X29510 located at 397 Millcraft isolated to relocate plant | Ottawa | Scheduled Outage | Preventive Maintenance
14130 | 2009 | 4 | 1 | 0.4375 |  | 30 | 8 | 17 | Eastview | 4.16kV | UT02 | Transformer #X29509 located at 399 Millcraft isolated to install 2 new poles | Ottawa | Scheduled Outage
14186 | 2009 | 4 | 17 | 0.35417 |  | 364 | 61 | 10 | EASTVIEW | 4.16kV | UT02 | transformer at 401 Irwin Miller isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
14204 | 2009 | 4 | 23 | 0.45833 |  | 140 | 79 | 34 | Eastview | 4.16kV | UT02 | Isolated transformers X29509 at 399 Irwin Miller St and X29510 at 397 Irwin Miller St to replace poles | Ottawa | Scheduled Outage | Construction
16009 | 2010 | 4 | 28 | 0.59653 |  | 34 | 337 | 595 | Eastview | 4.16kV | UT02 | Customers reports balloons blow in the overhead circuit causing outage to circuit. 24/7 reports overhead looks is clear at this time. Circuit picked up all customers restored. | Ottawa | Foreign Interference | Foreign Object
6819 | 2005 | 6 | 28 | 0.083333 |  | 120 | 8 | 4 | Eastview | 4.16kV | UT02 | Trasformer fuse replaced restoring power at this location | Ottawa | Adverse Weather | Extreme Ambient Temperature
5440 | 2004 | 7 | 4 | 0.23264 |  | 21 | 8 | 22 | Eastview | 4.16kV | UT02 | The transformer feeding 395 & 401 Carmen was taken out of service to remove a span guy over the plaza at 320 McArthur for fire dep't | Ottawa | Adverse Environment | Fire
4112 | 2003 | 9 | 21 | 0.14583 |  | 139 | 517 | 223 | Eastview | 4.16kV | UT02 | A single phase came down in the backyard of 396 Carmen at Stevens for no apparent reason. Crew repaired phase midspan and load was restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9361 | 2006 | 10 | 2 | 0.54167 |  | 65 | 6 | 6 | Eastview | 4.16kV | UT02 | Transformer located at the corner of Eve & Stevens isolated to install a new 1/0 service. PC10A#1699 | Ottawa | Scheduled Outage
9368 | 2006 | 10 | 3 | 0.54167 |  | 55 | 6 | 7 | Eastview | 4.16kV | UT02 | AT 13:00 trans at 384 Crete was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9406 | 2006 | 10 | 10 | 0.39583 |  | 100 | 10 | 6 | Eastview | 4.16kV | UT02 | Transformer located at 283 Brebeuf isolated for PCB transformer replacement. PC10A #1100 | Ottawa | Scheduled Outage | Preventive Maintenance
9412 | 2006 | 10 | 10 | 0.54167 |  | 95 | 11 | 7 | Eastview | 4.16kV | UT02 | Transformer located at 399 Millcraft isolated for PCB transformer replacement. PC10A #1188 | Ottawa | Scheduled Outage | Preventive Maintenance
9421 | 2006 | 10 | 12 | 0.52083 |  | 85 | 10 | 7 | Eastview | 4.16kV | UT02 | At 12:30 trans x29170 at 392 Carmen St was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
9565 | 2006 | 10 | 30 | 0.70833 |  | 100 | 33 | 20 | Eastview | 4.16kV | UT02 | Isolated and replaced transformer at 388 Carmen Ave (PCB OIL) | Ottawa | Scheduled Outage | Preventive Maintenance
19741 | 2011 | 12 | 19 | 0.43264 |  | 54 | 9 | 10 | Eastview | 4.16kV | UT02 | Transformer X29154 at 406 Maria Goretti Cir isolated for pole maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
12045 | 2008 | 2 | 14 | 0.51389 |  | 95 | 13 | 8 | Eastview | 4.16kV | UT03 | Replaced broken switch to transformer at 28 Carlotta Ave | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7991 | 2006 | 3 | 7 | 0.013194 |  | 21 | 2 | 7 | Eastview | 4.16kV | UT03 | Overhead transformer at 27 Stevens was interrupted to repair secondary connections. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12377 | 2008 | 5 | 2 | 0.40278 |  | 106 | 18 | 10 | EASTVIEW | 4.16kV | UT03 | Transformer at 344 Dundas isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
6908 | 2005 | 7 | 12 | 0.42431 |  | 16 | 2 | 9 | Eastview | 4.16kV | UT03 | Interrupted power to Transformer OTT5440 at 384 N River Rd to disconnect service | Ottawa | Scheduled Outage | Repair
19047 | 2011 | 8 | 29 | 0.37153 |  | 5 | 1 | 10 | Eastview |  | UT03 | Transformer X29545 @ 27 Stevens Ave was isolated to allow crew to remove branch near drop wire. | Ottawa | Tree Contacts | Tree Limb Fallen
9234 | 2006 | 9 | 17 | 0.29097 |  | 365 | 209 | 277 | Eastview | 4.16kV | UT03 | Top of Hydro pole broken off at River RD & 1 span North of Selkirk rd. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9343 | 2006 | 9 | 29 | 0.45833 |  | 85 | 11 | 8 | Eastview | 4.16kV | UT03 | Transformer #OTT2615 located at 343 Gardner St isolated to replace transformer (PCB oil). PC10A#1197 | Ottawa | Scheduled Outage | Preventive Maintenance
9345 | 2006 | 9 | 29 | 0.55 |  | 61 | 9 | 9 | Eastview | 4.16kV | UT03 | Transformer #K1060 located at 335 Gardner St isolated replace transformer (PCB oil). PC10A#1193 | Ottawa | Scheduled Outage | Preventive Maintenance
9420 | 2006 | 10 | 12 | 0.53472 |  | 82 | 11 | 8 | Eastview | 4.16kV | UT03 | At 12:520 trans at 401 Millcraft Ave was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
15751 | 2010 | 2 | 27 | 0.7125 |  | 65 | 48 | 44 | Eastview | 4.16kV | UT04 | Single phase line clamp burnt off feeding 2 O/H xfmrs & 2 Kiosks K713 & K714 at Eastwood Place & McArthur, line clamp was replaced and line picked up with load disconnected & then the load was restored. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8259 | 2006 | 5 | 9 | 0.41667 |  | 53 | 1 | 1 | Eastview | 4.16kV | UT04 | V444, Vanier community center & arena at 343 Lacasse was isolated due to animal contact at dip pole, 2 cut-outs were changed. The crew also verified cables were not damaged as there is renovation work going on in the arena. | Ottawa | Foreign Interference | Animal
20524 | 2012 | 5 | 16 | 0.040278 |  | 22 | 0 | 1 | Eastview | 4.16kV | UT04 | At 00:58 crew isolated K712 at 353 McArthur to move transformer back on it's pad. 1 customer affected for 22 mins. Eastview, UT04 ID#20524 | Ottawa | Foreign Interference | Vehicle
20535 | 2012 | 5 | 17 | 0.69097 |  | 30 | 6 | 11 | Eastview | 4.16kV | UT04 | Transformer #X21539 located at 197 Maple St opened by crew to disconnect old serv and reconnect new serv. | Ottawa | Scheduled Outage | Repair
8340 | 2006 | 5 | 23 | 0.40347 |  | 375 | 75 | 12 | Eastview | 4.16kV | UT04 | P226 @260 McArthur was isolated and replaced with TP3902 | Ottawa | Scheduled Outage | Construction
7189 | 2005 | 8 | 23 | 0.45833 |  | 8 | 5 | 40 | Eastview | 4.16kV | UT04 | Transformer at 369 Lafontaine St was isolated for contractor to do pole testing | Ottawa | Scheduled Outage | Preventive Maintenance
13280 | 2008 | 9 | 23 | 0.58333 |  | 45 | 10 | 13 | EASTVIEW | 4.16kV | UT04 | Replaced Transformer X29150 due to leaking oil | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
9291 | 2006 | 9 | 24 | 0.45833 |  | 146 | 465 | 191 | Eastview | 4.16kV | UT04 | With the high winds the UT04 O/H circuit slapped together causing the breaker to trip. O/h patrolled nothing fopund. | Ottawa | Adverse Weather | Wind
6012 | 2004 | 12 | 11 | 0.075 |  | 57 | 273 | 195 | Eastview | 4.16kV | UT04 | Circuit opened and locked out due to heavy snow and winds. Investigated calls on Lafontaine and Eastwood place as probable causes was suspected that o/h wires slapped together but nothing was conclusive. | Ottawa | Adverse Weather | Snow
20373 | 2012 | 4 | 23 | 0.83333 |  | 15 | 1 | 5 | Eastview | 4.16kV | UT05 | 4kV transformer X2463 at 94 Montreal Rd. isolated to allow crews to repair a cut out lead. | Ottawa | Scheduled Outage | Repair
20776 | 2012 | 6 | 14 | 0.57639 |  | 1 | 0 | 1 | Eastview | 4.16kV | UT05 | Vault V543 was isolated due to a cable fire at 70 Montreal Rd.. Vault still isolated, to be de-commissioned. Customer decided not to rebuild vault. | Ottawa | Adverse Environment | Fire
9407 | 2006 | 10 | 10 | 0.40278 |  | 140 | 30 | 13 | Eastview | 4.16kV | UT05 | Transformer located at 294 Palace isolated for PCB transformer replacement. PC10A #1198 | Ottawa | Scheduled Outage | Preventive Maintenance
19806 | 2012 | 1 | 10 | 0.41667 |  | 155 | 8 | 3 | Eastview | 4.16kV | UT06 | Transformer X29203 at 214 Montreal Rd. isolated to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
6221 | 2005 | 2 | 19 | 0.95833 |  | 110 | 7 | 4 | Eastview | 4.16kV | UT06 | A connection burnt clear on cable on Mole in Handhole 2350 on Montreal rd. causing part out to 4 customers. Crew replaced mole completely. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20371 | 2012 | 4 | 23 | 0.24167 |  | 412 | 124 | 18 | Eastview | 4.16kV | UT06 | Transformer # 23216 at the rear of 296 Blake Blvd was replaced due to broken primary bushing. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
7195 | 2005 | 8 | 24 | 0.027778 |  | 220 | 37 | 10 | Eastview | 4.16kV | UT06 | Transformer K1197 was opened to replace bad cable 1197-3 between handhole 2350 mole 88 and manhole 2351 mole 66 on the UT06 circuit. Both moles 88 and 66 were also replaced. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
19009 | 2011 | 8 | 24 | 0.71736 |  | 16 | 2 | 8 | Eastview | 4.16kV | UT06 | Transformer #X23218 located at 245 Jeanne Mance opened by crew to do emergency tree trimming due to sparking wires | Ottawa | Tree Contacts | Inadequate Trimming
4101 | 2003 | 9 | 19 | 0.53958 |  | 378 | 6 | 1 | Eastview | 4.16kV | UT06 | Secondary service at 206 Levis Street was torn down due to a tree contact. The service was disconnected to allow an electrician to make repairs to the standpipe. When repairs were made a new service wire was installed and power was restored. | Ottawa | Tree Contacts | Tree Fallen
7435 | 2005 | 10 | 7 | 0.50764 |  | 89 | 7 | 5 | Eastview | 4.16kV | UT06 | Isolated Transformer at 292 Blake to remove vine | Ottawa | Tree Contacts | Inadequate Trimming
4405 | 2003 | 11 | 7 | 0.94722 |  | 39 | 13 | 20 | Eastview | 4.16kV | UT06 | 4kv K1197 at 242 Montreal Rd isolated to repair faulty secondary service. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19547 | 2011 | 11 | 9 | 0.35417 |  | 160 | 19 | 7 | Eastview | 4.16kV | UT06 | Isolated transformer X29204 at 200 Levis Ave to replace pole | Ottawa | Scheduled Outage | Construction
9638 | 2006 | 11 | 10 | 0.70833 |  | 45 | 2 | 3 | Eastview | 4.16kV | UT06 | Transformer located at 364 Lacasse isolated to re-do connections at the pole & stand pipe | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11762 | 2007 | 11 | 25 | 0.33333 |  | 150 | 12 | 5 | Eastview | 4.16kV | UT06 | Leaking transformer at 297 Olmstead in Ottawa isolated for replacement. | Ottawa | Scheduled Outage | Repair
7872 | 2006 | 1 | 30 | 0.52083 |  | 90 | 21 | 14 | Eastview | 4.16kV | UT07 | Transformer OTT1617 at 159 Columbus Ave was isolated to relocate services to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
3228 | 2003 | 3 | 6 | 0.60347 |  | 135 | 2 | 1 | Eastview | 4.16kV | UT07 | Scheduled outage to transformer feeding school at 161 Donald | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6266 | 2005 | 3 | 11 | 0.67708 |  | 74 | 123 | 10 | Eastview | 4.16kV | UT07 | Opened transformer switch to replace triplex at 133 Columbus | Ottawa | Defective Equipment
14456 | 2009 | 7 | 3 | 0.71181 |  | 1255 | 21 | 1 | Eastview | 4.16kV | UT07 | Customer at V333, 201 Donald st reported all-out. Crew found 4kv main breaker tripped, cause unknown. | Ottawa | Unknown/Other
9304 | 2006 | 9 | 25 | 0.54514 |  | 106 | 9 | 5 | Eastview | 4.16kV | UT07 | Transformer #OTT1619 located at 179 Columbus isolated to replace transformer due to PCB content, PC10A#1144 | Ottawa | Scheduled Outage | Preventive Maintenance
9306 | 2006 | 9 | 25 | 0.42014 |  | 110 | 28 | 15 | Eastview | 4.16kV | UT07 | Transformer #OTT1632 located at 205 Columbus isolated to replace transformer due to PCB change, PC10A#110035 | Ottawa | Scheduled Outage | Preventive Maintenance
9307 | 2006 | 9 | 25 | 0.54167 |  | 99 | 31 | 19 | Eastview | 4.16kV | UT07 | Transformer #OTT1626 located at 293 Columbus isolated to replace transformer due to PCB content, PC10A#1145 | Ottawa | Scheduled Outage | Preventive Maintenance
7545 | 2005 | 10 | 31 | 0.54167 |  | 30 | 5 | 10 | eastview | 4.16kV | UT07 | isolated transformer to change pole @ 196 Donald. No xfmer | Ottawa | Scheduled Outage | Construction
6225 | 2005 | 2 | 22 | 0.39236 |  | 320 | 11 | 2 | Eastview | 12/7.2kV | UT12 | K1156 isloated for elec to replace defective main switch at # 2 Columbus | Ottawa | Scheduled Outage | Repair
14083 | 2009 | 3 | 20 | 0.42014 |  | 45 | 22 | 29 | Eastview | 4.16kV | UT12 | Section of UT12 on Wolfe st transferred to UT03 to allow section between temp 94 & temp 137 on Margueritte st made to be made NIU. Clearance for construction of new building. | Ottawa | Scheduled Outage | Construction
5067 | 2004 | 4 | 27 | 0.55903 |  | 384 | 6 | 1 | Eastview | 4.16kV | UT12 | 4 kv transformer K1156 isolated for DanCan Electric to repair defective secondary switch at 2 Columbus. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10392 | 2007 | 5 | 9 | 0.39583 |  | 125 | 29 | 14 | Eastview | 4.16kV | UT12 | Isolated two transformers at Stevens Ave and Marguerite Ave to install new poles | Ottawa | Scheduled Outage | Construction
13284 | 2008 | 9 | 24 | 0.45833 |  | 131 | 11 | 5 | EASTVIEW | 4.16kV | UT12 | Transformer OTT4211 at Wolff St was openned for pole replacement. | Ottawa | Scheduled Outage
9330 | 2006 | 9 | 28 | 0.38542 |  | 70 | 8 | 7 | Eastview | 4.16kV | UT12 | Isolated and replaced transformer OTT 2797 at 106 Glynn Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
9331 | 2006 | 9 | 28 | 0.38611 |  | 69 | 5 | 4 | Eastview | 4.16kV | UT12 | Isolated and replaced transformer OTT 2798 at 116 Glynn Ave (PCB oil) | Ottawa | Scheduled Outage | Preventive Maintenance
15314 | 2009 | 10 | 27 | 0.40972 |  | 44 | 29 | 39 | Eastview | 4.16kV | UT12 | O/H section of the UT12 circuit on Margerite & Wolfe was isolated to transfer the section from the UT03 circuit to UT12 circuit. The section had been temperarily transferred to the UT03 circuit. | Ottawa | Scheduled Outage | Construction
13639 | 2008 | 11 | 19 | 0.41667 |  | 60 | 9 | 9 | EASTVIEW | 4.16kV | UT12 | Xfmr X29547 at 949 Marguerite Ave isolated to allow for pole change | Ottawa | Scheduled Outage | Construction
13803 | 2008 | 12 | 28 | 0.37639 |  | 58 | 1241 | 1284 | Eastview | 13.2kV | UTT1 | Due to skywire falling down into 13kV & 4kV underbuild caused UTT1 breaker and TO30 (TO3UT) breaker to trip, and UT03 auto reclosed. Crew cut skywire clear. 1875 customers affected, 1284 customers affected from UTT1, and 591 customers affected from TO30 | Ottawa | Defective Equipment
19827 | 2012 | 1 | 14 | 0.16042 |  | 402 | 87 | 13 | Edwin | 4.16kV | UV02 | Defective overhead 50kVA transformer at 1245 Cobden required change out, done by On Call crew. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16008 | 2010 | 4 | 28 | 0.41667 |  | 85 | 17 | 12 | Edwin | 4.16kV | UV02 | Transformer #X32714 located at 2528 Iris opened by crew to REPLACE SECONDARY SERVICE, REPLACE SPLIT BOLT CONNECTIONS @ TRANS AND SERVICES @ POLE. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18095 | 2011 | 5 | 5 | 0.37917 |  | 51 | 10 | 12 | Edwin | 4.16kV | UV02 | K778 @ 1312 Greenbank was isolated to allow crew to replace transformer. 12 customer were affected. Edwin UV02. | Ottawa | Scheduled Outage
8325 | 2006 | 5 | 20 | 0.099306 |  | 200 | 128 | 208 | Edwin | 4.16kV | UV02 | UV02 circuit opened due to a local fuse blowing. Tree contact probable cause. | Ottawa | Tree Contacts | Inadequate Trimming
19896 | 2012 | 1 | 25 | 0.90764 |  | 34 | 13 | 23 | EDWIN | 4.16kV | UV03 | Refused transformer X32708 at 2257 Elmira Dr. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4736 | 2004 | 1 | 26 | 0.67222 |  | 52 | 7 | 8 | Edwin | 4.16kV | UV03 | Transformer at 2402 Monroe interrupted to replace a customer service. | Ottawa | Defective Equipment
4739 | 2004 | 1 | 27 | 0.79653 |  | 68 | 9 | 8 | Edwin | 4.16kV | UV03 | O/H transformer at rear of 2402 Monroe was interrupted to make repairs to secondary connections. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13936 | 2009 | 2 | 6 | 0.39931 |  | 30 | 4 | 7 | EDWIN | 4.16kV | UV03 | xfmr X35101 at 1284 Tompkins isolated to allow for service change | Ottawa | Scheduled Outage | Construction
9997 | 2007 | 2 | 7 | 0.51389 |  | 85 | 11 | 8 | Edwin | 4.16kV | UV03 | Dave Jones replaced connections @ TRF. & @ house stack | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10038 | 2007 | 2 | 19 | 0.52083 |  | 83 | 7 | 5 | Edwin | 4.16kV | Uv03 | Lee Piper isolated TRF. @ 2348 Dempsey to do line mtce. | Ottawa | Scheduled Outage | Preventive Maintenance
10045 | 2007 | 2 | 21 | 0.35417 |  | 300 | 25 | 5 | Edwin | 4.16kV | UV03 | Lee isolated TRF. @ 2348 for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
10048 | 2007 | 2 | 21 | 0.31389 |  | 358 | 60 | 10 | Edwin | 4.16kV | UV03 | UV03 overhead section from temp 139 switches to end of line was isolated to change poles and change transformers. 2 transformers removed 1 was installed. | Ottawa | Scheduled Outage | Construction
10067 | 2007 | 2 | 26 | 0.39583 |  | 288 | 29 | 6 | Edwin | 4.16kV | UV03 | Planned outage to transformer on Iris & Dempsey to change transformer. | Ottawa | Scheduled Outage | Repair
3453 | 2003 | 5 | 18 | 0.83333 |  | 20 | 4 | 12 | Edwin | 4.16kV | UV03 | Transfomer supplying 1210 Placid was interrupted in order to replace connections. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20696 | 2012 | 6 | 5 | 0.49653 |  | 40 | 7 | 10 | Edwin | 4.16kV | UV03 | at 11:55, transformer X37159 inn the rear of 1293 Southwood was openned to allow crews to repair broken neutral. 10 customers affected for 40 minutes. Edwin (UV03) ID #20696 | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
10625 | 2007 | 6 | 14 | 0.079861 |  | 45 | 4 | 5 | Edwin | 4.16kV | UV03 | O/H transformer isolated to replace triplex to 2573 Iris. Customers interrupted on Dempsey & Iris. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
8900 | 2006 | 8 | 1 | 0.64514 |  | 291 | 15 | 3 | Edwin | 4.16kV | UV03 | Transformer #55C3D-0410 located at 1136 Soderlind isolated due to broken cut out (lightning) | Ottawa | Lightning | Direct Strike
7050 | 2005 | 8 | 2 | 0.41111 |  | 22 | 3 | 8 | Edwin | 4.16kV | UV03 | Power interruption to transformer at 2366 Sheldon St to replace service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13075 | 2008 | 8 | 18 | 0.67569 |  | 1 | 6 | 388 | EDWIN |  | UV03 | BREAKER OPENED DUE TO WEATHER, CLOSED VIA SCADA | Ottawa | Adverse Weather | Lightning
7240 | 2005 | 8 | 30 | 0.37917 |  | 24 | 2 | 6 | Edwin | 4.16kV | UV03 | Transformer at 6 Aylmer Ave was isolated to replace underground service | Ottawa | Scheduled Outage | Repair
9093 | 2006 | 8 | 30 | 0.45139 |  | 40 | 4 | 6 | EDWIN | 4.16kV | UV03 | Isolated transformer OTT2883 at 38 Grosvenor Ave to replace service | Ottawa | Scheduled Outage | Repair
4163 | 2003 | 9 | 27 | 0.52292 |  | 6 | 2 | 20 | Edwin | 4.16kV | UV03 | Transformer at 2301 Baseline opened to cut free defective service wire. | Ottawa | Defective Equipment
17145 | 2010 | 10 | 20 | 0.55694 |  | 28 | 1 | 3 | EDWIN | 4.16kV | UV03 | Transformer X32713 at rear of 1130 Soderlind isolated to replace connections | Ottawa | Defective Equipment
5848 | 2004 | 10 | 21 | 0.66944 |  | 30 | 6 | 11 | Edwin Sub | 4.16kV | UV03 | Loose connections on secondary. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
13457 | 2008 | 10 | 28 | 0.91042 |  | 5 | 16 | 196 | Edwin | 4.16kV | UV03 | CB CLOSED DETERMINED BY OPERATOR RESPONDING | Ottawa | Adverse Weather
5927 | 2004 | 11 | 25 | 0.66458 |  | 43 | 8 | 11 | Edwin | 4.16kV | UV03 | Transformer 55C3D-0186 at 2325 Elmira was taken out of service to repair bad connection on secondary causing flickering lights to customers. 11 customers on Elmira, Dempsey and Iris were affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
5930 | 2004 | 11 | 26 | 0.45833 |  | 105 | 19 | 11 | Edwin | 4.16kV | UV03 | Xfmr 55C3D-0186 at 2325 Elmira taken out of service to redo secondary connections by Glen Carswell. 11 customers on Elmira Dempsey & Iris affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6082 | 2004 | 12 | 21 | 0.18958 |  | 94 | 9 | 6 | Edwin | 4.16kV | UV03 | Crew refused transformer at rear of 2391 baseline. Possible defective fuse. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6085 | 2004 | 12 | 21 | 0.88681 |  | 363 | 48 | 8 | Edwin | 4.16kV | UV03 | Defective transformer at 1315 Southwood in Ottawa replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
13825 | 2008 | 12 | 30 | 0.71528 |  | 77 | 5 | 4 | WOODROFFE | 4.16kV | UV03 | Transformer X33401 at 2344 Tobin isolated to allow repairs to service at 2340 Tobin | Ottawa | Scheduled Outage | Repair
15599 | 2009 | 12 | 30 | 0.92014 |  | 35 | 4 | 6 | Edwin | 4.16kV | UV03 | Transformer X35121at 2393 Sheldon Avenue was isolated to allow crew to replace defective secondary O/H service. | Ottawa | Defective Equipment
19843 | 2012 | 1 | 17 | 0.43472 |  | 81 | 36 | 27 | EDWIN | 4.16kV | UV04 | Transformer K00362 at 2724 Draper Ave to allow for service upgrade | Ottawa | Scheduled Outage | Construction
20234 | 2012 | 3 | 26 | 0.48889 |  | 31 | 1 | 2 | Edwin | 4.16kV | UV04 | Transformer #X33135 located at 2549 Baseline Rd opened by crew for tree trimming and to make repairs | Ottawa | Tree Contacts | Inadequate Trimming
17834 | 2011 | 4 | 5 | 0.86111 |  | 65 | 5 | 5 | Edwin | 4.16kV | UV04 | Transformer #X33990 located at 1183 Placid opened up due to defective transformer switch lead | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
17961 | 2011 | 4 | 19 | 0.13889 |  | 78 | 52 | 40 | EDWIN |  | UV04 | A broken cutout at UV04 White phase dip to K197 caused an outage to 40 customers for 78 mins. Edwin UV04 ID # 17961 | Ottawa | Defective Equipment
10579 | 2007 | 6 | 8 | 0.85 |  | 481 | 56 | 7 | Edwin | 4.16kV | UV04 | defective transfomer at 1340 Morrison was replaced. Possible direct lightning strike. | Ottawa | Adverse Weather | Lightning
14619 | 2009 | 6 | 26 | 0.60764 |  | 25 | 0 | 1 | Edwin |  | UV04 | V338 at 2675 Draper Ave Catholic School shut down for electrician to replace secondary fuse. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
14811 | 2009 | 7 | 23 | 0.41528 |  | 220 | 191 | 52 | Edwin | 4.16kV | UV04 | Crew isolated K361 & K362 as part of PCB replacement program. | Ottawa | Scheduled Outage | Preventive Maintenance
15003 | 2009 | 8 | 25 | 0.55347 |  | 28 | 9 | 20 | Edwin | 4.16kV | UV04 | Isolated K00374 at 1170 Morrison Dr to obtain oil sample | Ottawa | Scheduled Outage | Preventive Maintenance
11301 | 2007 | 9 | 13 | 0.39931 |  | 318 | 74 | 14 | Edwin | 4.16kV | UV04 | Replaced leaking Transformer K1072 on 47 Pathway. | Ottawa | Scheduled Outage
15103 | 2009 | 9 | 14 | 0.75069 |  | 434 | 65 | 9 | Edwin | 4.16kV | UV04 | Defective Xfrm'r X37905 at 1284 Morrison repaired by Rudy Grisel. | Ottawa | Defective Equipment
7345 | 2005 | 9 | 19 | 0.40625 |  | 23 | 0 | 1 | Edwin | 4.16kV | UV04 | 4KV VAULT V338 @ 2675 DRAPER WAS ISOLATED TO REPAIR DEFECTIVE DIP SWITCH | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9895 | 2007 | 1 | 1 | 0.62986 |  | 230 | 766 | 300 | Edwin | 4.16kV | UV05 | Circuit UV05 auto/reclose/auto trip. Faulted W phase cable section feeding K477 1250 Pinecrest. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9914 | 2007 | 1 | 10 | 0.40764 |  | 103 | 19 | 11 | Edwin | 4.16kV | UV05 | K477 asbestos removal at 1250 Pinecrest | Ottawa | Scheduled Outage | Preventive Maintenance
3173 | 2003 | 2 | 8 | 0.79861 |  | 140 | 23 | 10 | UV | 4.16kV | UV05 | Defective cut-out replaced at 2383 Malone cr. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17607 | 2011 | 2 | 18 | 0.62153 |  | 223 | 1267 | 341 | Edwin | 4.16kV | UV05 | Primary line down in the rear of 1165 Stanton caused UV05 to trip. On call crew called in to make back yard repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4878 | 2004 | 3 | 11 | 0.58333 |  | 35 | 6 | 11 | Edwin | 4.16kV | UV05 | Transformer at 1318 Firestone interrupted to replace defective switch. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
20235 | 2012 | 3 | 26 | 0.53819 |  | 70 | 9 | 8 | Edwin | 4.16kV | UV05 | Transformer #X32665 located at 2383 Malone Cres opened by crew to change service and cutout. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
20307 | 2012 | 4 | 11 | 0.72361 |  | 163 | 24 | 9 | Edwin | 4.16kV | UV05 | P99 at 2750 Iris was decomissioned and customers are now fed from TP9241 on the 13kV TW2UV circuit. | Ottawa | Scheduled Outage
15939 | 2010 | 4 | 15 | 0.375 |  | 264 | 48 | 11 | EDWIN | 4.16kV | UV05 | Transformer X32663 at 2404 Malone and X32662 at 2392 Malone isolated to allow for tree trimming | Ottawa | Tree Contacts | Inadequate Trimming
18044 | 2011 | 4 | 28 | 0.59792 |  | 410 | 2303 | 337 | Edwin | 4.16kV | UV05 | UV05 auto-reclosed and locked out during wind/lightning storm. Closed via scada unsuccessfully. Crews found tree in overhead, removed tree and restored power. | Ottawa | Tree Contacts | Tree Fallen
6605 | 2005 | 5 | 25 | 0.62153 |  | 434 | 1199 | 301 | UV | 4.16kV | UV05 | UV05 cct opened, patrol found no problem, riser cable tested OK, all cable dips opened & cct picked up. Defective cable found between K 471 & K472, also bad insulator at K473. K473 was repaired & defective cable was isolated. Fused dip to K473 did not operate correctly resulting in cct outage. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6641 | 2005 | 6 | 2 | 0.41528 |  | 244 | 65 | 16 | UV | 4.16kV | UV05 | K471, K472 supplying 1250 Pinecrest were isolated for planned repair & to complete repair of defective primary cable. | Ottawa | Scheduled Outage | Repair
6685 | 2005 | 6 | 9 | 0.375 |  | 300 | 390 | 78 | Edwin | 4.16kV | UV05 | Trans K472 ar 1250 Pinecrest isolated in order to clean up oil spilll | Ottawa | Scheduled Outage | Emergency Services Request
12721 | 2008 | 6 | 25 | 0.38125 |  | 153 | 43 | 17 | Edwin | 4.16kV | UV05 | Isolated the O/H on Thorson Ave from switch S28196 to allow for tree trimming. | Ottawa | Scheduled Outage
10831 | 2007 | 7 | 9 | 0.37708 |  | 13 | 65 | 301 | Edwin | 4.16kV | UV05 | Circuit tripped and locked out after direct lightening strike. | Ottawa | Lightning | Direct Strike
12813 | 2008 | 7 | 10 | 0.3625 |  | 23 | 13 | 34 | Edwin | 4.16kV | UV05 | at 8:42am Jamie LeBlanc isolated P99 at 2750 Iris to allow crews to disconnect secondary to 2750 Iris, building will be eventually demolished under PC10A#1732. 34 customers were affected and power was restored at 9:05am. Edwin (UV05). ID#12813. | Ottawa | Scheduled Outage | Construction
7316 | 2005 | 9 | 12 | 0.40625 |  | 120 | 6 | 3 | Edwin | 4.16kV | UV05 | Transformer at 1169 Stanton Ave was isolated and replaced to a larger size from two transformers 25KVA and a 37.5 KVA to a 75 KVA | Ottawa | Scheduled Outage | Construction
11432 | 2007 | 10 | 1 | 0.59722 |  | 30 | 3 | 6 | Edwin | 4.16kV | UV05 | Transformer #55C3C-0284 located at 2429 Sudbury Ave isolated to change secondary connections | Ottawa | Scheduled Outage | Emergency Services Request
19388 | 2011 | 10 | 16 | 0.31944 |  | 430 | 65 | 9 | Edwin DS | 4.16kV | UV05 | O/H crew established PC10A# 00829 on P99 to replace the cable dip & relocate the transformer. | Ottawa | Scheduled Outage | Construction
4331 | 2003 | 10 | 23 | 0.875 |  | 28 | 3 | 7 | EDWIN | 4.16kV | UV05 | Overhead transformer isolated to replace connection on customer service. Outage effected power to 7 customers on Firestone. Customers notified 45 mins. Before outage. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11600 | 2007 | 10 | 25 | 0.38194 |  | 30 | 8 | 16 | EDWIN | 4.16kV | UV05 | Transformer #55C3C-0187 at 1214 Firestone isolated to allow for replacement of service | Ottawa | Scheduled Outage | Repair
17306 | 2010 | 11 | 18 | 0.39653 |  | 379 | 341 | 54 | Edwin DS | 4.16kV | UV05 | Crews istalled TEMP 60 and establised PC10A # 1685 on the UV05 O/H section from TEMP 60 to EOL to allow crews to clear a tree that had fallen. | Ottawa | Tree Contacts | Tree Fallen
9878 | 2006 | 12 | 23 | 0.48264 |  | 55 | 9 | 10 | Edwin | 4.16kV | UV05 | Shawn isolated TRF. @ 1220 Stanton to replace secondary connections | Ottawa | Scheduled Outage | Preventive Maintenance
6096 | 2004 | 12 | 24 | 0.43403 |  | 45 | 2 | 3 | Edwin | 4.16kV | UV05 | Transformer P132 in rear of 1130 Sunderland was taken out of service to repair a bad connection at pole. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10065 | 2007 | 2 | 26 | 0.41667 |  | 255 | 21 | 5 | Edwin | 4.16kV | UV06 | Isolated transformer 55C3D-0261 at 2348 Dempster Ave to relocate Hydro plant | Ottawa | Scheduled Outage | Preventive Maintenance
4947 | 2004 | 3 | 30 | 0.56944 |  | 50 | 4 | 5 | Edwin | 4.16kV | UV06 | Transformer #55C3D-0261 was opened to allow crew to replace defective service at 2348 Dempsey Ave. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13943 | 2009 | 2 | 8 | 0.34028 |  | 470 | 31 | 4 | Edwin | 4.16kV | UV07 | Transformer P15 at 1120 Morrison Dr isolated for replacement. | Ottawa | Scheduled Outage | Construction
17668 | 2011 | 3 | 4 | 0.98472 |  | 388 | 1118 | 492 | Edwin |  | UV07 | At 17:15 UV07 CB auto reclosed and then locked-out on the White Phase. Crews patrolled the line and found no apparent cause, they proceeded to open the dips feeding the two underground loops on UV07. On Call crew sectionallized the cables and found a faulted cable section on one of the loops. Edwin (UV07) ID # 17668 | Ottawa | Defective Equipment
20251 | 2012 | 3 | 29 | 0.39236 |  | 7 | 3 | 25 | Edwin | 4.16kV | UV07 | Transformer #K231 located at 2530 Draper Ave opened by crew to lift the lid off the pedestal to disconnect a unit for the electrician | Ottawa | Scheduled Outage | Construction
20303 | 2012 | 4 | 11 | 0.40556 |  | 13 | 107 | 492 | Edwin | 4.16kV | UV07 | A tree trimming crew's bucket truck made contact with overhead conductor causing UV07 breaker to open and lock out under hold off protection. No injuries or equipment damage reported. | Ottawa | Human Element | Incorrect Use of Equipment
6408 | 2005 | 4 | 13 | 0.63542 |  | 13 | 4 | 19 | Edwin | 4.16kV | uv07 | Transformer #K231 located at 2530 Draper isolated to gain access to live front (for 999D Morrison) to change customer secondary service. | Ottawa | Foreign Interference
6459 | 2005 | 4 | 25 | 0.46181 |  | 15 | 5 | 19 | Edwin | 13.2kV | UV07 | Had power interruption to transformer K00231 at 999 Morrison Dr to reconnect underground service | Ottawa | Scheduled Outage | Emergency Services Request
10834 | 2007 | 7 | 9 | 0.37708 |  | 92 | 360 | 235 | Edwin | 4.16kV | UV07 | Circuit trpped and locked out after direct lightening strike. Pothead and switches repaired and circuit was restored | Ottawa | Lightning | Direct Strike
5536 | 2004 | 7 | 20 | 0.65903 |  | 16 | 7 | 25 | Edwin | 4.16kV | UV07 | Transformer K236 was interrupted to repair U/G service that was damaged by a dig-in. | Ottawa | Foreign Interference | Dig-in
5621 | 2004 | 8 | 6 | 0.54861 |  | 60 | 9 | 9 | Edwin | 4.16kV | UV07 | Dave reports transformer was opened to allow crews to replace service to 2698 Iris St. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11673 | 2007 | 11 | 6 | 0.50417 |  | 14 | 2 | 10 | Edwin | 4.16kV | UV07 | Transformer at 1045 Morrison isolated to connect new service | Ottawa | Scheduled Outage | Construction
4682 | 2004 | 1 | 7 | 0.39236 |  | 120 | 22 | 11 | UW | 4.16kV | UW01 | Tx Ott2354 @ 1321 Ferguson was opened to replace open wire secondaries. | Ottawa | Scheduled Outage | Preventive Maintenance
4684 | 2004 | 1 | 7 | 0.52153 |  | 124 | 8 | 4 | UW | 4.16kV | UW01 | A transformer at the rear of 1328 Heather Way was opened to replace open wire secondary. | Ottawa | Scheduled Outage | Preventive Maintenance
6136 | 2005 | 1 | 15 | 0.49236 |  | 4 | 14 | 213 | Woodroffe | 4.16kV | UW01 | UW01 breaker inadvertantly opened. Breaker would not close back in until racking interlock handle was re-positioned. | Ottawa | Human Element | Switching Errors
20357 | 2012 | 4 | 19 | 0.73958 |  | 110 | 18 | 10 | Woodroffe | 4.16kV | UW01 | Transformer #X32554 located at 1743 Baseline opened up due to defective switch, crew replaced switch and arrestor | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
5030 | 2004 | 4 | 20 | 0.49444 |  | 60 | 4 | 4 | Woodroffe | 4.16kV | UW01 | Transformer at 1796 Forman isolated to put cover up on line for tree trimming. | Ottawa | Scheduled Outage | Preventive Maintenance
20706 | 2012 | 6 | 7 | 0.40278 |  | 50 | 12 | 15 | WOODROFFE | 4.16kV | UW01 | Transformer X34450 at 1691 Baseline Rd. isolated to allow for connection of new service | Ottawa | Scheduled Outage | Construction
6690 | 2005 | 6 | 10 | 0.39583 |  | 50 | 5 | 6 | Woodroffe | 4.16kV | UW01 | Opened transformer OTT4842 to replace overhead service at 1821 Paisley Ave | Ottawa | Scheduled Outage | Repair
18724 | 2011 | 7 | 18 | 0.69861 |  | 202 | 279 | 83 | Woodroffe | 4.16kV | UW01 | S10334 white phase was opened to allow conductor repair of damage caused by tree limbs | Ottawa | Tree Contacts | Tree Limb Fallen
14865 | 2009 | 7 | 28 | 0.73958 |  | 30 | 3 | 6 | Woodroffe | 4.16kV | UW01 | Transformer #X31741 located at 1310 Agincourt isolated to install single point | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16734 | 2010 | 8 | 14 | 0.60764 |  | 49 | 245 | 761 | Woodroffe | 4.16kV | UW01 | UW01 auto-reclosed twice and TW13 opened at same time for no apparent reason. | Ottawa | Unknown/Other | No Apparent Cause
4554 | 2003 | 12 | 3 | 0.54514 |  | 113 | 30 | 16 | UW | 4.16kV | UW01 | At 13:05, Tx OTT 3063 @ 1317 Heather way was opened to replace open wire services. Power was restored at 14:58. 16 customers affected on Ainsley & Heather way. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4576 | 2003 | 12 | 8 | 0.54861 |  | 99 | 16 | 10 | Woodroffe | 4.16kV | UW01 | Inetruption to replace the service at 1785 Forman ID#4776 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4587 | 2003 | 12 | 10 | 0.41667 |  | 100 | 18 | 11 | Woodroffe | 4.16kV | UW01 | Transformer at rear of 1321 Fergusen was open to change open wire service to triplex. 11 cust. | Ottawa | Scheduled Outage | Construction
4611 | 2003 | 12 | 16 | 0.47222 |  | 80 | 5 | 4 | Woodroffe Sub |  | UW01 | Transformer 4841 at 1802 Forman was taken out of service to replace a defective open wire service. 4 customers on Paisley & Forman were affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4612 | 2003 | 12 | 16 | 0.56944 |  | 60 | 7 | 7 | Woodroffe Sub | 4.16kV | UW01 | Transformer 2661 at 1786 Gilbert was taken out of service to replace a defective open wire service. 7 customers on Gage & Gilbert were affected. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17476 | 2011 | 1 | 10 | 0.5625 |  | 25 | 4 | 9 | Woodroffe | 4.16kV | UW02 | Isolated transformer X34720 at 1213 Maitland Ave to connect new streetlight service | Ottawa | Scheduled Outage | Emergency Services Request
6410 | 2005 | 4 | 14 | 0.33333 |  | 6 | 1 | 6 | Woodroofe | 4.16kV | UW02 | Trans OTT785 at 1716 Baseline isolated to replace defective live line clamp. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12391 | 2008 | 5 | 5 | 0.40625 |  | 105 | 14 | 8 | Woodroffe | 4.16kV | UW02 | Isolated and replaced transformer X33431 at 1243 Marygrove Cir (PCB Oil) | Ottawa | Scheduled Outage | Preventive Maintenance
16228 | 2010 | 6 | 9 | 0.20833 |  | 132 | 548 | 249 | Woodroffe | 4.16kV | UW02 | UW02 circuit complete isolated to allow crews to replace defective insulators at Baseline and Clyde. 249 customers affected and streets affected are Clyde, Maitland, Cameo, Greyrock, Castlehill, marygrove and Henry Farm | Ottawa | Defective Equipment | Repair
5348 | 2004 | 6 | 21 | 0.39583 |  | 30 | 4 | 9 | UW | 4.16kV | UW02 | Tx OTT4159 on UW02 was opened to replace service connections. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
16549 | 2010 | 7 | 23 | 0.45486 |  | 35 | 3 | 5 | Woodroffe | 4.16kV | UW02 | Transformer #X35126 located at 1256 Maitland opened by crew to replace triplex service | Ottawa | Scheduled Outage | Construction
11373 | 2007 | 9 | 24 | 0.51389 |  | 40 | 6 | 9 | Woodroffe | 4.16kV | UW02 | Isolated transformer OTT4159 at 1240 Marygrove Cir to replace connections on the secodary service to 1240 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15191 | 2009 | 9 | 30 | 0.42361 |  | 25 | 2 | 6 | WOODROFFE UW | 4.16kV | UW02 | transformer X32567 at 1716 Baseline isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
19371 | 2011 | 10 | 13 | 0.84722 |  | 20 | 3 | 9 | Woodroffe | 4.16kV | UW02 | Isolated transformer X35126 at 1240 Marygrove Cir to replace secondary service | Ottawa | Scheduled Outage | Emergency Services Request
9480 | 2006 | 10 | 20 | 0.43056 |  | 55 | 8 | 9 | Woodroffe | 4.16kV | UW02 | Transformer #OTT4157 located at 1215 Maitland isolated to relocate two O/H services. PC10A #1398 | Ottawa | Scheduled Outage | Preventive Maintenance
17164 | 2010 | 10 | 24 | 0.61806 |  | 45 | 5 | 7 | Woodroffe | 4.16kV | UW02 | overhead transformer X32054at 1468 baseline was opened for crew to re-arrange overhead circuit. | Ottawa | Scheduled Outage | Construction
4680 | 2004 | 1 | 6 | 0.40278 |  | 140 | 35 | 15 | Woodroffe | 4.16kV | UW03 | Transformer 2393 at 1232 Field St isolated to replace defective service wire. | Ottawa | Scheduled Outage | Repair
13897 | 2009 | 1 | 27 | 0.45833 |  | 60 | 12 | 12 | Woodroffe | 4.16kV | UW03 | Transformer #X31735 located at 2196 Calder isolated to install new service to streetlight feed | Ottawa | Scheduled Outage | Preventive Maintenance
4776 | 2004 | 2 | 10 | 0.42986 |  | 121 | 18 | 9 | Woodroffe | 4.16kV | UW03 | Transformer OTT4168 at 1239 Major St isolated to replace a service. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14002 | 2009 | 2 | 24 | 0.92361 |  | 278 | 204 | 44 | Woodroffe Sub | 4.16kV | UW03 | Primary single phase circuit down, at 1113 Lizard St, causing S22909 W to blow. Repairs to primary circuit made, and all power restored. | Ottawa | Defective Equipment
17645 | 2011 | 2 | 25 | 0.42708 |  | 35 | 8 | 13 | Woodroffe | 4.16kV | UW03 | Isolated transformer X35095 at 1249 Woodroffe Ave for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
10129 | 2007 | 3 | 14 | 0.54028 |  | 38 | 108 | 170 | Walkley | 4.16kV | UW03 | A tree limb to trip UW03 Breaker and also TW13 tripped at the same time. Limb removed and power restored. | Ottawa | Tree Contacts | Tree Limb Fallen
15872 | 2010 | 3 | 30 | 0.60972 |  | 4 | 1 | 15 | WOODROFFE | 4.16kV | UW03 | TRANSFORMER # X32793 LOCATED AT 2146 BERWICK AVE ISOLATED TO ALLOW FUSE CHANGE FOR STREET LIGHT | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18099 | 2011 | 5 | 5 | 0.72847 |  | 21 | 2 | 6 | Woodroffe | 4.16kV | UW03 | Transformer X33782 at 1132 Bedbrooke St isolated to reconnect service after storm repairs | Ottawa | Scheduled Outage | Repair
16092 | 2010 | 5 | 16 | 0.83681 |  | 33 | 5 | 9 | Woodroffe | 4.16kV | UW03 | Transformer X32786 was isolated to allow crew to install new triplex at 1114 Checkers. | Ottawa | Defective Equipment
8320 | 2006 | 5 | 19 | 0.45833 |  | 30 | 5 | 10 | Woodroffe | 4.16kV | UW03 | Jeff Magee opened transformer OTT1378 to do secondary repairs. | Ottawa | Scheduled Outage | Preventive Maintenance
14403 | 2009 | 5 | 23 | 0.9375 |  | 143 | 24 | 10 | Woodroffe UW | 4.16kV | UW03 | Broken cut-out replaced at transformer X33784, 1218 Major st. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
20592 | 2012 | 5 | 25 | 0.7875 |  | 89 | 444 | 299 | Woodroffe | 4.16kV | UW03 | UW03 auto-reclosed and locked out during storm. Crew found branch at 1162 Field. Branch removed and circuit restored. | Ottawa | Adverse Weather | Wind
10622 | 2007 | 6 | 13 | 0.60417 |  | 76 | 16 | 13 | Woodroffe | 4.16kV | UW03 | At 14:30 trans at 1249 Woodroffe was isolated in order to replace a broken cutout | Ottawa | Defective Equipment | Repair
14566 | 2009 | 6 | 18 | 0.66319 |  | 66 | 295 | 283 | Woddroffe Sub | 4.16kV | uw03 | SCADA indicates a UW03 bkr auto/reclose/auto. Due to tree contact 283 customers affected. | Ottawa | Tree Contacts | Inadequate Trimming
8792 | 2006 | 7 | 20 | 0.68542 |  | 78 | 9 | 7 | Woodroffe | 4.16kV | UW03 | Transformer #OTT1381 located at 1155 Woodroffe Ave isolated due to a broken switch | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5555 | 2004 | 7 | 22 | 0.74306 |  | 115 | 58 | 30 | Woodriffe | 4.16kV | UW03 | Broken switch at Iris & Checkers replaced | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
3828 | 2003 | 8 | 1 | 0.42153 |  | 15 | 2 | 8 | Woddroffe | 4.16kV | UW03 | Transformer isolated to remove vines that had growen around it. | Ottawa | Foreign Interference | Foreign Object
3913 | 2003 | 8 | 18 | 0.41319 |  | 103 | 9 | 5 | Woodroffe | 13.2kV | UW03 | Crew opened transformer at 1298 Hanbury to change defective open wire service to Triplex. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7367 | 2005 | 9 | 23 | 0.4375 |  | 50 | 5 | 6 | Woodroofe | 4.16kV | UW03 | Isolated transformer # 1063 at 1162 Field st to change the Service wires | Ottawa | Scheduled Outage | Preventive Maintenance
16992 | 2010 | 9 | 24 | 0.79861 |  | 74 | 231 | 296 | Woodroffe | 4.16kV | UW03 | A branch fell on the O/H at Field and Iris and a tap also burnt off at Iris/Woodroffe on the UW03 circuit. The UW03 breaker did not open causing the TW13 to trip. | Ottawa | Adverse Weather | Wind
9323 | 2006 | 9 | 27 | 0.45486 |  | 135 | 11 | 5 | Woodroffe | 4.16kV | UW03 | Lee Piper isolated xfmr OTT1386 to replace a xfmr. Used tag PC10A # 900 | Ottawa | Scheduled Outage | Preventive Maintenance
15242 | 2009 | 10 | 9 | 0.74861 |  | 252 | 38 | 9 | Woodroffe | 4.16kV | UW03 | Transformer #X32786 located at 1119 Woodroffe isolated for tree removal | Ottawa | Tree Contacts | Tree Fallen
15259 | 2009 | 10 | 14 | 0.43611 |  | 284 | 61 | 21 | Woodroffe | 4.16kV | UW03 | UW03 line section on Dublin Ave with 4 O/H transformers was isolated to replace a defective pole . 2 transformers were restored with the line section the other 2 transformers were restored as the secondary plant was transferred. Customers affected were on Dublin, Bel-Air, Bedbrooke & Field. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15281 | 2009 | 10 | 20 | 0.46528 |  | 20 | 2 | 7 | Woodroffe | 4.16kV | UW03 | isolated transformer X32789 at 1129 Woodroffe Ave for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
19565 | 2011 | 11 | 12 | 0.39028 |  | 325 | 1625 | 300 | Woodroffe | 4.16kV | UW03 | The Woodroffe UW03 A/R and locked open due to fallen tree on O/H line at rear of 2143 Calder. | Ottawa | Tree Contacts | Tree Fallen
4589 | 2003 | 12 | 11 | 0.54861 |  | 155 | 439 | 170 | Woodroffe Sub | 4.16kV | UW03 | A white phase line clamp burned and the phase came down on Calder Ave causing UW03 to trip to lockout. Repairs were made and power restored. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17572 | 2011 | 2 | 11 | 0.67708 |  | 15 | 2 | 7 | Woodroffe | 4.16kV | UW04 | Xfmr 32760 at 1089 Minnetonka isolated to connect new service | Ottawa | Scheduled Outage | Construction
17597 | 2011 | 2 | 16 | 0.61458 |  | 15 | 2 | 7 | Woodroffe | 4.16kV | UW04 | J Streng isolated trans to remove a service feeding a Police logger | Ottawa | Scheduled Outage | Preventive Maintenance
17598 | 2011 | 2 | 16 | 0.61458 |  | 15 | 2 | 7 | Woodroffe | 4.16kV | UW04 | J Streng isolated trans to remove a service feeding a Police logger | Ottawa | Scheduled Outage | Construction
5589 | 2004 | 7 | 31 | 0.55972 |  | 120 | 12 | 6 | UW | 4.16kV | UW04 | Animal contact at 2272 Iris, Tx OTT3396 caused circuit to A/R, Switch & arrestor had to be replaced. | Ottawa | Foreign Interference | Animal
5812 | 2004 | 9 | 17 | 0.62708 |  | 74 | 146 | 118 | Woodroffe Sub | 4.16kV | UW04 | Wires burnt off in tree limbs. Circuit interrupted to clear & make repairs. | Ottawa | Tree Contacts | Inadequate Trimming
17018 | 2010 | 9 | 28 | 0.74722 |  | 34 | 91 | 160 | Woodroffe | 4.16kV | UW04 | UW04 circuit opened, no reports from customers, police or fire. Closed and held via SCADA. Patrolled by Billy Seamen, nothing found. | Ottawa | Unknown/Other | No Apparent Cause
5895 | 2004 | 11 | 16 | 0.42708 |  | 125 | 42 | 20 | Woodroffe | 4.16kV | UW04 | Transformer OTT4501 isolated to make repairs to primary circuit. | Ottawa | Scheduled Outage
19750 | 2011 | 12 | 20 | 0.46875 |  | 45 | 6 | 8 | WOODROFFE | 4.16kV | UW04 | Transformer X32760 at 1089 Minnetonka Rd isolated to allow for upgraded service | Ottawa | Scheduled Outage | Construction
17501 | 2011 | 1 | 21 | 0.32639 |  | 15 | 1 | 3 | WOODROFFE UW | 4.16kV | UW05 | Transformer X35063 at 1945 Baseline Rd isolated to move move phases up | Nepean | Scheduled Outage | Construction
4896 | 2004 | 3 | 15 | 0.51042 |  | 105 | 5 | 3 | Woodroffe | 4.16kV | UW05 | transformer at 1135 Albany opened to change secondary services. | Ottawa | Defective Equipment
4905 | 2004 | 3 | 16 | 0.55208 |  | 70 | 16 | 14 | Woodroffe | 4.16kV | UW05 | Transformer @ 1188 was opened to replace secondary open wire services. | Ottawa | Scheduled Outage | Preventive Maintenance
14328 | 2009 | 5 | 8 | 0.82639 |  | 26 | 4 | 10 | Woodroffe | 4.16kV | UW05 | Transformer at 1306 Albany isolated to allow crew to reconnect service. | Ottawa | Scheduled Outage | Repair
18190 | 2011 | 5 | 20 | 0.34375 |  | 33 | 1 | 2 | Woodroffe | 4.16kV | UW05 | Transformer X35063 @ 1945 Baseline was open to allow crew to perform service upgrade. 2 customer were affected. Woodroffe (UW05) | Ottawa | Scheduled Outage
16321 | 2010 | 6 | 23 | 0.43542 |  | 249 | 42 | 10 | Woodroffe | 4.16kV | UW05 | V117 @ 1865 Baseline was isolated to replace PCB transformers. | Ottawa | Scheduled Outage
14959 | 2009 | 8 | 18 | 0.37361 |  | 30 | 130 | 260 |  | 4.16kV | UW05 | UW05 Breaker opened due to vehicle hitting a pole near Woodroffe and Baseline. Crew patrolled line and found nothing, breaker was closed in and power restored. WOODROFFE (UW05) ID#14959. | Ottawa | Foreign Interference | Vehicle
16833 | 2010 | 8 | 29 | 0.57778 |  | 494 | 66 | 8 | Woodroffe | 4.16kV | UW05 | Defective overhead transformer at 1284 Hanbury was replaced by Oncall crew. 8 customers on Hanbury & Emerald were affected. | Ottawa | Defective Equipment
7421 | 2005 | 10 | 3 | 0.55347 |  | 56 | 24 | 26 | Woodroffe | 4.16kV | UW05 | Magee installed cuts on overhead of UW05 to the white phase runoff from three phase dead end on UW05 from Navahoe heading north at sherman. Cuts were opened feeding three transformers to remove tree from o/h. | Ottawa | Tree Contacts | Tree Fallen
19877 | 2012 | 1 | 23 | 0.38889 |  | 15 | 2 | 8 | Woodroffe | 4.16kV | UW06 | Transformer X35206 at 1208 tara dr openned to allow crews to upgrade seconday service. 8 customers affected for 15 minutes. Woodroffe (UW06) | Ottawa | Scheduled Outage
7888 | 2006 | 2 | 4 | 0.97431 |  | 261 | 979 | 225 | WOODROFFE | 4.16kV | UW06 | Heavy rain & Winds caused phases of UW06 circuit to come down in three different locations near Erindale & Forlan. | Ottawa | Adverse Weather | Rain
15750 | 2010 | 2 | 26 | 0.95486 |  | 47 | 8 | 10 | Woodroffe | 4.16kV | UW06 | Transformer #X32821 located at 1342 Henry Farm Dr isolated to make repairs due to triplex burnt through a tree | Ottawa | Tree Contacts | Inadequate Trimming
4897 | 2004 | 3 | 15 | 0.55903 |  | 35 | 5 | 9 | Woodroffe | 4.16kV | UW06 | Transformer at 1298 Amesbrooke was opened to change secondary sevice. | Ottawa | Defective Equipment
6285 | 2005 | 3 | 15 | 0.55208 |  | 74 | 6 | 5 | Woodroffe | 4.16kV | UW06 | Transformer #Ott2222 isolated at 1258 Erindale for a pole replacement | Ottawa | Scheduled Outage | Construction
14150 | 2009 | 4 | 7 | 0.38194 |  | 60 | 8 | 8 | Woodroffe | 4.16kV | UW06 | Isolated transformer X32818 at 1590 Ainsley Dr for service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
10506 | 2007 | 6 | 1 | 0.44444 |  | 44 | 6 | 8 | Woodroffe | 4.16kV | UW06 | Transformer #OTT4271 located at 1262 Maitland isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
10507 | 2007 | 6 | 1 | 0.38889 |  | 110 | 31 | 17 | Woodroffe | 4.16kV | UW06 | Transformer #55D4C-0032 at 173 Glen isolated to allow for maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
12789 | 2008 | 7 | 4 | 0.42708 |  | 35 | 2 | 3 | Woodroffe | 4.16kV | UW06 | Isolated transformer X33428 at 1244 Henry Farm Dr to replace secondary service | Ottawa | Scheduled Outage | Repair
16423 | 2010 | 7 | 7 | 0.95694 |  | 122 | 8 | 4 | Woodroffe | 4.16kV | UW06 | Replaced broken switch at transformer X32822 at 1207 Amesbrooke Drive | Ottawa | Tree Contacts | Inadequate Trimming
16489 | 2010 | 7 | 17 | 0.92986 |  | 67 | 10 | 9 | Woodruffe | 4.16kV | UW06 | A tree limb had fallen on the triplex that feedds 1333 AMESBROOKE DRIVE, , the transformer fuse at X35139 was open to make repairs. | Ottawa | Tree Contacts | Tree Limb Fallen
11098 | 2007 | 8 | 19 | 0.55556 |  | 34 | 5 | 9 | WOODROFFE | 4.16kV | UW06 | Transformer #OTT6196 at 1128 Tara isolated to allow for repairs of bad connection at pole due to fallen limb from customer tree trimming | Ottawa | Tree Contacts | Tree Limb Fallen
19048 | 2011 | 8 | 29 | 0.37153 |  | 198 | 13 | 4 | Woodroffe | 4.16kV | UW06 | Transfomre X33417 @ 1215 Woodside was isolated to allow crew to transfer plant. 4 customers were affected for 198 minutes. | Ottawa | Scheduled Outage | Preventive Maintenance
19052 | 2011 | 8 | 30 | 0.375 |  | 180 | 12 | 4 | Woodroofe | 4.16kV | UW06 | Trans X32817 at Navaho and Erindale was isolated for a service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
9252 | 2006 | 9 | 20 | 0.45139 |  | 30 | 5 | 10 | Woodroffe | 13.2kV | UW06 | Isolated transformer OTT2230 at 1581 Ainsley Dr to replace triplex service | Ottawa | Scheduled Outage | Repair
16970 | 2010 | 9 | 20 | 0.39306 |  | 119 | 97 | 49 | Woodroffe | 4.16kV | UW06 | UW06 white phase runoff from Navaho to end of line between Agincourt and Tara was isolated for tree contractor to perform trimming. | Ottawa | Scheduled Outage | Preventive Maintenance
5842 | 2004 | 10 | 13 | 0.49097 |  | 73 | 5 | 4 |  | 4.16kV | UW06 | Broken cutout replaced. |  | Defective Equipment | Equipment Deterioration Due to Age
19644 | 2011 | 11 | 27 | 0.47917 |  | 15 | 1 | 4 | Woodroffe | 4.16kV | UW06 | Isolated transformer X33910 at 1248 Henry Farm Dr to remove vines from around the transformer and switch | Ottawa | Scheduled Outage | Preventive Maintenance
4565 | 2003 | 12 | 5 | 0.41667 |  | 130 | 26 | 12 | Woodroffe | 4.16kV | UW06 | Transformer 6880 at 1158 Agincourt Rd 3 open wire services changed. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6005 | 2004 | 12 | 10 | 0.39931 |  | 85 | 14 | 10 | Woodroffe | 4.16kV | UW06 | Relocate services to new pole 1240 Woodside | Ottawa | Scheduled Outage | Construction
6095 | 2004 | 12 | 23 | 0.84028 |  | 20 | 4 | 12 | Woodroffe | 4.16kV | UW06 | Transformer OTT6775 @ 1257 Woodside was taken out of service to repair bad connections. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15584 | 2009 | 12 | 28 | 0.51389 |  | 670 | 112 | 8 | Woodroffe | 4.16kV | UW06 | At 1209 AMESBROOKE, Xfrm'r X32822 was opened up so crew could restring secondary. 8 customers affected for 15 mintes. Woodroffe (UW06) ID#15584 | Ottawa | Adverse Weather
19766 | 2011 | 12 | 28 | 0.48611 |  | 50 | 8 | 9 | Woodrooffe | 4.16kV | UW06 | Trans X32475 was isolated for repairs to downed neutral on open bus. also made repairs to burnt off neutral to 2024 navaho | Nepean | Defective Equipment | Equipment Deterioration Due to Age
6135 | 2005 | 1 | 14 | 0.18542 |  | 83 | 6 | 4 | Woodroffe | 4.16kV | UW07 | A pole at 1147 Field St was bumped by a vehicle (hit & run) causing the fuse to blow at transformer OTT2390. The crew had to replace the switch to restore power to the 4 customers on Field St. | Ottawa | Foreign Interference | Vehicle
7838 | 2006 | 1 | 21 | 0.53819 |  | 148 | 375 | 152 | Woodroffe | 4.16kV | UW07 | A blown arrestor on Cline cres. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4783 | 2004 | 2 | 12 | 0.40625 |  | 120 | 16 | 8 | Woodroffe | 4.16kV | UW07 | To replace services at 1193 cline | Ottawa | Scheduled Outage | Repair
12108 | 2008 | 3 | 6 | 0.49375 |  | 39 | 2 | 3 |  |  | UW07 | Transformer #X35099 located at 1185 Woodroffe Ave was isolated to allow for repairs to customer's triplex. | Nepean | Scheduled Outage | Repair
4898 | 2004 | 3 | 15 | 0.40625 |  | 34 | 6 | 10 | Woodroffe | 4.16kV | UW07 | Opened transformer at 1215 Whitmore to change open wire bus to triplex. | Ottawa | Scheduled Outage | Preventive Maintenance
4899 | 2004 | 3 | 15 | 0.46875 |  | 40 | 2 | 3 | Woodroffe | 4.16kV | UW07 | Opened transformer at 1108 Cline to change open wire bus to triplex. | Ottawa | Scheduled Outage | Preventive Maintenance
4900 | 2004 | 3 | 15 | 0.40625 |  | 70 | 16 | 14 | Woodroffe | 4.16kV | UW07 | Opened transformer at 1151 Cline to change open wire bus to triplex. | Ottawa | Scheduled Outage | Preventive Maintenance
14225 | 2009 | 4 | 25 | 0.87222 |  | 210 | 245 | 152 | Woodroffe | 4.16kV | UW07 | UW07 breaker tripped (A/R/A) during high winds, heavy rain & lightning which caused wires to come down on Bel-Air to TP3663. Damaged conductor was isolated and power was restored to all but TP3663 until repairs could be made. | Ottawa | Adverse Weather
18035 | 2011 | 4 | 28 | 0.59167 |  | 280 | 999 | 214 | Woodroffe | 4.16kV | UW07 | UW07 circuit breaker auto-reclosed and locked out during wind/lightning storm. Closed via scada and held. | Ottawa | Adverse Weather | Wind
20580 | 2012 | 5 | 25 | 0.78472 |  | 12 | 44 | 222 | Woodroffe | 4.16kV | UW07 | Lightning storm and high winds caused circuit to open. Woodroffe (UW07) ID#20580 | Ottawa | Adverse Weather | Wind
20593 | 2012 | 5 | 25 | 0.84167 |  | 11 | 41 | 222 | Woodroffe | 4.16kV | UW07 | UW07 was opened to allow crew to remove branch at 1162 Field. Branch removed and circuit restored. | Ottawa | Adverse Weather | Wind
16432 | 2010 | 7 | 9 | 0.36458 |  | 25 | 2 | 4 | WOODROFFE | 4.16kV | UW07 | Transformer X33842 at 1161 Cline Cres isolated to allow for connection for unmetered streetlight | Ottawa | Scheduled Outage | Repair
6980 | 2005 | 7 | 16 | 0.78819 |  | 1048 | 175 | 10 | Woodroffe Sub | 4.16kV | UW07 | Xfmr OTT3497 fuse found blown after lighning storm. Refused and restored at 0205. Customer called in 5 minutes later to say off again. Crew returned and did tree trimming, but found the xfmr lid blown off when went to refuse again. Defective xfmr replaced. | Ottawa | Adverse Weather | Wind
18767 | 2011 | 7 | 17 | 0.80903 |  | 3 | 11 | 214 | Woodroffe Sub | 4.16kV | UW07 | UW07 Tripped and was closed with success 3 minutes later. | Ottawa | Adverse Weather
4073 | 2003 | 9 | 16 | 0.37847 |  | 45 | 114 | 152 | Woodroffe | 4.16kV | UW07 | A tree contractor working in the backyard of 1186 Checkers inadvertantly dropped a limb onto the UW07 overhead causing the outage. They reported this incident themselves and remained on scene until crerw arrived. | Ottawa | Foreign Interference | Tree Limb Fallen
11607 | 2007 | 10 | 27 | 0.25694 |  | 185 | 37 | 12 | Woodroffe | 4.16kV | UW07 | Transformer #OTT3868 located at 1265 Joyce Cres isolated due to defective cut out | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5934 | 2004 | 11 | 26 | 0.80208 |  | 65 | 6 | 6 | Woodroffe | 4.16kV | UW07 | Overhead transformer at 1196 Cline interrupted due to a broken cut-out. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17443 | 2010 | 12 | 21 | 0.38542 |  | 120 | 20 | 10 | Woodroffe | 4.16kV | UW07 | Transformer #X35216 located at 1163 Whitmore opened by crew to change transformer | Ottawa | Scheduled Outage | Construction
8372 | 2006 | 5 | 29 | 0.96319 |  | 278 | 171 | 136 | Woodroffe | 4.16kV | UW13 | Rain and Lightning caused white phase primary of UW13 circuit to come down at rear of Highgate and Bloomsbury, which opened the circuit. | Ottawa | Adverse Weather | Lightning
8380 | 2006 | 5 | 29 | 0.97639 |  | 744 | 620 | 50 | Woodroffe | 4.16kV | UW13 | Some customers were restored when the primary wire was repaired & back on as of 03:58. However, there was another burn in the wire due to lightning. Customers at 2169 Elmira, some on Regency, Bloomsbury & Highgate were still out of power May 30/06 in the am. Jeff Magee & his crews checked it out & found the second problem. Repairs were made to the wire & all power was restored at 11:50 am May 30/06 | Ottawa | Adverse Weather | Lightning
8373 | 2006 | 5 | 30 | 0.10347 |  | 76 | 171 | 135 | Woodroffe | 4.16kV | UW13 | UW13 circuit was isolated to allow crew to repair phase that came down at rear of Highgate & Bloomsbury. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16295 | 2010 | 6 | 25 | 0.45486 |  | 68 | 9 | 8 | Woodroffe | 4.16kV | UW13 | Transformer #X33967 located at 1304 Highgate opened by crew to connect S/L feed | Ottawa | Scheduled Outage | Construction
18525 | 2011 | 6 | 25 | 0.86944 |  | 98 | 2 | 1 | Woodroffe | 4.16kV | UW13 | V752 at 2250 Torquay Avenue was isolated to replace defective transformers. Woodroffe (UW13) ID#18525 | Ottawa | Defective Equipment
14634 | 2009 | 6 | 28 | 0.66806 |  | 311 | 380 | 477 | Woodroffe | 4.16kV | UW13 | UW13 circuit A/R, 2 phases of the O/H conductor in the backyard on Westbury have broken and fallen to the ground. UW13 breaker opened to allow crew to cut O/H conductor clear. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6977 | 2005 | 7 | 16 | 0.78819 |  | 260 | 9 | 2 | Woodroffe Sub | 4.16kV | UW13 | Xfmr fuse on Elmira feeding 2200 & 2202 found blown due to lighning. Refused and restored. | Ottawa | Lightning | Direct Strike
6978 | 2005 | 7 | 16 | 0.78819 |  | 295 | 103 | 21 |  | 4.16kV | UW13 | Xfmr fuse on Elmira feeding 2169 & 2173 found blown due to lighning. Refused and restored. | Ottawa | Lightning | Direct Strike
6979 | 2005 | 7 | 16 | 0.78819 |  | 672 | 22 | 2 | Woodroffe Sub |  | UW13 | Xfmr OTT3771 feeding 2176 Elmira & 2192 Lambeth found defective due to lightning. Secondary jumpered to restore power until xfmr can be replaced. | Ottawa | Lightning
18745 | 2011 | 7 | 17 | 0.80764 |  | 6 | 51 | 514 | Woodroffe | 4.16kV | UW13 | UW13 Tripped during lightening storm and was closed back in with success after 6 minutes | Ottawa | Adverse Weather | Lightning
6998 | 2005 | 7 | 20 | 0.44792 |  | 131 | 26 | 12 | Woodroffe | 4.16kV | UW13 | At 10:45 trans @ 219A Elmira isolated for replacement due to leaking oil | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8883 | 2006 | 8 | 1 | 0.066667 |  | 188 | 426 | 136 | Woodroffe | 4.16kV | UW13 | Circuit tripped during heavy storm, problem later found to be broken primary wires. | Ottawa | Adverse Weather | Lightning
8884 | 2006 | 8 | 1 | 0.24653 |  | 35 | 79 | 136 | Woodroffe | 4.16kV | UW13 | Circuit tripped during heavy storm, problem later found to be broken primary wires., damaged section isolated. | Ottawa | Adverse Weather | Lightning
8892 | 2006 | 8 | 1 | 0.47431 |  | 52 | 118 | 136 | Woodroffe | 4.16kV | UW13 | Circuit was isolated to allow crew to make final repairs to overhead conductor. Circuit was sleeved back together and power was restoered. | Ottawa | Adverse Weather | Wind
13024 | 2008 | 8 | 8 | 0.53125 |  | 45 | 9 | 12 | WOODROFFE | 4.16kV | UW13 | Transformer X33961 at 2130 Westbury isolated to allow for repairs for streetlights | Nepean | Scheduled Outage | Construction
11253 | 2007 | 9 | 5 | 0.54861 |  | 50 | 6 | 7 | Woodroffe |  | UW13 | Transformer #55C3D-0108 at 2384 Cheshire isolated to allow for repairs to service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
11305 | 2007 | 9 | 14 | 0.41806 |  | 60 | 136 | 136 | Woodroffe | 4.16kV | UW13 | UW13 circuit was isolated to remove fallen tree from 3 phase primary behind 1288 Highgate. Overhead line crew worked in conjunction with Asplundh. Crew also had to re-tension conductor at dead end to remove sag from line. | Ottawa | Tree Contacts | Tree Fallen
7402 | 2005 | 9 | 29 | 0.69861 |  | 229 | 519 | 136 |  | 13.2kV | UW13 | Tree caused primary down | Ottawa | Tree Contacts | Tree Limb Fallen
7776 | 2006 | 1 | 5 | 0.40278 |  | 70 | 10 | 9 | Woodroffe | 4.16kV | UW14 | Transformer #55C3D-0319 located behind 1179 Maybank St isolated to repair the service to this home | Ottawa | Foreign Interference | Foreign Object
19836 | 2012 | 1 | 15 | 0.85417 |  | 20 | 6 | 18 | Woodroffe | 4.16kV | UW14 | Transformer X32772 at 2045 Kingsley was opened to allow the crew to renew the service connections at the transformer and the standpipe | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17521 | 2011 | 1 | 25 | 0.60069 |  | 45 | 14 | 18 | Woodroffe | 4.16kV | UW14 | Transformer #X32772 located at 2043 Kingsley Rd opened by crew to change a couple of services | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6269 | 2005 | 3 | 12 | 0.0625 |  | 50 | 15 | 18 | Woodroffe | 4.16kV | UW14 | O/H transformer on Kingsley interrupted to repair secondary connections to 2045 Kingsley. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
14190 | 2009 | 4 | 20 | 0.017361 |  | 126 | 17 | 8 | Woodroffe | 4.16kV | UW14 | Transformer X32657 at 2361 Iris was opened to replace a defective triplex to 2359 | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12434 | 2008 | 5 | 13 | 0.45417 |  | 111 | 11 | 6 | Woodrooffe | 4.16kV | UW14 | At 10:54 trans at 2077 Kinsley Rd was isolated in order to replace a pcb trans | Ottawa | Scheduled Outage | Preventive Maintenance
10585 | 2007 | 6 | 9 | 0.72222 |  | 32 | 98 | 184 | WOODROFFE | 4.16kV | UW14 | UW14 Circuit opened and isolated for Crew to remove tree limb off 3 phase line at 1190 Parkway Ave, Ottawa. | Ottawa | Tree Contacts | Tree Limb Fallen
16346 | 2010 | 6 | 28 | 0.61597 |  | 48 | 12 | 15 | Woodroffe | 4.16kV | UW14 | Transformer #X32774 located at 2079 Kingsley Rd opened by crew to replace connections at the transformer | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10794 | 2007 | 7 | 5 | 0.071528 |  | 47 | 8 | 10 | Woodroffe | 4.16kV | UW14 | A animal made contact with the O/H transformer 35114 at 1291 RUSTIC DR OTTAWA causing the fus to blow. | Ottawa | Foreign Interference | Animal
6894 | 2005 | 7 | 9 | 0.77778 |  | 59 | 18 | 18 | Woodroffe | 4.16kV | UW14 | Overhead Transformer was opened to redo connections. Customers were experiencing part outs. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18636 | 2011 | 7 | 10 | 0.55208 |  | 20 | 3 | 9 | Woodroffe | 4.16kV | UW14 | Isolated transformer X32705 at 2435 Iris St to replace triplex service feeding 3172 Lambeth Walk | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18782 | 2011 | 7 | 20 | 0.69583 |  | 169 | 476 | 547 | Woodroffe | 4.16kV | UW14 | UW14 circuit opened to allow taps to be cut off overhead at Iris & Parkway. Primary & tree down on Maybankin the backyard. Uw14 circuit closed restoring 447 customers . 100 customer remain out until tree is removed and conductor repaired. | Ottawa | Tree Contacts | Tree Fallen
15022 | 2009 | 8 | 28 | 0.62292 |  | 41 | 0 | 15 | WOODROFFE | 4.16kV | UW14 | Transformer X32774 at 2073 Kingsley isolated to allow for replacement of service connections at s/p & pole | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9278 | 2006 | 9 | 22 | 0.35764 |  | 35 | 9 | 15 | Woodroffe | 4.16kV | UW14 | Transformer #55C3B-0210 located at 2073 Kingsley Rd isolated to replace connections at the transformer pole | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16997 | 2010 | 9 | 25 | 0.41319 |  | 20 | 2 | 6 | Woodroffe | 4.16kV | UW14 | Transformer #X32770 located at 1135 Parkway opened by crew to replace switch, hot line clamp and connections at S/P | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15233 | 2009 | 10 | 8 | 0.39583 |  | 165 | 16 | 6 | Woodroffe | 4.16kV | UW14 | At 09:30 trans at 1223 Parkway Dr was isolated in order to replace a pole | Ottawa | Scheduled Outage | Preventive Maintenance
9405 | 2006 | 10 | 10 | 0.34722 |  | 50 | 8 | 9 | Woodroffe | 4.16kV | UW14 | Transformer located at 2168 Lambeth isolated for new service connection. PC10A #1352 | Ottawa | Scheduled Outage | Preventive Maintenance
13369 | 2008 | 10 | 15 | 0.375 |  | 45 | 4 | 6 | Woodroffe | 4.16kV | UW14 | Transformer X32769 @ 1135 Maybank St opened up for service | Ottawa | Scheduled Outage | Preventive Maintenance
9441 | 2006 | 10 | 16 | 0.55556 |  | 35 | 4 | 6 | Woodroffe | 4.16kV | UW14 | Transformer located at 1333 Rustic isolated for maintenance. PC10A #843 | Ottawa | Scheduled Outage | Preventive Maintenance
9777 | 2006 | 12 | 1 | 0.84167 |  | 333 | 1021 | 184 | Woodroffe | 4.16kV | UW14 | UW14 breaker opened from SCADA due to downed primary on Parkway Dr north of Iris. Circuit was isolated & repairs made to circuit. | Ottawa | Adverse Weather | Ice Storm
4634 | 2003 | 12 | 19 | 0.39792 |  | 80 | 7 | 5 | Woodroffe | 4.16kV | UW14 | To transfer customers. | Ottawa | Scheduled Outage | Preventive Maintenance
4635 | 2003 | 12 | 19 | 0.43056 |  | 33 | 3 | 6 | WOODROFFE | 4.16kV | UW14 | To transfer customers. | Ottawa | Scheduled Outage
19757 | 2011 | 12 | 22 | 0.24097 |  | 59 | 8 | 8 | Woodroffe | 4.16kV | UW14 | Transformer X33799 @ 2082 Westbury opened due to defective cut out. | Ottawa | Defective Equipment
14569 | 2009 | 6 | 18 | 0.66319 |  | 33 | 186 | 863 | Woodroffe Sub | 4.16kV | UWT1 | UW03 breaker closed and tripped free, and the TW13 breaker also tripped. At 16:02, UW02 & UW04 bkrs closed. At 16:04, UW03 bkr closed. At 16:28, UWK1Y1 closed to restore the UW01 load. | Ottawa | Tree Contacts
4830 | 2004 | 2 | 26 | 0.84375 |  | 195 | 75 | 23 | Gladstone | 4.16kV | UX02 | To replace the broken transformer switch at transformer 2572 @ 161 Frank St. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5256 | 2004 | 6 | 4 | 0.51042 |  | 65 | 14 | 13 | Gladstone | 4.16kV | UX02 | Transformer #OTT2572 at 161 Frank St interrupted to install a new pole. | Ottawa | Scheduled Outage | Construction
14516 | 2009 | 6 | 11 | 0.45833 |  | 30 | 12 | 24 | Gladstone | 4.16kV | UX02 | Transformer #X30859 located at 161 Frank St isolated to remove trees off secondary | Ottawa | Tree Contacts | Tree Limb Fallen
10659 | 2007 | 6 | 19 | 0.44792 |  | 39 | 1 | 2 | Gladstone | 4.16kV | UX02 | At 10:45 trans at 14 Lewis was isolated in order to transfer load for new cust connection | Ottawa | Scheduled Outage | Construction
10671 | 2007 | 6 | 19 | 0.53333 |  | 95 | 13 | 8 | Gladstone | 4.16kV | UX02 | Transformer #OTT4056 at 68 MacDonald isolated to allow for load transfer to reconnect new customer | Ottawa | Scheduled Outage | Construction
18666 | 2011 | 7 | 15 | 0.46875 |  | 40 | 2 | 3 | King Edward | 4.16kV | UX02 | Trans at 46 Cartier St was isolated for service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
11294 | 2007 | 9 | 12 | 0.33889 |  | 157 | 13 | 5 | Gladstone | 4.16kV | UX02 | Transformer #OTT3941 at 128 Lewis St isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
15674 | 2010 | 1 | 21 | 0.55208 |  | 15 | 0 | 1 | Gladstone | 4.16kV | UX03 | To be determined. | Ottawa | Human Element | Incorrect Records
10144 | 2007 | 3 | 18 | 0.20139 |  | 20 | 0 | 1 | Gladstone | 4.16kV | UX03 | At V807 the pph cable to the vault had burnt off. Repairs were made and power was restored to 317 Metcalfe. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6492 | 2005 | 5 | 2 | 0.77778 |  | 28 | 0 | 1 | UX | 4.16kV | UX03 | V528 @ 255 Metcalfe was isolated to replace primary transformer fuse & make minor repairs. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10516 | 2007 | 6 | 2 | 0.94792 |  | 95 | 127 | 80 | Gladstone | 4.16kV | UX03 | Customer main open at 196 Metcalf Algonquin Apts. Owner opened all secondary breaker and requested we close main. Thenall secondary breakers closed. All power restored. | Ottawa | Unknown/Other | No Apparent Cause
3651 | 2003 | 6 | 10 | 0.39583 |  | 190 | 177 | 56 | Gladstone | 4.16kV | UX03 | At 9:30am Tuesday, the vault at 305 Metcalfe in downtown Ottawa was shutdown to allow the contractor to clean the vault. 56 customers were interrupted, and power was restored at 12:40pm. | Ottawa | Scheduled Outage | Preventive Maintenance
9044 | 2006 | 8 | 24 | 0.44792 |  | 90 | 45 | 30 | Gladstone | 4.16kV | UX03 | Transformer #OTT1665 located at 295 Cooper isolated to install a new pole | Ottawa | Scheduled Outage | Construction
19399 | 2011 | 10 | 17 | 0.39583 |  | 100 | 148 | 89 | Gladstone | 4.16kV | UX03 | Isolated transformers X30554 and X26299 at 317 and 309 Cooper St to transfer Hydro plant | Ottawa | Scheduled Outage | Construction
9704 | 2006 | 11 | 22 | 0.43403 |  | 95 | 98 | 62 | Gladstone | 4.16kV | UX03 | Isolated transformer OTT1665 at 297 Cooper St to install new pole | Ottawa | Scheduled Outage | Construction
9726 | 2006 | 11 | 24 | 0.43056 |  | 235 | 118 | 30 | Gladstone | 4.16kV | UX03 | Isolated transformer OTT1665 at 295 Cooper St to replace poles | Ottawa | Scheduled Outage | Construction
19995 | 2012 | 2 | 9 | 0.44375 |  | 76 | 32 | 25 | Gladstone | 4.16kV | UX04 | Replaced broken switch feeding transformer X31716 at 44 Park Ave | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
8371 | 2006 | 5 | 29 | 0.80417 |  | 57 | 1 | 1 | Gladstone | 4.16kV | UX04 | 4kV vault V354 at 320 Jack Purcell Lane (community centre) was isolated to replace broken dip switches. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
5281 | 2004 | 6 | 11 | 0.35417 |  | 155 | 132 | 51 | Gladstone | 4.16kV | UX04 | Transformer OTT 2559 at 250 Frank St replaced by crew | Ottawa | Scheduled Outage | Preventive Maintenance
16469 | 2010 | 7 | 14 | 0.55556 |  | 25 | 2 | 4 | Gladstone | 4.16kV | UX04 | Transformer #X31055 located at 300 Elgin St opened by crew to disconnect service for electrician | Ottawa | Scheduled Outage | Construction
18802 | 2011 | 7 | 23 | 0.55208 |  | 34 | 16 | 29 | Gladstone | 4.16kV | UX04 | Transformer #X31867 located at 55 Park opened by crew to reconnect service to the bldg | Ottawa | Scheduled Outage | Construction
4424 | 2003 | 11 | 11 | 0.38194 |  | 185 | 43 | 14 | Gladstone | 4.16kV | UX04 | transformer 55D2D-0248 Rear of 439 Elgin St. for tree removal | Ottawa | Scheduled Outage | Preventive Maintenance
7825 | 2006 | 1 | 19 | 0.41667 |  | 80 | 19 | 14 | Gladsdtone | 4.16kV | UX05 | At 10:00 trans OTT4081 isolated to transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
15889 | 2010 | 4 | 3 | 0.94444 |  | 183 | 73 | 24 | Gladestone | 4.16kV | UX05 | Transformer X26010 at 50 Delaware was reported to be leaking and had to be replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
14196 | 2009 | 4 | 21 | 0.47986 |  | 338 | 1432 | 262 | Gladstone | 4.16kV | UX05 | Tracking caused pole to catch fire and primary conductor to fall at dip to V514 at 60 McLeod. Entire circuit had to be isolated to make repairs. Overhead was repaired and restored first, then dip to V514. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10496 | 2007 | 5 | 31 | 0.60417 |  | 30 | 7 | 14 | Gladstone | 4.16kV | UX05 | Mark isolted TRF. 1229 @ 116 Cartier to repair defective neutral connections | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
3781 | 2003 | 7 | 14 | 0.625 |  | 40 | 5 | 8 | Gladstone | 4.16kV | UX05 | Tree pulled down secondary service on July 13 @ 21:28, to 65 & 71 Delaware Ave. Repairs were made and transformer was isolated to connect repaired secondary service on July 14/03 from 15:00 - 15:40. | Ottawa | Tree Contacts | Tree Fallen
13060 | 2008 | 8 | 15 | 0.45833 |  | 50 | 9 | 11 | Gladstone | 4.16kV | UX05 | Transformer X30159 isolated to remove a tree limb from 99 Cartier Ave. | Ottawa | Tree Contacts | Tree Limb Fallen
19036 | 2011 | 8 | 28 | 0.84236 |  | 28 | 107 | 230 | Gladstone | 4.16kV | UX05 | UX05 circuit auto & locked out. Fire department report large flash at 77 Cartier St. 24/7 dispatched to patrol overhead and meet O.F.D.. Andy reports no problem found. Circuit closed and holding. | Ottawa | Adverse Weather | Wind
9126 | 2006 | 9 | 6 | 0.42708 |  | 30 | 1 | 2 | Gladstone | 4.16kV | UX05 | Greg Macmillan opened trans OTT5850 at 33 Somerset to do a load transfer | Ottawa | Scheduled Outage
11263 | 2007 | 9 | 6 | 0.54167 |  | 123 | 16 | 8 | Gladstone | 4.16kV | UX05 | At 13:00 trans at 66 Delaware was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
4425 | 2003 | 11 | 11 | 0.40278 |  | 155 | 72 | 28 | Gladstone | 4.16kV | UX05 | Transformer Ott 4861 O/S for maintenance on the secondary | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13722 | 2008 | 12 | 9 | 0.44792 |  | 80 | 21 | 16 | Gladstone | 4.16kV | UX05 | Transformer #X30796 located at 66 Delaware isolated to run a fly tap for a service | Ottawa | Scheduled Outage | Preventive Maintenance
13723 | 2008 | 12 | 9 | 0.44792 |  | 145 | 36 | 15 | Gladstone | 4.16kV | UX05 | Transformer #X30797 located at 78 Delaware isolated to run a fly tap for a service | Ottawa | Scheduled Outage | Preventive Maintenance
4668 | 2003 | 12 | 31 | 0.89583 |  | 245 | 1751 | 510 | Gladstone | 4.16kV | UX05, UX09 | Two different phases of UX05 conductor fell to the ground at different locations but both on Cartier St near Somerset. UX09 circuit was interrupted to allow repairs to UX05 above it. | Ottawa | Adverse Weather | Wind
17599 | 2011 | 2 | 16 | 0.77083 |  | 180 | 33 | 11 | Gladstone | 4.16kV | UX06 | Isolated transformer X31034 and X31035 at 116 Argyle Ave to replace secondary conductor | Ottawa | Scheduled Outage | Construction
12176 | 2008 | 3 | 26 | 0.53125 |  | 105 | 2 | 1 | Gladstone | 4.16kV | UX06 | Transformer #X31182 located at 231 Mcleod isolated due to electrician was putting up a new hit and the service came down | Ottawa | Foreign Interference | Foreign Object
18258 | 2011 | 5 | 31 | 0.4375 |  | 40 | 11 | 17 | Gladstone | 4.16kV | UX06 | Isolated transformer X27564 at 131 McLeod St for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
8911 | 2006 | 8 | 2 | 0.91319 |  | 415 | 76 | 11 | Gladstone | 4.16kV | UX06 | UX06 auto-reclosed once during thunderstorm. Cause was later determined to be a damaged transformer at Elgin & Argyle, suspect transformer took a lightning strike. On-call crew replaced transformer & restored power. | Ottawa | Adverse Weather | Lightning
11353 | 2007 | 9 | 21 | 0.29861 |  | 86 | 14 | 10 | Gladstone | 4.16kV | UX06 | Transformer at 165 MacLaren isolated to allow for pcb change | Ottawa | Scheduled Outage | Preventive Maintenance
15142 | 2009 | 9 | 21 | 0.43056 |  | 424 | 7 | 1 | Gladstone | 4.16kV | UX06 | V351 at 284 Elgin at MacLaren was isolated to investigate cause of blown primary fuse in vault. All equip tested good. When vault re-energized, fuse blew at dip pole, equipment isolated & tested again & bad transformer found. O/C crew replaced defective transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15228 | 2009 | 10 | 7 | 0.42361 |  | 95 | 6 | 4 | Gladstone | 4.16kV | UX06 | Transformer #X31184 located at 285 Mcleod isolated for an upgrade. | Ottawa | Scheduled Outage | Construction
15229 | 2009 | 10 | 7 | 0.42361 |  | 95 | 6 | 4 | Gladstone | 4.16kV | UX06 | Transformer #X31184 located 285 Mcleod isolated due to an upgrade | Ottawa | Scheduled Outage | Construction
17547 | 2011 | 2 | 3 | 0.38264 |  | 174 | 12 | 4 | Gladstone | 4.16kV | UX07 | Transformer X31069 at 252 Argyle Ave isolated to allow for service upgrade | Ottawa | Scheduled Outage | Construction
15811 | 2010 | 3 | 16 | 0.54722 |  | 201 | 3 | 1 | Gladstone | 4.16kV | UX07 | V48 at 229 Argyle was disconnected for non-payment, but was reconnected at the request of Ottawa Police Dept due to saftey reasons. | Ottawa | Unknown/Other
10159 | 2007 | 3 | 22 | 0.31944 |  | 391 | 7 | 1 | Gladstone | 4.16kV | UX07 | PPH Switches to V52 at 219 Argle were blown. Car hit base of pole. | Ottawa | Foreign Interference | Vehicle
10285 | 2007 | 4 | 19 | 0.33819 |  | 878 | 15 | 1 | Gladstone | 4.16kV | UX07 | Defective transformer P9 at 210 Gladstone isolated and replaced. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5110 | 2004 | 5 | 6 | 0.63889 |  | 245 | 21 | 14 | Gladstone | 4.16kV | UX07 | Power was interrupted to P165 to disconnect 380 Elgin from transformer in order for Imperial electric to replace customer's main breaker. Outage included 376 and 374 Elgin to isolate and then restore the service to 380 Elgin,from P165. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10652 | 2007 | 6 | 18 | 0.35417 |  | 142 | 90 | 38 | Gladstone | 4.16kV | UX07 | Transformer #OTT2704 at 274 Gladstone Ave. isolated to allow for disconnect of service wire pulled down by a truck | Ottawa | Foreign Interference | Vehicle
16769 | 2010 | 8 | 18 | 0.4375 |  | 85 | 54 | 38 | Gladstone | 4.16kV | UX07 | Isolated transformer X30347 at 270 Gladstone Ave for pole replacement | Ottawa | Scheduled Outage | Construction
17279 | 2010 | 11 | 16 | 0.375 |  | 120 | 78 | 39 | Gladstone | 4.16kV | UX07 | Isolated transformer X30348 at 270 Gladstone Ave for a pole change | Ottawa | Scheduled Outage | Construction
11836 | 2007 | 12 | 13 | 0.041667 |  | 353 | 6 | 1 | Gladstone | 4.16kV | UX07 | Blue phase cable duct collapsed causing the outage. Jean reports the other ducts are also collapsed and needs to be repaired soon. Blue phase cable is now replaced. All power restored at 229 ARGYLE AVE. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
15820 | 2010 | 3 | 18 | 0.60417 |  | 60 | 5 | 5 | Gladstone | 4.16kV | UX08 | Transformer #X33698 located at 328 O'Connor St isolated due to transformer replacement due to oil spill | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
6313 | 2005 | 3 | 23 | 0.13889 |  | 986 | 395 | 213 | Gladstone | 4.16kV | UX08 | UX08 breaker opened from SCADA to isolate buildings for the fire department to start work. O/H xfmrs X18 & X19 on Waverley opened to isolate buildings & UX08 circuit restored. Power restored to 385 Waverly at at 6:36am. | Ottawa | Adverse Environment | Fire
5758 | 2004 | 9 | 1 | 0.53819 |  | 60 | 1 | 1 | Gladstone | 4.16kV | UX08 | Dave Guy of 24/7 responded to a low voltage call at V378 @ 330 Gilmour. The vault main breaker was opened to check the 600V transformer bank. A defective box type switch was found and replaced. The transformer bank was checked OK & breaker closed to restore. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
4024 | 2003 | 9 | 5 | 0.48611 |  | 90 | 15 | 10 | Gladstone | 8/4.8kV | UX08 | Planned outage to transfromer 3709 to replace a service. | Ottawa | Scheduled Outage
9903 | 2007 | 1 | 4 | 0.42014 |  | 55 | 7 | 8 | Gladstone | 4.16kV | UX09 | Transformer #OTT6544 located at 34 Waverley St isolated to re-locate service | Ottawa | Scheduled Outage | Construction
19802 | 2012 | 1 | 9 | 0.61597 |  | 73 | 113 | 555 | Gladstone | 4.16kV | UX09 | Ottawa Fire Chief Steve Rehume request UX09 circuit to be opened to all fire crews to fight fire at 179 Waverley St. G. Carswell reports temp cuts installed and opened on West side of Cartier on Waverley st. UX09 circuit closed restoring load to 482 customers. 73 remain out on Waverley st. G. Carswell reports all power restored as of 16:00. | Ottawa | Adverse Environment | Fire
9949 | 2007 | 1 | 19 | 0.38889 |  | 125 | 17 | 8 | Gladstone | 4.16kV | UX09 | Isolated transformer OTT 6544 at 34 Waverly St to relocate services | Ottawa | Scheduled Outage | Construction
7856 | 2006 | 1 | 25 | 0.39583 |  | 135 | 14 | 6 | GLADSTONE | 4.16kV | UX09 | delivery truck caught the hydro wires from the house and pulled the mast from the wall @ 229 compton. | Ottawa | Scheduled Outage | Construction
4773 | 2004 | 2 | 9 | 0.80556 |  | 65 | 10 | 9 | Gladstone | 4.16kV | UX09 | Snow fell from roof, hit open base causing conductors to touch and transformer fuse to open, transformer refused and power restored. | Ottawa | Foreign Interference | Foreign Object
15710 | 2010 | 2 | 9 | 0.65972 |  | 20 | 5 | 14 | Gladstone | 4.16kV | UX09 | Transformer P221 located at 361 Elgin St isolated to replace blown fuse in transformer | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12102 | 2008 | 3 | 4 | 0.96875 |  | 101 | 24 | 14 | Gladstone | 4.16kV | UX09 | 24/7 replaced a failed fused cut-out supplying K1278. Customers on Cornerstone Pvt. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
12103 | 2008 | 3 | 4 | 0.96875 |  | 101 | 24 | 14 | Gladstone | 4.16kV | UX09 | Broken Dip pole cutout feeding transformer K1278 at Cornerstone Private. Switch repaired, closed and holding. 14 customers affected. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
17742 | 2011 | 3 | 20 | 0.40972 |  | 79 | 33 | 25 | Gladestone | 4.16kV | UX09 | A broken swtich at 192 Waverley that feeds transformer X30871. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
17856 | 2011 | 4 | 8 | 0.39583 |  | 66 | 13 | 12 | Gladstone | 4.16kV | UX09 | Transformer X26676 was open to allow crew to perform service upgrade at 70 MacDonlad. 12 customer were affected. Fed UX 09 out of Gladstone. | Ottawa | Scheduled Outage
10345 | 2007 | 4 | 30 | 0.45139 |  | 65 | 24 | 22 | Gladstone | 4.16kV | UX09 | Glen Carswell isolated TRF. 4098 to change defective TRF. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
18108 | 2011 | 5 | 6 | 0.35764 |  | 25 | 5 | 13 | Gladstone | 4.16kV | UX09 | Isolated transformer X30682 at 32 Lewis St for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
18227 | 2011 | 5 | 27 | 0.35764 |  | 90 | 33 | 22 | Gladstone | 4.16kV | UX09 | Transformer #X30823 located at 51 Waverley St opened by crew for tree trimmers | Ottawa | Scheduled Outage | Construction
14919 | 2009 | 8 | 7 | 0.12569 |  | 20 | 0 | 248 | Gladstone | 4.16kV | UX09 | Crew responding to wires down asked that circuit be dump to allow them to cut wires clear. | Ottawa | Defective Equipment
9052 | 2006 | 8 | 24 | 0.67917 |  | 22 | 3 | 8 | Gladstone | 4.16kV | UX09 | Isolated transformer OTT6544 and a section of 4kv line at 34 Waverley St to remove scaffolding that had been set up with in the safe limits of approach | Ottawa | Scheduled Outage | Emergency Services Request
9125 | 2006 | 9 | 6 | 0.42708 |  | 30 | 4 | 9 | Gladstone | 4.16kV | UX09 | Greg Macmillan opened transformer OTT4103 at 17 Maclaren to do a load transfer | Ottawa | Scheduled Outage | Preventive Maintenance
19256 | 2011 | 9 | 26 | 0.38889 |  | 241 | 36 | 9 | GLADSTONE | 4.16kV | UX09 | Transformer X30680 at 28 Gilmour St. isolated for contractor to do building maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
15331 | 2009 | 10 | 30 | 0.54583 |  | 64 | 38 | 36 | Gladestone | 4.16kV | UX09 | A broken W phase switch at the corner of Waverley and Cartier. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
19528 | 2011 | 11 | 4 | 0.57292 |  | 45 | 2 | 2 | Gladstone | 4.16kV | UX09 | Trans X30503 at 72 Maclaren St was isolated for Service work | Ottawa | Scheduled Outage | Preventive Maintenance
13574 | 2008 | 11 | 6 | 0.53472 |  | 114 | 66 | 35 | Gladstone | 4.16kV | UX09 | At 12:50 transformer at 48 ROBERT ST OTTAWA was isolated for secondary repairs. | Ottawa | Scheduled Outage | Repair
18275 | 2011 | 6 | 1 | 0.72569 |  | 258 | 349 | 236 | Gladstone | 4.16kV | UX10 | Wire down at 200 Cooper, caused by fallen tree. S13790 opened, to make repairs. | Ottawa | Tree Contacts | Tree Fallen
10951 | 2007 | 7 | 25 | 0.67639 |  | 316 | 5 | 1 | Gladstone | 4.16kV | UX10 | 131 Cooper St customer 600 amp main breaker overheating. Isolated under PC10C to Tom Moore. ESA received. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
15320 | 2009 | 10 | 28 | 0.47917 |  | 20 | 1 | 4 | Gladstone | 4.16kV | UX10 | at 11:30 trans at 74 Cooper st was isolated in order to install a new service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
17317 | 2010 | 11 | 21 | 0.32292 |  | 320 | 43 | 8 | Gladstone | 4.16kV | UX10 | Trans at 235 LISGAR ST OTT was isolated in order to replace pole and transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
7997 | 2006 | 3 | 9 | 0.38194 |  | 60 | 3 | 3 | Sunnyside | 4.16kV | UY03 | Mike Gruich opened transformer OTT2613 @ 7 Galt to do a pole change. | Ottawa | Scheduled Outage
10779 | 2007 | 7 | 3 | 0.47569 |  | 35 | 5 | 8 | Sunnyside | 4.16kV | UY03 | Transformer #OTT769 located at 36 Barton isolated due to pole change | Ottawa | Scheduled Outage | Construction
10930 | 2007 | 7 | 23 | 0.42708 |  | 105 | 10 | 6 | SUNNYSIDE | 4.16kV | UY03 | Transformer #OTT2882 at 16 Grosvenor isolated to allow for transfer of plant | Ottawa | Scheduled Outage | Preventive Maintenance
10981 | 2007 | 8 | 1 | 0.40625 |  | 53 | 5 | 6 | Sunnyside | 4.16kV | UY03 | Transformer #OTT2883 located at 38 Grosvenor isolated to install new pole | Ottawa | Scheduled Outage | Construction
11086 | 2007 | 8 | 17 | 0.40625 |  | 124 | 21 | 10 | Sunnyside | 4.16kV | UY03 | At 09:45 trans at 16 Pansey was isolated in order to prepare pole for transferring plant | Ottawa | Scheduled Outage | Preventive Maintenance
11105 | 2007 | 8 | 20 | 0.44444 |  | 35 | 8 | 13 | Sunnyside | 4.16kV | UY03 | Transformer #OTT5552 located at 69 Rosedale isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11122 | 2007 | 8 | 22 | 0.38542 |  | 186 | 140 | 45 | Sunnyside | 4.16kV | UY03 | The O/H line on Grosvenor was isolated to upgrade the O/H conductor. | Ottawa | Scheduled Outage | Construction
11133 | 2007 | 8 | 23 | 0.54514 |  | 70 | 16 | 14 | Sunnyside | 4.16kV | UY03 | Isolated transformer OTT5569 at 23 Roslyn for a pole change | Ottawa | Scheduled Outage | Construction
11169 | 2007 | 8 | 28 | 0.36806 |  | 175 | 38 | 13 | Sunnyside | 4.16kV | UY03 | Isolated transformer OTT5568 at 12 Roslyn Ave to replace pole and transformer | Ottawa | Scheduled Outage | Construction
11179 | 2007 | 8 | 29 | 0.4375 |  | 110 | 11 | 6 | Sunnyside | 4.16kV | UY03 | Isolated and replaced transformer OTT2883 at 38 Grosvenor Ave | Ottawa | Scheduled Outage | Preventive Maintenance
11223 | 2007 | 8 | 31 | 0.41667 |  | 75 | 10 | 8 | Sunnyside | 4.16kV | UY03 | Isolated and replaced transformer OTT655 at 14 Galt St | Ottawa | Scheduled Outage | Construction
11250 | 2007 | 9 | 5 | 0.40486 |  | 161 | 38 | 14 | SUNNYSIDE | 4.16kV | UY03 | Transformer #OTT5569 at 24 Roslyn isolated to allow for maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
11264 | 2007 | 9 | 6 | 0.41875 |  | 247 | 49 | 12 | Sunnyside | 13.2kV | UY03 | At 14:10 trans at 56 Grosvenor was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11306 | 2007 | 9 | 14 | 0.43333 |  | 68 | 8 | 7 | Sunnyside | 4.16kV | UY03 | At 10:24 trans at 9 Rosedale Ave was isolated in order to install a new guy... | Ottawa | Scheduled Outage | Preventive Maintenance
11371 | 2007 | 9 | 24 | 0.40972 |  | 130 | 22 | 10 | Sunnyside | 4.16kV | UY03 | Isolated and replaced transformer OTT5570 at 47 Roslyn Ave (transformer up-grade) | Ottawa | Scheduled Outage | Construction
11426 | 2007 | 10 | 1 | 0.42708 |  | 155 | 0 | 10 | Sunnyside | 4.16kV | UY03 | Transformer# X30391 at 43 Roslyn isolated for transferring of plant | Ottawa | Scheduled Outage | Construction
11531 | 2007 | 10 | 16 | 0.41667 |  | 205 | 31 | 9 | Sunnyside | 4.16kV | UY03 | Transformer #OTT651 located at 111 Aylmer isolated due to upgrading primary | Ottawa | Scheduled Outage | Construction
11532 | 2007 | 10 | 16 | 0.42014 |  | 150 | 20 | 8 | Sunnyside | 4.16kV | UY03 | Transformer #OTT769 located at 68 Barton isolated due to transferring plant | Ottawa | Scheduled Outage | Preventive Maintenance
11540 | 2007 | 10 | 17 | 0.38889 |  | 270 | 36 | 8 | SUNNYSIDE | 4.16kV | UY03 | Isolated and relocated transformer OTT769 at 46 Barton St to new pole | Ottawa | Scheduled Outage | Construction
11573 | 2007 | 10 | 22 | 0.54167 |  | 60 | 10 | 10 | Sunnyside | 4.16kV | UY03 | At 13:00 trans at 11 Aylmer was isolated in order to relocate conductor | Ottawa | Scheduled Outage | Repair
11580 | 2007 | 10 | 24 | 0.40625 |  | 110 | 11 | 6 | SUNNYSIDE | 4.16kV | UY03 | Transformer #X35431 at 7 Barton isolated to allow for replacement of transformer | Ottawa | Scheduled Outage | Preventive Maintenance
11595 | 2007 | 10 | 25 | 0.40972 |  | 130 | 22 | 10 | SUNNYSIDE | 4.16kV | UY03 | Transformer #OTT5570 at 38 Roslyn Ave isolated to allow for transfer of hydro plant | Ottawa | Scheduled Outage | Preventive Maintenance
11598 | 2007 | 10 | 25 | 0.40625 |  | 155 | 26 | 10 | SUNNYSIDE | 4.16kV | UY03 | Transformer #OTT654 at 10 Aylmer isolated to allow for transfer of Hydro plant | Ottawa | Scheduled Outage | Construction
11629 | 2007 | 10 | 30 | 0.35417 |  | 160 | 19 | 7 | Sunnyside | 4.16kV | UY03 | Isolated transformer OTT770 at 7 Barton to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Construction
11672 | 2007 | 11 | 6 | 0.375 |  | 268 | 45 | 10 | Suunyside | 4.16kV | UY03 | At 09:00 trans at 56 CARLYLE AVE was isolated inorder to upgrade trans | Ottawa | Scheduled Outage | Preventive Maintenance
11714 | 2007 | 11 | 15 | 0.43056 |  | 173 | 20 | 7 | Sunnyside | 4.16kV | UY03 | Transformer #OTT5550 located at 17 Rosedale isolated to replace transformer for upgrade (13Kv conversion) | Ottawa | Scheduled Outage | Preventive Maintenance
11736 | 2007 | 11 | 19 | 0.41319 |  | 125 | 19 | 9 | Sunnyside | 4.16kV | UY03 | Isolated transformer X26267 at 59 Rosedale Ave for 13kv conversion | Ottawa | Scheduled Outage | Construction
11768 | 2007 | 11 | 26 | 0.55208 |  | 135 | 36 | 16 | Sunnyside | 4.16kV | UY03 | Transformer #OTT5714 located at 25 Seneca isolated due to pole change | Ottawa | Scheduled Outage | Preventive Maintenance
11784 | 2007 | 11 | 28 | 0.375 |  | 150 | 600 | 240 | Sunnyside | 4.16kV | UY03 | UY03 feeder isolated and converted to 13 Kv feed from SC8233/TR3UY. | Ottawa | Scheduled Outage | Construction
11813 | 2007 | 12 | 5 | 0.39931 |  | 30 | 18 | 36 | Sunnyside | 4.16kV | UY03 | At 9:35 customers in the area of Aylmer and Seneca were without power for a scheduled maintenance to transfer UY03 circuit to SC8233-CA4. Bob Rolland informs system that everything east of Rosling along Aylmer has been transferred from UY03 to SC8233-CA4. ID 11813. | Ottawa | Scheduled Outage | Construction
11821 | 2007 | 12 | 7 | 0.375 |  | 75 | 12 | 10 | SUNNYSIDE | 4.16kV | UY03 | Transformers isolated to allow for pole replacements | Ottawa | Scheduled Outage | Construction
11968 | 2008 | 1 | 22 | 0.42708 |  | 99 | 13 | 8 | Sunnyside | 4.16kV | UY04 | At 10:15 trans at 24 Seneca was isolated in order to replace secondary service | Ottawa | Scheduled Outage | Preventive Maintenance
10037 | 2007 | 2 | 19 | 0.38056 |  | 127 | 11 | 5 | Sunnyside | 4.16kV | UY04 | Bob Rolland isolated TRF. @ 1097 Bronson for TRF. Change | Ottawa | Scheduled Outage | Preventive Maintenance
10047 | 2007 | 2 | 21 | 0.52778 |  | 120 | 80 | 40 | Sunnyside | 4.16kV | UY04 | At 12:40 ,3 trans on Fultan Ave were isolated in order to transfer plant to new poles | Ottawa | Scheduled Outage | Preventive Maintenance
10070 | 2007 | 2 | 27 | 0.39583 |  | 121 | 22 | 11 | Sunnyside | 4.16kV | UY04 | At 09:30 trans OTT2597 at 46 Fulton Ave was isolated in order to replace a pole | Ottawa | Scheduled Outage | Repair
10074 | 2007 | 2 | 28 | 0.35417 |  | 150 | 25 | 10 | Sunnyside | 4.16kV | UY04 | At 08:30 trans OTT2596 at 20 Fulton Ave was isolated in order to replace a pole | Ottawa | Scheduled Outage | Repair
10098 | 2007 | 3 | 7 | 0.55556 |  | 40 | 5 | 7 | Sunnyside | 4.16kV | UY04 | Rick Grisel isolated TRF at 73 Fulton to install new pole | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
10153 | 2007 | 3 | 21 | 0.375 |  | 210 | 175 | 50 | Sunnyside | 4.16kV | UY04 | Isolated 5 transformers on Fulton Av to string in new conductor | Ottawa | Scheduled Outage | Construction
10186 | 2007 | 3 | 27 | 0.37847 |  | 265 | 53 | 12 | Sunnyside | 4.16kV | UY04 | Transformer #OTT960 located at 1081 Bronson isolated due to pole transfer | Ottawa | Scheduled Outage | Preventive Maintenance
10192 | 2007 | 3 | 28 | 0.38611 |  | 142 | 14 | 6 | Sunnyside | 4.16kV | UY04 | At 09:16 trans OTT985 at 1097 Bronson Pl was isolated in order to replace a pole | Ottawa | Scheduled Outage | Repair
10197 | 2007 | 3 | 28 | 0.54514 |  | 160 | 27 | 10 | Sunnyside | 4.16kV | UY04 | Bob Rolland isolated the TRF. @ 1113 Bronson PL. for a pole change | Ottawa | Scheduled Outage | Equipment Deterioration Due to Age
10231 | 2007 | 4 | 10 | 0.36111 |  | 185 | 25 | 8 | Sunnyside | 4.16kV | UY04 | Isolated transformer OTT4853 at 48 Carlyle to replace pole | Ottawa | Scheduled Outage | Construction
10235 | 2007 | 4 | 10 | 0.53125 |  | 195 | 23 | 7 | Sunnyside | 4.16kV | UY04 | Transformer #OTT2600 located at 73 Fulton Ave isolated to transfer hydro plant | Ottawa | Scheduled Outage | Construction
10237 | 2007 | 4 | 11 | 0.35417 |  | 90 | 15 | 10 | Sunnyside | 4.16kV | UY04 | Isolated transformer 55D4C-0028 at 83 Fulton Ave to re-locate Hydro plante | Ottawa | Scheduled Outage | Construction
10243 | 2007 | 4 | 11 | 0.41667 |  | 360 | 42 | 7 | Sunnyside | 4.16kV | UY04 | Transformer #OTT2599 located at 74 Fulton isolated due to transferring Hydro plant | Ottawa | Scheduled Outage | Preventive Maintenance
10271 | 2007 | 4 | 17 | 0.38194 |  | 169 | 51 | 18 | SUNNYSIDE | 4.16kV | UY04 | BOB ROLLAND ISOLATED TRANSFORMER AT 37 FULLTON FOR POLE CHANGE. | Ottawa | Scheduled Outage | Preventive Maintenance
10277 | 2007 | 4 | 18 | 0.35417 |  | 205 | 27 | 8 | Sunnyside | 4.16kV | UY04 | BOB Rolland isolated TRF @ 27 Fulton for a pole change | Ottawa | Scheduled Outage | Preventive Maintenance
10282 | 2007 | 4 | 19 | 0.35069 |  | 245 | 33 | 8 | Sunnyside | 4.16kV | UY04 | Bob Rolland isolated TRF @ 5 Seneca for a pole change | Ottawa | Scheduled Outage | Preventive Maintenance
10804 | 2007 | 7 | 6 | 0.38194 |  | 199 | 13 | 4 | Sunnyside | 4.16kV | UY04 | At 09:10 trans at 16 Hopewell was isolated to replacae trans for voltage conversion | Ottawa | Scheduled Outage | Construction
10945 | 2007 | 7 | 24 | 0.42083 |  | 100 | 50 | 30 | Sunnyside | 4.16kV | UY04 | 4kv overhead section on Bronson Ave 4kv conversion to 13 kv, | Ottawa | Scheduled Outage | Construction
11280 | 2007 | 9 | 10 | 0.39583 |  | 173 | 46 | 16 | Sunnyside | 4.16kV | UY04 | Isolated and re-located transformer OTT5714 at 2 Pansy Ave to new pole | Ottawa | Scheduled Outage | Construction
9418 | 2006 | 10 | 12 | 0.4125 |  | 56 | 13 | 14 | Sunnyside | 4.16kV | UY04 | At 09:54 trans OTT1200 at 31 Pansy Ave was isolated for a service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
11702 | 2007 | 11 | 13 | 0.44097 |  | 105 | 12 | 7 | Sunnyside | 4.16kV | UY04 | At 10:354 trans at 3 Seneca St was isolated in order for voltage conversion | Ottawa | Scheduled Outage | Preventive Maintenance
5009 | 2004 | 4 | 17 | 0.84653 |  | 121 | 32 | 16 | Sunnyside | 4.16kV | UY05 | A fire at 109 Ossington,which call for the fuse at transfomer OTT4807 to be opened. The service to 109 Ossington was then disconnected. | Ottawa | Adverse Environment | Fire
10420 | 2007 | 5 | 15 | 0.45833 |  | 37 | 15 | 24 | Sunnyside | 4.16kV | UY05 | At 11:00 trans K544 at 1 Pentry was isolated in order to install a new pole | Ottawa | Scheduled Outage | Repair
10837 | 2007 | 7 | 10 | 0.47083 |  | 82 | 22 | 16 | Sunnyside | 4.16kV | UY05 | Transformer #OTT3287 at 47 Hopewell Ave isolated to allow for TX conversion | Ottawa | Scheduled Outage | Preventive Maintenance
3860 | 2003 | 8 | 6 | 0.60139 |  | 225 | 1129 | 301 | Sunnyside | 4.16kV | UY05 | UY05 circuit tripped and locked-out due to lightning strike. Phase separted from overhead insulator. This also caused UY06 to trip and lock-out. | Ottawa | Adverse Weather | Lightning
11316 | 2007 | 9 | 17 | 0.39931 |  | 85 | 14 | 10 | SUNNYSIDE | 4.16kV | UY05 | Transformer #X31973 at 195 Cameron isolated to allow for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11461 | 2007 | 10 | 4 | 0.375 |  | 150 | 30 | 12 | Sunnyside | 4.16kV | UY05 | 2 transformers isolated-1 at 149 Cameron (#OTT1113) & 1 at 191 Cameron (#OTT1119) for pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11544 | 2007 | 10 | 17 | 0.57292 |  | 75 | 12 | 10 | Sunnyside | 4.16kV | UY05 | At 13:45 trans at 10 Ossington was isolated ini order to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
11550 | 2007 | 10 | 18 | 0.38542 |  | 235 | 114 | 29 | Sunnyside | 4.16kV | UY05 | Transformer #OTT4806 & OTT4808 located at 7 & 16 Ossington isolated due to pole change | Ottawa | Scheduled Outage | Construction
11572 | 2007 | 10 | 22 | 0.375 |  | 180 | 30 | 10 | Sunnyside | 4.16kV | UY05 | At 09:00 trans at 70 Ozzington was isolated for a pole change | Ottawa | Scheduled Outage | Repair
11575 | 2007 | 10 | 22 | 0.39583 |  | 120 | 10 | 5 | Sunnyside | 4.16kV | UY05 | Transformer #OTT4814 located at 61 Ossington isolated due to pole change | Ottawa | Scheduled Outage
11597 | 2007 | 10 | 25 | 0.51042 |  | 13 | 2 | 10 | SUNNYSIDE | 4.16kV | UY05 | Transformer #X31678 at 39 Ossington isolated to allow for pole change | Ottawa | Scheduled Outage | Repair
11599 | 2007 | 10 | 25 | 0.37847 |  | 190 | 25 | 8 | SUNNYSIDE | 4.16kV | UY05 | Tranformer #OTT3941 at 89 Ossington isolated to allow for transfer of Hydro plant | Ottawa | Scheduled Outage | Preventive Maintenance
11625 | 2007 | 10 | 29 | 0.38542 |  | 165 | 36 | 13 | SUNNYSIDE | 4.16kV | UY05 | Transformer #X31683 at 55 Ossington isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
11627 | 2007 | 10 | 30 | 0.38889 |  | 60 | 15 | 15 | Sunnyside | 4.16kV | UY05 | The 4Kv O/H line in the Leonard & Cameron area was isolated to transfer plant over to 13Kv supply. | Ottawa | Scheduled Outage | Construction
11635 | 2007 | 10 | 31 | 0.35417 |  | 173 | 23 | 8 | Sunnyside | 4.16kV | UY05 | At 08:30 trans at 134 Ossington was isolated for PCB trans change | Ottawa | Scheduled Outage | Preventive Maintenance
11661 | 2007 | 11 | 5 | 0.29167 |  | 11 | 2 | 10 |  | 4.16kV | UY05 | At 7:00am a section of line on Glen Avenue, was isolated to allow the crew to convert from 4kV to the new 13kV system, 10 customers were affected for 11min. ID 11661. | Ottawa | Scheduled Outage | Construction
11681 | 2007 | 11 | 8 | 0.40694 |  | 77 | 128 | 100 | Sunnyside | 4.16kV | UY05 | The 4Kv O/h line on Ossington bet Seneca and Bank st was isolated for the 4kv to 13Kv conversion | Ottawa | Scheduled Outage
11703 | 2007 | 11 | 13 | 0.61806 |  | 17 | 8 | 30 | sunnyside | 4.16kV | UY05 | 4 transformers isolated on UY05 circuit and transferred to TR09 circuit | Ottawa | Scheduled Outage | Construction
11721 | 2007 | 11 | 15 | 0.85139 |  | 10 | 2 | 10 | Sunnyside | 4.16kV | UY05 | NIU UY05 circuit removed from service but some load still remains attached to circuit. Circuit restored from normal supply. | Ottawa | Human Element | Incorrect Construction
11943 | 2008 | 1 | 16 | 0.375 |  | 120 | 36 | 18 | Sunnyside | 4.16kV | UY06 | Transformer #OTT6155 located at 481 Sunnyside isolated to transfer hydro plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
11977 | 2008 | 1 | 24 | 0.54514 |  | 19 | 3 | 8 | Sunnyside | 4.16kV | UY06 | Transformer #55D4C-0152 located at 489 Sunnyside isolated due to conversion | Ottawa | Scheduled Outage | Preventive Maintenance
11999 | 2008 | 1 | 31 | 0.39931 |  | 83 | 14 | 10 | Sunnyside | 4.16kV | UY06 | At 09:35 trans at 451 Sunnyside was isolated in order for a pole change | Ottawa | Scheduled Outage
10044 | 2007 | 2 | 21 | 0.40417 |  | 43 | 6 | 8 | Sunnyside | 4.16kV | UY06 | Jim Yeldon isolated TRF OTT 2759 @ 42 Glen to transfer plant | Ottawa | Scheduled Outage | Preventive Maintenance
10324 | 2007 | 4 | 25 | 0.54167 |  | 120 | 14 | 7 | Sunnyside | 4.16kV | UY06 | At 13:00 trans at 141 Hopewell was isolated in order to relocate conductor | Ottawa | Scheduled Outage | Preventive Maintenance
10332 | 2007 | 4 | 26 | 0.44792 |  | 140 | 21 | 9 | Sunnyside | 4.16kV | UY06 | Isolated transformer OTT3282 at 141 Hopewell Ave to transfer hydro plante | Ottawa | Scheduled Outage | Construction
10333 | 2007 | 4 | 26 | 0.45694 |  | 13 | 2 | 11 | Sunnyside | 4.16kV | UY06 | Isolated transformer OTT3288 at 63 Hopewell Ave to relocate hydro plant | Ottawa | Scheduled Outage | Construction
10336 | 2007 | 4 | 26 | 0.56736 |  | 67 | 15 | 13 | Sunnyside | 4.16kV | UY06 | Isolated transformer OTT3284 at 174 Hopewell Ave to tranfer hydro plant | Ottawa | Scheduled Outage | Construction
10437 | 2007 | 5 | 22 | 0.375 |  | 230 | 92 | 24 | Sunnyside | 4.16kV | UY06 | At 12:50 trans at 54 Glen Ave was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
10440 | 2007 | 5 | 22 | 0.54167 |  | 75 | 30 | 24 | Sunnyside | 4.16kV | UY06 | Bob Rolland isolated TRF # 2760 @ 67 Glen for a pole change | Ottawa | Scheduled Outage | Preventive Maintenance
10449 | 2007 | 5 | 23 | 0.60694 |  | 26 | 5 | 11 | Sunnyside | 4.16kV | UY06 | Bob Rolland isolated TRF @ 50 Glen to tranfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
10450 | 2007 | 5 | 23 | 0.62847 |  | 55 | 9 | 10 | Sunnydide | 4.16kV | UY06 | Bob Rolland isolated trf. @ 95 Glen to relocate plant to new pole | Ottawa | Scheduled Outage
10469 | 2007 | 5 | 28 | 0.41667 |  | 210 | 21 | 6 | Sunnyside | 4.16kV | UY06 | Transformer #OTT2761 located at 74 Glen isolated to re-locate plant | Ottawa | Scheduled Outage | Construction
10476 | 2007 | 5 | 29 | 0.35417 |  | 285 | 38 | 8 | Sunnyside | 4.16kV | UY06 | Isolated transformer OTT2752 at 126 Glen Ave to replace pole | Ottawa | Scheduled Outage | Construction
10603 | 2007 | 6 | 11 | 0.42708 |  | 131 | 11 | 5 | Sunnyside | 4.16kV | UY06 | Isolated transformer at 150 Cameron Ave to replace primary switch | Ottawa | Scheduled Outage | Preventive Maintenance
10885 | 2007 | 7 | 16 | 0.57292 |  | 45 | 4 | 6 | SUNNYSIDE | 4.16kV | UY06 | Isolated transformer X31267 at 80 Grosvenor Ave to relocate the services to new pole | Ottawa | Scheduled Outage | Construction
10967 | 2007 | 7 | 30 | 0.37847 |  | 170 | 40 | 14 | Sunnyside | 4.16kV | UY06 | Crew isolated transformer OTT3290 at 91 Hopewell Ave to replace pole | Ottawa | Scheduled Outage | Construction
10980 | 2007 | 8 | 1 | 0.35069 |  | 98 | 24 | 15 | Sunnyside | 4.16kV | UY06 | Transformer #OTT3289 located at 73 Hopewell isolated to transfer plant to new poles | Ottawa | Scheduled Outage | Construction
3861 | 2003 | 8 | 6 | 0.60139 |  | 225 | 1099 | 293 | Sunnyside | 4.16kV | UY06 | UY05 circuit tripped and locked-out due to lightning strike. Phase separted from overhead insulator. This also caused UY06 to trip and lock-out. | Ottawa | Adverse Weather | Lightning
3864 | 2003 | 8 | 6 | 0.84583 |  | 132 | 24 | 11 | Bronson | 4.16kV | UY06 | One of two banked 37.5 KVA transformers 3280 at 133 Hopewell was defective. The remaining transformer was rewired to feed the 11 customers for the night by itself. The transformer bank is to be changed tomorrow. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
11007 | 2007 | 8 | 7 | 0.37917 |  | 144 | 22 | 9 | Sunnyside | 4.16kV | UY06 | At 09:06 trans at 99 Hopewell was isolated in order to replace trans pole | Ottawa | Scheduled Outage | Repair
11015 | 2007 | 8 | 8 | 0.54167 |  | 99 | 8 | 5 | Sunnyside | 4.16kV | UY06 | At 13:00 trans OTT3278 at 109 Hopewewll was isolated in order to energize new sec buss | Ottawa | Scheduled Outage | Construction
11027 | 2007 | 8 | 9 | 0.38889 |  | 130 | 11 | 5 | Sunnyside | 4.16kV | UY06 | Transformer #OTT3278 located at 111 Hopewell Ave isolated to transfer plant to new pole | Ottawa | Scheduled Outage | Construction
11042 | 2007 | 8 | 13 | 0.375 |  | 420 | 42 | 6 | Sunnyside | 4.16kV | UY06 | Transformer #OTT3282 at 137 Hopewell Ave isolated to allow for pole transfer | Ottawa | Scheduled Outage | Preventive Maintenance
11045 | 2007 | 8 | 14 | 0.375 |  | 120 | 22 | 11 | Sunnyside | 4.16kV | UY06 | At 09:00 trans OTT3280 at 135 Hopewell was isolated in order to transfer plant to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
11050 | 2007 | 8 | 14 | 0.59375 |  | 210 | 28 | 8 | Sunnyside | 4.16kV | UY06 | Transformer #OTT3279 at 117 Hopewell ave isolated to allow for conversion - transfer of plant | Ottawa | Scheduled Outage | Construction
11127 | 2007 | 8 | 22 | 0.45139 |  | 30 | 6 | 12 | Sunnyside | 4.16kV | UY06 | Isolated transformer X30377 at 197 Hopewell Av to replace pole | Ottawa | Scheduled Outage | Construction
11131 | 2007 | 8 | 23 | 0.375 |  | 195 | 49 | 15 | Sunnyside | 4.16kV | UY06 | 2 Transformers at 157 Hopewell & 190 Hopewell isolated due to transferring plant to new pole | Ottawa | Scheduled Outage | Construction
11135 | 2007 | 8 | 23 | 0.5625 |  | 50 | 11 | 13 | Sunnyside | 4.16kV | UY06 | Transformer #OTT3284 located at 177 Hopewell isolated due to transferring plant to new pole | Ottawa | Scheduled Outage | Construction
11252 | 2007 | 9 | 5 | 0.52431 |  | 55 | 11 | 12 | Sunnyside | 4.16kV | UY06 | Transformer #332281 at 197 Hopewell Ave isolated to allow for maintenance | Ottawa | Scheduled Outage | Preventive Maintenance
11293 | 2007 | 9 | 12 | 0.37222 |  | 94 | 13 | 8 | Sunnyside | 4.16kV | UY06 | Transformer at 50 Gravel isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
11384 | 2007 | 9 | 25 | 0.35417 |  | 120 | 18 | 9 | Sunnyside | 4.16kV | UY06 | Transformer #OTT2886 located at 105 Grove Ave isolated due to pole replacement | Ottawa | Scheduled Outage | Preventive Maintenance
11390 | 2007 | 9 | 26 | 0.53125 |  | 65 | 9 | 8 | Sunnyside | 4.16kV | UY06 | Transformer #OTT2888 located at 115 Grove Ave isolated due to pole transfer | Ottawa | Scheduled Outage | Preventive Maintenance
11442 | 2007 | 10 | 2 | 0.375 |  | 195 | 52 | 16 | SUNNYSIDE | 4.16kV | UY06 | Transformer #OTT2894 at 50 Grove isolated to allow for transfer of plant to new pole | Ottawa | Scheduled Outage | Construction
11444 | 2007 | 10 | 2 | 0.55417 |  | 102 | 22 | 13 | Sunnyside | 4.16kV | UY06 | Isolated transformer OTT2892 at 41 Grove Cres to transfer hydro plant | Ottawa | Scheduled Outage | Construction
11450 | 2007 | 10 | 3 | 0.36806 |  | 116 | 17 | 9 | Sunnyside | 4.16kV | UY06 | At 08:50 trans at 10 Grove Ave was isolated for a pole change | Ottawa | Scheduled Outage | Preventive Maintenance
11483 | 2007 | 10 | 9 | 0.36458 |  | 104 | 12 | 7 | Sunnyside | 4.16kV | UY06 | Transformer #OTT2890 located at 24 Grove isolated due to pole change. | Ottawa | Scheduled Outage | Construction
11488 | 2007 | 10 | 9 | 0.4375 |  | 60 | 8 | 8 | SUNNYSIDE | 4.16kV | UY06 | Tranformer #OTT2890 at 15 Grove isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
11497 | 2007 | 10 | 10 | 0.42361 |  | 320 | 80 | 15 | Sunnyside | 4.16kV | UY06 | Transformer #34449 at 97 Grove isolated to allow for pole change | Ottawa | Scheduled Outage | Preventive Maintenance
11644 | 2007 | 11 | 1 | 0.40347 |  | 39 | 39 | 60 | Sunnyside | 4.16kV | UY06 | Overhead section of the UY06 circuit on Hopewell Ave isolated to convert it from 4 Kv to 13 Kv. Section now being supplied from SC8233-CA3. | Ottawa | Scheduled Outage | Construction
11646 | 2007 | 11 | 1 | 0.375 |  | 146 | 19 | 8 | Sunnyside | 4.16kV | UY06 | At 09:00 trans at Leonard at Hopewell was isolated to transfer planr | Ottawa | Scheduled Outage | Preventive Maintenance
9855 | 2006 | 12 | 18 | 0.44444 |  | 20 | 4 | 13 | Sunnyside | 4.16kV | UY06 | Transformer #OTT2754 located at 151 Glen Ave isolated to connect secondary service | Ottawa | Scheduled Outage | Construction
11993 | 2008 | 1 | 30 | 0.52431 |  | 122 | 20 | 10 | Walkley | 4.16kV | UZ02 | Transformer K147 at 80 Sandwalk isolated to replace defective insulators. | Ottawa | Scheduled Outage | Repair
11994 | 2008 | 1 | 30 | 0.55556 |  | 76 | 13 | 10 | Walkley | 4.16kV | UZ02 | Transformer K146 at 79 Sandwalk isolated for insulator repairs. | Ottawa | Scheduled Outage
11996 | 2008 | 1 | 31 | 0.37153 |  | 111 | 37 | 20 | Walkley | 4.16kV | UZ02 | K190, K191 & K192 on the UZ02 were isolated to allow crew to replace broken bus insulators. | Ottawa | Scheduled Outage | Preventive Maintenance
10540 | 2007 | 6 | 6 | 0.45833 |  | 60 | 30 | 30 | Walkley | 4.16kV | UZ02 | Isolated and replaced transformer K395 at 1450 Heatherington Ave (PCB OIL) | Ottawa | Scheduled Outage | Preventive Maintenance
14492 | 2009 | 6 | 8 | 0.4375 |  | 22 | 4 | 10 | Walkley | 4.16kV | UZ02 | Transformer K771 at 12 Walton Court was isolated to allow for PCB sample | Nepean | Scheduled Outage
10611 | 2007 | 6 | 12 | 0.55556 |  | 115 | 17 | 9 | Walkley | 4.16kV | UZ02 | At 13:20 trans at 86 Sandwalk was isolated for trans PCB replacement | Ottawa | Scheduled Outage | Repair
10657 | 2007 | 6 | 19 | 0.375 |  | 177 | 9 | 3 | Walkley | 4.16kV | UZ02 | At 09:00 trans at 123 Dorothea Dr was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Repair
16307 | 2010 | 6 | 21 | 0.375 |  | 332 | 188 | 34 | Walkley | 4.16kV | UZ02 | At 9:00 am, a section of primary line on Blanchard was isolated for tree trimming and minor line repairs. | Ottawa | Scheduled Outage
5630 | 2004 | 8 | 9 | 0.875 |  | 331 | 33 | 6 | Walkley | 4.16kV | UZ02 | Faulty transformer switch in K765 caused outage to that tranformer only, call passed to the on-call crew | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9040 | 2006 | 8 | 24 | 0.42847 |  | 82 | 15 | 11 | WALKLEY | 4.16kV | UZ02 | K150 on Sandwalk Private was isolated to replace broken insulators. 11 Customers affected. | Ottawa | Scheduled Outage
9049 | 2006 | 8 | 24 | 0.39583 |  | 150 | 28 | 11 | Walkley | 4.16kV | UZ02 | Isoalted transformer K150 at 86 Sandwalk Prvt to replace broken insulator | Ottawa | Scheduled Outage | Repair
11198 | 2007 | 8 | 29 | 0.78264 |  | 14 | 29 | 123 | Walkley | 13.2kV | UZ02 | UZ02 opened and locked out, circuit closed back in via SCADA and holding | Ottawa | Adverse Weather
15573 | 2009 | 12 | 27 | 0.79167 |  | 59 | 49 | 50 | Walkley |  | UZ02 | Radial line section on Blanchard & Otterson isolatd to remove tree limbs from primary. | Ottawa | Adverse Weather | Ice Storm
3879 | 2003 | 8 | 9 | 0.31319 |  | 22 | 125 | 340 | Walkley | 4.16kV | UZ02, UZ12 | UZ02 & UZ12 locked out after an OC Transpo bus hit a hydro pole on Walkley Rd just west of Springland. The impact caused the circuits to make contact with each other. The pole hit by bus is leaning slightly but is secure. No apparent damage to UZ02 & UZ12 circuits. OC Transpo reports hydro pole was hit by Employee #2937 in Bus ID #9138 (run 140-4), on duty supervisor Mr. Smith, Control Rm 842-3611. (No Police report, police were called but did not respond as event was over with no major problems or injuries.) | Ottawa | Foreign Interference | Vehicle
6116 | 2005 | 1 | 4 | 0.44792 |  | 233 | 35 | 9 | Walkley | 4.16kV | UZ03 | Planned outage to transformer OTT2156 at 2573 Egan for pole replacement. | Ottawa | Scheduled Outage | Repair
12024 | 2008 | 2 | 8 | 0.54861 |  | 42 | 10 | 15 | WALKLEY | 13.2kV | UZ03 | transformer #24824 at 2635 Ulster isolated to allow to change a service | Ottawa | Scheduled Outage | Repair
4906 | 2004 | 3 | 16 | 0.38889 |  | 150 | 25 | 10 | Walkley | 4.16kV | UZ03 | Crew opened transformer at 2573 Egan to change the pole. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
4912 | 2004 | 3 | 17 | 0.39931 |  | 185 | 31 | 10 | Walkley | 4.16kV | UZ03 | Ott2156 at 2673 Egan Rd 10 customers out to reolcate plant by Lee Piper. | Ottawa | Scheduled Outage | Construction
20257 | 2012 | 3 | 30 | 0.375 |  | 85 | 6 | 4 | Walkley | 4.16kV | UZ03 | Transformer #X24820 located at 2637 Colman St opened by crew for maintenance. | Ottawa | Scheduled Outage | Construction
20258 | 2012 | 3 | 30 | 0.375 |  | 85 | 8 | 6 | Walkley | 4.16kV | UZ03 | Transformer #X27724 located at 2651 Colman St opened by crew for maintenance. | Ottawa | Scheduled Outage
14172 | 2009 | 4 | 14 | 0.75903 |  | 205 | 911 | 327 | Walkley | 4.16kV | UZ03 | UZ03 bkr auto trip, circuit sectionalized and patrolled, no problem found. Circuit energized and all customers restored. | Ottawa | Unknown/Other | No Apparent Cause
5031 | 2004 | 4 | 21 | 0.40208 |  | 8 | 26 | 198 | Walkley |  | UZ03 | UZ03 breaker at Walkley opened by SCADA at request of J. Magee for J. Petrachuk & crew to remove a large tree from the primary on Cromwell. 198 customers in area between Walkley & Cromwell and CNR tracks & Airport Pkwy affected. Breaker closed by SCADA when tree removed and men clear. | Ottawa | Tree Contacts | Tree Fallen
10532 | 2007 | 6 | 5 | 0.46875 |  | 90 | 15 | 10 | walkley | 4.16kV | UZ03 | Mark Branchaud isolated TRF @ 2754 Coleman for a service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
10620 | 2007 | 6 | 13 | 0.54792 |  | 96 | 11 | 7 | Walkley | 4.16kV | UZ03 | AT 13:09 trans at 1060 Wiseman was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
20774 | 2012 | 6 | 14 | 0.37847 |  | 33 | 3 | 6 | Walkley | 4.16kV | UZ03 | Isolated transformer X24822 at 947 Cromwell Dr to relocate secondary service | Ottawa | Scheduled Outage | Emergency Services Request
8550 | 2006 | 6 | 20 | 0.54514 |  | 25 | 2 | 4 | Walkley | 4.16kV | UZ03 | Transformer #OTT3002 located at 946 Harkness isolated to make secondary repairs | Ottawa | Adverse Weather | Wind
12807 | 2008 | 7 | 8 | 0.60764 |  | 7 | 23 | 198 | Walkley | 4.16kV | UZ03 | At 2:35pm UZ03 breaker opened due to tree contact where the circuit runs through the backyard of Coleman Street. Customers saw flash when trees made contact with overhead conductors. 198 customers were affected and power was restored at 2:42pm. Sent to forestry. Walkley (UZ03). ID#12807. | Ottawa | Tree Contacts
18622 | 2011 | 7 | 8 | 0.88819 |  | 151 | 93 | 37 | Walkley | 4.16kV | UZ03 | S22257 red phase was found open, patrol revealed nothing, refused and closed load restored. | Ottawa | Unknown/Other
18630 | 2011 | 7 | 9 | 0.40972 |  | 89 | 55 | 37 | Walkley | 4.16kV | UZ03 | Tree fell onto oerhead line at 93 Cromwell Drive, crew isolated line and contractor removed tree. Walkley (UZ03) ID#18630. | Ottawa | Tree Contacts
18780 | 2011 | 7 | 20 | 0.50347 |  | 94 | 58 | 37 | Walkley | 4.16kV | UZ03 | Switch S22257 was opened for isolation of UZ03 circuit on cromwell to allow crew to remove tree from primary. | Ottawa | Adverse Weather | Wind
5646 | 2004 | 8 | 10 | 0.88958 |  | 11 | 36 | 198 | Walkley | 4.16kV | UZ03 | Lightening caused primary phase down on Coleman. Phase was a dead ended run with no customers past the break in the primary. The circuit was opened by SCADA to allow the crew to cut clear the downed primary. | Ottawa | Lightning | Direct Strike
5664 | 2004 | 8 | 11 | 0.42917 |  | 20 | 66 | 198 | Walkley | 4.16kV | UZ03 | UZ03 breaker opened from SCADA in order to repair downed conductor from yesterday's storm. Repairs were made & circuit restored to normal. | Ottawa | Adverse Weather | Lightning
18942 | 2011 | 8 | 16 | 0.43264 |  | 23 | 4 | 10 | Walkley | 4.16kV | UZ03 | Transformer X24815 @ 1014 Cromwell was opened to allow crew to re-fuse street lighting | Ottawa | Scheduled Outage | Repair
9756 | 2006 | 11 | 30 | 0.37153 |  | 167 | 11 | 4 | Walkley | 4.16kV | UZ03 | Transformer #1600 located at 2708 Coleman isolated to change transformer for PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
11825 | 2007 | 12 | 9 | 0.27431 |  | 221 | 57 | 25 | Walkley | 4.16kV | UZ03 | At 3:22am customers in the area of Cromwell and Coleman called in claiming no power. 24-7 discovered the overhead circuit shorting across a connection to insulator in backyard of 1077 Cromwell. 24-7 opened blue phase S22257 and placed PC10a tag to do their work, from 12 to 25 customers were affected for …min. ID#11825. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
9856 | 2006 | 12 | 18 | 0.375 |  | 120 | 10 | 5 | Walkley | 4.16kV | UZ03 | Transformer located at 2702 Coleman isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
6119 | 2005 | 1 | 5 | 0.42361 |  | 155 | 23 | 9 | Walkley | 4.16kV | UZ04 | Transformer Ott 2156 isolated at 2573 Egan to transfer service. | Ottawa | Scheduled Outage | Repair
9962 | 2007 | 1 | 24 | 0.23264 |  | 265 | 43 | 11 | Walkley | 4.16kV | UZ04 | A burnt B phase connection on the O/H at the corner of Sringland and Confederation caused outage to the B phase customers and single phasing a three phase customers, so they had to be open up to protect there equipment and eny back feed. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
16144 | 2010 | 5 | 25 | 0.93333 |  | 337 | 110 | 213 | WALKLEY | 4.16kV | UZ04 | UZ04 breaker tripped. UZ04 breaker closed by SCADA and to be patrolled in daylight. Trouble call at 3:15 am, customer advised he had no power. 24/7 found blown arrestor which caused S23181 to blow. Arrestor cut clear switch refused and closed. | Ottawa | Unknown/Other
10683 | 2007 | 6 | 20 | 0.54167 |  | 188 | 19 | 6 | Walkley | 4.16kV | UZ04 | Transformer #OTT3214 located at 2603 Egan isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
18494 | 2011 | 6 | 24 | 0.68889 |  | 8 | 28 | 213 | Walkley | 4.16kV | UZ04 | UZ04 circuit auto reclosed & locked out. Circuit was reclosed via scada all load restored | Ottawa | Adverse Weather | Lightning
16795 | 2010 | 8 | 22 | 0.29583 |  | 331 | 44 | 8 | Walkley | 4.16kV | UZ04 | K803 dip switch & kiosk arrester at 12 Confederation Private were found defective and crews replaced and restored power. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
13198 | 2008 | 9 | 6 | 0.26458 |  | 272 | 115 | 187 | WALKLEY | 4.16kV | UZ04 | UZ04 Breaker auto tripped. S22074 found blown, due to blown arrester at K807 on Flannery Drive. Repairs made, S22074 refused to restore power. | Ottawa | Defective Equipment
19183 | 2011 | 9 | 15 | 0.41667 |  | 145 | 22 | 9 | Walkley | 4.16kV | UZ04 | Transformer #X28131 located at 2573 Egan Rd opened by crew for tree removal | Ottawa | Tree Contacts | Tree Fallen
7395 | 2005 | 9 | 29 | 0.24028 |  | 213 | 660 | 186 | Walkley | 4.16kV | UZ04 | Patrolled and nothing found restored and held. | Ottawa | Unknown/Other | No Apparent Cause
7410 | 2005 | 9 | 29 | 0.51667 |  | 202 | 630 | 187 | Walkley | 4.16kV | UZ04 | Tree fell across overhead pulling down 2 primary circuits, isolated for repairs | Ottawa | Tree Contacts | Tree Fallen
17734 | 2011 | 3 | 18 | 0.42708 |  | 30 | 6 | 13 |  |  | UZ05 | Transformer X27927 at 2998 Rankin isolated to change triplex switch and renew connections | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
6317 | 2005 | 3 | 24 | 0.053472 |  | 257 | 328 | 208 | Walkley | 4.16kV | UZ05 | At aprox 01:17 a vehicle hit a pole at Fielding and Farmington causing a phase to come down. 24/7crews responded. On call personal were called in at 02:05. Crew requested UZ05 be isolated to make repairs @ 04:38. 05:34 all customer restored | Ottawa | Foreign Interference | Vehicle
10260 | 2007 | 4 | 16 | 0.29167 |  | 335 | 843 | 208 | Walkley | 4.16kV | UZ05 | Tree fell pulling down the 3 phase of the UZ05 at 624 Southmore. Heavey Snow caused the tree limb to break off and fall on the O/H | Ottawa | Adverse Weather | Snow
10344 | 2007 | 4 | 30 | 0.38819 |  | 129 | 204 | 200 | Walkley | 4.16kV | UZ05 | Tree on circuit behind 658 Southmore. | Ottawa | Adverse Weather | Wind
18139 | 2011 | 5 | 12 | 0.42708 |  | 123 | 25 | 12 | Walkley | 4.16kV | UZ05 | Transformer X27383 at 529 Fielding Crt was open to allow tree trimmers to remove falling tree. 12 customers were affected. Walkley (UZ05) | Ottawa | Scheduled Outage
20573 | 2012 | 5 | 25 | 0.5 |  | 42 | 4 | 5 | Walkley | 4.16kV | UZ05 | Transformer #X27933 located at 715 Hartman opened by crew to reconnect after a fire, installed 15m of #2 triplex | Ottawa | Scheduled Outage | Imminent Equipment Failure Detected
20708 | 2012 | 6 | 7 | 0.54861 |  | 51 | 10 | 12 | Walkley | 4.16kV | UZ05 | Transformer X27925 at 721 Southmore Dr. isolated for service upgrade | Ottawa | Scheduled Outage | Construction
20721 | 2012 | 6 | 8 | 0.72847 |  | 175 | 88 | 30 | Walkley | 4.16kV | UZ05 | Tree fall and contacted overhead conductor causing outage to 30 customers in the Southmore area. | Ottawa | Tree Contacts | Tree Fallen
20729 | 2012 | 6 | 9 | 0.37153 |  | 55 | 11 | 12 | Walkley | 4.16kV | UZ05 | Isolated transformer X27893 at 638 Dickinson Ave to repair secondary services and trim trees | Ottawa | Tree Contacts | Tree Limb Fallen
8740 | 2006 | 7 | 16 | 0.64583 |  | 106 | 19 | 11 | Walkley | 4.16kV | UZ05 | Replaced a defective transformer OTT 6350 @ 606 Fielding Dr. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
5638 | 2004 | 8 | 10 | 0.75347 |  | 600 | 140 | 14 | Walkley | 4.16kV | UZ05 | Lightning storm, heavy rain & wind in area at time of trip. Lightening strike on a transformewr on Dickenson caused this outage and fryed the transformer. | Ottawa | Lightning | Direct Strike
7396 | 2005 | 9 | 29 | 0.39653 |  | 336 | 1154 | 206 | Walkley | 4.16kV | UZ05 | A tree fell on the primary on Southmore breaking all 3 phases of the primary. | Ottawa | Tree Contacts | Tree Fallen
7411 | 2005 | 9 | 29 | 0.51667 |  | 202 | 700 | 208 | Walkley | 4.16kV | UZ05 | Tree fell across overhead pulling down 2 primary circuits, isolated for repairs | Ottawa | Tree Contacts | Tree Fallen
4286 | 2003 | 10 | 17 | 0.375 |  | 80 | 19 | 14 | Walkley | 4.16kV | UZ05 | Transformer at 698 fielding was opened to remove tree limb from o/h. | Ottawa | Tree Contacts | Tree Limb Fallen
4287 | 2003 | 10 | 17 | 0.375 |  | 80 | 4 | 3 | Walkley | 4.16kV | UZ05 | transformer at 711 burton was opened to remove tree limb from o/h. | Ottawa | Tree Contacts
9735 | 2006 | 11 | 27 | 0.34722 |  | 150 | 35 | 14 | Walkley | 4.16kV | UZ05 | Chris Williams changed PCB trf. # 1036 @ 710 Buxton | Ottawa | Scheduled Outage | Preventive Maintenance
9740 | 2006 | 11 | 27 | 0.49653 |  | 142 | 33 | 14 | Walkley | 4.16kV | UZ05 | Transformer 2382 at 707 Farmington opened up to replace Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
9781 | 2006 | 12 | 2 | 0.71597 |  | 17 | 59 | 208 | Walkley | 4.16kV | UZ05 | Tree on the overhead at the rear of 558 Dickinson required isolation for safe removal | Ottawa | Tree Contacts | Tree Fallen
9869 | 2006 | 12 | 20 | 0.3875 |  | 95 | 8 | 5 | Walkley | 4.16kV | UZ05 | Isolated Transformer at 680 Hartman to replace the PCB Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
9994 | 2007 | 2 | 6 | 0.42708 |  | 10 | 2 | 10 | Walkley | 4.16kV | UZ06 | Isolated transformer OTT 4196 at 2657 Marble Cres to replace primary riser lead on the switch | Ottawa | Scheduled Outage | Preventive Maintenance
10211 | 2007 | 4 | 4 | 0.42361 |  | 30 | 4 | 8 | Walkley | 4.16kV | UZ06 | Isolated transformer K825 at the rear of 789 Mooney's Bay Place to replace connection on secondary service | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
12627 | 2008 | 6 | 14 | 0.80694 |  | 395 | 192 | 253 | Walkey | 4.16kV | UZ06 | Bird Contact at Pot Head caused flashover and possible damage to south side cable between PPH and V578. Cable did not meggar well. Power restored by spare cable. | Ottawa | Foreign Interference | Bird
10693 | 2007 | 6 | 21 | 0.37431 |  | 169 | 20 | 7 | Walkley | 4.16kV | UZ06 | At 08:59 trans at 1 Lyndhurst was isolated for PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
18691 | 2011 | 7 | 17 | 0.80903 |  | 1017 | 11085 | 654 | Walkley | 4.16kV | UZ06 | The wind caused the top of a tree to fall into the UZ06 causing the circuit to trip. | Ottawa | Adverse Weather | Wind
16835 | 2010 | 8 | 30 | 0.56181 |  | 61 | 665 | 654 | Walkey | 4.16kV | UZ06 | SCADA reports UZ06 OPEN, crews report tree contact at 2723 Flannery cause to twist at 2752 Colman. | Ottawa | Tree Contacts
15262 | 2009 | 10 | 14 | 0.66319 |  | 40 | 5 | 8 | Walkley | 4.16kV | UZ06 | Opened switch to transfomer X28135 at the rear of 2633 Norberry cres to isolate the seconday on the pole at the rear of 2627 Norberry to replace the pole pot head switchers feeding V733 | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
19770 | 2011 | 12 | 29 | 0.91458 |  | 39 | 577 | 888 | Walkley DS | 4.16kV | UZ06 & UZ07 | A MVA at 2723 Flannery Dr. Caused the UZ06 & UZ07 circuits to open. 24/7 crew inspected the pole & circuits. All ok. | Ottawa | Foreign Interference | Vehicle
11997 | 2008 | 1 | 31 | 0.52431 |  | 54 | 7 | 8 | WALKLEY | 4.16kV | UZ07 | K103 on Bayside Private was isolated to replace broken insulators in kiosk. | Ottawa | Scheduled Outage
12013 | 2008 | 2 | 6 | 0.44028 |  | 73 | 2 | 2 | Walkley | 4.16kV | UZ07 | Transformer P90 at 2817 Riverside Dr isolated to replace PPH switches damaged when a plow hit the pole. | Kanata | Foreign Interference | Vehicle
12016 | 2008 | 2 | 7 | 0.4 |  | 85 | 20 | 14 | Walkley | 4.16kV | UZ07 | At 9:36am, transformers K939 & K938, was isolated to allow crews to repair broken insulators in Kiosk and respective switches on Pole 9 & Pole 10, 14 customers affected for 85min. ID#12016. | Ottawa | Scheduled Outage | Preventive Maintenance
12017 | 2008 | 2 | 7 | 0.52083 |  | 60 | 12 | 12 | Walkley | 4.16kV | UZ07 | At am, transformer K924, was isolated to allow crews to repair broken insulators in Kiosk, 12 customers affected for 60min. ID#12017. | Ottawa | Scheduled Outage | Preventive Maintenance
10127 | 2007 | 3 | 14 | 0.50486 |  | 61 | 209 | 206 | Walkley | 4.16kV | UZ07 | An 18 wheeler truck hit and broke the pole at UZ07 Dip 1. Circuit was isolated (UZ07) to make repairs. | Ottawa | Foreign Interference | Vehicle
12308 | 2008 | 4 | 19 | 0.6625 |  | 158 | 116 | 44 | Walkley | 4.16kV | UZ07 | Dip pole switch feeding kiosk transformers on Flannery Dr & Ramsgate Pvt failed. | Ottawa | Defective Equipment
10421 | 2007 | 5 | 15 | 0.55556 |  | 80 | 11 | 8 | Walkley | 4.16kV | UZ07 | Isolated and replaced transformer OTT5923 at 2692 Springland Dr | Ottawa | Scheduled Outage | Preventive Maintenance
18270 | 2011 | 6 | 1 | 0.62708 |  | 3 | 12 | 235 | Walkley | 4.16kV | UZ07 | UZ07 tripped under hold off. High winds in place. UZ07 closed and load restored. Riverside, Springland area. | Ottawa | Adverse Weather | Wind
10580 | 2007 | 6 | 9 | 0.26389 |  | 221 | 11 | 3 | Walkley | 4.16kV | UZ07 | O/H transformer at Brookfield and Riverside isolated planned outage, to transfer plant to new pole. | Ottawa | Scheduled Outage | Construction
10609 | 2007 | 6 | 12 | 0.375 |  | 140 | 16 | 7 | Walkley | 4.16kV | UZ07 | Transformer #OTT690 located at 2015 Banff isolated to allow for PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
18495 | 2011 | 6 | 24 | 0.68889 |  | 8 | 31 | 235 | Walkley | 4.16kV | UZ07 | UZ07 circuit opened & locked out during lightening storm. UZ07 circuit was closed via scada. All load restored | Ottawa | Adverse Weather | Lightning
6864 | 2005 | 7 | 3 | 0.98611 |  | 30 | 102 | 203 | UZ | 4.16kV | UZ07 | UZ07 opened to remove broken tree from primary conductor at 2718 Dupont ( Mooney's Bay area ). | Ottawa | Tree Contacts | Tree Fallen
6878 | 2005 | 7 | 6 | 0.47917 |  | 41 | 1 | 1 | Walkley | 4.16kV | UZ07 | P44 at 2833 Riverside was isolated to change faulty cutout. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
11000 | 2007 | 8 | 6 | 0.21597 |  | 79 | 24 | 18 | Walkley | 4.16kV | UZ07 | 2 transformers interupted due to animal contact with a lateral fuse, broken cutout replaced 18 customers affected were on Springland, Dupont, and Ridgewood. | Ottawa | Foreign Interference | Animal
15582 | 2009 | 12 | 28 | 0.43889 |  | 62 | 126 | 122 | Walkley | 4.16kV | UZ07 | At 2657 Marble Cresent crews found primary conductors tangled together which caused the UZ07 breaker to open. | Gloucester | Adverse Weather | Ice Storm
17459 | 2010 | 12 | 30 | 0.34375 |  | 65 | 3 | 3 | Walkley | 4.16kV | UZ07 | At 08:15 transformer X28019 at 700 Brookfield was isolated to allow crew to replace broken pole. | Ottawa | Scheduled Outage
7826 | 2006 | 1 | 19 | 0.41667 |  | 56 | 11 | 12 | Walkly | 4.16kV | UZ10 | At 10:00 trans K812 isloated to replaced defective arresttor | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10147 | 2007 | 3 | 19 | 0.43611 |  | 42 | 6 | 8 | Walkley | 4.16kV | UZ10 | Isolate K812 @ 21 Sandhurst on the UZ10 circuit and tranfer to the UZ04 O/H ciruit. | Ottawa | Scheduled Outage | Construction
5073 | 2004 | 4 | 29 | 0.82986 |  | 138 | 23 | 10 | Walkley | 4.16kV | UZ10 | Crew changed defective insulators at K811 at 33 Sandhurst. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
5813 | 2004 | 9 | 15 | 0.21042 |  | 157 | 168 | 117 | Walkley Sub | 4.16kV | UZ10 | Blown arrestor @ kiosk K807 cleared. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
7468 | 2005 | 10 | 16 | 0.58333 |  | 50 | 148 | 177 | WALKLEY | 4.16kV | UZ10 | PIE BRANCH FOUND ON RED PHASE OF UZ10 CIRCUIT WHEN PATROLLED BY 24/7 CREW & FOUND BURNT. WAS CLEARED FROM LINE BY 24/7 CREW. | Ottawa | Tree Contacts | Tree Limb Fallen
7469 | 2005 | 10 | 16 | 0.76389 |  | 67 | 131 | 117 | UZ | 4.16kV | UZ10 | UZ10 tripped during windy conditions. Cct was patrolled & found to be clear. Closed via scada & held. Some burn marks were found on conductor indicating tree contacts. | Ottawa | Tree Contacts | Inadequate Trimming
9772 | 2006 | 12 | 1 | 0.56736 |  | 203 | 508 | 150 | Walkley | 4.16kV | UZ10 | P/P/H switchs @Flannery/Springland burnt up due to freezing rain. | Ottawa | Adverse Weather | Ice Storm
17467 | 2011 | 1 | 4 | 0.56944 |  | 20 | 3 | 10 | Walkley | 4.16kV | UZ11 | Isolated transformer X34446 at 889 Thorndale Dr for a service up-grade | Ottawa | Scheduled Outage | Emergency Services Request
20181 | 2012 | 3 | 20 | 0.38542 |  | 174 | 46 | 16 | Walkley | 4.16kV | UZ11 | K531 @ 829 Thorndale was isolated for planned replacement | Ottawa | Scheduled Outage | Construction
17780 | 2011 | 3 | 24 | 0.58681 |  | 60 | 4 | 4 | Walkley | 4.16kV | UZ11 | Transformer #X24908 located at 921 Garwood Ave opened by crew to reconnect service | Ottawa | Scheduled Outage | Construction
14118 | 2009 | 3 | 30 | 0.51875 |  | 22 | 4 | 10 | WALKLEY | 4.16kV | UZ11 | Transformer X27807 at 2982 Marcel St. isolated to allow for repair of streetlight fuse holder | Ottawa | Scheduled Outage | Repair
14278 | 2009 | 5 | 1 | 0.42708 |  | 51 | 19 | 22 | Walkley | 4.16kV | UZ11 | Single phase radial line south of Provost between Hyde & Marcel was isolated to remove tree from line. 2 O/H xfmrs were interrupted affecting 22 customers on Hyde & Marcel. | Ottawa | Tree Contacts | Tree Limb Fallen
18228 | 2011 | 5 | 27 | 0.35833 |  | 70 | 16 | 14 | Walkley | 4.16kV | UZ11 | Transformer #X27886 located at 3058 Cowan Cres opened up due to defective fuse barrel on transformer switch | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
12618 | 2008 | 6 | 12 | 0.55903 |  | 60 | 13 | 13 | Walkley | 4.16kV | UZ11 | Transformer #X27815 located at 770 Fielding isolated due to service upgrade | Ottawa | Scheduled Outage | Preventive Maintenance
16260 | 2010 | 6 | 14 | 0.37014 |  | 44 | 4 | 6 | WALKLEY |  | UZ11 | Transformer X29093 at 912 Stanstead isolated for service upgrade | Ottawa | Scheduled Outage | Construction
10699 | 2007 | 6 | 21 | 0.5625 |  | 75 | 14 | 11 | Walkley | 4.16kV | UZ11 | At 13:30 trans at 3737 Revelstoke was isolated fro PCB trans replacement | Ottawa | Scheduled Outage | Preventive Maintenance
16303 | 2010 | 6 | 21 | 0.0041667 |  | 74 | 17 | 14 | WALKLEY | 4.16kV | UZ11 | Squirrel contacted a transformer X27886 causing fuse to blow. | Ottawa | Foreign Interference | Animal
20827 | 2012 | 6 | 21 | 0.96875 |  | 115 | 12 | 6 | Walkley | 4.16kV | UZ11 | Transformer X24905 at rear of 912 Rand opened due to tree contact. | Ottawa | Tree Contacts | Inadequate Trimming
18760 | 2011 | 7 | 17 | 0.81319 |  | 25 | 198 | 474 | Walkley Sub | 4.16kV | UZ11 | UZ11 Tripped during severe storm, closed back in 25 minutes later | Ottawa | Adverse Weather | Wind
16593 | 2010 | 7 | 30 | 0.45486 |  | 65 | 11 | 10 | Walkley | 4.16kV | UZ11 | Isolated transformer X24904 at 877 Garwood Ave to replace blown arrester | Ottawa | Scheduled Outage | Preventive Maintenance
7407 | 2005 | 9 | 29 | 0.83333 |  | 21 | 63 | 180 | UZ | 4.16kV | UZ11 | UZ11 opened to remove tree limb from primary line. | Ottawa | Tree Contacts | Tree Limb Fallen
19322 | 2011 | 10 | 5 | 0.375 |  | 40 | 5 | 8 | Walkley | 4.16kV | UZ11 | Transformer #X29084 located at 1038 Walkley Rd opened by crew for a change over | Ottawa | Scheduled Outage | Construction
9812 | 2006 | 12 | 8 | 0.5 |  | 85 | 10 | 7 | Walkley | 4.16kV | UZ11 | Transformer #OTT3976 located at 2981 LintonRd isolated to change transformer as per PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
9864 | 2006 | 12 | 19 | 0.375 |  | 160 | 13 | 5 | Walkley | 4.16kV | UZ11 | Transformer located @ 923 Garwood isolated to change transformer due to PCB content | Ottawa | Scheduled Outage | Preventive Maintenance
9866 | 2006 | 12 | 19 | 0.37292 |  | 168 | 14 | 5 | Walkley | 4.16kV | UZ11 | Mike Gruich isolated the Transformer at 3002 Southmore to change the transformer | Ottawa | Scheduled Outage | Preventive Maintenance
9988 | 2007 | 2 | 5 | 0.26389 |  | 51 | 13 | 15 | Walkley | 4.16kV | UZ12 | opened switch at pole #2724 to isolate single phase run off to repair neutral. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
18061 | 2011 | 4 | 30 | 0.34792 |  | 179 | 33 | 11 | Walkley | 4.16kV | UZ12 | At 08:21 switch S19036 was isolated to allow crew to repair blue phase radial on Leopolds Drive. 11 customers were affected for 179 minutes. Walkley (UZ12) ID# 18061 | Ottawa | Adverse Weather | Wind
14435 | 2009 | 5 | 31 | 0.86458 |  | 373 | 56 | 9 | WALKLEY | 4.16kV | UZ12 | Transformer Fuse blew at 128 Dorothea due to tree contact with secondary bus. On call crew required to detangle secondary and remove trees. | Ottawa | Tree Contacts | Inadequate Trimming
10630 | 2007 | 6 | 14 | 0.41667 |  | 150 | 8 | 3 | Walkley | 4.16kV | UZ12 | Transformer #OTT4830 located at 3041 Otterson isolated due to PCB change | Ottawa | Scheduled Outage | Preventive Maintenance
10670 | 2007 | 6 | 19 | 0.54167 |  | 154 | 15 | 6 | Walkley | 4.16kV | UZ12 | Transformer #OtT3917 at 136 Leopolds Dr isolated to allow for transformer change (PCB) | Ottawa | Scheduled Outage | Preventive Maintenance
20884 | 2012 | 6 | 26 | 0.42778 |  | 474 | 71 | 9 | Walkley | 4.16kV | UZ12 | Tree branch contacted the primary and neutral and burnt the neutral to the ground feeding transformer X39148 at 151 Kamloops Ave | Ottawa | Tree Contacts | Inadequate Trimming
20904 | 2012 | 6 | 30 | 0.45139 |  | 130 | 61 | 28 | Walkley | 4.16kV | UZ12 | at 10:50 S18306 located at Riverside & Marilyn was openned to isolate UZ12 red pahse radial circuit to allow tree trimmers to perform emergency clearing. Mike Gruiich established PC10a #8230. | Ottawa | Tree Contacts
12779 | 2008 | 7 | 2 | 0.79167 |  | 200 | 10 | 3 | Walkley | 4.16kV | UZ12 | Transformer at 2978 Otterson, was isolated to replace defective cutout and lead. 3 customers affected. | Ottawa | Defective Equipment
3687 | 2003 | 7 | 5 | 0.74653 |  | 245 | 82 | 20 | Walkley | 4.16kV | UZ12 | At 16:44 a report of a tree on hydro wires at 145 Dorthea was received from the Ottawa F.D. The tree caused sparking which eventually started the tree on fire. The hydro wires was also supporting the flaming tree preventing it from crashing into a residential house. The single phase run off to the affected area was removed form service to safely extinguish the fire & remove the tree from the hydro line. | Ottawa | Tree Contacts | Tree Fallen
18795 | 2011 | 7 | 22 | 0.42083 |  | 100 | 28 | 17 | Walkley | 4.16kV | UZ12 | single red phase UZ12 4kv runoff on Marilyn was isolated to allow crew to remove broken trees off secondary services. | Ottawa | Tree Contacts | Tree Limb Fallen
16671 | 2010 | 8 | 5 | 0.79931 |  | 885 | 941 | 277 | Walkley |  | UZ12 | Phase came down @ 3358 Riverside dr., Crew isolated circuit to make repairs. | Ottawa | Defective Equipment | Imminent Equipment Failure Detected
16709 | 2010 | 8 | 10 | 0.47222 |  | 124 | 39 | 19 | Walkley | 4.16kV | UZ12 | A tree limb fell onto a section of the UZ12 circuit on Dorothea Dr. Crews isolated the section and made all necessary repairs. | Ottawa | Tree Contacts | Tree Limb Fallen
16829 | 2010 | 8 | 28 | 0.71667 |  | 271 | 195 | 48 | Walkley | 4.16kV | UZ12 | Tree contact caused open wire bus to burn down at the rear of 195 Kamloops, and primary neutral for approx 3 spans. Switch # S14132 was opened for isolation of primary in the rear of 195 Kamloops & Revelstoke Dr. | Ottawa | Tree Contacts | Inadequate Trimming
16841 | 2010 | 8 | 31 | 0.3625 |  | 269 | 85 | 19 | Walkley | 4.16kV | UZ12 | S14132 to end of line open to allow crews to perform tree trimming. | Ottawa | Scheduled Outage | Preventive Maintenance
16849 | 2010 | 9 | 2 | 0.35764 |  | 326 | 103 | 19 | Walkley | 4.16kV | UZ12 | S14132 at 3703 Revelstoke was isolated to allow crew to do tree trimming. | Ottawa | Scheduled Outage
15231 | 2009 | 10 | 8 | 0.41667 |  | 180 | 57 | 19 | Walkley | 4.16kV | UZ12 | At 10:00 swich TEMP142 at 3565 Revelstoke was isolated to allow crew to replace a pole. 19 customer were affected for 180 minutes. Walkley (UZ12) ID# 15231. | Ottawa | Scheduled Outage
19519 | 2011 | 11 | 2 | 0.63889 |  | 120 | 38 | 19 | Walkley DS | 4.16kV | UZ12 | O/H crews had to cut in new S25404 in order to isolate a section of line that had a tree limb fall on it. The switch was cut in to minimize the amount of customers affected by opening the feeder switch. | Ottawa | Tree Contacts | Tree Limb Fallen
11788 | 2007 | 11 | 29 | 0.39236 |  | 51 | 212 | 250 | Walkley | 4.16kV | UZ12 | Dave reports MVA (hit and run) at the corner of Riverside Dr & Walkley Rd. Down Guy found broken causing auto reclose on UZ02 & UZ12 to lock out. Also UZ12 breaker failed to close, cause unknown at this time. | Ottawa | Foreign Interference | Vehicle
11866 | 2007 | 12 | 21 | 0.96528 |  | 125 | 6 | 3 | Walkley | 13.2kV | UZ12 | Transformer OTT4828 at 2981 Otterson was isolated to allow crew to replace triplex and broken switch on the transformer. | Ottawa | Defective Equipment | Equipment Deterioration Due to Age
9955 | 2007 | 1 | 20 | 0.64931 |  | 85 | 13 | 9 | Walkley | 4.16kV | UZ15 | 24/7 advise Secondary bus wires tangled causing transformer OTT5301 fuse to blow. Repairs made and transformer refused and closed. | Ottawa | Adverse Weather | Wind
17659 | 2011 | 3 | 1 | 0.35833 |  | 1 | 34 | 2055 | Walkley | 4.16kV | UZT1 & UZT2 | At 8:36 while switching we loss load on UZT1 and UZT2 at Walkley due to a change of system conditions. 2055 customer were affected for 1min. Walkley UZT1 and UZT2, ID# 17659 | Ottawa | Human Element | Switching Errors
6193 | 2005 | 2 | 8 | 0.57986 |  | 308 | 5133 | 1000 | Casselman | 44kV | V11 | Hydro One reports 62M2 out due to a phase down in a farmers field. | Castleman | Loss of Supply | HEPC Circuit Fault
17564 | 2011 | 2 | 8 | 0.85069 |  | 227 | 5297 | 1400 | Casselman |  | V11 | At 20:25 Casselman MS loss it's supply from Hydro 62M2 circuit out of Hydro One's St Isiodore station due to a faulted circuit. 1400 customers were affected for 227 mins. St Isiodore 62M2 ID# 17564 | Castleman | Loss of Supply | HEPC Circuit Fault
5686 | 2004 | 8 | 16 | 0.92986 |  | 10 | 200 | 1200 | Casselman | 8/4.8kV | V11 | Blown 44KV arrester on the 44kV circuit in Casselman V11 sub-station. Crews unloaded V11 transformer to cut broken arrester clear. Which caused an outage to the town of Casselman approx 1200 Customers where affected in power outage. | Casselman | Defective Equipment | Equipment Deterioration Due to Age
6499 | 2005 | 5 | 4 | 0.37986 |  | 194 | 48 | 15 | Casselman | 8/4.8kV | V11 F1 | Isolated a section of O/H on Laval St to re-string new 44Kv. | Castleman | Scheduled Outage | Construction
10082 | 2007 | 3 | 1 | 0.875 |  | 171 | 6 | 2 | Casselman | 13.2kV | V11F1 | The overhead transformer at 625 Albert in Casselman was replaced due to PCB level. The Petro Canada & Burger King in Cassleman. | Ottawa | Scheduled Outage | Preventive Maintenance
10093 | 2007 | 3 | 6 | 0.088194 |  | 113 | 8 | 4 | Casselman | 8/4.8kV | V11F1 | Gord/Sproule reports that he found a transformer fuse open on Montcalm. Tx was refused to restore power. | Castleman | Defective Equipment | Equipment Failure - Cause Unknown
16001 | 2010 | 4 | 26 | 0.58333 |  | 130 | 17 | 8 | CASSELMAN | 8/4.8kV | V11F1 | At 14:00 trans at 39 FAUCHER BLVD CASSELMAN was isolated in order to replace leaking trans | Castleman | Defective Equipment | Equipment Deterioration Due to Age
6495 | 2005 | 5 | 3 | 0.37986 |  | 198 | 50 | 15 | Casselman | 8/4.8kV | V11F1 | Isolated a section of O/H on Laval St to re-string new 44Kv. | Castleman | Scheduled Outage | Construction
6516 | 2005 | 5 | 5 | 0.38472 |  | 181 | 48 | 16 | Casselman | 8/4.8kV | V11F1 | Planned interuption of txs 68 & 69 affecting 16 customers on Dollard & Laval Sts. H1 line rebuild of 44 Kv feeder. | Castleman | Scheduled Outage | Construction
10406 | 2007 | 5 | 11 | 0.42847 |  | 103 | 14 | 8 | Casselman | 8/4.8kV | V11F1 | TP2845 on rue des chenes in casselman was isolated to replace leaking transformer. | Castleman | Scheduled Outage | Repair
6664 | 2005 | 6 | 6 | 0.52083 |  | 75 | 11 | 9 | Casselman | 8/4.8kV | V11F1 | Transformer at 106 & 107 Isabelle in Casselman isolated to cut in new secondary services | Castleman | Scheduled Outage | Construction
8512 | 2006 | 6 | 19 | 0.34236 |  | 127 | 792 | 500 | Castleman | 8/4.8kV | V11F1 | V11F1 @ Castleman tripped. Donny of Spouril patrolled line and found a bad dead end insulator off of Racine St. in the Industreal park and also bad arrestor on St. Isidore. The load was picked up without changing either the insulators or arrestors. The V11F1 recloser is suspect as the cause of the outage as it would not properly pick all the load up. 1/5 of the load was transferred to V11F2 through S138. | Castleman | Defective Equipment | Equipment Failure - Cause Unknown
6774 | 2005 | 6 | 21 | 0.45278 |  | 82 | 23 | 17 | casselamn | 8/4.8kV | V11F1 | Isolation of O/H section on St Isadore St for circuit reconfiguration. | Castleman | Scheduled Outage | Construction
6831 | 2005 | 6 | 29 | 0.39653 |  | 130 | 43 | 20 | V11 | 8/4.8kV | V11F1 | Section of o/h line on St Isadore st isolated for transfer to new pole line by Hydro - One crew. | Castleman | Scheduled Outage | Construction
4361 | 2003 | 10 | 30 | 0.30833 |  | 186 | 31 | 10 | Casselman | 27.6/16kV | V11F1 | Primary lead to transformer 001 switch burnt off, switch replaced. | Castleman | Defective Equipment | Equipment Failure - Cause Unknown
9644 | 2006 | 11 | 13 | 0.37708 |  | 92 | 3 | 2 | Casselman | 8/4.8kV | V11F1 | Gord McNaughton from Sproule had a Transformer X21058 at 24 Industrial in Casselman open to replace transformer | Castleman | Scheduled Outage | Preventive Maintenance
9654 | 2006 | 11 | 13 | 0.54097 |  | 105 | 14 | 8 | Casselman | 4.16kV | V11F1 | Isolated Transformer at 20 Isabelle in Casselman to change Transformer | Castleman | Scheduled Outage | Preventive Maintenance
10266 | 2007 | 4 | 16 | 0.58333 |  | 102 | 598 | 352 | Casselman | 8/4.8kV | V11-F1 | V11-F1 feeder auto/tripped, same patrolled and no apparent cause found. Due to cold load pick up the feeder had to be sectionalized. | Castleman | Adverse Weather | Snow
5023 | 2004 | 4 | 19 | 0.81528 |  | 154 | 85 | 33 | Casselman | 8/4.8kV | V11-F1 | Switch S123 B phase found opened due to defective N/O switch S133 which had broken off the pole. Switch S133 repiared and customers restored. Note: required outage to addition O/H section to make repairs. | Castleman | Defective Equipment | Equipment Failure - Cause Unknown
5025 | 2004 | 4 | 19 | 0.88889 |  | 34 | 19 | 34 | Casselman | 8/4.8kV | V11-F1 | Switch S136 on St Isidore in Casselman opened to isolate S133 which had to be repaired. | Castleman | Defective Equipment
6460 | 2005 | 4 | 25 | 0.65625 |  | 91 | 392 | 352 | Casselman | 12/7.2kV | V11-F1 | Hydro One dug a new hole for a new pole. With all the rain the old existing pole started to lean over causing the phases to slap together. | Casselman | Foreign Interference | Foreign Object
6568 | 2005 | 5 | 18 | 0.37639 |  | 158 | 40 | 15 |  | 8/4.8kV | V11-F1 | Planned outage on Laval Street 44kv stringing. | Castleman | Scheduled Outage
6867 | 2005 | 7 | 4 | 0.58333 |  | 15 | 0 | 1 | Castleman | 13.2kV | V11-F1 | Highhoe dig in on customer premises. Customer is a highschool, and is not open in the summer. Customer requested permit to repair cable and do a bunch of work inside. Outage changed from a HOL outage to a customer requested isolation for maint. Re-energized July 27 at 09:10. | Castleman | Foreign Interference | Dig-in
5893 | 2004 | 11 | 16 | 0.79861 |  | 60 | 1 | 1 | Casselman | 8/4.8kV | V11-F1 | Defective lead to transformer 154 on Principal St in Casselman repaired. | Castleman | Defective Equipment | Equipment Failure - Cause Unknown
13741 | 2008 | 12 | 12 | 0.35903 |  | 20 | 3 | 10 | V11-F1 | 8/4.8kV | V11-F1 | TP6600 at Gange Cres, was interupted so that Sproule could move the Normally Open point from TP6600-H1A to TP6600-H1B | Castleman | Scheduled Outage
4621 | 2003 | 12 | 18 | 0.26042 |  | 207 | 1905 | 600 | Cassleman | 8/4.8kV | V11-F1 | No cause found, Very heavey snow,with wind. | Castleman | Adverse Weather | Snow
4622 | 2003 | 12 | 18 | 0.44097 |  | 57 | 570 | 600 | Casselman | 8/4.8kV | V11-F1 | With the high winds the O/H phases where slapping together. Eric tighten up the phases so it should not slap again. | Castleman | Adverse Weather | Wind
15832 | 2010 | 3 | 23 | 0.45556 |  | 235 | 1819 | 1076 | Casselman | 8/4.8kV | V11-F1 & F2 | A pole fire at Racine & Industial caused both circuits to open. V11-F2 circuit was transferred to V11-F3 cirucit. 1 customer on the F2 circuit and F1 remains off until temp repairs are made to hydro pole. Steve Rutherford reports S153 failed, and needs to be replaced. Steve reports S156 is now isolated from all Hydro Ottawa sources. | Castleman | Adverse Environment | Fire
12007 | 2008 | 2 | 4 | 0.54167 |  | 18 | 2 | 5 | Casselman | 4.16kV | V11F2 | Transformer #X21310 located at 666 St. Joseph St isolated due to maintenance-hot spot on one of the connections | Castleman | Scheduled Outage | Preventive Maintenance
15846 | 2010 | 3 | 25 | 0.65625 |  | 14 | 2 | 10 | Castleman | 8/4.8kV | V11F2 | Replaced defective switch for transformer X21305 at 687 Ste Marie St Casselman | Castleman | Defective Equipment | Equipment Failure - Cause Unknown
14141 | 2009 | 4 | 3 | 0.37083 |  | 111 | 7 | 4 | Casselman | 4.16kV | V11F2 | Transformer #X22513 located at 16 Riviere Nation Rd in Casselman isolated, fuse blew, no apparent cause | Castleman | Defective Equipment | Equipment Deterioration Due to Age
15911 | 2010 | 4 | 8 | 0.83958 |  | 158 | 16 | 6 | CASSELMAN MS | 8/4.8kV | V11F2 | Refused transformer at 3 Martin Street due to lightning strike | Casselman | Adverse Weather | Lightning
12469 | 2008 | 5 | 23 | 0.35417 |  | 240 | 28 | 7 | Castleman | 8/4.8kV | V11F2 | Isolated transformer X24222 at 700 ST. ISIDORE RD to replace the pole | Castleman | Scheduled Outage | Construction
16159 | 2010 | 5 | 28 | 0.4875 |  | 220 | 477 | 130 | Casselman DS | 8/4.8kV | V11F2 | Section of V11F2 circuit on Montcalm was isolated to install new hydro plant on overhead. | Castleman | Scheduled Outage | Construction
14517 | 2009 | 6 | 11 | 0.36319 |  | 337 | 112 | 20 | Casselman | 8/4.8kV | V11F2 | Transformers TP2846, TP3477, TP3478 & TP3479 on Des Chenes & Des Cedres ST in Casselman isolated for cable replacement. | Castleman | Scheduled Outage | Construction
16370 | 2010 | 6 | 30 | 0.40556 |  | 113 | 286 | 152 | Casselman | 4.16kV | V11F2 | V11F2 cable section from S19457 @ 723 Des Erables to S29115 @ St Isodre & Des Erables was isolated to allow crew to correct Red and Blue phase at both riser poles. 152 customers were affected between St Isdore ST and Rue Des Pommiers in Casselman | Castleman | Scheduled Outage | Repair
3769 | 2003 | 7 | 21 | 0.38542 |  | 435 | 87 | 12 | Casselman | 27.6/16kV | V11F2 | At 9:15am on Monday, approximately 12 customers in the St. Joseph Street area of Casselman were interrupted due to a defective transformer. Transformer was replaced and all customers were restored at 4:30pm. | Castleman | Defective Equipment | Equipment Failure - Cause Unknown
14868 | 2009 | 7 | 29 | 0.36458 |  | 219 | 376 | 103 | Casselman | 8/4.8kV | V11F2 | Steve Rutherford isolated from S135 to end of line to string additional conductors | Castleman | Scheduled Outage
13137 | 2008 | 8 | 22 | 0.3125 |  | 30 | 10 | 19 | Casselman | 4.16kV | V11F2 | Transformer #X21093 located at 657 Principale St Casselman isolated to hook up a service | Castleman | Scheduled Outage | Preventive Maintenance
7287 | 2005 | 9 | 7 | 0.35764 |  | 284 | 473 | 100 | Casselman | 8/4.8kV | V11F2 | Planed outage to Casselman for Hydro One to restring 44 Kv conductor. | Castleman | Loss of Supply | Construction
15271 | 2009 | 10 | 17 | 0.29861 |  | 336 | 2184 | 390 | Casselman | 8/4.8kV | V11F2 | V11F2 from S137,S138 S122 to end of line was isolated for H1 to give them working clearance to string new conductor along Laval St, St. Isidore street. | Castleman | Scheduled Outage | Construction
13384 | 2008 | 10 | 18 | 0.34167 |  | 325 | 726 | 134 | Castleman | 8/4.8kV | V11F2 | Outage to 134 customers due to planned work by Hydro One and Hydro Ottawa (Sproule) to raise and string new conductores. | Castleman | Scheduled Outage | Construction
19574 | 2011 | 11 | 14 | 0.83681 |  | 9 | 2 | 13 | Casselman | 8/4.8kV | V11F2 | Transformer #X21297 located at 677 Ste. Anne St Casselman opened by crew to replace burning hot line clamp | Castleman | Defective Equipment | Imminent Equipment Failure Detected
15863 | 2010 | 3 | 28 | 0.89792 |  | 82 | 18 | 13 | Casselman | 8/4.8kV | V11-F2 | Blown transformer fuse at 735 Laval St caused outage to 13 customers, Transformer location X24247. | Castleman | Defective Equipment | Equipment Deterioration Due to Age
15864 | 2010 | 3 | 28 | 0.99653 |  | 192 | 42 | 13 | Casselman | 8/4.8kV | V11-F2 | Transfomer #X24247 @ 735 Laval St was defective, and was replaced. | Castleman | Defective Equipment | Equipment Deterioration Due to Age
7122 | 2005 | 8 | 10 | 0.77083 |  | 78 | 585 | 450 | Casselman | 8/4.8kV | V11-F2 | V11-F2 recloser opened due to tree on circuit, tree removed and load restored from the F3 feeder because F2 recoser would not operate, suspected internal fault. | Castleman | Foreign Interference | Foreign Object
12009 | 2008 | 2 | 4 | 0.96944 |  | 89 | 30 | 20 | Casselman | 8/4.8kV | V11F3 | Transformer X22537 at 751 Principale was isolated to replace hot line clamp & perform secondary mtce. | Casselman | Scheduled Outage | Preventive Maintenance
20008 | 2012 | 2 | 14 | 0.29167 |  | 165 | 60 | 22 | Casselman | 8/4.8kV | V11F3 | Transformer X22534 at 767 Principale St. isolated by Sproule Powerlines to transfer plant to new pole | Castleman | Scheduled Outage | Preventive Maintenance
10873 | 2007 | 7 | 15 | 0.23611 |  | 194 | 97 | 30 | Castleman | 8/4.8kV | V11F3 | isolated Castleman F3 overhead circuit between S27518 and S143 to re-sag the conductor | Castleman | Scheduled Outage | Preventive Maintenance
8800 | 2006 | 7 | 22 | 0.22222 |  | 147 | 86 | 35 | Casselman | 8/4.8kV | V11F3 | O/H section of line isolated to allow crew to reconfigure O/H on Brisson Rd. in Casselman. Between S111, S104 and S103. | Castleman | Scheduled Outage | Preventive Maintenance
16572 | 2010 | 7 | 28 | 0.36111 |  | 65 | 38 | 35 | Castleman | 8/4.8kV | V11F3 | PC10A# 020853, Steve (Sproule) placed PC10 into effect on S11548 to isolate TP6394 at 779 Brebeuf to allow contractor to pull in secondary cables. | Castleman | Scheduled Outage | Construction
16576 | 2010 | 7 | 28 | 0.54583 |  | 27 | 167 | 371 |  | 8/4.8kV | V11F3 | switch flashed during operation of S112 on Montcalm and Brebeuf in Castleman, no injuries reports, crew cleared the area and closed the recloser at the station restoring all the load. | Castleman | Human Element | Switching Errors
19026 | 2011 | 8 | 27 | 0.29167 |  | 245 | 20 | 5 | Casselman | 8/4.8kV | V11F3 | Transformer #X22561 locate at 787 Montcalm opened by crew for a pole replacement | Castleman | Scheduled Outage | Construction
5820 | 2004 | 9 | 25 | 0.66319 |  | 65 | 11 | 10 | V11 | 8/4.8kV | V11F3 | Middle phase fuse found blown, Fuse holder all corroded | Castleman | Defective Equipment | Equipment Failure Due to Incorrect Maintenance
19713 | 2011 | 12 | 11 | 0.80694 |  | 73 | 7 | 6 | Casselman MS | 8/4.8kV | V11F3 | Transformer X22612 at 742 Brebeuf St. Opened up. Sproule was dispatched and found a blown fuse at the transformer, but could not find the cause. They re-fused the trasformer and the fuse held. | Castleman | Unknown/Other
6194 | 2005 | 2 | 9 | 0.0069444 |  | 30 | 2 | 5 | Casselman | 12/7.2kV | V11-F3 | TE#38 isolated to allow crew to new connections at transformer. | Ottawa | Defective Equipment | Equipment Failure - Cause Unknown
10398 | 2007 | 5 | 10 | 0.39097 |  | 112 | 4 | 2 | Casselman | 8/4.8kV | V11-F3 | Fues to transformer X22591 at 810 Principale St was found blown cause unknown refused switch power restored | Castleman | Defective Equipment | Equipment Failure - Cause Unknown
6776 | 2005 | 6 | 22 | 0.125 |  | 330 | 22 | 4 | Casselman |  | V11-F3 | A vehicle accident cause a broken pole at 601 St Isidor. The transformer leaked all it's oil. Police report # SP05101456. Transfomer & pole replaced by Sproule. Drain all cleaning up oil spill. | Casselman | Foreign Interference | Vehicle
16206 | 2010 | 6 | 6 | 0.29792 |  | 148 | 3774 | 1530 | Casselman | 8/4.8kV | V11T1 | Hydro One Loss of Supply to the St Isadore 62M2 circuit feeding Casselman MS. Hydro One crews isolated faulted section and restored power to Casselman sub. | Castleman | Loss of Supply | HEPC Circuit Fault
14669 | 2009 | 7 | 5 | 0.16667 |  | 80 | 2027 | 1520 | Casselman | 8/4.8kV | V11-T1 | Hydro One isolated a section of the 62M2 out of St. Isidore to replace lightning arrestors and insulators in the Rose Corner's area, inturupting power to Hydro Ottawa's Casselman MS station for the duration of the outage. | Castleman | Loss of Supply | Preventive Maintenance
9651 | 2006 | 11 | 13 | 0.52361 |  | 95 | 5 | 3 | Vaughn | 4.16kV | Vaughn | OpenedTtransformer at 503 Minto to change Transformer | Ottawa | Scheduled Outage | Preventive Maintenance
6542 | 2005 | 5 | 11 | 0.4125 |  | 156 | 78 | 30 | Casselman | 12/7.2kV | VF2 | Glen Bowman reports overhead conductor have been replaced. 30 customers affected on Laval st. | Castleman | Scheduled Outage | Construction
6322 | 2005 | 3 | 24 | 0.51667 |  | 120 | 6 | 3 | Woodroffe | 8/4.8kV | VW06 | Isolated Transformer # 2222 at 1262 Erindale to relocate transformer to new pole | Ottawa | Scheduled Outage | Preventive Maintenance
3342 | 2003 | 4 | 15 | 0.42917 |  | 205 | 15596 | 12134 | Bridlewood | 27.6/16kV | W6MC | W6MC, 115KV supply tripped causing multiple outages in Nepean, Kanata, Manotick, and Richmond. The cause was determined to be a defective HV fuse on Bridlewood T2 transformer. W6MC circuit was initially partially restored to Manotick & Richmond. Reliablity Crews performed switching to restore remaining customer load from alternate supply feeders. Note: All customer outage numbers after 11:32 may be considered caused by "Loss of Supply" because the IMO would not authorize W6MC to be energized until the line was patrolled. | Kanata | Defective Equipment | Equipment Failure - Cause Unknown
3633 | 2003 | 6 | 29 | 0.38889 |  | 300 | 11263 | 12000 | Bridlewood | 27.6/16kV | W6MC | Circuit W6MC loss of supply.09:46 606F2 load picked up from Longfields F2 100amps 10:17 circuit W6MC picked up from Hydro One 14:00 Recloser 911 closed on Kerwin Rd and Dunrobin Rd 14:20 Recloser 696 closed on 5TH LINE Kanata | Kanata | Loss of Supply | HEPC Circuit Fault
3646 | 2003 | 6 | 29 | 0.38333 |  | 59 | 9625 | 10000 | Hydro One | 115kV | W6MC | Hydro One circuit W6MC auto tripped interupting Marchwood, Bridlewood, Fallowfield, Richmond DS and Manotick DS. Fallowfield 606F2 feeder load restored at 09:46 using Longfield F2 feeder. W6MC and all other load restored at 10:15. The cause of the trip was a broken insulator on the 115 Kv circuit. | Kanata | Loss of Supply | HEPC Circuit Fault
4386 | 2003 | 11 | 4 | 0.73194 |  | 7 | 2281 | 19550 |  | 115kV | W6MC | Hydro One reports W6MC auto reclosed loss of Supply to Marchwood, Bridlewood, Manotick, Bridlewood, and Fallowfield. Outage to 19550 customers. ID#4386 | Kanata | Loss of Supply | HEPC Circuit Fault
4387 | 2003 | 11 | 4 | 0.74653 |  | 63 | 4746 | 19550 |  | 115kV | W6MC | Hydro One reports W6MC circuit re-opened all customers picked up. Hydro One reports unable to close 606F2 circuit. Reports of Flash in the area of Fallowfield DS. P. Paquett dispatched to patrol. Circuit. Hydro One reports control fuses blown. Fuses reported breaker now closed. ID#4386 | Kanata | Loss of Supply | HEPC Circuit Fault
4446 | 2003 | 11 | 13 | 0.81667 |  | 4 | 1303 | 15200 |  | 115kV | W6MC | Hydro One's W6MC circuit went out due to unknown causes. The circuit was re-energized within minutes by Hydro One and all customers came back on. Further investigation found that the BRD F4 breaker operated and went to lockout, the circuit switcher BRD-T1-B1, on the low side of the transformer BRD T1, also went to lockout aIong with the circuit switcher 605-W6MC on the high side of the transformer. Se ID#4451 | Kanata | Adverse Weather | Wind
11818 | 2007 | 12 | 7 | 0.36736 |  | 6 | 607 | 6074 | Lincoln | 13.2kV | W6MC | Hydro One 71T1 transformer auto trip while the companion transformer 71T2 was O/S. | Ottawa | Loss of Supply | HEPC Station Fault
10880 | 2007 | 7 | 16 | 0.38889 |  | 110 | 13 | 7 | Wonderland | 4.16kV | Wonderland F1 | At 09:20 trans at 257 St Patrick was isolated for PCB trans replacement | Goulburn | Scheduled Outage | Preventive Maintenance
5668 | 2004 | 8 | 11 | 0.39167 |  | 411 | 7 | 1 | Wonderland | 27.6/16kV | Wonderland F1 | Transformer at 1251 Ashton Station Rd fuse opened during lightening storm. | Goulburn | Adverse Weather | Lightning
8739 | 2006 | 7 | 16 | 0.33333 |  | 180 | 105 | 35 | Wonderland | 8/4.8kV | Wonderland F2 | Hydro One had a plan outage to work on new construction on HWY 7 & Ashton Rd. | Goulburn | Loss of Supply | Construction
10890 | 2007 | 7 | 16 | 0.81597 |  | 115 | 48 | 25 | Wonderland | 8/4.8kV | Wonderland F2 | Hydro One had a planned Outage on Wonderland F2 circuit, but failed to notify our customers in the area of Mcarton Rd. | Goulburn | Scheduled Outage | Construction
15211 | 2009 | 10 | 4 | 0.3125 |  | 185 | 92 | 30 | Wonderland | 8/4.8kV | Wonderland F2 | Hydro One had a planned outage to Wonderland F2 circuit. Which effected power to approx 30 customer on Overpass RD, Abb Rd & Hwy 7 area. | Kanata | Loss of Supply | Construction
7590 | 2005 | 11 | 10 | 0.41111 |  | 248 | 124 | 30 | Wonderland | 12/7.2kV | Wonderland F2 | A. Cooney reports conductor on center phase of Hydro One line down. Also when restoring load to normal Hydro One reports reclosure failed to closed at the station. Circuit put on bypass at Wonderland by H-1. | Kanata | Loss of Supply | HEPC Circuit Fault
14951 | 2009 | 8 | 16 | 0.375 |  | 270 | 36 | 8 | Wonderland | 27.6/16kV | WONDERLANDF2 | Wonderland F2 isolated from S18362 to E.O.L. to allow reconstruction of overhead at Hwy 7 and Ashton Station Rd | Goulburn | Scheduled Outage | Construction
12719 | 2008 | 6 | 25 | 0.23194 |  | 66 | 1 | 1 | Wonderland | 27.6/16kV | WONDF2 | Refused blown switch to transformer X10867 at 2044 Dwyer Hill Rd (Squirrel contact) | Goulburn | Foreign Interference | Animal
14863 | 2009 | 7 | 28 | 0.45972 |  | 48 | 16 | 20 | Wondeland | 8/4.8kV | WONDF2 | Wonderland F2 red & blue reclosers tripped & were both closed in successfully, no cause found. White phase never tripped. Customers affected in Ashton Station Rd area north of Hwy 7. | Goulburn | Unknown/Other