## Assumptions
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR DRC-8 Attachment C ORIGINAL
Underground Residential Transformer Service Wire Sizes Guideline - Assumptions and Calculations
Assumptions and Calculations:
-Each single unit ≤ 2000 sq.ft, natural gas heat, 100A/200A @ 120V/240V service.
-AC load within each unit is undiversified and assumes to draw no more than 10.5A @ 240V and 95% power factor
-Transformers utilize ≥ 95% power factor and low harmonics (see ECG0008).
-Residential units (100A/200A) are made according to a historical peak demand of ~4.5kW based on an average of 12 homes and a diversity according to the OBC
-Peak unit load assumed to be coincident with peak historical load
-Any transformer is subject to all units having stage-II EV chargers installed and in use (100% EV penetration)
-By the time a 100% EV penetration is in place, it is assumed that the demand response options are available that will limit the coincident peak load of EV charging to 50% of their maximum load
-Peak EV and AC consumption assumed to be coincident with peak unit load.
-Impact of DER and HOL DR projects is excluded
-Peak unit load is assumed to be coincident with AC and 50% of EV load, at an extended temperature of 30 degrees Celsius over ~8-hour timeframe
-All stage II EV chargers are assumed to draw no more than 32A (80% rated on 40A breaker) @ 240V and 95% power factor with no diversification
-Transformer lifetime is considered 30 years, where EV penetration will increase signatficantly in future, hence such load increase shall be considered earlier in the design stage.
-Transformer is assumed 90% pre-load at 30 degrees C
-Transformer overloading hours are as per ABB Loading Rules of Thumb as shown in below figure
-Calculations to determine the condcutor size for 100 A unit assumes that it has 80%protection (37A normal load and 43A for AC and EV Load, hence total = 80A)
-Calculations to determine the condcutor size for 200 A unit assumes that it has 80%protection (117A normal load and 43A for AC and EV Load, hence total = 160A)

## Transformer Sizing
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR DRC-8 Attachment C ORIGINAL
Underground Residential Transformer Service Wire Sizes Guideline - Transformer Sizing
Calculations
| EV Penetration | 100% | - Number of customers per Tx based on selected penetration rate
| % stage 1 chargers | 0% | - Number of customers per Tx based on selected stage 1 and stage 2 breakdown
| EV stage 1 load | 1.44 | - kW, assumed 12A @ 120V during peak
| EV stage 2 load | 7.296 | - kW, assumed 32A @240V during peak
| Stage 1 @Peak | 100% | - of charger load is coincident with unit peak
| Stage 2 @ Peak | 50% | - of charger load is coincident with unit peak
| Town house Loading |  |  |  |  | Tx Loading
| Number of Units | Diversity Factor (OESC) | Non-EV Load (kW) | EV Peak Load (kW) | Total Unit Load (kW) | Accum Load (kW) | Accum Load (kVA) PF = 0.95 | Tx Size (kVA) | Tx Load % @ 30 C
| 1 | 100% | 11.25 | 3.648 | 14.898 | 14.898 | 15.6821 | 50 | 31.3642
| 2 | 65% | 8.1525 | 3.648 | 11.8005 | 26.6985 | 28.1037 | 50 | 56.2074
| 3 | 65% | 8.1525 | 3.648 | 11.8005 | 38.499 | 40.5253 | 50 | 81.0505
| 4 | 40% | 5.94 | 3.648 | 9.588 | 48.087 | 50.6179 | 50 | 101.2358
| 5 | 40% | 5.94 | 3.648 | 9.588 | 57.675 | 60.7105 | 50 | 121.4211
| 6 | 25% | 4.6125 | 3.648 | 8.2605 | 65.9355 | 69.4058 | 75 | 92.5411
| 7 | 25% | 4.6125 | 3.648 | 8.2605 | 74.196 | 78.1011 | 75 | 104.1347
| 8 | 25% | 4.6125 | 3.648 | 8.2605 | 82.4565 | 86.7963 | 75 | 115.7284
| 9 | 25% | 4.6125 | 3.648 | 8.2605 | 90.717 | 95.4916 | 100 | 95.4916
| 10 | 25% | 4.6125 | 3.648 | 8.2605 | 98.9775 | 104.1868 | 100 | 104.1868
| 11 | 25% | 4.6125 | 3.648 | 8.2605 | 107.238 | 112.8821 | 100 | 112.8821
| 12 | 25% | 4.6125 | 3.648 | 8.2605 | 115.4985 | 121.5774 | 100 | 121.5774
| 13 | 25% | 4.6125 | 3.648 | 8.2605 | 123.759 | 130.2726 | 167 | 78.0076
| 14 | 25% | 4.6125 | 3.648 | 8.2605 | 132.0195 | 138.9679 | 167 | 83.2143
| 15 | 25% | 4.6125 | 3.648 | 8.2605 | 140.28 | 147.6632 | 167 | 88.4211
| 16 | 25% | 4.6125 | 3.648 | 8.2605 | 148.5405 | 156.3584 | 167 | 93.6278
| 17 | 25% | 4.6125 | 3.648 | 8.2605 | 156.801 | 165.0537 | 167 | 98.8345
| 18 | 25% | 4.6125 | 3.648 | 8.2605 | 165.0615 | 173.7489 | 167 | 104.0413
| 19 | 25% | 4.6125 | 3.648 | 8.2605 | 173.322 | 182.4442 | 167 | 109.248
| 20 | 25% | 4.6125 | 3.648 | 8.2605 | 181.5825 | 191.1395 | 167 | 114.4548
| 21 | 10% | 3.285 | 3.648 | 6.933 | 188.5155 | 198.4374 |  | #DIV/0!
| 22 | 10% | 3.285 | 3.648 | 6.933 | 195.4485 | 205.7353 |  | #DIV/0!
| 23 | 10% | 3.285 | 3.648 | 6.933 | 202.3815 | 213.0332 |  | #DIV/0!
| 24 | 10% | 3.285 | 3.648 | 6.933 | 209.3145 | 220.3311 |  | #DIV/0!
| 25 | 10% | 3.285 | 3.648 | 6.933 | 216.2475 | 227.6289 |  | #DIV/0!
| 26 | 10% | 3.285 | 3.648 | 6.933 | 223.1805 | 234.9268 |  | #DIV/0!
| 27 | 10% | 3.285 | 3.648 | 6.933 | 230.1135 | 242.2247 |  | #DIV/0!
| 28 | 10% | 3.285 | 3.648 | 6.933 | 237.0465 | 249.5226 |  | #DIV/0!
| 29 | 10% | 3.285 | 3.648 | 6.933 | 243.9795 | 256.8205 |  | #DIV/0!
| 30 | 10% | 3.285 | 3.648 | 6.933 | 250.9125 | 264.1184 |  | #DIV/0!

## Peak Load Assumption
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR DRC-8 Attachment C ORIGINAL
Underground Residential Transformer Service Wire Sizes Guideline - Peak Load Assumption
| # | DF (code) | Average Tx load (kW) | Profiled (kW) | AC load (kW) | Total (kW)
| 1 | 100% | 4.5 | 8.85 | 2.4 | 11.25
| 2 | 65% | 4.5 | 5.7525 | 2.4 | 8.1525
| 3 | 65% | 4.5 | 5.7525 | 2.4 | 8.1525
| 4 | 40% | 4.5 | 3.54 | 2.4 | 5.94
| 5 | 40% | 4.5 | 3.54 | 2.4 | 5.94
| 6 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 7 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 8 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 9 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 10 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 11 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 12 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 13 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 14 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 15 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 16 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 17 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 18 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 19 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 20 | 25% | 4.5 | 2.2125 | 2.4 | 4.6125
| 21 | 10% | 4.5 | 0.885 | 2.4 | 3.285
| 22 | 10% | 4.5 | 0.885 | 2.4 | 3.285
| 23 | 10% | 4.5 | 0.885 | 2.4 | 3.285
| 24 | 10% | 4.5 | 0.885 | 2.4 | 3.285
| 25 | 10% | 4.5 | 0.885 | 2.4 | 3.285
| 26 | 10% | 4.5 | 0.885 | 2.4 | 3.285
| 27 | 10% | 4.5 | 0.885 | 2.4 | 3.285
| 28 | 10% | 4.5 | 0.885 | 2.4 | 3.285
| 29 | 10% | 4.5 | 0.885 | 2.4 | 3.285
| 30 | 10% | 4.5 | 0.885 | 2.4 | 3.285
| Sum | 485% | 54

## Service and Conductor Size
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR DRC-8 Attachment C ORIGINAL
Underground Residential Transformer Service Wire Sizes Guideline - Service and Conductor Size
100A Units
Number of Units | Total Load (A) | Diverstified Load (A) Excluding AC and EV | AC + EV (A) | Total Load for Each Unit (A) | Running Total (A) | Conductor Size | Cable Loading (%) | Service Size
| 80 | 37 | 43
Diversity Factor (OESC)
1 | 100% | 37 | 43 | 80 | 80 | 3/0 Al | 45.71%
2 | 65% | 24.05 | 43 | 67.05 | 147.05 | 3/0 Al | 84.03%
3 | 65% | 24.05 | 43 | 67.05 | 214.1 | 500 Al | 61.17%
4 | 40% | 14.8 | 43 | 57.8 | 271.9 | 500 Al | 77.69%
5 | 40% | 14.8 | 43 | 57.8 | 329.7 | 500 Al | 94.2% | 400A (400x0.8=320A)
6 | 25% | 9.25 | 43 | 52.25 | 381.95 | 750 Cu | 71.39%
7 | 25% | 9.25 | 43 | 52.25 | 434.2 | 750 Cu | 81.16%
8 | 25% | 9.25 | 43 | 52.25 | 486.45 | 750 Cu | 90.93% | 600A (600x0.8=480A)
9 | 25% | 9.25 | 43 | 52.25 | 538.7
10 | 25% | 9.25 | 43 | 52.25 | 590.95
11 | 25% | 9.25 | 43 | 52.25 | 643.2
12 | 25% | 9.25 | 43 | 52.25 | 695.45
200A Units
Number of Units | Total Load (A) | Diverstified Load (A) Excluding AC and EV | AC + EV (A) | Total Load for Each Unit (A) | Running Total (A) | Conductor Size | Cable Loading (%) | Service Size
| 160 | 117 | 43
Diversity Factor (OESC)
1 | 100% | 117 | 43 | 160 | 160 | 3/0 Al | 91.43%
2 | 65% | 76.05 | 43 | 119.05 | 279.05 | 500 Al | 79.73% | 400A (400x0.8=320A)
3 | 65% | 76.05 | 43 | 119.05 | 398.1 | 750 Cu | 74.41%
4 | 40% | 46.8 | 43 | 89.8 | 487.9 | 750 Cu | 91.2% | 600A (600x0.8=480A)
5 | 40% | 46.8 | 43 | 89.8 | 577.7
6 | 25% | 29.25 | 43 | 72.25 | 649.95
7 | 25% | 29.25 | 43 | 72.25 | 722.2
8 | 25% | 29.25 | 43 | 72.25 | 794.45
9 | 25% | 29.25 | 43 | 72.25 | 866.7
10 | 25% | 29.25 | 43 | 72.25 | 938.95
11 | 25% | 29.25 | 43 | 72.25 | 1011.2
12 | 25% | 29.25 | 43 | 72.25 | 1083.45
Ampacity of three service conductors in a raceway or cable with 90 degree temp rise as per OESC (Table 2 for Cu and Table 4 for Al)
3/0 Al | 175
250 Al | 230
500 Al | 350
350 Cu | 350
500 Cu | 430
750 Cu | 535