## Comments
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR SEC-54 Attachment D ORIGINAL
Navigant Second Review
Document | Comment # | Description | Chapter
DSP | ES1 | Should add “deteriorating condition”? | 1
DSP | ES2 | Note that the Material Investments section on System Service do not list NWA in the list of alternatives/options evaluated. | 1
DSP | ES3 | Only pole data? Do we mean “circuit” | 1
DSP | ES4 | Do we need a summary subsection (at the end of this section) indicating how future climate changes have impacted the way Hydro Ottawa plans and designs its distribution system, and whether or not this has impacted proposed investments for 2021 – 2025? | 2
DSP | ES5 | Should this section also refer to the SAMP? | 3
DSP | ES6 | Seven are listed | 3
DSP | ES7 | Touch Logic survey shows percentages that are “neutral or satisfied” | 4
DSP | ES8 | Failed to meet the target? | 4
DSP | ES9 | Also failed to meet? | 4
DSP | ES10 | Planning? | 4
DSP | ES11 | Move paragraph before Table 4.14? | 4
DSP | ES12 | Move paragraph ahead of Table 4.15? | 4
DSP | ES13 | Need intro sentence and reference to Table 4.19 | 4
DSP | ES14 | Move table two paragraphs earlier | 4
DSP | ES15 | Should this section also refer to the SAMP? | 5
DSP | ES16 | Note that the Asset Renewal section of the Material Investments - Attachment E refers to, but typically does not show these indices or individual scores. | 5
DSP | ES17 | Does this criterion apply to all feeders? Do some longer rural or 4kV feeders have limited or no feeder back-up? | 5
DSP | ES18 | Not sure these are automation-related | 5
DSP | ES19 | This is the first time C55 is mentioned. Need to define or reword. | 5
DSP | ES20 | Also, assets that are not directly involved in power delivery functions? | 5
DSP | ES21 | Statement seems to suggest that all new technology investments are IT-related | 5
DSP | ES22 | Above, we refer to Renewable Energy Generation. Are REGs a subset of ERFs? | 5
DSP | ES23 | Cite source or derivation of customer interruption costs? | 5
DSP | ES24 | Might be helpful to list renewal or system service projects that fall into the “red zone” either in this section or later sections of the DSP. | 5
DSP | ES25 | May want to add a brief explanation as to why the condition of majority of transformers are designated as good to very good when Figure 6.4 shows over 50% of the transformers are within 10 years or less of their expected service life. | 6
DSP | ES26 | May want to add a brief explanation as to why the condition of majority of breakers are designated as good to very good when Figure 6.6 shows the large majority of air breakers (as an example) are within 10 years or less of their expected service life. | 6
DSP | ES27 | Break out by EM, electronic and microprocessor? | 6
DSP | ES28 | Unlike transformers and breakers, a figure showing condition is not included for P&C. May want to explain why. | 6
DSP | ES29 | From resistograph measurements? | 6
DSP | ES30 | Not sure I see this from the chart | 6
DSP | ES31 | May want to add comment regarding why 100% of PILC rates Fair, Good or Very Good despite the large percentage at or within 10 years of remaining life. | 6
DSP | ES32 | May want to add comment on why such a large percentage of XLPE rates poorly; e.g. early vintage polymer-based cable experience high failure due to treeing, exposed neutrals, etc. | 6
DSP | ES33 | Isolation from ground? | 6
DSP | ES34 | Resistograph tests? | 6
DSP | ES35 | ? | 6
DSP | ES36 | clarify | 7
DSP | ES37 | type and size? | 7
DSP | ES38 | type? | 7
DSP | ES39 | Type and size? | 7
DSP | ES40 | Would it be helpful to indicate how many are connected behind-the-meter and to the primary distribution system? | 7
DSP | ES41 | Update to December 2019? | 7
DSP | ES42 | Does this include ERFs < 1MW? | 7
DSP | ES43 | Transfer trip economically feasible only for larger ERFs | 7
DSP | ES44 | Var.” not mentioned in prior paragraph | 8
DSP | ES45 | Need * and text below | 8
DSP | ES46 | Need ** and text below | 8
DSP | ES47 | State which program(s) where spending was significant | 8
DSP | ES48 | Confirm | 8
DSP | ES49 | Essentially the same as Tables 8.2 & 8.3 | 8
DSP | ES50 | Are O&M impacts quantified in the DSP? | 8
DSP | ES51 | Alternatives? | 8
DSP | ES52 | Reduction? | 8
DSP | ES53 | Is this coincident with the Kanata North peak demand? | 8
DSP | ES54 | Planning process? | 8
DSP | ES55 | Can we say how much this percentage will increase over the next 5 years if no new capacity is added? | 8
DSP | ES56 | In the first sentence of this section, we say 16% of stations are currently above their planning rating. | 8
DSP | ES57 | Is this part of the IRRP? | 8
DSP | ES58 | Does HOL expect to change design standards or planning criteria (e.g. ratings) over the next 5 years as a result of the CVRA? | 8
DSP | ES59 | See prior comment regarding possible change to design standards and planning criteria. | 8
DSP | ES60 | Figure 8.5 shows 16,500 EV sales in 2018 | 8
DSP | ES61 | Should this include overhead as well? | 8
DSP | ES62 | Again, no overhead supply to commercial developments? | 8
DSP | ES63 | Footnotes are needed for the * and ** superscripts | 8
DSP | ES64 | Footnotes are needed for the * and ** superscripts | 8
DSP | ES65 | Footnotes are needed for the * and ** superscripts | 8
DSP | ES66 | Footnotes are needed for the * and ** superscripts | 8
DSP | ES67 | Does the automated equipment fall under this budget category? | 8
DSP | ES68 | Footnotes are needed for the * and ** superscripts | 8
DSP | ES69 | describe the project? | 8
DSP | ES70 | N/A | 8
DSP | ES71 | Replaced with what system? | 8
DSP | ES72 | Add a column to Table 8.27 that shows 5-year averages? | 8
DSP | ES73 | Is this a defined term? If yes, explain | 8
DSP | ES74 | May want to say “the distribution system” | Glossary
DSP | ES75 | Degradation or potential failures? | Glossary
DSP | ES76 | Aren’t stations included in Hydro Ottawa’s “Distribution Assets”? Do we need to clarify by adding “Overhead and Underground” in front of “Distribution Assets”? | Glossary
DSP | ES77 | Added this to account for padmounted devices | Glossary
DSP | ES78 | Is there a reason these are red? | Glossary
MIP | ES1 | Are any of these transformers also needed for capacity supply; e.g. System Service? If not, may want to state these are in addition to other transformers are added or replaced to meet load growth in the System Service section. | SR.1.1
MIP | ES2 | Is transformer expected life impacted or adjusted based on the health index? Also, does it makes sense to show the health index scores of the proposed replacements versus the remaining population of transformers? | SR.1.1
MIP | ES3 | May want to give an example | SR.1.1
MIP | ES4 | Design instead of construction? | SR.1.1
MIP | ES5 | Do we need to cite a 50-year timeframe? Could remove the segment and still retain the message. | SR.1.1
MIP | ES6 | “reduce” as this is one of the objectives of the program? | SR.1.1
MIP | ES7 | Was life extension considered as an option for power transformers (as well as other major equipment categories)? | SR.1.1
MIP | ES8 | Should we mention the failure rate is higher for “at risk” transformers? See paragraphs below on starting with the oldest transformers first and “increased potential for failure.” May want to say this is the “average” failure rate. Also, may want to state this as a percentage failure rate as well. The chart suggests the 0.40 average failure rate is the target failure rate for the total population of transformers. Is there a basis or rationale to select 0.40 as an acceptable average failure rate; for example, to meet SAIFI and CAIDI targets? | SR.1.1
MIP | ES9 | Use “Hydro Ottawa” throughout the document? | SR.1.1
MIP | ES10 | Not sure about the relevance of this table as it appears no switchgear line-ups are scheduled to be replaced. | SR.1.1
MIP | ES11 | Switchgear? | SR.1.1
MIP | ES12 | Is the rating of the replacement transformer increased, which will enable it to also serve greater amounts of future load? | SR.1.1
MIP | ES13 | Does this mean lower load or non-load losses, less maintenance or something else? | SR.1.1
MIP | ES14 | Clarify redundant (what system is providing back up?) | SR.1.1
MIP | ES15 | Should we add “Greater reliability encourages business expansion and development.”? | SR.1.1
MIP | ES16 | Do we quantity the increase in SAIFI, SAIDI and CAIDI if the devices are not replaced, and how this affects overall reliability metrics? | SR.1.1
MIP | ES17 | Should we state what the failure rate is for high risk transformers compared to the total population of transformers? | SR.1.1
MIP | ES18 | Does this include impact (e.g. increase) on SAIFI, SAIDI and CAIDI? | SR.1.1
MIP | ES19 | This is the first time the scoring methodology is mentioned. Do we need to refer to sections of the DSP or SAMP where scoring methods are addressed? | SR.1.1
MIP | ES20 | The low value for reliability, 5%, is surprising, as the impact of the loss of a transformer on customers often is high. Are additional details needed on how these scores are derived? | SR.1.1
MIP | ES21 | This table provides details on the Bayswater substation. Should there be another table that summarizes the cost of all replacements between 2021 and 2025? Also, transformer capacity/rating is not mentioned. | SR.1.1
MIP | ES22 | Most other references in the report refers “stations” as opposed to “substations” | SR.1.1
MIP | ES23 | Seems high. What station has this many breakers/feeder positions in one line-up? Does the line-up include a transfer bus; i.e. 12-14 breaker positions with tie transfer switches? | SR.1.2
MIP | ES24 | Is this the same designation as “unit property”? | SR.1.2
MIP | ES25 | May want to compare average cost of 2015-19 change-outs to full line-up future replacement for 2021-25. | SR.1.2
MIP | ES26 | Also, does it makes sense to show the health index scores of the proposed replacements versus the remaining population of switchgear line-ups or breakers? | SR.1.2
MIP | ES27 | Do we mean “switchgear line-ups”? | SR.1.2
MIP | ES28 | Should we describe the interrupting medium for switchgear line-ups versus stand-alone breakers to avoid confusion? | SR.1.2
MIP | ES29 | May want to show the predicted failure rate of the 4 high-risk line-ups compared to the total population of similar devices. | SR.1.2
MIP | ES30 | Given that only 4 line-up replacements are proposed, the chart suggests that a large number of breakers will still be at or beyond their expected lives. HOL may need to explain why it is acceptable to have a large percentage of air breakers beyond their expected lives. Same with oil breakers. | SR.1.2
MIP | ES31 | Again, may be helpful to show the scores of at-risk devices. | SR.1.2
MIP | ES32 | Again, scores of devices at risk compared to total population would be helpful | SR.1.2
MIP | ES33 | Can we provide any data that shows failure rates of at risk devices above the average of all station switchgear? Can we refer to Figure 1.12? | SR.1.2
MIP | ES34 | See prior comment on population of switchgear exceeded useful lives | SR.1.2
MIP | ES35 | This implies a benefit cost analysis was conducted | SR.1.2
MIP | ES36 | Similar to transformers, is life extension an option? | SR.1.2
MIP | ES37 | Has this objective been confirmed in above analysis? | SR.1.2
MIP | ES38 | Cost data would be helpful, if available, to confirm this statement | SR.1.2
MIP | ES39 | Has this been quantified in terms of increase in SAIFI, SAIDI & CAIDI based on the higher failure rates cited in the next sentence? | SR.1.2
MIP | ES40 | Note the contrast to the station transformer replacement program, where reliability is assigned 5%. | SR.1.2
MIP | ES41 | Table 1.11 shows only 3 switchgear renewal during the bridge and test years. | SR.1.2
MIP | ES42 | Need %’s inserted in the pie diagram | SR.1.2
MIP | ES43 | Assume this includes all 3 relay types | SR.1.3
MIP | ES44 | Similar to transformers and switchgear, does it make sense to show how reliability metrics will be impacted by P&C replacements? | SR.1.3
MIP | ES45 | Why just SAIDI and not SAIFI or CAIDI? | SR.1.3
MIP | ES46 | OK to add this? | SR.1.3
MIP | ES47 | This suggests a benefit cost analysis has been performed for each alternative, but results are not presented in Exhibit E.. | SR.1.3
MIP | ES48 | Quantities missing? | SR.1.3
MIP | ES49 | May want to mention microprocessor relays take up less space, so this is not likely to be a factor. | SR.1.3
MIP | ES50 | Will the new microprocessor relays accommodate greater amounts of ERFs due to greater sensitivity and functionality? | SR.1.3
MIP | ES51 | For transformers, switchgear and P&Cs, the summary table appears at the end of the section. It appears that after this table, the standard text format for this program (and the minor station renewal) has moved to a tabular format. Note that full paragraph text and section headings/numbering was used in the 3 prior renewal project categories | SR.1.4
MIP | ES52 | Not sure why we need to say this. It suggests other projects often are deferred. | SR.1.4
MIP | ES53 | Shouldn’t these be whole numbers? Can 50% of a battery bank be replaced on a cost-effective basis? | SR.1.4
MIP | ES54 | Seems to conflict with the prior sentence which states that HOL’s standard practice is to increase capacity ratings when equipment is replaced. Does it make sense to state that capacity ratings are increased when they fall below HOL’s current planning criteria? | SR.1.5
MIP | ES55 | Not clear how the other 12 are addressed with respect to condition and need for replacement. | SR.1.6
MIP | ES56 | Figure 1.23 and several charts that follow have already been presented in prior sections. Not sure we need to show them again (instead, refer to prior figure numbers). | SR.1.6
MIP | ES57 | Not clear why no entries appear | SR.1.6
MIP | ES58 | Not clear why no entries appear | SR.1.6
MIP | ES59 | Is it just “poor” condition?. Are there poles that are replaced due to clearance violations, undersized, attachments or other factors? | SR.2.1
MIP | ES60 | Does scope include enhanced guying and anchoring, or installation of guy insulators? | SR.2.1
MIP | ES61 | Strength or clearance? | SR.2.1
MIP | ES62 | May want to mention which program covers undersized or obsolete conductors. | SR.2.1
MIP | ES63 | Replacements? | SR.2.1
MIP | ES64 | In the above pie chart, what condition constitutes a “must replace” or “zero life” pole? Later, we refer to replacement of poles in “poor” condition, which implies that up to 26% of poles should be replaced based on this chart. | SR.2.1
MIP | ES65 | May be helpful to cite similar statistics for station renewal programs. | SR.2.1
MIP | ES66 | Given historical SAIFI statistics, is it possible to predict avoided increase in SAIFI due to the program? | SR.2.1
MIP | ES67 | How do we define or categorize “failure” based on resistograph results? | SR.2.1
MIP | ES68 | Does this have any impact on the cost or quantities of poles that will be replaced between 2021 and 2025? | SR.2.1
MIP | ES69 | Is the cost of these other replacements covered under other renewal programs? | SR.2.1
MIP | ES70 | Isolate? | SR.2.2
MIP | ES71 | Not sure what is meant by non gang-operated reclosers (Are these 1-phase devices?), and why these are allowed to run to failure. | SR.2.2
MIP | ES72 | Should we state how many of these are gang versus non-gang operated? | SR.2.2
MIP | ES73 | Is the amount of funding determined by need; that is, funding requirements are based the condition and performance of HOL’s assets? This statement implies that HOL has set a funding cap for its rate fling. | SR.2.2
MIP | ES74 | Would it be helpful to state how SAIFI has worsened due to porcelain insulator failures? | SR.2.2
MIP | ES75 | . . .carefully prioritize devices selected for replacement? | SR.2.2
MIP | ES76 | Is there data or reliability statistics that can be cited to further support this statement? | SR.2.2
MIP | ES77 | May want to cite the target in this statement. | SR.2.2
MIP | ES78 | Does the program stop at the end of 2024? | SR.2.2
MIP | ES79 | May be helpful to explain how costs decrease to support this statement. | SR.2.2
MIP | ES80 | These statements indicate that the $2.3 million for porcelain switch replacements will performed on only 3 feeders: TD07, TD05 and TW22. Does this mean there will no replacements on other feeders? | SR.2.2
MIP | ES81 | Should this be relabeled as “Vault Equipment Renewal” to distinguish it from renewal of the vault enclosure? | SR.3.1
MIP | ES82 | May want to state what these reliability goals are and how the extent to which vault renewal contributes to meeting this goal later in Section 3.1. | SR.3.1
MIP | ES83 | Is there a target SAIFI for these transformers? | SR.3.1
MIP | ES84 | Are vault structures included in this group? | SR.3.2
MIP | ES85 | Same comment raised earlier on funding caps versus determining the level of funding needed to maintain reliability and performance targets. | SR.3.2
MIP | ES86 | We have mentioned employee and public safety in prior sections. | SR.3.2
MIP | ES87 | Are there a limited number of contractors that can replace UG cable? | SR.3.2
MIP | ES88 | Targeted? | SR.3.2
MIP | ES89 | To clarify, does this mean existing direct buried cable is replaced with PVC-encased cable? Would be helpful to indicate how much existing cable is direct buried versus duct banks.. | SR.3.3
MIP | ES90 | Is the risk model used to recommend spending levels for all or most other renewal programs? If so, this may not have been mentioned in sections covering other replacement programs. | SR.3.3
MIP | ES91 | Does this include primary and secondary, or primary voltage cable only? | SR.3.3
MIP | ES92 | May want to mention defective polymer cable is a major contributor to SAIFI as compared to several other asset categories. | SR.3.3
MIP | ES93 | Aren’t these one and the same (e.g. end of life and reliability)? That is, cable reliability degrade to unacceptable levels when it reaches the end of its useful life? Perhaps a secondary driver is repair and replacement cost associated with cable failures. | SR.3.3
MIP | ES94 | Previously we indicated that underground location and physical separation limits safety hazards. Given the relatively high SAIFI impact, perhaps safety is a secondary factor. | SR.3.3
MIP | ES95 | Do we mean “external”? | SR.3.3
MIP | ES96 | Can we cite the SAIFI target? | SR.3.4
MIP | ES97 | Not quite sure is meant by expansion of outages | SR.4.1
MIP | ES98 | Values missing for Critical Renewal | SR.4.1
MIP | ES99 | Not clear why budgets are broken out in such detail given that the likelihood of assets actually failing in any specific category in the future will match these values. | SR.4.1
MIP | ES100 | Are the results of economic studies presented in this section? | SR.5.1
MIP | ES101 | Not clear why the replacement is targeted to 2024. Is this the year they are fully depreciated? If so, may want to make a general statement that meters will remain in service until they are fully depreciated. | SR.5.1
MIP | ES102 | Why only in 2025? Is this the date the meters are fully depreciated? | SR.5.1
MIP | ES103 | Is this sentence needed? | SR.5.1
MIP | ES104 | Is this ROR or payback interval? | SR.5.1
MIP | ES105 | Can we state how this decrease was derived? | SR.5.1
MIP | ES106 | Satisfaction? | SR.5.1
MIP | ES107 | May want to add this sentence segment in prior project expenditure descriptions, where applicable | SR.5.1
MIP | ES108 | Suggests that Renewal programs are designed to improve SAIFI and System Service capacity investments are designed to improved SAIDI & CAIDI. | SS.1.1
MIP | ES109 | Shouldn’t the planning rating be higher than 60 MVA due to the LTR rating for N-1 events? | SS.1.1
MIP | ES110 | Might be helpful to include a map illustrating where Limeback and Uplands stations are located, perhaps earlier in this section. Also, want to add a table showing capacity versus load for these stations help illustrate how the 4th transformer relieves area capacity constraints. | SS.1.1
MIP | ES111 | Not clear how these values are derived | SS.1.1
MIP | ES112 | Has reliability degraded? Not sure this was mentioned in prior sections. | SS.1.1
MIP | ES113 | Does the capacity deficiency also result in stranded load; that is, switching operations alone will not restore power to all customers? | SS.1.1
MIP | ES114 | The Limebank station project refers to a low-side voltage of 27.6 kV | SS.1.1
MIP | ES115 | Might be helpful to show a map highlighting the location of the new station. | SS.1.1
MIP | ES116 | From other stations? | SS.1.1
MIP | ES117 | Chart indicates capacity deficit is already near 25 MVA | SS.1.1
MIP | ES118 | Net forecast indicates DG is given capacity credits | SS.1.1
MIP | ES119 | Contingency “events”? | SS.1.1
MIP | ES120 | The description for Limebank shows “SAIDI and CAIDI” | SS.1.1
MIP | ES121 | Is something missing? Not clear what “1” refers to. | SS.1.1
MIP | ES122 | Are upgrades needed to operate the line at 230kV? | SS.1.1
MIP | ES123 | Will there be two sets of switchgear, one for each transformer, or is there a common 27.6kV bus? | SS.1.1
MIP | ES124 | Has project construction started? | SS.1.1
MIP | ES125 | Prior chart suggests station capacity already is deficient. | SS.1.1
MIP | ES126 | Again, station capacity already appears to be deficient | SS.1.1
MIP | ES127 | Has construction started? | SS.1.1
MIP | ES128 | Is it limited number of feeders or feeder capacity? | SS.1.1
MIP | ES129 | Outages? | SS.1.1
MIP | ES130 | Is this the LTR rating? Refer to Figure 1.3, which shows LTR. | SS.1.1
MIP | ES131 | May want to indicate the rating in MVA | SS.1.1
MIP | ES132 | Is this the same as design capacity referred to in the Uplands station? | SS.1.1
MIP | ES133 | Above, we refer to design rating | SS.1.1
MIP | ES134 | This differs from the prior 2 station capacity upgrade projects. | SS.1.1
MIP | ES135 | Previously, “design” and “planning” ratings have been used. Suggest using consistent terminology unless there is a basis for using different descriptions. | SS.1.1
MIP | ES136 | Prior Limebank station project includes a reliability component | SS.1.1
MIP | ES137 | Same comment as above regarding ratings. Note that this appears to be the first time that breaker ratings will be exceeded. | SS.1.1
MIP | ES138 | Increase? | SS.1.1
MIP | ES139 | N/A | SS.1.1
MIP | ES140 | N/A | SS.1.1
MIP | ES141 | N/A | SS.1.1
MIP | ES142 | N/A | SS.1.1
MIP | ES143 | First time that entire range of ratings is presented. May want to present the full set of ratings up front. | SS.1.1
MIP | ES144 | A bit unclear. Are we saying maintenance can be performed without the need for tie transfers? | SS.1.1
MIP | ES145 | Does this refer to installing a high-side tie breaker to provide isolation for each transformer? | SS.1.1
MIP | ES146 | Economic development impacts is mentioned for the Upland project, but not for the 2 prior station capacity projects. | SS.1.1
MIP | ES147 | Not sure we want to directly link economic growth to the project. The statement suggest HOL would not be able to connect new load requests. Perhaps better to say reliability would be degraded, thereby potentially discouraging economic development projects in the area. | SS.1.1
MIP | ES148 | Is there a separate switchgear line-up served by T2 or is there a common low-side bus? | SS.1.1
MIP | ES149 | Small amounts of DG may not cause reverse power flow | SS.1.1
MIP | ES150 | Do we need to mention DG fault current contribution as well? | SS.1.1
MIP | ES151 | May want to insert low-side voltage (27.6kV) | SS.1.1
MIP | ES152 | Is the existing low-side 27.6kV or a lower voltage. | SS.1.1
MIP | ES153 | Would be helpful to have a similar table for prior 3 station projects. | SS.1.1
MIP | ES154 | Tie transfer capacity? | SS.1.1
MIP | ES155 | Not sure I follow what is meant by “when considering” Do we mean when scheduled upgrades are “included”? | SS.1.1
MIP | ES156 | Same concern as prior comment on limiting economic growth | SS.1.1
MIP | ES157 | Other capacity initiatives or renewal or both? | SS.1.1
MIP | ES158 | lower priority seems to somewhat contradict high priority mentioned in the first sentence in this paragraph. | SS.1.1
MIP | ES159 | Could land acquisition issues delay the project? | SS.1.1
MIP | ES160 | Does this include contributions for HONI 230kV transmission? If yes, may want to mention this under project Scope. | SS.1.1
MIP | ES161 | Not clear about the type and timing of the capacity upgrades | SS.1.2
MIP | ES162 | Margin? | SS.1.2
MIP | ES163 | It might be helpful to summarize and list (1) Total number of new feeders; (2) Miles of line upgraded; (3) Number of new tie points enabled by the feeder additions or upgrades | SS.1.2
MIP | ES164 | Can we add “beyond 2025”? | SS.1.2
MIP | ES165 | Should heading say “Transformer”? | SS.1.2
MIP | ES166 | Should heading say “Transformer”? | SS.1.2
MIP | ES167 | Might be helpful to compare the cost of the feeder versus infrastructure upgrades. | SS.1.2
MIP | ES168 | Is this the same as the LTR? | SS.1.2
MIP | ES169 | Replace with “switching? | SS.1.2
MIP | ES170 | Do we mean distribution capacity upgrades or all other programs, including renewals? | SS.1.2
MIP | ES171 | Is this amount included in the $20.7 M cost? | SS.1.2
MIP | ES172 | Unintentionally? | SS.2.1
MIP | ES173 | Can we cite a source? For example, see reference to OEB below. | SS.2.1
MIP | ES174 | Measures? | SS.2.1
MIP | ES175 | Better to state the funding amounts needed to meet these requirements | SS.2.1
MIP | ES176 | Should we include Smart Grid applications on distribution feeders? | SS.2.1
MIP | ES177 | Do we need to insert a chart showing the quadrants? | SS.2.1
MIP | ES178 | Again, a chart, if available, would place these values into perspective | SS.2.1
MIP | ES179 | Need to reference the costs table that follows | SS.2.1
MIP | ES180 | Need intro sentence | SS.2.1
MIP | ES181 | Need to insert a caption and reference to the chart in this paragraph | SS.2.1
MIP | ES182 | Not sure this term has been defined previously | SS.2.1
MIP | ES183 | Is a statement needed to address ERFs that are connected to SCADA? | SS.2.1
MIP | ES184 | Do we need to summarize why spending will decline? Is this amount needed to maintain current levels of reliability? | SS.3.1
MIP | ES185 | Several new substations are included in the System Service category that includes circuit reconfigurations. Should these be mentioned or indicate that spending for capacity-based upgrades are covered under other investment categories? | SS.3.1
MIP | ES186 | Suggests this objective focuses on reducing SAIDI | SS.3.1
MIP | ES187 | Is there a target level of improvement? | SS.3.1
MIP | ES188 | Should we say “not recommended”? | SS.3.1
MIP | ES189 | Would be helpful to clarify where cap investments would be deferred | SS.3.1
MIP | ES190 | Detection and isolation? | SS.3.1
MIP | ES191 | Might be helpful to list each of these in bulleted form | SS.3.2
MIP | ES192 | This suggests projects are ranked and selected based on benefit to cost ratios. If so, may be helpful to cite results of the analysis | SS.3.2
MIP | ES193 | May want to add favourable benefit cost ratios | SS.3.2
MIP | ES194 | Will the voltage conversions accommodate greater amounts of ERFs? | SS.3.2
MIP | ES195 | Section 3. is also labeled as “Distribution Enhancement” | SS.3.3
MIP | ES196 | Sentence not finished | SS.3.3
MIP | ES197 | Scope or funding envelope? | SS.3.3
MIP | ES198 | These comments appear to suggest that Smart Grid programs are not good investments, in part due to limited funding. Is this the intent? | SS.3.3
MIP | ES199 | The following subsections describe the organization and processes that will be followed, but don’t describe or list any specific initiatives or programs. Should some examples be cited (e.g. feeder automation or outage analytics) or refer to Section 3.31.5.1 even if they are not yet approved by the steering committee? | SS.3.3
MIP | ES200 | Prior comments appear to suggest it is a low priority, in part due to uncertain funding. | SS.3.3
MIP | ES201 | Some smart grid strategies are designed to accommodate greater amounts of ERFs and provide better visibility on ERFs operations and their impact on utility distribution system performance | SS.3.3
MIP | ES202 | Implies that total reliability metrics will improve | SS.3.3
MIP | ES203 | This statement suggests a benefit cost analysis (e.g. B/C ratios) was conducted for projects under this program. If so, it would be helpful to show results | SS.3.3
MIP | ES204 | Violations? | SS.3.3
MIP | ES205 | Where does this appear? | SS.3.3
MIP | ES206 | Fully utilized? | SS.3.3
MIP | ES207 | Should we say key components are becoming obsolete and need to be replaced? | SS.4.1
MIP | ES208 | Should we say that these needs can only be met by replacing or upgrading the existing OMS? | SS.4.1
MIP | ES209 | Give examples | SS.4.1
MIP | ES210 | Secondary impact appears to be improved customer communications and notifications | SS.4.1
MIP | ES211 | Not sure how losses are affected by the OMS | SS.4.1
MIP | ES212 | Is this due solely to the OMS, and if yes, how will this be measured and tracked? | SS.4.1
MIP | ES213 | This is the first instance ADMS is mentioned. May want to introduce ADMS (DMS) and how it integrates with the OMS in prior sections (e.g. what added functionality is achieved via ADMS?) | SS.4.1
MIP | ES214 | This seems low for a new OMS. Do these costs include integration, training and introduction of new business processes? | SS.4.1
MIP | ES215 | Not sure I follow this statement | SS.4.1
MIP | ES216 | Not sure what this is intended to convey | SS.4.1
MIP | ES217 | Not sure if prior sections clearly indicated how OMS will improve DMS functionality | SS.4.1
MIP | ES218 | Do we need to mention documentation and adoption of new business processes associated with new features and enhanced functionality? | SS.4.1
MIP | ES219 | ? | SS.4.1
MIP | ES220 | Are we sure none of this can be capitalized as part of the upgrade? | SS.4.1
MIP | ES221 | Should we mention integration with the new OMS as well? | SS.4.1
MIP | ES222 | SCADA system? | SS.4.1
MIP | ES223 | May be helpful to mention the name of the system in the prior SCADA project write-up | SS.4.1
MIP | ES224 | Volt/Var optimization? | SS.4.1
MIP | ES225 | Losses are efficiency-related v. PQ-related | SS.4.1
MIP | ES226 | How will loss reductions be tracked for this program? | SS.4.1
MIP | ES227 | ? | SS.4.1
MIP | ES228 | As before, not clear what system wide effects refers to | SS.4.1
MIP | ES229 | By System Control Center staff? | SS.4.1
MIP | ES230 | The OMS Replacement project included a target reduction in SAIDI. Has HOL estimated the additional reduction in SAIDI that it expects to achieve via meter pinging? | SS.4.1
MIP | ES231 | May want to describe these upgrades in more detail in prior sections | SS.4.1
MIP | ES232 | Clarify or expand | SS.4.1
MIP | ES233 | Note that the prior AMI OMS Integration project will provide greater visibility on outage location | SS.4.1
MIP | ES234 | List of describe these devices | SS.4.1
MIP | ES235 | Not clear how improved monitoring will reduce the number of customer interruptions | SS.4.1
MIP | ES236 | For the OMS Replacement project, the reduction in SAIDI was quantified. Is there a target reduction for this program.? For example, can we use the estimates provided in the following table to estimate the reduction in system-wide SAIDI? | SS.4.1
MIP | ES237 | Need intro sentence | SS.4.1
MIP | ES238 | Do we know by how much? | SS.4.3
MIP | ES239 | Gaps? | SS.4.3
MIP | ES240 | Should we say operational efficiency and reliability improvements? | SS.4.3
MIP | ES241 | Format and details for this project are not the same as prior projects. | SS.5.1
MIP | ES242 | Will the program extend beyond the rate period to lower priority locations? | SS.5.1
MIP | ES243 | What are these? | GP1.1
MIP | ES244 | Need intro sentence and chart description | GP1.1
MIP | ES245 | Expand to describe upstream and downstream implications | GP1.1
MIP | ES246 | Table caption needed | GP1.1
MIP | ES247 | describe | GP1.1
MIP | ES248 | Other projects show the timing of specific activities in the work plan | GP1.1
MIP | ES249 | Is this accurate? | GP1.1
MIP | ES250 | Need caption and cross reference | GP1.1
MIP | ES251 | Need lead-in sentence | GP1.1
MIP | ES252 | Describe automation features, either here or elsewhere in this section? | GP1.1
MIP | ES253 | Need lead-in sentence | GP1.1
MIP | ES254 | Lead-in sentence | GP1.1
MIP | ES255 | Need lead-in sentence(s), caption and cross reference to table | GP1.1
MIP | ES256 | Timing of these steps? | GP1.1
MIP | ES257 | Need lead-in sentence(s) and cross reference to table 1.6 | GP1.1
MIP | ES258 | Need lead-in sentence(s), caption and cross reference to table | GP1.1
MIP | ES259 | Need lead-in sentence(s) and cross reference to table 1.8 | GP1.1
MIP | ES260 | Level of detail and format does not match other projects | GP1.1
MIP | ES261 | Need intro sentence | GP2.1
MIP | ES262 | Intro sentence | GP2.1
MIP | ES263 | Need lead-in sentence(s) and cross reference to table 2.1 | GP2.1
MIP | ES264 | Need lead-in sentence(s) and cross reference to table 2.2 | GP2.1
MIP | ES265 | Lead-in sentence | GP2.1
MIP | ES266 | Timing of work activities? | GP2.1
MIP | ES267 | Need table caption and cross reference | GP2.1
MIP | ES268 | Spell out | GP2.2
MIP | ES269 | Timing of work activities? | GP2.2
MIP | ES270 | Should results be presented in this section? | GP4.1
MIP | ES271 | Need lead-in sentence and cross reference to table 4.2 | GP4.1
MIP | ES272 | Cybersecurity was addressed earlier in the Distribution Station in section 2.1.2. Do we need to mention how this program differs from the prior program? | GP4.2
MIP | ES273 | Note prior comment on section 2.1.2 for distribution stations | GP4.2
MIP | ES274 | May want to insert a chart to illustrate quadrants | GP4.2
MIP | ES275 | Need lead-in sentence(s) and cross reference to table 4.4 | GP4.2
MIP | ES276 | Need table caption and cross reference | GP4.2
MIP | ES277 | Need intro sentence and cross reference to table 5.1 | GP5.1
MIP | ES278 | Expected to see some level of O&M w/ updated Data management systems | GP5.1
MIP | ES279 | Timing issues? | GP5.1
MIP | ES280 | Operational efficiency? | GP6.1
MIP | ES281 | Need to reference Figure 6.1, highlighting key interfaces and applications (analytics) that will be enhanced by this initiative | GP6.2
MIP | ES282 | Was load disaggregation been discussed previously? | GP6.2
MIP | ES283 | Need intro sentence and cross reference to table 6.3 | GP6.2
MIP | ES284 | Timing issues? | GP6.2
MIP | ES285 | Discuss how upgrades for this program/project integrates with and complements OMS, DMS and SCADA upgrades presented in prior sections of this document. | GP6.3