## Sheet1
Hydro Ottawa Limited EB-2019-0261 Interrogatory Response IRR SEC-54 Attachment C ORIGINAL
Navigant First Review
Discussion Topics, Questions & Observations | Section/Page No.
· Discuss “Strategic Objectives in following statement: “timing of investments are optimized to minimize overall risk to HOL`s Strategic Objectives” & Linkage to 8 core elements | 1.5, p. 12 & p. 33
· Has there been any change in engineering design standard due to current or expected climate change, including resiliency to major events? | 2.1, p. 25-29
· Is the reliability target for 2021-2025 the same for all years or does it change based on a rolling average of prior 5 years (e.g. 0.84 SAIFI)? Is proposed spending for System Renewal based on meeting the 5-year target? | 4.1.1.2, p. 44
· Has HOL estimated the reduction in losses for the voltage conversion projects? If yes, state in DSP or are losses addressed in business cases? | 4.1.4.3, pp. 60, 61
· Table 4.23 shows a large increase in tree-related interruptions. Although mostly O&M, are investments that are proposed to mitigate VM (e.g. tree wire, bundled conductor, etc.) | 4.3.1, pp. 62, 67
· Will new meters be linked to DMS/OMS upgrade to enhance functionality of outage detection processes from Distribution Control Centre? | 4.3.3, p. 74
· Does Table 3.25 include Energy Diversion (theft)? Is this the same as “Unmetered” Loads”? | 4.5.4, p. 75
· Is there a threshold at which an Asset Health Condition score triggers an intervention (capital investment or O&M) outside of C55 Process? | 5.1.2, p. 79
· Discuss process/methods for scoring/grading in Table 5.22 – Health Index Calculation Example | 5.1.2, p.80
· Need Attachment B-1 (D) – “GEG0001 – Asset Health Index Guideline” and “Asset Condition Assessment implementation” in Attachment B-1 (E). | 5.1.2, p. 81
· Are sensitivity analyses conducted for low/high forecasts, with impact on System Service investment levels? | 5.1.5, p. 84
· How are upper capacity limits derived for station transformers for n-1 loading conditions (.e.g. <1% allowable loss of life criterion)? | 5.1.6, p. 85
· Do all feeders, regardless of voltage, have n-1 back up capability? If not, how are capacity limits set for feeders that do not (e.g., 4kV circuits)? | 5.1.6, p. 85
· Discuss Asset Analytics & Optimization methodology and results. How are dissimilar investment options prioritized? Describe project selection criteria in Program Analytics, Life Cycle Optimization, Value Model & C55 Model? | 5.1.8, p. 87-90 5.2.2, p. 99
· Not clear how customer survey results are factored into project selection process and capital plan | 5.4, p. 114
· Figures 6.1 and 6.2. Can similar graphics be created that will show asset life expectancy if 5-Year capital program is approved and implemented? Same for Figures 6.4 to 6.27 on asset age by equipment category | 6.1, pp.119-120 pp. 121-157
· Figure 6.19: 90+Year-Old polymer cable? Check asset registry. Other asset categories also show unusually high age range. | 6.1, p. 145
· Table 6-19: Should table include NDT for UG cable? | 6.2.2, p. 159
· PILC: Is there a plan to phase out PILC over time? | 6.2.2.7, p. 162
· Does HOL transition to a standardized voltage (e.g. 27kV for outlying areas; 13kV for downtown). Several voltage conversions are cited to increase capacity. | 7.2, pp. 176-209
· What is meant by “with few contingencies between stations” on 8kV system? | 7.2.2.3, p. 185
· Will business cases show alternatives to proposed capacity additions? | 7.2, pp. 176-209
· Role of DER/ERF for capacity deferral (EE,DR DG)? Consideration of targeted DER. | 7.2, pp. 176-209
· Describe mitigation or reverse flow at substation and feeder level (e.g. LTC’s, regulators, protective relays). Will these appear in business cases? | 7.3.5, p. 217-218
· What percent of new feeder capacity will be UG v. OH and how does this impact 5-year System Service investment? | 8.1.2
· Should DSP quantify O&M savings (composite or by 4 spending categories, especially System Renewal)? | 8.1.2, p. 224
· Why no drivers for General Plant in Table 8.4? | 8.1.3, p. 227
· Currently, system capacity is 9% above rating. What will be O/L level in Year 5? Also, what will be the change in ave, loadings as percent of rating? | 8.1.6.1, p. 228
· Describe changes to be made to Copperleaf AM prioritization tool in 2020 and application to specific investment categories? | 8.1.6.4.2, p. 230
· Table 8.5: Typo “WYE” instead of “Why” | 8.2, p.233
· Breakout of annual values for contributions in aid of construction reflected in Table 8.7 (line extensions, relocations, EF upgrades, etc.) | 8.2.1, p. 235
· Reference for 2012-2025 spending should be Table 8.9, not 8.7 | 8.2.2, p. 238
· Typo. Change 2021 to 2016 | 8.3.1, p. 245
· Should description for Renewal Investment spending be based on condition rather than “aging infrastructure”? | 8.3.1, p. 246
· Table 8.11. Why was spending for OH was higher than UG despite 50% split on primary line miles and focus on cable replacements? | 8.3.1, p. 247
· Words missing? “Which allocate work . . .” | 8.3.1, p. 247, line 5
· UG replacements expected to increase 30% over 5 years. What is this based on? Is there inspection or testing data to support the increase? | 8.3.2, p. 250
· Corrective Renewal: Is there a correlation or linkage of annual budgets based on projected equipment failure rates? How are budgets derived? | 8.3.2, p. 250
· Table 8.13: Overhead Distribution. Note absence of conductor replacement (e.g. #6 wire to larger conductor) | 8.3.3, p. 251
· Note: Need Attachment 1-B, which provides additional details on Asset Renewal replacements | 8.3.3, p. 251
· Include integration of OMS w/ DMS/SCADA (plan, is to transition all 3 to a common platform)? | 8.4.2, p. 260, Line 19
· Metering replacements: Quantify expense reduction for meter replacements (not listed as a benefit in tables or text) | 4.5, 8.4.4, pp. 74, 265