## Sheet1
Hydro Ottawa Limited EB-2019-0261 Technical Conference Undertakings Undertaking TC-JT 2.3 Attachment B UPDATED August 10, 2020
Asset Class | 2014 Population | # Assets with HI Data | 2014 % Poor/very Poor | 2014 Average Age | 2018 Population | # Assets with HI Data | 2018 % Poor/very Poor | 2018 Average Age | Comments
Poles | 60113 | 35323 | 12% | 39 | 62808 | 39087 | 26% | 35 | Variance in Poor/Very Poor condition percent from 2014 to 2018 due to evolution of health index (HI) to include additional criteria to age. Hydro Ottawa has active renewal program prioritizing assets in Very Poor and Poor condition.
Polemounted Transformers | 15663 | 15663 | 11% | 30 | 15670 | 6499 | 1% | 32 | Variance in Poor/Very Poor condition percent from 2014 to 2018 due to evolution of health index (HI) to include additional criteria to age. The 2014 HI included only age demographics. Hydro Ottawa renews this asset as part of the pole renewal program and also prioritizes assets in Very Poor and Poor condition.
Kiosk & Padmounted Transformers | 15633 | 15297 | 4% | 33 | 17045 | 16413 | 1% | 23 | Variance in Poor/Very Poor condition percent from 2014 to 2018 due to: - Evolution of health index (HI) to include additional criteria to age. The 2014 HI included only age demographics. - Increased number of maintenance activities (beginning in 2016) to maintain transformers (improving their condition) when possible or queued for replacement as needed. Hydro Ottawa renews this asset as part of the cable renewal program and also prioritizes assets in Very Poor and Poor condition.
Vault Transformers | 3474 | 3474 | 7% | 34 | 3652 | 3280 | 13.4% | 37 | Variance in Poor/Very Poor condition percent from 2014 to 2018 due to: - Evolution of health index (HI) to include additional criteria to age. The 2014 HI included only age demographics. - Increased number of maintenance activities (beginning in 2016) to maintain transformers (improving their condition) when possible or queued for replacement as needed. Hydro Ottawa renews this asset as part of the cable renewal program and also prioritizes assets in Very Poor and Poor condition.
Distribution Cables (XLPE) | 4,128 km | 3,925 km | 17% | 25 | 2,674 km | 2,131 km | 58% | 26 | Quantity of cable in 2018, is lower than quantity reported in 2014, largely the result of quantity reported as circuit-km's instead of cable-km's. Variance in Poor/Very Poor condition percent from 2014 to 2018 due to evolution of health index (HI) to include additional criteria to age. Hydro Ottawa has active renewal program prioritizing assets in Very Poor and Poor condition.
Distribution Cables (PILC) | 356 km | 356 km | 15% | 35 | 385 km | 321 km | 0% | 39 | Variance in Poor/Very Poor condition percent from 2014 to 2018 due to evolution of health index (HI) to include additional criteria to age. The 2014 HI included only age demographics. Hydro Ottawa renews this asset as part of System Expansion project and as failures occur.
Underground Switchgear | 632 | 357 | 2% | 15 | 995 | 141 | 0% | 6 | Number of switchgear for 2018, is higher than 2014, as it includes assets installed within substations and vaults. Variance in Poor/Very Poor condition percent from 2014 to 2018 due to evolution of health index (HI) to include additional criteria to age. The 2014 HI included only age demographics. Hydro Ottawa has active renewal program prioritizing assets in Very Poor and Poor condition.
Station Transformers | 170 | 162 | 2% | 36 | 167 | 167 | 0% | 35 | Variance in Poor/Very Poor condition percent from 2014 to 2018 due to evolution of health index (HI) to include additional criteria to age. Hydro Ottawa has active renewal program prioritizing assets in Very Poor and Poor condition.
Station Breakers | 1003 | 924 | 5% | 36 | 991 | 374 | 0% | 34 | Variance in Poor/Very Poor condition percent from 2014 to 2018 due to evolution of health index (HI) to include additional criteria to age. The 2014 HI included only age demographics. Hydro Ottawa has active renewal program prioritizing assets in Very Poor and Poor condition.
Cable Chambers | 3508 | n/a | n/a | n/a | 3758 | 2697 | 4% | 27 | Variance in Poor/Very Poor condition percent from 2014 to 2018 due to development of a health index for this asset class. Hydro Ottawa has active renewal program prioritizing assets in Very Poor and Poor condition.