## 2021-FULL
Dry Core Transformer Losses Proposed for 2021
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.466 | 0.1329 |  | 5.0052
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87836 | 12.0782 | 12.9566 | 0.80431 | 13.7609
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1712 | 16.1043 | 17.2754 | 1.0724 | 18.3478
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4932 | 20.2596 | 21.7529 | 1.3673 | 23.1202
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.991 | 27.9239 | 29.9148 | 1.8231 | 31.7379
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4008 | 32.4672 | 34.868 | 2.1984 | 37.0664
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6919 | 36.3215 | 39.0134 | 2.4649 | 41.4783 |  | To be updated
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1767 | 42.7263 | 45.903 | 2.9089 | 48.8119 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9526 | 52.9854 | 56.938 | 3.6194 | 60.5574 | GS 50 to 1,499 kW | 0.01964 | 3.1059 | 1.9644 | 5.3505
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0422 | 54.201 | 58.2432 | 3.7014 | 61.9446 | GS 1,500 to 4,999 kW | 0.02099 | 3.2248 | 2.0995 | 4.8801
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.229 | 56.7204 | 60.9494 | 3.8724 | 64.8219 | Large Use | 0.02364 | 3.5749 | 2.3643 | 4.785
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5446 | 60.9567 | 65.5013 | 4.1615 | 69.6628
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8602 | 65.1929 | 70.0532 | 4.4505 | 74.5036
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0314 | 81.2972 | 87.3286 | 5.5229 | 92.8515 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45734 | 6.5565 | 7.0139 | 0.41879 | 7.4327
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.7027 | 9.9359 | 10.6386 | 0.64346 | 11.282 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4054 | 19.8717 | 21.2771 | 1.2869 | 22.564 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7567 | 24.1564 | 25.9131 | 1.6086 | 27.5218 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3423 | 32.2085 | 34.5508 | 2.1448 | 36.6957
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4549 | 48.0542 | 51.5091 | 3.1636 | 54.6727
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1868 | 56.7529 | 60.9397 | 3.8339 | 64.7736
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5356 | 61.9005 | 66.436 | 4.1532 | 70.5892
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8881 | 67.1195 | 72.0076 | 4.476 | 76.4836
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2409 | 72.3399 | 77.5808 | 4.7991 | 82.3799
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3535 | 88.1856 | 94.5391 | 5.8179 | 100.3569
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6359 | 160.39 | 171.0259 | 9.7392 | 180.7652
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0634 | 184.4582 | 196.5216 | 11.0464 | 207.5679
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.811 | 233.8055 | 249.6165 | 14.478 | 264.0945
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7435 | 264.2037 | 281.9472 | 16.2476 | 298.1948
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.7165 | 350.7082 | 374.4247 | 21.7171 | 396.1418
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2842 | 420.074 | 448.3582 | 25.8997 | 474.2578
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9645 | 505.2854 | 539.2499 | 31.1011 | 570.3509
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0547 | 597.7731 | 637.8278 | 36.6779 | 674.5057
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1901 | 736.5046 | 785.6947 | 45.043 | 830.7378
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5102 | 850.8212 | 907.3314 | 51.746 | 959.0774
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2022-FULL
Dry Core Transformer Losses Proposed for 2022
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4663 | 0.1329 |  | 5.3019
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87841 | 12.0782 | 12.9566 | 0.85199 | 13.8086
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1712 | 16.1043 | 17.2755 | 1.136 | 18.4115
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4933 | 20.2596 | 21.7529 | 1.4484 | 23.2013
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9911 | 27.9239 | 29.9149 | 1.9312 | 31.8461
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.401 | 32.4672 | 34.8681 | 2.3288 | 37.1969
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.692 | 36.3215 | 39.0135 | 2.6111 | 41.6246 |  | To be updated
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1769 | 42.7263 | 45.9032 | 3.0814 | 48.9845 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9528 | 52.9854 | 56.9382 | 3.8339 | 60.7722 | GS 50 to 1,499 kW | 0.01991 | 3.1059 | 1.9644 | 5.6201
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0424 | 54.201 | 58.2434 | 3.9208 | 62.1642 | GS 1,500 to 4,999 kW | 0.02128 | 3.2248 | 2.0995 | 5.1801
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2292 | 56.7204 | 60.9497 | 4.102 | 65.0517 | Large Use | 0.02396 | 3.5749 | 2.3643 | 5.1056
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5448 | 60.9567 | 65.5015 | 4.4082 | 69.9097
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8605 | 65.1929 | 70.0534 | 4.7143 | 74.7677
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0317 | 81.2972 | 87.3289 | 5.8503 | 93.1792 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45737 | 6.5565 | 7.0139 | 0.44361 | 7.4575
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.70274 | 9.9359 | 10.6386 | 0.6816 | 11.3202 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4055 | 19.8717 | 21.2772 | 1.3632 | 22.6404 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7568 | 24.1564 | 25.9132 | 1.704 | 27.6172 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3424 | 32.2085 | 34.551 | 2.272 | 36.823
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4551 | 48.0542 | 51.5093 | 3.3512 | 54.8605
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1871 | 56.7529 | 60.9399 | 4.0611 | 65.0011
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5358 | 61.9005 | 66.4363 | 4.3994 | 70.8357
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8883 | 67.1195 | 72.0079 | 4.7413 | 76.7492
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2412 | 72.3399 | 77.5811 | 5.0836 | 82.6647
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3539 | 88.1856 | 94.5394 | 6.1628 | 100.7022
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6365 | 160.39 | 171.0265 | 10.3166 | 181.3432
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0641 | 184.4582 | 196.5222 | 11.7013 | 208.2235
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8119 | 233.8055 | 249.6173 | 15.3364 | 264.9537
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7445 | 264.2037 | 281.9481 | 17.2109 | 299.159
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.7178 | 350.7082 | 374.426 | 23.0046 | 397.4305
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2857 | 420.074 | 448.3597 | 27.4351 | 475.7948
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9663 | 505.2854 | 539.2517 | 32.9449 | 572.1966
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0569 | 597.7731 | 637.83 | 38.8523 | 676.6823
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1928 | 736.5046 | 785.6974 | 47.7134 | 833.4108
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5132 | 850.8212 | 907.3344 | 54.8138 | 962.1482
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2023-FULL
Dry Core Transformer Losses Proposed for 2023
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4666 | 0.1329 |  | 5.5728
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87846 | 12.0782 | 12.9567 | 0.89552 | 13.8522
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1713 | 16.1043 | 17.2755 | 1.194 | 18.4696
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4934 | 20.2596 | 21.753 | 1.5224 | 23.2754
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9912 | 27.9239 | 29.915 | 2.0299 | 31.9449
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4011 | 32.4672 | 34.8683 | 2.4477 | 37.316
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6922 | 36.3215 | 39.0136 | 2.7444 | 41.7581 |  | To be updated
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1771 | 42.7263 | 45.9033 | 3.2388 | 49.1421 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.953 | 52.9854 | 56.9384 | 4.0298 | 60.9682 | GS 50 to 1,499 kW | 0.02017 | 3.1059 | 1.9644 | 5.8624
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0426 | 54.201 | 58.2436 | 4.1211 | 62.3647 | GS 1,500 to 4,999 kW | 0.02156 | 3.2248 | 2.0995 | 5.4535
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2294 | 56.7204 | 60.9499 | 4.3116 | 65.2614 | Large Use | 0.02427 | 3.5749 | 2.3643 | 5.4024
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5451 | 60.9567 | 65.5018 | 4.6334 | 70.1351
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8607 | 65.1929 | 70.0537 | 4.9551 | 75.0088
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.032 | 81.2972 | 87.3292 | 6.1492 | 93.4784 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45739 | 6.5565 | 7.0139 | 0.46627 | 7.4802
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.70277 | 9.9359 | 10.6386 | 0.71642 | 11.3551 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4055 | 19.8717 | 21.2773 | 1.4328 | 22.7101 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7569 | 24.1564 | 25.9133 | 1.791 | 27.7043 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3425 | 32.2085 | 34.5511 | 2.388 | 36.9391
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4553 | 48.0542 | 51.5095 | 3.5224 | 55.0318
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1873 | 56.7529 | 60.9402 | 4.2686 | 65.2088
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.536 | 61.9005 | 66.4365 | 4.6241 | 71.0606
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8886 | 67.1195 | 72.0081 | 4.9835 | 76.9917
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2415 | 72.3399 | 77.5814 | 5.3433 | 82.9246
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3542 | 88.1856 | 94.5397 | 6.4776 | 101.0173
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6371 | 160.39 | 171.0271 | 10.8436 | 181.8707
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0647 | 184.4582 | 196.5228 | 12.299 | 208.8218
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8127 | 233.8055 | 249.6181 | 16.1198 | 265.7379
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7454 | 264.2037 | 281.9491 | 18.09 | 300.0391
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.719 | 350.7082 | 374.4272 | 24.1797 | 398.6069
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2872 | 420.074 | 448.3612 | 28.8366 | 477.1977
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9681 | 505.2854 | 539.2535 | 34.6278 | 573.8812
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.059 | 597.7731 | 637.8321 | 40.837 | 678.669
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1953 | 736.5046 | 785.6999 | 50.1507 | 835.8507
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5162 | 850.8212 | 907.3373 | 57.6138 | 964.9511
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2024-FULL
Dry Core Transformer Losses Proposed for 2024
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4668 | 0.1329 |  | 5.7323
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87849 | 12.0782 | 12.9567 | 0.92115 | 13.8778
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1713 | 16.1043 | 17.2756 | 1.2282 | 18.5038
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4934 | 20.2596 | 21.7531 | 1.5659 | 23.319
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9913 | 27.9239 | 29.9151 | 2.0879 | 32.0031
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4012 | 32.4672 | 34.8684 | 2.5178 | 37.3861
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6923 | 36.3215 | 39.0138 | 2.823 | 41.8367 |  | To be updated
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1772 | 42.7263 | 45.9035 | 3.3315 | 49.2349 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9532 | 52.9854 | 56.9386 | 4.1451 | 61.0837 | GS 50 to 1,499 kW | 0.02038 | 3.1059 | 1.9644 | 5.9983
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0428 | 54.201 | 58.2438 | 4.2391 | 62.4829 | GS 1,500 to 4,999 kW | 0.02178 | 3.2248 | 2.0995 | 5.6304
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2296 | 56.7204 | 60.95 | 4.435 | 65.385 | Large Use | 0.02453 | 3.5749 | 2.3643 | 5.5681
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5453 | 60.9567 | 65.502 | 4.766 | 70.2679
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8609 | 65.1929 | 70.0539 | 5.097 | 75.1508
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0323 | 81.2972 | 87.3295 | 6.3252 | 93.6546 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45741 | 6.5565 | 7.014 | 0.47962 | 7.4936
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.7028 | 9.9359 | 10.6387 | 0.73693 | 11.3756 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4056 | 19.8717 | 21.2773 | 1.4739 | 22.7512 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.757 | 24.1564 | 25.9134 | 1.8423 | 27.7557 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3426 | 32.2085 | 34.5512 | 2.4564 | 37.0076
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4554 | 48.0542 | 51.5096 | 3.6232 | 55.1328
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1875 | 56.7529 | 60.9403 | 4.3908 | 65.3311
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5362 | 61.9005 | 66.4367 | 4.7565 | 71.1932
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8888 | 67.1195 | 72.0084 | 5.1262 | 77.1345
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2417 | 72.3399 | 77.5816 | 5.4962 | 83.0778
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3545 | 88.1856 | 94.54 | 6.663 | 101.203
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6375 | 160.39 | 171.0275 | 11.154 | 182.1815
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0652 | 184.4582 | 196.5233 | 12.651 | 209.1743
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8134 | 233.8055 | 249.6188 | 16.5812 | 266.2
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7462 | 264.2037 | 281.9498 | 18.6078 | 300.5576
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.72 | 350.7082 | 374.4282 | 24.8717 | 399.2999
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2884 | 420.074 | 448.3623 | 29.6619 | 478.0242
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9695 | 505.2854 | 539.2549 | 35.6189 | 574.8738
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0607 | 597.7731 | 637.8337 | 42.0058 | 679.8395
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1974 | 736.5046 | 785.702 | 51.5861 | 837.2881
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5185 | 850.8212 | 907.3397 | 59.2628 | 966.6025
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2025-FULL
Dry Core Transformer Losses Proposed for 2025
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4672 | 0.1329 |  | 5.7825
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87855 | 12.0782 | 12.9568 | 0.92922 | 13.886
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1714 | 16.1043 | 17.2757 | 1.239 | 18.5146
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4935 | 20.2596 | 21.7532 | 1.5797 | 23.3328
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9914 | 27.9239 | 29.9152 | 2.1063 | 32.0215
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4013 | 32.4672 | 34.8685 | 2.5399 | 37.4084
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6924 | 36.3215 | 39.0139 | 2.8477 | 41.8617 |  | To be updated
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1774 | 42.7263 | 45.9037 | 3.3607 | 49.2643 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9534 | 52.9854 | 56.9389 | 4.1815 | 61.1203 | GS 50 to 1,499 kW | 0.0207 | 3.1059 | 1.9644 | 6.0705
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.043 | 54.201 | 58.244 | 4.2762 | 62.5203 | GS 1,500 to 4,999 kW | 0.02212 | 3.2248 | 2.0995 | 5.6567
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2299 | 56.7204 | 60.9503 | 4.4739 | 65.4242 | Large Use | 0.02491 | 3.5749 | 2.3643 | 5.6204
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5456 | 60.9567 | 65.5023 | 4.8078 | 70.31
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8612 | 65.1929 | 70.0542 | 5.1417 | 75.1958
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0326 | 81.2972 | 87.3299 | 6.3806 | 93.7105 | Tier 1 | 0.119
[14 empty] | Tier 2 | 0.139
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45744 | 6.5565 | 7.014 | 0.48382 | 7.4978
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.70285 | 9.9359 | 10.6387 | 0.74339 | 11.3821 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4057 | 19.8717 | 21.2774 | 1.4868 | 22.7642 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7571 | 24.1564 | 25.9135 | 1.8584 | 27.7719 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3428 | 32.2085 | 34.5513 | 2.4779 | 37.0293
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4556 | 48.0542 | 51.5098 | 3.655 | 55.1648
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1877 | 56.7529 | 60.9406 | 4.4293 | 65.3699
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5365 | 61.9005 | 66.437 | 4.7982 | 71.2352
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8891 | 67.1195 | 72.0087 | 5.1711 | 77.1798
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.242 | 72.3399 | 77.5819 | 5.5444 | 83.1263
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3549 | 88.1856 | 94.5404 | 6.7214 | 101.2618
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6382 | 160.39 | 171.0282 | 11.2518 | 182.28
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0659 | 184.4582 | 196.5241 | 12.7619 | 209.286
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8144 | 233.8055 | 249.6198 | 16.7266 | 266.3464
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7473 | 264.2037 | 281.9509 | 18.771 | 300.7219
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.7215 | 350.7082 | 374.4297 | 25.0898 | 399.5195
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2902 | 420.074 | 448.3641 | 29.922 | 478.2861
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9717 | 505.2854 | 539.2571 | 35.9312 | 575.1883
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0632 | 597.7731 | 637.8363 | 42.3741 | 680.2104
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.2005 | 736.5046 | 785.7051 | 52.0385 | 837.7436
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5221 | 850.8212 | 907.3433 | 59.7824 | 967.1257
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1
New Transformers added 2021

## 2021 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2021
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.466 | 0.1329 |  | 5.0052
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87836 | 12.0782 | 12.9566 | 0.80431 | 13.7609
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1712 | 16.1043 | 17.2754 | 1.0724 | 18.3478
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4932 | 20.2596 | 21.7529 | 1.3673 | 23.1202
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.991 | 27.9239 | 29.9148 | 1.8231 | 31.7379
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4008 | 32.4672 | 34.868 | 2.1984 | 37.0664
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6919 | 36.3215 | 39.0134 | 2.4649 | 41.4783
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1767 | 42.7263 | 45.903 | 2.9089 | 48.8119
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9526 | 52.9854 | 56.938 | 3.6194 | 60.5574
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0422 | 54.201 | 58.2432 | 3.7014 | 61.9446
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.229 | 56.7204 | 60.9494 | 3.8724 | 64.8219
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5446 | 60.9567 | 65.5013 | 4.1615 | 69.6628
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8602 | 65.1929 | 70.0532 | 4.4505 | 74.5036
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0314 | 81.2972 | 87.3286 | 5.5229 | 92.8515
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45734 | 6.5565 | 7.0139 | 0.41879 | 7.4327
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.7027 | 9.9359 | 10.6386 | 0.64346 | 11.282
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4054 | 19.8717 | 21.2771 | 1.2869 | 22.564
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7567 | 24.1564 | 25.9131 | 1.6086 | 27.5218
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3423 | 32.2085 | 34.5508 | 2.1448 | 36.6957
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4549 | 48.0542 | 51.5091 | 3.1636 | 54.6727
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1868 | 56.7529 | 60.9397 | 3.8339 | 64.7736
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5356 | 61.9005 | 66.436 | 4.1532 | 70.5892
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8881 | 67.1195 | 72.0076 | 4.476 | 76.4836
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2409 | 72.3399 | 77.5808 | 4.7991 | 82.3799
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3535 | 88.1856 | 94.5391 | 5.8179 | 100.3569
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6359 | 160.39 | 171.0259 | 9.7392 | 180.7652
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0634 | 184.4582 | 196.5216 | 11.0464 | 207.5679
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.811 | 233.8055 | 249.6165 | 14.478 | 264.0945
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7435 | 264.2037 | 281.9472 | 16.2476 | 298.1948
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.7165 | 350.7082 | 374.4247 | 21.7171 | 396.1418
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2842 | 420.074 | 448.3582 | 25.8997 | 474.2578
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9645 | 505.2854 | 539.2499 | 31.1011 | 570.3509
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0547 | 597.7731 | 637.8278 | 36.6779 | 674.5057
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1901 | 736.5046 | 785.6947 | 45.043 | 830.7378
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5102 | 850.8212 | 907.3314 | 51.746 | 959.0774
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2022 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2022
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4663 | 0.1329 |  | 5.3019
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87841 | 12.0782 | 12.9566 | 0.85199 | 13.8086
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1712 | 16.1043 | 17.2755 | 1.136 | 18.4115
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4933 | 20.2596 | 21.7529 | 1.4484 | 23.2013
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9911 | 27.9239 | 29.9149 | 1.9312 | 31.8461
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.401 | 32.4672 | 34.8681 | 2.3288 | 37.1969
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.692 | 36.3215 | 39.0135 | 2.6111 | 41.6246
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1769 | 42.7263 | 45.9032 | 3.0814 | 48.9845
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9528 | 52.9854 | 56.9382 | 3.8339 | 60.7722
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0424 | 54.201 | 58.2434 | 3.9208 | 62.1642
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2292 | 56.7204 | 60.9497 | 4.102 | 65.0517
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5448 | 60.9567 | 65.5015 | 4.4082 | 69.9097
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8605 | 65.1929 | 70.0534 | 4.7143 | 74.7677
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0317 | 81.2972 | 87.3289 | 5.8503 | 93.1792
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45737 | 6.5565 | 7.0139 | 0.44361 | 7.4575
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.70274 | 9.9359 | 10.6386 | 0.6816 | 11.3202
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4055 | 19.8717 | 21.2772 | 1.3632 | 22.6404
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7568 | 24.1564 | 25.9132 | 1.704 | 27.6172
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3424 | 32.2085 | 34.551 | 2.272 | 36.823
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4551 | 48.0542 | 51.5093 | 3.3512 | 54.8605
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1871 | 56.7529 | 60.9399 | 4.0611 | 65.0011
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5358 | 61.9005 | 66.4363 | 4.3994 | 70.8357
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8883 | 67.1195 | 72.0079 | 4.7413 | 76.7492
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2412 | 72.3399 | 77.5811 | 5.0836 | 82.6647
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3539 | 88.1856 | 94.5394 | 6.1628 | 100.7022
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6365 | 160.39 | 171.0265 | 10.3166 | 181.3432
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0641 | 184.4582 | 196.5222 | 11.7013 | 208.2235
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8119 | 233.8055 | 249.6173 | 15.3364 | 264.9537
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7445 | 264.2037 | 281.9481 | 17.2109 | 299.159
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.7178 | 350.7082 | 374.426 | 23.0046 | 397.4305
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2857 | 420.074 | 448.3597 | 27.4351 | 475.7948
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9663 | 505.2854 | 539.2517 | 32.9449 | 572.1966
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0569 | 597.7731 | 637.83 | 38.8523 | 676.6823
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1928 | 736.5046 | 785.6974 | 47.7134 | 833.4108
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5132 | 850.8212 | 907.3344 | 54.8138 | 962.1482
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2023 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2023
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4666 | 0.1329 |  | 5.5728
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87846 | 12.0782 | 12.9567 | 0.89552 | 13.8522
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1713 | 16.1043 | 17.2755 | 1.194 | 18.4696
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4934 | 20.2596 | 21.753 | 1.5224 | 23.2754
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9912 | 27.9239 | 29.915 | 2.0299 | 31.9449
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4011 | 32.4672 | 34.8683 | 2.4477 | 37.316
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6922 | 36.3215 | 39.0136 | 2.7444 | 41.7581
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1771 | 42.7263 | 45.9033 | 3.2388 | 49.1421
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.953 | 52.9854 | 56.9384 | 4.0298 | 60.9682
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0426 | 54.201 | 58.2436 | 4.1211 | 62.3647
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2294 | 56.7204 | 60.9499 | 4.3116 | 65.2614
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5451 | 60.9567 | 65.5018 | 4.6334 | 70.1351
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8607 | 65.1929 | 70.0537 | 4.9551 | 75.0088
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.032 | 81.2972 | 87.3292 | 6.1492 | 93.4784
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45739 | 6.5565 | 7.0139 | 0.46627 | 7.4802
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.70277 | 9.9359 | 10.6386 | 0.71642 | 11.3551
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4055 | 19.8717 | 21.2773 | 1.4328 | 22.7101
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7569 | 24.1564 | 25.9133 | 1.791 | 27.7043
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3425 | 32.2085 | 34.5511 | 2.388 | 36.9391
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4553 | 48.0542 | 51.5095 | 3.5224 | 55.0318
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1873 | 56.7529 | 60.9402 | 4.2686 | 65.2088
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.536 | 61.9005 | 66.4365 | 4.6241 | 71.0606
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8886 | 67.1195 | 72.0081 | 4.9835 | 76.9917
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2415 | 72.3399 | 77.5814 | 5.3433 | 82.9246
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3542 | 88.1856 | 94.5397 | 6.4776 | 101.0173
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6371 | 160.39 | 171.0271 | 10.8436 | 181.8707
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0647 | 184.4582 | 196.5228 | 12.299 | 208.8218
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8127 | 233.8055 | 249.6181 | 16.1198 | 265.7379
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7454 | 264.2037 | 281.9491 | 18.09 | 300.0391
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.719 | 350.7082 | 374.4272 | 24.1797 | 398.6069
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2872 | 420.074 | 448.3612 | 28.8366 | 477.1977
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9681 | 505.2854 | 539.2535 | 34.6278 | 573.8812
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.059 | 597.7731 | 637.8321 | 40.837 | 678.669
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1953 | 736.5046 | 785.6999 | 50.1507 | 835.8507
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5162 | 850.8212 | 907.3373 | 57.6138 | 964.9511
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2024 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2024
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4668 | 0.1329 |  | 5.7323
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87849 | 12.0782 | 12.9567 | 0.92115 | 13.8778
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1713 | 16.1043 | 17.2756 | 1.2282 | 18.5038
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4934 | 20.2596 | 21.7531 | 1.5659 | 23.319
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9913 | 27.9239 | 29.9151 | 2.0879 | 32.0031
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4012 | 32.4672 | 34.8684 | 2.5178 | 37.3861
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6923 | 36.3215 | 39.0138 | 2.823 | 41.8367
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1772 | 42.7263 | 45.9035 | 3.3315 | 49.2349
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9532 | 52.9854 | 56.9386 | 4.1451 | 61.0837
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0428 | 54.201 | 58.2438 | 4.2391 | 62.4829
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2296 | 56.7204 | 60.95 | 4.435 | 65.385
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5453 | 60.9567 | 65.502 | 4.766 | 70.2679
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8609 | 65.1929 | 70.0539 | 5.097 | 75.1508
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0323 | 81.2972 | 87.3295 | 6.3252 | 93.6546
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45741 | 6.5565 | 7.014 | 0.47962 | 7.4936
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.7028 | 9.9359 | 10.6387 | 0.73693 | 11.3756
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4056 | 19.8717 | 21.2773 | 1.4739 | 22.7512
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.757 | 24.1564 | 25.9134 | 1.8423 | 27.7557
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3426 | 32.2085 | 34.5512 | 2.4564 | 37.0076
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4554 | 48.0542 | 51.5096 | 3.6232 | 55.1328
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1875 | 56.7529 | 60.9403 | 4.3908 | 65.3311
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5362 | 61.9005 | 66.4367 | 4.7565 | 71.1932
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8888 | 67.1195 | 72.0084 | 5.1262 | 77.1345
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2417 | 72.3399 | 77.5816 | 5.4962 | 83.0778
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3545 | 88.1856 | 94.54 | 6.663 | 101.203
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6375 | 160.39 | 171.0275 | 11.154 | 182.1815
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0652 | 184.4582 | 196.5233 | 12.651 | 209.1743
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8134 | 233.8055 | 249.6188 | 16.5812 | 266.2
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7462 | 264.2037 | 281.9498 | 18.6078 | 300.5576
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.72 | 350.7082 | 374.4282 | 24.8717 | 399.2999
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2884 | 420.074 | 448.3623 | 29.6619 | 478.0242
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9695 | 505.2854 | 539.2549 | 35.6189 | 574.8738
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0607 | 597.7731 | 637.8337 | 42.0058 | 679.8395
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1974 | 736.5046 | 785.702 | 51.5861 | 837.2881
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5185 | 850.8212 | 907.3397 | 59.2628 | 966.6025
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2025 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2025
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4672 | 0.1329 |  | 5.7825
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87855 | 12.0782 | 12.9568 | 0.92922 | 13.886
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1714 | 16.1043 | 17.2757 | 1.239 | 18.5146
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4935 | 20.2596 | 21.7532 | 1.5797 | 23.3328
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9914 | 27.9239 | 29.9152 | 2.1063 | 32.0215
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4013 | 32.4672 | 34.8685 | 2.5399 | 37.4084
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6924 | 36.3215 | 39.0139 | 2.8477 | 41.8617
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1774 | 42.7263 | 45.9037 | 3.3607 | 49.2643
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9534 | 52.9854 | 56.9389 | 4.1815 | 61.1203
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.043 | 54.201 | 58.244 | 4.2762 | 62.5203
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2299 | 56.7204 | 60.9503 | 4.4739 | 65.4242
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5456 | 60.9567 | 65.5023 | 4.8078 | 70.31
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8612 | 65.1929 | 70.0542 | 5.1417 | 75.1958
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0326 | 81.2972 | 87.3299 | 6.3806 | 93.7105
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45744 | 6.5565 | 7.014 | 0.48382 | 7.4978
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.70285 | 9.9359 | 10.6387 | 0.74339 | 11.3821
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4057 | 19.8717 | 21.2774 | 1.4868 | 22.7642
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7571 | 24.1564 | 25.9135 | 1.8584 | 27.7719
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3428 | 32.2085 | 34.5513 | 2.4779 | 37.0293
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4556 | 48.0542 | 51.5098 | 3.655 | 55.1648
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1877 | 56.7529 | 60.9406 | 4.4293 | 65.3699
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5365 | 61.9005 | 66.437 | 4.7982 | 71.2352
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8891 | 67.1195 | 72.0087 | 5.1711 | 77.1798
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.242 | 72.3399 | 77.5819 | 5.5444 | 83.1263
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3549 | 88.1856 | 94.5404 | 6.7214 | 101.2618
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6382 | 160.39 | 171.0282 | 11.2518 | 182.28
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0659 | 184.4582 | 196.5241 | 12.7619 | 209.286
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8144 | 233.8055 | 249.6198 | 16.7266 | 266.3464
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7473 | 264.2037 | 281.9509 | 18.771 | 300.7219
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.7215 | 350.7082 | 374.4297 | 25.0898 | 399.5195
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2902 | 420.074 | 448.3641 | 29.922 | 478.2861
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9717 | 505.2854 | 539.2571 | 35.9312 | 575.1883
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0632 | 597.7731 | 637.8363 | 42.3741 | 680.2104
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.2005 | 736.5046 | 785.7051 | 52.0385 | 837.7436
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5221 | 850.8212 | 907.3433 | 59.7824 | 967.1257
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard