## VVM Energy Savings Estimates
Energy Savings Estimated from VVM System
1. Table below is from 2018 CoS application with normalized load forecast.
2018 CoS Rate Application Data | [5 empty] | Loss Factor | 1.0481
| Total Base Revenue Requirement | Class % | Number of Customers | 2018 Test Year Weather Normal kWh (Load Forecast) | Class % | kW | 2018 Test Year Weather Normal (kWh w/LF) | Class %
Res | 11226807 | 58.5% | 29816 | 288323799 | 45.85% |  | 302192173.7319 | 45.85%
GS<50kW | 3149458 | 16.41% | 3431 | 92411463 | 14.69% |  | 96856454.3703 | 14.69%
GS>50kW | 4544464 | 23.68% | 357 | 244620598 | 38.9% | 614743 | 256386848.7638 | 38.9%
Sentinel lights | 34742 | 0.181% | 354 | 209800 | 0.03336% | 593 | 219891.38 | 0.03336%
Street lights | 195345 | 1.018% | 8070 | 2398221 | 0.3813% | 7030 | 2513575.4301 | 0.3813%
USL | 39551 | 0.2061% | 22 | 944731 | 0.1502% |  | 990172.5611 | 0.1502%
| 19190367 | 100% |  | 628908612 | 100% |  | 659159116.2372 | 100%
2. VVM Energy Savings estimate is only applicable to customers on the 12.5 kV distribution network with intended design & application.
3. A reduction of the energy consumption above in the GS>50kW customers connected to the 34.5kV subtransmission network is thus needed .
4. The 7 customers for above annual energy consumption was totaled across two years and an average of 41,744,343.60 kWh used.
5. Note: as actual consumption in period was above Normalized this creates a more conservative estimate on total energy saved by VVM.
6. The Table below shows where the reduction applied results in 617,414,773 kWh energy for VVM targeted customers on the LV customers.
2018 CoS Rate Application Data - adjusting 34.5kV load | [5 empty] | Loss Factor | 1.0481
| Total Base Revenue Requirement | Class % | Number of Customers | 2018 Test Year Weather Normal kWh (Load Forecast) | Class % | kW | 2018 Test Year Weather Normal (kWh w/LF) | Class % | Reduce GS>50kW 34.5kV (no VVM) | LV Feeder Energy Consumption Base for VVM
Res | 11226807 | 58.5% | 29816 | 288323799 | 45.85% |  | 302192173.7319 | 45.85% |  | 302192173.7319
GS<50kW | 3149458 | 16.41% | 3431 | 92411463 | 14.69% |  | 96856454.3703 | 14.69% |  | 96856454.3703
GS>50kW | 4544464 | 23.68% | 357 | 244620598 | 38.9% | 614743 | 256386848.7638 | 38.9% | 41744343.6 | 214642505.1638
Sentinel lights | 34742 | 0.181% | 354 | 209800 | 0.03336% | 593 | 219891.38 | 0.03336% |  | 219891.38
Street lights | 195345 | 1.018% | 8070 | 2398221 | 0.3813% | 7030 | 2513575.4301 | 0.3813% |  | 2513575.4301
USL | 39551 | 0.2061% | 22 | 944731 | 0.1502% |  | 990172.5611 | 0.1502% |  | 990172.5611
| 19190367 | 100% |  | 628908612 | 100% |  | 659159116.2372 | 100% | 16.28% | 617414772.6372
7. The Cost of Power forecast from the 2018 CoS rate Applcation was used in original application for estimating energy $ savings.
2018 CoS Cost of Power (CoS Application)
| Total | Residential | GS <50 | GS>50-Regular | GS> 50-TOU |  | GS >50-Intermediate | Large Use >5MW | Street Light | Sentinel | Unmetered Scattered Load
Cost of Power (COP*) | 77725426 | 35945091 | 11467389 | 29880767 | 0 |  | 0 | 0 | 288889 | 25865 | 117425
(*) gross w/loss factor
REDUCE GS>50kW by 16.3% |  |  |  | 4865120.8543
Revised COP | 72860305.1457 | 35945091 | 11467389 | 25015646.1457 | 0 |  | 0 | 0 | 288889 | 25865 | 117425
Estimate for VVM customers
8. Table below uses the current Cost of Power forecast with updated IESO rates as provided below and the 16.3% reduction in energy from the GS>50kW class kWh used to get balance for VVM customers.
2020 CoS Cost of Power (uses 2019 IESO rates)
| Total | Residential | GS <50 | GS>50-Regular | GS> 50-TOU |  | GS >50-Intermediate | Large Use >5MW | Street Light | Sentinel | Unmetered Scattered Load
Cost of Power (COP*) | 88047743 | 40624176 | 12936129 | 33995412 | 0 |  | 0 | 0 | 330827 | 29119 | 132080
(*) gross w/loss factor | 0.13358 | Avg rate
REDUCE GS>50kW by 16.3% |  |  |  | 5535058.316
Revised COP | 82512684.684 | 40624176 | 12936129 | 28460353.684 | 0 | 0 | 0 | 0 | 330827 | 29119 | 132080
Estimate for VVM customers
9. Next table describes the VVM energy and $ savings estimated to be achieved by the VVM system.
ENTER VALUES | CVR factor | 0.9 |  |  | System Energy Loss Savings Estimate kWh |  |  | 2.6% | 786513.1102
| Voltage Savings | 3 | volts |  | Using avg $/kWh from COP |  |  | 0.13364 | 105111.363
| Energy Savings | 2.7 | %
Total $'s saved with VVM | 2227842.4865 | 1096852.752 | 349275.483 | 768429.5495 | 0 | 0 | 0 | 0 | 8932.329 | 786.213 | 3566.16
Total VVM w/Syst losses included | 2332953.8494
Total kWh saved with VVM | 16670198.8612 | 8159188.6908 | 2615124.268 | 5795347.6394 | 0 | 0 | 0 | 0 | 67866.5366 | 5937.0673 | 26734.6591
Total kWh saved with losses incl. | 17456711.9714