## 2021-FULL
Dry Core Transformer Losses Proposed for 2021
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.466 | 0.1399 |  | 4.9376
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87836 | 12.7144 | 13.5927 | 0.79345 | 14.3862
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1712 | 16.9525 | 18.1237 | 1.0579 | 19.1816
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4932 | 21.3267 | 22.82 | 1.3489 | 24.1688
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.991 | 29.3946 | 31.3856 | 1.7985 | 33.1841
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4008 | 34.1772 | 36.5781 | 2.1687 | 38.7468
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6919 | 38.2346 | 40.9265 | 2.4316 | 43.3581 |  | UPDATED - DEC 1, 2020 - Draft Rate Order
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1767 | 44.9767 | 48.1535 | 2.8696 | 51.0231 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9526 | 55.7762 | 59.7288 | 3.5705 | 63.2993 | GS 50 to 1,499 kW | 0.01964 | 3.1059 | 1.9644 | 5.2905
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0422 | 57.0558 | 61.098 | 3.6514 | 64.7494 | GS 1,500 to 4,999 kW | 0.02099 | 3.2248 | 2.0995 | 4.8106
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.229 | 59.708 | 63.937 | 3.8201 | 67.7571 | Large Use | 0.02364 | 3.5749 | 2.3643 | 4.7117
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5446 | 64.1674 | 68.712 | 4.1053 | 72.8172
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8602 | 68.6267 | 73.487 | 4.3904 | 77.8773
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0314 | 85.5792 | 91.6106 | 5.4483 | 97.0589 | Tier 1 | 0.126
[14 empty] | Tier 2 | 0.146
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45734 | 6.9019 | 7.3592 | 0.41313 | 7.7724
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.7027 | 10.4592 | 11.1619 | 0.63477 | 11.7967 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4054 | 20.9184 | 22.3238 | 1.2695 | 23.5933 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7567 | 25.4288 | 27.1855 | 1.5869 | 28.7724 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3423 | 33.905 | 36.2473 | 2.1159 | 38.3632
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4549 | 50.5853 | 54.0402 | 3.1209 | 57.1611
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1868 | 59.7421 | 63.929 | 3.7821 | 67.711
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5356 | 65.1608 | 69.6964 | 4.0971 | 73.7935
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8881 | 70.6548 | 75.5429 | 4.4155 | 79.9584
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2409 | 76.1501 | 81.391 | 4.7342 | 86.1253
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3535 | 92.8304 | 99.1839 | 5.7393 | 104.9232
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6359 | 168.8379 | 179.4739 | 9.6077 | 189.0816
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0634 | 194.1738 | 206.2372 | 10.8972 | 217.1344
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.811 | 246.1203 | 261.9313 | 14.2825 | 276.2138
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7435 | 278.1196 | 295.8631 | 16.0282 | 311.8913
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.7165 | 369.1804 | 392.8969 | 21.4238 | 414.3207
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2842 | 442.1997 | 470.484 | 25.5499 | 496.0338
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9645 | 531.8994 | 565.8639 | 30.681 | 596.5449
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0547 | 629.2585 | 669.3132 | 36.1825 | 705.4957
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1901 | 775.2972 | 824.4873 | 44.4347 | 868.922
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5102 | 895.6349 | 952.1451 | 51.0471 | 1003.1923
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2022-FULL
Dry Core Transformer Losses Proposed for 2022
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4663 | 0.1399 |  | 5.2594
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87841 | 12.7144 | 13.5928 | 0.84516 | 14.438
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1712 | 16.9525 | 18.1237 | 1.1269 | 19.2506
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4933 | 21.3267 | 22.82 | 1.4368 | 24.2568
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9911 | 29.3946 | 31.3857 | 1.9157 | 33.3014
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.401 | 34.1772 | 36.5782 | 2.3101 | 38.8883
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.692 | 38.2346 | 40.9266 | 2.5901 | 43.5167 |  | UPDATED - DEC 1, 2020 - Draft Rate Order
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1769 | 44.9767 | 48.1536 | 3.0567 | 51.2103 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9528 | 55.7762 | 59.729 | 3.8032 | 63.5322 | GS 50 to 1,499 kW | 0.01991 | 3.1059 | 1.9644 | 5.6065
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0424 | 57.0558 | 61.0982 | 3.8894 | 64.9876 | GS 1,500 to 4,999 kW | 0.02128 | 3.2248 | 2.0995 | 5.1311
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2292 | 59.708 | 63.9372 | 4.0691 | 68.0063 | Large Use | 0.02396 | 3.5749 | 2.3643 | 5.0407
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5448 | 64.1674 | 68.7122 | 4.3728 | 73.085
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8605 | 68.6267 | 73.4872 | 4.6765 | 78.1637
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0317 | 85.5792 | 91.6109 | 5.8034 | 97.4143 | Tier 1 | 0.126
[14 empty] | Tier 2 | 0.146
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45737 | 6.9019 | 7.3593 | 0.44006 | 7.7993
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.70274 | 10.4592 | 11.1619 | 0.67614 | 11.8381 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4055 | 20.9184 | 22.3239 | 1.3523 | 23.6761 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7568 | 25.4288 | 27.1856 | 1.6903 | 28.8759 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3424 | 33.905 | 36.2474 | 2.2538 | 38.5012
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4551 | 50.5853 | 54.0404 | 3.3243 | 57.3647
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1871 | 59.7421 | 63.9292 | 4.0286 | 67.9578
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5358 | 65.1608 | 69.6966 | 4.3641 | 74.0608
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8883 | 70.6548 | 75.5432 | 4.7033 | 80.2465
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2412 | 76.1501 | 81.3913 | 5.0428 | 86.4341
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3539 | 92.8304 | 99.1842 | 6.1134 | 105.2976
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6365 | 168.8379 | 179.4744 | 10.2339 | 189.7084
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0641 | 194.1738 | 206.2378 | 11.6075 | 217.8453
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8119 | 246.1203 | 261.9321 | 15.2134 | 277.1456
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7445 | 278.1196 | 295.8641 | 17.0729 | 312.937
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.7178 | 369.1804 | 392.8982 | 22.8202 | 415.7184
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2857 | 442.1997 | 470.4855 | 27.2152 | 497.7007
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9663 | 531.8994 | 565.8657 | 32.6808 | 598.5465
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0569 | 629.2585 | 669.3154 | 38.5409 | 707.8563
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1928 | 775.2972 | 824.49 | 47.331 | 871.8209
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5132 | 895.6349 | 952.1482 | 54.3744 | 1006.5225
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2023-FULL
Dry Core Transformer Losses Proposed for 2023
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4666 | 0.1399 |  | 5.5484
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87846 | 12.7144 | 13.5928 | 0.8916 | 14.4844
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1713 | 16.9525 | 18.1238 | 1.1888 | 19.3126
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4934 | 21.3267 | 22.8201 | 1.5157 | 24.3358
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9912 | 29.3946 | 31.3858 | 2.021 | 33.4068
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4011 | 34.1772 | 36.5783 | 2.437 | 39.0154
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6922 | 38.2346 | 40.9267 | 2.7324 | 43.6592 |  | UPDATED - DEC 1, 2020 - Draft Rate Order
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1771 | 44.9767 | 48.1538 | 3.2246 | 51.3784 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.953 | 55.7762 | 59.7292 | 4.0122 | 63.7414 | GS 50 to 1,499 kW | 0.02017 | 3.1059 | 1.9644 | 5.8902
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0426 | 57.0558 | 61.0984 | 4.1031 | 65.2016 | GS 1,500 to 4,999 kW | 0.02156 | 3.2248 | 2.0995 | 5.4149
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2294 | 59.708 | 63.9374 | 4.2927 | 68.2301 | Large Use | 0.02427 | 3.5749 | 2.3643 | 5.3401
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5451 | 64.1674 | 68.7124 | 4.6131 | 73.3255
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8607 | 68.6267 | 73.4875 | 4.9335 | 78.4209
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.032 | 85.5792 | 91.6112 | 6.1223 | 97.7335 | Tier 1 | 0.126
[14 empty] | Tier 2 | 0.146
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45739 | 6.9019 | 7.3593 | 0.46423 | 7.8235
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.70277 | 10.4592 | 11.162 | 0.71329 | 11.8753 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4055 | 20.9184 | 22.3239 | 1.4266 | 23.7505 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7569 | 25.4288 | 27.1857 | 1.7832 | 28.9689 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3425 | 33.905 | 36.2476 | 2.3776 | 38.6252
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4553 | 50.5853 | 54.0405 | 3.507 | 57.5475
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1873 | 59.7421 | 63.9294 | 4.2499 | 68.1793
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.536 | 65.1608 | 69.6969 | 4.6039 | 74.3008
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8886 | 70.6548 | 75.5434 | 4.9618 | 80.5052
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2415 | 76.1501 | 81.3916 | 5.3199 | 86.7115
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3542 | 92.8304 | 99.1846 | 6.4493 | 105.6338
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6371 | 168.8379 | 179.475 | 10.7962 | 190.2712
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0647 | 194.1738 | 206.2385 | 12.2452 | 218.4837
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8127 | 246.1203 | 261.933 | 16.0493 | 277.9823
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7454 | 278.1196 | 295.865 | 18.0109 | 313.8759
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.719 | 369.1804 | 392.8994 | 24.074 | 416.9734
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2872 | 442.1997 | 470.4869 | 28.7105 | 499.1974
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9681 | 531.8994 | 565.8674 | 34.4764 | 600.3438
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.059 | 629.2585 | 669.3175 | 40.6584 | 709.9759
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1953 | 775.2972 | 824.4925 | 49.9314 | 874.4239
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5162 | 895.6349 | 952.1511 | 57.3619 | 1009.5129
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2024-FULL
Dry Core Transformer Losses Proposed for 2024
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4668 | 0.1399 |  | 5.728
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87849 | 12.7144 | 13.5929 | 0.92046 | 14.5133
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1713 | 16.9525 | 18.1238 | 1.2273 | 19.3511
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4934 | 21.3267 | 22.8202 | 1.5648 | 24.3849
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9913 | 29.3946 | 31.3859 | 2.0864 | 33.4723
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4012 | 34.1772 | 36.5784 | 2.5159 | 39.0943
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6923 | 38.2346 | 40.9269 | 2.8209 | 43.7477 |  | UPDATED - DEC 1, 2020 - Draft Rate Order
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1772 | 44.9767 | 48.1539 | 3.329 | 51.4829 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9532 | 55.7762 | 59.7294 | 4.142 | 63.8714 | GS 50 to 1,499 kW | 0.02038 | 3.1059 | 1.9644 | 6.0448
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0428 | 57.0558 | 61.0986 | 4.2359 | 65.3345 | GS 1,500 to 4,999 kW | 0.02178 | 3.2248 | 2.0995 | 5.5944
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2296 | 59.708 | 63.9376 | 4.4316 | 68.3692 | Large Use | 0.02453 | 3.5749 | 2.3643 | 5.5447
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5453 | 64.1674 | 68.7126 | 4.7624 | 73.475
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8609 | 68.6267 | 73.4877 | 5.0931 | 78.5808
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0323 | 85.5792 | 91.6115 | 6.3204 | 97.9319 | Tier 1 | 0.126
[14 empty] | Tier 2 | 0.146
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45741 | 6.9019 | 7.3593 | 0.47926 | 7.8386
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.7028 | 10.4592 | 11.162 | 0.73637 | 11.8984 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4056 | 20.9184 | 22.324 | 1.4727 | 23.7967 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.757 | 25.4288 | 27.1857 | 1.8409 | 29.0266 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3426 | 33.905 | 36.2476 | 2.4545 | 38.7022
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4554 | 50.5853 | 54.0407 | 3.6205 | 57.6612
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1875 | 59.7421 | 63.9296 | 4.3875 | 68.3171
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5362 | 65.1608 | 69.6971 | 4.7529 | 74.45
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8888 | 70.6548 | 75.5436 | 5.1223 | 80.6659
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2417 | 76.1501 | 81.3918 | 5.4921 | 86.8839
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3545 | 92.8304 | 99.1848 | 6.658 | 105.8428
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6375 | 168.8379 | 179.4754 | 11.1456 | 190.6211
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0652 | 194.1738 | 206.239 | 12.6415 | 218.8805
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8134 | 246.1203 | 261.9336 | 16.5687 | 278.5023
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7462 | 278.1196 | 295.8657 | 18.5938 | 314.4596
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.72 | 369.1804 | 392.9004 | 24.8531 | 417.7535
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2884 | 442.1997 | 470.4881 | 29.6396 | 500.1278
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9695 | 531.8994 | 565.8689 | 35.5922 | 601.461
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0607 | 629.2585 | 669.3192 | 41.9743 | 711.2934
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1974 | 775.2972 | 824.4946 | 51.5474 | 876.042
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5185 | 895.6349 | 952.1535 | 59.2183 | 1011.3718
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2025-FULL
Dry Core Transformer Losses Proposed for 2025
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4672 | 0.1399 |  | 5.8191
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87855 | 12.7144 | 13.5929 | 0.93509 | 14.528
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1714 | 16.9525 | 18.1239 | 1.2468 | 19.3707
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4935 | 21.3267 | 22.8203 | 1.5897 | 24.4099
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9914 | 29.3946 | 31.386 | 2.1196 | 33.5056
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4013 | 34.1772 | 36.5786 | 2.5559 | 39.1345
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6924 | 38.2346 | 40.927 | 2.8657 | 43.7928 |  | UPDATED - DEC 1, 2020 - Draft Rate Order
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1774 | 44.9767 | 48.1541 | 3.3819 | 51.536 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9534 | 55.7762 | 59.7297 | 4.2079 | 63.9375 | GS 50 to 1,499 kW | 0.0207 | 3.1059 | 1.9644 | 6.127
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.043 | 57.0558 | 61.0989 | 4.3033 | 65.4021 | GS 1,500 to 4,999 kW | 0.02212 | 3.2248 | 2.0995 | 5.6776
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2299 | 59.708 | 63.9379 | 4.5021 | 68.44 | Large Use | 0.02491 | 3.5749 | 2.3643 | 5.6526
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5456 | 64.1674 | 68.7129 | 4.8381 | 73.551
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8612 | 68.6267 | 73.488 | 5.1741 | 78.6621
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0326 | 85.5792 | 91.6119 | 6.4209 | 98.0328 | Tier 1 | 0.126
[14 empty] | Tier 2 | 0.146
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45744 | 6.9019 | 7.3593 | 0.48688 | 7.8462
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.70285 | 10.4592 | 11.162 | 0.74808 | 11.9101 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4057 | 20.9184 | 22.3241 | 1.4962 | 23.8202 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7571 | 25.4288 | 27.1858 | 1.8702 | 29.056 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3428 | 33.905 | 36.2478 | 2.4936 | 38.7414
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4556 | 50.5853 | 54.0409 | 3.6781 | 57.719
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1877 | 59.7421 | 63.9298 | 4.4573 | 68.3871
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5365 | 65.1608 | 69.6974 | 4.8285 | 74.5259
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8891 | 70.6548 | 75.5439 | 5.2038 | 80.7477
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.242 | 76.1501 | 81.3921 | 5.5794 | 86.9716
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3549 | 92.8304 | 99.1852 | 6.7639 | 105.9491
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6382 | 168.8379 | 179.4761 | 11.3229 | 190.799
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0659 | 194.1738 | 206.2397 | 12.8426 | 219.0823
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8144 | 246.1203 | 261.9346 | 16.8322 | 278.7669
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7473 | 278.1196 | 295.8668 | 18.8896 | 314.7564
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.7215 | 369.1804 | 392.9019 | 25.2483 | 418.1503
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2902 | 442.1997 | 470.4899 | 30.1111 | 500.601
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9717 | 531.8994 | 565.871 | 36.1582 | 602.0293
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0632 | 629.2585 | 669.3217 | 42.6418 | 711.9635
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.2005 | 775.2972 | 824.4977 | 52.3672 | 876.8649
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5221 | 895.6349 | 952.1571 | 60.1601 | 1012.3172
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1
New Transformers added 2021

## 2021 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2021
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.466 | 0.1399 |  | 4.9376
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87836 | 12.7144 | 13.5927 | 0.79345 | 14.3862
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1712 | 16.9525 | 18.1237 | 1.0579 | 19.1816
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4932 | 21.3267 | 22.82 | 1.3489 | 24.1688
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.991 | 29.3946 | 31.3856 | 1.7985 | 33.1841
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4008 | 34.1772 | 36.5781 | 2.1687 | 38.7468
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6919 | 38.2346 | 40.9265 | 2.4316 | 43.3581
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1767 | 44.9767 | 48.1535 | 2.8696 | 51.0231
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9526 | 55.7762 | 59.7288 | 3.5705 | 63.2993
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0422 | 57.0558 | 61.098 | 3.6514 | 64.7494
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.229 | 59.708 | 63.937 | 3.8201 | 67.7571
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5446 | 64.1674 | 68.712 | 4.1053 | 72.8172
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8602 | 68.6267 | 73.487 | 4.3904 | 77.8773
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0314 | 85.5792 | 91.6106 | 5.4483 | 97.0589
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45734 | 6.9019 | 7.3592 | 0.41313 | 7.7724
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.7027 | 10.4592 | 11.1619 | 0.63477 | 11.7967
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4054 | 20.9184 | 22.3238 | 1.2695 | 23.5933
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7567 | 25.4288 | 27.1855 | 1.5869 | 28.7724
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3423 | 33.905 | 36.2473 | 2.1159 | 38.3632
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4549 | 50.5853 | 54.0402 | 3.1209 | 57.1611
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1868 | 59.7421 | 63.929 | 3.7821 | 67.711
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5356 | 65.1608 | 69.6964 | 4.0971 | 73.7935
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8881 | 70.6548 | 75.5429 | 4.4155 | 79.9584
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2409 | 76.1501 | 81.391 | 4.7342 | 86.1253
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3535 | 92.8304 | 99.1839 | 5.7393 | 104.9232
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6359 | 168.8379 | 179.4739 | 9.6077 | 189.0816
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0634 | 194.1738 | 206.2372 | 10.8972 | 217.1344
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.811 | 246.1203 | 261.9313 | 14.2825 | 276.2138
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7435 | 278.1196 | 295.8631 | 16.0282 | 311.8913
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.7165 | 369.1804 | 392.8969 | 21.4238 | 414.3207
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2842 | 442.1997 | 470.484 | 25.5499 | 496.0338
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9645 | 531.8994 | 565.8639 | 30.681 | 596.5449
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0547 | 629.2585 | 669.3132 | 36.1825 | 705.4957
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1901 | 775.2972 | 824.4873 | 44.4347 | 868.922
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5102 | 895.6349 | 952.1451 | 51.0471 | 1003.1923
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2022 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2022
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4663 | 0.1399 |  | 5.2594
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87841 | 12.7144 | 13.5928 | 0.84516 | 14.438
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1712 | 16.9525 | 18.1237 | 1.1269 | 19.2506
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4933 | 21.3267 | 22.82 | 1.4368 | 24.2568
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9911 | 29.3946 | 31.3857 | 1.9157 | 33.3014
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.401 | 34.1772 | 36.5782 | 2.3101 | 38.8883
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.692 | 38.2346 | 40.9266 | 2.5901 | 43.5167
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1769 | 44.9767 | 48.1536 | 3.0567 | 51.2103
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9528 | 55.7762 | 59.729 | 3.8032 | 63.5322
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0424 | 57.0558 | 61.0982 | 3.8894 | 64.9876
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2292 | 59.708 | 63.9372 | 4.0691 | 68.0063
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5448 | 64.1674 | 68.7122 | 4.3728 | 73.085
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8605 | 68.6267 | 73.4872 | 4.6765 | 78.1637
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0317 | 85.5792 | 91.6109 | 5.8034 | 97.4143
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45737 | 6.9019 | 7.3593 | 0.44006 | 7.7993
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.70274 | 10.4592 | 11.1619 | 0.67614 | 11.8381
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4055 | 20.9184 | 22.3239 | 1.3523 | 23.6761
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7568 | 25.4288 | 27.1856 | 1.6903 | 28.8759
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3424 | 33.905 | 36.2474 | 2.2538 | 38.5012
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4551 | 50.5853 | 54.0404 | 3.3243 | 57.3647
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1871 | 59.7421 | 63.9292 | 4.0286 | 67.9578
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5358 | 65.1608 | 69.6966 | 4.3641 | 74.0608
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8883 | 70.6548 | 75.5432 | 4.7033 | 80.2465
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2412 | 76.1501 | 81.3913 | 5.0428 | 86.4341
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3539 | 92.8304 | 99.1842 | 6.1134 | 105.2976
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6365 | 168.8379 | 179.4744 | 10.2339 | 189.7084
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0641 | 194.1738 | 206.2378 | 11.6075 | 217.8453
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8119 | 246.1203 | 261.9321 | 15.2134 | 277.1456
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7445 | 278.1196 | 295.8641 | 17.0729 | 312.937
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.7178 | 369.1804 | 392.8982 | 22.8202 | 415.7184
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2857 | 442.1997 | 470.4855 | 27.2152 | 497.7007
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9663 | 531.8994 | 565.8657 | 32.6808 | 598.5465
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0569 | 629.2585 | 669.3154 | 38.5409 | 707.8563
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1928 | 775.2972 | 824.49 | 47.331 | 871.8209
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5132 | 895.6349 | 952.1482 | 54.3744 | 1006.5225
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2023 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2023
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4666 | 0.1399 |  | 5.5484
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87846 | 12.7144 | 13.5928 | 0.8916 | 14.4844
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1713 | 16.9525 | 18.1238 | 1.1888 | 19.3126
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4934 | 21.3267 | 22.8201 | 1.5157 | 24.3358
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9912 | 29.3946 | 31.3858 | 2.021 | 33.4068
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4011 | 34.1772 | 36.5783 | 2.437 | 39.0154
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6922 | 38.2346 | 40.9267 | 2.7324 | 43.6592
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1771 | 44.9767 | 48.1538 | 3.2246 | 51.3784
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.953 | 55.7762 | 59.7292 | 4.0122 | 63.7414
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0426 | 57.0558 | 61.0984 | 4.1031 | 65.2016
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2294 | 59.708 | 63.9374 | 4.2927 | 68.2301
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5451 | 64.1674 | 68.7124 | 4.6131 | 73.3255
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8607 | 68.6267 | 73.4875 | 4.9335 | 78.4209
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.032 | 85.5792 | 91.6112 | 6.1223 | 97.7335
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45739 | 6.9019 | 7.3593 | 0.46423 | 7.8235
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.70277 | 10.4592 | 11.162 | 0.71329 | 11.8753
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4055 | 20.9184 | 22.3239 | 1.4266 | 23.7505
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7569 | 25.4288 | 27.1857 | 1.7832 | 28.9689
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3425 | 33.905 | 36.2476 | 2.3776 | 38.6252
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4553 | 50.5853 | 54.0405 | 3.507 | 57.5475
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1873 | 59.7421 | 63.9294 | 4.2499 | 68.1793
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.536 | 65.1608 | 69.6969 | 4.6039 | 74.3008
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8886 | 70.6548 | 75.5434 | 4.9618 | 80.5052
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2415 | 76.1501 | 81.3916 | 5.3199 | 86.7115
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3542 | 92.8304 | 99.1846 | 6.4493 | 105.6338
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6371 | 168.8379 | 179.475 | 10.7962 | 190.2712
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0647 | 194.1738 | 206.2385 | 12.2452 | 218.4837
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8127 | 246.1203 | 261.933 | 16.0493 | 277.9823
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7454 | 278.1196 | 295.865 | 18.0109 | 313.8759
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.719 | 369.1804 | 392.8994 | 24.074 | 416.9734
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2872 | 442.1997 | 470.4869 | 28.7105 | 499.1974
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9681 | 531.8994 | 565.8674 | 34.4764 | 600.3438
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.059 | 629.2585 | 669.3175 | 40.6584 | 709.9759
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1953 | 775.2972 | 824.4925 | 49.9314 | 874.4239
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5162 | 895.6349 | 952.1511 | 57.3619 | 1009.5129
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2024 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2024
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4668 | 0.1399 |  | 5.728
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87849 | 12.7144 | 13.5929 | 0.92046 | 14.5133
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1713 | 16.9525 | 18.1238 | 1.2273 | 19.3511
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4934 | 21.3267 | 22.8202 | 1.5648 | 24.3849
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9913 | 29.3946 | 31.3859 | 2.0864 | 33.4723
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4012 | 34.1772 | 36.5784 | 2.5159 | 39.0943
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6923 | 38.2346 | 40.9269 | 2.8209 | 43.7477
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1772 | 44.9767 | 48.1539 | 3.329 | 51.4829
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9532 | 55.7762 | 59.7294 | 4.142 | 63.8714
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0428 | 57.0558 | 61.0986 | 4.2359 | 65.3345
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2296 | 59.708 | 63.9376 | 4.4316 | 68.3692
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5453 | 64.1674 | 68.7126 | 4.7624 | 73.475
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8609 | 68.6267 | 73.4877 | 5.0931 | 78.5808
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0323 | 85.5792 | 91.6115 | 6.3204 | 97.9319
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45741 | 6.9019 | 7.3593 | 0.47926 | 7.8386
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.7028 | 10.4592 | 11.162 | 0.73637 | 11.8984
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4056 | 20.9184 | 22.324 | 1.4727 | 23.7967
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.757 | 25.4288 | 27.1857 | 1.8409 | 29.0266
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3426 | 33.905 | 36.2476 | 2.4545 | 38.7022
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4554 | 50.5853 | 54.0407 | 3.6205 | 57.6612
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1875 | 59.7421 | 63.9296 | 4.3875 | 68.3171
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5362 | 65.1608 | 69.6971 | 4.7529 | 74.45
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8888 | 70.6548 | 75.5436 | 5.1223 | 80.6659
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2417 | 76.1501 | 81.3918 | 5.4921 | 86.8839
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3545 | 92.8304 | 99.1848 | 6.658 | 105.8428
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6375 | 168.8379 | 179.4754 | 11.1456 | 190.6211
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0652 | 194.1738 | 206.239 | 12.6415 | 218.8805
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8134 | 246.1203 | 261.9336 | 16.5687 | 278.5023
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7462 | 278.1196 | 295.8657 | 18.5938 | 314.4596
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.72 | 369.1804 | 392.9004 | 24.8531 | 417.7535
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2884 | 442.1997 | 470.4881 | 29.6396 | 500.1278
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9695 | 531.8994 | 565.8689 | 35.5922 | 601.461
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0607 | 629.2585 | 669.3192 | 41.9743 | 711.2934
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1974 | 775.2972 | 824.4946 | 51.5474 | 876.042
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5185 | 895.6349 | 952.1535 | 59.2183 | 1011.3718
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2025 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2025
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4672 | 0.1399 |  | 5.8191
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87855 | 12.7144 | 13.5929 | 0.93509 | 14.528
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1714 | 16.9525 | 18.1239 | 1.2468 | 19.3707
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4935 | 21.3267 | 22.8203 | 1.5897 | 24.4099
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9914 | 29.3946 | 31.386 | 2.1196 | 33.5056
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4013 | 34.1772 | 36.5786 | 2.5559 | 39.1345
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6924 | 38.2346 | 40.927 | 2.8657 | 43.7928
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1774 | 44.9767 | 48.1541 | 3.3819 | 51.536
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9534 | 55.7762 | 59.7297 | 4.2079 | 63.9375
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.043 | 57.0558 | 61.0989 | 4.3033 | 65.4021
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2299 | 59.708 | 63.9379 | 4.5021 | 68.44
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5456 | 64.1674 | 68.7129 | 4.8381 | 73.551
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8612 | 68.6267 | 73.488 | 5.1741 | 78.6621
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0326 | 85.5792 | 91.6119 | 6.4209 | 98.0328
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45744 | 6.9019 | 7.3593 | 0.48688 | 7.8462
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.70285 | 10.4592 | 11.162 | 0.74808 | 11.9101
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4057 | 20.9184 | 22.3241 | 1.4962 | 23.8202
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7571 | 25.4288 | 27.1858 | 1.8702 | 29.056
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3428 | 33.905 | 36.2478 | 2.4936 | 38.7414
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4556 | 50.5853 | 54.0409 | 3.6781 | 57.719
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1877 | 59.7421 | 63.9298 | 4.4573 | 68.3871
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5365 | 65.1608 | 69.6974 | 4.8285 | 74.5259
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8891 | 70.6548 | 75.5439 | 5.2038 | 80.7477
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.242 | 76.1501 | 81.3921 | 5.5794 | 86.9716
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3549 | 92.8304 | 99.1852 | 6.7639 | 105.9491
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6382 | 168.8379 | 179.4761 | 11.3229 | 190.799
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0659 | 194.1738 | 206.2397 | 12.8426 | 219.0823
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8144 | 246.1203 | 261.9346 | 16.8322 | 278.7669
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7473 | 278.1196 | 295.8668 | 18.8896 | 314.7564
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.7215 | 369.1804 | 392.9019 | 25.2483 | 418.1503
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2902 | 442.1997 | 470.4899 | 30.1111 | 500.601
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9717 | 531.8994 | 565.871 | 36.1582 | 602.0293
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0632 | 629.2585 | 669.3217 | 42.6418 | 711.9635
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.2005 | 775.2972 | 824.4977 | 52.3672 | 876.8649
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5221 | 895.6349 | 952.1571 | 60.1601 | 1012.3172
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard