## 2021-FULL
Dry Core Transformer Losses Proposed for 2021
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.466 | 0.1134 |  | 4.9376
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87836 | 10.306 | 11.1844 | 0.79345 | 11.9778
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1712 | 13.7413 | 14.9125 | 1.0579 | 15.9704
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4932 | 17.287 | 18.7802 | 1.3489 | 20.1291
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.991 | 23.8267 | 25.8176 | 1.7985 | 27.6161
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4008 | 27.7034 | 30.1042 | 2.1687 | 32.2729
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6919 | 30.9922 | 33.684 | 2.4316 | 36.1157 |  | UPDATED - DEC 16, 2020 - Draft Rate Order - RPP Update
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1767 | 36.4572 | 39.6339 | 2.8696 | 42.5035 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9526 | 45.211 | 49.1636 | 3.5705 | 52.7341 | GS 50 to 1,499 kW | 0.01964 | 3.1059 | 1.9644 | 5.2905
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0422 | 46.2483 | 50.2904 | 3.6514 | 53.9419 | GS 1,500 to 4,999 kW | 0.02099 | 3.2248 | 2.0995 | 4.8106
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.229 | 48.398 | 52.627 | 3.8201 | 56.4472 | Large Use | 0.02364 | 3.5749 | 2.3643 | 4.7117
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5446 | 52.0127 | 56.5573 | 4.1053 | 60.6626
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8602 | 55.6274 | 60.4876 | 4.3904 | 64.878
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0314 | 69.3687 | 75.4001 | 5.4483 | 80.8484 | Tier 1 | 0.101
[14 empty] | Tier 2 | 0.118
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45734 | 5.5945 | 6.0519 | 0.41313 | 6.465
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.7027 | 8.478 | 9.1807 | 0.63477 | 9.8155 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4054 | 16.956 | 18.3614 | 1.2695 | 19.6309 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7567 | 20.612 | 22.3687 | 1.5869 | 23.9556 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3423 | 27.4827 | 29.825 | 2.1159 | 31.9408
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4549 | 41.0034 | 44.4583 | 3.1209 | 47.5792
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1868 | 48.4257 | 52.6125 | 3.7821 | 56.3946
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5356 | 52.818 | 57.3536 | 4.0971 | 61.4507
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8881 | 57.2713 | 62.1594 | 4.4155 | 66.5749
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2409 | 61.7257 | 66.9666 | 4.7342 | 71.7008
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3535 | 75.2464 | 81.5999 | 5.7393 | 87.3392
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6359 | 136.8565 | 147.4924 | 9.6077 | 157.1001
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0634 | 157.3932 | 169.4566 | 10.8972 | 180.3538
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.811 | 199.4999 | 215.3109 | 14.2825 | 229.5934
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7435 | 225.4379 | 243.1814 | 16.0282 | 259.2096
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.7165 | 299.2499 | 322.9664 | 21.4238 | 344.3902
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2842 | 358.4378 | 386.722 | 25.5499 | 412.2719
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9645 | 431.1464 | 465.1109 | 30.681 | 495.792
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0547 | 510.0637 | 550.1185 | 36.1825 | 586.3009
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1901 | 628.4396 | 677.6297 | 44.4347 | 722.0644
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5102 | 725.9828 | 782.4931 | 51.0471 | 833.5402
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2022-FULL
Dry Core Transformer Losses Proposed for 2022
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4663 | 0.1134 |  | 5.2594
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87841 | 10.306 | 11.1844 | 0.84516 | 12.0296
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1712 | 13.7413 | 14.9126 | 1.1269 | 16.0394
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4933 | 17.287 | 18.7803 | 1.4368 | 20.2171
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9911 | 23.8267 | 25.8178 | 1.9157 | 27.7335
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.401 | 27.7034 | 30.1043 | 2.3101 | 32.4144
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.692 | 30.9922 | 33.6842 | 2.5901 | 36.2743 |  | UPDATED - DEC 16, 2020 - Draft Rate Order - RPP Update
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1769 | 36.4572 | 39.6341 | 3.0567 | 42.6907 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9528 | 45.211 | 49.1638 | 3.8032 | 52.967 | GS 50 to 1,499 kW | 0.01991 | 3.1059 | 1.9644 | 5.6065
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0424 | 46.2483 | 50.2907 | 3.8894 | 54.1801 | GS 1,500 to 4,999 kW | 0.02128 | 3.2248 | 2.0995 | 5.1311
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2292 | 48.398 | 52.6272 | 4.0691 | 56.6964 | Large Use | 0.02396 | 3.5749 | 2.3643 | 5.0407
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5448 | 52.0127 | 56.5576 | 4.3728 | 60.9304
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8605 | 55.6274 | 60.4879 | 4.6765 | 65.1644
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0317 | 69.3687 | 75.4004 | 5.8034 | 81.2038 | Tier 1 | 0.101
[14 empty] | Tier 2 | 0.118
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45737 | 5.5945 | 6.0519 | 0.44006 | 6.492
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.70274 | 8.478 | 9.1807 | 0.67614 | 9.8569 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4055 | 16.956 | 18.3615 | 1.3523 | 19.7138 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7568 | 20.612 | 22.3688 | 1.6903 | 24.0592 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3424 | 27.4827 | 29.8251 | 2.2538 | 32.0789
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4551 | 41.0034 | 44.4584 | 3.3243 | 47.7828
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1871 | 48.4257 | 52.6128 | 4.0286 | 56.6414
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5358 | 52.818 | 57.3538 | 4.3641 | 61.7179
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8883 | 57.2713 | 62.1597 | 4.7033 | 66.863
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2412 | 61.7257 | 66.9669 | 5.0428 | 72.0097
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3539 | 75.2464 | 81.6002 | 6.1134 | 87.7136
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6365 | 136.8565 | 147.493 | 10.2339 | 157.7269
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0641 | 157.3932 | 169.4572 | 11.6075 | 181.0647
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8119 | 199.4999 | 215.3118 | 15.2134 | 230.5252
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7445 | 225.4379 | 243.1824 | 17.0729 | 260.2553
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.7178 | 299.2499 | 322.9677 | 22.8202 | 345.7878
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2857 | 358.4378 | 386.7236 | 27.2152 | 413.9388
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9663 | 431.1464 | 465.1128 | 32.6808 | 497.7936
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0569 | 510.0637 | 550.1206 | 38.5409 | 588.6615
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1928 | 628.4396 | 677.6324 | 47.331 | 724.9633
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5132 | 725.9828 | 782.4961 | 54.3744 | 836.8705
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2023-FULL
Dry Core Transformer Losses Proposed for 2023
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4666 | 0.1134 |  | 5.5484
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87846 | 10.306 | 11.1845 | 0.8916 | 12.0761
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1713 | 13.7413 | 14.9126 | 1.1888 | 16.1014
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4934 | 17.287 | 18.7804 | 1.5157 | 20.2961
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9912 | 23.8267 | 25.8179 | 2.021 | 27.8388
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4011 | 27.7034 | 30.1045 | 2.437 | 32.5415
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6922 | 30.9922 | 33.6843 | 2.7324 | 36.4167 |  | UPDATED - DEC 16, 2020 - Draft Rate Order - RPP Update
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1771 | 36.4572 | 39.6343 | 3.2246 | 42.8588 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.953 | 45.211 | 49.1641 | 4.0122 | 53.1762 | GS 50 to 1,499 kW | 0.02017 | 3.1059 | 1.9644 | 5.8902
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0426 | 46.2483 | 50.2909 | 4.1031 | 54.394 | GS 1,500 to 4,999 kW | 0.02156 | 3.2248 | 2.0995 | 5.4149
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2294 | 48.398 | 52.6275 | 4.2927 | 56.9202 | Large Use | 0.02427 | 3.5749 | 2.3643 | 5.3401
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5451 | 52.0127 | 56.5578 | 4.6131 | 61.1709
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8607 | 55.6274 | 60.4881 | 4.9335 | 65.4216
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.032 | 69.3687 | 75.4007 | 6.1223 | 81.523 | Tier 1 | 0.101
[14 empty] | Tier 2 | 0.118
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45739 | 5.5945 | 6.0519 | 0.46423 | 6.5162
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.70277 | 8.478 | 9.1808 | 0.71329 | 9.8941 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4055 | 16.956 | 18.3615 | 1.4266 | 19.7881 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7569 | 20.612 | 22.3689 | 1.7832 | 24.1521 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3425 | 27.4827 | 29.8252 | 2.3776 | 32.2028
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4553 | 41.0034 | 44.4586 | 3.507 | 47.9656
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1873 | 48.4257 | 52.613 | 4.2499 | 56.8629
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.536 | 52.818 | 57.354 | 4.6039 | 61.958
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8886 | 57.2713 | 62.1599 | 4.9618 | 67.1217
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2415 | 61.7257 | 66.9672 | 5.3199 | 72.287
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3542 | 75.2464 | 81.6006 | 6.4493 | 88.0498
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6371 | 136.8565 | 147.4935 | 10.7962 | 158.2898
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0647 | 157.3932 | 169.4579 | 12.2452 | 181.7031
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8127 | 199.4999 | 215.3126 | 16.0493 | 231.3619
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7454 | 225.4379 | 243.1833 | 18.0109 | 261.1942
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.719 | 299.2499 | 322.9689 | 24.074 | 347.0429
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2872 | 358.4378 | 386.725 | 28.7105 | 415.4355
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9681 | 431.1464 | 465.1145 | 34.4764 | 499.5909
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.059 | 510.0637 | 550.1227 | 40.6584 | 590.7811
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1953 | 628.4396 | 677.6349 | 49.9314 | 727.5664
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5162 | 725.9828 | 782.499 | 57.3619 | 839.8609
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2024-FULL
Dry Core Transformer Losses Proposed for 2024
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4668 | 0.1134 |  | 5.728
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87849 | 10.306 | 11.1845 | 0.92046 | 12.105
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1713 | 13.7413 | 14.9127 | 1.2273 | 16.1399
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4934 | 17.287 | 18.7804 | 1.5648 | 20.3452
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9913 | 23.8267 | 25.8179 | 2.0864 | 27.9043
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4012 | 27.7034 | 30.1046 | 2.5159 | 32.6204
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6923 | 30.9922 | 33.6844 | 2.8209 | 36.5053 |  | UPDATED - DEC 16 2020 - Draft Rate Order - RPP Update
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1772 | 36.4572 | 39.6344 | 3.329 | 42.9633 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9532 | 45.211 | 49.1642 | 4.142 | 53.3062 | GS 50 to 1,499 kW | 0.02038 | 3.1059 | 1.9644 | 6.0448
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.0428 | 46.2483 | 50.291 | 4.2359 | 54.5269 | GS 1,500 to 4,999 kW | 0.02178 | 3.2248 | 2.0995 | 5.5944
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2296 | 48.398 | 52.6276 | 4.4316 | 57.0593 | Large Use | 0.02453 | 3.5749 | 2.3643 | 5.5447
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5453 | 52.0127 | 56.558 | 4.7624 | 61.3204
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8609 | 55.6274 | 60.4883 | 5.0931 | 65.5815
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0323 | 69.3687 | 75.401 | 6.3204 | 81.7214 | Tier 1 | 0.101
[14 empty] | Tier 2 | 0.118
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45741 | 5.5945 | 6.0519 | 0.47926 | 6.5312
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.7028 | 8.478 | 9.1808 | 0.73637 | 9.9172 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4056 | 16.956 | 18.3616 | 1.4727 | 19.8344 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.757 | 20.612 | 22.369 | 1.8409 | 24.2099 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3426 | 27.4827 | 29.8253 | 2.4545 | 32.2799
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4554 | 41.0034 | 44.4588 | 3.6205 | 48.0792
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1875 | 48.4257 | 52.6132 | 4.3875 | 57.0006
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5362 | 52.818 | 57.3542 | 4.7529 | 62.1072
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8888 | 57.2713 | 62.1601 | 5.1223 | 67.2824
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.2417 | 61.7257 | 66.9674 | 5.4921 | 72.4594
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3545 | 75.2464 | 81.6008 | 6.658 | 88.2588
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6375 | 136.8565 | 147.494 | 11.1456 | 158.6396
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0652 | 157.3932 | 169.4584 | 12.6415 | 182.0999
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8134 | 199.4999 | 215.3133 | 16.5687 | 231.882
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7462 | 225.4379 | 243.184 | 18.5938 | 261.7779
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.72 | 299.2499 | 322.9699 | 24.8531 | 347.823
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2884 | 358.4378 | 386.7262 | 29.6396 | 416.3659
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9695 | 431.1464 | 465.116 | 35.5922 | 500.7081
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0607 | 510.0637 | 550.1244 | 41.9743 | 592.0986
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.1974 | 628.4396 | 677.637 | 51.5474 | 729.1844
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5185 | 725.9828 | 782.5014 | 59.2183 | 841.7197
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2025-FULL
Dry Core Transformer Losses Proposed for 2025
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 5.4672 | 0.1134 |  | 5.8191
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 0.87855 | 10.306 | 11.1846 | 0.93509 | 12.1196
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.1714 | 13.7413 | 14.9127 | 1.2468 | 16.1595
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.4935 | 17.287 | 18.7805 | 1.5897 | 20.3702
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 1.9914 | 23.8267 | 25.8181 | 2.1196 | 27.9376
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.4013 | 27.7034 | 30.1047 | 2.5559 | 32.6606
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 2.6924 | 30.9922 | 33.6846 | 2.8657 | 36.5503 |  | UPDATED - DEC 16, 2020 - Draft Rate Order - RPP Update
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.1774 | 36.4572 | 39.6346 | 3.3819 | 43.0165 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 3.9534 | 45.211 | 49.1645 | 4.2079 | 53.3724 | GS 50 to 1,499 kW | 0.0207 | 3.1059 | 1.9644 | 6.127
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.043 | 46.2483 | 50.2913 | 4.3033 | 54.5946 | GS 1,500 to 4,999 kW | 0.02212 | 3.2248 | 2.0995 | 5.6776
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 4.2299 | 48.398 | 52.6279 | 4.5021 | 57.13 | Large Use | 0.02491 | 3.5749 | 2.3643 | 5.6526
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 4.5456 | 52.0127 | 56.5583 | 4.8381 | 61.3964
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 4.8612 | 55.6274 | 60.4886 | 5.1741 | 65.6628
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 6.0326 | 69.3687 | 75.4014 | 6.4209 | 81.8223 | Tier 1 | 0.101
[14 empty] | Tier 2 | 0.118
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.45744 | 5.5945 | 6.052 | 0.48688 | 6.5388
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.70285 | 8.478 | 9.1808 | 0.74808 | 9.9289 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.4057 | 16.956 | 18.3617 | 1.4962 | 19.8579 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 1.7571 | 20.612 | 22.3691 | 1.8702 | 24.2393 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.3428 | 27.4827 | 29.8255 | 2.4936 | 32.3191
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 3.4556 | 41.0034 | 44.459 | 3.6781 | 48.137
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 4.1877 | 48.4257 | 52.6134 | 4.4573 | 57.0707
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 4.5365 | 52.818 | 57.3545 | 4.8285 | 62.183
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 4.8891 | 57.2713 | 62.1604 | 5.2038 | 67.3642
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 5.242 | 61.7257 | 66.9677 | 5.5794 | 72.5471
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 6.3549 | 75.2464 | 81.6012 | 6.7639 | 88.3651
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 10.6382 | 136.8565 | 147.4947 | 11.3229 | 158.8176
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 12.0659 | 157.3932 | 169.4591 | 12.8426 | 182.3017
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 15.8144 | 199.4999 | 215.3143 | 16.8322 | 232.1465
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 17.7473 | 225.4379 | 243.1852 | 18.8896 | 262.0747
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 23.7215 | 299.2499 | 322.9714 | 25.2483 | 348.2198
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 28.2902 | 358.4378 | 386.728 | 30.1111 | 416.8391
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 33.9717 | 431.1464 | 465.1181 | 36.1582 | 501.2763
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 40.0632 | 510.0637 | 550.1269 | 42.6418 | 592.7687
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 49.2005 | 628.4396 | 677.6401 | 52.3672 | 730.0073
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 56.5221 | 725.9828 | 782.505 | 60.1601 | 842.6651
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1
New Transformers added 2021

## 2021 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2021
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.466 | 0.1134 |  | 4.9376
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87836 | 10.306 | 11.1844 | 0.79345 | 11.9778
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1712 | 13.7413 | 14.9125 | 1.0579 | 15.9704
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4932 | 17.287 | 18.7802 | 1.3489 | 20.1291
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.991 | 23.8267 | 25.8176 | 1.7985 | 27.6161
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4008 | 27.7034 | 30.1042 | 2.1687 | 32.2729
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6919 | 30.9922 | 33.684 | 2.4316 | 36.1157
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1767 | 36.4572 | 39.6339 | 2.8696 | 42.5035
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9526 | 45.211 | 49.1636 | 3.5705 | 52.7341
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0422 | 46.2483 | 50.2904 | 3.6514 | 53.9419
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.229 | 48.398 | 52.627 | 3.8201 | 56.4472
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5446 | 52.0127 | 56.5573 | 4.1053 | 60.6626
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8602 | 55.6274 | 60.4876 | 4.3904 | 64.878
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0314 | 69.3687 | 75.4001 | 5.4483 | 80.8484
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45734 | 5.5945 | 6.0519 | 0.41313 | 6.465
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.7027 | 8.478 | 9.1807 | 0.63477 | 9.8155
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4054 | 16.956 | 18.3614 | 1.2695 | 19.6309
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7567 | 20.612 | 22.3687 | 1.5869 | 23.9556
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3423 | 27.4827 | 29.825 | 2.1159 | 31.9408
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4549 | 41.0034 | 44.4583 | 3.1209 | 47.5792
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1868 | 48.4257 | 52.6125 | 3.7821 | 56.3946
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5356 | 52.818 | 57.3536 | 4.0971 | 61.4507
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8881 | 57.2713 | 62.1594 | 4.4155 | 66.5749
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2409 | 61.7257 | 66.9666 | 4.7342 | 71.7008
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3535 | 75.2464 | 81.5999 | 5.7393 | 87.3392
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6359 | 136.8565 | 147.4924 | 9.6077 | 157.1001
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0634 | 157.3932 | 169.4566 | 10.8972 | 180.3538
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.811 | 199.4999 | 215.3109 | 14.2825 | 229.5934
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7435 | 225.4379 | 243.1814 | 16.0282 | 259.2096
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.7165 | 299.2499 | 322.9664 | 21.4238 | 344.3902
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2842 | 358.4378 | 386.722 | 25.5499 | 412.2719
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9645 | 431.1464 | 465.1109 | 30.681 | 495.792
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0547 | 510.0637 | 550.1185 | 36.1825 | 586.3009
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1901 | 628.4396 | 677.6297 | 44.4347 | 722.0644
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5102 | 725.9828 | 782.4931 | 51.0471 | 833.5402
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2022 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2022
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4663 | 0.1134 |  | 5.2594
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87841 | 10.306 | 11.1844 | 0.84516 | 12.0296
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1712 | 13.7413 | 14.9126 | 1.1269 | 16.0394
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4933 | 17.287 | 18.7803 | 1.4368 | 20.2171
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9911 | 23.8267 | 25.8178 | 1.9157 | 27.7335
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.401 | 27.7034 | 30.1043 | 2.3101 | 32.4144
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.692 | 30.9922 | 33.6842 | 2.5901 | 36.2743
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1769 | 36.4572 | 39.6341 | 3.0567 | 42.6907
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9528 | 45.211 | 49.1638 | 3.8032 | 52.967
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0424 | 46.2483 | 50.2907 | 3.8894 | 54.1801
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2292 | 48.398 | 52.6272 | 4.0691 | 56.6964
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5448 | 52.0127 | 56.5576 | 4.3728 | 60.9304
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8605 | 55.6274 | 60.4879 | 4.6765 | 65.1644
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0317 | 69.3687 | 75.4004 | 5.8034 | 81.2038
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45737 | 5.5945 | 6.0519 | 0.44006 | 6.492
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.70274 | 8.478 | 9.1807 | 0.67614 | 9.8569
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4055 | 16.956 | 18.3615 | 1.3523 | 19.7138
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7568 | 20.612 | 22.3688 | 1.6903 | 24.0592
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3424 | 27.4827 | 29.8251 | 2.2538 | 32.0789
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4551 | 41.0034 | 44.4584 | 3.3243 | 47.7828
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1871 | 48.4257 | 52.6128 | 4.0286 | 56.6414
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5358 | 52.818 | 57.3538 | 4.3641 | 61.7179
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8883 | 57.2713 | 62.1597 | 4.7033 | 66.863
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2412 | 61.7257 | 66.9669 | 5.0428 | 72.0097
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3539 | 75.2464 | 81.6002 | 6.1134 | 87.7136
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6365 | 136.8565 | 147.493 | 10.2339 | 157.7269
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0641 | 157.3932 | 169.4572 | 11.6075 | 181.0647
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8119 | 199.4999 | 215.3118 | 15.2134 | 230.5252
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7445 | 225.4379 | 243.1824 | 17.0729 | 260.2553
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.7178 | 299.2499 | 322.9677 | 22.8202 | 345.7878
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2857 | 358.4378 | 386.7236 | 27.2152 | 413.9388
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9663 | 431.1464 | 465.1128 | 32.6808 | 497.7936
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0569 | 510.0637 | 550.1206 | 38.5409 | 588.6615
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1928 | 628.4396 | 677.6324 | 47.331 | 724.9633
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5132 | 725.9828 | 782.4961 | 54.3744 | 836.8705
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2023 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2023
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4666 | 0.1134 |  | 5.5484
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87846 | 10.306 | 11.1845 | 0.8916 | 12.0761
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1713 | 13.7413 | 14.9126 | 1.1888 | 16.1014
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4934 | 17.287 | 18.7804 | 1.5157 | 20.2961
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9912 | 23.8267 | 25.8179 | 2.021 | 27.8388
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4011 | 27.7034 | 30.1045 | 2.437 | 32.5415
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6922 | 30.9922 | 33.6843 | 2.7324 | 36.4167
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1771 | 36.4572 | 39.6343 | 3.2246 | 42.8588
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.953 | 45.211 | 49.1641 | 4.0122 | 53.1762
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0426 | 46.2483 | 50.2909 | 4.1031 | 54.394
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2294 | 48.398 | 52.6275 | 4.2927 | 56.9202
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5451 | 52.0127 | 56.5578 | 4.6131 | 61.1709
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8607 | 55.6274 | 60.4881 | 4.9335 | 65.4216
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.032 | 69.3687 | 75.4007 | 6.1223 | 81.523
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45739 | 5.5945 | 6.0519 | 0.46423 | 6.5162
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.70277 | 8.478 | 9.1808 | 0.71329 | 9.8941
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4055 | 16.956 | 18.3615 | 1.4266 | 19.7881
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7569 | 20.612 | 22.3689 | 1.7832 | 24.1521
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3425 | 27.4827 | 29.8252 | 2.3776 | 32.2028
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4553 | 41.0034 | 44.4586 | 3.507 | 47.9656
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1873 | 48.4257 | 52.613 | 4.2499 | 56.8629
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.536 | 52.818 | 57.354 | 4.6039 | 61.958
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8886 | 57.2713 | 62.1599 | 4.9618 | 67.1217
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2415 | 61.7257 | 66.9672 | 5.3199 | 72.287
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3542 | 75.2464 | 81.6006 | 6.4493 | 88.0498
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6371 | 136.8565 | 147.4935 | 10.7962 | 158.2898
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0647 | 157.3932 | 169.4579 | 12.2452 | 181.7031
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8127 | 199.4999 | 215.3126 | 16.0493 | 231.3619
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7454 | 225.4379 | 243.1833 | 18.0109 | 261.1942
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.719 | 299.2499 | 322.9689 | 24.074 | 347.0429
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2872 | 358.4378 | 386.725 | 28.7105 | 415.4355
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9681 | 431.1464 | 465.1145 | 34.4764 | 499.5909
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.059 | 510.0637 | 550.1227 | 40.6584 | 590.7811
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1953 | 628.4396 | 677.6349 | 49.9314 | 727.5664
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5162 | 725.9828 | 782.499 | 57.3619 | 839.8609
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2024 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2024
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4668 | 0.1134 |  | 5.728
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87849 | 10.306 | 11.1845 | 0.92046 | 12.105
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1713 | 13.7413 | 14.9127 | 1.2273 | 16.1399
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4934 | 17.287 | 18.7804 | 1.5648 | 20.3452
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9913 | 23.8267 | 25.8179 | 2.0864 | 27.9043
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4012 | 27.7034 | 30.1046 | 2.5159 | 32.6204
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6923 | 30.9922 | 33.6844 | 2.8209 | 36.5053
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1772 | 36.4572 | 39.6344 | 3.329 | 42.9633
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9532 | 45.211 | 49.1642 | 4.142 | 53.3062
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.0428 | 46.2483 | 50.291 | 4.2359 | 54.5269
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2296 | 48.398 | 52.6276 | 4.4316 | 57.0593
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5453 | 52.0127 | 56.558 | 4.7624 | 61.3204
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8609 | 55.6274 | 60.4883 | 5.0931 | 65.5815
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0323 | 69.3687 | 75.401 | 6.3204 | 81.7214
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45741 | 5.5945 | 6.0519 | 0.47926 | 6.5312
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.7028 | 8.478 | 9.1808 | 0.73637 | 9.9172
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4056 | 16.956 | 18.3616 | 1.4727 | 19.8344
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.757 | 20.612 | 22.369 | 1.8409 | 24.2099
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3426 | 27.4827 | 29.8253 | 2.4545 | 32.2799
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4554 | 41.0034 | 44.4588 | 3.6205 | 48.0792
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1875 | 48.4257 | 52.6132 | 4.3875 | 57.0006
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5362 | 52.818 | 57.3542 | 4.7529 | 62.1072
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8888 | 57.2713 | 62.1601 | 5.1223 | 67.2824
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.2417 | 61.7257 | 66.9674 | 5.4921 | 72.4594
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3545 | 75.2464 | 81.6008 | 6.658 | 88.2588
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6375 | 136.8565 | 147.494 | 11.1456 | 158.6396
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0652 | 157.3932 | 169.4584 | 12.6415 | 182.0999
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8134 | 199.4999 | 215.3133 | 16.5687 | 231.882
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7462 | 225.4379 | 243.184 | 18.5938 | 261.7779
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.72 | 299.2499 | 322.9699 | 24.8531 | 347.823
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2884 | 358.4378 | 386.7262 | 29.6396 | 416.3659
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9695 | 431.1464 | 465.116 | 35.5922 | 500.7081
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0607 | 510.0637 | 550.1244 | 41.9743 | 592.0986
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.1974 | 628.4396 | 677.637 | 51.5474 | 729.1844
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5185 | 725.9828 | 782.5014 | 59.2183 | 841.7197
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard

## 2025 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2025
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2019-0261
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 5.4672 | 0.1134 |  | 5.8191
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.87855 | 10.306 | 11.1846 | 0.93509 | 12.1196
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.1714 | 13.7413 | 14.9127 | 1.2468 | 16.1595
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.4935 | 17.287 | 18.7805 | 1.5897 | 20.3702
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 1.9914 | 23.8267 | 25.8181 | 2.1196 | 27.9376
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.4013 | 27.7034 | 30.1047 | 2.5559 | 32.6606
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 2.6924 | 30.9922 | 33.6846 | 2.8657 | 36.5503
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.1774 | 36.4572 | 39.6346 | 3.3819 | 43.0165
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 3.9534 | 45.211 | 49.1645 | 4.2079 | 53.3724
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.043 | 46.2483 | 50.2913 | 4.3033 | 54.5946
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 4.2299 | 48.398 | 52.6279 | 4.5021 | 57.13
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 4.5456 | 52.0127 | 56.5583 | 4.8381 | 61.3964
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 4.8612 | 55.6274 | 60.4886 | 5.1741 | 65.6628
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 6.0326 | 69.3687 | 75.4014 | 6.4209 | 81.8223
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.45744 | 5.5945 | 6.052 | 0.48688 | 6.5388
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.70285 | 8.478 | 9.1808 | 0.74808 | 9.9289
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.4057 | 16.956 | 18.3617 | 1.4962 | 19.8579
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 1.7571 | 20.612 | 22.3691 | 1.8702 | 24.2393
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.3428 | 27.4827 | 29.8255 | 2.4936 | 32.3191
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 3.4556 | 41.0034 | 44.459 | 3.6781 | 48.137
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 4.1877 | 48.4257 | 52.6134 | 4.4573 | 57.0707
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 4.5365 | 52.818 | 57.3545 | 4.8285 | 62.183
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 4.8891 | 57.2713 | 62.1604 | 5.2038 | 67.3642
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 5.242 | 61.7257 | 66.9677 | 5.5794 | 72.5471
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 6.3549 | 75.2464 | 81.6012 | 6.7639 | 88.3651
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 10.6382 | 136.8565 | 147.4947 | 11.3229 | 158.8176
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 12.0659 | 157.3932 | 169.4591 | 12.8426 | 182.3017
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 15.8144 | 199.4999 | 215.3143 | 16.8322 | 232.1465
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 17.7473 | 225.4379 | 243.1852 | 18.8896 | 262.0747
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 23.7215 | 299.2499 | 322.9714 | 25.2483 | 348.2198
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 28.2902 | 358.4378 | 386.728 | 30.1111 | 416.8391
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 33.9717 | 431.1464 | 465.1181 | 36.1582 | 501.2763
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 40.0632 | 510.0637 | 550.1269 | 42.6418 | 592.7687
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 49.2005 | 628.4396 | 677.6401 | 52.3672 | 730.0073
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 56.5221 | 725.9828 | 782.505 | 60.1601 | 842.6651
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard