## Sheet1
Asset Category | Pop. | Health Index Distribution (%) |  |  |  |  | Avg. Health Index | DAI | Asset Category | Pop. | Health Index Distribution (%) |  |  |  |  | Avg. Health Index | DAI | DAI Before Assumptions
|  | Very Good | Good | Fair | Poor | Very Poor |  |  |  |  | Very Good | Good | Fair | Poor | Very Poor
Wood Pole | 9570 | 581 | 6129 | 2662 | 196 | 2 | 73 | 1 | Wood Pole | 9570 | 6.071% | 64.04% | 27.82% | 2.048% | 0.0209% | 73% | 100% | 97.7%
Concrete Pole | 869 | 3 | 108 | 758 | 0 | 0 | 66 | 1 | Concrete Pole | 869 | 0.3452% | 12.43% | 87.23% | 0% | 0% | 66% | 100% | 100%
Steel Pole | 14 | 6 | 5 | 3 | 0 | 0 | 72 | 1 | Steel Pole | 14 | 42.86% | 35.71% | 21.43% | 0% | 0% | 72% | 100% | 100%
Overhead Primary Conductor (m) | 519869 | 293308 | 195578 | 6177 | 24806 | 0 | 84 | 1 | Overhead Primary Conductor (m) | 519869 | 56.42% | 37.62% | 1.188% | 4.772% | 0% | 84% | 100% | 53%
Underground Primary Cable (m) | 460325 | 172545 | 68208 | 136462 | 81042 | 2068 | 68 | 1 | Underground Primary Cable (m) | 460325 | 37.48% | 14.82% | 29.64% | 17.61% | 0.4492% | 68% | 100% | 95.5%
Pole mount Transformer | 2513 | 1219 | 1177 | 117 | 0 | 0 | 84 | 1 | Pole mount Transformer | 2513 | 48.51% | 46.84% | 4.656% | 0% | 0% | 84% | 100% | 99.96%
Pad mount Transformer | 3765 | 2065 | 1600 | 99 | 1 | 0 | 85 | 1 | Pad mount Transformer | 3765 | 54.85% | 42.5% | 2.629% | 0.02656% | 0% | 85% | 100%
Vault Transformer | 394 | 167 | 201 | 26 | 0 | 0 | 84 | 1 | Vault Transformer | 394 | 42.39% | 51.02% | 6.599% | 0% | 0% | 84% | 100%
Submersible Transformer | 20 | 8 | 11 | 1 | 0 | 0 | 83 | 1 | Submersible Transformer | 20 | 40% | 55% | 5% | 0% | 0% | 83% | 100%
Primary Switch | 1001 | 588 | 365 | 48 | 0 | 0 | 87 | 1 | Primary Switch | 1001 | 58.74% | 36.46% | 4.795% | 0% | 0% | 87% | 100% | 84%
Smart Switch | 15 | 15 | 0 | 0 | 0 | 0 | 100 | 1 | Smart Switch | 15 | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100%
Distribution Switchgear | 33 | 28 | 5 | 0 | 0 | 0 | 96 | 1 | Distribution Switchgear | 33 | 84.85% | 15.15% | 0% | 0% | 0% | 96% | 100% | 100%
Cutout Arrestor | 2830 | 1110 | 989 | 209 | 481 | 41 | 80 | 1 | Cutout Arrestor | 2830 | 39.22% | 34.95% | 7.385% | 17% | 1.449% | 80% | 100% | 93%
Elbow | 7192 | 4899 | 2032 | 261 | 0 | 0 | 90 | 1 | Elbow | 7192 | 68.12% | 28.25% | 3.629% | 0% | 0% | 90% | 100% | 32.7%
Recloser | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 1 | Recloser | 4 | 100% | 0% | 0% | 0% | 0% | 0% | 100% | 100%
Vault | 146 | 16 | 130 | 0 | 0 | 0 | 84 | 1 | Vault | 146 | 10.96% | 89.04% | 0% | 0% | 0% | 84% | 100% | 100%
Manhole | 120 | 0 | 120 | 0 | 0 | 0 | 83 | 1 | Manhole | 120 | 0% | 100% | 0% | 0% | 0% | 83% | 100% | 100%
Substations | [8 empty] | Substations
Power Transformer | 16 | 8 | 6 | 2 | 0 | 0 | 83 | 1 | Power Transformer | 16 | 50% | 37.5% | 12.5% | 0% | 0% | 83% | 100% | 100%
Circuit Breaker 13.8kV | 72 | 68 | 4 | 0 | 0 | 0 | 96 | 1 | Circuit Breaker 13.8kV | 72 | 94.44% | 5.556% | 0% | 0% | 0% | 96% | 100% | 100%
Circuit Breaker 44kV | 16 | 16 | 0 | 0 | 0 | 0 | 100 | 1 | Circuit Breaker 44kV | 16 | 100% | 0% | 0% | 0% | 0% | 100% | 100% | 100%
Switchgear | 8 | 0 | 1 | 2 | 5 | 0 | 43 | 1 | Switchgear | 8 | 0% | 12.5% | 25% | 62.5% | 0% | 43% | 100% | 100%
Protection Relay | 71 | 16 | 9 | 46 | 0 | 0 | 75 | 1 | Protection Relay | 71 | 22.54% | 12.68% | 64.79% | 0% | 0% | 75% | 100% | 100%
SCADA RTU | 8 | 0 | 0 | 8 | 0 | 0 | 60 | 1 | SCADA RTU | 8 | 0% | 0% | 100% | 0% | 0% | 60% | 100% | 100%
Battery | 8 | 5 | 3 | 0 | 0 | 0 | 94 | 1 | Battery and Charger | 8 | 62.5% | 37.5% | 0% | 0% | 0% | 94% | 100% | 100%
Ground Grid | 16 | 0 | 0 | 16 | 0 | 0 | 62 | 1 | Ground Grid | 16 | 0% | 0% | 100% | 0% | 0% | 62% | 100% | 100%
Fence | 8 | 0 | 0 | 8 | 0 | 0 | 60 | 1 | Fence | 8 | 0% | 0% | 100% | 0% | 0% | 60% | 100% | 100%
Building | 8 | 3 | 0 | 5 | 0 | 0 | 75 | 1 | Building | 8 | 37.5% | 0% | 62.5% | 0% | 0% | 75% | 100% | 100%