## Sheet1
Appendix 2-G
Service Reliability and Quality Indicators
2016 - 2020
Service Reliability
Index | Including outages caused by loss of supply |  |  |  |  | Excluding outages caused by loss of supply |  |  |  |  | Excluding Major Event Days*
| 2016 | 2017 | 2018 | 2019 | 2020 | 2016 | 2017 | 2018 | 2019 | 2020 | 2016 | 2017 | 2018 | 2019 | 2020
SAIDI | 13.2 | 13 | 22.9 | 10 | 14.5 | 12.6 | 12.2 | 21.2 | 8.9 | 13.5 | 8.3 | 8.5 | 7.6 | 8 | 8.2
SAIFI | 3.4 | 3.5 | 4.3 | 3.5 | 3.7 | 2.9 | 2.9 | 3.4 | 2.8 | 3.1 | 2.8 | 2.8 | 2.9 | 3.2 | 3.1
* Excluding force majeure and including loss of supply
5 Year Historical Average
SAIDI |  |  |  |  | 14.72 |  |  |  |  | 13.68 |  |  |  |  | 8.12
SAIFI |  |  |  |  | 3.68 |  |  |  |  | 3.02 |  |  |  |  | 2.96
SAIDI = System Average Interruption Duration Index
SAIFI = System Average Interruption Frequency Index
NOTE: For additional detail and discussion, see Exhibit B1-1-1, Section 1.4.2.1
Service Quality
Indicator |  |  |  | OEB Minimum Standard |  | 2016 | 2017 | 2018 | 2019 | 2020
Low Voltage Connections |  |  |  | 90% |  | 98.6% | 98.1% | 99.3% | 99.8% | 99.8%
High Voltage Connections* |  |  |  | 90% |  | n/a | n/a | n/a | n/a | n/a
Telephone Accessibility |  |  |  | 65% |  | 74.2% | 81.9% | 78.1% | 76.8% | 70.2%
Appointments Met |  |  |  | 90% |  | 99.5% | 98.9% | 100% | 100% | 100%
Written Response to Enquires |  |  |  | 80% |  | 100% | 100% | 100% | 100% | 99.33%
Emergency Urban Response |  |  |  | 80%
Emergency Rural Response** |  |  |  | 80% |  | 75.3% | 77.28% | 65.5% | 86.5% | 76.5%
Telephone Call Abandon Rate *** |  |  |  | 10% |  | 2.7% | 2.1% | 3% | 2% | 3.9%
Appointment Scheduling |  |  |  | 90% |  | 99.5% | 99% | 100% | 100% | 100%
Rescheduling a Missed Appointment |  |  |  | 100% |  | 98.5% | 99.7% | 97.3% | 100% | 100%
Reconnection Performance Standard |  |  |  | 85% |  | 98.5% | 98.2% | 98.3% | 99.8% | 98.5%
Results are consistent with the scorecard in DSP Section 3.5. Any differences are due to rounding between this template and the Scorecard produced by the OEB
in DSP Section 3.5.
* High Voltage Connections results are included with Low Voltage results.
** Emergency Response results include the impact of Force Majeure events.
*** Telephone Call Abandon Rate OEB Minimum Standard of 10.0% should be interpreted as no more than 10.0% of calls.