## CCC-31a
Asset Category |  | Population | Sample | Average | Average | Average DAI | Health Index Distribution
|  |  | Size | Health Index | Age |  | Very Poor (< 25%) |  | Poor (25 - <50%) |  | Fair (50 - <70%) |  | Good (70 - <85%) |  | Very Good (>= 85%)
[7 empty] | # | % | # | % | # | % | # | % | # | %
Substation Transformers |  | 53 | 53 | 61% | 32 | 75% | 9 | 17% | 10 | 19% | 12 | 23% | 3 | 6% | 19 | 36%
Circuit Breakers |  | 51 | 44 | 64% | 47 | 48% | 9 | 20% | 4 | 9% | 13 | 30% | 0 | 0% | 18 | 41%
Substation Reclosers |  | 14 | 14 | 90% | 14 | 15% | 0 | 0% | 2 | 14% | 0 | 0% | 0 | 0% | 12 | 86%
Battery Banks |  | 31 | 31 | 84% | 11 | 55% | 1 | 3% | 3 | 10% | 1 | 3% | 4 | 13% | 22 | 71%
Pole Mounted Transformers | 1 Phase | 3928 | 3906 | 87% | 25 | 35% | 118 | 3% | 319 | 8% | 141 | 4% | 350 | 9% | 2978 | 76%
| 3 Phase | 3786 | 3781 | 96% | 21 | 59% | 18 | < 1% | 40 | 1% | 85 | 2% | 148 | 4% | 3490 | 92%
| Step Down | 85 | 55 | 99% | 21 | age-based | 0 | 0% | 0 | 0% | 0 | 0% | 1 | 2% | 54 | 98%
Pad Mounted Transformers | 1 phase | 6608 | 6600 | 92% | 16 | 82% | 57 | < 1% | 261 | 4% | 96 | 1% | 477 | 7% | 5709 | 87%
| 3 Phase | 1339 | 1336 | 88% | 18 | 84% | 41 | 3% | 49 | 4% | 65 | 5% | 198 | 15% | 983 | 74%
Vault Transformer |  | 74 | 74 | 50% | 36 | age-based | 33 | 45% | 3 | 4% | 3 | 4% | 12 | 16% | 23 | 31%
Network Transformer |  | 68 | 68 | 97% | 17 | 100% | 0 | 0% | 0 | 0% | 1 | 1% | 7 | 10% | 60 | 88%
Network Protector |  | 65 | 65 | 99% | 17 | 100% | 0 | 0% | 1 | 2% | 0 | 0% | 0 | 0% | 64 | 98%
Pad Mounted Switchgear | 200 A Air Insulated | 30 | 30 | 59% | 29 | 100% | 7 | 23% | 3 | 10% | 2 | 7% | 14 | 47% | 4 | 13%
| 200 A Solid Dielectric | 77 | 77 | 99% | 8 | 69% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 77 | 100%
| 600 A | 21 | 21 | 100% | 8 | 76% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 21 | 100%
| SF6 | 33 | 33 | 100% | 15 | age-based | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 33 | 100%
OH Load Break Switch | Motorized | 66 | 66 | 100% | 17 | age-based | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 66 | 100%
Reclosers |  | 112 | 103 | 100% | 7 | age-based | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 103 | 100%
Poles | Poles - LH Wood | 26800 | 26658 | 88% | 27 | 73% | 231 | < 1% | 1826 | 7% | 2176 | 8% | 2495 | 9% | 19930 | 75%
| Poles - LH Concrete | 134 | 134 | 93% | 40 | 89% | 0 | 0% | 8 | 6% | 0 | 0% | 18 | 13% | 108 | 81%
| Poles - LH Steel | 54 | 54 | 96% | 28 | 41% | 0 | 0% | 0 | 0% | 0 | 0% | 12 | 22% | 42 | 78%
| Poles - H1 Wood | 721 | 555 | 92% | 30 | 49% | 12 | 2% | 16 | 3% | 48 | 9% | 19 | 3% | 460 | 83%
| Poles - H1 Steel | 60 | 18 | 100% | 29 | 2% | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 18 | 100%
| Poles - Bell Wood | 2591 | 2464 | 76% | 44 | 35% | 401 | 16% | 68 | 3% | 589 | 24% | 132 | 5% | 1274 | 52%
UG Cables | PILC1 | 35 | 27 | 89% | 40 | age-based | 0.71 | 3% | 0.35 | 1% | 0.77 | 3% | 6.77 | 25% | 18.16 | 68%
| EPR1 | 23 | 23 | 100% | 4 | age-based | 0 | 0% | 0 | 0% | 0 | 0% | 0 | 0% | 22.83 | 100%
| Egress Polymeric1 | 57 | 52 | 98% | 13 | age-based | 0.26 | < 1% | 0.17 | < 1% | 0.51 | < 1% | 2.99 | 6% | 48.53 | 93%
| Polymeric2 | 1444 | 1432 | 84% | 22 | age-based | 74.89 | 5% | 119.89 | 8% | 133.01 | 9% | 150.358 | 10% | 954.231 | 67%
Structures | Manholes | 1102 | 1102 | 81% | 42 | 61% | 58 | 5% | 65 | 6% | 106 | 10% | 238 | 22% | 635 | 58%
| Vaults | 61 | 61 | 75% | 47 | 74% | 1 | 2% | 9 | 15% | 10 | 16% | 15 | 25% | 26 | 43%
1 circuit-km
2 conductor-km

## CCC-31b
Asset Category |  | Age Limiter
Age Limit is a Weibull curve where,
Substation Transformers |  | Based on 50-60 year typical life | Low limit = 20% likelihood of removal
Circuit Breakers |  | Based on 50-60 year typical life | Upper limit = 95% likelihood of removal
Substation Reclosers |  | Based on 45-60 year typical life
Battery Banks |  | Based on 15-20 year typical life
Pole Mounted Transformers | 1 Phase | Based on 45-65 year typical life
| 3 Phase | Based on 45-65 year typical life
| Step Down | Based on 45-65 year typical life
Pad Mounted Transformers | 1 phase | Based on 35-50 year typical life
| 3 Phase | Based on 35-50 year typical life
Vault Transformer |  | Based on 40-55 year typical life
Network Transformer |  | Based on 40-50 year typical life
Network Protector |  | Based on 40-50 year typical life
Pad Mounted Switchgear | 200 A Air Insulated | Based on 30-45 year typical life
| 200 A Solid Dielectric | Based on 30-45 year typical life
| 600 A | Based on 30-45 year typical life
| SF6 | Based on 35-50 year typical life
OH Load Break Switch | Motorized | Based on 35-50 year typical life
Reclosers |  | Based on 35-50 year typical life
Poles | Poles - LH Wood | Based on 55-75 year typical life
| Poles - LH Concrete | Based on 60-80 year typical life
| Poles - LH Steel | Based on 60-80 year typical life
| Poles - H1 Wood | Based on 55-75 year typical life
| Poles - H1 Steel | Based on 60-80 year typical life
| Poles - Bell Wood | Based on 60-80 year typical life
UG Cables | PILC1 | Based on 55-70 year typical life
| EPR1 | Based on 40-55 year typical life
| Egress Polymeric1 | XLPE: Based on 30-50 year typical life TRXLPE: Based on 40-55 year typical life
| Polymeric2 | XLPE: Based on 30-50 year typical life TRXLPE: Based on 40-55 year typical life
Structures | Manholes | Based on 75-95 year typical life
| Vaults | Based on 75-95 year typical life

## CCC-31c
Asset Category |  | Population | Age Limiter | Low Limit | Upper Limit | > Low Limit |  | > High Limit |  | Poor/Very Poor |  | Age Limit is a Weibull curve where,
[6 empty] | # | % Population | # | % Population | # | % Population | Low limit = 20% likelihood of removal
Substation Transformers |  | 53 | 50-60 year typical life | 50 | 60 | 20 | 37.74% | 3 | 5.66% | 19 | 35.85% | Upper limit = 95% likelihood of removal
Circuit Breakers |  | 51 | 50-60 year typical life | 50 | 60 | 26 | 50.98% | 0 | 0% | 13 | 25.49%
Substation Reclosers |  | 14 | 45-60 year typical life | 45 | 60 | 0 | 0% | 0 | 0% | 2 | 14.29%
Battery Banks |  | 31 | 15-20 year typical life | 15 | 20 | 3 | 9.677% | 1 | 3.226% | 4 | 12.9%
Pole Mounted Transformers | 1 Phase | 3928 | 45-65 year typical life | 45 | 65 | 562 | 14.31% | 25 | 0.6365% | 437 | 11.13%
| 3 Phase | 3786 | 45-65 year typical life | 45 | 65 | 137 | 3.619% | 8 | 0.2113% | 58 | 1.532%
| Step Down | 85 | 45-65 year typical life | 45 | 65 | 0 | 0% | 0 | 0% | 0 | 0%
Pad Mounted Transformers | 1 phase | 6608 | 35-50 year typical life | 35 | 50 | 384 | 5.811% | 10 | 0.1513% | 318 | 4.812%
| 3 Phase | 1339 | 35-50 year typical life | 35 | 50 | 164 | 12.25% | 4 | 0.2987% | 90 | 6.721%
Vault Transformer |  | 74 | 40-55 year typical life | 40 | 55 | 39 | 52.7% | 10 | 13.51% | 36 | 48.65%
Network Transformer |  | 68 | 40-50 year typical life | 40 | 50 | 1 | 1.471% | 0 | 0% | 0 | 0%
Network Protector |  | 65 | 40-50 year typical life | 40 | 50 | 0 | 0% | 0 | 0% | 1 | 1.538%
Pad Mounted Switchgear | 200 A Air Insulated | 30 | 30-45 year typical life | 30 | 45 | 12 | 40% | 3 | 10% | 10 | 33.33%
| 200 A Solid Dielectric | 77 | 30-45 year typical life | 30 | 45 | 0 | 0% | 0 | 0% | 0 | 0%
| 600 A | 21 | 30-45 year typical life | 30 | 45 | 0 | 0% | 0 | 0% | 0 | 0%
| SF6 | 33 | 35-50 year typical life | 35 | 50 |  | 0% |  | 0% | 0 | 0%
OH Load Break Switch | Motorized | 66 | 35-50 year typical life | 35 | 50 | 0 | 0% | 0 | 0% | 0 | 0%
Reclosers |  | 112 | 35-50 year typical life | 35 | 50 | 0 | 0% | 0 | 0% | 0 | 0%
Poles | Poles - LH Wood | 26800 | 55-75 year typical life | 55 | 75 | 256 | 0.9552% | 0 | 0% | 2057 | 7.675%
| Poles - LH Concrete | 134 | 60-80 year typical life | 60 | 80 | 8 | 5.97% | 0 | 0% | 8 | 5.97%
| Poles - LH Steel | 54 | 60-80 year typical life | 60 | 80 | 0 | 0% | 0 | 0% | 0 | 0%
| Poles - H1 Wood | 721 | 55-75 year typical life | 55 | 75 | 65 | 9.015% | 0 | 0% | 28 | 3.883%
| Poles - H1 Steel | 60 | 60-80 year typical life | 60 | 80 | 0 | 0% | 0 | 0% | 0 | 0%
| Poles - Bell Wood | 2591 | 60-80 year typical life | 60 | 80 | 475 | 18.33% | 0 | 0% | 469 | 18.1%
UG Cables | PILC1 | 35 | 55-70 year typical life | 55 | 70 | 4.3 | 12.29% | 0 | 0% | 1.06 | 3.029%
| EPR1 | 23 | 40-55 year typical life | 40 | 55 | 0 | 0% | 0 | 0% | 0 | 0%
| Egress Polymeric1 | 57 | XLPE: 30-50 year typical life TRXLPE: 40-55 year typical life | 30 | 50 | 1 | 1.754% | 0.3 | 0.5263% | 0.43 | 0.7544%
| Polymeric2 | 1444 | XLPE: 30-50 year typical life TRXLPE: 40-55 year typical life | 30 | 50 | 446.4 | 30.91% | 4.8 | 0.3324% | 194.78 | 13.49%
Structures | Manholes | 1102 | 75-95 year typical life | 75 | 95 | 85 | 7.713% | 25 | 2.269% | 123 | 11.16%
| Vaults | 61 | 75-95 year typical life | 75 | 95 | 3 | 4.918% | 0 | 0% | 10 | 16.39%