## Fig 4
Figure 4 – Density: Customers per Distribution Circuit km
ID num | Cust/Circ km
10 | 11.5696
38 | 12.8585
32 | 13.7113
40 | 17.0366
204 | 19.3803
30 | 20.0688
207 | 21.0567
42 | 26.6803
205 | 28.6237
26 | 32.0863
41 | 33.7233
206 | 34.3575
39 | 35.2431
43 | 37.6421
24 | 39.1174
35 | 40.9975
203 | 44.6113
46 | 45.9241
36 | 46.9057
45 | 48.8429
34 | 51.463
201 | 53.2768
48 | 56.1734
Questions Asked to Gather Data |  | Raw data will not be supplied for this graph.
ST0050.1Q | Please provide us with the average number of customers per month - ultimate consumers, metered customer locations - as reported to FERC.
ST0050.1 |  | Distribution End-Use Customers | Residential
ST0050.2 |  | Distribution End-Use Customers | Commercial
ST0050.3 |  | Distribution End-Use Customers | Industrial
ST0050.4 |  | Distribution End-Use Customers | Other
ST0050.5 |  | Distribution End-Use Customers | Total
ST0450.1Q | How many distribution primary circuit miles/kilometers were on your system at the end of last year?
ST0450.1 | Circuit Miles | Overhead Circuit miles/kilometers (primary) | Miles/Kilometers
ST0450.2 |  | Underground Residential Distribution Circuit Miles/Kilometers | Miles/Kilometers
ST0450.3 |  | Underground Network Circuit Miles/Kilometers | Miles/Kilometers
ST0450.100 |  | Total

## Fig 5
Figure 5 – Density: Customers per Square km
ID num | Cust per sq km
10 | 1.4325
38 | 22.7469
204 | 33.9634
32 | 41.4355
30 | 48.0111
42 | 60.9072
36 | 63.8685
207 | 68.3764
48 | 79.1258
206 | 89.8423
41 | 123.9589
26 | 134.5049
205 | 136.5057
43 | 220.1239
35 | 266.8348
39 | 314.205
24 | 349.072
40 | 352.4526
203 | 478.5574
46 | 489.3494
201 | 551.2475
34 | 705.9144
Questions Asked to Gather Data |  | Raw data will not be supplied for this graph.
ST0050.1Q | Please provide us with the average number of customers per month - ultimate consumers, metered customer locations - as reported to FERC.
ST0050.1 |  | Distribution End-Use Customers | Residential
ST0050.2 |  | Distribution End-Use Customers | Commercial
ST0050.3 |  | Distribution End-Use Customers | Industrial
ST0050.4 |  | Distribution End-Use Customers | Other
ST0050.5 |  | Distribution End-Use Customers | Total
ST0250.1Q | What was the number of square miles/kilometers in your service territory? The service territory demographics apply to distribution utilities with defined end-use delivery customers.
ST0250.1 |  | Square Miles/Kilometers in Service Territory

## Fig 6
Figure 6 – Pole Refurbishment Process
Companies | Subtext
19 | Yes
25 | Yes
32 | Yes
34 | Yes
35 | Yes
36 | Yes
39 | Yes
40 | Yes
41 | Yes
42 | Yes
43 | Yes
45 | Yes
46 | Yes
203 | Yes
204 | Yes
205 | Yes
206 | Yes
207 | Yes
10 | No
24 | No
26 | No
30 | No
Questions Asked to Gather Data |  | Raw data above
DP3500.1Q | Do you have a "pole refurbishment” practice?
DP3500.1 |  | Yes
DP3500.2 |  | No

## Fig 7
Figure 7 – Cycle Time (in Years) for Inspection Process of Distribution Wood Poles
- | Companies | 10 | 19 | 24 | 25 | 26 | 30 | 32 | 34 | 35 | 36 | 39 | 40 | 41 | 42 | 43 | 45 | 46 | 203 | 204 | 205 | 206 | 207
Patrol |  | - | - | 10 | 10 | 2 | 10 | - | 10 | 8 | 1 | 99 | 10 | - | - | 10 | - | 10 | 5 | - | - | - | -
Visual |  | 3 | 10 | 10 | 10 | 10 | 10 | - | 10 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 12 | 10 | 8 | 12
Sound |  | 15 | 10 | 10 | 10 | 10 | 10 | - | 10 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 10 | 8 | 12
Bore |  | 15 | 10 | 10 | 10 | 10 | 10 | - | 10 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 10 | 8 | 12
Excavation |  | - | 10 | 10 | 10 | - | 10 | - | 10 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | - | 10 | 8 | -
Other |  | - | - | 10 | 10 | - | - | 99 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Ultrasonic |  | - | - | 10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Questions Asked to Gather Data |  | Raw data above
DP3200.1Q | How often / what is your cycle time for doing each of these types of inspections (in years)?
DP3200.1 |  | Patrol | Years between inspections
DP3200.2 |  | Visual | Years between inspections
DP3200.3 |  | Sound | Years between inspections
DP3200.4 |  | Bore | Years between inspections
DP3200.5 |  | Excavation | Years between inspections
DP3200.6 |  | Ultrasonic | Years between inspections
DP3200.7 |  | Other | Years between inspections

## Fig 8
Figure 8 – Percentage of In-Service Poles Inspected in 2019
ID num | Percent
203 | 23.53%
35 | 15.27%
26 | 11.92%
36 | 11.78%
43 | 10.46%
46 | 10.37%
206 | 10.2%
39 | 10.05%
205 | 9.367%
10 | 7.247%
34 | 5.181%
30 | 4.363%
32 | 1.413%
24 | 1.292%
Questions Asked to Gather Data
DP3300.1Q | Please provide the number of pole inspections actually completed last year.
DP3300.3 |  | Number of pole inspections completed
ST0500.1Q | How many distribution poles were on your system at year end?
ST0500.1 |  | Poles: Owned and Maintained
ST0500.2 |  | Poles: Maintained only
ST0500.100 |  | Total
Raw data |  |  | Calculation
Quest # | ST0500.1 | DP3300.3
Subtext | Poles: Owned and Maintained | Number of pole inspections completed
203 | 61683 | 14512 | 23.53%
35 | 264870 | 40435 | 15.27%
26 | 202283 | 24118 | 11.92%
36 | 1213424 | 142974 | 11.78%
43 | 1386572 | 145024 | 10.46%
46 | 390000 | 40434 | 10.37%
206 | 979129 | 99871.158 | 10.2%
39 | 961852 | 96625 | 10.05%
205 | 874356 | 82189.464 | 9.4%
10 | 1604582 | 116288 | 7.247%
34 | 156833 | 8126 | 5.181%
30 | 229214 | 10000 | 4.363%
32 | 2151700 | 30406 | 1.413%
24 | 378353 | 4889 | 1.292%

## Fig 9
Figure 9 – Average Age of Distribution Wood Poles
ID num | Years
24 | 26.0786
48 | 26.6529
35 | 26.6841
34 | 30.0707
204 | 30.175
206 | 31.0882
207 | 32.2153
203 | 33.575
32 | 35.0897
38 | 35.2755
45 | 36.9459
36 | 37.379
205 | 37.5454
42 | 37.9938
30 | 38.772
41 | 39.072
10 | 39.4802
26 | 40.1937
Questions Asked to Gather Data
ST1650.1Q | How many of your current in-service distribution and secondary poles were installed in each time period listed below?
ST1650.1A |  | Wood | Pre 1960
ST1650.1B |  | Wood | 1960's |  | Calculation | ((ST1650.1A*65+
ST1650.1C |  | Wood | 1970's |  |  | ST1650.1B*55+
ST1650.1D |  | Wood | 1980's |  |  | ST1650.1C*45+
ST1650.1E |  | Wood | 1990's |  |  | ST1650.1D*35+
ST1650.1F |  | Wood | 2000-2009 |  |  | ST1650.1E*25+
ST1650.1G |  | Wood | Since 2010 |  |  | ST1650.1F*15+
ST1650.1H |  | Wood | Unknown |  |  | ST1650.1G*5+
ST1650.1H*35)/
ST1650.Total)
Raw Data | [8 empty] | Calculation
Company ID | ST1650.1A | ST1650.1B | ST1650.1C | ST1650.1D | ST1650.1E | ST1650.1F | ST1650.1G | ST1650.1H
24 | 6175 | 18455 | 31430 | 55041 | 68596 | 66768 | 57388 | 18327 | 26.0786
48 | 16078 | 56244 | 146457 | 163762 | 172149 | 133319 | 204444 |  | 26.6529
35 | 6246 | 35053 | 33019 | 56626 | 54454 | 34333 | 83688 |  | 26.6841
34 | 0 | 0 | 6 | 0 | 1 | 12266 | 12868 | 102932 | 30.0707
204 | 37987 | 141962 | 217734 | 234416 | 253971 | 204134 | 192873 | 12758 | 30.175
206 | 1978 | 105771 | 112721 | 216150 | 188755 | 119811 | 74554 | 3007 | 31.0882
207 | 8815 | 53843 | 122997 | 223600 | 95522 | 109602 | 170139 | 1255266 | 32.2153
203 | 7972 | 9013 | 8593 | 6446 | 7099 | 8371 | 11853 | 2863 | 33.575
32 | 40577 | 638083 | 301730 | 442804 | 299784 | 305960 | 255699 | 36299 | 35.0897
38 | 12815 | 20676 | 32855 | 59923 | 106246 | 0 | 0 |  | 35.2755
45 | 22165 | 31339 | 9598 | 11261 | 6172 | 847 | 32833 | 52319 | 36.9459
36 | 295579 | 246059 | 76450 | 100376 | 71452 | 137169 | 274547 |  | 37.379
205 | 163290 | 130205 | 148838 | 112979 | 122994 | 86942 | 121791 | 43545 | 37.5454
42 | 25424 | 24709 | 20466 | 17458 | 15179 | 9832 | 20720 | 30396 | 37.9938
30 | 24645 | 40643 | 48119 | 32922 | 39713 | 27134 | 7633 | 8405 | 38.772
41 | 38354 | 31786 | 34750 | 34848 | 33183 | 18289 | 17103 | 18392 | 39.072
10 | 416411 | 230636 | 297451 | 404294 | 220056 | 175376 | 183851 | 48612 | 39.4802
26 | 42086 | 32034 | 34665 | 29766 | 25376 | 18685 | 19078 | 499 | 40.1937

## Fig 10
Figure 10 -- Percentage of Current In-Service Distribution and Secondary Wood Poles
Installed by Decade
ID num | Pre 1960 | 1960's | 1970's | 1980's | 1990's | 2000-2009 | Since 2010 | Unknown
34 | 0% | 0% | 0.004685% | 0% | 0.0007808% | 9.577% | 10.05% | 80.37%
206 | 0.2404% | 12.86% | 13.7% | 26.27% | 22.94% | 14.56% | 9.062% | 0.3655%
207 | 0.4322% | 2.64% | 6.03% | 10.96% | 4.683% | 5.373% | 8.341% | 61.54%
32 | 1.748% | 27.49% | 13% | 19.08% | 12.92% | 13.18% | 11.02% | 1.564%
48 | 1.802% | 6.302% | 16.41% | 18.35% | 19.29% | 14.94% | 22.91% | 0%
24 | 1.917% | 5.728% | 9.755% | 17.08% | 21.29% | 20.72% | 17.81% | 5.688%
35 | 2.059% | 11.55% | 10.88% | 18.66% | 17.95% | 11.32% | 27.58% | 0%
204 | 2.931% | 10.96% | 16.8% | 18.09% | 19.6% | 15.75% | 14.88% | 0.9845%
38 | 5.511% | 8.892% | 14.13% | 25.77% | 45.69% | 0% | 0% | 0%
30 | 10.75% | 17.73% | 20.99% | 14.36% | 17.33% | 11.84% | 3.33% | 3.667%
203 | 12.81% | 14.49% | 13.81% | 10.36% | 11.41% | 13.46% | 19.05% | 4.602%
45 | 13.31% | 18.82% | 5.763% | 6.762% | 3.706% | 0.5086% | 19.72% | 31.42%
42 | 15.49% | 15.05% | 12.47% | 10.63% | 9.245% | 5.988% | 12.62% | 18.51%
41 | 16.92% | 14.02% | 15.33% | 15.37% | 14.64% | 8.067% | 7.544% | 8.113%
205 | 17.55% | 13.99% | 15.99% | 12.14% | 13.22% | 9.343% | 13.09% | 4.679%
26 | 20.82% | 15.84% | 17.14% | 14.72% | 12.55% | 9.241% | 9.436% | 0.2468%
10 | 21.07% | 11.67% | 15.05% | 20.45% | 11.13% | 8.872% | 9.301% | 2.459%
36 | 24.6% | 20.48% | 6.362% | 8.353% | 5.946% | 11.42% | 22.85% | 0%
Questions Asked to Gather Data
ST1650.1Q | How many of your current in-service distribution and secondary poles were installed in each time period listed below?
ST1650.1A |  | Wood | Pre 1960
ST1650.1B |  | Wood | 1960's
ST1650.1C |  | Wood | 1970's
ST1650.1D |  | Wood | 1980's
ST1650.1E |  | Wood | 1990's
ST1650.1F |  | Wood | 2000-2009
ST1650.1G |  | Wood | Since 2010
ST1650.1H |  | Wood | Unknown
ST1650.1T |  | Wood | Total
Raw Data | [9 empty] | Calculation
Company ID | Pre 1960 | 1960's | 1970's | 1980's | 1990's | 2000-2009 | Since 2010 | Unknown |  | Pre 1960 | 1960's | 1970's | 1980's | 1990's | 2000-2009 | Since 2010 | Unknown
34 | 0 | 0 | 6 | 0 | 1 | 12266 | 12868 | 102932 | 128073 | 0% | 0% | 0.004685% | 0% | 0.0007808% | 9.577% | 10.05% | 80.37%
206 | 1978 | 105771 | 112721 | 216150 | 188755 | 119811 | 74554 | 3007 | 822747 | 0.2404% | 12.86% | 13.7% | 26.27% | 22.94% | 14.56% | 9.062% | 0.3655%
207 | 8815 | 53843 | 122997 | 223600 | 95522 | 109602 | 170139 | 1255266 | 2039784 | 0.4322% | 2.64% | 6.03% | 10.96% | 4.683% | 5.373% | 8.341% | 61.54%
32 | 40577 | 638083 | 301730 | 442804 | 299784 | 305960 | 255699 | 36299 | 2320936 | 1.748% | 27.49% | 13% | 19.08% | 12.92% | 13.18% | 11.02% | 1.564%
48 | 16078 | 56244 | 146457 | 163762 | 172149 | 133319 | 204444 | 0 | 892453 | 1.802% | 6.302% | 16.41% | 18.35% | 19.29% | 14.94% | 22.91% | 0%
24 | 6175 | 18455 | 31430 | 55041 | 68596 | 66768 | 57388 | 18327 | 322180 | 1.917% | 5.728% | 9.755% | 17.08% | 21.29% | 20.72% | 17.81% | 5.688%
35 | 6246 | 35053 | 33019 | 56626 | 54454 | 34333 | 83688 | 0 | 303419 | 2.059% | 11.55% | 10.88% | 18.66% | 17.95% | 11.32% | 27.58% | 0%
204 | 37987 | 141962 | 217734 | 234416 | 253971 | 204134 | 192873 | 12758 | 1295835 | 2.931% | 10.96% | 16.8% | 18.09% | 19.6% | 15.75% | 14.88% | 0.9845%
38 | 12815 | 20676 | 32855 | 59923 | 106246 | 0 | 0 | 0 | 232515 | 5.511% | 8.892% | 14.13% | 25.77% | 45.69% | 0% | 0% | 0%
30 | 24645 | 40643 | 48119 | 32922 | 39713 | 27134 | 7633 | 8405 | 229214 | 10.75% | 17.73% | 20.99% | 14.36% | 17.33% | 11.84% | 3.33% | 3.667%
203 | 7972 | 9013 | 8593 | 6446 | 7099 | 8371 | 11853 | 2863 | 62210 | 12.81% | 14.49% | 13.81% | 10.36% | 11.41% | 13.46% | 19.05% | 4.602%
45 | 22165 | 31339 | 9598 | 11261 | 6172 | 847 | 32833 | 52319 | 166534 | 13.31% | 18.82% | 5.763% | 6.762% | 3.706% | 0.5086% | 19.72% | 31.42%
42 | 25424 | 24709 | 20466 | 17458 | 15179 | 9832 | 20720 | 30396 | 164184 | 15.49% | 15.05% | 12.47% | 10.63% | 9.245% | 5.988% | 12.62% | 18.51%
41 | 38354 | 31786 | 34750 | 34848 | 33183 | 18289 | 17103 | 18392 | 226705 | 16.92% | 14.02% | 15.33% | 15.37% | 14.64% | 8.067% | 7.544% | 8.113%
205 | 163290 | 130205 | 148838 | 112979 | 122994 | 86942 | 121791 | 43545 | 930584 | 17.55% | 13.99% | 15.99% | 12.14% | 13.22% | 9.343% | 13.09% | 4.679%
26 | 42086 | 32034 | 34665 | 29766 | 25376 | 18685 | 19078 | 499 | 202189 | 20.82% | 15.84% | 17.14% | 14.72% | 12.55% | 9.241% | 9.436% | 0.2468%
10 | 416411 | 230636 | 297451 | 404294 | 220056 | 175376 | 183851 | 48612 | 1976687 | 21.07% | 11.67% | 15.05% | 20.45% | 11.13% | 8.872% | 9.301% | 2.459%
36 | 295579 | 246059 | 76450 | 100376 | 71452 | 137169 | 274547 | 0 | 1201632 | 24.6% | 20.48% | 6.362% | 8.353% | 5.946% | 11.42% | 22.85% | 0%

## Fig 11
Figure 11 – Percentage of Distribution Wood Poles Replaced and
Planned or Projected to be Replaced Annually
ID num | Last 5 Years | Next 5 Years
10 | 1.18% | 1.1%
38 | 0.8% | 0.8%
203 | 0.8% | 1.2%
26 | 0.31% | 0.66%
25 | 0.3% | 0.4%
34 | 0.26% | 0.26%
30 | 0.18% | 0.76%
Questions Asked to Gather Data
AM0350.1Q | What percent of components were replaced in the last 5 years? (include all actual component replacements for all reasons, regardless of whether they were paid for as O&M or as capital)
AM0350.1 |  | Transformers | % Replaced - Planned Program
AM0350.2 |  | Wood Poles | % Replaced - Planned Program
AM0350.3 |  | Transformers | % Replaced - Other Reasons
AM0350.4 |  | Wood Poles | % Replaced - Other Reasons
AM0400.1Q | What percent of components are you planning or expecting to replace in the next 5 years? (include all expected component replacements for all reasons)
AM0400.1 |  | Transformers | % Replaced - Planned Program
AM0400.2 |  | Wood Poles | % Replaced - Planned Program
AM0400.3 |  | Transformers | % Replaced - Other Reasons
AM0400.4 |  | Wood Poles | % Replaced - Other Reasons
Raw Data |  |  |  |  | Calculation
Quest # | AM0350.2 | AM0350.4 | AM0400.2 | AM0400.4
Subtext | Wood Poles | Wood Poles | Wood Poles | Wood Poles
Detail | % Replaced - Planned Program | % Replaced - Other Reasons | % Replaced - Planned Program | % Replaced - Other Reasons | % Replaced - Planned Program | % Replaced - Other Reasons | % Replaced - Planned Program | % Replaced - Other Reasons | Last 5 Years | Next 5 Years
Company ID
10 | 2.8 | 3.1 | 2.4 | 3.1 | 0.56 | 0.62 | 0.48 | 0.62 | 1.18 | 1.1
38 | 3 | 1 | 3 | 1 | 0.6 | 0.2 | 0.6 | 0.2 | 0.8 | 0.8
203 | 1 | 3 | 5 | 1 | 0.2 | 0.6 | 1 | 0.2 | 0.8 | 1.2
26 | 1.55 | 0 | 3.3 | 0 | 0.31 | 0 | 0.66 | 0 | 0.31 | 0.66
25 | 1 | 0.5 | 1.5 | 0.5 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | 0.4
34 | 0.32 | 1 | 0.32 | 1 | 0.064 | 0.2 | 0.064 | 0.2 | 0.264 | 0.264
30 | 0.8 | 0.3 | 1.6 | 2.2 | 0.16 | 0.06 | 0.32 | 0.44 | 0.22 | 0.76

## Fig 12
Figure 12 -- Percent of Total In-Service Poles on List for Replacement at End of 2019
ID Num | Percent
43 | 0.06195%
40 | 0.2962%
36 | 0.4134%
39 | 0.4807%
46 | 0.641%
30 | 0.7979%
24 | 1.269%
34 | 1.308%
26 | 1.533%
10 | 4.616%
Questions Asked to Gather Data
DP3800.1Q | As of the end of last year, how many wood poles were in your work backlog for replacement or refurbishment?
DP3800.1 | Backlog | # of Poles to be Replaced
DP3800.2 |  | # of Poles to be Refurbished
ST0500.1Q | How many distribution poles were on your system at year end?
ST0500.1 |  | Poles: Owned and Maintained
ST0500.2 |  | Poles: Maintained only
ST0500.100 |  | Total
Raw Data |  |  | Calculation
Quest # | DP3800.1 | ST0500.1
Subtext | # of Poles to be Replaced | Poles: Owned and Maintained
Company ID
43 | 859 | 1386572 | 0.06195%
40 | 1072 | 361972 | 0.2962%
36 | 5016 | 1213424 | 0.4134%
39 | 4624 | 961852 | 0.4807%
46 | 2500 | 390000 | 0.641%
30 | 1829 | 229214 | 0.7979%
24 | 4800 | 378353 | 1.269%
34 | 2052 | 156833 | 1.308%
26 | 3102 | 202283 | 1.533%
10 | 74065 | 1604582 | 4.616%
#DIV/0!

## Fig 13
Figure 13 -- Months to Replace or Refurbish a Pole After a Failed Inspection
ID num | Replacement | Refurbishment
34 | 2 | -
203 | 6 | 3
40 | 10 | 3
19 | 12 | 1
25 | 12 | 12
39 | 12 | 12
41 | 12 | 12
42 | 12 | 12
45 | 12 | 12
46 | 12 | 6
35 | 15 | 2
43 | 18 | 4
30 | 19 | -
36 | 19.8 | 18.7
26 | 24 | -
10 | 46 | -
Questions Asked to Gather Data |  | Raw data above
DP3650.1Q | On average, how long does it take to replace or refurbish a pole after a failed inspection?
DP3650.1 |  | Pole Replacement | Months After Failed Inspection
DP3650.2 |  | Pole Refurbishment | Months After Failed Inspection

## Fig 14
Figure 14 -- Spending on Pole Replacement per Pole Replaced
ID num | Direct Labor | Labor Overhead | Equipment | Materials | Contract Labor | Other
46 | 0 | 0 | 0 | 0 | 0 | 1618.75 | 1618.75
30 | 156.8145 | 86.2481 | 23.8095 | 443.7519 | 2919.3722 | 0 | 3629.9962
39 | 0 | 0 | 0 | 1112.918 | 4917.5237 | 0 | 6030.4417
24 | 1284.3273 | 1168.2226 | 191.0474 | 766.1083 | 2819.2114 | 0 | 6228.917
10 | 5859.7362 | 1276.4262 | 1598.8965 | 960.4486 | 1132.5313 | 162.0908 | 10990.1296
34 | 9015.0662 | 1748.8913 | 0 | 906.2391 | 0 | 0 | 11670.1966
203 | 5196.7213 | 819.6721 | 1229.5082 | 2360.6557 | 2185.7923 | 0 | 11792.3497
43 | 3180.4848 | 0 | 0 | 1553.92 | 8672.2024 | 0 | 13406.6073
36 | 693.3217 | 147.6775 | 0 | 2998.2458 | 11327.255 | 0 | 15166.5001
26 | 1202.977 | 726.839 | 563.747 | 1124.0027 | 13409.1719 | 0 | 17026.7375
40 | 5545.9034 | 2562.9586 | 714.6368 | 2919.0759 | 9762.7057 | 0 | 21505.2805
Questions Asked to Gather Data
DP3700.1Q | How many wood poles did you replace or refurbish last year?
DP3700.1 |  | # of Poles Replaced - Programmatic
DP3700.2 |  | # of Poles Replaced - Emergency Replacement
DP3700.3 |  | # of Poles Refurbished
DP3850.1Q | What did you spend on planned pole REPLACEMENT last year? (This includes the cost of pole replacement and any other components attached to the pole. This is likely to be tracked as a capital cost).
DP3850.1 |  | Company Direct Labor ($)
DP3850.2 |  | Company Direct Labor Overheads ($)
DP3850.3 |  | Equipment Cost ($)
DP3850.4 |  | Material Cost ($)
DP3850.5 |  | Contract Labor / Services Cost ($)
DP3850.6 |  | Breakdown Unavailable
DP3850.7 |  | Company Labor (Hours)
Raw Data | [8 empty] | Calculation
Quest # | DP3850.1 | DP3850.2 | DP3850.3 | DP3850.4 | DP3850.5 | DP3850.6 |  | DP3700.1
Subtext | Company Direct Labor ($) | Company Direct Labor Overheads ($) | Equipment Cost ($) | Material Cost ($) | Contract Labor / Services Cost ($) | Breakdown Unavailable |  | # of Poles Replaced - Programmatic
Company ID
46 | - | - | - | - | - | 1942500 |  | 1200 | 1618.75
30 | 125138 | 68826 | 19000 | 354114 | 2329659 | - |  | 798 | 3629.9962
39 | - | - | - | 3350996 | 14806664 | - |  | 3011 | 6030.4417
24 | 2218033.33 | 2017520.42 | 329938.8 | 1323069.02 | 4868778.05 | - |  | 1727 | 6228.917
10 | 25689083.39 | 5595852.45 | 7009562.1 | 4210606.63 | 4965017.32 | 710606.16 |  | 4384 | 10990.1296
34 | 1244079.13 | 241347 | - | 125061 | - | - |  | 138 | 11670.1966
203 | 951000 | 150000 | 225000 | 432000 | 400000 | - |  | 183 | 11792.3497
43 | 10778663 | - | - | 5266235 | 29390094 | - |  | 3389 | 13406.6073
36 | 11391275.51 | 2426341.6836 | - | 49261179.05 | 186106800.1 | - |  | 16430 | 15166.5001
26 | 1778000 | 1074268 | 833218 | 1661276 | 19818756 | - |  | 1478 | 17026.7375
40 | 2412468 | 1114887 | 310867 | 1269798 | 4246777 | - |  | 435 | 21505.2805

## Fig 15
Figure 15 – Distribution Substations In-Service, By Region
ID num | Urban | Mixed / Suburban | Rural | Not Classified
34 | 21.67% | 70% | 8.333% | 0%
48 | 0% | 0% | 0% | 100%
39 | 0% | 0% | 0% | 100%
24 | 0% | 0% | 0% | 100%
203 | 7.692% | 92.31% | 0% | 0%
10 | 29.78% | 0% | 70.22% | 0%
30 | 64.79% | 0% | 35.21% | 0%
26 | 63.58% | 23.18% | 10.6% | 2.649%
19 | 100% | 0% | 0% | 0%
35 | 0% | 0% | 0% | 100%
Questions Asked to Gather Data
ST0875.1Q | How many distribution substations do you currently have in service in each category? (e.g. 5 substations are rural with 1 transformer). Total should equal ST0850.6
ST0875.1 |  | 1 Xfrmr stations | Urban
ST0875.2 |  | 2 Xfrmr stations | Urban
ST0875.3 |  | 3 Xfrmr stations | Urban
ST0875.4 |  | 4 or more Xfrmr stations | Urban
ST0875.5 |  | 1 Xfrmr stations | Mixed/Suburban
ST0875.6 |  | 2 Xfrmr stations | Mixed/Suburban
ST0875.7 |  | 3 Xfrmr stations | Mixed/Suburban
ST0875.8 |  | 4 or more Xfrmr stations | Mixed/Suburban
ST0875.9 |  | 1 Xfrmr stations | Rural
ST0875.10 |  | 2 Xfrmr stations | Rural
ST0875.11 |  | 3 Xfrmr stations | Rural
ST0875.12 |  | 4 or more Xfrmr stations | Rural
ST0875.13 |  | 1 Xfrmr stations | Not Classified
ST0875.14 |  | 2 Xfrmr stations | Not Classified
ST0875.15 |  | 3 Xfrmr stations | Not Classified
ST0875.16 |  | 4 or more Xfrmr stations | Not Classified
Raw Data | [16 empty] | Calculated Data
Quest # | ST0875.1 | ST0875.2 | ST0875.3 | ST0875.4 | ST0875.5 | ST0875.6 | ST0875.7 | ST0875.8 | ST0875.9 | ST0875.10 | ST0875.11 | ST0875.12 | ST0875.13 | ST0875.14 | ST0875.15 | ST0875.16 |  |  |  |  | ST0850.1 | ST0850.2 | ST0850.3 | ST0850.4 | ST0850.5 | ST0850.6 | ST0850.7
Detail | Urban | Urban | Urban | Urban | Mixed/Suburban | Mixed/Suburban | Mixed/Suburban | Mixed/Suburban | Rural | Rural | Rural | Rural | Not Classified | Not Classified | Not Classified | Not Classified | Urban | Mixed/Suburban | Rural | Not Classified | Statistics | Statistics | Statistics | Statistics | Statistics | Statistics | Statistics
Company ID
34 | - | 6 | 3 | 4 | 2 | 18 | 13 | 9 | 2 | 2 | 1 | 0 | - | - | - | - | 21.67% | 70% | 8.333% | 0% | - | - | - | 169 | 604 | 60 | -
48 | - | - | - | - | - | - | - | - | - | - | - | - | 55 | 112 | 24 | 6 | 0% | 0% | 0% | 100% | 17078.354 | - | - | 380 | 2431 | 197 | 0
39 | - | - | - | - | - | - | - | - | - | - | - | - | 9 | 98 | 86 | 25 | 0% | 0% | 0% | 100% | 33654 | 47 | - | 575 | 2660 | 218 | 32
24 | - | - | - | - | - | - | - | - | - | - | - | - | 15 | 42 | 27 | 13 | 0% | 0% | 0% | 100% | 12865 | 40 | 47 | 228 | 1414 | 94 | 5
203 | 0 | 0 | 3 | 0 | 2 | 19 | 7 | 8 | - | - | - | - | - | - | - | - | 7.692% | 92.31% | 0% | 0% | 4396 | 39 | 42 | 110 | 316 | 39 | 0
10 | 261 | 32 | 3 | 0 | 0 | 0 | 0 | 0 | 600 | 89 | 8 | 1 | 0 | 0 | 0 | 0 | 29.78% | 0% | 70.22% | 0% | 8789 | 67 | - | 1193 | 155 | 994 | 0
30 | 5 | 24 | 9 | 8 | - | - | - | - | 8 | 6 | 3 | 8 | - | - | - | - | 64.79% | 0% | 35.21% | 0% | 4598 | - | - | 229 | 936 | 71 | 7
26 | 27 | 55 | 10 | 4 | 20 | 13 | 1 | 1 | 11 | 5 | 0 | 0 | 1 | 3 | 0 | 0 | 63.58% | 23.18% | 10.6% | 2.649% | 6689 | 50 | 57 | 272 | 643 | 151 | 0
19 | 12 | 104 | 19 | 17 | - | - | - | - | - | - | - | - | - | - | - | - | 100% | 0% | 0% | 0% | 8300 | 63 | - | 359 | - | 152 | 0
35 | - | - | - | - | - | - | - | - | - | - | - | - | 69 | 90 | - | 1 | 0% | 0% | 0% | 100% | 26589 | - | - | 283 | 1327 | 160 | -

## Fig 16
Figure 16 -- Distribution Substations In Service, By Number of Transformers
ID Num | 1 Xfrmr station | 2 Xfrmr station | 3 Xfrmr station | 4 or more Xfrmr station
34 | 6.667% | 43.33% | 28.33% | 21.67%
48 | 27.92% | 56.85% | 12.18% | 3.046%
39 | 4.128% | 44.95% | 39.45% | 11.47%
24 | 15.96% | 42.55% | 28.72% | 12.77%
203 | 5.128% | 48.72% | 25.64% | 20.51%
10 | 86.62% | 12.17% | 1.107% | 0.1006%
30 | 18.31% | 42.25% | 16.9% | 22.54%
26 | 39.07% | 50.33% | 7.285% | 3.311%
19 | 7.895% | 68.42% | 12.5% | 11.18%
35 | 43.12% | 56.25% | 0% | 0.625%
Questions Asked to Gather Data
ST0875.1Q | How many distribution substations do you currently have in service in each category? (e.g. 5 substations are rural with 1 transformer). Total should equal ST0850.6
ST0875.1 |  | 1 Xfrmr stations | Urban
ST0875.2 |  | 2 Xfrmr stations | Urban
ST0875.3 |  | 3 Xfrmr stations | Urban
ST0875.4 |  | 4 or more Xfrmr stations | Urban
ST0875.5 |  | 1 Xfrmr stations | Mixed/Suburban
ST0875.6 |  | 2 Xfrmr stations | Mixed/Suburban
ST0875.7 |  | 3 Xfrmr stations | Mixed/Suburban
ST0875.8 |  | 4 or more Xfrmr stations | Mixed/Suburban
ST0875.9 |  | 1 Xfrmr stations | Rural
ST0875.10 |  | 2 Xfrmr stations | Rural
ST0875.11 |  | 3 Xfrmr stations | Rural
ST0875.12 |  | 4 or more Xfrmr stations | Rural
ST0875.13 |  | 1 Xfrmr stations | Not Classified
ST0875.14 |  | 2 Xfrmr stations | Not Classified
ST0875.15 |  | 3 Xfrmr stations | Not Classified
ST0875.16 |  | 4 or more Xfrmr stations | Not Classified
Raw Data | [16 empty] | Calculated Data
Quest # | ST0875.1 | ST0875.2 | ST0875.3 | ST0875.4 | ST0875.5 | ST0875.6 | ST0875.7 | ST0875.8 | ST0875.9 | ST0875.10 | ST0875.11 | ST0875.12 | ST0875.13 | ST0875.14 | ST0875.15 | ST0875.16
Subtext | 1 Xfrmr stations | 2 Xfrmr stations | 3 Xfrmr stations | 4 or more Xfrmr stations | 1 Xfrmr stations | 2 Xfrmr stations | 3 Xfrmr stations | 4 or more Xfrmr stations | 1 Xfrmr stations | 2 Xfrmr stations | 3 Xfrmr stations | 4 or more Xfrmr stations | 1 Xfrmr stations | 2 Xfrmr stations | 3 Xfrmr stations | 4 or more Xfrmr stations | 1 Xfrmr stations | 2 Xfrmr stations | 3 Xfrmr stations | 4 or more Xfrmr stations
Company ID
34 | - | 6 | 3 | 4 | 2 | 18 | 13 | 9 | 2 | 2 | 1 | 0 | - | - | - | - | 6.667% | 43.33% | 28.33% | 21.67%
48 | - | - | - | - | - | - | - | - | - | - | - | - | 55 | 112 | 24 | 6 | 27.92% | 56.85% | 12.18% | 3.046%
39 | - | - | - | - | - | - | - | - | - | - | - | - | 9 | 98 | 86 | 25 | 4.128% | 44.95% | 39.45% | 11.47%
24 | - | - | - | - | - | - | - | - | - | - | - | - | 16 | 43 | 29 | 13 | 15.84% | 42.57% | 28.71% | 12.87%
203 | 0 | 0 | 3 | 0 | 2 | 19 | 7 | 8 | - | - | - | - | - | - | - | - | 5.128% | 48.72% | 25.64% | 20.51%
10 | 261 | 32 | 3 | 0 | 0 | 0 | 0 | 0 | 600 | 89 | 8 | 1 | 0 | 0 | 0 | 0 | 86.62% | 12.17% | 1.107% | 0.1006%
30 | 5 | 24 | 9 | 8 | - | - | - | - | 8 | 6 | 3 | 8 | - | - | - | - | 18.31% | 42.25% | 16.9% | 22.54%
26 | 27 | 55 | 10 | 4 | 20 | 13 | 1 | 1 | 11 | 5 | 0 | 0 | 1 | 3 | 0 | 0 | 39.07% | 50.33% | 7.285% | 3.311%
19 | 12 | 104 | 19 | 17 | - | - | - | - | - | - | - | - | - | - | - | - | 7.895% | 68.42% | 12.5% | 11.18%
35 | - | - | - | - | - | - | - | - | - | - | - | - | 69 | 90 | - | 1 | 43.12% | 56.25% | 0% | 0.625%

## Fig 17
Figure 17 -- Average Substation Transformer Loading at Peak: Distribution
ID Num | Percent
10 | 67%
43 | 66%
19 | 63%
38 | 50%
26 | 50%
39 | 47%
40 | 44%
47 | 44%
24 | 40%
203 | 39%
Questions Asked to Gather Data |  | Raw Data Above
ST0850.1Q | Please provide the following distribution substation statistics.
ST0850.2 |  | Average Transformer loading at Peak [%] | Statistics

## Fig 18
Figure 18 -- Distribution Substation Transformer Banks by Voltage Level
ID Num | 5kV class = >1kV, <=9kV | 15kV class = >9kV, <=15kV | 25kV class = >15kV to <=26kV | 35kV class = >26kV to <=36kV | 44kV class = >36kV to <=44kV
46 | 71.7% | 20.71% | 0% | 7.595% | 0%
10 | 56.75% | 24.56% | 4.737% | 10.26% | 3.684%
42 | 32.3% | 36.58% | 20.62% | 10.51% | 0%
36 | 28.98% | 51.12% | 15.8% | 4.101% | 0%
25 | 17.31% | 70.23% | 11.71% | 0.6944% | 0.0463%
43 | 17.07% | 65.37% | 0.579% | 16.86% | 0.1287%
19 | 15% | 85% | 0% | 0% | 0%
45 | 14.04% | 81.87% | 0% | 4.094% | 0%
41 | 10.67% | 74.72% | 5.618% | 8.989% | 0%
40 | 10.14% | 69.37% | 0% | 20.5% | 0%
32 | 9.909% | 63.89% | 24.07% | 2.128% | 0%
38 | 9.907% | 85.23% | 4.299% | 0.5607% | 0%
48 | 7.812% | 29.24% | 62.95% | 0% | 0%
30 | 6.55% | 93.45% | 0% | 0% | 0%
24 | 1.695% | 68.22% | 0% | 30.08% | 0%
39 | 0.8696% | 69.04% | 0% | 30.09% | 0%
201 | 0% | 16.67% | 0% | 26.67% | 56.67%
34 | 0% | 96.45% | 0% | 3.55% | 0%
203 | 0% | 76.92% | 23.08% | 0% | 0%
26 | 0% | 96.32% | 0% | 3.676% | 0%
35 | 0% | 100% | 0% | 0% | 0%
Questions Asked to Gather Data
ST0750.1Q | How many distribution substation transformers were on your system in each voltage class? [Determine distribution by low-side voltage]
ST0750.1 |  | 5kV class = >1kV, <=9kV | Transformers
ST0750.2 |  | 15kV class = >9kV, <=15kV | Transformers
ST0750.3 |  | 25kV class = >15kV to <=26kV | Transformers
ST0750.4 |  | 35kV class = >26kV to <=36kV | Transformers
ST0750.5 |  | 44kV class = >36kV to <=44kV | Transformers
ST0750.100 |  | Total
Raw Data | [6 empty] | Calculated Data
Quest # | ST0750.1 | ST0750.2 | ST0750.3 | ST0750.4 | ST0750.5 | ST0750.100
Subtext | 5kV class = >1kV, <=9kV | 15kV class = >9kV, <=15kV | 25kV class = >15kV to <=26kV | 35kV class = >26kV to <=36kV | 44kV class = >36kV to <=44kV | Total | 5kV class = >1kV, <=9kV | 15kV class = >9kV, <=15kV | 25kV class = >15kV to <=26kV | 35kV class = >26kV to <=36kV | 44kV class = >36kV to <=44kV
Company ID
46 | 793 | 229 | 0 | 84 | 0 | 1106 | 71.7% | 20.71% | 0% | 7.595% | 0% | 100%
10 | 647 | 280 | 54 | 117 | 42 | 1140 | 56.75% | 24.56% | 4.737% | 10.26% | 3.684% | 100%
42 | 83 | 94 | 53 | 27 | 0 | 257 | 32.3% | 36.58% | 20.62% | 10.51% | 0% | 100%
36 | 530 | 935 | 289 | 75 | 0 | 1829 | 28.98% | 51.12% | 15.8% | 4.101% | 0% | 100%
25 | 374 | 1517 | 253 | 15 | 1 | 2160 | 17.31% | 70.23% | 11.71% | 0.6944% | 0.0463% | 100%
43 | 796 | 3048 | 27 | 786 | 6 | 4663 | 17.07% | 65.37% | 0.579% | 16.86% | 0.1287% | 100%
19 | 54 | 306 | 0 | 0 | 0 | 360 | 15% | 85% | 0% | 0% | 0% | 100%
45 | 48 | 280 | 0 | 14 | 0 | 342 | 14.04% | 81.87% | 0% | 4.094% | 0% | 100%
41 | 19 | 133 | 10 | 16 | 0 | 178 | 10.67% | 74.72% | 5.618% | 8.989% | 0% | 100%
40 | 45 | 308 | 0 | 91 | 0 | 444 | 10.14% | 69.37% | 0% | 20.5% | 0% | 100%
32 | 163 | 1051 | 396 | 35 | 0 | 1645 | 9.909% | 63.89% | 24.07% | 2.128% | 0% | 100%
38 | 53 | 456 | 23 | 3 | 0 | 535 | 9.907% | 85.23% | 4.299% | 0.5607% | 0% | 100%
48 | 35 | 131 | 282 | 0 | 0 | 448 | 7.812% | 29.24% | 62.95% | 0% | 0% | 100%
30 | 15 | 214 | 0 | 0 | 0 | 229 | 6.55% | 93.45% | 0% | 0% | 0% | 100%
24 | 4 | 161 | 0 | 71 | 0 | 236 | 1.695% | 68.22% | 0% | 30.08% | 0% | 100%
39 | 5 | 397 | 0 | 173 | 0 | 575 | 0.8696% | 69.04% | 0% | 30.09% | 0% | 100%
201 | 0 | 40 | 0 | 64 | 136 | 240 | 0% | 16.67% | 0% | 26.67% | 56.67% | 100%
34 | 0 | 80 | 24 | 0 | 0 | 104 | 0% | 76.92% | 23.08% | 0% | 0% | 100%
203 | 0 | 262 | 0 | 10 | 0 | 272 | 0% | 96.32% | 0% | 3.676% | 0% | 100%
26 | 0 | 163 | 0 | 6 | 0 | 169 | 0% | 96.45% | 0% | 3.55% | 0% | 100%
35 | 0 | 283 | 0 | 0 | 0 | 283 | 0% | 100% | 0% | 0% | 0% | 100%

## Fig 19
Figure 19 – Installed Distribution MVA Capacity per 1000 Customers
ID Num | MVA per 1000 Customers
201 | 2.4112
10 | 6.3837
36 | 6.4051
25 | 6.4236
26 | 7.5156
43 | 7.9863
48 | 8.1966
203 | 8.4352
41 | 9.734
45 | 11.437
30 | 11.9013
39 | 13.3104
42 | 14.4157
24 | 15.1168
32 | 15.5813
40 | 23.3267
35 | 34.1487
Questions Asked to Gather Data |  | Raw Data Not Provided
ST0850.1Q | Please provide the following distribution substation statistics.
ST0850.1 |  | Installed MVA Capacity | Statistics
ST0050.1Q | Please provide us with the average number of customers per month - ultimate consumers, metered customer locations - as reported to FERC.
ST0050.1 |  | Distribution End-Use Customers | Residential
ST0050.2 |  | Distribution End-Use Customers | Commercial
ST0050.3 |  | Distribution End-Use Customers | Industrial
ST0050.4 |  | Distribution End-Use Customers | Other
ST0050.5 |  | Distribution End-Use Customers | Total

## Fig 20
Figure 20 -- Average Expected Service Life for Distribution Substation Equipment
| Group | Hydro One
Power Transformers | 47.9091 | 50
Low Side Breakers / Reclosers / Bus-Ties | 38.3636 | 40
Relays and Control Wiring | 29.7143 | 20
Switch Gear Control Panels | 38.8571 | 50
DC Components | 25.25 | 20
Metering | 32.1429 | 15
Questions Asked to Gather Data
AM0425.1Q | What is your expected service life of Distribution substation equipment components?
AM0425.1 |  | Power Transformers | Age (Years)
AM0425.2 |  | High Side Breakers / Switch Fuse Units / Bus-Ties | Age (Years)
AM0425.3 |  | Low Side Breakers / Reclosers / Bus-Ties | Age (Years)
AM0425.4 |  | Relays and Control Wiring | Age (Years)
AM0425.5 |  | Switch Gear Control Panels | Age (Years)
AM0425.6 |  | DC Components | Age (Years)
AM0425.7 |  | Metering | Age (Years)
Raw Data
Quest # | AM0425.1 | AM0425.2 | AM0425.3 | AM0425.4 | AM0425.5 | AM0425.6 | AM0425.7
Subtext | Power Transformers | High Side Breakers / Switch Fuse Units / Bus-Ties | Low Side Breakers / Reclosers / Bus-Ties | Relays and Control Wiring | Switch Gear Control Panels | DC Components | Metering
Detail | Age (Years) | Age (Years) | Age (Years) | Age (Years) | Age (Years) | Age (Years) | Age (Years)
Company ID
10 | 50 | 40 | 40 | 20 | 50 | 20 | 15
19 | 45 | 45 | 45 | - | - | - | -
24 | 50 | 40 | 40 | - | 40 | - | -
26 | 55 | 40 | 35 | 35 | 20 | 20 | 20
30 | 50 | 40 | 40 | - | 40 | 15 | -
33 | 45 | 30 | 30 | - | - | - | 30
34 | 35 | 35 | 35 | 30 | 30 | 35 | 35
35 | 42 | 42 | 42 | 42 | 42 | 42 | 42
36 | 30 | 30 | 30 | 30 | - | 20 | -
38 | 60 | 30 | 30 | 30 | 50 | 25 | 50
48 | 65 | 40 | 55 | 21 | - | 25 | 33
Calculated Data | 47.9091 | 37.4545 | 38.3636 | 29.7143 | 38.8571 | 25.25 | 32.1429

## Fig 21
Figure 21 -- Average Age of Distribution Substation Power Transformers
ID Num | Age
24 | 17.8634
34 | 20.858
39 | 24.7913
38 | 25.3717
35 | 26.3428
42 | 26.9008
203 | 28.8182
30 | 33.9083
26 | 35.8929
36 | 36.1744
45 | 36.2174
32 | 37.076
48 | 37.5263
10 | 37.7913
41 | 37.963
46 | 55.3788
Questions Asked to Gather Data
ST1750.1Q | How many of your current in-service distribution substation equipment components were manufactured in each time period?
ST1750.1A |  | Power Transformers | Pre 1960
ST1750.1B |  | Power Transformers | 1960's
ST1750.1C |  | Power Transformers | 1970's
ST1750.1D |  | Power Transformers | 1980's
ST1750.1E |  | Power Transformers | 1990's
ST1750.1F |  | Power Transformers | 2000-2009
ST1750.1G |  | Power Transformers | Since 2010
ST1750.1H |  | Power Transformers | Unknown
ST1750.1T |  | Power Transformers | Total
Raw Data | [16 empty] | Calculated Data
QPermID | ST1750_R_1A_25623DiPr2 | ST1750_R_1B_1289Powe | ST1750_R_1C_1290Powe | ST1750_R_1D_1291Powe | ST1750_R_1E_1292Powe | ST1750_R_1F_25626DiSi22 | ST1750_R_1G_25627DiUn22 | ST1750_R_1H_25627DiUn2
Quest # | ST1750.1A | ST1750.1B | ST1750.1C | ST1750.1D | ST1750.1E | ST1750.1F | ST1750.1G | ST1750.1H
Question Text | ST1750¦ How many of your current in-service distribution substation equipment components were manufactured in each time period? | ST1750¦ How many of your current in-service distribution substation equipment components were manufactured in each time period? | ST1750¦ How many of your current in-service distribution substation equipment components were manufactured in each time period? | ST1750¦ How many of your current in-service distribution substation equipment components were manufactured in each time period? | ST1750¦ How many of your current in-service distribution substation equipment components were manufactured in each time period? | ST1750¦ How many of your current in-service distribution substation equipment components were manufactured in each time period? | ST1750¦ How many of your current in-service distribution substation equipment components were manufactured in each time period? | ST1750¦ How many of your current in-service distribution substation equipment components were manufactured in each time period?
Subtext | Power Transformers | Power Transformers | Power Transformers | Power Transformers | Power Transformers | Power Transformers | Power Transformers | Power Transformers
Detail | Pre 1960 | 1960's | 1970's | 1980's | 1990's | 2000-2009 | Since 2010 | Unknown | Pre 1960 | 1960's | 1970's | 1980's | 1990's | 2000-2009 | Since 2010 | Unknown
Company ID
24 | 0 | 5 | 21 | 13 | 26 | 92 | 70 | 0 | 0 | 1.2115 | 4.163 | 2.0044 | 2.8634 | 6.0793 | 1.5419 | 0 | 17.8634
34 | 0 | 0 | 10 | 35 | 32 | 59 | 33 | 0 | 0 | 0 | 2.6627 | 7.2485 | 4.7337 | 5.2367 | 0.97633 | 0 | 20.858
39 | 4 | 31 | 97 | 101 | 82 | 104 | 156 | 0 | 0.45217 | 2.9652 | 7.5913 | 6.1478 | 3.5652 | 2.713 | 1.3565 | 0 | 24.7913
38 | 22 | 19 | 65 | 74 | 87 | 201 | 66 | 4 | 2.658 | 1.9424 | 5.4368 | 4.8141 | 4.0428 | 5.6041 | 0.61338 | 0.26022 | 25.3717
35 | 5 | 2 | 23 | 41 | 65 | 33 | 52 | 62 | 1.1484 | 0.38869 | 3.6572 | 5.0707 | 5.742 | 1.7491 | 0.91873 | 7.6678 | 26.3428
42 | 6 | 23 | 56 | 26 | 21 | 35 | 75 | 0 | 1.6116 | 5.2273 | 10.4132 | 3.7603 | 2.1694 | 2.1694 | 1.5496 | 0 | 26.9008
203 | 0 | 8 | 25 | 26 | 8 | 19 | 21 | 3 | 0 | 4 | 10.2273 | 8.2727 | 1.8182 | 2.5909 | 0.95455 | 0.95455 | 28.8182
30 | 31 | 32 | 33 | 13 | 43 | 47 | 26 | 4 | 8.7991 | 7.6856 | 6.4847 | 1.9869 | 4.6943 | 3.0786 | 0.56769 | 0.61135 | 33.9083
26 | 55 | 41 | 80 | 21 | 84 | 53 | 34 | 24 | 9.1199 | 5.7526 | 9.1837 | 1.875 | 5.3571 | 2.0281 | 0.43367 | 2.1429 | 35.8929
36 | 426 | 281 | 138 | 206 | 201 | 323 | 298 | 145 | 13.7215 | 7.6586 | 3.0773 | 3.5728 | 2.4901 | 2.4009 | 0.73835 | 2.5149 | 36.1744
45 | 16 | 76 | 88 | 44 | 50 | 17 | 54 | 0 | 3.0145 | 12.1159 | 11.4783 | 4.4638 | 3.6232 | 0.73913 | 0.78261 | 0 | 36.2174
32 | 282 | 216 | 263 | 212 | 121 | 178 | 249 | 6 | 12.0039 | 7.78 | 7.7505 | 4.8592 | 1.981 | 1.7485 | 0.81532 | 0.13752 | 37.076
48 | 35 | 69 | 111 | 44 | 28 | 49 | 44 | 0 | 5.9868 | 9.9868 | 13.1447 | 4.0526 | 1.8421 | 1.9342 | 0.57895 | 0 | 37.5263
10 | 107 | 195 | 352 | 159 | 174 | 62 | 144 | 0 | 5.8298 | 8.9899 | 13.2775 | 4.6647 | 3.6463 | 0.77955 | 0.60352 | 0 | 37.7913
41 | 33 | 21 | 50 | 20 | 15 | 24 | 24 | 2 | 11.3492 | 6.1111 | 11.9048 | 3.7037 | 1.9841 | 1.9048 | 0.63492 | 0.37037 | 37.963
46 | 378 | 454 | 142 | 50 | 32 | 0 | 0 | 0 | 23.267 | 23.6458 | 6.0511 | 1.6572 | 0.75758 | 0 | 0 | 0 | 55.3788

## Fig 22
Figure 22 -- Average Per-Unit Cost to Replace Power Transformers
and Associated Equipment
ID Num | Power Transformers
10 | 709520
47 | 780500
35 | 900000
26 | 1200000
24 | 1500000
200 | 2000000
34 | 2140924
48 | 5000000
Questions Asked to Gather Data |  | Raw Data Reported Above
SP1150.1Q | Keeping in mind your answer to the previous questions, what is your average per-unit cost to replace these key components, including the associated equipment?
SP1150.1 |  | Power Transformers
SP1150.2 |  | Circuit Breakers

## Fig 23
Figure 23 -- Refurbishment Project Cost per Substation Power Transformer
In Service at Refurbished Substation
ID Num | Equipment and Material | Engineering/Design | Construction Labor | Constructon Vehicles | Commissioning Labor | Other
6 | 159057.5 | 115288.9558 | 102358.2117 | 40114 | 19520.607 | 99888.1655 | 536227.44
38 | 159232 | 39808 | 66347 | 39808 | 331734 | 26539 | 663468
34 | 755448.4 | 148612.8 | 195938.9 | 0 | 0 | 10615.2 | 1110615.3
24 | 1404768.335 | 98391.345 | 881175.205 | 0 | 0 | 40090.915 | 2424425.8
8 | 805057 | 214089 | 596456 | 227086 | 115488 | 631029 | 2589205
10 | 1089137.02 | 300132 | 601153 | 197091 | 281325 | 330894 | 2799732.02
7 | 1207646 | 231121 | 694098 | 158103 | 163279 | 689931 | 3144178
200 | 1752000 | 494000 | 1465000 | 0 | 56000 | 617000 | 4384000
26 | 2011525.95 | 384026.245 | 1674014.685 | 33173.5 | 90654.305 | 1617072 | 5810466.685
31 | 4000000 | 391428 | 1317767 | 1160532 | 0 | 249160 | 7118887
Questions Asked to Gather Data
SP1000.1Q | For the station identified above, please provide the following cost information for ONE refurbishment project that was completed at the station since 1/1/2015
SP1000.1 |  | Equipment and Material Costs
SP1000.2 |  | Company Direct Labor | Engineering/Design Labor Costs
SP1000.3 |  | Company Direct Labor Overheads | Engineering/Design Labor Costs
SP1000.4 |  | Contract Labor or Services | Engineering/Design Labor Costs
SP1000.5 |  | Company Direct Labor | Construction Labor & Vehicle Costs
SP1000.6 |  | Company Direct Labor Overheads | Construction Labor & Vehicle Costs
SP1000.7 |  | Contract Labor or Services | Construction Labor & Vehicle Costs
SP1000.8 |  | Vehicle and Equipment Cost | Construction Labor & Vehicle Costs
SP1000.9 |  | Company Direct Labor | Commissioning Labor Costs
SP1000.10 |  | Company Direct Labor Overheads | Commissioning Labor Costs
SP1000.11 |  | Contract Labor or Services | Commissioning Labor Costs
SP1000.12 |  | Other Project Costs
SP1000.100 |  | Total Station Refurbishment Costs (since 1/1/2015)
Raw Data | [13 empty] | Calculated Data
Quest # | SP0950.2 | SP1000.1 | SP1000.2 | SP1000.3 | SP1000.4 | SP1000.5 | SP1000.6 | SP1000.7 | SP1000.8 | SP1000.9 | SP1000.10 | SP1000.11 | SP1000.12
Subtext | Number of Power Xfrmrs | Equipment and Material Costs | Company Direct Labor | Company Direct Labor Overheads | Contract Labor or Services | Company Direct Labor | Company Direct Labor Overheads | Contract Labor or Services | Vehicle and Equipment Cost | Company Direct Labor | Company Direct Labor Overheads | Contract Labor or Services | Other Project Costs
Detail | - | - | Engineering/Design Labor Costs | Engineering/Design Labor Costs | Engineering/Design Labor Costs | Construction Labor & Vehicle Costs | Construction Labor & Vehicle Costs | Construction Labor & Vehicle Costs | Construction Labor & Vehicle Costs | Commissioning Labor Costs | Commissioning Labor Costs | Commissioning Labor Costs | -
Company ID | [13 empty] | Equipment and Material | Engineering/Design | Construction Labor | Constructon Vehicles | Commissioning Labor | Other
6 | 2 | 318115 | 87117 | 9875.9117 | 133585 | 183872 | 20844.4234 | 0 | 80228 | 35066 | 3975.214 | 0 | 199776.3309 | 159057.5 | 115288.9558 | 102358.2117 | 40114 | 19520.607 | 99888.1655 | 536227.44
38 | 1 | 159232 | 39808 | - | - | - | - | 66347 | 39808 | 331734 | - | - | 26539 | 159232 | 39808 | 66347 | 39808 | 331734 | 26539 | 663468
34 | 3 | 2266345.2 | 445838.4 | - | 0 | 290591.1 | - | 297225.6 | 0 | - | - | - | 31845.6 | 755448.4 | 148612.8 | 195938.9 | 0 | 0 | 10615.2 | 1110615.3
24 | 2 | 2809536.67 | 131429.17 | 65353.52 | - | 973384.71 | 788965.7 | - | 0 | - | - | - | 80181.83 | 1404768.335 | 98391.345 | 881175.205 | 0 | 0 | 40090.915 | 2424425.8
8 | 1 | 805057 | 182640 | 20211 | 11238 | 521337 | 42527 | 32592 | 227086 | 111652 | 1848 | 1988 | 631029 | 805057 | 214089 | 596456 | 227086 | 115488 | 631029 | 2589205
10 | 1 | 1089137.02 | 0 | 0 | 300132 | 506134 | 52458 | 42561 | 197091 | 160389 | 47555 | 73381 | 330894 | 1089137.02 | 300132 | 601153 | 197091 | 281325 | 330894 | 2799732.02
7 | 1 | 1207646 | 51500 | 15358 | 164263 | 600109 | 64492 | 29497 | 158103 | 123867 | 36852 | 2560 | 689931 | 1207646 | 231121 | 694098 | 158103 | 163279 | 689931 | 3144178
200 | 1 | 1752000 | 177000 | 30000 | 287000 | 97000 | 16000 | 1352000 | 0 | 48000 | 8000 | - | 617000 | 1752000 | 494000 | 1465000 | 0 | 56000 | 617000 | 4384000
26 | 2 | 4023051.9 | 13438.85 | 2358.64 | 752255 | 227939.34 | 168716.44 | 2951373.59 | 66347 | 181308.61 | - | - | 3234144 | 2011525.95 | 384026.245 | 1674014.685 | 33173.5 | 90654.305 | 1617072 | 5810466.685
31 | 1 | 4000000 | 104577 | - | 286851 | 988928 | - | 328839 | 1160532 | - | - | - | 249160 | 4000000 | 391428 | 1317767 | 1160532 | 0 | 249160 | 7118887

## Fig 24
ID Num | Component | Station-Centric | Full Rebuild | Other
39 | 100% | - | - | -
24 | 100% | 0% | 0% | 0%
203 | 100% | 0% | 0% | 0%
35 | 100% | 0% | 0% | 0%
38 | 93.75% | 4.464% | 1.786% | -
34 | 89.05% | 10.95% | 0% | 0%
10 | 83.59% | 5.128% | 10.77% | 0.5128%
26 | - | 47.06% | 52.94% | -
Questions Asked to Gather Data
SP0700.1Q | How many distribution substation refurbishment projects have been completed and are planned for completion?
SP0700.1 |  | Individual Component-Focused | 2015 through 2019
SP0700.2 |  | Station-Centric | 2015 through 2019
SP0700.3 |  | Full Station Rebuild | 2015 through 2019
SP0700.4 |  | Other Refurbishment Approach | 2015 through 2019
SP0700.5 |  | Individual Component-Focused | 2020 through 2024
SP0700.6 |  | Station-Centric | 2020 through 2024
SP0700.7 |  | Full Station Rebuild | 2020 through 2024
SP0700.8 |  | Other Refurbishment Approach | 2020 through 2024
SP0700.100 |  | Please explain "other" above.
Raw Data |  |  |  |  | Calculated
Quest # | SP0700.1 | SP0700.2 | SP0700.3 | SP0700.4
Subtext | Individual Component-Focused | Station-Centric | Full Station Rebuild | Other Refurbishment Approach | Component | Station-Centric | Full Rebuild | Other
Detail | 2015 through 2019 | 2015 through 2019 | 2015 through 2019 | 2015 through 2019
Company ID
35 | 1 | 0 | 0 | 0 | 100% | 0% | 0% | 0%
203 | 12 | 0 | 0 | 0 | 100% | 0% | 0% | 0%
24 | 35 | 0 | 0 | 0 | 100% | 0% | 0% | 0%
39 | 153 | 0 | 0 | 0 | 100% | 0% | 0% | 0%
38 | 105 | 5 | 2 | 0 | 93.75% | 4.464% | 1.786% | 0%
34 | 122 | 15 | 0 | 0 | 89.05% | 10.95% | 0% | 0%
10 | 326 | 20 | 42 | 2 | 83.59% | 5.128% | 10.77% | 0.5128%
26 | 0 | 8 | 9 | 0 | 0% | 47.06% | 52.94% | 0%

## Fig 25
ID Num | Component | Station-Centric | Full Rebuild | Other
39 | 100% | - | - | -
203 | 96.97% | 0% | 3.03% | 0%
24 | 91.67% | 0% | 8.333% | 0%
10 | 86.25% | 4.465% | 2.468% | 6.816%
34 | 83.33% | 14.58% | 2.083% | 0%
26 | - | 63.64% | 36.36% | -
Questions Asked to Gather Data
SP0700.1Q | How many distribution substation refurbishment projects have been completed and are planned for completion?
SP0700.1 |  | Individual Component-Focused | 2015 through 2019
SP0700.2 |  | Station-Centric | 2015 through 2019
SP0700.3 |  | Full Station Rebuild | 2015 through 2019
SP0700.4 |  | Other Refurbishment Approach | 2015 through 2019
SP0700.5 |  | Individual Component-Focused | 2020 through 2024
SP0700.6 |  | Station-Centric | 2020 through 2024
SP0700.7 |  | Full Station Rebuild | 2020 through 2024
SP0700.8 |  | Other Refurbishment Approach | 2020 through 2024
SP0700.100 |  | Please explain "other" above.
Raw Data |  |  |  |  | Calculated
Quest # | SP0700.5 | SP0700.6 | SP0700.7 | SP0700.8
Subtext | Individual Component-Focused | Station-Centric | Full Station Rebuild | Other Refurbishment Approach | Component | Station-Centric | Full Rebuild | Other
Detail | 2020 through 2024 | 2020 through 2024 | 2020 through 2024 | 2020 through 2024
Company ID
39 | 260 | 0 | 0 | 0 | 100% | 0% | 0% | 0%
203 | 32 | 0 | 1 | 0 | 96.97% | 0% | 3.03% | 0%
24 | 33 | 0 | 3 | 0 | 91.67% | 0% | 8.333% | 0%
10 | 734 | 38 | 21 | 58 | 86.25% | 4.465% | 2.468% | 6.816%
34 | 40 | 7 | 1 | 0 | 83.33% | 14.58% | 2.083% | 0%
26 | 0 | 14 | 8 | 0 | 0% | 63.64% | 36.36% | 0%