## Sheet1
B2-AMPCO-18-Attachment #1
Major Asset Condition Summary
Ref: EB-2019-0082 I-12-AMPCO-20-01
Major Asset Condition Summary (EB-2016-0160)
2016
Asset Type | Very Low Risk1 | Low Risk | Fair Risk1 | High Risk | Very High Risk1 | To be Assessed | Total Population | % High Risk & Very High Risk
Transformers2 | 324 | 224 | 65 | 94 | 14 | - | 721 | 14.98%
Circuit Breakers | 2272 | 1090 | 681 | 454 | 45 | - | 4543 | 10.98%
Protection Systems | 4357 | 3994 | 484 | 1936 | 1331 | - | 12103 | 26.99%
Conductors (km) | - | 11748 | 5874 | 2643 | - | 9104 | 29369 | 8.999%
Wood Poles3 | - | 24218 | - | 4832 | - | 12950 | 42000 | 11.5%
Underground Cables (km) | - | 195 | 59 | 11 | - | 3 | 267 | 4.12%
Insulators
1 These categories are not used for all assets.
2 In prior transmission applications (EB-2016-0160 and EB-2019-0082) transformer condition (i.e. five risk categories) was presented based on Asset Analytics that only took into account the main tank oil test results. The more detailed condition assessment methodology and results are described in EB-2021-0110, TSP Section 2.2.2.1 and Interrogatory Staff-040. Based on Hydro One’s detailed transformer condition assessments, the number of high and very high risk (i.e. poor condition) transformers would have been 116 in 2016.
3 As per EB-2019-0082 Undertaking JT 1.22.
Major Asset Condition Summary (EB-2019-0082)
2018
Asset Type | Very Low Risk1 | Low Risk | Fair Risk1 | High Risk | Very High Risk1 | To be Assessed | Total Population | % High Risk & Very High Risk
Transformers2 | 336 | 163 | 95 | 99 | 23 | - | 716 | 17.04%
Circuit Breakers | 2035 | 1475 | 804 | 293 | 167 | - | 4774 | 9.636%
Protection Systems | 4800 | 3846 | 497 | 2387 | 976 | - | 12506 | 26.89%
Conductors (km) | - | 16050 | 3316 | 3680 | - | 6061 | 29107 | 12.64%
Wood Poles | - | 17640 | - | 5460 | - | 18900 | 42000 | 13%
Underground Cables (km) | - | 179 | 77 | 8 | - | - | 264 | 3.03%
Insulators
1 These categories are not used for all assets.
2 In prior transmission applications (EB-2016-0160 and EB-2019-0082) transformer condition (i.e. five risk categories) was presented based on Asset Analytics that only took into account the main tank oil test results. The more detailed condition assessment methodology and results are described in EB-2021-0110, TSP Section 2.2.2.1 and Interrogatory Staff-040. Based on Hydro One’s detailed transformer condition assessments, the number of high and very high risk (i.e. poor condition) transformers would have been 181 in 2018.
Major Asset Condition Summary (EB-2021-0110)
2020
Asset Type | Very Low Risk1 | Low Risk | Fair Risk1 | High Risk | Very High Risk1 | To be Assessed | Total Population | % High Risk & Very High Risk
| Good Condition2 |  | Fair Condition2 | Poor Condition2
Transformers3 | - | 449 | 74 | 198 | - | - | 721 | 27.46%
Circuit Breakers | 1723 | 982 | 1510 | 382 | 159 | - | 4756 | 11.38%
Protection Systems4 | 5267 | 3539 | 291 | 2542 | 855 | - | 12494 | 27.19%
Conductors (km) | - | 13685 | 3329 | 3874 | - | 7663 | 28552 | 13.57%
Wood Poles | - | 23866 | - | 4693 | - | 11482 | 40041 | 11.72%
Underground Cables (km) | - | 173 | 92 | 8 | - | - | 273 | 2.93%
Insulators
1 These categories are not used for all assets.
2 As part of Hydro One’s ongoing efforts to improve the accuracy and robustness of asset condition ratings, Hydro One has corrected and transitioned away from the use of the word “risk” in describing asset condition, as “risk” is used heavily in the Asset Risk Assessment (ARA). Further details can be found in Interrogatory Staff-040 part f.
3 In prior transmission applications (EB-2016-0160 and EB-2019-0082) transformer condition (i.e. five risk categories) was presented based on Asset Analytics that only took into account the main tank oil test results. The more detailed condition assessment methodology and results are described in EB-2021-0110, TSP Section 2.2.2.1 and Interrogatory Staff-040. Since transformer condition is presented based on the detailed assessment which only uses three condition categories in this application, the transformer condition cannot be divided into the five risk categories. However, the alignment between previous and current condition categories is shown in Interrogatory Staff-040 part g; and based on Hydro One’s current detailed transformer condition assessments, the number of high and very high risk transformers would have been 181 in 2018 and 116 in 2016. Please see JM1.1 for the transformer condition sub-index data which is aligned with the previous transformer condition breakdown that was presented (main tank oil only) however as explained in TSP 2.2 and JM1.1 this data is supplemented by additional asset data to complete the asset-specific needs assessments.
4 Please see Interrogatory B2-Staff-039 for further information regarding protection equipment replacements. For protections, high and very high risk (poor condition) represents protections beyond ESL.