## Sheet1
B2-AMPCO-24-Attachment #1 | This interrogatory has been updated to include the requested information for 2021.
Replacement History by ESL & Condition
TRANSMISSION ASSETS | Population | Expected Service Life (ESL) (Years) | total # replaced 2018 to 2020 (actual) | total # repaired 2018 to 2020 (actual)1 | # replaced 2021 to 2022 (forecast) | 2018 # replaced beyond ESL | 2019 # replaced beyond ESL | 2020 # replaced beyond ESL | 2021 # replaced beyond ESL | 2018 # replaced in poor condition | 2019 # replaced in poor condition | 2020 # replaced in poor condition | 2021 # replaced in poor condition | 2018 # replaced beyond ESL & in poor condition | 2019 # replaced beyond ESL & in poor condition | 2020 # replaced beyond ESL & in poor condition | 2021 # replaced beyond ESL & in poor condition
Transformer | 721 | 50 | 62 | -2 | 40 | 28 | 16 | 14 | 10 | 28 | 24 | 14 | 10 | 28 | 16 | 14 | 10
Circuit Breakers | 4756 | OCB - 55 Others - 40 | 358 | -2 | 298 | 54 | 67 | 66 | 87 | 63 | 63 | 60 | 95 | 54 | 58 | 59 | 87
Protection Systems3
Electromechanical | 1784 | 45 | 347 | -2 | 228 | 55 | 103 | 56 | 37 |  |  |  | - |  |  |  | -
Solid State | 3077 | 25 | 294 | -2 | 124 | 103 | 93 | 89 | 59 |  |  |  | - |  |  |  | -
Microprocessor | 7633 | 20 | 248 | -2 | 169 | 5 | 41 | 18 | 38 |  |  |  | - |  |  |  | -
Conductors (circuit km) | 28552 | ACSR - 90 Copper - 70 Aluminum - 100 | 214 | -2 | 533 | 51 | 7 | 22 | 2 | 51 | 82 | 81 | 31 | 51 | 7 | 22 | 2
Poles - Wood | 40041 | 50 | 2358 | -2 | 2046 | 735 | 827 | 796 | 1003 | 735 | 827 | 796 | 1003 | 735 | 827 | 796 | 1003
Insulators | 119459 | 90 | 10984 | -2 | 7311 | - | - | - | - | 3900 | 4290 | 2794 | 3690 | - | - | - | -
Underground Cable (circuit km) | 273 | LPLF/HPLF - 70 XLPE - 50 | 4.7 | -2 | - | - | - | - | - | - | - | 4.7 | - | - | - | - | -
Notes
1 Major repairs
2 Not applicable as these assets are not repaired (i.e. they are replaced) or any repair work is relatively minor
3 Please see Interrogatory B2-Staff-039 for further information regarding protection equipment replacements.

## Sheet2
2.0-AMPCO-
Hydro One Networks Inc. Transmission Rate Application
EB-2019-0082
Ex B TSP Section 2
Failure Rates
TRANSMISSION ASSETS
Transformer
115kV
230 kV
500 kV
Circuit Breakers
Oil
SF 6
Air Blast
GIS
Metaclad
Vacuum
Protection Systems
Electromechanical
Solid State
Microprocessor
Conductors
Poles
Wood
Steel Structures
Insulators
Glass
Poreclain
Polymer
circuit structures
Underground Cable