## 2023-FULL
Dry Core Transformer Losses Proposed for 2023
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates | [8 empty] | 6.682 | 0.1104 |  | 5.6302
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.0738 | 10.0334 | 11.1071 | 0.90474 | 12.0119
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.4317 | 13.3778 | 14.8095 | 1.2063 | 16.0158
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.8254 | 16.8297 | 18.6551 | 1.5381 | 20.1931
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.4339 | 23.1963 | 25.6302 | 2.0508 | 27.681
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.9349 | 26.9705 | 29.9054 | 2.473 | 32.3783
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.2907 | 30.1723 | 33.4629 | 2.7727 | 36.2357 |  | 2023 Proposed Rates
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.8834 | 35.4927 | 39.3761 | 3.2721 | 42.6482 |  | LV | Network | Line & Transmission | Variable
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 4.8319 | 44.015 | 48.8468 | 4.0713 | 52.9182 | GS 50 to 1,499 kW | 0.02011 | 3.9813 | 2.2255 | 5.9724
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.9414 | 45.0248 | 49.9662 | 4.1636 | 54.1297 | GS 1,500 to 4,999 kW | 0.02149 | 4.1337 | 2.3786 | 5.4993
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.1697 | 47.1177 | 52.2874 | 4.356 | 56.6434 | Large Use | 0.0242 | 4.5825 | 2.6785 | 5.4189
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 5.5556 | 50.6367 | 56.1923 | 4.6811 | 60.8734
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 5.9414 | 54.1558 | 60.0972 | 5.0062 | 65.1034
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 7.3731 | 67.5336 | 74.9067 | 6.2125 | 81.1192 | Tier 1 | 0.098 | May 1, 2022 Rate
500 KVA 1PH 1.2KV BIL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 KVA 1PH 1.2KV BIL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[14 empty] | Tier 2 | 0.115 | May 1, 2022 Rate
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.55908 | 5.4465 | 6.0056 | 0.47108 | 6.4767
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.85902 | 8.2537 | 9.1127 | 0.7238 | 9.8365 | WMSR | 0.003
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.718 | 16.5074 | 18.2255 | 1.4476 | 19.6731 | CBR | 0.0004
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.1475 | 20.0667 | 22.2142 | 1.8095 | 24.0237 | RRRP | 0.0005
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.8634 | 26.7556 | 29.619 | 2.4127 | 32.0316
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.2235 | 39.9186 | 44.1421 | 3.5587 | 47.7008
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.1182 | 47.1446 | 52.2628 | 4.3126 | 56.5754
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 5.5445 | 51.4207 | 56.9652 | 4.6718 | 61.637
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 5.9755 | 55.7562 | 61.7317 | 5.0349 | 66.7666
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 6.4068 | 60.0927 | 66.4995 | 5.3983 | 71.8978
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 7.7669 | 73.2557 | 81.0226 | 6.5443 | 87.567
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 13.0019 | 133.2359 | 146.2379 | 10.9554 | 157.1933
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 14.747 | 153.2294 | 167.9763 | 12.4257 | 180.4021
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 19.3283 | 194.2221 | 213.5504 | 16.2859 | 229.8363
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 21.6907 | 219.4739 | 241.1646 | 18.2765 | 259.4411
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 28.9924 | 291.3332 | 320.3256 | 24.4289 | 344.7545
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 34.5762 | 348.9553 | 383.5315 | 29.1338 | 412.6653
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 41.5201 | 419.7405 | 461.2605 | 34.9847 | 496.2452
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 48.9651 | 496.57 | 545.5351 | 41.2578 | 586.7929
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 60.1327 | 611.8142 | 671.9469 | 50.6676 | 722.6145
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 69.0812 | 706.7769 | 775.8581 | 58.2075 | 834.0657
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains May 1, 2022 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2022
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2023 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2023
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2022-0042
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 6.682 | 0.1104 |  | 5.6302
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.0738 | 10.0334 | 11.1071 | 0.90474 | 12.0119
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.4317 | 13.3778 | 14.8095 | 1.2063 | 16.0158
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.8254 | 16.8297 | 18.6551 | 1.5381 | 20.1931
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.4339 | 23.1963 | 25.6302 | 2.0508 | 27.681
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.9349 | 26.9705 | 29.9054 | 2.473 | 32.3783
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.2907 | 30.1723 | 33.4629 | 2.7727 | 36.2357
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.8834 | 35.4927 | 39.3761 | 3.2721 | 42.6482
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 4.8319 | 44.015 | 48.8468 | 4.0713 | 52.9182
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.9414 | 45.0248 | 49.9662 | 4.1636 | 54.1297
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.1697 | 47.1177 | 52.2874 | 4.356 | 56.6434
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 5.5556 | 50.6367 | 56.1923 | 4.6811 | 60.8734
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 5.9414 | 54.1558 | 60.0972 | 5.0062 | 65.1034
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 7.3731 | 67.5336 | 74.9067 | 6.2125 | 81.1192
500 KVA 1PH 1.2KV BIL | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 KVA 1PH 1.2KV BIL | 0 | 0 | 0 | 0 | 0 | 0 | 0
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.55908 | 5.4465 | 6.0056 | 0.47108 | 6.4767
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.85902 | 8.2537 | 9.1127 | 0.7238 | 9.8365
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.718 | 16.5074 | 18.2255 | 1.4476 | 19.6731
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.1475 | 20.0667 | 22.2142 | 1.8095 | 24.0237
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.8634 | 26.7556 | 29.619 | 2.4127 | 32.0316
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.2235 | 39.9186 | 44.1421 | 3.5587 | 47.7008
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.1182 | 47.1446 | 52.2628 | 4.3126 | 56.5754
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 5.5445 | 51.4207 | 56.9652 | 4.6718 | 61.637
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 5.9755 | 55.7562 | 61.7317 | 5.0349 | 66.7666
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 6.4068 | 60.0927 | 66.4995 | 5.3983 | 71.8978
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 7.7669 | 73.2557 | 81.0226 | 6.5443 | 87.567
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 13.0019 | 133.2359 | 146.2379 | 10.9554 | 157.1933
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 14.747 | 153.2294 | 167.9763 | 12.4257 | 180.4021
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 19.3283 | 194.2221 | 213.5504 | 16.2859 | 229.8363
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 21.6907 | 219.4739 | 241.1646 | 18.2765 | 259.4411
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 28.9924 | 291.3332 | 320.3256 | 24.4289 | 344.7545
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 34.5762 | 348.9553 | 383.5315 | 29.1338 | 412.6653
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 41.5201 | 419.7405 | 461.2605 | 34.9847 | 496.2452
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 48.9651 | 496.57 | 545.5351 | 41.2578 | 586.7929
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 60.1327 | 611.8142 | 671.9469 | 50.6676 | 722.6145
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 69.0812 | 706.7769 | 775.8581 | 58.2075 | 834.0657
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard