## 2023-FULL
Dry Core Transformer Losses Proposed for 2023
Transformers | No Load Loss (W) | Load Loss (W) | Monthly No Load Loss (kW) | Monthly No Load Loss (kWH) | Monthly Load Loss (kW) | Monthly Load Loss (kWH) | Monthly Total Loss (kW) | Monthly Total Loss (kWH) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh** | Total Monthly cost of power | Cost of Distribution per kW | Total |  | LV | Network | Line & Transmission | Variable
Rates | [8 empty] | 6.682 | 0.0989 |  | 5.6425 |  | General Service > 50 kW < 1500 kW | 0.02011 | 3.9813 | 2.2255 | 5.9845
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 0.1125 | 82.125 | 0.048195 | 8.7569 | 0.1607 | 90.8819 | 1.0738 | 8.9882 | 10.062 | 0.90673 | 10.9687 | General Service > 1500 kW | 0.02149 | 4.1337 | 2.3786 | 5.5121
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 0.15 | 109.5 | 0.06426 | 11.6758 | 0.21426 | 121.1758 | 1.4317 | 11.9843 | 13.416 | 1.209 | 14.6249 | Large Use (> 5000 kW) | 0.0242 | 4.5825 | 2.6785 | 5.431
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 0.1875 | 136.875 | 0.08568 | 15.5678 | 0.27318 | 152.4428 | 1.8254 | 15.0766 | 16.902 | 1.5414 | 18.4434
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 0.2625 | 191.625 | 0.10175 | 18.4868 | 0.36424 | 210.1118 | 2.4339 | 20.7801 | 23.2139 | 2.0553 | 25.2692
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 0.3 | 219 | 0.13923 | 25.2977 | 0.43923 | 244.2977 | 2.9349 | 24.161 | 27.096 | 2.4784 | 29.5743 | Tier 1 | 0.087 | Nov 1, 2022 Rate
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 0.33525 | 244.7325 | 0.15722 | 28.5669 | 0.49247 | 273.2994 | 3.2907 | 27.0293 | 30.32 | 2.7788 | 33.0988
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 0.39375 | 287.4375 | 0.18743 | 34.0546 | 0.58117 | 321.4921 | 3.8834 | 31.7956 | 35.679 | 3.2793 | 38.9583 | Tier 2 | 0.103 | Nov 1, 2022 Rate
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 0.4875 | 355.875 | 0.23562 | 42.8114 | 0.72312 | 398.6864 | 4.8319 | 39.4301 | 44.262 | 4.0802 | 48.3422
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 0.49875 | 364.0875 | 0.24076 | 43.7455 | 0.73951 | 407.833 | 4.9414 | 40.3347 | 45.2761 | 4.1727 | 49.4488 | WMSR | 0.003
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 0.522 | 381.06 | 0.25169 | 45.7304 | 0.77369 | 426.7904 | 5.1697 | 42.2096 | 47.3793 | 4.3655 | 51.7449 | CBR | 0.0004
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 0.561 | 409.53 | 0.27043 | 49.1359 | 0.83143 | 458.6659 | 5.5556 | 45.3621 | 50.9176 | 4.6914 | 55.609 | RRRP | 0.0005
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 0.6 | 438 | 0.28917 | 52.5413 | 0.88917 | 490.5413 | 5.9414 | 48.5145 | 54.4559 | 5.0172 | 59.4731
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 0.75 | 547.5 | 0.35343 | 64.2172 | 1.1034 | 611.7172 | 7.3731 | 60.4988 | 67.8719 | 6.2261 | 74.0981
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.06225 | 45.4425 | 0.02142 | 3.8919 | 0.08367 | 49.3344 | 0.55908 | 4.8792 | 5.4383 | 0.47211 | 5.9104
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.09375 | 68.4375 | 0.034808 | 6.3244 | 0.12856 | 74.7619 | 0.85902 | 7.394 | 8.253 | 0.72539 | 8.9784
30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 0.1875 | 136.875 | 0.069615 | 12.6488 | 0.25711 | 149.5238 | 1.718 | 14.7879 | 16.5059 | 1.4508 | 17.9567
45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 0.225 | 164.25 | 0.09639 | 17.5138 | 0.32139 | 181.7638 | 2.1475 | 17.9764 | 20.124 | 1.8135 | 21.9374
75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 0.3 | 219 | 0.12852 | 23.3517 | 0.42852 | 242.3517 | 2.8634 | 23.9686 | 26.8319 | 2.4179 | 29.2499
112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 0.45 | 328.5 | 0.18207 | 33.0816 | 0.63207 | 361.5816 | 4.2235 | 35.7604 | 39.9839 | 3.5665 | 43.5504
*125 KVA 3PH, 1.2kV BIL | 633 | 3767 | 0.47475 | 346.5675 | 0.20172 | 36.6524 | 0.67647 | 383.2199 | 4.5202 | 37.9005 | 42.4206 | 3.817 | 46.2376
150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 0.525 | 383.25 | 0.24098 | 43.7844 | 0.76597 | 427.0344 | 5.1182 | 42.2337 | 47.3519 | 4.322 | 51.674
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 0.5745 | 419.385 | 0.25527 | 46.3823 | 0.82977 | 465.7673 | 5.5445 | 46.0644 | 51.6089 | 4.682 | 56.2909
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 0.62475 | 456.0675 | 0.26952 | 48.9705 | 0.89427 | 505.038 | 5.9755 | 49.9483 | 55.9237 | 5.0459 | 60.9696
225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 0.675 | 492.75 | 0.28382 | 51.5683 | 0.95882 | 544.3183 | 6.4068 | 53.8331 | 60.2399 | 5.4101 | 65.65
300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 0.825 | 602.25 | 0.33737 | 61.2982 | 1.1624 | 663.5482 | 7.7669 | 65.6249 | 73.3918 | 6.5587 | 79.9505
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 1.5563 | 1136.0625 | 0.38958 | 70.7848 | 1.9458 | 1206.8473 | 13.0019 | 119.3572 | 132.3591 | 10.9794 | 143.3385
500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 1.8 | 1314 | 0.40698 | 73.947 | 2.207 | 1387.947 | 14.747 | 137.268 | 152.0149 | 12.453 | 164.4679
750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 2.25 | 1642.5 | 0.6426 | 116.7585 | 2.8926 | 1759.2585 | 19.3283 | 173.9907 | 193.3189 | 16.3216 | 209.6405
1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 2.55 | 1861.5 | 0.69615 | 126.4884 | 3.2462 | 1987.9884 | 21.6907 | 196.612 | 218.3027 | 18.3165 | 236.6192
1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 3.375 | 2463.75 | 0.9639 | 175.1377 | 4.3389 | 2638.8877 | 28.9924 | 260.986 | 289.9784 | 24.4824 | 314.4608
2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 4.05 | 2956.5 | 1.1246 | 204.3274 | 5.1746 | 3160.8274 | 34.5762 | 312.6058 | 347.182 | 29.1976 | 376.3796
2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 4.875 | 3558.75 | 1.3388 | 243.2469 | 6.2138 | 3801.9969 | 41.5201 | 376.0175 | 417.5376 | 35.0613 | 452.5989
3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 5.775 | 4215.75 | 1.553 | 282.1664 | 7.328 | 4497.9164 | 48.9651 | 444.8439 | 493.809 | 41.3482 | 535.1572
3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 7.125 | 5201.25 | 1.8742 | 340.5456 | 8.9992 | 5541.7956 | 60.1327 | 548.0836 | 608.2163 | 50.7786 | 658.9948
5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 8.25 | 6022.5 | 2.0884 | 379.4651 | 10.3384 | 6401.9651 | 69.0812 | 633.1543 | 702.2355 | 58.335 | 760.5706
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type transformers commercial use
Average load factor = 0.46 average loss factor = 0.2489
Loss factor = 0.15*load factor + 0.85(load factor)2
Average perunit loading squared=0.0714; per unit loading=0.2672
*For transformer sizes not included in the CSA standard, no load losses, load losses and associated costs are interpolated based on transformer size
** Cost of Energy and Wholesale Market per kWh contains Nov 1, 2019 RPP Tiered Pricing, WMRS Pricing to be effective January 1, 2019
Monthly No Load Loss (kW) = no load loss (kW) * .75 (responsibility factor)
Monthly No Load Loss (kWh) = monthly no load loss (kW) * 8760/12
Monthly Load loss (kW) = load loss (kW)*average perunit loading squared (.0714)*.75 (responsibility factor?)
Monthly Load loss (kWh) = monthly load loss (kW) *8760/12*average loss factor (.2489)
Responsibility Factor= (load at system peak/peak load)2= the ratio of the transformer load at system peak to the peak load, all squared=.75
Utilization Factor = peak load/rated load = 1

## 2023 PDF
DRAFT - TARIFF OF RATES AND CHARGES
Effective and Implementation Date January 1, 2023
This schedule supersedes and replaces all previously
approved schedules of Rates, Charges and Loss Factors
EB-2022-0042
Dry Core Transformer Charges
Transformers | No Load Loss (W) | Load Loss (W) | Cost of Transmission and LV per kW | Cost of Energy and Wholesale Market per kWh | Total Monthly cost of power | Cost of Distribution per kW | Total
Rates |  |  | 6.682 | 0.0989 |  | 5.6425
25 KVA 1 PH, 1.2kV BIL | 150 | 900 | 1.0738 | 8.9882 | 10.062 | 0.90673 | 10.9687
37.5 KVA 1 PH, 1.2kV BIL | 200 | 1200 | 1.4317 | 11.9843 | 13.416 | 1.209 | 14.6249
50 KVA 1 PH, 1.2kV BIL | 250 | 1600 | 1.8254 | 15.0766 | 16.902 | 1.5414 | 18.4434
75 KVA 1 PH, 1.2kV BIL | 350 | 1900 | 2.4339 | 20.7801 | 23.2139 | 2.0553 | 25.2692
100 KVA 1 PH, 1.2kV BIL | 400 | 2600 | 2.9349 | 24.161 | 27.096 | 2.4784 | 29.5743
112.5 kVA 1 PH, 1.2kV BIL | 447 | 2936 | 3.2907 | 27.0293 | 30.32 | 2.7788 | 33.0988
*150 KVA 1 PH, 1.2kV BIL | 525 | 3500 | 3.8834 | 31.7956 | 35.679 | 3.2793 | 38.9583
167 KVA 1 PH, 1.2kV BIL | 650 | 4400 | 4.8319 | 39.4301 | 44.262 | 4.0802 | 48.3422
175 KVA 1PH, 1.2kV BIL | 665 | 4496 | 4.9414 | 40.3347 | 45.2761 | 4.1727 | 49.4488
*200 KVA 1 PH, 1.2kV BIL | 696 | 4700 | 5.1697 | 42.2096 | 47.3793 | 4.3655 | 51.7449
*225 KVA 1 PH, 1.2kV BIL | 748 | 5050 | 5.5556 | 45.3621 | 50.9176 | 4.6914 | 55.609
250 KVA 1 PH, 1.2kV BIL | 800 | 5400 | 5.9414 | 48.5145 | 54.4559 | 5.0172 | 59.4731
333 KVA 1PH 1.2kV BIL | 1000 | 6600 | 7.3731 | 60.4988 | 67.8719 | 6.2261 | 74.0981
*10 kVA 3 PH, 1.2kV BIL | 83 | 400 | 0.55908 | 4.8792 | 5.4383 | 0.47211 | 5.9104
*15 KVA 3 PH, 1.2kV BIL | 125 | 650 | 0.85902 | 7.394 | 8.253 | 0.72539 | 8.9784
*30 kVA 3PH, 1.2kV BIL | 250 | 1300 | 1.718 | 14.7879 | 16.5059 | 1.4508 | 17.9567
*45 KVA 3 PH, 1.2kV BIL | 300 | 1800 | 2.1475 | 17.9764 | 20.124 | 1.8135 | 21.9374
*75 KVA 3 PH, 1.2kV BIL | 400 | 2400 | 2.8634 | 23.9686 | 26.8319 | 2.4179 | 29.2499
*112.5 KVA 3 PH, 1.2kV BIL | 600 | 3400 | 4.2235 | 35.7604 | 39.9839 | 3.5665 | 43.5504
125 KVA 3PH, 1.2kV BIL | 633 | 3767 | 4.5202 | 37.9005 | 42.4206 | 3.817 | 46.2376
*150 KVA 3 PH, 1.2kV BIL | 700 | 4500 | 5.1182 | 42.2337 | 47.3519 | 4.322 | 51.674
*175 KVA 3PH, 1.2kV BIL | 766 | 4767 | 5.5445 | 46.0644 | 51.6089 | 4.682 | 56.2909
*200 KVA 3PH, 1.2kV BIL | 833 | 5033 | 5.9755 | 49.9483 | 55.9237 | 5.0459 | 60.9696
*225 KVA 3 PH, 1.2kV BIL | 900 | 5300 | 6.4068 | 53.8331 | 60.2399 | 5.4101 | 65.65
*300 KVA 3 PH, 1.2kV BIL | 1100 | 6300 | 7.7669 | 65.6249 | 73.3918 | 6.5587 | 79.9505
*450 KVA 3PH, 1.2kV BIL | 2075 | 7275 | 13.0019 | 119.3572 | 132.3591 | 10.9794 | 143.3385
*500 KVA 3 PH, 95kV BIL | 2400 | 7600 | 14.747 | 137.268 | 152.0149 | 12.453 | 164.4679
*750 KVA 3 PH, 95kV BIL | 3000 | 12000 | 19.3283 | 173.9907 | 193.3189 | 16.3216 | 209.6405
*1000 KVA 3 PH, 95kV BIL | 3400 | 13000 | 21.6907 | 196.612 | 218.3027 | 18.3165 | 236.6192
*1500 KVA 3 PH, 95kV BIL | 4500 | 18000 | 28.9924 | 260.986 | 289.9784 | 24.4824 | 314.4608
*2000 KVA 3 PH, 95kV BIL | 5400 | 21000 | 34.5762 | 312.6058 | 347.182 | 29.1976 | 376.3796
*2500 KVA 3 PH, 95kV BIL | 6500 | 25000 | 41.5201 | 376.0175 | 417.5376 | 35.0613 | 452.5989
*3000 KVA 3PH, 95kV BIL | 7700 | 29000 | 48.9651 | 444.8439 | 493.809 | 41.3482 | 535.1572
*3750 KVA 3PH, 95kV BIL | 9500 | 35000 | 60.1327 | 548.0836 | 608.2163 | 50.7786 | 658.9948
*5000 KVA 3PH, 95kV BIL | 11000 | 39000 | 69.0812 | 633.1543 | 702.2355 | 58.335 | 760.5706
No Load and load losses from CSA standard C802-94: Maximum losses for distribution, power and dry-type
transformers commercial use.
Average load factor = 0.46 average loss factor = 0.2489
*For non-preferred KVA ratings no load and load losses are interpolated as per CSA standard