## Appendix B
Region | Operating Area (EGI) | Asset Class | Binary Screening (Pass/ Fail) | Cause of Binary Fail | Investment Code | Investment Name | In Service Date | 223-232 Forecast (Includes overhead allocation) | Investment Description - Binary Screening - Pass | Technical Evaluation Completion Status | Technical Evaluation Results | Technical Evaluation Comments | Economic Evaluation Completion Status | Economic Evaluation Results | Economic Evaluation - IRPAs Considered | IRP Plan Completion Status | IRP Plan - IRPAs Considered
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 11794 | A60: City Centre Complex - Ottawa | 2023 | 578721.0754
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 23126 | Concord St Isolated Steel Replace with Main St PE, Ottawa | 2023 | 599421.5011
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 23190 | VPM - 310 Cathcart St Header - Aldyl A | 2031 | 348701.8634
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 30334 | Ann St - Eastern - Area 60 - 1100 | 2032 | 1452020.9311
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 30342 | Carling Ave - Eastern - Area 60 - 1104 | 2031 | 1734079.3584
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 30343 | Centre St - Eastern - Area 60 - 1085 | 2027 | 1108905.5666
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 30347 | Elm St W - Eastern - Area 60 - 1726 | 2028 | 978032.9846
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 30352 | George St - Eastern - Area 60 - 1088 | 2027 | 1462055.7979
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 30358 | Highgate Rd - Eastern - Area 60 - 1166 | 2030 | 1212188.5916
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 30376 | Othello Ave - Eastern - Area 60 - 1096 | 2028 | 1212877.7247
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 30388 | Stanley Ave - Eastern - Area 60 - 1069 | 2030 | 1515707.5201
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 102424 | Relocation Program - Area 60* | 2020 | 13287715.1803
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 501823 | A60 1149 Shillington HDR Replacement | 2023 | 158255.5059
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | re | Morrison THP Replacement | 2023 | 305493.3023
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 502862 | Young St LP Replacement | 2023 | 1240656.9304
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 734548 | VSM-HWY 7 Dufferin St Perth | 2024 | 1301689.9003
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Dollar threshold | 734590 | Viewmount Dr Main Lowering | 2031 | 570661.7579
Eastern | 60 - Ottawa | Distribution Pipe | Fail | Emergent Safety | 4665 | Replacement Blanket - Area 60* |  | 12572770.2645
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 4671 | Anode Blanket - Area 60* | 2020 | 3382114.4848 | Justification: The Corrosion Department conducts pipe-to-soil readings each year on EGI’s steel pipelines. When a corrosion area is identified as having fallen below EGI’s minimum specifications, an order for a anode installation is processed. The capital request is for 12 months. | Completed | Fail | See investment description, IRPAs not applicable
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 4767 | AMP Fitting Replacement - Area 60* |  | 68867529.2639 | AMP Fittings are a below grade transition fittings. The inserted portion of copper tubing can fail due to internal corrosion. In these cases leaks develop immediately downstream of the AMP Fitting. | Completed | Fail | See investment description, IRPAs not applicable
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 8198 | LANCASTER GATE Station - Integrity Retrofit > 30% SMYS | 2026 | 1856496.6524 | Funds to install launcher (station rebuild occurred in 2016; no provisions for launcher were included) on pipeline to allow for inline inspection are required. This will allow in-line inspection of the pipeline which is required as per the Pipeline Integrity Management Program. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 8262 | VSM - Preston St - LP | 2026 | 3224565.3616 | Vintage Steel Mains, Isolated Steel Mains General: Vintage Steel Replacement Program is a proactive replacement program to renew aging vintage steel pipe assets before reaching their end of life. Vintage steel mains have shown signs of declining health due to the cumulative effect of poor, manufactured coating performance; construction practices; latent third-party damages to pipe coating; and the effect of stray currents from transit infrastructure such as subway and streetcars. The current failure projection model is forecasting an exponential increase in the number of corrosion-related failures, while the C55 value framework and the 40-year risk projection are showing an increase in the safety risk associated with steel main failures. Vintage steel systems also have potential to include compression couplings, shallow installation depth and shallow assemblies making pipe susceptible to third-party damage, and manufactured defects associated with seam welds and fittings. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 10288 | St. Laurent Phase 4 - Lower Section (Plastic) | 2025 | 11339012.0169 | Issue/Concern: General Concerns: Vintage steel mains have shown signs of declining health due to the cumulative effective of poor manufactured coating performance, construction practices, latent third-party damages to pipe coating, and the effect of stray currents from transit infrastructure such as subway and streetcars. The current failure projection model is forecasting an exponential increase in the number of corrosion-related failures, while the C55 value framework and the 40-year risk projection are showing an increase in the safety risk associated with steel main failures. In addition to age, vintage steel mains are also susceptible to accelerated degradation and/or higher risk of third-party damage in the following ways: • Compression couplings • Shallow blow-off valve assemblies that could be damaged during excavation activities • Reduction in the original depth of cover • Continuous exposure of road salt and seasonal ground movement on bridge crossing assets • Lack of cathodic protection with pipe casings that could result in corrosion causing excessive stress or shorts on the carrier pipe that is in contact with the casing, which could lead to the loss of containment • Manufacturing defects associated with seam welds and fittings that are weak points in the distribution system and could result in a loss of containment due to prolonged exposure to stress and corrosion • Latent damages to pipe coatings that were never reported to EGI for repair and became active corrosion sites, which could hamper the effect of the corrosion protection system and result in accelerated corrosion and potentially loss of containment. Site-Specific Concerns: Unable to determine leaks due to the close proximity of the NPS 12 470 psi system. Cathodic protection was not installed until the early 1970s. Approximately 429 services are off this network. Full replacement of main comprising Network 6584 is required - the NPS 12 St. Laurent Ottawa North line is 13.3 km and operates at 275 psi as Network 6584. It runs from south of St. Laurent Control Station (6584:653:1969) to Rockcliffe Control Station (Station #6B558A). It does not include the main south from St. Laurent Control Station to Industrial Avenue as well as the NPS 12 lateral main to Trans Alta (6584:1234:1235) but does include the NPS 12 lateral main along Tremblay Road (and does not include the crossing at the Rideau River to Station #61171A). In 2018, pressure increase to Avenue O was completed. In 2019/2020, approximately 3.1 km of plastic pipe was installed on Tremblay and the Avenues and the services transferred over to IP. Due to a road moratorium, 2 km of 6-inch PE IP main on St. Laurent between Donald St. and Montreal was brought forward from 2021 to 2019/2020 and approximately 80 services. Assets: Lower Section is comprised of two projects: • Lower Section Part 1: Lancaster and Gladwin Cres. - Install 1.9 km of 4-inch PE relaying 17 services, 8 headers and pressure increasing 2 headers and relighting 170 customers. • Lower Section Part 2: Industrial Ave. - Install 1.3 km of 4-inch PE and relay 13 services and pressure increase 2 headers and relight approximately 44 customers. Related Programs: 6422, 10089, 10289, 10290, 10291, 10292, 10293, 10294 | On Hold |  | Technical Evaluation "On Hold" until further assessment from the E-DIMP Program confirms the project scope and timing.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 10290 | St. Laurent Phase 3 - Coventry/Cummings/St. Laurent (Plastic) | 2024 | 11273058.774 | General Concerns: Vintage steel mains have shown signs of declining health due to the cumulative effective of poor manufactured coating performance, construction practices, latent third-party damages to pipe coating, and the effect of stray currents from transit infrastructure such as subway and streetcars. The current failure projection model is forecasting an exponential increase in the number of corrosion-related failures, while the C55 value framework and the 40-year risk projection are showing an increase in the safety risk associated with steel main failures. In addition to age, vintage steel mains are also susceptible to accelerated degradation and/or higher risk of third-party damage in the following ways: • Compression couplings • Shallow blow-off valve assemblies that could be damaged during excavation activities • Reduction in the original depth of cover • Continuous exposure of road salt and seasonal ground movement on bridge crossing assets • Lack of cathodic protection with pipe casings that could result in corrosion, causing excessive stress or shorts on the carrier pipe that is in contact with the casing, which could lead to the loss of containment • Manufacturing defects associated with seam welds and fittings that are weak points in the distribution system and could result in a loss of containment due to prolonged exposure to stress and corrosion • Latent damages to pipe coatings that were never reported to EGI for repair and became active corrosion sites, which could hamper the effect of the corrosion protection system and result in accelerated corrosion and potentially loss of containment. Site-Specific Concerns: Unable to determine leaks due to the close proximity of the NPS 12 470 psi system. Cathodic protection was not installed until the early 1970s. Approximately 429 services are off this network. Full replacement of main comprising Network 6584 is required - the NPS 12 St. Laurent Ottawa North line is 13.3 km and operates at 275 psi as Network 6584. It runs from south of St. Laurent Control Station (6584:653:1969) to Rockcliffe Control Station (Station #6B558A). It does not include the main south from St. Laurent Control Station to Industrial Avenue as well as the NPS 12 lateral main to Trans Alta (6584:1234:1235) but does include the NPS 12 lateral main along Tremblay Road (and does not include the crossing at the Rideau River to Station #61171A). In 2018, pressure increase to Avenue O was completed. In 2019/2020, approximately 3.1 km of plastic pipe was installed on Tremblay and the Avenues and the services transferred over to IP. Due to a road moratorium, 2 km of 6-inch PE IP main on St. Laurent between Donald St. and Montreal was brought forward from 2021 to 2019/2020 and approximately 80 services. Assets: This project is to install 800 m NPS 6, 525 m NPS 2 IP, transfer 27 services to IP from XHP, and abandon 1 station on Coventry and Cummings. Related Programs: 6422, 10089, 10288, 10289, 10291, 10292, 10293, 10294 General Concerns: Vintage steel mains have shown signs of declining health due to the cumulative effective of poor manufactured coating performance, construction practices, latent third party damages to pipe coating, and the effect of stray currents from transit infrastructure such as subway and streetcars. The current failure projection model is forecasting an exponential increase in the number of corrosion related failures, while the C55 value framework and the 40-year risk projection are showing an increase in the safety risk associated with steel main failures. In addition to age, vintage steel mains are also susceptible to accelerated degradation and/or higher risk of third party damage in the following ways: -Compression couplings -Shallow blow-off valve assemblies that could be damaged during excavation activities -Reduction in the original depth of cover -Continuous exposure of road salt and seasonal ground movement on bridge crossing assets -Lack of cathodic protection with pipe casings that could result in corrosion, causing excessive stress or shorts on the carrier pipe that is in contact with the casing, which could lead to the loss of containment -Manufacturing defects associated with seam welds and fittings that are weak points in the distribution system and could result in a loss of containment due to prolonged exposure to stress and corrosion -Latent damages to pipe coatings that were never reported to EGI for repair and became active corrosion sites, which could hamper the effect of the corrosion protection system and result in accelerated corrosion and potentially loss of containment. Site-specific Concerns: Unable to determine leaks due to the close proximity of the NPS 12 470 psi system. Cathodic protection wasn't installed until the early 1970s. Approximately 429 services are off this network. Full replacement of main comprising Network 6584 - The NPS 12 St. Laurent Ottawa North line is 13.3 km and operates at 275 psi as Network 6584. It runs from south of St. Laurent Control Station (6584:653:1969) to Rockcliffe Control Station (Station #6B558A). It does not include the main south from St Laurent Control Station to Industrial Avenue as well as the NPS 12 lateral main to Trans Alta (6584:1234:1235) but does include the NPS 12 lateral main along Tremblay Road (but does not include the crossing at the Rideau River to Station #61171A). In 2018, pressure increase to Avenue O was completed. In 2019/2020, approx. 3.1 km of plastic pipe has been installed on Tremblay and the Avenues and the services transferred over to IP. Due to a road moratorium, 2 km of 6" PE IP main on St Laurent between Donald St and Montreal was brought forward from 2021 to 2019/2020 and approx. 80 services. Assets: This project is to install 800 m NPS 6, 525 m NPS 2 IP, transfer 27 services to IP from XHP, abandon 1 station on Coventry and Cummings. Related Programs: 6422, 10089, 10288, 10289, 10291, 10292, 10293, 10294 | On Hold |  | Technical Evaluation "On Hold" until further assessment from the E-DIMP Program confirms the project scope and timing.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 10292 | St. Laurent Phase 3 - Montreal to Rockcliffe (Plastic) | 2024 | 11877934.0656 | General Concerns: Vintage steel mains have shown signs of declining health due to the cumulative effective of poor-manufactured coating performance, construction practices, latent third-party damages to pipe coating, and the effect of stray currents from transit infrastructure such as subway and streetcars. The current failure projection model is forecasting an exponential increase in the number of corrosion-related failures, while the C55 value framework and the 40-year risk projection show an increase in the safety risk associated with steel main failures. In addition to age, vintage steel mains are also susceptible to accelerated degradation and/or higher risk of third-party damage in the following ways: • Compression couplings • Shallow blow-off valve assemblies that could be damaged during excavation activities • Reduction in the original depth of cover • Continuous exposure of road salt and seasonal ground movement on bridge crossing assets • Lack of cathodic protection with pipe casings that could result in corrosion causing excessive stress or shorts on the carrier pipe that is in contact with the casing, which could lead to the loss of containment • Manufacturing defects associated with seam welds and fittings that are weak points in the distribution system and could result in a loss of containment due to prolonged exposure to stress and corrosion • Latent damages to pipe coatings that were never reported to EGI for repair and became active corrosion sites, which could hamper the effect of the corrosion protection system and result in accelerated corrosion and potentially loss of containment. Site-Specific Concerns: An inability to determine leaks due to the close proximity of the NPS 12 470 psi system is a concern. Cathodic protection was not installed until the early 1970s. Approximately 429 services are off this network. Full replacement of main comprising Network 6584 is required - the NPS 12 St. Laurent Ottawa North line is 13.3 km and operates at 275 psi as Network 6584. It runs from south of St. Laurent Control Station (6584:653:1969) to Rockcliffe Control Station (Station #6B558A). It does not include the main south from St. Laurent Control Station to Industrial Avenue as well as the NPS 12 lateral main to Trans Alta (6584:1234:1235) but does include the NPS 12 lateral main along Tremblay Road (and does not include the crossing at the Rideau River to Station #61171A). In 2018, pressure increase to Avenue O was completed. In 2019/2020, approximately 3.1 km of plastic pipe was installed on Tremblay and the Avenues and the services transferred over to IP. Due to a road moratorium, 2 km of 6-inch PE IP main on St. Laurent between Donald St. and Montreal was brought forward from 2021 to 2019/2020 and approximately 80 services. Assets: Install approximately 2.9 km of 6-inch PE and 122 m of 2-inch PE, transferring 135 customers to the IP, pressure decrease Hillsdale Rd. and abandon St 6B882 Lansdowne/Hillsdale. Related Programs: 6422, 10089, 10288, 10290, 10291, 10289, 10293, 10294 | On Hold |  | Technical Evaluation "On Hold" until further assessment from the E-DIMP Program confirms the project scope and timing.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 10293 | St. Laurent Phase 3 - North/South (NPS12/16 Steel) | 2024 | 59372891.6594 | The NPS 12 St Laurent Pipeline requires replacement due to various pipeline conditions associated with the 1970 vintage steel mains including poor coating, unknown compression coupling fittings, reduced depth of cover, corrosion induced by declining cathodic protection. Replacing the main will ensure continued operation of EGI's gas distribution system, and will mitigate safety risks to employees, contractors, and general public. This project will install 6.5 km NPS 12 Steel Gas Main, 2.4 km NPS 16 Steel Gas Main, 5.1 km Plastic Gas Main and relay all XHP services to the new plastic gas main. | On Hold |  | Technical Evaluation "On Hold" until further assessment from the E-DIMP Program confirms the project scope and timing.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 10294 | St. Laurent Phase 4 - East/West (NPS12 Steel) | 2025 | 24233805.1776 | The NPS 12 St Laurent Pipeline requires replacement due to various pipeline conditions associated with the 1970 vintage steel mains including poor coating, unknown compression coupling fittings, reduced depth of cover, corrosion induced by declining cathodic protection. Replacing the main will ensure continued operation of EGI's gas distribution system, and will mitigate safety risks to employees, contractors, and general public. This project will install 3.1 km NPS 12 Steel Gas Main, Install 3.2 km Plastic Gas Main and relay all XHP services to the new plastic gas main | On Hold |  | Technical Evaluation "On Hold" until further assessment from the E-DIMP Program confirms the project scope and timing.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 13609 | Service Relay Blanket - Area 60* | 2020 | 52687564.7838 | General: A distribution service refers to the pipe between the distribution main and the customer’s meter set. Over the years, different materials have been used for this asset, including steel, copper, and varying resins of plastic, each with unique characteristics that contribute to their performance over time. Services can be repaired or replaced depending on asset condition and the nature of the issue exhibited. Generally, replacement is the preferred approach to mitigate unacceptable asset condition. | Completed | Fail | See investment description, IRPAs not applicable
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30330 | 2nd Ave - Eastern - Area 60 - 1197 | 2028 | 4087217.3282 | 2nd Ave. - Eastern - Area 60 - 1197 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30331 | 3rd Ave - Eastern - Area 60 - 1226 | 2030 | 3232111.5592 | 3rd Ave. - Eastern - Area 60 - 1226 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30332 | Adelaide St - Eastern - Area 60 - 1218 | 2031 | 2158469.8345 | Adelaide St. - Eastern - Area 60 - 1218 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30333 | Ainsley Dr - Eastern - Area 60 - 1723 | 2027 | 2128899.7512 | Ainsley Dr - Eastern - Area 60 - 1723 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Remove 8 m of mains from project due to overlap (updated as per regional feedback). | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30338 | Beckwith St N - Eastern - Area 60 - 1198 | 2032 | 2688180.9431 | Beckwith St. N. - Eastern - Area 60 - 1198 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30339 | Bell St - Eastern - Area 60 - 1052 | 2032 | 2274692.74 | Bell St. - Eastern - Area 60 - 1052 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: No timing comment was provided. | Completed | Fail | NPS 2, cannot downsize or retire
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30340 | Borthwick Ave - Eastern - Area 60 - 1139 | 2031 | 3192788.0743 | Borthwick Ave. (moratorium is until 2025) - Eastern - Area 60 - 1139 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Road work was completed in 2020. Road restrictions will be in place for a long time. The 2025 execution date is based on region's comment. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30341 | Brock St - Eastern - Area 60 - 1485 | 2032 | 3472215.0625 | Brock St. - Eastern - Area 60 - 1485 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30345 | Drummond St W - Eastern - Area 60 - 1142 | 2028 | 2470449.8882 | Drummond St. W. - Eastern - Area 60 - 1142 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30346 | Elm St E - Eastern - Area 60 - 1147 | 2032 | 2426469.8141 | Elm St. E. - Eastern - Area 60 - 1147 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There are possible road restrictions on County Rd 29 and 15. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30348 | Elmsley St N - Eastern - Area 60 - 1725 | 2032 | 1861690.3013 | Elmsley St. N. - Eastern - Area 60 - 1725 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: A possible permit may be required due to proximity to rail yard. A possible Conservation Authority (CA) permit may be required due to historic buildings. Estimate includes 46 m of PE replacement but the number of services may not be correct; | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30349 | Emily St - Eastern - Area 60 - 1101 | 2031 | 2287957.2866 | Emily St. - Eastern - Area 60 - 1101 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There are possible road restrictions. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30350 | First Ave - Eastern - Area 60 - 1175 | 2031 | 3442054.7838 | First Ave. - Eastern - Area 60 - 1175 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30351 | Flora St - Eastern - Area 60 - 1151 | 2032 | 2528992.2648 | Flora St - Eastern - Area 60 - 1151 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Possible road work to occur along High St. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30354 | Grant St - Eastern - Area 60 - 1098 | 2032 | 2665699.2668 | Grant St. - Eastern - Area 60 - 1098 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Possible CA permit may be required due to proximity to Tay River. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30356 | Havelock St - Eastern - Area 60 - 1215 | 2031 | 4243310.7127 | Havelock St. - Eastern - Area 60 - 1215 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30357 | Herriott St - Eastern - Area 60 - 1089 | 2032 | 1848715.0779 | Herriott St. - Eastern - Area 60 - 1089 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There are possible road restrictions on Moffatt Asphalt Overlay. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30359 | Irene Cres - Eastern - Area 60 - 1141 | 2028 | 2919752.5764 | Irene Cres. - Eastern - Area 60 - 1141 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30360 | James St - Eastern - Area 60 - 1112 | 2029 | 2617144.2618 | James St. - Eastern - Area 60 - 1112 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: CR 34 Major Rd. into Quebec might require an MTO permit. Main St. is already dual-mained and side streets could be considered. Possible CA permit may be required due to proximity to Ottawa River. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30361 | James St W - Eastern - Area 60 - 1184 | 2031 | 2941172.3974 | James St. W. - Eastern - Area 60 - 1184 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30363 | Lake Ave E - Eastern - Area 60 - 1145 | 2032 | 4172549.0042 | Lake Ave. E. - Eastern - Area 60 - 1145 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30364 | LePage Ave - Eastern - Area 60 - 1214 | 2029 | 3885027.532 | LePage Ave. (execute by 2025 - paving proposed between 2022 - 2025) - Eastern - Area 60 - 1214 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Some road and sewer work was done in 2021, and paving is proposed between 2022 and 2025 - updated to reflect region's comments. | Completed | Fail | NPS 2, cannot downsize or retire
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30365 | Madawaska St - Eastern - Area 60 - 1072 | 2030 | 3169523.2131 | Madawaska St - Eastern - Area 60 - 1072 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30366 | Main St E - Eastern - Area 60 - 1172 | 2031 | 3168096.2442 | Main St. E. - Eastern - Area 60 - 1172 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There is 83 m of 2-inch steel being replaced. Downtown road is likely to have time restrictions. | Completed | Fail | NPS 2, cannot downsize or retire
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30367 | McCann St - Eastern - Area 60 - 1160 | 2029 | 4429657.887 | McCann St. - Eastern - Area 60 - 1160 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30368 | McGonigal St E - Eastern - Area 60 - 1041 | 2032 | 2640733.5126 | McGonigal St. E. - Eastern - Area 60 - 1041 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30369 | Moffatt St - Eastern - Area 60 - 1195 | 2032 | 3302942.1821 | Moffatt St. - Eastern - Area 60 - 1195 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Townline Rd. and Bridge St. are main roads. There are rectifier-protected areas. Main on Townline Rd. may have to stay steel. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30370 | Montgomery Pl - Eastern - Area 60 - 1228 | 2030 | 3228256.1096 | Montgomery Pl. - Eastern - Area 60 - 1228 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30372 | North St - Eastern - Area 60 - 1087 | 2029 | 2613031.06 | North St - Eastern - Area 60 - 1087 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30373 | Oak St - Eastern - Area 60 - 1133 | 2029 | 2720235.1023 | Oak St. - Eastern - Area 60 - 1133 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30378 | Prince Albert St - Eastern - Area 60 - 1099 | 2031 | 2866490.3335 | Prince Albert St. - Eastern - Area 60 - 1099 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30379 | Queen Mary St - Eastern - Area 60 - 1103 | 2030 | 3155878.101 | Queen Mary St. - Eastern - Area 60 - 1103 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30380 | Queen St N - Eastern - Area 60 - 1158 | 2030 | 3743197.7552 | Queen St. N. - Eastern - Area 60 - 1158 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30384 | Rochester St - Eastern - Area 60 - 1222 | 2031 | 2794056.6434 | Rochester St. - Eastern - Area 60 - 1222 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There is the potential for road restrictions due to congested area. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30385 | Sarah St - Eastern - Area 60 - 1188 | 2032 | 2805416.5778 | Sarah St. - Eastern - Area 60 - 1188 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30387 | Spring St - Eastern - Area 60 - 1047 | 2031 | 2097134.5716 | Spring St. - Eastern - Area 60 - 1047 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There are major roads where there could be difficulty with traffic management. CA permit is required due to proximity to river. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30389 | Summerville Ave - Eastern - Area 60 - 1484 | 2030 | 3502574.8368 | Summerville Ave. - Eastern - Area 60 - 1484 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30390 | Trenton Ave - Eastern - Area 60 - 1181 | 2032 | 2285031.9318 | Trenton Ave. - Eastern - Area 60 - 1181 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30391 | Victoria St - Eastern - Area 60 - 1138 | 2032 | 2566544.8259 | Victoria St - Eastern - Area 60 - 1138 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There is potential for road restrictions due to congested area. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30393 | William St - Eastern - Area 60 - 1092 | 2031 | 2157149.2309 | William St. - Eastern - Area 60 - 1092 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30394 | Wilson St E - Eastern - Area 60 - 1094 | 2029 | 2294785.6397 | Wilson St. E. - Eastern - Area 60 - 1094 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 30395 | Woodside Dr - Eastern - Area 60 - 1178 | 2030 | 3526589.3876 | Woodside Dr. - Eastern - Area 60 - 1178 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | 60 - Ottawa | Distribution Pipe | Pass |  | 101343 | A60: Sparks St, Ottawa, Replacement | 2024 | 11808967.2278 | Issue/Concern: Sparks Street’s NPS 12 steel main is approaching end of life and a replacement is necessary. This main was installed in the 1960s and 1970s and has compression couplings, Dresser-style fittings, drips and blow-off valves. Sparks Street is a pedestrian path through the downtown core of Ottawa with no vehicular access; therefore, performing maintenance activities or accessing the site during emergencies is a challenge. Replacement work is timed ahead of planned third-party road construction work along Sparks and Albert Street that could create third-party damage to these components and result in loss of containment. It will also provide an opportunity to coordinate development and design work with the Sparks Business Improvement Area (BIA) along with planned utility work on Albert Street. Assets: Approximately 1,100 m of NPS 12 intermediate pressure (IP) steel pipe on Albert Street, 900 m of NPS 4 IP Polyethylene (PE) pipe on Sparks Street, and 175 m of NPS 4 PE pipe from Lyons to Wellington. Related Programs: Not applicable. | Completed | Fail | ETEE - Potentially could reduce project scope. Project has failed the technical evaluation as this is a trunk main which should not be downsized due to security of supply.
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 1012 | LEEDS GATE | 2026 | 1046195.8802
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 7750 | HALEY GATE | 2025 | 530591.5458
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 7755 | PETAWAWA GATE | 2026 | 455649.1434
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 23766 | ST. PAUL & SANDFIELD DISTRICT ( ALEXANDRIA ) | 2027 | 305290.272
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 101151 | 6B758A - EAGLESON & HAZELDEAN DISTRICT | 2023 | 196824.9705
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 101152 | 6B562A - CAMPEAU & TERON DISTRICT HP ( O.P.P. ) | 2023 | 196824.9705
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 101153 | 6B435A - CORKSTOWN & WESTDALE DISTRICT | 2024 | 202265.3367
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 101154 | 61128A - CAMPBELL & MCNABB DISTRICT | 2024 | 202265.3367
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 501534 | Kemptville Gate Station - Electrical | 2023 | 249382.2876
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 501535 | Elizabethtown/Bethel - Electrical | 2027 | 416883.3592
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 735164 | 6B631A MCCARTHY DR AND HUNT CLUB RD | 2023 | 196824.9705
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 735165 | 6B602A STARTOP DISTRICT XHP | 2023 | 196824.9705
Eastern | 60 - Ottawa | Distribution Stations | Fail | Dollar threshold | 735167 | 61061A PEMBROKE W. DISTRICT | 2023 | 196824.9705
Eastern | 60 - Ottawa | Distribution Stations | Pass |  | 3455 | Harmer District Station | 2028 | 5271812.4324 | Issue/Concern: EGI has a high pressure (HP) to intermediate pressure (IP) district station located inside a building. The regulator station is located in the garage of a house and is not to current EGI standards. The station is located close to a school, hospital, shopping complex, and dense residential population. The Integrity team is planning an inline inspection of the Vital NPS 12 (Network 6582) and additional space is required for a receiver. Assets: Station# 6B005A Related Program(s): N/A | Completed | Fail | Distribution station condition related, IRPA not applicable
Eastern | 60 - Ottawa | Distribution Stations | Pass |  | 3608 | BROCKVILLE GATE | 2025 | 2620193.821 | Brockville Gate Station is located on EGI-owned property approximately 5 km from the town of Brockville, Ontario. This station accepts natural gas from TC Energy and provides supply to two separate XHP networks. Station components include measurement, gas preheat system, pressure regulation, odourant injection and a telemetry system. This station supplies natural gas to approximately 19,463 customers in Brockville region. The following issues have been identified at this station: Pipes, Valves & Others: The existing valves at this site have experienced issues in performance and operation of the valves. Valve maintenance has been unable to remediate the problem and the valves have deteriorated to the point where the reliability is no longer acceptable. All valves will have to be replaced. The inlet of the regulator runs is a challenge every year. Heating: The boiler system was replaced in 2019. However, the glycol tank and heat exchanger will need to be replaced and relocated to meet Electrical Safety Authority (ESA) requirements. Residual glycol impacts are to be evaluated and removed as required, as a result of glycol release that was reported from a boiler inside the Boiler building. Pressure Control: The regulator station has boot-style regulators posing an undesired higher risk and high associated ongoing maintenance costs. Engineering has identified that boot-style regulators operating as both monitor and operating regulators is unacceptable. The regulator runs will have to be rebuilt. Odourization: The odourant system was installed in 2000. A new Odourant building will have to be installed to ensure adequate containment in the event of a leak. The injection pumps are located in the regulator room and will have to be relocated into the Odourant building to meet current standards. Telemetry and Electrical: The size of the Remote Terminal Unit (RTU) building is not an issue but the leaky roof is. This building not only houses the RTU but also the St. Lawrence Control Centre (CC) (this is the gas control hub for Leeds, Brockville, Bethel, St. Lawrence, Summerstown and Lancaster Gate stations, as well as International Bridge CDN and USA, and Lisgar). The transfer switch, main panel, and junction box are located in the old RTU room, which is attached to the instrumentation room, but does not violate the Electrical code. Boilers were recently replaced and can be reused as well as the inlet/outlet and tank pressure transmitters. New temperature transmitters and a new tank level gauge are needed. The ultrasonic electronics should be upgraded. The main disconnect should be taken off the Hydro pole and moved to the electrical/RTU room. There should be an upgrade to the CC Uninterruptible Power Supply (UPS) system (specifically for the network switches). The odourant tank is located in an old-style, steel building. The RTU is an older Control Wave Micro (CWM), but could suffice; however, its UPS should be upgraded. There is no boiler room CO detector. The odourant injection system should be separated from the regulators. There is no weather station. | Completed | Fail | Distribution station condition related, IRPA not applicable
Eastern | 60 - Ottawa | Distribution Stations | Pass |  | 3622 | SUMMERSTOWN GATE | 2026 | 3582564.794 | Summerstown Gate Station is located on EGI-owned property of approximately 1,000 m2 fenced compound in South Glengarry Township, Ontario, approximately 16 km from Cornwall, Ontario, within a rural area. This station accepts natural gas from TC Energy and provides supply to an XHP network, through components within the measurement system, pressure control system, heating system, odourant system, and telemetry system. This station feeds 265 customers. The following issues have been identified at this station: Valves & Piping: The existing valves at this site have experienced issues in performance and operation of the valves. Maintenance has been performed to attempt to remediate the valves; however, the valves have deteriorated to the point where the reliability is no longer acceptable. The existing inlet and bypass valves are flange by flange and have experienced leaks through these flanges. Flanged valves on the station inlets are more prone to leaks and more difficult to repair. Odourization: The odourant system was installed in 1998. The current configuration of the odourant system does not ensure adequate containment of the odourant product in the event of a leak and does not meet the current engineering standards and approvals. Telemetry & Electrical: The existing electrical system does not meet current EGI electrical installation standards. This poses a potential electrical hazard and faulty wiring may result in lost communications. Tower: Tower is to be removed as it is not required for SCADA communications. | Completed | Fail | Distribution station condition related, IRPA not applicable
Eastern | 60 - Ottawa | Distribution Stations | Pass |  | 7751 | KEMPTVILLE GATE | 2025 | 5739416.1023 | Kemptville Gate Station is located on EGI-owned property of approximately 2,825 m2 fenced compound in the Municipality of North Grenville, Ontario, approximately 37 km south of Ottawa, within a rural area. This station accepts natural gas from TC Energy and provides supply to XHP networks, through components within the Measurement system, Pressure Control system , Heating system, Odourant system, and Telemetry system. This station supplies natural gas to approximately 3,256 customers in the Kemptville area. The following issues have been identified at this station: Pipe, Valves & Others: The existing valves at this site have experienced issues in performance and operation. Maintenance has been performed to attempt to remediate the valves; however, the valves have deteriorated to the point where the reliability is no longer acceptable. Heating: The existing boilers at this site are 22 years old and have reached end of life based on condition review and performance. Pressure Control: The Regulation system is installed within a building currently in disrepair with several leaks. The operator and monitor regulators are both double-boot style regulators and are both susceptible to boot failure should they be exposed to significant debris in the system. Repairs have been made where possible but the building continues to deteriorate. Also, the working space inside the building produces an ergonomic/safety risk to EGI employees. This will require addition of filtration or regulation replacement. Furthermore, a new building will be required to address safety/ergonomic issues at the station. Odourization: The building has containment but does not meet current standards. There are no issues with the current system. Telemetry & Electrical: The Telemetry and Electrical systems do not meet current EGI standards, do not contain backup power supply in the event of power loss, and are approaching end of useful life. The existing Remote Terminal Unit (RTU) is obsolete and is required to be upgraded to current standards along with new communications equipment in order to mitigate cybersecurity threats. | Completed | Fail | Distribution station condition related, IRPA not applicable
Eastern | 60 - Ottawa | Growth | Pass |  | 3758 | Area 60 - Apartment Ensuite - New Construction* |  | 101628.6627 | Vertical Subdivision - A multiple unit residential building where each suite is individually metered.Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGD develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long term plans EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. Enbridge reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers; and, - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing Assets: Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Eastern | 60 - Ottawa | Growth | Pass |  | 3759 | Area 60 - Apartment Traditional - New Construction* |  | 402686.8957 | Apartment - An apartment customer is a multi-residential dwelling containing more than six units that is bulk-metered Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGD develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long term plans EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. Enbridge reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers; and, - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing Assets: Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Eastern | 60 - Ottawa | Growth | Pass |  | 1024 | NW 6581 Ottawa Reinforcement Phase 2 SRP | 2032 | 71584954.6355 | Issue/Concern/Opportunity: Reinforcement projects broadly involve the installation of new or modification of existing gas distribution assets to maintain minimum required system pressure, maintain capacity, and meet customer demand. These projects are primarily driven by customer growth and system reliability considerations. Failure to implement reinforcement projects in a timely manner could lead to a potential inability to support increasing demands of existing customers and the addition of future customers. This network in Ottawa is predominantly made up of residential and commercial customers. In the current configuration, a high pressure network is exclusively fed by both the Ottawa and Richmond Gate Stations. An upstream flow constraint has been identified at the Ottawa Gate Station, along with a bottleneck constraint for gas fed from Richmond Gate Station. The South outlet of Ottawa Gate can be set to as low as 400 psig (normally 470 psig) while Richmond Gate is kept at 470 psig, thus flowing more gas from the west to the east. The current configuration, an existing NPS 12 high pressure pipeline along Fallowfield Road is a bottleneck for gas flowing from the west to Richmond Gate Station, and to eastern areas. The previously constructed Ottawa Reinforcement Plan (ORP) Phase 1 as well as the Strandherd River crossing has helped move gas from Richmond Gate eastward to areas of concentrated and growing gas demand. This reinforcement will assist in moving additional gas from Richmond Gate toward the areas that would be serviced by Ottawa Gate, and remove the bottleneck constraint. There were approximately 193,553 customers on the associated networks as of 2016. Assets: Existing NPS 12 HP Pipe Related Program: Not applicable | In Progress
Eastern | 60 - Ottawa | Growth | Pass |  | 3761 | Area 60 - Commercial - New Construction* |  | 25177089.1278 | Issue/Concern: Commercial New Construction refers to a customer intending to run a commercial business in a newly-constructed building and intending to using natural gas to meet energy needs Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Eastern | 60 - Ottawa | Growth | Pass |  | 3762 | Area 60 - Industrial - New Construction* |  | 34475558.4779 | Issue/Concern: Industrial New Construction refers to a customer intending to run an industrial manufacturing business in a newly-built facility and intending to use natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Eastern | 60 - Ottawa | Growth | Pass |  | 3764 | Area 60 - Residential - New Construction* |  | 237751447.4881 | Issue/Concern: Residential New Construction refers to a new residential construction development of detached single homes constructed by the builder for domestic purposes. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Eastern | 60 - Ottawa | Growth | Pass |  | 3765 | Area 60 - Residential - Replacement* |  | 169789900.1644 | Issue/Concern: Residential Replacement refers to a residential replacement customer using a fuel other than natural gas for domestic purposes and is converting to natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Eastern | 60 - Ottawa | Growth | Pass |  | 7743 | NW 6587 L'Original Reinforcement SRP | 2025 | 1883891.7028 | Victoria St - Eastern - Area 60 - 1138 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There is potential for road restrictions due to congested area. Issue/Concern: Reinforcement projects broadly involve the installation of new or modification of existing gas distribution assets to maintain minimum required system pressure to maintain the capacity to meet customer demand. These projects are primarily driven by customer growth and system reliability considerations. Failure to implement reinforcement projects in a timely manner could lead to a potential inability to support increasing demands of existing customers and the addition of future customers. • Project Purpose/Need: This reinforcement is to add capacity within legacy Enbridge Gas Distribution's pipe network to: o Satisfy the current contractually allowable demand of the Large Volume Contract (LVC) customer Ivaco Rolling Mills, which is 6,800 m3/h o Support customer growth of the downstream High Pressure Polyethylene (HPPE) network This geographic area sits at the eastern tail end of XHP network 6587, which is fed exclusively by Lancaster gate to the southeast. • Pressure Issue/Concern : The minimum system pressure was forecasted to be infeasible by 2020. • Customer Growth Issue/Concern: As of 2017, there are 2,039 customers on this network. Without reinforcement, a forecasted 24 customers may not be able to be added. • Risk If Not Completed: System risk without the reinforcement o EGI may not be able to satisfy contractual demand of a large-volume customer along with supporting forecasted customer growth o This network is at the mid-tail end of the East Valley line, with pressures approaching the minimum. o This XHP system is operating at over 30% Specified Minimum Yield Strength (SMYS). If this line pressure drops below 30% SMYS, this reinforcement will not be sufficient. o Approximately 1,430 customers would potentially be lost over the winter of 2017 – 2018. o There are approximately 2,039 customers forecasted to be connected by 2017. Assets (preferred option): • Station: 62328A set to 80 psig • Main: - 10 km - NPS 4 XHP main - from County Rd. 17 and Hwy 11 - to Cassburn Rd. and Emerson Rd. - along Hwy 11. Related Programs: Not applicable | Completed | Pass | CNG, ETEE - CNG potentially could defer project scope, ETEE potentially could eliminate (with CNG as bridging solution), reduce or defer project scope.
Eastern | 60 - Ottawa | Growth | Pass |  | 102119 | Brockville Gate Extension | 2025 | 3170326.6761 | Issue/Concern/Opportunity: Area 60 - the Maitland and Brockville regions are currently served by two Gate Stations (i.e., Brockville and Bethel). The Bethel Gate requires a rebuild to maintain safe and reliable operations; and there is an opportunity to add customers in the region if the network has more capacity. The preferred option is to build a lateral connected to the existing Brockville Network extending to the current Bethel Gate site; a district station would be required along with 3,500 m of pipe. Sixty-two potential customers have been identified along this route. A secondary option is to rebuild the Bethel Gate which will ensure safe and reliable operations but will not allow for the opportunity to connect potential new customers. Justification: Bethel Gate is scheduled for a rebuild in 2023 and the pipeline reinforcement is a second option which has added benefits of customer additions and lower future maintenance costs. Assets: Bethel Gate Station Related Program: Not applicable | Completed | Fail | Timing - Market based supply side alternatives not applicable
Eastern | 60 - Ottawa | Growth | Pass |  | 501824 | Huntmar Drive Reinforcement | 2023 | 3542335.7417 | Reinforcement required to maintain the gas capacity in the Kanata West area for multiple developments proposed and being built currently in the area. Scope: Install approx. 2.8km of NPS 6 XHP Steel gas main from NPS 12 XHP at Huntmar & Hazeldean going north on Huntmar to Palladium Dr, then install a XHP-HP station at 620 Palladium Drive with its outlet tied in to the existing NPS 6 HP Steel gas main on Palladium Drive. There are no station projects directly linked to this reinforcement project. | Planned
Eastern | 60 - Ottawa | Growth | Pass |  | 736679 | NW 6544 Sherwood Drive Crossing SRP | 2024 | 99947.3947 | Issue/Concern/Opportunity: Reinforcement required to resolve low pressure points that are below the minimum system pressure. Pressures are forecasted to be below the system minimum by 2024 Assets: 30m of NPS 2 PE IP road crossing at Sherwood Dr. and Old Irving Related Program: Not applicable | Planned
Eastern | 60 - Ottawa | Growth | Pass |  | 736680 | NW 6429 Rockland IP Reinforcement SRP | 2024 | 233210.5877 | Issue/Concern/Opportunity: Increase pressures that are below new system min in multiple locations. Pressure less then the 20 psi minimum in multiple locations on the network. Reinforcements are required to bring the system within standards. The system is single-fed and is located at the tail end of the XHP 6580 network that is primarily fed by the Ottawa Gate Station. Assets: Install 30m of 1 1/4" PE IP on Du Chateau Ave from Woods St to 30 m S of Woods St Install 55m of 2" PE IP on Lalonde St from Laurier St to 55 m N of Laurier St Install 100m of 2" PE IP On Notre Dame St from Laurier St to Alma St Related Program: Not applicable | Completed | Pass | CNG, ETEE - CNG potentially could defer project scope, ETEE potentially could reduce or defer project scope.
Eastern | 60 - Ottawa | Growth | Pass |  | 736682 | NW 6544 Bank St. Reinforcement SRP | 2024 | 174907.9408 | Issue/Concern/Opportunity: Reinforcement required to resolve operational issues and bring pressures above the 20 psig minimum sytem pressures and support future growth. The system being reinforced is in Ottawa central with high potential for growth. Current system pressures are below the minimum system pressures. Network is double-fed by Ottawa Gate and Richmond Gate Station Assets: 90m NPS 2 PE IP on Bank St. from Ardington Ave to Flora St. Related Program: Not applicable | Completed | Pass | CNG, ETEE - CNG potentially could defer project scope, ETEE potentially could eliminate or defer project scope.
Eastern | 60 - Ottawa | Growth | Pass |  | 736758 | NW 6466 Carp Pressure Increase SRP | 2024 | 25627.5371 | Issue/Concern/Opportunity: Reinforcement involves an in-class pressure increase to resolve operational issues and pressure low points on the network below the minimum system and support growth. The network being reinforced is single-fed and sits on the tail end of the 6583 high pressure network. Pressures are forecasted to go below the minimum system pressure by 2024. All pipes were installed after 1994. Assets:New district station replacing station near the intersection of Carp Rd. and March Rd. (Station ID: 526053). Related Investments: Not applicable | Planned
Eastern | 60 - Ottawa | Growth | Pass |  | 736759 | NW 6462 Russell Pressure Increase and Reinforcement SRP | 2024 | 25627.5371 | Issue/Concern/Opportunity: Reinforcement involves an in-class pressure increase from 45 psi to 55 psi to resolve operational issues and pressure lowpoints on the network below the 20 psig minimum system pressure and to support growth. All pipes installed after 1994. The two adjacent networks are not currently connected, and a future reinforcement will connect them. Eastern network contains ~42 km PE IP to be increased. Western network contains ~5.8 km PE IP to be increased. Station flows are 2022 and 2032 from previous project timing. The network is single-fed exclusively by Metcalfe Gate Station Assets: -Increase pressures at existing district stations on the intersection of Old Towne Ave. and Craig St. (Station ID 3180568) -Increase pressures at existing district station on the intersection of Castor St. and Warner St. (Station ID: 526844) -160 m of NPS 2 PE IP pipe on Craig St from Olde Towne Ave to Forced Rd Related Investments: Not applicable | Planned
Eastern | 60 - Ottawa | Growth | Pass |  | 736760 | NW 6652 Bunker Rd. Reinforcement SRP | 2028 | 134332.4723 | Issue/Concern/Opportunity: Reinforcement required to resolve operational issues and pressure lowpoints on the network below the 20 psig minimum system pressure and support growth. Network sits near the end of the XHP 6581 NW that is fed by Ottawa Gate and Richmond Gate Station. Pressure are forecasted to be below the minimum system pressures by 2027 Assets: -240 m NPS 2 PE IP on Bunker Rd. from Marina Dr. to 240m W of Marina Dr. Related Program: Not applicable | Completed | Pass | CNG, ETEE - CNG potentially could defer project scope, ETEE potentially could eliminate, reduce or defer project scope.
Eastern | 60 - Ottawa | Growth | Pass |  | 736761 | NW 6579 Kemptville Reinforcement SRP | 2026 | 533940.0065 | Issue/Concern/Opportunity:Reinforcement required to resolve operational issues and pressure lowpoints on the network below the 20 psig minimum system and support growth. Estimated 2 weeks of Aecon and 2 days for TFS. Also estimating to buy district station in 2025. System pressures are forecasted to be below the minimum system pressure by 2026. Network is single-fed exlusively by Kemptville Gate Station Assets: - 50 m NPS 2 SC XHP road crossing at Country Rd. 43 and Rideau St. - 40 m NPS 2 PE IP road crossing at Country road 43 and Rideau St. -20 m NPS 1 1/4 PE IP road crossing at Thomas St. and Asa. St. -New district station near the intersection of Country Rd. 43 and Rideau St. to feed the Kemptville community Related Program: Not applicable | Completed | Pass | CNG, ETEE - CNG potentially could defer project scope, ETEE potentially could reduce project scope with CNG as a bridging solution.
Eastern | 60 - Ottawa | Growth | Pass |  | 736762 | NW 6463 Embrun Reinforcement SRP | 2026 | 424995.6832 | Issue/Concern/Opportunity: Reinforcement to support imminent and significant growth in the area. Network is currently operating under 20psi Assets: NPS 4 PE IP along the south side of Ste Therese Blvd in Embrun Related Program: Growth investment # 737580 | Completed | Pass | CNG, ETEE - CNG potentially could defer project scope, ETEE potentially could reduce project scope with CNG as a bridging solution.
Eastern | 60 - Ottawa | Growth | Pass |  | 736763 | NW 6556 Des Paturages Rd Reinforcement SRP | 2029 | 124644.141 | Issue/Concern/Opportunity: Reinforcement required to resolve operational issues and pressure lowpoints on the network below the 20 psig minimum system. The reinforcement will also support future growth. Network 6556 estimated to be below minimum system pressures by 2029. NW 6556 is situated near the tail end of the of the XHP network 6587 fed exclusively by Lancaster Gate Station and the community is located next to the LVC Ivaco Rolling Mills. A reinforcement has also been called for the 6587 NW (C55 ID#: 7743) to support both this community and meet the contractual demands of Ivaco Rolling Mills. Assets: 220m of NPS 2 PE IP Related Program: C55 ID: 7743 | In Progress
Eastern | 60 - Ottawa | Growth | Pass |  | 736764 | NW 6518 Barrhaven Reinforcement SRP | 2028 | 35821.9926 | Issue/Concern/Opportunity: Reinforcement required to resolve operational issues and pressure lowpoints on the network below the 20 psig minimum system. The reinforcement will also support growth. Pressures are forecasted to be below 20 psig by 2028. The network supports a densely populated area that is fed by both Ottawa Gate Station and Richmond Gate Station Assets: -20 m NPS 1 1/4 PE IP -new district station at the intersection of Larkin Dr. and Fallowfield Rd. Related Program: Not applicable | Planned
Eastern | 60 - Ottawa | Growth | Pass |  | 736766 | NW 6540 Stevenage Dr Reinforcement SRP | 2029 | 320513.5054 | Issue/Concern/Opportunity: Reinforcement required to resolve operational issues and pressure lowpoints on the network below the 20 psig minimum system and support growth. Pressures are forecasted to be below the minimum system pressure by 2029. The network supports the demand of LVC Ottawa Fibre L.P. The reinforcement will mitigate the system risk of not being able to satisfy the contractual demand of this LVC and the needs of potential future growth. Assets: 310 m of NPS 4 PE IP on Stevenage Rd. from Hawthorne Rd. to Overton Dr. Related Program: Not applicable | Planned
Eastern | 60 - Ottawa | Growth | Pass |  | 736768 | NW 6414 Orville St Reinforcement SRP | 2030 | 45850.5112 | Issue/Concern/Opportunity: Reinforcement required to resolve operational issues and pressure lowpoints on the network below the 20 psig minimum system pressure and support growth. System pressures expected to be below minimum system pressures by 2030. Network supports a densely populated area in Ottawa. Assets:15m NPS 2 PE IP road crossing at Orville St. and Basswood Ave. Related Investments: Not applicable | Planned
Eastern | 60 - Ottawa | Growth | Pass |  | 736769 | NW 6524 Quincy Ave. Reinforcement SRP | 2030 | 201742.2492 | Issue/Concern/Opportunity: Reinforcement required to resolve operational issues and pressure lowpoints on the network below the 20 psig minimum system and support system growth. System pressures are forecasted to be below the minimum system pressure by 2031. Reinforcement will support a highly populated area in central Ottawa. Assets: - 30 m of NPS 2 PE IP road crossing at Ogilvie Rd. and Quincy Ave. - 15 m of NPS 4 PE IP road crossing at Canoteck Rd. Related Program: Not applicable | Planned
Eastern | 60 - Ottawa | Utilization | Pass |  | 13548 | MXGI Area 60* | 2019 | 56558620.592 | Meters: Meters are used to determine the gas consumption input of customer billing. The replacement program for meters is mandated by Measurement Canada. The program includes: testing, repair, and replacement requirements of meters and instruments. All verified meters are approved by Measurement Canada with an issuance of a certificate which identifies that the meter complies with Electricity and Gas Specification S-EG-02. The Company must ensure all measurement devices remain in compliance for annual audits by Measurement Canada. Measurement Canada specifies tolerances under which the meter must operate in the field. The Company must demonstrate that all aspects of its meter sampling, maintenance, and replacement comply with these criteria in order to be accredited by Measurement Canada to be an “Authorized Service Provider” and adhere to Measurement Canada’s accreditation standard S-A-01. Meters may also require exchange for issues such as: damages, leaks, customer billing issues. Regulation: Regulators are the last line of defense for over-pressure to the customer. The condition of regulation systems is determined by regulator performance, corrosion of piping and regulators, and adherence to installation specifications. Failure of the regulation system can cause pressured gas to enter the premise, resulting in failure of gas equipment, loss of containment, and potentially fire or explosion. | Completed | Fail | See investment description, IRPAs not applicable
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 1289 | Thurlow Township Retrofit |  | 1145916.207
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 48472 | KING: 22-21-043 Dist-Repl-Contractor Services* | 2020 | 4510485.2576
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 48477 | King: 22-YY-022 Mains Municipal* | 2020 | 7517484.6805
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 48478 | KING: 22-YY-023 Dist Company Mains Leakage* | 2020 | 2530759.0698
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 100690 | King - Block Valve Assembly Maintenance (Various Locations)) |  | 577970.4356
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 100693 | King - King Street East Replacement (Prescott) | 2029 | 1667332.9985
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 100744 | King - Collins Bay NPS10 Shallow Pipe | 2023 | 1284159.2771
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 100746 | King - Property Line PLPRS Replacement (Various Locations) | 2025 | 190929.9391
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 734706 | King: Thin Wall and Copper Pipe Replacement (Various Locations in Area) | 2032 | 583717.408
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 734740 | King: 520 Wallrich Ave. Service Block Valve Abandonment (Cornwall) | 2023 | 36743.1435
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 734742 | King: Victoria Street Depth of Cover (Port Hope) | 2029 | 1588743.3659
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 734743 | King: Bath and Gardiners Valve Replacement (Kingston) | 2031 | 139228.2164
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 734795 | King: HWY#2 Caravan Camp PRS Abandonment | 2023 | 43593.5601
Eastern | Div_22 - Kingston | Distribution Pipe | Fail | Dollar threshold | 734921 | NPS 8 Augusta |  | 1432367.7577
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30417 | Arthur St - Cornwall - Eastern - 1727 | 2029 | 3484008.5664 | General: Vintage Steel Replacement Program is a proactive replacement program to renew aging vintage steel pipe assets before reaching their end of life. Vintage steel mains have shown signs of declining health due to the cumulative effect of poor, manufactured coating performance; construction practices; latent third-party damages to pipe coating; and the effect of stray currents from transit infrastructure such as subway and streetcars. The current failure projection model is forecasting an exponential increase in the number of corrosion-related failures, while the C55 value framework and the 40-year risk projection are showing an increase in the safety risk associated with steel main failures. Vintage steel systems also have potential to include compression couplings, shallow installation depth and shallow assemblies making pipe susceptible to third-party damage, and manufactured defects associated with seam welds and fittings. | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30418 | Augustus St - Cornwall - Eastern - 1729 | 2029 | 2680608.7462 | Augustus St - Cornwall - Eastern - 1729Vintage steel exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (Vintage Steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization Comments: Remove York from 5th to 9th streets. Recently replaced - updated based on region's feedback (Augustus St - 1729) Road work on York in 2021 - removed York from project scope | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30419 | Bridge St W-Napanee-1602 | 2031 | 5565056.477 | Bridge St. W. - Napanee - 1602 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30420 | Cedar Alley-Ganonoque-1455 | 2032 | 3399814.5339 | Cedar Alley - Ganonoque - 1455 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30421 | Front St-Belleville-1592 | 2030 | 5630449.3584 | Front St. (moratorium until 2025) - Belleville - 1592 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There has been road construction within last 3 years - project has been updated to reflect moratorium until 2025. | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30423 | Garden Alley 2-Ganonoque-1494 | 2028 | 3968189.3732 | Garden Alley 2 - Ganonoque - 1494 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30426 | Hickory St-Ganonoque-1454 | 2031 | 2673448.9058 | Hickory St - Gananoque - 1454 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Elm and Hickory St. are deferred. Project is left as is and the moratorium should be complete once project is executed. Elm was within last five years; Victoria was repaved in the last seven years but has wide gravel shoulders; and Hickory St. was in the last ten years. | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30428 | Main St - Ganonoque - Eastern - 1737 | 2031 | 2570187.9693 | Main St. - Gananoque - Eastern - 1737 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30429 | Manse Alley-Ganonoque-1466 | 2032 | 5083071.3341 | Manse Alley - Ganonoque - 1466 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Stone Street was done approximately 10 years ago. | Completed | Fail | NPS 2, cannot downsize or retire
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30430 | Mcgill St-Trenton-1596 | 2032 | 2547243.1686 | McGill St. - Trenton - 1596 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Dufferin St. was redone in last 10 years. | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30432 | North Alley-Ganonoque-1468 | 2032 | 2476197.0848 | North Alley - Gananoque - 1468 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Nothing within 10 years. | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30436 | Victoria Ave-Ganonoque-1457 | 2030 | 3391369.6395 | Victoria Ave. - Ganonoque - 1457 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 30470 | King St W - Eastern - 1799 | 2027 | 2079659.2864 | King St. W. - Eastern - 1799 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Eastern | Div_22 - Kingston | Distribution Pipe | Pass |  | 48487 | KING: Anodes* | 2020 | 2703904.5631 | General: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within EGI's system. These installations and replacements are based on the internal Standard Operating Practice established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
Eastern | Div_22 - Kingston | Distribution Stations | Fail | Dollar threshold | 49888 | KING: Ingredion Cardinal (18800003) Rebuild | 2024 | 865092.3457
Eastern | Div_22 - Kingston | Distribution Stations | Fail | Dollar threshold | 100777 | KING - Under rated valve Trenton TBS 27601001 | 2027 | 305303.4504
Eastern | Div_22 - Kingston | Distribution Stations | Fail | Dollar threshold | 100835 | KING: Belleville Sidney St TBS (27801001) Valve Upgrades | 2026 | 319289.5706
Eastern | Div_22 - Kingston | Distribution Stations | Fail | Dollar threshold | 100907 | King - corrosion Diamond Head Park PRS 27301037 | 2023 | 87187.1202
Eastern | Div_22 - Kingston | Distribution Stations | Fail | Dollar threshold | 101198 | KING: 22-22-704 College and Sidney DRS (27801009) Rebuild | 2024 | 1325309.4835
Eastern | Div_22 - Kingston | Distribution Stations | Fail | Dollar threshold | 503270 | Eastern PFM Compliance Program* |  | 359005.1339
Eastern | Div_22 - Kingston | Distribution Stations | Pass |  | 101199 | KING - Cornwall East TBS rebuild | 2024 | 1870089.9479 | Issue/Concern: With the decline in much of the area's industrial load (i.e., Domtar, Cortaulds, Celanese, and ICI Chemicals), it has been extremely difficult to balance the two stations since they tend to overtake each other. This has resulted in control issues with pressure regulation, measurement and odourization issues and concerns. A redesign is required to mitigate the concerns. | Completed | Fail | Distribution station condition related, IRPA not applicable
Eastern | Div_22 - Kingston | Growth | Pass |  | 30507 | SRP_LUG East_Kingston_28401002STN & Reinforcement_NPS12_1000m_1210kPa | 2024 | 6217386.699 | Station upgrades and relocation is required for additional capacity. | Completed | Pass | CNG, ETEE - Potentially could reduce or defer project scope.
Eastern | Div_22 - Kingston | Growth | Pass |  | 30508 | SRP_LUG East_Barriefield_28403028STN_Rebuild | 2028 | 77065.8506 | Station upgrades are required for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30509 | SRP_LUG East_Barriefield_28403029STN_Rebuild | 2023 | 186829.5433 | Higher maximum sustainable pressure is required. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30510 | SRP_LUG East_Belleville_27802132STN_Rebuild | 2024 | 128161.7777 | Upgrades to existing station or a new station is needed for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30512 | SRP_LUG East_Colborne_27401005STN_Rebuild | 2025 | 258290.0925 | Station upgrades are required for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30513 | SRP_LUG East_Customer_29401011STN_Rebuild | 2023 | 373659.0865 | Station upgrades are required for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30514 | SRP_LUG East_Customer_29401037STN_Rebuild | 2023 | 69749.746 | Station upgrades are required for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30515 | SRP_LUG East_Deseronto_28103002STN_Rebuild | 2023 | 186829.5433 | Station upgrades are required for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30517 | SRP_LUG East_Grafton_27405001STN_Rebuild | 2027 | 346935.6836 | Station upgrades are required for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30518 | SRP_LUG East_Picton_28103006STN_Rebuild | 2024 | 3011802.9299 | Station upgrades are required for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30519 | SRP_LUG East_Tweed_27805090STN_Rebuild | 2026 | 260644.5996 | Station upgrades are required for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30520 | SRP_LUG East_Winchester_29301001STN_Rebuild | 2030 | 4810147.7468 | Station upgrades are required for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30521 | SRP_LUG East_Winchester_29301008STN_Rebuild | 2024 | 71770.6755 | Station upgrades are required for additional capacity. | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 30522 | SRP_LUG East_Winchester_Main St_Reinforcement_NPS4_550m_1724kPa | 2028 | 619278.7141 | A 4-inch looping from outlet of Winchester TBS is required. | Completed | Pass | CNG, ETEE - CNG potentially could reduce or defer project scope, ETEE potentially could eliminate, reduce or defer project scope.
Eastern | Div_22 - Kingston | Growth | Pass |  | 48471 | KING: 22-21-001 Company Program - New Business - Scattered Mains - Contractor* | 2020 | 27108230.6023 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Eastern | Div_22 - Kingston | Growth | Pass |  | 48497 | King - 22-20-709 McConnell Ave & Tollgate Rd PRS | 2024 | 352445.0297 | Issue/Concern/Opportunity: System Reinforcement is required; the existing Post Regulation Station (PRS) is undersized. Growth requires a rebuild but a relocate should be considered at the same time as this intersection will be getting widened soon. The existing station will eventually end up in a turning lane. Asset: not available Related Program: N/A | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 100703 | SRP_LUG East_Kingston_Creekford Rd_Reinforcement_NPS8_6200m_6895kPa | 2024 | 28702885.9164 | Issue/Concern/Opportunity: Kingston lateral replacement to be completed from Westbrook CMS to Woodbine TBS to account for forecast growth, and to address Class Location and depth of cover issues which exist on the current Kingston lateral. Assets: Kingston Lateral Replacement Related Program: N/A | Completed | Pass | CNG, ETEE - Potentially could reduce or defer project scope.
Eastern | Div_22 - Kingston | Growth | Pass |  | 100778 | King - Chesterville, Customer, Finch Reinforcement | 2023 | 311382.5721 | Issue/Concern/ Opportunity: The Chesterville, Finch and Customer System is primarily fed from the Winchester TBS 29301001. The pipeline run is approx. 40KM and services residential houses and commercial scale farms that have installed or are currently looking to install crop dryers. This reinforcement is required to add additional capacity to the system and maintain healthy system pressures. This area has seen significant agricultural growth which has resulted in the system falling below minimum pressures. There have been a couple low pressure calls from the customers at the end of the system. Distribution Optimization Engineering have halted future main extensions and commercial attachments. If this reinforcement is not done, we would be unable to attach future customers. Asset: 40KM of NPS 4 Steel pipe Related programs: N/A | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 102520 | King: 22-25-504 Tweed Reinforcement - McClellan and Pomeroy | 2025 | 284119.0449 | Issue/Concern/Opportunity: The southern end of the tweed system went below minimum pressure in 2020. Reinforcement is required to boost the pressures based on predicted growth as per Distribution Optimization Engineering. Assets : Connect 2-inch PE mains on McClellan ST and Pomeroy Ave. FID 517313684 ~150 m Related Program: N/A | In Progress
Eastern | Div_22 - Kingston | Growth | Pass |  | 500423 | KING: Company Program - Customer Connections* |  | 68257532.7837 | Kingston Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Eastern | Div_22 - Kingston | Growth | Pass |  | 501482 | SRP_LUG East_Odessa_28405001STN_Rebuild | 2023 | 574064.9099 | Issue/Concern/Opportunity: Full rebuild is required as station becomes under capacity during fall peaking with the addition of new customer. The customer cannot come online unless station is rebuilt. Station is also aging and there are concerns regarding its integrity. Assets: Odessa TBS (28405001) Related Program: N/A | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 734081 | King: 22-22-507 Second Street East - Tie NPS4 1210kPa Main Together | 2025 | 187260.2796 | Issue/Concern/Opportunity: SRPR Z13 2022_002 - Identified by Distribution Optimization Engineering (DOE) in June 2021. Two sections of NPS4 1,210 kPa main on Second Street at approximately #3306 are not tied together; both ends are capped off. A records research of Union and Centra Gas confirms that this section of main was broken in 1981 when linestoppers were installed and caps were welded on. Asset: Two sections of NPS4 1,210 kPa main on Second Street at approximately #330 Related Program: N/A | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Eastern | Div_22 - Kingston | Growth | Pass |  | 734705 | King: Madoc Lateral MOP Upgrade (Belleville North) | 2030 | 2354398.547 | Issue/Concern/Opportunity: Complete a Maximum Operating Pressure (MOP) upgrade on the Madoc Lateral and mitigate service line clearance and Property Line Post Regulator Sets (PLPRS) issues. Assets: Madoc Lateral Related Program: N/A | Planned
Eastern | Div_22 - Kingston | Growth | Pass |  | 736264 | King: 22-25-508Brighton Reinforcement - Main Street | 2025 | 379858.2391 | Issue/Concern/Opportunity: Looping upgrades to account for connection of 291 Main St. and for future residential/commercial growth to the west. Asset: 300M NPS 4 Pipe Related Program: Additional reinforcements as part of 733975. | Planned
Eastern | Div_22 - Kingston | Utilization | Pass |  | 48483 | KING: Meter & Regulator Inst Repl-Company* | 2020 | 18660612.7122 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
GTA East | 30 - Richmond Hill | Distribution Pipe | Fail | Dollar threshold | 4662 | Replacement Blanket - Area 30 |  | 596000.8659
GTA East | 30 - Richmond Hill | Distribution Pipe | Fail | Dollar threshold | 30176 | Yonge St 2 - GTA East - Area 30 - 1707 | 2028 | 1618990.0017
GTA East | 30 - Richmond Hill | Distribution Pipe | Fail | Dollar threshold | 103419 | 30: VSM - Major Mackenzie, Sussex To Newkirk, Replacement | 2023 | 1541430.6729
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 4668 | Anode Blanket - Area 30* | 2020 | 1672025.4736 | General Description: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within the EGI system. These installations and replacements are based on the Corrosion Operating Standard established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 4764 | AMP Fitting Replacement - Area 30* | 2020 | 48281159.3202 | AMP Fittings are a below grade transition fittings. The inserted portion of copper tubing can fail due to internal corrosion. In these cases leaks develop immediately downstream of the AMP Fitting. | Completed | Fail | See investment description, IRPAs not applicable
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 7666 | VSM - Major Mackenzie and Yonge | 2024 | 1799053.1052 | Replacement of 287 m of NPS 6 steel main on Major Mackenzie from Newkirk Rd. to Cedar Ave. including the CN crossing. | Completed | Fail | N/A - Investment Cancelled
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 13606 | Service Relay Blanket - Area 30* | 2020 | 19997215.1765 | General: A distribution service refers to the pipe between the distribution main and the customer’s meter set. Over the years, different materials have been used for this asset, including steel, copper, and varying resins of plastic, each with unique characteristics that contribute to their performance over time. Services can be repaired or replaced depending on asset condition and the nature of the issue exhibited. Generally, replacement is the preferred approach to mitigate unacceptable asset condition. | Completed | Fail | See investment description, IRPAs not applicable
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30162 | Ashlar Rd - GTA East - Area 30 - 1489 | 2028 | 2016259.978 | Ashlar Rd. - GTA East - Area 30 - 1489 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30163 | Axminster Dr - GTA East - Area 30 - 1490 | 2030 | 2918112.0221 | Axminster Dr. - GTA East - Area 30 - 1490 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30164 | Church St South_2 - GTA East - Area 30 - 1382 | 2032 | 7646910.596 | Church St. South 2 - GTA East - Area 30 - 1382 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30166 | Dunning Ave - GTA East - Area 30 - 1710 | 2032 | 2378506.066 | Dunning Ave. - GTA East - Area 30 - 1710 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30167 | Elgin Mills Rd E - GTA East - Area 30 - 1351 | 2030 | 7895978.945 | Elgin Mills Rd. E. - GTA East - Area 30 - 1351 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30168 | Paliser Cres S - GTA East - Area 30 - 1389 | 2029 | 3486582.0718 | Paliser Cres. S. - GTA East - Area 30 - 1389 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30169 | Ruggles Ave - GTA East - Area 30 - 1706 | 2027 | 3071774.3496 | Ruggles Ave. - GTA East - Area 30 - 1706 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: This was updated based on regional feedback (Ruggles Ave. - 1706). | Completed | Fail | NPS 2, cannot downsize or retire
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30170 | Rupert Ave - GTA East - Area 30 - 1815 | 2031 | 4627706.0894 | Rupert Ave. - GTA East - Area 30 - 1815 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30172 | Taylor Mills Dr S - GTA East - Area 30 - 1435 | 2031 | 4470636.5152 | Taylor Mills Dr. S. - GTA East - Area 30 - 1435 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30173 | Tecumseth St - GTA East - Area 30 - 1362 | 2032 | 4945270.4528 | Tecumseth St. - GTA East - Area 30 - 1362 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30174 | Wellington St - GTA East - Area 30 - 1417 | 2031 | 4327256.4461 | Wellington St. - GTA East - Area 30 - 1417 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 30175 | Yonge St - GTA East - Area 30 - 1358 | 2029 | 4149594.3366 | Yonge St. - GTA East - Area 30 - 1358 Vintage steel exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 102421 | Relocation Program - Area 30* | 2020 | 18602801.2793 | General: Projects in the relocation category are capital expenditures required to replace or relocate segments of pipeline in order to accommodate municipal infrastructure work. The cost sharing for this work is managed through the Franchise Agreements established with municipalities. A consultative approach is used between the municipality and EGI to avoid conflicts with municipal infrastructure early in the planning stage. If a conflict is unavoidable, pipeline assets are typically relocated or replaced. | Completed | Fail | See investment description, IRPAs not applicable
GTA East | 30 - Richmond Hill | Distribution Pipe | Pass |  | 103420 | 30: VSM - Major Mackenzie, Cedar to Newkirk, Replacement | 2026 | 2514079.0091 | Issue/Concern/Opportunity: Replace 40 m NPS 12 SC IP gas main, 645 m of NPS 6 SC IP gas main, 40 m of NPS 4 SC IP gas main, 100 m of NPS 2 SC IP, 40 m NPS 1.25 SC IP gas main, one district station (#8442841) and approximately 55 service relays. Justification: Richmond Hill Replacement Project Assets: Related Investments: | Planned
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 18911 | COUNTY RD #55 HWY #9 DISTRICT ( NEW TECUSETH ) | 2023 | 144018.2711
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 23730 | LESLIE & STEELES DISTRICT | 2026 | 283358.4003
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 101056 | 31428A - RAM FOREST & WESLEY CORNERS | 2023 | 305493.3023
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 101057 | 32311A - WILLIAM & PRESTON LAKE DISTRICT | 2023 | 305493.3023
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 101058 | 32717A - WESTON RD & KING RD DISTRICT | 2023 | 305493.3023
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 501533 | Beaverton District Station | 2025 | 129173.4878
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 733506 | Buttonville Interconnect | 2029 | 136971.5835
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 735169 | 33534A STEELES & BAYVIEW DISTRICT | 2023 | 238783.5404
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 735170 | 33171A - MAJOR MACKENZIE & VELLORE WOODS DISTRICT (VAUGHAN) | 2023 | 90401.0793
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 735172 | 30988A CONCESSION 2 & TWMARC DISTRICT | 2023 | 321079.6953
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 735173 | 32564A - MILL ST & KING SIDEROAD DISTRICT | 2023 | 319334.0193
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 735300 | 31335A GILBERT& YONGE DISTRIUCT (AURO | 2024 | 208223.739
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 735301 | 33300A ISLINGTON & HWY # 407 HP DIST | 2024 | 432464.6888
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 735302 | 33525A Bathurst & Rutherford hp-ip | 2024 | 219435.7865
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 735303 | 35053A Dufferin Langstaff (langstaff & 407) | 2024 | 221037.5076
GTA East | 30 - Richmond Hill | Distribution Stations | Fail | Dollar threshold | 735309 | 50356A COUNTY RD #55 HWY #9 DISTRICT ( NEW TECUSETH ) | 2023 | 144641.7268
GTA East | 30 - Richmond Hill | Distribution Stations | Pass |  | 1011 | SCHOMBERG GATE | 2024 | 4175220.6241 | Schomberg Gate Station is located on EGI-owned property of approximately 1,250 m2 fenced compound in the Township of King, Ontario, approximately 3 km from the town of Pottageville, within a rural/urban area, in close proximity to Kettleby. This station accepts natural gas from TC Energy and provides supply to two separate XHP networks, through components within the Measurement system, Pressure Control system, Heating system, Odourant system, and Telemetry system. This station supplies natural gas to approximately 23,501 customers in the King Region. The following issues have been identified at this station: Compliance: An engineering assessment of the site layout has identified a conflict with the location of the Telemetry or Boiler buildings with respect to the Electrical Safety Authority (ESA) Area Classification requirements which has identified that an ignition source is in close proximity to a potential leak source, as defined within the Electrical Codes and Standards. Measurement: The current system does not provide measurement of the individual outlet supplies. Visibility to each outlet supply provides greater redundancy to the existing measurement and improved response capabilities. Valve & Piping: The existing valves at this site have experienced issues in performance and operation of the valves. Maintenance has been performed to attempt to remediate the valves; however, the valves have deteriorated to the point where the reliability is no longer acceptable. Heating: The existing boilers at this site have experienced trouble call/failures over the recent years, including failures of the motors and pumps, burner lock-outs and exchanger failures. Due to recent and upcoming customer growth in the King area, the existing heating system will not be capable of supplying the heating requirements to meet the demand. Pressure Control: The Regulation system is undersized and not capable of supplying the demand required to meet the customer growth in the King area. The configuration of the existing regulators is double boot, posing an undesired higher risk and high associated ongoing maintenance costs. Telemetry & Electrical: The existing electrical system does not meet current EGI electrical installation standards. This poses a potential electrical hazard and faulty wiring may result in lost communications. Additional Scope: Replacement of 24 m NPS 6 road crossing NW 2103 is required in order to ensure the pipeline does not exceed the required %SMYS to be designated an Integrity Management Program (IMP) main and require retrofit and inspection. The deadline or this replacement is June 11, 2024. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 30 - Richmond Hill | Distribution Stations | Pass |  | 1013 | MARKHAM GATE | 2027 | 6498237.9721 | Markham Gate Station Pipe, Valves & Others: Updated Mechanical Piping is required for this station. The existing valves at this site have experienced issues in performance and operation of the valves. Maintenance has been performed to attempt to remediate the valves, however, the valves have deteriorated to the point where the reliability is no longer acceptable Heating System: Updated heating is required at this station. New Heat Exchanger is required including the associated piping for the glycol inlet and outlet to heating element. New boiler building will be procured as the existing building is within the ESA classification. Pressure Control: Not Required Odorant System: New Odorant system is required. This would include a new Odorant building including tank (Assume 500G – Enbridge standard). New Odorant cabinet including 2 new pumps and associated tubing from the tank equipment to cabinet. New sight glass for injection point is required. New odorant building to be outfitting with new electrical distribution and internal/external lighting. Galvanized building stairs to be accounted for. Telemetry/Electrical: New Control Wave Micro unit required and associated connections. Account for 1 new pressure transmitter and 1 new temperature transmitter. The telemetry and electrical systems do not meet current EGI standards, do not contain backup power supply in the event of power loss, and are approaching end of useful life. The existing RTU is obsolete and is required to be upgraded to current standards along with new communications equipment in order to eliminate cyber security threats. New Telemetry building will be required to be installed in new compliance location. Measurement: No information provided. Building: New Odorant Building required (See Odorant Scope for details). Additionally, new boiler building will need to be procured. An engineering assessment of the site layout has identified a conflict with the location of the telemetry or boiler Buildings with respect to the ESA Area Classification Compliance/Civil: Minor Site Grading will be required and new crash bar access and 2 sides of site. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 30 - Richmond Hill | Distribution Stations | Pass |  | 1148 | BATHURST GATE | 2025 | 4125265.1909 | The regulators are heavy and maintenance is difficult in the current arrangement, a lifting device is needed for ergonomic reasons. The current heating system consists of condensing boilers that have condensate which will reguire mitigation. A conversion to noncondensing boilers is required and during the conversion three-way valves and associated piping (6,000 by Stations Ops) will be added. The front gate experiences flooding and teh grade by the gate needs to be raised because water pools at the main gate. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 30 - Richmond Hill | Distribution Stations | Pass |  | 3614 | BOND HEAD GATE | 2026 | 6906782.6125 | Bond Head Gate Station is located on EGI-owned property of approximately 1,900 m2 fenced compound in the village of Bond Head, Ontario, approximately 8.5 km west of Bradford Ontario, within a rural area, in close proximity to several homes. This station accepts natural gas from TC Energy and provides supply to two separate XHP networks and one IP network, through components within the measurement system, pressure control system, heating system, odourant system, and telemetry system. This station supplies natural gas to approximately 60,000 customers in the Alliston, Orangeville, Bradford, and northern York Region. The following issues have been identified at this station: Compliance: An engineering assessment of the site layout has identified a conflict with the location of the Telemetry or Boiler buildings with respect to the Electrical Safety Authority (ESA) Area Classification requirements which has identified that an ignition source is in close proximity to a potential leak source, as defined within the Electrical Codes and Standards. Valves & Piping: The existing valves at this site have experienced issues in performance and operation of the valves. Maintenance has been performed to attempt to remediate the valves; however, the valves have deteriorated to the point where the reliability is no longer acceptable. Measurement: The current Turbine meter does not provide measurement of the individual outlet supplies. Visibility to each outlet supply provides greater redundancy to the existing measurement and improved response capabilities. As well, failures have been experienced over the past year including complete meter failure and jamming. Station has a backup orifice plate meter, which has experienced several alarms. Heating: The existing boilers at this site are approaching 20 years old, they have had 10 trouble call/failures over the recent years, including failures of the motors and pumps, burner lock-outs and exchanger failures. Due to recent and upcoming customer growth in the Bradford/York Region area, the existing heating system will not be capable of supplying the heating requirements to meet the demand. Pressure Control: The regulation system is undersized and not capable of supplying the demand required to meet the customer growth in the Bradford/York Region area. The configuration of the existing regulators are double boot, posing an undesired higher risk and high associated ongoing maintenance costs. Odourization: The odourant system was installed in 2003. The current configuration of the odourant system does not ensure adequate containment of the odourant product in the event of a leak and does not meet the current engineering standards and approvals. Telemetry & Electrical: The existing electrical system does not meet current EGI electrical installation standards, the existing Telemetry building is in poor condition beyond repair. This poses a potential electrical hazard and faulty wiring may result in lost communications. The existing generator and backup supply systems have reached end of life. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 30 - Richmond Hill | Distribution Stations | Pass |  | 3624 | VICTORIA SQUARE GATE | 2024 | 1737071.5741 | Pipe, Valves and Others: Current actuators on the inlet, outlet and heat exchanger valves need to be commissioned and programmed for remote control by Gas Control in the Remoter Terminal Unit (RTU). The RTU will have to be upgraded to accommodate the additional input/output (I/O) as its current capacity is full. NPS 8 Becker control valve was replaced in 2016. Fuel gas supply and meter set will be required to replace outdated station. Measurement: The existing Measurement system is scheduled for upgrade in 2019 and it is expected that this work will be sufficient for operation in 2024. No upgrade to the Measurement system is included in this business case. Heating System: Existing Heating system is not in compliance with the Area Classification and will require boiler building relocation. The boilers have recently been replaced and should continue to operate. The boiler building is location in a classified area and will have to be moved and/or remediated. Exhaust fans may resolve the issue but this will be determined in detailed engineering. Heat exchangers were recently inspected (2015/2016) and will not require replacement. Pressure Control: Low flow regulator run was added in 2017. No additional work is required on the regulation runs. Odourant: Install a new Odourant building as the current metallic odourant building is without adequate containment. This building rusts, leaks in rain and spill response is hampered due to difficulty wrapping the building. The tank has bottom connections to feed the injection pumps. Odourant pumps are also in a different building and will be located appropriately in the same building as the 3,500 gallon odourant tank. This tank will have to be upsized. Telemetry/Electrical: RTU replacement is required from an old Bristol 3330 to a new control wave RTU. RTU upgrade is required as the current design has no available expansion capacity to accommodate new actuator, measurement inputs, additional methane and CO sensing. This will require a new RTU building. Electrical Safety Authority (ESA) compliance Issues will be resolved by relocating electrical equipment. Upgrades to station wiring will be required to allow for new instrumentation. The electrical service will be upgraded to accommodate the new station loads. A new station grounding network, updated anti-climb tower, and updated instrumentation will be installed to meet current standards. A generator (installed 1999) and UPS system will be installed for backup power requirements in the event of a power outage. A new modem and firewall, improved station lighting, odourant tank instruments, and a weather station will be installed to meet current standards. Electrical upgrades are required. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 30 - Richmond Hill | Distribution Stations | Pass |  | 7753 | NOBLETON GATE | 2026 | 4302067.5642 | Issue/Concern: Nobleton Gate Station is located on a fenced, EGI-owned property of approximately 1,000 m2 in the City of Vaughan, Ontario, approximately 3 km from the Town of Nobleton, within a rural area. This station accepts natural gas from TC Energy and provides supply to an XHP network, with a Measurement system, Pressure Control system, Heating system, Odourant system, and a Telemetry and Controls system. This station supplies natural gas to approximately 1,800 customers in the Bolton and King City areas. The following issues have been identified at this station: Compliance: An engineering assessment of the site layout has identified a conflict with the location of the Telemetry and Boiler buildings with respect to the Electrical Safety Authority (ESA) area classification requirements, which have identified that an ignition source is in close proximity to a potential leak source, as defined within the Electrical Codes and Standards. Additional property will be required to remediate the area classification issue. Measurement: Gas measurement is completed using a turbine meter installed in 2004. This meter type has experienced failures causing potential downstream impacts and loss of service to customers. This meter has experienced six failures in the past two years, due to leaks and faulty measurement. A new mass flow meter will be installed to replace the turbine meter and a backup outlet Annubar meter will also be installed. Heating: The existing boilers at this site are 14 years old. They have had three trouble call/failures over the past year including failures of the motors and pumps, burner lock-outs and exchanger failures. The boilers, building, and glycol piping require replacement as they will be 20 years old by the target rebuild date. The heat exchanger is not expected to be replaced but inspection is to be included. Pressure Control: The regulators are the original regulators installed when the station was first commissioned. In 2001, a building was installed over them to improve maintenance and operation. The regulators have experienced 29 trouble calls/failures in the time period including leaks, boot failures, and pilot failures. Both monitor and operator runs are boot-style regulators, which poses an undesired higher risk and high associated ongoing maintenance costs. Odourization: The odourant system was installed in 2004 with the injection system installed in 2009. The current configuration of the odourant system does not ensure adequate containment of the odourant product in the event of a leak and does not meet the current engineering standards and approvals. The panel will have to be relocated into a new building with a larger new tank. Upgrade of odourant system (condition of containment and unsafe grating in the building for access) is to be included in refreshed scope – 500 GAL odourant system. A new Odourant building is required including new concrete foundation. Building is to be equipped with all electrical requirements. Building is to be equipped with new steel platform for Operations and Maintenance (O&M) activities including delivery. New sight, glass radar gauge equipment must be provided. Scope is to account for decommissioning and commissioning of the new odourant system. Telemetry and Electrical: The existing Electrical system does not meet current EGI electrical installation standards and there are area classification issues that need be resolved. The wiring poses a potential electrical hazard and faulty wiring may result in lost communications. Pipe, Valves & Others: Station inlet filtration (gas separator) is required under the Station's Engineering specification. Inlet piping configuration will need to be redesigned for filter and bypass. Other: Programming as required. Compliance/Civil: Site grading will be required as well as new security fencing (galvanized) including new swing gate and crash bar access. Pipe and concrete building foundation is to be accounted for under civil activities. Asset: Nobleton Gate Station assets. Related Program: Not applicable. In 2021, there was a request by Stations Engineering to replace the existing regulator spools for STN# 30460A. This will be replaced with NPS 2 EZR including spool and fabrication along with Non-Destructive Examination (NDE) and coating. Additionally, there is a hazardous tree that is leaning against the fence causing damage that will need to be removed. The station does not need to be shut down in order to complete this regulator spool replacement activity. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 30 - Richmond Hill | Distribution Stations | Pass |  | 7769 | KEELE AND STEELES/CNR FEEDER | 2025 | 2321252.7421 | Keele and Steeles/CNR Feeder Station is located on 3,000 m2 compound in the city of Vaughan, Ontario, approximately 1.5 km from York University, within an urban area in close proximity to CNR Railway Corridor. This station accepts natural gas from EGI XHP pipeline and provides supply to three separate XHP networks and an HP network, through components within the Pressure Control system, Heating system, Odourant system, and Telemetry system. This station supplies natural gas to approximately 20,000 customers in Vaughan and Toronto area. The following issues have been identified at this station: Valve & Piping: the existing valves at this site have experienced 10 failures and leak issues in performance and operation of the valves. Maintenance has been performed to attempt to remediate the valves; however, the valves have deteriorated to the point where the reliability is no longer acceptable. Pressure Control: The configuration of the existing regulators was installed in 1990 and is double boot, posing an undesired higher risk and high associated ongoing maintenance costs. The existing regulators have reached end of life. Telemetry & Electrical: The Telemetry and Electrical systems do not meet current EGI standards, do not contain backup power supply in the event of power loss, and are approaching end of useful life. The existing Remote Terminal Unit (RTU) is obsolete and is required to be upgraded to current standards along with new communications equipment in order to eliminate cybersecurity threats. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 30 - Richmond Hill | Distribution Stations | Pass |  | 7778 | WOODBINE & CNR FEEDER | 2024 | 2134241.1262 | Pipe, Valves & Others: Not required. Heating System: Not required. Pressure Control: Not required. Odourant System: A new Odourant system is required. This would include a new Odourant building including tank (assume 500 G – EGI standard). A new Odourant cabinet including two new pumps and associated tubing from the tank equipment to cabinet is required. A new sight glass for injection point is required. New Odourant building is to be outfitted with new electrical distribution and internal/external lighting. Galvanized building stairs are to be accounted for. Telemetry/Electrical: New Control Wave Micro unit and associated connections are required. One new pressure transmitter and one new temperature transmitter are to be accounted for. The Telemetry and Electrical systems do not meet current EGI standards, do not contain backup power supply in the event of power loss, and are approaching end of useful life. The existing Remote Terminal Unit (RTU) is obsolete and is required to be upgraded to current standards along with new communications equipment in order to eliminate cybersecurity threats. Measurement: Not required. Building: New Odourant building is required Compliance/Civil: Minor site grading, new crash bar access and two sides of site will be required. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 30 - Richmond Hill | Distribution Stations | Pass |  | 8567 | St John Sideroad Feeder Station | 2023 | 7020635.0997 | Issue/Concern: The property on which St. John’s Sideroad Feeder Station currently sits is insufficient for operation. It is located adjacent to a residential property and the area classification extends onto the adjacent private property. The Boiler building is located in a hazardous area classification and the non-compliance needs to be remedied. Road widening of St. John’s Sideroad currently has the sidewalk encroaching on our station. A land sale agreement with York Region was completed in 2016 and requires movement of the electrical meter. As the area classification issue risks shutdown of the station by the Electrical Safety Authority, EGI is planning to resolve the movement of the electrical meter (on site) pending a new land purchase for relocation of the entire station. As a result of station relocation, a complete rebuild will be required. Maintenance on the Boiler system piping, pumps and gauges, which are old and obsolete, suggest that the Heating system needs to be replaced regardless of station relocation. The Heating system is already undersized for the current demand. The FL regulators are difficult to work on due to their weight and ergonomic restrictions in a cramped building. These are to be replaced and upgraded. The old Remote Terminal Unit (RTU) 3330 Telemetry system needs to be upgraded, including the backup power generator which is old and obsolete. The station was updated in 2006 and a new generator and boilers were installed in 2003. Source records do not indicate any regulator capacity issue. Asset: Stn ID: 2944180 Related Programs: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 30 - Richmond Hill | Growth | Pass |  | 3736 | Area 30 - Industrial - New Construction* |  | 694952.467 | Industrial New Construction- A customer intending to run an industrial manufacturing business in a newly-built facility and intending to use natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGD develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long term plans EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. Enbridge reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers; and, - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing Assets: Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA East | 30 - Richmond Hill | Growth | Pass |  | 2522 | Rodinea Road | 2023 | 589363.9135 | Issue/Concern/Opportunity: The HP network system needs reinforcement through this proposed piping connection. This project is to address system capacity loss due to a previous transit-related main abandonment in Area 10. Assets: install 223m of 8" steel HP gas main to connect mains at the east and the west side. HDD under the railroad. Related Program: N/A | Planned
GTA East | 30 - Richmond Hill | Growth | Pass |  | 3731 | Area 30 - Apartment Ensuite - New Construction* |  | 4136135.1393 | Issue/Concern: Vertical Subdivision refers to a multiple unit residential building where each suite is individually metered. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA East | 30 - Richmond Hill | Growth | Pass |  | 3735 | Area 30 - Commercial - New Construction* |  | 46840811.6786 | Issue/Concern: Commercial New Construction refers to a customer intending to run a commercial business in a newly-constructed building and intending to using natural gas to meet energy needs. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA East | 30 - Richmond Hill | Growth | Pass |  | 3738 | Area 30 - Residential - New Construction* |  | 77074340.3177 | Issue/Concern: Residential New Construction refers to a new residential construction development of detached single homes constructed by the builder for domestic purposes. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA East | 30 - Richmond Hill | Growth | Pass |  | 3739 | Area 30 - Residential - Replacement* |  | 42584538.3498 | Issue/Concern: Residential Replacement refers to a residential replacement customer using a fuel other than natural gas for domestic purposes and is converting to natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA East | 30 - Richmond Hill | Growth | Pass |  | 736389 | A30: Interchange Way Reinf | 2023 | 640984.462 | Issue/Concern/Opportunity: There is future growth in the area from addition of condo towers and some commercial work. Justification: Existing NPS 4 Steel (ST) High Pressure (HP) gas main will need to be upsized to NPS 12 ST HP to support future load on system. Assets: N/A Related Investments: N/A | Planned
GTA East | 30 - Richmond Hill | Growth | Pass |  | 736532 | NW 3723 Jane St. Reinforcement SRP | 2024 | 993022.7579 | Issue/Concern/Opportunity: Install 1,280 m of NPS 4 PE Intermediate Pressure (IP) along Jane St. from King Rd., tying into NPS 2 main at Westgate Blvd. System pressures were projected to fall below minimum system pressures in 2022. Station 3577117 will need to be upsized due to station drooping and reaching capacity. Assets: Pipe and district station Related Program: Not applicable | Planned
GTA East | 30 - Richmond Hill | Utilization | Pass |  | 13545 | MXGI Area 30* | 2019 | 51771808.9772 | Meters: Meters are used to determine the gas consumption input of customer billing. The replacement program for meters is mandated by Measurement Canada. The program includes: testing, repair, and replacement requirements of meters and instruments. All verified meters are approved by Measurement Canada with an issuance of a certificate which identifies that the meter complies with Electricity and Gas Specification S-EG-02. The Company must ensure all measurement devices remain in compliance for annual audits by Measurement Canada. Measurement Canada specifies tolerances under which the meter must operate in the field. The Company must demonstrate that all aspects of its meter sampling, maintenance, and replacement comply with these criteria in order to be accredited by Measurement Canada to be an “Authorized Service Provider” and adhere to Measurement Canada’s accreditation standard S-A-01. Meters may also require exchange for issues such as: damages, leaks, customer billing issues. Regulation: Regulators are the last line of defense for over-pressure to the customer. The condition of regulation systems is determined by regulator performance, corrosion of piping and regulators, and adherence to installation specifications. Failure of the regulation system can cause pressured gas to enter the premise, resulting in failure of gas equipment, loss of containment, and potentially fire or explosion. | Completed | Fail | See investment description, IRPAs not applicable
GTA East | 30 - Richmond Hill | Utilization | Pass |  | 503324 | LEG: AMI Pilot Project | 2023 | 1870367.1572 | AMI Pilot Project Purpose & Need The AMI initiative is a key piece required to successfully test AMI & AMR functionality The AMI pilot is a proof of concept that will ensure when a large scale program is launched the greatest benefits will be gained. The Markham piece of the pilot will include approximately 3500 customers, each customer will have a new ultrasonic meter installed The new meters increase efficiency, reduce costs, provide extra safety features, and give real time consumption data to help model the distribution network, provide DSM opportunities, and assist with maintenance scheduling Some of the benefits of the new advanced system: Two way communication , Real time consumption, Increased meter data – example: pressure sensors, methane detectors, and shut off capabilities Key components required for a successful pilot: Communications / Accuracy / Functionality / Reporting / Reliability / Safety / Cyber Security Timing The pilot project will be rolled out in 2022 The pilot project will operate in 2022 and 2023 Any barriers/issues will be solved during the operational period | Completed | Fail | See investment description, IRPAs not applicable
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 4663 | Replacement Blanket - Area 40 |  | 485846.1695
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 13607 | Service Relay Blanket - Area 40* | 2020 | 15804345.9492
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 14147 | Copper Service Replacement - Area 40* | 2020 | 846997.2997
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 30183 | Howard Ave 1 - Kawartha Lakes - Area 40 - 1692 | 2027 | 925866.0909
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 30184 | Howard Ave 2 - Kawartha Lakes - Area 40 - 1694 | 2031 | 1740885.9072
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 30189 | Prospect St-Bowmanville-1086 | 2030 | 1371367.9665
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 30190 | Regent St - Kawartha Lakes - Area 40 - 1697 | 2028 | 817508.7388
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 100470 | Bannerman Crt. and Nordic Crt, Whitby | 2023 | 910371.2879
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 102671 | Campbellford Replacement Phase 3 Front St | 2029 | 851260.786
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 102672 | Campbellford Replacement Phase 4 Kent St | 2023 | 1446589.342
GTA East | 40 - Whitby | Distribution Pipe | Fail | Dollar threshold | 102673 | Campbellford Replacement Phase 5 Pellissier St & Bridge St | 2028 | 1050158.29
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 4669 | Anode Blanket - Area 40* | 2020 | 1535938.0058 | General Description: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within the EGI system. These installations and replacements are based on the Corrosion Operating Standard established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 4766 | AMP Fitting Replacement - Area 40* | 2020 | 28398914.2847 | AMP Fittings are a below grade transition fittings. The inserted portion of copper tubing can fail due to internal corrosion. In these cases leaks develop immediately downstream of the AMP Fitting. | Completed | Fail | See investment description, IRPAs not applicable
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30178 | Caddy St-Peterborough-1179 | 2032 | 3960180.2581 | Caddy St. - Peterborough - 1179 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30179 | Christena Cres 1 - Ajax - Area 40 - 1702 | 2030 | 3285942.0909 | Christena Cres. 1 - Ajax - Area 40 - 1702 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Scope is to be broken up into two investments given the large scope and potential conservation concerns and close proximity to MTO right-of-way (ROW). Project will be adjusted based on regional comments (Christena Cres. 1 - 1702 and Christena Cres. 2 - 1704). | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30181 | Durham St W - Kawartha Lakes - Area 40 - 1687 | 2031 | 5109709.1153 | Durham St. W. - Kawartha Lakes - Area 40 - 1687 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30182 | Euclid Ave-Peterborough-1106 | 2030 | 4142299.8477 | Euclid Ave. - Peterborough - 1106 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30186 | Poplar Ave 1 - Ajax - Area 40 - 1680 | 2032 | 4731769.9359 | Poplar Ave. 1 - Ajax - Area 40 – 1680 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: This scope could be broken up into two projects given the conservation authority impacts - project adjusted based on region's comments (Poplar Ave 1 - 1680 and Poplar Ave 2 - 1681). | Planned
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30187 | Poplar Ave 2 - Ajax - Area 40 - 1681 | 2029 | 2371613.22 | Poplar Ave. 2 - Ajax - Area 40 - 1681 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: This scope could be broken up into two projects given the conservation authority impacts; project was adjusted based on region's comments (Poplar Ave. 1 - 1680 and Poplar Ave. 2 - 1681) | Completed | Fail | NPS 2, cannot downsize or retire
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30188 | Prince St-Bowmanville-1450 | 2029 | 2275534.6123 | Prince St. - Bowmanville - 1450 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30192 | Simcoe Street-40-Kawartha Lakes-1060 | 2028 | 3081604.6057 | Simcoe Street - 40 - Kawartha Lakes - 1060 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30193 | Tulloch Dr-Ajax-1594 | 2031 | 4233089.3684 | Tulloch Dr. - Ajax - 1594 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30194 | Wellington St - Kawartha Lakes - Area 40 - 1678 | 2032 | 4398635.5155 | Wellington St. - Kawartha Lakes - Area 40 - 1678 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 30196 | Windsor Dr-Ajax-1193 | 2027 | 2191889.326 | Windsor Dr. - Ajax - 1193 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 100517 | Oshawa LP Replacement Phase 1 Olive Ave | 2024 | 4209857.8945 | Issue/Concern/Opportunity: Overall goal is to eventually replace the Oshawa Low Pressure network, reducing the risk of an overpressure on a system with no additional overpressure protection downstream of the district stations. Justification: This phase will follow Phase 1a (Olive Ave. replacement in 2020), and will allow for the abandonment of one of the low-pressure district stations with external sense lines. Assets: Replace approximately 3,000 m of PE and steel low-pressure main, and relay or reconnect approximately 400 services, including installation of regulators at the meter sets. Related Investments: Not applicable. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 101277 | Replacement - Vintage PE Lined Mains - Peterborough | 2023 | 2723456.5806 | Issue/Concern/Opportunity: This is a planned replacement of approximately 320 m of vintage PE pipe (1974) lined in old cast iron mains, installed in back laneways on Elias Ave., Maitland Ave., Pearl Ave., and Boswell Ave. in Peterborough. Justification: Vintage PE mains are reaching their life expectancy. Mains are cased in cast iron, making leaks difficult to pinpoint. Assets: There are 1974 NPS 1 1/4 PE mains (approximately 320 m) to be replaced with new NPS 2 PE mains (approximately 960 m if dual main) and there are approximately 60 service relays. Related Investments: Not applicable. | Completed | Fail | NPS 2, cannot downsize or retire
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 102422 | Relocation Program - Area 40* | 2020 | 42520688.5233 | General: Projects in the relocation category are capital expenditures required to replace or relocate segments of pipeline in order to accommodate municipal infrastructure work. The cost sharing for this work is managed through the Franchise Agreements established with municipalities. A consultative approach is used between the municipality and EGI to avoid conflicts with municipal infrastructure early in the planning stage. If a conflict is unavoidable, pipeline assets are typically relocated or replaced. | Completed | Fail | See investment description, IRPAs not applicable
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 103427 | Oshawa LP Replacement Phase 2 King St | 2026 | 5166298.6309 | Issue/Concern/Opportunity: Overall goal is to eventually replace the Oshawa Low Pressure network, reducing the risk of an overpressure on a system with no additional overpressure protection downstream of the district stations. It consists of Vintage steel main. Justification: This phase will follow Phase 1 - Olive Ave. Replacement in 2021 is timed with municipal work; it will allow for the abandonment of one of the low-pressure district stations with external sense lines. Assets: Replace approximately 7,600 m of PE and ST low-pressure main. Relay or reconnect approximately 300 services, including installation of regulators at the meter sets. Related Investments: Not applicable. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 103429 | Oshawa LP Replacement Phase 3 Masson St | 2026 | 8767138.2704 | Issue/Concern/Opportunity: Overall goal is to eventually replace the Oshawa Low Pressure network, reducing the risk of an overpressure on a system with no additional overpressure protection downstream of the district stations. Justification: This phase will follow Phase 2 King St. Replacement in 2024 and will allow for the abandonment of one of the low-pressure district stations with external sense lines. Assets: Replace approximately 8,064 m of PE and steel low-pressure main. Relay or reconnect approximately 748 services, including installation of regulators at the meter sets. Related Investments: Not applicable. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 735948 | AR40: VSM Replacement - Wilson Rd S Oshawa Ph 1 Bloor to Olive | 2026 | 5731465.9045 | Issue/Concern/Opportunity: There is vintage 12-inch steel high-pressure (HP) main with several potential maintenance risks. Justification: Main was ranked as HI 5 in recent Asset Health Review (AHR). It was installed in 1957, has multiple service connections with corrosion risk and possible unknown compression couplings. Assets: There is 950 m 12-inch ST HP main and approximately 30 services in Phase 1 Bloor St. to Olive Ave. Related Investments: Not applicable. | Completed | Pass | ETEE - Potentially could reduce project scope.
GTA East | 40 - Whitby | Distribution Pipe | Pass |  | 735949 | AR40: VSM Replacement - Wilson Rd S Oshawa Ph 2 Olive to King | 2026 | 5846848.272 | Issue/Concern/Opportunity: There is vintage 12-inch steel high-pressure (HP) main with several potential maintenance risks. Justification: Main was ranked as HI 5 in recent Asset Health Review (AHR). It was installed in 1957, has multiple service connections with corrosion risk and possible unknown compression couplings. Assets: 1,247m 12-inch ST HP main and approximately 30 services in Phase 2 Olive Ave. to Bloor St. Related Investments: Not applicable. | Completed | Pass | ETEE - Potentially could reduce project scope.
GTA East | 40 - Whitby | Distribution Stations | Fail | Dollar threshold | 7763 | CATHCART & STEWART DISTRICT | 2025 | 1451990.8294
GTA East | 40 - Whitby | Distribution Stations | Fail | Dollar threshold | 501531 | GM South Station | 2023 | 124691.1438
GTA East | 40 - Whitby | Distribution Stations | Fail | Dollar threshold | 501532 | Peterborough District Station | 2023 | 124691.1438
GTA East | 40 - Whitby | Distribution Stations | Fail | Dollar threshold | 735168 | 44512A YANKEE LINE & RUSSELL DISTRICT | 2023 | 277437.795
GTA East | 40 - Whitby | Distribution Stations | Fail | Dollar threshold | 735304 | 2885749 Taunton and Gillett | 2024 | 384413.0567
GTA East | 40 - Whitby | Distribution Stations | Pass |  | 7749 | BOWMANVILLE GATE | 2025 | 4964374.9603 | Issue/Concern: Bowmanville Gate Station is located on fenced EGI-owned property of approximately 700 m2 in Clarington, Ontario. It is approximately 5 km north of Newcastle Ontario, within a rural area. This station accepts natural gas from TC Energy and provides supply to two separate XHP networks, through a measurement system, pressure control system, gas pre-heat system, odourant injection system, and telemetry and controls system. This station supplies natural gas to approximately 61,000 customers in an area that spans from Bowmanville to Lindsay. The following issues have been identified at this station: Valves and Piping: The existing valves at this site have experienced issues in performance and operation of the valves. Maintenance has been performed to attempt to remediate the valves; however, the valves have deteriorated to the point where the reliability is no longer acceptable. The inlet piping to the heat exchanger shows signs of deterioration and should be replaced. The station is located close to Hwy 35/115 and its proximity to traffic puts it at a higher risk. The piping is to be relocated away from the road, as far as practical. Measurement: The current system does not provide measurement of the individual outlet supplies. Visibility to each outlet supply provides redundancy to the existing measurement, odourant injection reliability, and improved response capabilities. The turbine meter is to be replaced with a Coriolis meter. Heating: The existing boilers at this site are 18 years old, they have had 42 trouble call/failures over the life of the heating system, including failures of the motors and pumps, burner lock-outs and exchanger failures. The system, including buildings, will require replacement as it approaches end of life. Odourization: The odourant system was installed in 1999. The current configuration of the odourant system does not ensure adequate containment of the odourant product in the event of a leak and does not meet the current engineering standards and approvals. The building is an old-style, rusted metallic odourant building without adequate containment and a new building, tank, and Odourant Injection system will be required. Telemetry and Electrical: The existing Electrical system does not meet current EGI electrical installation standards. This poses a potential electrical hazard and faulty wiring may result in lost communications. Other: Odourant deliveries - a third-party company is used for traffic control during deliveries. Additional land, not included in this business case, may be identified under a separate business case for station expansion to improve safety during odourant deliveries off of Hwy 35/115. Asset: Bowmanville gate station assets. Related Program: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 40 - Whitby | Distribution Stations | Pass |  | 7754 | OSHAWA GATE | 2025 | 4252715.4078 | Oshawa Gate Station is located on EGI-owned property of approximately 1000 m2 fenced compound in Oshawa, Ontario, approximately 2 km from town, within a rural/urban area, in close proximity to Taunton. This station accepts natural gas from TC Energy and provides supply to 1 XHP network, through components within the Measurement system, Pressure Control system , Heating system, Odourant system, and Telemetry system. This station supplies natural gas to approximately 190,000 customers in the Oshawa Region. The following issues have been identified at this station: Heating System: The existing boilers are undersized for current capacity. Measurement: The current system does not provide measurement of the individual outlet supplies. Visibility to each outlet supply provides greater redundancy to the existing measurement and improved response capabilities. Odourization: The Odourant system was installed in 2011. The current configuration of the Odourant system does not ensure adequate containment of the odourant product in the event of a leak and does not meet the current engineering standards and approvals. Telemetry & Electrical: The existing Electrical system does not meet current EGI electrical installation standards. This poses a potential electrical hazard and faulty wiring may result in lost communications. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 40 - Whitby | Distribution Stations | Pass |  | 7766 | DURHAM 23 FEEDER | 2024 | 2141268.4289 | Durham Road 23 Feeder Station is located on EGI-owned property of approximately 150 m2 fenced compound in the Township of Whitby , Ontario, approximately 3 km east of Ajax, Ontario, within a rural area in proximity to commercial establishments. This station accepts natural gas from EGI XHP and provides supply to an HP network, through components within the Pressure Control system, Heating system, and Telemetry system. This station supplies natural gas to approximately 35,000 customers in Ajax and Whitby areas. The following issues have been identified at this station: Heating: The existing controls on the Heating system have become obsolete, parts are no longer available, and the system is failing to maintain adequate heating requirements. Telemetry & Electrical: The Telemetry and Electrical systems do not meet current EGI standards and are approaching end of useful life. The existing Remoter Terminal Unit (RTU) is obsolete and is required to be upgraded to current standards along with new communications equipment in order to eliminate cybersecurity threats. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA East | 40 - Whitby | Growth | Pass |  | 3740 | Area 40 - Apartment Ensuite - New Construction* |  | 640925.3456 | Vertical Subdivision - A multiple unit residential building where each suite is individually metered. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGD develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long term plans EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. Enbridge reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers; and, - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing Assets: Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA East | 40 - Whitby | Growth | Pass |  | 3744 | Area 40 - Commercial - New Construction* |  | 40540507.4678 | Issue/Concern: Commercial New Construction refers to a customer intending to run a commercial business in a newly-constructed building and intending to using natural gas to meet energy needs Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA East | 40 - Whitby | Growth | Pass |  | 3747 | Area 40 - Residential - New Construction* |  | 52089890.608 | Issue/Concern: Residential New Construction refers to a new residential construction development of detached single homes constructed by the builder for domestic purposes. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA East | 40 - Whitby | Growth | Pass |  | 3748 | Area 40 - Residential - Replacement* |  | 62612624.4069 | Issue/Concern: Residential Replacement refers to a residential replacement customer using a fuel other than natural gas for domestic purposes and is converting to natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA East | 40 - Whitby | Growth | Pass |  | 736524 | NW 4793 Carnwith Dr. Brooklin Reinforcement SRP | 2024 | 301123.5611 | Issue/Concern/Opportunity: Pipe reinforcement of 520 m of NPS 4 PE along Carnwith Dr. W. is required due to system pressures below new minimum allowable system pressure. Assets: Pipe Related Investments: Not applicable | Completed | Pass | CNG, ETEE - Potentially could defer project scope.
GTA East | 40 - Whitby | Growth | Pass |  | 736665 | Station Rebuild 42183A Brock and 3rd Conc SRP | 2023 | 218209.5017 | Issue/Concern/Opportunity: Scope: Station 42183A Rebuild Reinforcement - Pressure regulation upgrades are required to meet the downstream forecasted demands. The reason upgrades are required is to meet capacity requirements to feed network. Assets: District station rebuild Related Program: Not applicable | Planned
GTA East | 40 - Whitby | Utilization | Pass |  | 13546 | MXGI Area 40* | 2019 | 33673379.0207 | Meters: Meters are used to determine the gas consumption input of customer billing. The replacement program for meters is mandated by Measurement Canada. The program includes: testing, repair, and replacement requirements of meters and instruments. All verified meters are approved by Measurement Canada with an issuance of a certificate which identifies that the meter complies with Electricity and Gas Specification S-EG-02. The Company must ensure all measurement devices remain in compliance for annual audits by Measurement Canada. Measurement Canada specifies tolerances under which the meter must operate in the field. The Company must demonstrate that all aspects of its meter sampling, maintenance, and replacement comply with these criteria in order to be accredited by Measurement Canada to be an “Authorized Service Provider” and adhere to Measurement Canada’s accreditation standard S-A-01. Meters may also require exchange for issues such as: damages, leaks, customer billing issues. Regulation: Regulators are the last line of defense for over-pressure to the customer. The condition of regulation systems is determined by regulator performance, corrosion of piping and regulators, and adherence to installation specifications. Failure of the regulation system can cause pressured gas to enter the premise, resulting in failure of gas equipment, loss of containment, and potentially fire or explosion. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | 20 - Mississauga | Distribution Pipe | Fail | Dollar threshold | 1193 | Erin Mills and Leanne Vital | 2025 | 1513665.2635
GTA West | 20 - Mississauga | Distribution Pipe | Fail | Dollar threshold | 7655 | VSM - Bromsgrove Header | 2025 | 874324.2893
GTA West | 20 - Mississauga | Distribution Pipe | Fail | Dollar threshold | 7656 | VSM - Bramalea and Balmoral Rd | 2023 | 830068.9444
GTA West | 20 - Mississauga | Distribution Pipe | Fail | Dollar threshold | 8236 | 1" ST - Archill Crescent | 2022 | 104082.5158
GTA West | 20 - Mississauga | Distribution Pipe | Fail | Dollar threshold | 11127 | Copper Service Replacement - Area 20* | 2020 | 2667645.1424
GTA West | 20 - Mississauga | Distribution Pipe | Fail | Dollar threshold | 736516 | 3665 Flamewood Replacement Copper Relay | 2025 | 646404.547
GTA West | 20 - Mississauga | Distribution Pipe | Fail | Emergent Safety | 4661 | Replacement Blanket - Area 20* |  | 4898309.2011
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 4667 | Anode Blanket - Area 20* | 2020 | 2396036.2281 | General Description: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within the EGI system. These installations and replacements are based on the Corrosion Operating Standard established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 4763 | AMP Fitting Replacement - Area 20* | 2020 | 83572176.889 | AMP Fittings are a below grade transition fittings. The inserted portion of copper tubing can fail due to internal corrosion. In these cases leaks develop immediately downstream of the AMP Fitting. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 7660 | VPM - Erin Township | 2026 | 11695806.7786 | Issue/Concern: There are site-specific concerns. It has been reported through a leak event that the vintage plastic pipe in Erin Township has experienced cracking due to the stony soil in this area. The Gas Technology Institute (GTI) study on Aldyl A pipe has stated stress intensifier such as rock impingement could result in slow crack growth (SCG) in this type of plastic pipe. Assets: Vintage plastic pipe in Erin Township Related Programs: Pipe replacement vintage plastic | Planned
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 13605 | Service Relay Blanket - Area 20* | 2020 | 36638282.0846 | General: A distribution service refers to the pipe between the distribution main and the customer’s meter set. Over the years, different materials have been used for this asset, including steel, copper, and varying resins of plastic, each with unique characteristics that contribute to their performance over time. Services can be repaired or replaced depending on asset condition and the nature of the issue exhibited. Generally, replacement is the preferred approach to mitigate unacceptable asset condition. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30114 | Broadway_GTA West_Area 20_1249 | 2032 | 3764886.5609 | Broadway - GTA West - Area 20 - 1249 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30115 | Clarkson Rd 1 - GTA West - Area 20 - 1665 | 2029 | 2078780.7402 | Clarkson Rd. 1 - GTA West - Area 20 - 1665 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Clarkson Rd. 1 - 1665 and Clarkson Rd. 2 - 1666). | Planned
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30117 | Elizabeth St S 1 - GTA West - Area 20 - 1667 | 2028 | 2830220.8516 | Elizabeth St. S. 1 - GTA West - Area 20 -1667 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Elizabeth St. S. 1 – 1667 and Elizabeth St. S. 2 - 1668). | Planned
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30118 | Elizabeth St S 2 - GTA West - Area 20 - 1668 | 2032 | 3668253.7393 | Elizabeth St. S. 2 - GTA West - Area 20 - 1668 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Elizabeth St. S. 1 – 1667 and Elizabeth St. S. 2 - 1668) | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30120 | Gordon St_GTA West_Area 20_1227 | 2030 | 2508008.8542 | Gordon St._GTA West - Area 20 - 1227 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30121 | Haggert Ave_GTA West_Area 20_1477 | 2031 | 4208533.1695 | Haggert Ave. - GTA West - Area 20 - 1477 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30122 | Joymar Dr 1 - GTA West - Area 20 - 1670 | 2027 | 3195021.7459 | Joymar Dr. 1 (execute 2024 - road rehabilitation work planned for 2024) - GTA West - Area 20 - 1670 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Created two projects based on regional comments (Joyman Dr. 1 - 1670 and Joyman Dr. 2 - 1671). | Completed | Fail | NPS 2, cannot downsize or retire
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30123 | Joymar Dr 2 - GTA West - Area 20 - 1671 | 2027 | 3475138.3482 | Joymar Dr. 2 - GTA West - Area 20 - 1671 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Joyman Dr. 1 - 1670 and Joyman Dr. 2 - 1671). | Planned
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30125 | Main St_GTA West_Area 20_ 1231 | 2030 | 4273641.3316 | Main St. - GTA West - Area 20 - 1231 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30126 | Queen St S 1 - GTA West - Area 20 - 1672 | 2031 | 2839970.6362 | Queen St. S. 1 - GTA West - Area 20 - 1672 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Queen St. S. 1 - 1672 and Queen St. S. 2 - 1673). | Planned
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30127 | Queen St S 2- GTA West - Area 20 - 1673 | 2031 | 2172773.5292 | Queen St. S. 2 - GTA West - Area 20 - 1673 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Queen St. S. 1 - 1672 and Queen St. S. 2 - 1673). | Planned
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30128 | Seagull Dr 1 - GTA West - Area 20 - 1674 | 2032 | 3433839.026 | Seagull Dr. 1 - GTA West - Area 20 - 1674 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Seagull Dr. 1 - 1674 and Seagull Dr. 2 - 1675). | Planned
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30129 | Seagull Dr 2 - GTA West - Area 20 - 1675 | 2030 | 3657537.9397 | Seagull Dr. 2 - GTA West - Area 20 - 1675 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Seagull Dr. 1 - 1674 and Seagull Dr. 2 - 1675). | Completed | Fail | NPS 2, cannot downsize or retire
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30130 | Sproule Dr 1 - GTA West - Area 20 - 1676 | 2031 | 3915376.7233 | Sproule Dr. 1 - GTA West - Area 20 - 1676 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Sproule Dr. 1 – 1676 and Sproule Dr. 2 - 1677). | Planned
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30131 | Sproule Dr 2 - GTA West - Area 20 - 1677 | 2028 | 2502364.473 | Sproule Dr. 2 - GTA West - Area 20 - 1677 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Sproule Dr. 1 – 1676 and Sproule D.r 2 - 1677). | Planned
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 30132 | Vista Dr_GTA West_Area 20_1529 | 2032 | 4633826.4118 | Vista Dr. - GTA West - Area 20 - 1529 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
GTA West | 20 - Mississauga | Distribution Pipe | Pass |  | 102420 | Relocation Program - Area 20* | 2020 | 39569298.9202 | General: Projects in the relocation category are capital expenditures required to replace or relocate segments of pipeline in order to accommodate municipal infrastructure work. The cost sharing for this work is managed through the Franchise Agreements established with municipalities. A consultative approach is used between the municipality and EGI to avoid conflicts with municipal infrastructure early in the planning stage. If a conflict is unavoidable, pipeline assets are typically relocated or replaced. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | 20 - Mississauga | Distribution Stations | Fail | Dollar threshold | 7757 | SANDALWOOD GATE | 2027 | 489221.7049
GTA West | 20 - Mississauga | Distribution Stations | Fail | Dollar threshold | 7781 | EASTGATE AND DIXIE DISTRICT | 2025 | 726893.8755
GTA West | 20 - Mississauga | Distribution Stations | Fail | Dollar threshold | 18625 | MISSISSAUGA RD & HWY. #7 DISTRICT | 2024 | 128137.6856
GTA West | 20 - Mississauga | Distribution Stations | Fail | Dollar threshold | 18909 | BRAMALEA & ADVANCE BLVD. DISTRICT | 2026 | 156421.3649
GTA West | 20 - Mississauga | Distribution Stations | Fail | Dollar threshold | 101119 | 21116A - DERRY & HISTORIC TRAIL | 2024 | 128137.6856
GTA West | 20 - Mississauga | Distribution Stations | Fail | Dollar threshold | 101120 | 21102A - BRESLER & AIRPORT | 2024 | 128137.6856
GTA West | 20 - Mississauga | Distribution Stations | Fail | Dollar threshold | 501491 | Dixie and Derry District | 2023 | 62345.5719
GTA West | 20 - Mississauga | Distribution Stations | Fail | Dollar threshold | 735174 | 20782B DERRY & TOMKEN IP DISTRICT | 2023 | 124691.1438
GTA West | 20 - Mississauga | Distribution Stations | Fail | Dollar threshold | 735175 | 20702A DIXIE & BRITANNIA DISTRICT | 2023 | 124691.1438
GTA West | 20 - Mississauga | Distribution Stations | Pass |  | 1043 | CAWTHRA AND QUEENSWAY DISTRICT | 2024 | 2857248.0717 | Cawthra and Queensway Feeder Station is located on EGI-owned property of approximately 175 m2 fenced compound in the City of Mississauga, Ontario, within an urban area, within 30 m of residential homes in a densely populated subdivision. This station accepts natural gas from EGI XHP pipeline and provides supply to an IP network, through components within the Pressure Control system, and Telemetry system. This station supplies natural gas to approximately 10,000 customers in the City of Mississauga. The following issues have been identified at this station: Valve & Piping: The piping material and components used within this station have been identified as sub-standard with improper construction methods used during construction. Pressure Control: The configuration of the existing regulators is double boot, posing an undesired higher risk and high associated ongoing maintenance costs. Telemetry & Electrical: The Telemetry and Electrical systems do not meet current EGI standards and are approaching end of useful life. The existing Remote Terminal Unit (RTU) is obsolete and is required to be upgraded to current standards along with new communications equipment in order to eliminate cybersecurity threats. Additionally, new instrumentation, a lighting upgrade, and a tower upgrade which is compliant based on space available is required. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA West | 20 - Mississauga | Distribution Stations | Pass |  | 7777 | WINSTON CHURCHILL AND STEELES FEEDER | 2027 | 6197592.9478 | Winston Churchill and Steeles Feeder Gate Station is located on EGI-owned property fenced compound in Mississauga, Ontario, approximately 4 km from Meadowvale town centre, within a rural area in close proximity to industrial establishments. This station accepts natural gas from EGI XHP and provides supply to two separate XHP and HP networks, through components within the Pressure Control system, Heating system, and Telemetry system. This station supplies natural gas to approximately 20,000 customers in Mississauga and Brampton area. The following issues have been identified at this station: Telemetry & Electrical: The Telemetry and Electrical systems do not meet current EGI standards, do not contain backup power supply in the event of power loss, and are approaching end of useful life. The existing Remoter Terminal Unit (RTU) is obsolete and is required to be upgraded to current standards along with new communications equipment in order to eliminate cybersecurity threats. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA West | 20 - Mississauga | Distribution Stations | Pass |  | 503369 | Lisgar Station | 2023 | 21527375.9052 | Issue/Concern/Opportunity: The Lisgar Gate Station is located at a highly populated area in the City of Mississauga. The station is situated in an urban setting and is surrounded by residential buildings, a commercial plaza, and a church. The station has multiple feeds (two transmission lines and one XHP CER line) and various outlets to the local distribution networks. In the event of a major incident, the consequence would be significant given the close proximity to houses and buildings. Justification: The following issues and deficiencies have been identified: Pipes & Valves: They have been deemed unreliable at this site and require removal and installation of new pipes, fittings, and valves. The increased load demand will also allow the pipe to be upsized for current and future expansion. Heating: The Heating system has been deemed unreliable as it has reached its end-of-life cycle usage. The placement of the heat exchangers in the basement of the Boiler building has caused maintenance roadblocks along with flooding concerns. Pressure Regulation: The 20002A regulation has been deemed unreliable and will be rebuilt because of inconsistent flows throughout. The 20002D has suffered from frost-heaving issues as well and requires a rebuild. Odourization: The Odourant system’s current configuration does not ensure adequate containment of the odourant product in the event of a leak and does not meet the current engineering standards and approvals. The pumps need automation along with redundancy for better operational efficiency. Building: The Regulator building that houses 20002B and 20002C needs a noise evaluation study to determine a better noise attenuation solution. Measurement: Existing measurement is not reliable and accurate. A more robust and accurate measurement needs to be installed for custody transfer purposes. Assets: Distribution Station Assets at the Lisgar Gate Station. Related Program: AFF - 219 - NPS 24 Lisgar to Pine Valley - permanent launcher support (23192) | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA West | 20 - Mississauga | Distribution Stations | Pass |  | 735335 | GTAW Parkway Gate Station Rebuild Phase 2 | 2023 | 10598747.2244 | Project: Parkway East Phase 2. Phase 1 commenced in 2021. Issue/Concern/Opportunity: The following sub-assets will be rebuilt due to the issues described below: Regulators: Two existing Becker control valves, i.e., NPS-8 and NPS-6 downstream operators – PRV-0502 and PRV-0504, Runs 9 and 10 on TC Energy feed (quantity is two) are defective and will not lock up; therefore, replacement is required. Currently, the inlet valve from the TC Energy feed is used to completely shut off the TC Energy feed; otherwise, the control valves will bleed by and affect nominations in the summer, automated TC Energy inlet valve for emergency shutoff from TC Energy, as well as to ensure inlet valve is closed to avoid bleed by of Becker control valves in summer conditions (CLOSE ONLY VALVE). Flow control valves on the TC Energy feed are Fairchild’s (will replace with DNGPs – RUNS 9/10) not a computer-controlled regulator and do not sense downstream pressure. Isolation valves for each run are operational. DNGP should also replace Fairchild for 12-inch Union East – CV replacement (12-inch closest to Boiler building - RUN 1); 4th Fairchild is on the MSL – not required – disconnect and replace with VRP pilot (pressure control only due to downstream system operation). The station can be down to facilitate work as system can be fed from Parkway West. An additional five Jordan motors that are obsolete are to be replaced with Rotork motors (quantity is five). Due to capacity constraints and designing for future flow provided by Distribution Optimization Engineering (DOE) / TSP, Run 1 T4 Becker is to be replaced with T1 Becker (NPS 12). Run 3 has undersized isolation valves (currently NPS 8) and will need upsizing to NPS 16. Civil: There is no urethane layer between the pipe support cradle and the bottom of the pipe. A single new Odourant building is required. The wall between the Pressure Transmitter and Remote Terminal Unit (RTU) room is to be opened up for entire building to be RTU room. Demolition of existing Generator building is required. The Storage building is to be removed due to end of life. Piping & Valves: An increase in pipe size near heaters to NPS 30 along with inlet/outlet HX valves to ensure flow requirements can be achieved. Upsizing downstream header and inlet pipe to regulators to NPS 30 is required to ensure it can handle capacity requirements. Odourant: The Odourant system is a metallic odourant building without adequate containment with a rusted containment pan. The fill connection is outdoors. Supports are not fire-rated and no Fire Suppression system is installed. Grating within the building is not safe for accessing valves and equipment. A new Odourant building is required. Two 5,000 GAL odourant tanks complete with electric pumps are to be installed. Low-flow and high-flow pumps with full redundancy on winter pumps on each outlet are required. Switchover between pumps should be automated. Telemetry & Electrical: Existing obsolete Bristol 3330 is to be replaced with Control Wave Micro. Additional electrical wiring and cabling (including power distribution) and programming are to be included in scope. Assets: Station components are to be replaced as described above in Phase 2. Related Program: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA West | 20 - Mississauga | Growth | Pass |  | 3724 | Area 20 - Apartment Traditional - New Construction* |  | 2058.9766 | Apartment - An apartment customer is a multi-residential dwelling containing more than six units that is bulk-meteredIssue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGD develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long term plans EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. Enbridge reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers; and, - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing Assets: Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | 20 - Mississauga | Growth | Pass |  | 3722 | Area 20 - Apartment Ensuite - New Construction* |  | 3507120.7972 | Vertical Subdivision - A multiple unit residential building where each suite is individually metered. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | 20 - Mississauga | Growth | Pass |  | 3726 | Area 20 - Commercial - New Construction* |  | 43123319.2835 | Issue/Concern: Commercial New Construction refers to a customer intending to run a commercial business in a newly-constructed building and intending to using natural gas to meet energy needs. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | 20 - Mississauga | Growth | Pass |  | 3729 | Area 20 - Residential - New Construction* |  | 65585876.7049 | Issue/Concern: Residential New Construction refers to new residential construction development of detached single homes constructed by the builder for domestic purposes. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | 20 - Mississauga | Growth | Pass |  | 3730 | Area 20 - Residential - Replacement* |  | 30865248.1837 | Issue/Concern: Residential Replacement refers to a residential replacement customer using a fuel other than natural gas for domestic purposes and is converting to natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | 20 - Mississauga | Growth | Pass |  | 3783 | Area 20 - Commercial - Replacement* |  | 7028909.2133 | Issue/Concern: Commercial Replacement refers to a commercial replacement customer using a fuel other than natural gas for commercial business and is converting to natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | 20 - Mississauga | Growth | Pass |  | 16748 | Erin IP System Reinforcement | 2028 | 6204819.5534 | Issue/Concern: Reinforcement projects broadly involve the installation of new or modification of existing gas distribution assets to maintain minimum required system pressure, maintain capacity, and meet customer demand. These projects are primarily driven by customer growth and system reliability considerations. Failure to implement reinforcement projects in a timely manner could lead to a potential inability to support increasing demands of existing customers and the addition of future customers. • Project Purpose/Need: The purpose of Phase 1 main reinforcement is to provide capacity on the east side of district station RS21100A, Erin District along Main St. and improve the degrading pressures. Phase 2 and 3 will provide capacity and will improve the degrading pressures southwest of the station along Trafalgar Rd. • Pressure Issue/Concern: The minimum system pressure is 10 psi and is forecasted to be infeasible by 2019 (when the first phase is proposed to start). • Customer Growth Issue/Concern: As of 2018, there are 2,039 customers on this network. Without reinforcement, a forecasted 866 customers may not be able to be added. • Risk If Not Completed: At its current condition, the system will not be able to supply gas for large load additions (i.e., subdivision and commercial) as per the Long-Range Plan (LRP) projections since existing mains have limited capacity and pressures below the minimum system pressure. As per model results, in years 2019, 2023, and 2025, pressures were below minimum system pressures. Assets (preferred option): Phase 1 Year 2019 ‐ Upsize approximately 2,600 m existing NPS 4 ST/PE to NPS 6 PE on Main St. (Station RS21100A, Erin District to Wellington Rd. 124). • 2021 Updates: Phases 2 and 3 have been deferred to 2027 and 2028. o Phase 2 was deferred to 2027 from 2023 ‐ Upsize approximately 3,100 m existing NPS 4 ST to NPS and PE on Sideroad 17 (Station RS21100A, Erin District to Wellington Rd. 24). o Phase 3 was deferred to 2028 from 2025 ‐ Upsize approximately 5,000 m existing NPS 4 ST to NPS and PE on Wellington Rd. 24 (Sideroad 17 to Orangeville St.). Related Programs: Not applicable. | Planned
GTA West | 20 - Mississauga | Growth | Pass |  | 17243 | NW 2225 Terra Cotta IP Reinforcement SRP | 2028 | 1716322.9298 | Issue/Concern/Opportunity: Reinforcement projects broadly involve the installation of new or modification of existing gas distribution assets to maintain minimum required system pressure to maintain the capacity to meet customer demand. These projects are primarily driven by customer growth and system reliability considerations. Failure to implement reinforcement projects in a timely manner could lead to a potential inability to support increasing demands of existing customers and the addition of future customers. •Project Purpose/Need: The Long-Range Plan (LRP) load growth is on the Northwest of the district station RS21221A, King and Creditview District. Because of its collateral impact , the pressures at Mill St. are degraded to below minimum system pressure (MSP) due to less NPS 2 PE main capacity and distance from the NPS 4 PE main source. •Pressure Issue/Concern: The minimum system pressure is 10 PSI and was forecasted to be infeasible by 2021. Customer growth issue/concern: In 2017, there are 352 customers on this network. Without reinforcement, forecasted 26 customers (2018-2028) may not be able to be added. •Risk if Not Completed: Per model results, pressures on Mill St. will be below the MSP, if the NPS 4 PE main is not installed. •Project Benefits: Installing an NPS 4 PE main on Mill St. will mitigate the deteriorating pressures with the projected yearly load growth on the Northwest of the district station RS21221A, King and Creditview District comes in. Assets (preferred option): •Phase 1 Year 2021 ‐ Install approximately 1,700 m of NPS 4 PE on Mill St. (Creditview Rd. to Mississauga Rd.) . •Phase 2 Year 2030 ‐ Install approximately 1,300 m of NPS 4 PE on Mill St. (Mississauga Rd. to Caledon Trailway Path, then along Caledon Trailway Path to Heritage Rd.). Assets: Pipe Related Program: Not applicable | Planned
GTA West | 20 - Mississauga | Growth | Pass |  | 30500 | NW 2103 Dundalk XHP Reinforcement SRP | 2024 | 6919435.0201 | NW 2103 Dundalk XHP Reinforcement SRP Issue/Concern/Opportunity: Inlet to Ida and Hanbury district station (Dundalk) has dropped below system minimum requirements. Gas volume and flow will be diminished with a potential to limit supply to existing and future customers. There is potential for loss of supply to existing customers during peak period demands. Assets: Pipe and district station Related Program: Not applicable | Planned
GTA West | 20 - Mississauga | Growth | Pass |  | 30501 | NW 2103 Erin XHP Reinforcement SRP | 2031 | 6265955.2855 | NW 2103 Erin XHP Reinforcement SRP Issue/Concern/Opportunity: Install pipe to improve pressure for downstream station inlet - Network 2103 (i.e., 400 psig system) low pressures modeled at inlet to Erin Stn21100A (74.8psig) in 2030. After Phase 1 reinforcement, the inlet pressure will drop (82 psig) again in 2032. Assets: Pipe Related Program: Not applicable | Planned
GTA West | 20 - Mississauga | Growth | Pass |  | 30502 | NW 2201 Proton Station IP Reinforcement SRP | 2023 | 1421859.3475 | NW 2201 Proton Station IP Reinforcement SRP Issue/Concern/Opportunity: Existing Intermediate Pressure (IP) system is experiencing very low pressures - 2022 ERX reading low of 5 psig - January 24. Piping system is currently below minimum system requirements and must be improved prior to adding more customers. Assets: Pipe Related Program: Not applicable | Completed | Fail | Timing - Market based supply side alternatives not applicable
GTA West | 20 - Mississauga | Utilization | Pass |  | 13544 | MXGI Area 20* | 2019 | 73468749.0255 | Meters: Meters are used to determine the gas consumption input of customer billing. The replacement program for meters is mandated by Measurement Canada. The program includes: testing, repair, and replacement requirements of meters and instruments. All verified meters are approved by Measurement Canada with an issuance of a certificate which identifies that the meter complies with Electricity and Gas Specification S-EG-02. The Company must ensure all measurement devices remain in compliance for annual audits by Measurement Canada. Measurement Canada specifies tolerances under which the meter must operate in the field. The Company must demonstrate that all aspects of its meter sampling, maintenance, and replacement comply with these criteria in order to be accredited by Measurement Canada to be an “Authorized Service Provider” and adhere to Measurement Canada’s accreditation standard S-A-01. Meters may also require exchange for issues such as: damages, leaks, customer billing issues. Regulation: Regulators are the last line of defense for over-pressure to the customer. The condition of regulation systems is determined by regulator performance, corrosion of piping and regulators, and adherence to installation specifications. Failure of the regulation system can cause pressured gas to enter the premise, resulting in failure of gas equipment, loss of containment, and potentially fire or explosion. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | 50 - Barrie | Distribution Pipe | Fail | Dollar threshold | 4670 | Anode Blanket - Area 50* | 2020 | 755379.6822
GTA West | 50 - Barrie | Distribution Pipe | Fail | Dollar threshold | 13608 | Service Relay Blanket - Area 50* | 2020 | 8482186.62
GTA West | 50 - Barrie | Distribution Pipe | Fail | Dollar threshold | 30083 | Collier St - Area 50 - 1216 | 2032 | 1119847.3134
GTA West | 50 - Barrie | Distribution Pipe | Fail | Dollar threshold | 30087 | Main St - Area 50 - 1223 | 2031 | 1624860.7461
GTA West | 50 - Barrie | Distribution Pipe | Fail | Dollar threshold | 30099 | 000071, NRP - Wellington D2 - 1651 | 2027 | 714660.9749
GTA West | 50 - Barrie | Distribution Pipe | Fail | Dollar threshold | 30102 | 000724, NRP - HNS Grove B1 - 1605 | 2032 | 1561556.1683
GTA West | 50 - Barrie | Distribution Pipe | Fail | Dollar threshold | 30104 | Pr#57, NRP - Collins Street - Collingwood - 1614 | 2027 | 590028.3585
GTA West | 50 - Barrie | Distribution Pipe | Fail | Dollar threshold | 30108 | Pr#62, NRP - Cameron Street - Collingwood - 1616 | 2029 | 685338.9068
GTA West | 50 - Barrie | Distribution Pipe | Fail | Dollar threshold | 736572 | Shallow Main - High Street from Dunlop to Park St | 2023 | 104740.5608
GTA West | 50 - Barrie | Distribution Pipe | Fail | Emergent Safety | 4664 | Replacement Blanket - Area 50 |  | 1135352.9747
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 4765 | AMP Fitting Replacement - Area 50* | 2020 | 13407313.3853 | AMP Fittings are a below grade transition fittings. The inserted portion of copper tubing can fail due to internal corrosion. In these cases leaks develop immediately downstream of the AMP Fitting. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30085 | Ferris Ln - Area 50 - 1201 | 2030 | 2848979.3831 | Ferris Ln. - Area 50 - 1201 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30086 | Jeffrey St - Area 50 - 1199 | 2031 | 2211627.0624 | Jeffrey St. - Area 50 - 1199 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30088 | Market St - Area 50 - 1221 | 2032 | 3020905.0071 | Market St - Area 50 - 1221 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30089 | Oak St 1 - Area 50 - 1654 | 2030 | 2219411.0082 | Oak St. 1 - Area 50 - 1654 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Two projects were created based on regional comments (Oak St. 1 - Area 50 – 1654 and Oak St. 2 - Area 50 - 1655). | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30091 | Pine St - Area 50 - 1205 | 2031 | 2884425.2699 | Pine St. - Area 50 - 1205 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30092 | Ross St - Area 50 - 1210 | 2028 | 2795695.0089 | Ross St. - Area 50 - 1210 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30093 | Second St - Area 50 - 1194 | 2032 | 3634091.6154 | Second St. - Area 50 - 1194 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30094 | St Paul St - Area 50 - 1220 | 2031 | 2485346.532 | St. Paul St. - Area 50 - 1220 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30097 | Yonge St - Area 50 - 1206 | 2032 | 3089246.4818 | Yonge St - Area 50 - 1206 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30101 | 000715, NRP - Wellington B - 1604 | 2032 | 2762368.4922 | 000715, NRP - Wellington B - 2031 - 2033 - 1604 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30105 | Pr#58, NRP - High Street - Collingwood - 1653 | 2030 | 2256541.7961 | Pr#58, NRP - 2023 - High Street - Collingwood - 1653 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30110 | Z1193, NRP - HNS Brock Park B - 1613 | 2029 | 1979712.4812 | Z1193, NRP - HNS Brock Park B, 2024 – 2025 - 1613 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 30111 | Z74, NRP - HNS Queens Park B - 1652 | 2029 | 2507167.5859 | Z74, NRP - HNS Queens Park B, 2023 – 2025 – 1652 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
GTA West | 50 - Barrie | Distribution Pipe | Pass |  | 102423 | Relocation Program - Area 50* | 2020 | 31261154.4558 | General: Projects in the relocation category are capital expenditures required to replace or relocate segments of pipeline in order to accommodate municipal infrastructure work. The cost sharing for this work is managed through the Franchise Agreements established with municipalities. A consultative approach is used between the municipality and EGI to avoid conflicts with municipal infrastructure early in the planning stage. If a conflict is unavoidable, pipeline assets are typically relocated or replaced. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | 50 - Barrie | Distribution Stations | Fail | Dollar threshold | 21104 | Repeater Sites | 2025 | 82886.3105
GTA West | 50 - Barrie | Distribution Stations | Pass |  | 7756 | RUGBY GATE | 2025 | 3191800.1648 | Rugby Gate Station is located on EGI-owned property of approximately 1,350 m2 fenced compound in the Township of Oro-Medonte, Ontario, approximately 7 km from Orillia, within a rural area. This station accepts natural gas from TC Energy and provides supply to an XHP network, through components within the Measurement system, Pressure Control system , Heating system, Odourant system, and Telemetry system. This station supplies natural gas to approximately 20,000 customers in the Coldwater, Midland area. The following issues have been identified at this station: Measurement: The current system does not provide measurement of the individual outlet supplies. Visibility to each outlet supply provides greater redundancy to the existing measurement and improved response capabilities. Valve & Piping: The existing piping within this station have been assessed to be in poor corrosion condition with identified degradation of the piping. HEATING: the existing boilers at this site are 16 years old, they have had 5 trouble call/failures over the past year including failures of the motors and pumps, burner lock-outs and exchanger failures. Due to recent and upcoming customer growth in the Barrie area, the existing Heating system will not be capable of supplying the heating requirements to meet the demand. Odourization: The Odourant system was installed in 2003. The current configuration of the Odourant system does not ensure adequate containment of the odourant product in the event of a leak and does not meet the current engineering standards and approvals. Telemetry & Electrical: The existing Electrical system does not meet current EGI electrical installation standards. This poses a potential electrical hazard and faulty wiring may result in lost communications. Compliance: The existing Boiler building is located within a hazardous area and will have to be relocated. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA West | 50 - Barrie | Distribution Stations | Pass |  | 7758 | THORNTON GATE | 2024 | 4656346.2724 | Pipe, Valves & Others: Minor station piping is required for this project scope. The existing Piping and Valve system is in good shape. Due to the reconfiguration for the Heating system, minor station piping may be required to align the new equipment. Issue/Concern: Heating System: Updated heating is required at this station. A new heat exchanger is required including the associated piping for the glycol inlet and outlet to the heating element. New boilers can fit within the limits of the existing building. New modulating boilers are required. Pressure Control: New regulation is required to various flow ranges. New Becker regulators and two runs are required. One monitor and one operator is needed for two runs. This will involve new spools for both runs at a minimum. Odourant System: No changes are required. Telemetry/Electrical: New Control Wave Micro unit and associated connections are required. One new pressure transmitter and one new temperature transmitter are to be accounted for. Measurement: Annubar is sized correct. There is no requirement for replacement. Building: A new Remote Terminal Unit (RTU) building is required (concrete pre-cast building). The existing RTU building is to be removed. Compliance/Civil: Site grading will be required as well as new security fencing (galvanized) including new swing gate and crash bar access. Scope: Heating System: Updated heating is required at this station. New Heat Exchanger is required including the associated piping for the glycol inlet and outlet to heating element. New boilers can fit within the limits of the existing building. New modulating boilers are required. Pressure Control: New Regulation required to various flow ranges. New Becker regulators are 2 Run’s are required. 1 Monitor and 1 operator is needed for 2 runs. This will involve new spools for both runs at a minimum. Odorant System: No changes required Telemetry/Electrical: New Control Wave Micro unit required and associated connections. Account for 1 new pressure transmitter and 1 new temperature transmitter. Measurement: Annubar is sized correct. No requirement for replacement. Building: New RTU Building Required, Concrete Pre-Cast Building. Existing RTU building to be removed. Compliance/Civil: Site Grading will be required and new security Fencing (Galvanized) including new swing gate and crash bar access. | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA West | 50 - Barrie | Growth | Pass |  | 3753 | Area 50 - Commercial - New Construction* |  | 11233172.0236 | Issue/Concern: Commercial New Construction refers to a customer intending to run a commercial business in a newly-constructed building and intending to using natural gas to meet energy needs Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | 50 - Barrie | Growth | Pass |  | 3756 | Area 50 - Residential - New Construction* |  | 89321708.9452 | Issue/Concern: Residential New Construction refers to a new residential construction development of detached single homes constructed by the builder for domestic purposes. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | 50 - Barrie | Growth | Pass |  | 3757 | Area 50 - Residential - Replacement* |  | 61102549.1845 | Issue/Concern: Residential Replacement refers to a residential replacement customer using a fuel other than natural gas for domestic purposes and is converting to natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | 50 - Barrie | Growth | Pass |  | 30503 | NW 5346 Midhurst Reinforcement SRP | 2024 | 1334347.6934 | NW 5346 Midhurst Reinforcement SRP Issue/Concern/Opportunity: Total of 1,300 m NPS 4 is required to increase security of supply for Midhurst, and maintain 140 kPa as Minimum System Pressure in this Maximum Operating Pressure (MOP) 345 kPa system. Assets: Pipe Related Program: Not applicable | Planned
GTA West | 50 - Barrie | Growth | Pass |  | 30504 | NW 5446 Hwy 26 and Keith Reinforcement SRP | 2024 | 750549.8353 | NW 5446 Hwy 26 and Keith Reinforcement SRP Issue/Concern/Opportunity: A new station and total 420 m NPS 4 are required to increase security of supply for Intermediate Pressure (IP) NW5446/5372. Existing station #3362255 cannot maintain the system health and a damage occurred on November 1, 2021. Assets: Pipe and district station Related Program: Not applicable | Planned
GTA West | 50 - Barrie | Growth | Pass |  | 30505 | NW 5422 Robins Point Rd. Reinforcement SRP | 2024 | 717956.7336 | NW 5422 Robins Point Rd. Reinforcement SRP Issue/Concern/Opportunity: A total of 800 m NPS 2 is required to increase security of supply for Victoria Harbour, and maintain 140 kPa as minimum system pressure in this Maximum Operating Pressure (MOP) 310 kPa system. In January 2022, 13 psig was recorded as low pressure in cold snap. Assets: Pipe Related Program: Not applicable | Planned
GTA West | 50 - Barrie | Growth | Pass |  | 500705 | NW 5301 Barrie - Collingwood Pressure Increase SRP | 2022 | 1496293.7258 | Issue/Concern/Opportunity: Pressure issue is at the west tail end of network 5301. The long-range planning forecast shows by 2024 that the pressure will drop below 100 psig. Recently, a few customer load addition requests have been denied based on a diminished pressure and capacity constraint. Currently, the Maximum Operating Pressure in Network 5301 is 400 psig and this pressure elevation is looking to increase it to 500 psig. • With this pressure elevation, current new customers can be accommodated quickly. • With this pressure elevation, County Rd. 9 reinforcement can be deferred to 10 years later. • Preparation for next steps can happen to harmonize Barrie to Collingwood line with Rugby XHP system, by pressure increase on Rugby Gate Station, from 480 psig to 500 psig and removing Rugby Kicker Station. • By harmonizing these two systems, Penetanguishine Reinforcement project ($15.2M – BC#7723) can be deferred to 10 years later. Assets: All pipe and stations on Network 5301 will be assessed if any reinforcements need to be made. Related Program: Not applicable. | Completed | Fail | N/A - Project in construction phase
GTA West | 50 - Barrie | Utilization | Pass |  | 13547 | MXGI Area 50* | 2019 | 16833108.606 | Meters: Meters are used to determine the gas consumption input of customer billing. The replacement program for meters is mandated by Measurement Canada. The program includes: testing, repair, and replacement requirements of meters and instruments. All verified meters are approved by Measurement Canada with an issuance of a certificate which identifies that the meter complies with Electricity and Gas Specification S-EG-02. The Company must ensure all measurement devices remain in compliance for annual audits by Measurement Canada. Measurement Canada specifies tolerances under which the meter must operate in the field. The Company must demonstrate that all aspects of its meter sampling, maintenance, and replacement comply with these criteria in order to be accredited by Measurement Canada to be an “Authorized Service Provider” and adhere to Measurement Canada’s accreditation standard S-A-01. Meters may also require exchange for issues such as: damages, leaks, customer billing issues. Regulation: Regulators are the last line of defense for over-pressure to the customer. The condition of regulation systems is determined by regulator performance, corrosion of piping and regulators, and adherence to installation specifications. Failure of the regulation system can cause pressured gas to enter the premise, resulting in failure of gas equipment, loss of containment, and potentially fire or explosion. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | Div_17 - Halton | Distribution Pipe | Fail | Dollar threshold | 48454 | HALT: Dist-Repl-Contr-Mains Leakage* | 2019 | 1377825.1311
GTA West | Div_17 - Halton | Distribution Pipe | Fail | Dollar threshold | 48455 | HALT: Dist-Repl-Contr-Services* | 2020 | 10347400.119
GTA West | Div_17 - Halton | Distribution Pipe | Fail | Dollar threshold | 503061 | Halt: Harrop drive, Milton, BU Replacement | 2024 | 710529.1799
GTA West | Div_17 - Halton | Distribution Pipe | Pass |  | 48453 | HALT: Dist-Repl-Contr-Mains Municipal* | 2020 | 38392868.1898 | General: Projects in the relocation category are capital expenditures required to replace or relocate segments of pipeline in order to accommodate municipal infrastructure work. The cost sharing for this work is managed through the Franchise Agreements established with municipalities. A consultative approach is used between the municipality and EGI to avoid conflicts with municipal infrastructure early in the planning stage. If a conflict is unavoidable, pipeline assets are typically relocated or replaced. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | Div_17 - Halton | Distribution Pipe | Pass |  | 503196 | HALT: Anodes* | 2020 | 5858459.0628 | General: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within EGI's system. These installations and replacements are based on the internal Standard Operating Practice established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 101081 | HALT-Winston Churchill & 10 Side Rd | 2025 | 645725.1021
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 101085 | HALT-Lynden Gate Stn | 2025 | 645725.1021
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 101088 | HALT-Third Line and QEW Vault Station | 2025 | 645725.1021
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 101089 | HALT-Milton TBS | 2025 | 1291450.2041
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 101096 | HALT - York and Broadway | 2028 | 688087.4601
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 101099 | HALT - Dundas and Meadowridge | 2025 | 516580.0816
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 101125 | HALT - Centennial and Guelph Line Vault Station | 2023 | 622765.1442
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 735035 | Halt: Ninth/Britannia, Rebuild | 2024 | 640809.1449
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 735039 | HALT: Ford and Royal Windsor, Maintenance | 2025 | 516580.0816
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 735049 | HALT: EC Drury School,Rebuild | 2030 | 70737.4677
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 735052 | HALT: Saputo, rebuild | 2026 | 260644.5475
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 735055 | HALT: Morgan Thermal Ceramics, Maintenance | 2030 | 70737.4677
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 735066 | HALT: Affinia Canada Corp, Rebuild | 2032 | 271598.2547
GTA West | Div_17 - Halton | Distribution Stations | Fail | Dollar threshold | 735067 | HALT: Milton Hydro Dist Inc, Rebuild | 2030 | 282949.8708
GTA West | Div_17 - Halton | Distribution Stations | Pass |  | 735054 | HALT: Burlington Gate, boiler | 2028 | 2752349.8406 | Issue/Concern/Opportunity: VALVE & PIPING: Piping is experiencing corrosion and will be evaluated by FIMP closer to the proposed project date. FIMP will asses the existing valves for any iissues in performance and operation. FILTRATION: N/A HEATING: the existing boilers at this site have reached end of life based on condition review and performance. The building is in disrepair and will be replaced in this investment. This investment aligns with the obsolete heating system strategy that targets stations with heating equipment that have reached end of life, with a focus on systems where there is a risk of a glycol spill. Natural gas heating equipment is used in many System and Customer Stations to help mitigate failure of equipment due to the freezing of liquids in the gas stream and moisture surrounding buried piping. Over many years of operation, a variety of heating systems have been used, resulting in varying equipment age and ultimately, equipment obsolescence. This work will maintain system reliability, ensure operating costs for heating systems are minimized and reduce the potential for glycol spills, including providing the appropriate containment systems to minimize the impacts of an event. Loss of the heating system function could result in two scenarios, (1) frost heave or (2) pressure control failure due to the freezing of station components. Frost heave occurs when the gas is cooled due to the pressure reduction and causes an upward swelling of soil around public or private property near the gas main. Freezing of station components such as creating large ice buildup around valves can prevent operation if gas isolation is required. This could result in the loss of pressure control and potentially lead to an overpressure or underpressure situation. The financial impact includes commodity loss, service disruptions, increased network leak surveys and system checks, repairs or replacement of company-owned property, or damages caused to public, commercial or industrial property. Inoperable systems will lead to a failure to maintain operational supply to customers. PRESSURE CONTROL: Obsolete design will be replaced in this investment. ODOURIZATION: Current system is in working order. TELEMETRY & ELECTRICAL: the telemetry and electrical systems do not meet current EGI standards, do not contain backup power supply in the event of powerloss, and are approaching end of useful life. MEASUREMENT . COMPLIANCE & OTHER Eng: will be assessed closer to project date. Signage and site assess (fencing/egress) to be upgraded during this project. Assets: 18X-601 Related Program: N/A | Completed | Fail | Distribution station condition related, IRPA not applicable
GTA West | Div_17 - Halton | Growth | Pass |  | 48452 | HALT: Company Program - New Business - Scattered Mains - Contractor* | 2020 | 37840249.4909 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | Div_17 - Halton | Growth | Pass |  | 500422 | HALT: Company Program - Customer Connections* |  | 40491554.2816 | Hamilton Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
GTA West | Div_17 - Halton | Growth | Pass |  | 503058 | SRP_GTA West_Oakville_18Y-109RSTN_Rebuild | 2023 | 1307806.8028 | Growth in the Old Bronte/Khalsa gate area of Oakville requires a new station to be built. This is a placeholder for the station, land and installation cost. | Planned
GTA West | Div_17 - Halton | Growth | Pass |  | 735034 | SRP_GTA West_Lowville_18X-101STN_Rebuild | 2024 | 897132.8029 | Issue/Concern/Opportunity: Single feed to Campbellville, no filter, requires operator monitor, heater undersized, and no filtration. The scope is to build a monitor-operator system, upgrade regulation, install Remote Terminal Unit (RTU) and replace heater. | Planned
GTA West | Div_17 - Halton | Utilization | Pass |  | 48464 | HALT: Meter & Regulator Inst Repl-Contractor | 2020 | 33814149.7571 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Dollar threshold | 1180 | Integrity Capital Tools Program* |  | 509611.204
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Dollar threshold | 1905 | 2026 Integrity Program* |  | 387435.0612
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Dollar threshold | 49651 | Mattawa Bridge - North Bay 18 | 2023 | 952830.6706
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Dollar threshold | 100091 | Corrosion Program Rectifier Groundbed* | 2030 | 4145201.5685
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Timing | 1278 | 2023 Integrity Dig Program* | 2023 | 13514003.6293
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Timing | 1287 | 2024 Integrity Dig Program* | 2024 | 10989875.5539
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Timing | 1291 | 2025 Integrity Retrofit Program* | 2025 | 3874350.6124
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Timing | 1294 | 2025 Integrity Dig Program* | 2025 | 8136136.286
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Timing | 102450 | 2023 Class Location Replacement Program* | 2023 | 1245530.2884
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Timing | 102451 | 2024 Class Location Replacement Program* | 2024 | 2563236.5797
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Timing | 102452 | 2025 Class Location Replacement Program* | 2025 | 2582900.3566
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Fail | Timing | 736419 | 2023 DP Depth of Cover Mitigation Program* | 2023 | 7473181.7305
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 1276 | 2023 Integrity Retrofit Program* |  | 3736590.8652 | Project Specific: Integrity Retrofit program, supporting refinement of pipeline risk profile. The purpose of this program is to gain a more complete level of pipeline risk by making additional pipelines accessible for Inline Inspection. Specific pipelines for retrofit will be identified 1-2 years prior to year of construction. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 1284 | 2024 Integrity Retrofit Program* |  | 3844854.8696 | Project Specific: Integrity Retrofit program, supporting refinement of pipeline risk profile. The purpose of this program is to gain a more complete level of pipeline risk by making additional pipelines accessible for Inline Inspection. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGIs pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 49935 | Depth of Cover Mitigation Program* | 2028 | 19612548.9208 | General: In compliance with the TSSA Code Adoption Document, EGI has an annual depth of cover survey program for all 30 per cent SMYS pipelines. These surveys may identify locations where remediation is required. The current cycle of depth of cover surveys will be completed in 2023 at which time a prioritized list of capital replacements will be created to plan for any identified required remediation. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 49938 | MOP Verification Replacement Program* | 2029 | 51256030.9674 | Maximum Operating Pressure (MOP) verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of pipelines that are greater than 30 percent SMYS. While this is not currently mandated by code in Canada, it is required in the United States and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 percent SMYS, MOP verification will continue to be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102453 | 2026 Class Location Replacement Program* | 2034 | 6516113.7386 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102454 | 2027 Class Location Replacement Program* | 2035 | 6938714.782 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102455 | 2028 Class Location Replacement Program* | 2036 | 6880874.6014 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102456 | 2029 Class Location Replacement Program* | 2037 | 6831606.0283 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102457 | 2030 Class Location Replacement Program* | 2038 | 7073746.7698 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102744 | 2026 Integrity Dig Program* |  | 10145589.0099 | Forecast: not provided for 2026-2030 at this time, using average of 2020-2025 as placeholder General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102746 | 2027 Integrity Dig Program* |  | 10803578.9156 | Forecast: not provided for 2026-2030 at this time, using average of 2020-2025 as placeholder General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102747 | 2028 Integrity Dig Program* |  | 10713521.7544 | Forecast: not provided for 2026-2030 at this time, using average of 2020-2025 as placeholder General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102748 | 2029 Integrity Dig Program* |  | 10636810.586 | Forecast: not provided for 2026-2030 at this time, using average of 2020-2025 as placeholder General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102750 | 2030 Integrity Dig Program* |  | 11013823.7205 | Forecast: not provided for 2026-2032 at this time, using average of 2020-2025 as placeholder General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102751 | 2026 Integrity Retrofit Program* |  | 4300635.0331 | Project Specific: Forecast note provided for 2026-2030, using average of 2023-2025 as placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102752 | 2027 Integrity Retrofit Program* |  | 4579551.7561 | Project Specific: Forecast note provided for 2026-2030, using average of 2023-2025 as placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102753 | 2028 Integrity Retrofit Program* |  | 4541377.2369 | Project Specific: Forecast note provided for 2026-2030, using average of 2023-2025 as placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102754 | 2029 Integrity Retrofit Program* |  | 4508859.9786 | Project Specific: Forecast note provided for 2026-2030, using average of 2023-2025 as placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 102755 | 2030 Integrity Retrofit Program* |  | 4668672.868 | Project Specific: Forecast note provided for 2026-2032, using average of 2023-2025 as placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 503431 | Bridge Crossing Painting Program* |  | 6465631.2583 | Issue/Concern/Opportunity: Bridge crossing inspection results in different levels of action which can include replacement, recoating, or hanger repair/replacement work. This program is for recoating work and hanger repair. Justification: The integrated Corrosion Operating Standard ST-17-B13A-DDA9 was released 2020-11-25 and requires the following surveys: Annual visual, 5 year detailed. The standard outlines the following time frames: Bridge crossing – replace Per Engineering assessment per project plan; Bridge crossing – replace expansion joint / Ins flange within 24 months; Bridge crossing / paint pipe / repair hangers / replace casing end seal within 12 months. Assets: Related Investments: | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 733983 | 2031 Class Location Replacement Program* | 2039 | 6996392.7858 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 733984 | 2032 Class Location Replacement Program* | 2040 | 6789956.3676 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 733990 | 2031 Integrity Dig Program* |  | 10893383.5674 | Forecast: not provided for 2026-2032 at this time, using average of 2020-2025 as placeholder General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 733992 | 2032 Integrity Dig Program* |  | 10571962.0643 | Forecast: not provided for 2026-2032 at this time, using average of 2020-2025 as placeholder General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 733996 | 2031 Integrity Retrofit Program* |  | 4617619.2386 | Project Specific: Forecast note provided for 2026-2032, using average of 2023-2025 as placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Pipe | Pass |  | 733997 | 2032 Integrity Retrofit Program* |  | 4481371.2026 | Project Specific: Forecast note provided for 2026-2032, using average of 2023-2025 as placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 49612 | CFB Station Retirement | 2032 | 135799.073
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 102667 | 2023 Odourant Upgrades - MOIS Upgrades* | 2023 | 1245530.2884
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 102680 | 2023 Odourant Upgrades -Sweep Tanks* | 2023 | 373659.0865
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 102681 | 2024 Odourant Upgrades -Sweep Tanks* | 2024 | 384485.487
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 102683 | 2025 Odourant Upgrades -Sweep Tanks* | 2025 | 387435.0612
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 102721 | 2023 Odourant Upgrades -Disposal/Decommission* | 2023 | 49821.2115
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 102722 | 2024 Odourant Upgrades -Disposal/Decommission* | 2024 | 51264.7316
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 102723 | 2025 Odourant Upgrades -Disposal/Decommission* | 2025 | 51658.0082
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 102736 | 2023 Turbine Meter Automatic Oilers Upgrade | 2023 | 103408.9067
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 102737 | 2024 Turbine Meter Automatic Oilers Upgrade | 2024 | 108532.5633
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 102738 | 2025 Turbine Meter Automatic Oilers Upgrade | 2025 | 111552.8857
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735219 | 2026 Odourant Upgrades -Sweep Tanks* | 2026 | 390966.8212
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735220 | 2027 Odourant Upgrades -Sweep Tanks* | 2027 | 416322.8869
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735221 | 2028 Odourant Upgrades -Sweep Tanks* | 2028 | 412852.4761
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735222 | 2029 Odourant Upgrades -Sweep Tanks* | 2029 | 409896.3617
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735223 | 2030 Odourant Upgrades -Sweep Tanks* | 2030 | 424424.8062
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735224 | 2031 Odourant Upgrades -Sweep Tanks* | 2031 | 419783.5671
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735225 | 2032 Odourant Upgrades -Sweep Tanks* | 2032 | 407397.3821
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735227 | 2026 Odourant Upgrades -Disposal/Decommission* | 2026 | 52128.9095
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735228 | 2027 Odourant Upgrades -Disposal/Decommission* | 2027 | 55509.7183
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735230 | 2028 Odourant Upgrades -Disposal/Decommission* | 2028 | 55046.9968
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735231 | 2029 Odourant Upgrades -Disposal/Decommission* | 2029 | 54652.8482
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735232 | 2030 Odourant Upgrades -Disposal/Decommission* | 2030 | 56589.9742
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735233 | 2031 Odourant Upgrades -Disposal/Decommission* | 2031 | 55971.1423
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735234 | 2032 Odourant Upgrades -Disposal/Decommission* | 2032 | 54319.6509
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735236 | 2026Turbine Meter Automatic Oilers Upgrade | 2026 | 114821.7425
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735237 | 2027 Turbine Meter Automatic Oilers Upgrade | 2027 | 124713.684
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735238 | 2028 Turbine Meter Automatic Oilers Upgrade | 2028 | 126147.0741
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735240 | 2029 Turbine Meter Automatic Oilers Upgrade | 2029 | 127748.3001
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735241 | 2030 Turbine Meter Automatic Oilers Upgrade | 2030 | 134921.8164
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735243 | 2031 Turbine Meter Automatic Oilers Upgrade | 2031 | 136116.2209
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735244 | 2032 Turbine Meter Automatic Oilers Upgrade | 2032 | 134741.2521
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Dollar threshold | 735245 | 2027 Fire Suppression and Auto Transfer Generator | 2027 | 693871.4782
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Timing | 102668 | 2024 Odourant Upgrades - MOIS Upgrades* | 2024 | 1640471.411
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Timing | 102669 | 2025 Odourant Upgrades - MOIS Upgrades* | 2025 | 1692574.6375
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Timing | 102726 | 2023 RTU Upgrade Program* | 2023 | 1619189.3749
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Timing | 102727 | 2024 RTU Upgrade Program* | 2024 | 1537941.9478
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Timing | 102728 | 2025 RTU Upgrade Program* | 2025 | 1571210.6046
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Timing | 501373 | 2023 Fire Suppression and Auto Transfer Generator | 2023 | 2535899.6672
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Timing | 501374 | 2024 Fire Suppression and Auto Transfer Generator* | 2024 | 2509408.6115
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Timing | 501375 | 2025 Fire Suppression and Auto Transfer Generator* | 2025 | 2582900.4082
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Fail | Emergent Safety | 48743 | Distribution Operations Station Maintenance Blankets* |  | 21900913.9585
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 48667 | CNG Stations - Project #4 | 2023 | 3113825.721 | Traditionally, fleet operators fuel their vehicles with gasoline or diesel. EGI promotes the use of natural gas to these customers as an alternate fuel source to provide a lower-cost and lower-emission fueling solution for vehicles such as garbage trucks, light duty vehicles, and transit buses. Business Development is responsible for the installation, maintenance, and the safe and continued operation of NGT stations assets for these customers. NGT stations differ in operation from distribution system stations as NGT stations use and store compressed natural gas (CNG) on site at up to 4000psi. EGD has two general categories for NGT station types: Large, Mobile and Utility NGT stations and Small NGT stations (also referred to as VRAs). Large, Mobile and Utility NGT stations are similar in operation and will be evaluated for condition in the same manner. | Completed | Fail | See investment description, IRPAs not applicable for CNG
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 48744 | Distribution Operations Station Painting* |  | 26848160.1102 | Issue/concern: This is a centrally managed program in the Union rate zone to apply high performance paint to stations where existing paint has begun to fail or wear off of the facilities on which it has been applied. The Station Painting Program is a significant corrosion mitigation practice. The frequency and criteria for high performance painting at station sites is specifically prescribed in the Corrosion Control Standard Operating Practice (SOP) and is its documented and committed practice on its compliance with the applicable codes for corrosion control on above-grade station assets. This work will improve compliance and ensure the safety and reliability of EGI assets by reducing the risk of leaks and piping and/or equipment failure due to significant corrosion. Assets: Related Programs (enter N/A if not applicable): | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 501127 | FIMP Station Assessment Program* |  | 46581556.8597 | Issue/Concern/Opportunity: FIMP assesses stations against threats that are listed in the EGI Hazard and Risk Common Register Risk Register to identify susceptibility to identified risks and determine mitigation strategies for individual sites, ensuring that risk is managed to the lowest practical levels. The strategy for the FIMP program is to perform inspections using with approved technologies used at EGI or other utilities for similar asset types. These inspections will assess the condition of existing station assets and will detect any concerns or issues to help determine the likelihood and consequence of failure of individual components and evaluate the risk. This strategy will allow for targeted replacement and will extend the useful life of assets by identifying condition issues prior to the occurrence of an incident. When analysis indicates that ongoing repair costs are likely to exceed capital requirements to replace the asset, the mitigation strategy is evaluated to ensure that risk is managed to the lowest practicable level. Assets: FIMP DS Stations Related Investments: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 501672 | 2026 Fire Suppression and Auto Transfer Generator* | 2026 | 2841025.5673 | Issue/Concern/Opportunity: 75 buildings that have Odourant inside need fire suppression and 59 need auto transfer generators - as of now 16 have auto transfer generators, this is due to code compliance with building code and the fire code. Justification: To install fire suppression systems inside 75 Odourant buildings in order to be compliant with the fire code and 59 auto transfer generators which need to be installed for the emergency lighting based on the building code, maintaining 30 minutes of light to meet code requirements. Additional compliance requirements to be accordance with the LEG Building Standard to install with methane and CO gas detectors in the boiler building as per page 26. The building standard is being integrated and the above requirement will still be considered requiring the boiler buildings to be equipped through this installation program. Buildings with Gas Burning assets require CO and CH4 Detectors, buildings with gas require CO detectors. This work is in accordance with Code Sections: Ontario Building Code Sections: 9.10.1.3, 3.2.2.71, 3.2.4.1, 3.2.9.1, 3.2.9.2 to 3.2.9.7, 3.3.1.5.(1) and 3.3.5.2 Ontario Fire Code Sections: 2.8, 4.1.5.6, 4.2.7.7**, 4.3.12, 4.3.13.1, 4.3.13.4, 6.2, 6.8.1.1** Assets: 75 LUG Stations Related Investments: | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 733885 | Operations Services Central IRR Program | 2022 | 23657218.1891 | Issue/Concern/Opportunity: GDS has performed a survey to identify inside regulation at Customer Stations where the risk assessment identified the hazard of leaks from higher operating pressure piping will have a larger leak rate than pipes operating at lower pressures (for same hole size). Indoor regulators cause higher operating pressure pipe indoors - potential leaks may be able to reach LFL faster. Depending on leak rate, building ventilation, and room size, it is possible for indoor gas leak to build up to LFL leading to possible ignition resulting in an explosion. GDS is executing a program to relocate indoor regulators into an external regulator room (ERR) or relocate outdoors if possible. Some locations may not be immediately possible to relocate due to external factors not under the company's control, however over the long-term relocation may be possible. Similar treatment plans were previously considered and initiated in both legacy parts of the business. Review of Inside Regulator Rooms (IRR) in the LUG system and remediation as required Justification: We no longer allow IRRs as part of our standard designs as they pose various operational risks. Assets: Assets span the entire LUG system, review was done for all areas Related Investments: | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735115 | LUG DS - Gate, Feeder & A Stations Program* | 2031 | 146545887.4859 | Issue/concern: This Investment was created to hold program dollars for future projects that are not yet identified and/or developed for years later in the capital plan. Assets: Related Programs (enter N/A if not applicable): | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735204 | 2026 RTU Upgrade Program* | 2026 | 1961236.8393 | Issue/Concern: The forecast in this category includes projects to replace all the existing remote terminal units and replace with current technology, the ControlWave Micro introduced in 2003. Many current Remote Telemetry Units (RTUs) are 3330/3310 which have been obsolete since 2009 and are no longer supported by the manufacturer. This is a standardized approach that ensures enhanced control and current communication protocols for SCADA Gas Control, odourization, measurement data collection and volume nominations. Starting in 2024, the SCADA RTU lifecycle project will take over as the current technology will be 21 years old. The benefit of these projects will be smooth migration of in-service RTU fleet to current technology using a standardized approach. Currently, these legacy RTUs are at end-of-life and deferring this work may increase failure rate drastically due to the “wear-out” effect. Asset: System Station Assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735205 | 2027 RTU Upgrade Program* | 2027 | 2192853.1345 | Issue/Concern: The forecast in this category includes projects to replace all the existing remote terminal units and replace with current technology, the ControlWave Micro introduced in 2003. Many current Remote Telemetry Units (RTUs) are 3330/3310 which have been obsolete since 2009 and are no longer supported by the manufacturer. This is a standardized approach that ensures enhanced control and current communication protocols for SCADA Gas Control, odourization, measurement data collection and volume nominations. Starting in 2024, the SCADA RTU lifecycle project will take over as the current technology will be 21 years old. The benefit of these projects will be smooth migration of in-service RTU fleet to current technology using a standardized approach. Currently, these legacy RTUs are at end-of-life and deferring this work may increase failure rate drastically due to the “wear-out” effect. Asset: System Station Assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735206 | 2028 RTU Upgrade Program* | 2028 | 2283302.6378 | Issue/Concern: The forecast in this category includes projects to replace all the existing remote terminal units and replace with current technology, the ControlWave Micro introduced in 2003. Many current Remote Telemetry Units (RTUs) are 3330/3310 which have been obsolete since 2009 and are no longer supported by the manufacturer. This is a standardized approach that ensures enhanced control and current communication protocols for SCADA Gas Control, odourization, measurement data collection and volume nominations. Starting in 2024, the SCADA RTU lifecycle project will take over as the current technology will be 21 years old. The benefit of these projects will be smooth migration of in-service RTU fleet to current technology using a standardized approach. Currently, these legacy RTUs are at end-of-life and deferring this work may increase failure rate drastically due to the “wear-out” effect. Asset: System Station Assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735207 | 2029 RTU Upgrade Program* | 2029 | 2380300.9641 | Issue/Concern: The forecast in this category includes projects to replace all the existing remote terminal units and replace with current technology, the ControlWave Micro introduced in 2003. Many current Remote Telemetry Units (RTUs) are 3330/3310 which have been obsolete since 2009 and are no longer supported by the manufacturer. This is a standardized approach that ensures enhanced control and current communication protocols for SCADA Gas Control, odourization, measurement data collection and volume nominations. Starting in 2024, the SCADA RTU lifecycle project will take over as the current technology will be 21 years old. The benefit of these projects will be smooth migration of in-service RTU fleet to current technology using a standardized approach. Currently, these legacy RTUs are at end-of-life and deferring this work may increase failure rate drastically due to the “wear-out” effect. Asset: System Station Assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735208 | 2030 RTU Upgrade Program* | 2030 | 2587903.3755 | Issue/Concern: The forecast in this category includes projects to replace all the existing remote terminal units and replace with current technology, the ControlWave Micro introduced in 2003. Many current Remote Telemetry Units (RTUs) are 3330/3310 which have been obsolete since 2009 and are no longer supported by the manufacturer. This is a standardized approach that ensures enhanced control and current communication protocols for SCADA Gas Control, odourization, measurement data collection and volume nominations. Starting in 2024, the SCADA RTU lifecycle project will take over as the current technology will be 21 years old. The benefit of these projects will be smooth migration of in-service RTU fleet to current technology using a standardized approach. Currently, these legacy RTUs are at end-of-life and deferring this work may increase failure rate drastically due to the “wear-out” effect. Asset: System Station Assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735209 | 2031 RTU Upgrade Program* | 2031 | 2687583.1305 | Issue/Concern: The forecast in this category includes projects to replace all the existing remote terminal units and replace with current technology, the ControlWave Micro introduced in 2003. Many current Remote Telemetry Units (RTUs) are 3330/3310 which have been obsolete since 2009 and are no longer supported by the manufacturer. This is a standardized approach that ensures enhanced control and current communication protocols for SCADA Gas Control, odourization, measurement data collection and volume nominations. Starting in 2024, the SCADA RTU lifecycle project will take over as the current technology will be 21 years old. The benefit of these projects will be smooth migration of in-service RTU fleet to current technology using a standardized approach. Currently, these legacy RTUs are at end-of-life and deferring this work may increase failure rate drastically due to the “wear-out” effect. Asset: System Station Assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735210 | 2032 RTU Upgrade Program* | 2032 | 2738697.6671 | Issue/Concern: The forecast in this category includes projects to replace all the existing remote terminal units and replace with current technology, the ControlWave Micro introduced in 2003. Many current Remote Telemetry Units (RTUs) are 3330/3310 which have been obsolete since 2009 and are no longer supported by the manufacturer. This is a standardized approach that ensures enhanced control and current communication protocols for SCADA Gas Control, odourization, measurement data collection and volume nominations. Starting in 2024, the SCADA RTU lifecycle project will take over as the current technology will be 21 years old. The benefit of these projects will be smooth migration of in-service RTU fleet to current technology using a standardized approach. Currently, these legacy RTUs are at end-of-life and deferring this work may increase failure rate drastically due to the “wear-out” effect. Asset: System Station Assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735211 | 2026 Odourant Upgrades - MOIS Upgrades* | 2026 | 2033809.4038 | The expenditures in this portfolio include projects to upgrade odourant systems to ensure compliance to current codes, such as replacing old tanks and painting rusted containment pans and tank stands. Additionally, performance capability will be added by installing heat tracer lines, heated cabinets, improved tank valves and indoor regulator panels. This work will help to ensure safe, compliant and continuous odourization. This forecast will help mitigate the risk of tank rupture, frequent freeze off and nuisance odour calls. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735213 | 2027 Odourant Upgrades - MOIS Upgrades* | 2027 | 2165711.6578 | The expenditures in this portfolio include projects to upgrade odourant systems to ensure compliance to current codes, such as replacing old tanks and painting rusted containment pans and tank stands. Additionally, performance capability will be added by installing heat tracer lines, heated cabinets, improved tank valves and indoor regulator panels. This work will help to ensure safe, compliant and continuous odourization. This forecast will help mitigate the risk of tank rupture, frequent freeze off and nuisance odour calls. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735214 | 2028 Odourant Upgrades - MOIS Upgrades* | 2028 | 2147658.5806 | The expenditures in this portfolio include projects to upgrade odourant systems to ensure compliance to current codes, such as replacing old tanks and painting rusted containment pans and tank stands. Additionally, performance capability will be added by installing heat tracer lines, heated cabinets, improved tank valves and indoor regulator panels. This work will help to ensure safe, compliant and continuous odourization. This forecast will help mitigate the risk of tank rupture, frequent freeze off and nuisance odour calls. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735215 | 2029 Odourant Upgrades - MOIS Upgrades* | 2029 | 2132280.8735 | The expenditures in this portfolio include projects to upgrade odourant systems to ensure compliance to current codes, such as replacing old tanks and painting rusted containment pans and tank stands. Additionally, performance capability will be added by installing heat tracer lines, heated cabinets, improved tank valves and indoor regulator panels. This work will help to ensure safe, compliant and continuous odourization. This forecast will help mitigate the risk of tank rupture, frequent freeze off and nuisance odour calls. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735216 | 2030 Odourant Upgrades - MOIS Upgrades* | 2030 | 2207857.8418 | The expenditures in this portfolio include projects to upgrade odourant systems to ensure compliance to current codes, such as replacing old tanks and painting rusted containment pans and tank stands. Additionally, performance capability will be added by installing heat tracer lines, heated cabinets, improved tank valves and indoor regulator panels. This work will help to ensure safe, compliant and continuous odourization. This forecast will help mitigate the risk of tank rupture, frequent freeze off and nuisance odour calls. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735217 | 2031 Odourant Upgrades - MOIS Upgrades* | 2031 | 2183714.1163 | The expenditures in this portfolio include projects to upgrade odourant systems to ensure compliance to current codes, such as replacing old tanks and painting rusted containment pans and tank stands. Additionally, performance capability will be added by installing heat tracer lines, heated cabinets, improved tank valves and indoor regulator panels. This work will help to ensure safe, compliant and continuous odourization. This forecast will help mitigate the risk of tank rupture, frequent freeze off and nuisance odour calls. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Distribution Stations | Pass |  | 735218 | 2032 Odourant Upgrades - MOIS Upgrades* | 2032 | 2119281.1814 | The expenditures in this portfolio include projects to upgrade odourant systems to ensure compliance to current codes, such as replacing old tanks and painting rusted containment pans and tank stands. Additionally, performance capability will be added by installing heat tracer lines, heated cabinets, improved tank valves and indoor regulator panels. This work will help to ensure safe, compliant and continuous odourization. This forecast will help mitigate the risk of tank rupture, frequent freeze off and nuisance odour calls. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Growth | Pass |  | 49179 | SRP_Southeast_Port Rowan_Lakeshore Rd_Reinforcement_NPS6_2000m_860kPa | 2024 | 1473860.9821 | System Reinforcement - Replace existing 3-inch 860 Maximum Operating Pressure (MOP) line with 6-inch in Phase 1. Move forward from 2026 to 2024 per 2021 System Reinforcement Plan (SRP) refresh. | Planned
Head Office Support | Div_54 - Head Office Support | Utilization | Fail | Dollar threshold | 102816 | 2023 - LAB FACILITIES UPGRADE | 2023 | 99642.4231
Head Office Support | Div_54 - Head Office Support | Utilization | Fail | Dollar threshold | 102817 | 2024 - LAB FACILITIES UPGRADE | 2024 | 102529.4632
Head Office Support | Div_54 - Head Office Support | Utilization | Fail | Dollar threshold | 102818 | 2025 - LAB FACILITIES UPGRADE | 2025 | 103316.0163
Head Office Support | Div_54 - Head Office Support | Utilization | Fail | Dollar threshold | 736034 | Commercial / Industrial LPDMS* | 2021 | 1160366.9717
Head Office Support | Div_54 - Head Office Support | Utilization | Pass |  | 48500 | SMC-Meter & Regulator Additions South* |  | 41354890.587 | Meter & Reg Install- New | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Utilization | Pass |  | 48501 | SMC_Meter & Regulator Replacements - South* | 2020 | 183636762.2541 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Utilization | Pass |  | 48679 | SMC-Meter & Regulator Additions North* |  | 11327082.0452 | Meter & Reg Install- New | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Utilization | Pass |  | 48680 | SMC_Meter & Regulator Replacements - North* | 2020 | 48473262.177 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Utilization | Pass |  | 502199 | Farm Tap Program (LUG)* | 2021 | 3093331.9251 | The Farm Tap regulator purpose is to reduce pressure from XHP/HP to meet the design criteria for the downstream 2nd cut regulator. A malfunctioning Farm Tap regulator has the potential to create downstream hazards. A failure of the regulator set could potentially cause a higher than acceptable pressure entering the customer’s premise. This over-pressure can result in downstream customer appliances failing, loss of containment inside the premise, fire, and explosion. The Farm Tap consists of the inlet/outlet riser, a regulator, and a relief. The condition of the Farm Tap population is largely unknown. As they are installed away from the premise and near the property line, they are exposed to more elements originating from the roadway. Their placement can also make them susceptible to third party damage from maintenance equipment and vehicles. Farm Taps have not been part of pro-active inspection programs. They historically have not been included in MXGI regulator exchanges. 2021 DIMP survey for LUG - potential for some immediates | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Utilization | Pass |  | 738584 | SMC_Meter & Regulator Replacements - North* |  | 14218451.9895 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Utilization | Pass |  | 738583 | SMC_Meter & Regulator Replacements - South* |  | 53923496.49 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Transmission Pipe & Underground Storage | Fail | Timing | 102546 | Class Location Replacement Program 2023 - S&T Assets* | 2023 | 1245530.2386
Head Office Support | Div_54 - Head Office Support | Transmission Pipe & Underground Storage | Fail | Timing | 102552 | Class Location Replacement Program 2024 - S&T Assets* | 2024 | 2643337.7228
Head Office Support | Div_54 - Head Office Support | Transmission Pipe & Underground Storage | Fail | Timing | 102553 | Class Location Replacement Program 2025 - S&T Assets* | 2025 | 4035781.9395
Head Office Support | Div_54 - Head Office Support | Transmission Pipe & Underground Storage | Pass |  | 102554 | Class Location Replacement Program 2026 - S&T Assets* | 2034 | 5457245.1603 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Transmission Pipe & Underground Storage | Pass |  | 102555 | Class Location Replacement Program 2027 - S&T Assets* | 2035 | 7285650.5211 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Transmission Pipe & Underground Storage | Pass |  | 102556 | Class Location Replacement Program 2028 - S&T Assets* | 2036 | 7224918.3315 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Transmission Pipe & Underground Storage | Pass |  | 102557 | Class Location Replacement Program 2029 - S&T Assets* | 2037 | 7173186.3297 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Transmission Pipe & Underground Storage | Pass |  | 102558 | Class Location Replacement Program 2030 - S&T Assets* | 2038 | 7427434.1082 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Transmission Pipe & Underground Storage | Pass |  | 733985 | Class Location Replacement Program 2031 - S&T Assets* | 2039 | 7346212.425 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office Support | Div_54 - Head Office Support | Transmission Pipe & Underground Storage | Pass |  | 733986 | Class Location Replacement Program 2032 - S&T Assets* | 2040 | 7129454.186 | General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30 per cent SMYS, unless previously designed, tested, operated, and maintained for a Class 4 location. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development which occurs in close proximity to EGI’s pipelines typically triggers class location changes. An annual budget is required for EGI’s pipeline system in order to meet the current standard requirements. Remediation includes pressure testing, installation of valves, remediating depth of cover issues, and pipeline replacement. This work ensures EGI is compliant and fosters the safety of the public and EGI’s pipeline system. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 00 - Head Office | Distribution Pipe | Pass |  | 736833 | TIMP Geohazard Mitigation (LUG)* |  | 24533406.6845 | General: The Geohazard Mitigation program has been designed to comply with all applicable codes and standards. The program consists of the assessment and maintenance of the integrity of EGI's pipeline systems which may be impacted by geohazards. The assessment ensures asset's continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 00 - Head Office | Distribution Pipe | Pass |  | 736835 | TIMP Geohazard Mitigation (LEGD)* |  | 6133885.3993 | General: The Geohazard Mitigation Program has been designed to comply with all applicable codes and standards. The program consists of the assessment and maintenance of the integrity of EGI's pipeline systems which may be impacted by geohazards. The assessment ensures asset's continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% SMYS. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 00 - Head Office | Distribution Pipe | Pass |  | 736844 | Independent Asset Integrity Review (IAIR) - (LUG)* |  | 81727581.9974 | Dynamic Risk completed an independent review of TIMP to establish uncertainty levels in the fitness-for-service conclusions for all TIMP assets. This first phase of the project was completed last year. TIMP is currently developing plans to mitigate high and moderate uncertainties in the fitness-for-service conclusions by leveraging existing integrity activities and potentially introducing new ones. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 00 - Head Office | Distribution Pipe | Pass |  | 736845 | Independent Asset Integrity Review (IAIR) - (LEG)* |  | 8863546.2158 | Dynamic Risk completed an independent review of TIMP to establish uncertainty levels in the fitness-for-service conclusions for all TIMP assets. This first phase of the project was completed last year. TIMP is currently developing plans to mitigate high and moderate uncertainties in the fitness-for-service conclusions by leveraging existing integrity activities and potentially introducing new ones. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 00 - Head Office | Distribution Stations | Fail | Dollar threshold | 17404 | NGV Rental VRA's - (2026-2032) | 2028 | 1346723.2401
Head Office/All | 00 - Head Office | Distribution Stations | Pass |  | 2368 | NGV Rental VRA's | 2025 | 491107.908 | Issue/concern: Individual customers and arenas can achieve fuel cost savings, fuel handling savings, and reduced emission benefits by operating their cleaning machines, forklift trucks, and individual light-duty vehicles on natural gas versus propane or gasoline. This presents an opportunity to grow EGI’s natural gas vehicle (NGV) rental refueling business and promotes the use of natural gas to customers as an alternate source for fueling cleaning machines, forklift trucks, and individual light-duty vehicles at a lower cost, reducing fuel handling cost with lower emissions. By providing NGV Vehicle Refueling Appliance (VRA) equipment to customers on a rental basis, EGI can achieve growth in the marketplace, while fully recovering costs. Assets: There are currently over 200 VRA customers that EGI is successfully servicing, including City of Toronto, City of Ottawa, other small city arenas and some private customers. Related Program (if applicable): Not applicable. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 00 - Head Office | Distribution Stations | Pass |  | 503415 | Bellville Yard Station | 2024 | 1922427.4348 | The Enbridge fleet continues to achieve fuel cost savings and reduced emission benefits by operating their light-duty vehicles on natural gas versus gasoline. | Completed | Fail | See investment description, IRPAs not applicable for CNG
Head Office/All | 00 - Head Office | Transmission Pipe & Underground Storage | Pass |  | 736880 | Independent Asset Integrity Review (IAIR) - EGDTP* |  | 13295319.3237 | Dynamic Risk completed an independent review of TIMP to establish uncertainty levels in the fitness-for-service conclusions for all TIMP assets. This first phase of the project was completed last year. TIMP is currently developing plans to mitigate high and moderate uncertainties in the fitness-for-service conclusions by leveraging existing integrity activities and potentially introducing new ones. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 00 - Head Office | Transmission Pipe & Underground Storage | Pass |  | 736881 | Independent Asset Integrity Review (IAIR) - UGTP* |  | 19170667.3821 | Dynamic Risk completed an independent review of TIMP to establish uncertainty levels in the fitness-for-service conclusions for all TIMP assets. This first phase of the project was completed last year. TIMP is currently developing plans to mitigate high and moderate uncertainties in the fitness-for-service conclusions by leveraging existing integrity activities and potentially introducing new ones. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Fail | Dollar threshold | 102428 | Relocation Program - Transit* | 2020 | -46507006.89
Head Office/All | 01 - All | Distribution Pipe | Fail | Dollar threshold | 102760 | 2025 Integrity Dig Program* |  | 775040.8749
Head Office/All | 01 - All | Distribution Pipe | Fail | Timing | 102759 | 2024 Integrity Dig Program* | 2024 | 6406884.2266
Head Office/All | 01 - All | Distribution Pipe | Fail | Timing | 736439 | General Mains Replacement Blanket - All Regions* | 2020 | 47983533.337
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 6124 | Depth of Cover Mitigation Program* |  | 6088895.2372 | Mitigation of depth of cover sites on >30% SMYS lines that are out of compliance with CSA Z662 & TSSA requirements. Some of the known sites are discovered during the annual Depth of Cover Survey, while others are reported by company crews when performing maintenance work or by 3rd party . At this time the specific work scope of each year is not defined and this is a blanket program as a placeholder in the budget. The mitigation work will include the construction costs from sites identified and planned for the current year, as well as work on sites that are newly identified. Scope of work can vary from small remediation projects to add fill, concrete or bank stabilization, to short replacement of pipe. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 100225 | Rectifier Program - All Areas* |  | 3674496.4269 | Issue/Concern: This business case is created to group all Anode Blanket projects for all seven operations areas into one program business case to simplify the Risk Assessment process. Financial tracking will be done on the individual Blanket Anode project to provide financial reporting per area. Justification: The Corrosion Department conducts pipe to soil readings each year on our steel pipelines. When they identify a corrosion area which has fallen below our minimum specifications, they process an order for a anode installation which is completed. The capital request is for 12 months. Engineering has confirmed the Anode Installation as a compliance project. The Corrosion Prevention Program consists of the annual anode replacement to ensure the steel main system is receiving sufficient cathodic protection. The Program utilizes pipe-to-soil survey results to determine which steel main networks require additional or replacement anodes to improve the level of cathodic protection. In addition to active steel mains, the Corrosion Prevention Programs also cover the corrosion control on steel casings. Assets: Steel Mains Related Programs/Business Cases: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 100444 | Integrity Retrofit Program >30% SMYS* |  | 21792827.2377 | General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 102758 | 2023 Integrity Dig Program* |  | 1995058.2512 | 2023 forecast: 8 ILI digs estimated based on previous years inspection plan. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 102761 | 2026 Integrity Dig Program* |  | 3661501.2184 | Forecast: Forecast not provided for 2026-3030; average of 2020-2025 used as a placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 102762 | 2027 Integrity Dig Program* |  | 3890911.3525 | Forecast: Forecast not provided for 2026-3030; average of 2020-2025 used as a placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 102763 | 2028 Integrity Dig Program* |  | 3857753.0514 | Forecast: Forecast not provided for 2026-3030; average of 2020-2025 used as a placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 102764 | 2029 Integrity Dig Program* |  | 3835204.3376 | Forecast: Forecast not provided for 2026-2030; average of 2020-2025 used as a placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 102765 | 2030 Integrity Dig Program* |  | 3950197.8871 | Forecast: Forecast not provided for 2026- 2030; average of 2020-2025 used as a placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 502013 | Relocation Program - Engineering Construction* | 2020 | 22737339.5995 | General: Projects in the relocation category are capital expenditures required to replace or relocate segments of pipeline in order to accommodate municipal infrastructure work. The cost sharing for this work is managed through the Franchise Agreements established with municipalities. A consultative approach is used between the municipality and EGI to avoid conflicts with municipal infrastructure early in the planning stage. If a conflict is unavoidable, pipeline assets are typically relocated or replaced. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 503432 | Bridge Crossing Painting Program* |  | 2687788.5552 | Issue/Concern/Opportunity: Bridge crossing inspection results in different levels of action which can include replacement, recoating, or hanger repair/replacement work. This program is for recoating work and hanger repair. Justification: The integrated Corrosion Operating Standard ST-17-B13A-DDA9 was released November 25, 2022 and requires the following surveys: Annual visual and 5-year detailed. The standard outlines the following time frames: • Bridge crossing – replace per Engineering assessment per project plan • Bridge crossing – replace expansion joint / Ins flange within 24 month • Bridge crossing – paint pipe / repair hangers / replace casing end seal within 12 months. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 733993 | 2031 Integrity Dig Program* |  | 3905460.8698 | Forecast: Forecast not provided for 2026- 2030; average of 2020-2025 used as a placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Pipe | Pass |  | 733994 | 2032 Integrity Dig Program* |  | 3792071.7063 | Forecast: Forecast not provided for 2026- 2030; average of 2020-2025 used as a placeholder. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 9842 | 2023 Header stations rebuilds* | 2023 | 1152146.1689
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 9843 | 2024 Header stations rebuilds* | 2024 | 1183992.2146
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 9844 | 2023 Sales stations rebuilds* | 2023 | 1246911.4382
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 10300 | 2025 Header stations rebuilds* | 2025 | 1193563.027
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 10301 | 2026 Header stations rebuilds* | 2026 | 1208295.4193
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 10303 | 2024 Sales stations rebuilds* | 2024 | 1281376.8556
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 10304 | 2025 Sales stations rebuilds* | 2025 | 1291734.8777
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 10361 | 2026 Sales stations rebuilds* | 2026 | 1307679.0253
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 10362 | 2027 Sales stations rebuilds* | 2027 | 1389611.1973
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 10541 | 2027 Header stations rebuilds* | 2027 | 1284000.7463
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 16432 | 2028 Header stations rebuilds* | 2028 | 1273058.507
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 16433 | 2028 Sales stations rebuilds* | 2028 | 1377768.9469
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 101554 | 2029 Header stations rebuild* | 2029 | 1265617.4314
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 101555 | 2030 Header stations rebuilds* | 2030 | 1303565.3027
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 101558 | 2029 Sales stations rebuilds* | 2029 | 1369715.8349
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 101559 | 2030 Sales stations rebuilds* | 2030 | 1410784.9597
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 734297 | 2031 Sales stations rebuilds* | 2031 | 1394807.4535
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 734298 | 2032 Sales stations rebuilds* | 2032 | 1354311.3237
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 734299 | 2031 Header stations rebuilds* | 2031 | 1288802.087
Head Office/All | 01 - All | Distribution Stations | Fail | Dollar threshold | 734300 | 2032 Header stations rebuilds* | 2032 | 1251383.6631
Head Office/All | 01 - All | Distribution Stations | Fail | Timing | 9845 | 2024 Telemetry* | 2024 | 1573530.7787
Head Office/All | 01 - All | Distribution Stations | Fail | Timing | 9846 | 2023 Telemetry* | 2023 | 1745676.0633
Head Office/All | 01 - All | Distribution Stations | Fail | Timing | 9964 | 2025 Telemetry* | 2025 | 1623142.3779
Head Office/All | 01 - All | Distribution Stations | Fail | Timing | 10296 | 2024 District Station Rebuilds Program* | 2024 | 4988397.536
Head Office/All | 01 - All | Distribution Stations | Fail | Timing | 10297 | 2025 District Station Rebuilds Program* | 2025 | 6306185.0861
Head Office/All | 01 - All | Distribution Stations | Pass |  | 9552 | NGT Existing customer Maintenance Capital - (Until 2026)* |  | 1585984.0199 | Maintenance capital for refueling stations for external customer stations only Issue/concern: EGI fleet operators can continue to achieve fuel cost savings and reduced emission benefits by investing in the wellbeing of the NGV station. This can be achieved by adopting and continuously upgrading their NGV equipment as part of the maintenance strategy. By upgrading major NGV equipment, EGI can extend the life cycle of the equipment, resulting in a more cost-effective way of operating the NGV stations. Assets: There are a number of current NGV stations EGI maintains | Completed | Fail | See investment description, IRPAs not applicable for CNG
Head Office/All | 01 - All | Distribution Stations | Pass |  | 9553 | NGT Maintenance Capital for company/fleet NG refueling stations (2021 to 2032)* |  | 4284492.3626 | Maintenance capital for refueling stations for EGD NGT Fueling stations only Issue/concern: The EGD Fleet department can achieve fuel cost savings and reduced emission benefits by operating the 800-plus fleet vehicles on natural gas versus diesel or gasoline. This presents an opportunity for the EGD Fleet Department to realize fuel savings and promotes the use of natural gas to other fleet operators as an alternate source for fueling vehicles at a lower cost with lower emissions. By demonstrating the use of natural gas, EGD can achieve growth in the marketplace, while realizing fuel savings. Assets: EGD currently operates 19 Natural Gas Vehicle (NGV) fueling stations on company yards. The stations includes; Arnprior Yard, Barrie Yard, Beamsville Yard, Thorold Office, Brampton, Brockvill yard, Ottawa Office, Kelfield yard, Kennedy Road Yard, Midland Gate Station, Oshawa Office, Port Colbourne Yard, Peterborough yard, Shelburne Gate Station, South Merivall, Station B, Stayner Gate Station, Enbridge Training Centre, and the VPC Office. In addition, EGD will installing two new NGT stations to fuel recently converted vehicles and dedicated light duty trucks. These two new stations (Tecumseh Storage facility and Tallman Truck Center (Kemptville)) will also, need to be maintained. Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable for CNG
Head Office/All | 01 - All | Distribution Stations | Pass |  | 9965 | 2026 Telemetry* | 2026 | 1942806.9849 | Telemetry systems are required to monitor and control our pipeline system. Applicable Codes: Z662, Sec 11.26.4 provides code requirement for safe and reliable communication. The Telemetry system includes communication paths from the instrumentation at our stations to Gas Control and it allows them to monitor EGI Distribution conditions. Gas flow: For gas supply to meet nominations Leak detection: Indicated by large pressure drops Overpressure protection and Pressure Control: Condition monitoring equipment by gas control ensures gas delivery to the customers in a controlled and safe manner. Included in this program are upgrades to the Telemetry network that include: 1)Cyber Security - Ongoing upgrades to Scada system to ensure compliance with EI Cyber security standards and proposed CSA code 2)Legacy equipment - 3330 Bristol units(10/yr) must be replaced with Control Wave Micro units 3) RTU Programming Manual - Development of manual detailing programming standards for design, security and expansion 4)SCADA - Development of maintenance layer of Scada to allow site reporting of gas consumption for boiler gas, odourant pump strokes and usage tracking, boiler diagnostics, remote engineering and automation of gate/feeder stations 5)Broadband Communication - Development of broadband links between major stations to support security (i.e. intrusion detection) | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 9966 | 2027 Telemetry* | 2027 | 2105823.7842 | Telemetry systems are required to monitor and control our pipeline system. Applicable Codes: Z662, Sec 11.26.4 provides code requirement for safe and reliable communication. The Telemetry system includes communication paths from the instrumentation at our stations to Gas Control and it allows them to monitor EGI Distribution conditions. Gas flow: For gas supply to meet nominations Leak detection: Indicated by large pressure drops Overpressure protection and Pressure Control: Condition monitoring equipment by gas control ensures gas delivery to the customers in a controlled and safe manner. Included in this program are upgrades to the Telemetry network that include: 1)Cyber Security - Ongoing upgrades to Scada system to ensure compliance with EI Cyber security standards and proposed CSA code 2)Legacy equipment - 3330 Bristol units(10/yr) must be replaced with Control Wave Micro units 3) RTU Programming Manual - Development of manual detailing programming standards for design, security and expansion 4)SCADA - Development of maintenance layer of Scada to allow site reporting of gas consumption for boiler gas, odourant pump strokes and usage tracking, boiler diagnostics, remote engineering and automation of gate/feeder stations 5)Broadband Communication - Development of broadband links between major stations to support security (i.e. intrusion detection) | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 10298 | 2026 District Station Rebuilds Program* | 2026 | 7942642.3245 | Issue/Concern: The stations identified in this business case fall into one of the following categories: Below-ground box replacements: Removal of below-ground stations improves life cycle cost of stations due to accelerated corrosion related to salting and flooding, increased O&M costs related to increased paint frequency, and the requirement for two at a box when work is performed. An additional and very important benefit to the elimination of below-ground boxes is the improvement of worker health and safety by eliminating the need to handle potentially contaminated water, and non-ergonomic work conditions. Obsolete Regulators: The criteria for this category is that there are no spare parts available, or parts are no longer approved for use on new installations, or a combination of poor performance and manufacturer availability. Low Pressure Districts: The failure of a low pressure district can have disastrous downstream impacts in the event of over-pressure protection failure. The outlets of these stations feed customers who may not have individual regulators at their meter sets. This additional line of defense is not present to protect customer piping. Double Boot-style Regulators: Stations with both operator and monitor boot-style regulators have a common failure mechanism as a result of debris in the gas stream. Replacement of one boot-style regulator with a non-boot regulator reduces the vulnerability of failure. Increased Capacity: Stations that are operating over designed capacity due to system growth are targeted for replacement to maintain gas supply. Loss of Containment: Station experiencing loss of containment (leaks) and high maintenance calls to repair equipment are also identified for replacement. Asset: District station assets. Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 10299 | 2027 District Station Rebuilds Program* | 2027 | 8189676.3705 | Issue/Concern: The stations identified in this business case fall into one of the following categories: Below-ground box replacements: Removal of below-ground stations improves life cycle cost of stations due to accelerated corrosion related to salting and flooding, increased O&M costs related to increased paint frequency, and the requirement for two at a box when work is performed. An additional and very important benefit to the elimination of below-ground boxes is the improvement of worker health and safety by eliminating the need to handle potentially contaminated water, and non-ergonomic work conditions. Obsolete Regulators: The criteria for this category is that there are no spare parts available, or parts are no longer approved for use on new installations, or a combination of poor performance and manufacturer availability. Low Pressure Districts: The failure of a low pressure district can have disastrous downstream impacts in the event of over-pressure protection failure. The outlets of these stations feed customers who may not have individual regulators at their meter sets. This additional line of defense is not present to protect customer piping. Double Boot-style Regulators: Stations with both operator and monitor boot-style regulators have a common failure mechanism as a result of debris in the gas stream. Replacement of one boot-style regulator with a non-boot regulator reduces the vulnerability of failure. Increased Capacity: Stations that are operating over designed capacity due to system growth are targeted for replacement to maintain gas supply. Loss of Containment: Station experiencing loss of containment (leaks) and high maintenance calls to repair equipment are also identified for replacement. Asset: District station assets. Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 16430 | 2028 Telemetry* | 2028 | 2129635.5376 | Telemetry systems are required to monitor and control our pipeline system. Applicable Codes: Z662, Sec 11.26.4 provides code requirement for safe and reliable communication. The Telemetry system includes communication paths from the instrumentation at our stations to Gas Control and it allows them to monitor EGI Distribution conditions. Gas flow: For gas supply to meet nominations Leak detection: Indicated by large pressure drops Overpressure protection and Pressure Control: Condition monitoring equipment by gas control ensures gas delivery to the customers in a controlled and safe manner. Included in this program are upgrades to the Telemetry network that include: 1)Cyber Security - Ongoing upgrades to Scada system to ensure compliance with EI Cyber security standards and proposed CSA code 2)Legacy equipment - 3330 Bristol units(10/yr) must be replaced with Control Wave Micro units 3) RTU Programming Manual - Development of manual detailing programming standards for design, security and expansion 4)SCADA - Development of maintenance layer of Scada to allow site reporting of gas consumption for boiler gas, odourant pump strokes and usage tracking, boiler diagnostics, remote engineering and automation of gate/feeder stations 5)Broadband Communication - Development of broadband links between major stations to support security (i.e. intrusion detection) | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 16434 | 2028 District Station Rebuilds Program* | 2028 | 4372570.1961 | Issue/Concern: The stations identified in this business case fall into one of the following categories: Below-ground box replacements: Removal of below-ground stations improves life cycle cost of stations due to accelerated corrosion related to salting and flooding, increased O&M costs related to increased paint frequency, and the requirement for two at a box when work is performed. An additional and very important benefit to the elimination of below-ground boxes is the improvement of worker health and safety by eliminating the need to handle potentially contaminated water, and non-ergonomic work conditions. Obsolete Regulators: The criteria for this category is that there are no spare parts available, or parts are no longer approved for use on new installations, or a combination of poor performance and manufacturer availability. Low Pressure Districts: The failure of a low pressure district can have disastrous downstream impacts in the event of over-pressure protection failure. The outlets of these stations feed customers who may not have individual regulators at their meter sets. This additional line of defense is not present to protect customer piping. Double Boot-style Regulators: Stations with both operator and monitor boot-style regulators have a common failure mechanism as a result of debris in the gas stream. Replacement of one boot-style regulator with a non-boot regulator reduces the vulnerability of failure. Increased Capacity: Stations that are operating over designed capacity due to system growth are targeted for replacement to maintain gas supply. Loss of Containment: Station experiencing loss of containment (leaks) and high maintenance calls to repair equipment are also identified for replacement. Asset: District station assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 101552 | 2029 Telemetry* | 2029 | 2159531.5018 | Telemetry systems are required to monitor and control our pipeline system. Applicable Codes: Z662, Sec 11.26.4 provides code requirement for safe and reliable communication. The Telemetry system includes communication paths from the instrumentation at our stations to Gas Control and it allows them to monitor EGI Distribution conditions. Gas flow: For gas supply to meet nominations Leak detection: Indicated by large pressure drops Overpressure protection and Pressure Control: Condition monitoring equipment by gas control ensures gas delivery to the customers in a controlled and safe manner. Included in this program are upgrades to the Telemetry network that include: 1)Cyber Security - Ongoing upgrades to Scada system to ensure compliance with EI Cyber security standards and proposed CSA code 2)Legacy equipment - 3330 Bristol units(10/yr) must be replaced with Control Wave Micro units 3) RTU Programming Manual - Development of manual detailing programming standards for design, security and expansion 4)SCADA - Development of maintenance layer of Scada to allow site reporting of gas consumption for boiler gas, odourant pump strokes and usage tracking, boiler diagnostics, remote engineering and automation of gate/feeder stations 5)Broadband Communication - Development of broadband links between major stations to support security (i.e. intrusion detection) | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 101553 | 2030 Telemetry* | 2030 | 2268767.842 | Telemetry systems are required to monitor and control our pipeline system. Applicable Codes: Z662, Sec 11.26.4 provides code requirement for safe and reliable communication. The Telemetry system includes communication paths from the instrumentation at our stations to Gas Control and it allows them to monitor EGI Distribution conditions. Gas flow: For gas supply to meet nominations Leak detection: Indicated by large pressure drops Overpressure protection and Pressure Control: Condition monitoring equipment by gas control ensures gas delivery to the customers in a controlled and safe manner. Included in this program are upgrades to the Telemetry network that include: 1)Cyber Security - Ongoing upgrades to Scada system to ensure compliance with EI Cyber security standards and proposed CSA code 2)Legacy equipment - 3330 Bristol units(10/yr) must be replaced with Control Wave Micro units 3) RTU Programming Manual - Development of manual detailing programming standards for design, security and expansion 4)SCADA - Development of maintenance layer of Scada to allow site reporting of gas consumption for boiler gas, odourant pump strokes and usage tracking, boiler diagnostics, remote engineering and automation of gate/feeder stations 5)Broadband Communication - Development of broadband links between major stations to support security (i.e. intrusion detection) | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 101556 | 2029 District Station Rebuilds Program* | 2029 | 9588010.8441 | Issue/Concern: The stations identified in this business case fall into one of the following categories: Below-ground box replacements: Removal of below-ground stations improves life cycle cost of stations due to accelerated corrosion related to salting and flooding, increased O&M costs related to increased paint frequency, and the requirement for two at a box when work is performed. An additional and very important benefit to the elimination of below-ground boxes is the improvement of worker health and safety by eliminating the need to handle potentially contaminated water, and non-ergonomic work conditions. Obsolete Regulators: The criteria for this category is that there are no spare parts available, or parts are no longer approved for use on new installations, or a combination of poor performance and manufacturer availability. Low Pressure Districts: The failure of a low pressure district can have disastrous downstream impacts in the event of over-pressure protection failure. The outlets of these stations feed customers who may not have individual regulators at their meter sets. This additional line of defense is not present to protect customer piping. Double Boot-style Regulators: Stations with both operator and monitor boot-style regulators have a common failure mechanism as a result of debris in the gas stream. Replacement of one boot-style regulator with a non-boot regulator reduces the vulnerability of failure. Increased Capacity: Stations that are operating over designed capacity due to system growth are targeted for replacement to maintain gas supply. Loss of Containment: Station experiencing loss of containment (leaks) and high maintenance calls to repair equipment are also identified for replacement. Asset: District station assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 101557 | 2030 District Station Rebuilds Program* | 2030 | 9875494.7177 | Issue/Concern: The stations identified in this business case fall into one of the following categories: Below-ground box replacements: Removal of below-ground stations improves life cycle cost of stations due to accelerated corrosion related to salting and flooding, increased O&M costs related to increased paint frequency, and the requirement for two at a box when work is performed. An additional and very important benefit to the elimination of below-ground boxes is the improvement of worker health and safety by eliminating the need to handle potentially contaminated water, and non-ergonomic work conditions. Obsolete Regulators: The criteria for this category is that there are no spare parts available, or parts are no longer approved for use on new installations, or a combination of poor performance and manufacturer availability. Low Pressure Districts: The failure of a low pressure district can have disastrous downstream impacts in the event of over-pressure protection failure. The outlets of these stations feed customers who may not have individual regulators at their meter sets. This additional line of defense is not present to protect customer piping. Double Boot-style Regulators: Stations with both operator and monitor boot-style regulators have a common failure mechanism as a result of debris in the gas stream. Replacement of one boot-style regulator with a non-boot regulator reduces the vulnerability of failure. Increased Capacity: Stations that are operating over designed capacity due to system growth are targeted for replacement to maintain gas supply. Loss of Containment: Station experiencing loss of containment (leaks) and high maintenance calls to repair equipment are also identified for replacement. Asset: District station assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 501126 | FIMP Station Assessment Program* |  | 15572654.2186 | Issue/Concern/Opportunity: FIMP assesses stations against threats that are listed in the EGI Hazard and Risk Common Register Risk Register to identify susceptibility to identified risks and determine mitigation strategies for individual sites, ensuring that risk is managed to the lowest practical levels. The strategy for the FIMP program is to perform inspections using with approved technologies used at EGI or other utilities for similar asset types. These inspections will assess the condition of existing station assets and will detect any concerns or issues to help determine the likelihood and consequence of failure of individual components and evaluate the risk. This strategy will allow for targeted replacement and will extend the useful life of assets by identifying condition issues prior to the occurrence of an incident. When analysis indicates that ongoing repair costs are likely to exceed capital requirements to replace the asset, the mitigation strategy is evaluated to ensure that risk is managed to the lowest practicable level. Assets: FIMP DS Stations Related Investments: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 734294 | 2031 Telemetry* | 2031 | 2287934.9279 | Telemetry systems are required to monitor and control our pipeline system. Applicable Codes: Z662, Sec 11.26.4 provides code requirement for safe and reliable communication. The Telemetry system includes communication paths from the instrumentation at our stations to Gas Control and it allows them to monitor EGI Distribution conditions. Gas flow: For gas supply to meet nominations Leak detection: Indicated by large pressure drops Overpressure protection and Pressure Control: Condition monitoring equipment by gas control ensures gas delivery to the customers in a controlled and safe manner. Included in this program are upgrades to the Telemetry network that include: 1)Cyber Security - Ongoing upgrades to Scada system to ensure compliance with EI Cyber security standards and proposed CSA code 2)Legacy equipment - 3330 Bristol units(10/yr) must be replaced with Control Wave Micro units 3) RTU Programming Manual - Development of manual detailing programming standards for design, security and expansion 4)SCADA - Development of maintenance layer of Scada to allow site reporting of gas consumption for boiler gas, odourant pump strokes and usage tracking, boiler diagnostics, remote engineering and automation of gate/feeder stations 5)Broadband Communication - Development of broadband links between major stations to support security (i.e. intrusion detection) | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 734296 | 2032 Telemetry* | 2032 | 2274064.2312 | Telemetry systems are required to monitor and control our pipeline system. Applicable Codes: Z662, Sec 11.26.4 provides code requirement for safe and reliable communication. The Telemetry system includes communication paths from the instrumentation at our stations to Gas Control and it allows them to monitor EGI Distribution conditions. Gas flow: For gas supply to meet nominations Leak detection: Indicated by large pressure drops Overpressure protection and Pressure Control: Condition monitoring equipment by gas control ensures gas delivery to the customers in a controlled and safe manner. Included in this program are upgrades to the Telemetry network that include: 1)Cyber Security - Ongoing upgrades to Scada system to ensure compliance with EI Cyber security standards and proposed CSA code 2)Legacy equipment - 3330 Bristol units(10/yr) must be replaced with Control Wave Micro units 3) RTU Programming Manual - Development of manual detailing programming standards for design, security and expansion 4)SCADA - Development of maintenance layer of Scada to allow site reporting of gas consumption for boiler gas, odourant pump strokes and usage tracking, boiler diagnostics, remote engineering and automation of gate/feeder stations 5)Broadband Communication - Development of broadband links between major stations to support security (i.e. intrusion detection) | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 734307 | 2031 District Station Rebuilds Program* | 2031 | 9763652.1744 | Issue/Concern: The stations identified in this business case fall into one of the following categories: Below-ground box replacements: Removal of below-ground stations improves life cycle cost of stations due to accelerated corrosion related to salting and flooding, increased O&M costs related to increased paint frequency, and the requirement for two at a box when work is performed. An additional and very important benefit to the elimination of below-ground boxes is the improvement of worker health and safety by eliminating the need to handle potentially contaminated water, and non-ergonomic work conditions. Obsolete Regulators: The criteria for this category is that there are no spare parts available, or parts are no longer approved for use on new installations, or a combination of poor performance and manufacturer availability. Low Pressure Districts: The failure of a low pressure district can have disastrous downstream impacts in the event of over-pressure protection failure. The outlets of these stations feed customers who may not have individual regulators at their meter sets. This additional line of defense is not present to protect customer piping. Double Boot-style Regulators: Stations with both operator and monitor boot-style regulators have a common failure mechanism as a result of debris in the gas stream. Replacement of one boot-style regulator with a non-boot regulator reduces the vulnerability of failure. Increased Capacity: Stations that are operating over designed capacity due to system growth are targeted for replacement to maintain gas supply. Loss of Containment: Station experiencing loss of containment (leaks) and high maintenance calls to repair equipment are also identified for replacement. Asset: District station assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 734308 | 2032 District Station Rebuilds Program* | 2032 | 9480179.2657 | Issue/Concern: The stations identified in this business case fall into one of the following categories: Below-ground box replacements: Removal of below-ground stations improves life cycle cost of stations due to accelerated corrosion related to salting and flooding, increased O&M costs related to increased paint frequency, and the requirement for two at a box when work is performed. An additional and very important benefit to the elimination of below-ground boxes is the improvement of worker health and safety by eliminating the need to handle potentially contaminated water, and non-ergonomic work conditions. Obsolete Regulators: The criteria for this category is that there are no spare parts available, or parts are no longer approved for use on new installations, or a combination of poor performance and manufacturer availability. Low Pressure Districts: The failure of a low pressure district can have disastrous downstream impacts in the event of over-pressure protection failure. The outlets of these stations feed customers who may not have individual regulators at their meter sets. This additional line of defense is not present to protect customer piping. Double Boot-style Regulators: Stations with both operator and monitor boot-style regulators have a common failure mechanism as a result of debris in the gas stream. Replacement of one boot-style regulator with a non-boot regulator reduces the vulnerability of failure. Increased Capacity: Stations that are operating over designed capacity due to system growth are targeted for replacement to maintain gas supply. Loss of Containment: Station experiencing loss of containment (leaks) and high maintenance calls to repair equipment are also identified for replacement. Asset: District station assets Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Distribution Stations | Pass |  | 735117 | Stations with Auxiliary Equipment Replacement Program* | 2023 | 160911406.7616 | Issue/Concern: The replacement / renewal strategy for Stations with Auxiliary Equipment includes: Stations with Auxiliary Equipment Replacement strategy Compliance Remediation strategy Obsolete Heating Equipment strategy Odourization strategy Telemetry strategy Stations Retrofit strategy for Integrity pipe Stations Capital Upgrade program Facilities Integrity Management program Related Program: N/A | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 8543 | 2023 Commercial / Industrial LPDMS Program* | 2023 | 623455.7191
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 8544 | 2024 Commercial / Industrial LPDMS Program* | 2024 | 640688.4278
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 8545 | 2025 Commercial / Industrial LPDMS Program* | 2025 | 762123.5778
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 8546 | 2026 Commercial / Industrial LPDMS Program* | 2026 | 882683.342
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 8547 | 2027 Commercial / Industrial LPDMS Program* | 2027 | 1042208.398
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 8804 | 2023 Farm tap Program* | 2023 | 218209.5017
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 8805 | 2024 Farm tap Program* | 2024 | 224240.9497
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 8806 | 2025 Farm tap Program* | 2025 | 238970.9524
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 8807 | 2026 Farm tap Program* | 2026 | 274612.5953
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 8808 | 2027 Farm tap Program* | 2027 | 326558.6314
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 17966 | 2023 Assets Downstream of Bulk Meters* | 2023 | 253634.2058
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 17967 | 2025 Assets Downstream of Bulk Meters* | 2025 | 516693.8994
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 17968 | 2024 Assets Downstream of Bulk Meters* | 2024 | 260644.8149
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 17969 | 2026 Assets Downstream of Bulk Meters* | 2026 | 523071.5578
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 17970 | 2027 Assets Downstream of Bulk Meters* | 2027 | 555844.4233
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 17971 | 2028 Assets Downstream of Bulk Meters* | 2028 | 551107.5237
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 101968 | 2029 Assets Downstream of Bulk Meters* | 2029 | 547886.2792
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 101970 | 2028 Commercial / Industrial LPDMS Program* | 2028 | 1226214.3628
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 101971 | 2029 Commercial / Industrial LPDMS Program* | 2028 | 1219047.093
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 101972 | 2028 Farm tap Program* | 2028 | 378886.4604
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 101973 | 2029 Farm tap Program* | 2029 | 376671.8546
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 101974 | 2030 Farm tap Program* | 2030 | 1143973.5276
Head Office/All | 01 - All | Utilization | Fail | Dollar threshold | 101976 | 2030 Assets Downstream of Bulk Meters* | 2030 | 564313.9839
Head Office/All | 01 - All | Utilization | Pass |  | 19983 | Meter Purchases- MXGI's, MXG's, MXOT's* | 2027 | 313176431.1516 | Meters are used to determine the gas consumption input of customer billing. The replacement program for meters is mandated by Measurement Canada. The program includes: testing, repair, and replacement requirements of meters and instruments. All verified meters are approved by Measurement Canada with an issuance of a certificate which identifies that the meter complies with Electricity and Gas Specification S-EG-02. EGI must ensure all measurement devices remain in compliance for annual audits by Measurement Canada. Measurement Canada specifies tolerances under which the meter must operate in the field. EGD must demonstrate that all aspects of its meter sampling, maintenance, and replacement comply with these criteria in order to be accredited by Measurement Canada to be an “Authorized Service Provider” and adhere to Measurement Canada’s accreditation standard S-A-01. Meters may also require exchange for issues such as: damages, leaks, customer billing issues. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Utilization | Pass |  | 23228 | Meter Purchases- New Customer Additions* |  | 66275270.3469 | New meters are required for customer expansion projects. Meters are used to determine the gas consumption input of customer billing. | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Utilization | Pass |  | 101975 | 2030 Commercial / Industrial LPDMS Program* | 2030 | 3702314.3258 | These meter sets primarily serve commercial, industrial, and high density residential customers, typically with a meter > 400 series. They require proper operation to ensure gas does not exceed supply pressure. These sets consist of regulator(s), relief(s), riser, and meter. Failure of the regulation system has the potential to cause an over pressure to the customer’s supply line and appliances. Over-pressure can result in a loss of containment within the building making the event of ignition, fire, and explosion possible. The condition of these Commercial/Industrial LPDMS is largely unknown. They have not been part of pro-active inspection programs. A survey on a sample population indicated a number of potential issues including: - Old Regulators - Corrosion of piping and regulators - Non-Adherence to installation specifications | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | 01 - All | Utilization | Pass |  | 738580 | Meter Purchases- MXGI's, MXG's, MXOT's* |  | 115594242.8082 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Head Office/All | Div_54 - Head Office Support | Growth | Pass |  | 736972 | Hydrogen Fuel Heating Systems Feasibility Assessment | 2025 | 2334905.8348 | Issue/Concern/Opportunity: The feasibility study would explore two items: 1. Blending of hydrogen at gate and transmission regulating stations with the potential for on-site production of hydrogen. The study will quantify the maximum practical limits of hydrogen that can be blended into the natural gas fuel source of existing boiler systems. 2. Identifying the optimal site for a pilot project that will use an integrated pilot plant based on the availability of excess electricity and an opportunity to balance the demands on the electrical grid, availability of land for on-site hydrogen production and storage, and general operating conditions. EGI will review 35 of its roughly 165 boiler facilities as part of its mainline Dawn-Parkway gas transmission system and associated downstream distribution stations. These stations regulate EGI's transmission gas pressures to lower distribution pressures to safely feed the Ontario natural gas distribution area. Due to the cooling of gas while regulating a high-pressure cut from transmission to lower distribution pressures, heat is required to mitigate the possible damage of the cooling effect to ensure safe and reliable operations for customers. Additionally, the study will evaluate feasibility and alternatives for procurement or production of hydrogen as required to supply current boiler systems through Combined Heat & Power (CHP) applications where hydrogen will be used as the fuel source for boilers and the waste heat generated during hydrogen production is captured to maximize energy efficiency. Assets: EGI will review 35 of its roughly 165 boiler facilities as part of its mainline Dawn-Parkway gas transmission system and associated downstream distribution stations Related Program: 736973 - Hydrogen for Compression Facilities Feasibility Assessment | Completed | Fail | Hydrogen related projects are required as no IRPAs can replace the hydrogen feasibility assessments and hydrogen blending initiatives.
Head Office/All | Div_54 - Head Office Support | Growth | Pass |  | 736973 | Hydrogen for Compression Facilities Feasibility Assessment | 2025 | 1640842.1758 | Issue/Concern/Opportunity: The proposed feasibility study will: 1. Review the current compressor fleet, identify current and future projected fuel requirements, and evaluate the impact of varying hydrogen concentrations on turbine operations, emissions, safety and reliability. 2. Explore the requirements for partial conversion to hydrogen fuel with current equipment, with minor equipment upgrades, and with major upgrades to facilitate an envisioned 100% pure hydrogen fuel source. 3. Conduct a cost-benefit analysis to support a technically and economically feasible hydrogen transition. 4. Establish a strategy for hydrogen generation and conversion of the compressor fleet. 5. Refine company standards, policies and procedures to ensure continued safe, reliable and affordable operations. Assets: The feasibility study will evaluate the five major compressor sites along EGI’s Dawn-Parkway mainline transmission system: 1. Dawn Hub - Centred at 3332 Bentpath Line, Dawn-Euphemia, ON - 9 turbines totalling 189 MW 2. Lobo Compressor (14M-601) - 11025 Ivan Drive, Ilderton, ON - 5 turbines totalling 124 MW 3. Bright Compressor (16S-101) - 866139 Twp. Rd. #10, Bright, ON - 4 turbines totalling 115 MW 4. Parkway West Compressor (20Y-407) - 6699 8th Line, Milton, ON - 2 turbines totalling 66 MW 5. Parkway East Compressor (20Y-404) - 6626 9th Line, Missisauga, ON - 2 turbines totalling 50 MW Related Program: 736972 - Hydrogen Fuel Heating Systems Feasibility Assessment | Completed | Fail | Hydrogen related projects are required as no IRPAs can replace the hydrogen feasibility assessments and hydrogen blending initiatives.
Head Office/All | Div_54 - Head Office Support | Growth | Pass |  | 736974 | Hydrogen Blending Phase 2 | 2026 | 9050523.332 | The second part of the hydrogen blending project LCEP 1 . It will expand blended gas with hydrogen at 2% supplied to an additional 12400 customers approximately | Completed | Fail | Hydrogen related projects are required as no IRPAs can replace the hydrogen feasibility assessments and hydrogen blending initiatives.
Head Office/All | Div_54 - Head Office Support | Growth | Pass |  | 736975 | Enbridge Gas Distribution System Hydrogen Feasibility Study |  | 15523163.0341 | Comprehensive techno-economic feasibility study of blending hydrogen into Enbridge Gas Inc.'s (EGI) existing natural gas distribution and transmission network across Ontario. Evaluate the technical feasibility and maximum limits of blended hydrogen gas in existing networks,identify necessary retrofits or upgrades for varying concentrations of hydrogen, and develop a staged roadmap for transitioning Ontario's gas network to a low-carbon future in line with technical and economic barriers and opportunities. The assessment comprises the entirety of EGI's gas pipeline network in Ontario. By blending hydrogen at strategic locations across EGI's existing gas network, EGI aims to reduce the carbon intensity of its 3.8 million residential, commercial, institutional and industrial customers across over 500 communities in Ontario. | Completed | Fail | Hydrogen related projects are required as no IRPAs can replace the hydrogen feasibility assessments and hydrogen blending initiatives.
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 1268 | Thunder Bay Loop Retrofit |  | 809594.7373
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 48507 | THUN: Dist-Repl-Compy-Mains Municipal* | 2020 | 3221779.1488
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 48508 | THUN: Dist-Repl-Compy-Mains Leakage* | 2020 | 8390460.5093
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 48509 | THUN: Dist-Repl-Compy-Services* | 2020 | 3035772.9327
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 48511 | THUN: Land Rights-Replacements | 2023 | 3736.5909
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 48515 | THUN: Indirect Materials-Replacements | 2023 | 55036.2469
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 48524 | TBAY: 33-21-600 Centennial Park Exposed NPS 8 | 2023 | 769051.4311
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 49507 | TBAY: 33-22-600 Atikokan Lateral - TP8 -Leak | 2023 | 529350.4224
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 49509 | Atikokan Steep Rock Mine Valve Nest Retirement | 2031 | 139927.8557
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 49510 | Darlington Bay Bridge - NPS 2 Replacement | 2025 | 1291450.2041
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 501009 | THUN: PSLL Maintenance | 2023 | 175578.6682
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 503015 | TBAY: 33-22-601 Atikokan Lateral Leak Dwnst of Sapawe Mill | 2031 | 536346.7654
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 503375 | TBAY: Kenora 9 Brinkman Rectifier |  | 68504.1659
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 503376 | TBAY: Kenora 9 Rupert at Ninth Rectifier |  | 68504.1659
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 734922 | NPS 8 Redlake Retrofit |  | 1303222.7373
Northern | Div_33 - Thunder Bay | Distribution Pipe | Fail | Dollar threshold | 735679 | 45-22-000 TIMM Grierson Rd Valve Replacement | 2023 | 56048.863
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 1266 | Redrock Retrofit |  | 1718831.798 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2024 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30134 | 4th Ave S-Kenora-1562 | 2031 | 4954126.9813 | 4th Ave. S. - Kenora - 1562 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30136 | Arthur St W -Thunder Bay-1496 | 2027 | 4182490.4639 | Arthur St. W. -Thunder Bay - 1496 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There is a fault associated with the area. | Planned
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30142 | Dominion Ave 2-Kapuskasing-1540 | 2031 | 2481933.2319 | Dominion Ave. 2 - Kapuskasing - 1540 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30143 | Dominion Ave-Kapuskasing-1499 | 2030 | 5091520.5116 | Dominion Ave. – Kapuskasing - 1499 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30144 | Finlayson St-Thunder Bay-1563 | 2031 | 3175990.3965 | Finlayson St. - Thunder Bay - 1563 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30145 | George St-Hearst-1558 | 2032 | 5437097.432 | George St. - Hearst - 1558 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30146 | Hart St-Timmins -1559 | 2032 | 4955639.2798 | Hart St. - Timmins (moratorium until 2025) -1559 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: City will not allow work on Toke St. within the next five years as it was reconstructed in 2020. Moratorium is until 2025. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30151 | Marks St S-Thunder Bay-1537 | 2029 | 5500549.245 | Marks St. S. - Thunder Bay - 1537 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30155 | Ogden St-Thunder Bay-1568 | 2030 | 5556674.3106 | Ogden St. - Thunder Bay - 1568 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30156 | Prince Arthur Blvd-Thunder Bay-1538 | 2031 | 4043057.4403 | Prince Arthur Blvd. - Thunder Bay - 1538 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30157 | Seventh Ave N-Kenora-1546 | 2031 | 4237285.0281 | Seventh Ave. N. - Kenora - 1546 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30158 | Seventh St S-Kenora-1542 | 2032 | 3823133.8205 | Seventh St. S. - Kenora - 1542 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 30160 | Spruce St-Kapuskasing-1565 | 2029 | 5024950.6501 | Spruce St. - Kapuskasing - 1565 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 48517 | THUN: Anodes* | 2020 | 10076231.4972 | General: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within EGI's system. These installations and replacements are based on the internal Standard Operating Practice established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 49256 | NW_Lateral Clamp Cut Outs_ATIKOKAN | 2031 | 3078412.8257 | General: The capital expenditure included in this category covers a variety of planned maintenance projects. The projects covered under this expenditure include low-pressure system replacements, distribution pipeline replacements due to historical leakage and integrity concerns, pipeline casing replacements, bridge and water-crossing replacements and repairs, etc. These projects are often identified through planned inspections and pipeline surveys and would then be assessed and planned based on risk and resource availability. | Planned
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 503071 | Northern Region: Corrosion Rectifier Groundbed Program* | 2021 | 1514984.2101 | General: The corrosion program includes the expenditure other than anodes required to reduce the amount of down plant within EGI’s system. These installations and replacements are based on the internal Standard Operating Practice established to maintain the appropriate level of cathodic protection on steel pipeline assets. Individual projects will be set up to use these program dollars based on identification of rectifier and groundbed sites by the Corrosion group. Cloned inv #101794 to seperate due to boundary realignment in Northern Region vs 2020 investment creation date.. Updated name to identify as district planning blanket and reflect how forecast will be provided for budgeting. Program items will be named/numbered according to Division where work is performed. 2021 Forecast will also be adjusted from original placeholder value under Inv #101794 2022 Budget will be allocated based on split of forecast | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 734020 | NPS 8 Onion Lake Lateral Replacement |  | 1868295.4326 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. The entire ~320m Onion Lake Lateral is proposed for replacement between TCE and Onion Lake Primary Station (30201002). General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_33 - Thunder Bay | Distribution Pipe | Pass |  | 734021 | NPS 8 Onion Lake Loop Retrofit |  | 1868295.4326 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2024 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 48504 | TBAY & TIMM: Plan(T)-Dist-Stn Measuring/Corrosion Stn* | 2020 | 261452.9994
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 48527 | TBAY: Clark & Niven DRS Rebuild | 2024 | 640809.1449
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 100938 | TBAY: Dryden Domtar SMS, Station Modifications | 2030 | 282949.8708
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 100945 | TBAY: Longlac TBS, Heater Replacement | 2024 | 258039.7449
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 102993 | TBAY: Martha at Red River Station Rebuild | 2026 | 1042578.1898
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 502824 | TBAY: Kraft SMS Retirement | 2030 | 226359.8966
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 503274 | NW PFM Compliance Program* |  | 237009.7052
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733372 | TBAY: Wright at O'Brien DRS Pipe Supports | 2030 | 28294.9871
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733375 | TBAY: New Station at Mercury Ave & Maple Station Retirement (Atikokan) | 2025 | 968587.6531
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733772 | TBAY: Vermillion Bay PCS, Boiler Replacement | 2027 | 269222.1335
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733865 | TBAY: Kenora TBS, Boiler Replacement | 2028 | 222940.3371
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733866 | TBAY: McIrvine TBS, Boiler Replacement | 2029 | 151661.6538
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733867 | TBAY: Ignace TBS, Boiler Replacement | 2029 | 151661.6538
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733869 | TBAY: Belrose PCS, Boiler Replacement | 2029 | 956424.844
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733870 | TBAY: Nipigon TBS, Boiler Replacement | 2030 | 165525.6744
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733872 | TBAY: Balmertown - Goldcorp SMS, Boiler Replacement | 2030 | 253240.1344
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733875 | TBAY: Geraldton TBS, Boiler Replacement | 2032 | 183328.8219
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 733876 | TBAY: Kenora Airport Rd, Boiler Replacement | 2032 | 183328.8219
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 734565 | TBAY: 500 Toledo St MUB Rebuild | 2023 | 186829.5433
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 735629 | TBAY: Fisher 621 PRS Rebuild Program* | 2026 | 977417.053
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 735631 | TBAY: Paquette Road Station Rebuild | 2026 | 977417.053
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 735632 | TBAY: Burwood Rd TBS Filter | 2032 | 135799.1274
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 735633 | TBAY: Balsam St TBS Filter | 2025 | 129145.0204
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 735634 | TBAY: Dewe St DRS Relocation | 2031 | 839567.1343
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 735635 | TBAY: Mountdale at Francis DRS Rebuild | 2032 | 814794.7641
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 735669 | TBAY: 2022 Morecombe PRS (at Onion Lk) Rebuild | 2023 | 24910.6058
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 735707 | THUN: Gorevale Road PRS Station Relocation | 2031 | 839567.1343
Northern | Div_33 - Thunder Bay | Distribution Stations | Fail | Dollar threshold | 735729 | TBAY: Arthur St at Cooper Rd PRS Rebuild | 2031 | 1049458.9179
Northern | Div_33 - Thunder Bay | Distribution Stations | Pass |  | 100917 | TBAY: 33-22-700 Dryden TBS, Glycol and Odorant Upgrades | 2023 | 2117401.4903 | Issue/Concern/Opportunity: Due to new standards, there is need to relocate below-grade glycol lines to above-grade. Also, the replacement/relocation of separate odourant bulk and pump buildings with combined structure/building is required. This would facilitate removal of above-grade odourant gravity feed between buildings and below-grade odourant injection line. The most likely risk is the increased risk of a significant environmental incident. The worst-case scenario is leakage of the below-grade boiler glycol lines or odourant injection lines, either of which would cause significant environmental concerns. Assets: Station ID 30101001, Dryden Town Border Station (TBS) Related Program: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Northern | Div_33 - Thunder Bay | Distribution Stations | Pass |  | 100918 | TBAY: 33-23-700 Arthur St TBS, Thunder Bay, Station Rebuild | 2024 | 2563236.5797 | Issue/Concern/Opportunity: Based on 2021 Stations Engineering review, a full station rebuild is required including new inlet filter, ERX telemetry, and a CWT 1155. Station material estimate alone was $900,000. Alliance Partner. The most likely risk is regulation failure. The worst case scenario is significant system outage, as Thunder Bay North system backbone pipelines all lead to this station. Also, this station lies at the quadrant of a major MTO intersection. Assets: Station ID 30202014 Related Program: There are no related C55 investments. | Completed | Fail | Distribution station condition related, IRPA not applicable
Northern | Div_33 - Thunder Bay | Distribution Stations | Pass |  | 503174 | TBAY: English River PCS Station Rebuild | 2029 | 2049481.8085 | Issue/Concern/Opportunity: Station alterations need to have pilot heat, larger relief valve and larger trims due to TC Energy work. Assets: Station #30701001. Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Northern | Div_33 - Thunder Bay | Growth | Pass |  | 48506 | TBAY: Company Program - New Business - Scattered Mains - Company* | 2020 | 3643104.6646 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Northern | Div_33 - Thunder Bay | Growth | Pass |  | 500424 | TBAY: Company Program - Customer Connections* |  | 16175436.2517 | Thunder Bay Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Northern | Div_33 - Thunder Bay | Growth | Pass |  | 734531 | THUN: Rosslyn Rd at Sideroad 20 Reinforcement Project | 2031 | 174909.8196 | Issue/Concern/Opportunity: • Approximately 130 m 2-inch PE main extension is to tie together two existing 420 kPa systems. • The Goal is to abandon 30206036 STN (Rosslyn Rd. at 20th Side Rd.) and small customer station south of there. • Customers currently fed by this station will then be tied to the neighbouring 420 kPa system fed by 30206035 Station (Rosslyn Rd. at Almira Post Regulation Station [PRS]) and 30206034 Station (Rosslyn Rd. at R.S. Piper). Assets: Stations 30206036, 30206025, and 30206034 Related Program: None. | Planned
Northern | Div_33 - Thunder Bay | Utilization | Pass |  | 48513 | TBAY: Meter & Regulator Inst Repl-Company* | 2020 | 8731453.1944 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 1275 | Espanola Retrofit |  | 934147.7163
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 48534 | SUDB: Dist-Repl-Contr-Services* | 2020 | 2204560.4497
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 48544 | SUDB: Land Rights-Replacements | 2023 | 6227.6514
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 48548 | SUDB: Misc Materials-Company | 2023 | 6227.6514
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 48549 | SUDB: Anodes* | 2020 | 329311.9806
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 48553 | NE: Whittaker St., Sudbury, Replacement | 2028 | 443949.9008
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 49628 | SSM: Goulais Rd Main replacement SSM | 2030 | 1492560.5684
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 49641 | SUDB: Gagnon St Lateral, Azilda | 2031 | 209891.7836
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 49645 | 116 Simmons Rd, Dowling PLPR | 2024 | 44856.6914
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 49652 | NE: New Sudbury Mall Rooftop Main Coating | 2023 | 293627.5378
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 49653 | SUDB: Regent St grasshopper, Sudbury | 2027 | 381629.313
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 49666 | 863 Attlee St shallow main, Sudbury | 2030 | 113180.0049
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 49670 | Bay St. Roof top piping blocking Replacement and Maintenance, SSM | 2024 | 96121.3717
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 49673 | Kingsmount Blvd, Bannister Tees Replacement, SSM | 2023 | 112097.726
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 100737 | NE: Southview & Martindale, Sudbury, Valve Nest Repl | 2023 | 87187.1202
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 734394 | SUDB: Fourth Avenue, Sudbury Damage | 2023 | 73614.5766
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 734593 | SUDB: Bancroft Dr and Bellevue Ave, Valves Replacement | 2023 | 373659.0865
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 734613 | SUDB: Martindale Road, Sudbury Replacement | 2023 | 112097.726
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 734615 | NE: Second Ave & Centre St, Espanola, Valve Replacement | 2023 | 118325.3774
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 734616 | NE: Wellington St, SSM, Replacement | 2024 | 121753.7375
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Dollar threshold | 735465 | SUD: Copper Cliff Replacement | 2031 | 1708519.1183
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Timing | 736530 | Sudbury Lateral Integrity Digs 2023 | 2023 | 12455302.8842
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Fail | Timing | 736531 | Sudbury Lateral Integrity Digs 2024 | 2024 | 7433386.0812
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Pass |  | 2142 | Sudbury Section 1 Sturgeon River | 2023 | 2241954.5191 | Issue/Concern - Replace 236 m of NPS 10 steel transmission piping from the intersection of Delorme Street and Smiley Road to approximately 275 m south of Smiley Road Main Line Valve (MLV). Chainage 43236 – 43472. Class 1 to Class 2 change. General: Annual Class Location surveys are required as per the Canadian Standards Association Z662 – Oil and Gas Pipeline Systems for pipelines greater than 30% SMYS. Any changes in class location need to be assessed to the current standard to determine if pipeline modifications are required. Urban development occurs in close proximity to EGI’s pipelines, which triggers annual class location changes; this work ensures EGI is compliant and fosters the safety of the public and the pipeline system. Prework and execution capital dollars will cover the whole scope of North and South side. Assets: Sudbury Section 1 Sturgeon River. Related Programs: Not applicable. | Completed | Fail | Timing - Market based supply side alternatives not applicable
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Pipe | Pass |  | 734812 | SUDB: RR 15 Property Line, Chelmsford, Replacement | 2031 | 2098917.8357 | General: The capital expenditure included in this category covers a variety of planned maintenance projects. The projects covered under this expenditure include low pressure system replacements, distribution pipeline replacements due to historical leakage and integrity concerns, pipeline casing replacements, bridge and water crossing replacements and repairs etc. These projects are often identified through planned inspections and pipeline surveys and would then be assessed and planned based on risk and resource availability. Issue/Concern/Opportunity: The base of the issue at this site is risk related. There are ~108 first stage cuts at this location that are off the NPS 6 main 3723 kPa MOP (540 psi). There have been several leak replacements completed over the years as the risers end up corroding as the first stage cuts are not maintained. Section from 1 to 4: Install 4'' PE main from PRS #43202212 to Rouleau Rd. Tie-in required at Montee Principale Ave (FID# 551962868) and Rouleau Rd (FID# 552034281). Total length ~4000m . Modification required at PRS 43202212 to increase its capacity slightly. Abandon PRS #43202146. Section 5: Install 4'' PE main from PRS #43202147 to 3485 RR15. Total length ~850m . Section from 6 to 7: Extend 4" PE FID# 551830660 west on the southern side of the road & 2' PE on northern side of the road to PRS #43202147. The total length ~1920m Justification: modification required at some PRS to increase its capacity, to meet the expansion demand and growth, and to meet current Enbridge standards. Ensures the integrity of Enbridge assets and the safety of those working around the gas lines in the future. Assets: As shown above Related Investments: none | Planned
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 49611 | NE: 43202064 Vale Divisional Shops PRS Replacement | 2025 | 478311.8292
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 49678 | McCreedy West Stn., Sudbury | 2031 | 27985.6271
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 49894 | NE: 43202063 - Vale Engineering & Exploration, Rebuild/Relocation | 2027 | 284487.3061
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 101068 | NE: 13403001 - Vale Totten Mine, Rebuild | 2025 | 1087199.6056
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 101072 | NE: 43501002 - Coniston DRS, Rebuild | 2023 | 608436.1278
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 501160 | NE: 43202054 Inco Smelter, Station Modifications | 2025 | 452007.5714
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 501161 | NE: 43202154 - Bil-Mur PRS, Rebuild | 2025 | 258290.0408
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 502659 | NE: 45101125 - Essar #7 BF SMS, Gear Operator Replacement | 2023 | 12455.3029
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 502660 | NE: 45103001 - Airport Rd TBS and DRS, Boiler Replacement | 2024 | 512647.3159
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 502661 | NE: 45401095 - Great Northern Rd TBS, Boiler Replacement | 2023 | 373659.0865
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733753 | SUD: Lasalle TBS, Boiler Replacement | 2023 | 193057.1947
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733754 | SUD: Frood TBS, Boiler Replacement | 2023 | 158182.3466
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733755 | SUD: Inco Smelter SMS, Boiler Replacement | 2023 | 240387.3457
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733756 | SSM: Goulais Ave TBS Algoma 4, Boiler Replacement | 2025 | 968587.6531
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733762 | SUD: Barrydowne, Boiler Replacement | 2026 | 234580.0927
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733763 | SUD: Kelly Lake TBS, Boiler Replacement | 2025 | 189843.18
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733765 | SUD: Chelmsford, Boiler Replacement | 2027 | 213712.4153
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733767 | SUD: Maley Dr TBS, Boiler Replacement | 2026 | 200696.3015
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733813 | SUD: Coniston TBS, Boiler Replacement | 2028 | 145874.5415
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733814 | SUD: Walden TBS, Boiler Replacement | 2028 | 145874.5415
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733841 | SUD: Copper Cliff TBS, Boiler Replacement | 2031 | 172111.2625
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733843 | NE: Espanola DRS & Domtar SMS, Station Rebuild | 2028 | 1651409.9043
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733852 | SSM: Elliot Lake TBS, Boiler Replacement | 2031 | 263064.3687
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733853 | SUD: Inco North Mine SMS, Boiler Replacement | 2032 | 175180.8743
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733854 | SSM: Blind River TBS, Boiler Replacement | 2032 | 267524.2809
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733856 | SUD: Kukagami TBS, Boiler Replacement | 2032 | 175180.8743
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 733857 | SUD: Azilda DRS, Boiler Replacement | 2032 | 175180.8743
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 734400 | NE: 43204045 - Charlotte PRS, station rebuild | 2023 | 346941.2163
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 734581 | NE: 43204008 - Brierwood & Kelly Lake Rd PRS, Station Retirement | 2024 | 38448.5487
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 734582 | NE: 44301018 - Levack Mine Air Heater #2 SMS, Station Retirement | 2027 | 69387.1478
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 734583 | NE: 43202139 - First Nickel SMS, Station Retirement | 2032 | 114907.9424
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 736079 | SSM: Goulais Ave TBS Algoma 4, Station Modifications | 2031 | 69963.9279
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 736082 | NE: 45101001 - Sault Primary, Control Valve Modifications | 2030 | 247581.1369
Northern | Div_43 - Sudbury & S.S. Marie | Distribution Stations | Fail | Dollar threshold | 736083 | NE: 43201030 - Coniston Primary, Control Valve Modifications | 2026 | 293225.1159
Northern | Div_43 - Sudbury & S.S. Marie | Growth | Pass |  | 48539 | SUDB: Company Program - New Business - Scattered Mains - Company* | 2020 | 752037.0863 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Northern | Div_43 - Sudbury & S.S. Marie | Growth | Pass |  | 30523 | SRP_North_Parry Sound_Seguin Trail_Reinforcement_NPS6_8500m_4960kPa | 2032 | 23764847.2322 | Looping of existing NPS 4 main with NPS 6 for 8.5km | In Progress
Northern | Div_43 - Sudbury & S.S. Marie | Growth | Pass |  | 30524 | SRP_North_Sault Ste Marie_45103001STN_Rebuild | 2024 | 1796828.7911 | Station is flowing over capacity. | Planned
Northern | Div_43 - Sudbury & S.S. Marie | Growth | Pass |  | 500425 | SUDB: Company Program - Customer Connections* |  | 29806515.2827 | Sudbury & S.S Marie Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Northern | Div_43 - Sudbury & S.S. Marie | Utilization | Pass |  | 48546 | SUDB: Meter & Regulator Inst Repl-Company* | 2020 | 13543686.5002 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_45 - Timmins | Distribution Pipe | Fail | Dollar threshold | 48568 | TIMM: Land Rights-Replacements | 2023 | 3736.5909
Northern | Div_45 - Timmins | Distribution Pipe | Fail | Dollar threshold | 48572 | TIMM: Indirect Materials-Replacements | 2023 | 92290.0578
Northern | Div_45 - Timmins | Distribution Pipe | Fail | Dollar threshold | 100951 | TIMM: Xstrata (Kidd Creek) Smelter SMS Service Retirement | 2031 | 1260897.7811
Northern | Div_45 - Timmins | Distribution Pipe | Fail | Dollar threshold | 102490 | TIMM: Anodes* | 2020 | 235666.7859
Northern | Div_45 - Timmins | Distribution Pipe | Pass |  | 30137 | Bay St-Timmins-1561 | 2032 | 5199604.3133 | Bay St. - Timmins - 1561 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_45 - Timmins | Distribution Pipe | Pass |  | 30147 | Hemlock St-Timmins-1569 | 2032 | 2827017.6171 | Hemlock St. - Timmins - 1569 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_45 - Timmins | Distribution Pipe | Pass |  | 30150 | Maple St N-Timmins-1535 | 2028 | 4386353.9395 | Maple St. N. - Timmins - 1535 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Northern | Div_45 - Timmins | Distribution Pipe | Pass |  | 30159 | Sixth Ave-Timmins-1566 | 2030 | 4355345.6689 | Sixth Ave. - Timmins - 1566 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Northern | Div_45 - Timmins | Distribution Pipe | Pass |  | 733717 | NPS 6 Iroquois Falls Retrofit | 2026 | 4038813.2323 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2027 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_45 - Timmins | Distribution Pipe | Pass |  | 733718 | NPS 6 Kapuskasing Retrofit | 2026 | 4038813.2323 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2027 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_45 - Timmins | Distribution Pipe | Pass |  | 733719 | NPS 6 Cochrane Loop | 2026 | 4038813.2323 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2026 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 100922 | TIMM: Swastika TBS, Station Rebuild | 2027 | 832645.7738
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 502086 | TIMM: 45-23-700 2881 Hwy 655 TBS Low-Piping Modifications | 2029 | 683160.6028
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 502087 | TIMM: 45-23-701 Porcupine Primary Low-Piping Modifications | 2029 | 683160.6028
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 502088 | TIMM: 45-22-702 Kirkland Lake (Northland) Power SMS Rebuild | 2025 | 1637777.1139
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 503742 | TIMM: Glencore Concentrator SMS, Boiler Replacement | 2024 | 203777.3081
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733768 | TIMM: Glencore Mine SMS, Boiler Replacement | 2024 | 162765.5228
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733769 | TIMM: South Porcupine/Crawford TBS, Boiler Replacement | 2029 | 341580.3014
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733770 | TIMM: Porcupine PCS, Boiler Replacement | 2026 | 241096.2064
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733771 | TIMM: Kirkland Lake TBS, Boiler Replacement | 2026 | 191573.7424
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733773 | TIMM: Cochrane TBS, Boiler Replacement | 2027 | 213712.4153
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733864 | TIMM: Matheson TBS, Boiler Replacement | 2028 | 145874.5415
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733868 | TIMM: Schumacher TBS, Boiler Replacement | 2029 | 151661.6538
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733871 | TIMM: Dalton TBS ( Mcbride St S.), Station Rebuild and Boiler Replacement | 2030 | 1061062.0155
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733873 | TIMM: Kapuskasing TBS, Boiler Replacement | 2031 | 699639.2786
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733874 | TIMM: Moneta TBS, Boiler Replacement | 2032 | 267524.2809
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 733877 | TIMM: Hwy 655 TBS, Boiler Replacement | 2031 | 289650.6613
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 734572 | TIMM: Malette Kraft SMS Retirement | 2030 | 53860.9227
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 734573 | TIMM: Evergreen Greenhouse SMS Retirement | 2023 | 6377.1151
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 734574 | TIMM: Hallnor Mine PRS Retirement | 2030 | 70737.4677
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 734576 | TIMM: Munoro Mine SMS Retirement | 2032 | 47529.6946
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 734623 | TIMM: Opasatika TBS Rebuild | 2028 | 825704.9522
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 734624 | TIMM: Mattice TBS Rebuild | 2028 | 825704.9522
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 734625 | TIMM: Val Gagne TBS Rebuild | 2029 | 819792.7234
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 734626 | TIMM: Fauquier TBS Rebuild | 2029 | 819792.7234
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 734943 | TIMM: Kirkland Lake CMS (Kenogami) - Long-Term Odorant Solution | 2023 | 498212.1154
Northern | Div_45 - Timmins | Distribution Stations | Fail | Dollar threshold | 735730 | TIMM: Monteith CMS | 2025 | 1291450.2041
Northern | Div_45 - Timmins | Distribution Stations | Pass |  | 100920 | TIMM: Hearst TBS, Rebuild | 2023 | 2241954.5191 | Issue/Concern/Opportunity: According to a geological investigation completed on this station in 2021 it was determined that the existing facilities have undergone movements (frost heave, sinking, erosion) which have caused structural damages between the existing buildings and interconnecting pipeline facilities. The operations department also confirmed that heaving/ movements have been an ongoing issue at this station since it was rebuilt in 2004. There is a need to replace the station or remediate existing soil, due to extensive ground movement and assets. This site was constructed new in 2005 and experienced significant movement by 2008. The site has been reworked once already and now requires additional work. A cost analysis should be considered to compare reworking the existing site versus relocating the station. Assets: Station ID 41301001 Related Program: There are no related C55 investments. | Completed | Fail | Distribution station condition related, IRPA not applicable
Northern | Div_45 - Timmins | Distribution Stations | Pass |  | 101158 | TIMM: 45-22-700 Goldcorp Dome Mine SMS, Rebuild | 2023 | 2149400.4089 | Issue/Concern/Opportunity: Station needs to be raised or relocated due to seasonal flooding. Mine site has been built up around the station and there is no place for Spring thaw and/or rainwater to run off. Justification: The most likely risk/scenario is above-grade frozen valves/assets. The worst-case scenario is the inability to isolate and/or shut down the station in an emergency (i.e., injury, fire, or explosion) due to frozen flood waters. Assets: Station ID 42199002 Related Investments: 735784 (the heater replacement for this station) | Completed | Fail | Distribution station condition related, IRPA not applicable
Northern | Div_45 - Timmins | Distribution Stations | Pass |  | 733880 | TIMM: Tembec Spruce Falls SMS, Rebuild | 2024 | 1922427.4348 | Issue/Concern/Opportunity: Customer-driven station needs a rebuild. Assets: 41402004 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Northern | Div_45 - Timmins | Distribution Stations | Pass |  | 734628 | TIMM: Smooth Rock Falls CMS, TBS, and DRS Relocations/Retirements | 2025 | 3486915.5511 | Issue/Concern/Opportunity/Justification: Project may include modifications to whole town system. The project includes building new Town Border Station (TBS) at TC Energy. The existing Customer Meter Station (CMS) will be removed and the old TBS will be repurposed as Distribution Regulation Station (DRS). Scope is to be further defined in the future. Assets: Station #41501002 (TBS), 41501005 (CMS), 41502002 (DRS) Related Program: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Northern | Div_45 - Timmins | Distribution Stations | Pass |  | 734941 | TIMM: Iroquois Falls TBS, Station Rebuild | 2028 | 2752349.8406 | Issue/Concern/Opportunity: The current station is experiencing frost heave due to a large pressure cut and the soil conditions that is leading to pipe movement. The existing regulation building has moved as a result and a rebuild of all regulation is required to remediate the issues. The scope will include the demolition and removal old the Regulator building. The site will receivel new fencing, grading improvements, and a new Remoter Terminal Unit (RTU) building (currently mounted outside on side of boiler building). The station is experiecing odourant injection issues, related to the Co-Gen facility. Due to the reduction in load as a result of the Co-Gen customer no longer requiring natural gas, setting Odourization injection rates with the current equipment is difficult for all flow patterns. The existing Heating building does not have adequate containment in the event of a glycol leak and will be addressed as part of this project. When the piping is remediated due to the frost heave, the site will be reduced to include only one filter. Assets: 41701002 Related Investments: N/A | Completed | Fail | Distribution station condition related, IRPA not applicable
Northern | Div_45 - Timmins | Growth | Pass |  | 30525 | SRP_North_Timmins_Hwy 655_Reinforcement_NPS6_850m_6895kPa | 2024 | 2050589.2125 | A reinforcement project is required to ensure EGI can meet station minimum inlets on the 6,895 kPa Maximum Operating Pressure (MOP) system under design winter conditions (with 4,000 kPa minimum from TC). Station 41902024 only requires SAP/field update (no project cost associated). | Planned
Northern | Div_45 - Timmins | Growth | Pass |  | 100936 | TIMM: West Timmins System Reinforcement (McBride North and Shirley/Riverside Stations) | 2023 | 934147.7163 | Issue/Concern/Opportunity: Based on generic subsystem growth, as defined by Network Analysis at 0.74% annually for Timmins, a project will be required around 2032 as pressures along Majestic Drive go below minimum. To resolve this capacity issue, either the HWY 101 bottleneck at Shirley/Riverside Drive can be resolved, or the McBride North DRS can be rebuilt to accommodate a higher outlet pressure. However, the above conclusions/recommendations are based on the generic growth model. There is a relatively high probability that large commercial/industrial customers in the area of McBride North will be added to the system earlier than 2032, which would require that the above recommendations be acted upon as early as 2021. Depending on what loads are added, based on growth in this area of Timmins, Network Analysis will need to confirm at that time what the specific requirements are to accommodate the specific loads. Distribution Opimization Engineering (DOE) identified this as a System Reinforcement Plan (SRP) project (FBPSTN_2018_41903048). If these modifications are not made, this could result in a denial of system attachments (i.e., forgone revenue). The worst case scenario is that there is no additional capacity, and/or there is an incident during the winter months causing outage. Assets: Station ID 41903048 Related Program: This project might include modifications to the existing McBride North DRS (41903044), depending on the preferred solution to address the above issue/concern. | Planned
Northern | Div_45 - Timmins | Growth | Pass |  | 500426 | TIMM: Company Program - Customer Connections* |  | 3823692.9537 | Timmins Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Northern | Div_45 - Timmins | Growth | Pass |  | 502816 | TIMM 45-21-501 St Jean @ Shirley NPS4 Reinforcement - Timmins | 2023 | 62428.4691 | Issue/Concern/Opportunity: There is a bottleneck in the distribution system in west end of Timmins. Growth is limited in the area so reinforcement by way of removing bottlenecks is required. Assets: NPS PE 4 Related Program: Not applicable | Planned
Northern | Div_45 - Timmins | Growth | Pass |  | 502817 | TIMM 45-22-502 Shirley St @ Riverside Rd NPS4 Reinforcement - Timmins | 2023 | 113254.8236 | Issue/Concern/Opportunity: Bottlenecks in distribution system are contributing to restrictions on growth on the west side of Timmins. Distribution Optimization Engineering has indicated both pipeline and station reinforcement will be required to enhance the system. Assets: Riverside Rd NPS4 Reinforcement - Timmins Related Program: N/A | Planned
Northern | Div_45 - Timmins | Utilization | Pass |  | 48570 | TIMM: Meter & Regulator Inst Repl-Company* | 2020 | 4283544.5049 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 1273 | Marten River Retrofit |  | 996424.2307
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 1274 | Sudbury Loop & Sudbury Sec 2b Retrofit |  | 934147.7163
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30200 | Colborne St W 1 - Northeast - 1682 | 2030 | 1380559.4459
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30201 | Colborne St W 2 - Northeast - 1683 | 2030 | 1626151.6716
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30205 | Farah Ave - Northeast - 1288 | 2032 | 1582434.5849
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30208 | Galt St 1 - Northeast - 1690 | 2032 | 1695811.0492
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30214 | Janet St 1 - Northeast - 1699 | 2027 | 1632590.1621
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30218 | King St W - Northeast - 1239 | 2029 | 68316.0603
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30219 | Laforest Ave - Northeast - 1270 | 2029 | 1341662.3871
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30221 | Maher St 2 - Northeast - 1703 | 2032 | 1074810.2767
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30224 | Matchedash St N 1 - Northeast - 1719 | 2032 | 603294.7391
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30225 | Matchedash St N 2 - Northeast - 1720 | 2032 | 325216.8562
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30230 | Princess St W 1 - Northeast - 1721 | 2032 | 1099800.521
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 30232 | Tanguay Ave - Northeast - 1280 | 2029 | 866204.6872
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 48575 | NE: Dist-Repl-Contr-Mains Leakage* | 2020 | 4056177.1255
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 48580 | NE: Dist-Repl-Contr-Mains Municipal* | 2020 | 9933819.0421
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 48584 | NBAY: Land Rights-Replacements | 2023 | 6227.6514
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 48588 | NBAY: Misc Materials-Company | 2023 | 6227.6514
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 49621 | NBAY: 128 McIntyre St W, North Bay | 2023 | 42347.98
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 49623 | NBAY: 955 McKeown Ave, North Bay | 2025 | 96858.7653
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 49624 | NBAY: 198 Hughes Rd, North Bay | 2026 | 32580.5163
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 49625 | NBAY: 247 Whitewood Ave, New Liskeard Main Relocation | 2031 | 209891.7836
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 49627 | New Liskeard Mall, New Liskeard | 2023 | 79047.8289
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 49638 | NBAY: 205 Main St E, North Bay | 2023 | 80959.4687
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 49644 | NBAY: 300 Lakeshore Dr, North Bay | 2023 | 112097.726
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 49649 | Giroux St Dent Repair, Sudbury | 2027 | 104080.7217
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 102476 | NE: Ski Club Rd., North Bay | 2029 | 510000.9232
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 501007 | NBAY: PSLL Maintenance | 2023 | 196943.2492
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Fail | Dollar threshold | 735150 | NE: Hwy 11 and Barnett, North Bay, Grasshopper Valves Replacement | 2028 | 584874.3411
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30197 | 4th Ave E - Northeast - 1302 | 2031 | 1887402.3853 | 4th Ave. E. - Northeast - 1302 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There is rocky terrain. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30198 | Alder St 1 - Northeast - 1715 | 2031 | 2122239.6674 | Alder St. 1 (moratorium until 2026) - Northeast - 1715 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project will take 11 months / 2 years to complete. Project was updated based on regional feedback (Alder St. 1 – 1715 and Alder St. 2 - 1716). It is rocky and rectifier is in area. Road work was just completed on Beatty St. Project was updated to reflect a moratorium until 2026. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30199 | Alder St 2 - Northeast - 1716 | 2032 | 2045448.228 | Alder St. 2 (moratorium until 2026) - Northeast - 1716 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project will take 11 months / 2 years to complete. Project was updated based on regional feedback (Alder St. 1 – 1715 and Alder St. 2 - 1716). It is rocky and there is a rectifier in the area. Road work was just completed on Beatty St. Project was updated to reflect a moratorium until 2026. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30206 | Ferguson Ave 1 - Northeast - 1686 | 2032 | 2208807.245 | Ferguson Ave. 1 - Northeast - 1686 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project will take 16 months / 2.5 years to complete. Project was updated based on regional feedback (Ferguson Ave. 1 - 1686, Ferguson Ave. 2 - 1688). Permit may be required. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30207 | Ferguson Ave 2 - Northeast - 1688 | 2030 | 2470441.9995 | Ferguson Ave. 2 - Northeast - 1688 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: It will take 16 months / 2.5 years to complete. Project was updated based on regional feedback (Ferguson Ave. 1 - 1686 and Ferguson Ave. 2 - 1688). Permit may be required. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30209 | Galt St 2 - Northeast - 1691 | 2029 | 2101362.1177 | Galt St. 2 - Northeast - 1691 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project will take 12 months / 2 years to complete. Project was updated based on regional feedback (Galt St. 1 - 1690, Galt St. 1 - 1690). | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30211 | Georgina Ave 2 - Northeast - 1695 | 2028 | 2009206.0256 | Georgina Ave. 2 - Northeast - 1695 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project will take 16 months / 2.5 years to complete. Project was updated based on regional feedback (Georgina Ave. 1 - 1686, Ferguson Ave. 2 - 1688). Permit may be required. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30212 | Hilda St 1 - Northeast - 1696 | 2031 | 2386807.9248 | Hilda St. 1 - Northeast - 1696 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: It will take 14 months / 2 years to complete. Project was updated based on region (Hilda St. 1 - 1696 and Hilda St. 2 - 1698). | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30213 | Hilda St 2 - Northeast - 1698 | 2028 | 2151905.016 | Hilda St. 2 - Northeast - 1698 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project will take 14 months / 2 years to complete. Project was updated based on region (Hilda St. 1 - 1696, Hilda St. 2 - 1698). | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30215 | Janet St 2 - Northeast - 1700 | 2030 | 1869816.3296 | Janet St. 2 - Northeast - 1700 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project will take 13 months / 2 years to complete. Project was updated based on regional feedback (Janet St. 1 - 1699 and Janet St. 2 - 1700). There is rocky terrain. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30220 | Maher St 1 - Northeast - 1701 | 2030 | 2065519.3434 | Maher St. 1 - Northeast - 1701 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project is 8 months of work which is difficult to fit into one year. Project was updated based on regional feedback (Maher St. 1 - 1701, Maher St. 2 - 1703). Permit may be required. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30222 | Mary St 1 - Northeast - 1708 | 2029 | 2228996.1387 | Mary St. 1 - Northeast - 1708 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project will take 12 months / 2 years to complete. Project was updated based on regional feedback (Mary St. 1 - 1708 and Mary St. 2 - 1709). | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30228 | Presley St 1 - Northeast - 1713 | 2031 | 3227917.8476 | Presley St. 1 - Northeast - 1713 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: It will take 17 months / 2.5 years to complete. It is a tight area to work in. The project was updated based on regional feedback (Presley St. 1 - 1713 and Presley St. 2 – 1714). Permit may be required. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30229 | Presley St 2 - Northeast - 1714 | 2031 | 2224956.3405 | Presley St. 2 - Northeast - 1714 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project will take 17 months / 2.5 years to complete. There is a tight area to work in. Project was updated based on regional feedback (Presley St. 1 - 1713, Presley St. 2 - 1714). Permit may be required. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 30233 | Wickstead Ave - Northeast - 1510 | 2032 | 3326556.7169 | Wickstead Ave. (moratorium until 2026) - Northeast - 1510 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Water and sewer were just redone on Lavase at the middle of polygon. Also, from Mountainview to Lavase on Mountainview, water and sewer were done in 2021. The road will not be able to be cut in these sections. This project was updated to reflect a moratorium until 2026. | Planned
Northern | Div_46 - North Bay & Orillia | Distribution Pipe | Pass |  | 48590 | NBAY: Anodes* | 2020 | 8308340.3121 | General: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within EGI's system. These installations and replacements are based on the internal Standard Operating Practice established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 48577 | NBAY: Plan(T)-Dist-Stn Measuring/Corrosion Stn* | 2019 | 268021.9262
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 502662 | NE: 42801004 - Cobalt TBS, Rebuild | 2025 | 710297.6123
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 502663 | NE: 44702001 - Rutherglen TBS, Rebuild | 2028 | 688087.4601
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 502704 | NE: 43601001 - Balls Dr TBS, Rebuild | 2028 | 1307366.1743
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 503273 | NE PFM Compliance Program* |  | 411650.7678
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733366 | NE: 44602002 - Burks Falls TBS, Station Rebuild | 2023 | 809594.6875
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733757 | NBAY: Muskoka Falls TBS, Boiler Replacement | 2024 | 208903.7812
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733758 | NBAY: Ski Club/Trout Lake TBS, Boiler Replacement | 2024 | 320404.5725
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733759 | NBAY: Haileybury TBS, Boiler Replacement | 2025 | 220837.9849
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733760 | NBAY: Sturgeon Falls TBS, Boiler Replacement | 2025 | 180803.0286
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733761 | NBAY: Englehart TBS, Boiler Replacement | 2025 | 180803.0286
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733764 | NBAY: Eloy TBS, Boiler Replacement | 2026 | 325805.6843
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733766 | NBAY: West St TBS, Boiler Replacement | 2027 | 326119.5948
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733795 | NBAY: Widdifield TBS, Boiler Replacement | 2028 | 145874.5415
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733796 | NBAY: Mattawa TBS, Boiler Replacement | 2028 | 145874.5415
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733797 | NBAY: South River TBS, Boiler Replacement | 2028 | 145874.5415
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733820 | NBAY: Ferguson Road, Boiler Replacement | 2029 | 151661.6538
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733821 | NBAY: New Liskeard TBS, Boiler Replacement | 2029 | 232274.605
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733822 | NBAY: Earlton TBS, Boiler Replacement | 2029 | 151661.6538
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733823 | NBAY: Ravensglen TBS, Boiler Replacement | 2029 | 341580.3014
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733838 | NBAY: West Ferris TBS, Boiler Replacement | 2030 | 165525.6744
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733839 | NBAY: TCPL Co-gen North Bay, Boiler Replacement | 2030 | 253240.1344
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733840 | NBAY: Madill TBS _ Huntsville, Boiler Replacement | 2030 | 253240.1344
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733842 | NBAY: Callander TBS, Boiler Replacement | 2031 | 172111.2625
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 733851 | NBAY: Emsdale CMS, Boiler Replacement | 2031 | 172111.2625
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 734577 | NE: 43801032 - Stepan Industries, Station Retirement | 2026 | 78193.3642
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 734578 | NE: 43801017 - Huronia regional Centre, Station Retirement | 2025 | 64572.5102
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 734579 | NE: 43804002 - Occupational Centre PRS, Station Retirement | 2027 | 27754.8591
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 734580 | NE: 43101005 - Sturgeon Falls Mill SMS, Station Retirement | 2024 | 76897.0974
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Fail | Dollar threshold | 735030 | NBAY: Warren TBS, Boiler Replacement | 2030 | 165525.6744
Northern | Div_46 - North Bay & Orillia | Distribution Stations | Pass |  | 101073 | NE: 42601002 - Englehart TBS, Relocation | 2025 | 2187108.2199 | Issue/Concern/Opportunity: There is 1.5 km of unodourized gas from TC Energy pipeline to inlet of the existing TBS. The NPS2 transmission inlet line to the station has unodourized gas that could go undetected in the event of a leak due to the properties (colourless and odourless) of natural gas. Odourant is added within the station compound. However, the Odourant system is installed at the TBS which is in a populated area. The station requires relocation. Note, that the station bypass valve is also leaking on the unodourized side. A rebuild of the station and possible relocation to ensure that the natural gas is odourized appropriately. Justification: Station feeds town of Englehart and large customer Columbia Forest Products. Assets: Station 42601002 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Northern | Div_46 - North Bay & Orillia | Growth | Pass |  | 48574 | NBAY: Company Program - New Business - Scattered Mains - Contractor* | 2020 | 11650069.2731 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Northern | Div_46 - North Bay & Orillia | Growth | Pass |  | 49164 | NBAY: Upgrade Maplewood PRS (43801127) | 2023 | 5739.4036 | Issue/Concern/Opportunity: Station has growth concerns that were identified by Distribution Optimization Engineering. Station was over capacity in 2021 and will continue to be put further over capacity due to the growth. Station will require modifications to the regulators and reliefs to meet capacity concerns. The station has capacity concerns which could result in operational issues in the future. The station services approximately 650 customers and is not backfed. Assets: 43801127 Related Investments: Not applicable. | Completed | Fail | Timing - Market based supply side alternatives not applicable
Northern | Div_46 - North Bay & Orillia | Growth | Pass |  | 500427 | NBAY: Company Program - Customer Connections* |  | 48587762.1729 | North Bay Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Northern | Div_46 - North Bay & Orillia | Utilization | Pass |  | 48586 | NBAY: Meter & Regulator Inst Repl-Company* | 2020 | 8084506.2589 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 14063 | Copper Service Replacement - Area 80* | 2020 | 1291892.1834
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 30048 | Burleigh Hill Dr STC - Area 80 - 1131 | 2028 | 1757828.7048
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 30052 | Erie St STC - Area 80 - 1159 | 2029 | 1619620.8177
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 30053 | Food City Plaza STC - Area 80 - 1161 | 2032 | 641324.8638
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 30063 | Lockhart St NOTL - Area 80 - 1189 | 2031 | 1188270.3356
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 30065 | Neff St PTC - Area 80 - 1165 | 2030 | 1353297.8427
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 30074 | Rose St STC - Area 80 - 1134 | 2028 | 686333.2469
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 30076 | Shurie Rd LINC - Area 80 - 1154 | 2028 | 765231.9441
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 30077 | Summer St NFalls- Area 80 - 1137 | 2029 | 1527127.359
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 30079 | Victoria St STC- Area 80 - 1148 | 2027 | 979579.8442
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 30080 | Welland St PTC- Area 80 - 1173 | 2027 | 1039606.0453
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 102425 | Relocation Program - Area 80* | 2020 | 13424701.9126
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 103520 | Red Maple Dr Lincoln - 1-inch steel main replacement | 2028 | 392355.2344
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 502017 | Ridge Rd North Fort Erie | 2025 | 1190916.0691
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 502019 | Regional Rd 65 West Lincoln | 2025 | 216720.7225
Southeast | 80 - Niagara | Distribution Pipe | Fail | Dollar threshold | 503325 | Lundys Lane Reg. Road 20 Niagara Falls | 2025 | 625199.6808
Southeast | 80 - Niagara | Distribution Pipe | Fail | Emergent Safety | 4666 | Replacement Blanket - Area 80* |  | 2013705.2869
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 1938 | NPS 10 Glenridge Avenue, St. Catharines | 2026 | 15332118.4847 | Issue/Concern: General Concerns: Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (Vintage Steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Site-Specific Concerns: This project looks to replace approximately 8.7 km of mostly 1954 to 1960s vintage NPS 10 intermediate pressure (IP) pipe with sections of NPS 12 and NPS 8 spliced in over the years as repairs. A 2019 Depth of Cover (DOC) survey found that 366 (33%) survey locations had less than 90 cm of cover, and 90 survey locations (8%) had DOC<60 cm, with one location found having exposed pipe due to creek erosion. Poor depth of cover leads to increased third-party damages (as has been seen with blow-off valves). Other risk factors include black coal tar pipe coatings used on 1959/1960 vintage NPS 10 pipe which show evidence of degradation, yielding to corrosion. There are many unusual fittings (Stop-and-Go) and unusual construction practices (such as using unrestrained compression couplings to tie in service connections) that can lead to difficult emergency responses. For example, a recent leak repair took 24 days to complete at a cost of almost $500K due to complications from DOC, components, and construction practices. Unrestrained compression couplings (CC) have been the source of leaks due to ground settlement and increase the risk of pull-out. The river crossing at Twelve Mile Creek is very difficult to access due to steep creek banks and heavy vegetation, making it difficult to perform cathodic protection and leak surveys. It will pose as a significant concern for any required emergency response. The numerous transitions from NPS 8 to NPS 10 to NPS 12 also creates concern and difficulties for operational work to be completed. There are two main line valves that are suspected to be tied in with unrestrained CCs as per an Integrity Assessment for suspect CC locations. Cathodic protection for some of the NPS 10 segments has been historically poor, showing as much as 25% of historical readings over the last 20 years below minimum required levels. Assets: There is 8.7 km of mostly 1954 to 1960s vintage NPS 10 IP pipe with sections of NPS 12 and NPS 8 spliced in over the years as repairs that run along Glenridge Avenue from Russel Avenue south to Lockhart Drive, then along Lockhart Drive west to First Street South. Related Programs: Not applicable. | Completed | Pass | ETEE - Potentially could reduce project scope.
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 4673 | Anode Blanket - Area 80* | 2020 | 3190808.6263 | General Description: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within the EGI system. These installations and replacements are based on the Corrosion Operating Standard established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 4768 | AMP Fitting Replacement - Area 80* |  | 40070557.1653 | AMP Fittings are a below grade transition fittings. The inserted portion of copper tubing can fail due to internal corrosion. In these cases leaks develop immediately downstream of the AMP Fitting. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 8258 | Woodington Rd NFalls 1" ST Repalcement | 2023 | 1980450.7336 | Issue/Concern: 1-inch Steel and Copper Risers Replace existing 3,302 m of existing steel main and 151 services in area defined. | Completed | Fail | Timing - Market based supply side alternatives not applicable
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 13611 | Service Relay Blanket - Area 80* | 2020 | 24369554.4384 | General: A distribution service refers to the pipe between the distribution main and the customer’s meter set. Over the years, different materials have been used for this asset, including steel, copper, and varying resins of plastic, each with unique characteristics that contribute to their performance over time. Services can be repaired or replaced depending on asset condition and the nature of the issue exhibited. Generally, replacement is the preferred approach to mitigate unacceptable asset condition. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 23230 | Black Creek Rd and River Trail, Fort Erie - VPM Aldyl-A MP lined in steel | 2023 | 1706660.1545 | Issue/Concern: General: Proactive replacement program to renew aging vintage plastic pipe assets before reaching end-of-life. Vintage plastic Aldyl A mains are the earliest plastic mains used within the distribution system; the installation period of Aldyl A plastics started in the late 1960s on a field trial basis and was concluded by the end of 1976 for the EGD rate zone and 1984 for the Union rate zones. It is well known and studied in the North American gas industry that Aldyl A plastic mains have brittle-like cracking properties. The oxidation of the inner wall surface during manufacturing (also known as Low Ductile Inner Wall (LDIW)) and the large spherulites found in its microstructure causes pipe to be susceptible to cracking and premature failure in the presence of stress intensifiers such as a large number of connections, squeeze-off locations, and the presence of rock impingement points caused by rocky soil types. Site specific: MP vintage plastic main lined within old steel mains. If pipe is damaged or leaks, the migration path could cause gas to travel long distances. Difficult to pinpoint leaks and increased risk of migration into other conduits/utilities. Assets: Black Creek Rd and River Trail, Fort Erie - VPM Aldyl-A MP lined in steel Black Creek - Phase One - Scope: consists of 1001M, NPS 4 PE Intermediate Pressure (IP), 13 Medium Pressure (MP) to IP Services and one water crossing (drainage ditch). A Header at 13693 Niagara River Parkway also will be replaced as part of this phase: 230M NPS 2 PE IP and 4 MP to PI Services. Status as of 1/21/2021: Survey has been completed for both the Main Replacement as well as the Header Replacement. Drawing completed for the Main Replacement portion of the project and class 3 estimate has been submitted and completed by Construction, C55 numbers to be updated once Class 3 for Phase 2 is completed. Submitted to Land for preliminary Species at Risk (SAR) and permits review. Early consultation with Land shows existing valid easement at Header location. MTO permit will not be required. Follow up requested from Land 1/21/2021 and copy of DWG provided. Header DWG in progress – estimate was included with Phase 1 and is complete. Black Creek - Phase Two - Scope: consists of 3230M NPS 4 PE IP, 214M NPS 2 PE IP, the replacement of 17 IP to IP services and 34 MP to IP services. There are two Headers that will be replaced as part of this phase. 1) Private Laneway: 253M, NPS 2 PE IP and 2 MP to IP Services. 2) Switch Road: 363M NPS 2 PE IP and 3 MP to IP Services. Project also has one water crossing and 3 Concrete Culvert Crossings. Status as of 1/21/2021:Submitted to Land for preliminary SAR and permits review. MTO had confirmed no permit is required, SAR and other land permits are unknown at this time. Land has confirmed existing easement at one of two header locations. Letters have been prepared for delivery on site walk. Black Creek – Phase 3 – Scope: consists of 6619M NPS 2 PE IP, the replacement of 272 MP to IP services as well as the removal of MO STN 81160A and accompanying ERX recorder. Status as of 1/21/2021: Survey had been completed; submitted for preliminary SAR Review. MTO has confirmed no permit will be needed for this phase. Related Program: Not applicable | Completed | Fail | N/A - Project in construction phase
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30046 | 2nd Ave PTC - Area 80 - 1180 | 2032 | 4468978.3915 | 2nd Ave. - Area 80 - 1180 Vintage steel exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Plan Year 1 and Execute Year 2 (1711990). | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30047 | Briarsdale Dr STC - Area 80 - 1174 | 2032 | 3014797.7672 | Briarsdale Dr. - Area 80 - 1174 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization Comments: Plan Year 1 and execute Year 2. | Completed | Fail | NPS 2, cannot downsize or retire
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30049 | Cattell Dr NFalls- Area 80 - 1170 | 2032 | 2638617.049 | Cattell Dr. - Area 80 - 1170 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization | Planned
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30050 | Dexter Dr WELL - Area 80 - 1169 | 2030 | 3715273.6934 | Dexter Dr. - Area 80 - 1169 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Plan Year 1 and execute Year 2. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30054 | Forkes Rd E PTC - Area 80 - 1132 | 2031 | 3308747.1215 | Forkes Rd. E. - Area 80 - 1132 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Plan Year 1 and execute Year 2. | Planned
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30055 | Geneva St STC - Area 80 - 1187 | 2031 | 7869856.3715 | Geneva Street - Area 80 – 1187 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Plan Year 1 and execute Year 2. | Planned
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30056 | Flanders Ave STC - Area 80 - 1809 | 2030 | 4664378.1323 | Handers Ave. - Area 80 - 1156 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Plan Year 1 and execute Year 2. | Planned
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30057 | Hillcrest Ave STC - Area 80 - 1176 | 2028 | 1984698.2123 | Hillcrest Ave. - Area 80 - 1176 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30058 | Hixon St LINC - Area 80 - 1153 | 2032 | 2040131.2735 | Hixon St. - Area 80 - 1153 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30062 | Lavinia St FE - Area 80 - 1171 | 2029 | 2847536.1633 | Lavinia St. - Area 80 - 1171 Vintage steel pipes exhibit increased failures as they age, as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Plan Year 1 and execute Year 2. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30064 | McCain St PTC - Area 80 - 1136 | 2031 | 2321258.5935 | McCain St. - Area 80 - 1136 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Plan Year 1 and execute Year 2. | Planned
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30067 | Niagara Wine Route 2 NOTL- Area 80 - 1191 | 2030 | 1938421.9205 | Niagara Wine Route 2 - Area 80 - 1191 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Plan Year 1 and execute Year 2 | Planned
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30071 | Queen St LINC - Area 80 - 1150 | 2029 | 2241559.6877 | Queen St. - Area 80 - 1150 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Southeast | 80 - Niagara | Distribution Pipe | Pass |  | 30078 | Swan Dr STC- Area 80 - 1163 | 2032 | 4517357.3715 | Swan Dr. - Area 80 - 1163 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Plan Year 1 and execute Year 2. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southeast | 80 - Niagara | Distribution Stations | Fail | Dollar threshold | 7759 | THOROLD TOWNLINE GATE | 2024 | 888490.0538
Southeast | 80 - Niagara | Distribution Stations | Fail | Dollar threshold | 7760 | VINELAND GATE | 2026 | 875030.5121
Southeast | 80 - Niagara | Distribution Stations | Fail | Dollar threshold | 18850 | GRASSYBROOK & MCKENNY DISTRICT | 2026 | 157495.6018
Southeast | 80 - Niagara | Distribution Stations | Fail | Dollar threshold | 18851 | ONTARIO & DEERE DISTRICT LP | 2026 | 283358.4003
Southeast | 80 - Niagara | Distribution Stations | Fail | Dollar threshold | 18917 | TOWNLINE & RUSHOLME DISTRICT | 2023 | 144018.2711
Southeast | 80 - Niagara | Distribution Stations | Pass |  | 3610 | CROWLAND STORAGE TRANSFER | 2023 | 24124880.2414 | Crowland Storage Transfer Station is located on EGI-owned property of approximately 7,300 m2 fenced compound in the Port Colborne, Ontario, approximately 7 km southeast of Welland, Ontario, within a rural area, in close proximity to a railway corridor. This station accepts natural gas from EGI Crowland Gas Storage facilities and provides supply to and from XHP networks, through components within the measurement system, pressure control system , heating system, odourant system, and telemetry system. This station delivers and withdraws natural gas from Storage Operations Wells in the Niagara Region. The following issues have been identified at this station: Odourization: The odourant system was installed in 2000. The current configuration of the odourant system does not ensure adequate containment of the odourant product in the event of a leak and does not meet the current engineering standards and approvals. Telemetry & Electrical: The existing electrical system does not meet current EGI electrical installation standards. This poses a potential electrical hazard and faulty wiring may result in lost communications. Compliance: The Canadian Electrical Code Section 22.1 indicates that all electrical and instrumentation equipment located in a hazardous area must be rated for that area classification. The Remoter Terminal Unit (RTU) building has been identified as being located in an area classification and its equipment is not rated to operate in this environment. This is a risk of ignition and fire in the event of a gas leak. Scope Includes: 1) Install annubars on inlet and outlet. -Install actuator on each operator regulator and on valves 8, 9 and 10. Required electrical work: -Relocate RTU building out of classified area (including new building and foundation). -Install generator and automatic transfer switch. -Upgrade tower to improve signal quality. -Upgrade lighting. 2) Install filter separator and receiver on inlet. -Install moisture analyzer and gas chromatograph. -Install new YZ odourant system (including new building and foundation). -Include station bypass equipment and setup (assume bypass of the whole station is needed to complete the work). Includes retrofits to station piping for temporary station connection. -Includes all planning/design costs including drafting, surveys and permits, and geotechnical study. Assets: Crowland Station Related Programs: Major work is scheduled to take place to upgrade the EGI Storage facilities at Crowland. This project would be linked and completed in conjunction with that Storage upgrade | Completed | Fail | Distribution station condition related, IRPA not applicable
Southeast | 80 - Niagara | Distribution Stations | Pass |  | 3620 | MOUNTAIN RD GATE | 2026 | 4651715.2021 | Mountain Road Gate Station is located on EGI-owned property of approximately 1,800 m2 in a fenced compound in Niagara Falls, Ontario, approximately 10 km from Niagara Falls, within a rural/urban area. This station accepts natural gas from TC Energy and provides supply to one NPS 12 XHP network (Glendale), one NPS 12 HP network (Dorchester), and one NPS 8 IP network (Lundy’s Lane). The gate station includes a measurement system, pressure control system, heating system, odourant system, and telemetry system. This station supplies natural gas to approximately 85,700 customers in the Niagara region. The following issues have been identified at this station: Valves & Piping: Valve actuators have been installed on the outlet valves and on the heat exchanger isolation and bypass valves, but programming is required to control the actuators with the Remote Terminal Unit (RTU). Valves are functioning well but are all original valves that were installed during the installation of the gate station (approximately 30 years) and may need to be replaced due to age. Measurement: The inlet is metered by a relatively new NPS 12 ultrasonic meter (approximately 10 years). The current system does not provide measurement of the individual outlet supplies. Visibility to each outlet supply provides greater redundancy to the existing measurement and improved response capabilities. Outlet metering is to be connected to SCADA and visible to the Gas Control group. Heating: Three existing boilers at this site are old boilers that are approximately 20 years old. They have had 10 trouble call/failures over the recent years, including failures of the motors and pumps, burner lock-outs and exchanger failures. The existing heat exchanger was installed in 1995 and will be at end of life by the rebuild date. Due to recent and upcoming customer growth in the Niagara Falls area, the existing heating system will not be capable of supplying the heating requirements to meet the demand. Fuel gas station to the boilers is metered but conversion of the generator from diesel to natural gas will require it to be upsized. Pressure Control: The configuration of the existing regulators are all boot-style regulators, posing an undesired higher risk and high associated ongoing maintenance costs. The regulators will have to be replaced. In addition, an upstream filter should be installed. Odourization: The odourant injection system is a combination of Link and Wilroy pumps which are located in a separate building from the tank. The Pump building has no containment if a leak is experienced. The tank sits in a metallic odourant building without adequate containment which will have to be replaced with a functional building with proper containment, and ancillary equipment including fire suppression and gas detection. The current configuration of the odourant system does not meet the current engineering standards and approvals. The odourant package should be replaced. Telemetry and Electrical: The existing electrical system does not meet current EGI electrical installation standards. This poses a potential electrical hazard and faulty wiring may result in lost communications. The RTU has been recently replaced (2016) and rewiring will have to be done to install it into an RTU building. The existing generator is an old diesel generator and will be replaced with a new natural gas generator. Asset: Mountain Road Gate station assets. Related Program: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southeast | 80 - Niagara | Distribution Stations | Pass |  | 7752 | NIAGARA GATE | 2024 | 4550640.3949 | Niagara Gate Station is located on EGI-owned property of approximately 1,900 m2 fenced compound in the Town of Niagara-on-the-Lake , Ontario, approximately 7 km from Niagara-on-the-Lake, ON, within a rural area. This station accepts natural gas from TC Energy and provides supply to an XHP network, through components within the Measurement system, Pressure Control system, Heating system, Odourant system, and Telemetry system. This station supplies natural gas to approximately 6,800 customers in the Niagara Region. The following issues have been identified at this station: Heating: The existing boilers at this site are 15 years old, they have had numerous trouble call/failures recently, including failures of the motors and pumps, burner lock-outs and exchanger failures, and are at end of life. Repairs have been made but the reliability of the heating system is no longer acceptable. The proposal is to replace the existing boiler system with a CWT outside of any hazardous area. Telemetry & Electrical: The existing Electrical system does not meet current EGI electrical installation standards. This poses a potential electrical hazard and faulty wiring may result in lost communications. A new natural gas generator for backup power will also be required. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southeast | 80 - Niagara | Distribution Stations | Pass |  | 16586 | TALISMAN PRODUCTION | 2025 | 1916320.9958 | Issue/Concern: Measurement: Currently, a Turbine meter is used with no problems. Assets: Odourant, Telemetry, Related Program (if applicable). Measurement: There is flanged obsolete Daniel Senior orifice meter on site on the outlet piping that needs to be removed; a simple flanged spool piece can be inserted. Odourant: Old odourant pumps and a separate odourant tank need to be put into a single building with containment. Telemetry and Electrical: Currently, old Remote Terminal Unit (RTU) 3330 is required to be upgraded. The Telemetry and Electrical systems do not meet current EGI standards, do not contain backup power supply in the event of power loss, and are approaching end of useful life. The existing RTU is obsolete and is required to be upgraded to current standards along with new communications equipment in order to eliminate cybersecurity threats. There should be an upgrade of RTU to Control Wave Micro. There should be an upgrade of electrical wiring to the new Odourant building. This site has no generator. Piping: There is a live riser in place that is flanged closed, so removing it may be a consideration. There is no distribution regulation; line pressure is taken from the compressors. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southeast | 80 - Niagara | Growth | Pass |  | 3766 | Area 80 - Apartment Ensuite - New Construction* |  | 9616.3834 | Vertical Subdivision - A multiple unit residential building where each suite is individually metered. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGD develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long term plans EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. Enbridge reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers; and, - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing Assets: Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | 80 - Niagara | Growth | Pass |  | 3769 | Area 80 - Commercial - New Construction* |  | 23213666.6144 | Issue/Concern: Commercial New Construction refers to a customer intending to run a commercial business in a newly-constructed building and intending to using natural gas to meet energy needs Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | 80 - Niagara | Growth | Pass |  | 3770 | Area 80 - Industrial - New Construction* |  | 9245468.4331 | Issue/Concern: Industrial New Construction refers to a customer intending to run an industrial manufacturing business in a newly-built facility and intending to use natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | 80 - Niagara | Growth | Pass |  | 3772 | Area 80 - Residential - New Construction* |  | 53055300.4678 | Issue/Concern: Residential New Construction refers to anew residential construction development of detached single homes constructed by the builder for domestic purposes. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | 80 - Niagara | Growth | Pass |  | 3773 | Area 80 - Residential - Replacement* |  | 8130461.751 | Issue/Concern: Residential Replacement refers to a residential replacement customer using a fuel other than natural gas for domestic purposes and is converting to natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | 80 - Niagara | Growth | Pass |  | 3822 | Area 80 - Commercial - Replacement* | 2028 | 8819477.0506 | Issue/Concern: Commercial Replacement refers to a commercial replacement customer using a fuel other than natural gas for commercial business and is converting to natural gas. EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | 80 - Niagara | Growth | Pass |  | 736688 | NW 8521 Feeder Rd E Station Reinforcement SRP | 2023 | 309806.369 | Issue/Concern/Opportunity: A new station is required to increase security of supply for Intermediate Pressure (IP) NW8521, and maintain 140 kPa as minimum system pressure in this Maximum Operating Pressure (MOP) 276 kPa system. In January 2022, 17 psig was recorded as low pressure in cold snap. Assets: District station Related Program: Not applicable | In Progress
Southeast | 80 - Niagara | Utilization | Pass |  | 13549 | MXGI Area 80* | 2019 | 26240787.1903 | Meters: Meters are used to determine the gas consumption input of customer billing. The replacement program for meters is mandated by Measurement Canada. The program includes: testing, repair, and replacement requirements of meters and instruments. All verified meters are approved by Measurement Canada with an issuance of a certificate which identifies that the meter complies with Electricity and Gas Specification S-EG-02. The Company must ensure all measurement devices remain in compliance for annual audits by Measurement Canada. Measurement Canada specifies tolerances under which the meter must operate in the field. The Company must demonstrate that all aspects of its meter sampling, maintenance, and replacement comply with these criteria in order to be accredited by Measurement Canada to be an “Authorized Service Provider” and adhere to Measurement Canada’s accreditation standard S-A-01. Meters may also require exchange for issues such as: damages, leaks, customer billing issues. Regulation: Regulators are the last line of defense for over-pressure to the customer. The condition of regulation systems is determined by regulator performance, corrosion of piping and regulators, and adherence to installation specifications. Failure of the regulation system can cause pressured gas to enter the premise, resulting in failure of gas equipment, loss of containment, and potentially fire or explosion. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_03 - Sarnia | Distribution Pipe | Pass |  | 733553 | NPS 6 Retrofit | 2024 | 2594374.8369 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2025 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 1272 | Brantford North Retrofit |  | 934147.7163
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48381 | BRAN: Dist-Repl-Contr-Mains Leakage* | 2020 | 4027223.936
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48849 | BRAN - Otterville Rd. (James to Middleton) Repl. BU - Otterville | 2023 | 871871.2019
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48929 | BRAN - Lawrence Rd Repl. BU - Norfolk | 2023 | 92564.0246
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48933 | BRAN - Water St. Repl. BU - Vittoria | 2023 | 165186.0133
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48934 | BRAN - Rebecca St. Repl. BU - Vittoria | 2023 | 95341.6568
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48935 | BRAN - Colborne St. at Johnson Rd. Repl. BU - Brantford | 2023 | 47842.1137
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48955 | BRAN -Northern Ave. (Adams to Connaught) Repl. BU - Delhi | 2024 | 775572.5897
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48956 | BRAN - Connaught Ave. (Hwy 3 to Delcrest) Repl. BU - Delhi | 2024 | 417724.2573
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48958 | BRAN - Churchill (Connaught to Argyle) Repl. BU - Delhi | 2024 | 129138.3709
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48963 | BRAN - Given Rd at Lyndoch Rd Repl. BU - Norfolk | 2024 | 32508.2479
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48964 | BRAN - Clyde St. and North Court St. Repl. BU - Norwich | 2024 | 79065.5955
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48966 | BRAN - Carmen St. Repl. BU - Norwich | 2024 | 52138.8465
Southeast | Div_06 - Brantford | Distribution Pipe | Fail | Dollar threshold | 48967 | BRAN - King St. (Ffth to Third) Repl. BU - Tillsonburg | 2024 | 97797.7285
Southeast | Div_06 - Brantford | Distribution Pipe | Pass |  | 48928 | BRAN - Schafer Side Rd. Repl. BU - Norfolk | 2023 | 1644624.2991 | Project-Specific: 511907170 General: The Bare Unprotected Program is to replace all the bare and unprotected steel mains within EGI’s franchise. These mains are more susceptible to leaks as they have not been cathodically protected since installation. Removing these mains from service will reduce potential for leaks due to corrosion. If this project spend is reduced or deferred, more maintenance dollars will have to be spent repairing leaks on pipe which is nearing end of life. | Planned
Southeast | Div_06 - Brantford | Distribution Pipe | Pass |  | 733722 | NPS 12 Kirkwall-Dominion Tie-over |  | 2211936.7083 | General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent In-line Inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_06 - Brantford | Distribution Pipe | Pass |  | 733743 | NPS 12 Guelph Reinf-Guelph Tie-over | 2026 | 4103385.7425 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2027 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_06 - Brantford | Distribution Pipe | Pass |  | 735641 | Brantford Transmission Station Take-off Retrofit ECDA to ILI 2027 |  | 2081614.4346 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2029 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 100343 | BRAN: 13T-403 Otterville Springford Distribution Station, Norwich Twp, Station Rebuild (Capital Maintenance), Proj# 06-21-701 | 2023 | 90723.1807
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 100422 | BRAN: 12U-504 Simcoe Hunt Street South Distribution Station, Simcoe, Station Rebuild (Capital Maintenance) | 2032 | 2715.9825
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 100550 | BRAN: 12S-101 Tillsonburg Potter's Road Distribution Station, Tillsonburg, Station Rebuild (Capital Maintenance) | 2026 | 32580.5684
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 100610 | BRAN: 12S-202 Fernlea Farm Distribution Station, Delhi, Station Rebuild (Capital Maintenance), Proj# 06-22-701 | 2023 | 239764.5805
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 100611 | BRAN: 16V-402R Dunsdon St Distribution Station, Brantford, Station Rebuild (Capital Maintenance), Proj# 06-22-704 | 2023 | 257202.0046
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 100614 | BRAN: 15V-111R Stanley St Distribution Station, Brantford, Station Rebuild (Capital Maintenance), Proj# 06-22-703 | 2023 | 239764.5805
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 100624 | BRAN: 12T-503 ON Energy Producer Station, Delhi, Station Rebuild (Capital Maintenance), Proj# 06-21-704 | 2023 | 34381.6181
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 100626 | BRAN: 11V-101 Port Dover South Distribution Station, Port Dover, Station Rebuild (Capital Maintenance), Proj# 06-22-700 | 2023 | 6850.4166
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 100627 | BRAN: 11V-101 Port Dover South Distribution Station, Port Dover, Station Rebuild (Telemetry) | 2032 | 74689.52
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 503639 | BRAN: 17U-302 Brantford Transmission Station, Brantford, Station Rebuild (Capital Maintenance), Proj# | 2023 | 109606.6654
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735246 | WATE: 17T-202 N.Dumphries Trans. Stn FIMP* | 2031 | 209891.7836
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735277 | BRAN: 11V-401R Pt Ryerse Commercial St LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735278 | BRAN: 09T-306R Front Street Avenue LP | 2026 | 65161.1369
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735279 | BRAN: 11U-601R Pt Ryerse Young & Rolph W Hill LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735280 | BRAN: 12R-607R Tillson Ave, South of Hyman LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735281 | BRAN: 12T-506R Delhi Queen & Church Stn LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735282 | BRAN: 12U-607R Simcoe Queen St S & Grove LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735283 | BRAN: 12U-609R Simcoe South & John St LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735284 | BRAN: 13U-603R Waterford Temperence & Leamon LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735285 | BRAN: 15U-301R St Paul & Dublin LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735287 | BRAN: 15V-406R Mohawk Brighton LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735313 | BRAN: 15U-308R Brantford Grand & Jubilee LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735319 | BRAN: 15V-408R Brighton & Superior LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735326 | BRAN: 11V-202R Pt Dover Nelson & George St LP | 2024 | 64080.9145
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735327 | BRAN: 11V-204R Pt Dover Clinton & St Patrick LP | 2024 | 64080.9145
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735328 | BRAN: 09T-303R Church St & Erie Ave LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735329 | WATE: 09T-307R Ellis & Alley St LP | 2024 | 64080.9145
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735330 | BRAN: 12R-302R Victoria St & Niagara St Station LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735331 | BRAN: 12R-303R Tillson Ave Dist Station LP | 2024 | 64080.9145
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735332 | BRAN: 12U-501 Simcoe Queen St South of Hwy 3 (2nd Stage) LP | 2024 | 64080.9145
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735333 | BRAN: 12U-602R Simcoe Union & Talbot Stn LP | 2024 | 64080.9145
Southeast | Div_06 - Brantford | Distribution Stations | Fail | Dollar threshold | 735334 | BRAN: 12U-606R Simcoe Metcalfe & Robinson LP | 2023 | 62276.5144
Southeast | Div_06 - Brantford | Distribution Stations | Pass |  | 103426 | BRAN: 16U-601 Brantford Gate Station, Station Rebuild (Capital Maintenance), Proj# 57-22-701 | 2023 | 9179558.2256 | Issue/Concern/Opportunity: Rebuild entire station to address station integrity issues, maintenance/operational issues, and also allow for additional load capacity through the Eastern Transmission system. Justification: A full rebuild will correct station integrity issues, maintenance/operational issues, and enable additional capacity. Assets: Brantford Gate Station (16U-601) Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southeast | Div_06 - Brantford | Growth | Pass |  | 48379 | BRAN: Company Program - New Business - Scattered Mains - Contractor* | 2020 | 12733740.0826 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | Div_06 - Brantford | Growth | Pass |  | 500419 | BRAN: Company Program - Customer Connections* |  | 31915261.14 | Brantford Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | Div_06 - Brantford | Utilization | Pass |  | 48386 | BRAN: Meter & Regulator Inst Repl-Contractor* | 2020 | 21705028.5603 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_07 - Waterloo | Distribution Pipe | Fail | Dollar threshold | 1282 | Owen Sound Section 2 Retrofit |  | 992351.9248
Southeast | Div_07 - Waterloo | Distribution Pipe | Fail | Dollar threshold | 48398 | WATE: Dist-Repl-Contr-Services* | 2020 | 11786290.7515
Southeast | Div_07 - Waterloo | Distribution Pipe | Fail | Dollar threshold | 48936 | WATE - Hamilton St. Repl. BU - Cambridge | 2023 | 593079.1753
Southeast | Div_07 - Waterloo | Distribution Pipe | Fail | Dollar threshold | 48937 | WATE - Glen Morris (Selkirk to Stanley) Repl. BU - Cambridge | 2023 | 194377.4568
Southeast | Div_07 - Waterloo | Distribution Pipe | Fail | Dollar threshold | 733713 | NPS 12 Owen Sound Section 1 Retrofit |  | 934147.7163
Southeast | Div_07 - Waterloo | Distribution Pipe | Fail | Dollar threshold | 733714 | NPS 6 Hawtrey Trans. Station Take-off Replacement | 2023 | 498212.1154
Southeast | Div_07 - Waterloo | Distribution Pipe | Fail | Timing | 1269 | Owen Sound Section 1 Retrofit | 2023 | 1992848.4116
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30234 | Div. 06 - Brant - Broadway St W - Southeast - Waterloo - 1378 | 2032 | 5408533.6608 | Div. 06 - Brant - Broadway St. W. - Southeast - Waterloo - 1378 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Brantford is currently doing a lot of road reconstruction around this area. Contact municipality to see which roads have been recently redone - project has been updated to reflect moratorium until 2026. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30237 | Div. 06 - Brantford - Abigail Ave - Southeast - Waterloo - 1309 | 2032 | 3398728.3039 | Div. 06 - Brantford - Abigail Ave - Southeast - Waterloo - 1309 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Every home will require a new farm tap. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30238 | Div. 06 - Brantford - Balmoral Dr - Southeast - Waterloo - 1291 | 2030 | 3118012.3918 | Div. 06 - Brantford - Balmoral Dr. - Southeast - Waterloo - 1291 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Station 11T-440 may need to be rebuilt as part of the project. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30243 | Div. 06 - Brantford - Dundas St E - Southeast - Waterloo - 1303 | 2028 | 2095705.5002 | Div. 06 - Brantford - Dundas St. E. - Southeast - Waterloo - 1303 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30244 | Div. 06 - Brantford - Elgin St - Southeast - Waterloo - 1296 | 2032 | 5590098.1261 | Div. 06 - Brantford - Elgin St. - Southeast - Waterloo - 1296 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Some of the piping is inside of Brantford Balmoral Gate Station (16U-602). Scope of project would require a bypass of station to install the new inlet and outlet. There is a history of mercury in the soil in and around the Brantford Balmoral Gate Station, so soil assessments will be required. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30245 | Div. 06 - Brantford - Ewing Dr - Southeast - Waterloo - 1316 | 2029 | 3311557.133 | Div. 06 - Brantford - Ewing Dr. - Southeast - Waterloo - 1316 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: City of Brantford is restoring Wood St. and Charing Cross. Project was updated to reflect a moratorium until 2026. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30246 | Div. 06 - Brantford - Franklin St - Southeast - Waterloo - 1388 | 2031 | 4963681.9269 | Div. 06 - Brantford - Franklin St. - Southeast - Waterloo - 1388 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30248 | Div. 06 - Brantford - Greenwich St - Southeast - Waterloo - 1332 | 2029 | 3486631.7391 | Div. 06 - Brantford - Greenwich St - Southeast - Waterloo - 1332 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30252 | Div. 06 - Brantford - St George St - Southeast - Waterloo - 1312 | 2031 | 5813158.8079 | Div. 06 - Brantford - St. George St. - Southeast - Waterloo - 1312 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30253 | Div. 06 - Brantford - St George St 2 - Southeast - Waterloo - 1386 | 2030 | 6018336.4516 | Div. 06 - Brantford - St. George St. 2 - Southeast - Waterloo - 1386 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: MTO permit may be required and it is a lengthy process. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30256 | Div. 06 - Brantford - Toll Gate Rd - Southeast - Waterloo - 1314 | 2029 | 3565964.3926 | Div. 06 - Brantford - Toll Gate Rd. - Southeast - Waterloo - 1314 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Piping on Hill Ave. from Charing Cross to Wood St. was replaced with NPS 2 PE in 2021 as part of 06-21-609 Hill Ave. (Charing Cross to Wood St.) replacement project. The City of Brantford is restoring Hill Ave., Wood St. and Charing Cross. Pipe on Hill Ave. from Charing Cross to Wood St. was replaced in 2021. This project was updated to reflect a moratorium until 2026. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30260 | Div. 06 - Norfolk County - Andy's Corners - Norfolk County Rd 21 - Southeast - Waterloo - 1325 | 2028 | 1674984.8817 | Div. 06 - Norfolk County - Andy's Corners - Norfolk County Rd. 21 - Southeast - Waterloo - 1325 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Customer station 12U-327C will need to be shut down and monetary compensation may be required. Producer station 12U-301 may need to be built. Inlet gas is not owned by EGI and coordination is required. Farm taps will need to be built for every service. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30266 | Div. 06 - Norfolk County - Tillsonburg - 3rd Concession Rd N - Southeast - Waterloo - 1310 | 2031 | 4084703.4964 | Div. 06 - Norfolk County - Tillsonburg - 3rd Concession Rd. N. - Southeast - Waterloo - 1310 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There is a rail crossing. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30267 | Div. 06 - Tillsonburg - Brownsville Rd - Southeast - Waterloo - 1391 | 2027 | 2548548.5292 | Div. 06 - Tillsonburg - Brownsville Rd. - Southeast - Waterloo - 1391 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There are inside regulators and wall-to-wall concrete in downtown core. | Completed | Fail | NPS 2, cannot downsize or retire
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30269 | Div. 06 - Tillsonburg - Potters Rd - Southeast - Waterloo - 1375 | 2028 | 2759507.2713 | Div. 06 - Tillsonburg - Potters Rd. - Southeast - Waterloo - 1375 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30270 | Div. 06 - Tillsonburg - Quarter Town Line - Southeast - Waterloo - 1383 | 2032 | 4182287.7477 | Div. 06 - Tillsonburg - Quarter Town Line - Southeast - Waterloo - 1383 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Geotechnical assessments are required. Installation across Grand River required. Large industrial customers would require planned shutdowns as a result of replacement. Permitting can be lengthy. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 30272 | Div. 06 - Tillsonburg - Victoria St - Southeast - Waterloo - 1324 | 2030 | 2085173.2678 | Div. 06 - Tillsonburg - Victoria St. - Southeast - Waterloo - 1324 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Reconstruction of Union St. (Moore St. to Margaret St.) is proposed sometime in the future by City of Waterloo; however, timing/funding has not been confirmed as it is a lower-priority project for them. Also, Union St., Waterloo (King St. to Moore St.), just east of the limits of this project, is scheduled for reconstruction by City of Waterloo for 2022 – 2023. | Planned
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 48397 | WATE: Dist-Repl-Contr-Mains Municipal* | 2020 | 105647507.9209 | General: Projects in the relocation category are capital expenditures required to replace or relocate segments of pipeline in order to accommodate municipal infrastructure work. The cost sharing for this work is managed through the Franchise Agreements established with municipalities. A consultative approach is used between the municipality and EGI to avoid conflicts with municipal infrastructure early in the planning stage. If a conflict is unavoidable, pipeline assets are typically relocated or replaced. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 48409 | WATE: Anodes* | 2020 | 8337037.8949 | General: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within EGI's system. These installations and replacements are based on the internal Standard Operating Practice established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 733619 | NPS 12 Owen Sound Reinforcement Retrofit |  | 1763772.2693 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2027 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% SMYS. It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_07 - Waterloo | Distribution Pipe | Pass |  | 735796 | NPS 12 Waterloo-Erbsville Take-Off Project, Dig Site 37 |  | 1743742.4038 | 2022 forecast: One dig based on previous years ECDA. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent in-line inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 48418 | WATE: 19V-105R Stone & Gordon Vault Station, Guelph, Station Rebuild (Capital Maintenance), Proj# 07-19-702 | 2023 | 800377.7633
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 49057 | WATE: 19R-501R Wellesley Distribution Station, Wellesley Twp, Station Rebuild (Load Growth), Proj# 07-21-703 | 2023 | 62276.5144
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 100240 | WATE: Mt Elgin Dist Stn, Mt Elgin, Station | 2027 | 156107.2052
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 100615 | WATE: 17T-202 North Dumfries Distribution Station, North Dumfries, Station Rebuild (Obsolete Heater) | 2023 | 112097.726
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 100617 | WATE: 18U-504 Cambridge East Distribution Station, Cambridge, Station Rebuild (Obsolete Heater) | 2024 | 961213.7174
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 100829 | WATE: 19U-601 Guelph Highway 24 Gate Station, Guelph, Station Rebuild (Capital Maintenance), Proj# 07-21-711 | 2023 | 623387.9094
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 100833 | WATE: 21T-301 Salem Gate Station, Salem, Station Rebuild (Capital Maintenance), Proj# 07-22-700 | 2023 | 232914.1639
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 100912 | WATE: 23Q-301 Harriston Gate Station, Harriston, Station Rebuild (Capital Maintenance), Proj# 07-21-713 | 2023 | 498212.1154
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 101092 | HALT-440 Harrop | 2025 | 387435.0612
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 503214 | WATE: 19S-603 Waterloo-Laurel Creek Station, Waterloo, Station Rebuild (Capital Maintenance), Proj# 07-22-705 | 2023 | 239764.5805
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 503215 | WATE: 22T-501R Alma Distribution Station, Alma, Station Rebuild (Capital Maintenance), Proj# 07-21-707 | 2031 | 637750.6391
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735226 | WATE: 19U-201 Guelph West Gate Stn. FIMP | 2023 | 186829.5433
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735235 | WATE: 21s-601 Fergus 1st Trans Stn FIMP* | 2031 | 351366.719
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735239 | WATE: 19S-201 Heidelburg Gate FIMP* | 2032 | 203698.691
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735247 | WATE: 23R-602 Rothsay Trans Stn,FIMP* | 2032 | 193717.5306
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735248 | WATE: 18S-401 Markdale Stn. FIMP* | 2028 | 206426.238
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735249 | BRAN: 14S-601 Norwich Brick Gate Stn. FIMP | 2030 | 212212.4031
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735250 | WATE: 17T-201 New Dundee Gate Stn FIMP | 2030 | 212212.4031
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735252 | WATE: 18T-402 Mannheim Trans Stn | 2032 | 203698.691
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735258 | WATE: 19U-601R Rozelle Rd. Dist. Stn FIMP | 2030 | 212212.4031
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735260 | WATE: 22S-402 Moorefield Dist. Stn. FIMP | 2030 | 212212.4031
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735262 | WATE: 30N-501 Southhampton Gate Stn. FIMP | 2032 | 203698.691
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735263 | WATE: 30Q-105C Sutherland Downs Pit FIMP | 2032 | 203698.691
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735269 | WATE: 12T-102 Norwich-Middleton Town Stn. FIMP | 2030 | 212212.4031
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735307 | WATE: 18U-205R Hungerford & Walker LP | 2023 | 62276.5144
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735308 | WATE: 18U-220R Bechtel & Millvue LP | 2023 | 62276.5144
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735310 | WATE: 18U-407R Church & Sherring LP | 2023 | 62276.5144
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735320 | WATE: 17U-211R Stanley @ Glenmorris LP | 2023 | 62276.5144
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735321 | WATE: 17U-214R Middleton St at Waterworks LP | 2023 | 62276.5144
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735322 | WATE: 18U-403R Agnes & William LP | 2023 | 62276.5144
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735324 | WATE: 18U-418R 122 Dolph St N LP | 2023 | 62276.5144
Southeast | Div_07 - Waterloo | Distribution Stations | Fail | Dollar threshold | 735325 | WATE: 18U-506R Bishop & King LP | 2023 | 62276.5144
Southeast | Div_07 - Waterloo | Distribution Stations | Pass |  | 503275 | Waterloo/Brantford PFM Compliance Program* |  | 1190069.2461 | Issue/Concern/Opportunity: -PFMs that require a bypass will be rebuilt w/bypass to the new standard: oWhen they are due for a meter exchange and in the meter seal expiry year, provided that year is between 2022 and 2026. This will fall under the meter exchange budget and costs are not covered in this program. oIf the meter seal year is not between 2022 and 2026, the set will be rebuilt with a bypass the year after it is inspected. This will allow the technicians to identify which will require rebuilt at the time of inspection, and Sohan and I will be developing a process to get work orders generated for these rebuilds after the inspection. Also ensures that we focus our efforts on rebuilding active PFMs requiring rebuild. While I originally mentioned a proactive strategy to rebuild prior to the inspection year, we decided against that. -Assumption is that 50% of PFMs will need to be rebuilt. -Calculations are based on an estimate of $5500 per rebuild. As you know there is a significant swing depending on the pipe size, volume, existing set up (first stage cut, etc) that may influence this including the release of the new SEADs designs, that I have not seen yet. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30527 | SRP_Southeast_Baden_18S-501STN_Rebuild | 2029 | 956424.7893 | Increase capacity. | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30528 | SRP_Southeast_Baden_Peel St_Reinforcement_NPS6_400m_420kPa | 2028 | 644963.2575 | New reinforcement main along Bleams Rd. E. is required. | Completed | Pass | CNG, ETEE - Potentially could reduce or defer project scope.
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30529 | SRP_Southeast_Brantford_Maple Grove Rd_Reinforcement_NPS6_830m_420kPa | 2027 | 1323086.6243 | Pipe reinforcement required to maintain system pressures due to growth | Completed | Pass | CNG , ETEE - CNG could defer project and ETEE could reduce or defer project.
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30530 | SRP_Southeast_Breslau_19T-601RSTN_Rebuild | 2028 | 1350207.9308 | Increase capacity. | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30532 | SRP_Southeast_Breslau_Sawmill Rd_Reinforcement_NPS4_500m_3450kPa | 2027 | 797040.1753 | High Pressure (HP) reinforcement along Sawmill Rd. is required. | Completed | Pass | CNG, ETEE - Potentially could reduce or defer project scope.
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30533 | SRP_Southeast_Breslau_Sawmill Rd_Reinforcement_NPS4_900m_3450kPa | 2032 | 1550035.0859 | High Pressure (HP) reinforcement is required along Sawmill Rd. This is a continuation of project SRPR OSGW 2027_005. | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30536 | SRP_Southeast_Cambridge_Guelph Ave_Reinforcement_NPS6_1000m_420kPa | 2026 | 1467639.8722 | Reinforce existing main along Guelph Ave. in Cambridge with 1,000 m NPS 6 PE. | Completed | Pass | CNG, ETEE - Potentially could reduce or defer project scope.
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30537 | SRP_Southeast_Cambridge_Pinebush Rd_Reinforcement_NPS6_470m_420kPa | 2023 | 614669.1973 | Reinforce existing NPS 2 PE along Pinbush Rd. with approximately 470 m NPS 6 PE. Project has been pushed to 2023. | Completed | Fail | N/A - Investment Cancelled
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30540 | SRP_Southeast_Kitchener_Bleams_Reinforcement_NPS12_10m_6160kPa | 2023 | 809594.7373 | Install an above-grade valve site with 12-inch crossover and scraper bar tees. | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30541 | SRP_Southeast_Listowel_21Q-103RSTN_Rebuild | 2024 | 411014.9856 | Increase capacity and maximum sustainable. | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30542 | SRP_Southeast_Owen Sound_County Rd 40_Reinforcement_NPS12_11800m_4670kPa | 2025 | 34094285.3888 | Loop existing 10-inch Steel 4,670 kPa main from existing PH4 reinforcement to Squire, Ontario with 12-inch steel main. Install valve site and 12-inch receiver facilities. | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30545 | SRP_Southeast_Port Elgin_29N-101STN_Rebuild | 2024 | 1318144.3599 | Increase capacity. | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30547 | SRP_Southeast_Southampton_30N-501STN_Rebuild | 2030 | 1335240.4403 | Increase capacity. | Completed | Pass | CNG, ETEE - Potentially could reduce or defer project scope.
Southeast | Div_07 - Waterloo | Growth | Pass |  | 30548 | SRP_Southeast_Southampton_South St_Reinforcement_NPS6_600m_550kPa | 2028 | 967444.9688 | A new main from Railway Rd. running along South St. is required. | Completed | Pass | CNG, ETEE - Potentially could reduce or defer project scope.
Southeast | Div_07 - Waterloo | Growth | Pass |  | 48396 | WATE: Company Program - New Business - Scattered Mains - Contractor* | 2020 | 29699612.9061 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | Div_07 - Waterloo | Growth | Pass |  | 48998 | WATE - Breslau System Reinforcement | 2022 | 2816.144 | Issue/Concern/Opportunity: System Reinforcement - Loop existing 2-inch PE with 1,300 m 6-inch PE along Victoria Rd. S. from Clair Rd. E. southerly to #1953 Victoria Ave. S. tying into NPS 4 PE main. (WAT FBPR 2022_1) Per Distribution Optimization Engineering (DOE) 2021 System Reinforcement Plan (SRP). Asset: 2-inch PE with 1,300 m 6-inch PE along Victoria Rd. S. from Clair Rd. E. southerly to #1953 Victoria Ave. S. tying into NPS 4 PE main. (WAT FBPR 2022_1) Related Program: N/A | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 49079 | SRP_Southeast_Guelph_Victoria Rd S_Reinforcement_NPS6_1500m_420kPa | 2026 | 1204125.6804 | Issue/Concern/Opportunity: System Reinforcement - Loop existing 2-inch PE with 1,300 m 6-inch PE along Victoria Rd. S. from Clair Rd. E. southerly to #1953 Victoria Ave. S. tying into NPS 4 PE main. (WAT FBPR 2022_1) Per Distribution Optimization Engineering (DOE) 2021 System Reinforcement Plan (SRP) review, project was deferred from 2022 to 2026. Asset: 2-inch PE with 1,300 m 6-inch PE along Victoria Rd. S. from Clair Rd. E. southerly to #1953 Victoria Ave. S. tying into NPS 4 PE main. (WAT FBPR 2022_1) Related Program: N/A | Completed | Pass | CNG, ETEE - CNG potentially could reduce or defer project scope, ETEE potentially could eliminate, reduce or defer project scope.
Southeast | Div_07 - Waterloo | Growth | Pass |  | 49104 | WATE: Starlight Dist Stn, Meaford, Growth | 2025 | 14978.2395 | Issue/Concern/Opportunity: Station is to be rebuilt with 9.S-150FR. There is over-capacity due to load additions. Asset: Station ID: 31T-102R. Related Program: N/A | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 49105 | WATE: Baden Dist Stn, Baden, Growth | 2025 | 1056820.8741 | Issue/Concern/Opportunity: A new distribution station for growth in Baden off the 6,160 kPa system delivering 1,900 kPa outlet is required. Predicted flow of 8,000 m3/h is required. It is a similar station to 18S-374 in 2018. EGI is not meeting minimum inlets at 19R-501R (Wellesley District Regulating Station) and 19R-502R (Hammer District Regulating Station). This project may be pushed into 2024 but need it to be flowing in 2024. This has been deferred to 2025 per the 2021 System Reinforcement Plan (SRP) updates. Asset: 19R-501R (Wellesley District Regulating Station) and 19R-502R (Hammer District Regulating Station) Related Program: N/A | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 49149 | WATE - Mount Forest System Reinforcement | 2027 | 388568.0278 | Issue/Concern/Opportunity: A system reinforcement is required. Loop 2-inch PE with 4-inch PE along Main St. N. 600 m NPS 4 PE from Sligo Rd. to Cora Lea St. Minimum pressures are NW of town. (WAT FBPR 2025_4) Asset: Main St. N. 600 m NPS 4 PE from Sligo Rd. to Cora Lea St. Related Program: N/A | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 49794 | WATE: Listowel System Reinforcement, Proj# 07-21-705 | 2023 | 1743742.4038 | Listowel - 1.9 km of 6-inch ST at 1,900 kPa MOP. This project in conjunction with the 2024 project will accommodate approximately 5 years' growth on the Listowel lateral starting in 2023, preferred alternative is MOP upgrade. This project has 2021 prework (direct assessment, etc.). Results of the prework may change the 2024 capital requirements. | Completed | Pass | CNG, ETEE - CNG potentially could reduce or defer project scope, ETEE potentially could eliminate, reduce or defer project scope.
Southeast | Div_07 - Waterloo | Growth | Pass |  | 100831 | WATE: 21U-101 Fergus Second Stage, Fergus, Station Rebuild (Load Growth), Proj# | 2023 | 890554.1562 | Issue/Concern/Opportunity: Station is expected to be at capacity in 2023. Rebuild is required to restore capacity for Fergus system and enable additional growth. Assets: 21U-101 Fergus Second Stage Related Program: Not applicable | Planned
Southeast | Div_07 - Waterloo | Growth | Pass |  | 500420 | WATE: Company Program - Customer Connections* |  | 88065709.5982 | Waterloo Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | Div_07 - Waterloo | Utilization | Pass |  | 48406 | WATE: Meter & Regulator Inst Repl-Contractor* | 2020 | 50721224.6356 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_07 - Waterloo | Transmission Pipe & Underground Storage | Pass |  | 735006 | Trafalgar NPS 26 - Line Lowering | 2023 | 6352204.4709 | Project-Specific: Replacement of 6 sections (1.3 km, 0.5 km, 0.2 km, two small depth-of-cover areas, and a stream crossing) of NPS 26 of the Trafalgar Lines due to depth-of-cover issues found. General: Sections of the NPS 26 Trafalgar pipeline have been identified as shallow with depth of cover below the minimum permissible by TSSA. This project will mitigate these areas by lowering the pipeline through these areas. There will be two to three segments lowered within the Galt Gate-Kirkwall segment. Mitigation of depth-of-cover sites that are out of compliance with CSA Z662 and TSSA requirements will be necessary. Some of the known sites are discovered during annual Depth of Cover Surveying, while others are reported by company crews when performing maintenance work or by a third party. At this time, the specific work scope of each year is not defined and this is a blanket program as a placeholder in the budget. The mitigation work will include the construction costs from sites identified and planned for the current year, as well as work on sites that are newly identified. Scope of work can vary from small remediation projects to add fill, concrete or bank stabilization, to short replacement of pipe. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 30400 | Div. 16 - Haldimand - Fisherville - Erie Ave N 2 - Hamilton - 1730 | 2030 | 1696336.9909
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 30409 | Div. 16 - Hamilton - Oak Ave - Hamilton - 1818 | 2027 | 1463707.4507
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 30410 | Div. 16 - Hamilton - Province St N - Hamilton - 1416 | 2028 | 1223329.2821
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 30411 | Div. 16 - Hamilton - Rosemary Ave - Hamilton - 1731 | 2030 | 1477245.0578
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48429 | HAMI: Dist-Repl-Contr-Mains Leakage* | 2019 | 4822387.7574
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48430 | HAMI: Dist-Repl-Contr-Services* | 2020 | 4788741.6033
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48788 | HAMI-Haldimand Trail - Dunn | 2024 | 433353.5923
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48910 | HAMI-South Coast - Walpole | 2023 | 107613.8169
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48912 | HAMI - HWY 6 - Walpole | 2023 | 197291.9977
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48939 | HAMI: Haldimand Rd 12, Rainham, BU Replacement | 2023 | 95905.8322
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48940 | HAMI- Taylor - Dunnville | 2023 | 92653.7028
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48941 | HAMI- Albion - York | 2023 | 22419.5452
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48953 | HAMI- Upper Wellington - Hamilton | 2024 | 171736.8508
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48954 | HAMI- Rainham Road - Walpole | 2023 | 684543.4465
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48977 | HAMI - Haldimand road 55 - Walpole | 2023 | 269034.5423
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48983 | HAMI - Park - Hamilton | 2024 | 57416.4994
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48984 | HAMI - Mohawk - Hamilton | 2024 | 64593.5618
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 48985 | HAMI - Main at Leland - Hamilton | 2024 | 173341.4369
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 100843 | HAMI: 295 Dundas St E Shallow Main Waterdown | 2028 | 166457.9898
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 100924 | HAMI: Jackson Street Leakage, Hamilton, Leakage | 2023 | 1252370.7408
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 100928 | Park St, Jarvis | 2023 | 58290.8175
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 101631 | HAMI: Lloyminn/Crestview, Ancaster, Replacement | 2023 | 1342370.2683
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733609 | HAMI: Cheapside Rd Ph2, Walpole, BU Replacement | 2023 | 35871.2723
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733621 | HAMI: Main St E, Dunnville, BU Replacement | 2023 | 276507.724
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733622 | HAMI: Rainham Rd Ph1, Dunn, BU Replacement | 2023 | 1271437.3184
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733623 | HAMI: Rainham Rd Ph2, Dunn, BU Replacement | 2023 | 1210655.4403
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733626 | HAMI: Haldimand Rd 20, Walpole, BU Replacement | 2023 | 139001.1802
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733627 | HAMI: Conc 3/Walpole Rd, Walpole, BU Replacement | 2023 | 109855.7714
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733628 | HAMI: Rymer Rd, Sherbrooke, BU Replacement | 2023 | 127791.4076
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733629 | HAMI: Victoria Ave E, Dunnville, BU Replacement | 2023 | 76226.4537
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733631 | HAMI: North Shore/Hutchinson, Moulton, BU Replacement | 2024 | 34603.6938
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733632 | HAMI: Port Maitland/Secord Rd, Dunnville, BU Replacement | 2023 | 107613.8169
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733633 | HAMI: Robinson Rd, Canborough, BU Replacement | 2024 | 39473.8433
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733634 | HAMI: Peacock Point, BU Replacement | 2025 | 78836.1814
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733635 | HAMI: Diltz Rd, Moulton, BU Replacement | 2024 | 14354.1248
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733642 | HAMI: Seneca Dr, Ancaster, BU Replacement | 2023 | 201775.9067
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733643 | HAMI: Powerline Rd W, Ancaster, BU Replacement | 2023 | 11209.7726
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733644 | HAMI: Woodbridge Rd, Hamilton, BU Replacement | 2023 | 13451.7271
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733645 | HAMI: Rifle Range Rd, Hamilton, BU Replacement | 2023 | 248109.6335
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733646 | HAMI: Glen/Dromore, Hamilton, BU Replacement | 2023 | 26903.4542
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733647 | HAMI: Melvin Av, Hamilton, BU Replacement | 2023 | 44839.0904
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733648 | HAMI: Hamilton East, BU Replacement | 2023 | 22419.5452
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733649 | HAMI: Osler Dr @ Rail Trail, Dundas, BU Replacement | 2024 | 129699.7709
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733650 | HAMI: Fleming Ave, Dundas, BU Replacement | 2024 | 108424.9073
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733651 | HAMI: Mohawk Rd W, Hamilton, BU Replacement | 2024 | 26145.0131
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733652 | HAMI: Hamilton Mountain East Ph2, Hamilton, BU Replacement | 2024 | 102529.4632
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733654 | HAMI:Upper Gage Ave, Hamilton, BU Replacement | 2024 | 984282.8466
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733655 | HAMI: Wellington St N /Wilson St, Hamilton, BU Replacement | 2024 | 35885.3121
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733656 | HAMI:Barnaby St /Waterloo St, Hamilton, BU Replacement | 2024 | 64593.5618
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733657 | HAMI: Hamilton Core, BU Replacement | 2024 | 41524.4326
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733658 | HAMI: Stoney Creek, BU Replacement | 2024 | 78435.0393
Southeast | Div_16 - Hamilton | Distribution Pipe | Fail | Dollar threshold | 733659 | HAMI: Burlington St E, Hamilton, BU Replacement | 2024 | 49726.7896
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 30396 | Div. 16 - Haldimand - Caledonia - Argyle St S - Hamilton - 1486 | 2031 | 5384116.8302 | Div. 16 - Haldimand - Caledonia - Argyle St. S. - Hamilton - 1486 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There is significant overlap with the Bare and Unprotected (BU) Program. There is a reduction due to amount of main that will be replaced in 2022. The significant overlap is with the BU main project that was to be complete in 2021 and the proposed BU project on Peebles St. in 2022. | Planned
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 30397 | Div. 16 - Haldimand - Canborough - Smithville Rd - Hamilton - 1488 | 2031 | 3812569.5637 | Div. 16 - Haldimand - Canborough - Smithville Rd. - Hamilton - 1488 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Conservation authority permits are required. | Planned
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 30398 | Div. 16 - Haldimand - Dunnville - Central Lane - Hamilton - 1361 | 2030 | 4399493.6581 | Div. 16 - Haldimand - Dunnville - Central Lane - Hamilton - 1361 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There is significant overlap with the Bare and Unprotected (BU) Program. There is reduction due to amount of main that will be replaced in 2022. The significant overlap between three BU steel mains are to be replaced in 2022. | Planned
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 30399 | Div. 16 - Haldimand - Fisherville - Erie Ave N 1 - Hamilton - 1728 | 2029 | 3307361.7618 | Div. 16 - Haldimand - Fisherville - Erie Ave N 1 - Hamilton - 1728 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: This project is best divided into two projects (Ph1 - Concession 5 Rd. and Ph2 - Erie Ave. N.). The estimate is to be adjusted after additional project is created. Conservation authority permits are required. | Completed | Fail | NPS 2, cannot downsize or retire
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 30404 | Div. 16 - Hamilton - Centennial Pkwy N - Hamilton - 1747 | 2029 | 3353704.6444 | Div. 16 - Hamilton - Centennial Pkwy. N. - Hamilton - 1747 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Include steel main at southeast of Limeridge Mall and the strip malls just south of Violet as it will be isolated steel. | Planned
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 30405 | Div. 16 - Hamilton - Crooks St 1 - Hamilton - 1745 | 2028 | 2959507.0477 | Div. 16 - Hamilton - Crooks St. 1 - Hamilton - 1745 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 30406 | Div. 16 - Hamilton - Crooks St 2 - Hamilton - 1746 | 2031 | 2717544.7068 | Div. 16 - Hamilton - Crooks St. 2 - Hamilton - 1746 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 30413 | Div. 16 - Hamilton - Wentworth St S 2 - Hamilton - 1743 | 2032 | 1773629.1096 | Div. 16 - Hamilton - Wentworth St. S. 2 - Hamilton - 1743 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project will be split into two or three smaller projects with division at Main or King St. The estimate is low. The City is repaving the south portion of Wentworth Ave. S. near Cumberland. | Planned
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 30414 | Div. 17 - Halton - Burlington - Guelph Line - Hamilton - 1429 | 2032 | 7289614.8076 | Div. 17 - Halton - Burlington - Guelph Line - Hamilton - 1429 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 30415 | Div. 17 - Halton - Oakville - 6th Line - Hamilton - 1413 | 2032 | 4985105.0831 | Div. 17 - Halton - Oakville - 6th Line - Hamilton - 1413 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 48428 | HAMI: Dist-Repl-Contr-Mains Municipal* | 2020 | 42151610.5301 | General: Projects in the relocation category are capital expenditures required to replace or relocate segments of pipeline in order to accommodate municipal infrastructure work. The cost sharing for this work is managed through the Franchise Agreements established with municipalities. A consultative approach is used between the municipality and EGI to avoid conflicts with municipal infrastructure early in the planning stage. If a conflict is unavoidable, pipeline assets are typically relocated or replaced. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 48442 | HAMI: Anodes* | 2020 | 15547448.5724 | General: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within EGI's system. These installations and replacements are based on the internal Standard Operating Practice established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 100849 | HAMI: NPS 10 Dominon Line Power Line Rd, Ancaster | 2026 | 2746488.9411 | Issue/Concern/Opportunity: Pipeline Engineering has recommended that customer services no longer be installed directly off the 10" Dominion Line in the Ancaster/Flamborough. To address both the customer connection issue and to eliminate Punch-it tees, a station and IP main installation is proposed. Pipe size TBD. | Planned
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 503350 | Moulton Replacement BU | 2025 | 18528994.181 | Issue/Concern/Opportunity: There is 5.6 km of NPS 8 Intermediate Pressure (IP) bare steel main to be replaced with NPS 8 IP Yellow Jacket (YJ) steel main between #1472 Hwy 3 to #2199 Hwy 3. The in-service date (ISD) is 2025. Justification: Replacement of NPS 8 IP bare steel with size-on-size NPS 8 IP YJ steel main for the 5.6 km segment is required. Assets: NPS 8 IP gas main between #1472 Hwy 3 to #2199 Hwy 3. Related Investments: Not applicable. | Planned
Southeast | Div_16 - Hamilton | Distribution Pipe | Pass |  | 733612 | NPS 12 Retrofit | 2024 | 2594374.8369 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2025 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101084 | HAMI: Cascade & Lanark Station Rebuild, Vault | 2025 | 1286534.247
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101090 | HAMI: Glancaster Hwy 6 & 20 Rd Station Rebuild, Frost Heave | 2023 | 523122.7211
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101094 | HAMI-Summit Trans Stn, | 2030 | 565899.7416
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101098 | HAMI - Six Nations | 2023 | 24910.6058
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101101 | HAMI - Diltz Rd IP North | 2026 | 521289.0949
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101103 | HAMI: Kenora & Bancroft Station Rebuild, Vault | 2023 | 622765.1442
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101126 | HAMI - Industrial St Vault Station | 2025 | 645725.1021
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101130 | HAMI - King St E Stn - Dundas | 2025 | 645725.1021
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101131 | HAMI - South Bend & Upper James Stn - Hamilton | 2025 | 645725.1021
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101132 | HAMI - Bancroft and Nash Vault Station | 2025 | 645725.1021
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101133 | HAMI - Ferrie and Wellington Vault Station | 2025 | 645725.1021
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101135 | HAMI - Clappison's Corners | 2025 | 645725.1021
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 101140 | HAMI - US Steel Blast Furnace Atm Tank Replacement - Walpole | 2031 | 1399278.5572
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 103529 | HAMI: 12Z-301 Port Maitland Rymer Station, Haldimand, Heater Installation | 2024 | 640809.1449
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735023 | HAMI: Hamilton Gate 2, Noise Issues | 2027 | 1345482.8469
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735037 | HAMI: Woodward bio gas, reinforcement | 2027 | 555097.1826
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735041 | HAMI: SE Corner of HWY 5 & 6, Maintenance | 2025 | 387435.0612
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735044 | HAMI: WATERDOWN NORTH DISTR'N STN, Boiler | 2026 | 1303222.7373
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735047 | HAMI: VOORTMAN STN, heater Replacement | 2026 | 651611.3686
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735050 | HAMI: Empire Steel, Maintenance | 2030 | 141474.9354
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735051 | HAMI: Voith Fabrics, Maintenance | 2030 | 141474.9354
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735056 | HAMI: Mye Canada, Maintenance | 2030 | 70737.4677
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735057 | HAMI: Temple Canada, Maintenance | 2030 | 70737.4677
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735058 | HAMI: Birmingham and Burlington, Maintenance | 2028 | 550469.9681
Southeast | Div_16 - Hamilton | Distribution Stations | Fail | Dollar threshold | 735065 | HAMI: Saint Gobain Abrasives, maintenance | 2030 | 282949.8708
Southeast | Div_16 - Hamilton | Distribution Stations | Pass |  | 101086 | HAMI-Hamilton Gate 3 | 2024 | 8550130.8192 | Issue/Concern/Opportunity: The Hamilton Gate 3 Station needs a whole rebuild driven by integrity concerns. The station does not operate at full capacity. An early review of the heating system indicates that a redesign is required to improve the operation at the site. Furthermore, the property drains into the Boiler room depending on the amount of snowfall. The rebuild will address this water runoff concern. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southeast | Div_16 - Hamilton | Distribution Stations | Pass |  | 101345 | HAMI - Hillcrest Station | 2027 | 2081614.4346 | Issue/Concern/Opportunity: There are noise issues and old heater needs to be replaced on single feed station. Station is in high density area along the escarpment. It is a critical site and regulation should be buried. Scope is full rebuild. Assets: Station ID: 16X-218R Related Program: N/A | Completed | Fail | Distribution station condition related, IRPA not applicable
Southeast | Div_16 - Hamilton | Distribution Stations | Pass |  | 503271 | Hamilton/Halton PFM Compliance Program* |  | 843392.3757 | Issue/Concern/Opportunity: -PFMs that require a bypass will be rebuilt w/bypass to the new standard: oWhen they are due for a meter exchange and in the meter seal expiry year, provided that year is between 2022 and 2026. This will fall under the meter exchange budget and costs are not covered in this program. oIf the meter seal year is not between 2022 and 2026, the set will be rebuilt with a bypass the year after it is inspected. This will allow the technicians to identify which will require rebuilt at the time of inspection, and Sohan and I will be developing a process to get work orders generated for these rebuilds after the inspection. Also ensures that we focus our efforts on rebuilding active PFMs requiring rebuild. While I originally mentioned a proactive strategy to rebuild prior to the inspection year, we decided against that. -Assumption is that 50% of PFMs will need to be rebuilt. -Calculations are based on an estimate of $5500 per rebuild. As you know there is a significant swing depending on the pipe size, volume, existing set up (first stage cut, etc) that may influence this including the release of the new SEADs designs, that I have not seen yet. | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_16 - Hamilton | Distribution Stations | Pass |  | 735038 | HAMI: Hamilton Takeoff & Carlisle Gate, Rebuild | 2026 | 7819336.4238 | Issue/Concern/Opportunity: The current station is experiencing frost heave due to a large pressure cut and the soil conditions that is leading to pipe movement. The odourant lines are kinked as a result of the station heaving. The existing heating system will be evaluated and possibly replaced with a CWT heater. The current pressure control devices are Control valves that have been experiencing reliability concerns and have required maintenance. The scope of this project is to rebuild with below-grade control valves. Assets: Related Investments: N/A | Completed | Fail | Distribution station condition related, IRPA not applicable
Southeast | Div_16 - Hamilton | Distribution Stations | Pass |  | 735043 | HAMI: Jarvis trans, full rebuild | 2026 | 6516113.6865 | Station rebuild not required if Growth investment #30538 proceeds | Completed | Fail | N/A - Investment Cancelled
Southeast | Div_16 - Hamilton | Distribution Stations | Pass |  | 735045 | HAMI: KIRKWALL/DOMINION, Full Rebuild | 2029 | 8197927.2339 | Issue/Concern/Opportunity: Noise issues This site has received numerous noise complaints and odour from residents in the area. Constant bleeds on the control valves are causing the odour complaints. Consider Becker below grade ball valve station with no bleed pilots and DNGP for any needed flow control/pressure control. Fisher control valves are not a good option as they come with high O&M annual spend to operate and maintain. VALVE & PIPING: Most valves becoming difficult to turn even with greasing. Many position indicators on tops of valves have fallen off due to ongoing corrosion. FILTRATION: Filter decent shape – gas is dry and clean HEATING: System is in constant state of repair and boiler age is old. A lot of corrsosion on the glycol piping. There is not proper containement for the heat exchanger. Current system used all un-odourized gas inside. PRESSURE CONTROL: Control valves needs support from Lakeside Controls to perfrom annual Operations ODOURIZATION: Mois system (older vintage) room is very tight to get all assets inside the cabinet and room. Odourant cabinet in poor condition. No fire suppression system installed on odourant. TELEMETRY & ELECTRICAL: Back up generator in decent shape. Electrical panels in poor shape and not properly labelled. All building do not have any methane detection or CO detection in boiler rooms. MEASUREMENT . COMPLIANCE & OTHER Eng: Turbine meter is in decent shape and is used for process control only. Buildings are old and in declining condition. One is brick façade and the others are metal buildings. Fencing in decent shape. Gates droop in the winter and would be better to go to the sliding gate standard. Consider adding swipe card access to compound and buildings to meet corporate security standards to compound and buildings. There is not a containment area for any chemicals being stored on site. Ancaster Gate South is inside compound and is also in similar condition to Kirkwall-Dominion. There is supposed to be a pig launcher added to this site. Assets: 16W-606 Related Investments: N/A | Completed | Fail | Distribution station condition related, IRPA not applicable
Southeast | Div_16 - Hamilton | Distribution Stations | Pass |  | 735048 | HAMI :CALEDONIA TRANSMISSION STN, Rebuild | 2027 | 8326457.7384 | Issue/Concern/Opportunity: VALVE & PIPING: Most valves becoming difficult to turn even with greasing. Many position indicators on tops of valves have fallen off due to ongoing corrosion. Lots of corrosion on piping and leaks on an orifice meter that cannot be repaired. Frost heave on the Mount Hope line. Paint of piping in entire site is in poor condition and lots of external rust. FILTRATION: Filter is getting replaced next month. If pigging at this site, a separator is needed. HEATING: System is old and poor shape. The heaters are oversized and there is some cracking on some of the older boilers. Because heaters do not run the correct length of time, some of the gas lines remain frosted on the second and third cut. Heat exchangers are not contained and boiler rooms only have angle iron containment on the floors. PRESSURE CONTROL: second station cut cannot keep up with demand to the Dunnville market. A pressure cuts are single regs and full capacity reliefs. Consider Becker buried ball valve station with no bleed pilots. ODOURIZATION: no odurant on site TELEMETRY & ELECTRICAL: Transmitters are old anolgue devices and situated to make ongoing testing and maintaining difficult. Electrical panels are old and not properly labbeled. There are no methane or CO detectors in boiler room. Should consider swipe card access to compound and buildings. Site does not have a back up generator. MEASUREMENT . COMPLIANCE & OTHER Eng: Orifice measurement has leaks and should be upgraded to a properly sized turbine meter. Measurement runs do not have any bypass piping. Site has an old storage building of metal construction. Need new storage building as this is a location where the Dunnville yard keeps materials and supplies in a remote location. There is not a contained area for any chemicals being stored on site. Need space from existing fencing to ajacent neighbors to keep vegetation controlled. Lots of vegetation coming up through fencing and gates are drooping, consider a new slide gate standard. Site access is off of highway 6 where traffic is at a high rate of speed (80 kph +) Consider possibility of accessing yard from rear laneway. Front fence line should be lined with Jersey barriers for compound protection. Snow plowing is a challenge at this location due to closeness to road and high rate of traffic speed. Existing compound does not have any crash bar man gates for egress. The heating system will be replaced during this project. Assets: 15X-401 Related Investments: N/A | Completed | Fail | Distribution station condition related, IRPA not applicable
Southeast | Div_16 - Hamilton | Growth | Pass |  | 30526 | SRP_Southeast_Ancaster_16W-601STN_Rebuild | 2024 | 181989.7459 | Build to higher capacity. | Planned
Southeast | Div_16 - Hamilton | Growth | Pass |  | 30538 | SRP_Southeast_Jarvis_12W-102STN_Rebuild | 2026 | 4430957.3068 | Rebuild for increased capacity and lower pressure differential across station is required. | Planned
Southeast | Div_16 - Hamilton | Growth | Pass |  | 30539 | SRP_Southeast_Jarvis_12W-201STN_Rebuild | 2023 | 1806018.8684 | Build to higher outlet pressure and higher capacity. | Planned
Southeast | Div_16 - Hamilton | Growth | Pass |  | 48427 | HAMI: Company Program - New Business - Scattered Mains - Contractor* | 2020 | 37827801.1711 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | Div_16 - Hamilton | Growth | Pass |  | 500421 | HAMI: Company Program - Customer Connections* |  | 43466496.2515 | Hamilton Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southeast | Div_16 - Hamilton | Growth | Pass |  | 736259 | Hamilton Industrial Reinforcement | 2025 | 132907738.5449 | Issue/Concern/Opportunity :Reinforcement required to support changes to industrial demand in the area. Assets: Distribution Reinforcement Related Program: N/A | In Progress
Southeast | Div_16 - Hamilton | Utilization | Pass |  | 48439 | HAMI: Meter & Regulator Inst Repl-Contractor | 2020 | 42953109.1509 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Southeast | Div_16 - Hamilton | Transmission Pipe & Underground Storage | Pass |  | 48654 | Dawn Parkway Expansion Project (Kirkwall-Hamilton NPS 48) | 2026 | 245855288.5858 | Issue/Concern: In response to increased natural gas demand growth along the Dawn Parkway System, the Kirkwall to Hamilton Expansion has a forecast in-service date of November 1, 2026 and will provide reliable, secure, economic natural gas capacity to meet the growing design day demand of the Dawn Parkway Transmission system which serves both in- and ex-franchise markets. Assets: The Kirkwall-Hamilton Expansion Project consists of 10.2 km of NPS 48 pipeline from the Kirkwall Valve Site to the Hamilton Valve Site. Related Programs: N/A | In Progress |  | Market side supply options to be assessed prior to LTC application
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 30003 | Base Line 2 - Southwest - Windsor - 1347 | 2031 | 1702262.3282
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 30007 | Callie Ave - Southwest - Windsor - 1377 | 2027 | 1441870.3717
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 30008 | County Road 46 - Southwest - Windsor - 1352 | 2029 | 1680920.7076
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 30014 | Elinor St - Southwest - Windsor - 1279 | 2031 | 1229092.1982
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 30022 | Lanoue St - Southwest - Windsor - 1354 | 2027 | 1729506.522
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 30029 | Morand St 2 - Southwest - Windsor - 1657 | 2029 | 1407792.4974
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 30034 | River View Line - Southwest - Windsor - 1381 | 2029 | 360916.5338
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 48289 | WIND: Dist-Repl-Contr-Mains Leakage* | 2020 | 7382794.1733
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 48290 | WIND: Dist-Repl-Contr-Services* | 2020 | 15407551.5561
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 48762 | WIND: Riverside Dr (Arlington to Kensington), Windsor, Replacement | 2027 | 380935.4415
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 48779 | WIND: Maidstone Ave & Talbot St, Essex, Replacement | 2027 | 270609.8765
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 48781 | WIND: Laird IP, Essex, Replacement | 2027 | 902032.9217
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 48782 | WIND: Lacasse (St Denis to Tecumseh Rd E), Windsor, Replacement | 2023 | 204889.7324
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 48796 | WIND: County Rd 27 Ph 1, Lakeshore, Replacement | 2028 | 1513792.4123
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 48851 | WIND: County Rd 31 & Essex County Rd 2, Lakeshore, Replacement | 2027 | 936726.4956
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 48865 | WIND: County Rd 2 & Riverside Rd, Lakeshore, Replacement | 2027 | 242855.0174
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49007 | WIND: Somme Valve, Windsor, Replacement | 2025 | 128499.2953
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49714 | Bush Line Leakage Replacement Phase 1 & 2 | 2031 | 1816263.6232
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49719 | WIND: 2200 - 2204 County Rd 27, Lakeshore, Replacement | 2028 | 48166.1222
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49722 | WIND: Bertha Ave, Windsor, Replacement | 2027 | 575913.3269
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49729 | WIND: Devonshire Rd, Windsor, Replacement | 2027 | 346241.8676
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49732 | Fairview Line Replacement | 2031 | 1277541.2667
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49734 | WIND: Glenwood Line & Port Rd, Chatham-Kent, Replacement | 2031 | 483450.7415
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49746 | WIND: Woodslee Ph 2, Lakeshore, Replacement | 2027 | 464893.8904
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49750 | WIND: Trenton St, Windsor, Replacement | 2031 | 489047.8557
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49752 | WIND: Tecumseh Rd E - Ph3, Windsor, Replacement | 2027 | 825707.0591
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 49889 | WIND: Caille Ave, Lakeshore, Replacement | 2027 | 548158.4678
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 101175 | WIND: Tecumseh Rd E - Ph4, Windsor, Replacement | 2023 | 466451.093
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 101177 | WIND: Tecumseh Rd E - Ph6, Windsor, Replacement | 2023 | 466451.093
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 101797 | WIND: Corrosion Rectifier Groundbed Program* | 2021 | 77750.9827
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 102255 | WIND: Bayshore Dr, Leamington, Replacement | 2023 | 180601.8918
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 102257 | WIND: County Rd 27 Ph 2, Lakeshore, Replacement | 2028 | 1617005.5313
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 102262 | WIND: Woodslee Ph 1, Lakeshore, Replacement | 2027 | 867339.3478
Southwest | Div_01 - Windsor | Distribution Pipe | Fail | Dollar threshold | 501004 | WIND: PSLL Maintenance | 2023 | 503194.2365
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30001 | Aberdeen St - Southwest - Windsor - 1356 | 2032 | 2314586.0198 | Aberdeen St. - Southwest - Windsor - 1356 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30002 | Base Line - Southwest - Windsor - 1623 | 2032 | 2648940.1474 | Base Line - Southwest - Windsor - 1623 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30004 | Belle River Rd - Southwest - Windsor - 1366 | 2032 | 1809149.9244 | Belle River Rd. - Southwest - Windsor - 1366 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | N/A - Investment Cancelled
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30006 | Cabana Rd W - Southwest - Windsor - 1353 | 2032 | 3007648.8165 | Cabana Rd. W. - Southwest - Windsor - 1353 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | N/A - Investment Cancelled
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30010 | Delaware Ave - Southwest - Windsor - 1364 | 2028 | 2461467.0871 | Delaware Ave. - Southwest - Windsor - 1364 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30012 | Ducharme St - Southwest - Windsor - 1301 | 2029 | 3706129.6012 | Ducharme St - Southwest - Windsor - 1301 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30013 | Edgar St - Southwest - Windsor - 1277 | 2031 | 3447577.659 | Edgar St. - Southwest - Windsor - 1277 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30015 | Elm Ave - Southwest - Windsor - 1295 | 2030 | 4253853.1348 | Elm Ave. - Southwest - Windsor - 1295 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30016 | Giles Blvd E - Southwest - Windsor - 1282 | 2030 | 2204265.8498 | Giles Blvd. E. - Southwest - Windsor - 1282 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30018 | Hanley Cres - Southwest - Windsor - 1350 | 2030 | 2822041.2811 | Hanley Cres. - Southwest - Windsor - 1350 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30021 | Laird Ave - Southwest - Windsor - 1371 | 2032 | 3361270.8849 | Laird Ave. - Southwest - Windsor - 1371 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | N/A - Investment Cancelled
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30026 | Malden Rd 2 - Southwest - Windsor - 1660 | 2032 | 2819823.9571 | Malden Rd. 2 - Southwest - Windsor - 1660 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: This project will be split into a smaller project based on feedback from the region (Malden Rd. 1, 2, 3). | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30031 | Pillette Rd - Southwest - Windsor - 1320 | 2032 | 4419420.4012 | Pillette Rd. - Southwest - Windsor - 1320 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30032 | Randolph Ave - Southwest - Windsor - 1334 | 2031 | 3027762.5241 | Randolph Ave. - Southwest - Windsor - 1334 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30033 | Rholaine Dr - Southwest - Windsor - 1299 | 2028 | 2183223.5094 | Rholaine Dr. - Southwest - Windsor - 1299 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30035 | Riverside Dr E - Southwest - Windsor - 1357 | 2032 | 2567901.638 | Riverside Dr. E. - Southwest - Windsor - 1357 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30036 | Rourke Line Rd - Southwest - Windsor - 1373 | 2031 | 3170019.451 | Rourke Line Rd. - Southwest - Windsor - 1373 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30037 | Spring Garden Rd - Southwest - Windsor - 1658 | 2028 | 2195451.5392 | Spring Garden Rd. - Southwest - Windsor - 1658 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Project is split into smaller projects based on feedback from region (Spring Garden Rd. and included in Malden Rd.). | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30038 | St Anne Blvd - Southwest - Windsor - 1319 | 2030 | 2221990.8483 | St. Anne Blvd. - Southwest - Windsor - 1319 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | N/A - Investment Cancelled
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30039 | Talbot Rd - Southwest - Windsor - 1369 | 2031 | 3120987.555 | Talbot Rd. - Southwest - Windsor - 1369 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30042 | Tecumseh Rd W 2 - Southwest - Windsor - 1492 | 2031 | 3772556.4658 | Tecumseh Rd. W. 2 - Southwest - Windsor - 1492 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 30044 | Walker Rd - Southwest - Windsor - 1333 | 2029 | 3711443.1697 | Walker Rd. - Southwest - Windsor - 1333 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 48288 | WIND: Dist-Repl-Contr-Mains Municipal* | 2020 | 71550345.2628 | General: Projects in the relocation category are capital expenditures required to replace or relocate segments of pipeline in order to accommodate municipal infrastructure work. The cost sharing for this work is managed through the Franchise Agreements established with municipalities. A consultative approach is used between the municipality and EGI to avoid conflicts with municipal infrastructure early in the planning stage. If a conflict is unavoidable, pipeline assets are typically relocated or replaced. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 48302 | WIND: Anodes* | 2020 | 8143099.5815 | General: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within EGI's system. These installations and replacements are based on the internal Standard Operating Practice established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 48994 | WIND: Laird & Centre MIP, Essex, Replacement | 2028 | 2057381.5058 | Replace 2,400 m of 2-inch/4-inch S DL protected main (35 kPa) with 250 m of 4-inch plastic main (420 kPa) and 3,850 m of 2-inch plastic main (420 kPa) on Laird Ave. and Centre St. in the Town of Essex. Abandon existing station and replace with new Lakeside pre-fab station. There are 150 services that will either need to be replaced or tied over. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 49743 | WIND: Riverside Aldyl A - Ph 1, Windsor, Replacement | 2027 | 2151001.5824 | This project will replace the approximately 1.1km of 1978 vintage Aldyl-A PE main along Riverside Drive in Windsor, from Bertha Street to Clover Drive. This main is known to be very brittle, has a total of 4 known C leaks, and many lined services. A portion of this 4" PE main is lined in the former 6" S CT main installed in 1968 that continues on either side of Riverside Drive, making maintenance and new service connections extremely difficult. There are approximately 18 services renewals required. Main to be replaced with 1100 m of 4" PE IP. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 49747 | WIND: Tecumseh Rd W, Windsor, Replacement | 2028 | 2683541.0945 | This job will replace 1,025 m of NPS 8 steel (S) Prior to Records (PTR) main on Tecumseh Rd. W. from Everts Ave. to Betts Ave. with 1,025 m of 8-inch S Yellow Jacket (YJ). This main is either too poor condition or laminated, and as a result cannot be welded on. In addition to weldability issues, several leaks have occurred over the last several years, which have all resulted in high capital expenditures to repair them. This main also requires many anodes try and maintain cathodic protection levels, all of which must be installed in wall-to-wall concrete. The most recent anodes were installed in the last two to three years meaning by 2025, new ones will need to be installed to replace them. This project will also include the renewal of 16 services. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 49812 | WIND: Oak St - Ph 2, Leamington, Replacement | 2031 | 2091921.4429 | Phase 2 will continue from the end point of the 2017 project, and replace the remaining 600 m of NPS 8 Prior to Records (PTR) pipe from Danforth to Oak Street station with 10-inch steel (S) Yellow Jacket (YJ). There will be 12 service renewals. There is one leak on this section of main. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 49814 | WIND: Tecumseh Rd E - Ph 2, Windsor, Replacement | 2028 | 2993180.4516 | Phase 2 will replace 1,000 m of Prior to Records (PTR) / DL protected NPS 8 Steel (S) main from 10490 to 11168 Tecumseh Rd. E. with 1,000 m of 8-inch S Yellow Jacket (YJ). There are a total of 14 services and 3 main tie-overs. This main is either in too poor condition or laminated, and as a result cannot be welded on. In addition to weldability issues, several leaks have occurred over the last several years which have all resulted in high capital expenditures to repair them. This area requires a substantial amount of anodes to keep it cathodically protected. This area also contains a large amount of growth and development for which the district currently cannot service due to the lacking pipe weldability. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 49816 | WIND: Mersea Rd 2 - Ph 2, Leamington, Replacement | 2023 | 1690807.3665 | This project is Phase 2 of a two-phase project to replace approximately 2,200 m of Coal Tar Wrap (C&W) (620 kPa) steel main along Mersea Rd. 2 (Oak St. Station to Deer Run Rd.). The second phase of this project will involve the replacement of 1,243 m of NPS 6 and 8 C&W (620 kPa) steel main with 1,200 m of 8-inch Steel (S) Yellow Jacket (YJ) gas main and 100 m of 2-inch S YJ. This project will also involve the renewal of 30 steel services. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 100688 | WIND: Riverside Aldyl A - Ph 2, Windsor, Replacement | 2028 | 3027584.8246 | This project will replace the approximately 1.7km of 1978 vintage Aldyl-A PE main along Riverside Drive in Windsor, from Bertha Street to Clover Drive. This main is known to be very brittle, has a total of 4 known C leaks, and many lined services. A portion of this 4" PE main is lined in the former 6" S CT main installed in 1968 that continues on either side of Riverside Drive, making maintenance and new service connections extremely difficult. There are approximately 73 services renewals required. Main to be replaced with 700 m of 4" PE IP. | Planned
Southwest | Div_01 - Windsor | Distribution Pipe | Pass |  | 733732 | NPS 12, 10 Baldoon | 2024 | 4672493.5578 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2025 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 48291 | WIND: Plan(T)-Dist-Stn Measuring/Corrosion Stn* | 2020 | 4591035.287
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 101342 | WIND - 03B-102R County Rd 20 & Concession Rd 3 - Heater addition | 2023 | 215816.7697
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 101347 | WIND - 05B-401R Smith Ind Park - Station Rebuild with Heater | 2024 | 214677.4716
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 101357 | WIND - 06B-548I Chrysler Paint - Heater Replacement | 2024 | 206068.8416
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 101360 | WIND - 04B-401R Howard and Pike - Rebuild with Heater | 2026 | 305411.5517
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 101608 | WIND - 06D-401 Belle River Gate - Replace heater | 2031 | 624761.0844
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 101611 | WIND - 05A-304R Sprucewood IP - Replace heater | 2030 | 716553.5708
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 502698 | WIND - 03D-322C Leamington Hospital - rebuild | 2023 | 271970.2572
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 502700 | WIND - 06B-401 Grand Marais - reg repl & liquid tank | 2025 | 291404.6321
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 502701 | WIND - 04D-601R Albuna Station rebuild | 2030 | 1173123.8308
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 502772 | WIND - 06B-314R Isabelle Place LP - rebuild | 2023 | 197166.1991
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 502773 | WIND - 06B-517R Ypres LP - rebuild | 2024 | 204809.0108
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 502774 | WIND - 03E-104C Thiessen Flower Shop - rebuild | 2028 | 265879.7469
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 502777 | WIND - 04A-302R Texas Rd | 2023 | 321022.9765
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 502950 | WIND: 06B-607I Ford/Nemak Station Rebuild | 2028 | 1273402.1772
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 503331 | WIND - 06C-401 Manning Rd station rebuild | 2025 | 696312.498
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 503333 | WIND - 06C-502 Patillo Rd station rebuild | 2024 | 739648.8291
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 734654 | WIND: 04E-438C Protolight Farms | 2026 | 311740.0013
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 734663 | WIND: 05B-205R Howard & Outer | 2029 | 300134.6965
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 734665 | WIND: 06C-602 Puce Transmission | 2027 | 225447.1697
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 734666 | WIND: 06A-605R Matchette & Prince | 2029 | 1450501.5941
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 734667 | WIND: 06B-404 Bruce Ave | 2028 | 1533144.184
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 734673 | WIND: 06B-502 WALKER RD | 2032 | 694756.4835
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 735375 | WIND: 07H-402R Peter St Station LP | 2024 | 205225.5368
Southwest | Div_01 - Windsor | Distribution Stations | Fail | Dollar threshold | 735378 | WIND: 06B-105R 540 Ouellette Dist |  | 99642.4231
Southwest | Div_01 - Windsor | Distribution Stations | Pass |  | 101626 | WIND - 05A-203 LaSalle Boismier Ave - Heater replacement | 2025 | 3099480.4899 | Issue/Concern/Opportunity: Heater controls are located within the hazardous area and are not rated to be within this zone. There is obsolete heating equipment; BS&B style heater that is on the risk register is to be replaced. Justification: Station needs to be rebuilt with new CWT 770. Potential requirement for additional land. Assets: 05A-203 LaSalle Boismier Ave. Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_01 - Windsor | Distribution Stations | Pass |  | 502697 | WIND - 05B-201 Windsor McGregor Line - rebuild | 2026 | 1749027.8681 | Issue/Concern/Opportunity: Known corrosion issues are on risers. Justification: Rebuild station to eliminate potential for leak. Assets: 05B-201 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_01 - Windsor | Distribution Stations | Pass |  | 502699 | WIND - 05A-601 Front & Malden full rebuild | 2025 | 1697712.0264 | Issue/Concern/Opportunity: Station freezes in winter so heater is required. Corrosion is significant on outlet riser. Land will be required to rebuild this station. Justification: Eliminate station freeze risk and remediate corrosion on riser. Assets: 05A-601 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_01 - Windsor | Distribution Stations | Pass |  | 503276 | Windsor/Chatham PFM Compliance Program* |  | 676389.1022 | Issue/Concern/Opportunity: -PFMs that require a bypass will be rebuilt w/bypass to the new standard: oWhen they are due for a meter exchange and in the meter seal expiry year, provided that year is between 2022 and 2026. This will fall under the meter exchange budget and costs are not covered in this program. oIf the meter seal year is not between 2022 and 2026, the set will be rebuilt with a bypass the year after it is inspected. This will allow the technicians to identify which will require rebuilt at the time of inspection, and Sohan and I will be developing a process to get work orders generated for these rebuilds after the inspection. Also ensures that we focus our efforts on rebuilding active PFMs requiring rebuild. While I originally mentioned a proactive strategy to rebuild prior to the inspection year, we decided against that. -Assumption is that 50% of PFMs will need to be rebuilt. -Calculations are based on an estimate of $5500 per rebuild. As you know there is a significant swing depending on the pipe size, volume, existing set up (first stage cut, etc) that may influence this including the release of the new SEADs designs, that I have not seen yet. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_01 - Windsor | Distribution Stations | Pass |  | 503332 | WIND - 06B-403 California Ave station rebuild | 2024 | 4101178.5275 | Issue/Concern/Opportunity: There are asbestos concerns. The converted NATCO heating system is out of date. There are hazardous area concerns. The maintenance of station is an ergonomics concern. The residential neighbourhood location not ideal. There is no containment for glycol. Justification: Station rebuild. Assets: 06B-403 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_01 - Windsor | Growth | Pass |  | 30549 | SRP_Southwest_Amherstburg_County Rd 20_Reinforcement_NPS4_1500m_420kPa | 2032 | 407397.3821 | Main extension connecting two 420 kPa pipes together in rural Amherstburg is required. | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 30550 | SRP_Southwest_Blenheim_Industrial Ave_Reinforcement_NPS6_600m_420kPa | 2032 | 711587.4816 | Main reinforcement to tie larger mains together at the low point in Blenheim is required. Replace the existing 2-inch on the north side of Industrial Ave. | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 30552 | SRP_Southwest_Essex_05B-401RSTN_Rebuild | 2023 | 1126974.4879 | Increase station maximum sustainable from 275 kPa to 380 kPa. | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 30561 | SRP_Southwest_Amherstburg_New STN & Reinforcement_NPS4_2200m_3450kPa | 2032 | 4619499.285 | Main extension to the west of the 3,450 kPa pipe and a new distribution station to feed into the 420 kPa network in rural Amherstburg is required. | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 30574 | SRP_Southwest_Tecumseh_Manning_Reinforcement_NPS6_250m_420kPa | 2023 | 311382.5721 | Main extension to the south of Manning Rd. Station is required. | Completed | Fail | N/A - Project in construction phase
Southwest | Div_01 - Windsor | Growth | Pass |  | 30576 | SRP_Southwest_Windsor_05B-205RSTN_Rebuild | 2026 | 23692.5894 | Station is flowing over capacity. | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 30577 | SRP_Southwest_Windsor_County Rd 42_Reinforcement_NPS6_3800m_420kPa | 2032 | 678995.6911 | Main extension to connect two existing 420 kPa pipes together south of the airport is required. | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 30578 | SRP_Southwest_Windsor_Howard_Reinforcement_NPS6_1800m_420kPa | 2026 | 847094.8314 | Main extension and reinforcement to the south of Howard and Outer Station is required. | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 48287 | WIND: Company Program - New Business - Scattered Mains - Contractor* | 2020 | 11245853.2807 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southwest | Div_01 - Windsor | Growth | Pass |  | 48306 | WIND: Generic Greenhouse Windsor* | 2020 | 81077242.7124 | Customer Growth | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southwest | Div_01 - Windsor | Growth | Pass |  | 101359 | SRP_Southwest_Windsor_05A-201STN_Rebuild | 2023 | 2138291.5243 | Issue/Concern/Opportunity: There is no station heat. The IP cut is at risk for freeze-off due to large pressure drop (3450kPa to 420kPa). Frost heave, fish-mouth supports, and ankle-level pipe are all concerns. Justification: Eliminate risk of regulator freeze-off and frost heave by adding a CWT 385, rebuild regulator runs (ankle-level and fish-mouth supports). Mercury remediation is needed. Assets: 05A-201 Turkey Creek Related Investments: 502777 - Texas Rd. - Valve MUST be fixed at Texas Rd. before work can begin. | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 500415 | WIND: Company Program - Customer Connections* |  | 50761394.1852 | Windsor Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southwest | Div_01 - Windsor | Growth | Pass |  | 736070 | WIND: LEAM-3 Panhandle Distribution Reinforcement - Essex Road 37 Reinforcement | 2026 | 1432720.9337 | Issue/Concern/Opportunity: Greenhouse growth in the Windsor area continues. The Panhandle distribution network needs to be reinforced to allow for the continued industrial customer expansion. A Panhandle transmission reinforcement is also required to meet the demand of the region. LEAM-3 is a distribution system looping project with a station upgrade. Assets: 1,200 m of NPS 6 PE 420 kPa. Station Modification/Rebuild of 04E-501R - Mersea Rd 6/ Cty Rd 37. Related Program: Panhandle Regional Expansion Project 49758 | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 736071 | WIND: LEAM-4 Panhandle Distribution Reinforcement - Mersea Road 12 Reinforcement | 2031 | 1960382.3517 | Issue/Concern/Opportunity: Greenhouse growth in the Windsor area continues. The Panhandle distribution network needs to be reinforced to allow for the continued industrial customer expansion. A Panhandle transmission reinforcement is also required to meet the demand of the region. LEAM-4 is a distribution system looping project: Assets: 1,600 m of NPS 6 ST 3450 kPa Related Program: Panhandle Regional Expansion Project 49758 | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 736073 | WIND: LEAM-7 Panhandle Distribution Reinforcement - Mersea Road 8 Reinforcement | 2023 | 1270440.8942 | Issue/Concern/Opportunity: Greenhouse growth in the Windsor area continues. The Panhandle distribution network needs to be reinforced to allow for the continued industrial customer expansion. A Panhandle transmission reinforcement is also required to meet the demand of the region. LEAM-7 is a distribution system looping project: Assets: 1,300 m of NPS 6 ST, 3450 kPa Related Program: Panhandle Regional Expansion Project 49758 | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 736074 | WIND: Staples-1A Panhandle Distribution Reinforcement - Ontario Hwy 77 and Mersea Rd 7 Reinforcement | 2023 | 6090643.1104 | Issue/Concern/Opportunity: Greenhouse growth in the Windsor area continues. The Panhandle distribution network needs to be reinforced to allow for the continued industrial customer expansion. A Panhandle transmission reinforcement is also required to meet the demand of the region. Staples-1A is a distribution system looping project which requires stations upgrades at Mersea Twp. Conc. 6 Assets: 2,000 m of NPS 6 ST 3450 kPa. Mersea Twp Conc 6 Station (04E-401) modifications/rebuild Related Program: Panhandle Regional Expansion Project 49758 | Planned
Southwest | Div_01 - Windsor | Growth | Pass |  | 736075 | WIND: Wheatley-1B - Panhandle Distribution Reinforcement - Wheatley Lateral Replacement and Reinforcement | 2024 | 21106551.4098 | Risk/Concern/Opportunity: Greenhouse growth in the Windsor area continues. The Panhandle distribution network needs to be reinforced to allow for the continued industrial customer expansion. A Panhandle transmission reinforcement is also required to meet the demand of the region. Assets: Distribution Reinforcement Related Programs: N/A | Completed | Fail | N/A - Investment cancelled
Southwest | Div_01 - Windsor | Utilization | Pass |  | 48298 | WIND: Meter & Regulator Inst Repl-Contractor* | 2020 | 55151860.6919 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_01 - Windsor | Transmission Pipe & Underground Storage | Pass |  | 100086 | Panhandle Line Replacement | 2024 | 37488222.8843 | Issue/Concern: EGI’s Integrity Management team initiated work in 2019 to better understand the risk associated with the two NPS 12 crossings that connect the Panhandle Eastern System owned and operated by Energy Transfer in Michigan with the EGI system in Ontario. These two crossings, installed in 1947, have never been internally inspected to check for the presence of the primary threat of internal corrosion; such inspection cannot be achieved given the configuration of the asset. A risk assessment was recently completed for the river crossings. The risk owner and risk approver reviewed the risk results and have decided the risk requires treatment with a permanent solution. Assets: Transmission Pipeline (Canada Energy Regulator-regulated crossing) Related Programs: Not applicable. | Planned
Southwest | Div_01 - Windsor | Transmission Pipe & Underground Storage | Pass |  | 736923 | Panhandle Regional Expansion Project - Leamington Interconnect | 2024 | 69934844.1262 | Issue/Concern/Opportunity: To provide reliable, secure, and affordable natural gas supply to meet the growth in Design Day demand of the Panhandle System, Assets: i) Leamington Interconnect : 12 km of 6040 kPag MOP NPS16 pipeline connecting the Leamington North Line, Leamington North Loop, Mersea Line and Kingsville East Line. ii. Leamington Interconnect Valve Sites: Three new valve sites with isolation valves are required to connect to each of the existing laterals (1. Leamington North Line and Leamington North Loop, 2. Mersea Line and 3. Kingsville East Line). Launcher/receiver facilities will be installed at location 1 and 3. Related Program: Not Applicable | In Progress |  | Market side supply options to be assessed prior to LTC application
Southwest | Div_02 - Chatham | Distribution Pipe | Fail | Dollar threshold | 48323 | CHAT: Dist-Repl-Contr-Services* |  | 244087.8162
Southwest | Div_02 - Chatham | Distribution Pipe | Fail | Dollar threshold | 49721 | CHAT: Base Line, Wallaceburg, Replacement | 2025 | 1097732.6735
Southwest | Div_02 - Chatham | Distribution Pipe | Fail | Dollar threshold | 49856 | CHAT: St Clair St, Tilbury, Replacement | 2027 | 312103.3909
Southwest | Div_02 - Chatham | Distribution Pipe | Fail | Dollar threshold | 49893 | CHAT: Water St & Talbot Trail, Chatham-Kent, Replacement | 2031 | 277756.7936
Southwest | Div_02 - Chatham | Distribution Pipe | Fail | Dollar threshold | 101164 | CHAT: Ridge St, West Lorne, Replacement | 2023 | 49198.4464
Southwest | Div_02 - Chatham | Distribution Pipe | Fail | Dollar threshold | 102251 | CHAT: Gordon St & Elm St, Chatham-Kent, Replacement | 2026 | 78193.3642
Southwest | Div_02 - Chatham | Distribution Pipe | Pass |  | 49742 | CHAT: Ridgetown LP, Ridgetown, Replacement | 2027 | 1908146.5651 | Replace approximately 1.9 km of NPS 4 low-pressure (LP) steel main in downtown Ridgetown with approximately 1.0 km of NPS 4 intermediate-pressure (IP) plastic main and 760 m of 2-inch IP plastic main. This IP system contains several leaks and is located mostly in wall-to-wall concrete (from Market Lane to Victoria Ave.). There are approximately 75 homes and businesses fed off of this system. | Planned
Southwest | Div_02 - Chatham | Distribution Pipe | Pass |  | 49749 | Tilbury South Line Replacement | 2031 | 2863693.4752 | General: The capital expenditure included in this category covers a variety of planned maintenance projects. The projects covered under this expenditure include low-pressure system replacements, distribution pipeline replacements due to historical leakage and integrity concerns, pipeline casing replacements, bridge and water-crossing replacements and repairs, etc. These projects are often identified through planned inspections and pipeline surveys and would then be assessed and planned based on risk and resource availability. | Planned
Southwest | Div_02 - Chatham | Distribution Pipe | Pass |  | 49859 | CHAT: Tweedsmuir LP, Chatham, Replacement | 2027 | 3046095.7893 | Replace 2,300 m of 4-inch steel, bare, protected gas main (2.5 kPa) with 4,300 m of 2-inch plastic gas main (420 kPa) in the Tweedsmuir subdivision in the Municipality of Chatham-Kent. There are 167 services that will need to be replaced. | Planned
Southwest | Div_02 - Chatham | Distribution Pipe | Pass |  | 733723 | NPS 8 Dover Centre Retrofit |  | 2065337.1352 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2026 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_02 - Chatham | Distribution Pipe | Pass |  | 733733 | NPS 10 Essex | 2024 | 4031684.4128 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2025 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_02 - Chatham | Distribution Stations | Fail | Dollar threshold | 101354 | CHAT - 07H-601 Burke Line - Heater Replacement | 2027 | 975725.1683
Southwest | Div_02 - Chatham | Distribution Stations | Fail | Dollar threshold | 101610 | CHAT - 07J-301 Ridgetown North Transmission - Replace heater | 2024 | 603602.4844
Southwest | Div_02 - Chatham | Distribution Stations | Fail | Dollar threshold | 502775 | CHAT - 08H-302C Greenhill Produce - rebuild and heater addition | 2023 | 570843.9686
Southwest | Div_02 - Chatham | Distribution Stations | Fail | Dollar threshold | 502778 | CHAT - 09G-502 Tupperville Trans - heater replacement | 2026 | 1027617.1928
Southwest | Div_02 - Chatham | Distribution Stations | Fail | Dollar threshold | 734661 | CHAT: 06J-103 Blenheim North Gate | 2026 | 285331.9258
Southwest | Div_02 - Chatham | Distribution Stations | Fail | Dollar threshold | 734669 | CHAT: 07H-501 MAYNARD LINE | 2030 | 701073.3834
Southwest | Div_02 - Chatham | Distribution Stations | Fail | Dollar threshold | 734671 | CHAT: 07K-409 MCKINLAY RD STATION | 2031 | 1602256.5054
Southwest | Div_02 - Chatham | Distribution Stations | Pass |  | 101627 | CHAT - 07G-201 Baldoon Transmission - Station Rebuild | 2023 | 996424.2307 | Issue/Concern/Opportunity: Obsolete regulators cannot be serviced nor parts obtained to repair them; obsolete heating equipment contains 20,000 L of glycol and is on the risk register. Justification: Replace regulators and heaters. Assets: 07G-201 Baldoon Transmission Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_02 - Chatham | Distribution Stations | Pass |  | 503334 | CHAT - 07G-601 Chatham North Gate | 2026 | 2830045.9158 | Issue/Concern/Opportunity: Converted BS&B and heat exchanger replacement is required. There have already been several environmental spills (glycol) as a result of condition failures from these converted heaters and is known on the risk register. Also, the condition of the heaters is creating risks around reliability and the ability to adequately provide heat. Justification: Potential for reliability issues with the safe and reliable delivery of natural gas. In addition, Possible glycol leaks from heating system equipment or piping inside building (indoor equipment typically includes boilers, pressure relief, glycol recirculation pumps, air extractors, instruments/controls, gauges, expansion tanks). Possible leaks from heating system equipment or piping located outside on station property (outdoor equipment typically includes the heat exchanger, overpressure burst disk, air extractors, instruments/controls, gauges, and atmospheric glycol expansion tank) Assets: 07G-601 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_02 - Chatham | Distribution Stations | Pass |  | 734660 | CHAT: 09F-501 Wallaceburg Baseline | 2025 | 2047658.8711 | Issue/Concern/Opportunity: There are concerns from Station Operations around the condition of the existing filter. If the filter cannot operate as per its intended use there is a potential to It is recommended to replace the complete station as there are reliability and integrity concerns. Justification: Replace filter (like for like). Assets: 09F-501 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_02 - Chatham | Growth | Pass |  | 48320 | CHAT: Company Program - New Business - Scattered Mains - Contractor* | 2020 | 2303368.5645 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southwest | Div_02 - Chatham | Growth | Pass |  | 500416 | CHAT: Company Program - Customer Connections* |  | 8728284.1719 | Chatham Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southwest | Div_02 - Chatham | Utilization | Pass |  | 48328 | CHAT: Meter & Regulator Inst Repl-Company* | 2020 | 8657519.0129 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_02 - Chatham | Transmission Pipe & Underground Storage | Pass |  | 49758 | Panhandle Regional Expansion Project | 2023 | 219431846.4836 | Issue/Concern: To provide reliable, secure, and affordable natural gas supply to meet the growth in Design Day demand of the Panhandle System: Assets: i. Dawn Yard: 700 m of 8960 kPa MOP NPS42 station header is required to maintain the maximum sustainable pressure on design day. This header will also provide operational flexibility and security of supply to the Panhandle system. ii. Panhandle Take-off Station: The existing station will be modified to meet the new system capacity demand requiring measurement, odourization and regulation assets. iii. Dover Transmission Station: This existing regulating station will be modified to connect the new NPS 36 pipeline to the upstream system. Flow measurement equipment will also be added to the station. iv. Panhandle Loop : 19 km of 6040 kPag MOP NPS36 pipeline will parallel the NPS 20 from Dover Transmission station to a new valve site at Richardson Sideroad. v. Richardson Sideroad Valve Site: A new valve site is required at the end of the NPS 36 Panhandle loop to connect to the existing NPS20 mainline. Isolation valves and launcher/receiver facilities will be installed at this location. Related Program: Not applicable | On Hold |  | LTC regulatory process in progress
Southwest | Div_02 - Chatham | Transmission Pipe & Underground Storage | Pass |  | 735972 | PREP: NPS 36 looping to Comber Transmission | 2028 | 95914555.6421 | Issue/Concern: Panhandle System expansion is driven by in-franchise growth in Chatham-Kent, Windsor-Essex and surrounding areas, including the fast-growing greenhouse market in the Leamington/Kingsville area. Based on the current forecast for in-franchise general service and contract growth in the Panhandle Transmission System market, EGI has determined that the next Panhandle facilities for expansion will need to be in place as early as the 2028 to 2029 winter season (construction beginning in 2028). These facilities are incremental to the Panhandle Regional Expansion Project and timing is dependent on the Panhandle System demands. Assets: Install approximately 12 km of NPS 36 pipeline from Richardson sideroad, looping the existing Panhandle NPS 20 pipeline to Comber Transmission Station (05E-403). Related Program: Not applicable | In Progress |  | Market side supply options to be assessed prior to LTC application
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 48336 | SARN: Dist-Repl-Contr-Services* |  | 87270.5707
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 48771 | SARN - Highway Dr and Lynwood Ave - Sarnia BU | 2024 | 369106.0675
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 48831 | SARN-Point Edward LP Leakage - Sarnia BU | 2024 | 922765.1687
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 48846 | SARN - Errol Rd E Leakage - Sarnia BU | 2023 | 1006388.473
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 48951 | SARN - Errol Rd W & Newell St. Leakage - Sarnia BU | 2023 | 848206.1264
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 101192 | SARN - Vidal & Cromwell Leakage - Sarnia BU | 2024 | 35188.1118
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 101193 | SARN - Lakeshore Rd. and Modeland Rd Leakage - Sarnia BU | 2024 | 752647.0018
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 101194 | SARN - Christina St at Highbury Pk Leakage - Sarnia BU | 2023 | 229762.9723
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 101210 | SARN - Smith Line Leakage - Sombra BU | 2024 | 142451.8729
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 101214 | SARN - Eastlawn Ave and Kember Ave Leakage - Sarnia BU | 2023 | 973537.6117
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 101295 | SARN -Kathleen Ave Leakage - Sarnia BU | 2023 | 69712.3302
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 502679 | SARN- Brigden Rd and Duncan St Leakage - Moore Twp | 2024 | 138414.7753
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 733836 | SARN - Oil Heritage Rd and Douglas Line Exposed Main | 2024 | 139696.3936
Southwest | Div_03 - Sarnia | Distribution Pipe | Fail | Dollar threshold | 735710 | SARN- Zone St Leakage BU- Wyoming | 2024 | 96890.3427
Southwest | Div_03 - Sarnia | Distribution Pipe | Pass |  | 1267 | Cogen Retrofit |  | 2005303.8142 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2024 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGIs pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_03 - Sarnia | Distribution Pipe | Pass |  | 733720 | NPS 6 Retrofit | 2024 | 4485664.0145 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2025 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_03 - Sarnia | Distribution Pipe | Pass |  | 733734 | NPS 6 Sarnia | 2024 | 2750066.123 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2025 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_03 - Sarnia | Distribution Stations | Fail | Dollar threshold | 734679 | SARN: 12F-201I Suncor Ethanol | 2029 | 396233.1496
Southwest | Div_03 - Sarnia | Distribution Stations | Fail | Dollar threshold | 734680 | SARN: 13F-323R McPlank | 2029 | 642170.9667
Southwest | Div_03 - Sarnia | Distribution Stations | Fail | Dollar threshold | 734685 | SARN: 13F-402 Shell Canada | 2029 | 512370.4521
Southwest | Div_03 - Sarnia | Distribution Stations | Fail | Dollar threshold | 734693 | SARN: 11H-201R Oil Spring Reg Stn | 2026 | 221547.8653
Southwest | Div_03 - Sarnia | Distribution Stations | Fail | Dollar threshold | 734696 | SARN: 14F-503R Point Edward Victoria and St. Clair Reg Stn | 2027 | 242855.0174
Southwest | Div_03 - Sarnia | Distribution Stations | Pass |  | 48664 | CNG Stations - Project #1 - Dawn CNG | 2025 | 3228625.5103 | Traditionally, fleet operators fuel their vehicles with gasoline or diesel. EGI promotes the use of natural gas to these customers as an alternate fuel source to provide a lower-cost and lower-emission fueling solution for vehicles such as garbage trucks, light duty vehicles, and transit buses. Business Development is responsible for the installation, maintenance, and the safe and continued operation of NGT stations assets for these customers. NGT stations differ in operation from distribution system stations as NGT stations use and store compressed natural gas (CNG) on site at up to 4000psi. EGD has two general categories for NGT station types: Large, Mobile and Utility NGT stations and Small NGT stations (also referred to as VRAs). Large, Mobile and Utility NGT stations are similar in operation and will be evaluated for condition in the same manner. | Completed | Fail | See investment description, IRPAs not applicable for CNG
Southwest | Div_03 - Sarnia | Distribution Stations | Pass |  | 734662 | SARN: 12F-106I Suncor Hydrogen/Air Products | 2029 | 2418388.534 | Issue/Concern/Opportunity: Heater age (per integrity) is a concern. Justification: Replace heater. Assets: 12F-106I Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_03 - Sarnia | Distribution Stations | Pass |  | 734670 | SARN: 13F-501 Sarnia Industrial | 2027 | 13296976.3158 | Issue/Concern/Opportunity: The station is located on leased property that is limited in size and makes it difficult to install a required filter. In addition, the heater is past its average lifespan and there are other ergonomic concerns. There is an opportunity to merge the station with 13F-503 Churchill Rd Station and will be assessed during this project. Justification: Entire rebuild, potentially relocate. Assets: 13F-501 Related Investments: 13F-503 may potentially be merged with this station in a relocation. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_03 - Sarnia | Distribution Stations | Pass |  | 734676 | SARN: 13F-220R Vidal St | 2032 | 10592331.9334 | Issue/Concern/Opportunity: 13F-220R is experiencing flooding due to its current location. The heater age is of concern and the control valves require an upgrade. Potential relocation is necessary due to building floods. Justification: Full rebuild is required. Assets:13F-220R Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_03 - Sarnia | Distribution Stations | Pass |  | 734683 | SARN: 12F-205 Novacor Moore Trans | 2028 | 3719374.0563 | Issue/Concern/Opportunity: The heater short cycles and there are visible condition issues. The regulators’ design is insufficient causing operational concerns and will be redesigned in this project to meet current standards. Justification: Complete rebuild is required. Assets: 12F-205 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_03 - Sarnia | Distribution Stations | Pass |  | 734684 | SARN: 13O-402 Westmount Gate | 2026 | 1898795.5282 | Issue/Concern/Opportunity: Heater age (per integrity) is a concern. Loss of Heating System Function: Loss of the heating system function could result in two scenarios, (1) frost heave or (2) pressure control failure due to the freezing of station components. Frost heave occurs when the gas is cooled due to the pressure reduction and causes an upward swelling of soil around public or private property near the gas main. Freezing of station components such as creating large ice buildup around valves can prevent operation if gas isolation is required. This could result in the loss of pressure control and potentially lead to an overpressure or underpressure situation. The financial impact includes commodity loss, service disruptions, increased network leak surveys and system checks, repairs or replacement of company-owned property, or damages caused to public, commercial or industrial property. Inoperable systems will lead to a failure to maintain operational supply to customers. Justification: Replace heater. Assets: 13O-402 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_03 - Sarnia | Distribution Stations | Pass |  | 734697 | SARN: 13F-503 Churchill Rd. Trans Stn | 2027 | 6997194.8695 | Issue/Concern/Opportunity: Aging heater is a concern related to the reliable and safe delivery of natural gas. The heating system components ensure that gas temperatures within the distribution system remain above a site-specific targeted setpoint, as the reduction in temperature caused by pressure regulation can have detrimental effects on equipment performance. Loss of Heating System Function: Loss of the heating system function could result in two scenarios, (1) frost heave or (2) pressure control failure due to the freezing of station components. Frost heave occurs when the gas is cooled due to the pressure reduction and causes an upward swelling of soil around public or private property near the gas main. Freezing of station components such as creating large ice buildup around valves can prevent operation if gas isolation is required. This could result in the loss of pressure control and potentially lead to an overpressure or underpressure situation. The financial impact includes commodity loss, service disruptions, increased network leak surveys and system checks, repairs or replacement of company-owned property, or damages caused to public, commercial or industrial property. Inoperable systems will lead to a failure to maintain operational supply to customers. Justification: Heater replacement is required. Assets: 13F-503 Related Investments: INV CODE 734670 NOTE: This project could potentially be combined with Sarnia Industrial Station rebuild (under inv code noted above). If not, it will be a separate project for the heater replacement only. The execution and design team will evaluate the options closer to the execution year. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_03 - Sarnia | Distribution Stations | Pass |  | 735540 | LOND - 12F-501 Payne Kimball Rebuild | 2026 | 12445777.1412 | Issue/Concern/Opportunity: 12F-501 Payne Kimball has obsolete Jetstream pressure regulation equipment. Obsolete pressure control equipment cold increase the risk of an overpressure or under-pressure scenario. Due to the regulators being obsolete, maintenance may be impracticle. There is no meter bypass and there are ergonomic concerns. The piping and equipment layout presents ergonomic concerns and limits the ability for an employee to perform work and could lead to a potential LTI and has been risk ranked as a Medium risk. Justification: Complete rebuild is required. Assets: 9S-147H is similar to Mersea Rd 11 Trans with Odourant, backup generator. Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_03 - Sarnia | Growth | Pass |  | 48335 | SARN: Company Program - New Business - Scattered Mains - Contractor* | 2020 | 2980518.4212 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southwest | Div_03 - Sarnia | Growth | Pass |  | 500417 | SARN: Company Program - Customer Connections* |  | 8617147.3387 | Sarnia Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 30285 | Creston Ave - Southwest - London - 1734 | 2031 | 1653462.7683
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 30317 | Ross St - Southwest - London - 1560 | 2032 | 1593598.9028
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 30329 | Wortley Rd - Southwest - London - 1474 | 2032 | 1536131.9169
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 30442 | Stratford-Daly Ave with Birmingham to Worsley-1756 | 2031 | 141026.7931
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 30443 | Stratford-Mercer St from Caledonia to Brittania-1757 | 2029 | 359080.0341
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 30445 | Stratford-Mowat St from W. Gore to Brydges-1760 | 2031 | 879032.1628
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 30464 | Downie St 3 - Southwest - London - 1808 | 2029 | 1667749.5463
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48349 | LOND: Dist-Repl-Contr-Mains Leakage* | 2019 | 3661794.8442
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48350 | LOND: Dist-Repl-Contr-Services* | 2020 | 8746720.5702
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48372 | LOND - Waterloo St. BU - London | 2024 | 812421.6788
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48759 | LOND - Talbot Line BU - Talbotville | 2024 | 224283.2007
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48760 | LOND - St George & Talbot BU - St Thomas | 2024 | 92276.5169
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48765 | LOND - Belgrave BU - London | 2024 | 192242.7435
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48766 | LOND - Beverly St. BU - St Thomas | 2024 | 92302.1492
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48797 | LOND - Kent & Central BU - London | 2024 | 275547.9323
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48808 | LOND - Church & Water BU - Beachville | 2024 | 133339.5669
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48811 | LOND - Jacqueline BU - London | 2023 | 1353505.3091
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48816 | LOND - St George St BU-Yarmouth | 2024 | 66152.0096
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48826 | LOND- Whetter & Wellington BU - London | 2023 | 112097.726
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48828 | LOND-Sycamore & St Julien - London | 2024 | 198650.8349
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48829 | LOND - Dalmage & Wood BU - London | 2024 | 192242.7435
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48852 | LOND - St Neots & Ridout BU - London | 2024 | 106671.6535
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48856 | LOND - PH 2 Stevenson & Brydges BU - London | 2023 | 493229.9942
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48860 | LOND - Cathcart & Alma BU - Ingersoll | 2024 | 93337.6968
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48873 | LOND - Seeley & Burslem BU - London | 2024 | 80003.7401
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48874 | LOND - Elworthy & Edward BU - London | 2024 | 133339.5669
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48875 | LOND - Malcolm Street BU - London | 2024 | 80003.7401
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48876 | LOND - Summit & Oxford BU - London | 2024 | 115345.6461
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48877 | LOND - Pall Mall & William BU - London | 2024 | 80003.7401
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48878 | LOND - Grand & Wellington BU - London | 2024 | 106671.6535
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48879 | LOND: - Elmwood Place BU - London | 2024 | 106671.6535
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48880 | LOND - King & Adelaide BU - London | 2024 | 26667.9134
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48881 | LOND - Riverside Dr & Wharncliffe BU - London | 2024 | 140978.0119
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48882 | LOND - Tweedsmuir BU- London | 2024 | 66669.7834
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48888 | LOND - Parkway & Huron BU - London | 2023 | 219213.3308
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48891 | LOND - Fellner & Langmuir, Ashland & Wilton BU - London | 2024 | 945193.4888
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48913 | LOND - Borden St. BU - London | 2024 | 89713.2803
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48917 | LOND - Cheapside, Gammage & Linwood BU - London | 2023 | 986459.9884
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48918 | LOND - Wharncliffe & Baseline BU - London | 2023 | 311382.5721
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48919 | LOND - Putnam Rd. BU - London | 2024 | 93337.6968
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48922 | LOND - Lexington & Wharncliffe BU - London | 2024 | 44856.6401
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 48923 | LOND - Tecumseh Ave BU - London | 2024 | 358853.1212
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 101543 | LOND - SCLAIR Pipe Replacement- Mount Brydges | 2031 | 979494.99
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 101791 | LOND: Corrosion Rectifier Groundbed Program* | 2021 | 77750.9827
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 501003 | LOND: PSLL Maintenance | 2023 | 367431.4351
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 501665 | LOND - Murray St. BU - London | 2024 | 51264.7316
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 503339 | LOND - Wonham St Leakage, Ingersoll | 2023 | 78954.165
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 733531 | LOND - Waterloo St at Horton St Leakage BU- London | 2024 | 232120.2966
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 734459 | LOND - 7113 to 7079 Longwoods Rd. - London | 2031 | 251870.1403
Southwest | Div_04 - London | Distribution Pipe | Fail | Dollar threshold | 734460 | LOND - Breck Ave. & Eastgate Cres. - London | 2031 | 251870.1403
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30275 | Adelaide St N - Southwest - London - 1527 | 2027 | 3803718.5691 | Adelaide St. N. - Southwest - London - 1527 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30277 | Base Line Rd E - Southwest - London - 1461 | 2030 | 5321934.6272 | Base Line Rd. E. - Southwest - London – 1461 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30278 | Briscoe St W - Southwest - London -1735 | 2027 | 3096133.3595 | Briscoe St. W. - Southwest - London - 1735 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30279 | Briscoe St W 2 - Southwest - London - 1736 | 2027 | 3520899.4411 | Briscoe St. W. 2 - Southwest - London - 1736 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30282 | Cheapside St - Southwest - London - 1453 | 2030 | 2974341.1995 | Cheapside St. - Southwest - London - 1453 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Majority will be replaced with bare and unprotected (BU) in 2023. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30283 | Cheapside St 2 - Southwest - London -1534 | 2032 | 5227158.3908 | Cheapside St. 2 - Southwest - London -1534 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Some bare and unprotected – low-pressure (LP) was already replaced in 2021. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30284 | Clarke Rd- Southwest - London - 1483 | 2029 | 3533833.9285 | Clarke Rd. - Southwest - London - 1483 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30290 | E Centre St - Southwest - London - 1412 | 2032 | 2605398.8189 | E. Centre St. - Southwest - London - 1412 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30291 | Elworthy Ave - Southwest - London - 1446 | 2031 | 5537291.4881 | Elworthy Ave. (moratorium until 2026) - Southwest - London - 1446 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Majority of this project is scheduled for 2024. Lambeth had city work in 2021 and moratorium is until 2026. This project was updated to reflect moratorium until 2026. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30292 | Emery St E - Southwest - London - 1472 | 2032 | 5024155.5345 | Emery St. E. (moratorium until 2026) - Southwest - London - 1472 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: City did reconstruction in 2020 and moratorium is until 2026. This project was updated to reflect moratorium until 2026. | Completed | Fail | Potential project scope could be replaced with NPS 2. It is recommended to maintain pipe size for trunk mains or system resiliency. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30294 | Front St - Southwest - London - 1393 | 2031 | 2375054.4886 | Front St. - Southwest - London - 1393 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | NPS 2, cannot downsize or retire
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30298 | Glenora Dr - Southwest - London - 1517 | 2030 | 3151367.7675 | Glenora Dr. - Southwest - London - 1517 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30300 | Greenwood Ave - Southwest - London - 1428 | 2030 | 3359335.7528 | Greenwood Ave. - Southwest - London - 1428 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30301 | Hamilton Rd - Southwest - London - 1408 | 2031 | 3833564.2832 | Hamilton Rd. - Southwest - London - 1408 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30312 | Mornington Ave - Southwest - London - 1531 | 2031 | 8694188.3369 | Mornington Ave. - Southwest - London - 1531 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: Some bare and unprotected (BU) and the 24-inch is on Strand s/b a separate project. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30313 | Old Lakeshore Rd - Southwest - London - 1572 | 2031 | 4281495.1781 | Old Lakeshore Rd. - Southwest - London - 1572 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Completed | Fail | Potential project scope could be replaced with NPS 2. IRPAs not applicable and scope to be confirmed when project enters the detailed design phase.
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30316 | Ridout St S - Southwest - London - 1470 | 2029 | 2840206.6494 | Ridout St. S. - Southwest - London - 1470 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30319 | Southdale Rd E - Southwest - London - 1434 | 2032 | 8236024.6737 | Southdale Rd. E. - Southwest - London - 1434 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30325 | Wellington Rd - Southwest - London - 1449 | 2029 | 4758337.8246 | Wellington Rd. - Southwest - London - 1449 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30327 | Wilton Grove Rd - Southwest - London - 1395 | 2032 | 5077157.2821 | Wilton Grove Rd. - Southwest - London - 1395 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30328 | Windsor Ave - Southwest - London - 1515 | 2029 | 3248499.9884 | Windsor Ave. - Southwest - London - 1515 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30441 | Stratford-Huron St-Matilda to Douglas Phase 2-1758 | 2030 | 3143889.4024 | Stratford - Huron St. - Matilda to Douglas Phase 2 - 1758 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30461 | Courthouse Sq - Southwest - London - 1802 | 2032 | 1860013.8134 | Courthouse Sq. - Southwest - London - 1802 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30462 | Downie St 1 - Southwest - London - 1806 | 2030 | 3536340.3576 | Downie St. 1 - Southwest - London - 1806 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30465 | Ontario Rd - Southwest - London - 1803 | 2032 | 1299308.5596 | Ontario Rd. - Southwest - London - 1803 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 30466 | Queen St E - Southwest - London - 1804 | 2030 | 2662891.2337 | Queen St. E. - Southwest - London - 1804 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. | Planned
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 48348 | LOND: Dist-Repl-Contr-Mains Municipal* | 2020 | 45104908.0831 | General: Projects in the relocation category are capital expenditures required to replace or relocate segments of pipeline in order to accommodate municipal infrastructure work. The cost sharing for this work is managed through the Franchise Agreements established with municipalities. A consultative approach is used between the municipality and EGI to avoid conflicts with municipal infrastructure early in the planning stage. If a conflict is unavoidable, pipeline assets are typically relocated or replaced. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 48364 | LOND: Anodes* | 2020 | 8279618.9486 | General: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within EGI's system. These installations and replacements are based on the internal Standard Operating Practice established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 100295 | NPS 8 Port Stanley Replacement | 2024 | 19067428.5231 | Issue/Concern/Opportunity: The NPS 8 Port Stanley line is approximately 20 km of NPS 8 built in 1959, with unknown grade and wall thickness, bare and protected, and Dresser construction (some gas welded – such welds are usually susceptible to lack of fusion imperfections). There has been a history of a significant number of leaks due to corrosion on this single-feed system that provides natural gas to Port Stanley and St. Thomas, with about 13,000 customers including the St. Thomas hospital, a psychiatric hospital in St. Thomas and a retirement home in Port Stanley. External corrosion has created difficulties with repairs due to the inability to weld. In one repair case, it took Operations three weeks to locate a suitable weld location for a repair. Repairs often require the use of split sleeves ($8K/each). Depth of cover is a significant risk factor, with two exposed pipe sections being reported over creek crossings in December 2019. There are significant accessibility issues with locations of the pipe, making it difficult for emergency response and condition surveys. Some sections of pipe are heavily overgrown while other locations can be over 500 m from the nearest road. There are three below-grade stations that are considered confined spaces and which often flood, and must be evacuated before inspections and maintenance can occur. Gas supply from Lake Erie (New Dundee Comp) was known to have high moisture content and may contribute to internal corrosion. No isolation is built into the single feed system; so if supply needs to be shut down, all downstream customers would be affected. In 2000, 6.8 km of main were replaced due to corrosion and exposed pipe. In 2003, 230 meters were replaced due to a Class B leak under a river crossing. Three casings on the system are known to be shorted. An attempted pressure increase in 1970 resulted in numerous leaks from compression couplings and pipe; therefore, the pipe cannot be pressure-elevated. Assets: Port Stanley line is approximately 20 km of NPS 8 built in 1959. Related Programs: Not applicable. | On Hold |  | Technical Evaluation "On Hold" until further assessment from the E-DIMP Program confirms the project scope and timing.
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 733736 | NPS 6 London | 2023 | 2491060.5768 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2024 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_04 - London | Distribution Pipe | Pass |  | 736302 | Wardsville Line - Southwest - London - 1797 | 2028 | 13046196.0574 | Wardsville Line - Southwest - London - 1797 Vintage steel exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (Vintage Steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization Site Specific: Recently completed a CIS/DCVG survey on it and it has many possible coating holidays. There was also a leak discovered in early December 2021. The pipeline has the same characteristics as the London Lines with respect to aerial crossings oThe design / construction method at the time of installation was to install aerial crossing over any drainage ditch or water crossing oCoating issues where the pipeline transitions out of the ground. The majority of the pipeline is within easement, travelling cross county for most of the running line; operationally the preference would be to relocate to the right of the way. | Completed | Pass | ETEE - Potentially could reduce project scope.
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 48376 | LOND - Mitchell Station Rebuild - London | 2028 | 427164.6953
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 49861 | LOND: 14O-619I 3M Customer Station Rebuild; 528 | 2030 | 466867.2868
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 49862 | LOND: 14O-603I 3M Customer Station Rebuild | 2030 | 466867.2868
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 100978 | LOND - 17K-601R Grand Bend Northgate | 2023 | 993873.3847
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 100993 | 19O-101 Dublin Gate | 2027 | 1298927.4072
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 100994 | 15O-401R Bryanston Gate | 2023 | 1167061.8802
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 100998 | 15R-604R Young & Peel LP Stn | 2026 | 175935.0695
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 100999 | 13O-113R Bathurse & Talbot | 2023 | 215476.7399
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 733607 | LOND - 15N-671 Medway Creek Removal and Main Extension | 2023 | 74731.8173
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734658 | LOND: 13O-109R Edith and Mt. Pleasant | 2023 | 215476.7399
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734664 | LOND: 10M-503R Main and Shackleton | 2024 | 211467.0178
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734668 | LOND: 13O-210R Hale and Burslem | 2024 | 211467.0178
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734678 | LOND: 13O-212R Highbury and Brydges | 2024 | 211467.0178
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734681 | LOND: 14O-510R Curry and Oxford | 2024 | 211467.0178
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734687 | LOND: 19O-601 Mitchell Gate | 2027 | 520403.6087
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734688 | LOND: 13O-206R London Baseline Reg Station | 2025 | 1350856.9135
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734690 | LOND: 17M-601 Centralia Stn | 2025 | 342234.3041
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734691 | LOND: 15R-608R Walter and Fyfe Reg Stn | 2025 | 219546.5347
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734692 | LOND: 13O-123R Napier and Blackfriars Reg Stn | 2025 | 219546.5347
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 734694 | LOND: 11O-306R Wellington and Fifth Reg Stn | 2026 | 221547.8653
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 735272 | LOND: 13O-401 White Oaks | 2028 | 646802.2125
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 735275 | LOND: 16O-301 St. Mary's Gate | 2028 | 646802.2125
Southwest | Div_04 - London | Distribution Stations | Fail | Dollar threshold | 735276 | LOND: 15J-401 Forest Gate Transmission Station | 2025 | 374520.5592
Southwest | Div_04 - London | Distribution Stations | Fail | Timing | 500438 | 10O-501 Port Stanley Gate Reg Corrosion Repair | 2023 | 3113825.721
Southwest | Div_04 - London | Distribution Stations | Pass |  | 100996 | 13P-101R Sovereign & Gore | 2024 | 1867317.8483 | Issue/Concern/Opportunity: There is frost heave impacting the road outside of station. Stations where a highpressure reduction occurs can be subject to freezing of station components, which may cause a loss of pressure control if there is moisture in the gas, heaving of the station piping if there is moisture in the ground surrounding the station, or the temperature reduction of the gas could cool the downstream piping and impact the surrounding grounds including the potential to damage roads. The effects of the Joule-Thomson Effect. Ice buildup is visible on the downstream components and the station assembly is misaligned due to heaving. Consequence on a 35DD ION: The southeast corner of London will have low pressures and areas dropping below minimums. Approximate number of customers Lost: 3,600+ Assets: Tembec Spruce Falls SMS (41402004) Related Investments: N/A | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_04 - London | Distribution Stations | Pass |  | 503272 | London/Sarnia PFM Compliance Program* |  | 1031773.3734 | Issue/Concern/Opportunity: -PFMs that require a bypass will be rebuilt w/bypass to the new standard: oWhen they are due for a meter exchange and in the meter seal expiry year, provided that year is between 2022 and 2026. This will fall under the meter exchange budget and costs are not covered in this program. oIf the meter seal year is not between 2022 and 2026, the set will be rebuilt with a bypass the year after it is inspected. This will allow the technicians to identify which will require rebuilt at the time of inspection, and Sohan and I will be developing a process to get work orders generated for these rebuilds after the inspection. Also ensures that we focus our efforts on rebuilding active PFMs requiring rebuild. While I originally mentioned a proactive strategy to rebuild prior to the inspection year, we decided against that. -Assumption is that 50% of PFMs will need to be rebuilt. -Calculations are based on an estimate of $5500 per rebuild. As you know there is a significant swing depending on the pipe size, volume, existing set up (first stage cut, etc) that may influence this including the release of the new SEADs designs, that I have not seen yet. | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_04 - London | Distribution Stations | Pass |  | 734674 | LOND: 14O-503R Highbury and Cheapside Dist Stn | 2024 | 9583266.7728 | Issue/Concern/Opportunity: The station has obsolete regulators (Grove regulators) where replacement parts are no longer available. In the event of a failure, no replacement parts are available. In addition, the station is receving liquids and only has a dry gas filter installed. There are concerns with the potential of liquids entering the pressure control equipment and potentially impacting the performance of these assets. There is a single bypass valve that does not meet the current design standards and could impact manual bypass operations. The site has a large pressure drop and heat is required to prevent heaving. Justification: Complete station rebuild is required. Assets: 14O-503R Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_04 - London | Distribution Stations | Pass |  | 734689 | LOND: 14R-104 Beachville Domtar Trans Stn | 2024 | 8458680.713 | Issue/Concern/Opportunity: The station is equipped with a dry gas filter and is currently receiving liquids at the inlet of the station without the ability to remove the liquids. There are concerns that if liquid gets to the pressure control equipment, there may not be reliable pressure control and may lead to other operational issues. The heating system is obsolete and has the potential to leak glycol to the ground. There is a significant volume of glycol in the heating system (i.e., > 5,000 L) that could lead to environmental concerns if released from the existing aging heating system. This investment is to replace the heating system, the filter and remove underground insulation. Justification: Complete rebuild is required. Assets: 14R-104 Related Program: Not applicable | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_04 - London | Distribution Stations | Pass |  | 734695 | LOND: 15Q-603 C C Trans Stn | 2027 | 4635769.8634 | Issue/Concern/Opportunity: Heater age (per integrity) is a concern. Loss of Heating System Function: Loss of the heating system function could result in two scenarios, (1) frost heave or (2) pressure control failure due to the freezing of station components. Frost heave occurs when the gas is cooled due to the pressure reduction and causes an upward swelling of soil around public or private property near the gas main. Freezing of station components such as creating large ice buildup around valves can prevent operation if gas isolation is required. This could result in the loss of pressure control and potentially lead to an overpressure or underpressure situation. The financial impact includes commodity loss, service disruptions, increased network leak surveys and system checks, repairs or replacement of company-owned property, or damages caused to public, commercial or industrial property. Inoperable systems will lead to a failure to maintain operational supply to customers. FIMP will assess the site closer to execution to determine if additional components require replacement. Assets: 15Q-603 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_04 - London | Distribution Stations | Pass |  | 735155 | LOND: 21L-201 Goderich Gate | 2028 | 2005086.8588 | Issue/Concern/Opportunity: Heater age (per integrity) is a concern. Justification: Replace heater. Assets: 21L-201 Related Investments: Not applicable. | Completed | Fail | Distribution station condition related, IRPA not applicable
Southwest | Div_04 - London | Growth | Pass |  | 30551 | SRP_Southwest_Embro_15Q-301STN_Rebuild | 2023 | 504895.6309 | Station flows over capacity in Winter 2023. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30553 | SRP_Southwest_Forest_Townsend Line_Reinforcement_NPS6_4500m_3450kPa | 2031 | 6156825.7074 | Maintain system minimum inlets to downstream constraints. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30554 | SRP_Southwest_Innerkip_16S-503STN_Rebuild | 2029 | 1373565.6593 | Rebuild Innerkip Transmission Station to a capacity of 2,470 m3/hr and set pressure to 1,860 kPa so downstream stations meet their inlet pressures. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30555 | SRP_Southwest_Kettle Point_Ravenswood Line_Reinforcement_NPS4_2000m_3450kPa | 2027 | 2359163.0814 | Maintain system minimum inlets to downstream constraints. | Completed | Pass | CNG, ETEE - CNG potentially could reduce or defer project scope, ETEE potentially could eliminate, reduce or defer project scope.
Southwest | Div_04 - London | Growth | Pass |  | 30556 | SRP_Southwest_London_13O-402STN_Rebuild | 2023 | 1758068.2441 | Westmount station is flowing over capacity, currently without System Reinforcement Plan (SRP) growth. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30557 | SRP_Southwest_London_Bradley Ave_Reinforcement_NPS6_500m_420kPa | 2031 | 322329.4687 | A 6-inch reinforcement to maintain system minimum pressures is required. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30558 | SRP_Southwest_London_Byron Baseline_Reinforcement_NPS8_700m_420kPa | 2023 | 1684679.3575 | There is 8-inch main out of Byron station required to increase pressures north. | Completed | Pass | CNG, ETEE - Potentially could reduce or defer project scope.
Southwest | Div_04 - London | Growth | Pass |  | 30559 | SRP_Southwest_Mt. Brydges_12M-303RSTN_Rebuild | 2023 | 1316573.2934 | Station is flowing over capacity. Minimum inlet can increase. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30560 | SRP_Southwest_Sarnia_New STN & Reinforcement_NPS6_1600m_420kPa | 2032 | 1176279.6019 | A new distribution station off of the existing 1,210 kPa system and a main extension to tie into the 420 kPa system north of Sarnia along the water is required. | In Progress
Southwest | Div_04 - London | Growth | Pass |  | 30563 | SRP_Southwest_Bluewater_New STN & Reinforcement_NPS4_7200m_3450kPa | 2025 | 8833102.2061 | Transmission pipe from Bluewater to a new station in Saint Joseph is required (verify Maximum Operating Pressure [MOP] of 550 kPa). | Completed | Pass | CNG, ETEE - Potentially could reduce or defer project scope.
Southwest | Div_04 - London | Growth | Pass |  | 30564 | SRP_Southwest_Oil Springs_11H-201RSTN_Rebuild | 2023 | 192796.7294 | Station is flowing over capacity at Oil Springs. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30565 | SRP_Southwest_Port Stanley_George Street_Reinforcement_NPS4_300m_420kPa | 2029 | 149246.0526 | A 4-inch looping is required to increase pressures downstream. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30566 | SRP_Southwest_Woodstock_Reinforcement & Reinforcement_NPS6_8200m_1900kPa | 2024 | 11662726.3864 | New 6-inch ST (1,900 kPa) line from Beachville Lateral to existing 6-inch main. New station is to be constructed on ether end of new main. | In Progress
Southwest | Div_04 - London | Growth | Pass |  | 30568 | SRP_Southwest_Sarnia_13F-324RSTN_Rebuild | 2023 | 51723.9832 | Station is flowing over capacity. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30569 | SRP_Southwest_St. Marys_Church Street_Reinforcement_NPS6_100m_420kPa | 2032 | 59949.8284 | Trout Creek River Crossing | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30570 | SRP_Southwest_St. Marys_Glass Street_Reinforcement_NPS4_650m_420kPa | 2030 | 108562.263 | New business reinforcement on new street in St Mary's is required. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30571 | SRP_Southwest_Stratford_18Q-501RSTN_Rebuild | 2030 | 1422250.5814 | Increase maximum sustainable and increase capacity. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30572 | SRP_Southwest_Talbotville_11O-173STN_Rebuild | 2023 | 385229.8138 | Talbotville South Station will be flowing over capacity in Winter 2023. Station upgrades are required. New station should have an outlet of 380 kPa instead of the existing 275 kPa. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30573 | SRP_Southwest_Talbotville_Talbotville Gore Rd_Reinforcement_NPS4_500m_420kPa | 2030 | 222927.7713 | A 4-inch main reinforcement is required to maintain system minimum pressures. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30575 | SRP_Southwest_Thamesford_Thorndale Road_Reinforcement_NPS4_570m_420kPa | 2031 | 246999.3076 | Reinforcement is needed to maintain system minimum pressures in Thamesford. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30579 | SRP_Southwest_Wonderland_New STN & MOP Upgrade | 2026 | 13032227.3209 | A Maximum Operating Pressure (MOP) upgrade of the 6,160 listed pipe out of Hensall Transmission, upgrade to the inlets of existing stations along this line to 6,160 kPa inlet MOP, and installation of new station near Lucan to regulate from 6,160 to 3,450 is required. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 30580 | SRP_Southwest_Woodstock_Oxford Road 17_Reinforcement_NPS6_1100m_420kPa | 2023 | 502456.8328 | A 6-inch loop is required to bump up pressures in north Woodstock. | Planned
Southwest | Div_04 - London | Growth | Pass |  | 48347 | LOND: Company Program - New Business - Scattered Mains - Contractor* | 2020 | 38833989.6103 | Scattered Mains | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southwest | Div_04 - London | Growth | Pass |  | 49805 | SRP_Southwest_Hensall Trans_14N-302STN_Rebuild | 2023 | 8220499.9035 | A rebuild of the Hensall Transmission Station (14N-302) is required to increase capacity and maximum sustainable outlet pressure to defer reinforcement of the Hensall Transmission System by three years. This project was assumed to be completed in 2023 for the community expansion projects on this system. This could affect its ability to be optimized or deferred. Grain dryer customer inquiries on this system are the driver for this project. | Completed | Fail | Timing - Market based supply side alternatives not applicable
Southwest | Div_04 - London | Growth | Pass |  | 500418 | LOND: Company Program - Customer Connections* |  | 108963295.8613 | London Customer Connections Program Items | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Southwest | Div_04 - London | Growth | Pass |  | 734672 | SRP_Southwest_Kerwood_12K-301STN_Rebuild | 2026 | 3905901.0013 | Issue/Concern/Opportunity: Heater, building, dry gas filter, general condition, heater past average lifespan (per integrity), and capacity increase are all concerns. A complete rebuild is required. Distribution Optimization Engineering (DOE) has also called out a need for additional capacity and a new station design will add this. Assets: 12K-301 Related Programs: Not applicable | Planned
Southwest | Div_04 - London | Utilization | Pass |  | 48361 | LOND: Meter & Regulator Inst Repl-Contractor* | 2020 | 89253270.7901 | Meter & Reg Install- Replacement | Completed | Fail | See investment description, IRPAs not applicable
Southwest | Div_04 - London | Transmission Pipe & Underground Storage | Pass |  | 100699 | Dawn Parkway Expansion Project (Dawn-Enniskillen NPS 48) | 2029 | 339185786.9137 | Issue/Concern: In response to increased natural gas demand growth along the Dawn Parkway System, the Kirkwall to Hamilton Expansion has a forecast in-service date of 2029 to 2030 and will provide reliable, secure, economic natural gas capacity to meet the growing design day demand of the Dawn Parkway Transmission system which serves both in- and ex-franchise markets. These facilities are incremental to the Kirkwall to Hamilton Expansion (INV 48654) and timing is dependent on the Dawn Parkway System demands. Assets: Install approximately 17.2 km of NPS 48 internally-coated pipeline from Dawn Compressor Station (10G-301) to Enniskillen Valve Site (11H-301V) on the Dawn Parkway System. Related Program: Not applicable | In Progress |  | Market side supply options to be assessed prior to LTC application
Southwest | Div_16 - Hamilton | Distribution Pipe | Pass |  | 733738 | NPS 8 Port Elgin South Hampton | 2025 | 5422124.4745 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) Program, supporting refinement of pipeline risk profile. Associated 2026 Operations and Maintenance (O&M) spend for ILI. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 3380 | SCOR:61004 Top End-O/H incl. Cam Upgrade |  | 24938.2288
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 4145 | SCOR:132FCV033-Upgrade | 2023 | 311727.8097
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8469 | SCOR:iNET-Upgrade | 2027 | 90324.7834
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8624 | SCHT:Control Room-Expand | 2023 | 1296787.8957
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8626 | SCHT:Controls-Upgrade | 2027 | 90324.7834
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8627 | SCHT:XV,ESV,Actuators-O/H* | 2032 | 1795921.2911
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8628 | SCHT:Dehy Automatn-Upgrade | 2023 | 405246.1675
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8631 | SSOM:Instr,Controls-Upgrade* | 2029 | 875746.0152
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8632 | SSOM:GAC Fan-Upgrade | 2025 | 505897.5793
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8633 | SSOM:Transfr Switch-Replace | 2027 | 270974.1835
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8652 | LM:MS Wireless Mesh-Install* | 2024 | 493016.2173
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8687 | SSOM:61001-Engine Minor | 2023 | 162098.5867
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8688 | SSOM:61002-Engine minor | 2023 | 162098.5867
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8841 | SCOR:HMI Hi Perf Grafx-Install | 2024 | 1150370.9714
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8842 | MM:HMI Hi Perf Grafx-Replace 2026 | 2026 | 1182733.1179
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8843 | MM:HMI Hi Perf Grafx-Replace 2029 | 2029 | 1250105.3559
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8844 | SCOR:HMI PCs-Replace* | 2023 | 81049.2934
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8845 | SCOR:HMI PCs-Replace* | 2025 | 83962.8187
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8846 | SCOR:HMI PCs-Replace* | 2028 | 89555.0367
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8848 | SCOR:810001 IDC-Replace 2026 | 2026 | 849991.4187
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8849 | SCOR:810001 IDC-Replace 2031 | 2031 | 906624.9006
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8850 | SSOM:810001 IDC-Replace | 2028 | 551107.5237
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8851 | SSOM:UPS-replace 2023 | 2023 | 162098.4371
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 8852 | SSOM:UPS-replace 2027 | 2027 | 180649.4001
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9023 | SM:FIMP Recommend'ns-Implement 2023* | 2023 | 62345.6218
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9024 | SM:FIMP Recommend'ns-Implement 2024* | 2024 | 64068.894
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9025 | SM:FIMP Recommend'ns-Implement 2025* | 2025 | 64586.7956
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9026 | SM:FIMP Recommend'ns-Implement 2026* | 2026 | 65384.0036
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9027 | SM:FIMP Recommend'ns-Implement 2027* | 2027 | 69480.6154
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9028 | SM:FIMP Recommend'ns-Implement 2028* | 2028 | 68888.5025
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9063 | SM:SCADA-Annual Upgrade 2023* | 2023 | 68580.0792
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9064 | SM:SCADA-Annual Upgrade 2024* | 2024 | 70475.6758
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9065 | SM:SCADA-Annual Upgrade 2025* | 2025 | 71045.3666
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9066 | SM:SCADA-Annual Upgrade 2026* | 2026 | 71922.2941
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9081 | SM:SCADA-Annual Upgrade 2027* | 2027 | 76428.5603
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 9082 | SM:SCADA-Annual Upgrade 2028* | 2028 | 75777.237
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 10030 | SCHT:UPS-replace | 2026 | 33999.55
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12863 | SCOR:Unit Pre-Heat-Convrt 12863 | 2024 | 352378.5328
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12864 | SCOR:Unit Pre-Heat-Convrt 12864 | 2024 | 352378.5328
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12865 | SCOR:Unit Pre-Heat-Convrt 2025 | 2025 | 355226.988
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12869 | SM:Obsolete Elec-Replace 2023* | 2023 | 68580.2289
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12870 | SM:Obsolete Elec-Replace 2024* | 2024 | 70475.8296
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12871 | SM:Obsolete Elec-Replace 2025* | 2025 | 71045.5216
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12872 | SM:Obsolete Elec-Replace 2026* | 2026 | 71922.451
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12873 | SM:Obsolete Elec-Replace 2027* | 2027 | 76428.727
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12878 | SM:Obsolete Instr-Replace 2023* | 2023 | 68580.2289
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12879 | SM:Obsolete Instr-Replace 2024* | 2024 | 70475.8296
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12880 | SM:Obsolete Instr-Replace 2025* | 2025 | 71045.5216
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12881 | SM:Obsolete Instr-Replace 2026* | 2026 | 71922.451
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12882 | SM:Obsolete Instr-Replace 2027* | 2027 | 76428.727
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12913 | SCOR:62008 Comp-Major O/H | 2031 | 453312.3666
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12914 | SCOR:62009 Comp-Major O/H | 2030 | 458505.0555
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12915 | SCOR:62010 Comp-Major O/H | 2029 | 445157.5915
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12916 | SCOR:62011 Comp-Major O/H | 2028 | 447774.8526
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12919 | SCOR:61004 Bottom End-O/H | 2023 | 124691.1438
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12922 | SCOR:620xx Cyl Liner-Replace* | 2023 | 327987.4351
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12923 | SCOR:620xx Cyl Liner-Replace* | 2025 | 365523.3293
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12928 | SCOR:64109 JWC-Replace | 2028 | 738159.7378
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12929 | SCOR:641 JWC VFD-Install | 2029 | 852739.8234
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12940 | SCOR:Obsolete Mech-Replace 2023* | 2023 | 118456.4869
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12947 | SM:100MOV Yard Valve-Replace 2024* | 2024 | 503464.3964
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12951 | SCOR:100MOV Yard Valve-Replace 2023* | 2023 | 979845.253
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12952 | SM:100MOV Yard Valve-Replace 2027* | 2027 | 545990.6348
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12953 | SM:100MOV Yard Valve-Replace 2025* | 2025 | 507534.1557
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12954 | SM:100MOV Yard Valve-Replace 2026* | 2026 | 513798.7535
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12955 | SM:100MOV Yard Valve-Replace 2029* | 2029 | 538173.5694
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12975 | SCOR:622xx Bypass Valve-Upgrade 2026 | 2026 | 345227.2627
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12977 | SCOR:622xx Bypass Valve-Upgrade 2023 | 2023 | 329184.7693
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12978 | SCOR:622xx Bypass Valve-Upgrade 2024 | 2024 | 338283.6436
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12979 | SCOR:622xx Bypass Valve-Upgrade 2025 | 2025 | 170508.8488
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12984 | SCOR:622xx Unit Vlv-Heat Trace* | 2023 | 16459.0814
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12985 | SCOR:622xx Unit Vlv-Heat Trace* | 2024 | 16914.0207
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12986 | SCOR:622xx Unit Vlv-Heat Trace* | 2025 | 17050.7454
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12992 | SCOR:352 Gas Detectrs-Replace 2023 | 2023 | 16459.0814
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12993 | SCOR:352 Gas Detectrs-Replace 2024 | 2024 | 16914.0207
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12994 | SCOR:352 Gas Detectrs-Replace 2025 | 2025 | 17050.7454
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12995 | SCOR:352 Gas Detectrs-Replace 2026 | 2026 | 17261.2062
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12996 | SCOR:352 Gas Detectrs-Replace 2027 | 2027 | 18342.7011
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12997 | SCOR:530 FCV Positioners-Replace 2024 | 2024 | 169141.5912
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12998 | SCOR:530 FCV Positioners-Replace 2025 | 2025 | 170508.8488
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 12999 | SCOR:530 FIT186-Upgrade | 2025 | 83962.6637
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 13000 | SCOR:530 FIT126-Upgrade | 2026 | 84999.032
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 13002 | SCOR:520 MCC2 Starter-Upgrade | 2025 | 83962.6637
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 13003 | SCOR:820 APU PLC-Upgrade | 2026 | 172613.4744
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 13023 | SCOR:810 Touch Screens-Rplace | 2028 | 27279.8251
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 13026 | SCOR:810 Touch Screens-Rplace* | 2023 | 24688.8465
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 13027 | SCOR:810 Touch Screens-Rplace* | 2024 | 25371.2617
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 13028 | SCOR:810 Touch Screens-Rplace* | 2025 | 25576.3506
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 13029 | SCOR:810 Touch Screens-Rplace* | 2026 | 25892.0447
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 13030 | SCOR:810 Touch Screens-Rplace* | 2027 | 27514.3017
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 13031 | SCOR:MCC3 APU PLC-Rplace | 2025 | 596781.5135
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 17109 | SCOR:Obsolete Mech-Replace 2024* | 2024 | 121730.6988
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 17117 | SCOR:Obsolete Mech-Replace 2025* | 2025 | 122714.71
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 17118 | SCOR:Obsolete Mech-Replace 2026* | 2026 | 124229.4028
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 17119 | SCOR:Obsolete Mech-Replace 2027* | 2027 | 132012.9526
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 17120 | SCOR:Obsolete Mech-Replace 2028* | 2028 | 130887.9397
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 17204 | SM:100MOV Yard Valve-Replace 2028* | 2028 | 541337.7089
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 17205 | SCOR:352 Gas Detectrs-Replace 2028 | 2028 | 18186.3848
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 17206 | SM:Obsolete Instr-Replace 2028* | 2028 | 75777.4023
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 17208 | SM:Obsolete Elec-Replace 2028* | 2028 | 75777.4023
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 19388 | SCOR:525 UPS-Replace* | 2028 | 181865.3357
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 19389 | SCOR:810002 IDC-Replace | 2028 | 909327.6703
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 40007 | SCOR:60004 Oil Filtr-Replace | 2023 | 211351.5386
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 40008 | SCOR:65004 AUX Pump-Replace | 2023 | 23691.3173
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 100870 | SCOR:62211-PSV-010-Decrease Set Pressure | 2023 | 716122.6733
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 100969 | SCOR:65004 Forced Lube-Replace | 2023 | 37407.3431
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 101606 | SCOR:352 Gas Detectrs-Replace 2029 | 2029 | 18080.0847
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 101607 | SCOR:352 Gas Detectrs-Replace 2030 | 2030 | 18622.1922
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 101863 | SCOR:Obsolete Mech-Replace 2029* | 2029 | 130122.8947
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 101864 | SCOR:Obsolete Mech-Replace 2030* | 2030 | 134024.4583
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 101865 | SM:Obsolete Elec-Replace 2029* | 2029 | 75334.4805
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 101866 | SM:Obsolete Elec-Replace 2030* | 2030 | 77593.2856
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 101867 | SM:Obsolete Instr-Replace 2029* | 2029 | 75334.4805
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 101868 | SM:Obsolete Instr-Replace 2030* | 2030 | 77593.2856
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 102022 | SCHT:62001 Comp-Major O/H | 2025 | 419813.7836
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 102032 | SCOR:61009 Top End-O/H incl. Cam Upgrade | 2027 | 528052.255
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 102033 | SCOR:61011 Top End-O/H incl. Cam Upgrade | 2028 | 523552.1998
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 102034 | SCOR:61010 Top End-O/H incl. Cam Upgrade | 2027 | 528052.255
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 501399 | SCOR:541 MOP/OPP-Upgrade | 2024 | 713674.859
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 501402 | SCOR:TBD OPP-Upgrades | 2024 | 673035.4004
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 501524 | SSOM:K-801 Isolation Valves - Replace | 2023 | 733218.5898
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 502781 | SCOR:541 Drainage System-Upgrade | 2023 | 510236.1605
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734136 | SM:100MOV Yard Valve-Replace 2030* | 2030 | 554309.9949
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734137 | SM:100MOV Yard Valve-Replace 2031* | 2031 | 548032.2902
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734138 | SM:100MOV Yard Valve-Replace 2032* | 2032 | 532120.9995
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734319 | Methane Leak Remediation : Valve Replacement 2023* |  | 62345.5719
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734320 | Methane Leak Remediation : Valve Replacement 2024* |  | 64068.8428
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734321 | Methane Leak Remediation : Valve Replacement 2025* |  | 64586.7439
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734322 | Methane Leak Remediation : Valve Replacement 2026* |  | 65383.9513
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734323 | Methane Leak Remediation : Valve Replacement 2027* |  | 69480.5599
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734324 | Methane Leak Remediation : Valve Replacement 2028* |  | 68888.4473
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734325 | Methane Leak Remediation : Valve Replacement 2029* |  | 68485.7917
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734326 | Methane Leak Remediation : Valve Replacement 2030* |  | 70539.248
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734327 | Methane Leak Remediation : Valve Replacement 2031* |  | 69740.3727
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734328 | Methane Leak Remediation : Valve Replacement 2032* |  | 67715.5662
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734330 | SCOR:525 UPS-Replace* | 2032 | 178768.9322
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734331 | SCOR:HMI PCs-Replace* | 2031 | 90662.5403
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734332 | SCOR:Obsolete Mech-Replace 2031* | 2031 | 132506.5965
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734333 | SCOR:Obsolete Mech-Replace 2032* | 2032 | 128659.4674
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734334 | SM:Obsolete Elec-Replace 2031* | 2031 | 76714.5215
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734335 | SM:Obsolete Elec-Replace 2032* | 2032 | 74487.2311
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734336 | SM:Obsolete Instr-Replace 2031* | 2031 | 76714.5215
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734337 | SM:Obsolete Instr-Replace 2032* | 2032 | 74487.2311
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734338 | SM:SCADA-Annual Upgrade 2029* | 2029 | 75334.3161
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734339 | SM:SCADA-Annual Upgrade 2030* | 2030 | 77593.1164
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734340 | SM:SCADA-Annual Upgrade 2031* | 2031 | 76714.3541
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734341 | SM:SCADA-Annual Upgrade 2032* | 2032 | 74487.0686
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734342 | SM:FIMP Recommend'ns-Implement 2031* | 2031 | 69740.4285
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734343 | SM:FIMP Recommend'ns-Implement 2029* | 2029 | 68485.8465
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734344 | SM:FIMP Recommend'ns-Implement 2030* | 2030 | 70539.3044
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 734345 | SM:FIMP Recommend'ns-Implement 2032* | 2032 | 67715.6204
STO - EGD | 70 - Storage | Compression Stations | Fail | Dollar threshold | 736505 | SCOR: K711 MOD Hdr Valves-Replace | 2023 | 810492.4348
STO - EGD | 70 - Storage | Compression Stations | Fail | Timing | 12959 | SM:100MOD Hdr Valves-Replace* | 2023 | 2880365.4222
STO - EGD | 70 - Storage | Compression Stations | Fail | Timing | 12960 | SM:100MOD Hdr Valves-Replace* | 2025 | 1989271.7116
STO - EGD | 70 - Storage | Compression Stations | Pass |  | 5624 | SCOR:60004-Fdn Blk-Replace | 2023 | 3366660.883 | Issue/Concern: Due to the age of the compressor infrastructure, hours operating, and oil contamination, engine block foundations are deteriorating. Industry benchmarks suggest that reciprocating engine block foundations degrade in 25 years or less for engines that run 24/7. Excessive bearing deflections place cyclic stresses on the crankshaft of the unit, leading to increased frequency of bearing failure and increased potential for a crankshaft fatigue failure. Unit reliability will be diminished dramatically if repairs are not performed. Worst case consequence is unit unavailability during a design day. Compressor foundations have been considered in the Asset Health Review. Condition assessment is largely visual. The telltale sign of poor foundation condition is the existence of cracks on the surface of the foundation, with oil seeping out of the crack. Cracks typically extend to a depth that is consistent with the bottom of the unit's anchor bolts. Without remediation, failing foundations will allow unit settlement, creating a misalignment of bearings. Frequency of bearing failures increases reducing operation reliability. Collateral damage to the crankshaft is also common. Asset: Compressor foundations Related Programs: Not applicable | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - EGD | 70 - Storage | Compression Stations | Pass |  | 12884 | SCOR:60011-Fdn Blk-Replace | 2032 | 2992383.3731 | Issue/Concern: Due to the age of the compressor infrastructure, hours operating and oil contamination, engine block foundations are deteriorating. Industry benchmarks suggest that reciprocating engine block foundations degrade in 25 years or less for engines that run 24/7. Excessive bearing deflections place cyclic stresses on the crankshaft of the unit leading to increased frequency of bearing failure and increased potential for a crankshaft fatigue failure. Unit reliability will diminish dramatically if repairs are not performed. Worst case consequence is unit unavailability during a design day. Compressor foundations have been considered in the Asset Health Review. Condition assessment is largely visual. The telltale sign of poor foundation condition is the existence of cracks on the surface of the foundation, with oil seeping out of the crack. Cracks typically extend to a depth that is consistent with the bottom of the unit's anchor bolts. Without remediation, failing foundations will allow unit settlement, creating a misalignment of bearings. Frequency of bearing failures increases reducing operation reliability. Collateral damage to the crankshaft is also common. Asset: Compressor foundations. Related Program: Not applicable. | In Progress
STO - EGD | 70 - Storage | Compression Stations | Pass |  | 12961 | SM:100MOD Hdr Valves-Replace* | 2026 | 3020738.5483 | *Issue/Concern* Operations have identified compressor station yard isolation valves that to not provide sufficient seal quality that they could be trusted to provide isolation during normal maintenance activities or emergency situations. Valve condition - i.e. it's ability to perform it's intended function - is under investigation in the Asset Health Review. Condition assessment results are rudimentary. Leaking valve seals are not necessarily valves that leak to atmosphere or pose a loss of containment threat. The valves referenced in this business case are those that allow gas to flow, when in the closed position. These leaking valves pose: (i) a process safety threat; (ii) a loss of system performance by creating recycle loops; and (iii) decreased ability to provide a safe work environment for maintenance activities that require double lock and bleed. If valve condition is not maintained at a reasonable level, the ability to isolate assets during an emergency, will be compromised. Valves in question are sometimes used to separate piping with different MOPs. If these valves are allowed to leak, there is an increased threat of overpressuring lower MOP pipe as gas bleeds through the valve from higher MOP pipe. *Asset* ¼ Turn Isolation valves . There are dozens of these valves in service. *Related Program* Not Applicable | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Compression Stations | Pass |  | 100901 | Dawn to Corunna | 2023 | 165101439.9979 | Issue/Concern/Opportunity: EGI recognizes its obligation to meet the firm demands of its customers; and as a result, assets are continually evaluated to identify hazards and to assess risks in order to ensure that they remain reliable, suitable, and fit for continued service. To this end, an Asset Health Review (AHR) was performed in 2018 and updated in 2021 as part of EGI’s comprehensive Reliability, Availability and Maintainability (RAM) Study for the Corunna Compressor Station (CCS), which was completed by a consultant. The results of this study indicate that the health and maintainability of certain compressor units at the CCS are in decline. Reasons for this decline include, but are not limited to performance, functional issues with custom components (i.e., spare parts) and wear. As a result of these assessments, EGI has identified increasing obsolescence and reliability risks associated with certain CCS compressor units and is experiencing a need for increased maintenance and repair work to keep the units operational going forward. Further, as a result of the compressor units’ obsolescence and reliability issues, EGI has experienced continued and increasing compressor unit downtime and long lead repair time. This has created a need for increased maintenance and repair work performed by EGI personnel at the CCS. EGI has also undertaken comprehensive studies, including a site-wide quantitative risk assessment (QRA) to determine the severity of the increasing safety risks, and has determined that the current configuration of compressor units (which includes multiple compressor units in close proximity within a single building) results in an excessive level of process safety risk. Assets: Compressors K701, K702, K703, K705, K706, K707 and K708 Related Investments: 734634 - Dawn to Corunna (Dawn Tie-in) | Completed | Fail | A Leave to construct regulatory process has received OEB decision for approval of proposed project scope.
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 1918 | NPS 24 Mid Kimball Transmission Pipeline Retrofit |  | 799998.8494
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 1919 | NPS 20 South Mid Kimball Gathering Pipeline Retrofit |  | 1120343.0121
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 1920 | NPS 16 South Mid Kimball Gathering Pipeline Retrofit |  | 1024239.7479
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 1921 | 2024 Depth of Cover Mitigation Program* |  | 640688.479
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 1923 | 2025 Depth of Cover Mitigation Program* |  | 419554.8334
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 1924 | 2025 Dig Program S&T* |  | 775040.9266
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 6376 | LCRW:Wells-Upgrade | 2025 | 516693.9511
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8859 | PM:Wells-Acidize 2024* | 2024 | 317781.4602
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8860 | PM:Wells-Acidize 2026* | 2026 | 324304.3983
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8861 | PM:Wells-Acidize 2028* | 2028 | 341686.6988
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8971 | LM:Well Loops-Adjust* | 2023 | 88587.3219
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8972 | LM:Well Loops-Adjust* | 2024 | 91035.9313
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8973 | LM:Well Loops-Adjust* | 2025 | 91771.8211
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8974 | LM:Well Loops-Adjust* | 2026 | 92904.5794
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8975 | LM:Well Loops-Adjust* | 2027 | 98725.4834
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8976 | LM:Well Loops-Adjust* | 2028 | 97884.1459
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8991 | LM:Leaking Valves-Replace* | 2023 | 382801.7616
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8992 | LM:Leaking Valves-Replace* | 2024 | 197332.1383
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8993 | LM:Leaking Valves-Replace* | 2025 | 198927.2745
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8994 | LM:Leaking Valves-Replace* | 2026 | 201382.6745
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8995 | LM:Leaking Valves-Replace* | 2027 | 214000.2356
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 8997 | LM:Leaking Valves-Replace* | 2028 | 212176.528
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9184 | LM:MS UPS-Replace* | 2023 | 17144.9824
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9185 | LM:MS UPS-Replace* | 2024 | 17618.8805
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9186 | LM:MS UPS-Replace* | 2025 | 17761.3029
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9187 | LM:MS UPS-Replace* | 2026 | 17980.5343
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9188 | LM:MS UPS-Replace* | 2027 | 19107.0984
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9189 | LM:MS UPS-Replace* | 2028 | 18944.2679
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9545 | PM:Well Casing-Replace Program 2023* | 2023 | 263410.6648
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9546 | PM:Well Casing-Replace Program 2024* | 2024 | 270693.4235
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9547 | PM:Well Casing-Replace Program 2025* | 2025 | 272881.5764
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9548 | PM:Well Casing-Replace Program 2026* | 2026 | 276249.8094
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9549 | PM:Well Casing-Replace Program 2027* | 2027 | 293558.1447
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9550 | PM:Well Casing-Replace Program 2028* | 2028 | 291056.4456
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9583 | PM:Roads&Laneways-Improve* | 2023 | 82296.3045
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9584 | PM:Roads&Laneways-Improve* | 2024 | 84571.0262
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9585 | PM:Roads&Laneways-Improve* | 2025 | 85254.6569
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9586 | PM:Roads&Laneways-Improve* | 2026 | 86306.9726
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9587 | PM:Roads&Laneways-Improve* | 2027 | 91714.5058
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 9588 | PM:Roads&Laneways-Improve* | 2028 | 90932.9158
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 13046 | LSEC:TS22H G/L-Modify | 2024 | 962599.0804
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 13048 | LSEC:TS23H G/L-Modify | 2024 | 962599.0804
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 16808 | MM:ESD Bottles-Upgrade* | 2023 | 149629.3726
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 16809 | MM:Atm Liquids Tanks-Replace - 2023* | 2023 | 249382.3375
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 16810 | MM:Atm Liquids Tanks-Replace - 2024* | 2024 | 256275.4224
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 16811 | MM:Atm Liquids Tanks-Replace - 2025* | 2025 | 258347.0272
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 16812 | MM:Atm Liquids Tanks-Replace - 2026* | 2026 | 261535.8574
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 16823 | MM:Atm Liquids Tanks-Replace - 2027* | 2027 | 277922.295
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 16833 | PM:Well Tools-Purchase* | 2023 | 104740.5608
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 16834 | PM:Well Tools-Purchase* | 2025 | 108505.7297
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 16835 | LM:Lateral Separator-Build* | 2023 | 1184565.7665
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101184 | PM:Roads&Laneways-Improve* | 2029 | 90401.4095
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101185 | PM:Roads&Laneways-Improve* | 2030 | 93111.9766
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101902 | PM:Well Tools-Purchase* | 2027 | 116727.3406
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101903 | PM:Well Tools-Purchase* | 2029 | 115056.1301
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101904 | LM:Leaking Valves-Replace* | 2029 | 210936.3481
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101905 | LM:Leaking Valves-Replace* | 2030 | 217260.9967
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101907 | PM:Wells-Acidize 2023* | 2023 | 309234.0367
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101908 | PM:Wells-Acidize 2025* | 2025 | 320350.2497
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101909 | PM:Wells-Acidize 2027* | 2027 | 344623.5769
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101910 | PM:Wells-Acidize 2029* | 2029 | 339689.527
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101911 | PM:Wells-Acidize 2030* | 2030 | 349874.67
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101912 | LM:Well Loops-Adjust* | 2029 | 97312.0094
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101913 | LM:Well Loops-Adjust* | 2030 | 100229.7818
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101914 | PM:Roads&Laneways-Improve* | 2031 | 92057.4593
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101915 | PM:Roads&Laneways-Improve* | 2032 | 89384.7099
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101916 | PM:Well Casing-Replace Program 2029* | 2029 | 289355.2095
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 101917 | PM:Well Casing-Replace Program 2030* | 2030 | 298031.1443
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102418 | Rectifier Ground Bed Replacement Program* | 2021 | 1342470.1913
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102794 | 2026 Depth of Cover Mitigation Program* |  | 539417.5979
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102795 | 2027 Depth of Cover Mitigation Program* |  | 573214.6189
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102796 | 2028 Depth of Cover Mitigation Program* |  | 568329.6906
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102797 | 2029 Depth of Cover Mitigation Program* |  | 565007.7819
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102798 | 2030 Depth of Cover Mitigation Program* |  | 581948.7959
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735061 | PM:Well Casing-Replace Program 2031* | 2030 | 294655.8642
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735062 | PM:Well Casing-Replace Program 2032* | 2030 | 286100.9757
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735063 | PM:Wells-Acidize 2031* | 2031 | 345912.2485
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735064 | PM:Wells-Acidize 2032* | 2032 | 335869.2083
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735359 | PM:Well Tools-Purchase - 2031* | 2029 | 117163.8261
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735376 | 2031 Depth of Cover Mitigation Program* |  | 575358.0746
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735377 | 2032 Depth of Cover Mitigation Program* |  | 558653.421
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735399 | LM:MS UPS-Replace - 2029* | 2029 | 18833.5379
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735400 | LM:MS UPS-Replace - 2030* | 2030 | 19398.2368
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735401 | LM:MS UPS-Replace - 2031* | 2031 | 19178.5467
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735402 | LM:MS UPS-Replace - 2032* | 2032 | 18621.7265
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735992 | Bluewater A1 Well | 2023 | 1119731.7293
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 736101 | New Well Lateral/Crossover (Well Lifecycle Replacement)* | 2020 | 1312724.6167
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Timing | 1917 | 2023 Dig Program S&T* | 2023 | 2493822.8763
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Timing | 1922 | 2024 Dig Program S&T* | 2024 | 3331579.8245
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Fail | Timing | 736855 | 2025 S&T Pipelines Integrity Program* | 2025 | 3965626.0745
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 6377 | PCRW:Wells-Upgrade | 2023 | 12841156.7216 | Issue/Concern: Wells at Crowland are much older than other wells at EGI. Due to age, the wells were constructed to a production standard which would normally be retired after 10 years. Instead, the wells were converted to Storage service in the early 1970s and continue to operate ever since. Many wells have been relined, increasing the risk of leaks. Most wells possess only two casings; the current standard requires a minimum of three casings. The two-casing design at Crowland is comprised of an inner casing that runs from the surface to the reservoir (about 225 m) plus a surface casing that runs from the surface to a depth of about 20 m. Most wells do not have an intermediate casing with cement between the inner and intermediate casings; however, there is cement between the inner casing and the surrounding rock. This provides a poor barrier to gas flow should the inner casing fail. In addition, none of the wells at Crowland employ wellheads and master valves. Instead, the inner casing is simply connected to a flanged 1/4 turn valve without wing valves or wellhead vents. The surface casing is separated from the surface using cement. There are no casing vents and part of the inner casing (typically a length of 2 to 16 inches) is exposed at the surface. The lack of casing vents eliminates normal approaches to controlling a failed well. Vertilogs have been performed in the last 5 years, and indicated that the inner casing integrity is adequate, although 2 of 26 wells needed to be abandoned. Currently, there are 24 wells remaining. Bond logs have not been performed yet to determine the condition of cement at sulphur layers. Primary concerns are: (1) Code compliance of the wells and wellheads - Technically, these wells were constructed before CSA Z341 came into force and are grandfathered. However, a well failure would likely be viewed negatively by technical regulators. (2) Risk to employees and the public - In the event of a loss of containment, there are insufficient barriers to gas flow. Public risk also extends to possible sulphur contamination of well water at surface levels. In addition to the wells, much of the gathering system is as old as the wells. The gathering system is operating at <30% SMYS, which means they have not been considered for integrity inspections until recently and the gathering system pipe condition is unknown after 50 to 100 years of operation. Assets: Crowland wells and gathering system. Related Programs: This investment is under consideration in conjunction with other Crowland investments in the Distribution Station asset class and Compressor Station asset class. Issues related to the wells and gathering system should be considered together with the additional distribution station and compressor station issues/concerns. | Completed | Fail | Storage Pools & Well related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 13044 | PSEC:TS22H Well-Install | 2024 | 3182591.743 | Issue/Concern: Micro-annulus leaks have been occurring on wells that have been relined. Relining a well may be performed when the integrity of an existing casing is inadequate, and a smaller diameter casing is installed inside the original casing (concentrically). A recent rash of these relined wells has experienced leakage between the two casings. Concerns: 1. Localized leakage can be prevented by sealing the flow path at the wellhead (casing vent). This action causes pressure in the space between the two casings to achieve full reservoir pressure. 2. If the annulus space is allowed to be pressurized, there is the potential for a breach of the original casing; the original casings are known to have inadequate integrity. 3. A breach of the original casing could occur anywhere along the well string which is 2,000 ft long/deep. Leaking, unodourized gas could come to surface at unpredictable locations. About half of the relined wells operated by EGI are those which have not yet started to leak. Of the 20+ relined wells currently in-service at EGD Storage, 11 were recently found to be actively leaking and are being or have been abandoned. The mechanism by which a relined well becomes a leaking well has not been conclusively determined. The remaining (non-leaking) wells are expected to develop a leak in the short term. Once the wells are actively leaking, the problem becomes a compliance issue as follows: • CSA Z341.1-14 - 5.3.1 (a) The design of a well casing program shall provide control of pressures and fluids encountered by the well. • CSA Z341.1-14 - 5.3.6 (c) Well casings shall be set and cemented at sufficient depth to ensure isolation of storage zones. • OGSRA (O/Reg 245.97) - 17 (1) An operator of a well...shall provide casing and blowout prevention equipment and maintain it in such a condition that any oil, gas or water encountered can be effectively controlled. • OGSRA (O/Reg 245.97) - 17 (3) The operator shall ensure that the well does not flow uncontrolled. • O. Reg. 22/00, s. 6 (2) Well abandonments resulting from the Leaking and Relined well replacement programs will diminish the flow capacity of the associated reservoir. This performance degradation negatively impacts peak day deliverability. Reservoir performance deterioration, due to abandonment of relined wells, is currently unknown. Assets: Seckerton reservoir (Wells and Well Equipment asset program) and gathering system (Field Lines asset program). Related Programs: Installation of wells is performed by the reservoir group (Wells and Well Equipment asset program), installation of laterals is performed by the project execution group (Field Lines asset program). This separation is based on skill set and qualifications. There is a programmatic time dependence between the two asset programs. | Completed | Fail | Storage Pools & Well related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 13047 | PSEC:TS23H Well-Install | 2024 | 3182591.743 | Issue/Concern: Well abandonments resulting from abandoned wells since 2007 have already diminished the flow capacity of Seckerton. The proposed relined well replacement program will diminish the flow capacity of the Seckerton Reservoir even further. In addition, wells on the northern saddle of Seckerton (referred to as Seckerton North) are being shut in during low-end withdrawal in order to mitigate crude oil carryover. The North and South saddles have limited interconnected permeability, meaning that gas migrates very slowly between the two saddles. Shutting in wells has the effect of stranding an estimated 1.5 BCF for three weeks at the end of the withdrawal cycle. This performance problem negatively impacts peak day deliverability. Assets: Seckerton reservoir (Wells and Well Equipment asset program) and gathering system (Field Lines asset program). Related Programs: Installation of wells is performed by the Reservoir group (Wells and Well Equipment asset program), installation of laterals is performed by the project execution group (Field Lines asset program). This separation is based on skill set and qualifications. There is a programmatic time dependence between the two asset programs. | Completed | Fail | Storage Pools & Well related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 102767 | 2026 Dig Program S&T* |  | 1788904.9066 | 2026 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 102768 | 2027 Dig Program S&T* |  | 2167793.4678 | 2027 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 102769 | 2028 Dig Program S&T* |  | 2149319.5572 | 2028 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 102770 | 2029 Dig Program S&T* |  | 2136756.7024 | 2029 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 102771 | 2030 Dig Program S&T* |  | 2200824.5371 | 2030 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 102788 | 2026 S&T Pipelines Integrity Program* |  | 4014574.6075 | 2026 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2024 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 102789 | 2027 S&T Pipelines Integrity Program* |  | 4266106.3757 | 2027 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2024 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 102790 | 2028 S&T Pipelines Integrity Program* |  | 4229750.667 | 2028 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2024 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 102792 | 2029 S&T Pipelines Integrity Program* |  | 4205027.613 | 2029 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2024 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 102793 | 2030 S&T Pipelines Integrity Program* |  | 4331109.8262 | 2030 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2024 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 733835 | NPS 20 Seckerton Gathering Retrofit |  | 1870367.1572 | Issue/Concern: General concern: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent in-line inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, repair and replacement of pipeline segments with integrity issues that are identified through the inspections. Assets: NPS 20 Seckerton Gathering System Related Programs: Transmission Integrity Management Program (TIMP) | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735379 | 2031 Dig Program S&T* |  | 2175899.6274 | 2031 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735380 | 2032 Dig Program S&T* |  | 2112725.6649 | 2032 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735381 | 2031 S&T Pipelines Integrity Program* |  | 4282058.8822 | 2031 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2024 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735382 | 2032 S&T Pipelines Integrity Program* |  | 4157735.7637 | 2032 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2024 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735385 | MOP Verification Replacement Program 2025 - S&T Assets* | 2030 | 1291734.9294 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735386 | MOP Verification Replacement Program 2026 - S&T Assets* | 2031 | 2615358.1028 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735387 | MOP Verification Replacement Program 2027 - S&T Assets* | 2032 | 2779222.3946 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735388 | MOP Verification Replacement Program 2028 - S&T Assets* | 2033 | 2755537.8938 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735389 | MOP Verification Replacement Program 2029 - S&T Assets* | 2034 | 2739431.6697 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735390 | MOP Verification Replacement Program 2030 - S&T Assets* | 2035 | 2821569.9193 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735391 | MOP Verification Replacement Program 2031 - S&T Assets* | 2036 | 2789614.907 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735392 | MOP Verification Replacement Program 2032 - S&T Assets* | 2037 | 2708622.6473 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735770 | A1 observation program* |  | 7253620.3147 | Issue/Concern: Observation wells are required pursuant to Section 7.5 of CSA Z341 – Storage of hydrocarbons in underground formations . The observation well will monitor gas content and pressure in the underground storage area which will assist with the continued safe and reliable delivery of natural gas to our existing and future customers. Section 7.5: “Observation wells shall be incorporated into the storage facility and shall monitor pressures and the presence of hydrocarbons within the storage zone and associated permeable zones. The location and design of the observation well shall take into consideration: (a) locations within the storage zone that are suitable for monitoring reservoir pressures; (b) potential migratory paths from the reservoir to another formation; (c) fluid interface monitoring at the location of the spill point; (d) permeable zones and stratigraphic traps above the storage zone; and (e) low-permeability zones or formations adjacent to and in communication with" In addition, interpretations of the latest reservoir simulations indicate that the A-1 sucrosic dolomite may extend beyond the geographical edge of some DSAs. The DSA boundary protects the reef from any unwanted drilling by a third party. If the A-1 does, in fact, extend beyond the DSA boundary, a third party could receive permission to drill and if they penetrated the A-1 sucrosic they would be connected to the associated reef. EGD would then be forced to extend the DSA boundary and include, or buy out, the 3rd party. While the seismic provides a good interpretation of the A-1 it is not definitive and the only way to fully determine if the A-1 sucrosic is located beyond the boundary of the DSA is to drill a well. Mitigation of this risk will protect EGD's rights to the associated reservoir facility. Finally, the A1 Observation wells were originally proposed as a means to verify the integrity of the reservoir boundaries and demonstrate the relationship of low permeability zones to LUF. EGD receives rate recovery on LUF, and A1 zones were considered a potential means by which gas was leaking out of the reservoirs or becoming trapped, thereby creating LUF. The issue is that EGI must continue to investigate causes of LUF in order to argue for cost recovery from rates. This program drills one A1 well per year for 9 years. There are currently no A1 observation wells at the following pools. Airport Oil Springs East Mandaumin Oil City Bluewater Heritage Tipperary Black Creek Chatham D Wilkesport | Completed | Fail | See investment description, IRPAs not applicable
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735974 | Well Lifecycle Replacement* | 2028 | 13855731.5227 | Issue/Concern: This project is intended to recover lost design day deliverability due to well relines and abandonments. The deliverability of the new well is not intended to increase but maintain the deliverability. This project will drill one new vertical injection/withdrawal well and connect it to the existing gathering system of the desired pool. The new injection/withdrawal well will maintain the current split between the regulated/unregulated percentages of the pool. Asset: Wells Related Program: N/A | Completed | Fail | Storage Pools & Well related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - EGD | 70 - Storage | Transmission Pipe & Underground Storage | Pass |  | 735995 | Black Creek A1 Observation well | 2026 | 2701793.4551 | Issue/Concern/Opportunity: The storage pool pressure at the Black Creek pool is monitored by a Guelph formation observation well. This well's pressure is monitored and recorded continuously. and represents an inventory by the pools specific Pressure/inventory ratio. These pressures/inventories are compared to daily metered gas injections and withdrawals from the pool to perform an annual inventory verification. All discrepancies arising from this verification must be investigated. Assets: This project drills one A1 observation well in the Black Creek pool DSA. The well will be a 5 1/2" production casing, cemented at least 20m into the A1 formation and perforated in the A1 formation. Pressures from this well will be conveyed to the SCADA system for continuous monitoring and recording. These pressures will be assessed on an ongoing basis and during inventory verifications to confirm structural integrity of the Black Creek storage pool. Any increase in pressure would be proof of gas migration to the A1 formation. Related Program: Well Casing Inspection, Maintenance and Replacements | Completed | Fail | Storage Pools & Well related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Distribution Stations | Pass |  | 48993 | SANDWICH YARD DRAINAGE | 2023 | 1494636.3461 | Issue/Concern: Heater, Pressure Drop, Glycol, Pipe Integrity Assets: Sandwich Station Related Programs: Not applicable | Completed | Fail | Distribution station condition related, IRPA not applicable
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48211 | Waubuno Pool PLC Upgrade | 2023 | 54927.8857
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48217 | Tecumseh 2 PLC Upgrade | 2023 | 68005.9537
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48219 | TCPL Dawn PLC Upgrade | 2023 | 480525.5853
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48221 | Sombra/St. Clair Station PLC Upgrade | 2023 | 57917.1584
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48223 | Siemens Valve Controllers Replacement - Dawn I & Parkway D* |  | 604082.1899
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48224 | Sandwich Compressor Overhaul |  | 902032.9217
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48229 | Parkway A PLC Upgrade | 2023 | 903009.4591
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48237 | Lobo MCR PLC Upgrade | 2024 | 70488.9547
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48270 | Enniskillen Pool Siemens MCC replacement | 2024 | 74718.3463
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48271 | Enniskillen Pool PLC Upgrade | 2023 | 46209.1737
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48273 | Dow A Pool Siemens MCC replacement | 2023 | 94535.7489
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48274 | Dawn G Siemens MCC replacement | 2023 | 398009.2037
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48275 | Dawn E Siemens MCC replacement | 2023 | 539908.5842
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48278 | Dawn Aux 4 Siemens MCC replacement | 2024 | 118421.53
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48281 | Bright MCR PLC Upgrade | 2024 | 70488.9547
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48283 | Bluewater, Mandaumin, Airport Station PLC Upgrade | 2023 | 105371.8624
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48284 | Bickford Pool Siemens MCC replacement | 2026 | 81712.0656
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48639 | Parkway Main Control Building - Fire Ga | 2023 | 174374.2404
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48706 | Enniskillen Control Building | 2025 | 106818.171
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48712 | Large Diameter - Valve Replacement 2024 | 2024 | 577492.7414
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48723 | Obsolete MCC Replace 2030* | 2030 | 326807.1008
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 48726 | STO Paving replacements | 2026 | 569466.6331
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 49904 | Payne Compressor Stn Transformer | 2024 | 106004.9557
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 49908 | DAWN YARD PAVING and TRENWAY REPLACE | 2028 | 137617.437
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 49909 | 156 Control Room Building Replace | 2023 | 56369.4625
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 49953 | 167 Control Building | 2026 | 128129.9924
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 49959 | Bright B Power Turbine - Mid life Overhaul | 2025 | 470268.6773
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 100113 | Bright MCR MCC Replacement | 2023 | 161918.9375
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 100117 | Obsolete PLC Program Upgrade 2025* | 2025 | 340942.8539
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 100167 | Dawn G - Fire & Gas Detection Panel | 2023 | 91110.5406
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 100937 | Storage: Recip Compressor O/H* | 2031 | 531725.8517
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 100939 | OSE #2 Top End O/H | 2023 | 150210.9528
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 100940 | Edys Mills Top End O/H | 2026 | 166551.8658
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101242 | Lobo/Bright Compressor Station Lighting 2023 | 2023 | 49821.2115
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101243 | Lobo/Bright Compressor Station Lighting 2024 | 2024 | 51264.7316
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101244 | Lobo/Bright Compressor Station Lighting 2025 | 2025 | 51658.0082
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101245 | Lobo/Bright Compressor Station Lighting 2026 | 2026 | 52128.9095
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101246 | Lobo/Bright Compressor Station Lighting 2027 | 2027 | 55509.7183
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101247 | Lobo/Bright Compressor Station Lighting 2028 | 2028 | 55046.9968
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101248 | Lobo/Bright Compressor Station Lighting 2029 | 2029 | 54652.8482
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101249 | Lobo/Bright Compressor Station Lighting 2030* | 2030 | 56589.9742
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101257 | Bright A Plant air compressors | 2024 | 275547.9323
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101259 | Bright Ring Road Paving |  | 324249.4273
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101306 | Parkway West Perimeter Security Path |  | 311382.5721
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101308 | Parkway West Storage Quonset Hut |  | 180601.8918
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101310 | Parkway/Hagar Compressor Building Lighting 2023 | 2023 | 49821.2115
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101312 | Parkway/Hagar Compressor Building Lighting 2024 | 2024 | 51264.7316
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101313 | Parkway/Hagar Compressor Building Lighting 2025 | 2025 | 51658.0082
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101314 | Parkway/Hagar Compressor Building Lighting 2026 | 2026 | 52128.9095
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101315 | Parkway/Hagar Compressor Building Lighting 2027 | 2027 | 55509.7183
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101316 | Parkway/Hagar Compressor Building Lighting 2028 | 2028 | 55046.9968
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101317 | Parkway/Hagar Compressor Building Lighting 2029 | 2029 | 54652.8482
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101318 | Parkway/Hagar Compressor Building Lighting 2030 | 2030 | 56589.9742
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101571 | Obsolete PLC Program Upgrade 2026* | 2026 | 417031.2759
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101572 | Obsolete PLC Program Upgrade 2027* | 2027 | 444077.746
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101573 | Obsolete PLC Program Upgrade 2028* | 2028 | 440375.9745
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101574 | Obsolete PLC Program Upgrade 2029* | 2029 | 437222.7858
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101575 | Obsolete PLC Program Upgrade 2030* | 2030 | 452719.7933
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101576 | Siemens Valve Controllers Replacement - Lobo D & Dawn H* |  | 1247938.2196
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101845 | Dawn Safety & Security Upgrades 2023* |  | 131362.3927
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101846 | Dawn Safety & Security Upgrades 2024* |  | 135168.4874
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101847 | Dawn Safety & Security Upgrades 2025* |  | 136205.4303
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101848 | Dawn Safety & Security Upgrades 2026* |  | 137446.9924
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101849 | Dawn Safety & Security Upgrades 2027* |  | 146361.0864
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101850 | Dawn Safety & Security Upgrades 2028* |  | 145141.0403
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101851 | Dawn Safety & Security Upgrades 2029* |  | 144101.7986
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101852 | Dawn Safety & Security Upgrades 2030* |  | 149209.3701
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101855 | TCO Safety & Security Upgrades 2023* |  | 78184.4273
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101856 | TCO Safety & Security Upgrades 2024* |  | 80449.7433
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101857 | TCO Safety & Security Upgrades 2025* |  | 81066.9122
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101858 | TCO Safety & Security Upgrades 2026* |  | 81805.8977
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101859 | TCO Safety & Security Upgrades 2027* |  | 87111.4009
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101860 | TCO Safety & Security Upgrades 2028* |  | 86385.2521
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101861 | TCO Safety & Security Upgrades 2029* |  | 85766.7147
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101862 | TCO Safety & Security Upgrades 2030* |  | 88806.6464
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101871 | Obsolete Electrical-Replace 2023* | 2023 | 102756.2488
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101872 | Obsolete Electrical-Replace 2024* | 2024 | 105733.5089
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101873 | Obsolete Electrical-Replace 2025* | 2025 | 106544.6418
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101874 | Obsolete Electrical-Replace 2026* | 2026 | 162902.8422
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101875 | Obsolete Electrical-Replace 2027* | 2027 | 173467.8696
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101876 | Obsolete Electrical-Replace 2028* | 2028 | 172021.865
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101877 | Obsolete Electrical-Replace 2029* | 2029 | 170790.1507
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101878 | Obsolete Electrical-Replace 2030* | 2030 | 176843.6692
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101880 | Obsolete Instrumentation-Replace 2023* | 2023 | 102756.2488
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101881 | Obsolete Instrumentation-Replace 2024* | 2024 | 105733.5089
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101882 | Obsolete Instrumentation-Replace 2025* | 2025 | 106544.6418
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101883 | Obsolete Instrumentation-Replace 2026* | 2026 | 162902.8422
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101884 | Obsolete Instrumentation-Replace 2031* | 2031 | 174909.8196
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101885 | Obsolete Instrumentation-Replace 2027* | 2027 | 173467.8696
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101886 | Obsolete Instrumentation-Replace 2028* | 2028 | 172021.865
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101887 | Obsolete Instrumentation-Replace 2029* | 2029 | 170790.1507
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101888 | Obsolete Instrumentation-Replace 2030* | 2030 | 176843.6692
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101890 | Dawn Compressor Building Lighting 2023 | 2023 | 156936.8163
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101892 | Dawn Compressor Building Lighting 2024 | 2024 | 161483.9045
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101893 | Dawn Compressor Building Lighting 2025 | 2025 | 162722.7257
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101894 | Dawn Compressor Building Lighting 2026 | 2026 | 164206.0649
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101895 | Dawn Compressor Building Lighting 2027 | 2027 | 174855.6125
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101896 | Dawn Compressor Building Lighting 2028 | 2028 | 173398.04
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101897 | Dawn Compressor Building Lighting 2029 | 2029 | 172156.4719
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101898 | Dawn Compressor Building Lighting 2030 | 2030 | 178258.4186
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101922 | High Performance Coating Program 2023* | 2022 | 697496.9615
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101924 | High Performance Coating Program 2024* | 2023 | 717706.2423
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101925 | High Performance Coating Program 2025* | 2025 | 723212.1143
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101927 | High Performance Coating Program 2026* | 2026 | 729804.7329
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101928 | High Performance Coating Program 2027* | 2027 | 777136.0556
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101930 | High Performance Coating Program 2028* | 2028 | 770657.9554
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101931 | High Performance Coating Program 2029* | 2029 | 765139.8752
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101933 | High Performance Coating Program 2030* | 2030 | 792259.6382
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101955 | OSE #1 Top End O/H | 2028 | 165966.6954
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101960 | Dawn Aux 4-2 Gen Top End O/H | 2025 | 195267.2709
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101961 | Dawn Aux 3 Gen Top End O/H | 2023 | 188324.1796
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101962 | OSE #1 Bottom End O/H | 2028 | 138305.5795
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101963 | OSE #2 Bottom End O/H | 2023 | 125175.794
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 101980 | OSE #1 Compressor Crankcase Rebuild |  | 68808.746
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 102344 | Dawn Aux 4-1 Gen Turbo Rebuild | 2025 | 21696.3634
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 102348 | Edys Mills Engine Turbo Rebuild | 2025 | 18338.5929
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 102355 | OSE #2 Compressor Crankcase Rebuild |  | 62276.5144
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 102356 | Edys Mills Compressor Crankcase Rebuild |  | 65161.1369
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 102731 | STO - UPS Battery replacements 2023 | 2023 | 149463.6346
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 102732 | STO - UPS Battery replacements 2024 | 2024 | 153794.1948
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 102733 | STO - UPS Battery replacements 2025 | 2025 | 154974.0245
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 103156 | FIMP Recommend'ns-Implement* | 2022 | 934147.7163
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 103157 | FIMP Recommend'ns-Implement* | 2024 | 128161.829
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 103159 | FIMP Recommend'ns-Implement* | 2025 | 129145.0204
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 501141 | Lobo C GGLO Scheduling Valve & Controller replacement | 2023 | 324460.6401
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 501148 | Dawn H GGLO Sheculing valve and controller replacement | 2023 | 353837.8774
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 501149 | Bright A1 GGLO valve & Controller replacement | 2023 | 276507.724
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 501150 | Bright C GGLO scheduling valve and Controller replacement | 2022 | 89678.1808
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 501151 | Bright A2 GGLO scheduling valve & controller replacement | 2025 | 286701.9453
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 501152 | Parkway C GGLO scheduling valve & controller replacement | 2023 | 66013.1053
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 501153 | Parkway B GGLO scheduling valve & controller replacement | 2025 | 362124.2556
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 503219 | Lobo B Power Gas Dryer Upgrade | 2023 | 137008.3317
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 503237 | Lobo North Yard Drip Tank Replacement | 2023 | 51066.7418
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 733364 | Dawn Salt Building - Replace |  | 373659.0865
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 733980 | Parkway Leaking Valves - Replace - P611 (plug 3”) & P603 (plug 8”) | 2023 | 622765.1442
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734139 | Methane Leak Remediation : Valve Replacement 2023* |  | 249106.0577
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734140 | Methane Leak Remediation : Valve Replacement 2024* |  | 256323.658
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734141 | Methane Leak Remediation : Valve Replacement 2025* |  | 258290.0408
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734142 | Methane Leak Remediation : Valve Replacement 2026* |  | 260644.5475
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734143 | Methane Leak Remediation : Valve Replacement 2027* |  | 277548.5913
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734144 | Methane Leak Remediation : Valve Replacement 2028* |  | 275234.9841
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734145 | Methane Leak Remediation : Valve Replacement 2029* |  | 273264.2411
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734146 | Methane Leak Remediation : Valve Replacement 2030* |  | 282949.8708
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734147 | Methane Leak Remediation : Valve Replacement 2031* |  | 279855.7114
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734148 | Methane Leak Remediation : Valve Replacement 2032* |  | 271598.2547
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734150 | Large Diameter - Valve Replacement 2025* | 2025 | 968587.6531
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734151 | Large Diameter - Valve Replacement 2027* | 2027 | 1040807.2173
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734152 | Large Diameter - Valve Replacement 2029* | 2029 | 1024740.9042
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734153 | Large Diameter - Valve Replacement 2030* | 2030 | 1061062.0155
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734154 | Large Diameter - Valve Replacement 2031* | 2031 | 1049458.9179
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734155 | Large Diameter - Valve Replacement 2032* | 2032 | 1018493.4551
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734156 | Dawn Safety & Security Upgrades 2031* |  | 147577.7116
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734158 | Dawn Safety & Security Upgrades 2032* |  | 143223.2656
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734161 | TCO Safety & Security Upgrades 2031* |  | 87835.5136
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734162 | TCO Safety & Security Upgrades 2032* |  | 85243.8282
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734196 | Obsolete Electrical-Replace 2031* | 2031 | 174909.8196
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734197 | Obsolete Electrical-Replace 2032* | 2032 | 169748.9092
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734198 | Obsolete Instrumentation-Replace 2032* | 2032 | 169748.9092
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734199 | Obsolete PLC Program Upgrade 2031* | 2031 | 447769.1383
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734200 | Obsolete PLC Program Upgrade 2032* | 2032 | 434557.2075
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734203 | Obsolete MCC Replace 2031* | 2038 | 323233.3467
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734204 | Obsolete MCC Replace 2032* | 2039 | 313695.9842
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734205 | STO Obsolete Mechanical - Replace 2023* | 2023 | 164409.9981
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734206 | STO Obsolete Mechanical - Replace 2024* | 2024 | 169173.6143
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734207 | STO Obsolete Mechanical - Replace 2025* | 2025 | 170471.4269
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734208 | STO Obsolete Mechanical - Replace 2026* | 2026 | 172025.4013
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734209 | STO Obsolete Mechanical - Replace 2027* | 2027 | 183182.0702
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734210 | STO Obsolete Mechanical - Replace 2028* | 2028 | 181655.0895
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734211 | STO Obsolete Mechanical - Replace 2029* | 2029 | 180354.3991
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734212 | STO Obsolete Mechanical - Replace 2030* | 2030 | 186746.9147
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734213 | STO Obsolete Mechanical - Replace 2031* | 2031 | 184704.7695
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734214 | STO Obsolete Mechanical - Replace 2032* | 2032 | 179254.8481
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734215 | TCO Obsolete Mechanical - Replace 2023* | 2023 | 217967.8005
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734216 | TCO Obsolete Mechanical - Replace 2024* | 2024 | 224283.2007
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734217 | TCO Obsolete Mechanical - Replace 2025* | 2025 | 226003.7857
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734219 | TCO Obsolete Mechanical - Replace 2026* | 2026 | 228063.979
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734220 | TCO Obsolete Mechanical - Replace 2027* | 2027 | 242855.0174
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734221 | TCO Obsolete Mechanical - Replace 2028* | 2028 | 240830.611
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734222 | TCO Obsolete Mechanical - Replace 2029* | 2029 | 239106.211
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734223 | TCO Obsolete Mechanical - Replace 2030* | 2030 | 247581.1369
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734224 | TCO Obsolete Mechanical - Replace 2031* | 2031 | 244873.7475
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734225 | TCO Obsolete Mechanical - Replace 2032* | 2032 | 237648.4729
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734236 | Parkway Ultrasonic Meter Upgrades 2023* |  | 106294.4516
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734237 | Parkway Ultrasonic Meter Upgrades 2024* |  | 109374.2276
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734274 | High Performance Coating Program 2031* | 2030 | 783595.992
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734275 | High Performance Coating Program 2032* | 2032 | 760475.1132
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734347 | STO - UPS Battery replacements 2026 | 2026 | 156386.7285
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734348 | STO - UPS Battery replacements 2027 | 2027 | 166529.1548
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734349 | STO - UPS Battery replacements 2028 | 2028 | 165140.9904
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734350 | STO - UPS Battery replacements 2029 | 2029 | 163958.5447
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734351 | STO - UPS Battery replacements 2030 | 2030 | 169769.9225
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734352 | STO - UPS Battery replacements 2031 | 2031 | 167913.4269
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 734353 | STO - UPS Battery replacements 2032 | 2032 | 162958.9528
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 735627 | Bright A1 Scrubber Replacement | 2024 | 1268802.107
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 735656 | Parkway East Generator Control Upgrade | 2023 | 1245530.2884
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 735978 | STO Moisture Analyzer Upgrade 2023* |  | 74731.8173
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736014 | STO Moisture Analyzer Upgrade 2024* |  | 76897.0974
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736015 | STO Moisture Analyzer Upgrade 2025* |  | 77487.0122
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736016 | STO Moisture Analyzer Upgrade 2026* |  | 78193.3642
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736017 | STO Moisture Analyzer Upgrade 2027* |  | 83264.5774
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736018 | STO Moisture Analyzer Upgrade 2028* |  | 82570.4952
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736019 | STO Moisture Analyzer Upgrade 2029* |  | 81979.2723
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736021 | STO Moisture Analyzer Upgrade 2030* |  | 84884.9612
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736022 | STO Moisture Analyzer Upgrade 2031* |  | 83956.7134
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736023 | STO Moisture Analyzer Upgrade 2032* |  | 81479.4764
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736182 | Lobo C Siemens Valve Controllers Replacement | 2023 | 105870.0745
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736274 | Dawn Fire Pump 1 | 2023 | 940375.3678
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736276 | Large Diameter - Valve Replacement 2026* | 2026 | 977417.053
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736277 | Large Diameter - Valve Replacement 2028* | 2028 | 1032131.1902
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736325 | Parkway C Siemens Valve Controllers Replacement | 2023 | 105870.0745
STO - UG | Div_53 - Union South Storage | Compression Stations | Fail | Dollar threshold | 736922 | Dawn Fire Pond Weir | 2023 | 62276.5144
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 48231 | Parkway A Gas Generator(38148) End-of-Life Overhaul | 2027 | 2886505.3493 | Issue/Concern/Opportunity: The consequence of compressor failure is dominated by gas cost impacts to customers. The compressor package is comprised of a gas turbine engine driver, compressor, power turbine and ancillary equipment such as lube oil, fuel supply, and electronic control systems, which are required for the compressor to operate. The gas turbine engine is very complex and carries the greatest failure risk of all of the compressor package components. By continuing to comply with original equipment manufacturer (OEM) recommended Preventive Maintenance (PM) schedules and overhauls, compressor reliability risks are controlled to moderate levels. In the case of performing regular OEM prescribed overhauls, the risk of unit failure is proposed as a sawtooth function, whereby risk increases gradually over the recommended interval between overhauls and then drops suddenly after an overhaul. Critical internal wear components are on a path to failure and generally in sync with operating hours. If the operating hours are extended too far, the resulting additional operational stress on internal components, such as high temperature coatings and bearings, will increase the component scrap rate when performing the overhaul. This will add significant (10 to 20% or more) cost to the base overhaul and increases the risk of a random failure leading to system unreliability and further cost increases. Justification: Potential for unexpected or catastrophic failure if timing is extended. Assets: Avon serial 38148 Related Investments: Not applicable. | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 48240 | Lobo A1 Gas Generator (38425) End-of-Life Overhaul | 2025 | 2686216.4246 | Issue/Concern/Opportunity: The consequence of compressor failure is dominated by gas cost impacts to customers. The compressor package is comprised of a gas turbine engine driver, compressor, power turbine and ancillary equipment such as lube oil, fuel supply, and electronic control systems, which are required for the compressor to operate. The gas turbine engine is very complex and carries the greatest failure risk of all of the compressor package components. By continuing to comply with original equipment manufacturer (OEM) recommended Preventive Maintenance (PM) schedules and overhauls, compressor reliability risks are controlled to moderate levels. In the case of performing regular OEM prescribed overhauls, the risk of unit failure is proposed as a sawtooth function, whereby risk increases gradually over the recommended interval between overhauls and then drops suddenly after an overhaul. Critical internal wear components are on a path to failure and generally in sync with operating hours. If the operating hours are extended too far, the resulting additional operational stress on internal components, such as high temperature coatings and bearings, will increase the component scrap rate when performing the overhaul. This will add significant (10 to 20% or more) cost to the base overhaul and increases the risk of a random failure leading to system unreliability and further cost increases. Justification: Potential for unexpected or catastrophic failure if timing is extended. Asset: Avon serial 38425 Related Investments: Not applicable. | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 48715 | Dawn C Compression Lifecycle | 2026 | 163382650.0748 | Issue/Concern: Dawn C Plant is one of the nine centrifugal compressors located at the Dawn Compressor Station. It is primarily used to lift from lower storage pressure levels, experienced later in the operations season, to intermediate pressure levels. The intermediate pressure level is typically elevated further in pressure by another compressor to reach the desired Dawn outlet pressure. Dawn Plant C and Plant D have a suction pressure rating of 195 psig, the lowest rating of the compressor fleet at Dawn. Considering the other compressors at Dawn have a 225 psig minimum inlet rating, Dawn Plants C and D become very critical when pool storage levels fall below 225 psig, as they typically do late in the operational season. Overall, compression can pose a very large consequence of failure as compressors are integral assets required to achieve the Dawn to Parkway Transmission System deliverability requirements throughout the year. The consequence of compressor failure is dominated by gas cost impacts to customers. Transmission system consequences associated with failure of a single compressor are heavily influenced by the time of year, weather severity and time to mitigate the failure. Siemens, the original equipment manufacturer (OEM) of the Dawn C compressor, has indicated that 40 years is the typical timeframe for supporting the supply of engine parts required to recover from a critical engine failure or to complete recommended overhauls. Dawn Plant C was installed in 1984, which indicates that the RB211- 24A engine in Plant C is reaching end of life. Justification: By continuing to comply with OEM-recommended Preventive Maintenance (PM) schedules and overhauls, compressor reliability risk is controlled to moderate levels but risk increases gradually over the 25,000-hour recommended interval between overhauls. Availability of parts is essential to repair internal engine failures and complete overhauls. Notably, the RB211-24A in Plant C has non-standard dimensions and cannot be retrofitted with more modern editions of the RB211 without significant plant retrofits. Similar to the 40-year old Dawn Plant B, which was replaced and retired in 2017 due to the risks associated with discontinued OEM support of critical engine parts, it is expected that Dawn Plant C will be exposed to a similar level of risk as the global inventory of spare components diminishes. Assets: Dawn Plant C Related Programs: Not applicable. | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 48732 | Waubuno Compression Lifecycle | 2025 | 20113718.9466 | Issue/Concern/Opportunity: The Waubuno compressor elevates available pipeline pressure to the Waubuno Pool Maximum Operating Pressure (MOP). Compression increases the working inventory value of the pool by approximately3.5 PJ on top of what the pipeline alone can achieve. The compressor is operated approximately 45 days per year in late summer to early fall to top off the pool. The consequence of compressor failure is dominated by customer impact. Risk associated with failure of the Waubuno compressor is heavily influenced by the level of the pool at which the failure occurs and time to mitigate the failure. The Joy Compressor (manufactured in 1985) was a used compressor package and installed at Waubuno in 1988. The Joy Compressor Company changed ownership approximately 20 years ago whereupon original equipment manufacturer (OEM) support for the compressor was discontinued. Although normal wear components are still available in the marketplace, replacement major compressor items such as cylinders, crankshafts, and rods, etc., required to support a critical failure are no longer available. In the event of a critical failure, sourcing used parts (which are rare) or aftermarket custom machining services would be the only options for repair. This was the case in 2007 when a discharge valve seat failed, resulting in catastrophic damage to cylinder 611. An extensive search across the used parts dealers was required to secure a viable used cylinder head. Other internal damage was repaired through custom machining services. Justification: In the event of a future failure, if usable parts or custom machining are not available, the two options would be custom-designed aftermarket castings (if possible) or replacement of the entire compressor. However, both options would render the compressor out of service for at least one operational season. Assets: Waubuno Compressor Related Programs: N/A | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 48753 | Parkway C Gas Generator Midlife Overhaul | 2026 | 4039990.4335 | Issue/Concern/Opportunity: The consequence of compressor failure is dominated by gas cost impacts to customers. The compressor package is comprised of a gas turbine engine driver, compressor, power turbine and ancillary equipment such as lube oil, fuel supply, and electronic control systems, which are required for the compressor to operate. The gas turbine engine is very complex and carries the greatest failure risk of all of the compressor package components. By continuing to comply with original equipment manufacturer (OEM) recommended Preventive Maintenance (PM) schedules and overhauls, compressor reliability risks are controlled to moderate levels. In the case of performing regular OEM prescribed overhauls, the risk of unit failure is proposed as a sawtooth function, whereby risk increases gradually over the recommended interval between overhauls and then drops suddenly after an overhaul. Critical internal wear components are on a path to failure and generally in sync with operating hours. If the operating hours are extended too far, the resulting additional operational stress on internal components, such as high temperature coatings and bearings, will increase the component scrap rate when performing the overhaul. This will add significant (10 to 20% or more) cost to the base overhaul and increases the risk of a random failure leading to system unreliability and further cost increases. Assets: Related Investments: | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 49954 | Avon 1534 Gas Generator (37433)End-of-Life Overhaul | 2026 | 2710703.2936 | Issue/Concern/Opportunity: The consequence of compressor failure is dominated by gas cost impacts to customers. The compressor package is comprised of a gas turbine engine driver, compressor, power turbine and ancillary equipment such as lube oil, fuel supply, and electronic control systems, which are required for the compressor to operate. The gas turbine engine is very complex and carries the greatest failure risk of all of the compressor package components. By continuing to comply with original equipment manufacturer (OEM) recommended Preventive Maintenance (PM) schedules and overhauls, compressor reliability risks are controlled to moderate levels. In the case of performing regular OEM prescribed overhauls, the risk of unit failure is proposed as a sawtooth function, whereby risk increases gradually over the recommended interval between overhauls and then drops suddenly after an overhaul. Critical internal wear components are on a path to failure and generally in sync with operating hours. If the operating hours are extended too far, the resulting additional operational stress on internal components, such as high temperature coatings and bearings, will increase the component scrap rate when performing the overhaul. This will add significant (10 to 20% or more) cost to the base overhaul and increases the risk of a random failure leading to system unreliability and further cost increases. Justification: Extension of interval can result in unexpected or catastrophic failure Asset: 37433 Related Investments: Not applicable. | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 49956 | Bright A1 Gas Generator - Mid life Overhaul | 2028 | 5367082.1891 | Issue/Concern/Opportunity: The consequence of compressor failure is dominated by gas cost impacts to customers. The compressor package is comprised of a gas turbine engine driver, compressor, power turbine and ancillary equipment such as lube oil, fuel supply, and electronic control systems, which are required for the compressor to operate. The gas turbine engine is very complex and carries the greatest failure risk of all of the compressor package components. By continuing to comply with original equipment manufacturer (OEM) recommended Preventive Maintenance (PM) schedules and overhauls, compressor reliability risks are controlled to moderate levels. In the case of performing regular OEM prescribed overhauls, the risk of unit failure is proposed as a sawtooth function, whereby risk increases gradually over the recommended interval between overhauls and then drops suddenly after an overhaul. Critical internal wear components are on a path to failure and generally in sync with operating hours. If the operating hours are extended too far, the resulting additional operational stress on internal components, such as high temperature coatings and bearings, will increase the component scrap rate when performing the overhaul. This will add significant (10 to 20% or more) cost to the base overhaul and increases the risk of a random failure leading to system unreliability and further cost increases. Justification: Extension of interval can result in unexpected or catastrophic failure. Assets: RB211-G DLE 1790-863 Related Investments: Not applicable. | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 49958 | Bright B Gas Generator End-of-Life Overhaul | 2025 | 4003495.6328 | Issue/Concern/Opportunity: The consequence of compressor failure is dominated by gas cost impacts to customers. The compressor package is comprised of a gas turbine engine driver, compressor, power turbine and ancillary equipment such as lube oil, fuel supply, and electronic control systems, which are required for the compressor to operate. The gas turbine engine is very complex and carries the greatest failure risk of all of the compressor package components. By continuing to comply with original equipment manufacturer (OEM) recommended Preventive Maintenance (PM) schedules and overhauls, compressor reliability risks are controlled to moderate levels. In the case of performing regular OEM prescribed overhauls, the risk of unit failure is proposed as a sawtooth function, whereby risk increases gradually over the recommended interval between overhauls and then drops suddenly after an overhaul. Critical internal wear components are on a path to failure and generally in sync with operating hours. If the operating hours are extended too far, the resulting additional operational stress on internal components, such as high temperature coatings and bearings, will increase the component scrap rate when performing the overhaul. This will add significant (10 to 20% or more) cost to the base overhaul and increases the risk of a random failure leading to system unreliability and further cost increases. Justification: Extension of interval can result in unexpected or catastrophic failure. Assets: Bright B RB211-24C Related Investments: Not applicable. | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 49965 | Dawn F2 Gas Producer Overhaul | 2025 | 2149799.6678 | Issue/Concern/Opportunity: The consequence of compressor failure is dominated by gas cost impacts to customers. The compressor package is comprised of a gas turbine engine driver, compressor, power turbine and ancillary equipment such as lube oil, fuel supply, and electronic control systems, which are required for the compressor to operate. The gas turbine engine is very complex and carries the greatest failure risk of all of the compressor package components. By continuing to comply with original equipment manufacturer (OEM) recommended Preventive Maintenance (PM) schedules and overhauls, compressor reliability risks are controlled to moderate levels. In the case of performing regular OEM prescribed overhauls, the risk of unit failure is proposed as a saw tooth function, whereby risk increases gradually over the recommended interval between overhauls and then drops suddenly after an overhaul. Critical internal wear components are on a path to failure and generally in sync with operating hours. If the operating hours are extended too far, the resulting additional operational stress on internal components, such as high temperature coatings and bearings, will increase the component scrap rate when performing the overhaul. This will add significant (10 to 20 per cent or more) cost to the base overhaul and increases the risk of a random failure leading to system unreliability and further cost increases. Justification: Extension of interval can result in unexpected or catastrophic failure Asset: Taurus 70- TC06299/OHC15-B3953 Related Investments: Not applicable. | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 100948 | Dawn: 5985 CV & Piping - Improvements | 2023 | 2327024.2378 | Issue/Concern/Opportunity: Flow control to and from the Dawn 5985 pool consists of a high-flow and low-flow control valve run. Flow dynamic of natural gas out of this critical supply high deliverability pool into the Dawn Yard has changed over the years such that the flow regime during normal non-peak day operations falls greater than the capability of the low-flow control valve run but at the very low end of the large control valve flow run. The high-flow control valve is an older style ball Fisher type valve which does not work efficiently at low flows. Extreme noise is created, over the 100 dB level, resulting in high cycle vibration of the valve internals leading to premature failure. A failure occurred in 2019 whereupon a clanging noise was being produced. The valves were removed and examined by Fisher. The large diameter valve was found to be excessively worn. Fisher rebuilt the large diameter valve after which it was reinstalled in order to place the 5985 pool back in service. Fisher’s recommendation is that EGI avoids operating the large diameter valve under these conditions. Assets: Control valves (CV 12 and CV 20) Related Investments: Not applicable. | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 733780 | Dawn D Gas Generator - Mid life Overhaul | 2024 | 2772130.108 | Issue/Concern/Opportunity: The consequence of compressor failure is dominated by gas cost impacts to customers. The compressor package is comprised of a gas turbine engine driver, compressor, power turbine and ancillary equipment such as lube oil, fuel supply, and electronic control systems, which are required for the compressor to operate. The gas turbine engine is very complex and carries the greatest failure risk of all of the compressor package components. By continuing to comply with original equipment manufacturer (OEM) recommended Preventive Maintenance (PM) schedules and overhauls, compressor reliability risks are controlled to moderate levels. In the case of performing regular OEM prescribed overhauls, the risk of unit failure is proposed as a sawtooth function, whereby risk increases gradually over the recommended interval between overhauls and then drops suddenly after an overhaul. Critical internal wear components are on a path to failure and generally in sync with operating hours. If the operating hours are extended too far, the resulting additional operational stress on internal components, such as high temperature coatings and bearings, will increase the component scrap rate when performing the overhaul. This will add significant (10 to 20% or more) cost to the base overhaul and increases the risk of a random failure leading to system unreliability and further cost increases. Justification: Extension of interval can result in unexpected or catastrophic failure. Assets: RB211-G DLE 1790-864 Related Investments: Not applicable. | Completed | Fail | Compression Station related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 734634 | Dawn to Corunna (Dawn Tie-in) | 2023 | 47886298.9165 | Issue/Concern/Opportunity: EGI recognizes its obligation to meet the firm demands of its customers; and as a result, assets are continually evaluated to identify hazards and to assess risks in order to ensure that they remain reliable, suitable, and fit for continued service. To this end, an Asset Health Review (AHR) was performed in 2018 and updated in 2021 as part of the Company’s comprehensive Reliability, Availability and Maintainability (RAM) Study for the Corunna Compressor Station (CCS), which was completed by a consultant. The results of this study indicate that the health and maintainability of certain compressor units at the CCS are in decline. Reasons for this decline include, but are not limited to performance, functional issues with custom components (i.e., spare parts), and wear. As a result of these assessments, the Company has identified serious and increasing obsolescence and reliability risks associated with certain CCS compressor units and is experiencing a need for increased maintenance and repair work to keep the units operational going forward. Further, as a result of the compressor units’ obsolescence and reliability issues, the Company has experienced continued and increasing compressor unit downtime and long lead repair time. This has created a need for increased maintenance and repair work performed by EGI personnel at the CCS. EGI has also undertaken comprehensive studies, including a site-wide quantitative risk assessment (QRA) to determine the severity of the increasing safety risks, and has determined that the current configuration of compressor units (which includes multiple compressor units in close proximity within a single building), results in an excessive level of process safety risk. Assets: Compressors K701, K702, K703, K705, K706, K707 and K708 Related Investments: 100901 - Dawn to Corunna | Completed | Fail | A Leave to construct regulatory process has received OEB decision for approval of proposed project scope.
STO - UG | Div_53 - Union South Storage | Compression Stations | Pass |  | 735801 | Parkway D Gas Generator Midlife Overhaul | 2032 | 4209772.8936 | Issue/Concern/Opportunity: The consequence of compressor failure is dominated by gas cost impacts to customers. The compressor package is comprised of a gas turbine engine driver, compressor, power turbine and ancillary equipment such as lube oil, fuel supply, and electronic control systems, which are required for the compressor to operate. The gas turbine engine is very complex and carries the greatest failure risk of all of the compressor package components. By continuing to comply with original equipment manufacturer (OEM) recommended Preventive Maintenance (PM) schedules and overhauls, compressor reliability risks are controlled to moderate levels. In the case of performing regular OEM prescribed overhauls, the risk of unit failure is proposed as a sawtooth function, whereby risk increases gradually over the recommended interval between overhauls and then drops suddenly after an overhaul. Critical internal wear components are on a path to failure and generally in sync with operating hours. If the operating hours are extended too far, the resulting additional operational stress on internal components, such as high temperature coatings and bearings, will increase the component scrap rate when performing the overhaul. This will add significant (10 to 20% or more) cost to the base overhaul and increases the risk of a random failure leading to system unreliability and further cost increases. Assets: Related Investments: | In Progress
STO - UG | Div_53 - Union South Storage | LNG | Pass |  | 48714 | Hagar Cold Box | 2032 | 15041122.2178 | Issue/Concern: The Cold Box is several heat exchangers in series used to cool the natural gas feedstock to -160°C at which point the natural gas turns into a liquid. The Cold Box is the core of the liquefied natural gas (LNG) station and is necessary to produce LNG. The consequence of a Cold Box failure is dominated by customer impact. Risk of associated failure is heavily influenced by thermal cycling and operational hours. Over its 50 years of operation, the Cold Box has amassed 140,000 operational hours. Significant failure modes include leakage of natural gas or refrigerants out of the piping into the interior of the Cold Box shell reaching potentially explosive levels or heat exchanger cross leaks that reduce the effectiveness of the refrigeration process. Both of these failure modes impair LNG production to the extent the plant cannot meet its annual production requirements. As the Cold Box internals are encased in very densely packed insulation and clad in an outer steel jacket, troubleshooting and repair of either of these failure modes is extremely difficult and time consuming. Assets: Cold Box Related Programs: Not applicable | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 1270 | Oil City Retrofit |  | 313873.5953
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 1271 | NPS 10 Sombra Line ILI Retrofit |  | 308891.4866
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 1784 | Panhandle NPS 16 - Bradley Line Class Location Replacement |  | 1494636.3461
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 48708 | Gas Chromatograph Replacement* | 2021 | 602658.2747
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 100533 | Wellhead Upgrade Project | 2024 | 451600.8873
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 100769 | Well Protection Improvements - Lock Blocks and Fences | 2021 | 1009415.2025
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102417 | Rectifier Ground Bed Replacement Program* | 2021 | 1240384.9723
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102528 | Well Optimization Program 2023* | 2023 | 311382.5721
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102529 | Well Optimization Program 2024* | 2024 | 320404.5725
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102530 | Well Optimization Program 2025* | 2025 | 322862.551
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102531 | Well Optimization Program 2026* | 2026 | 325805.6843
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102532 | Well Optimization Program 2027* | 2027 | 346935.7391
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102533 | Well Optimization Program 2028* | 2028 | 344043.7301
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102535 | Well Optimization Program 2029* | 2029 | 341580.3014
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102536 | Well Optimization Program 2030* | 2030 | 353687.3385
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102561 | STO STORAGE WELL UPGRADES 2023* | 2023 | 267789.012
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102562 | STO STORAGE WELL UPGRADES 2024* | 2024 | 275547.9323
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102563 | STO STORAGE WELL UPGRADES 2025* | 2025 | 277661.7939
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102564 | STO STORAGE WELL UPGRADES 2026* | 2026 | 423547.3896
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102565 | STO STORAGE WELL UPGRADES 2027* | 2027 | 451016.4608
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102567 | STO STORAGE WELL UPGRADES 2028* | 2028 | 447256.8491
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102568 | STO STORAGE WELL UPGRADES 2029* | 2029 | 444054.3918
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 102569 | STO STORAGE WELL UPGRADES 2030* | 2030 | 459793.54
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 503062 | Atmospheric Storage Tank Level Instrumentation 2023* |  | 61653.7493
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 503064 | Atmospheric Storage Tank Level Instrumentation 2024* |  | 63440.1053
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 503066 | Atmospheric Storage Tank Level Instrumentation 2025* |  | 63926.7851
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 733613 | NPS 10 Bentpath East - Booth Creek Retrofit |  | 1464366.8847
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 733830 | NPS 10 Oil City Pool Retrofit |  | 463337.2673
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 734280 | Ultrasonic Meter Upgrade 2023* |  | 398569.6923
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 734281 | Ultrasonic Meter Upgrade 2024* |  | 410117.8528
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 734891 | Bentpath Pool Gathering System |  | 671554.1061
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 734893 | Rosedale Pool Gathering System |  | 736126.6163
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 734896 | Bickford Pool Gathering System 2027 ECDA to ILI |  | 791013.4852
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 734923 | Oil Springs East Gathering System |  | 873159.234
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735404 | Well Optimization Program 2031* | 2031 | 349819.6393
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735405 | Well Optimization Program 2032* | 2032 | 339497.8184
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735417 | STO STORAGE WELL UPGRADES 2031* | 2031 | 454765.5311
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735418 | STO STORAGE WELL UPGRADES 2032* | 2032 | 441347.1639
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735747 | Ennisksillen Well Laterals Retrofit |  | 1026702.9123
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735748 | Booth Creek Pool Retrofit |  | 1103504.4961
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735749 | Mandaumin Pool Line Retrofit | 2031 | 1679134.2686
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 735994 | Oil City A1 Observation Well | 2025 | 1576614.1487
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 736098 | New Well Lateral/Crossover (Well Lifecycle Replacement)* | 2020 | 1304613.0263
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 736408 | 156 Storage Pool Gathering System Retrofits |  | 437139.0313
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Dollar threshold | 736651 | Mandaumin A1 observation well | 2024 | 1416750.0455
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Timing | 1277 | 2023 Well Lateral Integrity Program* | 2023 | 4982119.958
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Timing | 1279 | 2023 Integrity Dig Program S&T* | 2023 | 3051549.2066
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Timing | 1283 | 2024 Well Lateral Integrity Program* | 2024 | 5126473.2107
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Timing | 1286 | 2024 Depth of Cover Mitigation Program* | 2024 | 2563236.631
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Timing | 1288 | 2024 Integrity Dig Program S&T* | 2024 | 7016860.137
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Timing | 1293 | 2025 Depth of Cover Mitigation Program* | 2025 | 3260663.3945
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Timing | 1295 | 2025 Integrity Dig Program S&T* | 2025 | 3616059.2801
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Timing | 1296 | 2025 Well Lateral Integrity Program* | 2025 | 4429672.9603
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Fail | Timing | 736365 | A1 Observation Well Program* | 2022 | 9031716.0827
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 48257 | INTE: Dawn - Cuthbert - NPS 42 replacement | 2022 | 626338.5706 | General Concern: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI’s pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% SMYS. It includes installation costs for a permanent in-line inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and repair and replacement of pipeline segments with integrity issues that are identified through the inspections. Project-Specific Concern: The NPS 42, NPS 34, and NPS 26 pipelines between Dawn Compressor Station and Cuthbert Road receiver site have been inspected using external corrosion direct assessment (ECDA). Although it meets the intent of the Transmission Integrity Management Program (TIMP), there are specific features that ECDA could not detect comparing to the ILI. ILI of these transmission lines is required to ensure continued safety and reliability of EGI's assets. Assets: Transmission Pipeline (NPS 42, NPS 34, and NPS 26 pipelines between Dawn Compressor Station and Cuthbert Road receiver site) Related Programs: TIMP | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 48258 | INTE: Dawn - Cuthbert - ECDA to ILI Retrofit NPS 34* | 2022 | 143401.6387 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) retrofit of NPS 34 pipeline between Dawn Compressor station and Cuthbert Road receiver site. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 48259 | INTE: Dawn - Cuthbert - ECDA to ILI Retrofit NPS 26 | 2022 | 75061.8828 | Project-Specific: External Corrosion Direct Assessment (ECDA) to In-Line Inspection (ILI) retrofit of NPS 26 pipeline between Dawn Compressor station and Cuthbert Road receiver site. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30% Specified Minimum Yield Strength (SMYS). It includes installation costs for permanent ILI tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 48735 | Well Lifecycle Replacement | 2032 | 14292295.9338 | Issue/Concern: This project is intended to recover lost design day deliverability due to well relines and abandonments. The deliverability of the new well is not intended to increase but maintain the deliverability. This project will drill one new vertical injection/withdrawal well and connect it to the existing gathering system of the desired pool. Asset: Wells Related Program: N/A | Completed | Fail | Storage Pools & Well related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102573 | MOP Verification Replacement Program 2025 - S&T Assets* | 2030 | 1291450.2558 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102772 | 2026 Integrity Dig Program S&T* |  | 4346247.8289 | 2026 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102773 | 2027 Integrity Dig Program S&T* |  | 4628122.7596 | 2027 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102774 | 2028 Integrity Dig Program S&T* |  | 4589543.3591 | 2028 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102775 | 2029 Integrity Dig Program S&T* |  | 4556681.2208 | 2029 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102776 | 2030 Integrity Dig Program S&T* |  | 4718189.0954 | 2030 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102777 | 2026 Depth of Cover Mitigation Program* |  | 4289775.2259 | 2026 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 Mitigation of depth of cover sites that are out of compliance with CSA Z662 & TSSA requirements. Some of the known sites are discovered during annual Depth of Cover Surveying, while others are reported by company crews when performing maintenance work or by 3rd party . At this time the specific work scope of each year is not defined and this is a blanket program as a placeholder in the budget. The mitigation work will include the construction costs from sites identified and planned for the current year, as well as work on sites that are newly identified. Scope of work can vary from small remediation projects to add fill, concrete or bank stabilization, to short replacement of pipe. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102778 | 2027 Depth of Cover Mitigation Program* |  | 4567987.6941 | 2027 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 Mitigation of depth of cover sites that are out of compliance with CSA Z662 & TSSA requirements. Some of the known sites are discovered during annual Depth of Cover Surveying, while others are reported by company crews when performing maintenance work or by 3rd party . At this time the specific work scope of each year is not defined and this is a blanket program as a placeholder in the budget. The mitigation work will include the construction costs from sites identified and planned for the current year, as well as work on sites that are newly identified. Scope of work can vary from small remediation projects to add fill, concrete or bank stabilization, to short replacement of pipe. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102779 | 2028 Depth of Cover Mitigation Program* |  | 4529909.5713 | 2028 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 Mitigation of depth of cover sites that are out of compliance with CSA Z662 & TSSA requirements. Some of the known sites are discovered during annual Depth of Cover Surveying, while others are reported by company crews when performing maintenance work or by 3rd party . At this time the specific work scope of each year is not defined and this is a blanket program as a placeholder in the budget. The mitigation work will include the construction costs from sites identified and planned for the current year, as well as work on sites that are newly identified. Scope of work can vary from small remediation projects to add fill, concrete or bank stabilization, to short replacement of pipe. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102781 | 2029 Depth of Cover Mitigation Program* |  | 4497474.424 | 2029 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 Mitigation of depth of cover sites that are out of compliance with CSA Z662 & TSSA requirements. Some of the known sites are discovered during annual Depth of Cover Surveying, while others are reported by company crews when performing maintenance work or by 3rd party . At this time the specific work scope of each year is not defined and this is a blanket program as a placeholder in the budget. The mitigation work will include the construction costs from sites identified and planned for the current year, as well as work on sites that are newly identified. Scope of work can vary from small remediation projects to add fill, concrete or bank stabilization, to short replacement of pipe. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102782 | 2030 Depth of Cover Mitigation Program* |  | 4656883.7617 | 2030 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 Mitigation of depth of cover sites that are out of compliance with CSA Z662 & TSSA requirements. Some of the known sites are discovered during annual Depth of Cover Surveying, while others are reported by company crews when performing maintenance work or by 3rd party . At this time the specific work scope of each year is not defined and this is a blanket program as a placeholder in the budget. The mitigation work will include the construction costs from sites identified and planned for the current year, as well as work on sites that are newly identified. Scope of work can vary from small remediation projects to add fill, concrete or bank stabilization, to short replacement of pipe. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102783 | 2026 Well Lateral Integrity Program* |  | 3905324.6226 | 2026 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2023-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools or subject to other integrity verification. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102784 | 2027 Well Lateral Integrity Program* |  | 4651252.2715 | 2027 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2023-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools or subject to other integrity verification. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102785 | 2028 Well Lateral Integrity Program* |  | 5045975.1664 | 2028 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2023-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools or subject to other integrity verification. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102786 | 2029 Well Lateral Integrity Program* |  | 5009844.8762 | 2029 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2023-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools or subject to other integrity verification. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102787 | 2030 Well Lateral Integrity Program* |  | 4083910.2733 | 2030 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2023-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools or subject to other integrity verification. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 102801 | MOP Verification Replacement Program 2026 - S&T Assets* | 2031 | 2606445.5267 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 503024 | 2024 Waubuno 2 replacement wells | 2024 | 5322148.2169 | Issue: The deliverability of the Waubuno pool has declined due to the relines of the injection withdrawal wells UI20, UM20, UI22 and UI25 as well as the abandonment of the well UI30. The well UI20 is in a flood plain which is inaccessible during the spring months. Any response to a well incident would be severely impacted by the condition of the well and access to the well. The proposed abandonment of this will reduce deliverability. This project drills abandoned one well UI20 and drills two 8 5/8-inch wells. The two new wells will offset the reduction of deliverability due to the relines and abandonments. Assets: Waubuno pool and Gathering lines Related Program: Not applicable. | Completed | Fail | Storage Pools & Well related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 503069 | Dow A McPlank Connection | 2024 | 2632571.4867 | Issue/Concern/Opportunity: The Dow A pool is currently used to supply gas to the Sarnia market. Current Sarnia design day models assume that the Dow A pool is being completely drained. However, the Dow A pool can only be utilized until the pool reaches 700 psig without running the compressor. The purpose of this project is to tie Dow A into a lower pressure distribution line so that the inventory below 700 psi can be utilized without requiring compression. Assets: A new pipeline from Dow A Compression Station to McPlank distribution Related Program: Not applicable | Completed | Fail | Storage Pools & Well related projects are required to maintain existing deliverability and throughput. This is necessary to maintain security of supply and stable natural gas pricing during supply disruptions.
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 503195 | NPS 24 Trafalgar Bypass Retrofit | 2023 | 2491060.5768 | Issue/Concern/Opportunity: The NPS 24 Trafalgar Bypass pipeline connects the NPS 26 Trafalgar pipeline to Kirkwall Custody Transfer Station. The length is approximately 1.1 km. This pipeline’s condition is currently monitored via External Corrosion Direct Assessment (ECDA), which does not provide as complete a data set as In-Line Inspection (ILI) for Integrity Management purposes. By inspecting the pipeline via ILI, the condition of the asset will be more fully understood and the asset risk profile defined and managed in accordance with company standard. Justification: Move pipeline Condition Monitoring from ECDA to ILI in order to provide more complete data for Integrity Management purposes. Assets: NPS 24 Trafalgar Bypass Pipeline; Kirkwall Custody Transfer Station. Related Investments: 2024 Operations and Maintenance (O&M) budget for in-line inspection. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 734057 | 2031 Integrity Dig Program S&T* |  | 4666593.9881 | 2030 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 734058 | 2032 Integrity Dig Program S&T* |  | 4528900.8972 | 2030 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 735413 | 2031 Depth of Cover Mitigation Program* |  | 4605959.0504 | 2031 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 Mitigation of depth of cover sites that are out of compliance with CSA Z662 & TSSA requirements. Some of the known sites are discovered during annual Depth of Cover Surveying, while others are reported by company crews when performing maintenance work or by 3rd party . At this time the specific work scope of each year is not defined and this is a blanket program as a placeholder in the budget. The mitigation work will include the construction costs from sites identified and planned for the current year, as well as work on sites that are newly identified. Scope of work can vary from small remediation projects to add fill, concrete or bank stabilization, to short replacement of pipe. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 735414 | 2032 Depth of Cover Mitigation Program* |  | 4470055.0613 | 2032 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2021-2025 Mitigation of depth of cover sites that are out of compliance with CSA Z662 & TSSA requirements. Some of the known sites are discovered during annual Depth of Cover Surveying, while others are reported by company crews when performing maintenance work or by 3rd party . At this time the specific work scope of each year is not defined and this is a blanket program as a placeholder in the budget. The mitigation work will include the construction costs from sites identified and planned for the current year, as well as work on sites that are newly identified. Scope of work can vary from small remediation projects to add fill, concrete or bank stabilization, to short replacement of pipe. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 735415 | 2031 Well Lateral Integrity Program* |  | 5130688.5093 | 2031 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2023-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools or subject to other integrity verification. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 735416 | 2032 Well Lateral Integrity Program* |  | 4979301.7889 | 2032 forecast: This is a program budget placeholder, estimated using an average of the spend profile between 2023-2025 General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools or subject to other integrity verification. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 735427 | MOP Verification Replacement Program 2027 - S&T Assets* | 2032 | 2775485.9128 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 735428 | MOP Verification Replacement Program 2028 - S&T Assets* | 2033 | 2752349.8406 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 735429 | MOP Verification Replacement Program 2029 - S&T Assets* | 2034 | 2732642.4113 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 735430 | MOP Verification Replacement Program 2030 - S&T Assets* | 2035 | 2829498.7079 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 735431 | MOP Verification Replacement Program 2031 - S&T Assets* | 2036 | 2798557.1143 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_53 - Union South Storage | Transmission Pipe & Underground Storage | Pass |  | 735432 | MOP Verification Replacement Program 2032 - S&T Assets* | 2037 | 2715982.547 | General: MOP verification is the process of reviewing all existing records for a pipeline system and confirming the maximum operating pressure of existing greater than 30 per cent SMYS pipeline systems based upon these records. While this is not currently mandated by code in Canada, it is required in the U.S. and is expected to become a requirement in Canada in the future. Given the number of pipelines greater than 30 per cent SMYS, MOP Verification will be a multi-year project requiring a dedicated team to complete the verifications and determine if any pipeline remediation is required. This forecast includes the costs of replacing sections of pipelines as identified through the MOP verification work. MOP verification was also included in the 2017 customer engagement survey: while 43 per cent of those surveyed recommend waiting for regulation requirements to keep costs down, 40 per cent recommend proactively implementing industry standard. Spreading the verifications over several years will keep costs down and proactively implement an industry standard, which provides additional support for this program. Starting this program as forecast will mitigate the need for higher expenditures in a shorter time frame to meet these expected future mandated requirements. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_92 - Union North Storage | Compression Stations | Fail | Dollar threshold | 49021 | IROQUOIS FALLS VIBRATION MONITOR | 2023 | 498212.1154
STO - UG | Div_92 - Union North Storage | Compression Stations | Fail | Dollar threshold | 101371 | Hagar Solar 1 Control Panel Upgrade | 2023 | 404797.3437
STO - UG | Div_92 - Union North Storage | Compression Stations | Fail | Dollar threshold | 101493 | Hagar Solar 2 Control Panel Upgrade | 2025 | 1284813.662
STO - UG | Div_92 - Union North Storage | Compression Stations | Fail | Dollar threshold | 735296 | Hagar Blowdown and Knockout Tank | 2024 | 256323.658
STO - UG | Div_92 - Union North Storage | Compression Stations | Fail | Dollar threshold | 736038 | Hagar Solar Yard Cable Tray Supports |  | 186829.5433
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 49911 | Hagar Site Drainage Improvements | 2025 | 534867.0655
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 734363 | Hagar Leaking Valves - Replace (Unit 2) | 2023 | 48765.0019
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 735290 | Hagar Transformer Area Wall | 2023 | 37365.9087
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 735291 | Hagar Pipeduct Refurbishment | 2023 | 186829.5433
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 735292 | Hagar Molecular Sieves 3 Way Valve - Replace | 2024 | 76897.0974
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 735293 | Hagar MCC Building - Upgrades | 2025 | 193717.5306
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 735295 | Hagar Salt Bath Heater Obsolete Controls | 2024 | 51264.7316
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 736832 | Hagar KVGR MSAPR Mitigations | 2023 | 479529.161
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 736935 | Hagar Obsolete Mechanical - Replace* | 2037 | 830225.8267
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 736938 | Hagar Obsolete Electrical-Replace* | 2037 | 830225.8267
STO - UG | Div_92 - Union North Storage | LNG | Fail | Dollar threshold | 736939 | Hagar Obsolete Instrumentation-Replace* | 2037 | 830225.8267
STO - UG | Div_92 - Union North Storage | LNG | Pass |  | 48709 | Hagar KVGR and Cycle Mix Cooler | 2032 | 25988700.3194 | Issue/Concern: The Hagar Liquefied Natural Gas (LNG) Plant was installed in 1968 to provide security of supply to the Sudbury industrial and distribution markets. The KVGR Compressor is one of the two compressors used to power the refrigerant process which cools the natural gas feedstock to -160°C at which point the natural gas turns into a liquid. The KVGR Compressor is necessary to produce LNG. The consequence of compressor failure is dominated by customer impact. Risk associated with failure of the KVGR Compressor is heavily influenced by the time of year, weather severity and time to mitigate the failure. Over its 50 years of operation, the 1,500 horsepower Ingersoll Rand KVGR Compressor has amassed 140,000 operational hours. The compressor is obsolete and, although normal wear components are still available in the marketplace, core compressor replacement items such as cylinders, crankshafts, pistons, etc., required to support a critical failure are no longer manufactured by the original equipment manufacturer (OEM). In the event of a critical failure, aftermarket, custom machining services are the only option for repair. In the event custom machining services are not able to make a repair, a custom-designed aftermarket casting option or complete replacement of the compressor would be required rendering the LNG plant out of service for at least one operational season and rendering the plant unable to perform its regulated requirements. Assets: Compressor and Cycle Mix Cooler Related Programs: Not applicable. | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_92 - Union North Storage | LNG | Pass |  | 49955 | Hagar JVG Compressor Upgrade | 2032 | 21914726.4989 | Issue/Concern: The Boil-Off Gas (BOG) compressor is one of the two compressors used to power the refrigerant process which cools the natural gas feedstock to -160°C at which point the natural gas turns into a liquid. The BOG compressor was also used to recover BOG (i.e., natural gas vapours) from the liquefied natural gas (LNG) storage tank which occurs on a continuous basis due to the ambient warming of the tank exterior. In 2012, a separate compressor was installed to manage the LNG storage tank boil-off gas. The BOG compressor is necessary to produce LNG. The consequence of compressor failure is dominated by customer impact. Risk associated with failure of the BOG compressor is heavily influenced by the time of year, weather severity and time to mitigate the failure. Over its 50 years of operation, the 240 horsepower Ingersoll Rand BOG compressor has amassed 325,000 operational hours. The compressor is obsolete and, although normal wear components are still available in the marketplace, core compressor replacement parts such as cylinders, crankshafts, pistons, etc., required to support a critical failure are no longer manufactured by the original equipment manufacturer(OEM). In the event of a critical failure, securing used parts (which are rare) or aftermarket custom machining services are the only options for a timely repair. This was the case in 2017 when an aftermarket service was solicited to develop a weld and machine repair of a compressor cylinder which had failed. The aftermarket service was able to design a custom repair which took three months to complete. In the event that the cylinder is not repairable, a custom-designed aftermarket casting or a complete replacement of the compressor may be options. These options would take the plant out of service for at least one operational season, rendering the plant unable to perform its regulated requirements. Assets: BOG compressor Related Programs: Not applicable | Completed | Fail | See investment description, IRPAs not applicable
STO - UG | Div_92 - Union North Storage | LNG | Pass |  | 502916 | Hagar LNG Tank Boil Off Gas Recovery System | 2027 | 13523812.7756 | Issue/Concern/Opportunity: During sudden atmospheric pressure changes, boil-off gas venting from the liquified natural gas (LNG) storage tank vents occurs frequently. The current boil-off compressor is undersized for Hagar, which is one of Gas Distribution and Storage’s (GDS’s) largest emitter of unrecovered (or destroyed) natural gas at approximately 590,000 m3/year. The decision on whether the project is justified under greenhouse gas (GHG) compliance or based on the Corporate Emission Reduction Plans is currently in the works. In consideration of EGI’s Corporate Emission Reduction Plans and targets, Hagar is a single-point source and can be recovered by installing a single process within the existing LNG facility. Assets: Hagar LNG storage tank Related Investments: Not applicable. | Completed | Fail | See investment description, IRPAs not applicable
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 1638 | Alamosa Dr & Finch Ave E | 2024 | 51255.023
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 1691 | Bayview & Post Compression Couplings | 2024 | 79996.3571
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 1692 | Bayview & St. Leonards Compression Couplings | 2025 | 165664.9981
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 1693 | Bayview & Steeles CC Replacement | 2026 | 435926.1528
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 1702 | Bloor St. W. & The Kingsway Replacement | 2024 | 578697.9783
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 2334 | Meadowvale & Sheppard CC Replacement | 2027 | 345368.4085
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 2562 | Sheppard & Markham Compression Couplings | 2026 | 433766.2864
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 2563 | Sheppard Ave & Brimley Rd (Compression Couplings) | 2025 | 147257.7761
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 2698 | Weston Rd & Imogene Compression Couplings | 2023 | 177684.8799
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 4792 | Copper Service Replacement - Area 10* |  | 847572.7339
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 7604 | A10: Kipling Ave & Lake Shore Blvd W, Etobicoke, PH2 Replacement | 2024 | 468859.3281
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 7639 | A10: 46-68 Goodview Rd (North), North York, Noded Header Replacement | 2023 | 432805.7533
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 7646 | HR - 160-260 Chester Lee Blvd | 2025 | 1329752.2886
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 7647 | HR - 1021 Midland Ave | 2024 | 330720.0477
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 7649 | HR - 201 Bridletowne Circle | 2024 | 140307.4854
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 7651 | 121 – 151 L’Amoreaux Dr Steel Header Replacements | 2025 | 587884.1341
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 100505 | HR - 200-250 Bridletowne Circle | 2024 | 474021.5854
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 100506 | HR - 1040 Bridletowne Circle | 2024 | 438501.1142
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 100512 | Invergordon Ave, Toronto 3" PE Replacement | 2023 | 447113.7628
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 102203 | NPS 12 Victoria Square Pipeline - Integrity Retrofit > 30% SMYS |  | 257725.4942
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 102419 | Relocation Program - Area 10* | 2020 | 13287715.1803
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 502932 | TOR10YR - Toro to Cataford Replacement Standardization - Network # 161_169_172 | 2031 | 1733078.7236
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 502933 | TOR10YR - Dubray to Cornelius Replacement Standardization - Network # 161_169_172 | 2030 | 861826.9469
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 503156 | TOR10YR - Horner and Carson Replacement - Network # 123_368_373 | 2027 | 1418768.3669
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 503159 | TOR10YR - Rimilton Replacement - Network # 123_368_373 | 2029 | 1222291.1691
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 503160 | TOR10YR - Delta and Gamma Replacement - Network # 123_368_373 | 2028 | 1584145.9908
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 503164 | TOR10YR - Alderbrae Replacement - Network # 123_368_373 | 2028 | 753747.1902
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 503169 | TOR10YR - Delta North Replacement - Network # 123_368_373 | 2030 | 1033184.9511
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 733664 | TOR10YR - Silvercrest to Aldercrest Replacement- Network # 123_368_373 | 2031 | 809194.6708
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 733665 | TOR10YR - Evans Industrial Replacement- Network # 123_368_373 | 2032 | 1111220.4721
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 733667 | TOR10YR - Browns Evans Gair Replacement- Network # 123_368_373 | 2029 | 1618970.9149
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 733672 | TOR10YR - Horner and Orianna Replacement- Network # 123_368_373 | 2030 | 1328808.2241
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 733677 | TOR10YR - Browns and Owen Replacement- Network # 123_368_373 | 2031 | 1313524.3517
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 733799 | TOR10YR - Belleglade and Palms Replacement Standardization - Network # 152_154 | 2029 | 1046066.2418
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 733801 | TOR10YR - Bradstock to Verobeach Replacement Standardization - Network # 152_154 | 2031 | 430538.2295
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 733802 | TOR10YR - Lilac and Griffith Replacement Standardization - Network # 152_154 | 2028 | 1651311.1799
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 733803 | TOR10YR - Westin and Jasmine Replacement Standardization - Network # 152_154 | 2029 | 1372479.9214
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 735491 | TOR10YR - Treverton & Stratton Replacement - Network # 455 | 2030 | 1816430.0189
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 735492 | TOR10YR - Mooregate and Treverton Replacement - Network # 455 | 2028 | 1393155.595
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 735495 | TOR10YR - Moorecroft and Sedgewick Replacement - Network # 455 | 2030 | 1807057.8076
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 735498 | TOR10YR - Bertrand and Birchmount Replacement - Network # 455 | 2028 | 1542245.0474
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 735817 | TOR10YR - Bay Mills and Birchmount Replacement - Network # 455 | 2029 | 581222.4094
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 735848 | TOR10YR - Laurentide and Silverdale Replacement - Network # 455 | 2031 | 1676584.5165
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 735851 | TOR10YR - Groveland and Lacewood Replacement - Network # 455 | 2031 | 1759440.1939
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 735853 | TOR10YR - Fenelon and Graydon Hall Replacement - Network # 455 | 2030 | 1663440.4912
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 735864 | TOR10YR - Tiffany and Woodthorpe Replacement - Network # 455 | 2032 | 1122977.005
Toronto | 10 - Toronto | Distribution Pipe | Fail | Dollar threshold | 735865 | TOR10YR - Anewen and Kenewen Replacement - Network # 455 | 2032 | 1550830.632
Toronto | 10 - Toronto | Distribution Pipe | Fail | Emergent Safety | 4660 | Replacement Blanket - Area 10* |  | 21849758.8503
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 3430 | Anode Blanket - Area 10* | 2020 | 7495415.5816 | General: The anodes program within the corrosion program includes the required expenditure to install anodes in order to reduce the amount of down plant within EGI's system. These installations and replacements are based on the internal Standard Operating Practice established to maintain the appropriate level of cathodic protection on steel pipeline assets. | Completed | Fail | See investment description, IRPAs not applicable
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 4160 | Vintage Steel: NPS 12 SC HP on Parliament St, Carlton St to Front St | 2023 | 6830552.1793 | Issue/Concern: General Concerns: Vintage steel mains have shown signs of declining health due to the cumulative effect of poorly manufactured coating performance, construction practices, latent third-party damages to pipe coating, and the effect of stray currents from transit infrastructure such as subway and streetcars. The current failure projection model is forecasting an exponential increase in the number of corrosion-related failures, while the quantitative risk assessment and the 40-year risk projection are showing an increase in the safety risk associated with steel main failures. In addition to its age, vintage steel mains are also susceptible to accelerated degradation and/or higher risk of third-party damage in the following ways: 1) Compression couplings (e.g., mechanical fittings which are not welded onto the main) on steel mains that are not properly restrained or unrestrained could cause a loss of containment due to exposed points of thrust. In this case, the weight of the soil is required to hold the fittings in place. When the soil is disturbed, the pipe pulls out of the fitting, resulting in blowing gas through the open pipe end with the potential of full bore release of gas. 2) Compression couplings on steel mains that are unknowingly isolated from the corrosion protection system could result in inadequate cathodic protection, leading to the assets’ accelerated corrosion and potentially loss of containment. 3) The existence of shallow blow-off valve assemblies could be damaged during excavation activities. 4) Reduction in the original depth of cover due to urban development could increase the potential of damages due to excavation activities and increased external loading. According to the codes and standards, a minimum depth of cover is needed to ensure the appropriate distribution of weight of transportation vehicles across pipelines is not exceeded. If the depth of cover is not appropriate, excessive stresses are introduced into the pipe and failures could result. 5) The continuous exposure of road salt and seasonal ground movement on bridge-crossing assets could result in accelerated corrosion and external loading/stresses. 6) Lack of cathodic protection with pipe casings could result in corrosion causing excessive stress or shorts on the carrier pipe that is in contact with the casing, which could lead to the loss of containment. 7) Manufacturing defects associated with seam welds and fittings that are weak points in the distribution system could result in a loss of containment due to prolonged exposure to stress and corrosion. 8) Latent damages to pipe coatings that were never reported to EGI for repair and became active corrosion sites could hamper the effect of the corrosion protection system and result in accelerated corrosion and potentially loss of containment. Site-Specific Concerns: Early 1960s NPS 12 SC High Pressure (HP) subject to corrosion issues should be replaced. Coating damages and corrosion leaks were previously reported on the northern section of this NPS 12 gas main, which was replaced in 2015. Replacement pipe size is to be finalized by Planning during design phase. Assets: Network 180 KOL system. Related Programs: Vintage Steel Replacement. | Completed | Fail | Timing - Market based supply side alternatives not applicable
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 4760 | AMP Fitting Replacement - Area 10* | 2020 | 113626049.1104 | AMP Fittings are a below grade transition fittings. The inserted portion of copper tubing can fail due to internal corrosion. In these cases leaks develop immediately downstream of the AMP Fitting. | Completed | Fail | See investment description, IRPAs not applicable
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 10088 | NPS 20 Lake Shore Replacement (Cherry to Bathurst) | 2022 | 3241969.7392 | The NPS 20 assessment identifies risk results that exceeds EGI's risk threshold and supports the recommendation that this section of the pipeline (Cherry to Bathurst) requires replacement. The vintage steel replacement of the NPS 20 main on Lakeshore KOL from Cherry St to Bathurst will help address known pipe integrity and operational field concerns by proactively replacing the steel main approaching intolerable risk due to failing pipes or pipes in poor condition. This project will replace approximately 4.5 km of NPS 20 HP steel main and will abandon approximately 4.5 km of the existing NPS 20 HP main on Lakeshore Blvd in Toronto. | Completed | Fail | N/A - Project in construction phase
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 11443 | NPS 12 Martin Grove Rd Main Replacement: Lavington to St. Albans Rd. | 2026 | 23963833.6719 | Issue/Concern: General Concerns: Vintage steel mains have shown signs of declining health due to the cumulative effects of poorly manufactured coatings, construction practices, latent third-party damages to pipe coatings, and the effect of stray currents from transit infrastructure (such as the subway and streetcars). The current failure projection model forecasts an exponential increase in the number of corrosion-related failures. The C55 value framework and the 40-year risk projection show an aggressive increase in the safety risk associated with steel main failures. In addition to age, vintage steel mains are also susceptible to accelerated degradation and/or higher risk of third-party damage in the following ways: • Compression couplings • Shallow blow-off valve assemblies that could be damaged during excavation activities • Reduction in the original depth of cover • Continuous exposure to road salt and seasonal ground movement on bridge-crossing assets • Lack of cathodic protection on pipe casings that could result in corrosion and could lead to the loss of containment • Manufacturing defects associated with seam welds and fittings that could result in a loss of containment due to prolonged stress and corrosion • Latent damages to pipe coatings that were never reported to EGI for repair and became active corrosion sites, resulting in accelerated corrosion and potential loss of containment. Site-Specific Concerns: Martin Grove to St. Albans Road: Address NPS 12 pipe from Lavington Drive South to Burnhamthorpe Road, then west to Ashbourne Drive, then following Auckland Road south to St. Albans Road. There are over 360 service connections that will be removed from the high-pressure (HP) steel main and an intermediate pressure (IP) polyethylene (PE) subsystem installed to reconnect these customers. Depth of cover (DOC) has been identified as a significant concern for these main segments as identified by 2018 and 2019 DOC surveys that found over 52% of the survey locations had DOC less than 90 cm, with 77 survey locations measuring less than 60 cm of cover. Poor DOC can lead to increased third-party damages. Additional risk factors include two unrestrained compression couplings (CCs), nine restrained CCs, and three suspect valves where, due to their installation dates, may have been tied in using unrestrained CCs (as discovered by an Integrity Assessment showing significant correlation between valves of this vintage with unrestrained CC tie-ins). Cathodic protection history for the past 20 years shows that over 15% of the readings taken each year were below the minimum requirements. Poor cathodic protection levels can lead to corrosion. Assets: NPS 12 pipe from Lavington Drive south to Burnhamthorpe Road, then west to Ashbourne Drive, then following Auckland Rd. South to St. Albans Road. Related Programs: 6421, 10086. | On Hold |  | Technical Evaluation "On Hold" until further assessment from the E-DIMP Program confirms the project scope and timing.
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 13612 | Service Relay Blanket - Area 10* | 2020 | 114559612.831 | General: A distribution service refers to the pipe between the distribution main and the customer’s meter set. Over the years, different materials have been used for this asset, including steel, copper, and varying resins of plastic, each with unique characteristics that contribute to their performance over time. Services can be repaired or replaced depending on asset condition and the nature of the issue exhibited. Generally, replacement is the preferred approach to mitigate unacceptable asset condition. | Completed | Fail | See investment description, IRPAs not applicable
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 23147 | Toronto Island NPS 2 Feed Relocation | 2025 | 3900832.1702 | Issue/Concern: Currently, a 2-inch SC HP gas line (asset 61054) is sole feed to Toronto Island and is running through Western Gap Utility Tunnel. The utility tunnel is now considered a mine shaft, preventing necessary inspections of the line and the hangers that are supporting the line. This 2-inch SC HP main was installed in 1963 and the last known inspection of this line and hangers was in 1992. Should the line fail, the only recourse would be shutting the feed to Toronto Island, losing approximately 300 customers and undertaking an emergency replacement to resume service. Assets: NPS 2 SC HP Main (asset ID 61054) Related Program: Steel Mains Replacement Program | Completed | Fail | NPS 2, cannot downsize or retire
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 100339 | A10: Wilson Avenue, Toronto, VSM Replacement | 2025 | 91158783.5023 | Issue/Concern/Opportunity: Phased replacement of 12 gas main from Bathurst Ave. to Walsh Ave. Main is currently protected by Rectifier. -The main on Wilson Ave. has numerous Pumpkins that have been installed on it. Starting from Wendell Ave. and going east towards Bathurst St. -Corrosion on main has been an issue on Wilson Ave. due to stray current from Toronto Transit Commission (TTC) which continues to be an ongoing concern. -The service connections have field-applied coatings which leaves a concern for future corrosion issues on this main. -Regarding the main in the middle of the road on Wilson Ave., Curbside Valve Tee (CVT) repairs are problematic due to the location of the main. Assets: There is 8.5 km of NPS 12 HP Vintage Steel Main (VSM) installed between 1955 and 1964 on Wilson Ave. between Walsh Ave. and Bathurst St., Toronto. Related Program: Not applicable. Phased replacement of 12 Gas Main from Bathurst Ave. to Walsh Ave. Main is currently protected by Rectifier. -The main on Wilson Ave. has numerous Pumpkins that have been installed on it. Starting from Wendell Ave. and going east towards Bathurst St. -Corrosion on main has been an issue on Wilson Ave. due to stray current from Toronto Transit Commission (TTC) which continues to be an ongoing concern. -The service connections have field-applied coatings which leaves a concern for future corrosion issues on this main. -Regarding the main in the middle of the road on Wilson Ave. , Curbside Valve Tee (CVT) repairs are problematic due to the location of the main. Assets: There is 8.5 km of NPS 12 HP Vintage Steel Main (VSM) installed between 1955 and 1964 on Wilson Ave. between Walsh Ave. and Bathurst St., Toronto. Related Program: N/A | On Hold |  | Technical Evaluation "On Hold" until further assessment from the E-DIMP Program confirms the project scope and timing.
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 100497 | VSM - Firestone Road - 2" ST - PH1 | 2023 | 1968820.7906 | Issue/Concern/Opportunity: General Concerns: Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Assets: Approximately 1623.3 m 2-inch SC Intermediate Pressure (IP) to be replaced by 2-inch PE IP. Related Investments: Investment code #735792. | Completed | Fail | NPS 2, cannot downsize or retire
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 102204 | NPS 42 GTA Transmission - Integrity Retrofit > 30% SMYS | 2025 | 2577254.9421 | Funds to install launcher (station rebuild occurred in 2016; no provisions for launcher were included) on pipeline to allow for inline inspection are required. This will allow in-line inspection of the pipeline which is required as per the Pipeline Integrity Management Program. General: The Integrity Management Program is a mandated regulatory requirement which has been designed to comply with all applicable codes and standards. The program consists of the regular assessment and maintenance of the integrity of EGI's pipeline systems to ensure their continued safety and reliability. Most of the expenditure included in this category is for pipelines that operate above 30 per cent SMYS. It includes installation costs for permanent inline inspection (ILI) tool launcher and receiver facilities, retrofits to existing lines to remove restrictive fittings or pipe configurations so they can be inspected with ILI tools, and replacement of pipeline segments with integrity issues that are identified through the inspections. | Completed | Fail | See investment description, IRPAs not applicable
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 502929 | TOR10YR - Keelesgate and Cuffley Replacement Standardization - Network # 161_169_172 | 2030 | 1969836.1231 | TOR10YR - Keelesgate and Cuffley Replacement Standardization - Network #161_169_172 The 25 PSI Intermediate Pressure (IP) Pipe system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI requires reinforcing upgrades of mains and services. Scope: Replace gas mains with 300 m of NPS 4 PE and 1,040 m of NPS 2 PE, relay 90 services and reconnect 28 services. Resources: NPL to execute. Solution Impact: General Main (GM) upgrades will elevate pressure to reinforce system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 502935 | TOR10YR - Bayford to Dubray Replacement Standardization - Network # 161_169_172 | 2030 | 1872755.2134 | TOR10YR - Bayford to Dubray Replacement Standardization - Network #161_169_172 The 25 PSI Intermediate Pressure (IP) Pipe system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI requires main extension to 55 PSI network and upgrades to services. Scope: Upgrade gas mains and add main extension with 320 m of NPS 4 PE and 1,010 m of NPS 2 PE, relay 72 services, reconnect 27 services, and remove district station. Resources: NPL to execute. Solution Impact: General Main (GM) replacement and extension will elevate pressure and reinforce system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 503158 | TOR10YR - Horner from Browns Line Replacement - Network # 123_368_373 | 2027 | 1848506.8942 | TOR10YR - Horner from Browns Line Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 575 m NPS 8 PE, 13 service relays and 8 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 503161 | TOR10YR - Beta and Aldercrest Replacement - Network # 123_368_373 | 2029 | 1903272.7633 | TOR10YR - Beta and Aldercrest Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 575 m NPS 4 PE, 430 NPS 2 PE, 81 service relays and 44 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 503165 | TOR10YR - Hallmark to Lunness Replacement - Network # 123_368_373 | 2028 | 1806165.7549 | TOR10YR - Hallmark to Lunness Replacement - Network # 123_368_373 MP system running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services Scope: Replace and Upgrade gas mains and services with 1100 NPS 2 PE 88 Service Relays, 33 Service Reconnects. Resources: NPL to execute Solution Impact: GM replacements to meet pressure elevation requirements in system to meet growth requirements Project Timing: TBD. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 503167 | TOR10YR - Lanor and Valermo Replacement - Network # 123_368_373 | 2029 | 1956524.0825 | TOR10YR - Lanor and Valermo Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 1,300 NPS 2 PE, 79 service relays and 42 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 503168 | TOR10YR - Beta and Gamma North Replacement - Network # 123_368_373 | 2029 | 1849686.2473 | TOR10YR - Beta and Gamma North Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 1,000 NPS 2 PE, 105 service relays and 27 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733447 | TOR10YR - Aldercrest to Lunness North Replacement - Network # 123_368_373 | 2029 | 2156415.7955 | TOR10YR - Aldercrest to Lunness North Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 540 NPS 4 PE, 950 NPS 2 PE, 91 service relays and 52 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733448 | TOR10YR - Evans Ave Replacement- Network # 123_368_373 | 2029 | 2719150.3969 | TOR10YR - Evans Ave. Replacement - Network # 123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains (like for like) and services with 1,200m NPS 8 PE, 400 m NPS 4 PE, 70 service relays, 26 service reconnects, and upgrade station to 55 PSI. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733666 | TOR10YR - Bellman to N Carson Replacement- Network # 123_368_373 | 2029 | 2309839.0769 | TOR10YR - Bellman to N. Carson Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 1,400 NPS 2 PE, 119 service relays and 42 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733668 | TOR10YR - Savona and Bisset Replacement- Network # 123_368_373 | 2031 | 2229895.6089 | TOR10YR - Savona and Bisset Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 1,600 NPS 2 PE, 112 service relays, and 50 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733669 | TOR10YR - Delma and Ecker Replacement- Network # 123_368_373 | 2031 | 2367588.2111 | TOR10YR - Delma and Ecker Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 320 NPS 4 PE, 1,170 NPS 2 PE, 100 service relays and 32 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733670 | TOR10YR - Westhead Replacement- Network # 123_368_373 | 2029 | 1955611.2627 | Victoria St - Eastern - Area 60 - 1138 Vintage steel pipes exhibit increased failures as they age as steel mains are susceptible to external corrosion when barriers of pipe coatings and cathodic protection are compromised. The current pipe replacement rate (mains and services) is inadequate to prevent the average age of the population from increasing and hence reaching the end of their useful life. EGI has determined that a long-term proactive replacement program targeting higher-risk steel pipes installed on or before 1970 (vintage steel) is required to manage the increasing number of expected leaks that create increasing risk for the organization. Comments: There is potential for road restrictions due to congested area. TOR10YR - Westhead Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 1,250 m NPS 2 PE, 91 service relays and 34 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733671 | TOR10YR - Browns and Finsbury Replacement- Network # 123_368_373 | 2030 | 2229128.6925 | TOR10YR - Browns and Finsbury Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 180 m NPS 8 PE, 650 m NPS 4 PE, and 580 NPS 2 PE; 66 service relays and 14 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733673 | TOR10YR - Mitcham and Fulham Replacement - Network # 123_368_373 | 2030 | 2311877.593 | TOR10YR - Mitcham and Fulham Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 1,400 NPS 2 PE, 85 service relays and 70 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733674 | TOR10YR - Eltham and Delma Replacement- Network # 123_368_373 | 2030 | 2337978.1305 | TOR10YR - Eltham and Delma Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 1,550 NPS 2 PE, 76 service relays and 58 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733675 | TOR10YR - Browns Line at Horner Replacement- Network # 123_368_373 | 2030 | 1867745.0363 | TOR10YR - Browns Line at Horner Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 400 NPS 8 PE, 14 service relays and 9 service reconnects. There is approximately 400 m of NPS 4 PE required on 3 services and there is 1 garage header reconnect. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733678 | TOR10YR - Sunset and Burlington Replacement- Network # 123_368_373 | 2030 | 2165108.8652 | TOR10YR - Sunset and Burlington Replacement- Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 920 NPS 2 PE and 400 NPS 4 PE, 73 service relays and 44 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733679 | TOR10YR - Albright and Roseland Replacement- Network # 123_368_373 | 2030 | 2417165.8712 | TOR10YR - Albright and Roseland Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 900 NPS 2 PE, 500 NPS 4 PE, 81 service relays and 98 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733680 | TOR10YR - Foch and Woodbury Replacement- Network # 123_368_373 | 2031 | 2349455.7142 | TOR10YR - Foch and Woodbury Replacement - Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains and services with 1,220 NPS 2 PE, 220 NPS 4 PE, 98 service relays and 51 service reconnects. Resources: NPL to execute. Solution Impact: General Main (GM) replacements to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733681 | TOR10YR - St Lucie Replacement Standardization - Network # 152_154 | 2027 | 2174984.7474 | TOR10YR - St. Lucie Replacement Standardization - Network #152_154 The 25 PSI Intermediate Pressure (IP) Pipe system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI requires reinforcing upgrades of mains and services. Scope: Replace gas mains with 500 m of NPS 4 PE and 760 m of NPS 2 PE, relay 120 services and reconnect 58 services. Resources: NPL to execute. Solution Impact: General Main (GM) replacement will elevate pressure to reinforce system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733682 | TOR10YR - Gulfstream and Franson Replacement Standardization - Network # 152_154 | 2028 | 1923418.37 | TOR10YR - Gulfstream and Franson Replacement Standardization - Network # 152_154 25 PSI IP Pipe system running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI requires reinforcing upgrades of mains and services Scope: Replace gas mains with 400m of NPS 4 PE and 630m of NPS 2 PE Relay 95 services; Reconnect 37 Services Resources: NPL to execute Solution Impact: GM Replacement in order to elevate pressure to reinforce system to meet growth requirements Project Timing: TBD | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733683 | TOR10YR - Verobeach Replacement Standardization - Network # 152_154 | 2031 | 2526510.9822 | TOR10YR - Verobeach Replacement Standardization - Network #152_154 The 25 PSI Intermediate Pressure (IP) Pipe system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI requires reinforcing upgrades of mains and services. Scope: Replace gas mains with 690 m of NPS 4 PE and 900 m of NPS 2 PE, relay 135 services, and reconnect 48 services. Resources: NPL to execute. Solution Impact: General Main (GM) replacement will elevate pressure to reinforce system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733800 | TOR10YR - Coral Gable Replacement Standardization - Network # 152_154 | 2031 | 2322509.3034 | TOR10YR - Coral Gable Replacement Standardization - Network #152_154 The 25 PSI Intermediate Pressure (IP) Pipe system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI requires reinforcing upgrades of mains and services. Scope: Replace gas mains with 570 m of NPS 4 PE, 1,170 m of NPS 2 PE (like for like), relay 79 services, reconnect 52 services and remove 25 PSI station. Resources: NPL to execute. Solution Impact: General Main (GM) replacement will elevate pressure to reinforce system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733804 | TOR10YR - Yorkdale and Wallasey Replacement Standardization - Network # 152_154 | 2030 | 2327022.7787 | TOR10YR - Yorkdale and Wallasey Replacement Standardization - Network #152_154 The 25 PSI Intermediate Pressure (IP) Pipe system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI requires reinforcing upgrades of mains and services. Scope: Replace gas mains with 1,160 m of NPS 2 PE, relay 129 services and reconnect 60 services. Resources: NPL to execute. Solution Impact: General Main (GM) replacement will elevate pressure to reinforce system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733805 | TOR10YR - Starview and Weston Replacement Standardization - Network # 152_154 | 2030 | 2371979.4306 | TOR10YR - Starview and Weston Replacement Standardization - Network #152_154 25 PSI Intermediate Pressure (IP) Pipe system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI requires reinforcing upgrades of mains and services. Scope: Replace gas mains with 1,330 m of NPS 2 PE, relay 146 services and reconnect 12 services. Resources: NPL to execute. Solution Impact: General Main (GM) replacement will elevate pressure to reinforce system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733806 | TOR10YR - Gaydon and Highbury Replacement Standardization - Network # 152_154 | 2029 | 2308230.647 | TOR10YR - Gaydon and Highbury Replacement Standardization - Network #152_154 25 PSI Intermediate Pressure (IP) Pipe system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI requires reinforcing upgrades of mains and services. Scope: Install 350 m of NPS 4 PE and replace gas mains with 1,330 m of NPS 2 PE, relay 117 services, reconnect 55 services and upgrade station to 55 PSI. Resources: NPL to execute. Solution Impact: General Main (GM) replacement will elevate pressure to reinforce system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 733910 | TOR10YR - Browns Line and Jellicoe Replacement- Network # 123_368_373 | 2032 | 5197776.5308 | TOR10YR - Browns Line and Jellicoe Replacement- Network #123_368_373 Medium Pressure (MP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system requires replacement of MP mains and services. Scope: Replace and upgrade gas mains (like for like) and services with 80 m NPS 8 PE, 950 m NPS 4 PE, 2,275 m NPS 2 PE, 196 service relays, and 145 service reconnects; abandon station and outlet piping. Resources: NPL to execute. Solution Impact: General Main (GM) replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 734406 | Vintage Steel Replacement Program - 10 Toronto* | 2026 | 25545051.6341 | Issue/Concern: The VS Steel Main Replacement Program is both a reactive and proactive asset renewal program. Over the next ten years, the program will focus on reactively replacing steel mains that have experienced failure and integrity issues. The planned replacement will replace gas mains that exhibit signs of approaching end-of-life found in recent leak survey results and through field discovery of integrity issues (such as poor coating condition, severe corrosion, insufficient depth of cover or exposure, and leaks), as supported by the DIMP risk model. | Completed | Fail | See investment description, IRPAs not applicable
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735485 | TOR10YR - Foxbridge-Roebuck Replacement - Network # 277 | 2031 | 2354727.6121 | TOR10YR - Foxbridge-Roebuck Replacement - Network #277 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires replacement of some mains and services. Scope: Replace and upgrade gas mains with 450 m NPS 2 PE, 192 service relays, and 12 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735487 | TOR10YR - Birchmount & Foxbridge Replacement - Network # 277 | 2028 | 2752981.9947 | TOR10YR - Birchmount & Foxbridge Replacement - Network # 277 IP system running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires replacement of some mains and services Scope: Install Replace and Upgrade gas mains with 1500m NPS 2 PE, 1000m NPS 4 PE 32 Service Relays, CC removals Resources: NPL to execute Solution Impact: Gas Plant replacements and install to meet pressure elevation requirements in system to meet growth requirements Project Timing: TBD | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735489 | TOR10YR - Willowmount & Birchmount Replacement - Network # 277 | 2031 | 2353768.0822 | TOR10YR - Willowmount and Birchmount Replacement - Network #277 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires replacement of some mains and services. Scope: There are 181 service relays, 73 service reconnects, station removal/abandonment, and compression couplings (CCs) removal. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735497 | TOR10YR - Kingsdown and Ranstone Replacement - Network # 455 | 2028 | 2736596.7535 | TOR10YR - Kingsdown and Ranstone Replacement - Network # 455 IP system running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires replacement of some mains and services Scope: Replace and Upgrade gas mains with 1100m NPS 2 PE, 100m NPS 4 (Like for Like) 120 Service Relays, 91 Service Reconnects Resources: NPL to execute Solution Impact: Gas Plant replacements to meet pressure elevation requirements in system to meet growth requirements Project Timing: TBD | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735501 | TOR10YR - Ionview South Replacement - Network # 455 | 2028 | 2230995.9875 | TOR10YR - Ionview South Replacement - Network # 455 IP system running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires replacement of some mains and services Scope:Replace and Upgrade gas mains with 1300m NPS 2 PE (Like for Like) Install tie-in 30m NPS 4 109 Service Relays, 32 Service Reconnects Remove Station, tie-in to network 262 Resources: NPL to execute Solution Impact: Gas Plant replacements to meet pressure elevation requirements in system to meet growth requirements Project Timing: TBD | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735819 | TOR10YR - Bay Mills and Birchmount Services Replacement - Network # 455 | 2029 | 2616745.0034 | TOR10YR - Bay Mills and Birchmount Services Replacement - Network #455 Intermediate pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas services including 274 service relays and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. Permit: Some services may encroach in regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735820 | TOR10YR - Amethyst and Cass Replacement - Network # 455 | 2029 | 4372195.2122 | TOR10YR - Amethyst and Cass Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services Scope: Replace and upgrade gas mains and services with 2,350 m NPS 2 PE, 1,000 m NPS 4 PE (like for like), 98 service relays, 27 service reconnects, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735821 | TOR10YR - Aragon and Malamute Replacement - Network # 455 | 2030 | 2458254.0944 | TOR10YR - Aragon and Malamute Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 1,600 m NPS 2 PE, 121 service relays and 17 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735822 | TOR10YR - Scarden and Tourmaline Replacement - Network # 455 | 2030 | 2545630.4966 | TOR10YR - Scarden and Tourmaline Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 1,600 m NPS 2 PE, 250 m NPS 4, 96 service relays, and 18 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735824 | TOR10YR - Moraine Hill and Sunmount Replacement - Network # 455 | 2031 | 3799869.5101 | TOR10YR - Moraine Hill and Sunmount Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 2,800 m NPS 2 PE, 450 m NPS 4 (like for like), 154 service relays and 34 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735830 | TOR10YR - Birchmount South Sheppard Replacement - Network # 455 | 2029 | 3731512.4932 | TOR10YR - Birchmount South Sheppard Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 900 m NPS 8 PE (like for like), 17 service relays, 3 service reconnects, 100 m NPS 1.25 header, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735835 | TOR10YR - Allanford and Pender Replacement - Network # 455 | 2031 | 3673333.4845 | TOR10YR - Allanford and Pender Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 500 m NPS 6 PE, 600 m NPS 4 PE, 1,700 m NPS 2 PE (like for like), 140 service relays and 20 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735836 | TOR10YR - Araman and Earlton Replacement - Network # 455 | 2031 | 3673333.4845 | TOR10YR - Araman and Earlton Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 2,800 m NPS 6 PE (like for like), 176 service relays, and 19 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735839 | TOR10YR - Colingwood and Dempster Replacement - Network # 455 | 2030 | 2494336.2741 | TOR10YR - Colingwood and Dempster Replacement - Network #455 Intermediate Pressure (IP) is system running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 50 m NPS 4 PE, 650 NPS 8 PE, 137 service relays and 29 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735847 | TOR10YR - Birchmount North Ellesmere Replacement - Network # 455 | 2030 | 2314209.2961 | TOR10YR - Birchmount North Ellesmere Replacement - Network #455 Intermediate Pressure (IP) system running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 650 m NPS 8 PE, 50 NPS 2 PE (like for like) 36 service relays, 7 service reconnects (commercial services), and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. Toronto and Region Conservation Authority (TRCA) Permit - Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735849 | TOR10YR - Larabee and Tetbury Replacement - Network # 455 | 2031 | 2010060.9825 | TOR10YR - Larabee and Tetbury Replacement - Network #455 Intermediate Pressure (IP) is system running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 1,700m NPS 2 PE (like for like) 72 service relays and 45 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. Permit: Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735850 | TOR10YR - Three Valley Dr Replacement - Network # 455 | 2031 | 2879976.3362 | TOR10YR - Three Valley Dr. Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 60 m NPS 6 PE, 900 m NPS 4 PE, 500 m NPS 2 PE (like for like), 148 service relays, and 39 service reconnects. Resources: NPL to execute. Solution Impact: Gas Plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. Permit: Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735852 | TOR10YR - Valentine and York Mills Replacement - Network # 455 | 2030 | 2252485.1968 | TOR10YR - Valentine and York Mills Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 200 m NPS 4 PE, 650 m NPS 2 PE, 168 service relays, 20 service reconnects, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Permit: Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735854 | TOR10YR - Fenside and Lynedock Replacement - Network # 455 | 2030 | 5285358.9041 | TOR10YR - Fenside and Lynedock Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 150 m NPS 6 PE, 400 m NPS 4 PE, 2,700 m NPS 2 PE (like for like), 301 service relays, 46 service reconnects, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Permit – Creek Crossing | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735855 | TOR10YR - Roywood and York Mills Replacement - Network # 455 | 2032 | 5008876.8624 | TOR10YR - Roywood and York Mills Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 200 m NPS 2 PE (like for like), 569 service relays, 1 service reconnect, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Permit: Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735856 | TOR10YR - Sloane and Ruscica Replacement - Network # 455 | 2032 | 2972934.3791 | TOR10YR - Sloane and Ruscica Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 30 m NPS 6 PE, 1,100 m NPS 4 PE, 1,000 m NPS 2 PE (like for like), 71 service relays, 34 service reconnects, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Permit: Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735857 | TOR10YR - Wigmore and Draycott Replacement - Network # 455 | 2031 | 2969602.1022 | TOR10YR - Wigmore and Draycott Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 1,900 m NPS 2 PE, 104 service relays, and 54 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Permit: Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735858 | TOR10YR - Elvaston Replacement - Network # 455 | 2031 | 2516299.6108 | TOR10YR - Elvaston Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 1,600 m NPS 2 PE, 102 service relays and 30 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Toronto and Region Conservation Authority (TRCA) Permit - Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735859 | TOR10YR - Eccleston and Tinder Replacement - Network # 455 | 2031 | 2144072.5902 | TOR10YR - Eccleston and Tinder Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 1,200 m NPS 2 PE, 104 service relays, 24 service reconnects, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Toronto and Region Conservation Authority (TRCA) Permit: Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735860 | TOR10YR - North Sloane Replacement - Network # 455 | 2031 | 3558129.5163 | TOR10YR - North Sloane Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 100 m NPS 6 PE, 900 m NPS 4 PE, 1,350 m NPS 2 PE (like for like), 62 service relays, 20 service reconnects, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735861 | TOR10YR - Sweeney Replacement - Network # 455 | 2031 | 5123664.1917 | TOR10YR - Sweeney Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 750 m NPS 6 PE, 200 m NPS 4 PE, and 2,000 m NPS 2 PE (like for like), 124 service relays, 65 service reconnects, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. Permit: Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735862 | TOR10YR - Knighton and Prestbury Replacement - Network # 455 | 2031 | 3509187.0618 | TOR10YR - Knighton and Prestbury Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 200 m NPS 4 PE, 2,100 m NPS 2 PE (like for like) 89 service relays, and 82 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735863 | TOR10YR - Carnforth and Wyndcliff Replacement - Network # 455 | 2032 | 4062624.9307 | TOR10YR - Carnforth and Wyndcliff Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 700 m NPS 4 PE, 2,200 m NPS 2 PE (like for like), 100 service relays, 104 service reconnects, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735866 | TOR10YR - Pharmacy and Dewey Replacement - Network # 455 | 2032 | 1808002.9085 | TOR10YR - Pharmacy and Dewey Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 350 m NPS 2, 219 service relays, 7 service reconnects, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735867 | TOR10YR - Victoria Park Ivordale Replacement - Network # 455 | 2032 | 2556851.7353 | TOR10YR - Victoria Park Ivordale Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 760 m NPS 4 PE, 50 m NPS 2 PE (like for like), 214 service relays, 18 service reconnects, and compression coupling (CC) removals. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735868 | TOR10YR - Combermere Replacement - Network # 455 | 2032 | 4289302.7479 | TOR10YR - Combermere Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 550 m NPS 4 PE, 2,700 m NPS 2 PE (like for like), 181 service relays and 45 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735869 | TOR10YR - Parkwoods Village Replacement - Network # 455 | 2032 | 3359998.7764 | TOR10YR - Parkwoods Village Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services Scope: Replace and upgrade gas mains and services with 650 m NPS 4 PE, 2,200 m NPS 2 PE (like for like) 145 service relays, and 33 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735870 | TOR10YR - Brookbanks and Valley Woods Replacement - Network # 455 | 2032 | 3535865.1757 | TOR10YR - Brookbanks and Valley Woods Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 1,000 m NPS 4 PE, 1,850 m NPS 2 PE (like for like), compression couplings (CCs), 65 service relays, and 26 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. Permit: Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735871 | TOR10YR - Truxford and Overbank Replacement - Network # 455 | 2032 | 2491912.9001 | TOR10YR - Truxford and Overbank Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 100 m NPS 4 PE, 2,100 m NPS 2 PE (like for like), compression coupling (CC) removals, 61 service relays, and 54 service reconnects. Resources: NPL to execute. Solution Impact: Gas Plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. Permit – Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 735872 | TOR10YR - Wallingford Replacement - Network # 455 | 2032 | 3061748.7884 | TOR10YR - Wallingford Replacement - Network #455 Intermediate Pressure (IP) system is running close to capacity and not meeting growth needs. Plans to elevate pressure to 55 PSI system from 25 PSI requires upgrades and replacement of some mains and services. Scope: Replace and upgrade gas mains and services with 500 m NPS 4 PE, 2,100 m NPS 2 PE (like for like), compression coupling (CC) removals, 94 service relays, and 31 service reconnects. Resources: NPL to execute. Solution Impact: Gas plant replacements are to meet pressure elevation requirements in system to meet growth requirements. Project Timing: To be determined. Permit – Some services and mains may encroach into regulated area. | Planned
Toronto | 10 - Toronto | Distribution Pipe | Pass |  | 736024 | A:10 Dawlish Ave & Valleyanna Dr | 2023 | 1620984.8696 | Issue/Concern/Opportunity: Replace approximately 850 m of pipe on Dawlish Ave. and Valleyanna Dr. due to pipe age and opportunity to remove single-sourced district station that is currently leaking. Assets: STN#12443A to be removed Related Program: Not applicable | In Progress
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 2719 | YONGE AND STEELES FEEDER | 2024 | 476377.848
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 7765 | DOWNSVIEW FEEDER | 2026 | 500583.8093
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 7773 | NEILSON RD FEEDER | 2025 | 864675.3276
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 7775 | SIGNET & FINCH FEEDER | 2025 | 617728.5022
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18811 | SHEPPARD & KENNEDY DISTRICT | 2023 | 244768.7153
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18812 | BAYVIEW & SHEPPARD DISTRICT | 2023 | 264032.2501
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18815 | BAYVIEW & BYNG DISTRICT | 2023 | 576073.0844
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18816 | BRIMLEY & ELESMERE DISTRICT | 2024 | 425563.8518
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18818 | BAY & SCOLLARD DISTRICT LP | 2025 | 1026877.4376
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18844 | SHEPPARD AVE E & GRAND MARSHALL DISTRICT | 2024 | 160127.9175
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18845 | REPLIN & LAWRENCE DISTRICT | 2026 | 202610.5282
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18886 | SPADINA & MACPHERSON DISTRICT | 2023 | 1246911.4382
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18887 | DELORAINE & YONGE DISTRICT | 2025 | 284904.9239
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18888 | HARVIE & MORRISON DISTRICT | 2025 | 854792.4569
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18889 | KIPLING & NORTH QUEEN DISTRICT | 2023 | 411480.7746
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18963 | YORKGATE & FINCH DISTRICT | 2027 | 509228.8561
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18964 | CALEDONIA & RAITHERM DISTRICT | 2024 | 499564.6965
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 18965 | MCCOWAN AND SHEPPARD DISTRICT | 2027 | 746301.5273
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 20376 | FINCH & HALESIA DISTRICT | 2026 | 333478.7456
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 21023 | Telemetry Internal Work Scheduling | 2025 | 955.0058
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 101006 | 14378A - TRETHEWAY & CLEARVIEW DISTRICT | 2023 | 263971.1515
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 101229 | Enbridge Yard CNG Station B |  | 368462.33
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 501540 | Station B - Electrical | 2025 | 129173.4878
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 733451 | Station B Actuated Valve and Upgrades | 2029 | 136971.5835
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 733503 | NPS 30 Eglington Valve Actuation | 2024 | 128137.6856
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 733504 | NPS 30/NPS 36 Sheppard Interconnect Valve Actuation | 2025 | 129173.4878
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 734640 | CNG - Kennedy Upgrade/Redesign |  | 342900.6954
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 735176 | 17904A Rathburn and Dorlen District | 2023 | 518341.0848
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 735177 | 14435A BIRMINGHAM & NINTH DISTRICT | 2023 | 283173.5876
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 735179 | 12696A BROOKFIELD AND DONINO DISTRICT | 2023 | 244768.7153
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 735181 | 3226575 SHEPPARD & MORNINGSIDE DISTRICT | 2023 | 219830.4865
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 735182 | 2936953 MEADOWVALE & GENERATION DISTRICT | 2024 | 232141.2968
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 735183 | 2936745 MARKHAM & VERNE DISTRICT | 2024 | 130528.1122
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 735187 | 14887A GLAMORGAN & KENNEDY DISTRICT | 2024 | 287368.6393
Toronto | 10 - Toronto | Distribution Stations | Fail | Dollar threshold | 735188 | 17461A CAVERLY & MARTINGROVE DISTRICT | 2025 | 180403.5723
Toronto | 10 - Toronto | Distribution Stations | Fail | Emergent Safety | 10295 | Station Emergency Replacement Blanket - All Areas* |  | 2684940.3825
Toronto | 10 - Toronto | Distribution Stations | Pass |  | 1147 | KEELE AND FINCH FEEDER | 2025 | 5256579.6943 | Issue/Concern: The Keele and Finch Feeder station is adjacent to a transit station (subway) and there are electric transmission towers nearby. Due to transit upgrades, this project was deferred for many years. The subsystem issues are described below. Pipe, Valves & Others: Updated Mechanical Piping is required for this station. The isolation valves for the pressure control are hard to turn. The pressure control stations inlet/outlet valves are seized. Heating System: The Heating system is aging and an update is required at this station. Pressure Control: This station has four boot-style regulators that are undersized and require replacement. Odourant System: Not required. Telemetry/Electrical: Telemetry assets have been deemed within the hazardous classified area. Relocation of assets is required. New Control Wave Micro unit and associated connections are required. New generator is required to support backup power requirements. New Annubar on outlet of station is required for redundant measurement. Measurement: Not required. Building: One building needs to be considered to house all assets due to the surrounding environment (i.e., subway station, etc.) if additional land cannot be obtained. Assets: Station# 16997A Related Programs: Not applicable. | In Progress
Toronto | 10 - Toronto | Distribution Stations | Pass |  | 3605 | BAYVIEW FEEDER | 2024 | 6532377.7302 | Pipe, Valves & Others: Updated piping is required for this station to connect the new valve's and fittings and other associated materials. New inlet (NPS 12) and outlet (NPS 16) piping configurations are required to separate Maximum Operating Pressures (MOPs). Bayview Station will need to be shut in to execute piping installation. Station inlet filtration (gas separator) will be considered during the rebuild. Heating System: Updated heating is required at this station. Due to the area, this would more than likely be a conventional boiler system with two boilers minimum for heating load and redundancy. New building (concrete is required) with Glycol piping and new Glycol substance is required. The building is to be outfitted with all electrical elements (-5°C outlet temps during winter). A new heat exchanger will be required. Pressure Control: New regulation is required to support pressure cuts to separate MOPs. Three new runs (Operator and Monitor) will be required. These will be Becker Control Regulators and six are required. Odourant System: Not required. Telemetry/Electrical: Telemetry assets have been deemed within the hazardous classified area. Relocation of assets is required. New Control Wave Micro unit and associated connections are required. A new generator is required to support backup power requirements. Pressure and temperature transmitters (two each) are required. Measurement: The orifice plate is improperly sized and not accessible (below grade) and is to be replaced with above grade including piping. New Annubar on outlet of station is required for redundant measurement. Building: A new, large building format is required. The boiler, regulator and Remoter Terminal Unit (RTU) are all to be under one building (similar to Station A approach). Compliance/Civil: Site grading and new security fencing (galvanized) including new swing gate and crash bar access will be required. Existing lands will need to be confirmed if property is owned or leased. Tree trimming/removal may be required. The station is located on the Don Valley Trail. | Completed | Fail | Distribution station condition related, IRPA not applicable
Toronto | 10 - Toronto | Distribution Stations | Pass |  | 17403 | NGT Existing customer Maintenance Capital - (+2027)* |  | 2796842.5741 | Issue/concern: EGI Fleet operators can continue to achieve fuel cost savings and reduced emission benefits by investing in the wellbeing of the NGV station. This can be achieves by adopting continuously upgrading the major NGV equipment as part of the maintenance strategy. By upgrading the major NGV equipment, EGD can extend the life cycle of the equipment, resulting in a more cost effective way of operating the NGV stations. Assets: There is a number of current NGV Station EGI maintains. | Completed | Fail | See investment description, IRPAs not applicable for CNG
Toronto | 10 - Toronto | Distribution Stations | Pass |  | 18962 | (O)-ELLESMERE / BUDEA | 2025 | 195387.6969 | Issue/Concern: BOOT ABOVE GROUND BOX AGE: 31.9 Customer Count: 554 Utilization: 0.01858793 Can't short Sense # of Regs/Avg Size: 4 / 0in Assets: Related Program (if applicable): N/A | Completed | Fail | See investment description, IRPAs not applicable
Toronto | 10 - Toronto | Distribution Stations | Pass |  | 503183 | Albion Feeder Station Control Valve Upgrade | 2023 | 2638215.171 | At Albion Gate, valve F54201D controls the flow rate from the EGT line to the TC Energy Kings North outlet. All gas flowing to TC Energy must pass through the valve; there is no bypass, isolation, or redundancy included in the existing design. If this valve (F54201D) failed (and required maintenance), the inlet to both the EGI system and TC Energy’s outlets would be affected. The original purpose of the valve was to control flow to TC Energy to their contractual limit when flows on the EGT line were at their peaks. This control would guarantee the inlet pressure to the station feeding the EGI XHP systems which would be sufficient during peak operations. It was expected that this valve would be primarily 100% open and only be in service on the coldest of high-market demand days. Utilization was expected to be less than 10% of the winter days. In the winter period November 1, 2020 to February 25, 2021, the valve had been less than 100% open, 50% of the time (1407 hours / 2788 hours – source SCADA). Gas Control has utilized this valve more often for two purposes: (1) to carry higher pressure to Albion Gate for the distribution station; and (2) to maintain the operation of Parkway West compression within tolerances. Parkway West compressors are each 40,000 HP plus units. For the units to operate in their limited emission mode, both the volume pumped by the compressor and the lift across the compressor must be maintained within specific ranges. Using F54201D at Albion to limit flow to TC Energy allows the EGT line to act as a buffer for the compression. Compression volumes and lift can be maintained by operating the EGT line at higher pressure on warmer days. Risks: With no bypass and a single valve, a failure of the valve to open when needed will not allow EGI to deliver contracted quantities to TC Energy. Although this station rarely operates in summer months, summer would be the only time to work on the valve controls. Recommendation: Identify the appropriate design for the control valve feeding TC Energy Kings North that will meet EGI‘s control, bypass, and maintenance requirements. | Completed | Fail | Distribution station condition related, IRPA not applicable
Toronto | 10 - Toronto | Distribution Stations | Pass |  | 733809 | Parliament & Winchester Station Replacement - Execution Phase | 2023 | 1147245.8069 | Phase 2 ( Execution Phase) of the Parliament and Winchester Station Replacement Phase 2 project was created because original investment 1217 exceeded 5-years. The first station purchased in 2017 will not be used for this station rebuild and will be repurposed for future projects. | Completed | Fail | Distribution station condition related, IRPA not applicable
Toronto | 10 - Toronto | Distribution Stations | Pass |  | 735180 | 12377A PURPLE DUSK TRAIL & NEILSON DISTRICT | 2023 | 143020.742 | Issue/Concern/Opportunity: (from Field) • Below ground box Assets: District Station 12377A | Completed | Fail | See investment description, IRPAs not applicable
Toronto | 10 - Toronto | Growth | Pass |  | 3405 | Area 10 - Apartment Traditional - New Construction* |  | 31629.0892 | Apartment - An apartment customer is a multi-residential dwelling containing more than six units that is bulk-metered Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGD develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long term plans EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. Enbridge reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers; and, - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing Assets: Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Toronto | 10 - Toronto | Growth | Pass |  | 3720 | Area 10 - Industrial - New Construction* |  | 435335.86 | Industrial New Construction- A customer intending to run an industrial manufacturing business in a newly-built facility and intending to use natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGD develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long term plans EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. Enbridge reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers; and, - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing Assets: Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Toronto | 10 - Toronto | Growth | Pass |  | 3402 | Area 10 - Apartment Ensuite - New Construction* |  | 33932813.4162 | Issue/Concern: Vertical Subdivision refers to a multiple unit residential building where each suite is individually metered. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Toronto | 10 - Toronto | Growth | Pass |  | 3406 | Area 10 - Commercial - New Construction* |  | 88357564.8315 | Commercial New Construction- A commercial customer in a newly-built facility intending to use natural gas for a commercial business. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Toronto | 10 - Toronto | Growth | Pass |  | 3407 | Area 10 - Commercial - Replacement* |  | 20036048.0727 | Commercial Replacement - A commercial replacement customer using a fuel other than natural gas for commercial business and is converting to natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Toronto | 10 - Toronto | Growth | Pass |  | 3408 | Area 10 - Residential - Replacement* |  | 98154217.7815 | Issue/Concern: Residential Replacement refers to a residential replacement customer using a fuel other than natural gas for domestic purposes and is converting to natural gas. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Toronto | 10 - Toronto | Growth | Pass |  | 3700 | Area 10 - Residential - New Construction* |  | 118460850.1753 | Issue/Concern: Residential New Construction refers to a new residential construction development of detached single homes constructed by the builder for domestic purposes. Issue/Concern: EGI is mandated to provide new or upgraded natural gas services to feasible residential and commercial/industrial customers. Feasibility is measured using the Profitability Index metric that ensures gas cost impacts are minimized. Without the required CAPEX captured under this program, EGI will not be able to provide new or upgraded natural gas services to feasible customers. Each year, EGI develops a customer additions forecast using a number of information sources: - Projections of potential customer growth resulting from current projects in different geographical areas of operation based on information from builders, developers and municipalities - Projections for customer growth based on housing start forecasts and other economic factors such as GDP growth, employment rates, and mortgage rates - Projections developed by external consultants specializing in population growth forecasting - Municipal long-term plans: EGI extends its gas main within its franchise area to serve new customers when economically feasible, as per criteria prescribed by the Ontario Energy Board (OEB) in the EBO 188 report. EGI reviews the following when determining feasibility: - The number of potential new customers - The consumption of natural gas by new customers - The cost of extending the gas main The OEB, through EBO 188, directs utilities to have an average PI of 1.0 or greater for their total portfolio of projects and that any one individual project must meet a PI of at least 0.8, ensuring the minimization of cross-subsidization among customers across all projects. This ensures that the costs of projects are recovered from the customer(s) who would directly benefit. Without this approach to system expansion, the utility would not collect enough revenue to fund its projects, and the shortfall would need to be recovered from all other customers. If the cost of the extension is not economically feasible, the applicant(s) will be required to pay a contribution in aid of construction (CIAC). EGI determines the CIAC amount and communicate with the applicant(s) in writing. Generally, there are three components of capital investments needed to support customer addition requirements: - Installation costs related to mains, services, and meters - Material costs related to mains, services and meters - Costs related to measurement and regulation equipment required to support customer growth. Assets: All applicable assets. Related Program: N/A | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Toronto | 10 - Toronto | Growth | Pass |  | 7710 | McCowan Ave HP Reinforcement | 2022 | 31172.786 | Issue/Concern: Reinforcement projects broadly involve the installation of new or modification of existing gas distribution assets to maintain minimum required system pressure to maintain the capacity to meet customer demand. These projects are primarily driven by customer growth and system reliability considerations. Failure to implement reinforcement projects in a timely manner could lead to a potential inability to support increasing demands of existing customers and the addition of future customers. • Project Purpose/Need: This reinforcement is meant to support upstream and downstream load growth, bring back the flexibility EGI previously had in the system and to reduce dependency of other stations feeding the Intermediate Pressure (IP) network. Both McCowan and Southdale and South Unionville districts have been set to 40 psi and 50 psi respectively in 2016 to increase the tail‐end pressures in the High Pressure (HP) network. Operations has posed concerns with leaving these stations set at their current outlet pressures for an extended period of time. If the reinforcement is completed, the set pressures can be increased to 55 psi, the downstream networks’ intended pressure setting. Monitor points have been set up near the tail end of the HP network to determine if a reinforcement would be required in the near future. Mostly large volume customers and HP‐IP district stations are fed off of the HP network and maintaining an inlet above 100 psi has always been an EGI standard (according to the PDR). As indicated, there are many alternate sources available, but the pressure tends to diminish as it approaches the tail end of the network. This constraint will become apparent in the event of a damage or repairs need to be performed on one of the alternate feeds. If the reinforcement is performed at the date indicated, key decisions can be made in the field with high levels of confidence. • Pressure Issue/Concern: McCowan and Southdale District is approaching the minimum inlet pressure of 100 psi. There is a need to shift the flow to other sources in order to boost pressures near the tail end of the HP network. • Risk If Not Completed: If the inlet to STN 36013A ‐ McCowan and Southdale District or STN 32758A ‐ South Unionville and McCowan District ( Markham ) fall below 100 psi during design conditions in 2021, approximately 5,000 customers downstream will be lost. Scheduled maintenance for both stations beyond 2017 will need to occur in summer months due to the instability of the HP feed. If this reinforcement is completed by the in‐service date, either station could be taken offline for servicing without customer losses. Updates from 2021 review Assets (preferred option): • Deferred to 2022 from 2021: Install XHP to HP station at Steeles Ave. and IBM. The station will have a designed inlet of 485 psi with an outlet of 175 psi. The primary feed for this station will come from Victoria Gate. The tie‐in for the inlet will be off of the NPS 30 Steel Coated (SC) and the outlet will feed into the NPS 12 Steel (ST) HP on Steeles Ave. Approximately 25 m for the inlet and 25 m for the outlet will be required. • Deferred to 2023 from 2022: Raise STN 36013A ‐ McCowan and Southdale District from 40 psi to 50 psi. • 2024: Install 1.4 km of NPS 12 SC main on Tapscott Ave. from Passmore Ave. to Steeles Ave. • 2024: Raise pressure of STN 32758A ‐ South Unionville and McCowan District (Markham) from 40 psi to 55 psi and raise pressure of STN 36013A ‐ McCowan and Southdale District from 50 psi to 55 psi. In February 2022, Distribution Optimization Engineering confirmed that the feeder station at IBM is no longer required. The reinforcement on Steeles Ave. between Tapscott Rd. and New Side Rd. is sufficient to support the pressure in the surrounding area. Related Programs: Not applicable. | Completed | Fail | N/A - Project in construction phase
Toronto | 10 - Toronto | Growth | Pass |  | 11850 | Area 10 - Sales Stations - Replacements* |  | 6380455.4367 | Area 10 - Sales Station - Replacements | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Toronto | 10 - Toronto | Growth | Pass |  | 736616 | Area 10 Sales Station - New* |  | 18731557.7255 | Area 10 - Sales Station - New | Completed | Fail | Customer Connection-related projects are required to serve new customers connected in accordance with guidelines of EBO 188. Due to the the inability to offer non-gas IRPAs within the first-generation IRP Framework, IRPA's not applicable.
Toronto | 10 - Toronto | Growth | Pass |  | 736690 | Station Rebuild 14164A Lakeshore & Stadium SRP | 2023 | 1151409.6307 | Issue/Concern/Opportunity: Model shows a requirement to increase capacity through pressure control for the district station. ERX also shows outlet pressure dropping at 34 Degree Day (DD). System Reinforcement Plan (SRP) predicts the downstream will continue to grow in the next 10 years. Assets: District station rebuild Related Program: Not applicable | Completed | Fail | Timing - Market based supply side alternatives not applicable
Toronto | 10 - Toronto | Utilization | Pass |  | 13543 | MXGI Area 10* | 2019 | 142732655.4581 | Meters: Meters are used to determine the gas consumption input of customer billing. The replacement program for meters is mandated by Measurement Canada. The program includes: testing, repair, and replacement requirements of meters and instruments. All verified meters are approved by Measurement Canada with an issuance of a certificate which identifies that the meter complies with Electricity and Gas Specification S-EG-02. The Company must ensure all measurement devices remain in compliance for annual audits by Measurement Canada. Measurement Canada specifies tolerances under which the meter must operate in the field. The Company must demonstrate that all aspects of its meter sampling, maintenance, and replacement comply with these criteria in order to be accredited by Measurement Canada to be an “Authorized Service Provider” and adhere to Measurement Canada’s accreditation standard S-A-01. Meters may also require exchange for issues such as: damages, leaks, customer billing issues. Regulation: Regulators are the last line of defense for over-pressure to the customer. The condition of regulation systems is determined by regulator performance, corrosion of piping and regulators, and adherence to installation specifications. Failure of the regulation system can cause pressured gas to enter the premise, resulting in failure of gas equipment, loss of containment, and potentially fire or explosion. | Completed | Fail | See investment description, IRPAs not applicable