## HP_Contribution
Contribution of heat pumps to peak electricity demand (kW per average home & efficiency)
The analysis for the P2NZ study was conducted on a top-down basis, and the P2NZ study did not model contributions of individual heat pumps.
To answer intervenor's question on this topic, the calculation below estimates the peak load contribution of one ASHP.
The calculation uses average household gas consumption and efficiency, average weather data for Toronto, and cold climate ASHP performance data.
The calculation finds that, for an average Ontario home, a cold climate ASHP would contribute about 2.28 kW to electric peak load.
Assumptions
Assumption | Value | Unit | Source
Average gas consumption for a SF home in Ontario | 90.8 | GJ | https://www.cer-rec.gc.ca/en/data-analysis/energy-commodities/natural-gas/report/canadian-residential-natural-gasbill/index.html
Typical gas furnace efficiency in Ontario | 85% | AFUE
Conversion factor | 277.778 | kWh/GJ
Typical annual heating load | 21438.906 | kWh/yr | Calculated
Total annual heating degree hours (HDH) | 147604.7092 | HDH | Calculated
Heating load per HDH | 0.14525 | kW/HDH | Calculated
Calculations
| Hour of Year | Month | Day | Timestep | Season | Outdoor Temp (C) | HDH 18 | Hourly Heating Load (kW) | ASHP COP | ASHP Electric Demand (kW)
Source: | Weather Data for Toronto, Avg. 2017-2021 | [6 empty] | = HDH * load_per_HDH | Average COP curve | = Load / COP
| 1417 | 2 | 29 | 1 | Winter Peak | -11.6 | 29.6 | 4.2993 | 2.237 | 1.9219
| 1418 | 2 | 29 | 2 | Winter Peak | -12.1 | 30.1 | 4.3719 | 2.2192 | 1.97
| 1419 | 2 | 29 | 3 | Winter Peak | -12.4 | 30.4 | 4.4155 | 2.2088 | 1.9991
| 1420 | 2 | 29 | 4 | Winter Peak | -12.8 | 30.8 | 4.4736 | 2.195 | 2.038
| 1421 | 2 | 29 | 5 | Winter Peak | -13.9 | 31.9 | 4.6333 | 2.1586 | 2.1464
| 1422 | 2 | 29 | 6 | Winter Peak | -15.6 | 33.6 | 4.8802 | 2.1063 | 2.317
| 1423 | 2 | 29 | 7 | Winter Peak | -15.2 | 33.2 | 4.8221 | 2.1182 | 2.2766
| 1424 | 2 | 29 | 8 | Winter Peak | -15.5 | 33.5 | 4.8657 | 2.1092 | 2.3069
| 1425 | 2 | 29 | 9 | Winter Peak | -14.5 | 32.5 | 4.7205 | 2.1396 | 2.2062
| 1426 | 2 | 29 | 10 | Winter Peak | -14.1 | 32.1 | 4.6624 | 2.1522 | 2.1663
| 1427 | 2 | 29 | 11 | Winter Peak | -12.3 | 30.3 | 4.4009 | 2.2123 | 1.9893
| 1428 | 2 | 29 | 12 | Winter Peak | -10.3 | 28.3 | 4.1104 | 2.2852 | 1.7988
| 1429 | 2 | 29 | 13 | Winter Peak | -9.1 | 27.1 | 3.9362 | 2.332 | 1.6879
| 1430 | 2 | 29 | 14 | Winter Peak | -7.6 | 25.6 | 3.7183 | 2.3939 | 1.5532
| 1431 | 2 | 29 | 15 | Winter Peak | -7 | 25 | 3.6311 | 2.4197 | 1.5006
| 1432 | 2 | 29 | 16 | Winter Peak | -6.2 | 24.2 | 3.5149 | 2.4551 | 1.4317
| 1433 | 2 | 29 | 17 | Winter Peak | -5.6 | 23.6 | 3.4278 | 2.4822 | 1.3809
| 1434 | 2 | 29 | 18 | Winter Peak | -7.2 | 25.2 | 3.6602 | 2.4111 | 1.5181
| 1435 | 2 | 29 | 19 | Winter Peak | -7.8 | 25.8 | 3.7473 | 2.3855 | 1.5709
| 1436 | 2 | 29 | 20 | Winter Peak | -7.8 | 25.8 | 3.7473 | 2.3855 | 1.5709
| 1437 | 2 | 29 | 21 | Winter Peak | -7.9 | 25.9 | 3.7619 | 2.3813 | 1.5798
| 1438 | 2 | 29 | 22 | Winter Peak | -8.4 | 26.4 | 3.8345 | 2.3605 | 1.6245
| 1439 | 2 | 29 | 23 | Winter Peak | -11.6 | 29.6 | 4.2993 | 2.237 | 1.9219
| 1440 | 2 | 29 | 24 | Winter Peak | -11 | 29 | 4.2121 | 2.2589 | 1.8647
Heat Pump Performance Data
Five 3-ton cold-climate ASHPs sampled from NEEP cold-climate ASHP database
Performance data (COP vs outdoor temp) retrieved from ASHP manufacturer data (linked below)
For temperatures not included in manufacturer data, COP values are extrapolated or interpolated.
Average COP calculated, plotted and fit to 2-dimension polynomial.
Legend
[5 empty] | no color | = provided by datasheet
[5 empty] | gray | = interpolated
[5 empty] | yellow | = extrapolated
Outdoor Temperature (C)
3-ton Cold-Climate ASHP Models |  | 23.8889 | 22.2222 | 19.4444 | 18 | 16.6667 | 15.5556 | 13.8889 | 12.7778 | 11.1111 | 10 | 8.3333 | 7 | 5.5556 | 4.4444 | 2.7778 | 1.6667 | 0 | -1.1111 | -2.7778 | -3.8889 | -5.5556 | -6.6667 | -8.3333 | -9.4444 | -10 | -11.1111 | -12.2222 | -13.8889 | -15 | -16.6667 | -17.7778 | -20 | -20.5556 | -23.3333 | -25 | -30
Daikin DZ6VSA3610A (page 18) | COP | 3.6638 | 3.5971 | 3.4843 | 3.4349 | 3.3704 | 3.3274 | 3.2538 | 3.2047 | 3.1323 | 3.0841 | 3.0001 | 2.9307 | 2.8333 | 2.7684 | 2.6571 | 2.5828 | 2.519 | 2.4764 | 2.4258 | 2.392 | 2.3669 | 2.3502 | 2.3312 | 2.2773 | 2.2501 | 2.1957 | 2.1413 | 2.0552 | 1.9977 | 1.913 | 1.8565 | 1.7282 | 1.6962 | 1.5262 | 1.4337 | 1.137
Samsung CXH36UPB (page 17) | COP | 4.7286 | 4.5453 | 4.2398 | 4.1177 | 3.9344 | 3.8122 | 3.6289 | 3.5067 | 3.3234 | 3.2012 | 3.0179 | 3.0157 | 3.0123 | 3.01 | 3.0066 | 3.0044 | 3.001 | 2.9397 | 2.8477 | 2.7864 | 2.6945 | 2.6332 | 2.5412 | 2.4799 | 2.4493 | 2.3861 | 2.323 | 2.2283 | 2.1652 | 2.1127 | 2.0778 | 2.0078 | 1.9836 | 1.8622 | 1.7894 | 1.5913
Pioneer YH3036GHFD18R2 (page 19) | COP | 4.9978 | 4.824 | 4.4808 | 4.3691 | 4.2014 | 4.0684 | 3.8689 | 3.746 | 3.5615 | 3.474 | 3.3428 | 3.1877 | 2.9551 | 2.903 | 2.8249 | 2.7835 | 2.7214 | 2.6245 | 2.4792 | 2.4398 | 2.3807 | 2.387 | 2.3964 | 2.347 | 2.3223 | 2.273 | 2.2285 | 2.1617 | 2.1314 | 2.0858 | 2.0498 | 1.9778 | 1.9643 | 1.8782 | 1.8253 | 1.6711
Bosch BOVA-36HDN1-M18M (page 23) | COP | 5.8386 | 5.534 | 5.147 | 5.0145 | 4.8157 | 4.6656 | 4.4405 | 4.2989 | 4.0866 | 3.9856 | 3.8341 | 3.6564 | 3.3898 | 3.3316 | 3.2444 | 3.1954 | 3.1221 | 3.0123 | 2.8478 | 2.8015 | 2.7322 | 2.7376 | 2.7457 | 2.6877 | 2.6587 | 2.6006 | 2.5517 | 2.4782 | 2.4434 | 2.3911 | 2.3511 | 2.271 | 2.2552 | 2.1587 | 2.0997 | 1.9268
Carrier 38MURA (page 51) | COP | 3.686 | 3.6125 | 3.4922 | 3.4269 | 3.3685 | 3.3206 | 3.2489 | 3.1927 | 3.1084 | 3.0584 | 2.9834 | 2.9234 | 2.7552 | 2.6672 | 2.5352 | 2.4784 | 2.3932 | 2.3655 | 2.324 | 2.2811 | 2.2168 | 2.1641 | 2.085 | 2.1062 | 2.1168 | 2.1151 | 2.1135 | 2.111 | 2.1094 | 2.1187 | 2.1249 | 2.1355 | 2.1381 | 2.1513 | 2.1623 | 2.1954
Average | COP | 4.583 | 4.4226 | 4.1688 | 4.0726 | 3.9381 | 3.8389 | 3.6882 | 3.5898 | 3.4424 | 3.3607 | 3.2357 | 3.1428 | 2.9891 | 2.936 | 2.8536 | 2.8089 | 2.7513 | 2.6837 | 2.5849 | 2.5402 | 2.4782 | 2.4544 | 2.4199 | 2.3796 | 2.3594 | 2.3141 | 2.2716 | 2.2069 | 2.1694 | 2.1243 | 2.092 | 2.0241 | 2.0075 | 1.9153 | 1.8621 | 1.7043
Second-order polynomial fit to average COP vs. ODT
| A | B | C
| 0.00081783 | 0.054933 | 2.7642
Weather Data from Environment Canada
Average hourly temperature (degrees Celcius) over the 5 year period from 2017-2021 (inclusive).
Tbl_Weather_Data
hour_of_year | station | month | day | hour_end | avg_temp | hdh_18 | cdh_18
1 | TORONTO BUTTONVILLE A | 1 | 1 | 1 | -3.84 | 21.84 | 0
2 | TORONTO BUTTONVILLE A | 1 | 1 | 2 | -4.14 | 22.14 | 0
3 | TORONTO BUTTONVILLE A | 1 | 1 | 3 | -4.64 | 22.64 | 0
4 | TORONTO BUTTONVILLE A | 1 | 1 | 4 | -5.08 | 23.08 | 0
5 | TORONTO BUTTONVILLE A | 1 | 1 | 5 | -5.6 | 23.6 | 0
6 | TORONTO BUTTONVILLE A | 1 | 1 | 6 | -5.22 | 23.22 | 0
7 | TORONTO BUTTONVILLE A | 1 | 1 | 7 | -5.06 | 23.06 | 0
8 | TORONTO BUTTONVILLE A | 1 | 1 | 8 | -5.24 | 23.24 | 0
9 | TORONTO BUTTONVILLE A | 1 | 1 | 9 | -5.18 | 23.18 | 0
10 | TORONTO BUTTONVILLE A | 1 | 1 | 10 | -5.26 | 23.26 | 0
11 | TORONTO BUTTONVILLE A | 1 | 1 | 11 | -3.6 | 21.6 | 0
12 | TORONTO BUTTONVILLE A | 1 | 1 | 12 | -2.8 | 20.8 | 0
13 | TORONTO BUTTONVILLE A | 1 | 1 | 13 | -2.44 | 20.44 | 0
14 | TORONTO BUTTONVILLE A | 1 | 1 | 14 | -2.16 | 20.16 | 0
15 | TORONTO BUTTONVILLE A | 1 | 1 | 15 | -2.22 | 20.22 | 0
16 | TORONTO BUTTONVILLE A | 1 | 1 | 16 | -2.38 | 20.38 | 0
17 | TORONTO BUTTONVILLE A | 1 | 1 | 17 | -3.1 | 21.1 | 0
18 | TORONTO BUTTONVILLE A | 1 | 1 | 18 | -3.64 | 21.64 | 0
19 | TORONTO BUTTONVILLE A | 1 | 1 | 19 | -4.4 | 22.4 | 0
20 | TORONTO BUTTONVILLE A | 1 | 1 | 20 | -4.84 | 22.84 | 0
21 | TORONTO BUTTONVILLE A | 1 | 1 | 21 | -4.98 | 22.98 | 0
22 | TORONTO BUTTONVILLE A | 1 | 1 | 22 | -5.48 | 23.48 | 0
23 | TORONTO BUTTONVILLE A | 1 | 1 | 23 | -6.16 | 24.16 | 0
24 | TORONTO BUTTONVILLE A | 1 | 1 | 24 | -6.22 | 24.22 | 0
25 | TORONTO BUTTONVILLE A | 1 | 2 | 1 | -6.16 | 24.16 | 0
26 | TORONTO BUTTONVILLE A | 1 | 2 | 2 | -6.16 | 24.16 | 0
27 | TORONTO BUTTONVILLE A | 1 | 2 | 3 | -6 | 24 | 0
28 | TORONTO BUTTONVILLE A | 1 | 2 | 4 | -5.66 | 23.66 | 0
29 | TORONTO BUTTONVILLE A | 1 | 2 | 5 | -5.66 | 23.66 | 0
30 | TORONTO BUTTONVILLE A | 1 | 2 | 6 | -4.78 | 22.78 | 0
31 | TORONTO BUTTONVILLE A | 1 | 2 | 7 | -4.9 | 22.9 | 0
32 | TORONTO BUTTONVILLE A | 1 | 2 | 8 | -4.38 | 22.38 | 0
33 | TORONTO BUTTONVILLE A | 1 | 2 | 9 | -4.18 | 22.18 | 0
34 | TORONTO BUTTONVILLE A | 1 | 2 | 10 | -3.96 | 21.96 | 0
35 | TORONTO BUTTONVILLE A | 1 | 2 | 11 | -2.92 | 20.92 | 0
36 | TORONTO BUTTONVILLE A | 1 | 2 | 12 | -2.02 | 20.02 | 0
37 | TORONTO BUTTONVILLE A | 1 | 2 | 13 | -1.38 | 19.38 | 0
38 | TORONTO BUTTONVILLE A | 1 | 2 | 14 | -0.64 | 18.64 | 0
39 | TORONTO BUTTONVILLE A | 1 | 2 | 15 | -0.48 | 18.48 | 0
40 | TORONTO BUTTONVILLE A | 1 | 2 | 16 | -0.58 | 18.58 | 0
41 | TORONTO BUTTONVILLE A | 1 | 2 | 17 | -0.84 | 18.84 | 0
42 | TORONTO BUTTONVILLE A | 1 | 2 | 18 | -0.86 | 18.86 | 0
43 | TORONTO BUTTONVILLE A | 1 | 2 | 19 | -1.08 | 19.08 | 0
44 | TORONTO BUTTONVILLE A | 1 | 2 | 20 | -1.28 | 19.28 | 0
45 | TORONTO BUTTONVILLE A | 1 | 2 | 21 | -1.46 | 19.46 | 0
46 | TORONTO BUTTONVILLE A | 1 | 2 | 22 | -1.68 | 19.68 | 0
47 | TORONTO BUTTONVILLE A | 1 | 2 | 23 | -1.64 | 19.64 | 0
48 | TORONTO BUTTONVILLE A | 1 | 2 | 24 | -1.8 | 19.8 | 0
49 | TORONTO BUTTONVILLE A | 1 | 3 | 1 | -1.94 | 19.94 | 0
50 | TORONTO BUTTONVILLE A | 1 | 3 | 2 | -1.98 | 19.98 | 0
51 | TORONTO BUTTONVILLE A | 1 | 3 | 3 | -1.86 | 19.86 | 0
52 | TORONTO BUTTONVILLE A | 1 | 3 | 4 | -2.02 | 20.02 | 0
53 | TORONTO BUTTONVILLE A | 1 | 3 | 5 | -2.16 | 20.16 | 0
54 | TORONTO BUTTONVILLE A | 1 | 3 | 6 | -1.92 | 19.92 | 0
55 | TORONTO BUTTONVILLE A | 1 | 3 | 7 | -1.4 | 19.4 | 0
56 | TORONTO BUTTONVILLE A | 1 | 3 | 8 | -1.16 | 19.16 | 0
57 | TORONTO BUTTONVILLE A | 1 | 3 | 9 | -1.08 | 19.08 | 0
58 | TORONTO BUTTONVILLE A | 1 | 3 | 10 | -0.86 | 18.86 | 0
59 | TORONTO BUTTONVILLE A | 1 | 3 | 11 | -0.42 | 18.42 | 0
60 | TORONTO BUTTONVILLE A | 1 | 3 | 12 | -2.2187e-17 | 18 | 0
61 | TORONTO BUTTONVILLE A | 1 | 3 | 13 | 0.18 | 17.82 | 0
62 | TORONTO BUTTONVILLE A | 1 | 3 | 14 | 0.3 | 17.7 | 0
63 | TORONTO BUTTONVILLE A | 1 | 3 | 15 | 0.46 | 17.54 | 0
64 | TORONTO BUTTONVILLE A | 1 | 3 | 16 | 0.44 | 17.56 | 0
65 | TORONTO BUTTONVILLE A | 1 | 3 | 17 | 0.18 | 17.82 | 0
66 | TORONTO BUTTONVILLE A | 1 | 3 | 18 | -0.08 | 18.08 | 0
67 | TORONTO BUTTONVILLE A | 1 | 3 | 19 | -0.14 | 18.14 | 0
68 | TORONTO BUTTONVILLE A | 1 | 3 | 20 | -0.58 | 18.58 | 0
69 | TORONTO BUTTONVILLE A | 1 | 3 | 21 | -0.86 | 18.86 | 0
70 | TORONTO BUTTONVILLE A | 1 | 3 | 22 | -1.02 | 19.02 | 0
71 | TORONTO BUTTONVILLE A | 1 | 3 | 23 | -1.3 | 19.3 | 0
72 | TORONTO BUTTONVILLE A | 1 | 3 | 24 | -1.42 | 19.42 | 0
73 | TORONTO BUTTONVILLE A | 1 | 4 | 1 | -1.38 | 19.38 | 0
74 | TORONTO BUTTONVILLE A | 1 | 4 | 2 | -1.36 | 19.36 | 0
75 | TORONTO BUTTONVILLE A | 1 | 4 | 3 | -1.48 | 19.48 | 0
76 | TORONTO BUTTONVILLE A | 1 | 4 | 4 | -1.5 | 19.5 | 0
77 | TORONTO BUTTONVILLE A | 1 | 4 | 5 | -1.5 | 19.5 | 0
78 | TORONTO BUTTONVILLE A | 1 | 4 | 6 | -1.6 | 19.6 | 0
79 | TORONTO BUTTONVILLE A | 1 | 4 | 7 | -1.92 | 19.92 | 0
80 | TORONTO BUTTONVILLE A | 1 | 4 | 8 | -2.22 | 20.22 | 0
81 | TORONTO BUTTONVILLE A | 1 | 4 | 9 | -2.5 | 20.5 | 0
82 | TORONTO BUTTONVILLE A | 1 | 4 | 10 | -2.26 | 20.26 | 0
83 | TORONTO BUTTONVILLE A | 1 | 4 | 11 | -2.12 | 20.12 | 0
84 | TORONTO BUTTONVILLE A | 1 | 4 | 12 | -1.98 | 19.98 | 0
85 | TORONTO BUTTONVILLE A | 1 | 4 | 13 | -2.06 | 20.06 | 0
86 | TORONTO BUTTONVILLE A | 1 | 4 | 14 | -1.98 | 19.98 | 0
87 | TORONTO BUTTONVILLE A | 1 | 4 | 15 | -1.94 | 19.94 | 0
88 | TORONTO BUTTONVILLE A | 1 | 4 | 16 | -1.94 | 19.94 | 0
89 | TORONTO BUTTONVILLE A | 1 | 4 | 17 | -2.4 | 20.4 | 0
90 | TORONTO BUTTONVILLE A | 1 | 4 | 18 | -3.16 | 21.16 | 0
91 | TORONTO BUTTONVILLE A | 1 | 4 | 19 | -3.68 | 21.68 | 0
92 | TORONTO BUTTONVILLE A | 1 | 4 | 20 | -4.7 | 22.7 | 0
93 | TORONTO BUTTONVILLE A | 1 | 4 | 21 | -5.74 | 23.74 | 0
94 | TORONTO BUTTONVILLE A | 1 | 4 | 22 | -6.08 | 24.08 | 0
95 | TORONTO BUTTONVILLE A | 1 | 4 | 23 | -6.42 | 24.42 | 0
96 | TORONTO BUTTONVILLE A | 1 | 4 | 24 | -6.5 | 24.5 | 0
97 | TORONTO BUTTONVILLE A | 1 | 5 | 1 | -7 | 25 | 0
98 | TORONTO BUTTONVILLE A | 1 | 5 | 2 | -6.9 | 24.9 | 0
99 | TORONTO BUTTONVILLE A | 1 | 5 | 3 | -6.96 | 24.96 | 0
100 | TORONTO BUTTONVILLE A | 1 | 5 | 4 | -6.86 | 24.86 | 0
101 | TORONTO BUTTONVILLE A | 1 | 5 | 5 | -6.8 | 24.8 | 0
102 | TORONTO BUTTONVILLE A | 1 | 5 | 6 | -6.74 | 24.74 | 0
103 | TORONTO BUTTONVILLE A | 1 | 5 | 7 | -6.62 | 24.62 | 0
104 | TORONTO BUTTONVILLE A | 1 | 5 | 8 | -6.66 | 24.66 | 0
105 | TORONTO BUTTONVILLE A | 1 | 5 | 9 | -6.72 | 24.72 | 0
106 | TORONTO BUTTONVILLE A | 1 | 5 | 10 | -6.32 | 24.32 | 0
107 | TORONTO BUTTONVILLE A | 1 | 5 | 11 | -5.88 | 23.88 | 0
108 | TORONTO BUTTONVILLE A | 1 | 5 | 12 | -5.4 | 23.4 | 0
109 | TORONTO BUTTONVILLE A | 1 | 5 | 13 | -4.96 | 22.96 | 0
110 | TORONTO BUTTONVILLE A | 1 | 5 | 14 | -4.58 | 22.58 | 0
111 | TORONTO BUTTONVILLE A | 1 | 5 | 15 | -4.42 | 22.42 | 0
112 | TORONTO BUTTONVILLE A | 1 | 5 | 16 | -4.24 | 22.24 | 0
113 | TORONTO BUTTONVILLE A | 1 | 5 | 17 | -4.34 | 22.34 | 0
114 | TORONTO BUTTONVILLE A | 1 | 5 | 18 | -4.88 | 22.88 | 0
115 | TORONTO BUTTONVILLE A | 1 | 5 | 19 | -5.26 | 23.26 | 0
116 | TORONTO BUTTONVILLE A | 1 | 5 | 20 | -5.62 | 23.62 | 0
117 | TORONTO BUTTONVILLE A | 1 | 5 | 21 | -5.82 | 23.82 | 0
118 | TORONTO BUTTONVILLE A | 1 | 5 | 22 | -5.88 | 23.88 | 0
119 | TORONTO BUTTONVILLE A | 1 | 5 | 23 | -6.12 | 24.12 | 0
120 | TORONTO BUTTONVILLE A | 1 | 5 | 24 | -6.38 | 24.38 | 0
121 | TORONTO BUTTONVILLE A | 1 | 6 | 1 | -6.54 | 24.54 | 0
122 | TORONTO BUTTONVILLE A | 1 | 6 | 2 | -6.56 | 24.56 | 0
123 | TORONTO BUTTONVILLE A | 1 | 6 | 3 | -6.58 | 24.58 | 0
124 | TORONTO BUTTONVILLE A | 1 | 6 | 4 | -6.88 | 24.88 | 0
125 | TORONTO BUTTONVILLE A | 1 | 6 | 5 | -7.1 | 25.1 | 0
126 | TORONTO BUTTONVILLE A | 1 | 6 | 6 | -7.3 | 25.3 | 0
127 | TORONTO BUTTONVILLE A | 1 | 6 | 7 | -7.5 | 25.5 | 0
128 | TORONTO BUTTONVILLE A | 1 | 6 | 8 | -7.6 | 25.6 | 0
129 | TORONTO BUTTONVILLE A | 1 | 6 | 9 | -7.72 | 25.72 | 0
130 | TORONTO BUTTONVILLE A | 1 | 6 | 10 | -7.34 | 25.34 | 0
131 | TORONTO BUTTONVILLE A | 1 | 6 | 11 | -6.8 | 24.8 | 0
132 | TORONTO BUTTONVILLE A | 1 | 6 | 12 | -6.06 | 24.06 | 0
133 | TORONTO BUTTONVILLE A | 1 | 6 | 13 | -5.74 | 23.74 | 0
134 | TORONTO BUTTONVILLE A | 1 | 6 | 14 | -5.52 | 23.52 | 0
135 | TORONTO BUTTONVILLE A | 1 | 6 | 15 | -5.3 | 23.3 | 0
136 | TORONTO BUTTONVILLE A | 1 | 6 | 16 | -5.22 | 23.22 | 0
137 | TORONTO BUTTONVILLE A | 1 | 6 | 17 | -5.54 | 23.54 | 0
138 | TORONTO BUTTONVILLE A | 1 | 6 | 18 | -5.92 | 23.92 | 0
139 | TORONTO BUTTONVILLE A | 1 | 6 | 19 | -6.8 | 24.8 | 0
140 | TORONTO BUTTONVILLE A | 1 | 6 | 20 | -7.22 | 25.22 | 0
141 | TORONTO BUTTONVILLE A | 1 | 6 | 21 | -7.66 | 25.66 | 0
142 | TORONTO BUTTONVILLE A | 1 | 6 | 22 | -7.98 | 25.98 | 0
143 | TORONTO BUTTONVILLE A | 1 | 6 | 23 | -8.1 | 26.1 | 0
144 | TORONTO BUTTONVILLE A | 1 | 6 | 24 | -8.62 | 26.62 | 0
145 | TORONTO BUTTONVILLE A | 1 | 7 | 1 | -9.16 | 27.16 | 0
146 | TORONTO BUTTONVILLE A | 1 | 7 | 2 | -9.28 | 27.28 | 0
147 | TORONTO BUTTONVILLE A | 1 | 7 | 3 | -9.4 | 27.4 | 0
148 | TORONTO BUTTONVILLE A | 1 | 7 | 4 | -9.54 | 27.54 | 0
149 | TORONTO BUTTONVILLE A | 1 | 7 | 5 | -9.74 | 27.74 | 0
150 | TORONTO BUTTONVILLE A | 1 | 7 | 6 | -9.74 | 27.74 | 0
151 | TORONTO BUTTONVILLE A | 1 | 7 | 7 | -9.9 | 27.9 | 0
152 | TORONTO BUTTONVILLE A | 1 | 7 | 8 | -9.74 | 27.74 | 0
153 | TORONTO BUTTONVILLE A | 1 | 7 | 9 | -9.58 | 27.58 | 0
154 | TORONTO BUTTONVILLE A | 1 | 7 | 10 | -8.58 | 26.58 | 0
155 | TORONTO BUTTONVILLE A | 1 | 7 | 11 | -7.76 | 25.76 | 0
156 | TORONTO BUTTONVILLE A | 1 | 7 | 12 | -5.66 | 23.66 | 0
157 | TORONTO BUTTONVILLE A | 1 | 7 | 13 | -5.16 | 23.16 | 0
158 | TORONTO BUTTONVILLE A | 1 | 7 | 14 | -4.48 | 22.48 | 0
159 | TORONTO BUTTONVILLE A | 1 | 7 | 15 | -4.26 | 22.26 | 0
160 | TORONTO BUTTONVILLE A | 1 | 7 | 16 | -3.82 | 21.82 | 0
161 | TORONTO BUTTONVILLE A | 1 | 7 | 17 | -4.02 | 22.02 | 0
162 | TORONTO BUTTONVILLE A | 1 | 7 | 18 | -4.3 | 22.3 | 0
163 | TORONTO BUTTONVILLE A | 1 | 7 | 19 | -4.5 | 22.5 | 0
164 | TORONTO BUTTONVILLE A | 1 | 7 | 20 | -4.46 | 22.46 | 0
165 | TORONTO BUTTONVILLE A | 1 | 7 | 21 | -4.32 | 22.32 | 0
166 | TORONTO BUTTONVILLE A | 1 | 7 | 22 | -4.28 | 22.28 | 0
167 | TORONTO BUTTONVILLE A | 1 | 7 | 23 | -4.22 | 22.22 | 0
168 | TORONTO BUTTONVILLE A | 1 | 7 | 24 | -4.36 | 22.36 | 0
169 | TORONTO BUTTONVILLE A | 1 | 8 | 1 | -4.38 | 22.38 | 0
170 | TORONTO BUTTONVILLE A | 1 | 8 | 2 | -4.42 | 22.42 | 0
171 | TORONTO BUTTONVILLE A | 1 | 8 | 3 | -4.48 | 22.48 | 0
172 | TORONTO BUTTONVILLE A | 1 | 8 | 4 | -3.6 | 21.6 | 0
173 | TORONTO BUTTONVILLE A | 1 | 8 | 5 | -3.36 | 21.36 | 0
174 | TORONTO BUTTONVILLE A | 1 | 8 | 6 | -3.5 | 21.5 | 0
175 | TORONTO BUTTONVILLE A | 1 | 8 | 7 | -4 | 22 | 0
176 | TORONTO BUTTONVILLE A | 1 | 8 | 8 | -4.52 | 22.52 | 0
177 | TORONTO BUTTONVILLE A | 1 | 8 | 9 | -4.76 | 22.76 | 0
178 | TORONTO BUTTONVILLE A | 1 | 8 | 10 | -4.42 | 22.42 | 0
179 | TORONTO BUTTONVILLE A | 1 | 8 | 11 | -3.94 | 21.94 | 0
180 | TORONTO BUTTONVILLE A | 1 | 8 | 12 | -3.44 | 21.44 | 0
181 | TORONTO BUTTONVILLE A | 1 | 8 | 13 | -3.22 | 21.22 | 0
182 | TORONTO BUTTONVILLE A | 1 | 8 | 14 | -3.1 | 21.1 | 0
183 | TORONTO BUTTONVILLE A | 1 | 8 | 15 | -2.92 | 20.92 | 0
184 | TORONTO BUTTONVILLE A | 1 | 8 | 16 | -2.98 | 20.98 | 0
185 | TORONTO BUTTONVILLE A | 1 | 8 | 17 | -3.38 | 21.38 | 0
186 | TORONTO BUTTONVILLE A | 1 | 8 | 18 | -4.02 | 22.02 | 0
187 | TORONTO BUTTONVILLE A | 1 | 8 | 19 | -4.4 | 22.4 | 0
188 | TORONTO BUTTONVILLE A | 1 | 8 | 20 | -4.44 | 22.44 | 0
189 | TORONTO BUTTONVILLE A | 1 | 8 | 21 | -4.34 | 22.34 | 0
190 | TORONTO BUTTONVILLE A | 1 | 8 | 22 | -4.28 | 22.28 | 0
191 | TORONTO BUTTONVILLE A | 1 | 8 | 23 | -4.1 | 22.1 | 0
192 | TORONTO BUTTONVILLE A | 1 | 8 | 24 | -4.04 | 22.04 | 0
193 | TORONTO BUTTONVILLE A | 1 | 9 | 1 | -4.3 | 22.3 | 0
194 | TORONTO BUTTONVILLE A | 1 | 9 | 2 | -4.44 | 22.44 | 0
195 | TORONTO BUTTONVILLE A | 1 | 9 | 3 | -4.56 | 22.56 | 0
196 | TORONTO BUTTONVILLE A | 1 | 9 | 4 | -4.9 | 22.9 | 0
197 | TORONTO BUTTONVILLE A | 1 | 9 | 5 | -5.26 | 23.26 | 0
198 | TORONTO BUTTONVILLE A | 1 | 9 | 6 | -5.56 | 23.56 | 0
199 | TORONTO BUTTONVILLE A | 1 | 9 | 7 | -5.66 | 23.66 | 0
200 | TORONTO BUTTONVILLE A | 1 | 9 | 8 | -5.68 | 23.68 | 0
201 | TORONTO BUTTONVILLE A | 1 | 9 | 9 | -5.38 | 23.38 | 0
202 | TORONTO BUTTONVILLE A | 1 | 9 | 10 | -4.96 | 22.96 | 0
203 | TORONTO BUTTONVILLE A | 1 | 9 | 11 | -4.52 | 22.52 | 0
204 | TORONTO BUTTONVILLE A | 1 | 9 | 12 | -3.64 | 21.64 | 0
205 | TORONTO BUTTONVILLE A | 1 | 9 | 13 | -2.54 | 20.54 | 0
206 | TORONTO BUTTONVILLE A | 1 | 9 | 14 | -1.96 | 19.96 | 0
207 | TORONTO BUTTONVILLE A | 1 | 9 | 15 | -1.98 | 19.98 | 0
208 | TORONTO BUTTONVILLE A | 1 | 9 | 16 | -1.76 | 19.76 | 0
209 | TORONTO BUTTONVILLE A | 1 | 9 | 17 | -2.06 | 20.06 | 0
210 | TORONTO BUTTONVILLE A | 1 | 9 | 18 | -2.44 | 20.44 | 0
211 | TORONTO BUTTONVILLE A | 1 | 9 | 19 | -2.74 | 20.74 | 0
212 | TORONTO BUTTONVILLE A | 1 | 9 | 20 | -2.68 | 20.68 | 0
213 | TORONTO BUTTONVILLE A | 1 | 9 | 21 | -2.66 | 20.66 | 0
214 | TORONTO BUTTONVILLE A | 1 | 9 | 22 | -2.62 | 20.62 | 0
215 | TORONTO BUTTONVILLE A | 1 | 9 | 23 | -2.82 | 20.82 | 0
216 | TORONTO BUTTONVILLE A | 1 | 9 | 24 | -2.6 | 20.6 | 0
217 | TORONTO BUTTONVILLE A | 1 | 10 | 1 | -2.46 | 20.46 | 0
218 | TORONTO BUTTONVILLE A | 1 | 10 | 2 | -2.24 | 20.24 | 0
219 | TORONTO BUTTONVILLE A | 1 | 10 | 3 | -2.32 | 20.32 | 0
220 | TORONTO BUTTONVILLE A | 1 | 10 | 4 | -2.32 | 20.32 | 0
221 | TORONTO BUTTONVILLE A | 1 | 10 | 5 | -1.94 | 19.94 | 0
222 | TORONTO BUTTONVILLE A | 1 | 10 | 6 | -2.38 | 20.38 | 0
223 | TORONTO BUTTONVILLE A | 1 | 10 | 7 | -2.08 | 20.08 | 0
224 | TORONTO BUTTONVILLE A | 1 | 10 | 8 | -2.42 | 20.42 | 0
225 | TORONTO BUTTONVILLE A | 1 | 10 | 9 | -2.26 | 20.26 | 0
226 | TORONTO BUTTONVILLE A | 1 | 10 | 10 | -1.8 | 19.8 | 0
227 | TORONTO BUTTONVILLE A | 1 | 10 | 11 | -0.9 | 18.9 | 0
228 | TORONTO BUTTONVILLE A | 1 | 10 | 12 | -0.72 | 18.72 | 0
229 | TORONTO BUTTONVILLE A | 1 | 10 | 13 | -0.18 | 18.18 | 0
230 | TORONTO BUTTONVILLE A | 1 | 10 | 14 | -0.2 | 18.2 | 0
231 | TORONTO BUTTONVILLE A | 1 | 10 | 15 | 1.725 | 16.275 | 0
232 | TORONTO BUTTONVILLE A | 1 | 10 | 16 | -0.12 | 18.12 | 0
233 | TORONTO BUTTONVILLE A | 1 | 10 | 17 | -0.14 | 18.14 | 0
234 | TORONTO BUTTONVILLE A | 1 | 10 | 18 | -0.26 | 18.26 | 0
235 | TORONTO BUTTONVILLE A | 1 | 10 | 19 | -0.52 | 18.52 | 0
236 | TORONTO BUTTONVILLE A | 1 | 10 | 20 | -0.5 | 18.5 | 0
237 | TORONTO BUTTONVILLE A | 1 | 10 | 21 | -0.28 | 18.28 | 0
238 | TORONTO BUTTONVILLE A | 1 | 10 | 22 | -0.24 | 18.24 | 0
239 | TORONTO BUTTONVILLE A | 1 | 10 | 23 | -0.5 | 18.5 | 0
240 | TORONTO BUTTONVILLE A | 1 | 10 | 24 | -0.86 | 18.86 | 0
241 | TORONTO BUTTONVILLE A | 1 | 11 | 1 | -0.74 | 18.74 | 0
242 | TORONTO BUTTONVILLE A | 1 | 11 | 2 | -0.8 | 18.8 | 0
243 | TORONTO BUTTONVILLE A | 1 | 11 | 3 | -1.56 | 19.56 | 0
244 | TORONTO BUTTONVILLE A | 1 | 11 | 4 | -1.4 | 19.4 | 0
245 | TORONTO BUTTONVILLE A | 1 | 11 | 5 | -1.58 | 19.58 | 0
246 | TORONTO BUTTONVILLE A | 1 | 11 | 6 | -1.72 | 19.72 | 0
247 | TORONTO BUTTONVILLE A | 1 | 11 | 7 | -0.7 | 18.7 | 0
248 | TORONTO BUTTONVILLE A | 1 | 11 | 8 | -0.36 | 18.36 | 0
249 | TORONTO BUTTONVILLE A | 1 | 11 | 9 | -0.36 | 18.36 | 0
250 | TORONTO BUTTONVILLE A | 1 | 11 | 10 | 0.02 | 17.98 | 0
251 | TORONTO BUTTONVILLE A | 1 | 11 | 11 | 0.68 | 17.32 | 0
252 | TORONTO BUTTONVILLE A | 1 | 11 | 12 | 1.82 | 16.18 | 0
253 | TORONTO BUTTONVILLE A | 1 | 11 | 13 | 1.28 | 16.72 | 0
254 | TORONTO BUTTONVILLE A | 1 | 11 | 14 | 1.1 | 16.9 | 0
255 | TORONTO BUTTONVILLE A | 1 | 11 | 15 | 1.22 | 16.78 | 0
256 | TORONTO BUTTONVILLE A | 1 | 11 | 16 | 1.48 | 16.52 | 0
257 | TORONTO BUTTONVILLE A | 1 | 11 | 17 | 1.4 | 16.6 | 0
258 | TORONTO BUTTONVILLE A | 1 | 11 | 18 | 0.8 | 17.2 | 0
259 | TORONTO BUTTONVILLE A | 1 | 11 | 19 | 0.6 | 17.4 | 0
260 | TORONTO BUTTONVILLE A | 1 | 11 | 20 | 0.74 | 17.26 | 0
261 | TORONTO BUTTONVILLE A | 1 | 11 | 21 | 0.66 | 17.34 | 0
262 | TORONTO BUTTONVILLE A | 1 | 11 | 22 | 0.74 | 17.26 | 0
263 | TORONTO BUTTONVILLE A | 1 | 11 | 23 | 0.88 | 17.12 | 0
264 | TORONTO BUTTONVILLE A | 1 | 11 | 24 | 0.84 | 17.16 | 0
265 | TORONTO BUTTONVILLE A | 1 | 12 | 1 | 0.64 | 17.36 | 0
266 | TORONTO BUTTONVILLE A | 1 | 12 | 2 | 1.16 | 16.84 | 0
267 | TORONTO BUTTONVILLE A | 1 | 12 | 3 | 1.42 | 16.58 | 0
268 | TORONTO BUTTONVILLE A | 1 | 12 | 4 | 1.68 | 16.32 | 0
269 | TORONTO BUTTONVILLE A | 1 | 12 | 5 | 1.22 | 16.78 | 0
270 | TORONTO BUTTONVILLE A | 1 | 12 | 6 | 1.26 | 16.74 | 0
271 | TORONTO BUTTONVILLE A | 1 | 12 | 7 | 0.32 | 17.68 | 0
272 | TORONTO BUTTONVILLE A | 1 | 12 | 8 | -0.56 | 18.56 | 0
273 | TORONTO BUTTONVILLE A | 1 | 12 | 9 | -1.5 | 19.5 | 0
274 | TORONTO BUTTONVILLE A | 1 | 12 | 10 | -2.46 | 20.46 | 0
275 | TORONTO BUTTONVILLE A | 1 | 12 | 11 | -2.76 | 20.76 | 0
276 | TORONTO BUTTONVILLE A | 1 | 12 | 12 | -2.4 | 20.4 | 0
277 | TORONTO BUTTONVILLE A | 1 | 12 | 13 | -2.78 | 20.78 | 0
278 | TORONTO BUTTONVILLE A | 1 | 12 | 14 | -3.22 | 21.22 | 0
279 | TORONTO BUTTONVILLE A | 1 | 12 | 15 | -4.55 | 22.55 | 0
280 | TORONTO BUTTONVILLE A | 1 | 12 | 16 | -3.64 | 21.64 | 0
281 | TORONTO BUTTONVILLE A | 1 | 12 | 17 | -4.28 | 22.28 | 0
282 | TORONTO BUTTONVILLE A | 1 | 12 | 18 | -4.78 | 22.78 | 0
283 | TORONTO BUTTONVILLE A | 1 | 12 | 19 | -5.08 | 23.08 | 0
284 | TORONTO BUTTONVILLE A | 1 | 12 | 20 | -5.42 | 23.42 | 0
285 | TORONTO BUTTONVILLE A | 1 | 12 | 21 | -5.6 | 23.6 | 0
286 | TORONTO BUTTONVILLE A | 1 | 12 | 22 | -5.78 | 23.78 | 0
287 | TORONTO BUTTONVILLE A | 1 | 12 | 23 | -5.92 | 23.92 | 0
288 | TORONTO BUTTONVILLE A | 1 | 12 | 24 | -6.3 | 24.3 | 0
289 | TORONTO BUTTONVILLE A | 1 | 13 | 1 | -6.52 | 24.52 | 0
290 | TORONTO BUTTONVILLE A | 1 | 13 | 2 | -6.7 | 24.7 | 0
291 | TORONTO BUTTONVILLE A | 1 | 13 | 3 | -6.92 | 24.92 | 0
292 | TORONTO BUTTONVILLE A | 1 | 13 | 4 | -7.14 | 25.14 | 0
293 | TORONTO BUTTONVILLE A | 1 | 13 | 5 | -7.38 | 25.38 | 0
294 | TORONTO BUTTONVILLE A | 1 | 13 | 6 | -7.5 | 25.5 | 0
295 | TORONTO BUTTONVILLE A | 1 | 13 | 7 | -7.48 | 25.48 | 0
296 | TORONTO BUTTONVILLE A | 1 | 13 | 8 | -7.82 | 25.82 | 0
297 | TORONTO BUTTONVILLE A | 1 | 13 | 9 | -7.86 | 25.86 | 0
298 | TORONTO BUTTONVILLE A | 1 | 13 | 10 | -7.48 | 25.48 | 0
299 | TORONTO BUTTONVILLE A | 1 | 13 | 11 | -6.58 | 24.58 | 0
300 | TORONTO BUTTONVILLE A | 1 | 13 | 12 | -5.94 | 23.94 | 0
301 | TORONTO BUTTONVILLE A | 1 | 13 | 13 | -5.28 | 23.28 | 0
302 | TORONTO BUTTONVILLE A | 1 | 13 | 14 | -4.88 | 22.88 | 0
303 | TORONTO BUTTONVILLE A | 1 | 13 | 15 | -4.4 | 22.4 | 0
304 | TORONTO BUTTONVILLE A | 1 | 13 | 16 | -4.3 | 22.3 | 0
305 | TORONTO BUTTONVILLE A | 1 | 13 | 17 | -4.7 | 22.7 | 0
306 | TORONTO BUTTONVILLE A | 1 | 13 | 18 | -5.2 | 23.2 | 0
307 | TORONTO BUTTONVILLE A | 1 | 13 | 19 | -5.4 | 23.4 | 0
308 | TORONTO BUTTONVILLE A | 1 | 13 | 20 | -5.52 | 23.52 | 0
309 | TORONTO BUTTONVILLE A | 1 | 13 | 21 | -5.98 | 23.98 | 0
310 | TORONTO BUTTONVILLE A | 1 | 13 | 22 | -6.46 | 24.46 | 0
311 | TORONTO BUTTONVILLE A | 1 | 13 | 23 | -6.9 | 24.9 | 0
312 | TORONTO BUTTONVILLE A | 1 | 13 | 24 | -7.2 | 25.2 | 0
313 | TORONTO BUTTONVILLE A | 1 | 14 | 1 | -7.44 | 25.44 | 0
314 | TORONTO BUTTONVILLE A | 1 | 14 | 2 | -7.74 | 25.74 | 0
315 | TORONTO BUTTONVILLE A | 1 | 14 | 3 | -7.72 | 25.72 | 0
316 | TORONTO BUTTONVILLE A | 1 | 14 | 4 | -7.7 | 25.7 | 0
317 | TORONTO BUTTONVILLE A | 1 | 14 | 5 | -7.66 | 25.66 | 0
318 | TORONTO BUTTONVILLE A | 1 | 14 | 6 | -7.6 | 25.6 | 0
319 | TORONTO BUTTONVILLE A | 1 | 14 | 7 | -7.5 | 25.5 | 0
320 | TORONTO BUTTONVILLE A | 1 | 14 | 8 | -7.42 | 25.42 | 0
321 | TORONTO BUTTONVILLE A | 1 | 14 | 9 | -7 | 25 | 0
322 | TORONTO BUTTONVILLE A | 1 | 14 | 10 | -6.04 | 24.04 | 0
323 | TORONTO BUTTONVILLE A | 1 | 14 | 11 | -4.82 | 22.82 | 0
324 | TORONTO BUTTONVILLE A | 1 | 14 | 12 | -3.94 | 21.94 | 0
325 | TORONTO BUTTONVILLE A | 1 | 14 | 13 | -2.98 | 20.98 | 0
326 | TORONTO BUTTONVILLE A | 1 | 14 | 14 | -2.58 | 20.58 | 0
327 | TORONTO BUTTONVILLE A | 1 | 14 | 15 | -2.04 | 20.04 | 0
328 | TORONTO BUTTONVILLE A | 1 | 14 | 16 | -1.7 | 19.7 | 0
329 | TORONTO BUTTONVILLE A | 1 | 14 | 17 | -1.76 | 19.76 | 0
330 | TORONTO BUTTONVILLE A | 1 | 14 | 18 | -2.38 | 20.38 | 0
331 | TORONTO BUTTONVILLE A | 1 | 14 | 19 | -2.52 | 20.52 | 0
332 | TORONTO BUTTONVILLE A | 1 | 14 | 20 | -2.88 | 20.88 | 0
333 | TORONTO BUTTONVILLE A | 1 | 14 | 21 | -2.9 | 20.9 | 0
334 | TORONTO BUTTONVILLE A | 1 | 14 | 22 | -2.88 | 20.88 | 0
335 | TORONTO BUTTONVILLE A | 1 | 14 | 23 | -3 | 21 | 0
336 | TORONTO BUTTONVILLE A | 1 | 14 | 24 | -2.86 | 20.86 | 0
337 | TORONTO BUTTONVILLE A | 1 | 15 | 1 | -2.86 | 20.86 | 0
338 | TORONTO BUTTONVILLE A | 1 | 15 | 2 | -2.9 | 20.9 | 0
339 | TORONTO BUTTONVILLE A | 1 | 15 | 3 | -2.94 | 20.94 | 0
340 | TORONTO BUTTONVILLE A | 1 | 15 | 4 | -3 | 21 | 0
341 | TORONTO BUTTONVILLE A | 1 | 15 | 5 | -2.68 | 20.68 | 0
342 | TORONTO BUTTONVILLE A | 1 | 15 | 6 | -2.36 | 20.36 | 0
343 | TORONTO BUTTONVILLE A | 1 | 15 | 7 | -2.34 | 20.34 | 0
344 | TORONTO BUTTONVILLE A | 1 | 15 | 8 | -2.52 | 20.52 | 0
345 | TORONTO BUTTONVILLE A | 1 | 15 | 9 | -2.72 | 20.72 | 0
346 | TORONTO BUTTONVILLE A | 1 | 15 | 10 | -2.56 | 20.56 | 0
347 | TORONTO BUTTONVILLE A | 1 | 15 | 11 | -2.06 | 20.06 | 0
348 | TORONTO BUTTONVILLE A | 1 | 15 | 12 | -1.72 | 19.72 | 0
349 | TORONTO BUTTONVILLE A | 1 | 15 | 13 | -1.26 | 19.26 | 0
350 | TORONTO BUTTONVILLE A | 1 | 15 | 14 | -1.16 | 19.16 | 0
351 | TORONTO BUTTONVILLE A | 1 | 15 | 15 | -1.06 | 19.06 | 0
352 | TORONTO BUTTONVILLE A | 1 | 15 | 16 | -0.9 | 18.9 | 0
353 | TORONTO BUTTONVILLE A | 1 | 15 | 17 | -1.14 | 19.14 | 0
354 | TORONTO BUTTONVILLE A | 1 | 15 | 18 | -1.42 | 19.42 | 0
355 | TORONTO BUTTONVILLE A | 1 | 15 | 19 | -1.56 | 19.56 | 0
356 | TORONTO BUTTONVILLE A | 1 | 15 | 20 | -1.8 | 19.8 | 0
357 | TORONTO BUTTONVILLE A | 1 | 15 | 21 | -2.1 | 20.1 | 0
358 | TORONTO BUTTONVILLE A | 1 | 15 | 22 | -2.46 | 20.46 | 0
359 | TORONTO BUTTONVILLE A | 1 | 15 | 23 | -2.54 | 20.54 | 0
360 | TORONTO BUTTONVILLE A | 1 | 15 | 24 | -2.62 | 20.62 | 0
361 | TORONTO BUTTONVILLE A | 1 | 16 | 1 | -2.5 | 20.5 | 0
362 | TORONTO BUTTONVILLE A | 1 | 16 | 2 | -2.94 | 20.94 | 0
363 | TORONTO BUTTONVILLE A | 1 | 16 | 3 | -3.16 | 21.16 | 0
364 | TORONTO BUTTONVILLE A | 1 | 16 | 4 | -3.18 | 21.18 | 0
365 | TORONTO BUTTONVILLE A | 1 | 16 | 5 | -3.34 | 21.34 | 0
366 | TORONTO BUTTONVILLE A | 1 | 16 | 6 | -3.38 | 21.38 | 0
367 | TORONTO BUTTONVILLE A | 1 | 16 | 7 | -3.4 | 21.4 | 0
368 | TORONTO BUTTONVILLE A | 1 | 16 | 8 | -3.38 | 21.38 | 0
369 | TORONTO BUTTONVILLE A | 1 | 16 | 9 | -3.36 | 21.36 | 0
370 | TORONTO BUTTONVILLE A | 1 | 16 | 10 | -2.68 | 20.68 | 0
371 | TORONTO BUTTONVILLE A | 1 | 16 | 11 | -2.16 | 20.16 | 0
372 | TORONTO BUTTONVILLE A | 1 | 16 | 12 | -1.78 | 19.78 | 0
373 | TORONTO BUTTONVILLE A | 1 | 16 | 13 | -1.32 | 19.32 | 0
374 | TORONTO BUTTONVILLE A | 1 | 16 | 14 | -1.1 | 19.1 | 0
375 | TORONTO BUTTONVILLE A | 1 | 16 | 15 | -1.3 | 19.3 | 0
376 | TORONTO BUTTONVILLE A | 1 | 16 | 16 | -1.5 | 19.5 | 0
377 | TORONTO BUTTONVILLE A | 1 | 16 | 17 | -2.12 | 20.12 | 0
378 | TORONTO BUTTONVILLE A | 1 | 16 | 18 | -2.82 | 20.82 | 0
379 | TORONTO BUTTONVILLE A | 1 | 16 | 19 | -3.5 | 21.5 | 0
380 | TORONTO BUTTONVILLE A | 1 | 16 | 20 | -3.94 | 21.94 | 0
381 | TORONTO BUTTONVILLE A | 1 | 16 | 21 | -4.76 | 22.76 | 0
382 | TORONTO BUTTONVILLE A | 1 | 16 | 22 | -5.48 | 23.48 | 0
383 | TORONTO BUTTONVILLE A | 1 | 16 | 23 | -5.58 | 23.58 | 0
384 | TORONTO BUTTONVILLE A | 1 | 16 | 24 | -6.32 | 24.32 | 0
385 | TORONTO BUTTONVILLE A | 1 | 17 | 1 | -6.92 | 24.92 | 0
386 | TORONTO BUTTONVILLE A | 1 | 17 | 2 | -7.38 | 25.38 | 0
387 | TORONTO BUTTONVILLE A | 1 | 17 | 3 | -7.74 | 25.74 | 0
388 | TORONTO BUTTONVILLE A | 1 | 17 | 4 | -7.9 | 25.9 | 0
389 | TORONTO BUTTONVILLE A | 1 | 17 | 5 | -7.98 | 25.98 | 0
390 | TORONTO BUTTONVILLE A | 1 | 17 | 6 | -7.84 | 25.84 | 0
391 | TORONTO BUTTONVILLE A | 1 | 17 | 7 | -8.16 | 26.16 | 0
392 | TORONTO BUTTONVILLE A | 1 | 17 | 8 | -8.36 | 26.36 | 0
393 | TORONTO BUTTONVILLE A | 1 | 17 | 9 | -8.36 | 26.36 | 0
394 | TORONTO BUTTONVILLE A | 1 | 17 | 10 | -7.5 | 25.5 | 0
395 | TORONTO BUTTONVILLE A | 1 | 17 | 11 | -6.28 | 24.28 | 0
396 | TORONTO BUTTONVILLE A | 1 | 17 | 12 | -5.36 | 23.36 | 0
397 | TORONTO BUTTONVILLE A | 1 | 17 | 13 | -4.72 | 22.72 | 0
398 | TORONTO BUTTONVILLE A | 1 | 17 | 14 | -4.38 | 22.38 | 0
399 | TORONTO BUTTONVILLE A | 1 | 17 | 15 | -4.18 | 22.18 | 0
400 | TORONTO BUTTONVILLE A | 1 | 17 | 16 | -4.12 | 22.12 | 0
401 | TORONTO BUTTONVILLE A | 1 | 17 | 17 | -4.06 | 22.06 | 0
402 | TORONTO BUTTONVILLE A | 1 | 17 | 18 | -4.28 | 22.28 | 0
403 | TORONTO BUTTONVILLE A | 1 | 17 | 19 | -4.44 | 22.44 | 0
404 | TORONTO BUTTONVILLE A | 1 | 17 | 20 | -4.78 | 22.78 | 0
405 | TORONTO BUTTONVILLE A | 1 | 17 | 21 | -4.88 | 22.88 | 0
406 | TORONTO BUTTONVILLE A | 1 | 17 | 22 | -4.76 | 22.76 | 0
407 | TORONTO BUTTONVILLE A | 1 | 17 | 23 | -4.78 | 22.78 | 0
408 | TORONTO BUTTONVILLE A | 1 | 17 | 24 | -4.92 | 22.92 | 0
409 | TORONTO BUTTONVILLE A | 1 | 18 | 1 | -4.9 | 22.9 | 0
410 | TORONTO BUTTONVILLE A | 1 | 18 | 2 | -4.92 | 22.92 | 0
411 | TORONTO BUTTONVILLE A | 1 | 18 | 3 | -5.06 | 23.06 | 0
412 | TORONTO BUTTONVILLE A | 1 | 18 | 4 | -5.1 | 23.1 | 0
413 | TORONTO BUTTONVILLE A | 1 | 18 | 5 | -5.16 | 23.16 | 0
414 | TORONTO BUTTONVILLE A | 1 | 18 | 6 | -4.78 | 22.78 | 0
415 | TORONTO BUTTONVILLE A | 1 | 18 | 7 | -4.46 | 22.46 | 0
416 | TORONTO BUTTONVILLE A | 1 | 18 | 8 | -4.3 | 22.3 | 0
417 | TORONTO BUTTONVILLE A | 1 | 18 | 9 | -4.14 | 22.14 | 0
418 | TORONTO BUTTONVILLE A | 1 | 18 | 10 | -3.8 | 21.8 | 0
419 | TORONTO BUTTONVILLE A | 1 | 18 | 11 | -3.04 | 21.04 | 0
420 | TORONTO BUTTONVILLE A | 1 | 18 | 12 | -2.64 | 20.64 | 0
421 | TORONTO BUTTONVILLE A | 1 | 18 | 13 | -2.18 | 20.18 | 0
422 | TORONTO BUTTONVILLE A | 1 | 18 | 14 | -1.94 | 19.94 | 0
423 | TORONTO BUTTONVILLE A | 1 | 18 | 15 | -1.7 | 19.7 | 0
424 | TORONTO BUTTONVILLE A | 1 | 18 | 16 | -1.58 | 19.58 | 0
425 | TORONTO BUTTONVILLE A | 1 | 18 | 17 | -1.36 | 19.36 | 0
426 | TORONTO BUTTONVILLE A | 1 | 18 | 18 | -1.54 | 19.54 | 0
427 | TORONTO BUTTONVILLE A | 1 | 18 | 19 | -1.82 | 19.82 | 0
428 | TORONTO BUTTONVILLE A | 1 | 18 | 20 | -1.86 | 19.86 | 0
429 | TORONTO BUTTONVILLE A | 1 | 18 | 21 | -2 | 20 | 0
430 | TORONTO BUTTONVILLE A | 1 | 18 | 22 | -1.8 | 19.8 | 0
431 | TORONTO BUTTONVILLE A | 1 | 18 | 23 | -1.78 | 19.78 | 0
432 | TORONTO BUTTONVILLE A | 1 | 18 | 24 | -2.34 | 20.34 | 0
433 | TORONTO BUTTONVILLE A | 1 | 19 | 1 | -3 | 21 | 0
434 | TORONTO BUTTONVILLE A | 1 | 19 | 2 | -3.44 | 21.44 | 0
435 | TORONTO BUTTONVILLE A | 1 | 19 | 3 | -3.4 | 21.4 | 0
436 | TORONTO BUTTONVILLE A | 1 | 19 | 4 | -3.52 | 21.52 | 0
437 | TORONTO BUTTONVILLE A | 1 | 19 | 5 | -3.48 | 21.48 | 0
438 | TORONTO BUTTONVILLE A | 1 | 19 | 6 | -3.5 | 21.5 | 0
439 | TORONTO BUTTONVILLE A | 1 | 19 | 7 | -3.66 | 21.66 | 0
440 | TORONTO BUTTONVILLE A | 1 | 19 | 8 | -4.22 | 22.22 | 0
441 | TORONTO BUTTONVILLE A | 1 | 19 | 9 | -4.46 | 22.46 | 0
442 | TORONTO BUTTONVILLE A | 1 | 19 | 10 | -4.48 | 22.48 | 0
443 | TORONTO BUTTONVILLE A | 1 | 19 | 11 | -4.72 | 22.72 | 0
444 | TORONTO BUTTONVILLE A | 1 | 19 | 12 | -4.84 | 22.84 | 0
445 | TORONTO BUTTONVILLE A | 1 | 19 | 13 | -4.44 | 22.44 | 0
446 | TORONTO BUTTONVILLE A | 1 | 19 | 14 | -4.34 | 22.34 | 0
447 | TORONTO BUTTONVILLE A | 1 | 19 | 15 | -4.28 | 22.28 | 0
448 | TORONTO BUTTONVILLE A | 1 | 19 | 16 | -4.36 | 22.36 | 0
449 | TORONTO BUTTONVILLE A | 1 | 19 | 17 | -4.54 | 22.54 | 0
450 | TORONTO BUTTONVILLE A | 1 | 19 | 18 | -5.02 | 23.02 | 0
451 | TORONTO BUTTONVILLE A | 1 | 19 | 19 | -5.2 | 23.2 | 0
452 | TORONTO BUTTONVILLE A | 1 | 19 | 20 | -5.34 | 23.34 | 0
453 | TORONTO BUTTONVILLE A | 1 | 19 | 21 | -5.26 | 23.26 | 0
454 | TORONTO BUTTONVILLE A | 1 | 19 | 22 | -5.26 | 23.26 | 0
455 | TORONTO BUTTONVILLE A | 1 | 19 | 23 | -5.32 | 23.32 | 0
456 | TORONTO BUTTONVILLE A | 1 | 19 | 24 | -5.68 | 23.68 | 0
457 | TORONTO BUTTONVILLE A | 1 | 20 | 1 | -5.9 | 23.9 | 0
458 | TORONTO BUTTONVILLE A | 1 | 20 | 2 | -6.28 | 24.28 | 0
459 | TORONTO BUTTONVILLE A | 1 | 20 | 3 | -6.62 | 24.62 | 0
460 | TORONTO BUTTONVILLE A | 1 | 20 | 4 | -6.88 | 24.88 | 0
461 | TORONTO BUTTONVILLE A | 1 | 20 | 5 | -7.1 | 25.1 | 0
462 | TORONTO BUTTONVILLE A | 1 | 20 | 6 | -7.2 | 25.2 | 0
463 | TORONTO BUTTONVILLE A | 1 | 20 | 7 | -7.22 | 25.22 | 0
464 | TORONTO BUTTONVILLE A | 1 | 20 | 8 | -7.56 | 25.56 | 0
465 | TORONTO BUTTONVILLE A | 1 | 20 | 9 | -7.72 | 25.72 | 0
466 | TORONTO BUTTONVILLE A | 1 | 20 | 10 | -7.1 | 25.1 | 0
467 | TORONTO BUTTONVILLE A | 1 | 20 | 11 | -6.5 | 24.5 | 0
468 | TORONTO BUTTONVILLE A | 1 | 20 | 12 | -5.84 | 23.84 | 0
469 | TORONTO BUTTONVILLE A | 1 | 20 | 13 | -5.38 | 23.38 | 0
470 | TORONTO BUTTONVILLE A | 1 | 20 | 14 | -4.84 | 22.84 | 0
471 | TORONTO BUTTONVILLE A | 1 | 20 | 15 | -4.3 | 22.3 | 0
472 | TORONTO BUTTONVILLE A | 1 | 20 | 16 | -3.88 | 21.88 | 0
473 | TORONTO BUTTONVILLE A | 1 | 20 | 17 | -3.94 | 21.94 | 0
474 | TORONTO BUTTONVILLE A | 1 | 20 | 18 | -4.46 | 22.46 | 0
475 | TORONTO BUTTONVILLE A | 1 | 20 | 19 | -4.84 | 22.84 | 0
476 | TORONTO BUTTONVILLE A | 1 | 20 | 20 | -5.22 | 23.22 | 0
477 | TORONTO BUTTONVILLE A | 1 | 20 | 21 | -5.84 | 23.84 | 0
478 | TORONTO BUTTONVILLE A | 1 | 20 | 22 | -6.34 | 24.34 | 0
479 | TORONTO BUTTONVILLE A | 1 | 20 | 23 | -6.58 | 24.58 | 0
480 | TORONTO BUTTONVILLE A | 1 | 20 | 24 | -6.62 | 24.62 | 0
481 | TORONTO BUTTONVILLE A | 1 | 21 | 1 | -6.7 | 24.7 | 0
482 | TORONTO BUTTONVILLE A | 1 | 21 | 2 | -7.06 | 25.06 | 0
483 | TORONTO BUTTONVILLE A | 1 | 21 | 3 | -7.3 | 25.3 | 0
484 | TORONTO BUTTONVILLE A | 1 | 21 | 4 | -7.36 | 25.36 | 0
485 | TORONTO BUTTONVILLE A | 1 | 21 | 5 | -7.44 | 25.44 | 0
486 | TORONTO BUTTONVILLE A | 1 | 21 | 6 | -7.86 | 25.86 | 0
487 | TORONTO BUTTONVILLE A | 1 | 21 | 7 | -7.7 | 25.7 | 0
488 | TORONTO BUTTONVILLE A | 1 | 21 | 8 | -7.3 | 25.3 | 0
489 | TORONTO BUTTONVILLE A | 1 | 21 | 9 | -6.88 | 24.88 | 0
490 | TORONTO BUTTONVILLE A | 1 | 21 | 10 | -5.96 | 23.96 | 0
491 | TORONTO BUTTONVILLE A | 1 | 21 | 11 | -4.38 | 22.38 | 0
492 | TORONTO BUTTONVILLE A | 1 | 21 | 12 | -2.98 | 20.98 | 0
493 | TORONTO BUTTONVILLE A | 1 | 21 | 13 | -2.06 | 20.06 | 0
494 | TORONTO BUTTONVILLE A | 1 | 21 | 14 | -1.5 | 19.5 | 0
495 | TORONTO BUTTONVILLE A | 1 | 21 | 15 | -1.26 | 19.26 | 0
496 | TORONTO BUTTONVILLE A | 1 | 21 | 16 | -0.88 | 18.88 | 0
497 | TORONTO BUTTONVILLE A | 1 | 21 | 17 | -0.94 | 18.94 | 0
498 | TORONTO BUTTONVILLE A | 1 | 21 | 18 | -1.7 | 19.7 | 0
499 | TORONTO BUTTONVILLE A | 1 | 21 | 19 | -2.3 | 20.3 | 0
500 | TORONTO BUTTONVILLE A | 1 | 21 | 20 | -2.5 | 20.5 | 0
501 | TORONTO BUTTONVILLE A | 1 | 21 | 21 | -2.6 | 20.6 | 0
502 | TORONTO BUTTONVILLE A | 1 | 21 | 22 | -2.9 | 20.9 | 0
503 | TORONTO BUTTONVILLE A | 1 | 21 | 23 | -3.36 | 21.36 | 0
504 | TORONTO BUTTONVILLE A | 1 | 21 | 24 | -3.66 | 21.66 | 0
505 | TORONTO BUTTONVILLE A | 1 | 22 | 1 | -3.9 | 21.9 | 0
506 | TORONTO BUTTONVILLE A | 1 | 22 | 2 | -3.92 | 21.92 | 0
507 | TORONTO BUTTONVILLE A | 1 | 22 | 3 | -3.9 | 21.9 | 0
508 | TORONTO BUTTONVILLE A | 1 | 22 | 4 | -3.62 | 21.62 | 0
509 | TORONTO BUTTONVILLE A | 1 | 22 | 5 | -4.16 | 22.16 | 0
510 | TORONTO BUTTONVILLE A | 1 | 22 | 6 | -4.18 | 22.18 | 0
511 | TORONTO BUTTONVILLE A | 1 | 22 | 7 | -4.42 | 22.42 | 0
512 | TORONTO BUTTONVILLE A | 1 | 22 | 8 | -4.62 | 22.62 | 0
513 | TORONTO BUTTONVILLE A | 1 | 22 | 9 | -4.44 | 22.44 | 0
514 | TORONTO BUTTONVILLE A | 1 | 22 | 10 | -3.88 | 21.88 | 0
515 | TORONTO BUTTONVILLE A | 1 | 22 | 11 | -2.86 | 20.86 | 0
516 | TORONTO BUTTONVILLE A | 1 | 22 | 12 | -2.16 | 20.16 | 0
517 | TORONTO BUTTONVILLE A | 1 | 22 | 13 | -1.32 | 19.32 | 0
518 | TORONTO BUTTONVILLE A | 1 | 22 | 14 | -1.04 | 19.04 | 0
519 | TORONTO BUTTONVILLE A | 1 | 22 | 15 | -1.1 | 19.1 | 0
520 | TORONTO BUTTONVILLE A | 1 | 22 | 16 | -0.9 | 18.9 | 0
521 | TORONTO BUTTONVILLE A | 1 | 22 | 17 | -1.02 | 19.02 | 0
522 | TORONTO BUTTONVILLE A | 1 | 22 | 18 | -1.06 | 19.06 | 0
523 | TORONTO BUTTONVILLE A | 1 | 22 | 19 | -1.14 | 19.14 | 0
524 | TORONTO BUTTONVILLE A | 1 | 22 | 20 | -1.28 | 19.28 | 0
525 | TORONTO BUTTONVILLE A | 1 | 22 | 21 | -1.5 | 19.5 | 0
526 | TORONTO BUTTONVILLE A | 1 | 22 | 22 | -1.62 | 19.62 | 0
527 | TORONTO BUTTONVILLE A | 1 | 22 | 23 | -1.86 | 19.86 | 0
528 | TORONTO BUTTONVILLE A | 1 | 22 | 24 | -1.86 | 19.86 | 0
529 | TORONTO BUTTONVILLE A | 1 | 23 | 1 | -1.84 | 19.84 | 0
530 | TORONTO BUTTONVILLE A | 1 | 23 | 2 | -2.06 | 20.06 | 0
531 | TORONTO BUTTONVILLE A | 1 | 23 | 3 | -2.52 | 20.52 | 0
532 | TORONTO BUTTONVILLE A | 1 | 23 | 4 | -2.58 | 20.58 | 0
533 | TORONTO BUTTONVILLE A | 1 | 23 | 5 | -2.88 | 20.88 | 0
534 | TORONTO BUTTONVILLE A | 1 | 23 | 6 | -3.32 | 21.32 | 0
535 | TORONTO BUTTONVILLE A | 1 | 23 | 7 | -3.56 | 21.56 | 0
536 | TORONTO BUTTONVILLE A | 1 | 23 | 8 | -3.32 | 21.32 | 0
537 | TORONTO BUTTONVILLE A | 1 | 23 | 9 | -3.08 | 21.08 | 0
538 | TORONTO BUTTONVILLE A | 1 | 23 | 10 | -2.58 | 20.58 | 0
539 | TORONTO BUTTONVILLE A | 1 | 23 | 11 | -1.48 | 19.48 | 0
540 | TORONTO BUTTONVILLE A | 1 | 23 | 12 | 0.02 | 17.98 | 0
541 | TORONTO BUTTONVILLE A | 1 | 23 | 13 | 0.82 | 17.18 | 0
542 | TORONTO BUTTONVILLE A | 1 | 23 | 14 | 1.4 | 16.6 | 0
543 | TORONTO BUTTONVILLE A | 1 | 23 | 15 | 1.48 | 16.52 | 0
544 | TORONTO BUTTONVILLE A | 1 | 23 | 16 | 1.52 | 16.48 | 0
545 | TORONTO BUTTONVILLE A | 1 | 23 | 17 | 1.34 | 16.66 | 0
546 | TORONTO BUTTONVILLE A | 1 | 23 | 18 | 0.96 | 17.04 | 0
547 | TORONTO BUTTONVILLE A | 1 | 23 | 19 | 0.48 | 17.52 | 0
548 | TORONTO BUTTONVILLE A | 1 | 23 | 20 | -0.04 | 18.04 | 0
549 | TORONTO BUTTONVILLE A | 1 | 23 | 21 | -0.42 | 18.42 | 0
550 | TORONTO BUTTONVILLE A | 1 | 23 | 22 | -0.8 | 18.8 | 0
551 | TORONTO BUTTONVILLE A | 1 | 23 | 23 | -1.16 | 19.16 | 0
552 | TORONTO BUTTONVILLE A | 1 | 23 | 24 | -1.82 | 19.82 | 0
553 | TORONTO BUTTONVILLE A | 1 | 24 | 1 | -1.92 | 19.92 | 0
554 | TORONTO BUTTONVILLE A | 1 | 24 | 2 | -2.46 | 20.46 | 0
555 | TORONTO BUTTONVILLE A | 1 | 24 | 3 | -2.68 | 20.68 | 0
556 | TORONTO BUTTONVILLE A | 1 | 24 | 4 | -3.06 | 21.06 | 0
557 | TORONTO BUTTONVILLE A | 1 | 24 | 5 | -3.3 | 21.3 | 0
558 | TORONTO BUTTONVILLE A | 1 | 24 | 6 | -3.5 | 21.5 | 0
559 | TORONTO BUTTONVILLE A | 1 | 24 | 7 | -4.04 | 22.04 | 0
560 | TORONTO BUTTONVILLE A | 1 | 24 | 8 | -4.36 | 22.36 | 0
561 | TORONTO BUTTONVILLE A | 1 | 24 | 9 | -4.44 | 22.44 | 0
562 | TORONTO BUTTONVILLE A | 1 | 24 | 10 | -4.28 | 22.28 | 0
563 | TORONTO BUTTONVILLE A | 1 | 24 | 11 | -3.64 | 21.64 | 0
564 | TORONTO BUTTONVILLE A | 1 | 24 | 12 | -2.86 | 20.86 | 0
565 | TORONTO BUTTONVILLE A | 1 | 24 | 13 | -2.1 | 20.1 | 0
566 | TORONTO BUTTONVILLE A | 1 | 24 | 14 | -1.8 | 19.8 | 0
567 | TORONTO BUTTONVILLE A | 1 | 24 | 15 | -1.66 | 19.66 | 0
568 | TORONTO BUTTONVILLE A | 1 | 24 | 16 | -1.68 | 19.68 | 0
569 | TORONTO BUTTONVILLE A | 1 | 24 | 17 | -1.86 | 19.86 | 0
570 | TORONTO BUTTONVILLE A | 1 | 24 | 18 | -2.16 | 20.16 | 0
571 | TORONTO BUTTONVILLE A | 1 | 24 | 19 | -2.48 | 20.48 | 0
572 | TORONTO BUTTONVILLE A | 1 | 24 | 20 | -2.44 | 20.44 | 0
573 | TORONTO BUTTONVILLE A | 1 | 24 | 21 | -2.68 | 20.68 | 0
574 | TORONTO BUTTONVILLE A | 1 | 24 | 22 | -2.7 | 20.7 | 0
575 | TORONTO BUTTONVILLE A | 1 | 24 | 23 | -2.96 | 20.96 | 0
576 | TORONTO BUTTONVILLE A | 1 | 24 | 24 | -3.22 | 21.22 | 0
577 | TORONTO BUTTONVILLE A | 1 | 25 | 1 | -3.36 | 21.36 | 0
578 | TORONTO BUTTONVILLE A | 1 | 25 | 2 | -3.52 | 21.52 | 0
579 | TORONTO BUTTONVILLE A | 1 | 25 | 3 | -3.42 | 21.42 | 0
580 | TORONTO BUTTONVILLE A | 1 | 25 | 4 | -3.36 | 21.36 | 0
581 | TORONTO BUTTONVILLE A | 1 | 25 | 5 | -3.32 | 21.32 | 0
582 | TORONTO BUTTONVILLE A | 1 | 25 | 6 | -3.54 | 21.54 | 0
583 | TORONTO BUTTONVILLE A | 1 | 25 | 7 | -3.64 | 21.64 | 0
584 | TORONTO BUTTONVILLE A | 1 | 25 | 8 | -3.6 | 21.6 | 0
585 | TORONTO BUTTONVILLE A | 1 | 25 | 9 | -3.7 | 21.7 | 0
586 | TORONTO BUTTONVILLE A | 1 | 25 | 10 | -3.14 | 21.14 | 0
587 | TORONTO BUTTONVILLE A | 1 | 25 | 11 | -2.48 | 20.48 | 0
588 | TORONTO BUTTONVILLE A | 1 | 25 | 12 | -1.76 | 19.76 | 0
589 | TORONTO BUTTONVILLE A | 1 | 25 | 13 | -1.46 | 19.46 | 0
590 | TORONTO BUTTONVILLE A | 1 | 25 | 14 | -1.24 | 19.24 | 0
591 | TORONTO BUTTONVILLE A | 1 | 25 | 15 | -1 | 19 | 0
592 | TORONTO BUTTONVILLE A | 1 | 25 | 16 | -1.26 | 19.26 | 0
593 | TORONTO BUTTONVILLE A | 1 | 25 | 17 | -1.5 | 19.5 | 0
594 | TORONTO BUTTONVILLE A | 1 | 25 | 18 | -1.8 | 19.8 | 0
595 | TORONTO BUTTONVILLE A | 1 | 25 | 19 | -2.02 | 20.02 | 0
596 | TORONTO BUTTONVILLE A | 1 | 25 | 20 | -2.22 | 20.22 | 0
597 | TORONTO BUTTONVILLE A | 1 | 25 | 21 | -2.16 | 20.16 | 0
598 | TORONTO BUTTONVILLE A | 1 | 25 | 22 | -2.38 | 20.38 | 0
599 | TORONTO BUTTONVILLE A | 1 | 25 | 23 | -2.66 | 20.66 | 0
600 | TORONTO BUTTONVILLE A | 1 | 25 | 24 | -2.78 | 20.78 | 0
601 | TORONTO BUTTONVILLE A | 1 | 26 | 1 | -2.86 | 20.86 | 0
602 | TORONTO BUTTONVILLE A | 1 | 26 | 2 | -2.86 | 20.86 | 0
603 | TORONTO BUTTONVILLE A | 1 | 26 | 3 | -3 | 21 | 0
604 | TORONTO BUTTONVILLE A | 1 | 26 | 4 | -3 | 21 | 0
605 | TORONTO BUTTONVILLE A | 1 | 26 | 5 | -3 | 21 | 0
606 | TORONTO BUTTONVILLE A | 1 | 26 | 6 | -3.04 | 21.04 | 0
607 | TORONTO BUTTONVILLE A | 1 | 26 | 7 | -3.26 | 21.26 | 0
608 | TORONTO BUTTONVILLE A | 1 | 26 | 8 | -3.34 | 21.34 | 0
609 | TORONTO BUTTONVILLE A | 1 | 26 | 9 | -3.1 | 21.1 | 0
610 | TORONTO BUTTONVILLE A | 1 | 26 | 10 | -2.56 | 20.56 | 0
611 | TORONTO BUTTONVILLE A | 1 | 26 | 11 | -1.98 | 19.98 | 0
612 | TORONTO BUTTONVILLE A | 1 | 26 | 12 | -1.76 | 19.76 | 0
613 | TORONTO BUTTONVILLE A | 1 | 26 | 13 | -1.58 | 19.58 | 0
614 | TORONTO BUTTONVILLE A | 1 | 26 | 14 | -1.2 | 19.2 | 0
615 | TORONTO BUTTONVILLE A | 1 | 26 | 15 | -1.12 | 19.12 | 0
616 | TORONTO BUTTONVILLE A | 1 | 26 | 16 | -0.96 | 18.96 | 0
617 | TORONTO BUTTONVILLE A | 1 | 26 | 17 | -1.16 | 19.16 | 0
618 | TORONTO BUTTONVILLE A | 1 | 26 | 18 | -1.68 | 19.68 | 0
619 | TORONTO BUTTONVILLE A | 1 | 26 | 19 | -1.8 | 19.8 | 0
620 | TORONTO BUTTONVILLE A | 1 | 26 | 20 | -2.06 | 20.06 | 0
621 | TORONTO BUTTONVILLE A | 1 | 26 | 21 | -2.34 | 20.34 | 0
622 | TORONTO BUTTONVILLE A | 1 | 26 | 22 | -2.52 | 20.52 | 0
623 | TORONTO BUTTONVILLE A | 1 | 26 | 23 | -2.8 | 20.8 | 0
624 | TORONTO BUTTONVILLE A | 1 | 26 | 24 | -2.84 | 20.84 | 0
625 | TORONTO BUTTONVILLE A | 1 | 27 | 1 | -1.94 | 19.94 | 0
626 | TORONTO BUTTONVILLE A | 1 | 27 | 2 | -1.2 | 19.2 | 0
627 | TORONTO BUTTONVILLE A | 1 | 27 | 3 | -1.46 | 19.46 | 0
628 | TORONTO BUTTONVILLE A | 1 | 27 | 4 | -1.6 | 19.6 | 0
629 | TORONTO BUTTONVILLE A | 1 | 27 | 5 | -1.74 | 19.74 | 0
630 | TORONTO BUTTONVILLE A | 1 | 27 | 6 | -1.46 | 19.46 | 0
631 | TORONTO BUTTONVILLE A | 1 | 27 | 7 | -1.56 | 19.56 | 0
632 | TORONTO BUTTONVILLE A | 1 | 27 | 8 | -1.84 | 19.84 | 0
633 | TORONTO BUTTONVILLE A | 1 | 27 | 9 | -1.94 | 19.94 | 0
634 | TORONTO BUTTONVILLE A | 1 | 27 | 10 | -1.7 | 19.7 | 0
635 | TORONTO BUTTONVILLE A | 1 | 27 | 11 | -1.24 | 19.24 | 0
636 | TORONTO BUTTONVILLE A | 1 | 27 | 12 | -0.7 | 18.7 | 0
637 | TORONTO BUTTONVILLE A | 1 | 27 | 13 | -0.54 | 18.54 | 0
638 | TORONTO BUTTONVILLE A | 1 | 27 | 14 | -0.68 | 18.68 | 0
639 | TORONTO BUTTONVILLE A | 1 | 27 | 15 | -1.02 | 19.02 | 0
640 | TORONTO BUTTONVILLE A | 1 | 27 | 16 | -1.52 | 19.52 | 0
641 | TORONTO BUTTONVILLE A | 1 | 27 | 17 | -2 | 20 | 0
642 | TORONTO BUTTONVILLE A | 1 | 27 | 18 | -2.54 | 20.54 | 0
643 | TORONTO BUTTONVILLE A | 1 | 27 | 19 | -2.96 | 20.96 | 0
644 | TORONTO BUTTONVILLE A | 1 | 27 | 20 | -3.22 | 21.22 | 0
645 | TORONTO BUTTONVILLE A | 1 | 27 | 21 | -3.52 | 21.52 | 0
646 | TORONTO BUTTONVILLE A | 1 | 27 | 22 | -3.86 | 21.86 | 0
647 | TORONTO BUTTONVILLE A | 1 | 27 | 23 | -4.34 | 22.34 | 0
648 | TORONTO BUTTONVILLE A | 1 | 27 | 24 | -4.5 | 22.5 | 0
649 | TORONTO BUTTONVILLE A | 1 | 28 | 1 | -5.02 | 23.02 | 0
650 | TORONTO BUTTONVILLE A | 1 | 28 | 2 | -5.88 | 23.88 | 0
651 | TORONTO BUTTONVILLE A | 1 | 28 | 3 | -6.72 | 24.72 | 0
652 | TORONTO BUTTONVILLE A | 1 | 28 | 4 | -6.96 | 24.96 | 0
653 | TORONTO BUTTONVILLE A | 1 | 28 | 5 | -7.24 | 25.24 | 0
654 | TORONTO BUTTONVILLE A | 1 | 28 | 6 | -7.94 | 25.94 | 0
655 | TORONTO BUTTONVILLE A | 1 | 28 | 7 | -8.06 | 26.06 | 0
656 | TORONTO BUTTONVILLE A | 1 | 28 | 8 | -8.1 | 26.1 | 0
657 | TORONTO BUTTONVILLE A | 1 | 28 | 9 | -8.16 | 26.16 | 0
658 | TORONTO BUTTONVILLE A | 1 | 28 | 10 | -7.12 | 25.12 | 0
659 | TORONTO BUTTONVILLE A | 1 | 28 | 11 | -6.32 | 24.32 | 0
660 | TORONTO BUTTONVILLE A | 1 | 28 | 12 | -5.42 | 23.42 | 0
661 | TORONTO BUTTONVILLE A | 1 | 28 | 13 | -4.98 | 22.98 | 0
662 | TORONTO BUTTONVILLE A | 1 | 28 | 14 | -4.68 | 22.68 | 0
663 | TORONTO BUTTONVILLE A | 1 | 28 | 15 | -4.66 | 22.66 | 0
664 | TORONTO BUTTONVILLE A | 1 | 28 | 16 | -4.62 | 22.62 | 0
665 | TORONTO BUTTONVILLE A | 1 | 28 | 17 | -4.74 | 22.74 | 0
666 | TORONTO BUTTONVILLE A | 1 | 28 | 18 | -5.34 | 23.34 | 0
667 | TORONTO BUTTONVILLE A | 1 | 28 | 19 | -5.54 | 23.54 | 0
668 | TORONTO BUTTONVILLE A | 1 | 28 | 20 | -5.48 | 23.48 | 0
669 | TORONTO BUTTONVILLE A | 1 | 28 | 21 | -5.52 | 23.52 | 0
670 | TORONTO BUTTONVILLE A | 1 | 28 | 22 | -5.62 | 23.62 | 0
671 | TORONTO BUTTONVILLE A | 1 | 28 | 23 | -5.5 | 23.5 | 0
672 | TORONTO BUTTONVILLE A | 1 | 28 | 24 | -6.22 | 24.22 | 0
673 | TORONTO BUTTONVILLE A | 1 | 29 | 1 | -6.76 | 24.76 | 0
674 | TORONTO BUTTONVILLE A | 1 | 29 | 2 | -7.02 | 25.02 | 0
675 | TORONTO BUTTONVILLE A | 1 | 29 | 3 | -7.38 | 25.38 | 0
676 | TORONTO BUTTONVILLE A | 1 | 29 | 4 | -7.16 | 25.16 | 0
677 | TORONTO BUTTONVILLE A | 1 | 29 | 5 | -7.02 | 25.02 | 0
678 | TORONTO BUTTONVILLE A | 1 | 29 | 6 | -6.98 | 24.98 | 0
679 | TORONTO BUTTONVILLE A | 1 | 29 | 7 | -6.32 | 24.32 | 0
680 | TORONTO BUTTONVILLE A | 1 | 29 | 8 | -6.64 | 24.64 | 0
681 | TORONTO BUTTONVILLE A | 1 | 29 | 9 | -7.02 | 25.02 | 0
682 | TORONTO BUTTONVILLE A | 1 | 29 | 10 | -7.1 | 25.1 | 0
683 | TORONTO BUTTONVILLE A | 1 | 29 | 11 | -7.08 | 25.08 | 0
684 | TORONTO BUTTONVILLE A | 1 | 29 | 12 | -6.68 | 24.68 | 0
685 | TORONTO BUTTONVILLE A | 1 | 29 | 13 | -6.46 | 24.46 | 0
686 | TORONTO BUTTONVILLE A | 1 | 29 | 14 | -5.84 | 23.84 | 0
687 | TORONTO BUTTONVILLE A | 1 | 29 | 15 | -5.66 | 23.66 | 0
688 | TORONTO BUTTONVILLE A | 1 | 29 | 16 | -5.64 | 23.64 | 0
689 | TORONTO BUTTONVILLE A | 1 | 29 | 17 | -5.72 | 23.72 | 0
690 | TORONTO BUTTONVILLE A | 1 | 29 | 18 | -6.3 | 24.3 | 0
691 | TORONTO BUTTONVILLE A | 1 | 29 | 19 | -6.86 | 24.86 | 0
692 | TORONTO BUTTONVILLE A | 1 | 29 | 20 | -7.34 | 25.34 | 0
693 | TORONTO BUTTONVILLE A | 1 | 29 | 21 | -8 | 26 | 0
694 | TORONTO BUTTONVILLE A | 1 | 29 | 22 | -8.6 | 26.6 | 0
695 | TORONTO BUTTONVILLE A | 1 | 29 | 23 | -9.06 | 27.06 | 0
696 | TORONTO BUTTONVILLE A | 1 | 29 | 24 | -9.54 | 27.54 | 0
697 | TORONTO BUTTONVILLE A | 1 | 30 | 1 | -10.02 | 28.02 | 0
698 | TORONTO BUTTONVILLE A | 1 | 30 | 2 | -10.64 | 28.64 | 0
699 | TORONTO BUTTONVILLE A | 1 | 30 | 3 | -11.08 | 29.08 | 0
700 | TORONTO BUTTONVILLE A | 1 | 30 | 4 | -11.5 | 29.5 | 0
701 | TORONTO BUTTONVILLE A | 1 | 30 | 5 | -12.04 | 30.04 | 0
702 | TORONTO BUTTONVILLE A | 1 | 30 | 6 | -12.42 | 30.42 | 0
703 | TORONTO BUTTONVILLE A | 1 | 30 | 7 | -12.78 | 30.78 | 0
704 | TORONTO BUTTONVILLE A | 1 | 30 | 8 | -13 | 31 | 0
705 | TORONTO BUTTONVILLE A | 1 | 30 | 9 | -12.72 | 30.72 | 0
706 | TORONTO BUTTONVILLE A | 1 | 30 | 10 | -11.94 | 29.94 | 0
707 | TORONTO BUTTONVILLE A | 1 | 30 | 11 | -10.82 | 28.82 | 0
708 | TORONTO BUTTONVILLE A | 1 | 30 | 12 | -10.06 | 28.06 | 0
709 | TORONTO BUTTONVILLE A | 1 | 30 | 13 | -8.98 | 26.98 | 0
710 | TORONTO BUTTONVILLE A | 1 | 30 | 14 | -8.66 | 26.66 | 0
711 | TORONTO BUTTONVILLE A | 1 | 30 | 15 | -8.4 | 26.4 | 0
712 | TORONTO BUTTONVILLE A | 1 | 30 | 16 | -7.96 | 25.96 | 0
713 | TORONTO BUTTONVILLE A | 1 | 30 | 17 | -8.1 | 26.1 | 0
714 | TORONTO BUTTONVILLE A | 1 | 30 | 18 | -8.62 | 26.62 | 0
715 | TORONTO BUTTONVILLE A | 1 | 30 | 19 | -9.24 | 27.24 | 0
716 | TORONTO BUTTONVILLE A | 1 | 30 | 20 | -9.96 | 27.96 | 0
717 | TORONTO BUTTONVILLE A | 1 | 30 | 21 | -10.52 | 28.52 | 0
718 | TORONTO BUTTONVILLE A | 1 | 30 | 22 | -10.92 | 28.92 | 0
719 | TORONTO BUTTONVILLE A | 1 | 30 | 23 | -11.36 | 29.36 | 0
720 | TORONTO BUTTONVILLE A | 1 | 30 | 24 | -11.8 | 29.8 | 0
721 | TORONTO BUTTONVILLE A | 1 | 31 | 1 | -12.34 | 30.34 | 0
722 | TORONTO BUTTONVILLE A | 1 | 31 | 2 | -12.44 | 30.44 | 0
723 | TORONTO BUTTONVILLE A | 1 | 31 | 3 | -12.52 | 30.52 | 0
724 | TORONTO BUTTONVILLE A | 1 | 31 | 4 | -12.06 | 30.06 | 0
725 | TORONTO BUTTONVILLE A | 1 | 31 | 5 | -11.9 | 29.9 | 0
726 | TORONTO BUTTONVILLE A | 1 | 31 | 6 | -11.6 | 29.6 | 0
727 | TORONTO BUTTONVILLE A | 1 | 31 | 7 | -11.2 | 29.2 | 0
728 | TORONTO BUTTONVILLE A | 1 | 31 | 8 | -10.4 | 28.4 | 0
729 | TORONTO BUTTONVILLE A | 1 | 31 | 9 | -9.88 | 27.88 | 0
730 | TORONTO BUTTONVILLE A | 1 | 31 | 10 | -8.66 | 26.66 | 0
731 | TORONTO BUTTONVILLE A | 1 | 31 | 11 | -7.78 | 25.78 | 0
732 | TORONTO BUTTONVILLE A | 1 | 31 | 12 | -6.98 | 24.98 | 0
733 | TORONTO BUTTONVILLE A | 1 | 31 | 13 | -6.6 | 24.6 | 0
734 | TORONTO BUTTONVILLE A | 1 | 31 | 14 | -6.02 | 24.02 | 0
735 | TORONTO BUTTONVILLE A | 1 | 31 | 15 | -5.74 | 23.74 | 0
736 | TORONTO BUTTONVILLE A | 1 | 31 | 16 | -5.5 | 23.5 | 0
737 | TORONTO BUTTONVILLE A | 1 | 31 | 17 | -5.42 | 23.42 | 0
738 | TORONTO BUTTONVILLE A | 1 | 31 | 18 | -5.48 | 23.48 | 0
739 | TORONTO BUTTONVILLE A | 1 | 31 | 19 | -5.84 | 23.84 | 0
740 | TORONTO BUTTONVILLE A | 1 | 31 | 20 | -6.04 | 24.04 | 0
741 | TORONTO BUTTONVILLE A | 1 | 31 | 21 | -6.18 | 24.18 | 0
742 | TORONTO BUTTONVILLE A | 1 | 31 | 22 | -6.4 | 24.4 | 0
743 | TORONTO BUTTONVILLE A | 1 | 31 | 23 | -6.7 | 24.7 | 0
744 | TORONTO BUTTONVILLE A | 1 | 31 | 24 | -6.96 | 24.96 | 0
745 | TORONTO BUTTONVILLE A | 2 | 1 | 1 | -7.6 | 25.6 | 0
746 | TORONTO BUTTONVILLE A | 2 | 1 | 2 | -8.4 | 26.4 | 0
747 | TORONTO BUTTONVILLE A | 2 | 1 | 3 | -8.68 | 26.68 | 0
748 | TORONTO BUTTONVILLE A | 2 | 1 | 4 | -9.02 | 27.02 | 0
749 | TORONTO BUTTONVILLE A | 2 | 1 | 5 | -8.26 | 26.26 | 0
750 | TORONTO BUTTONVILLE A | 2 | 1 | 6 | -7.78 | 25.78 | 0
751 | TORONTO BUTTONVILLE A | 2 | 1 | 7 | -7.12 | 25.12 | 0
752 | TORONTO BUTTONVILLE A | 2 | 1 | 8 | -6.88 | 24.88 | 0
753 | TORONTO BUTTONVILLE A | 2 | 1 | 9 | -6.76 | 24.76 | 0
754 | TORONTO BUTTONVILLE A | 2 | 1 | 10 | -6.12 | 24.12 | 0
755 | TORONTO BUTTONVILLE A | 2 | 1 | 11 | -4.54 | 22.54 | 0
756 | TORONTO BUTTONVILLE A | 2 | 1 | 12 | -3.62 | 21.62 | 0
757 | TORONTO BUTTONVILLE A | 2 | 1 | 13 | -3.3 | 21.3 | 0
758 | TORONTO BUTTONVILLE A | 2 | 1 | 14 | -2.98 | 20.98 | 0
759 | TORONTO BUTTONVILLE A | 2 | 1 | 15 | -2.9 | 20.9 | 0
760 | TORONTO BUTTONVILLE A | 2 | 1 | 16 | -3.48 | 21.48 | 0
761 | TORONTO BUTTONVILLE A | 2 | 1 | 17 | -3.52 | 21.52 | 0
762 | TORONTO BUTTONVILLE A | 2 | 1 | 18 | -4.28 | 22.28 | 0
763 | TORONTO BUTTONVILLE A | 2 | 1 | 19 | -5.32 | 23.32 | 0
764 | TORONTO BUTTONVILLE A | 2 | 1 | 20 | -5.76 | 23.76 | 0
765 | TORONTO BUTTONVILLE A | 2 | 1 | 21 | -6.18 | 24.18 | 0
766 | TORONTO BUTTONVILLE A | 2 | 1 | 22 | -6.58 | 24.58 | 0
767 | TORONTO BUTTONVILLE A | 2 | 1 | 23 | -6.98 | 24.98 | 0
768 | TORONTO BUTTONVILLE A | 2 | 1 | 24 | -7.12 | 25.12 | 0
769 | TORONTO BUTTONVILLE A | 2 | 2 | 1 | -7.42 | 25.42 | 0
770 | TORONTO BUTTONVILLE A | 2 | 2 | 2 | -7.66 | 25.66 | 0
771 | TORONTO BUTTONVILLE A | 2 | 2 | 3 | -8 | 26 | 0
772 | TORONTO BUTTONVILLE A | 2 | 2 | 4 | -7.98 | 25.98 | 0
773 | TORONTO BUTTONVILLE A | 2 | 2 | 5 | -8.1 | 26.1 | 0
774 | TORONTO BUTTONVILLE A | 2 | 2 | 6 | -8.62 | 26.62 | 0
775 | TORONTO BUTTONVILLE A | 2 | 2 | 7 | -8.68 | 26.68 | 0
776 | TORONTO BUTTONVILLE A | 2 | 2 | 8 | -8.64 | 26.64 | 0
777 | TORONTO BUTTONVILLE A | 2 | 2 | 9 | -8.62 | 26.62 | 0
778 | TORONTO BUTTONVILLE A | 2 | 2 | 10 | -8.02 | 26.02 | 0
779 | TORONTO BUTTONVILLE A | 2 | 2 | 11 | -7.3 | 25.3 | 0
780 | TORONTO BUTTONVILLE A | 2 | 2 | 12 | -6.4 | 24.4 | 0
781 | TORONTO BUTTONVILLE A | 2 | 2 | 13 | -5.76 | 23.76 | 0
782 | TORONTO BUTTONVILLE A | 2 | 2 | 14 | -5.24 | 23.24 | 0
783 | TORONTO BUTTONVILLE A | 2 | 2 | 15 | -4.46 | 22.46 | 0
784 | TORONTO BUTTONVILLE A | 2 | 2 | 16 | -3.92 | 21.92 | 0
785 | TORONTO BUTTONVILLE A | 2 | 2 | 17 | -3.72 | 21.72 | 0
786 | TORONTO BUTTONVILLE A | 2 | 2 | 18 | -3.2 | 21.2 | 0
787 | TORONTO BUTTONVILLE A | 2 | 2 | 19 | -3.9 | 21.9 | 0
788 | TORONTO BUTTONVILLE A | 2 | 2 | 20 | -3.86 | 21.86 | 0
789 | TORONTO BUTTONVILLE A | 2 | 2 | 21 | -3.86 | 21.86 | 0
790 | TORONTO BUTTONVILLE A | 2 | 2 | 22 | -2.2 | 20.2 | 0
791 | TORONTO BUTTONVILLE A | 2 | 2 | 23 | -4.06 | 22.06 | 0
792 | TORONTO BUTTONVILLE A | 2 | 2 | 24 | -4.22 | 22.22 | 0
793 | TORONTO BUTTONVILLE A | 2 | 3 | 1 | -4.38 | 22.38 | 0
794 | TORONTO BUTTONVILLE A | 2 | 3 | 2 | -4.56 | 22.56 | 0
795 | TORONTO BUTTONVILLE A | 2 | 3 | 3 | -4.6 | 22.6 | 0
796 | TORONTO BUTTONVILLE A | 2 | 3 | 4 | -4.76 | 22.76 | 0
797 | TORONTO BUTTONVILLE A | 2 | 3 | 5 | -5.1 | 23.1 | 0
798 | TORONTO BUTTONVILLE A | 2 | 3 | 6 | -5.12 | 23.12 | 0
799 | TORONTO BUTTONVILLE A | 2 | 3 | 7 | -5.16 | 23.16 | 0
800 | TORONTO BUTTONVILLE A | 2 | 3 | 8 | -5.14 | 23.14 | 0
801 | TORONTO BUTTONVILLE A | 2 | 3 | 9 | -4.84 | 22.84 | 0
802 | TORONTO BUTTONVILLE A | 2 | 3 | 10 | -4.28 | 22.28 | 0
803 | TORONTO BUTTONVILLE A | 2 | 3 | 11 | -3.24 | 21.24 | 0
804 | TORONTO BUTTONVILLE A | 2 | 3 | 12 | -2.34 | 20.34 | 0
805 | TORONTO BUTTONVILLE A | 2 | 3 | 13 | -1.5 | 19.5 | 0
806 | TORONTO BUTTONVILLE A | 2 | 3 | 14 | -0.6 | 18.6 | 0
807 | TORONTO BUTTONVILLE A | 2 | 3 | 15 | -0.56 | 18.56 | 0
808 | TORONTO BUTTONVILLE A | 2 | 3 | 16 | -0.14 | 18.14 | 0
809 | TORONTO BUTTONVILLE A | 2 | 3 | 17 | -0.28 | 18.28 | 0
810 | TORONTO BUTTONVILLE A | 2 | 3 | 18 | -0.74 | 18.74 | 0
811 | TORONTO BUTTONVILLE A | 2 | 3 | 19 | -1.46 | 19.46 | 0
812 | TORONTO BUTTONVILLE A | 2 | 3 | 20 | -1.98 | 19.98 | 0
813 | TORONTO BUTTONVILLE A | 2 | 3 | 21 | -1.88 | 19.88 | 0
814 | TORONTO BUTTONVILLE A | 2 | 3 | 22 | -2.14 | 20.14 | 0
815 | TORONTO BUTTONVILLE A | 2 | 3 | 23 | -2.18 | 20.18 | 0
816 | TORONTO BUTTONVILLE A | 2 | 3 | 24 | -1.8 | 19.8 | 0
817 | TORONTO BUTTONVILLE A | 2 | 4 | 1 | -1.66 | 19.66 | 0
818 | TORONTO BUTTONVILLE A | 2 | 4 | 2 | -1.56 | 19.56 | 0
819 | TORONTO BUTTONVILLE A | 2 | 4 | 3 | -1.34 | 19.34 | 0
820 | TORONTO BUTTONVILLE A | 2 | 4 | 4 | -1.12 | 19.12 | 0
821 | TORONTO BUTTONVILLE A | 2 | 4 | 5 | -1.3 | 19.3 | 0
822 | TORONTO BUTTONVILLE A | 2 | 4 | 6 | -1.64 | 19.64 | 0
823 | TORONTO BUTTONVILLE A | 2 | 4 | 7 | -1.84 | 19.84 | 0
824 | TORONTO BUTTONVILLE A | 2 | 4 | 8 | -2.24 | 20.24 | 0
825 | TORONTO BUTTONVILLE A | 2 | 4 | 9 | -2.52 | 20.52 | 0
826 | TORONTO BUTTONVILLE A | 2 | 4 | 10 | -1.48 | 19.48 | 0
827 | TORONTO BUTTONVILLE A | 2 | 4 | 11 | -0.5 | 18.5 | 0
828 | TORONTO BUTTONVILLE A | 2 | 4 | 12 | 0.38 | 17.62 | 0
829 | TORONTO BUTTONVILLE A | 2 | 4 | 13 | 1.5 | 16.5 | 0
830 | TORONTO BUTTONVILLE A | 2 | 4 | 14 | 2.04 | 15.96 | 0
831 | TORONTO BUTTONVILLE A | 2 | 4 | 15 | 2.4 | 15.6 | 0
832 | TORONTO BUTTONVILLE A | 2 | 4 | 16 | 2.32 | 15.68 | 0
833 | TORONTO BUTTONVILLE A | 2 | 4 | 17 | 2.16 | 15.84 | 0
834 | TORONTO BUTTONVILLE A | 2 | 4 | 18 | 1.2 | 16.8 | 0
835 | TORONTO BUTTONVILLE A | 2 | 4 | 19 | -0.08 | 18.08 | 0
836 | TORONTO BUTTONVILLE A | 2 | 4 | 20 | -1.06 | 19.06 | 0
837 | TORONTO BUTTONVILLE A | 2 | 4 | 21 | -0.96 | 18.96 | 0
838 | TORONTO BUTTONVILLE A | 2 | 4 | 22 | -1.24 | 19.24 | 0
839 | TORONTO BUTTONVILLE A | 2 | 4 | 23 | -1.26 | 19.26 | 0
840 | TORONTO BUTTONVILLE A | 2 | 4 | 24 | -1.3 | 19.3 | 0
841 | TORONTO BUTTONVILLE A | 2 | 5 | 1 | -1.46 | 19.46 | 0
842 | TORONTO BUTTONVILLE A | 2 | 5 | 2 | -1.92 | 19.92 | 0
843 | TORONTO BUTTONVILLE A | 2 | 5 | 3 | -2.12 | 20.12 | 0
844 | TORONTO BUTTONVILLE A | 2 | 5 | 4 | -2.34 | 20.34 | 0
845 | TORONTO BUTTONVILLE A | 2 | 5 | 5 | -2.78 | 20.78 | 0
846 | TORONTO BUTTONVILLE A | 2 | 5 | 6 | -3.08 | 21.08 | 0
847 | TORONTO BUTTONVILLE A | 2 | 5 | 7 | -3.68 | 21.68 | 0
848 | TORONTO BUTTONVILLE A | 2 | 5 | 8 | -4.06 | 22.06 | 0
849 | TORONTO BUTTONVILLE A | 2 | 5 | 9 | -4.52 | 22.52 | 0
850 | TORONTO BUTTONVILLE A | 2 | 5 | 10 | -5.04 | 23.04 | 0
851 | TORONTO BUTTONVILLE A | 2 | 5 | 11 | -5 | 23 | 0
852 | TORONTO BUTTONVILLE A | 2 | 5 | 12 | -4.52 | 22.52 | 0
853 | TORONTO BUTTONVILLE A | 2 | 5 | 13 | -4.5 | 22.5 | 0
854 | TORONTO BUTTONVILLE A | 2 | 5 | 14 | -4.44 | 22.44 | 0
855 | TORONTO BUTTONVILLE A | 2 | 5 | 15 | -4.36 | 22.36 | 0
856 | TORONTO BUTTONVILLE A | 2 | 5 | 16 | -4.64 | 22.64 | 0
857 | TORONTO BUTTONVILLE A | 2 | 5 | 17 | -4.74 | 22.74 | 0
858 | TORONTO BUTTONVILLE A | 2 | 5 | 18 | -5.06 | 23.06 | 0
859 | TORONTO BUTTONVILLE A | 2 | 5 | 19 | -5.6 | 23.6 | 0
860 | TORONTO BUTTONVILLE A | 2 | 5 | 20 | -5.82 | 23.82 | 0
861 | TORONTO BUTTONVILLE A | 2 | 5 | 21 | -6.12 | 24.12 | 0
862 | TORONTO BUTTONVILLE A | 2 | 5 | 22 | -6.26 | 24.26 | 0
863 | TORONTO BUTTONVILLE A | 2 | 5 | 23 | -6.42 | 24.42 | 0
864 | TORONTO BUTTONVILLE A | 2 | 5 | 24 | -6.48 | 24.48 | 0
865 | TORONTO BUTTONVILLE A | 2 | 6 | 1 | -6.58 | 24.58 | 0
866 | TORONTO BUTTONVILLE A | 2 | 6 | 2 | -6.74 | 24.74 | 0
867 | TORONTO BUTTONVILLE A | 2 | 6 | 3 | -6.92 | 24.92 | 0
868 | TORONTO BUTTONVILLE A | 2 | 6 | 4 | -6.98 | 24.98 | 0
869 | TORONTO BUTTONVILLE A | 2 | 6 | 5 | -7.26 | 25.26 | 0
870 | TORONTO BUTTONVILLE A | 2 | 6 | 6 | -7.76 | 25.76 | 0
871 | TORONTO BUTTONVILLE A | 2 | 6 | 7 | -7.8 | 25.8 | 0
872 | TORONTO BUTTONVILLE A | 2 | 6 | 8 | -7.72 | 25.72 | 0
873 | TORONTO BUTTONVILLE A | 2 | 6 | 9 | -7.62 | 25.62 | 0
874 | TORONTO BUTTONVILLE A | 2 | 6 | 10 | -7.14 | 25.14 | 0
875 | TORONTO BUTTONVILLE A | 2 | 6 | 11 | -6.36 | 24.36 | 0
876 | TORONTO BUTTONVILLE A | 2 | 6 | 12 | -5.52 | 23.52 | 0
877 | TORONTO BUTTONVILLE A | 2 | 6 | 13 | -4.9 | 22.9 | 0
878 | TORONTO BUTTONVILLE A | 2 | 6 | 14 | -4.36 | 22.36 | 0
879 | TORONTO BUTTONVILLE A | 2 | 6 | 15 | -4 | 22 | 0
880 | TORONTO BUTTONVILLE A | 2 | 6 | 16 | -3.88 | 21.88 | 0
881 | TORONTO BUTTONVILLE A | 2 | 6 | 17 | -3.74 | 21.74 | 0
882 | TORONTO BUTTONVILLE A | 2 | 6 | 18 | -3.96 | 21.96 | 0
883 | TORONTO BUTTONVILLE A | 2 | 6 | 19 | -4.02 | 22.02 | 0
884 | TORONTO BUTTONVILLE A | 2 | 6 | 20 | -4.36 | 22.36 | 0
885 | TORONTO BUTTONVILLE A | 2 | 6 | 21 | -4.88 | 22.88 | 0
886 | TORONTO BUTTONVILLE A | 2 | 6 | 22 | -5.42 | 23.42 | 0
887 | TORONTO BUTTONVILLE A | 2 | 6 | 23 | -5.48 | 23.48 | 0
888 | TORONTO BUTTONVILLE A | 2 | 6 | 24 | -5.68 | 23.68 | 0
889 | TORONTO BUTTONVILLE A | 2 | 7 | 1 | -5.74 | 23.74 | 0
890 | TORONTO BUTTONVILLE A | 2 | 7 | 2 | -5.74 | 23.74 | 0
891 | TORONTO BUTTONVILLE A | 2 | 7 | 3 | -5.78 | 23.78 | 0
892 | TORONTO BUTTONVILLE A | 2 | 7 | 4 | -5.62 | 23.62 | 0
893 | TORONTO BUTTONVILLE A | 2 | 7 | 5 | -5.54 | 23.54 | 0
894 | TORONTO BUTTONVILLE A | 2 | 7 | 6 | -5.36 | 23.36 | 0
895 | TORONTO BUTTONVILLE A | 2 | 7 | 7 | -5.44 | 23.44 | 0
896 | TORONTO BUTTONVILLE A | 2 | 7 | 8 | -5.42 | 23.42 | 0
897 | TORONTO BUTTONVILLE A | 2 | 7 | 9 | -5.34 | 23.34 | 0
898 | TORONTO BUTTONVILLE A | 2 | 7 | 10 | -5.26 | 23.26 | 0
899 | TORONTO BUTTONVILLE A | 2 | 7 | 11 | -5.8 | 23.8 | 0
900 | TORONTO BUTTONVILLE A | 2 | 7 | 12 | -5.08 | 23.08 | 0
901 | TORONTO BUTTONVILLE A | 2 | 7 | 13 | -5.06 | 23.06 | 0
902 | TORONTO BUTTONVILLE A | 2 | 7 | 14 | -5.08 | 23.08 | 0
903 | TORONTO BUTTONVILLE A | 2 | 7 | 15 | -5.06 | 23.06 | 0
904 | TORONTO BUTTONVILLE A | 2 | 7 | 16 | -4.98 | 22.98 | 0
905 | TORONTO BUTTONVILLE A | 2 | 7 | 17 | -5.12 | 23.12 | 0
906 | TORONTO BUTTONVILLE A | 2 | 7 | 18 | -5.4 | 23.4 | 0
907 | TORONTO BUTTONVILLE A | 2 | 7 | 19 | -5.82 | 23.82 | 0
908 | TORONTO BUTTONVILLE A | 2 | 7 | 20 | -6.06 | 24.06 | 0
909 | TORONTO BUTTONVILLE A | 2 | 7 | 21 | -5.92 | 23.92 | 0
910 | TORONTO BUTTONVILLE A | 2 | 7 | 22 | -5.84 | 23.84 | 0
911 | TORONTO BUTTONVILLE A | 2 | 7 | 23 | -6.08 | 24.08 | 0
912 | TORONTO BUTTONVILLE A | 2 | 7 | 24 | -6.24 | 24.24 | 0
913 | TORONTO BUTTONVILLE A | 2 | 8 | 1 | -6.22 | 24.22 | 0
914 | TORONTO BUTTONVILLE A | 2 | 8 | 2 | -6 | 24 | 0
915 | TORONTO BUTTONVILLE A | 2 | 8 | 3 | -6.08 | 24.08 | 0
916 | TORONTO BUTTONVILLE A | 2 | 8 | 4 | -7.02 | 25.02 | 0
917 | TORONTO BUTTONVILLE A | 2 | 8 | 5 | -7.36 | 25.36 | 0
918 | TORONTO BUTTONVILLE A | 2 | 8 | 6 | -8.16 | 26.16 | 0
919 | TORONTO BUTTONVILLE A | 2 | 8 | 7 | -8.32 | 26.32 | 0
920 | TORONTO BUTTONVILLE A | 2 | 8 | 8 | -8.42 | 26.42 | 0
921 | TORONTO BUTTONVILLE A | 2 | 8 | 9 | -8.84 | 26.84 | 0
922 | TORONTO BUTTONVILLE A | 2 | 8 | 10 | -8.6 | 26.6 | 0
923 | TORONTO BUTTONVILLE A | 2 | 8 | 11 | -8.18 | 26.18 | 0
924 | TORONTO BUTTONVILLE A | 2 | 8 | 12 | -7.56 | 25.56 | 0
925 | TORONTO BUTTONVILLE A | 2 | 8 | 13 | -6.86 | 24.86 | 0
926 | TORONTO BUTTONVILLE A | 2 | 8 | 14 | -6.56 | 24.56 | 0
927 | TORONTO BUTTONVILLE A | 2 | 8 | 15 | -6.72 | 24.72 | 0
928 | TORONTO BUTTONVILLE A | 2 | 8 | 16 | -6.76 | 24.76 | 0
929 | TORONTO BUTTONVILLE A | 2 | 8 | 17 | -6.94 | 24.94 | 0
930 | TORONTO BUTTONVILLE A | 2 | 8 | 18 | -7.62 | 25.62 | 0
931 | TORONTO BUTTONVILLE A | 2 | 8 | 19 | -8.16 | 26.16 | 0
932 | TORONTO BUTTONVILLE A | 2 | 8 | 20 | -8.6 | 26.6 | 0
933 | TORONTO BUTTONVILLE A | 2 | 8 | 21 | -9.1 | 27.1 | 0
934 | TORONTO BUTTONVILLE A | 2 | 8 | 22 | -9.44 | 27.44 | 0
935 | TORONTO BUTTONVILLE A | 2 | 8 | 23 | -9.92 | 27.92 | 0
936 | TORONTO BUTTONVILLE A | 2 | 8 | 24 | -10.2 | 28.2 | 0
937 | TORONTO BUTTONVILLE A | 2 | 9 | 1 | -10.44 | 28.44 | 0
938 | TORONTO BUTTONVILLE A | 2 | 9 | 2 | -10.48 | 28.48 | 0
939 | TORONTO BUTTONVILLE A | 2 | 9 | 3 | -10.36 | 28.36 | 0
940 | TORONTO BUTTONVILLE A | 2 | 9 | 4 | -10.6 | 28.6 | 0
941 | TORONTO BUTTONVILLE A | 2 | 9 | 5 | -10.46 | 28.46 | 0
942 | TORONTO BUTTONVILLE A | 2 | 9 | 6 | -10.44 | 28.44 | 0
943 | TORONTO BUTTONVILLE A | 2 | 9 | 7 | -10.08 | 28.08 | 0
944 | TORONTO BUTTONVILLE A | 2 | 9 | 8 | -9.88 | 27.88 | 0
945 | TORONTO BUTTONVILLE A | 2 | 9 | 9 | -9.64 | 27.64 | 0
946 | TORONTO BUTTONVILLE A | 2 | 9 | 10 | -8.88 | 26.88 | 0
947 | TORONTO BUTTONVILLE A | 2 | 9 | 11 | -7.82 | 25.82 | 0
948 | TORONTO BUTTONVILLE A | 2 | 9 | 12 | -6.74 | 24.74 | 0
949 | TORONTO BUTTONVILLE A | 2 | 9 | 13 | -5.58 | 23.58 | 0
950 | TORONTO BUTTONVILLE A | 2 | 9 | 14 | -5 | 23 | 0
951 | TORONTO BUTTONVILLE A | 2 | 9 | 15 | -4.82 | 22.82 | 0
952 | TORONTO BUTTONVILLE A | 2 | 9 | 16 | -4.4 | 22.4 | 0
953 | TORONTO BUTTONVILLE A | 2 | 9 | 17 | -4.16 | 22.16 | 0
954 | TORONTO BUTTONVILLE A | 2 | 9 | 18 | -4.4 | 22.4 | 0
955 | TORONTO BUTTONVILLE A | 2 | 9 | 19 | -4.94 | 22.94 | 0
956 | TORONTO BUTTONVILLE A | 2 | 9 | 20 | -5.08 | 23.08 | 0
957 | TORONTO BUTTONVILLE A | 2 | 9 | 21 | -5.36 | 23.36 | 0
958 | TORONTO BUTTONVILLE A | 2 | 9 | 22 | -5.6 | 23.6 | 0
959 | TORONTO BUTTONVILLE A | 2 | 9 | 23 | -5.94 | 23.94 | 0
960 | TORONTO BUTTONVILLE A | 2 | 9 | 24 | -6.18 | 24.18 | 0
961 | TORONTO BUTTONVILLE A | 2 | 10 | 1 | -6.44 | 24.44 | 0
962 | TORONTO BUTTONVILLE A | 2 | 10 | 2 | -6.62 | 24.62 | 0
963 | TORONTO BUTTONVILLE A | 2 | 10 | 3 | -6.8 | 24.8 | 0
964 | TORONTO BUTTONVILLE A | 2 | 10 | 4 | -6.76 | 24.76 | 0
965 | TORONTO BUTTONVILLE A | 2 | 10 | 5 | -6.88 | 24.88 | 0
966 | TORONTO BUTTONVILLE A | 2 | 10 | 6 | -6.86 | 24.86 | 0
967 | TORONTO BUTTONVILLE A | 2 | 10 | 7 | -6.8 | 24.8 | 0
968 | TORONTO BUTTONVILLE A | 2 | 10 | 8 | -6.86 | 24.86 | 0
969 | TORONTO BUTTONVILLE A | 2 | 10 | 9 | -6.68 | 24.68 | 0
970 | TORONTO BUTTONVILLE A | 2 | 10 | 10 | -5.9 | 23.9 | 0
971 | TORONTO BUTTONVILLE A | 2 | 10 | 11 | -4.9 | 22.9 | 0
972 | TORONTO BUTTONVILLE A | 2 | 10 | 12 | -4.22 | 22.22 | 0
973 | TORONTO BUTTONVILLE A | 2 | 10 | 13 | -3.74 | 21.74 | 0
974 | TORONTO BUTTONVILLE A | 2 | 10 | 14 | -3.64 | 21.64 | 0
975 | TORONTO BUTTONVILLE A | 2 | 10 | 15 | -3.9 | 21.9 | 0
976 | TORONTO BUTTONVILLE A | 2 | 10 | 16 | -3.86 | 21.86 | 0
977 | TORONTO BUTTONVILLE A | 2 | 10 | 17 | -4.02 | 22.02 | 0
978 | TORONTO BUTTONVILLE A | 2 | 10 | 18 | -3.88 | 21.88 | 0
979 | TORONTO BUTTONVILLE A | 2 | 10 | 19 | -4.12 | 22.12 | 0
980 | TORONTO BUTTONVILLE A | 2 | 10 | 20 | -4.26 | 22.26 | 0
981 | TORONTO BUTTONVILLE A | 2 | 10 | 21 | -4.3 | 22.3 | 0
982 | TORONTO BUTTONVILLE A | 2 | 10 | 22 | -4.6 | 22.6 | 0
983 | TORONTO BUTTONVILLE A | 2 | 10 | 23 | -4.62 | 22.62 | 0
984 | TORONTO BUTTONVILLE A | 2 | 10 | 24 | -4.68 | 22.68 | 0
985 | TORONTO BUTTONVILLE A | 2 | 11 | 1 | -4.8 | 22.8 | 0
986 | TORONTO BUTTONVILLE A | 2 | 11 | 2 | -4.94 | 22.94 | 0
987 | TORONTO BUTTONVILLE A | 2 | 11 | 3 | -4.94 | 22.94 | 0
988 | TORONTO BUTTONVILLE A | 2 | 11 | 4 | -4.96 | 22.96 | 0
989 | TORONTO BUTTONVILLE A | 2 | 11 | 5 | -4.88 | 22.88 | 0
990 | TORONTO BUTTONVILLE A | 2 | 11 | 6 | -4.9 | 22.9 | 0
991 | TORONTO BUTTONVILLE A | 2 | 11 | 7 | -4.78 | 22.78 | 0
992 | TORONTO BUTTONVILLE A | 2 | 11 | 8 | -4.9 | 22.9 | 0
993 | TORONTO BUTTONVILLE A | 2 | 11 | 9 | -5.04 | 23.04 | 0
994 | TORONTO BUTTONVILLE A | 2 | 11 | 10 | -4.72 | 22.72 | 0
995 | TORONTO BUTTONVILLE A | 2 | 11 | 11 | -4.02 | 22.02 | 0
996 | TORONTO BUTTONVILLE A | 2 | 11 | 12 | -3.44 | 21.44 | 0
997 | TORONTO BUTTONVILLE A | 2 | 11 | 13 | -2.68 | 20.68 | 0
998 | TORONTO BUTTONVILLE A | 2 | 11 | 14 | -1.98 | 19.98 | 0
999 | TORONTO BUTTONVILLE A | 2 | 11 | 15 | -1.92 | 19.92 | 0
1000 | TORONTO BUTTONVILLE A | 2 | 11 | 16 | -2.04 | 20.04 | 0
1001 | TORONTO BUTTONVILLE A | 2 | 11 | 17 | -2.14 | 20.14 | 0
1002 | TORONTO BUTTONVILLE A | 2 | 11 | 18 | -2.48 | 20.48 | 0
1003 | TORONTO BUTTONVILLE A | 2 | 11 | 19 | -2.96 | 20.96 | 0
1004 | TORONTO BUTTONVILLE A | 2 | 11 | 20 | -3.42 | 21.42 | 0
1005 | TORONTO BUTTONVILLE A | 2 | 11 | 21 | -3.7 | 21.7 | 0
1006 | TORONTO BUTTONVILLE A | 2 | 11 | 22 | -4 | 22 | 0
1007 | TORONTO BUTTONVILLE A | 2 | 11 | 23 | -4.34 | 22.34 | 0
1008 | TORONTO BUTTONVILLE A | 2 | 11 | 24 | -4.9 | 22.9 | 0
1009 | TORONTO BUTTONVILLE A | 2 | 12 | 1 | -5.22 | 23.22 | 0
1010 | TORONTO BUTTONVILLE A | 2 | 12 | 2 | -5.6 | 23.6 | 0
1011 | TORONTO BUTTONVILLE A | 2 | 12 | 3 | -6.12 | 24.12 | 0
1012 | TORONTO BUTTONVILLE A | 2 | 12 | 4 | -6.8 | 24.8 | 0
1013 | TORONTO BUTTONVILLE A | 2 | 12 | 5 | -7.16 | 25.16 | 0
1014 | TORONTO BUTTONVILLE A | 2 | 12 | 6 | -7.52 | 25.52 | 0
1015 | TORONTO BUTTONVILLE A | 2 | 12 | 7 | -7.84 | 25.84 | 0
1016 | TORONTO BUTTONVILLE A | 2 | 12 | 8 | -7.88 | 25.88 | 0
1017 | TORONTO BUTTONVILLE A | 2 | 12 | 9 | -8 | 26 | 0
1018 | TORONTO BUTTONVILLE A | 2 | 12 | 10 | -7.68 | 25.68 | 0
1019 | TORONTO BUTTONVILLE A | 2 | 12 | 11 | -7.04 | 25.04 | 0
1020 | TORONTO BUTTONVILLE A | 2 | 12 | 12 | -6.24 | 24.24 | 0
1021 | TORONTO BUTTONVILLE A | 2 | 12 | 13 | -5.72 | 23.72 | 0
1022 | TORONTO BUTTONVILLE A | 2 | 12 | 14 | -5.36 | 23.36 | 0
1023 | TORONTO BUTTONVILLE A | 2 | 12 | 15 | -4.66 | 22.66 | 0
1024 | TORONTO BUTTONVILLE A | 2 | 12 | 16 | -4.5 | 22.5 | 0
1025 | TORONTO BUTTONVILLE A | 2 | 12 | 17 | -4.38 | 22.38 | 0
1026 | TORONTO BUTTONVILLE A | 2 | 12 | 18 | -4.5 | 22.5 | 0
1027 | TORONTO BUTTONVILLE A | 2 | 12 | 19 | -4.78 | 22.78 | 0
1028 | TORONTO BUTTONVILLE A | 2 | 12 | 20 | -4.98 | 22.98 | 0
1029 | TORONTO BUTTONVILLE A | 2 | 12 | 21 | -4.88 | 22.88 | 0
1030 | TORONTO BUTTONVILLE A | 2 | 12 | 22 | -4.96 | 22.96 | 0
1031 | TORONTO BUTTONVILLE A | 2 | 12 | 23 | -5.32 | 23.32 | 0
1032 | TORONTO BUTTONVILLE A | 2 | 12 | 24 | -5.36 | 23.36 | 0
1033 | TORONTO BUTTONVILLE A | 2 | 13 | 1 | -5.58 | 23.58 | 0
1034 | TORONTO BUTTONVILLE A | 2 | 13 | 2 | -5.46 | 23.46 | 0
1035 | TORONTO BUTTONVILLE A | 2 | 13 | 3 | -5.84 | 23.84 | 0
1036 | TORONTO BUTTONVILLE A | 2 | 13 | 4 | -6.52 | 24.52 | 0
1037 | TORONTO BUTTONVILLE A | 2 | 13 | 5 | -6.92 | 24.92 | 0
1038 | TORONTO BUTTONVILLE A | 2 | 13 | 6 | -6.98 | 24.98 | 0
1039 | TORONTO BUTTONVILLE A | 2 | 13 | 7 | -7.18 | 25.18 | 0
1040 | TORONTO BUTTONVILLE A | 2 | 13 | 8 | -7.38 | 25.38 | 0
1041 | TORONTO BUTTONVILLE A | 2 | 13 | 9 | -7.36 | 25.36 | 0
1042 | TORONTO BUTTONVILLE A | 2 | 13 | 10 | -6.7 | 24.7 | 0
1043 | TORONTO BUTTONVILLE A | 2 | 13 | 11 | -5.88 | 23.88 | 0
1044 | TORONTO BUTTONVILLE A | 2 | 13 | 12 | -5.42 | 23.42 | 0
1045 | TORONTO BUTTONVILLE A | 2 | 13 | 13 | -5.6 | 23.6 | 0
1046 | TORONTO BUTTONVILLE A | 2 | 13 | 14 | -5.44 | 23.44 | 0
1047 | TORONTO BUTTONVILLE A | 2 | 13 | 15 | -5.78 | 23.78 | 0
1048 | TORONTO BUTTONVILLE A | 2 | 13 | 16 | -5.8 | 23.8 | 0
1049 | TORONTO BUTTONVILLE A | 2 | 13 | 17 | -6.12 | 24.12 | 0
1050 | TORONTO BUTTONVILLE A | 2 | 13 | 18 | -6.62 | 24.62 | 0
1051 | TORONTO BUTTONVILLE A | 2 | 13 | 19 | -7.3 | 25.3 | 0
1052 | TORONTO BUTTONVILLE A | 2 | 13 | 20 | -7.54 | 25.54 | 0
1053 | TORONTO BUTTONVILLE A | 2 | 13 | 21 | -7.6 | 25.6 | 0
1054 | TORONTO BUTTONVILLE A | 2 | 13 | 22 | -7.88 | 25.88 | 0
1055 | TORONTO BUTTONVILLE A | 2 | 13 | 23 | -7.96 | 25.96 | 0
1056 | TORONTO BUTTONVILLE A | 2 | 13 | 24 | -8.6 | 26.6 | 0
1057 | TORONTO BUTTONVILLE A | 2 | 14 | 1 | -9.28 | 27.28 | 0
1058 | TORONTO BUTTONVILLE A | 2 | 14 | 2 | -9.26 | 27.26 | 0
1059 | TORONTO BUTTONVILLE A | 2 | 14 | 3 | -10.16 | 28.16 | 0
1060 | TORONTO BUTTONVILLE A | 2 | 14 | 4 | -10.46 | 28.46 | 0
1061 | TORONTO BUTTONVILLE A | 2 | 14 | 5 | -10.06 | 28.06 | 0
1062 | TORONTO BUTTONVILLE A | 2 | 14 | 6 | -10 | 28 | 0
1063 | TORONTO BUTTONVILLE A | 2 | 14 | 7 | -9.78 | 27.78 | 0
1064 | TORONTO BUTTONVILLE A | 2 | 14 | 8 | -9.72 | 27.72 | 0
1065 | TORONTO BUTTONVILLE A | 2 | 14 | 9 | -9.02 | 27.02 | 0
1066 | TORONTO BUTTONVILLE A | 2 | 14 | 10 | -7.9 | 25.9 | 0
1067 | TORONTO BUTTONVILLE A | 2 | 14 | 11 | -5.78 | 23.78 | 0
1068 | TORONTO BUTTONVILLE A | 2 | 14 | 12 | -5 | 23 | 0
1069 | TORONTO BUTTONVILLE A | 2 | 14 | 13 | -3.16 | 21.16 | 0
1070 | TORONTO BUTTONVILLE A | 2 | 14 | 14 | -2 | 20 | 0
1071 | TORONTO BUTTONVILLE A | 2 | 14 | 15 | -1.48 | 19.48 | 0
1072 | TORONTO BUTTONVILLE A | 2 | 14 | 16 | -1.22 | 19.22 | 0
1073 | TORONTO BUTTONVILLE A | 2 | 14 | 17 | -1.64 | 19.64 | 0
1074 | TORONTO BUTTONVILLE A | 2 | 14 | 18 | -1.68 | 19.68 | 0
1075 | TORONTO BUTTONVILLE A | 2 | 14 | 19 | -2.04 | 20.04 | 0
1076 | TORONTO BUTTONVILLE A | 2 | 14 | 20 | -2.1 | 20.1 | 0
1077 | TORONTO BUTTONVILLE A | 2 | 14 | 21 | -2.1 | 20.1 | 0
1078 | TORONTO BUTTONVILLE A | 2 | 14 | 22 | -2.44 | 20.44 | 0
1079 | TORONTO BUTTONVILLE A | 2 | 14 | 23 | -2.68 | 20.68 | 0
1080 | TORONTO BUTTONVILLE A | 2 | 14 | 24 | -2.78 | 20.78 | 0
1081 | TORONTO BUTTONVILLE A | 2 | 15 | 1 | -3.36 | 21.36 | 0
1082 | TORONTO BUTTONVILLE A | 2 | 15 | 2 | -3.18 | 21.18 | 0
1083 | TORONTO BUTTONVILLE A | 2 | 15 | 3 | -3 | 21 | 0
1084 | TORONTO BUTTONVILLE A | 2 | 15 | 4 | -2.98 | 20.98 | 0
1085 | TORONTO BUTTONVILLE A | 2 | 15 | 5 | -3.38 | 21.38 | 0
1086 | TORONTO BUTTONVILLE A | 2 | 15 | 6 | -3.16 | 21.16 | 0
1087 | TORONTO BUTTONVILLE A | 2 | 15 | 7 | -2.3 | 20.3 | 0
1088 | TORONTO BUTTONVILLE A | 2 | 15 | 8 | -2.06 | 20.06 | 0
1089 | TORONTO BUTTONVILLE A | 2 | 15 | 9 | -1.78 | 19.78 | 0
1090 | TORONTO BUTTONVILLE A | 2 | 15 | 10 | -1.36 | 19.36 | 0
1091 | TORONTO BUTTONVILLE A | 2 | 15 | 11 | -0.92 | 18.92 | 0
1092 | TORONTO BUTTONVILLE A | 2 | 15 | 12 | -0.62 | 18.62 | 0
1093 | TORONTO BUTTONVILLE A | 2 | 15 | 13 | -0.14 | 18.14 | 0
1094 | TORONTO BUTTONVILLE A | 2 | 15 | 14 | -0.4 | 18.4 | 0
1095 | TORONTO BUTTONVILLE A | 2 | 15 | 15 | -0.64 | 18.64 | 0
1096 | TORONTO BUTTONVILLE A | 2 | 15 | 16 | -0.86 | 18.86 | 0
1097 | TORONTO BUTTONVILLE A | 2 | 15 | 17 | -1.36 | 19.36 | 0
1098 | TORONTO BUTTONVILLE A | 2 | 15 | 18 | -1.8 | 19.8 | 0
1099 | TORONTO BUTTONVILLE A | 2 | 15 | 19 | -2.1 | 20.1 | 0
1100 | TORONTO BUTTONVILLE A | 2 | 15 | 20 | -2.28 | 20.28 | 0
1101 | TORONTO BUTTONVILLE A | 2 | 15 | 21 | -2.64 | 20.64 | 0
1102 | TORONTO BUTTONVILLE A | 2 | 15 | 22 | -3.1 | 21.1 | 0
1103 | TORONTO BUTTONVILLE A | 2 | 15 | 23 | -3.26 | 21.26 | 0
1104 | TORONTO BUTTONVILLE A | 2 | 15 | 24 | -3.44 | 21.44 | 0
1105 | TORONTO BUTTONVILLE A | 2 | 16 | 1 | -3.42 | 21.42 | 0
1106 | TORONTO BUTTONVILLE A | 2 | 16 | 2 | -3.42 | 21.42 | 0
1107 | TORONTO BUTTONVILLE A | 2 | 16 | 3 | -3.6 | 21.6 | 0
1108 | TORONTO BUTTONVILLE A | 2 | 16 | 4 | -4.22 | 22.22 | 0
1109 | TORONTO BUTTONVILLE A | 2 | 16 | 5 | -4.76 | 22.76 | 0
1110 | TORONTO BUTTONVILLE A | 2 | 16 | 6 | -5.02 | 23.02 | 0
1111 | TORONTO BUTTONVILLE A | 2 | 16 | 7 | -5.22 | 23.22 | 0
1112 | TORONTO BUTTONVILLE A | 2 | 16 | 8 | -5.7 | 23.7 | 0
1113 | TORONTO BUTTONVILLE A | 2 | 16 | 9 | -5.92 | 23.92 | 0
1114 | TORONTO BUTTONVILLE A | 2 | 16 | 10 | -6.2 | 24.2 | 0
1115 | TORONTO BUTTONVILLE A | 2 | 16 | 11 | -5.92 | 23.92 | 0
1116 | TORONTO BUTTONVILLE A | 2 | 16 | 12 | -5.6 | 23.6 | 0
1117 | TORONTO BUTTONVILLE A | 2 | 16 | 13 | -5.16 | 23.16 | 0
1118 | TORONTO BUTTONVILLE A | 2 | 16 | 14 | -4.48 | 22.48 | 0
1119 | TORONTO BUTTONVILLE A | 2 | 16 | 15 | -4.16 | 22.16 | 0
1120 | TORONTO BUTTONVILLE A | 2 | 16 | 16 | -3.7 | 21.7 | 0
1121 | TORONTO BUTTONVILLE A | 2 | 16 | 17 | -3.64 | 21.64 | 0
1122 | TORONTO BUTTONVILLE A | 2 | 16 | 18 | -4.22 | 22.22 | 0
1123 | TORONTO BUTTONVILLE A | 2 | 16 | 19 | -5.02 | 23.02 | 0
1124 | TORONTO BUTTONVILLE A | 2 | 16 | 20 | -5.82 | 23.82 | 0
1125 | TORONTO BUTTONVILLE A | 2 | 16 | 21 | -6.4 | 24.4 | 0
1126 | TORONTO BUTTONVILLE A | 2 | 16 | 22 | -7.08 | 25.08 | 0
1127 | TORONTO BUTTONVILLE A | 2 | 16 | 23 | -7.78 | 25.78 | 0
1128 | TORONTO BUTTONVILLE A | 2 | 16 | 24 | -7.86 | 25.86 | 0
1129 | TORONTO BUTTONVILLE A | 2 | 17 | 1 | -8.26 | 26.26 | 0
1130 | TORONTO BUTTONVILLE A | 2 | 17 | 2 | -8.48 | 26.48 | 0
1131 | TORONTO BUTTONVILLE A | 2 | 17 | 3 | -8.78 | 26.78 | 0
1132 | TORONTO BUTTONVILLE A | 2 | 17 | 4 | -9.44 | 27.44 | 0
1133 | TORONTO BUTTONVILLE A | 2 | 17 | 5 | -10.34 | 28.34 | 0
1134 | TORONTO BUTTONVILLE A | 2 | 17 | 6 | -10.22 | 28.22 | 0
1135 | TORONTO BUTTONVILLE A | 2 | 17 | 7 | -10.08 | 28.08 | 0
1136 | TORONTO BUTTONVILLE A | 2 | 17 | 8 | -9.58 | 27.58 | 0
1137 | TORONTO BUTTONVILLE A | 2 | 17 | 9 | -9.16 | 27.16 | 0
1138 | TORONTO BUTTONVILLE A | 2 | 17 | 10 | -7.3 | 25.3 | 0
1139 | TORONTO BUTTONVILLE A | 2 | 17 | 11 | -5.6 | 23.6 | 0
1140 | TORONTO BUTTONVILLE A | 2 | 17 | 12 | -4.62 | 22.62 | 0
1141 | TORONTO BUTTONVILLE A | 2 | 17 | 13 | -3.86 | 21.86 | 0
1142 | TORONTO BUTTONVILLE A | 2 | 17 | 14 | -3.5 | 21.5 | 0
1143 | TORONTO BUTTONVILLE A | 2 | 17 | 15 | -3.3 | 21.3 | 0
1144 | TORONTO BUTTONVILLE A | 2 | 17 | 16 | -3.04 | 21.04 | 0
1145 | TORONTO BUTTONVILLE A | 2 | 17 | 17 | -2.96 | 20.96 | 0
1146 | TORONTO BUTTONVILLE A | 2 | 17 | 18 | -3.32 | 21.32 | 0
1147 | TORONTO BUTTONVILLE A | 2 | 17 | 19 | -3.62 | 21.62 | 0
1148 | TORONTO BUTTONVILLE A | 2 | 17 | 20 | -4.08 | 22.08 | 0
1149 | TORONTO BUTTONVILLE A | 2 | 17 | 21 | -4.14 | 22.14 | 0
1150 | TORONTO BUTTONVILLE A | 2 | 17 | 22 | -4.2 | 22.2 | 0
1151 | TORONTO BUTTONVILLE A | 2 | 17 | 23 | -4.06 | 22.06 | 0
1152 | TORONTO BUTTONVILLE A | 2 | 17 | 24 | -3.98 | 21.98 | 0
1153 | TORONTO BUTTONVILLE A | 2 | 18 | 1 | -4.28 | 22.28 | 0
1154 | TORONTO BUTTONVILLE A | 2 | 18 | 2 | -4.6 | 22.6 | 0
1155 | TORONTO BUTTONVILLE A | 2 | 18 | 3 | -4.88 | 22.88 | 0
1156 | TORONTO BUTTONVILLE A | 2 | 18 | 4 | -5.02 | 23.02 | 0
1157 | TORONTO BUTTONVILLE A | 2 | 18 | 5 | -5.5 | 23.5 | 0
1158 | TORONTO BUTTONVILLE A | 2 | 18 | 6 | -5.12 | 23.12 | 0
1159 | TORONTO BUTTONVILLE A | 2 | 18 | 7 | -4.8 | 22.8 | 0
1160 | TORONTO BUTTONVILLE A | 2 | 18 | 8 | -4.62 | 22.62 | 0
1161 | TORONTO BUTTONVILLE A | 2 | 18 | 9 | -4.12 | 22.12 | 0
1162 | TORONTO BUTTONVILLE A | 2 | 18 | 10 | -2.46 | 20.46 | 0
1163 | TORONTO BUTTONVILLE A | 2 | 18 | 11 | -1.16 | 19.16 | 0
1164 | TORONTO BUTTONVILLE A | 2 | 18 | 12 | 0.3 | 17.7 | 0
1165 | TORONTO BUTTONVILLE A | 2 | 18 | 13 | 0.98 | 17.02 | 0
1166 | TORONTO BUTTONVILLE A | 2 | 18 | 14 | 1.44 | 16.56 | 0
1167 | TORONTO BUTTONVILLE A | 2 | 18 | 15 | 1.26 | 16.74 | 0
1168 | TORONTO BUTTONVILLE A | 2 | 18 | 16 | 1.48 | 16.52 | 0
1169 | TORONTO BUTTONVILLE A | 2 | 18 | 17 | 1.1 | 16.9 | 0
1170 | TORONTO BUTTONVILLE A | 2 | 18 | 18 | 0.46 | 17.54 | 0
1171 | TORONTO BUTTONVILLE A | 2 | 18 | 19 | -0.28 | 18.28 | 0
1172 | TORONTO BUTTONVILLE A | 2 | 18 | 20 | -0.9 | 18.9 | 0
1173 | TORONTO BUTTONVILLE A | 2 | 18 | 21 | -1.4 | 19.4 | 0
1174 | TORONTO BUTTONVILLE A | 2 | 18 | 22 | -1.72 | 19.72 | 0
1175 | TORONTO BUTTONVILLE A | 2 | 18 | 23 | -2.3 | 20.3 | 0
1176 | TORONTO BUTTONVILLE A | 2 | 18 | 24 | -2.64 | 20.64 | 0
1177 | TORONTO BUTTONVILLE A | 2 | 19 | 1 | -2.96 | 20.96 | 0
1178 | TORONTO BUTTONVILLE A | 2 | 19 | 2 | -3.26 | 21.26 | 0
1179 | TORONTO BUTTONVILLE A | 2 | 19 | 3 | -3.4 | 21.4 | 0
1180 | TORONTO BUTTONVILLE A | 2 | 19 | 4 | -3.46 | 21.46 | 0
1181 | TORONTO BUTTONVILLE A | 2 | 19 | 5 | -3.66 | 21.66 | 0
1182 | TORONTO BUTTONVILLE A | 2 | 19 | 6 | -3.98 | 21.98 | 0
1183 | TORONTO BUTTONVILLE A | 2 | 19 | 7 | -4.6 | 22.6 | 0
1184 | TORONTO BUTTONVILLE A | 2 | 19 | 8 | -4.46 | 22.46 | 0
1185 | TORONTO BUTTONVILLE A | 2 | 19 | 9 | -4.16 | 22.16 | 0
1186 | TORONTO BUTTONVILLE A | 2 | 19 | 10 | -3.08 | 21.08 | 0
1187 | TORONTO BUTTONVILLE A | 2 | 19 | 11 | -1.68 | 19.68 | 0
1188 | TORONTO BUTTONVILLE A | 2 | 19 | 12 | -0.34 | 18.34 | 0
1189 | TORONTO BUTTONVILLE A | 2 | 19 | 13 | 0.06 | 17.94 | 0
1190 | TORONTO BUTTONVILLE A | 2 | 19 | 14 | 0.3 | 17.7 | 0
1191 | TORONTO BUTTONVILLE A | 2 | 19 | 15 | 0.24 | 17.76 | 0
1192 | TORONTO BUTTONVILLE A | 2 | 19 | 16 | 0.06 | 17.94 | 0
1193 | TORONTO BUTTONVILLE A | 2 | 19 | 17 | -0.28 | 18.28 | 0
1194 | TORONTO BUTTONVILLE A | 2 | 19 | 18 | -0.66 | 18.66 | 0
1195 | TORONTO BUTTONVILLE A | 2 | 19 | 19 | -1.32 | 19.32 | 0
1196 | TORONTO BUTTONVILLE A | 2 | 19 | 20 | -1.72 | 19.72 | 0
1197 | TORONTO BUTTONVILLE A | 2 | 19 | 21 | -2.18 | 20.18 | 0
1198 | TORONTO BUTTONVILLE A | 2 | 19 | 22 | -2.64 | 20.64 | 0
1199 | TORONTO BUTTONVILLE A | 2 | 19 | 23 | -3.08 | 21.08 | 0
1200 | TORONTO BUTTONVILLE A | 2 | 19 | 24 | -2.94 | 20.94 | 0
1201 | TORONTO BUTTONVILLE A | 2 | 20 | 1 | -3.66 | 21.66 | 0
1202 | TORONTO BUTTONVILLE A | 2 | 20 | 2 | -3.96 | 21.96 | 0
1203 | TORONTO BUTTONVILLE A | 2 | 20 | 3 | -4.42 | 22.42 | 0
1204 | TORONTO BUTTONVILLE A | 2 | 20 | 4 | -4.78 | 22.78 | 0
1205 | TORONTO BUTTONVILLE A | 2 | 20 | 5 | -4.92 | 22.92 | 0
1206 | TORONTO BUTTONVILLE A | 2 | 20 | 6 | -4.96 | 22.96 | 0
1207 | TORONTO BUTTONVILLE A | 2 | 20 | 7 | -4.92 | 22.92 | 0
1208 | TORONTO BUTTONVILLE A | 2 | 20 | 8 | -5.38 | 23.38 | 0
1209 | TORONTO BUTTONVILLE A | 2 | 20 | 9 | -4.68 | 22.68 | 0
1210 | TORONTO BUTTONVILLE A | 2 | 20 | 10 | -3.74 | 21.74 | 0
1211 | TORONTO BUTTONVILLE A | 2 | 20 | 11 | -3.02 | 21.02 | 0
1212 | TORONTO BUTTONVILLE A | 2 | 20 | 12 | -1.68 | 19.68 | 0
1213 | TORONTO BUTTONVILLE A | 2 | 20 | 13 | -0.78 | 18.78 | 0
1214 | TORONTO BUTTONVILLE A | 2 | 20 | 14 | 0.5 | 17.5 | 0
1215 | TORONTO BUTTONVILLE A | 2 | 20 | 15 | 0.6 | 17.4 | 0
1216 | TORONTO BUTTONVILLE A | 2 | 20 | 16 | 1.02 | 16.98 | 0
1217 | TORONTO BUTTONVILLE A | 2 | 20 | 17 | 1.14 | 16.86 | 0
1218 | TORONTO BUTTONVILLE A | 2 | 20 | 18 | 0.36 | 17.64 | 0
1219 | TORONTO BUTTONVILLE A | 2 | 20 | 19 | -0.18 | 18.18 | 0
1220 | TORONTO BUTTONVILLE A | 2 | 20 | 20 | -0.62 | 18.62 | 0
1221 | TORONTO BUTTONVILLE A | 2 | 20 | 21 | -0.84 | 18.84 | 0
1222 | TORONTO BUTTONVILLE A | 2 | 20 | 22 | -1.14 | 19.14 | 0
1223 | TORONTO BUTTONVILLE A | 2 | 20 | 23 | -1.36 | 19.36 | 0
1224 | TORONTO BUTTONVILLE A | 2 | 20 | 24 | -1.14 | 19.14 | 0
1225 | TORONTO BUTTONVILLE A | 2 | 21 | 1 | -1.42 | 19.42 | 0
1226 | TORONTO BUTTONVILLE A | 2 | 21 | 2 | -1.24 | 19.24 | 0
1227 | TORONTO BUTTONVILLE A | 2 | 21 | 3 | -0.94 | 18.94 | 0
1228 | TORONTO BUTTONVILLE A | 2 | 21 | 4 | -0.96 | 18.96 | 0
1229 | TORONTO BUTTONVILLE A | 2 | 21 | 5 | -0.72 | 18.72 | 0
1230 | TORONTO BUTTONVILLE A | 2 | 21 | 6 | -1.52 | 19.52 | 0
1231 | TORONTO BUTTONVILLE A | 2 | 21 | 7 | -1.72 | 19.72 | 0
1232 | TORONTO BUTTONVILLE A | 2 | 21 | 8 | -3.22 | 21.22 | 0
1233 | TORONTO BUTTONVILLE A | 2 | 21 | 9 | -3.02 | 21.02 | 0
1234 | TORONTO BUTTONVILLE A | 2 | 21 | 10 | -1.72 | 19.72 | 0
1235 | TORONTO BUTTONVILLE A | 2 | 21 | 11 | -0.74 | 18.74 | 0
1236 | TORONTO BUTTONVILLE A | 2 | 21 | 12 | 0.24 | 17.76 | 0
1237 | TORONTO BUTTONVILLE A | 2 | 21 | 13 | 0.66 | 17.34 | 0
1238 | TORONTO BUTTONVILLE A | 2 | 21 | 14 | 0.72 | 17.28 | 0
1239 | TORONTO BUTTONVILLE A | 2 | 21 | 15 | 1.08 | 16.92 | 0
1240 | TORONTO BUTTONVILLE A | 2 | 21 | 16 | 1.16 | 16.84 | 0
1241 | TORONTO BUTTONVILLE A | 2 | 21 | 17 | 0.92 | 17.08 | 0
1242 | TORONTO BUTTONVILLE A | 2 | 21 | 18 | 0.46 | 17.54 | 0
1243 | TORONTO BUTTONVILLE A | 2 | 21 | 19 | 0.04 | 17.96 | 0
1244 | TORONTO BUTTONVILLE A | 2 | 21 | 20 | -0.52 | 18.52 | 0
1245 | TORONTO BUTTONVILLE A | 2 | 21 | 21 | -1.02 | 19.02 | 0
1246 | TORONTO BUTTONVILLE A | 2 | 21 | 22 | -1.22 | 19.22 | 0
1247 | TORONTO BUTTONVILLE A | 2 | 21 | 23 | -1.08 | 19.08 | 0
1248 | TORONTO BUTTONVILLE A | 2 | 21 | 24 | -0.94 | 18.94 | 0
1249 | TORONTO BUTTONVILLE A | 2 | 22 | 1 | -1.12 | 19.12 | 0
1250 | TORONTO BUTTONVILLE A | 2 | 22 | 2 | -1.44 | 19.44 | 0
1251 | TORONTO BUTTONVILLE A | 2 | 22 | 3 | -1.84 | 19.84 | 0
1252 | TORONTO BUTTONVILLE A | 2 | 22 | 4 | -1.7 | 19.7 | 0
1253 | TORONTO BUTTONVILLE A | 2 | 22 | 5 | -1.54 | 19.54 | 0
1254 | TORONTO BUTTONVILLE A | 2 | 22 | 6 | -1.92 | 19.92 | 0
1255 | TORONTO BUTTONVILLE A | 2 | 22 | 7 | -1.82 | 19.82 | 0
1256 | TORONTO BUTTONVILLE A | 2 | 22 | 8 | -1.72 | 19.72 | 0
1257 | TORONTO BUTTONVILLE A | 2 | 22 | 9 | -1.24 | 19.24 | 0
1258 | TORONTO BUTTONVILLE A | 2 | 22 | 10 | -0.5 | 18.5 | 0
1259 | TORONTO BUTTONVILLE A | 2 | 22 | 11 | 0.32 | 17.68 | 0
1260 | TORONTO BUTTONVILLE A | 2 | 22 | 12 | 1.16 | 16.84 | 0
1261 | TORONTO BUTTONVILLE A | 2 | 22 | 13 | 1.74 | 16.26 | 0
1262 | TORONTO BUTTONVILLE A | 2 | 22 | 14 | 2.16 | 15.84 | 0
1263 | TORONTO BUTTONVILLE A | 2 | 22 | 15 | 2.58 | 15.42 | 0
1264 | TORONTO BUTTONVILLE A | 2 | 22 | 16 | 3.04 | 14.96 | 0
1265 | TORONTO BUTTONVILLE A | 2 | 22 | 17 | 3.12 | 14.88 | 0
1266 | TORONTO BUTTONVILLE A | 2 | 22 | 18 | 2.72 | 15.28 | 0
1267 | TORONTO BUTTONVILLE A | 2 | 22 | 19 | 2.14 | 15.86 | 0
1268 | TORONTO BUTTONVILLE A | 2 | 22 | 20 | 1.38 | 16.62 | 0
1269 | TORONTO BUTTONVILLE A | 2 | 22 | 21 | 0.86 | 17.14 | 0
1270 | TORONTO BUTTONVILLE A | 2 | 22 | 22 | 0.48 | 17.52 | 0
1271 | TORONTO BUTTONVILLE A | 2 | 22 | 23 | 0.1 | 17.9 | 0
1272 | TORONTO BUTTONVILLE A | 2 | 22 | 24 | 0.1 | 17.9 | 0
1273 | TORONTO BUTTONVILLE A | 2 | 23 | 1 | -0.18 | 18.18 | 0
1274 | TORONTO BUTTONVILLE A | 2 | 23 | 2 | -0.4 | 18.4 | 0
1275 | TORONTO BUTTONVILLE A | 2 | 23 | 3 | -0.48 | 18.48 | 0
1276 | TORONTO BUTTONVILLE A | 2 | 23 | 4 | -0.6 | 18.6 | 0
1277 | TORONTO BUTTONVILLE A | 2 | 23 | 5 | -0.4 | 18.4 | 0
1278 | TORONTO BUTTONVILLE A | 2 | 23 | 6 | -0.62 | 18.62 | 0
1279 | TORONTO BUTTONVILLE A | 2 | 23 | 7 | 0.26 | 17.74 | 0
1280 | TORONTO BUTTONVILLE A | 2 | 23 | 8 | 0.32 | 17.68 | 0
1281 | TORONTO BUTTONVILLE A | 2 | 23 | 9 | 0.92 | 17.08 | 0
1282 | TORONTO BUTTONVILLE A | 2 | 23 | 10 | 2.26 | 15.74 | 0
1283 | TORONTO BUTTONVILLE A | 2 | 23 | 11 | 3.6 | 14.4 | 0
1284 | TORONTO BUTTONVILLE A | 2 | 23 | 12 | 4.28 | 13.72 | 0
1285 | TORONTO BUTTONVILLE A | 2 | 23 | 13 | 5.38 | 12.62 | 0
1286 | TORONTO BUTTONVILLE A | 2 | 23 | 14 | 5.96 | 12.04 | 0
1287 | TORONTO BUTTONVILLE A | 2 | 23 | 15 | 6.06 | 11.94 | 0
1288 | TORONTO BUTTONVILLE A | 2 | 23 | 16 | 6.04 | 11.96 | 0
1289 | TORONTO BUTTONVILLE A | 2 | 23 | 17 | 5.22 | 12.78 | 0
1290 | TORONTO BUTTONVILLE A | 2 | 23 | 18 | 5.08 | 12.92 | 0
1291 | TORONTO BUTTONVILLE A | 2 | 23 | 19 | 4.42 | 13.58 | 0
1292 | TORONTO BUTTONVILLE A | 2 | 23 | 20 | 4.04 | 13.96 | 0
1293 | TORONTO BUTTONVILLE A | 2 | 23 | 21 | 4.22 | 13.78 | 0
1294 | TORONTO BUTTONVILLE A | 2 | 23 | 22 | 3.64 | 14.36 | 0
1295 | TORONTO BUTTONVILLE A | 2 | 23 | 23 | 3.36 | 14.64 | 0
1296 | TORONTO BUTTONVILLE A | 2 | 23 | 24 | 3.14 | 14.86 | 0
1297 | TORONTO BUTTONVILLE A | 2 | 24 | 1 | 2.94 | 15.06 | 0
1298 | TORONTO BUTTONVILLE A | 2 | 24 | 2 | 2.78 | 15.22 | 0
1299 | TORONTO BUTTONVILLE A | 2 | 24 | 3 | 2.24 | 15.76 | 0
1300 | TORONTO BUTTONVILLE A | 2 | 24 | 4 | 1.54 | 16.46 | 0
1301 | TORONTO BUTTONVILLE A | 2 | 24 | 5 | 1.16 | 16.84 | 0
1302 | TORONTO BUTTONVILLE A | 2 | 24 | 6 | 1.38 | 16.62 | 0
1303 | TORONTO BUTTONVILLE A | 2 | 24 | 7 | 1.64 | 16.36 | 0
1304 | TORONTO BUTTONVILLE A | 2 | 24 | 8 | 1.42 | 16.58 | 0
1305 | TORONTO BUTTONVILLE A | 2 | 24 | 9 | 1.6 | 16.4 | 0
1306 | TORONTO BUTTONVILLE A | 2 | 24 | 10 | 1.9 | 16.1 | 0
1307 | TORONTO BUTTONVILLE A | 2 | 24 | 11 | 2.86 | 15.14 | 0
1308 | TORONTO BUTTONVILLE A | 2 | 24 | 12 | 3.56 | 14.44 | 0
1309 | TORONTO BUTTONVILLE A | 2 | 24 | 13 | 4.64 | 13.36 | 0
1310 | TORONTO BUTTONVILLE A | 2 | 24 | 14 | 5.18 | 12.82 | 0
1311 | TORONTO BUTTONVILLE A | 2 | 24 | 15 | 5.14 | 12.86 | 0
1312 | TORONTO BUTTONVILLE A | 2 | 24 | 16 | 5.06 | 12.94 | 0
1313 | TORONTO BUTTONVILLE A | 2 | 24 | 17 | 5.32 | 12.68 | 0
1314 | TORONTO BUTTONVILLE A | 2 | 24 | 18 | 5.14 | 12.86 | 0
1315 | TORONTO BUTTONVILLE A | 2 | 24 | 19 | 4.38 | 13.62 | 0
1316 | TORONTO BUTTONVILLE A | 2 | 24 | 20 | 3.32 | 14.68 | 0
1317 | TORONTO BUTTONVILLE A | 2 | 24 | 21 | 2.72 | 15.28 | 0
1318 | TORONTO BUTTONVILLE A | 2 | 24 | 22 | 1.58 | 16.42 | 0
1319 | TORONTO BUTTONVILLE A | 2 | 24 | 23 | 0.98 | 17.02 | 0
1320 | TORONTO BUTTONVILLE A | 2 | 24 | 24 | 0.64 | 17.36 | 0
1321 | TORONTO BUTTONVILLE A | 2 | 25 | 1 | 0.52 | 17.48 | 0
1322 | TORONTO BUTTONVILLE A | 2 | 25 | 2 | 0.38 | 17.62 | 0
1323 | TORONTO BUTTONVILLE A | 2 | 25 | 3 | 0.12 | 17.88 | 0
1324 | TORONTO BUTTONVILLE A | 2 | 25 | 4 | 0.14 | 17.86 | 0
1325 | TORONTO BUTTONVILLE A | 2 | 25 | 5 | -0.1 | 18.1 | 0
1326 | TORONTO BUTTONVILLE A | 2 | 25 | 6 | -0.24 | 18.24 | 0
1327 | TORONTO BUTTONVILLE A | 2 | 25 | 7 | -0.48 | 18.48 | 0
1328 | TORONTO BUTTONVILLE A | 2 | 25 | 8 | -0.76 | 18.76 | 0
1329 | TORONTO BUTTONVILLE A | 2 | 25 | 9 | -0.58 | 18.58 | 0
1330 | TORONTO BUTTONVILLE A | 2 | 25 | 10 | 0.1 | 17.9 | 0
1331 | TORONTO BUTTONVILLE A | 2 | 25 | 11 | 0.58 | 17.42 | 0
1332 | TORONTO BUTTONVILLE A | 2 | 25 | 12 | 1.96 | 16.04 | 0
1333 | TORONTO BUTTONVILLE A | 2 | 25 | 13 | 2.5 | 15.5 | 0
1334 | TORONTO BUTTONVILLE A | 2 | 25 | 14 | 3.95 | 14.05 | 0
1335 | TORONTO BUTTONVILLE A | 2 | 25 | 15 | 3.8 | 14.2 | 0
1336 | TORONTO BUTTONVILLE A | 2 | 25 | 16 | 3.375 | 14.625 | 0
1337 | TORONTO BUTTONVILLE A | 2 | 25 | 17 | 2.44 | 15.56 | 0
1338 | TORONTO BUTTONVILLE A | 2 | 25 | 18 | 1.72 | 16.28 | 0
1339 | TORONTO BUTTONVILLE A | 2 | 25 | 19 | 0.84 | 17.16 | 0
1340 | TORONTO BUTTONVILLE A | 2 | 25 | 20 | 0.24 | 17.76 | 0
1341 | TORONTO BUTTONVILLE A | 2 | 25 | 21 | -0.34 | 18.34 | 0
1342 | TORONTO BUTTONVILLE A | 2 | 25 | 22 | -0.78 | 18.78 | 0
1343 | TORONTO BUTTONVILLE A | 2 | 25 | 23 | -1.24 | 19.24 | 0
1344 | TORONTO BUTTONVILLE A | 2 | 25 | 24 | -1.32 | 19.32 | 0
1345 | TORONTO BUTTONVILLE A | 2 | 26 | 1 | -1.36 | 19.36 | 0
1346 | TORONTO BUTTONVILLE A | 2 | 26 | 2 | -1.82 | 19.82 | 0
1347 | TORONTO BUTTONVILLE A | 2 | 26 | 3 | -2.44 | 20.44 | 0
1348 | TORONTO BUTTONVILLE A | 2 | 26 | 4 | -2.74 | 20.74 | 0
1349 | TORONTO BUTTONVILLE A | 2 | 26 | 5 | -3.12 | 21.12 | 0
1350 | TORONTO BUTTONVILLE A | 2 | 26 | 6 | -3.78 | 21.78 | 0
1351 | TORONTO BUTTONVILLE A | 2 | 26 | 7 | -4.4 | 22.4 | 0
1352 | TORONTO BUTTONVILLE A | 2 | 26 | 8 | -4.46 | 22.46 | 0
1353 | TORONTO BUTTONVILLE A | 2 | 26 | 9 | -3.82 | 21.82 | 0
1354 | TORONTO BUTTONVILLE A | 2 | 26 | 10 | -3 | 21 | 0
1355 | TORONTO BUTTONVILLE A | 2 | 26 | 11 | -1.76 | 19.76 | 0
1356 | TORONTO BUTTONVILLE A | 2 | 26 | 12 | -1.04 | 19.04 | 0
1357 | TORONTO BUTTONVILLE A | 2 | 26 | 13 | -0.6 | 18.6 | 0
1358 | TORONTO BUTTONVILLE A | 2 | 26 | 14 | -0.32 | 18.32 | 0
1359 | TORONTO BUTTONVILLE A | 2 | 26 | 15 | -0.36 | 18.36 | 0
1360 | TORONTO BUTTONVILLE A | 2 | 26 | 16 | 0.12 | 17.88 | 0
1361 | TORONTO BUTTONVILLE A | 2 | 26 | 17 | -0.06 | 18.06 | 0
1362 | TORONTO BUTTONVILLE A | 2 | 26 | 18 | -0.76 | 18.76 | 0
1363 | TORONTO BUTTONVILLE A | 2 | 26 | 19 | -1.48 | 19.48 | 0
1364 | TORONTO BUTTONVILLE A | 2 | 26 | 20 | -2 | 20 | 0
1365 | TORONTO BUTTONVILLE A | 2 | 26 | 21 | -2.18 | 20.18 | 0
1366 | TORONTO BUTTONVILLE A | 2 | 26 | 22 | -2.54 | 20.54 | 0
1367 | TORONTO BUTTONVILLE A | 2 | 26 | 23 | -2.96 | 20.96 | 0
1368 | TORONTO BUTTONVILLE A | 2 | 26 | 24 | -3 | 21 | 0
1369 | TORONTO BUTTONVILLE A | 2 | 27 | 1 | -3.5 | 21.5 | 0
1370 | TORONTO BUTTONVILLE A | 2 | 27 | 2 | -3.68 | 21.68 | 0
1371 | TORONTO BUTTONVILLE A | 2 | 27 | 3 | -3.82 | 21.82 | 0
1372 | TORONTO BUTTONVILLE A | 2 | 27 | 4 | -3.5 | 21.5 | 0
1373 | TORONTO BUTTONVILLE A | 2 | 27 | 5 | -2.94 | 20.94 | 0
1374 | TORONTO BUTTONVILLE A | 2 | 27 | 6 | -3.42 | 21.42 | 0
1375 | TORONTO BUTTONVILLE A | 2 | 27 | 7 | -3.66 | 21.66 | 0
1376 | TORONTO BUTTONVILLE A | 2 | 27 | 8 | -3.76 | 21.76 | 0
1377 | TORONTO BUTTONVILLE A | 2 | 27 | 9 | -2.9 | 20.9 | 0
1378 | TORONTO BUTTONVILLE A | 2 | 27 | 10 | -1.64 | 19.64 | 0
1379 | TORONTO BUTTONVILLE A | 2 | 27 | 11 | -0.24 | 18.24 | 0
1380 | TORONTO BUTTONVILLE A | 2 | 27 | 12 | 0.54 | 17.46 | 0
1381 | TORONTO BUTTONVILLE A | 2 | 27 | 13 | 1.48 | 16.52 | 0
1382 | TORONTO BUTTONVILLE A | 2 | 27 | 14 | 1.76 | 16.24 | 0
1383 | TORONTO BUTTONVILLE A | 2 | 27 | 15 | 1.98 | 16.02 | 0
1384 | TORONTO BUTTONVILLE A | 2 | 27 | 16 | 2.1 | 15.9 | 0
1385 | TORONTO BUTTONVILLE A | 2 | 27 | 17 | 2.16 | 15.84 | 0
1386 | TORONTO BUTTONVILLE A | 2 | 27 | 18 | 1.8 | 16.2 | 0
1387 | TORONTO BUTTONVILLE A | 2 | 27 | 19 | 0.7 | 17.3 | 0
1388 | TORONTO BUTTONVILLE A | 2 | 27 | 20 | -0.22 | 18.22 | 0
1389 | TORONTO BUTTONVILLE A | 2 | 27 | 21 | -1.06 | 19.06 | 0
1390 | TORONTO BUTTONVILLE A | 2 | 27 | 22 | -1.6 | 19.6 | 0
1391 | TORONTO BUTTONVILLE A | 2 | 27 | 23 | -1.94 | 19.94 | 0
1392 | TORONTO BUTTONVILLE A | 2 | 27 | 24 | -2.86 | 20.86 | 0
1393 | TORONTO BUTTONVILLE A | 2 | 28 | 1 | -3.12 | 21.12 | 0
1394 | TORONTO BUTTONVILLE A | 2 | 28 | 2 | -3.4 | 21.4 | 0
1395 | TORONTO BUTTONVILLE A | 2 | 28 | 3 | -3.8 | 21.8 | 0
1396 | TORONTO BUTTONVILLE A | 2 | 28 | 4 | -4.58 | 22.58 | 0
1397 | TORONTO BUTTONVILLE A | 2 | 28 | 5 | -4.2 | 22.2 | 0
1398 | TORONTO BUTTONVILLE A | 2 | 28 | 6 | -4.36 | 22.36 | 0
1399 | TORONTO BUTTONVILLE A | 2 | 28 | 7 | -4.76 | 22.76 | 0
1400 | TORONTO BUTTONVILLE A | 2 | 28 | 8 | -4.48 | 22.48 | 0
1401 | TORONTO BUTTONVILLE A | 2 | 28 | 9 | -3.92 | 21.92 | 0
1402 | TORONTO BUTTONVILLE A | 2 | 28 | 10 | -2.22 | 20.22 | 0
1403 | TORONTO BUTTONVILLE A | 2 | 28 | 11 | -1.1 | 19.1 | 0
1404 | TORONTO BUTTONVILLE A | 2 | 28 | 12 | 0.22 | 17.78 | 0
1405 | TORONTO BUTTONVILLE A | 2 | 28 | 13 | 1.42 | 16.58 | 0
1406 | TORONTO BUTTONVILLE A | 2 | 28 | 14 | 1.78 | 16.22 | 0
1407 | TORONTO BUTTONVILLE A | 2 | 28 | 15 | 2.32 | 15.68 | 0
1408 | TORONTO BUTTONVILLE A | 2 | 28 | 16 | 2.44 | 15.56 | 0
1409 | TORONTO BUTTONVILLE A | 2 | 28 | 17 | 2.12 | 15.88 | 0
1410 | TORONTO BUTTONVILLE A | 2 | 28 | 18 | 1.78 | 16.22 | 0
1411 | TORONTO BUTTONVILLE A | 2 | 28 | 19 | 0.9 | 17.1 | 0
1412 | TORONTO BUTTONVILLE A | 2 | 28 | 20 | -0.26 | 18.26 | 0
1413 | TORONTO BUTTONVILLE A | 2 | 28 | 21 | -0.92 | 18.92 | 0
1414 | TORONTO BUTTONVILLE A | 2 | 28 | 22 | -1.18 | 19.18 | 0
1415 | TORONTO BUTTONVILLE A | 2 | 28 | 23 | -0.84 | 18.84 | 0
1416 | TORONTO BUTTONVILLE A | 2 | 28 | 24 | -1.48 | 19.48 | 0
1417 | TORONTO BUTTONVILLE A | 2 | 29 | 1 | -11.6 | 29.6 | 0
1417 | TORONTO BUTTONVILLE A | 3 | 1 | 1 | 1.1 | 16.9 | 0
1418 | TORONTO BUTTONVILLE A | 2 | 29 | 2 | -12.1 | 30.1 | 0
1418 | TORONTO BUTTONVILLE A | 3 | 1 | 2 | 1.05 | 16.95 | 0
1419 | TORONTO BUTTONVILLE A | 2 | 29 | 3 | -12.4 | 30.4 | 0
1419 | TORONTO BUTTONVILLE A | 3 | 1 | 3 | 0.825 | 17.175 | 0
1420 | TORONTO BUTTONVILLE A | 2 | 29 | 4 | -12.8 | 30.8 | 0
1420 | TORONTO BUTTONVILLE A | 3 | 1 | 4 | 0.425 | 17.575 | 0
1421 | TORONTO BUTTONVILLE A | 2 | 29 | 5 | -13.9 | 31.9 | 0
1421 | TORONTO BUTTONVILLE A | 3 | 1 | 5 | -0.15 | 18.15 | 0
1422 | TORONTO BUTTONVILLE A | 2 | 29 | 6 | -15.6 | 33.6 | 0
1422 | TORONTO BUTTONVILLE A | 3 | 1 | 6 | -0.65 | 18.65 | 0
1423 | TORONTO BUTTONVILLE A | 2 | 29 | 7 | -15.2 | 33.2 | 0
1423 | TORONTO BUTTONVILLE A | 3 | 1 | 7 | -1.15 | 19.15 | 0
1424 | TORONTO BUTTONVILLE A | 2 | 29 | 8 | -15.5 | 33.5 | 0
1424 | TORONTO BUTTONVILLE A | 3 | 1 | 8 | -0.625 | 18.625 | 0
1425 | TORONTO BUTTONVILLE A | 2 | 29 | 9 | -14.5 | 32.5 | 0
1425 | TORONTO BUTTONVILLE A | 3 | 1 | 9 | 0.125 | 17.875 | 0
1426 | TORONTO BUTTONVILLE A | 2 | 29 | 10 | -14.1 | 32.1 | 0
1426 | TORONTO BUTTONVILLE A | 3 | 1 | 10 | 0.725 | 17.275 | 0
1427 | TORONTO BUTTONVILLE A | 2 | 29 | 11 | -12.3 | 30.3 | 0
1427 | TORONTO BUTTONVILLE A | 3 | 1 | 11 | 2.175 | 15.825 | 0
1428 | TORONTO BUTTONVILLE A | 2 | 29 | 12 | -10.3 | 28.3 | 0
1428 | TORONTO BUTTONVILLE A | 3 | 1 | 12 | 2.575 | 15.425 | 0
1429 | TORONTO BUTTONVILLE A | 2 | 29 | 13 | -9.1 | 27.1 | 0
1429 | TORONTO BUTTONVILLE A | 3 | 1 | 13 | 2.625 | 15.375 | 0
1430 | TORONTO BUTTONVILLE A | 2 | 29 | 14 | -7.6 | 25.6 | 0
1430 | TORONTO BUTTONVILLE A | 3 | 1 | 14 | 3.15 | 14.85 | 0
1431 | TORONTO BUTTONVILLE A | 2 | 29 | 15 | -7 | 25 | 0
1431 | TORONTO BUTTONVILLE A | 3 | 1 | 15 | 3.125 | 14.875 | 0
1432 | TORONTO BUTTONVILLE A | 2 | 29 | 16 | -6.2 | 24.2 | 0
1432 | TORONTO BUTTONVILLE A | 3 | 1 | 16 | 2.55 | 15.45 | 0
1433 | TORONTO BUTTONVILLE A | 2 | 29 | 17 | -5.6 | 23.6 | 0
1433 | TORONTO BUTTONVILLE A | 3 | 1 | 17 | 1.675 | 16.325 | 0
1434 | TORONTO BUTTONVILLE A | 2 | 29 | 18 | -7.2 | 25.2 | 0
1434 | TORONTO BUTTONVILLE A | 3 | 1 | 18 | 1.4 | 16.6 | 0
1435 | TORONTO BUTTONVILLE A | 2 | 29 | 19 | -7.8 | 25.8 | 0
1435 | TORONTO BUTTONVILLE A | 3 | 1 | 19 | 0.675 | 17.325 | 0
1436 | TORONTO BUTTONVILLE A | 2 | 29 | 20 | -7.8 | 25.8 | 0
1436 | TORONTO BUTTONVILLE A | 3 | 1 | 20 | 0.175 | 17.825 | 0
1437 | TORONTO BUTTONVILLE A | 2 | 29 | 21 | -7.9 | 25.9 | 0
1437 | TORONTO BUTTONVILLE A | 3 | 1 | 21 | -0.6 | 18.6 | 0
1438 | TORONTO BUTTONVILLE A | 2 | 29 | 22 | -8.4 | 26.4 | 0
1438 | TORONTO BUTTONVILLE A | 3 | 1 | 22 | -1.675 | 19.675 | 0
1439 | TORONTO BUTTONVILLE A | 2 | 29 | 23 | -11.6 | 29.6 | 0
1439 | TORONTO BUTTONVILLE A | 3 | 1 | 23 | -2.725 | 20.725 | 0
1440 | TORONTO BUTTONVILLE A | 2 | 29 | 24 | -11 | 29 | 0
1440 | TORONTO BUTTONVILLE A | 3 | 1 | 24 | -3.725 | 21.725 | 0
1441 | TORONTO BUTTONVILLE A | 3 | 1 | 1 | -12.4 | 30.4 | 0
1441 | TORONTO BUTTONVILLE A | 3 | 2 | 1 | -5.175 | 23.175 | 0
1442 | TORONTO BUTTONVILLE A | 3 | 1 | 2 | -13.2 | 31.2 | 0
1442 | TORONTO BUTTONVILLE A | 3 | 2 | 2 | -6.25 | 24.25 | 0
1443 | TORONTO BUTTONVILLE A | 3 | 1 | 3 | -14.2 | 32.2 | 0
1443 | TORONTO BUTTONVILLE A | 3 | 2 | 3 | -6.775 | 24.775 | 0
1444 | TORONTO BUTTONVILLE A | 3 | 1 | 4 | -13.7 | 31.7 | 0
1444 | TORONTO BUTTONVILLE A | 3 | 2 | 4 | -7.175 | 25.175 | 0
1445 | TORONTO BUTTONVILLE A | 3 | 1 | 5 | -13.2 | 31.2 | 0
1445 | TORONTO BUTTONVILLE A | 3 | 2 | 5 | -6.925 | 24.925 | 0
1446 | TORONTO BUTTONVILLE A | 3 | 1 | 6 | -11.2 | 29.2 | 0
1446 | TORONTO BUTTONVILLE A | 3 | 2 | 6 | -6.95 | 24.95 | 0
1447 | TORONTO BUTTONVILLE A | 3 | 1 | 7 | -10.7 | 28.7 | 0
1447 | TORONTO BUTTONVILLE A | 3 | 2 | 7 | -6.825 | 24.825 | 0
1448 | TORONTO BUTTONVILLE A | 3 | 1 | 8 | -11.3 | 29.3 | 0
1448 | TORONTO BUTTONVILLE A | 3 | 2 | 8 | -6.825 | 24.825 | 0
1449 | TORONTO BUTTONVILLE A | 3 | 1 | 9 | -8.3 | 26.3 | 0
1449 | TORONTO BUTTONVILLE A | 3 | 2 | 9 | -6.5 | 24.5 | 0
1450 | TORONTO BUTTONVILLE A | 3 | 1 | 10 | -4.5 | 22.5 | 0
1450 | TORONTO BUTTONVILLE A | 3 | 2 | 10 | -5.775 | 23.775 | 0
1451 | TORONTO BUTTONVILLE A | 3 | 1 | 11 | -2.3 | 20.3 | 0
1451 | TORONTO BUTTONVILLE A | 3 | 2 | 11 | -5 | 23 | 0
1452 | TORONTO BUTTONVILLE A | 3 | 1 | 12 | -0.6 | 18.6 | 0
1452 | TORONTO BUTTONVILLE A | 3 | 2 | 12 | -4.425 | 22.425 | 0
1453 | TORONTO BUTTONVILLE A | 3 | 1 | 13 | 1 | 17 | 0
1453 | TORONTO BUTTONVILLE A | 3 | 2 | 13 | -3.4 | 21.4 | 0
1454 | TORONTO BUTTONVILLE A | 3 | 1 | 14 | 1.2 | 16.8 | 0
1454 | TORONTO BUTTONVILLE A | 3 | 2 | 14 | -2.675 | 20.675 | 0
1455 | TORONTO BUTTONVILLE A | 3 | 1 | 15 | 0.9 | 17.1 | 0
1455 | TORONTO BUTTONVILLE A | 3 | 2 | 15 | -2.275 | 20.275 | 0
1456 | TORONTO BUTTONVILLE A | 3 | 1 | 16 | 1.4 | 16.6 | 0
1456 | TORONTO BUTTONVILLE A | 3 | 2 | 16 | -1.9 | 19.9 | 0
1457 | TORONTO BUTTONVILLE A | 3 | 1 | 17 | 0.9 | 17.1 | 0
1457 | TORONTO BUTTONVILLE A | 3 | 2 | 17 | -1.675 | 19.675 | 0
1458 | TORONTO BUTTONVILLE A | 3 | 1 | 18 | 0.6 | 17.4 | 0
1458 | TORONTO BUTTONVILLE A | 3 | 2 | 18 | -1.7 | 19.7 | 0
1459 | TORONTO BUTTONVILLE A | 3 | 1 | 19 | 0.3 | 17.7 | 0
1459 | TORONTO BUTTONVILLE A | 3 | 2 | 19 | -2.325 | 20.325 | 0
1460 | TORONTO BUTTONVILLE A | 3 | 1 | 20 | 0.4 | 17.6 | 0
1460 | TORONTO BUTTONVILLE A | 3 | 2 | 20 | -2.825 | 20.825 | 0
1461 | TORONTO BUTTONVILLE A | 3 | 1 | 21 | 0.6 | 17.4 | 0
1461 | TORONTO BUTTONVILLE A | 3 | 2 | 21 | -3.35 | 21.35 | 0
1462 | TORONTO BUTTONVILLE A | 3 | 1 | 22 | 0.8 | 17.2 | 0
1462 | TORONTO BUTTONVILLE A | 3 | 2 | 22 | -3.625 | 21.625 | 0
1463 | TORONTO BUTTONVILLE A | 3 | 1 | 23 | 1.1 | 16.9 | 0
1463 | TORONTO BUTTONVILLE A | 3 | 2 | 23 | -3.875 | 21.875 | 0
1464 | TORONTO BUTTONVILLE A | 3 | 1 | 24 | 1 | 17 | 0
1464 | TORONTO BUTTONVILLE A | 3 | 2 | 24 | -3.875 | 21.875 | 0
1465 | TORONTO BUTTONVILLE A | 3 | 2 | 1 | 0.2 | 17.8 | 0
1465 | TORONTO BUTTONVILLE A | 3 | 3 | 1 | -3.425 | 21.425 | 0
1466 | TORONTO BUTTONVILLE A | 3 | 2 | 2 | 0.6 | 17.4 | 0
1466 | TORONTO BUTTONVILLE A | 3 | 3 | 2 | -3.475 | 21.475 | 0
1467 | TORONTO BUTTONVILLE A | 3 | 2 | 3 | 1.3 | 16.7 | 0
1467 | TORONTO BUTTONVILLE A | 3 | 3 | 3 | -3.75 | 21.75 | 0
1468 | TORONTO BUTTONVILLE A | 3 | 2 | 4 | 1.2 | 16.8 | 0
1468 | TORONTO BUTTONVILLE A | 3 | 3 | 4 | -3.9 | 21.9 | 0
1469 | TORONTO BUTTONVILLE A | 3 | 2 | 5 | 1 | 17 | 0
1469 | TORONTO BUTTONVILLE A | 3 | 3 | 5 | -3.95 | 21.95 | 0
1470 | TORONTO BUTTONVILLE A | 3 | 2 | 6 | -0.9 | 18.9 | 0
1470 | TORONTO BUTTONVILLE A | 3 | 3 | 6 | -3.975 | 21.975 | 0
1471 | TORONTO BUTTONVILLE A | 3 | 2 | 7 | -1.1 | 19.1 | 0
1471 | TORONTO BUTTONVILLE A | 3 | 3 | 7 | -4.25 | 22.25 | 0
1472 | TORONTO BUTTONVILLE A | 3 | 2 | 8 | 0 | 18 | 0
1472 | TORONTO BUTTONVILLE A | 3 | 3 | 8 | -4.6 | 22.6 | 0
1473 | TORONTO BUTTONVILLE A | 3 | 2 | 9 | 1 | 17 | 0
1473 | TORONTO BUTTONVILLE A | 3 | 3 | 9 | -4.2 | 22.2 | 0
1474 | TORONTO BUTTONVILLE A | 3 | 2 | 10 | 5.7 | 12.3 | 0
1474 | TORONTO BUTTONVILLE A | 3 | 3 | 10 | -3.275 | 21.275 | 0
1475 | TORONTO BUTTONVILLE A | 3 | 2 | 11 | 6 | 12 | 0
1475 | TORONTO BUTTONVILLE A | 3 | 3 | 11 | -2.45 | 20.45 | 0
1476 | TORONTO BUTTONVILLE A | 3 | 2 | 12 | 5.4 | 12.6 | 0
1476 | TORONTO BUTTONVILLE A | 3 | 3 | 12 | -1.5 | 19.5 | 0
1477 | TORONTO BUTTONVILLE A | 3 | 2 | 13 | 5.3 | 12.7 | 0
1477 | TORONTO BUTTONVILLE A | 3 | 3 | 13 | -1.175 | 19.175 | 0
1478 | TORONTO BUTTONVILLE A | 3 | 2 | 14 | 5.7 | 12.3 | 0
1478 | TORONTO BUTTONVILLE A | 3 | 3 | 14 | -0.675 | 18.675 | 0
1479 | TORONTO BUTTONVILLE A | 3 | 2 | 15 | 5.6 | 12.4 | 0
1479 | TORONTO BUTTONVILLE A | 3 | 3 | 15 | -0.425 | 18.425 | 0
1480 | TORONTO BUTTONVILLE A | 3 | 2 | 16 | 5.8 | 12.2 | 0
1480 | TORONTO BUTTONVILLE A | 3 | 3 | 16 | -0.425 | 18.425 | 0
1481 | TORONTO BUTTONVILLE A | 3 | 2 | 17 | 6.1 | 11.9 | 0
1481 | TORONTO BUTTONVILLE A | 3 | 3 | 17 | -0.475 | 18.475 | 0
1482 | TORONTO BUTTONVILLE A | 3 | 2 | 18 | 5.9 | 12.1 | 0
1482 | TORONTO BUTTONVILLE A | 3 | 3 | 18 | -1.175 | 19.175 | 0
1483 | TORONTO BUTTONVILLE A | 3 | 2 | 19 | 5.5 | 12.5 | 0
1483 | TORONTO BUTTONVILLE A | 3 | 3 | 19 | -2.45 | 20.45 | 0
1484 | TORONTO BUTTONVILLE A | 3 | 2 | 20 | 4.6 | 13.4 | 0
1484 | TORONTO BUTTONVILLE A | 3 | 3 | 20 | -3.175 | 21.175 | 0
1485 | TORONTO BUTTONVILLE A | 3 | 2 | 21 | 3.2 | 14.8 | 0
1485 | TORONTO BUTTONVILLE A | 3 | 3 | 21 | -3.4 | 21.4 | 0
1486 | TORONTO BUTTONVILLE A | 3 | 2 | 22 | 1.6 | 16.4 | 0
1486 | TORONTO BUTTONVILLE A | 3 | 3 | 22 | -3.95 | 21.95 | 0
1487 | TORONTO BUTTONVILLE A | 3 | 2 | 23 | 1 | 17 | 0
1487 | TORONTO BUTTONVILLE A | 3 | 3 | 23 | -4.55 | 22.55 | 0
1488 | TORONTO BUTTONVILLE A | 3 | 2 | 24 | 0 | 18 | 0
1488 | TORONTO BUTTONVILLE A | 3 | 3 | 24 | -4.575 | 22.575 | 0
1489 | TORONTO BUTTONVILLE A | 3 | 3 | 1 | -0.9 | 18.9 | 0
1489 | TORONTO BUTTONVILLE A | 3 | 4 | 1 | -4.85 | 22.85 | 0
1490 | TORONTO BUTTONVILLE A | 3 | 3 | 2 | 0.1 | 17.9 | 0
1490 | TORONTO BUTTONVILLE A | 3 | 4 | 2 | -5.25 | 23.25 | 0
1491 | TORONTO BUTTONVILLE A | 3 | 3 | 3 | -0.1 | 18.1 | 0
1491 | TORONTO BUTTONVILLE A | 3 | 4 | 3 | -5.725 | 23.725 | 0
1492 | TORONTO BUTTONVILLE A | 3 | 3 | 4 | 0 | 18 | 0
1492 | TORONTO BUTTONVILLE A | 3 | 4 | 4 | -6.225 | 24.225 | 0
1493 | TORONTO BUTTONVILLE A | 3 | 3 | 5 | 0.1 | 17.9 | 0
1493 | TORONTO BUTTONVILLE A | 3 | 4 | 5 | -7.075 | 25.075 | 0
1494 | TORONTO BUTTONVILLE A | 3 | 3 | 6 | 0 | 18 | 0
1494 | TORONTO BUTTONVILLE A | 3 | 4 | 6 | -8.075 | 26.075 | 0
1495 | TORONTO BUTTONVILLE A | 3 | 3 | 7 | -0.6 | 18.6 | 0
1495 | TORONTO BUTTONVILLE A | 3 | 4 | 7 | -8.85 | 26.85 | 0
1496 | TORONTO BUTTONVILLE A | 3 | 3 | 8 | -0.1 | 18.1 | 0
1496 | TORONTO BUTTONVILLE A | 3 | 4 | 8 | -9.375 | 27.375 | 0
1497 | TORONTO BUTTONVILLE A | 3 | 3 | 9 | 0.5 | 17.5 | 0
1497 | TORONTO BUTTONVILLE A | 3 | 4 | 9 | -9.175 | 27.175 | 0
1498 | TORONTO BUTTONVILLE A | 3 | 3 | 10 | 1.5 | 16.5 | 0
1498 | TORONTO BUTTONVILLE A | 3 | 4 | 10 | -8.4 | 26.4 | 0
1499 | TORONTO BUTTONVILLE A | 3 | 3 | 11 | 2 | 16 | 0
1499 | TORONTO BUTTONVILLE A | 3 | 4 | 11 | -7.875 | 25.875 | 0
1500 | TORONTO BUTTONVILLE A | 3 | 3 | 12 | 2.5 | 15.5 | 0
1500 | TORONTO BUTTONVILLE A | 3 | 4 | 12 | -7.05 | 25.05 | 0
1501 | TORONTO BUTTONVILLE A | 3 | 3 | 13 | 2.7 | 15.3 | 0
1501 | TORONTO BUTTONVILLE A | 3 | 4 | 13 | -6.625 | 24.625 | 0
1502 | TORONTO BUTTONVILLE A | 3 | 3 | 14 | 2.9 | 15.1 | 0
1502 | TORONTO BUTTONVILLE A | 3 | 4 | 14 | -6.225 | 24.225 | 0
1503 | TORONTO BUTTONVILLE A | 3 | 3 | 15 | 2.6 | 15.4 | 0
1503 | TORONTO BUTTONVILLE A | 3 | 4 | 15 | -5.825 | 23.825 | 0
1504 | TORONTO BUTTONVILLE A | 3 | 3 | 16 | 3 | 15 | 0
1504 | TORONTO BUTTONVILLE A | 3 | 4 | 16 | -5.775 | 23.775 | 0
1505 | TORONTO BUTTONVILLE A | 3 | 3 | 17 | 2.9 | 15.1 | 0
1505 | TORONTO BUTTONVILLE A | 3 | 4 | 17 | -6.125 | 24.125 | 0
1506 | TORONTO BUTTONVILLE A | 3 | 3 | 18 | 2.9 | 15.1 | 0
1506 | TORONTO BUTTONVILLE A | 3 | 4 | 18 | -6.625 | 24.625 | 0
1507 | TORONTO BUTTONVILLE A | 3 | 3 | 19 | 3 | 15 | 0
1507 | TORONTO BUTTONVILLE A | 3 | 4 | 19 | -7.45 | 25.45 | 0
1508 | TORONTO BUTTONVILLE A | 3 | 3 | 20 | 2.6 | 15.4 | 0
1508 | TORONTO BUTTONVILLE A | 3 | 4 | 20 | -7.9 | 25.9 | 0
1509 | TORONTO BUTTONVILLE A | 3 | 3 | 21 | 2.2 | 15.8 | 0
1509 | TORONTO BUTTONVILLE A | 3 | 4 | 21 | -8.225 | 26.225 | 0
1510 | TORONTO BUTTONVILLE A | 3 | 3 | 22 | 1.7 | 16.3 | 0
1510 | TORONTO BUTTONVILLE A | 3 | 4 | 22 | -8.575 | 26.575 | 0
1511 | TORONTO BUTTONVILLE A | 3 | 3 | 23 | 1.9 | 16.1 | 0
1511 | TORONTO BUTTONVILLE A | 3 | 4 | 23 | -8.85 | 26.85 | 0
1512 | TORONTO BUTTONVILLE A | 3 | 3 | 24 | 1.7 | 16.3 | 0
1512 | TORONTO BUTTONVILLE A | 3 | 4 | 24 | -9.325 | 27.325 | 0
1513 | TORONTO BUTTONVILLE A | 3 | 4 | 1 | 1.7 | 16.3 | 0
1513 | TORONTO BUTTONVILLE A | 3 | 5 | 1 | -9.725 | 27.725 | 0
1514 | TORONTO BUTTONVILLE A | 3 | 4 | 2 | 2.4 | 15.6 | 0
1514 | TORONTO BUTTONVILLE A | 3 | 5 | 2 | -10.225 | 28.225 | 0
1515 | TORONTO BUTTONVILLE A | 3 | 4 | 3 | 2.5 | 15.5 | 0
1515 | TORONTO BUTTONVILLE A | 3 | 5 | 3 | -10.4 | 28.4 | 0
1516 | TORONTO BUTTONVILLE A | 3 | 4 | 4 | 2.4 | 15.6 | 0
1516 | TORONTO BUTTONVILLE A | 3 | 5 | 4 | -10.775 | 28.775 | 0
1517 | TORONTO BUTTONVILLE A | 3 | 4 | 5 | 2.3 | 15.7 | 0
1517 | TORONTO BUTTONVILLE A | 3 | 5 | 5 | -11 | 29 | 0
1518 | TORONTO BUTTONVILLE A | 3 | 4 | 6 | 2.3 | 15.7 | 0
1518 | TORONTO BUTTONVILLE A | 3 | 5 | 6 | -11.15 | 29.15 | 0
1519 | TORONTO BUTTONVILLE A | 3 | 4 | 7 | 1.9 | 16.1 | 0
1519 | TORONTO BUTTONVILLE A | 3 | 5 | 7 | -11.125 | 29.125 | 0
1520 | TORONTO BUTTONVILLE A | 3 | 4 | 8 | 1.1 | 16.9 | 0
1520 | TORONTO BUTTONVILLE A | 3 | 5 | 8 | -11.075 | 29.075 | 0
1521 | TORONTO BUTTONVILLE A | 3 | 4 | 9 | 1.9 | 16.1 | 0
1521 | TORONTO BUTTONVILLE A | 3 | 5 | 9 | -9.8 | 27.8 | 0
1522 | TORONTO BUTTONVILLE A | 3 | 4 | 10 | 2.8 | 15.2 | 0
1522 | TORONTO BUTTONVILLE A | 3 | 5 | 10 | -8.2 | 26.2 | 0
1523 | TORONTO BUTTONVILLE A | 3 | 4 | 11 | 2.8 | 15.2 | 0
1523 | TORONTO BUTTONVILLE A | 3 | 5 | 11 | -6.65 | 24.65 | 0
1524 | TORONTO BUTTONVILLE A | 3 | 4 | 12 | 4 | 14 | 0
1524 | TORONTO BUTTONVILLE A | 3 | 5 | 12 | -5.65 | 23.65 | 0
1525 | TORONTO BUTTONVILLE A | 3 | 4 | 13 | 4.6 | 13.4 | 0
1525 | TORONTO BUTTONVILLE A | 3 | 5 | 13 | -4.925 | 22.925 | 0
1526 | TORONTO BUTTONVILLE A | 3 | 4 | 14 | 4.5 | 13.5 | 0
1526 | TORONTO BUTTONVILLE A | 3 | 5 | 14 | -3.9 | 21.9 | 0
1527 | TORONTO BUTTONVILLE A | 3 | 4 | 15 | 4.5 | 13.5 | 0
1527 | TORONTO BUTTONVILLE A | 3 | 5 | 15 | -3.425 | 21.425 | 0
1528 | TORONTO BUTTONVILLE A | 3 | 4 | 16 | 4.3 | 13.7 | 0
1528 | TORONTO BUTTONVILLE A | 3 | 5 | 16 | -2.75 | 20.75 | 0
1529 | TORONTO BUTTONVILLE A | 3 | 4 | 17 | 2.5 | 15.5 | 0
1529 | TORONTO BUTTONVILLE A | 3 | 5 | 17 | -3.225 | 21.225 | 0
1530 | TORONTO BUTTONVILLE A | 3 | 4 | 18 | 1.9 | 16.1 | 0
1530 | TORONTO BUTTONVILLE A | 3 | 5 | 18 | -3.475 | 21.475 | 0
1531 | TORONTO BUTTONVILLE A | 3 | 4 | 19 | 1.9 | 16.1 | 0
1531 | TORONTO BUTTONVILLE A | 3 | 5 | 19 | -4.175 | 22.175 | 0
1532 | TORONTO BUTTONVILLE A | 3 | 4 | 20 | 1.3 | 16.7 | 0
1532 | TORONTO BUTTONVILLE A | 3 | 5 | 20 | -4.7 | 22.7 | 0
1533 | TORONTO BUTTONVILLE A | 3 | 4 | 21 | 1.2 | 16.8 | 0
1533 | TORONTO BUTTONVILLE A | 3 | 5 | 21 | -4.9 | 22.9 | 0
1534 | TORONTO BUTTONVILLE A | 3 | 4 | 22 | 1.2 | 16.8 | 0
1534 | TORONTO BUTTONVILLE A | 3 | 5 | 22 | -4.875 | 22.875 | 0
1535 | TORONTO BUTTONVILLE A | 3 | 4 | 23 | 1.3 | 16.7 | 0
1535 | TORONTO BUTTONVILLE A | 3 | 5 | 23 | -5.225 | 23.225 | 0
1536 | TORONTO BUTTONVILLE A | 3 | 4 | 24 | 0.8 | 17.2 | 0
1536 | TORONTO BUTTONVILLE A | 3 | 5 | 24 | -5.525 | 23.525 | 0
1537 | TORONTO BUTTONVILLE A | 3 | 5 | 1 | 0.8 | 17.2 | 0
1537 | TORONTO BUTTONVILLE A | 3 | 6 | 1 | -5.775 | 23.775 | 0
1538 | TORONTO BUTTONVILLE A | 3 | 5 | 2 | 0.6 | 17.4 | 0
1538 | TORONTO BUTTONVILLE A | 3 | 6 | 2 | -5.95 | 23.95 | 0
1539 | TORONTO BUTTONVILLE A | 3 | 5 | 3 | 0.3 | 17.7 | 0
1539 | TORONTO BUTTONVILLE A | 3 | 6 | 3 | -5.725 | 23.725 | 0
1540 | TORONTO BUTTONVILLE A | 3 | 5 | 4 | -0.2 | 18.2 | 0
1540 | TORONTO BUTTONVILLE A | 3 | 6 | 4 | -5.8 | 23.8 | 0
1541 | TORONTO BUTTONVILLE A | 3 | 5 | 5 | -0.4 | 18.4 | 0
1541 | TORONTO BUTTONVILLE A | 3 | 6 | 5 | -5.9 | 23.9 | 0
1542 | TORONTO BUTTONVILLE A | 3 | 5 | 6 | -0.5 | 18.5 | 0
1542 | TORONTO BUTTONVILLE A | 3 | 6 | 6 | -5.75 | 23.75 | 0
1543 | TORONTO BUTTONVILLE A | 3 | 5 | 7 | -1.5 | 19.5 | 0
1543 | TORONTO BUTTONVILLE A | 3 | 6 | 7 | -5.775 | 23.775 | 0
1544 | TORONTO BUTTONVILLE A | 3 | 5 | 8 | -1.6 | 19.6 | 0
1544 | TORONTO BUTTONVILLE A | 3 | 6 | 8 | -5.9 | 23.9 | 0
1545 | TORONTO BUTTONVILLE A | 3 | 5 | 9 | -0.7 | 18.7 | 0
1545 | TORONTO BUTTONVILLE A | 3 | 6 | 9 | -5.6 | 23.6 | 0
1546 | TORONTO BUTTONVILLE A | 3 | 5 | 10 | -0.2 | 18.2 | 0
1546 | TORONTO BUTTONVILLE A | 3 | 6 | 10 | -5.15 | 23.15 | 0
1547 | TORONTO BUTTONVILLE A | 3 | 5 | 11 | 1.2 | 16.8 | 0
1547 | TORONTO BUTTONVILLE A | 3 | 6 | 11 | -4.45 | 22.45 | 0
1548 | TORONTO BUTTONVILLE A | 3 | 5 | 12 | 2.2 | 15.8 | 0
1548 | TORONTO BUTTONVILLE A | 3 | 6 | 12 | -3.875 | 21.875 | 0
1549 | TORONTO BUTTONVILLE A | 3 | 5 | 13 | 3.3 | 14.7 | 0
1549 | TORONTO BUTTONVILLE A | 3 | 6 | 13 | -3.075 | 21.075 | 0
1550 | TORONTO BUTTONVILLE A | 3 | 5 | 14 | 3.6 | 14.4 | 0
1550 | TORONTO BUTTONVILLE A | 3 | 6 | 14 | -2.825 | 20.825 | 0
1551 | TORONTO BUTTONVILLE A | 3 | 5 | 15 | 4.3 | 13.7 | 0
1551 | TORONTO BUTTONVILLE A | 3 | 6 | 15 | -2.875 | 20.875 | 0
1552 | TORONTO BUTTONVILLE A | 3 | 5 | 16 | 5.4 | 12.6 | 0
1552 | TORONTO BUTTONVILLE A | 3 | 6 | 16 | -2.575 | 20.575 | 0
1553 | TORONTO BUTTONVILLE A | 3 | 5 | 17 | 5.3 | 12.7 | 0
1553 | TORONTO BUTTONVILLE A | 3 | 6 | 17 | -2.425 | 20.425 | 0
1554 | TORONTO BUTTONVILLE A | 3 | 5 | 18 | 4.5 | 13.5 | 0
1554 | TORONTO BUTTONVILLE A | 3 | 6 | 18 | -2.7 | 20.7 | 0
1555 | TORONTO BUTTONVILLE A | 3 | 5 | 19 | 3.5 | 14.5 | 0
1555 | TORONTO BUTTONVILLE A | 3 | 6 | 19 | -3.05 | 21.05 | 0
1556 | TORONTO BUTTONVILLE A | 3 | 5 | 20 | 2.1 | 15.9 | 0
1556 | TORONTO BUTTONVILLE A | 3 | 6 | 20 | -3.275 | 21.275 | 0
1557 | TORONTO BUTTONVILLE A | 3 | 5 | 21 | 1.2 | 16.8 | 0
1557 | TORONTO BUTTONVILLE A | 3 | 6 | 21 | -3.225 | 21.225 | 0
1558 | TORONTO BUTTONVILLE A | 3 | 5 | 22 | 0.9 | 17.1 | 0
1558 | TORONTO BUTTONVILLE A | 3 | 6 | 22 | -3.225 | 21.225 | 0
1559 | TORONTO BUTTONVILLE A | 3 | 5 | 23 | 0.5 | 17.5 | 0
1559 | TORONTO BUTTONVILLE A | 3 | 6 | 23 | -3.125 | 21.125 | 0
1560 | TORONTO BUTTONVILLE A | 3 | 5 | 24 | 0.2 | 17.8 | 0
1560 | TORONTO BUTTONVILLE A | 3 | 6 | 24 | -3.175 | 21.175 | 0
1561 | TORONTO BUTTONVILLE A | 3 | 6 | 1 | 0.6 | 17.4 | 0
1561 | TORONTO BUTTONVILLE A | 3 | 7 | 1 | -3.6 | 21.6 | 0
1562 | TORONTO BUTTONVILLE A | 3 | 6 | 2 | 0 | 18 | 0
1562 | TORONTO BUTTONVILLE A | 3 | 7 | 2 | -3.775 | 21.775 | 0
1563 | TORONTO BUTTONVILLE A | 3 | 6 | 3 | -0.5 | 18.5 | 0
1563 | TORONTO BUTTONVILLE A | 3 | 7 | 3 | -3.9 | 21.9 | 0
1564 | TORONTO BUTTONVILLE A | 3 | 6 | 4 | -0.5 | 18.5 | 0
1564 | TORONTO BUTTONVILLE A | 3 | 7 | 4 | -3.725 | 21.725 | 0
1565 | TORONTO BUTTONVILLE A | 3 | 6 | 5 | 0.2 | 17.8 | 0
1565 | TORONTO BUTTONVILLE A | 3 | 7 | 5 | -4.125 | 22.125 | 0
1566 | TORONTO BUTTONVILLE A | 3 | 6 | 6 | 0.6 | 17.4 | 0
1566 | TORONTO BUTTONVILLE A | 3 | 7 | 6 | -4.3 | 22.3 | 0
1567 | TORONTO BUTTONVILLE A | 3 | 6 | 7 | 0.8 | 17.2 | 0
1567 | TORONTO BUTTONVILLE A | 3 | 7 | 7 | -4.075 | 22.075 | 0
1568 | TORONTO BUTTONVILLE A | 3 | 6 | 8 | -0.2 | 18.2 | 0
1568 | TORONTO BUTTONVILLE A | 3 | 7 | 8 | -4.5 | 22.5 | 0
1569 | TORONTO BUTTONVILLE A | 3 | 6 | 9 | 0.1 | 17.9 | 0
1569 | TORONTO BUTTONVILLE A | 3 | 7 | 9 | -2.825 | 20.825 | 0
1570 | TORONTO BUTTONVILLE A | 3 | 6 | 10 | 0.4 | 17.6 | 0
1570 | TORONTO BUTTONVILLE A | 3 | 7 | 10 | -2 | 20 | 0
1571 | TORONTO BUTTONVILLE A | 3 | 6 | 11 | 0.5 | 17.5 | 0
1571 | TORONTO BUTTONVILLE A | 3 | 7 | 11 | -0.975 | 18.975 | 0
1572 | TORONTO BUTTONVILLE A | 3 | 6 | 12 | 0.5 | 17.5 | 0
1572 | TORONTO BUTTONVILLE A | 3 | 7 | 12 | -0.15 | 18.15 | 0
1573 | TORONTO BUTTONVILLE A | 3 | 6 | 13 | 0.3 | 17.7 | 0
1573 | TORONTO BUTTONVILLE A | 3 | 7 | 13 | 0.25 | 17.75 | 0
1574 | TORONTO BUTTONVILLE A | 3 | 6 | 14 | 1.4 | 16.6 | 0
1574 | TORONTO BUTTONVILLE A | 3 | 7 | 14 | 0.7 | 17.3 | 0
1575 | TORONTO BUTTONVILLE A | 3 | 6 | 15 | 2.5 | 15.5 | 0
1575 | TORONTO BUTTONVILLE A | 3 | 7 | 15 | 0.85 | 17.15 | 0
1576 | TORONTO BUTTONVILLE A | 3 | 6 | 16 | 1.8 | 16.2 | 0
1576 | TORONTO BUTTONVILLE A | 3 | 7 | 16 | 0.8 | 17.2 | 0
1577 | TORONTO BUTTONVILLE A | 3 | 6 | 17 | 1.5 | 16.5 | 0
1577 | TORONTO BUTTONVILLE A | 3 | 7 | 17 | 1.25 | 16.75 | 0
1578 | TORONTO BUTTONVILLE A | 3 | 6 | 18 | 0.9 | 17.1 | 0
1578 | TORONTO BUTTONVILLE A | 3 | 7 | 18 | 0.775 | 17.225 | 0
1579 | TORONTO BUTTONVILLE A | 3 | 6 | 19 | 0.6 | 17.4 | 0
1579 | TORONTO BUTTONVILLE A | 3 | 7 | 19 | 0.2 | 17.8 | 0
1580 | TORONTO BUTTONVILLE A | 3 | 6 | 20 | 0.2 | 17.8 | 0
1580 | TORONTO BUTTONVILLE A | 3 | 7 | 20 | -0.875 | 18.875 | 0
1581 | TORONTO BUTTONVILLE A | 3 | 6 | 21 | 0.2 | 17.8 | 0
1581 | TORONTO BUTTONVILLE A | 3 | 7 | 21 | -1.55 | 19.55 | 0
1582 | TORONTO BUTTONVILLE A | 3 | 6 | 22 | 0 | 18 | 0
1582 | TORONTO BUTTONVILLE A | 3 | 7 | 22 | -2.1 | 20.1 | 0
1583 | TORONTO BUTTONVILLE A | 3 | 6 | 23 | -0.5 | 18.5 | 0
1583 | TORONTO BUTTONVILLE A | 3 | 7 | 23 | -2.575 | 20.575 | 0
1584 | TORONTO BUTTONVILLE A | 3 | 6 | 24 | -1.1 | 19.1 | 0
1584 | TORONTO BUTTONVILLE A | 3 | 7 | 24 | -2.925 | 20.925 | 0
1585 | TORONTO BUTTONVILLE A | 3 | 7 | 1 | -1.9 | 19.9 | 0
1585 | TORONTO BUTTONVILLE A | 3 | 8 | 1 | -3.575 | 21.575 | 0
1586 | TORONTO BUTTONVILLE A | 3 | 7 | 2 | -3 | 21 | 0
1586 | TORONTO BUTTONVILLE A | 3 | 8 | 2 | -4.175 | 22.175 | 0
1587 | TORONTO BUTTONVILLE A | 3 | 7 | 3 | -4 | 22 | 0
1587 | TORONTO BUTTONVILLE A | 3 | 8 | 3 | -4.7 | 22.7 | 0
1588 | TORONTO BUTTONVILLE A | 3 | 7 | 4 | -4.9 | 22.9 | 0
1588 | TORONTO BUTTONVILLE A | 3 | 8 | 4 | -5.2 | 23.2 | 0
1589 | TORONTO BUTTONVILLE A | 3 | 7 | 5 | -5.9 | 23.9 | 0
1589 | TORONTO BUTTONVILLE A | 3 | 8 | 5 | -5.525 | 23.525 | 0
1590 | TORONTO BUTTONVILLE A | 3 | 7 | 6 | -6.6 | 24.6 | 0
1590 | TORONTO BUTTONVILLE A | 3 | 8 | 6 | -5.875 | 23.875 | 0
1591 | TORONTO BUTTONVILLE A | 3 | 7 | 7 | -7.3 | 25.3 | 0
1591 | TORONTO BUTTONVILLE A | 3 | 8 | 7 | -5.775 | 23.775 | 0
1592 | TORONTO BUTTONVILLE A | 3 | 7 | 8 | -7.6 | 25.6 | 0
1592 | TORONTO BUTTONVILLE A | 3 | 8 | 8 | -5.9 | 23.9 | 0
1593 | TORONTO BUTTONVILLE A | 3 | 7 | 9 | -6.6 | 24.6 | 0
1593 | TORONTO BUTTONVILLE A | 3 | 8 | 9 | -4.275 | 22.275 | 0
1594 | TORONTO BUTTONVILLE A | 3 | 7 | 10 | -5.8 | 23.8 | 0
1594 | TORONTO BUTTONVILLE A | 3 | 8 | 10 | -5.1 | 23.1 | 0
1595 | TORONTO BUTTONVILLE A | 3 | 7 | 11 | -3.6 | 21.6 | 0
1595 | TORONTO BUTTONVILLE A | 3 | 8 | 11 | -0.5 | 18.5 | 0
1596 | TORONTO BUTTONVILLE A | 3 | 7 | 12 | -1.8 | 19.8 | 0
1596 | TORONTO BUTTONVILLE A | 3 | 8 | 12 | 0.65 | 17.35 | 0
1597 | TORONTO BUTTONVILLE A | 3 | 7 | 13 | -0.9 | 18.9 | 0
1597 | TORONTO BUTTONVILLE A | 3 | 8 | 13 | 1.5 | 16.5 | 0
1598 | TORONTO BUTTONVILLE A | 3 | 7 | 14 | -0.2 | 18.2 | 0
1598 | TORONTO BUTTONVILLE A | 3 | 8 | 14 | 1.975 | 16.025 | 0
1599 | TORONTO BUTTONVILLE A | 3 | 7 | 15 | 1.4 | 16.6 | 0
1599 | TORONTO BUTTONVILLE A | 3 | 8 | 15 | 2.4 | 15.6 | 0
1600 | TORONTO BUTTONVILLE A | 3 | 7 | 16 | 3 | 15 | 0
1600 | TORONTO BUTTONVILLE A | 3 | 8 | 16 | 2.65 | 15.35 | 0
1601 | TORONTO BUTTONVILLE A | 3 | 7 | 17 | 3.7 | 14.3 | 0
1601 | TORONTO BUTTONVILLE A | 3 | 8 | 17 | 2.9 | 15.1 | 0
1602 | TORONTO BUTTONVILLE A | 3 | 7 | 18 | 3.2 | 14.8 | 0
1602 | TORONTO BUTTONVILLE A | 3 | 8 | 18 | 2.525 | 15.475 | 0
1603 | TORONTO BUTTONVILLE A | 3 | 7 | 19 | 1.8 | 16.2 | 0
1603 | TORONTO BUTTONVILLE A | 3 | 8 | 19 | 1.75 | 16.25 | 0
1604 | TORONTO BUTTONVILLE A | 3 | 7 | 20 | 0.7 | 17.3 | 0
1604 | TORONTO BUTTONVILLE A | 3 | 8 | 20 | 0.575 | 17.425 | 0
1605 | TORONTO BUTTONVILLE A | 3 | 7 | 21 | 0 | 18 | 0
1605 | TORONTO BUTTONVILLE A | 3 | 8 | 21 | -0.125 | 18.125 | 0
1606 | TORONTO BUTTONVILLE A | 3 | 7 | 22 | 0.4 | 17.6 | 0
1606 | TORONTO BUTTONVILLE A | 3 | 8 | 22 | -0.775 | 18.775 | 0
1607 | TORONTO BUTTONVILLE A | 3 | 7 | 23 | 0.2 | 17.8 | 0
1607 | TORONTO BUTTONVILLE A | 3 | 8 | 23 | -1.4 | 19.4 | 0
1608 | TORONTO BUTTONVILLE A | 3 | 7 | 24 | -0.2 | 18.2 | 0
1608 | TORONTO BUTTONVILLE A | 3 | 8 | 24 | -2.075 | 20.075 | 0
1609 | TORONTO BUTTONVILLE A | 3 | 8 | 1 | -0.2 | 18.2 | 0
1609 | TORONTO BUTTONVILLE A | 3 | 9 | 1 | -0.725 | 18.725 | 0
1610 | TORONTO BUTTONVILLE A | 3 | 8 | 2 | 0 | 18 | 0
1610 | TORONTO BUTTONVILLE A | 3 | 9 | 2 | -1.675 | 19.675 | 0
1611 | TORONTO BUTTONVILLE A | 3 | 8 | 3 | 0.2 | 17.8 | 0
1611 | TORONTO BUTTONVILLE A | 3 | 9 | 3 | -2.225 | 20.225 | 0
1612 | TORONTO BUTTONVILLE A | 3 | 8 | 4 | 0.3 | 17.7 | 0
1612 | TORONTO BUTTONVILLE A | 3 | 9 | 4 | -2.775 | 20.775 | 0
1613 | TORONTO BUTTONVILLE A | 3 | 8 | 5 | 0.6 | 17.4 | 0
1613 | TORONTO BUTTONVILLE A | 3 | 9 | 5 | -2.875 | 20.875 | 0
1614 | TORONTO BUTTONVILLE A | 3 | 8 | 6 | 0.3 | 17.7 | 0
1614 | TORONTO BUTTONVILLE A | 3 | 9 | 6 | -3.575 | 21.575 | 0
1615 | TORONTO BUTTONVILLE A | 3 | 8 | 7 | 0.3 | 17.7 | 0
1615 | TORONTO BUTTONVILLE A | 3 | 9 | 7 | -3.225 | 21.225 | 0
1616 | TORONTO BUTTONVILLE A | 3 | 8 | 8 | 0.1 | 17.9 | 0
1616 | TORONTO BUTTONVILLE A | 3 | 9 | 8 | -3.5 | 21.5 | 0
1617 | TORONTO BUTTONVILLE A | 3 | 8 | 9 | 1.8 | 16.2 | 0
1617 | TORONTO BUTTONVILLE A | 3 | 9 | 9 | -2.625 | 20.625 | 0
1618 | TORONTO BUTTONVILLE A | 3 | 8 | 10 | 3.7 | 14.3 | 0
1618 | TORONTO BUTTONVILLE A | 3 | 9 | 10 | -0.775 | 18.775 | 0
1619 | TORONTO BUTTONVILLE A | 3 | 8 | 11 | 5.8 | 12.2 | 0
1619 | TORONTO BUTTONVILLE A | 3 | 9 | 11 | 0.425 | 17.575 | 0
1620 | TORONTO BUTTONVILLE A | 3 | 8 | 12 | 7.8 | 10.2 | 0
1620 | TORONTO BUTTONVILLE A | 3 | 9 | 12 | 1.25 | 16.75 | 0
1621 | TORONTO BUTTONVILLE A | 3 | 8 | 13 | 10 | 8 | 0
1621 | TORONTO BUTTONVILLE A | 3 | 9 | 13 | 2.1 | 15.9 | 0
1622 | TORONTO BUTTONVILLE A | 3 | 8 | 14 | 10.8 | 7.2 | 0
1622 | TORONTO BUTTONVILLE A | 3 | 9 | 14 | 2.15 | 15.85 | 0
1623 | TORONTO BUTTONVILLE A | 3 | 8 | 15 | 11.7 | 6.3 | 0
1623 | TORONTO BUTTONVILLE A | 3 | 9 | 15 | 2.725 | 15.275 | 0
1624 | TORONTO BUTTONVILLE A | 3 | 8 | 16 | 11.2 | 6.8 | 0
1624 | TORONTO BUTTONVILLE A | 3 | 9 | 16 | 2.5 | 15.5 | 0
1625 | TORONTO BUTTONVILLE A | 3 | 8 | 17 | 11.2 | 6.8 | 0
1625 | TORONTO BUTTONVILLE A | 3 | 9 | 17 | 2.85 | 15.15 | 0
1626 | TORONTO BUTTONVILLE A | 3 | 8 | 18 | 11.1 | 6.9 | 0
1626 | TORONTO BUTTONVILLE A | 3 | 9 | 18 | 1.95 | 16.05 | 0
1627 | TORONTO BUTTONVILLE A | 3 | 8 | 19 | 10.6 | 7.4 | 0
1627 | TORONTO BUTTONVILLE A | 3 | 9 | 19 | 0.975 | 17.025 | 0
1628 | TORONTO BUTTONVILLE A | 3 | 8 | 20 | 9.7 | 8.3 | 0
1628 | TORONTO BUTTONVILLE A | 3 | 9 | 20 | 0.45 | 17.55 | 0
1629 | TORONTO BUTTONVILLE A | 3 | 8 | 21 | 9.6 | 8.4 | 0
1629 | TORONTO BUTTONVILLE A | 3 | 9 | 21 | -0.05 | 18.05 | 0
1630 | TORONTO BUTTONVILLE A | 3 | 8 | 22 | 9.2 | 8.8 | 0
1630 | TORONTO BUTTONVILLE A | 3 | 9 | 22 | -0.475 | 18.475 | 0
1631 | TORONTO BUTTONVILLE A | 3 | 8 | 23 | 9.8 | 8.2 | 0
1631 | TORONTO BUTTONVILLE A | 3 | 9 | 23 | -0.475 | 18.475 | 0
1632 | TORONTO BUTTONVILLE A | 3 | 8 | 24 | 9.2 | 8.8 | 0
1632 | TORONTO BUTTONVILLE A | 3 | 9 | 24 | -0.95 | 18.95 | 0
1633 | TORONTO BUTTONVILLE A | 3 | 9 | 1 | 9.9 | 8.1 | 0
1633 | TORONTO BUTTONVILLE A | 3 | 10 | 1 | -1.525 | 19.525 | 0
1634 | TORONTO BUTTONVILLE A | 3 | 9 | 2 | 10.1 | 7.9 | 0
1634 | TORONTO BUTTONVILLE A | 3 | 10 | 2 | -1.05 | 19.05 | 0
1635 | TORONTO BUTTONVILLE A | 3 | 9 | 3 | 9.9 | 8.1 | 0
1635 | TORONTO BUTTONVILLE A | 3 | 10 | 3 | -1.325 | 19.325 | 0
1636 | TORONTO BUTTONVILLE A | 3 | 9 | 4 | 9.5 | 8.5 | 0
1636 | TORONTO BUTTONVILLE A | 3 | 10 | 4 | -1.5 | 19.5 | 0
1637 | TORONTO BUTTONVILLE A | 3 | 9 | 5 | 8.8 | 9.2 | 0
1637 | TORONTO BUTTONVILLE A | 3 | 10 | 5 | -1.35 | 19.35 | 0
1638 | TORONTO BUTTONVILLE A | 3 | 9 | 6 | 8 | 10 | 0
1638 | TORONTO BUTTONVILLE A | 3 | 10 | 6 | -1.425 | 19.425 | 0
1639 | TORONTO BUTTONVILLE A | 3 | 9 | 7 | 8 | 10 | 0
1639 | TORONTO BUTTONVILLE A | 3 | 10 | 7 | -1.75 | 19.75 | 0
1640 | TORONTO BUTTONVILLE A | 3 | 9 | 8 | 7.9 | 10.1 | 0
1640 | TORONTO BUTTONVILLE A | 3 | 10 | 8 | -1.725 | 19.725 | 0
1641 | TORONTO BUTTONVILLE A | 3 | 9 | 9 | 9.3 | 8.7 | 0
1641 | TORONTO BUTTONVILLE A | 3 | 10 | 9 | -1.375 | 19.375 | 0
1642 | TORONTO BUTTONVILLE A | 3 | 9 | 10 | 10.7 | 7.3 | 0
1642 | TORONTO BUTTONVILLE A | 3 | 10 | 10 | -0.1 | 18.1 | 0
1643 | TORONTO BUTTONVILLE A | 3 | 9 | 11 | 12.4 | 5.6 | 0
1643 | TORONTO BUTTONVILLE A | 3 | 10 | 11 | 0.975 | 17.025 | 0
1644 | TORONTO BUTTONVILLE A | 3 | 9 | 12 | 14.4 | 3.6 | 0
1644 | TORONTO BUTTONVILLE A | 3 | 10 | 12 | 2.1 | 15.9 | 0
1645 | TORONTO BUTTONVILLE A | 3 | 9 | 13 | 15.4 | 2.6 | 0
1645 | TORONTO BUTTONVILLE A | 3 | 10 | 13 | 2.525 | 15.475 | 0
1646 | TORONTO BUTTONVILLE A | 3 | 9 | 14 | 15.9 | 2.1 | 0
1646 | TORONTO BUTTONVILLE A | 3 | 10 | 14 | 2.775 | 15.225 | 0
1647 | TORONTO BUTTONVILLE A | 3 | 9 | 15 | 17.1 | 0.9 | 0
1647 | TORONTO BUTTONVILLE A | 3 | 10 | 15 | 2.85 | 15.15 | 0
1648 | TORONTO BUTTONVILLE A | 3 | 9 | 16 | 16.1 | 1.9 | 0
1648 | TORONTO BUTTONVILLE A | 3 | 10 | 16 | 2.05 | 15.95 | 0
1649 | TORONTO BUTTONVILLE A | 3 | 9 | 17 | 15.6 | 2.4 | 0
1649 | TORONTO BUTTONVILLE A | 3 | 10 | 17 | 1.25 | 16.75 | 0
1650 | TORONTO BUTTONVILLE A | 3 | 9 | 18 | 14.7 | 3.3 | 0
1650 | TORONTO BUTTONVILLE A | 3 | 10 | 18 | 0.95 | 17.05 | 0
1651 | TORONTO BUTTONVILLE A | 3 | 9 | 19 | 14.2 | 3.8 | 0
1651 | TORONTO BUTTONVILLE A | 3 | 10 | 19 | 0.5 | 17.5 | 0
1652 | TORONTO BUTTONVILLE A | 3 | 9 | 20 | 13.6 | 4.4 | 0
1652 | TORONTO BUTTONVILLE A | 3 | 10 | 20 | 0.05 | 17.95 | 0
1653 | TORONTO BUTTONVILLE A | 3 | 9 | 21 | 13.2 | 4.8 | 0
1653 | TORONTO BUTTONVILLE A | 3 | 10 | 21 | -0.675 | 18.675 | 0
1654 | TORONTO BUTTONVILLE A | 3 | 9 | 22 | 13.1 | 4.9 | 0
1654 | TORONTO BUTTONVILLE A | 3 | 10 | 22 | -1.075 | 19.075 | 0
1655 | TORONTO BUTTONVILLE A | 3 | 9 | 23 | 12 | 6 | 0
1655 | TORONTO BUTTONVILLE A | 3 | 10 | 23 | -1.125 | 19.125 | 0
1656 | TORONTO BUTTONVILLE A | 3 | 9 | 24 | 11.8 | 6.2 | 0
1656 | TORONTO BUTTONVILLE A | 3 | 10 | 24 | -1.05 | 19.05 | 0
1657 | TORONTO BUTTONVILLE A | 3 | 10 | 1 | 11.1 | 6.9 | 0
1657 | TORONTO BUTTONVILLE A | 3 | 11 | 1 | 0.275 | 17.725 | 0
1658 | TORONTO BUTTONVILLE A | 3 | 10 | 2 | 10.8 | 7.2 | 0
1658 | TORONTO BUTTONVILLE A | 3 | 11 | 2 | -0.15 | 18.15 | 0
1659 | TORONTO BUTTONVILLE A | 3 | 10 | 3 | 10.5 | 7.5 | 0
1659 | TORONTO BUTTONVILLE A | 3 | 11 | 3 | 0.05 | 17.95 | 0
1660 | TORONTO BUTTONVILLE A | 3 | 10 | 4 | 10 | 8 | 0
1660 | TORONTO BUTTONVILLE A | 3 | 11 | 4 | -0.1 | 18.1 | 0
1661 | TORONTO BUTTONVILLE A | 3 | 10 | 5 | 9.7 | 8.3 | 0
1661 | TORONTO BUTTONVILLE A | 3 | 11 | 5 | -0.275 | 18.275 | 0
1662 | TORONTO BUTTONVILLE A | 3 | 10 | 6 | 9.3 | 8.7 | 0
1662 | TORONTO BUTTONVILLE A | 3 | 11 | 6 | -1.075 | 19.075 | 0
1663 | TORONTO BUTTONVILLE A | 3 | 10 | 7 | 8.8 | 9.2 | 0
1663 | TORONTO BUTTONVILLE A | 3 | 11 | 7 | -1.4 | 19.4 | 0
1664 | TORONTO BUTTONVILLE A | 3 | 10 | 8 | 8.9 | 9.1 | 0
1664 | TORONTO BUTTONVILLE A | 3 | 11 | 8 | -1.4 | 19.4 | 0
1665 | TORONTO BUTTONVILLE A | 3 | 10 | 9 | 9.2 | 8.8 | 0
1665 | TORONTO BUTTONVILLE A | 3 | 11 | 9 | -0.725 | 18.725 | 0
1666 | TORONTO BUTTONVILLE A | 3 | 10 | 10 | 9.7 | 8.3 | 0
1666 | TORONTO BUTTONVILLE A | 3 | 11 | 10 | 0.05 | 17.95 | 0
1667 | TORONTO BUTTONVILLE A | 3 | 10 | 11 | 10.3 | 7.7 | 0
1667 | TORONTO BUTTONVILLE A | 3 | 11 | 11 | 0.875 | 17.125 | 0
1668 | TORONTO BUTTONVILLE A | 3 | 10 | 12 | 10.5 | 7.5 | 0
1668 | TORONTO BUTTONVILLE A | 3 | 11 | 12 | 1.975 | 16.025 | 0
1669 | TORONTO BUTTONVILLE A | 3 | 10 | 13 | 7 | 11 | 0
1669 | TORONTO BUTTONVILLE A | 3 | 11 | 13 | 2.475 | 15.525 | 0
1670 | TORONTO BUTTONVILLE A | 3 | 10 | 14 | 3 | 15 | 0
1670 | TORONTO BUTTONVILLE A | 3 | 11 | 14 | 2.725 | 15.275 | 0
1671 | TORONTO BUTTONVILLE A | 3 | 10 | 15 | 1.7 | 16.3 | 0
1671 | TORONTO BUTTONVILLE A | 3 | 11 | 15 | 2.75 | 15.25 | 0
1672 | TORONTO BUTTONVILLE A | 3 | 10 | 16 | 1 | 17 | 0
1672 | TORONTO BUTTONVILLE A | 3 | 11 | 16 | 2.6 | 15.4 | 0
1673 | TORONTO BUTTONVILLE A | 3 | 10 | 17 | 0.9 | 17.1 | 0
1673 | TORONTO BUTTONVILLE A | 3 | 11 | 17 | 2.775 | 15.225 | 0
1674 | TORONTO BUTTONVILLE A | 3 | 10 | 18 | 1.2 | 16.8 | 0
1674 | TORONTO BUTTONVILLE A | 3 | 11 | 18 | 2.025 | 15.975 | 0
1675 | TORONTO BUTTONVILLE A | 3 | 10 | 19 | 0.3 | 17.7 | 0
1675 | TORONTO BUTTONVILLE A | 3 | 11 | 19 | 0.45 | 17.55 | 0
1676 | TORONTO BUTTONVILLE A | 3 | 10 | 20 | -0.1 | 18.1 | 0
1676 | TORONTO BUTTONVILLE A | 3 | 11 | 20 | -0.525 | 18.525 | 0
1677 | TORONTO BUTTONVILLE A | 3 | 10 | 21 | -0.3 | 18.3 | 0
1677 | TORONTO BUTTONVILLE A | 3 | 11 | 21 | -1.25 | 19.25 | 0
1678 | TORONTO BUTTONVILLE A | 3 | 10 | 22 | -0.2 | 18.2 | 0
1678 | TORONTO BUTTONVILLE A | 3 | 11 | 22 | -1.8 | 19.8 | 0
1679 | TORONTO BUTTONVILLE A | 3 | 10 | 23 | -0.3 | 18.3 | 0
1679 | TORONTO BUTTONVILLE A | 3 | 11 | 23 | -2.4 | 20.4 | 0
1680 | TORONTO BUTTONVILLE A | 3 | 10 | 24 | -0.8 | 18.8 | 0
1680 | TORONTO BUTTONVILLE A | 3 | 11 | 24 | -2.8 | 20.8 | 0
1681 | TORONTO BUTTONVILLE A | 3 | 11 | 1 | -1.1 | 19.1 | 0
1681 | TORONTO BUTTONVILLE A | 3 | 12 | 1 | -3.1 | 21.1 | 0
1682 | TORONTO BUTTONVILLE A | 3 | 11 | 2 | -1.6 | 19.6 | 0
1682 | TORONTO BUTTONVILLE A | 3 | 12 | 2 | -3.2 | 21.2 | 0
1683 | TORONTO BUTTONVILLE A | 3 | 11 | 3 | -2.4 | 20.4 | 0
1683 | TORONTO BUTTONVILLE A | 3 | 12 | 3 | -3.525 | 21.525 | 0
1684 | TORONTO BUTTONVILLE A | 3 | 11 | 4 | -2.4 | 20.4 | 0
1684 | TORONTO BUTTONVILLE A | 3 | 12 | 4 | -3.7 | 21.7 | 0
1685 | TORONTO BUTTONVILLE A | 3 | 11 | 5 | -3.6 | 21.6 | 0
1685 | TORONTO BUTTONVILLE A | 3 | 12 | 5 | -4.225 | 22.225 | 0
1686 | TORONTO BUTTONVILLE A | 3 | 11 | 6 | -3.9 | 21.9 | 0
1686 | TORONTO BUTTONVILLE A | 3 | 12 | 6 | -4.75 | 22.75 | 0
1687 | TORONTO BUTTONVILLE A | 3 | 11 | 7 | -3.4 | 21.4 | 0
1687 | TORONTO BUTTONVILLE A | 3 | 12 | 7 | -5.2 | 23.2 | 0
1688 | TORONTO BUTTONVILLE A | 3 | 11 | 8 | -3.1 | 21.1 | 0
1688 | TORONTO BUTTONVILLE A | 3 | 12 | 8 | -4.95 | 22.95 | 0
1689 | TORONTO BUTTONVILLE A | 3 | 11 | 9 | -2 | 20 | 0
1689 | TORONTO BUTTONVILLE A | 3 | 12 | 9 | -4.125 | 22.125 | 0
1690 | TORONTO BUTTONVILLE A | 3 | 11 | 10 | -0.3 | 18.3 | 0
1690 | TORONTO BUTTONVILLE A | 3 | 12 | 10 | -3.075 | 21.075 | 0
1691 | TORONTO BUTTONVILLE A | 3 | 11 | 11 | 0.7 | 17.3 | 0
1691 | TORONTO BUTTONVILLE A | 3 | 12 | 11 | -2.1 | 20.1 | 0
1692 | TORONTO BUTTONVILLE A | 3 | 11 | 12 | 1.5 | 16.5 | 0
1692 | TORONTO BUTTONVILLE A | 3 | 12 | 12 | -0.75 | 18.75 | 0
1693 | TORONTO BUTTONVILLE A | 3 | 11 | 13 | 1.7 | 16.3 | 0
1693 | TORONTO BUTTONVILLE A | 3 | 12 | 13 | 0.05 | 17.95 | 0
1694 | TORONTO BUTTONVILLE A | 3 | 11 | 14 | 2 | 16 | 0
1694 | TORONTO BUTTONVILLE A | 3 | 12 | 14 | 0.7 | 17.3 | 0
1695 | TORONTO BUTTONVILLE A | 3 | 11 | 15 | 2.8 | 15.2 | 0
1695 | TORONTO BUTTONVILLE A | 3 | 12 | 15 | 0.425 | 17.575 | 0
1696 | TORONTO BUTTONVILLE A | 3 | 11 | 16 | 1.6 | 16.4 | 0
1696 | TORONTO BUTTONVILLE A | 3 | 12 | 16 | -0.175 | 18.175 | 0
1697 | TORONTO BUTTONVILLE A | 3 | 11 | 17 | 1.1 | 16.9 | 0
1697 | TORONTO BUTTONVILLE A | 3 | 12 | 17 | -0.55 | 18.55 | 0
1698 | TORONTO BUTTONVILLE A | 3 | 11 | 18 | 0.6 | 17.4 | 0
1698 | TORONTO BUTTONVILLE A | 3 | 12 | 18 | -0.9 | 18.9 | 0
1699 | TORONTO BUTTONVILLE A | 3 | 11 | 19 | 0 | 18 | 0
1699 | TORONTO BUTTONVILLE A | 3 | 12 | 19 | -1.975 | 19.975 | 0
1700 | TORONTO BUTTONVILLE A | 3 | 11 | 20 | -0.2 | 18.2 | 0
1700 | TORONTO BUTTONVILLE A | 3 | 12 | 20 | -2.875 | 20.875 | 0
1701 | TORONTO BUTTONVILLE A | 3 | 11 | 21 | -0.3 | 18.3 | 0
1701 | TORONTO BUTTONVILLE A | 3 | 12 | 21 | -3.525 | 21.525 | 0
1702 | TORONTO BUTTONVILLE A | 3 | 11 | 22 | -0.4 | 18.4 | 0
1702 | TORONTO BUTTONVILLE A | 3 | 12 | 22 | -4.45 | 22.45 | 0
1703 | TORONTO BUTTONVILLE A | 3 | 11 | 23 | -0.5 | 18.5 | 0
1703 | TORONTO BUTTONVILLE A | 3 | 12 | 23 | -4.6 | 22.6 | 0
1704 | TORONTO BUTTONVILLE A | 3 | 11 | 24 | -0.5 | 18.5 | 0
1704 | TORONTO BUTTONVILLE A | 3 | 12 | 24 | -5 | 23 | 0
1705 | TORONTO BUTTONVILLE A | 3 | 12 | 1 | -0.5 | 18.5 | 0
1705 | TORONTO BUTTONVILLE A | 3 | 13 | 1 | -5.45 | 23.45 | 0
1706 | TORONTO BUTTONVILLE A | 3 | 12 | 2 | -0.3 | 18.3 | 0
1706 | TORONTO BUTTONVILLE A | 3 | 13 | 2 | -5.525 | 23.525 | 0
1707 | TORONTO BUTTONVILLE A | 3 | 12 | 3 | -0.4 | 18.4 | 0
1707 | TORONTO BUTTONVILLE A | 3 | 13 | 3 | -5.65 | 23.65 | 0
1708 | TORONTO BUTTONVILLE A | 3 | 12 | 4 | -0.8 | 18.8 | 0
1708 | TORONTO BUTTONVILLE A | 3 | 13 | 4 | -5.825 | 23.825 | 0
1709 | TORONTO BUTTONVILLE A | 3 | 12 | 5 | -0.8 | 18.8 | 0
1709 | TORONTO BUTTONVILLE A | 3 | 13 | 5 | -5.95 | 23.95 | 0
1710 | TORONTO BUTTONVILLE A | 3 | 12 | 6 | -0.9 | 18.9 | 0
1710 | TORONTO BUTTONVILLE A | 3 | 13 | 6 | -6.025 | 24.025 | 0
1711 | TORONTO BUTTONVILLE A | 3 | 12 | 7 | -1.2 | 19.2 | 0
1711 | TORONTO BUTTONVILLE A | 3 | 13 | 7 | -5.85 | 23.85 | 0
1712 | TORONTO BUTTONVILLE A | 3 | 12 | 8 | -1.4 | 19.4 | 0
1712 | TORONTO BUTTONVILLE A | 3 | 13 | 8 | -5.65 | 23.65 | 0
1713 | TORONTO BUTTONVILLE A | 3 | 12 | 9 | -0.5 | 18.5 | 0
1713 | TORONTO BUTTONVILLE A | 3 | 13 | 9 | -5.1 | 23.1 | 0
1714 | TORONTO BUTTONVILLE A | 3 | 12 | 10 | 0.8 | 17.2 | 0
1714 | TORONTO BUTTONVILLE A | 3 | 13 | 10 | -4.175 | 22.175 | 0
1715 | TORONTO BUTTONVILLE A | 3 | 12 | 11 | 2.1 | 15.9 | 0
1715 | TORONTO BUTTONVILLE A | 3 | 13 | 11 | -3 | 21 | 0
1716 | TORONTO BUTTONVILLE A | 3 | 12 | 12 | 3 | 15 | 0
1716 | TORONTO BUTTONVILLE A | 3 | 13 | 12 | -2.225 | 20.225 | 0
1717 | TORONTO BUTTONVILLE A | 3 | 12 | 13 | 4 | 14 | 0
1717 | TORONTO BUTTONVILLE A | 3 | 13 | 13 | -1.475 | 19.475 | 0
1718 | TORONTO BUTTONVILLE A | 3 | 12 | 14 | 3.5 | 14.5 | 0
1718 | TORONTO BUTTONVILLE A | 3 | 13 | 14 | -0.825 | 18.825 | 0
1719 | TORONTO BUTTONVILLE A | 3 | 12 | 15 | 4 | 14 | 0
1719 | TORONTO BUTTONVILLE A | 3 | 13 | 15 | -0.525 | 18.525 | 0
1720 | TORONTO BUTTONVILLE A | 3 | 12 | 16 | 3.8 | 14.2 | 0
1720 | TORONTO BUTTONVILLE A | 3 | 13 | 16 | -0.35 | 18.35 | 0
1721 | TORONTO BUTTONVILLE A | 3 | 12 | 17 | 3.7 | 14.3 | 0
1721 | TORONTO BUTTONVILLE A | 3 | 13 | 17 | -0.45 | 18.45 | 0
1722 | TORONTO BUTTONVILLE A | 3 | 12 | 18 | 3.5 | 14.5 | 0
1722 | TORONTO BUTTONVILLE A | 3 | 13 | 18 | -0.85 | 18.85 | 0
1723 | TORONTO BUTTONVILLE A | 3 | 12 | 19 | 3.8 | 14.2 | 0
1723 | TORONTO BUTTONVILLE A | 3 | 13 | 19 | -1.15 | 19.15 | 0
1724 | TORONTO BUTTONVILLE A | 3 | 12 | 20 | 3.7 | 14.3 | 0
1724 | TORONTO BUTTONVILLE A | 3 | 13 | 20 | -1.375 | 19.375 | 0
1725 | TORONTO BUTTONVILLE A | 3 | 12 | 21 | 4 | 14 | 0
1725 | TORONTO BUTTONVILLE A | 3 | 13 | 21 | -1.45 | 19.45 | 0
1726 | TORONTO BUTTONVILLE A | 3 | 12 | 22 | 5.2 | 12.8 | 0
1726 | TORONTO BUTTONVILLE A | 3 | 13 | 22 | -1.625 | 19.625 | 0
1727 | TORONTO BUTTONVILLE A | 3 | 12 | 23 | 6 | 12 | 0
1727 | TORONTO BUTTONVILLE A | 3 | 13 | 23 | -1.7 | 19.7 | 0
1728 | TORONTO BUTTONVILLE A | 3 | 12 | 24 | 5.6 | 12.4 | 0
1728 | TORONTO BUTTONVILLE A | 3 | 13 | 24 | -2 | 20 | 0
1729 | TORONTO BUTTONVILLE A | 3 | 13 | 1 | 5.2 | 12.8 | 0
1729 | TORONTO BUTTONVILLE A | 3 | 14 | 1 | -2.05 | 20.05 | 0
1730 | TORONTO BUTTONVILLE A | 3 | 13 | 2 | 5 | 13 | 0
1730 | TORONTO BUTTONVILLE A | 3 | 14 | 2 | -2.175 | 20.175 | 0
1731 | TORONTO BUTTONVILLE A | 3 | 13 | 3 | 5.6 | 12.4 | 0
1731 | TORONTO BUTTONVILLE A | 3 | 14 | 3 | -2 | 20 | 0
1732 | TORONTO BUTTONVILLE A | 3 | 13 | 4 | 6.2 | 11.8 | 0
1732 | TORONTO BUTTONVILLE A | 3 | 14 | 4 | -2.375 | 20.375 | 0
1733 | TORONTO BUTTONVILLE A | 3 | 13 | 5 | 6.7 | 11.3 | 0
1733 | TORONTO BUTTONVILLE A | 3 | 14 | 5 | -2.775 | 20.775 | 0
1734 | TORONTO BUTTONVILLE A | 3 | 13 | 6 | 7.6 | 10.4 | 0
1734 | TORONTO BUTTONVILLE A | 3 | 14 | 6 | -3.225 | 21.225 | 0
1735 | TORONTO BUTTONVILLE A | 3 | 13 | 7 | 7 | 11 | 0
1735 | TORONTO BUTTONVILLE A | 3 | 14 | 7 | -3.15 | 21.15 | 0
1736 | TORONTO BUTTONVILLE A | 3 | 13 | 8 | 6.4 | 11.6 | 0
1736 | TORONTO BUTTONVILLE A | 3 | 14 | 8 | -2.95 | 20.95 | 0
1737 | TORONTO BUTTONVILLE A | 3 | 13 | 9 | 4.5 | 13.5 | 0
1737 | TORONTO BUTTONVILLE A | 3 | 14 | 9 | -2.95 | 20.95 | 0
1738 | TORONTO BUTTONVILLE A | 3 | 13 | 10 | 5.2 | 12.8 | 0
1738 | TORONTO BUTTONVILLE A | 3 | 14 | 10 | -2.125 | 20.125 | 0
1739 | TORONTO BUTTONVILLE A | 3 | 13 | 11 | 5.7 | 12.3 | 0
1739 | TORONTO BUTTONVILLE A | 3 | 14 | 11 | -1.725 | 19.725 | 0
1740 | TORONTO BUTTONVILLE A | 3 | 13 | 12 | 5.3 | 12.7 | 0
1740 | TORONTO BUTTONVILLE A | 3 | 14 | 12 | -1.375 | 19.375 | 0
1741 | TORONTO BUTTONVILLE A | 3 | 13 | 13 | 4.3 | 13.7 | 0
1741 | TORONTO BUTTONVILLE A | 3 | 14 | 13 | -1.425 | 19.425 | 0
1742 | TORONTO BUTTONVILLE A | 3 | 13 | 14 | 4.3 | 13.7 | 0
1742 | TORONTO BUTTONVILLE A | 3 | 14 | 14 | -1.375 | 19.375 | 0
1743 | TORONTO BUTTONVILLE A | 3 | 13 | 15 | 4.1 | 13.9 | 0
1743 | TORONTO BUTTONVILLE A | 3 | 14 | 15 | -1.175 | 19.175 | 0
1744 | TORONTO BUTTONVILLE A | 3 | 13 | 16 | 4.3 | 13.7 | 0
1744 | TORONTO BUTTONVILLE A | 3 | 14 | 16 | -1.175 | 19.175 | 0
1745 | TORONTO BUTTONVILLE A | 3 | 13 | 17 | 4.7 | 13.3 | 0
1745 | TORONTO BUTTONVILLE A | 3 | 14 | 17 | -1.45 | 19.45 | 0
1746 | TORONTO BUTTONVILLE A | 3 | 13 | 18 | 4 | 14 | 0
1746 | TORONTO BUTTONVILLE A | 3 | 14 | 18 | -1.275 | 19.275 | 0
1747 | TORONTO BUTTONVILLE A | 3 | 13 | 19 | 3.7 | 14.3 | 0
1747 | TORONTO BUTTONVILLE A | 3 | 14 | 19 | -1.8 | 19.8 | 0
1748 | TORONTO BUTTONVILLE A | 3 | 13 | 20 | 3.1 | 14.9 | 0
1748 | TORONTO BUTTONVILLE A | 3 | 14 | 20 | -2.4 | 20.4 | 0
1749 | TORONTO BUTTONVILLE A | 3 | 13 | 21 | 3.3 | 14.7 | 0
1749 | TORONTO BUTTONVILLE A | 3 | 14 | 21 | -2.225 | 20.225 | 0
1750 | TORONTO BUTTONVILLE A | 3 | 13 | 22 | 3.3 | 14.7 | 0
1750 | TORONTO BUTTONVILLE A | 3 | 14 | 22 | -2.425 | 20.425 | 0
1751 | TORONTO BUTTONVILLE A | 3 | 13 | 23 | 2.7 | 15.3 | 0
1751 | TORONTO BUTTONVILLE A | 3 | 14 | 23 | -2.4 | 20.4 | 0
1752 | TORONTO BUTTONVILLE A | 3 | 13 | 24 | 2.1 | 15.9 | 0
1752 | TORONTO BUTTONVILLE A | 3 | 14 | 24 | -2.225 | 20.225 | 0
1753 | TORONTO BUTTONVILLE A | 3 | 14 | 1 | 1.8 | 16.2 | 0
1753 | TORONTO BUTTONVILLE A | 3 | 15 | 1 | -3.05 | 21.05 | 0
1754 | TORONTO BUTTONVILLE A | 3 | 14 | 2 | 1.7 | 16.3 | 0
1754 | TORONTO BUTTONVILLE A | 3 | 15 | 2 | -3.625 | 21.625 | 0
1755 | TORONTO BUTTONVILLE A | 3 | 14 | 3 | 1.7 | 16.3 | 0
1755 | TORONTO BUTTONVILLE A | 3 | 15 | 3 | -3.925 | 21.925 | 0
1756 | TORONTO BUTTONVILLE A | 3 | 14 | 4 | 0.8 | 17.2 | 0
1756 | TORONTO BUTTONVILLE A | 3 | 15 | 4 | -3.85 | 21.85 | 0
1757 | TORONTO BUTTONVILLE A | 3 | 14 | 5 | 0.2 | 17.8 | 0
1757 | TORONTO BUTTONVILLE A | 3 | 15 | 5 | -4.025 | 22.025 | 0
1758 | TORONTO BUTTONVILLE A | 3 | 14 | 6 | 0.4 | 17.6 | 0
1758 | TORONTO BUTTONVILLE A | 3 | 15 | 6 | -4.35 | 22.35 | 0
1759 | TORONTO BUTTONVILLE A | 3 | 14 | 7 | 0.3 | 17.7 | 0
1759 | TORONTO BUTTONVILLE A | 3 | 15 | 7 | -4.575 | 22.575 | 0
1760 | TORONTO BUTTONVILLE A | 3 | 14 | 8 | 0.2 | 17.8 | 0
1760 | TORONTO BUTTONVILLE A | 3 | 15 | 8 | -4.825 | 22.825 | 0
1761 | TORONTO BUTTONVILLE A | 3 | 14 | 9 | 0.4 | 17.6 | 0
1761 | TORONTO BUTTONVILLE A | 3 | 15 | 9 | -3.675 | 21.675 | 0
1762 | TORONTO BUTTONVILLE A | 3 | 14 | 10 | 0.6 | 17.4 | 0
1762 | TORONTO BUTTONVILLE A | 3 | 15 | 10 | -2.65 | 20.65 | 0
1763 | TORONTO BUTTONVILLE A | 3 | 14 | 11 | 0.7 | 17.3 | 0
1763 | TORONTO BUTTONVILLE A | 3 | 15 | 11 | -1.8 | 19.8 | 0
1764 | TORONTO BUTTONVILLE A | 3 | 14 | 12 | 1.3 | 16.7 | 0
1764 | TORONTO BUTTONVILLE A | 3 | 15 | 12 | -0.95 | 18.95 | 0
1765 | TORONTO BUTTONVILLE A | 3 | 14 | 13 | 1.5 | 16.5 | 0
1765 | TORONTO BUTTONVILLE A | 3 | 15 | 13 | -0.25 | 18.25 | 0
1766 | TORONTO BUTTONVILLE A | 3 | 14 | 14 | 1.6 | 16.4 | 0
1766 | TORONTO BUTTONVILLE A | 3 | 15 | 14 | 0.125 | 17.875 | 0
1767 | TORONTO BUTTONVILLE A | 3 | 14 | 15 | 1.9 | 16.1 | 0
1767 | TORONTO BUTTONVILLE A | 3 | 15 | 15 | 0.425 | 17.575 | 0
1768 | TORONTO BUTTONVILLE A | 3 | 14 | 16 | 2.5 | 15.5 | 0
1768 | TORONTO BUTTONVILLE A | 3 | 15 | 16 | 0.525 | 17.475 | 0
1769 | TORONTO BUTTONVILLE A | 3 | 14 | 17 | 2.1 | 15.9 | 0
1769 | TORONTO BUTTONVILLE A | 3 | 15 | 17 | 0.45 | 17.55 | 0
1770 | TORONTO BUTTONVILLE A | 3 | 14 | 18 | 1.4 | 16.6 | 0
1770 | TORONTO BUTTONVILLE A | 3 | 15 | 18 | -0.3 | 18.3 | 0
1771 | TORONTO BUTTONVILLE A | 3 | 14 | 19 | 0.4 | 17.6 | 0
1771 | TORONTO BUTTONVILLE A | 3 | 15 | 19 | -1.125 | 19.125 | 0
1772 | TORONTO BUTTONVILLE A | 3 | 14 | 20 | 0 | 18 | 0
1772 | TORONTO BUTTONVILLE A | 3 | 15 | 20 | -1.675 | 19.675 | 0
1773 | TORONTO BUTTONVILLE A | 3 | 14 | 21 | -0.5 | 18.5 | 0
1773 | TORONTO BUTTONVILLE A | 3 | 15 | 21 | -2 | 20 | 0
1774 | TORONTO BUTTONVILLE A | 3 | 14 | 22 | -0.6 | 18.6 | 0
1774 | TORONTO BUTTONVILLE A | 3 | 15 | 22 | -2.275 | 20.275 | 0
1775 | TORONTO BUTTONVILLE A | 3 | 14 | 23 | -0.7 | 18.7 | 0
1775 | TORONTO BUTTONVILLE A | 3 | 15 | 23 | -2.375 | 20.375 | 0
1776 | TORONTO BUTTONVILLE A | 3 | 14 | 24 | -0.9 | 18.9 | 0
1776 | TORONTO BUTTONVILLE A | 3 | 15 | 24 | -2.625 | 20.625 | 0
1777 | TORONTO BUTTONVILLE A | 3 | 15 | 1 | -1.4 | 19.4 | 0
1777 | TORONTO BUTTONVILLE A | 3 | 16 | 1 | -2.9 | 20.9 | 0
1778 | TORONTO BUTTONVILLE A | 3 | 15 | 2 | -1.4 | 19.4 | 0
1778 | TORONTO BUTTONVILLE A | 3 | 16 | 2 | -3.125 | 21.125 | 0
1779 | TORONTO BUTTONVILLE A | 3 | 15 | 3 | -1.4 | 19.4 | 0
1779 | TORONTO BUTTONVILLE A | 3 | 16 | 3 | -3.525 | 21.525 | 0
1780 | TORONTO BUTTONVILLE A | 3 | 15 | 4 | -1.5 | 19.5 | 0
1780 | TORONTO BUTTONVILLE A | 3 | 16 | 4 | -4.025 | 22.025 | 0
1781 | TORONTO BUTTONVILLE A | 3 | 15 | 5 | -2.5 | 20.5 | 0
1781 | TORONTO BUTTONVILLE A | 3 | 16 | 5 | -4.025 | 22.025 | 0
1782 | TORONTO BUTTONVILLE A | 3 | 15 | 6 | -3 | 21 | 0
1782 | TORONTO BUTTONVILLE A | 3 | 16 | 6 | -4.4 | 22.4 | 0
1783 | TORONTO BUTTONVILLE A | 3 | 15 | 7 | -4 | 22 | 0
1783 | TORONTO BUTTONVILLE A | 3 | 16 | 7 | -4.675 | 22.675 | 0
1784 | TORONTO BUTTONVILLE A | 3 | 15 | 8 | -4.3 | 22.3 | 0
1784 | TORONTO BUTTONVILLE A | 3 | 16 | 8 | -4.625 | 22.625 | 0
1785 | TORONTO BUTTONVILLE A | 3 | 15 | 9 | -3.5 | 21.5 | 0
1785 | TORONTO BUTTONVILLE A | 3 | 16 | 9 | -4.2 | 22.2 | 0
1786 | TORONTO BUTTONVILLE A | 3 | 15 | 10 | -2.5 | 20.5 | 0
1786 | TORONTO BUTTONVILLE A | 3 | 16 | 10 | -3.6 | 21.6 | 0
1787 | TORONTO BUTTONVILLE A | 3 | 15 | 11 | -1.3 | 19.3 | 0
1787 | TORONTO BUTTONVILLE A | 3 | 16 | 11 | -2.625 | 20.625 | 0
1788 | TORONTO BUTTONVILLE A | 3 | 15 | 12 | -0.4 | 18.4 | 0
1788 | TORONTO BUTTONVILLE A | 3 | 16 | 12 | -1.85 | 19.85 | 0
1789 | TORONTO BUTTONVILLE A | 3 | 15 | 13 | 0.6 | 17.4 | 0
1789 | TORONTO BUTTONVILLE A | 3 | 16 | 13 | -1.35 | 19.35 | 0
1790 | TORONTO BUTTONVILLE A | 3 | 15 | 14 | 1.9 | 16.1 | 0
1790 | TORONTO BUTTONVILLE A | 3 | 16 | 14 | -1.225 | 19.225 | 0
1791 | TORONTO BUTTONVILLE A | 3 | 15 | 15 | 2 | 16 | 0
1791 | TORONTO BUTTONVILLE A | 3 | 16 | 15 | -0.3 | 18.3 | 0
1792 | TORONTO BUTTONVILLE A | 3 | 15 | 16 | 2.8 | 15.2 | 0
1792 | TORONTO BUTTONVILLE A | 3 | 16 | 16 | 0.075 | 17.925 | 0
1793 | TORONTO BUTTONVILLE A | 3 | 15 | 17 | 2.2 | 15.8 | 0
1793 | TORONTO BUTTONVILLE A | 3 | 16 | 17 | 0.1 | 17.9 | 0
1794 | TORONTO BUTTONVILLE A | 3 | 15 | 18 | 1.7 | 16.3 | 0
1794 | TORONTO BUTTONVILLE A | 3 | 16 | 18 | -0.175 | 18.175 | 0
1795 | TORONTO BUTTONVILLE A | 3 | 15 | 19 | 0.6 | 17.4 | 0
1795 | TORONTO BUTTONVILLE A | 3 | 16 | 19 | -0.8 | 18.8 | 0
1796 | TORONTO BUTTONVILLE A | 3 | 15 | 20 | -0.8 | 18.8 | 0
1796 | TORONTO BUTTONVILLE A | 3 | 16 | 20 | -1.3 | 19.3 | 0
1797 | TORONTO BUTTONVILLE A | 3 | 15 | 21 | -1 | 19 | 0
1797 | TORONTO BUTTONVILLE A | 3 | 16 | 21 | -1.775 | 19.775 | 0
1798 | TORONTO BUTTONVILLE A | 3 | 15 | 22 | -1.8 | 19.8 | 0
1798 | TORONTO BUTTONVILLE A | 3 | 16 | 22 | -2.1 | 20.1 | 0
1799 | TORONTO BUTTONVILLE A | 3 | 15 | 23 | -2.9 | 20.9 | 0
1799 | TORONTO BUTTONVILLE A | 3 | 16 | 23 | -2.425 | 20.425 | 0
1800 | TORONTO BUTTONVILLE A | 3 | 15 | 24 | -3.5 | 21.5 | 0
1800 | TORONTO BUTTONVILLE A | 3 | 16 | 24 | -2.725 | 20.725 | 0
1801 | TORONTO BUTTONVILLE A | 3 | 16 | 1 | -4.2 | 22.2 | 0
1801 | TORONTO BUTTONVILLE A | 3 | 17 | 1 | -3.125 | 21.125 | 0
1802 | TORONTO BUTTONVILLE A | 3 | 16 | 2 | -4.4 | 22.4 | 0
1802 | TORONTO BUTTONVILLE A | 3 | 17 | 2 | -3.2 | 21.2 | 0
1803 | TORONTO BUTTONVILLE A | 3 | 16 | 3 | -4.8 | 22.8 | 0
1803 | TORONTO BUTTONVILLE A | 3 | 17 | 3 | -3.45 | 21.45 | 0
1804 | TORONTO BUTTONVILLE A | 3 | 16 | 4 | -5.1 | 23.1 | 0
1804 | TORONTO BUTTONVILLE A | 3 | 17 | 4 | -3.55 | 21.55 | 0
1805 | TORONTO BUTTONVILLE A | 3 | 16 | 5 | -5.3 | 23.3 | 0
1805 | TORONTO BUTTONVILLE A | 3 | 17 | 5 | -3.7 | 21.7 | 0
1806 | TORONTO BUTTONVILLE A | 3 | 16 | 6 | -5.1 | 23.1 | 0
1806 | TORONTO BUTTONVILLE A | 3 | 17 | 6 | -4.025 | 22.025 | 0
1807 | TORONTO BUTTONVILLE A | 3 | 16 | 7 | -5.1 | 23.1 | 0
1807 | TORONTO BUTTONVILLE A | 3 | 17 | 7 | -3.625 | 21.625 | 0
1808 | TORONTO BUTTONVILLE A | 3 | 16 | 8 | -4.5 | 22.5 | 0
1808 | TORONTO BUTTONVILLE A | 3 | 17 | 8 | -3.25 | 21.25 | 0
1809 | TORONTO BUTTONVILLE A | 3 | 16 | 9 | -1.4 | 19.4 | 0
1809 | TORONTO BUTTONVILLE A | 3 | 17 | 9 | -1.725 | 19.725 | 0
1810 | TORONTO BUTTONVILLE A | 3 | 16 | 10 | -1 | 19 | 0
1810 | TORONTO BUTTONVILLE A | 3 | 17 | 10 | -0.25 | 18.25 | 0
1811 | TORONTO BUTTONVILLE A | 3 | 16 | 11 | -0.2 | 18.2 | 0
1811 | TORONTO BUTTONVILLE A | 3 | 17 | 11 | 0.875 | 17.125 | 0
1812 | TORONTO BUTTONVILLE A | 3 | 16 | 12 | 0.3 | 17.7 | 0
1812 | TORONTO BUTTONVILLE A | 3 | 17 | 12 | 2.55 | 15.45 | 0
1813 | TORONTO BUTTONVILLE A | 3 | 16 | 13 | 1.4 | 16.6 | 0
1813 | TORONTO BUTTONVILLE A | 3 | 17 | 13 | 3.575 | 14.425 | 0
1814 | TORONTO BUTTONVILLE A | 3 | 16 | 14 | 1.3 | 16.7 | 0
1814 | TORONTO BUTTONVILLE A | 3 | 17 | 14 | 4.125 | 13.875 | 0
1815 | TORONTO BUTTONVILLE A | 3 | 16 | 15 | 1.9 | 16.1 | 0
1815 | TORONTO BUTTONVILLE A | 3 | 17 | 15 | 4.25 | 13.75 | 0
1816 | TORONTO BUTTONVILLE A | 3 | 16 | 16 | 2.2 | 15.8 | 0
1816 | TORONTO BUTTONVILLE A | 3 | 17 | 16 | 4.475 | 13.525 | 0
1817 | TORONTO BUTTONVILLE A | 3 | 16 | 17 | 2.2 | 15.8 | 0
1817 | TORONTO BUTTONVILLE A | 3 | 17 | 17 | 3.8 | 14.2 | 0
1818 | TORONTO BUTTONVILLE A | 3 | 16 | 18 | 1.5 | 16.5 | 0
1818 | TORONTO BUTTONVILLE A | 3 | 17 | 18 | 3.25 | 14.75 | 0
1819 | TORONTO BUTTONVILLE A | 3 | 16 | 19 | 1.2 | 16.8 | 0
1819 | TORONTO BUTTONVILLE A | 3 | 17 | 19 | 2.25 | 15.75 | 0
1820 | TORONTO BUTTONVILLE A | 3 | 16 | 20 | 0.9 | 17.1 | 0
1820 | TORONTO BUTTONVILLE A | 3 | 17 | 20 | 1.425 | 16.575 | 0
1821 | TORONTO BUTTONVILLE A | 3 | 16 | 21 | 1.1 | 16.9 | 0
1821 | TORONTO BUTTONVILLE A | 3 | 17 | 21 | 0.4 | 17.6 | 0
1822 | TORONTO BUTTONVILLE A | 3 | 16 | 22 | 1.1 | 16.9 | 0
1822 | TORONTO BUTTONVILLE A | 3 | 17 | 22 | -0.1 | 18.1 | 0
1823 | TORONTO BUTTONVILLE A | 3 | 16 | 23 | 0.1 | 17.9 | 0
1823 | TORONTO BUTTONVILLE A | 3 | 17 | 23 | -0.775 | 18.775 | 0
1824 | TORONTO BUTTONVILLE A | 3 | 16 | 24 | 0.3 | 17.7 | 0
1824 | TORONTO BUTTONVILLE A | 3 | 17 | 24 | -0.825 | 18.825 | 0
1825 | TORONTO BUTTONVILLE A | 3 | 17 | 1 | 0.4 | 17.6 | 0
1825 | TORONTO BUTTONVILLE A | 3 | 18 | 1 | -1.35 | 19.35 | 0
1826 | TORONTO BUTTONVILLE A | 3 | 17 | 2 | 1.1 | 16.9 | 0
1826 | TORONTO BUTTONVILLE A | 3 | 18 | 2 | -1.65 | 19.65 | 0
1827 | TORONTO BUTTONVILLE A | 3 | 17 | 3 | 1.3 | 16.7 | 0
1827 | TORONTO BUTTONVILLE A | 3 | 18 | 3 | -2.025 | 20.025 | 0
1828 | TORONTO BUTTONVILLE A | 3 | 17 | 4 | 1.6 | 16.4 | 0
1828 | TORONTO BUTTONVILLE A | 3 | 18 | 4 | -2 | 20 | 0
1829 | TORONTO BUTTONVILLE A | 3 | 17 | 5 | 1.9 | 16.1 | 0
1829 | TORONTO BUTTONVILLE A | 3 | 18 | 5 | -2.15 | 20.15 | 0
1830 | TORONTO BUTTONVILLE A | 3 | 17 | 6 | 2.3 | 15.7 | 0
1830 | TORONTO BUTTONVILLE A | 3 | 18 | 6 | -2.125 | 20.125 | 0
1831 | TORONTO BUTTONVILLE A | 3 | 17 | 7 | 2.7 | 15.3 | 0
1831 | TORONTO BUTTONVILLE A | 3 | 18 | 7 | -2.175 | 20.175 | 0
1832 | TORONTO BUTTONVILLE A | 3 | 17 | 8 | 2.9 | 15.1 | 0
1832 | TORONTO BUTTONVILLE A | 3 | 18 | 8 | -1.9 | 19.9 | 0
1833 | TORONTO BUTTONVILLE A | 3 | 17 | 9 | 3.3 | 14.7 | 0
1833 | TORONTO BUTTONVILLE A | 3 | 18 | 9 | -0.475 | 18.475 | 0
1834 | TORONTO BUTTONVILLE A | 3 | 17 | 10 | 3.8 | 14.2 | 0
1834 | TORONTO BUTTONVILLE A | 3 | 18 | 10 | 0.425 | 17.575 | 0
1835 | TORONTO BUTTONVILLE A | 3 | 17 | 11 | 4.1 | 13.9 | 0
1835 | TORONTO BUTTONVILLE A | 3 | 18 | 11 | 1.3 | 16.7 | 0
1836 | TORONTO BUTTONVILLE A | 3 | 17 | 12 | 4.7 | 13.3 | 0
1836 | TORONTO BUTTONVILLE A | 3 | 18 | 12 | 1.875 | 16.125 | 0
1837 | TORONTO BUTTONVILLE A | 3 | 17 | 13 | 5.4 | 12.6 | 0
1837 | TORONTO BUTTONVILLE A | 3 | 18 | 13 | 2.55 | 15.45 | 0
1838 | TORONTO BUTTONVILLE A | 3 | 17 | 14 | 6.2 | 11.8 | 0
1838 | TORONTO BUTTONVILLE A | 3 | 18 | 14 | 3.35 | 14.65 | 0
1839 | TORONTO BUTTONVILLE A | 3 | 17 | 15 | 6.5 | 11.5 | 0
1839 | TORONTO BUTTONVILLE A | 3 | 18 | 15 | 3.25 | 14.75 | 0
1840 | TORONTO BUTTONVILLE A | 3 | 17 | 16 | 6.4 | 11.6 | 0
1840 | TORONTO BUTTONVILLE A | 3 | 18 | 16 | 2.9 | 15.1 | 0
1841 | TORONTO BUTTONVILLE A | 3 | 17 | 17 | 6.5 | 11.5 | 0
1841 | TORONTO BUTTONVILLE A | 3 | 18 | 17 | 2.975 | 15.025 | 0
1842 | TORONTO BUTTONVILLE A | 3 | 17 | 18 | 5.9 | 12.1 | 0
1842 | TORONTO BUTTONVILLE A | 3 | 18 | 18 | 2.575 | 15.425 | 0
1843 | TORONTO BUTTONVILLE A | 3 | 17 | 19 | 4.9 | 13.1 | 0
1843 | TORONTO BUTTONVILLE A | 3 | 18 | 19 | 1.825 | 16.175 | 0
1844 | TORONTO BUTTONVILLE A | 3 | 17 | 20 | 3.6 | 14.4 | 0
1844 | TORONTO BUTTONVILLE A | 3 | 18 | 20 | 1.05 | 16.95 | 0
1845 | TORONTO BUTTONVILLE A | 3 | 17 | 21 | 2.7 | 15.3 | 0
1845 | TORONTO BUTTONVILLE A | 3 | 18 | 21 | 0.45 | 17.55 | 0
1846 | TORONTO BUTTONVILLE A | 3 | 17 | 22 | 1.8 | 16.2 | 0
1846 | TORONTO BUTTONVILLE A | 3 | 18 | 22 | -0.275 | 18.275 | 0
1847 | TORONTO BUTTONVILLE A | 3 | 17 | 23 | 0 | 18 | 0
1847 | TORONTO BUTTONVILLE A | 3 | 18 | 23 | -0.775 | 18.775 | 0
1848 | TORONTO BUTTONVILLE A | 3 | 17 | 24 | -0.1 | 18.1 | 0
1848 | TORONTO BUTTONVILLE A | 3 | 18 | 24 | -1.125 | 19.125 | 0
1849 | TORONTO BUTTONVILLE A | 3 | 18 | 1 | -0.5 | 18.5 | 0
1849 | TORONTO BUTTONVILLE A | 3 | 19 | 1 | -1.325 | 19.325 | 0
1850 | TORONTO BUTTONVILLE A | 3 | 18 | 2 | -1.5 | 19.5 | 0
1850 | TORONTO BUTTONVILLE A | 3 | 19 | 2 | -1.7 | 19.7 | 0
1851 | TORONTO BUTTONVILLE A | 3 | 18 | 3 | -1.9 | 19.9 | 0
1851 | TORONTO BUTTONVILLE A | 3 | 19 | 3 | -2.375 | 20.375 | 0
1852 | TORONTO BUTTONVILLE A | 3 | 18 | 4 | -2.1 | 20.1 | 0
1852 | TORONTO BUTTONVILLE A | 3 | 19 | 4 | -3.275 | 21.275 | 0
1853 | TORONTO BUTTONVILLE A | 3 | 18 | 5 | -3 | 21 | 0
1853 | TORONTO BUTTONVILLE A | 3 | 19 | 5 | -3.925 | 21.925 | 0
1854 | TORONTO BUTTONVILLE A | 3 | 18 | 6 | -3.8 | 21.8 | 0
1854 | TORONTO BUTTONVILLE A | 3 | 19 | 6 | -4.65 | 22.65 | 0
1855 | TORONTO BUTTONVILLE A | 3 | 18 | 7 | -3.3 | 21.3 | 0
1855 | TORONTO BUTTONVILLE A | 3 | 19 | 7 | -4.875 | 22.875 | 0
1856 | TORONTO BUTTONVILLE A | 3 | 18 | 8 | -2.3 | 20.3 | 0
1856 | TORONTO BUTTONVILLE A | 3 | 19 | 8 | -4.675 | 22.675 | 0
1857 | TORONTO BUTTONVILLE A | 3 | 18 | 9 | -0.9 | 18.9 | 0
1857 | TORONTO BUTTONVILLE A | 3 | 19 | 9 | -3.7 | 21.7 | 0
1858 | TORONTO BUTTONVILLE A | 3 | 18 | 10 | 0.8 | 17.2 | 0
1858 | TORONTO BUTTONVILLE A | 3 | 19 | 10 | -2.1 | 20.1 | 0
1859 | TORONTO BUTTONVILLE A | 3 | 18 | 11 | 1.4 | 16.6 | 0
1859 | TORONTO BUTTONVILLE A | 3 | 19 | 11 | -0.7 | 18.7 | 0
1860 | TORONTO BUTTONVILLE A | 3 | 18 | 12 | 2 | 16 | 0
1860 | TORONTO BUTTONVILLE A | 3 | 19 | 12 | 0.8 | 17.2 | 0
1861 | TORONTO BUTTONVILLE A | 3 | 18 | 13 | 2.2 | 15.8 | 0
1861 | TORONTO BUTTONVILLE A | 3 | 19 | 13 | 1.975 | 16.025 | 0
1862 | TORONTO BUTTONVILLE A | 3 | 18 | 14 | 2.6 | 15.4 | 0
1862 | TORONTO BUTTONVILLE A | 3 | 19 | 14 | 3.025 | 14.975 | 0
1863 | TORONTO BUTTONVILLE A | 3 | 18 | 15 | 2.8 | 15.2 | 0
1863 | TORONTO BUTTONVILLE A | 3 | 19 | 15 | 3.675 | 14.325 | 0
1864 | TORONTO BUTTONVILLE A | 3 | 18 | 16 | 3.2 | 14.8 | 0
1864 | TORONTO BUTTONVILLE A | 3 | 19 | 16 | 3.825 | 14.175 | 0
1865 | TORONTO BUTTONVILLE A | 3 | 18 | 17 | 3.1 | 14.9 | 0
1865 | TORONTO BUTTONVILLE A | 3 | 19 | 17 | 3.775 | 14.225 | 0
1866 | TORONTO BUTTONVILLE A | 3 | 18 | 18 | 3.1 | 14.9 | 0
1866 | TORONTO BUTTONVILLE A | 3 | 19 | 18 | 3.65 | 14.35 | 0
1867 | TORONTO BUTTONVILLE A | 3 | 18 | 19 | 3.1 | 14.9 | 0
1867 | TORONTO BUTTONVILLE A | 3 | 19 | 19 | 2.425 | 15.575 | 0
1868 | TORONTO BUTTONVILLE A | 3 | 18 | 20 | 2.9 | 15.1 | 0
1868 | TORONTO BUTTONVILLE A | 3 | 19 | 20 | 1.075 | 16.925 | 0
1869 | TORONTO BUTTONVILLE A | 3 | 18 | 21 | 2.9 | 15.1 | 0
1869 | TORONTO BUTTONVILLE A | 3 | 19 | 21 | 0.1 | 17.9 | 0
1870 | TORONTO BUTTONVILLE A | 3 | 18 | 22 | 3 | 15 | 0
1870 | TORONTO BUTTONVILLE A | 3 | 19 | 22 | -1.025 | 19.025 | 0
1871 | TORONTO BUTTONVILLE A | 3 | 18 | 23 | 2.8 | 15.2 | 0
1871 | TORONTO BUTTONVILLE A | 3 | 19 | 23 | -1.75 | 19.75 | 0
1872 | TORONTO BUTTONVILLE A | 3 | 18 | 24 | 2.8 | 15.2 | 0
1872 | TORONTO BUTTONVILLE A | 3 | 19 | 24 | -2.5 | 20.5 | 0
1873 | TORONTO BUTTONVILLE A | 3 | 19 | 1 | 3 | 15 | 0
1873 | TORONTO BUTTONVILLE A | 3 | 20 | 1 | -2.925 | 20.925 | 0
1874 | TORONTO BUTTONVILLE A | 3 | 19 | 2 | 2.9 | 15.1 | 0
1874 | TORONTO BUTTONVILLE A | 3 | 20 | 2 | -3.175 | 21.175 | 0
1875 | TORONTO BUTTONVILLE A | 3 | 19 | 3 | 3.2 | 14.8 | 0
1875 | TORONTO BUTTONVILLE A | 3 | 20 | 3 | -2.975 | 20.975 | 0
1876 | TORONTO BUTTONVILLE A | 3 | 19 | 4 | 3.1 | 14.9 | 0
1876 | TORONTO BUTTONVILLE A | 3 | 20 | 4 | -3.3 | 21.3 | 0
1877 | TORONTO BUTTONVILLE A | 3 | 19 | 5 | 3.3 | 14.7 | 0
1877 | TORONTO BUTTONVILLE A | 3 | 20 | 5 | -3.5 | 21.5 | 0
1878 | TORONTO BUTTONVILLE A | 3 | 19 | 6 | 3.2 | 14.8 | 0
1878 | TORONTO BUTTONVILLE A | 3 | 20 | 6 | -2.925 | 20.925 | 0
1879 | TORONTO BUTTONVILLE A | 3 | 19 | 7 | 3.4 | 14.6 | 0
1879 | TORONTO BUTTONVILLE A | 3 | 20 | 7 | -2.675 | 20.675 | 0
1880 | TORONTO BUTTONVILLE A | 3 | 19 | 8 | 2.8 | 15.2 | 0
1880 | TORONTO BUTTONVILLE A | 3 | 20 | 8 | -2.55 | 20.55 | 0
1881 | TORONTO BUTTONVILLE A | 3 | 19 | 9 | 3 | 15 | 0
1881 | TORONTO BUTTONVILLE A | 3 | 20 | 9 | -0.225 | 18.225 | 0
1882 | TORONTO BUTTONVILLE A | 3 | 19 | 10 | 4 | 14 | 0
1882 | TORONTO BUTTONVILLE A | 3 | 20 | 10 | 1.975 | 16.025 | 0
1883 | TORONTO BUTTONVILLE A | 3 | 19 | 11 | 5.2 | 12.8 | 0
1883 | TORONTO BUTTONVILLE A | 3 | 20 | 11 | 3.65 | 14.35 | 0
1884 | TORONTO BUTTONVILLE A | 3 | 19 | 12 | 5.9 | 12.1 | 0
1884 | TORONTO BUTTONVILLE A | 3 | 20 | 12 | 4.975 | 13.025 | 0
1885 | TORONTO BUTTONVILLE A | 3 | 19 | 13 | 6.3 | 11.7 | 0
1885 | TORONTO BUTTONVILLE A | 3 | 20 | 13 | 6.2 | 11.8 | 0
1886 | TORONTO BUTTONVILLE A | 3 | 19 | 14 | 6.1 | 11.9 | 0
1886 | TORONTO BUTTONVILLE A | 3 | 20 | 14 | 6.85 | 11.15 | 0
1887 | TORONTO BUTTONVILLE A | 3 | 19 | 15 | 6.2 | 11.8 | 0
1887 | TORONTO BUTTONVILLE A | 3 | 20 | 15 | 7.15 | 10.85 | 0
1888 | TORONTO BUTTONVILLE A | 3 | 19 | 16 | 6.2 | 11.8 | 0
1888 | TORONTO BUTTONVILLE A | 3 | 20 | 16 | 7.525 | 10.475 | 0
1889 | TORONTO BUTTONVILLE A | 3 | 19 | 17 | 5.8 | 12.2 | 0
1889 | TORONTO BUTTONVILLE A | 3 | 20 | 17 | 7.325 | 10.675 | 0
1890 | TORONTO BUTTONVILLE A | 3 | 19 | 18 | 5.8 | 12.2 | 0
1890 | TORONTO BUTTONVILLE A | 3 | 20 | 18 | 6.675 | 11.325 | 0
1891 | TORONTO BUTTONVILLE A | 3 | 19 | 19 | 5.4 | 12.6 | 0
1891 | TORONTO BUTTONVILLE A | 3 | 20 | 19 | 5.875 | 12.125 | 0
1892 | TORONTO BUTTONVILLE A | 3 | 19 | 20 | 5.2 | 12.8 | 0
1892 | TORONTO BUTTONVILLE A | 3 | 20 | 20 | 4.75 | 13.25 | 0
1893 | TORONTO BUTTONVILLE A | 3 | 19 | 21 | 5.2 | 12.8 | 0
1893 | TORONTO BUTTONVILLE A | 3 | 20 | 21 | 3.375 | 14.625 | 0
1894 | TORONTO BUTTONVILLE A | 3 | 19 | 22 | 5.5 | 12.5 | 0
1894 | TORONTO BUTTONVILLE A | 3 | 20 | 22 | 2.95 | 15.05 | 0
1895 | TORONTO BUTTONVILLE A | 3 | 19 | 23 | 5.1 | 12.9 | 0
1895 | TORONTO BUTTONVILLE A | 3 | 20 | 23 | 2.3 | 15.7 | 0
1896 | TORONTO BUTTONVILLE A | 3 | 19 | 24 | 5.3 | 12.7 | 0
1896 | TORONTO BUTTONVILLE A | 3 | 20 | 24 | 1.65 | 16.35 | 0
1897 | TORONTO BUTTONVILLE A | 3 | 20 | 1 | 5.5 | 12.5 | 0
1897 | TORONTO BUTTONVILLE A | 3 | 21 | 1 | 1.4 | 16.6 | 0
1898 | TORONTO BUTTONVILLE A | 3 | 20 | 2 | 5.6 | 12.4 | 0
1898 | TORONTO BUTTONVILLE A | 3 | 21 | 2 | 0.95 | 17.05 | 0
1899 | TORONTO BUTTONVILLE A | 3 | 20 | 3 | 5.9 | 12.1 | 0
1899 | TORONTO BUTTONVILLE A | 3 | 21 | 3 | 0.5 | 17.5 | 0
1900 | TORONTO BUTTONVILLE A | 3 | 20 | 4 | 7.4 | 10.6 | 0
1900 | TORONTO BUTTONVILLE A | 3 | 21 | 4 | -0.05 | 18.05 | 0
1901 | TORONTO BUTTONVILLE A | 3 | 20 | 5 | 10.3 | 7.7 | 0
1901 | TORONTO BUTTONVILLE A | 3 | 21 | 5 | -0.525 | 18.525 | 0
1902 | TORONTO BUTTONVILLE A | 3 | 20 | 6 | 11.8 | 6.2 | 0
1902 | TORONTO BUTTONVILLE A | 3 | 21 | 6 | -0.825 | 18.825 | 0
1903 | TORONTO BUTTONVILLE A | 3 | 20 | 7 | 13.6 | 4.4 | 0
1903 | TORONTO BUTTONVILLE A | 3 | 21 | 7 | -1.125 | 19.125 | 0
1904 | TORONTO BUTTONVILLE A | 3 | 20 | 8 | 15.7 | 2.3 | 0
1904 | TORONTO BUTTONVILLE A | 3 | 21 | 8 | -0.75 | 18.75 | 0
1905 | TORONTO BUTTONVILLE A | 3 | 20 | 9 | 16.1 | 1.9 | 0
1905 | TORONTO BUTTONVILLE A | 3 | 21 | 9 | 0.975 | 17.025 | 0
1906 | TORONTO BUTTONVILLE A | 3 | 20 | 10 | 17 | 1 | 0
1906 | TORONTO BUTTONVILLE A | 3 | 21 | 10 | 3.175 | 14.825 | 0
1907 | TORONTO BUTTONVILLE A | 3 | 20 | 11 | 17.9 | 0.1 | 0
1907 | TORONTO BUTTONVILLE A | 3 | 21 | 11 | 5.05 | 12.95 | 0
1908 | TORONTO BUTTONVILLE A | 3 | 20 | 12 | 14 | 4 | 0
1908 | TORONTO BUTTONVILLE A | 3 | 21 | 12 | 6.475 | 11.525 | 0
1909 | TORONTO BUTTONVILLE A | 3 | 20 | 13 | 10.4 | 7.6 | 0
1909 | TORONTO BUTTONVILLE A | 3 | 21 | 13 | 7.675 | 10.325 | 0
1910 | TORONTO BUTTONVILLE A | 3 | 20 | 14 | 9.8 | 8.2 | 0
1910 | TORONTO BUTTONVILLE A | 3 | 21 | 14 | 8.675 | 9.325 | 0
1911 | TORONTO BUTTONVILLE A | 3 | 20 | 15 | 7.5 | 10.5 | 0
1911 | TORONTO BUTTONVILLE A | 3 | 21 | 15 | 8.95 | 9.05 | 0
1912 | TORONTO BUTTONVILLE A | 3 | 20 | 16 | 5.9 | 12.1 | 0
1912 | TORONTO BUTTONVILLE A | 3 | 21 | 16 | 9.025 | 8.975 | 0
1913 | TORONTO BUTTONVILLE A | 3 | 20 | 17 | 5.2 | 12.8 | 0
1913 | TORONTO BUTTONVILLE A | 3 | 21 | 17 | 8.8 | 9.2 | 0
1914 | TORONTO BUTTONVILLE A | 3 | 20 | 18 | 2.5 | 15.5 | 0
1914 | TORONTO BUTTONVILLE A | 3 | 21 | 18 | 7.75 | 10.25 | 0
1915 | TORONTO BUTTONVILLE A | 3 | 20 | 19 | 0.3 | 17.7 | 0
1915 | TORONTO BUTTONVILLE A | 3 | 21 | 19 | 6.05 | 11.95 | 0
1916 | TORONTO BUTTONVILLE A | 3 | 20 | 20 | -0.9 | 18.9 | 0
1916 | TORONTO BUTTONVILLE A | 3 | 21 | 20 | 3.725 | 14.275 | 0
1917 | TORONTO BUTTONVILLE A | 3 | 20 | 21 | -2.3 | 20.3 | 0
1917 | TORONTO BUTTONVILLE A | 3 | 21 | 21 | 2.775 | 15.225 | 0
1918 | TORONTO BUTTONVILLE A | 3 | 20 | 22 | -2.2 | 20.2 | 0
1918 | TORONTO BUTTONVILLE A | 3 | 21 | 22 | 2.075 | 15.925 | 0
1919 | TORONTO BUTTONVILLE A | 3 | 20 | 23 | -3 | 21 | 0
1919 | TORONTO BUTTONVILLE A | 3 | 21 | 23 | 1.575 | 16.425 | 0
1920 | TORONTO BUTTONVILLE A | 3 | 20 | 24 | -3.7 | 21.7 | 0
1920 | TORONTO BUTTONVILLE A | 3 | 21 | 24 | 0.65 | 17.35 | 0
1921 | TORONTO BUTTONVILLE A | 3 | 21 | 1 | -4.2 | 22.2 | 0
1921 | TORONTO BUTTONVILLE A | 3 | 22 | 1 | -0.175 | 18.175 | 0
1922 | TORONTO BUTTONVILLE A | 3 | 21 | 2 | -5.1 | 23.1 | 0
1922 | TORONTO BUTTONVILLE A | 3 | 22 | 2 | -0.75 | 18.75 | 0
1923 | TORONTO BUTTONVILLE A | 3 | 21 | 3 | -5.9 | 23.9 | 0
1923 | TORONTO BUTTONVILLE A | 3 | 22 | 3 | -1.7 | 19.7 | 0
1924 | TORONTO BUTTONVILLE A | 3 | 21 | 4 | -6.6 | 24.6 | 0
1924 | TORONTO BUTTONVILLE A | 3 | 22 | 4 | -2.225 | 20.225 | 0
1925 | TORONTO BUTTONVILLE A | 3 | 21 | 5 | -7.3 | 25.3 | 0
1925 | TORONTO BUTTONVILLE A | 3 | 22 | 5 | -2.65 | 20.65 | 0
1926 | TORONTO BUTTONVILLE A | 3 | 21 | 6 | -8.3 | 26.3 | 0
1926 | TORONTO BUTTONVILLE A | 3 | 22 | 6 | -2.9 | 20.9 | 0
1927 | TORONTO BUTTONVILLE A | 3 | 21 | 7 | -9.1 | 27.1 | 0
1927 | TORONTO BUTTONVILLE A | 3 | 22 | 7 | -3.45 | 21.45 | 0
1928 | TORONTO BUTTONVILLE A | 3 | 21 | 8 | -9.3 | 27.3 | 0
1928 | TORONTO BUTTONVILLE A | 3 | 22 | 8 | -3.175 | 21.175 | 0
1929 | TORONTO BUTTONVILLE A | 3 | 21 | 9 | -8.6 | 26.6 | 0
1929 | TORONTO BUTTONVILLE A | 3 | 22 | 9 | -1.625 | 19.625 | 0
1930 | TORONTO BUTTONVILLE A | 3 | 21 | 10 | -7.5 | 25.5 | 0
1930 | TORONTO BUTTONVILLE A | 3 | 22 | 10 | -0.175 | 18.175 | 0
1931 | TORONTO BUTTONVILLE A | 3 | 21 | 11 | -6.2 | 24.2 | 0
1931 | TORONTO BUTTONVILLE A | 3 | 22 | 11 | 1.325 | 16.675 | 0
1932 | TORONTO BUTTONVILLE A | 3 | 21 | 12 | -4.7 | 22.7 | 0
1932 | TORONTO BUTTONVILLE A | 3 | 22 | 12 | 2.25 | 15.75 | 0
1933 | TORONTO BUTTONVILLE A | 3 | 21 | 13 | -3.4 | 21.4 | 0
1933 | TORONTO BUTTONVILLE A | 3 | 22 | 13 | 2.625 | 15.375 | 0
1934 | TORONTO BUTTONVILLE A | 3 | 21 | 14 | -2.2 | 20.2 | 0
1934 | TORONTO BUTTONVILLE A | 3 | 22 | 14 | 3.775 | 14.225 | 0
1935 | TORONTO BUTTONVILLE A | 3 | 21 | 15 | -1.2 | 19.2 | 0
1935 | TORONTO BUTTONVILLE A | 3 | 22 | 15 | 4.05 | 13.95 | 0
1936 | TORONTO BUTTONVILLE A | 3 | 21 | 16 | -0.9 | 18.9 | 0
1936 | TORONTO BUTTONVILLE A | 3 | 22 | 16 | 3.625 | 14.375 | 0
1937 | TORONTO BUTTONVILLE A | 3 | 21 | 17 | -0.8 | 18.8 | 0
1937 | TORONTO BUTTONVILLE A | 3 | 22 | 17 | 3.35 | 14.65 | 0
1938 | TORONTO BUTTONVILLE A | 3 | 21 | 18 | -1.4 | 19.4 | 0
1938 | TORONTO BUTTONVILLE A | 3 | 22 | 18 | 2.375 | 15.625 | 0
1939 | TORONTO BUTTONVILLE A | 3 | 21 | 19 | -1.8 | 19.8 | 0
1939 | TORONTO BUTTONVILLE A | 3 | 22 | 19 | 0.85 | 17.15 | 0
1940 | TORONTO BUTTONVILLE A | 3 | 21 | 20 | -2.8 | 20.8 | 0
1940 | TORONTO BUTTONVILLE A | 3 | 22 | 20 | -0.15 | 18.15 | 0
1941 | TORONTO BUTTONVILLE A | 3 | 21 | 21 | -3.7 | 21.7 | 0
1941 | TORONTO BUTTONVILLE A | 3 | 22 | 21 | -0.725 | 18.725 | 0
1942 | TORONTO BUTTONVILLE A | 3 | 21 | 22 | -4.5 | 22.5 | 0
1942 | TORONTO BUTTONVILLE A | 3 | 22 | 22 | -1.3 | 19.3 | 0
1943 | TORONTO BUTTONVILLE A | 3 | 21 | 23 | -5.6 | 23.6 | 0
1943 | TORONTO BUTTONVILLE A | 3 | 22 | 23 | -1.65 | 19.65 | 0
1944 | TORONTO BUTTONVILLE A | 3 | 21 | 24 | -6 | 24 | 0
1944 | TORONTO BUTTONVILLE A | 3 | 22 | 24 | -2.15 | 20.15 | 0
1945 | TORONTO BUTTONVILLE A | 3 | 22 | 1 | -6.1 | 24.1 | 0
1945 | TORONTO BUTTONVILLE A | 3 | 23 | 1 | -2.425 | 20.425 | 0
1946 | TORONTO BUTTONVILLE A | 3 | 22 | 2 | -6 | 24 | 0
1946 | TORONTO BUTTONVILLE A | 3 | 23 | 2 | -2.9 | 20.9 | 0
1947 | TORONTO BUTTONVILLE A | 3 | 22 | 3 | -6.2 | 24.2 | 0
1947 | TORONTO BUTTONVILLE A | 3 | 23 | 3 | -3.025 | 21.025 | 0
1948 | TORONTO BUTTONVILLE A | 3 | 22 | 4 | -7.1 | 25.1 | 0
1948 | TORONTO BUTTONVILLE A | 3 | 23 | 4 | -3.525 | 21.525 | 0
1949 | TORONTO BUTTONVILLE A | 3 | 22 | 5 | -7 | 25 | 0
1949 | TORONTO BUTTONVILLE A | 3 | 23 | 5 | -3.85 | 21.85 | 0
1950 | TORONTO BUTTONVILLE A | 3 | 22 | 6 | -6.7 | 24.7 | 0
1950 | TORONTO BUTTONVILLE A | 3 | 23 | 6 | -4.45 | 22.45 | 0
1951 | TORONTO BUTTONVILLE A | 3 | 22 | 7 | -6.6 | 24.6 | 0
1951 | TORONTO BUTTONVILLE A | 3 | 23 | 7 | -5.025 | 23.025 | 0
1952 | TORONTO BUTTONVILLE A | 3 | 22 | 8 | -5.7 | 23.7 | 0
1952 | TORONTO BUTTONVILLE A | 3 | 23 | 8 | -4.2 | 22.2 | 0
1953 | TORONTO BUTTONVILLE A | 3 | 22 | 9 | -4.1 | 22.1 | 0
1953 | TORONTO BUTTONVILLE A | 3 | 23 | 9 | -1.9 | 19.9 | 0
1954 | TORONTO BUTTONVILLE A | 3 | 22 | 10 | -2.9 | 20.9 | 0
1954 | TORONTO BUTTONVILLE A | 3 | 23 | 10 | 0.425 | 17.575 | 0
1955 | TORONTO BUTTONVILLE A | 3 | 22 | 11 | -2 | 20 | 0
1955 | TORONTO BUTTONVILLE A | 3 | 23 | 11 | 2.125 | 15.875 | 0
1956 | TORONTO BUTTONVILLE A | 3 | 22 | 12 | -1 | 19 | 0
1956 | TORONTO BUTTONVILLE A | 3 | 23 | 12 | 3.55 | 14.45 | 0
1957 | TORONTO BUTTONVILLE A | 3 | 22 | 13 | -1.6 | 19.6 | 0
1957 | TORONTO BUTTONVILLE A | 3 | 23 | 13 | 4.525 | 13.475 | 0
1958 | TORONTO BUTTONVILLE A | 3 | 22 | 14 | -0.7 | 18.7 | 0
1958 | TORONTO BUTTONVILLE A | 3 | 23 | 14 | 5.225 | 12.775 | 0
1959 | TORONTO BUTTONVILLE A | 3 | 22 | 15 | -1 | 19 | 0
1959 | TORONTO BUTTONVILLE A | 3 | 23 | 15 | 5.625 | 12.375 | 0
1960 | TORONTO BUTTONVILLE A | 3 | 22 | 16 | -0.7 | 18.7 | 0
1960 | TORONTO BUTTONVILLE A | 3 | 23 | 16 | 5.675 | 12.325 | 0
1961 | TORONTO BUTTONVILLE A | 3 | 22 | 17 | -1 | 19 | 0
1961 | TORONTO BUTTONVILLE A | 3 | 23 | 17 | 5.975 | 12.025 | 0
1962 | TORONTO BUTTONVILLE A | 3 | 22 | 18 | -1.1 | 19.1 | 0
1962 | TORONTO BUTTONVILLE A | 3 | 23 | 18 | 5.375 | 12.625 | 0
1963 | TORONTO BUTTONVILLE A | 3 | 22 | 19 | -1.5 | 19.5 | 0
1963 | TORONTO BUTTONVILLE A | 3 | 23 | 19 | 4.15 | 13.85 | 0
1964 | TORONTO BUTTONVILLE A | 3 | 22 | 20 | -1.8 | 19.8 | 0
1964 | TORONTO BUTTONVILLE A | 3 | 23 | 20 | 3.125 | 14.875 | 0
1965 | TORONTO BUTTONVILLE A | 3 | 22 | 21 | -1.8 | 19.8 | 0
1965 | TORONTO BUTTONVILLE A | 3 | 23 | 21 | 2.175 | 15.825 | 0
1966 | TORONTO BUTTONVILLE A | 3 | 22 | 22 | -1.5 | 19.5 | 0
1966 | TORONTO BUTTONVILLE A | 3 | 23 | 22 | 1.65 | 16.35 | 0
1967 | TORONTO BUTTONVILLE A | 3 | 22 | 23 | -1.3 | 19.3 | 0
1967 | TORONTO BUTTONVILLE A | 3 | 23 | 23 | 1.125 | 16.875 | 0
1968 | TORONTO BUTTONVILLE A | 3 | 22 | 24 | -1 | 19 | 0
1968 | TORONTO BUTTONVILLE A | 3 | 23 | 24 | 0.825 | 17.175 | 0
1969 | TORONTO BUTTONVILLE A | 3 | 23 | 1 | -0.8 | 18.8 | 0
1969 | TORONTO BUTTONVILLE A | 3 | 24 | 1 | 1.15 | 16.85 | 0
1970 | TORONTO BUTTONVILLE A | 3 | 23 | 2 | -0.4 | 18.4 | 0
1970 | TORONTO BUTTONVILLE A | 3 | 24 | 2 | 0.975 | 17.025 | 0
1971 | TORONTO BUTTONVILLE A | 3 | 23 | 3 | 0.2 | 17.8 | 0
1971 | TORONTO BUTTONVILLE A | 3 | 24 | 3 | 0.35 | 17.65 | 0
1972 | TORONTO BUTTONVILLE A | 3 | 23 | 4 | 0.2 | 17.8 | 0
1972 | TORONTO BUTTONVILLE A | 3 | 24 | 4 | 0.05 | 17.95 | 0
1973 | TORONTO BUTTONVILLE A | 3 | 23 | 5 | -0.2 | 18.2 | 0
1973 | TORONTO BUTTONVILLE A | 3 | 24 | 5 | -0.075 | 18.075 | 0
1974 | TORONTO BUTTONVILLE A | 3 | 23 | 6 | -0.4 | 18.4 | 0
1974 | TORONTO BUTTONVILLE A | 3 | 24 | 6 | -0.025 | 18.025 | 0
1975 | TORONTO BUTTONVILLE A | 3 | 23 | 7 | -0.2 | 18.2 | 0
1975 | TORONTO BUTTONVILLE A | 3 | 24 | 7 | -0.05 | 18.05 | 0
1976 | TORONTO BUTTONVILLE A | 3 | 23 | 8 | 0 | 18 | 0
1976 | TORONTO BUTTONVILLE A | 3 | 24 | 8 | 1.05 | 16.95 | 0
1977 | TORONTO BUTTONVILLE A | 3 | 23 | 9 | 0.3 | 17.7 | 0
1977 | TORONTO BUTTONVILLE A | 3 | 24 | 9 | 1.975 | 16.025 | 0
1978 | TORONTO BUTTONVILLE A | 3 | 23 | 10 | 0.8 | 17.2 | 0
1978 | TORONTO BUTTONVILLE A | 3 | 24 | 10 | 2.95 | 15.05 | 0
1979 | TORONTO BUTTONVILLE A | 3 | 23 | 11 | 1.2 | 16.8 | 0
1979 | TORONTO BUTTONVILLE A | 3 | 24 | 11 | 4.9 | 13.1 | 0
1980 | TORONTO BUTTONVILLE A | 3 | 23 | 12 | 1.2 | 16.8 | 0
1980 | TORONTO BUTTONVILLE A | 3 | 24 | 12 | 5.675 | 12.325 | 0
1981 | TORONTO BUTTONVILLE A | 3 | 23 | 13 | 1.4 | 16.6 | 0
1981 | TORONTO BUTTONVILLE A | 3 | 24 | 13 | 7.075 | 10.925 | 0
1982 | TORONTO BUTTONVILLE A | 3 | 23 | 14 | 2.1 | 15.9 | 0
1982 | TORONTO BUTTONVILLE A | 3 | 24 | 14 | 7.975 | 10.025 | 0
1983 | TORONTO BUTTONVILLE A | 3 | 23 | 15 | 2.4 | 15.6 | 0
1983 | TORONTO BUTTONVILLE A | 3 | 24 | 15 | 8.825 | 9.175 | 0
1984 | TORONTO BUTTONVILLE A | 3 | 23 | 16 | 2 | 16 | 0
1984 | TORONTO BUTTONVILLE A | 3 | 24 | 16 | 8.95 | 9.05 | 0
1985 | TORONTO BUTTONVILLE A | 3 | 23 | 17 | 2 | 16 | 0
1985 | TORONTO BUTTONVILLE A | 3 | 24 | 17 | 9.25 | 8.75 | 0
1986 | TORONTO BUTTONVILLE A | 3 | 23 | 18 | 1.9 | 16.1 | 0
1986 | TORONTO BUTTONVILLE A | 3 | 24 | 18 | 8.575 | 9.425 | 0
1987 | TORONTO BUTTONVILLE A | 3 | 23 | 19 | 2 | 16 | 0
1987 | TORONTO BUTTONVILLE A | 3 | 24 | 19 | 6.6 | 11.4 | 0
1988 | TORONTO BUTTONVILLE A | 3 | 23 | 20 | 2 | 16 | 0
1988 | TORONTO BUTTONVILLE A | 3 | 24 | 20 | 4.925 | 13.075 | 0
1989 | TORONTO BUTTONVILLE A | 3 | 23 | 21 | 2.2 | 15.8 | 0
1989 | TORONTO BUTTONVILLE A | 3 | 24 | 21 | 3.775 | 14.225 | 0
1990 | TORONTO BUTTONVILLE A | 3 | 23 | 22 | 2 | 16 | 0
1990 | TORONTO BUTTONVILLE A | 3 | 24 | 22 | 3.075 | 14.925 | 0
1991 | TORONTO BUTTONVILLE A | 3 | 23 | 23 | 2 | 16 | 0
1991 | TORONTO BUTTONVILLE A | 3 | 24 | 23 | 2.375 | 15.625 | 0
1992 | TORONTO BUTTONVILLE A | 3 | 23 | 24 | 1.9 | 16.1 | 0
1992 | TORONTO BUTTONVILLE A | 3 | 24 | 24 | 1.75 | 16.25 | 0
1993 | TORONTO BUTTONVILLE A | 3 | 24 | 1 | 1.7 | 16.3 | 0
1993 | TORONTO BUTTONVILLE A | 3 | 25 | 1 | 1.275 | 16.725 | 0
1994 | TORONTO BUTTONVILLE A | 3 | 24 | 2 | 1.4 | 16.6 | 0
1994 | TORONTO BUTTONVILLE A | 3 | 25 | 2 | 0.5 | 17.5 | 0
1995 | TORONTO BUTTONVILLE A | 3 | 24 | 3 | 1.3 | 16.7 | 0
1995 | TORONTO BUTTONVILLE A | 3 | 25 | 3 | -0.175 | 18.175 | 0
1996 | TORONTO BUTTONVILLE A | 3 | 24 | 4 | 0.4 | 17.6 | 0
1996 | TORONTO BUTTONVILLE A | 3 | 25 | 4 | -1.05 | 19.05 | 0
1997 | TORONTO BUTTONVILLE A | 3 | 24 | 5 | -0.1 | 18.1 | 0
1997 | TORONTO BUTTONVILLE A | 3 | 25 | 5 | -1.125 | 19.125 | 0
1998 | TORONTO BUTTONVILLE A | 3 | 24 | 6 | 0.4 | 17.6 | 0
1998 | TORONTO BUTTONVILLE A | 3 | 25 | 6 | -1.475 | 19.475 | 0
1999 | TORONTO BUTTONVILLE A | 3 | 24 | 7 | 0.4 | 17.6 | 0
1999 | TORONTO BUTTONVILLE A | 3 | 25 | 7 | -1.825 | 19.825 | 0
2000 | TORONTO BUTTONVILLE A | 3 | 24 | 8 | 0.7 | 17.3 | 0
2000 | TORONTO BUTTONVILLE A | 3 | 25 | 8 | -1.45 | 19.45 | 0
2001 | TORONTO BUTTONVILLE A | 3 | 24 | 9 | 1 | 17 | 0
2001 | TORONTO BUTTONVILLE A | 3 | 25 | 9 | 0.25 | 17.75 | 0
2002 | TORONTO BUTTONVILLE A | 3 | 24 | 10 | 1.5 | 16.5 | 0
2002 | TORONTO BUTTONVILLE A | 3 | 25 | 10 | 2.2 | 15.8 | 0
2003 | TORONTO BUTTONVILLE A | 3 | 24 | 11 | 1.8 | 16.2 | 0
2003 | TORONTO BUTTONVILLE A | 3 | 25 | 11 | 3.425 | 14.575 | 0
2004 | TORONTO BUTTONVILLE A | 3 | 24 | 12 | 3.1 | 14.9 | 0
2004 | TORONTO BUTTONVILLE A | 3 | 25 | 12 | 4.55 | 13.45 | 0
2005 | TORONTO BUTTONVILLE A | 3 | 24 | 13 | 4 | 14 | 0
2005 | TORONTO BUTTONVILLE A | 3 | 25 | 13 | 5.5 | 12.5 | 0
2006 | TORONTO BUTTONVILLE A | 3 | 24 | 14 | 4.5 | 13.5 | 0
2006 | TORONTO BUTTONVILLE A | 3 | 25 | 14 | 6.175 | 11.825 | 0
2007 | TORONTO BUTTONVILLE A | 3 | 24 | 15 | 5.2 | 12.8 | 0
2007 | TORONTO BUTTONVILLE A | 3 | 25 | 15 | 6.85 | 11.15 | 0
2008 | TORONTO BUTTONVILLE A | 3 | 24 | 16 | 5.4 | 12.6 | 0
2008 | TORONTO BUTTONVILLE A | 3 | 25 | 16 | 7.45 | 10.55 | 0
2009 | TORONTO BUTTONVILLE A | 3 | 24 | 17 | 4.6 | 13.4 | 0
2009 | TORONTO BUTTONVILLE A | 3 | 25 | 17 | 6.95 | 11.05 | 0
2010 | TORONTO BUTTONVILLE A | 3 | 24 | 18 | 4.3 | 13.7 | 0
2010 | TORONTO BUTTONVILLE A | 3 | 25 | 18 | 6.225 | 11.775 | 0
2011 | TORONTO BUTTONVILLE A | 3 | 24 | 19 | 3.9 | 14.1 | 0
2011 | TORONTO BUTTONVILLE A | 3 | 25 | 19 | 5.5 | 12.5 | 0
2012 | TORONTO BUTTONVILLE A | 3 | 24 | 20 | 2.8 | 15.2 | 0
2012 | TORONTO BUTTONVILLE A | 3 | 25 | 20 | 3.7 | 14.3 | 0
2013 | TORONTO BUTTONVILLE A | 3 | 24 | 21 | 1.6 | 16.4 | 0
2013 | TORONTO BUTTONVILLE A | 3 | 25 | 21 | 2.95 | 15.05 | 0
2014 | TORONTO BUTTONVILLE A | 3 | 24 | 22 | 1.1 | 16.9 | 0
2014 | TORONTO BUTTONVILLE A | 3 | 25 | 22 | 2.225 | 15.775 | 0
2015 | TORONTO BUTTONVILLE A | 3 | 24 | 23 | 0.7 | 17.3 | 0
2015 | TORONTO BUTTONVILLE A | 3 | 25 | 23 | 1.725 | 16.275 | 0
2016 | TORONTO BUTTONVILLE A | 3 | 24 | 24 | 0 | 18 | 0
2016 | TORONTO BUTTONVILLE A | 3 | 25 | 24 | 1 | 17 | 0
2017 | TORONTO BUTTONVILLE A | 3 | 25 | 1 | 0.1 | 17.9 | 0
2017 | TORONTO BUTTONVILLE A | 3 | 26 | 1 | 0.35 | 17.65 | 0
2018 | TORONTO BUTTONVILLE A | 3 | 25 | 2 | 0.3 | 17.7 | 0
2018 | TORONTO BUTTONVILLE A | 3 | 26 | 2 | 0.075 | 17.925 | 0
2019 | TORONTO BUTTONVILLE A | 3 | 25 | 3 | 0.2 | 17.8 | 0
2019 | TORONTO BUTTONVILLE A | 3 | 26 | 3 | 0.375 | 17.625 | 0
2020 | TORONTO BUTTONVILLE A | 3 | 25 | 4 | 0.6 | 17.4 | 0
2020 | TORONTO BUTTONVILLE A | 3 | 26 | 4 | 0.55 | 17.45 | 0
2021 | TORONTO BUTTONVILLE A | 3 | 25 | 5 | 0.4 | 17.6 | 0
2021 | TORONTO BUTTONVILLE A | 3 | 26 | 5 | 0.65 | 17.35 | 0
2022 | TORONTO BUTTONVILLE A | 3 | 25 | 6 | 0.6 | 17.4 | 0
2022 | TORONTO BUTTONVILLE A | 3 | 26 | 6 | 0.35 | 17.65 | 0
2023 | TORONTO BUTTONVILLE A | 3 | 25 | 7 | 0.5 | 17.5 | 0
2023 | TORONTO BUTTONVILLE A | 3 | 26 | 7 | 0.225 | 17.775 | 0
2024 | TORONTO BUTTONVILLE A | 3 | 25 | 8 | 0.6 | 17.4 | 0
2024 | TORONTO BUTTONVILLE A | 3 | 26 | 8 | 0.875 | 17.125 | 0
2025 | TORONTO BUTTONVILLE A | 3 | 25 | 9 | 1.2 | 16.8 | 0
2025 | TORONTO BUTTONVILLE A | 3 | 26 | 9 | 2.2 | 15.8 | 0
2026 | TORONTO BUTTONVILLE A | 3 | 25 | 10 | 2.3 | 15.7 | 0
2026 | TORONTO BUTTONVILLE A | 3 | 26 | 10 | 3.125 | 14.875 | 0
2027 | TORONTO BUTTONVILLE A | 3 | 25 | 11 | 3 | 15 | 0
2027 | TORONTO BUTTONVILLE A | 3 | 26 | 11 | 3.275 | 14.725 | 0
2028 | TORONTO BUTTONVILLE A | 3 | 25 | 12 | 4 | 14 | 0
2028 | TORONTO BUTTONVILLE A | 3 | 26 | 12 | 3.675 | 14.325 | 0
2029 | TORONTO BUTTONVILLE A | 3 | 25 | 13 | 6.1 | 11.9 | 0
2029 | TORONTO BUTTONVILLE A | 3 | 26 | 13 | 3.95 | 14.05 | 0
2030 | TORONTO BUTTONVILLE A | 3 | 25 | 14 | 7.1 | 10.9 | 0
2030 | TORONTO BUTTONVILLE A | 3 | 26 | 14 | 3.825 | 14.175 | 0
2031 | TORONTO BUTTONVILLE A | 3 | 25 | 15 | 7.2 | 10.8 | 0
2031 | TORONTO BUTTONVILLE A | 3 | 26 | 15 | 4.925 | 13.075 | 0
2032 | TORONTO BUTTONVILLE A | 3 | 25 | 16 | 7.7 | 10.3 | 0
2032 | TORONTO BUTTONVILLE A | 3 | 26 | 16 | 5.1 | 12.9 | 0
2033 | TORONTO BUTTONVILLE A | 3 | 25 | 17 | 9.5 | 8.5 | 0
2033 | TORONTO BUTTONVILLE A | 3 | 26 | 17 | 5.1 | 12.9 | 0
2034 | TORONTO BUTTONVILLE A | 3 | 25 | 18 | 8 | 10 | 0
2034 | TORONTO BUTTONVILLE A | 3 | 26 | 18 | 4.475 | 13.525 | 0
2035 | TORONTO BUTTONVILLE A | 3 | 25 | 19 | 6.5 | 11.5 | 0
2035 | TORONTO BUTTONVILLE A | 3 | 26 | 19 | 3.625 | 14.375 | 0
2036 | TORONTO BUTTONVILLE A | 3 | 25 | 20 | 4.7 | 13.3 | 0
2036 | TORONTO BUTTONVILLE A | 3 | 26 | 20 | 2.875 | 15.125 | 0
2037 | TORONTO BUTTONVILLE A | 3 | 25 | 21 | 3.9 | 14.1 | 0
2037 | TORONTO BUTTONVILLE A | 3 | 26 | 21 | 2.625 | 15.375 | 0
2038 | TORONTO BUTTONVILLE A | 3 | 25 | 22 | 2.9 | 15.1 | 0
2038 | TORONTO BUTTONVILLE A | 3 | 26 | 22 | 2.7 | 15.3 | 0
2039 | TORONTO BUTTONVILLE A | 3 | 25 | 23 | 2.4 | 15.6 | 0
2039 | TORONTO BUTTONVILLE A | 3 | 26 | 23 | 2.075 | 15.925 | 0
2040 | TORONTO BUTTONVILLE A | 3 | 25 | 24 | 1.8 | 16.2 | 0
2040 | TORONTO BUTTONVILLE A | 3 | 26 | 24 | 2.025 | 15.975 | 0
2041 | TORONTO BUTTONVILLE A | 3 | 26 | 1 | 0.9 | 17.1 | 0
2041 | TORONTO BUTTONVILLE A | 3 | 27 | 1 | 1.825 | 16.175 | 0
2042 | TORONTO BUTTONVILLE A | 3 | 26 | 2 | 0.5 | 17.5 | 0
2042 | TORONTO BUTTONVILLE A | 3 | 27 | 2 | 1.55 | 16.45 | 0
2043 | TORONTO BUTTONVILLE A | 3 | 26 | 3 | 0.4 | 17.6 | 0
2043 | TORONTO BUTTONVILLE A | 3 | 27 | 3 | 1.8 | 16.2 | 0
2044 | TORONTO BUTTONVILLE A | 3 | 26 | 4 | 1.1 | 16.9 | 0
2044 | TORONTO BUTTONVILLE A | 3 | 27 | 4 | 1.625 | 16.375 | 0
2045 | TORONTO BUTTONVILLE A | 3 | 26 | 5 | 0.8 | 17.2 | 0
2045 | TORONTO BUTTONVILLE A | 3 | 27 | 5 | 1.55 | 16.45 | 0
2046 | TORONTO BUTTONVILLE A | 3 | 26 | 6 | 0.6 | 17.4 | 0
2046 | TORONTO BUTTONVILLE A | 3 | 27 | 6 | 1.625 | 16.375 | 0
2047 | TORONTO BUTTONVILLE A | 3 | 26 | 7 | 0.7 | 17.3 | 0
2047 | TORONTO BUTTONVILLE A | 3 | 27 | 7 | 1.8 | 16.2 | 0
2048 | TORONTO BUTTONVILLE A | 3 | 26 | 8 | 1.6 | 16.4 | 0
2048 | TORONTO BUTTONVILLE A | 3 | 27 | 8 | 2.075 | 15.925 | 0
2049 | TORONTO BUTTONVILLE A | 3 | 26 | 9 | 4.6 | 13.4 | 0
2049 | TORONTO BUTTONVILLE A | 3 | 27 | 9 | 2.975 | 15.025 | 0
2050 | TORONTO BUTTONVILLE A | 3 | 26 | 10 | 8.1 | 9.9 | 0
2050 | TORONTO BUTTONVILLE A | 3 | 27 | 10 | 4.125 | 13.875 | 0
2051 | TORONTO BUTTONVILLE A | 3 | 26 | 11 | 8.9 | 9.1 | 0
2051 | TORONTO BUTTONVILLE A | 3 | 27 | 11 | 4.775 | 13.225 | 0
2052 | TORONTO BUTTONVILLE A | 3 | 26 | 12 | 9.9 | 8.1 | 0
2052 | TORONTO BUTTONVILLE A | 3 | 27 | 12 | 5.525 | 12.475 | 0
2053 | TORONTO BUTTONVILLE A | 3 | 26 | 13 | 10.9 | 7.1 | 0
2053 | TORONTO BUTTONVILLE A | 3 | 27 | 13 | 6.325 | 11.675 | 0
2054 | TORONTO BUTTONVILLE A | 3 | 26 | 14 | 11.8 | 6.2 | 0
2054 | TORONTO BUTTONVILLE A | 3 | 27 | 14 | 7.3 | 10.7 | 0
2055 | TORONTO BUTTONVILLE A | 3 | 26 | 15 | 11.7 | 6.3 | 0
2055 | TORONTO BUTTONVILLE A | 3 | 27 | 15 | 7.45 | 10.55 | 0
2056 | TORONTO BUTTONVILLE A | 3 | 26 | 16 | 11 | 7 | 0
2056 | TORONTO BUTTONVILLE A | 3 | 27 | 16 | 7.675 | 10.325 | 0
2057 | TORONTO BUTTONVILLE A | 3 | 26 | 17 | 7.9 | 10.1 | 0
2057 | TORONTO BUTTONVILLE A | 3 | 27 | 17 | 7.6 | 10.4 | 0
2058 | TORONTO BUTTONVILLE A | 3 | 26 | 18 | 7.8 | 10.2 | 0
2058 | TORONTO BUTTONVILLE A | 3 | 27 | 18 | 7.05 | 10.95 | 0
2059 | TORONTO BUTTONVILLE A | 3 | 26 | 19 | 5.8 | 12.2 | 0
2059 | TORONTO BUTTONVILLE A | 3 | 27 | 19 | 6.3 | 11.7 | 0
2060 | TORONTO BUTTONVILLE A | 3 | 26 | 20 | 4.4 | 13.6 | 0
2060 | TORONTO BUTTONVILLE A | 3 | 27 | 20 | 5.75 | 12.25 | 0
2061 | TORONTO BUTTONVILLE A | 3 | 26 | 21 | 3.5 | 14.5 | 0
2061 | TORONTO BUTTONVILLE A | 3 | 27 | 21 | 5.525 | 12.475 | 0
2062 | TORONTO BUTTONVILLE A | 3 | 26 | 22 | 3.7 | 14.3 | 0
2062 | TORONTO BUTTONVILLE A | 3 | 27 | 22 | 5.35 | 12.65 | 0
2063 | TORONTO BUTTONVILLE A | 3 | 26 | 23 | 3.3 | 14.7 | 0
2063 | TORONTO BUTTONVILLE A | 3 | 27 | 23 | 5.175 | 12.825 | 0
2064 | TORONTO BUTTONVILLE A | 3 | 26 | 24 | 3.3 | 14.7 | 0
2064 | TORONTO BUTTONVILLE A | 3 | 27 | 24 | 4.225 | 13.775 | 0
2065 | TORONTO BUTTONVILLE A | 3 | 27 | 1 | 2.6 | 15.4 | 0
2065 | TORONTO BUTTONVILLE A | 3 | 28 | 1 | 4.025 | 13.975 | 0
2066 | TORONTO BUTTONVILLE A | 3 | 27 | 2 | 2.3 | 15.7 | 0
2066 | TORONTO BUTTONVILLE A | 3 | 28 | 2 | 3.9 | 14.1 | 0
2067 | TORONTO BUTTONVILLE A | 3 | 27 | 3 | 1.7 | 16.3 | 0
2067 | TORONTO BUTTONVILLE A | 3 | 28 | 3 | 3.625 | 14.375 | 0
2068 | TORONTO BUTTONVILLE A | 3 | 27 | 4 | 1.8 | 16.2 | 0
2068 | TORONTO BUTTONVILLE A | 3 | 28 | 4 | 3.075 | 14.925 | 0
2069 | TORONTO BUTTONVILLE A | 3 | 27 | 5 | 1.6 | 16.4 | 0
2069 | TORONTO BUTTONVILLE A | 3 | 28 | 5 | 2.975 | 15.025 | 0
2070 | TORONTO BUTTONVILLE A | 3 | 27 | 6 | 1.5 | 16.5 | 0
2070 | TORONTO BUTTONVILLE A | 3 | 28 | 6 | 3.325 | 14.675 | 0
2071 | TORONTO BUTTONVILLE A | 3 | 27 | 7 | 1.3 | 16.7 | 0
2071 | TORONTO BUTTONVILLE A | 3 | 28 | 7 | 3.575 | 14.425 | 0
2072 | TORONTO BUTTONVILLE A | 3 | 27 | 8 | 1.4 | 16.6 | 0
2072 | TORONTO BUTTONVILLE A | 3 | 28 | 8 | 3.55 | 14.45 | 0
2073 | TORONTO BUTTONVILLE A | 3 | 27 | 9 | 1.6 | 16.4 | 0
2073 | TORONTO BUTTONVILLE A | 3 | 28 | 9 | 3.2 | 14.8 | 0
2074 | TORONTO BUTTONVILLE A | 3 | 27 | 10 | 2 | 16 | 0
2074 | TORONTO BUTTONVILLE A | 3 | 28 | 10 | 3.675 | 14.325 | 0
2075 | TORONTO BUTTONVILLE A | 3 | 27 | 11 | 3.1 | 14.9 | 0
2075 | TORONTO BUTTONVILLE A | 3 | 28 | 11 | 4.55 | 13.45 | 0
2076 | TORONTO BUTTONVILLE A | 3 | 27 | 12 | 5.4 | 12.6 | 0
2076 | TORONTO BUTTONVILLE A | 3 | 28 | 12 | 5.475 | 12.525 | 0
2077 | TORONTO BUTTONVILLE A | 3 | 27 | 13 | 7.9 | 10.1 | 0
2077 | TORONTO BUTTONVILLE A | 3 | 28 | 13 | 7.175 | 10.825 | 0
2078 | TORONTO BUTTONVILLE A | 3 | 27 | 14 | 8.9 | 9.1 | 0
2078 | TORONTO BUTTONVILLE A | 3 | 28 | 14 | 7.8 | 10.2 | 0
2079 | TORONTO BUTTONVILLE A | 3 | 27 | 15 | 10.3 | 7.7 | 0
2079 | TORONTO BUTTONVILLE A | 3 | 28 | 15 | 8.775 | 9.225 | 0
2080 | TORONTO BUTTONVILLE A | 3 | 27 | 16 | 10 | 8 | 0
2080 | TORONTO BUTTONVILLE A | 3 | 28 | 16 | 8.6 | 9.4 | 0
2081 | TORONTO BUTTONVILLE A | 3 | 27 | 17 | 9.6 | 8.4 | 0
2081 | TORONTO BUTTONVILLE A | 3 | 28 | 17 | 7.95 | 10.05 | 0
2082 | TORONTO BUTTONVILLE A | 3 | 27 | 18 | 9.3 | 8.7 | 0
2082 | TORONTO BUTTONVILLE A | 3 | 28 | 18 | 7.2 | 10.8 | 0
2083 | TORONTO BUTTONVILLE A | 3 | 27 | 19 | 8.9 | 9.1 | 0
2083 | TORONTO BUTTONVILLE A | 3 | 28 | 19 | 6.3 | 11.7 | 0
2084 | TORONTO BUTTONVILLE A | 3 | 27 | 20 | 6.9 | 11.1 | 0
2084 | TORONTO BUTTONVILLE A | 3 | 28 | 20 | 5.5 | 12.5 | 0
2085 | TORONTO BUTTONVILLE A | 3 | 27 | 21 | 5.3 | 12.7 | 0
2085 | TORONTO BUTTONVILLE A | 3 | 28 | 21 | 4.725 | 13.275 | 0
2086 | TORONTO BUTTONVILLE A | 3 | 27 | 22 | 4.4 | 13.6 | 0
2086 | TORONTO BUTTONVILLE A | 3 | 28 | 22 | 3.9 | 14.1 | 0
2087 | TORONTO BUTTONVILLE A | 3 | 27 | 23 | 2.3 | 15.7 | 0
2087 | TORONTO BUTTONVILLE A | 3 | 28 | 23 | 3 | 15 | 0
2088 | TORONTO BUTTONVILLE A | 3 | 27 | 24 | 1.6 | 16.4 | 0
2088 | TORONTO BUTTONVILLE A | 3 | 28 | 24 | 2.45 | 15.55 | 0
2089 | TORONTO BUTTONVILLE A | 3 | 28 | 1 | 1.5 | 16.5 | 0
2089 | TORONTO BUTTONVILLE A | 3 | 29 | 1 | 1.975 | 16.025 | 0
2090 | TORONTO BUTTONVILLE A | 3 | 28 | 2 | 0.6 | 17.4 | 0
2090 | TORONTO BUTTONVILLE A | 3 | 29 | 2 | 1.575 | 16.425 | 0
2091 | TORONTO BUTTONVILLE A | 3 | 28 | 3 | 1 | 17 | 0
2091 | TORONTO BUTTONVILLE A | 3 | 29 | 3 | 1.45 | 16.55 | 0
2092 | TORONTO BUTTONVILLE A | 3 | 28 | 4 | 1.9 | 16.1 | 0
2092 | TORONTO BUTTONVILLE A | 3 | 29 | 4 | 1 | 17 | 0
2093 | TORONTO BUTTONVILLE A | 3 | 28 | 5 | 2.6 | 15.4 | 0
2093 | TORONTO BUTTONVILLE A | 3 | 29 | 5 | 0.925 | 17.075 | 0
2094 | TORONTO BUTTONVILLE A | 3 | 28 | 6 | 3.5 | 14.5 | 0
2094 | TORONTO BUTTONVILLE A | 3 | 29 | 6 | 1.25 | 16.75 | 0
2095 | TORONTO BUTTONVILLE A | 3 | 28 | 7 | 4 | 14 | 0
2095 | TORONTO BUTTONVILLE A | 3 | 29 | 7 | 1.225 | 16.775 | 0
2096 | TORONTO BUTTONVILLE A | 3 | 28 | 8 | 4 | 14 | 0
2096 | TORONTO BUTTONVILLE A | 3 | 29 | 8 | 1.55 | 16.45 | 0
2097 | TORONTO BUTTONVILLE A | 3 | 28 | 9 | 5.2 | 12.8 | 0
2097 | TORONTO BUTTONVILLE A | 3 | 29 | 9 | 2.15 | 15.85 | 0
2098 | TORONTO BUTTONVILLE A | 3 | 28 | 10 | 5.9 | 12.1 | 0
2098 | TORONTO BUTTONVILLE A | 3 | 29 | 10 | 3.15 | 14.85 | 0
2099 | TORONTO BUTTONVILLE A | 3 | 28 | 11 | 5.7 | 12.3 | 0
2099 | TORONTO BUTTONVILLE A | 3 | 29 | 11 | 4.325 | 13.675 | 0
2100 | TORONTO BUTTONVILLE A | 3 | 28 | 12 | 5.5 | 12.5 | 0
2100 | TORONTO BUTTONVILLE A | 3 | 29 | 12 | 5.225 | 12.775 | 0
2101 | TORONTO BUTTONVILLE A | 3 | 28 | 13 | 5.7 | 12.3 | 0
2101 | TORONTO BUTTONVILLE A | 3 | 29 | 13 | 6.25 | 11.75 | 0
2102 | TORONTO BUTTONVILLE A | 3 | 28 | 14 | 6 | 12 | 0
2102 | TORONTO BUTTONVILLE A | 3 | 29 | 14 | 7.275 | 10.725 | 0
2103 | TORONTO BUTTONVILLE A | 3 | 28 | 15 | 7.7 | 10.3 | 0
2103 | TORONTO BUTTONVILLE A | 3 | 29 | 15 | 7.65 | 10.35 | 0
2104 | TORONTO BUTTONVILLE A | 3 | 28 | 16 | 9.4 | 8.6 | 0
2104 | TORONTO BUTTONVILLE A | 3 | 29 | 16 | 7.875 | 10.125 | 0
2105 | TORONTO BUTTONVILLE A | 3 | 28 | 17 | 9.6 | 8.4 | 0
2105 | TORONTO BUTTONVILLE A | 3 | 29 | 17 | 7.55 | 10.45 | 0
2106 | TORONTO BUTTONVILLE A | 3 | 28 | 18 | 7.9 | 10.1 | 0
2106 | TORONTO BUTTONVILLE A | 3 | 29 | 18 | 7.1 | 10.9 | 0
2107 | TORONTO BUTTONVILLE A | 3 | 28 | 19 | 7.5 | 10.5 | 0
2107 | TORONTO BUTTONVILLE A | 3 | 29 | 19 | 6.15 | 11.85 | 0
2108 | TORONTO BUTTONVILLE A | 3 | 28 | 20 | 7.5 | 10.5 | 0
2108 | TORONTO BUTTONVILLE A | 3 | 29 | 20 | 4.8 | 13.2 | 0
2109 | TORONTO BUTTONVILLE A | 3 | 28 | 21 | 6.3 | 11.7 | 0
2109 | TORONTO BUTTONVILLE A | 3 | 29 | 21 | 4.2 | 13.8 | 0
2110 | TORONTO BUTTONVILLE A | 3 | 28 | 22 | 5.9 | 12.1 | 0
2110 | TORONTO BUTTONVILLE A | 3 | 29 | 22 | 3.6 | 14.4 | 0
2111 | TORONTO BUTTONVILLE A | 3 | 28 | 23 | 5.7 | 12.3 | 0
2111 | TORONTO BUTTONVILLE A | 3 | 29 | 23 | 3.3 | 14.7 | 0
2112 | TORONTO BUTTONVILLE A | 3 | 28 | 24 | 6 | 12 | 0
2112 | TORONTO BUTTONVILLE A | 3 | 29 | 24 | 2.825 | 15.175 | 0
2113 | TORONTO BUTTONVILLE A | 3 | 29 | 1 | 6.1 | 11.9 | 0
2113 | TORONTO BUTTONVILLE A | 3 | 30 | 1 | 2.325 | 15.675 | 0
2114 | TORONTO BUTTONVILLE A | 3 | 29 | 2 | 6 | 12 | 0
2114 | TORONTO BUTTONVILLE A | 3 | 30 | 2 | 2.05 | 15.95 | 0
2115 | TORONTO BUTTONVILLE A | 3 | 29 | 3 | 5.8 | 12.2 | 0
2115 | TORONTO BUTTONVILLE A | 3 | 30 | 3 | 1.675 | 16.325 | 0
2116 | TORONTO BUTTONVILLE A | 3 | 29 | 4 | 5.6 | 12.4 | 0
2116 | TORONTO BUTTONVILLE A | 3 | 30 | 4 | 1.55 | 16.45 | 0
2117 | TORONTO BUTTONVILLE A | 3 | 29 | 5 | 5.4 | 12.6 | 0
2117 | TORONTO BUTTONVILLE A | 3 | 30 | 5 | 1.825 | 16.175 | 0
2118 | TORONTO BUTTONVILLE A | 3 | 29 | 6 | 5.4 | 12.6 | 0
2118 | TORONTO BUTTONVILLE A | 3 | 30 | 6 | 1.075 | 16.925 | 0
2119 | TORONTO BUTTONVILLE A | 3 | 29 | 7 | 5.3 | 12.7 | 0
2119 | TORONTO BUTTONVILLE A | 3 | 30 | 7 | 0.875 | 17.125 | 0
2120 | TORONTO BUTTONVILLE A | 3 | 29 | 8 | 5.6 | 12.4 | 0
2120 | TORONTO BUTTONVILLE A | 3 | 30 | 8 | 1.2 | 16.8 | 0
2121 | TORONTO BUTTONVILLE A | 3 | 29 | 9 | 5.8 | 12.2 | 0
2121 | TORONTO BUTTONVILLE A | 3 | 30 | 9 | 2.625 | 15.375 | 0
2122 | TORONTO BUTTONVILLE A | 3 | 29 | 10 | 6.1 | 11.9 | 0
2122 | TORONTO BUTTONVILLE A | 3 | 30 | 10 | 4.2 | 13.8 | 0
2123 | TORONTO BUTTONVILLE A | 3 | 29 | 11 | 6.6 | 11.4 | 0
2123 | TORONTO BUTTONVILLE A | 3 | 30 | 11 | 4.85 | 13.15 | 0
2124 | TORONTO BUTTONVILLE A | 3 | 29 | 12 | 7.2 | 10.8 | 0
2124 | TORONTO BUTTONVILLE A | 3 | 30 | 12 | 5.25 | 12.75 | 0
2125 | TORONTO BUTTONVILLE A | 3 | 29 | 13 | 7.9 | 10.1 | 0
2125 | TORONTO BUTTONVILLE A | 3 | 30 | 13 | 5.9 | 12.1 | 0
2126 | TORONTO BUTTONVILLE A | 3 | 29 | 14 | 9.2 | 8.8 | 0
2126 | TORONTO BUTTONVILLE A | 3 | 30 | 14 | 6.55 | 11.45 | 0
2127 | TORONTO BUTTONVILLE A | 3 | 29 | 15 | 11.7 | 6.3 | 0
2127 | TORONTO BUTTONVILLE A | 3 | 30 | 15 | 6.6 | 11.4 | 0
2128 | TORONTO BUTTONVILLE A | 3 | 29 | 16 | 14.8 | 3.2 | 0
2128 | TORONTO BUTTONVILLE A | 3 | 30 | 16 | 6.475 | 11.525 | 0
2129 | TORONTO BUTTONVILLE A | 3 | 29 | 17 | 16.9 | 1.1 | 0
2129 | TORONTO BUTTONVILLE A | 3 | 30 | 17 | 6.1 | 11.9 | 0
2130 | TORONTO BUTTONVILLE A | 3 | 29 | 18 | 15.8 | 2.2 | 0
2130 | TORONTO BUTTONVILLE A | 3 | 30 | 18 | 5.925 | 12.075 | 0
2131 | TORONTO BUTTONVILLE A | 3 | 29 | 19 | 13.1 | 4.9 | 0
2131 | TORONTO BUTTONVILLE A | 3 | 30 | 19 | 5.5 | 12.5 | 0
2132 | TORONTO BUTTONVILLE A | 3 | 29 | 20 | 11.9 | 6.1 | 0
2132 | TORONTO BUTTONVILLE A | 3 | 30 | 20 | 4.675 | 13.325 | 0
2133 | TORONTO BUTTONVILLE A | 3 | 29 | 21 | 11 | 7 | 0
2133 | TORONTO BUTTONVILLE A | 3 | 30 | 21 | 4.325 | 13.675 | 0
2134 | TORONTO BUTTONVILLE A | 3 | 29 | 22 | 10.4 | 7.6 | 0
2134 | TORONTO BUTTONVILLE A | 3 | 30 | 22 | 4 | 14 | 0
2135 | TORONTO BUTTONVILLE A | 3 | 29 | 23 | 9.7 | 8.3 | 0
2135 | TORONTO BUTTONVILLE A | 3 | 30 | 23 | 3.8 | 14.2 | 0
2136 | TORONTO BUTTONVILLE A | 3 | 29 | 24 | 9.2 | 8.8 | 0
2136 | TORONTO BUTTONVILLE A | 3 | 30 | 24 | 3.825 | 14.175 | 0
2137 | TORONTO BUTTONVILLE A | 3 | 30 | 1 | 8.9 | 9.1 | 0
2137 | TORONTO BUTTONVILLE A | 3 | 31 | 1 | 3.85 | 14.15 | 0
2138 | TORONTO BUTTONVILLE A | 3 | 30 | 2 | 8.5 | 9.5 | 0
2138 | TORONTO BUTTONVILLE A | 3 | 31 | 2 | 4.4667 | 13.5333 | 0
2139 | TORONTO BUTTONVILLE A | 3 | 30 | 3 | 8.2 | 9.8 | 0
2139 | TORONTO BUTTONVILLE A | 3 | 31 | 3 | 3.9667 | 14.0333 | 0
2140 | TORONTO BUTTONVILLE A | 3 | 30 | 4 | 7.8 | 10.2 | 0
2140 | TORONTO BUTTONVILLE A | 3 | 31 | 4 | 2.95 | 15.05 | 0
2141 | TORONTO BUTTONVILLE A | 3 | 30 | 5 | 7.6 | 10.4 | 0
2141 | TORONTO BUTTONVILLE A | 3 | 31 | 5 | 3.525 | 14.475 | 0
2142 | TORONTO BUTTONVILLE A | 3 | 30 | 6 | 7.4 | 10.6 | 0
2142 | TORONTO BUTTONVILLE A | 3 | 31 | 6 | 3.6 | 14.4 | 0
2143 | TORONTO BUTTONVILLE A | 3 | 30 | 7 | 6.9 | 11.1 | 0
2143 | TORONTO BUTTONVILLE A | 3 | 31 | 7 | 3.45 | 14.55 | 0
2144 | TORONTO BUTTONVILLE A | 3 | 30 | 8 | 5.8 | 12.2 | 0
2144 | TORONTO BUTTONVILLE A | 3 | 31 | 8 | 1.875 | 16.125 | 0
2145 | TORONTO BUTTONVILLE A | 3 | 30 | 9 | 5.6 | 12.4 | 0
2145 | TORONTO BUTTONVILLE A | 3 | 31 | 9 | 2.3 | 15.7 | 0
2146 | TORONTO BUTTONVILLE A | 3 | 30 | 10 | 6.3 | 11.7 | 0
2146 | TORONTO BUTTONVILLE A | 3 | 31 | 10 | 3 | 15 | 0
2147 | TORONTO BUTTONVILLE A | 3 | 30 | 11 | 6.8 | 11.2 | 0
2147 | TORONTO BUTTONVILLE A | 3 | 31 | 11 | 3.575 | 14.425 | 0
2148 | TORONTO BUTTONVILLE A | 3 | 30 | 12 | 6.6 | 11.4 | 0
2148 | TORONTO BUTTONVILLE A | 3 | 31 | 12 | 3.85 | 14.15 | 0
2149 | TORONTO BUTTONVILLE A | 3 | 30 | 13 | 7.3 | 10.7 | 0
2149 | TORONTO BUTTONVILLE A | 3 | 31 | 13 | 4.35 | 13.65 | 0
2150 | TORONTO BUTTONVILLE A | 3 | 30 | 14 | 7.4 | 10.6 | 0
2150 | TORONTO BUTTONVILLE A | 3 | 31 | 14 | 4.7 | 13.3 | 0
2151 | TORONTO BUTTONVILLE A | 3 | 30 | 15 | 7 | 11 | 0
2151 | TORONTO BUTTONVILLE A | 3 | 31 | 15 | 4.775 | 13.225 | 0
2152 | TORONTO BUTTONVILLE A | 3 | 30 | 16 | 6.7 | 11.3 | 0
2152 | TORONTO BUTTONVILLE A | 3 | 31 | 16 | 4.825 | 13.175 | 0
2153 | TORONTO BUTTONVILLE A | 3 | 30 | 17 | 5.2 | 12.8 | 0
2153 | TORONTO BUTTONVILLE A | 3 | 31 | 17 | 4.65 | 13.35 | 0
2154 | TORONTO BUTTONVILLE A | 3 | 30 | 18 | 5.2 | 12.8 | 0
2154 | TORONTO BUTTONVILLE A | 3 | 31 | 18 | 3.425 | 14.575 | 0
2155 | TORONTO BUTTONVILLE A | 3 | 30 | 19 | 5 | 13 | 0
2155 | TORONTO BUTTONVILLE A | 3 | 31 | 19 | 2.675 | 15.325 | 0
2156 | TORONTO BUTTONVILLE A | 3 | 30 | 20 | 4.7 | 13.3 | 0
2156 | TORONTO BUTTONVILLE A | 3 | 31 | 20 | 1.95 | 16.05 | 0
2157 | TORONTO BUTTONVILLE A | 3 | 30 | 21 | 4.7 | 13.3 | 0
2157 | TORONTO BUTTONVILLE A | 3 | 31 | 21 | 1.75 | 16.25 | 0
2158 | TORONTO BUTTONVILLE A | 3 | 30 | 22 | 4.4 | 13.6 | 0
2158 | TORONTO BUTTONVILLE A | 3 | 31 | 22 | 1.65 | 16.35 | 0
2159 | TORONTO BUTTONVILLE A | 3 | 30 | 23 | 4.4 | 13.6 | 0
2159 | TORONTO BUTTONVILLE A | 3 | 31 | 23 | 1.35 | 16.65 | 0
2160 | TORONTO BUTTONVILLE A | 3 | 30 | 24 | 4.4 | 13.6 | 0
2160 | TORONTO BUTTONVILLE A | 3 | 31 | 24 | 0.6 | 17.4 | 0
2161 | TORONTO BUTTONVILLE A | 3 | 31 | 1 | 4.5 | 13.5 | 0
2161 | TORONTO BUTTONVILLE A | 4 | 1 | 1 | -0.3 | 18.3 | 0
2162 | TORONTO BUTTONVILLE A | 3 | 31 | 2 | 4.5 | 13.5 | 0
2162 | TORONTO BUTTONVILLE A | 4 | 1 | 2 | -0.95 | 18.95 | 0
2163 | TORONTO BUTTONVILLE A | 3 | 31 | 3 | 4.5 | 13.5 | 0
2163 | TORONTO BUTTONVILLE A | 4 | 1 | 3 | -1.55 | 19.55 | 0
2164 | TORONTO BUTTONVILLE A | 3 | 31 | 4 | 4.6 | 13.4 | 0
2164 | TORONTO BUTTONVILLE A | 4 | 1 | 4 | -1.85 | 19.85 | 0
2165 | TORONTO BUTTONVILLE A | 3 | 31 | 5 | 4.6 | 13.4 | 0
2165 | TORONTO BUTTONVILLE A | 4 | 1 | 5 | -2.075 | 20.075 | 0
2166 | TORONTO BUTTONVILLE A | 3 | 31 | 6 | 4.5 | 13.5 | 0
2166 | TORONTO BUTTONVILLE A | 4 | 1 | 6 | -2.4 | 20.4 | 0
2167 | TORONTO BUTTONVILLE A | 3 | 31 | 7 | 4.7 | 13.3 | 0
2167 | TORONTO BUTTONVILLE A | 4 | 1 | 7 | -2.625 | 20.625 | 0
2168 | TORONTO BUTTONVILLE A | 3 | 31 | 8 | 4.8 | 13.2 | 0
2168 | TORONTO BUTTONVILLE A | 4 | 1 | 8 | -2.2 | 20.2 | 0
2169 | TORONTO BUTTONVILLE A | 3 | 31 | 9 | 5.2 | 12.8 | 0
2169 | TORONTO BUTTONVILLE A | 4 | 1 | 9 | -1.225 | 19.225 | 0
2170 | TORONTO BUTTONVILLE A | 3 | 31 | 10 | 5.7 | 12.3 | 0
2170 | TORONTO BUTTONVILLE A | 4 | 1 | 10 | -0.225 | 18.225 | 0
2171 | TORONTO BUTTONVILLE A | 3 | 31 | 11 | 5.2 | 12.8 | 0
2171 | TORONTO BUTTONVILLE A | 4 | 1 | 11 | 0.775 | 17.225 | 0
2172 | TORONTO BUTTONVILLE A | 3 | 31 | 12 | 5 | 13 | 0
2172 | TORONTO BUTTONVILLE A | 4 | 1 | 12 | 1.65 | 16.35 | 0
2173 | TORONTO BUTTONVILLE A | 3 | 31 | 13 | 4.9 | 13.1 | 0
2173 | TORONTO BUTTONVILLE A | 4 | 1 | 13 | 2.05 | 15.95 | 0
2174 | TORONTO BUTTONVILLE A | 3 | 31 | 14 | 4.8 | 13.2 | 0
2174 | TORONTO BUTTONVILLE A | 4 | 1 | 14 | 2.65 | 15.35 | 0
2175 | TORONTO BUTTONVILLE A | 3 | 31 | 15 | 4.7 | 13.3 | 0
2175 | TORONTO BUTTONVILLE A | 4 | 1 | 15 | 3.125 | 14.875 | 0
2176 | TORONTO BUTTONVILLE A | 3 | 31 | 16 | 5 | 13 | 0
2176 | TORONTO BUTTONVILLE A | 4 | 1 | 16 | 2.675 | 15.325 | 0
2177 | TORONTO BUTTONVILLE A | 3 | 31 | 17 | 5.3 | 12.7 | 0
2177 | TORONTO BUTTONVILLE A | 4 | 1 | 17 | 2.8 | 15.2 | 0
2178 | TORONTO BUTTONVILLE A | 3 | 31 | 18 | 5.3 | 12.7 | 0
2178 | TORONTO BUTTONVILLE A | 4 | 1 | 18 | 2.725 | 15.275 | 0
2179 | TORONTO BUTTONVILLE A | 3 | 31 | 19 | 5.4 | 12.6 | 0
2179 | TORONTO BUTTONVILLE A | 4 | 1 | 19 | 2.25 | 15.75 | 0
2180 | TORONTO BUTTONVILLE A | 3 | 31 | 20 | 5.3 | 12.7 | 0
2180 | TORONTO BUTTONVILLE A | 4 | 1 | 20 | 1.35 | 16.65 | 0
2181 | TORONTO BUTTONVILLE A | 3 | 31 | 21 | 4.9 | 13.1 | 0
2181 | TORONTO BUTTONVILLE A | 4 | 1 | 21 | 0.85 | 17.15 | 0
2182 | TORONTO BUTTONVILLE A | 3 | 31 | 22 | 4.6 | 13.4 | 0
2182 | TORONTO BUTTONVILLE A | 4 | 1 | 22 | 0.525 | 17.475 | 0
2183 | TORONTO BUTTONVILLE A | 3 | 31 | 23 | 4.5 | 13.5 | 0
2183 | TORONTO BUTTONVILLE A | 4 | 1 | 23 | 0.275 | 17.725 | 0
2184 | TORONTO BUTTONVILLE A | 3 | 31 | 24 | 4.1 | 13.9 | 0
2184 | TORONTO BUTTONVILLE A | 4 | 1 | 24 | 0.075 | 17.925 | 0
2185 | TORONTO BUTTONVILLE A | 4 | 1 | 1 | 3.9 | 14.1 | 0
2185 | TORONTO BUTTONVILLE A | 4 | 2 | 1 | -0.5 | 18.5 | 0
2186 | TORONTO BUTTONVILLE A | 4 | 1 | 2 | 3.5 | 14.5 | 0
2186 | TORONTO BUTTONVILLE A | 4 | 2 | 2 | -0.775 | 18.775 | 0
2187 | TORONTO BUTTONVILLE A | 4 | 1 | 3 | 3.4 | 14.6 | 0
2187 | TORONTO BUTTONVILLE A | 4 | 2 | 3 | -0.975 | 18.975 | 0
2188 | TORONTO BUTTONVILLE A | 4 | 1 | 4 | 2.6 | 15.4 | 0
2188 | TORONTO BUTTONVILLE A | 4 | 2 | 4 | -1.275 | 19.275 | 0
2189 | TORONTO BUTTONVILLE A | 4 | 1 | 5 | 1 | 17 | 0
2189 | TORONTO BUTTONVILLE A | 4 | 2 | 5 | -1.125 | 19.125 | 0
2190 | TORONTO BUTTONVILLE A | 4 | 1 | 6 | 0.6 | 17.4 | 0
2190 | TORONTO BUTTONVILLE A | 4 | 2 | 6 | -1.025 | 19.025 | 0
2191 | TORONTO BUTTONVILLE A | 4 | 1 | 7 | 0.3 | 17.7 | 0
2191 | TORONTO BUTTONVILLE A | 4 | 2 | 7 | -1.225 | 19.225 | 0
2192 | TORONTO BUTTONVILLE A | 4 | 1 | 8 | 1.3 | 16.7 | 0
2192 | TORONTO BUTTONVILLE A | 4 | 2 | 8 | -0.55 | 18.55 | 0
2193 | TORONTO BUTTONVILLE A | 4 | 1 | 9 | 3.3 | 14.7 | 0
2193 | TORONTO BUTTONVILLE A | 4 | 2 | 9 | 1.375 | 16.625 | 0
2194 | TORONTO BUTTONVILLE A | 4 | 1 | 10 | 5.4 | 12.6 | 0
2194 | TORONTO BUTTONVILLE A | 4 | 2 | 10 | 3.075 | 14.925 | 0
2195 | TORONTO BUTTONVILLE A | 4 | 1 | 11 | 6.9 | 11.1 | 0
2195 | TORONTO BUTTONVILLE A | 4 | 2 | 11 | 4 | 14 | 0
2196 | TORONTO BUTTONVILLE A | 4 | 1 | 12 | 8.2 | 9.8 | 0
2196 | TORONTO BUTTONVILLE A | 4 | 2 | 12 | 5.4 | 12.6 | 0
2197 | TORONTO BUTTONVILLE A | 4 | 1 | 13 | 8.6 | 9.4 | 0
2197 | TORONTO BUTTONVILLE A | 4 | 2 | 13 | 6.425 | 11.575 | 0
2198 | TORONTO BUTTONVILLE A | 4 | 1 | 14 | 9 | 9 | 0
2198 | TORONTO BUTTONVILLE A | 4 | 2 | 14 | 7 | 11 | 0
2199 | TORONTO BUTTONVILLE A | 4 | 1 | 15 | 9.8 | 8.2 | 0
2199 | TORONTO BUTTONVILLE A | 4 | 2 | 15 | 7.4 | 10.6 | 0
2200 | TORONTO BUTTONVILLE A | 4 | 1 | 16 | 9.1 | 8.9 | 0
2200 | TORONTO BUTTONVILLE A | 4 | 2 | 16 | 7.775 | 10.225 | 0
2201 | TORONTO BUTTONVILLE A | 4 | 1 | 17 | 10.2 | 7.8 | 0
2201 | TORONTO BUTTONVILLE A | 4 | 2 | 17 | 7.75 | 10.25 | 0
2202 | TORONTO BUTTONVILLE A | 4 | 1 | 18 | 10 | 8 | 0
2202 | TORONTO BUTTONVILLE A | 4 | 2 | 18 | 7.1 | 10.9 | 0
2203 | TORONTO BUTTONVILLE A | 4 | 1 | 19 | 9.4 | 8.6 | 0
2203 | TORONTO BUTTONVILLE A | 4 | 2 | 19 | 6.175 | 11.825 | 0
2204 | TORONTO BUTTONVILLE A | 4 | 1 | 20 | 8 | 10 | 0
2204 | TORONTO BUTTONVILLE A | 4 | 2 | 20 | 5.1 | 12.9 | 0
2205 | TORONTO BUTTONVILLE A | 4 | 1 | 21 | 7.2 | 10.8 | 0
2205 | TORONTO BUTTONVILLE A | 4 | 2 | 21 | 4.375 | 13.625 | 0
2206 | TORONTO BUTTONVILLE A | 4 | 1 | 22 | 6.4 | 11.6 | 0
2206 | TORONTO BUTTONVILLE A | 4 | 2 | 22 | 4.2 | 13.8 | 0
2207 | TORONTO BUTTONVILLE A | 4 | 1 | 23 | 5 | 13 | 0
2207 | TORONTO BUTTONVILLE A | 4 | 2 | 23 | 3.4 | 14.6 | 0
2208 | TORONTO BUTTONVILLE A | 4 | 1 | 24 | 4.5 | 13.5 | 0
2208 | TORONTO BUTTONVILLE A | 4 | 2 | 24 | 2.775 | 15.225 | 0
2209 | TORONTO BUTTONVILLE A | 4 | 2 | 1 | 4.4 | 13.6 | 0
2209 | TORONTO BUTTONVILLE A | 4 | 3 | 1 | 2.05 | 15.95 | 0
2210 | TORONTO BUTTONVILLE A | 4 | 2 | 2 | 4.4 | 13.6 | 0
2210 | TORONTO BUTTONVILLE A | 4 | 3 | 2 | 1.75 | 16.25 | 0
2211 | TORONTO BUTTONVILLE A | 4 | 2 | 3 | 3.7 | 14.3 | 0
2211 | TORONTO BUTTONVILLE A | 4 | 3 | 3 | 1.6 | 16.4 | 0
2212 | TORONTO BUTTONVILLE A | 4 | 2 | 4 | 3.1 | 14.9 | 0
2212 | TORONTO BUTTONVILLE A | 4 | 3 | 4 | 1.55 | 16.45 | 0
2213 | TORONTO BUTTONVILLE A | 4 | 2 | 5 | 2.8 | 15.2 | 0
2213 | TORONTO BUTTONVILLE A | 4 | 3 | 5 | 1.1 | 16.9 | 0
2214 | TORONTO BUTTONVILLE A | 4 | 2 | 6 | 1.7 | 16.3 | 0
2214 | TORONTO BUTTONVILLE A | 4 | 3 | 6 | 1.025 | 16.975 | 0
2215 | TORONTO BUTTONVILLE A | 4 | 2 | 7 | 2 | 16 | 0
2215 | TORONTO BUTTONVILLE A | 4 | 3 | 7 | 1.275 | 16.725 | 0
2216 | TORONTO BUTTONVILLE A | 4 | 2 | 8 | 2.9 | 15.1 | 0
2216 | TORONTO BUTTONVILLE A | 4 | 3 | 8 | 1.925 | 16.075 | 0
2217 | TORONTO BUTTONVILLE A | 4 | 2 | 9 | 4.8 | 13.2 | 0
2217 | TORONTO BUTTONVILLE A | 4 | 3 | 9 | 3.75 | 14.25 | 0
2218 | TORONTO BUTTONVILLE A | 4 | 2 | 10 | 7.3 | 10.7 | 0
2218 | TORONTO BUTTONVILLE A | 4 | 3 | 10 | 4.525 | 13.475 | 0
2219 | TORONTO BUTTONVILLE A | 4 | 2 | 11 | 9.1 | 8.9 | 0
2219 | TORONTO BUTTONVILLE A | 4 | 3 | 11 | 4.7 | 13.3 | 0
2220 | TORONTO BUTTONVILLE A | 4 | 2 | 12 | 10.4 | 7.6 | 0
2220 | TORONTO BUTTONVILLE A | 4 | 3 | 12 | 6.275 | 11.725 | 0
2221 | TORONTO BUTTONVILLE A | 4 | 2 | 13 | 11.1 | 6.9 | 0
2221 | TORONTO BUTTONVILLE A | 4 | 3 | 13 | 6.375 | 11.625 | 0
2222 | TORONTO BUTTONVILLE A | 4 | 2 | 14 | 11.8 | 6.2 | 0
2222 | TORONTO BUTTONVILLE A | 4 | 3 | 14 | 6.2 | 11.8 | 0
2223 | TORONTO BUTTONVILLE A | 4 | 2 | 15 | 11.8 | 6.2 | 0
2223 | TORONTO BUTTONVILLE A | 4 | 3 | 15 | 6.6 | 11.4 | 0
2224 | TORONTO BUTTONVILLE A | 4 | 2 | 16 | 11.3 | 6.7 | 0
2224 | TORONTO BUTTONVILLE A | 4 | 3 | 16 | 6.3 | 11.7 | 0
2225 | TORONTO BUTTONVILLE A | 4 | 2 | 17 | 10.6 | 7.4 | 0
2225 | TORONTO BUTTONVILLE A | 4 | 3 | 17 | 6.025 | 11.975 | 0
2226 | TORONTO BUTTONVILLE A | 4 | 2 | 18 | 9.9 | 8.1 | 0
2226 | TORONTO BUTTONVILLE A | 4 | 3 | 18 | 4.925 | 13.075 | 0
2227 | TORONTO BUTTONVILLE A | 4 | 2 | 19 | 8.4 | 9.6 | 0
2227 | TORONTO BUTTONVILLE A | 4 | 3 | 19 | 5.25 | 12.75 | 0
2228 | TORONTO BUTTONVILLE A | 4 | 2 | 20 | 7.2 | 10.8 | 0
2228 | TORONTO BUTTONVILLE A | 4 | 3 | 20 | 5 | 13 | 0
2229 | TORONTO BUTTONVILLE A | 4 | 2 | 21 | 6.7 | 11.3 | 0
2229 | TORONTO BUTTONVILLE A | 4 | 3 | 21 | 4.6 | 13.4 | 0
2230 | TORONTO BUTTONVILLE A | 4 | 2 | 22 | 6.2 | 11.8 | 0
2230 | TORONTO BUTTONVILLE A | 4 | 3 | 22 | 4.725 | 13.275 | 0
2231 | TORONTO BUTTONVILLE A | 4 | 2 | 23 | 5.4 | 12.6 | 0
2231 | TORONTO BUTTONVILLE A | 4 | 3 | 23 | 3.525 | 14.475 | 0
2232 | TORONTO BUTTONVILLE A | 4 | 2 | 24 | 5.2 | 12.8 | 0
2232 | TORONTO BUTTONVILLE A | 4 | 3 | 24 | 2.85 | 15.15 | 0
2233 | TORONTO BUTTONVILLE A | 4 | 3 | 1 | 4.5 | 13.5 | 0
2233 | TORONTO BUTTONVILLE A | 4 | 4 | 1 | 2.425 | 15.575 | 0
2234 | TORONTO BUTTONVILLE A | 4 | 3 | 2 | 4.2 | 13.8 | 0
2234 | TORONTO BUTTONVILLE A | 4 | 4 | 2 | 2.35 | 15.65 | 0
2235 | TORONTO BUTTONVILLE A | 4 | 3 | 3 | 3.4 | 14.6 | 0
2235 | TORONTO BUTTONVILLE A | 4 | 4 | 3 | 2.3 | 15.7 | 0
2236 | TORONTO BUTTONVILLE A | 4 | 3 | 4 | 2.8 | 15.2 | 0
2236 | TORONTO BUTTONVILLE A | 4 | 4 | 4 | 2.325 | 15.675 | 0
2237 | TORONTO BUTTONVILLE A | 4 | 3 | 5 | 2 | 16 | 0
2237 | TORONTO BUTTONVILLE A | 4 | 4 | 5 | 2.075 | 15.925 | 0
2238 | TORONTO BUTTONVILLE A | 4 | 3 | 6 | 1.8 | 16.2 | 0
2238 | TORONTO BUTTONVILLE A | 4 | 4 | 6 | 2.05 | 15.95 | 0
2239 | TORONTO BUTTONVILLE A | 4 | 3 | 7 | 1.5 | 16.5 | 0
2239 | TORONTO BUTTONVILLE A | 4 | 4 | 7 | 1.925 | 16.075 | 0
2240 | TORONTO BUTTONVILLE A | 4 | 3 | 8 | 2.2 | 15.8 | 0
2240 | TORONTO BUTTONVILLE A | 4 | 4 | 8 | 2.45 | 15.55 | 0
2241 | TORONTO BUTTONVILLE A | 4 | 3 | 9 | 3.5 | 14.5 | 0
2241 | TORONTO BUTTONVILLE A | 4 | 4 | 9 | 3.225 | 14.775 | 0
2242 | TORONTO BUTTONVILLE A | 4 | 3 | 10 | 5.1 | 12.9 | 0
2242 | TORONTO BUTTONVILLE A | 4 | 4 | 10 | 4.325 | 13.675 | 0
2243 | TORONTO BUTTONVILLE A | 4 | 3 | 11 | 6.1 | 11.9 | 0
2243 | TORONTO BUTTONVILLE A | 4 | 4 | 11 | 5.325 | 12.675 | 0
2244 | TORONTO BUTTONVILLE A | 4 | 3 | 12 | 7.8 | 10.2 | 0
2244 | TORONTO BUTTONVILLE A | 4 | 4 | 12 | 6 | 12 | 0
2245 | TORONTO BUTTONVILLE A | 4 | 3 | 13 | 8.7 | 9.3 | 0
2245 | TORONTO BUTTONVILLE A | 4 | 4 | 13 | 6.175 | 11.825 | 0
2246 | TORONTO BUTTONVILLE A | 4 | 3 | 14 | 9.3 | 8.7 | 0
2246 | TORONTO BUTTONVILLE A | 4 | 4 | 14 | 6.975 | 11.025 | 0
2247 | TORONTO BUTTONVILLE A | 4 | 3 | 15 | 9.9 | 8.1 | 0
2247 | TORONTO BUTTONVILLE A | 4 | 4 | 15 | 6.975 | 11.025 | 0
2248 | TORONTO BUTTONVILLE A | 4 | 3 | 16 | 10 | 8 | 0
2248 | TORONTO BUTTONVILLE A | 4 | 4 | 16 | 6.775 | 11.225 | 0
2249 | TORONTO BUTTONVILLE A | 4 | 3 | 17 | 9.6 | 8.4 | 0
2249 | TORONTO BUTTONVILLE A | 4 | 4 | 17 | 5.95 | 12.05 | 0
2250 | TORONTO BUTTONVILLE A | 4 | 3 | 18 | 7.5 | 10.5 | 0
2250 | TORONTO BUTTONVILLE A | 4 | 4 | 18 | 5.575 | 12.425 | 0
2251 | TORONTO BUTTONVILLE A | 4 | 3 | 19 | 6.3 | 11.7 | 0
2251 | TORONTO BUTTONVILLE A | 4 | 4 | 19 | 4.8 | 13.2 | 0
2252 | TORONTO BUTTONVILLE A | 4 | 3 | 20 | 5.6 | 12.4 | 0
2252 | TORONTO BUTTONVILLE A | 4 | 4 | 20 | 3.65 | 14.35 | 0
2253 | TORONTO BUTTONVILLE A | 4 | 3 | 21 | 5.5 | 12.5 | 0
2253 | TORONTO BUTTONVILLE A | 4 | 4 | 21 | 2.85 | 15.15 | 0
2254 | TORONTO BUTTONVILLE A | 4 | 3 | 22 | 5.5 | 12.5 | 0
2254 | TORONTO BUTTONVILLE A | 4 | 4 | 22 | 2.325 | 15.675 | 0
2255 | TORONTO BUTTONVILLE A | 4 | 3 | 23 | 5.5 | 12.5 | 0
2255 | TORONTO BUTTONVILLE A | 4 | 4 | 23 | 1.85 | 16.15 | 0
2256 | TORONTO BUTTONVILLE A | 4 | 3 | 24 | 5.5 | 12.5 | 0
2256 | TORONTO BUTTONVILLE A | 4 | 4 | 24 | 1.125 | 16.875 | 0
2257 | TORONTO BUTTONVILLE A | 4 | 4 | 1 | 5.6 | 12.4 | 0
2257 | TORONTO BUTTONVILLE A | 4 | 5 | 1 | 0.675 | 17.325 | 0
2258 | TORONTO BUTTONVILLE A | 4 | 4 | 2 | 5.4 | 12.6 | 0
2258 | TORONTO BUTTONVILLE A | 4 | 5 | 2 | 0.3 | 17.7 | 0
2259 | TORONTO BUTTONVILLE A | 4 | 4 | 3 | 5.7 | 12.3 | 0
2259 | TORONTO BUTTONVILLE A | 4 | 5 | 3 | 0.475 | 17.525 | 0
2260 | TORONTO BUTTONVILLE A | 4 | 4 | 4 | 5.7 | 12.3 | 0
2260 | TORONTO BUTTONVILLE A | 4 | 5 | 4 | 0.55 | 17.45 | 0
2261 | TORONTO BUTTONVILLE A | 4 | 4 | 5 | 5.7 | 12.3 | 0
2261 | TORONTO BUTTONVILLE A | 4 | 5 | 5 | 0.475 | 17.525 | 0
2262 | TORONTO BUTTONVILLE A | 4 | 4 | 6 | 5.8 | 12.2 | 0
2262 | TORONTO BUTTONVILLE A | 4 | 5 | 6 | 0.35 | 17.65 | 0
2263 | TORONTO BUTTONVILLE A | 4 | 4 | 7 | 6 | 12 | 0
2263 | TORONTO BUTTONVILLE A | 4 | 5 | 7 | -0.075 | 18.075 | 0
2264 | TORONTO BUTTONVILLE A | 4 | 4 | 8 | 6.2 | 11.8 | 0
2264 | TORONTO BUTTONVILLE A | 4 | 5 | 8 | 0.55 | 17.45 | 0
2265 | TORONTO BUTTONVILLE A | 4 | 4 | 9 | 6.5 | 11.5 | 0
2265 | TORONTO BUTTONVILLE A | 4 | 5 | 9 | 2.025 | 15.975 | 0
2266 | TORONTO BUTTONVILLE A | 4 | 4 | 10 | 7.2 | 10.8 | 0
2266 | TORONTO BUTTONVILLE A | 4 | 5 | 10 | 3.225 | 14.775 | 0
2267 | TORONTO BUTTONVILLE A | 4 | 4 | 11 | 8.3 | 9.7 | 0
2267 | TORONTO BUTTONVILLE A | 4 | 5 | 11 | 4.175 | 13.825 | 0
2268 | TORONTO BUTTONVILLE A | 4 | 4 | 12 | 9 | 9 | 0
2268 | TORONTO BUTTONVILLE A | 4 | 5 | 12 | 5.025 | 12.975 | 0
2269 | TORONTO BUTTONVILLE A | 4 | 4 | 13 | 10.1 | 7.9 | 0
2269 | TORONTO BUTTONVILLE A | 4 | 5 | 13 | 5.725 | 12.275 | 0
2270 | TORONTO BUTTONVILLE A | 4 | 4 | 14 | 10.4 | 7.6 | 0
2270 | TORONTO BUTTONVILLE A | 4 | 5 | 14 | 6.4 | 11.6 | 0
2271 | TORONTO BUTTONVILLE A | 4 | 4 | 15 | 10.2 | 7.8 | 0
2271 | TORONTO BUTTONVILLE A | 4 | 5 | 15 | 6 | 12 | 0
2272 | TORONTO BUTTONVILLE A | 4 | 4 | 16 | 9.3 | 8.7 | 0
2272 | TORONTO BUTTONVILLE A | 4 | 5 | 16 | 5.4 | 12.6 | 0
2273 | TORONTO BUTTONVILLE A | 4 | 4 | 17 | 9.6 | 8.4 | 0
2273 | TORONTO BUTTONVILLE A | 4 | 5 | 17 | 5.425 | 12.575 | 0
2274 | TORONTO BUTTONVILLE A | 4 | 4 | 18 | 9.8 | 8.2 | 0
2274 | TORONTO BUTTONVILLE A | 4 | 5 | 18 | 5.275 | 12.725 | 0
2275 | TORONTO BUTTONVILLE A | 4 | 4 | 19 | 9.6 | 8.4 | 0
2275 | TORONTO BUTTONVILLE A | 4 | 5 | 19 | 5.075 | 12.925 | 0
2276 | TORONTO BUTTONVILLE A | 4 | 4 | 20 | 9.3 | 8.7 | 0
2276 | TORONTO BUTTONVILLE A | 4 | 5 | 20 | 4.475 | 13.525 | 0
2277 | TORONTO BUTTONVILLE A | 4 | 4 | 21 | 8.5 | 9.5 | 0
2277 | TORONTO BUTTONVILLE A | 4 | 5 | 21 | 4.1 | 13.9 | 0
2278 | TORONTO BUTTONVILLE A | 4 | 4 | 22 | 7.1 | 10.9 | 0
2278 | TORONTO BUTTONVILLE A | 4 | 5 | 22 | 3.575 | 14.425 | 0
2279 | TORONTO BUTTONVILLE A | 4 | 4 | 23 | 6.8 | 11.2 | 0
2279 | TORONTO BUTTONVILLE A | 4 | 5 | 23 | 3.575 | 14.425 | 0
2280 | TORONTO BUTTONVILLE A | 4 | 4 | 24 | 6.8 | 11.2 | 0
2280 | TORONTO BUTTONVILLE A | 4 | 5 | 24 | 3.2 | 14.8 | 0
2281 | TORONTO BUTTONVILLE A | 4 | 5 | 1 | 7 | 11 | 0
2281 | TORONTO BUTTONVILLE A | 4 | 6 | 1 | 2.825 | 15.175 | 0
2282 | TORONTO BUTTONVILLE A | 4 | 5 | 2 | 7 | 11 | 0
2282 | TORONTO BUTTONVILLE A | 4 | 6 | 2 | 2.925 | 15.075 | 0
2283 | TORONTO BUTTONVILLE A | 4 | 5 | 3 | 6.9 | 11.1 | 0
2283 | TORONTO BUTTONVILLE A | 4 | 6 | 3 | 2.775 | 15.225 | 0
2284 | TORONTO BUTTONVILLE A | 4 | 5 | 4 | 6.8 | 11.2 | 0
2284 | TORONTO BUTTONVILLE A | 4 | 6 | 4 | 3.075 | 14.925 | 0
2285 | TORONTO BUTTONVILLE A | 4 | 5 | 5 | 6.1 | 11.9 | 0
2285 | TORONTO BUTTONVILLE A | 4 | 6 | 5 | 2.525 | 15.475 | 0
2286 | TORONTO BUTTONVILLE A | 4 | 5 | 6 | 5.3 | 12.7 | 0
2286 | TORONTO BUTTONVILLE A | 4 | 6 | 6 | 2.125 | 15.875 | 0
2287 | TORONTO BUTTONVILLE A | 4 | 5 | 7 | 4.9 | 13.1 | 0
2287 | TORONTO BUTTONVILLE A | 4 | 6 | 7 | 2.375 | 15.625 | 0
2288 | TORONTO BUTTONVILLE A | 4 | 5 | 8 | 5.1 | 12.9 | 0
2288 | TORONTO BUTTONVILLE A | 4 | 6 | 8 | 3.275 | 14.725 | 0
2289 | TORONTO BUTTONVILLE A | 4 | 5 | 9 | 4.8 | 13.2 | 0
2289 | TORONTO BUTTONVILLE A | 4 | 6 | 9 | 4.9 | 13.1 | 0
2290 | TORONTO BUTTONVILLE A | 4 | 5 | 10 | 6 | 12 | 0
2290 | TORONTO BUTTONVILLE A | 4 | 6 | 10 | 5.75 | 12.25 | 0
2291 | TORONTO BUTTONVILLE A | 4 | 5 | 11 | 7.1 | 10.9 | 0
2291 | TORONTO BUTTONVILLE A | 4 | 6 | 11 | 6.675 | 11.325 | 0
2292 | TORONTO BUTTONVILLE A | 4 | 5 | 12 | 5.6 | 12.4 | 0
2292 | TORONTO BUTTONVILLE A | 4 | 6 | 12 | 6.825 | 11.175 | 0
2293 | TORONTO BUTTONVILLE A | 4 | 5 | 13 | 7 | 11 | 0
2293 | TORONTO BUTTONVILLE A | 4 | 6 | 13 | 7.125 | 10.875 | 0
2294 | TORONTO BUTTONVILLE A | 4 | 5 | 14 | 7.5 | 10.5 | 0
2294 | TORONTO BUTTONVILLE A | 4 | 6 | 14 | 7.475 | 10.525 | 0
2295 | TORONTO BUTTONVILLE A | 4 | 5 | 15 | 7.5 | 10.5 | 0
2295 | TORONTO BUTTONVILLE A | 4 | 6 | 15 | 7.6 | 10.4 | 0
2296 | TORONTO BUTTONVILLE A | 4 | 5 | 16 | 8 | 10 | 0
2296 | TORONTO BUTTONVILLE A | 4 | 6 | 16 | 7.65 | 10.35 | 0
2297 | TORONTO BUTTONVILLE A | 4 | 5 | 17 | 8.5 | 9.5 | 0
2297 | TORONTO BUTTONVILLE A | 4 | 6 | 17 | 8.4 | 9.6 | 0
2298 | TORONTO BUTTONVILLE A | 4 | 5 | 18 | 8.4 | 9.6 | 0
2298 | TORONTO BUTTONVILLE A | 4 | 6 | 18 | 7.825 | 10.175 | 0
2299 | TORONTO BUTTONVILLE A | 4 | 5 | 19 | 7.9 | 10.1 | 0
2299 | TORONTO BUTTONVILLE A | 4 | 6 | 19 | 6.45 | 11.55 | 0
2300 | TORONTO BUTTONVILLE A | 4 | 5 | 20 | 6 | 12 | 0
2300 | TORONTO BUTTONVILLE A | 4 | 6 | 20 | 5.6 | 12.4 | 0
2301 | TORONTO BUTTONVILLE A | 4 | 5 | 21 | 4.6 | 13.4 | 0
2301 | TORONTO BUTTONVILLE A | 4 | 6 | 21 | 4.9 | 13.1 | 0
2302 | TORONTO BUTTONVILLE A | 4 | 5 | 22 | 3.4 | 14.6 | 0
2302 | TORONTO BUTTONVILLE A | 4 | 6 | 22 | 4.6 | 13.4 | 0
2303 | TORONTO BUTTONVILLE A | 4 | 5 | 23 | 2.7 | 15.3 | 0
2303 | TORONTO BUTTONVILLE A | 4 | 6 | 23 | 3.65 | 14.35 | 0
2304 | TORONTO BUTTONVILLE A | 4 | 5 | 24 | 1.9 | 16.1 | 0
2304 | TORONTO BUTTONVILLE A | 4 | 6 | 24 | 2.9 | 15.1 | 0
2305 | TORONTO BUTTONVILLE A | 4 | 6 | 1 | 1.8 | 16.2 | 0
2305 | TORONTO BUTTONVILLE A | 4 | 7 | 1 | 2.55 | 15.45 | 0
2306 | TORONTO BUTTONVILLE A | 4 | 6 | 2 | 1.2 | 16.8 | 0
2306 | TORONTO BUTTONVILLE A | 4 | 7 | 2 | 2.4 | 15.6 | 0
2307 | TORONTO BUTTONVILLE A | 4 | 6 | 3 | 1 | 17 | 0
2307 | TORONTO BUTTONVILLE A | 4 | 7 | 3 | 1.9 | 16.1 | 0
2308 | TORONTO BUTTONVILLE A | 4 | 6 | 4 | 0.9 | 17.1 | 0
2308 | TORONTO BUTTONVILLE A | 4 | 7 | 4 | 1.525 | 16.475 | 0
2309 | TORONTO BUTTONVILLE A | 4 | 6 | 5 | 0.3 | 17.7 | 0
2309 | TORONTO BUTTONVILLE A | 4 | 7 | 5 | 1.05 | 16.95 | 0
2310 | TORONTO BUTTONVILLE A | 4 | 6 | 6 | 0.1 | 17.9 | 0
2310 | TORONTO BUTTONVILLE A | 4 | 7 | 6 | 1.175 | 16.825 | 0
2311 | TORONTO BUTTONVILLE A | 4 | 6 | 7 | 0.2 | 17.8 | 0
2311 | TORONTO BUTTONVILLE A | 4 | 7 | 7 | 1.2 | 16.8 | 0
2312 | TORONTO BUTTONVILLE A | 4 | 6 | 8 | 1.9 | 16.1 | 0
2312 | TORONTO BUTTONVILLE A | 4 | 7 | 8 | 1.95 | 16.05 | 0
2313 | TORONTO BUTTONVILLE A | 4 | 6 | 9 | 4.9 | 13.1 | 0
2313 | TORONTO BUTTONVILLE A | 4 | 7 | 9 | 3.3 | 14.7 | 0
2314 | TORONTO BUTTONVILLE A | 4 | 6 | 10 | 7.1 | 10.9 | 0
2314 | TORONTO BUTTONVILLE A | 4 | 7 | 10 | 4.475 | 13.525 | 0
2315 | TORONTO BUTTONVILLE A | 4 | 6 | 11 | 9.2 | 8.8 | 0
2315 | TORONTO BUTTONVILLE A | 4 | 7 | 11 | 5.1 | 12.9 | 0
2316 | TORONTO BUTTONVILLE A | 4 | 6 | 12 | 10.4 | 7.6 | 0
2316 | TORONTO BUTTONVILLE A | 4 | 7 | 12 | 5.95 | 12.05 | 0
2317 | TORONTO BUTTONVILLE A | 4 | 6 | 13 | 11.8 | 6.2 | 0
2317 | TORONTO BUTTONVILLE A | 4 | 7 | 13 | 6.3 | 11.7 | 0
2318 | TORONTO BUTTONVILLE A | 4 | 6 | 14 | 12.7 | 5.3 | 0
2318 | TORONTO BUTTONVILLE A | 4 | 7 | 14 | 6.8 | 11.2 | 0
2319 | TORONTO BUTTONVILLE A | 4 | 6 | 15 | 13.9 | 4.1 | 0
2319 | TORONTO BUTTONVILLE A | 4 | 7 | 15 | 7.4 | 10.6 | 0
2320 | TORONTO BUTTONVILLE A | 4 | 6 | 16 | 13.2 | 4.8 | 0
2320 | TORONTO BUTTONVILLE A | 4 | 7 | 16 | 7.475 | 10.525 | 0
2321 | TORONTO BUTTONVILLE A | 4 | 6 | 17 | 13.2 | 4.8 | 0
2321 | TORONTO BUTTONVILLE A | 4 | 7 | 17 | 7.45 | 10.55 | 0
2322 | TORONTO BUTTONVILLE A | 4 | 6 | 18 | 13.4 | 4.6 | 0
2322 | TORONTO BUTTONVILLE A | 4 | 7 | 18 | 7.475 | 10.525 | 0
2323 | TORONTO BUTTONVILLE A | 4 | 6 | 19 | 12.5 | 5.5 | 0
2323 | TORONTO BUTTONVILLE A | 4 | 7 | 19 | 7.05 | 10.95 | 0
2324 | TORONTO BUTTONVILLE A | 4 | 6 | 20 | 10.9 | 7.1 | 0
2324 | TORONTO BUTTONVILLE A | 4 | 7 | 20 | 6.325 | 11.675 | 0
2325 | TORONTO BUTTONVILLE A | 4 | 6 | 21 | 11.6 | 6.4 | 0
2325 | TORONTO BUTTONVILLE A | 4 | 7 | 21 | 5.925 | 12.075 | 0
2326 | TORONTO BUTTONVILLE A | 4 | 6 | 22 | 10.5 | 7.5 | 0
2326 | TORONTO BUTTONVILLE A | 4 | 7 | 22 | 5.575 | 12.425 | 0
2327 | TORONTO BUTTONVILLE A | 4 | 6 | 23 | 9.2 | 8.8 | 0
2327 | TORONTO BUTTONVILLE A | 4 | 7 | 23 | 5.1 | 12.9 | 0
2328 | TORONTO BUTTONVILLE A | 4 | 6 | 24 | 9 | 9 | 0
2328 | TORONTO BUTTONVILLE A | 4 | 7 | 24 | 4.175 | 13.825 | 0
2329 | TORONTO BUTTONVILLE A | 4 | 7 | 1 | 9 | 9 | 0
2329 | TORONTO BUTTONVILLE A | 4 | 8 | 1 | 4.225 | 13.775 | 0
2330 | TORONTO BUTTONVILLE A | 4 | 7 | 2 | 9.1 | 8.9 | 0
2330 | TORONTO BUTTONVILLE A | 4 | 8 | 2 | 3.875 | 14.125 | 0
2331 | TORONTO BUTTONVILLE A | 4 | 7 | 3 | 8.4 | 9.6 | 0
2331 | TORONTO BUTTONVILLE A | 4 | 8 | 3 | 3.475 | 14.525 | 0
2332 | TORONTO BUTTONVILLE A | 4 | 7 | 4 | 7.2 | 10.8 | 0
2332 | TORONTO BUTTONVILLE A | 4 | 8 | 4 | 3.15 | 14.85 | 0
2333 | TORONTO BUTTONVILLE A | 4 | 7 | 5 | 5.1 | 12.9 | 0
2333 | TORONTO BUTTONVILLE A | 4 | 8 | 5 | 2.45 | 15.55 | 0
2334 | TORONTO BUTTONVILLE A | 4 | 7 | 6 | 4.2 | 13.8 | 0
2334 | TORONTO BUTTONVILLE A | 4 | 8 | 6 | 2.125 | 15.875 | 0
2335 | TORONTO BUTTONVILLE A | 4 | 7 | 7 | 3.7 | 14.3 | 0
2335 | TORONTO BUTTONVILLE A | 4 | 8 | 7 | 2.375 | 15.625 | 0
2336 | TORONTO BUTTONVILLE A | 4 | 7 | 8 | 5.2 | 12.8 | 0
2336 | TORONTO BUTTONVILLE A | 4 | 8 | 8 | 3.325 | 14.675 | 0
2337 | TORONTO BUTTONVILLE A | 4 | 7 | 9 | 7.7 | 10.3 | 0
2337 | TORONTO BUTTONVILLE A | 4 | 8 | 9 | 4.675 | 13.325 | 0
2338 | TORONTO BUTTONVILLE A | 4 | 7 | 10 | 9.9 | 8.1 | 0
2338 | TORONTO BUTTONVILLE A | 4 | 8 | 10 | 6 | 12 | 0
2339 | TORONTO BUTTONVILLE A | 4 | 7 | 11 | 12 | 6 | 0
2339 | TORONTO BUTTONVILLE A | 4 | 8 | 11 | 7.825 | 10.175 | 0
2340 | TORONTO BUTTONVILLE A | 4 | 7 | 12 | 13.1 | 4.9 | 0
2340 | TORONTO BUTTONVILLE A | 4 | 8 | 12 | 9.175 | 8.825 | 0
2341 | TORONTO BUTTONVILLE A | 4 | 7 | 13 | 13.8 | 4.2 | 0
2341 | TORONTO BUTTONVILLE A | 4 | 8 | 13 | 10.375 | 7.625 | 0
2342 | TORONTO BUTTONVILLE A | 4 | 7 | 14 | 13.2 | 4.8 | 0
2342 | TORONTO BUTTONVILLE A | 4 | 8 | 14 | 10.8 | 7.2 | 0
2343 | TORONTO BUTTONVILLE A | 4 | 7 | 15 | 13.3 | 4.7 | 0
2343 | TORONTO BUTTONVILLE A | 4 | 8 | 15 | 10.95 | 7.05 | 0
2344 | TORONTO BUTTONVILLE A | 4 | 7 | 16 | 13.3 | 4.7 | 0
2344 | TORONTO BUTTONVILLE A | 4 | 8 | 16 | 11 | 7 | 0
2345 | TORONTO BUTTONVILLE A | 4 | 7 | 17 | 12.9 | 5.1 | 0
2345 | TORONTO BUTTONVILLE A | 4 | 8 | 17 | 11.125 | 6.875 | 0
2346 | TORONTO BUTTONVILLE A | 4 | 7 | 18 | 11 | 7 | 0
2346 | TORONTO BUTTONVILLE A | 4 | 8 | 18 | 11.1 | 6.9 | 0
2347 | TORONTO BUTTONVILLE A | 4 | 7 | 19 | 7.6 | 10.4 | 0
2347 | TORONTO BUTTONVILLE A | 4 | 8 | 19 | 10.5 | 7.5 | 0
2348 | TORONTO BUTTONVILLE A | 4 | 7 | 20 | 6.4 | 11.6 | 0
2348 | TORONTO BUTTONVILLE A | 4 | 8 | 20 | 9.225 | 8.775 | 0
2349 | TORONTO BUTTONVILLE A | 4 | 7 | 21 | 5.5 | 12.5 | 0
2349 | TORONTO BUTTONVILLE A | 4 | 8 | 21 | 8.55 | 9.45 | 0
2350 | TORONTO BUTTONVILLE A | 4 | 7 | 22 | 5.1 | 12.9 | 0
2350 | TORONTO BUTTONVILLE A | 4 | 8 | 22 | 7.65 | 10.35 | 0
2351 | TORONTO BUTTONVILLE A | 4 | 7 | 23 | 5.2 | 12.8 | 0
2351 | TORONTO BUTTONVILLE A | 4 | 8 | 23 | 6.35 | 11.65 | 0
2352 | TORONTO BUTTONVILLE A | 4 | 7 | 24 | 5.3 | 12.7 | 0
2352 | TORONTO BUTTONVILLE A | 4 | 8 | 24 | 5.1 | 12.9 | 0
2353 | TORONTO BUTTONVILLE A | 4 | 8 | 1 | 5.2 | 12.8 | 0
2353 | TORONTO BUTTONVILLE A | 4 | 9 | 1 | 4.35 | 13.65 | 0
2354 | TORONTO BUTTONVILLE A | 4 | 8 | 2 | 5.1 | 12.9 | 0
2354 | TORONTO BUTTONVILLE A | 4 | 9 | 2 | 4.35 | 13.65 | 0
2355 | TORONTO BUTTONVILLE A | 4 | 8 | 3 | 5.5 | 12.5 | 0
2355 | TORONTO BUTTONVILLE A | 4 | 9 | 3 | 3.925 | 14.075 | 0
2356 | TORONTO BUTTONVILLE A | 4 | 8 | 4 | 5.6 | 12.4 | 0
2356 | TORONTO BUTTONVILLE A | 4 | 9 | 4 | 3.45 | 14.55 | 0
2357 | TORONTO BUTTONVILLE A | 4 | 8 | 5 | 5.8 | 12.2 | 0
2357 | TORONTO BUTTONVILLE A | 4 | 9 | 5 | 2.925 | 15.075 | 0
2358 | TORONTO BUTTONVILLE A | 4 | 8 | 6 | 5.9 | 12.1 | 0
2358 | TORONTO BUTTONVILLE A | 4 | 9 | 6 | 2.775 | 15.225 | 0
2359 | TORONTO BUTTONVILLE A | 4 | 8 | 7 | 6.1 | 11.9 | 0
2359 | TORONTO BUTTONVILLE A | 4 | 9 | 7 | 2.875 | 15.125 | 0
2360 | TORONTO BUTTONVILLE A | 4 | 8 | 8 | 6.1 | 11.9 | 0
2360 | TORONTO BUTTONVILLE A | 4 | 9 | 8 | 3.475 | 14.525 | 0
2361 | TORONTO BUTTONVILLE A | 4 | 8 | 9 | 6.3 | 11.7 | 0
2361 | TORONTO BUTTONVILLE A | 4 | 9 | 9 | 5.6 | 12.4 | 0
2362 | TORONTO BUTTONVILLE A | 4 | 8 | 10 | 7 | 11 | 0
2362 | TORONTO BUTTONVILLE A | 4 | 9 | 10 | 7.25 | 10.75 | 0
2363 | TORONTO BUTTONVILLE A | 4 | 8 | 11 | 8.5 | 9.5 | 0
2363 | TORONTO BUTTONVILLE A | 4 | 9 | 11 | 8.825 | 9.175 | 0
2364 | TORONTO BUTTONVILLE A | 4 | 8 | 12 | 9.2 | 8.8 | 0
2364 | TORONTO BUTTONVILLE A | 4 | 9 | 12 | 9.975 | 8.025 | 0
2365 | TORONTO BUTTONVILLE A | 4 | 8 | 13 | 11.4 | 6.6 | 0
2365 | TORONTO BUTTONVILLE A | 4 | 9 | 13 | 9.7 | 8.3 | 0
2366 | TORONTO BUTTONVILLE A | 4 | 8 | 14 | 12.2 | 5.8 | 0
2366 | TORONTO BUTTONVILLE A | 4 | 9 | 14 | 10.225 | 7.775 | 0
2367 | TORONTO BUTTONVILLE A | 4 | 8 | 15 | 11.9 | 6.1 | 0
2367 | TORONTO BUTTONVILLE A | 4 | 9 | 15 | 10.625 | 7.375 | 0
2368 | TORONTO BUTTONVILLE A | 4 | 8 | 16 | 12.5 | 5.5 | 0
2368 | TORONTO BUTTONVILLE A | 4 | 9 | 16 | 10.75 | 7.25 | 0
2369 | TORONTO BUTTONVILLE A | 4 | 8 | 17 | 12.1 | 5.9 | 0
2369 | TORONTO BUTTONVILLE A | 4 | 9 | 17 | 11.025 | 6.975 | 0
2370 | TORONTO BUTTONVILLE A | 4 | 8 | 18 | 12 | 6 | 0
2370 | TORONTO BUTTONVILLE A | 4 | 9 | 18 | 11.2 | 6.8 | 0
2371 | TORONTO BUTTONVILLE A | 4 | 8 | 19 | 11.6 | 6.4 | 0
2371 | TORONTO BUTTONVILLE A | 4 | 9 | 19 | 10.475 | 7.525 | 0
2372 | TORONTO BUTTONVILLE A | 4 | 8 | 20 | 10.7 | 7.3 | 0
2372 | TORONTO BUTTONVILLE A | 4 | 9 | 20 | 9.275 | 8.725 | 0
2373 | TORONTO BUTTONVILLE A | 4 | 8 | 21 | 9.6 | 8.4 | 0
2373 | TORONTO BUTTONVILLE A | 4 | 9 | 21 | 8.125 | 9.875 | 0
2374 | TORONTO BUTTONVILLE A | 4 | 8 | 22 | 8.5 | 9.5 | 0
2374 | TORONTO BUTTONVILLE A | 4 | 9 | 22 | 6.5 | 11.5 | 0
2375 | TORONTO BUTTONVILLE A | 4 | 8 | 23 | 6.5 | 11.5 | 0
2375 | TORONTO BUTTONVILLE A | 4 | 9 | 23 | 5.8 | 12.2 | 0
2376 | TORONTO BUTTONVILLE A | 4 | 8 | 24 | 7.3 | 10.7 | 0
2376 | TORONTO BUTTONVILLE A | 4 | 9 | 24 | 5.6 | 12.4 | 0
2377 | TORONTO BUTTONVILLE A | 4 | 9 | 1 | 7.2 | 10.8 | 0
2377 | TORONTO BUTTONVILLE A | 4 | 10 | 1 | 5.175 | 12.825 | 0
2378 | TORONTO BUTTONVILLE A | 4 | 9 | 2 | 7.1 | 10.9 | 0
2378 | TORONTO BUTTONVILLE A | 4 | 10 | 2 | 4.575 | 13.425 | 0
2379 | TORONTO BUTTONVILLE A | 4 | 9 | 3 | 6.8 | 11.2 | 0
2379 | TORONTO BUTTONVILLE A | 4 | 10 | 3 | 4.25 | 13.75 | 0
2380 | TORONTO BUTTONVILLE A | 4 | 9 | 4 | 6.8 | 11.2 | 0
2380 | TORONTO BUTTONVILLE A | 4 | 10 | 4 | 4.425 | 13.575 | 0
2381 | TORONTO BUTTONVILLE A | 4 | 9 | 5 | 6.7 | 11.3 | 0
2381 | TORONTO BUTTONVILLE A | 4 | 10 | 5 | 4.5 | 13.5 | 0
2382 | TORONTO BUTTONVILLE A | 4 | 9 | 6 | 1.4 | 16.6 | 0
2382 | TORONTO BUTTONVILLE A | 4 | 10 | 6 | 4.2 | 13.8 | 0
2383 | TORONTO BUTTONVILLE A | 4 | 9 | 7 | 1.1 | 16.9 | 0
2383 | TORONTO BUTTONVILLE A | 4 | 10 | 7 | 3.925 | 14.075 | 0
2384 | TORONTO BUTTONVILLE A | 4 | 9 | 8 | 1.6 | 16.4 | 0
2384 | TORONTO BUTTONVILLE A | 4 | 10 | 8 | 4.625 | 13.375 | 0
2385 | TORONTO BUTTONVILLE A | 4 | 9 | 9 | 2.3 | 15.7 | 0
2385 | TORONTO BUTTONVILLE A | 4 | 10 | 9 | 6.475 | 11.525 | 0
2386 | TORONTO BUTTONVILLE A | 4 | 9 | 10 | 4.2 | 13.8 | 0
2386 | TORONTO BUTTONVILLE A | 4 | 10 | 10 | 8.25 | 9.75 | 0
2387 | TORONTO BUTTONVILLE A | 4 | 9 | 11 | 5.6 | 12.4 | 0
2387 | TORONTO BUTTONVILLE A | 4 | 10 | 11 | 9.575 | 8.425 | 0
2388 | TORONTO BUTTONVILLE A | 4 | 9 | 12 | 6.8 | 11.2 | 0
2388 | TORONTO BUTTONVILLE A | 4 | 10 | 12 | 11.5 | 6.5 | 0
2389 | TORONTO BUTTONVILLE A | 4 | 9 | 13 | 7.1 | 10.9 | 0
2389 | TORONTO BUTTONVILLE A | 4 | 10 | 13 | 12.1 | 5.9 | 0
2390 | TORONTO BUTTONVILLE A | 4 | 9 | 14 | 7.4 | 10.6 | 0
2390 | TORONTO BUTTONVILLE A | 4 | 10 | 14 | 12.375 | 5.625 | 0
2391 | TORONTO BUTTONVILLE A | 4 | 9 | 15 | 7.5 | 10.5 | 0
2391 | TORONTO BUTTONVILLE A | 4 | 10 | 15 | 12.775 | 5.225 | 0
2392 | TORONTO BUTTONVILLE A | 4 | 9 | 16 | 7 | 11 | 0
2392 | TORONTO BUTTONVILLE A | 4 | 10 | 16 | 11.15 | 6.85 | 0
2393 | TORONTO BUTTONVILLE A | 4 | 9 | 17 | 6.7 | 11.3 | 0
2393 | TORONTO BUTTONVILLE A | 4 | 10 | 17 | 11.95 | 6.05 | 0
2394 | TORONTO BUTTONVILLE A | 4 | 9 | 18 | 6.4 | 11.6 | 0
2394 | TORONTO BUTTONVILLE A | 4 | 10 | 18 | 12.05 | 5.95 | 0
2395 | TORONTO BUTTONVILLE A | 4 | 9 | 19 | 5.6 | 12.4 | 0
2395 | TORONTO BUTTONVILLE A | 4 | 10 | 19 | 11.85 | 6.15 | 0
2396 | TORONTO BUTTONVILLE A | 4 | 9 | 20 | 4.5 | 13.5 | 0
2396 | TORONTO BUTTONVILLE A | 4 | 10 | 20 | 10.65 | 7.35 | 0
2397 | TORONTO BUTTONVILLE A | 4 | 9 | 21 | 3.3 | 14.7 | 0
2397 | TORONTO BUTTONVILLE A | 4 | 10 | 21 | 10.225 | 7.775 | 0
2398 | TORONTO BUTTONVILLE A | 4 | 9 | 22 | 3 | 15 | 0
2398 | TORONTO BUTTONVILLE A | 4 | 10 | 22 | 9.225 | 8.775 | 0
2399 | TORONTO BUTTONVILLE A | 4 | 9 | 23 | 2.5 | 15.5 | 0
2399 | TORONTO BUTTONVILLE A | 4 | 10 | 23 | 8.725 | 9.275 | 0
2400 | TORONTO BUTTONVILLE A | 4 | 9 | 24 | 2 | 16 | 0
2400 | TORONTO BUTTONVILLE A | 4 | 10 | 24 | 8.425 | 9.575 | 0
2401 | TORONTO BUTTONVILLE A | 4 | 10 | 1 | 1.4 | 16.6 | 0
2401 | TORONTO BUTTONVILLE A | 4 | 11 | 1 | 7.85 | 10.15 | 0
2402 | TORONTO BUTTONVILLE A | 4 | 10 | 2 | 1.2 | 16.8 | 0
2402 | TORONTO BUTTONVILLE A | 4 | 11 | 2 | 7.6 | 10.4 | 0
2403 | TORONTO BUTTONVILLE A | 4 | 10 | 3 | 0.9 | 17.1 | 0
2403 | TORONTO BUTTONVILLE A | 4 | 11 | 3 | 6.775 | 11.225 | 0
2404 | TORONTO BUTTONVILLE A | 4 | 10 | 4 | 0.8 | 17.2 | 0
2404 | TORONTO BUTTONVILLE A | 4 | 11 | 4 | 6.4 | 11.6 | 0
2405 | TORONTO BUTTONVILLE A | 4 | 10 | 5 | 0.6 | 17.4 | 0
2405 | TORONTO BUTTONVILLE A | 4 | 11 | 5 | 6.8 | 11.2 | 0
2406 | TORONTO BUTTONVILLE A | 4 | 10 | 6 | 0.6 | 17.4 | 0
2406 | TORONTO BUTTONVILLE A | 4 | 11 | 6 | 6.7 | 11.3 | 0
2407 | TORONTO BUTTONVILLE A | 4 | 10 | 7 | 0.2 | 17.8 | 0
2407 | TORONTO BUTTONVILLE A | 4 | 11 | 7 | 6.575 | 11.425 | 0
2408 | TORONTO BUTTONVILLE A | 4 | 10 | 8 | -0.1 | 18.1 | 0
2408 | TORONTO BUTTONVILLE A | 4 | 11 | 8 | 5.6 | 12.4 | 0
2409 | TORONTO BUTTONVILLE A | 4 | 10 | 9 | 0.5 | 17.5 | 0
2409 | TORONTO BUTTONVILLE A | 4 | 11 | 9 | 5.825 | 12.175 | 0
2410 | TORONTO BUTTONVILLE A | 4 | 10 | 10 | 1.5 | 16.5 | 0
2410 | TORONTO BUTTONVILLE A | 4 | 11 | 10 | 6.675 | 11.325 | 0
2411 | TORONTO BUTTONVILLE A | 4 | 10 | 11 | 2.6 | 15.4 | 0
2411 | TORONTO BUTTONVILLE A | 4 | 11 | 11 | 9.7667 | 8.2333 | 0
2412 | TORONTO BUTTONVILLE A | 4 | 10 | 12 | 3.6 | 14.4 | 0
2412 | TORONTO BUTTONVILLE A | 4 | 11 | 12 | 9.7333 | 8.2667 | 0
2413 | TORONTO BUTTONVILLE A | 4 | 10 | 13 | 4.1 | 13.9 | 0
2413 | TORONTO BUTTONVILLE A | 4 | 11 | 13 | 8.075 | 9.925 | 0
2414 | TORONTO BUTTONVILLE A | 4 | 10 | 14 | 5 | 13 | 0
2414 | TORONTO BUTTONVILLE A | 4 | 11 | 14 | 8.45 | 9.55 | 0
2415 | TORONTO BUTTONVILLE A | 4 | 10 | 15 | 5.5 | 12.5 | 0
2415 | TORONTO BUTTONVILLE A | 4 | 11 | 15 | 8.175 | 9.825 | 0
2416 | TORONTO BUTTONVILLE A | 4 | 10 | 16 | 5 | 13 | 0
2416 | TORONTO BUTTONVILLE A | 4 | 11 | 16 | 8.175 | 9.825 | 0
2417 | TORONTO BUTTONVILLE A | 4 | 10 | 17 | 5.3 | 12.7 | 0
2417 | TORONTO BUTTONVILLE A | 4 | 11 | 17 | 8.35 | 9.65 | 0
2418 | TORONTO BUTTONVILLE A | 4 | 10 | 18 | 4.6 | 13.4 | 0
2418 | TORONTO BUTTONVILLE A | 4 | 11 | 18 | 8.25 | 9.75 | 0
2419 | TORONTO BUTTONVILLE A | 4 | 10 | 19 | 4.3 | 13.7 | 0
2419 | TORONTO BUTTONVILLE A | 4 | 11 | 19 | 8.3 | 9.7 | 0
2420 | TORONTO BUTTONVILLE A | 4 | 10 | 20 | 3 | 15 | 0
2420 | TORONTO BUTTONVILLE A | 4 | 11 | 20 | 8.125 | 9.875 | 0
2421 | TORONTO BUTTONVILLE A | 4 | 10 | 21 | 2.1 | 15.9 | 0
2421 | TORONTO BUTTONVILLE A | 4 | 11 | 21 | 6.95 | 11.05 | 0
2422 | TORONTO BUTTONVILLE A | 4 | 10 | 22 | 1.6 | 16.4 | 0
2422 | TORONTO BUTTONVILLE A | 4 | 11 | 22 | 6.875 | 11.125 | 0
2423 | TORONTO BUTTONVILLE A | 4 | 10 | 23 | 0.9 | 17.1 | 0
2423 | TORONTO BUTTONVILLE A | 4 | 11 | 23 | 6.575 | 11.425 | 0
2424 | TORONTO BUTTONVILLE A | 4 | 10 | 24 | 0.2 | 17.8 | 0
2424 | TORONTO BUTTONVILLE A | 4 | 11 | 24 | 6.4 | 11.6 | 0
2425 | TORONTO BUTTONVILLE A | 4 | 11 | 1 | -0.2 | 18.2 | 0
2425 | TORONTO BUTTONVILLE A | 4 | 12 | 1 | 5.925 | 12.075 | 0
2426 | TORONTO BUTTONVILLE A | 4 | 11 | 2 | 0.1 | 17.9 | 0
2426 | TORONTO BUTTONVILLE A | 4 | 12 | 2 | 5.475 | 12.525 | 0
2427 | TORONTO BUTTONVILLE A | 4 | 11 | 3 | 0 | 18 | 0
2427 | TORONTO BUTTONVILLE A | 4 | 12 | 3 | 5.075 | 12.925 | 0
2428 | TORONTO BUTTONVILLE A | 4 | 11 | 4 | 0 | 18 | 0
2428 | TORONTO BUTTONVILLE A | 4 | 12 | 4 | 4.6 | 13.4 | 0
2429 | TORONTO BUTTONVILLE A | 4 | 11 | 5 | -0.4 | 18.4 | 0
2429 | TORONTO BUTTONVILLE A | 4 | 12 | 5 | 4.25 | 13.75 | 0
2430 | TORONTO BUTTONVILLE A | 4 | 11 | 6 | -0.9 | 18.9 | 0
2430 | TORONTO BUTTONVILLE A | 4 | 12 | 6 | 4.2 | 13.8 | 0
2431 | TORONTO BUTTONVILLE A | 4 | 11 | 7 | -0.7 | 18.7 | 0
2431 | TORONTO BUTTONVILLE A | 4 | 12 | 7 | 4.375 | 13.625 | 0
2432 | TORONTO BUTTONVILLE A | 4 | 11 | 8 | 0.1 | 17.9 | 0
2432 | TORONTO BUTTONVILLE A | 4 | 12 | 8 | 4.65 | 13.35 | 0
2433 | TORONTO BUTTONVILLE A | 4 | 11 | 9 | 1.3 | 16.7 | 0
2433 | TORONTO BUTTONVILLE A | 4 | 12 | 9 | 5.05 | 12.95 | 0
2434 | TORONTO BUTTONVILLE A | 4 | 11 | 10 | 2.9 | 15.1 | 0
2434 | TORONTO BUTTONVILLE A | 4 | 12 | 10 | 5.875 | 12.125 | 0
2435 | TORONTO BUTTONVILLE A | 4 | 11 | 11 | 4.2 | 13.8 | 0
2435 | TORONTO BUTTONVILLE A | 4 | 12 | 11 | 6.675 | 11.325 | 0
2436 | TORONTO BUTTONVILLE A | 4 | 11 | 12 | 4.9 | 13.1 | 0
2436 | TORONTO BUTTONVILLE A | 4 | 12 | 12 | 7.1 | 10.9 | 0
2437 | TORONTO BUTTONVILLE A | 4 | 11 | 13 | 5.8 | 12.2 | 0
2437 | TORONTO BUTTONVILLE A | 4 | 12 | 13 | 7.4 | 10.6 | 0
2438 | TORONTO BUTTONVILLE A | 4 | 11 | 14 | 6.2 | 11.8 | 0
2438 | TORONTO BUTTONVILLE A | 4 | 12 | 14 | 7.45 | 10.55 | 0
2439 | TORONTO BUTTONVILLE A | 4 | 11 | 15 | 6.3 | 11.7 | 0
2439 | TORONTO BUTTONVILLE A | 4 | 12 | 15 | 7.9 | 10.1 | 0
2440 | TORONTO BUTTONVILLE A | 4 | 11 | 16 | 7.1 | 10.9 | 0
2440 | TORONTO BUTTONVILLE A | 4 | 12 | 16 | 8 | 10 | 0
2441 | TORONTO BUTTONVILLE A | 4 | 11 | 17 | 7.3 | 10.7 | 0
2441 | TORONTO BUTTONVILLE A | 4 | 12 | 17 | 8.725 | 9.275 | 0
2442 | TORONTO BUTTONVILLE A | 4 | 11 | 18 | 8.1 | 9.9 | 0
2442 | TORONTO BUTTONVILLE A | 4 | 12 | 18 | 9.525 | 8.475 | 0
2443 | TORONTO BUTTONVILLE A | 4 | 11 | 19 | 8.3 | 9.7 | 0
2443 | TORONTO BUTTONVILLE A | 4 | 12 | 19 | 9.65 | 8.35 | 0
2444 | TORONTO BUTTONVILLE A | 4 | 11 | 20 | 7.9 | 10.1 | 0
2444 | TORONTO BUTTONVILLE A | 4 | 12 | 20 | 8.925 | 9.075 | 0
2445 | TORONTO BUTTONVILLE A | 4 | 11 | 21 | 7.2 | 10.8 | 0
2445 | TORONTO BUTTONVILLE A | 4 | 12 | 21 | 8.975 | 9.025 | 0
2446 | TORONTO BUTTONVILLE A | 4 | 11 | 22 | 6.4 | 11.6 | 0
2446 | TORONTO BUTTONVILLE A | 4 | 12 | 22 | 7.9 | 10.1 | 0
2447 | TORONTO BUTTONVILLE A | 4 | 11 | 23 | 5.4 | 12.6 | 0
2447 | TORONTO BUTTONVILLE A | 4 | 12 | 23 | 7.4 | 10.6 | 0
2448 | TORONTO BUTTONVILLE A | 4 | 11 | 24 | 4.2 | 13.8 | 0
2448 | TORONTO BUTTONVILLE A | 4 | 12 | 24 | 7.2 | 10.8 | 0
2449 | TORONTO BUTTONVILLE A | 4 | 12 | 1 | 3 | 15 | 0
2449 | TORONTO BUTTONVILLE A | 4 | 13 | 1 | 6.35 | 11.65 | 0
2450 | TORONTO BUTTONVILLE A | 4 | 12 | 2 | 3.2 | 14.8 | 0
2450 | TORONTO BUTTONVILLE A | 4 | 13 | 2 | 5.4 | 12.6 | 0
2451 | TORONTO BUTTONVILLE A | 4 | 12 | 3 | 3.5 | 14.5 | 0
2451 | TORONTO BUTTONVILLE A | 4 | 13 | 3 | 4.625 | 13.375 | 0
2452 | TORONTO BUTTONVILLE A | 4 | 12 | 4 | 2.6 | 15.4 | 0
2452 | TORONTO BUTTONVILLE A | 4 | 13 | 4 | 3.875 | 14.125 | 0
2453 | TORONTO BUTTONVILLE A | 4 | 12 | 5 | 3 | 15 | 0
2453 | TORONTO BUTTONVILLE A | 4 | 13 | 5 | 3.475 | 14.525 | 0
2454 | TORONTO BUTTONVILLE A | 4 | 12 | 6 | 3 | 15 | 0
2454 | TORONTO BUTTONVILLE A | 4 | 13 | 6 | 3.55 | 14.45 | 0
2455 | TORONTO BUTTONVILLE A | 4 | 12 | 7 | 3 | 15 | 0
2455 | TORONTO BUTTONVILLE A | 4 | 13 | 7 | 2.825 | 15.175 | 0
2456 | TORONTO BUTTONVILLE A | 4 | 12 | 8 | 3.8 | 14.2 | 0
2456 | TORONTO BUTTONVILLE A | 4 | 13 | 8 | 4.675 | 13.325 | 0
2457 | TORONTO BUTTONVILLE A | 4 | 12 | 9 | 4.3 | 13.7 | 0
2457 | TORONTO BUTTONVILLE A | 4 | 13 | 9 | 6.15 | 11.85 | 0
2458 | TORONTO BUTTONVILLE A | 4 | 12 | 10 | 5.2 | 12.8 | 0
2458 | TORONTO BUTTONVILLE A | 4 | 13 | 10 | 7.275 | 10.725 | 0
2459 | TORONTO BUTTONVILLE A | 4 | 12 | 11 | 6 | 12 | 0
2459 | TORONTO BUTTONVILLE A | 4 | 13 | 11 | 8.725 | 9.275 | 0
2460 | TORONTO BUTTONVILLE A | 4 | 12 | 12 | 7.6 | 10.4 | 0
2460 | TORONTO BUTTONVILLE A | 4 | 13 | 12 | 9.3 | 8.7 | 0
2461 | TORONTO BUTTONVILLE A | 4 | 12 | 13 | 8.8 | 9.2 | 0
2461 | TORONTO BUTTONVILLE A | 4 | 13 | 13 | 9.725 | 8.275 | 0
2462 | TORONTO BUTTONVILLE A | 4 | 12 | 14 | 10 | 8 | 0
2462 | TORONTO BUTTONVILLE A | 4 | 13 | 14 | 10.25 | 7.75 | 0
2463 | TORONTO BUTTONVILLE A | 4 | 12 | 15 | 11.7 | 6.3 | 0
2463 | TORONTO BUTTONVILLE A | 4 | 13 | 15 | 10.95 | 7.05 | 0
2464 | TORONTO BUTTONVILLE A | 4 | 12 | 16 | 11.5 | 6.5 | 0
2464 | TORONTO BUTTONVILLE A | 4 | 13 | 16 | 11.525 | 6.475 | 0
2465 | TORONTO BUTTONVILLE A | 4 | 12 | 17 | 11.3 | 6.7 | 0
2465 | TORONTO BUTTONVILLE A | 4 | 13 | 17 | 11.175 | 6.825 | 0
2466 | TORONTO BUTTONVILLE A | 4 | 12 | 18 | 11.6 | 6.4 | 0
2466 | TORONTO BUTTONVILLE A | 4 | 13 | 18 | 10.975 | 7.025 | 0
2467 | TORONTO BUTTONVILLE A | 4 | 12 | 19 | 11.2 | 6.8 | 0
2467 | TORONTO BUTTONVILLE A | 4 | 13 | 19 | 10.325 | 7.675 | 0
2468 | TORONTO BUTTONVILLE A | 4 | 12 | 20 | 10.9 | 7.1 | 0
2468 | TORONTO BUTTONVILLE A | 4 | 13 | 20 | 9.2 | 8.8 | 0
2469 | TORONTO BUTTONVILLE A | 4 | 12 | 21 | 10.7 | 7.3 | 0
2469 | TORONTO BUTTONVILLE A | 4 | 13 | 21 | 7.125 | 10.875 | 0
2470 | TORONTO BUTTONVILLE A | 4 | 12 | 22 | 10.8 | 7.2 | 0
2470 | TORONTO BUTTONVILLE A | 4 | 13 | 22 | 6.3 | 11.7 | 0
2471 | TORONTO BUTTONVILLE A | 4 | 12 | 23 | 10.8 | 7.2 | 0
2471 | TORONTO BUTTONVILLE A | 4 | 13 | 23 | 5.575 | 12.425 | 0
2472 | TORONTO BUTTONVILLE A | 4 | 12 | 24 | 10.5 | 7.5 | 0
2472 | TORONTO BUTTONVILLE A | 4 | 13 | 24 | 4.75 | 13.25 | 0
2473 | TORONTO BUTTONVILLE A | 4 | 13 | 1 | 10.6 | 7.4 | 0
2473 | TORONTO BUTTONVILLE A | 4 | 14 | 1 | 4.2 | 13.8 | 0
2474 | TORONTO BUTTONVILLE A | 4 | 13 | 2 | 10.3 | 7.7 | 0
2474 | TORONTO BUTTONVILLE A | 4 | 14 | 2 | 3.775 | 14.225 | 0
2475 | TORONTO BUTTONVILLE A | 4 | 13 | 3 | 8.8 | 9.2 | 0
2475 | TORONTO BUTTONVILLE A | 4 | 14 | 3 | 3.525 | 14.475 | 0
2476 | TORONTO BUTTONVILLE A | 4 | 13 | 4 | 8.3 | 9.7 | 0
2476 | TORONTO BUTTONVILLE A | 4 | 14 | 4 | 3.05 | 14.95 | 0
2477 | TORONTO BUTTONVILLE A | 4 | 13 | 5 | 9.4 | 8.6 | 0
2477 | TORONTO BUTTONVILLE A | 4 | 14 | 5 | 3.1 | 14.9 | 0
2478 | TORONTO BUTTONVILLE A | 4 | 13 | 6 | 9.9 | 8.1 | 0
2478 | TORONTO BUTTONVILLE A | 4 | 14 | 6 | 2.675 | 15.325 | 0
2479 | TORONTO BUTTONVILLE A | 4 | 13 | 7 | 9.8 | 8.2 | 0
2479 | TORONTO BUTTONVILLE A | 4 | 14 | 7 | 2.55 | 15.45 | 0
2480 | TORONTO BUTTONVILLE A | 4 | 13 | 8 | 9.6 | 8.4 | 0
2480 | TORONTO BUTTONVILLE A | 4 | 14 | 8 | 3.2 | 14.8 | 0
2481 | TORONTO BUTTONVILLE A | 4 | 13 | 9 | 10 | 8 | 0
2481 | TORONTO BUTTONVILLE A | 4 | 14 | 9 | 4 | 14 | 0
2482 | TORONTO BUTTONVILLE A | 4 | 13 | 10 | 12.3 | 5.7 | 0
2482 | TORONTO BUTTONVILLE A | 4 | 14 | 10 | 4.975 | 13.025 | 0
2483 | TORONTO BUTTONVILLE A | 4 | 13 | 11 | 12.6 | 5.4 | 0
2483 | TORONTO BUTTONVILLE A | 4 | 14 | 11 | 6.6 | 11.4 | 0
2484 | TORONTO BUTTONVILLE A | 4 | 13 | 12 | 13.4 | 4.6 | 0
2484 | TORONTO BUTTONVILLE A | 4 | 14 | 12 | 6.9 | 11.1 | 0
2485 | TORONTO BUTTONVILLE A | 4 | 13 | 13 | 14 | 4 | 0
2485 | TORONTO BUTTONVILLE A | 4 | 14 | 13 | 7.3 | 10.7 | 0
2486 | TORONTO BUTTONVILLE A | 4 | 13 | 14 | 13.8 | 4.2 | 0
2486 | TORONTO BUTTONVILLE A | 4 | 14 | 14 | 7.425 | 10.575 | 0
2487 | TORONTO BUTTONVILLE A | 4 | 13 | 15 | 10.8 | 7.2 | 0
2487 | TORONTO BUTTONVILLE A | 4 | 14 | 15 | 7.05 | 10.95 | 0
2488 | TORONTO BUTTONVILLE A | 4 | 13 | 16 | 8.3 | 9.7 | 0
2488 | TORONTO BUTTONVILLE A | 4 | 14 | 16 | 7.1 | 10.9 | 0
2489 | TORONTO BUTTONVILLE A | 4 | 13 | 17 | 7.2 | 10.8 | 0
2489 | TORONTO BUTTONVILLE A | 4 | 14 | 17 | 6.825 | 11.175 | 0
2490 | TORONTO BUTTONVILLE A | 4 | 13 | 18 | 6.6 | 11.4 | 0
2490 | TORONTO BUTTONVILLE A | 4 | 14 | 18 | 6.45 | 11.55 | 0
2491 | TORONTO BUTTONVILLE A | 4 | 13 | 19 | 5 | 13 | 0
2491 | TORONTO BUTTONVILLE A | 4 | 14 | 19 | 6.025 | 11.975 | 0
2492 | TORONTO BUTTONVILLE A | 4 | 13 | 20 | 4.3 | 13.7 | 0
2492 | TORONTO BUTTONVILLE A | 4 | 14 | 20 | 5.5 | 12.5 | 0
2493 | TORONTO BUTTONVILLE A | 4 | 13 | 21 | 4 | 14 | 0
2493 | TORONTO BUTTONVILLE A | 4 | 14 | 21 | 4.675 | 13.325 | 0
2494 | TORONTO BUTTONVILLE A | 4 | 13 | 22 | 3.6 | 14.4 | 0
2494 | TORONTO BUTTONVILLE A | 4 | 14 | 22 | 4.15 | 13.85 | 0
2495 | TORONTO BUTTONVILLE A | 4 | 13 | 23 | 3.6 | 14.4 | 0
2495 | TORONTO BUTTONVILLE A | 4 | 14 | 23 | 3.475 | 14.525 | 0
2496 | TORONTO BUTTONVILLE A | 4 | 13 | 24 | 3 | 15 | 0
2496 | TORONTO BUTTONVILLE A | 4 | 14 | 24 | 2.725 | 15.275 | 0
2497 | TORONTO BUTTONVILLE A | 4 | 14 | 1 | 1.9 | 16.1 | 0
2497 | TORONTO BUTTONVILLE A | 4 | 15 | 1 | 2.375 | 15.625 | 0
2498 | TORONTO BUTTONVILLE A | 4 | 14 | 2 | 1.9 | 16.1 | 0
2498 | TORONTO BUTTONVILLE A | 4 | 15 | 2 | 1.825 | 16.175 | 0
2499 | TORONTO BUTTONVILLE A | 4 | 14 | 3 | 0.5 | 17.5 | 0
2499 | TORONTO BUTTONVILLE A | 4 | 15 | 3 | 1.725 | 16.275 | 0
2500 | TORONTO BUTTONVILLE A | 4 | 14 | 4 | 0 | 18 | 0
2500 | TORONTO BUTTONVILLE A | 4 | 15 | 4 | 1.575 | 16.425 | 0
2501 | TORONTO BUTTONVILLE A | 4 | 14 | 5 | -0.2 | 18.2 | 0
2501 | TORONTO BUTTONVILLE A | 4 | 15 | 5 | 1.5 | 16.5 | 0
2502 | TORONTO BUTTONVILLE A | 4 | 14 | 6 | -0.6 | 18.6 | 0
2502 | TORONTO BUTTONVILLE A | 4 | 15 | 6 | 1.625 | 16.375 | 0
2503 | TORONTO BUTTONVILLE A | 4 | 14 | 7 | -0.6 | 18.6 | 0
2503 | TORONTO BUTTONVILLE A | 4 | 15 | 7 | 1.625 | 16.375 | 0
2504 | TORONTO BUTTONVILLE A | 4 | 14 | 8 | 0.5 | 17.5 | 0
2504 | TORONTO BUTTONVILLE A | 4 | 15 | 8 | 2.1 | 15.9 | 0
2505 | TORONTO BUTTONVILLE A | 4 | 14 | 9 | 1.8 | 16.2 | 0
2505 | TORONTO BUTTONVILLE A | 4 | 15 | 9 | 2.45 | 15.55 | 0
2506 | TORONTO BUTTONVILLE A | 4 | 14 | 10 | 2.6 | 15.4 | 0
2506 | TORONTO BUTTONVILLE A | 4 | 15 | 10 | 2.525 | 15.475 | 0
2507 | TORONTO BUTTONVILLE A | 4 | 14 | 11 | 4 | 14 | 0
2507 | TORONTO BUTTONVILLE A | 4 | 15 | 11 | 2.55 | 15.45 | 0
2508 | TORONTO BUTTONVILLE A | 4 | 14 | 12 | 4.8 | 13.2 | 0
2508 | TORONTO BUTTONVILLE A | 4 | 15 | 12 | 2.825 | 15.175 | 0
2509 | TORONTO BUTTONVILLE A | 4 | 14 | 13 | 4.6 | 13.4 | 0
2509 | TORONTO BUTTONVILLE A | 4 | 15 | 13 | 3.125 | 14.875 | 0
2510 | TORONTO BUTTONVILLE A | 4 | 14 | 14 | 5 | 13 | 0
2510 | TORONTO BUTTONVILLE A | 4 | 15 | 14 | 3.85 | 14.15 | 0
2511 | TORONTO BUTTONVILLE A | 4 | 14 | 15 | 5.1 | 12.9 | 0
2511 | TORONTO BUTTONVILLE A | 4 | 15 | 15 | 4.575 | 13.425 | 0
2512 | TORONTO BUTTONVILLE A | 4 | 14 | 16 | 5.3 | 12.7 | 0
2512 | TORONTO BUTTONVILLE A | 4 | 15 | 16 | 5.725 | 12.275 | 0
2513 | TORONTO BUTTONVILLE A | 4 | 14 | 17 | 4 | 14 | 0
2513 | TORONTO BUTTONVILLE A | 4 | 15 | 17 | 6.975 | 11.025 | 0
2514 | TORONTO BUTTONVILLE A | 4 | 14 | 18 | 3.7 | 14.3 | 0
2514 | TORONTO BUTTONVILLE A | 4 | 15 | 18 | 7.625 | 10.375 | 0
2515 | TORONTO BUTTONVILLE A | 4 | 14 | 19 | 2.6 | 15.4 | 0
2515 | TORONTO BUTTONVILLE A | 4 | 15 | 19 | 7.5 | 10.5 | 0
2516 | TORONTO BUTTONVILLE A | 4 | 14 | 20 | 1.8 | 16.2 | 0
2516 | TORONTO BUTTONVILLE A | 4 | 15 | 20 | 6.525 | 11.475 | 0
2517 | TORONTO BUTTONVILLE A | 4 | 14 | 21 | 1.7 | 16.3 | 0
2517 | TORONTO BUTTONVILLE A | 4 | 15 | 21 | 5.875 | 12.125 | 0
2518 | TORONTO BUTTONVILLE A | 4 | 14 | 22 | 0.5 | 17.5 | 0
2518 | TORONTO BUTTONVILLE A | 4 | 15 | 22 | 4.775 | 13.225 | 0
2519 | TORONTO BUTTONVILLE A | 4 | 14 | 23 | -0.1 | 18.1 | 0
2519 | TORONTO BUTTONVILLE A | 4 | 15 | 23 | 5.025 | 12.975 | 0
2520 | TORONTO BUTTONVILLE A | 4 | 14 | 24 | -0.7 | 18.7 | 0
2520 | TORONTO BUTTONVILLE A | 4 | 15 | 24 | 5.175 | 12.825 | 0
2521 | TORONTO BUTTONVILLE A | 4 | 15 | 1 | -1.1 | 19.1 | 0
2521 | TORONTO BUTTONVILLE A | 4 | 16 | 1 | 4.625 | 13.375 | 0
2522 | TORONTO BUTTONVILLE A | 4 | 15 | 2 | -1.4 | 19.4 | 0
2522 | TORONTO BUTTONVILLE A | 4 | 16 | 2 | 5.85 | 12.15 | 0
2523 | TORONTO BUTTONVILLE A | 4 | 15 | 3 | -2 | 20 | 0
2523 | TORONTO BUTTONVILLE A | 4 | 16 | 3 | 6.225 | 11.775 | 0
2524 | TORONTO BUTTONVILLE A | 4 | 15 | 4 | -2.5 | 20.5 | 0
2524 | TORONTO BUTTONVILLE A | 4 | 16 | 4 | 6.1 | 11.9 | 0
2525 | TORONTO BUTTONVILLE A | 4 | 15 | 5 | -2.9 | 20.9 | 0
2525 | TORONTO BUTTONVILLE A | 4 | 16 | 5 | 5.525 | 12.475 | 0
2526 | TORONTO BUTTONVILLE A | 4 | 15 | 6 | -2.9 | 20.9 | 0
2526 | TORONTO BUTTONVILLE A | 4 | 16 | 6 | 5.35 | 12.65 | 0
2527 | TORONTO BUTTONVILLE A | 4 | 15 | 7 | -2.8 | 20.8 | 0
2527 | TORONTO BUTTONVILLE A | 4 | 16 | 7 | 4.75 | 13.25 | 0
2528 | TORONTO BUTTONVILLE A | 4 | 15 | 8 | -1.5 | 19.5 | 0
2528 | TORONTO BUTTONVILLE A | 4 | 16 | 8 | 6 | 12 | 0
2529 | TORONTO BUTTONVILLE A | 4 | 15 | 9 | 0 | 18 | 0
2529 | TORONTO BUTTONVILLE A | 4 | 16 | 9 | 6.75 | 11.25 | 0
2530 | TORONTO BUTTONVILLE A | 4 | 15 | 10 | -0.2 | 18.2 | 0
2530 | TORONTO BUTTONVILLE A | 4 | 16 | 10 | 7.675 | 10.325 | 0
2531 | TORONTO BUTTONVILLE A | 4 | 15 | 11 | -1.3 | 19.3 | 0
2531 | TORONTO BUTTONVILLE A | 4 | 16 | 11 | 8.45 | 9.55 | 0
2532 | TORONTO BUTTONVILLE A | 4 | 15 | 12 | 0.8 | 17.2 | 0
2532 | TORONTO BUTTONVILLE A | 4 | 16 | 12 | 9.275 | 8.725 | 0
2533 | TORONTO BUTTONVILLE A | 4 | 15 | 13 | 1.8 | 16.2 | 0
2533 | TORONTO BUTTONVILLE A | 4 | 16 | 13 | 9.425 | 8.575 | 0
2534 | TORONTO BUTTONVILLE A | 4 | 15 | 14 | 3.1 | 14.9 | 0
2534 | TORONTO BUTTONVILLE A | 4 | 16 | 14 | 9.525 | 8.475 | 0
2535 | TORONTO BUTTONVILLE A | 4 | 15 | 15 | 2.3 | 15.7 | 0
2535 | TORONTO BUTTONVILLE A | 4 | 16 | 15 | 9.225 | 8.775 | 0
2536 | TORONTO BUTTONVILLE A | 4 | 15 | 16 | 2.6 | 15.4 | 0
2536 | TORONTO BUTTONVILLE A | 4 | 16 | 16 | 9.05 | 8.95 | 0
2537 | TORONTO BUTTONVILLE A | 4 | 15 | 17 | 1.9 | 16.1 | 0
2537 | TORONTO BUTTONVILLE A | 4 | 16 | 17 | 8.575 | 9.425 | 0
2538 | TORONTO BUTTONVILLE A | 4 | 15 | 18 | 1.3 | 16.7 | 0
2538 | TORONTO BUTTONVILLE A | 4 | 16 | 18 | 8.275 | 9.725 | 0
2539 | TORONTO BUTTONVILLE A | 4 | 15 | 19 | 1 | 17 | 0
2539 | TORONTO BUTTONVILLE A | 4 | 16 | 19 | 8 | 10 | 0
2540 | TORONTO BUTTONVILLE A | 4 | 15 | 20 | -0.4 | 18.4 | 0
2540 | TORONTO BUTTONVILLE A | 4 | 16 | 20 | 7.45 | 10.55 | 0
2541 | TORONTO BUTTONVILLE A | 4 | 15 | 21 | -1.1 | 19.1 | 0
2541 | TORONTO BUTTONVILLE A | 4 | 16 | 21 | 6.5 | 11.5 | 0
2542 | TORONTO BUTTONVILLE A | 4 | 15 | 22 | -1.2 | 19.2 | 0
2542 | TORONTO BUTTONVILLE A | 4 | 16 | 22 | 5.625 | 12.375 | 0
2543 | TORONTO BUTTONVILLE A | 4 | 15 | 23 | -1.5 | 19.5 | 0
2543 | TORONTO BUTTONVILLE A | 4 | 16 | 23 | 5.475 | 12.525 | 0
2544 | TORONTO BUTTONVILLE A | 4 | 15 | 24 | -1.9 | 19.9 | 0
2544 | TORONTO BUTTONVILLE A | 4 | 16 | 24 | 4.775 | 13.225 | 0
2545 | TORONTO BUTTONVILLE A | 4 | 16 | 1 | -2.6 | 20.6 | 0
2545 | TORONTO BUTTONVILLE A | 4 | 17 | 1 | 4.1 | 13.9 | 0
2546 | TORONTO BUTTONVILLE A | 4 | 16 | 2 | -2.9 | 20.9 | 0
2546 | TORONTO BUTTONVILLE A | 4 | 17 | 2 | 4.8333 | 13.1667 | 0
2547 | TORONTO BUTTONVILLE A | 4 | 16 | 3 | -3.1 | 21.1 | 0
2547 | TORONTO BUTTONVILLE A | 4 | 17 | 3 | 4.2667 | 13.7333 | 0
2548 | TORONTO BUTTONVILLE A | 4 | 16 | 4 | -3.3 | 21.3 | 0
2548 | TORONTO BUTTONVILLE A | 4 | 17 | 4 | 3.8667 | 14.1333 | 0
2549 | TORONTO BUTTONVILLE A | 4 | 16 | 5 | -3.5 | 21.5 | 0
2549 | TORONTO BUTTONVILLE A | 4 | 17 | 5 | 3.3 | 14.7 | 0
2550 | TORONTO BUTTONVILLE A | 4 | 16 | 6 | -3.7 | 21.7 | 0
2550 | TORONTO BUTTONVILLE A | 4 | 17 | 6 | 2.3 | 15.7 | 0
2551 | TORONTO BUTTONVILLE A | 4 | 16 | 7 | -3.1 | 21.1 | 0
2551 | TORONTO BUTTONVILLE A | 4 | 17 | 7 | 2.8 | 15.2 | 0
2552 | TORONTO BUTTONVILLE A | 4 | 16 | 8 | -1.8 | 19.8 | 0
2552 | TORONTO BUTTONVILLE A | 4 | 17 | 8 | 4.3667 | 13.6333 | 0
2553 | TORONTO BUTTONVILLE A | 4 | 16 | 9 | -0.2 | 18.2 | 0
2553 | TORONTO BUTTONVILLE A | 4 | 17 | 9 | 4.275 | 13.725 | 0
2554 | TORONTO BUTTONVILLE A | 4 | 16 | 10 | 0.8 | 17.2 | 0
2554 | TORONTO BUTTONVILLE A | 4 | 17 | 10 | 5.15 | 12.85 | 0
2555 | TORONTO BUTTONVILLE A | 4 | 16 | 11 | 1.6 | 16.4 | 0
2555 | TORONTO BUTTONVILLE A | 4 | 17 | 11 | 5.65 | 12.35 | 0
2556 | TORONTO BUTTONVILLE A | 4 | 16 | 12 | 2.4 | 15.6 | 0
2556 | TORONTO BUTTONVILLE A | 4 | 17 | 12 | 5.975 | 12.025 | 0
2557 | TORONTO BUTTONVILLE A | 4 | 16 | 13 | 2 | 16 | 0
2557 | TORONTO BUTTONVILLE A | 4 | 17 | 13 | 7.025 | 10.975 | 0
2558 | TORONTO BUTTONVILLE A | 4 | 16 | 14 | 2 | 16 | 0
2558 | TORONTO BUTTONVILLE A | 4 | 17 | 14 | 7.425 | 10.575 | 0
2559 | TORONTO BUTTONVILLE A | 4 | 16 | 15 | 0.3 | 17.7 | 0
2559 | TORONTO BUTTONVILLE A | 4 | 17 | 15 | 8.025 | 9.975 | 0
2560 | TORONTO BUTTONVILLE A | 4 | 16 | 16 | 1.1 | 16.9 | 0
2560 | TORONTO BUTTONVILLE A | 4 | 17 | 16 | 8.55 | 9.45 | 0
2561 | TORONTO BUTTONVILLE A | 4 | 16 | 17 | 2.9 | 15.1 | 0
2561 | TORONTO BUTTONVILLE A | 4 | 17 | 17 | 8.7 | 9.3 | 0
2562 | TORONTO BUTTONVILLE A | 4 | 16 | 18 | 2.6 | 15.4 | 0
2562 | TORONTO BUTTONVILLE A | 4 | 17 | 18 | 8.45 | 9.55 | 0
2563 | TORONTO BUTTONVILLE A | 4 | 16 | 19 | 2.5 | 15.5 | 0
2563 | TORONTO BUTTONVILLE A | 4 | 17 | 19 | 7.525 | 10.475 | 0
2564 | TORONTO BUTTONVILLE A | 4 | 16 | 20 | 1.2 | 16.8 | 0
2564 | TORONTO BUTTONVILLE A | 4 | 17 | 20 | 6.15 | 11.85 | 0
2565 | TORONTO BUTTONVILLE A | 4 | 16 | 21 | 1.3 | 16.7 | 0
2565 | TORONTO BUTTONVILLE A | 4 | 17 | 21 | 5.45 | 12.55 | 0
2566 | TORONTO BUTTONVILLE A | 4 | 16 | 22 | 1 | 17 | 0
2566 | TORONTO BUTTONVILLE A | 4 | 17 | 22 | 5.25 | 12.75 | 0
2567 | TORONTO BUTTONVILLE A | 4 | 16 | 23 | 0.2 | 17.8 | 0
2567 | TORONTO BUTTONVILLE A | 4 | 17 | 23 | 4.6 | 13.4 | 0
2568 | TORONTO BUTTONVILLE A | 4 | 16 | 24 | -0.4 | 18.4 | 0
2568 | TORONTO BUTTONVILLE A | 4 | 17 | 24 | 4.2 | 13.8 | 0
2569 | TORONTO BUTTONVILLE A | 4 | 17 | 1 | -0.9 | 18.9 | 0
2569 | TORONTO BUTTONVILLE A | 4 | 18 | 1 | 3.5 | 14.5 | 0
2570 | TORONTO BUTTONVILLE A | 4 | 17 | 2 | -1.2 | 19.2 | 0
2570 | TORONTO BUTTONVILLE A | 4 | 18 | 2 | 3.225 | 14.775 | 0
2571 | TORONTO BUTTONVILLE A | 4 | 17 | 3 | -1.4 | 19.4 | 0
2571 | TORONTO BUTTONVILLE A | 4 | 18 | 3 | 3.025 | 14.975 | 0
2572 | TORONTO BUTTONVILLE A | 4 | 17 | 4 | -1.7 | 19.7 | 0
2572 | TORONTO BUTTONVILLE A | 4 | 18 | 4 | 2.825 | 15.175 | 0
2573 | TORONTO BUTTONVILLE A | 4 | 17 | 5 | -1.8 | 19.8 | 0
2573 | TORONTO BUTTONVILLE A | 4 | 18 | 5 | 2.35 | 15.65 | 0
2574 | TORONTO BUTTONVILLE A | 4 | 17 | 6 | -2 | 20 | 0
2574 | TORONTO BUTTONVILLE A | 4 | 18 | 6 | 2.35 | 15.65 | 0
2575 | TORONTO BUTTONVILLE A | 4 | 17 | 7 | -1.6 | 19.6 | 0
2575 | TORONTO BUTTONVILLE A | 4 | 18 | 7 | 3.125 | 14.875 | 0
2576 | TORONTO BUTTONVILLE A | 4 | 17 | 8 | -0.5 | 18.5 | 0
2576 | TORONTO BUTTONVILLE A | 4 | 18 | 8 | 4.5 | 13.5 | 0
2577 | TORONTO BUTTONVILLE A | 4 | 17 | 9 | 1.4 | 16.6 | 0
2577 | TORONTO BUTTONVILLE A | 4 | 18 | 9 | 5.7 | 12.3 | 0
2578 | TORONTO BUTTONVILLE A | 4 | 17 | 10 | 3.5 | 14.5 | 0
2578 | TORONTO BUTTONVILLE A | 4 | 18 | 10 | 7.95 | 10.05 | 0
2579 | TORONTO BUTTONVILLE A | 4 | 17 | 11 | 4.4 | 13.6 | 0
2579 | TORONTO BUTTONVILLE A | 4 | 18 | 11 | 8.9 | 9.1 | 0
2580 | TORONTO BUTTONVILLE A | 4 | 17 | 12 | 5.6 | 12.4 | 0
2580 | TORONTO BUTTONVILLE A | 4 | 18 | 12 | 9.85 | 8.15 | 0
2581 | TORONTO BUTTONVILLE A | 4 | 17 | 13 | 5.7 | 12.3 | 0
2581 | TORONTO BUTTONVILLE A | 4 | 18 | 13 | 9.95 | 8.05 | 0
2582 | TORONTO BUTTONVILLE A | 4 | 17 | 14 | 6.1 | 11.9 | 0
2582 | TORONTO BUTTONVILLE A | 4 | 18 | 14 | 10.3 | 7.7 | 0
2583 | TORONTO BUTTONVILLE A | 4 | 17 | 15 | 5.6 | 12.4 | 0
2583 | TORONTO BUTTONVILLE A | 4 | 18 | 15 | 10.975 | 7.025 | 0
2584 | TORONTO BUTTONVILLE A | 4 | 17 | 16 | 5.1 | 12.9 | 0
2584 | TORONTO BUTTONVILLE A | 4 | 18 | 16 | 11.225 | 6.775 | 0
2585 | TORONTO BUTTONVILLE A | 4 | 17 | 17 | 4.2 | 13.8 | 0
2585 | TORONTO BUTTONVILLE A | 4 | 18 | 17 | 10.85 | 7.15 | 0
2586 | TORONTO BUTTONVILLE A | 4 | 17 | 18 | 2.7 | 15.3 | 0
2586 | TORONTO BUTTONVILLE A | 4 | 18 | 18 | 10.5 | 7.5 | 0
2587 | TORONTO BUTTONVILLE A | 4 | 17 | 19 | 2.2 | 15.8 | 0
2587 | TORONTO BUTTONVILLE A | 4 | 18 | 19 | 9.85 | 8.15 | 0
2588 | TORONTO BUTTONVILLE A | 4 | 17 | 20 | 2 | 16 | 0
2588 | TORONTO BUTTONVILLE A | 4 | 18 | 20 | 8.8 | 9.2 | 0
2589 | TORONTO BUTTONVILLE A | 4 | 17 | 21 | 1.5 | 16.5 | 0
2589 | TORONTO BUTTONVILLE A | 4 | 18 | 21 | 8.15 | 9.85 | 0
2590 | TORONTO BUTTONVILLE A | 4 | 17 | 22 | 1.5 | 16.5 | 0
2590 | TORONTO BUTTONVILLE A | 4 | 18 | 22 | 7.825 | 10.175 | 0
2591 | TORONTO BUTTONVILLE A | 4 | 17 | 23 | 1.2 | 16.8 | 0
2591 | TORONTO BUTTONVILLE A | 4 | 18 | 23 | 7.35 | 10.65 | 0
2592 | TORONTO BUTTONVILLE A | 4 | 17 | 24 | -0.3 | 18.3 | 0
2592 | TORONTO BUTTONVILLE A | 4 | 18 | 24 | 7.05 | 10.95 | 0
2593 | TORONTO BUTTONVILLE A | 4 | 18 | 1 | -1 | 19 | 0
2593 | TORONTO BUTTONVILLE A | 4 | 19 | 1 | 6.2 | 11.8 | 0
2594 | TORONTO BUTTONVILLE A | 4 | 18 | 2 | -1.2 | 19.2 | 0
2594 | TORONTO BUTTONVILLE A | 4 | 19 | 2 | 5.625 | 12.375 | 0
2595 | TORONTO BUTTONVILLE A | 4 | 18 | 3 | -1.2 | 19.2 | 0
2595 | TORONTO BUTTONVILLE A | 4 | 19 | 3 | 5.375 | 12.625 | 0
2596 | TORONTO BUTTONVILLE A | 4 | 18 | 4 | -0.9 | 18.9 | 0
2596 | TORONTO BUTTONVILLE A | 4 | 19 | 4 | 4.975 | 13.025 | 0
2597 | TORONTO BUTTONVILLE A | 4 | 18 | 5 | -1.6 | 19.6 | 0
2597 | TORONTO BUTTONVILLE A | 4 | 19 | 5 | 4.925 | 13.075 | 0
2598 | TORONTO BUTTONVILLE A | 4 | 18 | 6 | -2.6 | 20.6 | 0
2598 | TORONTO BUTTONVILLE A | 4 | 19 | 6 | 4.425 | 13.575 | 0
2599 | TORONTO BUTTONVILLE A | 4 | 18 | 7 | -2.6 | 20.6 | 0
2599 | TORONTO BUTTONVILLE A | 4 | 19 | 7 | 4.125 | 13.875 | 0
2600 | TORONTO BUTTONVILLE A | 4 | 18 | 8 | 0.2 | 17.8 | 0
2600 | TORONTO BUTTONVILLE A | 4 | 19 | 8 | 5.15 | 12.85 | 0
2601 | TORONTO BUTTONVILLE A | 4 | 18 | 9 | 2 | 16 | 0
2601 | TORONTO BUTTONVILLE A | 4 | 19 | 9 | 6.325 | 11.675 | 0
2602 | TORONTO BUTTONVILLE A | 4 | 18 | 10 | 4.6 | 13.4 | 0
2602 | TORONTO BUTTONVILLE A | 4 | 19 | 10 | 7.175 | 10.825 | 0
2603 | TORONTO BUTTONVILLE A | 4 | 18 | 11 | 6 | 12 | 0
2603 | TORONTO BUTTONVILLE A | 4 | 19 | 11 | 8.725 | 9.275 | 0
2604 | TORONTO BUTTONVILLE A | 4 | 18 | 12 | 7 | 11 | 0
2604 | TORONTO BUTTONVILLE A | 4 | 19 | 12 | 9.225 | 8.775 | 0
2605 | TORONTO BUTTONVILLE A | 4 | 18 | 13 | 7 | 11 | 0
2605 | TORONTO BUTTONVILLE A | 4 | 19 | 13 | 9.825 | 8.175 | 0
2606 | TORONTO BUTTONVILLE A | 4 | 18 | 14 | 9.2 | 8.8 | 0
2606 | TORONTO BUTTONVILLE A | 4 | 19 | 14 | 10.15 | 7.85 | 0
2607 | TORONTO BUTTONVILLE A | 4 | 18 | 15 | 9 | 9 | 0
2607 | TORONTO BUTTONVILLE A | 4 | 19 | 15 | 10.125 | 7.875 | 0
2608 | TORONTO BUTTONVILLE A | 4 | 18 | 16 | 9.1 | 8.9 | 0
2608 | TORONTO BUTTONVILLE A | 4 | 19 | 16 | 10.85 | 7.15 | 0
2609 | TORONTO BUTTONVILLE A | 4 | 18 | 17 | 9.5 | 8.5 | 0
2609 | TORONTO BUTTONVILLE A | 4 | 19 | 17 | 10.875 | 7.125 | 0
2610 | TORONTO BUTTONVILLE A | 4 | 18 | 18 | 8.1 | 9.9 | 0
2610 | TORONTO BUTTONVILLE A | 4 | 19 | 18 | 10.775 | 7.225 | 0
2611 | TORONTO BUTTONVILLE A | 4 | 18 | 19 | 8.7 | 9.3 | 0
2611 | TORONTO BUTTONVILLE A | 4 | 19 | 19 | 9.225 | 8.775 | 0
2612 | TORONTO BUTTONVILLE A | 4 | 18 | 20 | 7.8 | 10.2 | 0
2612 | TORONTO BUTTONVILLE A | 4 | 19 | 20 | 7.75 | 10.25 | 0
2613 | TORONTO BUTTONVILLE A | 4 | 18 | 21 | 7.1 | 10.9 | 0
2613 | TORONTO BUTTONVILLE A | 4 | 19 | 21 | 6.775 | 11.225 | 0
2614 | TORONTO BUTTONVILLE A | 4 | 18 | 22 | 6.3 | 11.7 | 0
2614 | TORONTO BUTTONVILLE A | 4 | 19 | 22 | 5.975 | 12.025 | 0
2615 | TORONTO BUTTONVILLE A | 4 | 18 | 23 | 5.8 | 12.2 | 0
2615 | TORONTO BUTTONVILLE A | 4 | 19 | 23 | 5.275 | 12.725 | 0
2616 | TORONTO BUTTONVILLE A | 4 | 18 | 24 | 5.8 | 12.2 | 0
2616 | TORONTO BUTTONVILLE A | 4 | 19 | 24 | 4.775 | 13.225 | 0
2617 | TORONTO BUTTONVILLE A | 4 | 19 | 1 | 5.4 | 12.6 | 0
2617 | TORONTO BUTTONVILLE A | 4 | 20 | 1 | 4.475 | 13.525 | 0
2618 | TORONTO BUTTONVILLE A | 4 | 19 | 2 | 5.3 | 12.7 | 0
2618 | TORONTO BUTTONVILLE A | 4 | 20 | 2 | 3.775 | 14.225 | 0
2619 | TORONTO BUTTONVILLE A | 4 | 19 | 3 | 6.4 | 11.6 | 0
2619 | TORONTO BUTTONVILLE A | 4 | 20 | 3 | 3.5 | 14.5 | 0
2620 | TORONTO BUTTONVILLE A | 4 | 19 | 4 | 6.6 | 11.4 | 0
2620 | TORONTO BUTTONVILLE A | 4 | 20 | 4 | 3.3 | 14.7 | 0
2621 | TORONTO BUTTONVILLE A | 4 | 19 | 5 | 6.8 | 11.2 | 0
2621 | TORONTO BUTTONVILLE A | 4 | 20 | 5 | 3.4 | 14.6 | 0
2622 | TORONTO BUTTONVILLE A | 4 | 19 | 6 | 6.6 | 11.4 | 0
2622 | TORONTO BUTTONVILLE A | 4 | 20 | 6 | 3.1 | 14.9 | 0
2623 | TORONTO BUTTONVILLE A | 4 | 19 | 7 | 7 | 11 | 0
2623 | TORONTO BUTTONVILLE A | 4 | 20 | 7 | 2.85 | 15.15 | 0
2624 | TORONTO BUTTONVILLE A | 4 | 19 | 8 | 7.3 | 10.7 | 0
2624 | TORONTO BUTTONVILLE A | 4 | 20 | 8 | 3.1 | 14.9 | 0
2625 | TORONTO BUTTONVILLE A | 4 | 19 | 9 | 7 | 11 | 0
2625 | TORONTO BUTTONVILLE A | 4 | 20 | 9 | 3.425 | 14.575 | 0
2626 | TORONTO BUTTONVILLE A | 4 | 19 | 10 | 6.2 | 11.8 | 0
2626 | TORONTO BUTTONVILLE A | 4 | 20 | 10 | 3.925 | 14.075 | 0
2627 | TORONTO BUTTONVILLE A | 4 | 19 | 11 | 6.7 | 11.3 | 0
2627 | TORONTO BUTTONVILLE A | 4 | 20 | 11 | 4.2 | 13.8 | 0
2628 | TORONTO BUTTONVILLE A | 4 | 19 | 12 | 7.6 | 10.4 | 0
2628 | TORONTO BUTTONVILLE A | 4 | 20 | 12 | 4.425 | 13.575 | 0
2629 | TORONTO BUTTONVILLE A | 4 | 19 | 13 | 9.2 | 8.8 | 0
2629 | TORONTO BUTTONVILLE A | 4 | 20 | 13 | 4.725 | 13.275 | 0
2630 | TORONTO BUTTONVILLE A | 4 | 19 | 14 | 10.3 | 7.7 | 0
2630 | TORONTO BUTTONVILLE A | 4 | 20 | 14 | 5.25 | 12.75 | 0
2631 | TORONTO BUTTONVILLE A | 4 | 19 | 15 | 11.6 | 6.4 | 0
2631 | TORONTO BUTTONVILLE A | 4 | 20 | 15 | 5.475 | 12.525 | 0
2632 | TORONTO BUTTONVILLE A | 4 | 19 | 16 | 9.4 | 8.6 | 0
2632 | TORONTO BUTTONVILLE A | 4 | 20 | 16 | 5.6 | 12.4 | 0
2633 | TORONTO BUTTONVILLE A | 4 | 19 | 17 | 7.3 | 10.7 | 0
2633 | TORONTO BUTTONVILLE A | 4 | 20 | 17 | 5.5 | 12.5 | 0
2634 | TORONTO BUTTONVILLE A | 4 | 19 | 18 | 6.1 | 11.9 | 0
2634 | TORONTO BUTTONVILLE A | 4 | 20 | 18 | 5.45 | 12.55 | 0
2635 | TORONTO BUTTONVILLE A | 4 | 19 | 19 | 5.2 | 12.8 | 0
2635 | TORONTO BUTTONVILLE A | 4 | 20 | 19 | 5.225 | 12.775 | 0
2636 | TORONTO BUTTONVILLE A | 4 | 19 | 20 | 3.4 | 14.6 | 0
2636 | TORONTO BUTTONVILLE A | 4 | 20 | 20 | 4.925 | 13.075 | 0
2637 | TORONTO BUTTONVILLE A | 4 | 19 | 21 | 2.2 | 15.8 | 0
2637 | TORONTO BUTTONVILLE A | 4 | 20 | 21 | 4.6 | 13.4 | 0
2638 | TORONTO BUTTONVILLE A | 4 | 19 | 22 | 1.5 | 16.5 | 0
2638 | TORONTO BUTTONVILLE A | 4 | 20 | 22 | 4.25 | 13.75 | 0
2639 | TORONTO BUTTONVILLE A | 4 | 19 | 23 | 0.8 | 17.2 | 0
2639 | TORONTO BUTTONVILLE A | 4 | 20 | 23 | 3.875 | 14.125 | 0
2640 | TORONTO BUTTONVILLE A | 4 | 19 | 24 | 0.3 | 17.7 | 0
2640 | TORONTO BUTTONVILLE A | 4 | 20 | 24 | 3.975 | 14.025 | 0
2641 | TORONTO BUTTONVILLE A | 4 | 20 | 1 | -0.4 | 18.4 | 0
2641 | TORONTO BUTTONVILLE A | 4 | 21 | 1 | 3.925 | 14.075 | 0
2642 | TORONTO BUTTONVILLE A | 4 | 20 | 2 | -1.2 | 19.2 | 0
2642 | TORONTO BUTTONVILLE A | 4 | 21 | 2 | 3.275 | 14.725 | 0
2643 | TORONTO BUTTONVILLE A | 4 | 20 | 3 | -2 | 20 | 0
2643 | TORONTO BUTTONVILLE A | 4 | 21 | 3 | 2.9 | 15.1 | 0
2644 | TORONTO BUTTONVILLE A | 4 | 20 | 4 | -3 | 21 | 0
2644 | TORONTO BUTTONVILLE A | 4 | 21 | 4 | 2.775 | 15.225 | 0
2645 | TORONTO BUTTONVILLE A | 4 | 20 | 5 | -3.2 | 21.2 | 0
2645 | TORONTO BUTTONVILLE A | 4 | 21 | 5 | 2.4 | 15.6 | 0
2646 | TORONTO BUTTONVILLE A | 4 | 20 | 6 | -3.5 | 21.5 | 0
2646 | TORONTO BUTTONVILLE A | 4 | 21 | 6 | 2.275 | 15.725 | 0
2647 | TORONTO BUTTONVILLE A | 4 | 20 | 7 | -3.7 | 21.7 | 0
2647 | TORONTO BUTTONVILLE A | 4 | 21 | 7 | 2.25 | 15.75 | 0
2648 | TORONTO BUTTONVILLE A | 4 | 20 | 8 | -0.6 | 18.6 | 0
2648 | TORONTO BUTTONVILLE A | 4 | 21 | 8 | 3.875 | 14.125 | 0
2649 | TORONTO BUTTONVILLE A | 4 | 20 | 9 | 1.4 | 16.6 | 0
2649 | TORONTO BUTTONVILLE A | 4 | 21 | 9 | 5.525 | 12.475 | 0
2650 | TORONTO BUTTONVILLE A | 4 | 20 | 10 | 2.2 | 15.8 | 0
2650 | TORONTO BUTTONVILLE A | 4 | 21 | 10 | 6.325 | 11.675 | 0
2651 | TORONTO BUTTONVILLE A | 4 | 20 | 11 | 3.1 | 14.9 | 0
2651 | TORONTO BUTTONVILLE A | 4 | 21 | 11 | 7.375 | 10.625 | 0
2652 | TORONTO BUTTONVILLE A | 4 | 20 | 12 | 3.8 | 14.2 | 0
2652 | TORONTO BUTTONVILLE A | 4 | 21 | 12 | 7.875 | 10.125 | 0
2653 | TORONTO BUTTONVILLE A | 4 | 20 | 13 | 4.3 | 13.7 | 0
2653 | TORONTO BUTTONVILLE A | 4 | 21 | 13 | 8.8 | 9.2 | 0
2654 | TORONTO BUTTONVILLE A | 4 | 20 | 14 | 5.2 | 12.8 | 0
2654 | TORONTO BUTTONVILLE A | 4 | 21 | 14 | 9.275 | 8.725 | 0
2655 | TORONTO BUTTONVILLE A | 4 | 20 | 15 | 5.7 | 12.3 | 0
2655 | TORONTO BUTTONVILLE A | 4 | 21 | 15 | 9.625 | 8.375 | 0
2656 | TORONTO BUTTONVILLE A | 4 | 20 | 16 | 7 | 11 | 0
2656 | TORONTO BUTTONVILLE A | 4 | 21 | 16 | 9.75 | 8.25 | 0
2657 | TORONTO BUTTONVILLE A | 4 | 20 | 17 | 6.1 | 11.9 | 0
2657 | TORONTO BUTTONVILLE A | 4 | 21 | 17 | 9.675 | 8.325 | 0
2658 | TORONTO BUTTONVILLE A | 4 | 20 | 18 | 6.8 | 11.2 | 0
2658 | TORONTO BUTTONVILLE A | 4 | 21 | 18 | 8.6 | 9.4 | 0
2659 | TORONTO BUTTONVILLE A | 4 | 20 | 19 | 5.1 | 12.9 | 0
2659 | TORONTO BUTTONVILLE A | 4 | 21 | 19 | 7.8 | 10.2 | 0
2660 | TORONTO BUTTONVILLE A | 4 | 20 | 20 | 3.4 | 14.6 | 0
2660 | TORONTO BUTTONVILLE A | 4 | 21 | 20 | 6.725 | 11.275 | 0
2661 | TORONTO BUTTONVILLE A | 4 | 20 | 21 | 3.1 | 14.9 | 0
2661 | TORONTO BUTTONVILLE A | 4 | 21 | 21 | 6 | 12 | 0
2662 | TORONTO BUTTONVILLE A | 4 | 20 | 22 | 3.7 | 14.3 | 0
2662 | TORONTO BUTTONVILLE A | 4 | 21 | 22 | 5.25 | 12.75 | 0
2663 | TORONTO BUTTONVILLE A | 4 | 20 | 23 | 3.1 | 14.9 | 0
2663 | TORONTO BUTTONVILLE A | 4 | 21 | 23 | 4.65 | 13.35 | 0
2664 | TORONTO BUTTONVILLE A | 4 | 20 | 24 | 3.6 | 14.4 | 0
2664 | TORONTO BUTTONVILLE A | 4 | 21 | 24 | 4.3 | 13.7 | 0
2665 | TORONTO BUTTONVILLE A | 4 | 21 | 1 | 2.4 | 15.6 | 0
2665 | TORONTO BUTTONVILLE A | 4 | 22 | 1 | 3.35 | 14.65 | 0
2666 | TORONTO BUTTONVILLE A | 4 | 21 | 2 | 2.3 | 15.7 | 0
2666 | TORONTO BUTTONVILLE A | 4 | 22 | 2 | 2.775 | 15.225 | 0
2667 | TORONTO BUTTONVILLE A | 4 | 21 | 3 | 2.8 | 15.2 | 0
2667 | TORONTO BUTTONVILLE A | 4 | 22 | 3 | 2.5 | 15.5 | 0
2668 | TORONTO BUTTONVILLE A | 4 | 21 | 4 | 3.4 | 14.6 | 0
2668 | TORONTO BUTTONVILLE A | 4 | 22 | 4 | 2.225 | 15.775 | 0
2669 | TORONTO BUTTONVILLE A | 4 | 21 | 5 | 5.5 | 12.5 | 0
2669 | TORONTO BUTTONVILLE A | 4 | 22 | 5 | 1.95 | 16.05 | 0
2670 | TORONTO BUTTONVILLE A | 4 | 21 | 6 | 6.6 | 11.4 | 0
2670 | TORONTO BUTTONVILLE A | 4 | 22 | 6 | 2.1 | 15.9 | 0
2671 | TORONTO BUTTONVILLE A | 4 | 21 | 7 | 1.6 | 16.4 | 0
2671 | TORONTO BUTTONVILLE A | 4 | 22 | 7 | 2.225 | 15.775 | 0
2672 | TORONTO BUTTONVILLE A | 4 | 21 | 8 | 2.7 | 15.3 | 0
2672 | TORONTO BUTTONVILLE A | 4 | 22 | 8 | 3.75 | 14.25 | 0
2673 | TORONTO BUTTONVILLE A | 4 | 21 | 9 | 2.9 | 15.1 | 0
2673 | TORONTO BUTTONVILLE A | 4 | 22 | 9 | 5.35 | 12.65 | 0
2674 | TORONTO BUTTONVILLE A | 4 | 21 | 10 | 3.5 | 14.5 | 0
2674 | TORONTO BUTTONVILLE A | 4 | 22 | 10 | 6.8 | 11.2 | 0
2675 | TORONTO BUTTONVILLE A | 4 | 21 | 11 | 2.7 | 15.3 | 0
2675 | TORONTO BUTTONVILLE A | 4 | 22 | 11 | 8.3 | 9.7 | 0
2676 | TORONTO BUTTONVILLE A | 4 | 21 | 12 | 3.1 | 14.9 | 0
2676 | TORONTO BUTTONVILLE A | 4 | 22 | 12 | 9.85 | 8.15 | 0
2677 | TORONTO BUTTONVILLE A | 4 | 21 | 13 | 3.2 | 14.8 | 0
2677 | TORONTO BUTTONVILLE A | 4 | 22 | 13 | 10.45 | 7.55 | 0
2678 | TORONTO BUTTONVILLE A | 4 | 21 | 14 | 2.3 | 15.7 | 0
2678 | TORONTO BUTTONVILLE A | 4 | 22 | 14 | 11.475 | 6.525 | 0
2679 | TORONTO BUTTONVILLE A | 4 | 21 | 15 | 2.2 | 15.8 | 0
2679 | TORONTO BUTTONVILLE A | 4 | 22 | 15 | 11.9 | 6.1 | 0
2680 | TORONTO BUTTONVILLE A | 4 | 21 | 16 | 1 | 17 | 0
2680 | TORONTO BUTTONVILLE A | 4 | 22 | 16 | 12.075 | 5.925 | 0
2681 | TORONTO BUTTONVILLE A | 4 | 21 | 17 | 1.5 | 16.5 | 0
2681 | TORONTO BUTTONVILLE A | 4 | 22 | 17 | 12.275 | 5.725 | 0
2682 | TORONTO BUTTONVILLE A | 4 | 21 | 18 | 0.9 | 17.1 | 0
2682 | TORONTO BUTTONVILLE A | 4 | 22 | 18 | 11.9 | 6.1 | 0
2683 | TORONTO BUTTONVILLE A | 4 | 21 | 19 | 0.6 | 17.4 | 0
2683 | TORONTO BUTTONVILLE A | 4 | 22 | 19 | 11.375 | 6.625 | 0
2684 | TORONTO BUTTONVILLE A | 4 | 21 | 20 | 0.1 | 17.9 | 0
2684 | TORONTO BUTTONVILLE A | 4 | 22 | 20 | 10.025 | 7.975 | 0
2685 | TORONTO BUTTONVILLE A | 4 | 21 | 21 | -0.6 | 18.6 | 0
2685 | TORONTO BUTTONVILLE A | 4 | 22 | 21 | 8.75 | 9.25 | 0
2686 | TORONTO BUTTONVILLE A | 4 | 21 | 22 | -0.9 | 18.9 | 0
2686 | TORONTO BUTTONVILLE A | 4 | 22 | 22 | 7.475 | 10.525 | 0
2687 | TORONTO BUTTONVILLE A | 4 | 21 | 23 | -1.4 | 19.4 | 0
2687 | TORONTO BUTTONVILLE A | 4 | 22 | 23 | 6.55 | 11.45 | 0
2688 | TORONTO BUTTONVILLE A | 4 | 21 | 24 | -1.7 | 19.7 | 0
2688 | TORONTO BUTTONVILLE A | 4 | 22 | 24 | 5.575 | 12.425 | 0
2689 | TORONTO BUTTONVILLE A | 4 | 22 | 1 | -1.8 | 19.8 | 0
2689 | TORONTO BUTTONVILLE A | 4 | 23 | 1 | 5 | 13 | 0
2690 | TORONTO BUTTONVILLE A | 4 | 22 | 2 | -2 | 20 | 0
2690 | TORONTO BUTTONVILLE A | 4 | 23 | 2 | 4.6 | 13.4 | 0
2691 | TORONTO BUTTONVILLE A | 4 | 22 | 3 | -2.1 | 20.1 | 0
2691 | TORONTO BUTTONVILLE A | 4 | 23 | 3 | 3.85 | 14.15 | 0
2692 | TORONTO BUTTONVILLE A | 4 | 22 | 4 | -2.5 | 20.5 | 0
2692 | TORONTO BUTTONVILLE A | 4 | 23 | 4 | 3.1 | 14.9 | 0
2693 | TORONTO BUTTONVILLE A | 4 | 22 | 5 | -2.5 | 20.5 | 0
2693 | TORONTO BUTTONVILLE A | 4 | 23 | 5 | 3.1 | 14.9 | 0
2694 | TORONTO BUTTONVILLE A | 4 | 22 | 6 | -2.8 | 20.8 | 0
2694 | TORONTO BUTTONVILLE A | 4 | 23 | 6 | 2.9 | 15.1 | 0
2695 | TORONTO BUTTONVILLE A | 4 | 22 | 7 | -2.6 | 20.6 | 0
2695 | TORONTO BUTTONVILLE A | 4 | 23 | 7 | 3.325 | 14.675 | 0
2696 | TORONTO BUTTONVILLE A | 4 | 22 | 8 | -1.7 | 19.7 | 0
2696 | TORONTO BUTTONVILLE A | 4 | 23 | 8 | 6.05 | 11.95 | 0
2697 | TORONTO BUTTONVILLE A | 4 | 22 | 9 | -0.8 | 18.8 | 0
2697 | TORONTO BUTTONVILLE A | 4 | 23 | 9 | 9.225 | 8.775 | 0
2698 | TORONTO BUTTONVILLE A | 4 | 22 | 10 | -0.1 | 18.1 | 0
2698 | TORONTO BUTTONVILLE A | 4 | 23 | 10 | 11.375 | 6.625 | 0
2699 | TORONTO BUTTONVILLE A | 4 | 22 | 11 | 0.7 | 17.3 | 0
2699 | TORONTO BUTTONVILLE A | 4 | 23 | 11 | 12.725 | 5.275 | 0
2700 | TORONTO BUTTONVILLE A | 4 | 22 | 12 | 2 | 16 | 0
2700 | TORONTO BUTTONVILLE A | 4 | 23 | 12 | 13.725 | 4.275 | 0
2701 | TORONTO BUTTONVILLE A | 4 | 22 | 13 | 2 | 16 | 0
2701 | TORONTO BUTTONVILLE A | 4 | 23 | 13 | 15.125 | 2.875 | 0
2702 | TORONTO BUTTONVILLE A | 4 | 22 | 14 | 3 | 15 | 0
2702 | TORONTO BUTTONVILLE A | 4 | 23 | 14 | 15.325 | 2.675 | 0
2703 | TORONTO BUTTONVILLE A | 4 | 22 | 15 | 4.1 | 13.9 | 0
2703 | TORONTO BUTTONVILLE A | 4 | 23 | 15 | 15.85 | 2.15 | 0
2704 | TORONTO BUTTONVILLE A | 4 | 22 | 16 | 4.5 | 13.5 | 0
2704 | TORONTO BUTTONVILLE A | 4 | 23 | 16 | 16.175 | 1.825 | 0
2705 | TORONTO BUTTONVILLE A | 4 | 22 | 17 | 4.7 | 13.3 | 0
2705 | TORONTO BUTTONVILLE A | 4 | 23 | 17 | 16.675 | 1.325 | 0
2706 | TORONTO BUTTONVILLE A | 4 | 22 | 18 | 4.1 | 13.9 | 0
2706 | TORONTO BUTTONVILLE A | 4 | 23 | 18 | 15.85 | 2.15 | 0
2707 | TORONTO BUTTONVILLE A | 4 | 22 | 19 | 3.4 | 14.6 | 0
2707 | TORONTO BUTTONVILLE A | 4 | 23 | 19 | 14.6 | 3.4 | 0
2708 | TORONTO BUTTONVILLE A | 4 | 22 | 20 | 1.6 | 16.4 | 0
2708 | TORONTO BUTTONVILLE A | 4 | 23 | 20 | 12.75 | 5.25 | 0
2709 | TORONTO BUTTONVILLE A | 4 | 22 | 21 | 0.6 | 17.4 | 0
2709 | TORONTO BUTTONVILLE A | 4 | 23 | 21 | 11.6 | 6.4 | 0
2710 | TORONTO BUTTONVILLE A | 4 | 22 | 22 | -0.6 | 18.6 | 0
2710 | TORONTO BUTTONVILLE A | 4 | 23 | 22 | 10.425 | 7.575 | 0
2711 | TORONTO BUTTONVILLE A | 4 | 22 | 23 | -1.6 | 19.6 | 0
2711 | TORONTO BUTTONVILLE A | 4 | 23 | 23 | 9.025 | 8.975 | 0
2712 | TORONTO BUTTONVILLE A | 4 | 22 | 24 | -1.5 | 19.5 | 0
2712 | TORONTO BUTTONVILLE A | 4 | 23 | 24 | 8.875 | 9.125 | 0
2713 | TORONTO BUTTONVILLE A | 4 | 23 | 1 | -1.9 | 19.9 | 0
2713 | TORONTO BUTTONVILLE A | 4 | 24 | 1 | 8.025 | 9.975 | 0
2714 | TORONTO BUTTONVILLE A | 4 | 23 | 2 | -3.4 | 21.4 | 0
2714 | TORONTO BUTTONVILLE A | 4 | 24 | 2 | 7.45 | 10.55 | 0
2715 | TORONTO BUTTONVILLE A | 4 | 23 | 3 | -3.7 | 21.7 | 0
2715 | TORONTO BUTTONVILLE A | 4 | 24 | 3 | 6.875 | 11.125 | 0
2716 | TORONTO BUTTONVILLE A | 4 | 23 | 4 | -4.5 | 22.5 | 0
2716 | TORONTO BUTTONVILLE A | 4 | 24 | 4 | 6.925 | 11.075 | 0
2717 | TORONTO BUTTONVILLE A | 4 | 23 | 5 | -3.4 | 21.4 | 0
2717 | TORONTO BUTTONVILLE A | 4 | 24 | 5 | 6.175 | 11.825 | 0
2718 | TORONTO BUTTONVILLE A | 4 | 23 | 6 | -2.4 | 20.4 | 0
2718 | TORONTO BUTTONVILLE A | 4 | 24 | 6 | 4.875 | 13.125 | 0
2719 | TORONTO BUTTONVILLE A | 4 | 23 | 7 | -1.9 | 19.9 | 0
2719 | TORONTO BUTTONVILLE A | 4 | 24 | 7 | 5.25 | 12.75 | 0
2720 | TORONTO BUTTONVILLE A | 4 | 23 | 8 | -0.7 | 18.7 | 0
2720 | TORONTO BUTTONVILLE A | 4 | 24 | 8 | 6.75 | 11.25 | 0
2721 | TORONTO BUTTONVILLE A | 4 | 23 | 9 | 2.1 | 15.9 | 0
2721 | TORONTO BUTTONVILLE A | 4 | 24 | 9 | 8.725 | 9.275 | 0
2722 | TORONTO BUTTONVILLE A | 4 | 23 | 10 | 2.5 | 15.5 | 0
2722 | TORONTO BUTTONVILLE A | 4 | 24 | 10 | 10.3 | 7.7 | 0
2723 | TORONTO BUTTONVILLE A | 4 | 23 | 11 | 3.1 | 14.9 | 0
2723 | TORONTO BUTTONVILLE A | 4 | 24 | 11 | 11.125 | 6.875 | 0
2724 | TORONTO BUTTONVILLE A | 4 | 23 | 12 | 3 | 15 | 0
2724 | TORONTO BUTTONVILLE A | 4 | 24 | 12 | 11.8 | 6.2 | 0
2725 | TORONTO BUTTONVILLE A | 4 | 23 | 13 | 3.4 | 14.6 | 0
2725 | TORONTO BUTTONVILLE A | 4 | 24 | 13 | 12.225 | 5.775 | 0
2726 | TORONTO BUTTONVILLE A | 4 | 23 | 14 | 4.3 | 13.7 | 0
2726 | TORONTO BUTTONVILLE A | 4 | 24 | 14 | 12.75 | 5.25 | 0
2727 | TORONTO BUTTONVILLE A | 4 | 23 | 15 | 5.2 | 12.8 | 0
2727 | TORONTO BUTTONVILLE A | 4 | 24 | 15 | 13.2 | 4.8 | 0
2728 | TORONTO BUTTONVILLE A | 4 | 23 | 16 | 6 | 12 | 0
2728 | TORONTO BUTTONVILLE A | 4 | 24 | 16 | 13.475 | 4.525 | 0
2729 | TORONTO BUTTONVILLE A | 4 | 23 | 17 | 5.7 | 12.3 | 0
2729 | TORONTO BUTTONVILLE A | 4 | 24 | 17 | 13.625 | 4.375 | 0
2730 | TORONTO BUTTONVILLE A | 4 | 23 | 18 | 5 | 13 | 0
2730 | TORONTO BUTTONVILLE A | 4 | 24 | 18 | 12.75 | 5.25 | 0
2731 | TORONTO BUTTONVILLE A | 4 | 23 | 19 | 4.9 | 13.1 | 0
2731 | TORONTO BUTTONVILLE A | 4 | 24 | 19 | 12.125 | 5.875 | 0
2732 | TORONTO BUTTONVILLE A | 4 | 23 | 20 | 4.4 | 13.6 | 0
2732 | TORONTO BUTTONVILLE A | 4 | 24 | 20 | 10.95 | 7.05 | 0
2733 | TORONTO BUTTONVILLE A | 4 | 23 | 21 | 4.2 | 13.8 | 0
2733 | TORONTO BUTTONVILLE A | 4 | 24 | 21 | 10.05 | 7.95 | 0
2734 | TORONTO BUTTONVILLE A | 4 | 23 | 22 | 4.1 | 13.9 | 0
2734 | TORONTO BUTTONVILLE A | 4 | 24 | 22 | 9.35 | 8.65 | 0
2735 | TORONTO BUTTONVILLE A | 4 | 23 | 23 | 4.2 | 13.8 | 0
2735 | TORONTO BUTTONVILLE A | 4 | 24 | 23 | 8.975 | 9.025 | 0
2736 | TORONTO BUTTONVILLE A | 4 | 23 | 24 | 4.3 | 13.7 | 0
2736 | TORONTO BUTTONVILLE A | 4 | 24 | 24 | 8.625 | 9.375 | 0
2737 | TORONTO BUTTONVILLE A | 4 | 24 | 1 | 4.4 | 13.6 | 0
2737 | TORONTO BUTTONVILLE A | 4 | 25 | 1 | 7.875 | 10.125 | 0
2738 | TORONTO BUTTONVILLE A | 4 | 24 | 2 | 4.6 | 13.4 | 0
2738 | TORONTO BUTTONVILLE A | 4 | 25 | 2 | 7.725 | 10.275 | 0
2739 | TORONTO BUTTONVILLE A | 4 | 24 | 3 | 4.7 | 13.3 | 0
2739 | TORONTO BUTTONVILLE A | 4 | 25 | 3 | 7.025 | 10.975 | 0
2740 | TORONTO BUTTONVILLE A | 4 | 24 | 4 | 4.8 | 13.2 | 0
2740 | TORONTO BUTTONVILLE A | 4 | 25 | 4 | 6.425 | 11.575 | 0
2741 | TORONTO BUTTONVILLE A | 4 | 24 | 5 | 4.8 | 13.2 | 0
2741 | TORONTO BUTTONVILLE A | 4 | 25 | 5 | 6.5 | 11.5 | 0
2742 | TORONTO BUTTONVILLE A | 4 | 24 | 6 | 4.8 | 13.2 | 0
2742 | TORONTO BUTTONVILLE A | 4 | 25 | 6 | 6.625 | 11.375 | 0
2743 | TORONTO BUTTONVILLE A | 4 | 24 | 7 | 5 | 13 | 0
2743 | TORONTO BUTTONVILLE A | 4 | 25 | 7 | 6.65 | 11.35 | 0
2744 | TORONTO BUTTONVILLE A | 4 | 24 | 8 | 5.1 | 12.9 | 0
2744 | TORONTO BUTTONVILLE A | 4 | 25 | 8 | 7.6 | 10.4 | 0
2745 | TORONTO BUTTONVILLE A | 4 | 24 | 9 | 5.1 | 12.9 | 0
2745 | TORONTO BUTTONVILLE A | 4 | 25 | 9 | 8.1 | 9.9 | 0
2746 | TORONTO BUTTONVILLE A | 4 | 24 | 10 | 6 | 12 | 0
2746 | TORONTO BUTTONVILLE A | 4 | 25 | 10 | 8.025 | 9.975 | 0
2747 | TORONTO BUTTONVILLE A | 4 | 24 | 11 | 7.4 | 10.6 | 0
2747 | TORONTO BUTTONVILLE A | 4 | 25 | 11 | 8.675 | 9.325 | 0
2748 | TORONTO BUTTONVILLE A | 4 | 24 | 12 | 8.2 | 9.8 | 0
2748 | TORONTO BUTTONVILLE A | 4 | 25 | 12 | 9.825 | 8.175 | 0
2749 | TORONTO BUTTONVILLE A | 4 | 24 | 13 | 8.4 | 9.6 | 0
2749 | TORONTO BUTTONVILLE A | 4 | 25 | 13 | 10.025 | 7.975 | 0
2750 | TORONTO BUTTONVILLE A | 4 | 24 | 14 | 8.5 | 9.5 | 0
2750 | TORONTO BUTTONVILLE A | 4 | 25 | 14 | 10.175 | 7.825 | 0
2751 | TORONTO BUTTONVILLE A | 4 | 24 | 15 | 9.1 | 8.9 | 0
2751 | TORONTO BUTTONVILLE A | 4 | 25 | 15 | 10.55 | 7.45 | 0
2752 | TORONTO BUTTONVILLE A | 4 | 24 | 16 | 8.3 | 9.7 | 0
2752 | TORONTO BUTTONVILLE A | 4 | 25 | 16 | 9.75 | 8.25 | 0
2753 | TORONTO BUTTONVILLE A | 4 | 24 | 17 | 8.2 | 9.8 | 0
2753 | TORONTO BUTTONVILLE A | 4 | 25 | 17 | 9.275 | 8.725 | 0
2754 | TORONTO BUTTONVILLE A | 4 | 24 | 18 | 7.5 | 10.5 | 0
2754 | TORONTO BUTTONVILLE A | 4 | 25 | 18 | 8.4 | 9.6 | 0
2755 | TORONTO BUTTONVILLE A | 4 | 24 | 19 | 6.3 | 11.7 | 0
2755 | TORONTO BUTTONVILLE A | 4 | 25 | 19 | 7.925 | 10.075 | 0
2756 | TORONTO BUTTONVILLE A | 4 | 24 | 20 | 5.5 | 12.5 | 0
2756 | TORONTO BUTTONVILLE A | 4 | 25 | 20 | 7.1 | 10.9 | 0
2757 | TORONTO BUTTONVILLE A | 4 | 24 | 21 | 5.2 | 12.8 | 0
2757 | TORONTO BUTTONVILLE A | 4 | 25 | 21 | 6.125 | 11.875 | 0
2758 | TORONTO BUTTONVILLE A | 4 | 24 | 22 | 5.2 | 12.8 | 0
2758 | TORONTO BUTTONVILLE A | 4 | 25 | 22 | 5.9 | 12.1 | 0
2759 | TORONTO BUTTONVILLE A | 4 | 24 | 23 | 5.3 | 12.7 | 0
2759 | TORONTO BUTTONVILLE A | 4 | 25 | 23 | 5.85 | 12.15 | 0
2760 | TORONTO BUTTONVILLE A | 4 | 24 | 24 | 5 | 13 | 0
2760 | TORONTO BUTTONVILLE A | 4 | 25 | 24 | 5.775 | 12.225 | 0
2761 | TORONTO BUTTONVILLE A | 4 | 25 | 1 | 4.3 | 13.7 | 0
2761 | TORONTO BUTTONVILLE A | 4 | 26 | 1 | 5.925 | 12.075 | 0
2762 | TORONTO BUTTONVILLE A | 4 | 25 | 2 | 2.3 | 15.7 | 0
2762 | TORONTO BUTTONVILLE A | 4 | 26 | 2 | 5.675 | 12.325 | 0
2763 | TORONTO BUTTONVILLE A | 4 | 25 | 3 | 1.6 | 16.4 | 0
2763 | TORONTO BUTTONVILLE A | 4 | 26 | 3 | 5.375 | 12.625 | 0
2764 | TORONTO BUTTONVILLE A | 4 | 25 | 4 | 1.2 | 16.8 | 0
2764 | TORONTO BUTTONVILLE A | 4 | 26 | 4 | 5.15 | 12.85 | 0
2765 | TORONTO BUTTONVILLE A | 4 | 25 | 5 | 1.8 | 16.2 | 0
2765 | TORONTO BUTTONVILLE A | 4 | 26 | 5 | 5 | 13 | 0
2766 | TORONTO BUTTONVILLE A | 4 | 25 | 6 | 0.8 | 17.2 | 0
2766 | TORONTO BUTTONVILLE A | 4 | 26 | 6 | 4.925 | 13.075 | 0
2767 | TORONTO BUTTONVILLE A | 4 | 25 | 7 | 1.6 | 16.4 | 0
2767 | TORONTO BUTTONVILLE A | 4 | 26 | 7 | 5.15 | 12.85 | 0
2768 | TORONTO BUTTONVILLE A | 4 | 25 | 8 | 4.4 | 13.6 | 0
2768 | TORONTO BUTTONVILLE A | 4 | 26 | 8 | 6.2 | 11.8 | 0
2769 | TORONTO BUTTONVILLE A | 4 | 25 | 9 | 6 | 12 | 0
2769 | TORONTO BUTTONVILLE A | 4 | 26 | 9 | 6.625 | 11.375 | 0
2770 | TORONTO BUTTONVILLE A | 4 | 25 | 10 | 8.8 | 9.2 | 0
2770 | TORONTO BUTTONVILLE A | 4 | 26 | 10 | 7.7 | 10.3 | 0
2771 | TORONTO BUTTONVILLE A | 4 | 25 | 11 | 11 | 7 | 0
2771 | TORONTO BUTTONVILLE A | 4 | 26 | 11 | 8.675 | 9.325 | 0
2772 | TORONTO BUTTONVILLE A | 4 | 25 | 12 | 12.3 | 5.7 | 0
2772 | TORONTO BUTTONVILLE A | 4 | 26 | 12 | 9.675 | 8.325 | 0
2773 | TORONTO BUTTONVILLE A | 4 | 25 | 13 | 13.1 | 4.9 | 0
2773 | TORONTO BUTTONVILLE A | 4 | 26 | 13 | 10.3333 | 7.6667 | 0
2774 | TORONTO BUTTONVILLE A | 4 | 25 | 14 | 12.1 | 5.9 | 0
2774 | TORONTO BUTTONVILLE A | 4 | 26 | 14 | 10.0667 | 7.9333 | 0
2775 | TORONTO BUTTONVILLE A | 4 | 25 | 15 | 12.9 | 5.1 | 0
2775 | TORONTO BUTTONVILLE A | 4 | 26 | 15 | 10.7667 | 7.2333 | 0
2776 | TORONTO BUTTONVILLE A | 4 | 25 | 16 | 12.8 | 5.2 | 0
2776 | TORONTO BUTTONVILLE A | 4 | 26 | 16 | 10.8667 | 7.1333 | 0
2777 | TORONTO BUTTONVILLE A | 4 | 25 | 17 | 12.8 | 5.2 | 0
2777 | TORONTO BUTTONVILLE A | 4 | 26 | 17 | 12.325 | 5.675 | 0
2778 | TORONTO BUTTONVILLE A | 4 | 25 | 18 | 12.5 | 5.5 | 0
2778 | TORONTO BUTTONVILLE A | 4 | 26 | 18 | 11.75 | 6.25 | 0
2779 | TORONTO BUTTONVILLE A | 4 | 25 | 19 | 11.8 | 6.2 | 0
2779 | TORONTO BUTTONVILLE A | 4 | 26 | 19 | 11.325 | 6.675 | 0
2780 | TORONTO BUTTONVILLE A | 4 | 25 | 20 | 10.6 | 7.4 | 0
2780 | TORONTO BUTTONVILLE A | 4 | 26 | 20 | 10.3 | 7.7 | 0
2781 | TORONTO BUTTONVILLE A | 4 | 25 | 21 | 9.9 | 8.1 | 0
2781 | TORONTO BUTTONVILLE A | 4 | 26 | 21 | 9.525 | 8.475 | 0
2782 | TORONTO BUTTONVILLE A | 4 | 25 | 22 | 9.3 | 8.7 | 0
2782 | TORONTO BUTTONVILLE A | 4 | 26 | 22 | 8.7 | 9.3 | 0
2783 | TORONTO BUTTONVILLE A | 4 | 25 | 23 | 8.8 | 9.2 | 0
2783 | TORONTO BUTTONVILLE A | 4 | 26 | 23 | 7.925 | 10.075 | 0
2784 | TORONTO BUTTONVILLE A | 4 | 25 | 24 | 8.8 | 9.2 | 0
2784 | TORONTO BUTTONVILLE A | 4 | 26 | 24 | 6.475 | 11.525 | 0
2785 | TORONTO BUTTONVILLE A | 4 | 26 | 1 | 8.4 | 9.6 | 0
2785 | TORONTO BUTTONVILLE A | 4 | 27 | 1 | 5.95 | 12.05 | 0
2786 | TORONTO BUTTONVILLE A | 4 | 26 | 2 | 9.2 | 8.8 | 0
2786 | TORONTO BUTTONVILLE A | 4 | 27 | 2 | 5.75 | 12.25 | 0
2787 | TORONTO BUTTONVILLE A | 4 | 26 | 3 | 8.9 | 9.1 | 0
2787 | TORONTO BUTTONVILLE A | 4 | 27 | 3 | 5.675 | 12.325 | 0
2788 | TORONTO BUTTONVILLE A | 4 | 26 | 4 | 9.4 | 8.6 | 0
2788 | TORONTO BUTTONVILLE A | 4 | 27 | 4 | 5 | 13 | 0
2789 | TORONTO BUTTONVILLE A | 4 | 26 | 5 | 9.6 | 8.4 | 0
2789 | TORONTO BUTTONVILLE A | 4 | 27 | 5 | 4.825 | 13.175 | 0
2790 | TORONTO BUTTONVILLE A | 4 | 26 | 6 | 9.2 | 8.8 | 0
2790 | TORONTO BUTTONVILLE A | 4 | 27 | 6 | 4.35 | 13.65 | 0
2791 | TORONTO BUTTONVILLE A | 4 | 26 | 7 | 9.2 | 8.8 | 0
2791 | TORONTO BUTTONVILLE A | 4 | 27 | 7 | 4.45 | 13.55 | 0
2792 | TORONTO BUTTONVILLE A | 4 | 26 | 8 | 9.7 | 8.3 | 0
2792 | TORONTO BUTTONVILLE A | 4 | 27 | 8 | 5.95 | 12.05 | 0
2793 | TORONTO BUTTONVILLE A | 4 | 26 | 9 | 9.6 | 8.4 | 0
2793 | TORONTO BUTTONVILLE A | 4 | 27 | 9 | 7.7 | 10.3 | 0
2794 | TORONTO BUTTONVILLE A | 4 | 26 | 10 | 10.2 | 7.8 | 0
2794 | TORONTO BUTTONVILLE A | 4 | 27 | 10 | 9.15 | 8.85 | 0
2795 | TORONTO BUTTONVILLE A | 4 | 26 | 11 | 11.1 | 6.9 | 0
2795 | TORONTO BUTTONVILLE A | 4 | 27 | 11 | 10.65 | 7.35 | 0
2796 | TORONTO BUTTONVILLE A | 4 | 26 | 12 | 11.4 | 6.6 | 0
2796 | TORONTO BUTTONVILLE A | 4 | 27 | 12 | 12.15 | 5.85 | 0
2797 | TORONTO BUTTONVILLE A | 4 | 26 | 13 | 10.2 | 7.8 | 0
2797 | TORONTO BUTTONVILLE A | 4 | 27 | 13 | 12.85 | 5.15 | 0
2798 | TORONTO BUTTONVILLE A | 4 | 26 | 14 | 9.4 | 8.6 | 0
2798 | TORONTO BUTTONVILLE A | 4 | 27 | 14 | 13.775 | 4.225 | 0
2799 | TORONTO BUTTONVILLE A | 4 | 26 | 15 | 9.3 | 8.7 | 0
2799 | TORONTO BUTTONVILLE A | 4 | 27 | 15 | 14.125 | 3.875 | 0
2800 | TORONTO BUTTONVILLE A | 4 | 26 | 16 | 9 | 9 | 0
2800 | TORONTO BUTTONVILLE A | 4 | 27 | 16 | 14.375 | 3.625 | 0
2801 | TORONTO BUTTONVILLE A | 4 | 26 | 17 | 10 | 8 | 0
2801 | TORONTO BUTTONVILLE A | 4 | 27 | 17 | 13.725 | 4.275 | 0
2802 | TORONTO BUTTONVILLE A | 4 | 26 | 18 | 9.7 | 8.3 | 0
2802 | TORONTO BUTTONVILLE A | 4 | 27 | 18 | 13.275 | 4.725 | 0
2803 | TORONTO BUTTONVILLE A | 4 | 26 | 19 | 8.1 | 9.9 | 0
2803 | TORONTO BUTTONVILLE A | 4 | 27 | 19 | 11.85 | 6.15 | 0
2804 | TORONTO BUTTONVILLE A | 4 | 26 | 20 | 6.8 | 11.2 | 0
2804 | TORONTO BUTTONVILLE A | 4 | 27 | 20 | 10.775 | 7.225 | 0
2805 | TORONTO BUTTONVILLE A | 4 | 26 | 21 | 6 | 12 | 0
2805 | TORONTO BUTTONVILLE A | 4 | 27 | 21 | 10.65 | 7.35 | 0
2806 | TORONTO BUTTONVILLE A | 4 | 26 | 22 | 5.9 | 12.1 | 0
2806 | TORONTO BUTTONVILLE A | 4 | 27 | 22 | 10.075 | 7.925 | 0
2807 | TORONTO BUTTONVILLE A | 4 | 26 | 23 | 6.7 | 11.3 | 0
2807 | TORONTO BUTTONVILLE A | 4 | 27 | 23 | 9.175 | 8.825 | 0
2808 | TORONTO BUTTONVILLE A | 4 | 26 | 24 | 8.1 | 9.9 | 0
2808 | TORONTO BUTTONVILLE A | 4 | 27 | 24 | 8.675 | 9.325 | 0
2809 | TORONTO BUTTONVILLE A | 4 | 27 | 1 | 9.2 | 8.8 | 0
2809 | TORONTO BUTTONVILLE A | 4 | 28 | 1 | 7.9 | 10.1 | 0
2810 | TORONTO BUTTONVILLE A | 4 | 27 | 2 | 7.6 | 10.4 | 0
2810 | TORONTO BUTTONVILLE A | 4 | 28 | 2 | 7.675 | 10.325 | 0
2811 | TORONTO BUTTONVILLE A | 4 | 27 | 3 | 5.4 | 12.6 | 0
2811 | TORONTO BUTTONVILLE A | 4 | 28 | 3 | 7.3 | 10.7 | 0
2812 | TORONTO BUTTONVILLE A | 4 | 27 | 4 | 4.4 | 13.6 | 0
2812 | TORONTO BUTTONVILLE A | 4 | 28 | 4 | 6.975 | 11.025 | 0
2813 | TORONTO BUTTONVILLE A | 4 | 27 | 5 | 4 | 14 | 0
2813 | TORONTO BUTTONVILLE A | 4 | 28 | 5 | 6.525 | 11.475 | 0
2814 | TORONTO BUTTONVILLE A | 4 | 27 | 6 | 3 | 15 | 0
2814 | TORONTO BUTTONVILLE A | 4 | 28 | 6 | 6.375 | 11.625 | 0
2815 | TORONTO BUTTONVILLE A | 4 | 27 | 7 | 4 | 14 | 0
2815 | TORONTO BUTTONVILLE A | 4 | 28 | 7 | 6.475 | 11.525 | 0
2816 | TORONTO BUTTONVILLE A | 4 | 27 | 8 | 6.2 | 11.8 | 0
2816 | TORONTO BUTTONVILLE A | 4 | 28 | 8 | 7.15 | 10.85 | 0
2817 | TORONTO BUTTONVILLE A | 4 | 27 | 9 | 7.7 | 10.3 | 0
2817 | TORONTO BUTTONVILLE A | 4 | 28 | 9 | 7.875 | 10.125 | 0
2818 | TORONTO BUTTONVILLE A | 4 | 27 | 10 | 9.4 | 8.6 | 0
2818 | TORONTO BUTTONVILLE A | 4 | 28 | 10 | 8.025 | 9.975 | 0
2819 | TORONTO BUTTONVILLE A | 4 | 27 | 11 | 11.7 | 6.3 | 0
2819 | TORONTO BUTTONVILLE A | 4 | 28 | 11 | 8.65 | 9.35 | 0
2820 | TORONTO BUTTONVILLE A | 4 | 27 | 12 | 12.8 | 5.2 | 0
2820 | TORONTO BUTTONVILLE A | 4 | 28 | 12 | 9.1 | 8.9 | 0
2821 | TORONTO BUTTONVILLE A | 4 | 27 | 13 | 13.7 | 4.3 | 0
2821 | TORONTO BUTTONVILLE A | 4 | 28 | 13 | 9.6 | 8.4 | 0
2822 | TORONTO BUTTONVILLE A | 4 | 27 | 14 | 13.6 | 4.4 | 0
2822 | TORONTO BUTTONVILLE A | 4 | 28 | 14 | 9.65 | 8.35 | 0
2823 | TORONTO BUTTONVILLE A | 4 | 27 | 15 | 13.4 | 4.6 | 0
2823 | TORONTO BUTTONVILLE A | 4 | 28 | 15 | 10.1 | 7.9 | 0
2824 | TORONTO BUTTONVILLE A | 4 | 27 | 16 | 13.4 | 4.6 | 0
2824 | TORONTO BUTTONVILLE A | 4 | 28 | 16 | 10.625 | 7.375 | 0
2825 | TORONTO BUTTONVILLE A | 4 | 27 | 17 | 14.6 | 3.4 | 0
2825 | TORONTO BUTTONVILLE A | 4 | 28 | 17 | 10.6 | 7.4 | 0
2826 | TORONTO BUTTONVILLE A | 4 | 27 | 18 | 14.6 | 3.4 | 0
2826 | TORONTO BUTTONVILLE A | 4 | 28 | 18 | 10.575 | 7.425 | 0
2827 | TORONTO BUTTONVILLE A | 4 | 27 | 19 | 12.7 | 5.3 | 0
2827 | TORONTO BUTTONVILLE A | 4 | 28 | 19 | 10.125 | 7.875 | 0
2828 | TORONTO BUTTONVILLE A | 4 | 27 | 20 | 11.1 | 6.9 | 0
2828 | TORONTO BUTTONVILLE A | 4 | 28 | 20 | 9.175 | 8.825 | 0
2829 | TORONTO BUTTONVILLE A | 4 | 27 | 21 | 10.2 | 7.8 | 0
2829 | TORONTO BUTTONVILLE A | 4 | 28 | 21 | 8.675 | 9.325 | 0
2830 | TORONTO BUTTONVILLE A | 4 | 27 | 22 | 9.5 | 8.5 | 0
2830 | TORONTO BUTTONVILLE A | 4 | 28 | 22 | 7.55 | 10.45 | 0
2831 | TORONTO BUTTONVILLE A | 4 | 27 | 23 | 8.6 | 9.4 | 0
2831 | TORONTO BUTTONVILLE A | 4 | 28 | 23 | 6.85 | 11.15 | 0
2832 | TORONTO BUTTONVILLE A | 4 | 27 | 24 | 8.3 | 9.7 | 0
2832 | TORONTO BUTTONVILLE A | 4 | 28 | 24 | 6.625 | 11.375 | 0
2833 | TORONTO BUTTONVILLE A | 4 | 28 | 1 | 8.2 | 9.8 | 0
2833 | TORONTO BUTTONVILLE A | 4 | 29 | 1 | 6.475 | 11.525 | 0
2834 | TORONTO BUTTONVILLE A | 4 | 28 | 2 | 8.1 | 9.9 | 0
2834 | TORONTO BUTTONVILLE A | 4 | 29 | 2 | 6.175 | 11.825 | 0
2835 | TORONTO BUTTONVILLE A | 4 | 28 | 3 | 8.2 | 9.8 | 0
2835 | TORONTO BUTTONVILLE A | 4 | 29 | 3 | 5.675 | 12.325 | 0
2836 | TORONTO BUTTONVILLE A | 4 | 28 | 4 | 5.8 | 12.2 | 0
2836 | TORONTO BUTTONVILLE A | 4 | 29 | 4 | 5.025 | 12.975 | 0
2837 | TORONTO BUTTONVILLE A | 4 | 28 | 5 | 5.4 | 12.6 | 0
2837 | TORONTO BUTTONVILLE A | 4 | 29 | 5 | 3.825 | 14.175 | 0
2838 | TORONTO BUTTONVILLE A | 4 | 28 | 6 | 5.9 | 12.1 | 0
2838 | TORONTO BUTTONVILLE A | 4 | 29 | 6 | 3.325 | 14.675 | 0
2839 | TORONTO BUTTONVILLE A | 4 | 28 | 7 | 5.5 | 12.5 | 0
2839 | TORONTO BUTTONVILLE A | 4 | 29 | 7 | 3.65 | 14.35 | 0
2840 | TORONTO BUTTONVILLE A | 4 | 28 | 8 | 5.6 | 12.4 | 0
2840 | TORONTO BUTTONVILLE A | 4 | 29 | 8 | 4.8 | 13.2 | 0
2841 | TORONTO BUTTONVILLE A | 4 | 28 | 9 | 5.7 | 12.3 | 0
2841 | TORONTO BUTTONVILLE A | 4 | 29 | 9 | 5.75 | 12.25 | 0
2842 | TORONTO BUTTONVILLE A | 4 | 28 | 10 | 5.5 | 12.5 | 0
2842 | TORONTO BUTTONVILLE A | 4 | 29 | 10 | 6.475 | 11.525 | 0
2843 | TORONTO BUTTONVILLE A | 4 | 28 | 11 | 6.5 | 11.5 | 0
2843 | TORONTO BUTTONVILLE A | 4 | 29 | 11 | 6.725 | 11.275 | 0
2844 | TORONTO BUTTONVILLE A | 4 | 28 | 12 | 8 | 10 | 0
2844 | TORONTO BUTTONVILLE A | 4 | 29 | 12 | 7.5 | 10.5 | 0
2845 | TORONTO BUTTONVILLE A | 4 | 28 | 13 | 10.1 | 7.9 | 0
2845 | TORONTO BUTTONVILLE A | 4 | 29 | 13 | 8.4 | 9.6 | 0
2846 | TORONTO BUTTONVILLE A | 4 | 28 | 14 | 11.1 | 6.9 | 0
2846 | TORONTO BUTTONVILLE A | 4 | 29 | 14 | 8.65 | 9.35 | 0
2847 | TORONTO BUTTONVILLE A | 4 | 28 | 15 | 10.9 | 7.1 | 0
2847 | TORONTO BUTTONVILLE A | 4 | 29 | 15 | 8.7 | 9.3 | 0
2848 | TORONTO BUTTONVILLE A | 4 | 28 | 16 | 11.1 | 6.9 | 0
2848 | TORONTO BUTTONVILLE A | 4 | 29 | 16 | 8.6 | 9.4 | 0
2849 | TORONTO BUTTONVILLE A | 4 | 28 | 17 | 11.5 | 6.5 | 0
2849 | TORONTO BUTTONVILLE A | 4 | 29 | 17 | 8.225 | 9.775 | 0
2850 | TORONTO BUTTONVILLE A | 4 | 28 | 18 | 11.5 | 6.5 | 0
2850 | TORONTO BUTTONVILLE A | 4 | 29 | 18 | 7.55 | 10.45 | 0
2851 | TORONTO BUTTONVILLE A | 4 | 28 | 19 | 10.1 | 7.9 | 0
2851 | TORONTO BUTTONVILLE A | 4 | 29 | 19 | 7.175 | 10.825 | 0
2852 | TORONTO BUTTONVILLE A | 4 | 28 | 20 | 9.6 | 8.4 | 0
2852 | TORONTO BUTTONVILLE A | 4 | 29 | 20 | 6.5 | 11.5 | 0
2853 | TORONTO BUTTONVILLE A | 4 | 28 | 21 | 9 | 9 | 0
2853 | TORONTO BUTTONVILLE A | 4 | 29 | 21 | 6.1 | 11.9 | 0
2854 | TORONTO BUTTONVILLE A | 4 | 28 | 22 | 8.7 | 9.3 | 0
2854 | TORONTO BUTTONVILLE A | 4 | 29 | 22 | 5.9 | 12.1 | 0
2855 | TORONTO BUTTONVILLE A | 4 | 28 | 23 | 8.6 | 9.4 | 0
2855 | TORONTO BUTTONVILLE A | 4 | 29 | 23 | 5.875 | 12.125 | 0
2856 | TORONTO BUTTONVILLE A | 4 | 28 | 24 | 8.2 | 9.8 | 0
2856 | TORONTO BUTTONVILLE A | 4 | 29 | 24 | 5.7 | 12.3 | 0
2857 | TORONTO BUTTONVILLE A | 4 | 29 | 1 | 9.4 | 8.6 | 0
2857 | TORONTO BUTTONVILLE A | 4 | 30 | 1 | 5.575 | 12.425 | 0
2858 | TORONTO BUTTONVILLE A | 4 | 29 | 2 | 9.9 | 8.1 | 0
2858 | TORONTO BUTTONVILLE A | 4 | 30 | 2 | 5.525 | 12.475 | 0
2859 | TORONTO BUTTONVILLE A | 4 | 29 | 3 | 9.1 | 8.9 | 0
2859 | TORONTO BUTTONVILLE A | 4 | 30 | 3 | 5.35 | 12.65 | 0
2860 | TORONTO BUTTONVILLE A | 4 | 29 | 4 | 8.9 | 9.1 | 0
2860 | TORONTO BUTTONVILLE A | 4 | 30 | 4 | 5.2 | 12.8 | 0
2861 | TORONTO BUTTONVILLE A | 4 | 29 | 5 | 8.8 | 9.2 | 0
2861 | TORONTO BUTTONVILLE A | 4 | 30 | 5 | 4.875 | 13.125 | 0
2862 | TORONTO BUTTONVILLE A | 4 | 29 | 6 | 8.9 | 9.1 | 0
2862 | TORONTO BUTTONVILLE A | 4 | 30 | 6 | 4.8 | 13.2 | 0
2863 | TORONTO BUTTONVILLE A | 4 | 29 | 7 | 9.3 | 8.7 | 0
2863 | TORONTO BUTTONVILLE A | 4 | 30 | 7 | 4.475 | 13.525 | 0
2864 | TORONTO BUTTONVILLE A | 4 | 29 | 8 | 9.3 | 8.7 | 0
2864 | TORONTO BUTTONVILLE A | 4 | 30 | 8 | 5.05 | 12.95 | 0
2865 | TORONTO BUTTONVILLE A | 4 | 29 | 9 | 9 | 9 | 0
2865 | TORONTO BUTTONVILLE A | 4 | 30 | 9 | 5.875 | 12.125 | 0
2866 | TORONTO BUTTONVILLE A | 4 | 29 | 10 | 8.8 | 9.2 | 0
2866 | TORONTO BUTTONVILLE A | 4 | 30 | 10 | 6.8 | 11.2 | 0
2867 | TORONTO BUTTONVILLE A | 4 | 29 | 11 | 8.5 | 9.5 | 0
2867 | TORONTO BUTTONVILLE A | 4 | 30 | 11 | 7.325 | 10.675 | 0
2868 | TORONTO BUTTONVILLE A | 4 | 29 | 12 | 9.2 | 8.8 | 0
2868 | TORONTO BUTTONVILLE A | 4 | 30 | 12 | 7.95 | 10.05 | 0
2869 | TORONTO BUTTONVILLE A | 4 | 29 | 13 | 11 | 7 | 0
2869 | TORONTO BUTTONVILLE A | 4 | 30 | 13 | 8.725 | 9.275 | 0
2870 | TORONTO BUTTONVILLE A | 4 | 29 | 14 | 12 | 6 | 0
2870 | TORONTO BUTTONVILLE A | 4 | 30 | 14 | 9.35 | 8.65 | 0
2871 | TORONTO BUTTONVILLE A | 4 | 29 | 15 | 13.1 | 4.9 | 0
2871 | TORONTO BUTTONVILLE A | 4 | 30 | 15 | 9.975 | 8.025 | 0
2872 | TORONTO BUTTONVILLE A | 4 | 29 | 16 | 13.9 | 4.1 | 0
2872 | TORONTO BUTTONVILLE A | 4 | 30 | 16 | 10.025 | 7.975 | 0
2873 | TORONTO BUTTONVILLE A | 4 | 29 | 17 | 13.4 | 4.6 | 0
2873 | TORONTO BUTTONVILLE A | 4 | 30 | 17 | 10.475 | 7.525 | 0
2874 | TORONTO BUTTONVILLE A | 4 | 29 | 18 | 12.9 | 5.1 | 0
2874 | TORONTO BUTTONVILLE A | 4 | 30 | 18 | 10.5 | 7.5 | 0
2875 | TORONTO BUTTONVILLE A | 4 | 29 | 19 | 13.1 | 4.9 | 0
2875 | TORONTO BUTTONVILLE A | 4 | 30 | 19 | 10.075 | 7.925 | 0
2876 | TORONTO BUTTONVILLE A | 4 | 29 | 20 | 13.9 | 4.1 | 0
2876 | TORONTO BUTTONVILLE A | 4 | 30 | 20 | 9.225 | 8.775 | 0
2877 | TORONTO BUTTONVILLE A | 4 | 29 | 21 | 13.2 | 4.8 | 0
2877 | TORONTO BUTTONVILLE A | 4 | 30 | 21 | 8.675 | 9.325 | 0
2878 | TORONTO BUTTONVILLE A | 4 | 29 | 22 | 12.6 | 5.4 | 0
2878 | TORONTO BUTTONVILLE A | 4 | 30 | 22 | 8.1 | 9.9 | 0
2879 | TORONTO BUTTONVILLE A | 4 | 29 | 23 | 11.5 | 6.5 | 0
2879 | TORONTO BUTTONVILLE A | 4 | 30 | 23 | 7.025 | 10.975 | 0
2880 | TORONTO BUTTONVILLE A | 4 | 29 | 24 | 10.6 | 7.4 | 0
2880 | TORONTO BUTTONVILLE A | 4 | 30 | 24 | 6.35 | 11.65 | 0
2881 | TORONTO BUTTONVILLE A | 4 | 30 | 1 | 11.3 | 6.7 | 0
2881 | TORONTO BUTTONVILLE A | 5 | 1 | 1 | 5.7 | 12.3 | 0
2882 | TORONTO BUTTONVILLE A | 4 | 30 | 2 | 10.4 | 7.6 | 0
2882 | TORONTO BUTTONVILLE A | 5 | 1 | 2 | 5.15 | 12.85 | 0
2883 | TORONTO BUTTONVILLE A | 4 | 30 | 3 | 10.5 | 7.5 | 0
2883 | TORONTO BUTTONVILLE A | 5 | 1 | 3 | 4.575 | 13.425 | 0
2884 | TORONTO BUTTONVILLE A | 4 | 30 | 4 | 9.8 | 8.2 | 0
2884 | TORONTO BUTTONVILLE A | 5 | 1 | 4 | 4.475 | 13.525 | 0
2885 | TORONTO BUTTONVILLE A | 4 | 30 | 5 | 9.3 | 8.7 | 0
2885 | TORONTO BUTTONVILLE A | 5 | 1 | 5 | 4.575 | 13.425 | 0
2886 | TORONTO BUTTONVILLE A | 4 | 30 | 6 | 9.2 | 8.8 | 0
2886 | TORONTO BUTTONVILLE A | 5 | 1 | 6 | 4.3 | 13.7 | 0
2887 | TORONTO BUTTONVILLE A | 4 | 30 | 7 | 9.2 | 8.8 | 0
2887 | TORONTO BUTTONVILLE A | 5 | 1 | 7 | 4.775 | 13.225 | 0
2888 | TORONTO BUTTONVILLE A | 4 | 30 | 8 | 8.5 | 9.5 | 0
2888 | TORONTO BUTTONVILLE A | 5 | 1 | 8 | 5.75 | 12.25 | 0
2889 | TORONTO BUTTONVILLE A | 4 | 30 | 9 | 9.3 | 8.7 | 0
2889 | TORONTO BUTTONVILLE A | 5 | 1 | 9 | 7.225 | 10.775 | 0
2890 | TORONTO BUTTONVILLE A | 4 | 30 | 10 | 10.7 | 7.3 | 0
2890 | TORONTO BUTTONVILLE A | 5 | 1 | 10 | 8.6 | 9.4 | 0
2891 | TORONTO BUTTONVILLE A | 4 | 30 | 11 | 11.5 | 6.5 | 0
2891 | TORONTO BUTTONVILLE A | 5 | 1 | 11 | 10.225 | 7.775 | 0
2892 | TORONTO BUTTONVILLE A | 4 | 30 | 12 | 11.7 | 6.3 | 0
2892 | TORONTO BUTTONVILLE A | 5 | 1 | 12 | 11.725 | 6.275 | 0
2893 | TORONTO BUTTONVILLE A | 4 | 30 | 13 | 11.8 | 6.2 | 0
2893 | TORONTO BUTTONVILLE A | 5 | 1 | 13 | 12.3 | 5.7 | 0
2894 | TORONTO BUTTONVILLE A | 4 | 30 | 14 | 12.2 | 5.8 | 0
2894 | TORONTO BUTTONVILLE A | 5 | 1 | 14 | 12.65 | 5.35 | 0
2895 | TORONTO BUTTONVILLE A | 4 | 30 | 15 | 11.6 | 6.4 | 0
2895 | TORONTO BUTTONVILLE A | 5 | 1 | 15 | 13.375 | 4.625 | 0
2896 | TORONTO BUTTONVILLE A | 4 | 30 | 16 | 12.1 | 5.9 | 0
2896 | TORONTO BUTTONVILLE A | 5 | 1 | 16 | 14.275 | 3.725 | 0
2897 | TORONTO BUTTONVILLE A | 4 | 30 | 17 | 13.5 | 4.5 | 0
2897 | TORONTO BUTTONVILLE A | 5 | 1 | 17 | 14.625 | 3.375 | 0
2898 | TORONTO BUTTONVILLE A | 4 | 30 | 18 | 12.8 | 5.2 | 0
2898 | TORONTO BUTTONVILLE A | 5 | 1 | 18 | 15.025 | 2.975 | 0
2899 | TORONTO BUTTONVILLE A | 4 | 30 | 19 | 11.9 | 6.1 | 0
2899 | TORONTO BUTTONVILLE A | 5 | 1 | 19 | 14.85 | 3.15 | 0
2900 | TORONTO BUTTONVILLE A | 4 | 30 | 20 | 10.4 | 7.6 | 0
2900 | TORONTO BUTTONVILLE A | 5 | 1 | 20 | 14.3 | 3.7 | 0
2901 | TORONTO BUTTONVILLE A | 4 | 30 | 21 | 9.9 | 8.1 | 0
2901 | TORONTO BUTTONVILLE A | 5 | 1 | 21 | 13.55 | 4.45 | 0
2902 | TORONTO BUTTONVILLE A | 4 | 30 | 22 | 9.9 | 8.1 | 0
2902 | TORONTO BUTTONVILLE A | 5 | 1 | 22 | 13.15 | 4.85 | 0
2903 | TORONTO BUTTONVILLE A | 4 | 30 | 23 | 9.9 | 8.1 | 0
2903 | TORONTO BUTTONVILLE A | 5 | 1 | 23 | 12.7 | 5.3 | 0
2904 | TORONTO BUTTONVILLE A | 4 | 30 | 24 | 9.8 | 8.2 | 0
2904 | TORONTO BUTTONVILLE A | 5 | 1 | 24 | 11.975 | 6.025 | 0
2905 | TORONTO BUTTONVILLE A | 5 | 1 | 1 | 9.9 | 8.1 | 0
2905 | TORONTO BUTTONVILLE A | 5 | 2 | 1 | 11.45 | 6.55 | 0
2906 | TORONTO BUTTONVILLE A | 5 | 1 | 2 | 10 | 8 | 0
2906 | TORONTO BUTTONVILLE A | 5 | 2 | 2 | 11.425 | 6.575 | 0
2907 | TORONTO BUTTONVILLE A | 5 | 1 | 3 | 10.3 | 7.7 | 0
2907 | TORONTO BUTTONVILLE A | 5 | 2 | 3 | 10.925 | 7.075 | 0
2908 | TORONTO BUTTONVILLE A | 5 | 1 | 4 | 10.4 | 7.6 | 0
2908 | TORONTO BUTTONVILLE A | 5 | 2 | 4 | 10.175 | 7.825 | 0
2909 | TORONTO BUTTONVILLE A | 5 | 1 | 5 | 10.4 | 7.6 | 0
2909 | TORONTO BUTTONVILLE A | 5 | 2 | 5 | 9.65 | 8.35 | 0
2910 | TORONTO BUTTONVILLE A | 5 | 1 | 6 | 9.3 | 8.7 | 0
2910 | TORONTO BUTTONVILLE A | 5 | 2 | 6 | 9.625 | 8.375 | 0
2911 | TORONTO BUTTONVILLE A | 5 | 1 | 7 | 8.7 | 9.3 | 0
2911 | TORONTO BUTTONVILLE A | 5 | 2 | 7 | 10.6 | 7.4 | 0
2912 | TORONTO BUTTONVILLE A | 5 | 1 | 8 | 8.4 | 9.6 | 0
2912 | TORONTO BUTTONVILLE A | 5 | 2 | 8 | 11.4 | 6.6 | 0
2913 | TORONTO BUTTONVILLE A | 5 | 1 | 9 | 7.7 | 10.3 | 0
2913 | TORONTO BUTTONVILLE A | 5 | 2 | 9 | 12.35 | 5.65 | 0
2914 | TORONTO BUTTONVILLE A | 5 | 1 | 10 | 8.1 | 9.9 | 0
2914 | TORONTO BUTTONVILLE A | 5 | 2 | 10 | 12.75 | 5.25 | 0
2915 | TORONTO BUTTONVILLE A | 5 | 1 | 11 | 8.5 | 9.5 | 0
2915 | TORONTO BUTTONVILLE A | 5 | 2 | 11 | 13.175 | 4.825 | 0
2916 | TORONTO BUTTONVILLE A | 5 | 1 | 12 | 8.7 | 9.3 | 0
2916 | TORONTO BUTTONVILLE A | 5 | 2 | 12 | 13.575 | 4.425 | 0
2917 | TORONTO BUTTONVILLE A | 5 | 1 | 13 | 9.2 | 8.8 | 0
2917 | TORONTO BUTTONVILLE A | 5 | 2 | 13 | 14.15 | 3.85 | 0
2918 | TORONTO BUTTONVILLE A | 5 | 1 | 14 | 11.4 | 6.6 | 0
2918 | TORONTO BUTTONVILLE A | 5 | 2 | 14 | 14.5 | 3.5 | 0
2919 | TORONTO BUTTONVILLE A | 5 | 1 | 15 | 13.8 | 4.2 | 0
2919 | TORONTO BUTTONVILLE A | 5 | 2 | 15 | 14.025 | 3.975 | 0
2920 | TORONTO BUTTONVILLE A | 5 | 1 | 16 | 14.7 | 3.3 | 0
2920 | TORONTO BUTTONVILLE A | 5 | 2 | 16 | 14.425 | 3.575 | 0
2921 | TORONTO BUTTONVILLE A | 5 | 1 | 17 | 15.1 | 2.9 | 0
2921 | TORONTO BUTTONVILLE A | 5 | 2 | 17 | 14.9 | 3.1 | 0
2922 | TORONTO BUTTONVILLE A | 5 | 1 | 18 | 14.6 | 3.4 | 0
2922 | TORONTO BUTTONVILLE A | 5 | 2 | 18 | 14.45 | 3.55 | 0
2923 | TORONTO BUTTONVILLE A | 5 | 1 | 19 | 14.3 | 3.7 | 0
2923 | TORONTO BUTTONVILLE A | 5 | 2 | 19 | 13.525 | 4.475 | 0
2924 | TORONTO BUTTONVILLE A | 5 | 1 | 20 | 13.1 | 4.9 | 0
2924 | TORONTO BUTTONVILLE A | 5 | 2 | 20 | 13.3 | 4.7 | 0
2925 | TORONTO BUTTONVILLE A | 5 | 1 | 21 | 11.4 | 6.6 | 0
2925 | TORONTO BUTTONVILLE A | 5 | 2 | 21 | 12.8 | 5.2 | 0
2926 | TORONTO BUTTONVILLE A | 5 | 1 | 22 | 10 | 8 | 0
2926 | TORONTO BUTTONVILLE A | 5 | 2 | 22 | 11.3 | 6.7 | 0
2927 | TORONTO BUTTONVILLE A | 5 | 1 | 23 | 9.5 | 8.5 | 0
2927 | TORONTO BUTTONVILLE A | 5 | 2 | 23 | 10.525 | 7.475 | 0
2928 | TORONTO BUTTONVILLE A | 5 | 1 | 24 | 7.8 | 10.2 | 0
2928 | TORONTO BUTTONVILLE A | 5 | 2 | 24 | 9.65 | 8.35 | 0
2929 | TORONTO BUTTONVILLE A | 5 | 2 | 1 | 8.8 | 9.2 | 0
2929 | TORONTO BUTTONVILLE A | 5 | 3 | 1 | 9.05 | 8.95 | 0
2930 | TORONTO BUTTONVILLE A | 5 | 2 | 2 | 6.5 | 11.5 | 0
2930 | TORONTO BUTTONVILLE A | 5 | 3 | 2 | 8.85 | 9.15 | 0
2931 | TORONTO BUTTONVILLE A | 5 | 2 | 3 | 5.5 | 12.5 | 0
2931 | TORONTO BUTTONVILLE A | 5 | 3 | 3 | 9.925 | 8.075 | 0
2932 | TORONTO BUTTONVILLE A | 5 | 2 | 4 | 5.4 | 12.6 | 0
2932 | TORONTO BUTTONVILLE A | 5 | 3 | 4 | 9.225 | 8.775 | 0
2933 | TORONTO BUTTONVILLE A | 5 | 2 | 5 | 4.9 | 13.1 | 0
2933 | TORONTO BUTTONVILLE A | 5 | 3 | 5 | 9.25 | 8.75 | 0
2934 | TORONTO BUTTONVILLE A | 5 | 2 | 6 | 4.9 | 13.1 | 0
2934 | TORONTO BUTTONVILLE A | 5 | 3 | 6 | 9.325 | 8.675 | 0
2935 | TORONTO BUTTONVILLE A | 5 | 2 | 7 | 6.6 | 11.4 | 0
2935 | TORONTO BUTTONVILLE A | 5 | 3 | 7 | 9.1 | 8.9 | 0
2936 | TORONTO BUTTONVILLE A | 5 | 2 | 8 | 10.3 | 7.7 | 0
2936 | TORONTO BUTTONVILLE A | 5 | 3 | 8 | 9.7 | 8.3 | 0
2937 | TORONTO BUTTONVILLE A | 5 | 2 | 9 | 13.6 | 4.4 | 0
2937 | TORONTO BUTTONVILLE A | 5 | 3 | 9 | 10.6 | 7.4 | 0
2938 | TORONTO BUTTONVILLE A | 5 | 2 | 10 | 15.1 | 2.9 | 0
2938 | TORONTO BUTTONVILLE A | 5 | 3 | 10 | 11.7 | 6.3 | 0
2939 | TORONTO BUTTONVILLE A | 5 | 2 | 11 | 17.7 | 0.3 | 0
2939 | TORONTO BUTTONVILLE A | 5 | 3 | 11 | 12.475 | 5.525 | 0
2940 | TORONTO BUTTONVILLE A | 5 | 2 | 12 | 15.2 | 2.8 | 0
2940 | TORONTO BUTTONVILLE A | 5 | 3 | 12 | 12.975 | 5.025 | 0
2941 | TORONTO BUTTONVILLE A | 5 | 2 | 13 | 16 | 2 | 0
2941 | TORONTO BUTTONVILLE A | 5 | 3 | 13 | 13.025 | 4.975 | 0
2942 | TORONTO BUTTONVILLE A | 5 | 2 | 14 | 15.4 | 2.6 | 0
2942 | TORONTO BUTTONVILLE A | 5 | 3 | 14 | 13.525 | 4.475 | 0
2943 | TORONTO BUTTONVILLE A | 5 | 2 | 15 | 13.9 | 4.1 | 0
2943 | TORONTO BUTTONVILLE A | 5 | 3 | 15 | 13.45 | 4.55 | 0
2944 | TORONTO BUTTONVILLE A | 5 | 2 | 16 | 13.5 | 4.5 | 0
2944 | TORONTO BUTTONVILLE A | 5 | 3 | 16 | 13.5 | 4.5 | 0
2945 | TORONTO BUTTONVILLE A | 5 | 2 | 17 | 12.6 | 5.4 | 0
2945 | TORONTO BUTTONVILLE A | 5 | 3 | 17 | 12.625 | 5.375 | 0
2946 | TORONTO BUTTONVILLE A | 5 | 2 | 18 | 13.2 | 4.8 | 0
2946 | TORONTO BUTTONVILLE A | 5 | 3 | 18 | 11.7 | 6.3 | 0
2947 | TORONTO BUTTONVILLE A | 5 | 2 | 19 | 12.1 | 5.9 | 0
2947 | TORONTO BUTTONVILLE A | 5 | 3 | 19 | 11.375 | 6.625 | 0
2948 | TORONTO BUTTONVILLE A | 5 | 2 | 20 | 11.4 | 6.6 | 0
2948 | TORONTO BUTTONVILLE A | 5 | 3 | 20 | 10.65 | 7.35 | 0
2949 | TORONTO BUTTONVILLE A | 5 | 2 | 21 | 10.4 | 7.6 | 0
2949 | TORONTO BUTTONVILLE A | 5 | 3 | 21 | 10.025 | 7.975 | 0
2950 | TORONTO BUTTONVILLE A | 5 | 2 | 22 | 9.1 | 8.9 | 0
2950 | TORONTO BUTTONVILLE A | 5 | 3 | 22 | 9.6 | 8.4 | 0
2951 | TORONTO BUTTONVILLE A | 5 | 2 | 23 | 8.7 | 9.3 | 0
2951 | TORONTO BUTTONVILLE A | 5 | 3 | 23 | 8.725 | 9.275 | 0
2952 | TORONTO BUTTONVILLE A | 5 | 2 | 24 | 7.9 | 10.1 | 0
2952 | TORONTO BUTTONVILLE A | 5 | 3 | 24 | 8.075 | 9.925 | 0
2953 | TORONTO BUTTONVILLE A | 5 | 3 | 1 | 7.3 | 10.7 | 0
2953 | TORONTO BUTTONVILLE A | 5 | 4 | 1 | 7.65 | 10.35 | 0
2954 | TORONTO BUTTONVILLE A | 5 | 3 | 2 | 12.6 | 5.4 | 0
2954 | TORONTO BUTTONVILLE A | 5 | 4 | 2 | 7.275 | 10.725 | 0
2955 | TORONTO BUTTONVILLE A | 5 | 3 | 3 | 10.9 | 7.1 | 0
2955 | TORONTO BUTTONVILLE A | 5 | 4 | 3 | 7.1 | 10.9 | 0
2956 | TORONTO BUTTONVILLE A | 5 | 3 | 4 | 10.6 | 7.4 | 0
2956 | TORONTO BUTTONVILLE A | 5 | 4 | 4 | 7.175 | 10.825 | 0
2957 | TORONTO BUTTONVILLE A | 5 | 3 | 5 | 7.8 | 10.2 | 0
2957 | TORONTO BUTTONVILLE A | 5 | 4 | 5 | 7.375 | 10.625 | 0
2958 | TORONTO BUTTONVILLE A | 5 | 3 | 6 | 7.2 | 10.8 | 0
2958 | TORONTO BUTTONVILLE A | 5 | 4 | 6 | 7.325 | 10.675 | 0
2959 | TORONTO BUTTONVILLE A | 5 | 3 | 7 | 8.9 | 9.1 | 0
2959 | TORONTO BUTTONVILLE A | 5 | 4 | 7 | 7.15 | 10.85 | 0
2960 | TORONTO BUTTONVILLE A | 5 | 3 | 8 | 13.1 | 4.9 | 0
2960 | TORONTO BUTTONVILLE A | 5 | 4 | 8 | 7.8 | 10.2 | 0
2961 | TORONTO BUTTONVILLE A | 5 | 3 | 9 | 15.2 | 2.8 | 0
2961 | TORONTO BUTTONVILLE A | 5 | 4 | 9 | 8.275 | 9.725 | 0
2962 | TORONTO BUTTONVILLE A | 5 | 3 | 10 | 17.4 | 0.6 | 0
2962 | TORONTO BUTTONVILLE A | 5 | 4 | 10 | 8.8 | 9.2 | 0
2963 | TORONTO BUTTONVILLE A | 5 | 3 | 11 | 18.8 | 0 | 0.8
2963 | TORONTO BUTTONVILLE A | 5 | 4 | 11 | 9.25 | 8.75 | 0
2964 | TORONTO BUTTONVILLE A | 5 | 3 | 12 | 19.4 | 0 | 1.4
2964 | TORONTO BUTTONVILLE A | 5 | 4 | 12 | 10.025 | 7.975 | 0
2965 | TORONTO BUTTONVILLE A | 5 | 3 | 13 | 19.5 | 0 | 1.5
2965 | TORONTO BUTTONVILLE A | 5 | 4 | 13 | 11.125 | 6.875 | 0
2966 | TORONTO BUTTONVILLE A | 5 | 3 | 14 | 20.3 | 0 | 2.3
2966 | TORONTO BUTTONVILLE A | 5 | 4 | 14 | 12.65 | 5.35 | 0
2967 | TORONTO BUTTONVILLE A | 5 | 3 | 15 | 20.1 | 0 | 2.1
2967 | TORONTO BUTTONVILLE A | 5 | 4 | 15 | 12.95 | 5.05 | 0
2968 | TORONTO BUTTONVILLE A | 5 | 3 | 16 | 19.7 | 0 | 1.7
2968 | TORONTO BUTTONVILLE A | 5 | 4 | 16 | 10.7 | 7.3 | 0
2969 | TORONTO BUTTONVILLE A | 5 | 3 | 17 | 18.3 | 0 | 0.3
2969 | TORONTO BUTTONVILLE A | 5 | 4 | 17 | 12.3 | 5.7 | 0
2970 | TORONTO BUTTONVILLE A | 5 | 3 | 18 | 17 | 1 | 0
2970 | TORONTO BUTTONVILLE A | 5 | 4 | 18 | 9.825 | 8.175 | 0
2971 | TORONTO BUTTONVILLE A | 5 | 3 | 19 | 16.1 | 1.9 | 0
2971 | TORONTO BUTTONVILLE A | 5 | 4 | 19 | 9.45 | 8.55 | 0
2972 | TORONTO BUTTONVILLE A | 5 | 3 | 20 | 13.4 | 4.6 | 0
2972 | TORONTO BUTTONVILLE A | 5 | 4 | 20 | 9.325 | 8.675 | 0
2973 | TORONTO BUTTONVILLE A | 5 | 3 | 21 | 12.3 | 5.7 | 0
2973 | TORONTO BUTTONVILLE A | 5 | 4 | 21 | 9.075 | 8.925 | 0
2974 | TORONTO BUTTONVILLE A | 5 | 3 | 22 | 11.7 | 6.3 | 0
2974 | TORONTO BUTTONVILLE A | 5 | 4 | 22 | 8.775 | 9.225 | 0
2975 | TORONTO BUTTONVILLE A | 5 | 3 | 23 | 10.7 | 7.3 | 0
2975 | TORONTO BUTTONVILLE A | 5 | 4 | 23 | 8.8 | 9.2 | 0
2976 | TORONTO BUTTONVILLE A | 5 | 3 | 24 | 9.9 | 8.1 | 0
2976 | TORONTO BUTTONVILLE A | 5 | 4 | 24 | 7.8 | 10.2 | 0
2977 | TORONTO BUTTONVILLE A | 5 | 4 | 1 | 9.2 | 8.8 | 0
2977 | TORONTO BUTTONVILLE A | 5 | 5 | 1 | 7.45 | 10.55 | 0
2978 | TORONTO BUTTONVILLE A | 5 | 4 | 2 | 8.7 | 9.3 | 0
2978 | TORONTO BUTTONVILLE A | 5 | 5 | 2 | 7.45 | 10.55 | 0
2979 | TORONTO BUTTONVILLE A | 5 | 4 | 3 | 8.3 | 9.7 | 0
2979 | TORONTO BUTTONVILLE A | 5 | 5 | 3 | 7.125 | 10.875 | 0
2980 | TORONTO BUTTONVILLE A | 5 | 4 | 4 | 7.7 | 10.3 | 0
2980 | TORONTO BUTTONVILLE A | 5 | 5 | 4 | 7.125 | 10.875 | 0
2981 | TORONTO BUTTONVILLE A | 5 | 4 | 5 | 6.8 | 11.2 | 0
2981 | TORONTO BUTTONVILLE A | 5 | 5 | 5 | 7.25 | 10.75 | 0
2982 | TORONTO BUTTONVILLE A | 5 | 4 | 6 | 6 | 12 | 0
2982 | TORONTO BUTTONVILLE A | 5 | 5 | 6 | 6.85 | 11.15 | 0
2983 | TORONTO BUTTONVILLE A | 5 | 4 | 7 | 5.8 | 12.2 | 0
2983 | TORONTO BUTTONVILLE A | 5 | 5 | 7 | 7.3 | 10.7 | 0
2984 | TORONTO BUTTONVILLE A | 5 | 4 | 8 | 5.8 | 12.2 | 0
2984 | TORONTO BUTTONVILLE A | 5 | 5 | 8 | 8.65 | 9.35 | 0
2985 | TORONTO BUTTONVILLE A | 5 | 4 | 9 | 5.6 | 12.4 | 0
2985 | TORONTO BUTTONVILLE A | 5 | 5 | 9 | 10.125 | 7.875 | 0
2986 | TORONTO BUTTONVILLE A | 5 | 4 | 10 | 6 | 12 | 0
2986 | TORONTO BUTTONVILLE A | 5 | 5 | 10 | 11.475 | 6.525 | 0
2987 | TORONTO BUTTONVILLE A | 5 | 4 | 11 | 7.7 | 10.3 | 0
2987 | TORONTO BUTTONVILLE A | 5 | 5 | 11 | 12.425 | 5.575 | 0
2988 | TORONTO BUTTONVILLE A | 5 | 4 | 12 | 7.3 | 10.7 | 0
2988 | TORONTO BUTTONVILLE A | 5 | 5 | 12 | 13.7 | 4.3 | 0
2989 | TORONTO BUTTONVILLE A | 5 | 4 | 13 | 7.7 | 10.3 | 0
2989 | TORONTO BUTTONVILLE A | 5 | 5 | 13 | 14.625 | 3.375 | 0
2990 | TORONTO BUTTONVILLE A | 5 | 4 | 14 | 8.2 | 9.8 | 0
2990 | TORONTO BUTTONVILLE A | 5 | 5 | 14 | 14.85 | 3.15 | 0
2991 | TORONTO BUTTONVILLE A | 5 | 4 | 15 | 8.4 | 9.6 | 0
2991 | TORONTO BUTTONVILLE A | 5 | 5 | 15 | 15.15 | 2.85 | 0
2992 | TORONTO BUTTONVILLE A | 5 | 4 | 16 | 8.8 | 9.2 | 0
2992 | TORONTO BUTTONVILLE A | 5 | 5 | 16 | 15.4 | 2.6 | 0
2993 | TORONTO BUTTONVILLE A | 5 | 4 | 17 | 8.4 | 9.6 | 0
2993 | TORONTO BUTTONVILLE A | 5 | 5 | 17 | 14.975 | 3.025 | 0
2994 | TORONTO BUTTONVILLE A | 5 | 4 | 18 | 7.3 | 10.7 | 0
2994 | TORONTO BUTTONVILLE A | 5 | 5 | 18 | 14.775 | 3.225 | 0
2995 | TORONTO BUTTONVILLE A | 5 | 4 | 19 | 6.1 | 11.9 | 0
2995 | TORONTO BUTTONVILLE A | 5 | 5 | 19 | 13.85 | 4.15 | 0
2996 | TORONTO BUTTONVILLE A | 5 | 4 | 20 | 4.9 | 13.1 | 0
2996 | TORONTO BUTTONVILLE A | 5 | 5 | 20 | 12.675 | 5.325 | 0
2997 | TORONTO BUTTONVILLE A | 5 | 4 | 21 | 4.1 | 13.9 | 0
2997 | TORONTO BUTTONVILLE A | 5 | 5 | 21 | 11.525 | 6.475 | 0
2998 | TORONTO BUTTONVILLE A | 5 | 4 | 22 | 3.7 | 14.3 | 0
2998 | TORONTO BUTTONVILLE A | 5 | 5 | 22 | 11.3 | 6.7 | 0
2999 | TORONTO BUTTONVILLE A | 5 | 4 | 23 | 2.9 | 15.1 | 0
2999 | TORONTO BUTTONVILLE A | 5 | 5 | 23 | 10.4 | 7.6 | 0
3000 | TORONTO BUTTONVILLE A | 5 | 4 | 24 | 2.4 | 15.6 | 0
3000 | TORONTO BUTTONVILLE A | 5 | 5 | 24 | 9.45 | 8.55 | 0
3001 | TORONTO BUTTONVILLE A | 5 | 5 | 1 | 2.6 | 15.4 | 0
3001 | TORONTO BUTTONVILLE A | 5 | 6 | 1 | 8.925 | 9.075 | 0
3002 | TORONTO BUTTONVILLE A | 5 | 5 | 2 | 2 | 16 | 0
3002 | TORONTO BUTTONVILLE A | 5 | 6 | 2 | 8.15 | 9.85 | 0
3003 | TORONTO BUTTONVILLE A | 5 | 5 | 3 | 1.3 | 16.7 | 0
3003 | TORONTO BUTTONVILLE A | 5 | 6 | 3 | 7.55 | 10.45 | 0
3004 | TORONTO BUTTONVILLE A | 5 | 5 | 4 | 0.7 | 17.3 | 0
3004 | TORONTO BUTTONVILLE A | 5 | 6 | 4 | 7.075 | 10.925 | 0
3005 | TORONTO BUTTONVILLE A | 5 | 5 | 5 | 0.3 | 17.7 | 0
3005 | TORONTO BUTTONVILLE A | 5 | 6 | 5 | 6.575 | 11.425 | 0
3006 | TORONTO BUTTONVILLE A | 5 | 5 | 6 | 0 | 18 | 0
3006 | TORONTO BUTTONVILLE A | 5 | 6 | 6 | 6.1 | 11.9 | 0
3007 | TORONTO BUTTONVILLE A | 5 | 5 | 7 | 0.5 | 17.5 | 0
3007 | TORONTO BUTTONVILLE A | 5 | 6 | 7 | 7.025 | 10.975 | 0
3008 | TORONTO BUTTONVILLE A | 5 | 5 | 8 | 2.1 | 15.9 | 0
3008 | TORONTO BUTTONVILLE A | 5 | 6 | 8 | 9.275 | 8.725 | 0
3009 | TORONTO BUTTONVILLE A | 5 | 5 | 9 | 3.1 | 14.9 | 0
3009 | TORONTO BUTTONVILLE A | 5 | 6 | 9 | 11 | 7 | 0
3010 | TORONTO BUTTONVILLE A | 5 | 5 | 10 | 4.7 | 13.3 | 0
3010 | TORONTO BUTTONVILLE A | 5 | 6 | 10 | 12.3 | 5.7 | 0
3011 | TORONTO BUTTONVILLE A | 5 | 5 | 11 | 5.8 | 12.2 | 0
3011 | TORONTO BUTTONVILLE A | 5 | 6 | 11 | 13.125 | 4.875 | 0
3012 | TORONTO BUTTONVILLE A | 5 | 5 | 12 | 7.5 | 10.5 | 0
3012 | TORONTO BUTTONVILLE A | 5 | 6 | 12 | 13.975 | 4.025 | 0
3013 | TORONTO BUTTONVILLE A | 5 | 5 | 13 | 8.3 | 9.7 | 0
3013 | TORONTO BUTTONVILLE A | 5 | 6 | 13 | 14.05 | 3.95 | 0
3014 | TORONTO BUTTONVILLE A | 5 | 5 | 14 | 10.4 | 7.6 | 0
3014 | TORONTO BUTTONVILLE A | 5 | 6 | 14 | 14.55 | 3.45 | 0
3015 | TORONTO BUTTONVILLE A | 5 | 5 | 15 | 10.4 | 7.6 | 0
3015 | TORONTO BUTTONVILLE A | 5 | 6 | 15 | 14.45 | 3.55 | 0
3016 | TORONTO BUTTONVILLE A | 5 | 5 | 16 | 10.5 | 7.5 | 0
3016 | TORONTO BUTTONVILLE A | 5 | 6 | 16 | 14.8 | 3.2 | 0
3017 | TORONTO BUTTONVILLE A | 5 | 5 | 17 | 11.1 | 6.9 | 0
3017 | TORONTO BUTTONVILLE A | 5 | 6 | 17 | 14.625 | 3.375 | 0
3018 | TORONTO BUTTONVILLE A | 5 | 5 | 18 | 10.7 | 7.3 | 0
3018 | TORONTO BUTTONVILLE A | 5 | 6 | 18 | 14.15 | 3.85 | 0
3019 | TORONTO BUTTONVILLE A | 5 | 5 | 19 | 10.1 | 7.9 | 0
3019 | TORONTO BUTTONVILLE A | 5 | 6 | 19 | 12.7 | 5.3 | 0
3020 | TORONTO BUTTONVILLE A | 5 | 5 | 20 | 9 | 9 | 0
3020 | TORONTO BUTTONVILLE A | 5 | 6 | 20 | 11.475 | 6.525 | 0
3021 | TORONTO BUTTONVILLE A | 5 | 5 | 21 | 7.3 | 10.7 | 0
3021 | TORONTO BUTTONVILLE A | 5 | 6 | 21 | 11.075 | 6.925 | 0
3022 | TORONTO BUTTONVILLE A | 5 | 5 | 22 | 5.3 | 12.7 | 0
3022 | TORONTO BUTTONVILLE A | 5 | 6 | 22 | 10.175 | 7.825 | 0
3023 | TORONTO BUTTONVILLE A | 5 | 5 | 23 | 4.2 | 13.8 | 0
3023 | TORONTO BUTTONVILLE A | 5 | 6 | 23 | 9.4 | 8.6 | 0
3024 | TORONTO BUTTONVILLE A | 5 | 5 | 24 | 4.2 | 13.8 | 0
3024 | TORONTO BUTTONVILLE A | 5 | 6 | 24 | 9.075 | 8.925 | 0
3025 | TORONTO BUTTONVILLE A | 5 | 6 | 1 | 3.1 | 14.9 | 0
3025 | TORONTO BUTTONVILLE A | 5 | 7 | 1 | 8.75 | 9.25 | 0
3026 | TORONTO BUTTONVILLE A | 5 | 6 | 2 | 2.3 | 15.7 | 0
3026 | TORONTO BUTTONVILLE A | 5 | 7 | 2 | 8.075 | 9.925 | 0
3027 | TORONTO BUTTONVILLE A | 5 | 6 | 3 | 2.1 | 15.9 | 0
3027 | TORONTO BUTTONVILLE A | 5 | 7 | 3 | 7.4 | 10.6 | 0
3028 | TORONTO BUTTONVILLE A | 5 | 6 | 4 | 1.9 | 16.1 | 0
3028 | TORONTO BUTTONVILLE A | 5 | 7 | 4 | 6.475 | 11.525 | 0
3029 | TORONTO BUTTONVILLE A | 5 | 6 | 5 | 2 | 16 | 0
3029 | TORONTO BUTTONVILLE A | 5 | 7 | 5 | 6.625 | 11.375 | 0
3030 | TORONTO BUTTONVILLE A | 5 | 6 | 6 | 2.6 | 15.4 | 0
3030 | TORONTO BUTTONVILLE A | 5 | 7 | 6 | 6.575 | 11.425 | 0
3031 | TORONTO BUTTONVILLE A | 5 | 6 | 7 | 3.1 | 14.9 | 0
3031 | TORONTO BUTTONVILLE A | 5 | 7 | 7 | 6.6 | 11.4 | 0
3032 | TORONTO BUTTONVILLE A | 5 | 6 | 8 | 5.1 | 12.9 | 0
3032 | TORONTO BUTTONVILLE A | 5 | 7 | 8 | 7.1 | 10.9 | 0
3033 | TORONTO BUTTONVILLE A | 5 | 6 | 9 | 6.8 | 11.2 | 0
3033 | TORONTO BUTTONVILLE A | 5 | 7 | 9 | 7.85 | 10.15 | 0
3034 | TORONTO BUTTONVILLE A | 5 | 6 | 10 | 9 | 9 | 0
3034 | TORONTO BUTTONVILLE A | 5 | 7 | 10 | 8.35 | 9.65 | 0
3035 | TORONTO BUTTONVILLE A | 5 | 6 | 11 | 10.5 | 7.5 | 0
3035 | TORONTO BUTTONVILLE A | 5 | 7 | 11 | 9.7 | 8.3 | 0
3036 | TORONTO BUTTONVILLE A | 5 | 6 | 12 | 11.5 | 6.5 | 0
3036 | TORONTO BUTTONVILLE A | 5 | 7 | 12 | 10.25 | 7.75 | 0
3037 | TORONTO BUTTONVILLE A | 5 | 6 | 13 | 11.4 | 6.6 | 0
3037 | TORONTO BUTTONVILLE A | 5 | 7 | 13 | 10.725 | 7.275 | 0
3038 | TORONTO BUTTONVILLE A | 5 | 6 | 14 | 12.7 | 5.3 | 0
3038 | TORONTO BUTTONVILLE A | 5 | 7 | 14 | 11.45 | 6.55 | 0
3039 | TORONTO BUTTONVILLE A | 5 | 6 | 15 | 12.8 | 5.2 | 0
3039 | TORONTO BUTTONVILLE A | 5 | 7 | 15 | 12.35 | 5.65 | 0
3040 | TORONTO BUTTONVILLE A | 5 | 6 | 16 | 13.8 | 4.2 | 0
3040 | TORONTO BUTTONVILLE A | 5 | 7 | 16 | 12.425 | 5.575 | 0
3041 | TORONTO BUTTONVILLE A | 5 | 6 | 17 | 13.8 | 4.2 | 0
3041 | TORONTO BUTTONVILLE A | 5 | 7 | 17 | 12.375 | 5.625 | 0
3042 | TORONTO BUTTONVILLE A | 5 | 6 | 18 | 13.8 | 4.2 | 0
3042 | TORONTO BUTTONVILLE A | 5 | 7 | 18 | 11.75 | 6.25 | 0
3043 | TORONTO BUTTONVILLE A | 5 | 6 | 19 | 12.8 | 5.2 | 0
3043 | TORONTO BUTTONVILLE A | 5 | 7 | 19 | 11.1 | 6.9 | 0
3044 | TORONTO BUTTONVILLE A | 5 | 6 | 20 | 11.1 | 6.9 | 0
3044 | TORONTO BUTTONVILLE A | 5 | 7 | 20 | 10.15 | 7.85 | 0
3045 | TORONTO BUTTONVILLE A | 5 | 6 | 21 | 9.5 | 8.5 | 0
3045 | TORONTO BUTTONVILLE A | 5 | 7 | 21 | 8.725 | 9.275 | 0
3046 | TORONTO BUTTONVILLE A | 5 | 6 | 22 | 8.6 | 9.4 | 0
3046 | TORONTO BUTTONVILLE A | 5 | 7 | 22 | 7.675 | 10.325 | 0
3047 | TORONTO BUTTONVILLE A | 5 | 6 | 23 | 8.4 | 9.6 | 0
3047 | TORONTO BUTTONVILLE A | 5 | 7 | 23 | 6.675 | 11.325 | 0
3048 | TORONTO BUTTONVILLE A | 5 | 6 | 24 | 7.8 | 10.2 | 0
3048 | TORONTO BUTTONVILLE A | 5 | 7 | 24 | 5.9 | 12.1 | 0
3049 | TORONTO BUTTONVILLE A | 5 | 7 | 1 | 7.1 | 10.9 | 0
3049 | TORONTO BUTTONVILLE A | 5 | 8 | 1 | 5.4 | 12.6 | 0
3050 | TORONTO BUTTONVILLE A | 5 | 7 | 2 | 5.9 | 12.1 | 0
3050 | TORONTO BUTTONVILLE A | 5 | 8 | 2 | 4.8 | 13.2 | 0
3051 | TORONTO BUTTONVILLE A | 5 | 7 | 3 | 4.5 | 13.5 | 0
3051 | TORONTO BUTTONVILLE A | 5 | 8 | 3 | 4.025 | 13.975 | 0
3052 | TORONTO BUTTONVILLE A | 5 | 7 | 4 | 6.1 | 11.9 | 0
3052 | TORONTO BUTTONVILLE A | 5 | 8 | 4 | 3.575 | 14.425 | 0
3053 | TORONTO BUTTONVILLE A | 5 | 7 | 5 | 6.1 | 11.9 | 0
3053 | TORONTO BUTTONVILLE A | 5 | 8 | 5 | 3.225 | 14.775 | 0
3054 | TORONTO BUTTONVILLE A | 5 | 7 | 6 | 6.4 | 11.6 | 0
3054 | TORONTO BUTTONVILLE A | 5 | 8 | 6 | 2.95 | 15.05 | 0
3055 | TORONTO BUTTONVILLE A | 5 | 7 | 7 | 7.8 | 10.2 | 0
3055 | TORONTO BUTTONVILLE A | 5 | 8 | 7 | 4.45 | 13.55 | 0
3056 | TORONTO BUTTONVILLE A | 5 | 7 | 8 | 7.6 | 10.4 | 0
3056 | TORONTO BUTTONVILLE A | 5 | 8 | 8 | 6.8 | 11.2 | 0
3057 | TORONTO BUTTONVILLE A | 5 | 7 | 9 | 8.9 | 9.1 | 0
3057 | TORONTO BUTTONVILLE A | 5 | 8 | 9 | 8.725 | 9.275 | 0
3058 | TORONTO BUTTONVILLE A | 5 | 7 | 10 | 11.4 | 6.6 | 0
3058 | TORONTO BUTTONVILLE A | 5 | 8 | 10 | 10.625 | 7.375 | 0
3059 | TORONTO BUTTONVILLE A | 5 | 7 | 11 | 11.3 | 6.7 | 0
3059 | TORONTO BUTTONVILLE A | 5 | 8 | 11 | 11.775 | 6.225 | 0
3060 | TORONTO BUTTONVILLE A | 5 | 7 | 12 | 10.2 | 7.8 | 0
3060 | TORONTO BUTTONVILLE A | 5 | 8 | 12 | 12.55 | 5.45 | 0
3061 | TORONTO BUTTONVILLE A | 5 | 7 | 13 | 9.9 | 8.1 | 0
3061 | TORONTO BUTTONVILLE A | 5 | 8 | 13 | 13.025 | 4.975 | 0
3062 | TORONTO BUTTONVILLE A | 5 | 7 | 14 | 5.6 | 12.4 | 0
3062 | TORONTO BUTTONVILLE A | 5 | 8 | 14 | 12.825 | 5.175 | 0
3063 | TORONTO BUTTONVILLE A | 5 | 7 | 15 | 4.9 | 13.1 | 0
3063 | TORONTO BUTTONVILLE A | 5 | 8 | 15 | 13.475 | 4.525 | 0
3064 | TORONTO BUTTONVILLE A | 5 | 7 | 16 | 7.3 | 10.7 | 0
3064 | TORONTO BUTTONVILLE A | 5 | 8 | 16 | 13.675 | 4.325 | 0
3065 | TORONTO BUTTONVILLE A | 5 | 7 | 17 | 8.4 | 9.6 | 0
3065 | TORONTO BUTTONVILLE A | 5 | 8 | 17 | 13.675 | 4.325 | 0
3066 | TORONTO BUTTONVILLE A | 5 | 7 | 18 | 8.9 | 9.1 | 0
3066 | TORONTO BUTTONVILLE A | 5 | 8 | 18 | 13.2 | 4.8 | 0
3067 | TORONTO BUTTONVILLE A | 5 | 7 | 19 | 8.8 | 9.2 | 0
3067 | TORONTO BUTTONVILLE A | 5 | 8 | 19 | 12.15 | 5.85 | 0
3068 | TORONTO BUTTONVILLE A | 5 | 7 | 20 | 6.7 | 11.3 | 0
3068 | TORONTO BUTTONVILLE A | 5 | 8 | 20 | 10.35 | 7.65 | 0
3069 | TORONTO BUTTONVILLE A | 5 | 7 | 21 | 4.7 | 13.3 | 0
3069 | TORONTO BUTTONVILLE A | 5 | 8 | 21 | 9.2 | 8.8 | 0
3070 | TORONTO BUTTONVILLE A | 5 | 7 | 22 | 3.8 | 14.2 | 0
3070 | TORONTO BUTTONVILLE A | 5 | 8 | 22 | 8.775 | 9.225 | 0
3071 | TORONTO BUTTONVILLE A | 5 | 7 | 23 | 3.5 | 14.5 | 0
3071 | TORONTO BUTTONVILLE A | 5 | 8 | 23 | 8.15 | 9.85 | 0
3072 | TORONTO BUTTONVILLE A | 5 | 7 | 24 | 2.6 | 15.4 | 0
3072 | TORONTO BUTTONVILLE A | 5 | 8 | 24 | 7.85 | 10.15 | 0
3073 | TORONTO BUTTONVILLE A | 5 | 8 | 1 | 2.2 | 15.8 | 0
3073 | TORONTO BUTTONVILLE A | 5 | 9 | 1 | 7.875 | 10.125 | 0
3074 | TORONTO BUTTONVILLE A | 5 | 8 | 2 | 1.1 | 16.9 | 0
3074 | TORONTO BUTTONVILLE A | 5 | 9 | 2 | 7.65 | 10.35 | 0
3075 | TORONTO BUTTONVILLE A | 5 | 8 | 3 | 0.4 | 17.6 | 0
3075 | TORONTO BUTTONVILLE A | 5 | 9 | 3 | 7.125 | 10.875 | 0
3076 | TORONTO BUTTONVILLE A | 5 | 8 | 4 | -0.2 | 18.2 | 0
3076 | TORONTO BUTTONVILLE A | 5 | 9 | 4 | 6.975 | 11.025 | 0
3077 | TORONTO BUTTONVILLE A | 5 | 8 | 5 | 0 | 18 | 0
3077 | TORONTO BUTTONVILLE A | 5 | 9 | 5 | 6.775 | 11.225 | 0
3078 | TORONTO BUTTONVILLE A | 5 | 8 | 6 | -0.2 | 18.2 | 0
3078 | TORONTO BUTTONVILLE A | 5 | 9 | 6 | 5.975 | 12.025 | 0
3079 | TORONTO BUTTONVILLE A | 5 | 8 | 7 | 0.4 | 17.6 | 0
3079 | TORONTO BUTTONVILLE A | 5 | 9 | 7 | 6.65 | 11.35 | 0
3080 | TORONTO BUTTONVILLE A | 5 | 8 | 8 | 0.6 | 17.4 | 0
3080 | TORONTO BUTTONVILLE A | 5 | 9 | 8 | 8.425 | 9.575 | 0
3081 | TORONTO BUTTONVILLE A | 5 | 8 | 9 | 1.5 | 16.5 | 0
3081 | TORONTO BUTTONVILLE A | 5 | 9 | 9 | 9.925 | 8.075 | 0
3082 | TORONTO BUTTONVILLE A | 5 | 8 | 10 | 2.5 | 15.5 | 0
3082 | TORONTO BUTTONVILLE A | 5 | 9 | 10 | 10.85 | 7.15 | 0
3083 | TORONTO BUTTONVILLE A | 5 | 8 | 11 | 4 | 14 | 0
3083 | TORONTO BUTTONVILLE A | 5 | 9 | 11 | 11.8 | 6.2 | 0
3084 | TORONTO BUTTONVILLE A | 5 | 8 | 12 | 4.2 | 13.8 | 0
3084 | TORONTO BUTTONVILLE A | 5 | 9 | 12 | 12.875 | 5.125 | 0
3085 | TORONTO BUTTONVILLE A | 5 | 8 | 13 | 4 | 14 | 0
3085 | TORONTO BUTTONVILLE A | 5 | 9 | 13 | 14.075 | 3.925 | 0
3086 | TORONTO BUTTONVILLE A | 5 | 8 | 14 | 3.8 | 14.2 | 0
3086 | TORONTO BUTTONVILLE A | 5 | 9 | 14 | 15.025 | 2.975 | 0
3087 | TORONTO BUTTONVILLE A | 5 | 8 | 15 | 3.4 | 14.6 | 0
3087 | TORONTO BUTTONVILLE A | 5 | 9 | 15 | 15.1 | 2.9 | 0
3088 | TORONTO BUTTONVILLE A | 5 | 8 | 16 | 3.4 | 14.6 | 0
3088 | TORONTO BUTTONVILLE A | 5 | 9 | 16 | 15.85 | 2.15 | 0
3089 | TORONTO BUTTONVILLE A | 5 | 8 | 17 | 3.6 | 14.4 | 0
3089 | TORONTO BUTTONVILLE A | 5 | 9 | 17 | 14.65 | 3.35 | 0
3090 | TORONTO BUTTONVILLE A | 5 | 8 | 18 | 2.8 | 15.2 | 0
3090 | TORONTO BUTTONVILLE A | 5 | 9 | 18 | 13.35 | 4.65 | 0
3091 | TORONTO BUTTONVILLE A | 5 | 8 | 19 | 1.4 | 16.6 | 0
3091 | TORONTO BUTTONVILLE A | 5 | 9 | 19 | 13.35 | 4.65 | 0
3092 | TORONTO BUTTONVILLE A | 5 | 8 | 20 | 0.2 | 17.8 | 0
3092 | TORONTO BUTTONVILLE A | 5 | 9 | 20 | 12.25 | 5.75 | 0
3093 | TORONTO BUTTONVILLE A | 5 | 8 | 21 | -0.8 | 18.8 | 0
3093 | TORONTO BUTTONVILLE A | 5 | 9 | 21 | 11.25 | 6.75 | 0
3094 | TORONTO BUTTONVILLE A | 5 | 8 | 22 | -1.3 | 19.3 | 0
3094 | TORONTO BUTTONVILLE A | 5 | 9 | 22 | 10.975 | 7.025 | 0
3095 | TORONTO BUTTONVILLE A | 5 | 8 | 23 | -1.7 | 19.7 | 0
3095 | TORONTO BUTTONVILLE A | 5 | 9 | 23 | 10.75 | 7.25 | 0
3096 | TORONTO BUTTONVILLE A | 5 | 8 | 24 | -2.3 | 20.3 | 0
3096 | TORONTO BUTTONVILLE A | 5 | 9 | 24 | 10.3 | 7.7 | 0
3097 | TORONTO BUTTONVILLE A | 5 | 9 | 1 | -2.9 | 20.9 | 0
3097 | TORONTO BUTTONVILLE A | 5 | 10 | 1 | 10.05 | 7.95 | 0
3098 | TORONTO BUTTONVILLE A | 5 | 9 | 2 | -2.9 | 20.9 | 0
3098 | TORONTO BUTTONVILLE A | 5 | 10 | 2 | 9.825 | 8.175 | 0
3099 | TORONTO BUTTONVILLE A | 5 | 9 | 3 | -3.4 | 21.4 | 0
3099 | TORONTO BUTTONVILLE A | 5 | 10 | 3 | 9.525 | 8.475 | 0
3100 | TORONTO BUTTONVILLE A | 5 | 9 | 4 | -3.9 | 21.9 | 0
3100 | TORONTO BUTTONVILLE A | 5 | 10 | 4 | 9.95 | 8.05 | 0
3101 | TORONTO BUTTONVILLE A | 5 | 9 | 5 | -4 | 22 | 0
3101 | TORONTO BUTTONVILLE A | 5 | 10 | 5 | 9.7 | 8.3 | 0
3102 | TORONTO BUTTONVILLE A | 5 | 9 | 6 | -4 | 22 | 0
3102 | TORONTO BUTTONVILLE A | 5 | 10 | 6 | 9.4 | 8.6 | 0
3103 | TORONTO BUTTONVILLE A | 5 | 9 | 7 | -2.9 | 20.9 | 0
3103 | TORONTO BUTTONVILLE A | 5 | 10 | 7 | 9.85 | 8.15 | 0
3104 | TORONTO BUTTONVILLE A | 5 | 9 | 8 | -1.8 | 19.8 | 0
3104 | TORONTO BUTTONVILLE A | 5 | 10 | 8 | 10.775 | 7.225 | 0
3105 | TORONTO BUTTONVILLE A | 5 | 9 | 9 | -0.4 | 18.4 | 0
3105 | TORONTO BUTTONVILLE A | 5 | 10 | 9 | 11.825 | 6.175 | 0
3106 | TORONTO BUTTONVILLE A | 5 | 9 | 10 | 1.4 | 16.6 | 0
3106 | TORONTO BUTTONVILLE A | 5 | 10 | 10 | 12.6 | 5.4 | 0
3107 | TORONTO BUTTONVILLE A | 5 | 9 | 11 | 2.5 | 15.5 | 0
3107 | TORONTO BUTTONVILLE A | 5 | 10 | 11 | 12.525 | 5.475 | 0
3108 | TORONTO BUTTONVILLE A | 5 | 9 | 12 | 1.7 | 16.3 | 0
3108 | TORONTO BUTTONVILLE A | 5 | 10 | 12 | 12.775 | 5.225 | 0
3109 | TORONTO BUTTONVILLE A | 5 | 9 | 13 | 1.8 | 16.2 | 0
3109 | TORONTO BUTTONVILLE A | 5 | 10 | 13 | 12.6 | 5.4 | 0
3110 | TORONTO BUTTONVILLE A | 5 | 9 | 14 | 2.4 | 15.6 | 0
3110 | TORONTO BUTTONVILLE A | 5 | 10 | 14 | 13.5 | 4.5 | 0
3111 | TORONTO BUTTONVILLE A | 5 | 9 | 15 | 3.3 | 14.7 | 0
3111 | TORONTO BUTTONVILLE A | 5 | 10 | 15 | 13.175 | 4.825 | 0
3112 | TORONTO BUTTONVILLE A | 5 | 9 | 16 | 4.2 | 13.8 | 0
3112 | TORONTO BUTTONVILLE A | 5 | 10 | 16 | 13 | 5 | 0
3113 | TORONTO BUTTONVILLE A | 5 | 9 | 17 | 4 | 14 | 0
3113 | TORONTO BUTTONVILLE A | 5 | 10 | 17 | 12.25 | 5.75 | 0
3114 | TORONTO BUTTONVILLE A | 5 | 9 | 18 | 4.7 | 13.3 | 0
3114 | TORONTO BUTTONVILLE A | 5 | 10 | 18 | 11.025 | 6.975 | 0
3115 | TORONTO BUTTONVILLE A | 5 | 9 | 19 | 4.3 | 13.7 | 0
3115 | TORONTO BUTTONVILLE A | 5 | 10 | 19 | 9.625 | 8.375 | 0
3116 | TORONTO BUTTONVILLE A | 5 | 9 | 20 | 3.8 | 14.2 | 0
3116 | TORONTO BUTTONVILLE A | 5 | 10 | 20 | 9.2 | 8.8 | 0
3117 | TORONTO BUTTONVILLE A | 5 | 9 | 21 | 3.3 | 14.7 | 0
3117 | TORONTO BUTTONVILLE A | 5 | 10 | 21 | 8.6 | 9.4 | 0
3118 | TORONTO BUTTONVILLE A | 5 | 9 | 22 | 2.7 | 15.3 | 0
3118 | TORONTO BUTTONVILLE A | 5 | 10 | 22 | 7.75 | 10.25 | 0
3119 | TORONTO BUTTONVILLE A | 5 | 9 | 23 | 1.8 | 16.2 | 0
3119 | TORONTO BUTTONVILLE A | 5 | 10 | 23 | 6.725 | 11.275 | 0
3120 | TORONTO BUTTONVILLE A | 5 | 9 | 24 | 1 | 17 | 0
3120 | TORONTO BUTTONVILLE A | 5 | 10 | 24 | 5.825 | 12.175 | 0
3121 | TORONTO BUTTONVILLE A | 5 | 10 | 1 | 0.8 | 17.2 | 0
3121 | TORONTO BUTTONVILLE A | 5 | 11 | 1 | 5 | 13 | 0
3122 | TORONTO BUTTONVILLE A | 5 | 10 | 2 | 1.5 | 16.5 | 0
3122 | TORONTO BUTTONVILLE A | 5 | 11 | 2 | 4.65 | 13.35 | 0
3123 | TORONTO BUTTONVILLE A | 5 | 10 | 3 | 1.6 | 16.4 | 0
3123 | TORONTO BUTTONVILLE A | 5 | 11 | 3 | 4.45 | 13.55 | 0
3124 | TORONTO BUTTONVILLE A | 5 | 10 | 4 | 1.6 | 16.4 | 0
3124 | TORONTO BUTTONVILLE A | 5 | 11 | 4 | 4.2 | 13.8 | 0
3125 | TORONTO BUTTONVILLE A | 5 | 10 | 5 | 1 | 17 | 0
3125 | TORONTO BUTTONVILLE A | 5 | 11 | 5 | 3.925 | 14.075 | 0
3126 | TORONTO BUTTONVILLE A | 5 | 10 | 6 | 0.1 | 17.9 | 0
3126 | TORONTO BUTTONVILLE A | 5 | 11 | 6 | 3.75 | 14.25 | 0
3127 | TORONTO BUTTONVILLE A | 5 | 10 | 7 | 0.9 | 17.1 | 0
3127 | TORONTO BUTTONVILLE A | 5 | 11 | 7 | 4.45 | 13.55 | 0
3128 | TORONTO BUTTONVILLE A | 5 | 10 | 8 | 3.5 | 14.5 | 0
3128 | TORONTO BUTTONVILLE A | 5 | 11 | 8 | 5.825 | 12.175 | 0
3129 | TORONTO BUTTONVILLE A | 5 | 10 | 9 | 3.7 | 14.3 | 0
3129 | TORONTO BUTTONVILLE A | 5 | 11 | 9 | 6.975 | 11.025 | 0
3130 | TORONTO BUTTONVILLE A | 5 | 10 | 10 | 5.3 | 12.7 | 0
3130 | TORONTO BUTTONVILLE A | 5 | 11 | 10 | 8.2 | 9.8 | 0
3131 | TORONTO BUTTONVILLE A | 5 | 10 | 11 | 4 | 14 | 0
3131 | TORONTO BUTTONVILLE A | 5 | 11 | 11 | 8.7 | 9.3 | 0
3132 | TORONTO BUTTONVILLE A | 5 | 10 | 12 | 3.1 | 14.9 | 0
3132 | TORONTO BUTTONVILLE A | 5 | 11 | 12 | 10 | 8 | 0
3133 | TORONTO BUTTONVILLE A | 5 | 10 | 13 | 3 | 15 | 0
3133 | TORONTO BUTTONVILLE A | 5 | 11 | 13 | 10.275 | 7.725 | 0
3134 | TORONTO BUTTONVILLE A | 5 | 10 | 14 | 4.2 | 13.8 | 0
3134 | TORONTO BUTTONVILLE A | 5 | 11 | 14 | 11.175 | 6.825 | 0
3135 | TORONTO BUTTONVILLE A | 5 | 10 | 15 | 5.2 | 12.8 | 0
3135 | TORONTO BUTTONVILLE A | 5 | 11 | 15 | 11.2 | 6.8 | 0
3136 | TORONTO BUTTONVILLE A | 5 | 10 | 16 | 5.5 | 12.5 | 0
3136 | TORONTO BUTTONVILLE A | 5 | 11 | 16 | 11.4 | 6.6 | 0
3137 | TORONTO BUTTONVILLE A | 5 | 10 | 17 | 5.5 | 12.5 | 0
3137 | TORONTO BUTTONVILLE A | 5 | 11 | 17 | 11.45 | 6.55 | 0
3138 | TORONTO BUTTONVILLE A | 5 | 10 | 18 | 5.3 | 12.7 | 0
3138 | TORONTO BUTTONVILLE A | 5 | 11 | 18 | 11.25 | 6.75 | 0
3139 | TORONTO BUTTONVILLE A | 5 | 10 | 19 | 5.2 | 12.8 | 0
3139 | TORONTO BUTTONVILLE A | 5 | 11 | 19 | 10.7 | 7.3 | 0
3140 | TORONTO BUTTONVILLE A | 5 | 10 | 20 | 4.9 | 13.1 | 0
3140 | TORONTO BUTTONVILLE A | 5 | 11 | 20 | 9.875 | 8.125 | 0
3141 | TORONTO BUTTONVILLE A | 5 | 10 | 21 | 4.4 | 13.6 | 0
3141 | TORONTO BUTTONVILLE A | 5 | 11 | 21 | 9.05 | 8.95 | 0
3142 | TORONTO BUTTONVILLE A | 5 | 10 | 22 | 4.2 | 13.8 | 0
3142 | TORONTO BUTTONVILLE A | 5 | 11 | 22 | 8.75 | 9.25 | 0
3143 | TORONTO BUTTONVILLE A | 5 | 10 | 23 | 3.7 | 14.3 | 0
3143 | TORONTO BUTTONVILLE A | 5 | 11 | 23 | 8.175 | 9.825 | 0
3144 | TORONTO BUTTONVILLE A | 5 | 10 | 24 | 3.5 | 14.5 | 0
3144 | TORONTO BUTTONVILLE A | 5 | 11 | 24 | 8.025 | 9.975 | 0
3145 | TORONTO BUTTONVILLE A | 5 | 11 | 1 | 3.2 | 14.8 | 0
3145 | TORONTO BUTTONVILLE A | 5 | 12 | 1 | 7.5 | 10.5 | 0
3146 | TORONTO BUTTONVILLE A | 5 | 11 | 2 | 2 | 16 | 0
3146 | TORONTO BUTTONVILLE A | 5 | 12 | 2 | 6.65 | 11.35 | 0
3147 | TORONTO BUTTONVILLE A | 5 | 11 | 3 | 1.7 | 16.3 | 0
3147 | TORONTO BUTTONVILLE A | 5 | 12 | 3 | 6.65 | 11.35 | 0
3148 | TORONTO BUTTONVILLE A | 5 | 11 | 4 | 1 | 17 | 0
3148 | TORONTO BUTTONVILLE A | 5 | 12 | 4 | 6.525 | 11.475 | 0
3149 | TORONTO BUTTONVILLE A | 5 | 11 | 5 | 0.7 | 17.3 | 0
3149 | TORONTO BUTTONVILLE A | 5 | 12 | 5 | 6.35 | 11.65 | 0
3150 | TORONTO BUTTONVILLE A | 5 | 11 | 6 | 0.7 | 17.3 | 0
3150 | TORONTO BUTTONVILLE A | 5 | 12 | 6 | 6.35 | 11.65 | 0
3151 | TORONTO BUTTONVILLE A | 5 | 11 | 7 | 0.6 | 17.4 | 0
3151 | TORONTO BUTTONVILLE A | 5 | 12 | 7 | 6.825 | 11.175 | 0
3152 | TORONTO BUTTONVILLE A | 5 | 11 | 8 | 0.9 | 17.1 | 0
3152 | TORONTO BUTTONVILLE A | 5 | 12 | 8 | 8.7 | 9.3 | 0
3153 | TORONTO BUTTONVILLE A | 5 | 11 | 9 | 1.9 | 16.1 | 0
3153 | TORONTO BUTTONVILLE A | 5 | 12 | 9 | 9.65 | 8.35 | 0
3154 | TORONTO BUTTONVILLE A | 5 | 11 | 10 | 2.4 | 15.6 | 0
3154 | TORONTO BUTTONVILLE A | 5 | 12 | 10 | 10.25 | 7.75 | 0
3155 | TORONTO BUTTONVILLE A | 5 | 11 | 11 | 3.2 | 14.8 | 0
3155 | TORONTO BUTTONVILLE A | 5 | 12 | 11 | 11.325 | 6.675 | 0
3156 | TORONTO BUTTONVILLE A | 5 | 11 | 12 | 4 | 14 | 0
3156 | TORONTO BUTTONVILLE A | 5 | 12 | 12 | 12.25 | 5.75 | 0
3157 | TORONTO BUTTONVILLE A | 5 | 11 | 13 | 5.3 | 12.7 | 0
3157 | TORONTO BUTTONVILLE A | 5 | 12 | 13 | 13.125 | 4.875 | 0
3158 | TORONTO BUTTONVILLE A | 5 | 11 | 14 | 5.8 | 12.2 | 0
3158 | TORONTO BUTTONVILLE A | 5 | 12 | 14 | 13.725 | 4.275 | 0
3159 | TORONTO BUTTONVILLE A | 5 | 11 | 15 | 5.2 | 12.8 | 0
3159 | TORONTO BUTTONVILLE A | 5 | 12 | 15 | 13.275 | 4.725 | 0
3160 | TORONTO BUTTONVILLE A | 5 | 11 | 16 | 5.5 | 12.5 | 0
3160 | TORONTO BUTTONVILLE A | 5 | 12 | 16 | 13.575 | 4.425 | 0
3161 | TORONTO BUTTONVILLE A | 5 | 11 | 17 | 5.9 | 12.1 | 0
3161 | TORONTO BUTTONVILLE A | 5 | 12 | 17 | 13.325 | 4.675 | 0
3162 | TORONTO BUTTONVILLE A | 5 | 11 | 18 | 5.9 | 12.1 | 0
3162 | TORONTO BUTTONVILLE A | 5 | 12 | 18 | 12.95 | 5.05 | 0
3163 | TORONTO BUTTONVILLE A | 5 | 11 | 19 | 4.9 | 13.1 | 0
3163 | TORONTO BUTTONVILLE A | 5 | 12 | 19 | 12.425 | 5.575 | 0
3164 | TORONTO BUTTONVILLE A | 5 | 11 | 20 | 4.5 | 13.5 | 0
3164 | TORONTO BUTTONVILLE A | 5 | 12 | 20 | 11.425 | 6.575 | 0
3165 | TORONTO BUTTONVILLE A | 5 | 11 | 21 | 3.1 | 14.9 | 0
3165 | TORONTO BUTTONVILLE A | 5 | 12 | 21 | 10.475 | 7.525 | 0
3166 | TORONTO BUTTONVILLE A | 5 | 11 | 22 | 1.9 | 16.1 | 0
3166 | TORONTO BUTTONVILLE A | 5 | 12 | 22 | 10.175 | 7.825 | 0
3167 | TORONTO BUTTONVILLE A | 5 | 11 | 23 | 0.9 | 17.1 | 0
3167 | TORONTO BUTTONVILLE A | 5 | 12 | 23 | 9.9 | 8.1 | 0
3168 | TORONTO BUTTONVILLE A | 5 | 11 | 24 | 0.6 | 17.4 | 0
3168 | TORONTO BUTTONVILLE A | 5 | 12 | 24 | 9.2 | 8.8 | 0
3169 | TORONTO BUTTONVILLE A | 5 | 12 | 1 | -0.2 | 18.2 | 0
3169 | TORONTO BUTTONVILLE A | 5 | 13 | 1 | 8.775 | 9.225 | 0
3170 | TORONTO BUTTONVILLE A | 5 | 12 | 2 | -0.9 | 18.9 | 0
3170 | TORONTO BUTTONVILLE A | 5 | 13 | 2 | 8.5 | 9.5 | 0
3171 | TORONTO BUTTONVILLE A | 5 | 12 | 3 | -1.3 | 19.3 | 0
3171 | TORONTO BUTTONVILLE A | 5 | 13 | 3 | 7.975 | 10.025 | 0
3172 | TORONTO BUTTONVILLE A | 5 | 12 | 4 | -1.5 | 19.5 | 0
3172 | TORONTO BUTTONVILLE A | 5 | 13 | 4 | 7.725 | 10.275 | 0
3173 | TORONTO BUTTONVILLE A | 5 | 12 | 5 | -2 | 20 | 0
3173 | TORONTO BUTTONVILLE A | 5 | 13 | 5 | 7.525 | 10.475 | 0
3174 | TORONTO BUTTONVILLE A | 5 | 12 | 6 | -2.3 | 20.3 | 0
3174 | TORONTO BUTTONVILLE A | 5 | 13 | 6 | 7.475 | 10.525 | 0
3175 | TORONTO BUTTONVILLE A | 5 | 12 | 7 | -0.8 | 18.8 | 0
3175 | TORONTO BUTTONVILLE A | 5 | 13 | 7 | 8.025 | 9.975 | 0
3176 | TORONTO BUTTONVILLE A | 5 | 12 | 8 | 0.6 | 17.4 | 0
3176 | TORONTO BUTTONVILLE A | 5 | 13 | 8 | 8.825 | 9.175 | 0
3177 | TORONTO BUTTONVILLE A | 5 | 12 | 9 | 2.4 | 15.6 | 0
3177 | TORONTO BUTTONVILLE A | 5 | 13 | 9 | 10.225 | 7.775 | 0
3178 | TORONTO BUTTONVILLE A | 5 | 12 | 10 | 4.3 | 13.7 | 0
3178 | TORONTO BUTTONVILLE A | 5 | 13 | 10 | 11.35 | 6.65 | 0
3179 | TORONTO BUTTONVILLE A | 5 | 12 | 11 | 5.7 | 12.3 | 0
3179 | TORONTO BUTTONVILLE A | 5 | 13 | 11 | 12.725 | 5.275 | 0
3180 | TORONTO BUTTONVILLE A | 5 | 12 | 12 | 7.3 | 10.7 | 0
3180 | TORONTO BUTTONVILLE A | 5 | 13 | 12 | 13.525 | 4.475 | 0
3181 | TORONTO BUTTONVILLE A | 5 | 12 | 13 | 6.8 | 11.2 | 0
3181 | TORONTO BUTTONVILLE A | 5 | 13 | 13 | 14.125 | 3.875 | 0
3182 | TORONTO BUTTONVILLE A | 5 | 12 | 14 | 5.2 | 12.8 | 0
3182 | TORONTO BUTTONVILLE A | 5 | 13 | 14 | 14.45 | 3.55 | 0
3183 | TORONTO BUTTONVILLE A | 5 | 12 | 15 | 5.2 | 12.8 | 0
3183 | TORONTO BUTTONVILLE A | 5 | 13 | 15 | 14.275 | 3.725 | 0
3184 | TORONTO BUTTONVILLE A | 5 | 12 | 16 | 6.4 | 11.6 | 0
3184 | TORONTO BUTTONVILLE A | 5 | 13 | 16 | 14.675 | 3.325 | 0
3185 | TORONTO BUTTONVILLE A | 5 | 12 | 17 | 6.2 | 11.8 | 0
3185 | TORONTO BUTTONVILLE A | 5 | 13 | 17 | 15.125 | 2.875 | 0
3186 | TORONTO BUTTONVILLE A | 5 | 12 | 18 | 6.8 | 11.2 | 0
3186 | TORONTO BUTTONVILLE A | 5 | 13 | 18 | 14.875 | 3.125 | 0
3187 | TORONTO BUTTONVILLE A | 5 | 12 | 19 | 6.6 | 11.4 | 0
3187 | TORONTO BUTTONVILLE A | 5 | 13 | 19 | 14.625 | 3.375 | 0
3188 | TORONTO BUTTONVILLE A | 5 | 12 | 20 | 6.2 | 11.8 | 0
3188 | TORONTO BUTTONVILLE A | 5 | 13 | 20 | 12.975 | 5.025 | 0
3189 | TORONTO BUTTONVILLE A | 5 | 12 | 21 | 4.1 | 13.9 | 0
3189 | TORONTO BUTTONVILLE A | 5 | 13 | 21 | 11.5 | 6.5 | 0
3190 | TORONTO BUTTONVILLE A | 5 | 12 | 22 | 2.8 | 15.2 | 0
3190 | TORONTO BUTTONVILLE A | 5 | 13 | 22 | 10.6 | 7.4 | 0
3191 | TORONTO BUTTONVILLE A | 5 | 12 | 23 | 1.5 | 16.5 | 0
3191 | TORONTO BUTTONVILLE A | 5 | 13 | 23 | 9.875 | 8.125 | 0
3192 | TORONTO BUTTONVILLE A | 5 | 12 | 24 | 0.7 | 17.3 | 0
3192 | TORONTO BUTTONVILLE A | 5 | 13 | 24 | 9.55 | 8.45 | 0
3193 | TORONTO BUTTONVILLE A | 5 | 13 | 1 | 0 | 18 | 0
3193 | TORONTO BUTTONVILLE A | 5 | 14 | 1 | 8.9 | 9.1 | 0
3194 | TORONTO BUTTONVILLE A | 5 | 13 | 2 | 0.3 | 17.7 | 0
3194 | TORONTO BUTTONVILLE A | 5 | 14 | 2 | 8.6 | 9.4 | 0
3195 | TORONTO BUTTONVILLE A | 5 | 13 | 3 | -0.1 | 18.1 | 0
3195 | TORONTO BUTTONVILLE A | 5 | 14 | 3 | 7.675 | 10.325 | 0
3196 | TORONTO BUTTONVILLE A | 5 | 13 | 4 | -0.8 | 18.8 | 0
3196 | TORONTO BUTTONVILLE A | 5 | 14 | 4 | 7.475 | 10.525 | 0
3197 | TORONTO BUTTONVILLE A | 5 | 13 | 5 | -0.7 | 18.7 | 0
3197 | TORONTO BUTTONVILLE A | 5 | 14 | 5 | 6.925 | 11.075 | 0
3198 | TORONTO BUTTONVILLE A | 5 | 13 | 6 | -1.8 | 19.8 | 0
3198 | TORONTO BUTTONVILLE A | 5 | 14 | 6 | 6.35 | 11.65 | 0
3199 | TORONTO BUTTONVILLE A | 5 | 13 | 7 | 0.5 | 17.5 | 0
3199 | TORONTO BUTTONVILLE A | 5 | 14 | 7 | 7.425 | 10.575 | 0
3200 | TORONTO BUTTONVILLE A | 5 | 13 | 8 | 4.8 | 13.2 | 0
3200 | TORONTO BUTTONVILLE A | 5 | 14 | 8 | 10.225 | 7.775 | 0
3201 | TORONTO BUTTONVILLE A | 5 | 13 | 9 | 6.5 | 11.5 | 0
3201 | TORONTO BUTTONVILLE A | 5 | 14 | 9 | 12.8 | 5.2 | 0
3202 | TORONTO BUTTONVILLE A | 5 | 13 | 10 | 7.9 | 10.1 | 0
3202 | TORONTO BUTTONVILLE A | 5 | 14 | 10 | 14.675 | 3.325 | 0
3203 | TORONTO BUTTONVILLE A | 5 | 13 | 11 | 9.2 | 8.8 | 0
3203 | TORONTO BUTTONVILLE A | 5 | 14 | 11 | 15.775 | 2.225 | 0
3204 | TORONTO BUTTONVILLE A | 5 | 13 | 12 | 9.9 | 8.1 | 0
3204 | TORONTO BUTTONVILLE A | 5 | 14 | 12 | 17 | 1 | 0
3205 | TORONTO BUTTONVILLE A | 5 | 13 | 13 | 11.2 | 6.8 | 0
3205 | TORONTO BUTTONVILLE A | 5 | 14 | 13 | 16.1 | 1.9 | 0
3206 | TORONTO BUTTONVILLE A | 5 | 13 | 14 | 11.6 | 6.4 | 0
3206 | TORONTO BUTTONVILLE A | 5 | 14 | 14 | 17.375 | 0.625 | 0
3207 | TORONTO BUTTONVILLE A | 5 | 13 | 15 | 12.4 | 5.6 | 0
3207 | TORONTO BUTTONVILLE A | 5 | 14 | 15 | 17.575 | 0.425 | 0
3208 | TORONTO BUTTONVILLE A | 5 | 13 | 16 | 12.9 | 5.1 | 0
3208 | TORONTO BUTTONVILLE A | 5 | 14 | 16 | 17.475 | 0.525 | 0
3209 | TORONTO BUTTONVILLE A | 5 | 13 | 17 | 13.2 | 4.8 | 0
3209 | TORONTO BUTTONVILLE A | 5 | 14 | 17 | 17.65 | 0.35 | 0
3210 | TORONTO BUTTONVILLE A | 5 | 13 | 18 | 13 | 5 | 0
3210 | TORONTO BUTTONVILLE A | 5 | 14 | 18 | 17.3 | 0.7 | 0
3211 | TORONTO BUTTONVILLE A | 5 | 13 | 19 | 12.1 | 5.9 | 0
3211 | TORONTO BUTTONVILLE A | 5 | 14 | 19 | 16.45 | 1.55 | 0
3212 | TORONTO BUTTONVILLE A | 5 | 13 | 20 | 10.6 | 7.4 | 0
3212 | TORONTO BUTTONVILLE A | 5 | 14 | 20 | 15.35 | 2.65 | 0
3213 | TORONTO BUTTONVILLE A | 5 | 13 | 21 | 9.4 | 8.6 | 0
3213 | TORONTO BUTTONVILLE A | 5 | 14 | 21 | 14.05 | 3.95 | 0
3214 | TORONTO BUTTONVILLE A | 5 | 13 | 22 | 8.6 | 9.4 | 0
3214 | TORONTO BUTTONVILLE A | 5 | 14 | 22 | 13.325 | 4.675 | 0
3215 | TORONTO BUTTONVILLE A | 5 | 13 | 23 | 7.9 | 10.1 | 0
3215 | TORONTO BUTTONVILLE A | 5 | 14 | 23 | 12.825 | 5.175 | 0
3216 | TORONTO BUTTONVILLE A | 5 | 13 | 24 | 7.2 | 10.8 | 0
3216 | TORONTO BUTTONVILLE A | 5 | 14 | 24 | 12.275 | 5.725 | 0
3217 | TORONTO BUTTONVILLE A | 5 | 14 | 1 | 6.2 | 11.8 | 0
3217 | TORONTO BUTTONVILLE A | 5 | 15 | 1 | 11.05 | 6.95 | 0
3218 | TORONTO BUTTONVILLE A | 5 | 14 | 2 | 5 | 13 | 0
3218 | TORONTO BUTTONVILLE A | 5 | 15 | 2 | 10.35 | 7.65 | 0
3219 | TORONTO BUTTONVILLE A | 5 | 14 | 3 | 4 | 14 | 0
3219 | TORONTO BUTTONVILLE A | 5 | 15 | 3 | 9.775 | 8.225 | 0
3220 | TORONTO BUTTONVILLE A | 5 | 14 | 4 | 4.7 | 13.3 | 0
3220 | TORONTO BUTTONVILLE A | 5 | 15 | 4 | 9.2 | 8.8 | 0
3221 | TORONTO BUTTONVILLE A | 5 | 14 | 5 | 5.1 | 12.9 | 0
3221 | TORONTO BUTTONVILLE A | 5 | 15 | 5 | 8.6 | 9.4 | 0
3222 | TORONTO BUTTONVILLE A | 5 | 14 | 6 | 5.3 | 12.7 | 0
3222 | TORONTO BUTTONVILLE A | 5 | 15 | 6 | 8.9 | 9.1 | 0
3223 | TORONTO BUTTONVILLE A | 5 | 14 | 7 | 5.4 | 12.6 | 0
3223 | TORONTO BUTTONVILLE A | 5 | 15 | 7 | 9.95 | 8.05 | 0
3224 | TORONTO BUTTONVILLE A | 5 | 14 | 8 | 6.7 | 11.3 | 0
3224 | TORONTO BUTTONVILLE A | 5 | 15 | 8 | 12.225 | 5.775 | 0
3225 | TORONTO BUTTONVILLE A | 5 | 14 | 9 | 8.2 | 9.8 | 0
3225 | TORONTO BUTTONVILLE A | 5 | 15 | 9 | 14.275 | 3.725 | 0
3226 | TORONTO BUTTONVILLE A | 5 | 14 | 10 | 10.3 | 7.7 | 0
3226 | TORONTO BUTTONVILLE A | 5 | 15 | 10 | 16.1 | 1.9 | 0
3227 | TORONTO BUTTONVILLE A | 5 | 14 | 11 | 11 | 7 | 0
3227 | TORONTO BUTTONVILLE A | 5 | 15 | 11 | 17.225 | 0.775 | 0
3228 | TORONTO BUTTONVILLE A | 5 | 14 | 12 | 10.7 | 7.3 | 0
3228 | TORONTO BUTTONVILLE A | 5 | 15 | 12 | 17.7 | 0.3 | 0
3229 | TORONTO BUTTONVILLE A | 5 | 14 | 13 | 10.6 | 7.4 | 0
3229 | TORONTO BUTTONVILLE A | 5 | 15 | 13 | 17.7 | 0.3 | 0
3230 | TORONTO BUTTONVILLE A | 5 | 14 | 14 | 11.3 | 6.7 | 0
3230 | TORONTO BUTTONVILLE A | 5 | 15 | 14 | 18.025 | 0 | 0.025
3231 | TORONTO BUTTONVILLE A | 5 | 14 | 15 | 9.9 | 8.1 | 0
3231 | TORONTO BUTTONVILLE A | 5 | 15 | 15 | 17.05 | 0.95 | 0
3232 | TORONTO BUTTONVILLE A | 5 | 14 | 16 | 9.4 | 8.6 | 0
3232 | TORONTO BUTTONVILLE A | 5 | 15 | 16 | 18.7 | 0 | 0.7
3233 | TORONTO BUTTONVILLE A | 5 | 14 | 17 | 10.3 | 7.7 | 0
3233 | TORONTO BUTTONVILLE A | 5 | 15 | 17 | 18.675 | 0 | 0.675
3234 | TORONTO BUTTONVILLE A | 5 | 14 | 18 | 8.9 | 9.1 | 0
3234 | TORONTO BUTTONVILLE A | 5 | 15 | 18 | 18.825 | 0 | 0.825
3235 | TORONTO BUTTONVILLE A | 5 | 14 | 19 | 8.2 | 9.8 | 0
3235 | TORONTO BUTTONVILLE A | 5 | 15 | 19 | 17.9 | 0.1 | 0
3236 | TORONTO BUTTONVILLE A | 5 | 14 | 20 | 7.1 | 10.9 | 0
3236 | TORONTO BUTTONVILLE A | 5 | 15 | 20 | 16.675 | 1.325 | 0
3237 | TORONTO BUTTONVILLE A | 5 | 14 | 21 | 7.4 | 10.6 | 0
3237 | TORONTO BUTTONVILLE A | 5 | 15 | 21 | 15.3 | 2.7 | 0
3238 | TORONTO BUTTONVILLE A | 5 | 14 | 22 | 7.9 | 10.1 | 0
3238 | TORONTO BUTTONVILLE A | 5 | 15 | 22 | 13.6 | 4.4 | 0
3239 | TORONTO BUTTONVILLE A | 5 | 14 | 23 | 7.9 | 10.1 | 0
3239 | TORONTO BUTTONVILLE A | 5 | 15 | 23 | 12.2 | 5.8 | 0
3240 | TORONTO BUTTONVILLE A | 5 | 14 | 24 | 8.1 | 9.9 | 0
3240 | TORONTO BUTTONVILLE A | 5 | 15 | 24 | 11.375 | 6.625 | 0
3241 | TORONTO BUTTONVILLE A | 5 | 15 | 1 | 8.3 | 9.7 | 0
3241 | TORONTO BUTTONVILLE A | 5 | 16 | 1 | 11.15 | 6.85 | 0
3242 | TORONTO BUTTONVILLE A | 5 | 15 | 2 | 8.5 | 9.5 | 0
3242 | TORONTO BUTTONVILLE A | 5 | 16 | 2 | 10.8 | 7.2 | 0
3243 | TORONTO BUTTONVILLE A | 5 | 15 | 3 | 8.8 | 9.2 | 0
3243 | TORONTO BUTTONVILLE A | 5 | 16 | 3 | 10 | 8 | 0
3244 | TORONTO BUTTONVILLE A | 5 | 15 | 4 | 8.9 | 9.1 | 0
3244 | TORONTO BUTTONVILLE A | 5 | 16 | 4 | 9.275 | 8.725 | 0
3245 | TORONTO BUTTONVILLE A | 5 | 15 | 5 | 9.3 | 8.7 | 0
3245 | TORONTO BUTTONVILLE A | 5 | 16 | 5 | 8.25 | 9.75 | 0
3246 | TORONTO BUTTONVILLE A | 5 | 15 | 6 | 9.5 | 8.5 | 0
3246 | TORONTO BUTTONVILLE A | 5 | 16 | 6 | 7.875 | 10.125 | 0
3247 | TORONTO BUTTONVILLE A | 5 | 15 | 7 | 9.7 | 8.3 | 0
3247 | TORONTO BUTTONVILLE A | 5 | 16 | 7 | 9.05 | 8.95 | 0
3248 | TORONTO BUTTONVILLE A | 5 | 15 | 8 | 9.9 | 8.1 | 0
3248 | TORONTO BUTTONVILLE A | 5 | 16 | 8 | 11.025 | 6.975 | 0
3249 | TORONTO BUTTONVILLE A | 5 | 15 | 9 | 10.2 | 7.8 | 0
3249 | TORONTO BUTTONVILLE A | 5 | 16 | 9 | 12.65 | 5.35 | 0
3250 | TORONTO BUTTONVILLE A | 5 | 15 | 10 | 10.9 | 7.1 | 0
3250 | TORONTO BUTTONVILLE A | 5 | 16 | 10 | 14.4 | 3.6 | 0
3251 | TORONTO BUTTONVILLE A | 5 | 15 | 11 | 11.7 | 6.3 | 0
3251 | TORONTO BUTTONVILLE A | 5 | 16 | 11 | 15.6 | 2.4 | 0
3252 | TORONTO BUTTONVILLE A | 5 | 15 | 12 | 11.9 | 6.1 | 0
3252 | TORONTO BUTTONVILLE A | 5 | 16 | 12 | 16.625 | 1.375 | 0
3253 | TORONTO BUTTONVILLE A | 5 | 15 | 13 | 13.1 | 4.9 | 0
3253 | TORONTO BUTTONVILLE A | 5 | 16 | 13 | 17.2 | 0.8 | 0
3254 | TORONTO BUTTONVILLE A | 5 | 15 | 14 | 14.8 | 3.2 | 0
3254 | TORONTO BUTTONVILLE A | 5 | 16 | 14 | 17.55 | 0.45 | 0
3255 | TORONTO BUTTONVILLE A | 5 | 15 | 15 | 16.4 | 1.6 | 0
3255 | TORONTO BUTTONVILLE A | 5 | 16 | 15 | 19.1667 | 0 | 1.1667
3256 | TORONTO BUTTONVILLE A | 5 | 15 | 16 | 13.7 | 4.3 | 0
3256 | TORONTO BUTTONVILLE A | 5 | 16 | 16 | 18.65 | 0 | 0.65
3257 | TORONTO BUTTONVILLE A | 5 | 15 | 17 | 14.1 | 3.9 | 0
3257 | TORONTO BUTTONVILLE A | 5 | 16 | 17 | 18.9 | 0 | 0.9
3258 | TORONTO BUTTONVILLE A | 5 | 15 | 18 | 14.8 | 3.2 | 0
3258 | TORONTO BUTTONVILLE A | 5 | 16 | 18 | 17.1333 | 0.86667 | 0
3259 | TORONTO BUTTONVILLE A | 5 | 15 | 19 | 14.3 | 3.7 | 0
3259 | TORONTO BUTTONVILLE A | 5 | 16 | 19 | 18.125 | 0 | 0.125
3260 | TORONTO BUTTONVILLE A | 5 | 15 | 20 | 13.5 | 4.5 | 0
3260 | TORONTO BUTTONVILLE A | 5 | 16 | 20 | 16.875 | 1.125 | 0
3261 | TORONTO BUTTONVILLE A | 5 | 15 | 21 | 12 | 6 | 0
3261 | TORONTO BUTTONVILLE A | 5 | 16 | 21 | 16.1 | 1.9 | 0
3262 | TORONTO BUTTONVILLE A | 5 | 15 | 22 | 11 | 7 | 0
3262 | TORONTO BUTTONVILLE A | 5 | 16 | 22 | 13.575 | 4.425 | 0
3263 | TORONTO BUTTONVILLE A | 5 | 15 | 23 | 10.6 | 7.4 | 0
3263 | TORONTO BUTTONVILLE A | 5 | 16 | 23 | 12.4 | 5.6 | 0
3264 | TORONTO BUTTONVILLE A | 5 | 15 | 24 | 9.8 | 8.2 | 0
3264 | TORONTO BUTTONVILLE A | 5 | 16 | 24 | 12.05 | 5.95 | 0
3265 | TORONTO BUTTONVILLE A | 5 | 16 | 1 | 9.1 | 8.9 | 0
3265 | TORONTO BUTTONVILLE A | 5 | 17 | 1 | 12.1667 | 5.8333 | 0
3266 | TORONTO BUTTONVILLE A | 5 | 16 | 2 | 9.2 | 8.8 | 0
3266 | TORONTO BUTTONVILLE A | 5 | 17 | 2 | 11.5667 | 6.4333 | 0
3267 | TORONTO BUTTONVILLE A | 5 | 16 | 3 | 9.1 | 8.9 | 0
3267 | TORONTO BUTTONVILLE A | 5 | 17 | 3 | 10.8333 | 7.1667 | 0
3268 | TORONTO BUTTONVILLE A | 5 | 16 | 4 | 9 | 9 | 0
3268 | TORONTO BUTTONVILLE A | 5 | 17 | 4 | 10.2667 | 7.7333 | 0
3269 | TORONTO BUTTONVILLE A | 5 | 16 | 5 | 8.9 | 9.1 | 0
3269 | TORONTO BUTTONVILLE A | 5 | 17 | 5 | 10.1 | 7.9 | 0
3270 | TORONTO BUTTONVILLE A | 5 | 16 | 6 | 8.8 | 9.2 | 0
3270 | TORONTO BUTTONVILLE A | 5 | 17 | 6 | 10.0333 | 7.9667 | 0
3271 | TORONTO BUTTONVILLE A | 5 | 16 | 7 | 8.8 | 9.2 | 0
3271 | TORONTO BUTTONVILLE A | 5 | 17 | 7 | 11.9333 | 6.0667 | 0
3272 | TORONTO BUTTONVILLE A | 5 | 16 | 8 | 10 | 8 | 0
3272 | TORONTO BUTTONVILLE A | 5 | 17 | 8 | 14.625 | 3.375 | 0
3273 | TORONTO BUTTONVILLE A | 5 | 16 | 9 | 11.8 | 6.2 | 0
3273 | TORONTO BUTTONVILLE A | 5 | 17 | 9 | 16.225 | 1.775 | 0
3274 | TORONTO BUTTONVILLE A | 5 | 16 | 10 | 13.2 | 4.8 | 0
3274 | TORONTO BUTTONVILLE A | 5 | 17 | 10 | 17.775 | 0.225 | 0
3275 | TORONTO BUTTONVILLE A | 5 | 16 | 11 | 14.7 | 3.3 | 0
3275 | TORONTO BUTTONVILLE A | 5 | 17 | 11 | 21.9333 | 0 | 3.9333
3276 | TORONTO BUTTONVILLE A | 5 | 16 | 12 | 16 | 2 | 0
3276 | TORONTO BUTTONVILLE A | 5 | 17 | 12 | 20.75 | 0 | 2.75
3277 | TORONTO BUTTONVILLE A | 5 | 16 | 13 | 16.8 | 1.2 | 0
3277 | TORONTO BUTTONVILLE A | 5 | 17 | 13 | 21.375 | 0 | 3.375
3278 | TORONTO BUTTONVILLE A | 5 | 16 | 14 | 17.3 | 0.7 | 0
3278 | TORONTO BUTTONVILLE A | 5 | 17 | 14 | 22.1 | 0 | 4.1
3279 | TORONTO BUTTONVILLE A | 5 | 16 | 15 | 16.2 | 1.8 | 0
3279 | TORONTO BUTTONVILLE A | 5 | 17 | 15 | 22.775 | 0 | 4.775
3280 | TORONTO BUTTONVILLE A | 5 | 16 | 16 | 17.2 | 0.8 | 0
3280 | TORONTO BUTTONVILLE A | 5 | 17 | 16 | 23.25 | 0 | 5.25
3281 | TORONTO BUTTONVILLE A | 5 | 16 | 17 | 16.1 | 1.9 | 0
3281 | TORONTO BUTTONVILLE A | 5 | 17 | 17 | 22.775 | 0 | 4.775
3282 | TORONTO BUTTONVILLE A | 5 | 16 | 18 | 15.2 | 2.8 | 0
3282 | TORONTO BUTTONVILLE A | 5 | 17 | 18 | 22.6 | 0 | 4.6
3283 | TORONTO BUTTONVILLE A | 5 | 16 | 19 | 14.8 | 3.2 | 0
3283 | TORONTO BUTTONVILLE A | 5 | 17 | 19 | 21.45 | 0 | 3.45
3284 | TORONTO BUTTONVILLE A | 5 | 16 | 20 | 13.1 | 4.9 | 0
3284 | TORONTO BUTTONVILLE A | 5 | 17 | 20 | 19.875 | 0 | 1.875
3285 | TORONTO BUTTONVILLE A | 5 | 16 | 21 | 11.3 | 6.7 | 0
3285 | TORONTO BUTTONVILLE A | 5 | 17 | 21 | 18.1 | 0 | 0.1
3286 | TORONTO BUTTONVILLE A | 5 | 16 | 22 | 10.8 | 7.2 | 0
3286 | TORONTO BUTTONVILLE A | 5 | 17 | 22 | 19.6 | 0 | 1.6
3287 | TORONTO BUTTONVILLE A | 5 | 16 | 23 | 10.3 | 7.7 | 0
3287 | TORONTO BUTTONVILLE A | 5 | 17 | 23 | 15.8 | 2.2 | 0
3288 | TORONTO BUTTONVILLE A | 5 | 16 | 24 | 8.9 | 9.1 | 0
3288 | TORONTO BUTTONVILLE A | 5 | 17 | 24 | 17.2 | 0.8 | 0
3289 | TORONTO BUTTONVILLE A | 5 | 17 | 1 | 9 | 9 | 0
3289 | TORONTO BUTTONVILLE A | 5 | 18 | 1 | 16.9 | 1.1 | 0
3290 | TORONTO BUTTONVILLE A | 5 | 17 | 2 | 8 | 10 | 0
3290 | TORONTO BUTTONVILLE A | 5 | 18 | 2 | 16.4 | 1.6 | 0
3291 | TORONTO BUTTONVILLE A | 5 | 17 | 3 | 8.1 | 9.9 | 0
3291 | TORONTO BUTTONVILLE A | 5 | 18 | 3 | 15.6667 | 2.3333 | 0
3292 | TORONTO BUTTONVILLE A | 5 | 17 | 4 | 6.7 | 11.3 | 0
3292 | TORONTO BUTTONVILLE A | 5 | 18 | 4 | 14.6667 | 3.3333 | 0
3293 | TORONTO BUTTONVILLE A | 5 | 17 | 5 | 6.7 | 11.3 | 0
3293 | TORONTO BUTTONVILLE A | 5 | 18 | 5 | 13.5 | 4.5 | 0
3294 | TORONTO BUTTONVILLE A | 5 | 17 | 6 | 6.4 | 11.6 | 0
3294 | TORONTO BUTTONVILLE A | 5 | 18 | 6 | 13 | 5 | 0
3295 | TORONTO BUTTONVILLE A | 5 | 17 | 7 | 8.7 | 9.3 | 0
3295 | TORONTO BUTTONVILLE A | 5 | 18 | 7 | 12.2 | 5.8 | 0
3296 | TORONTO BUTTONVILLE A | 5 | 17 | 8 | 11.4 | 6.6 | 0
3296 | TORONTO BUTTONVILLE A | 5 | 18 | 8 | 16.6 | 1.4 | 0
3297 | TORONTO BUTTONVILLE A | 5 | 17 | 9 | 13.6 | 4.4 | 0
3297 | TORONTO BUTTONVILLE A | 5 | 18 | 9 | 16.8 | 1.2 | 0
3298 | TORONTO BUTTONVILLE A | 5 | 17 | 10 | 14.8 | 3.2 | 0
3298 | TORONTO BUTTONVILLE A | 5 | 18 | 10 | 18.625 | 0 | 0.625
3299 | TORONTO BUTTONVILLE A | 5 | 17 | 11 | 16.1 | 1.9 | 0
3299 | TORONTO BUTTONVILLE A | 5 | 18 | 11 | 19.25 | 0 | 1.25
3300 | TORONTO BUTTONVILLE A | 5 | 17 | 12 | 15.9 | 2.1 | 0
3300 | TORONTO BUTTONVILLE A | 5 | 18 | 12 | 20.6 | 0 | 2.6
3301 | TORONTO BUTTONVILLE A | 5 | 17 | 13 | 15.9 | 2.1 | 0
3301 | TORONTO BUTTONVILLE A | 5 | 18 | 13 | 21.225 | 0 | 3.225
3302 | TORONTO BUTTONVILLE A | 5 | 17 | 14 | 15.5 | 2.5 | 0
3302 | TORONTO BUTTONVILLE A | 5 | 18 | 14 | 21.2 | 0 | 3.2
3303 | TORONTO BUTTONVILLE A | 5 | 17 | 15 | 17 | 1 | 0
3303 | TORONTO BUTTONVILLE A | 5 | 18 | 15 | 21.7 | 0 | 3.7
3304 | TORONTO BUTTONVILLE A | 5 | 17 | 16 | 16.5 | 1.5 | 0
3304 | TORONTO BUTTONVILLE A | 5 | 18 | 16 | 21.45 | 0 | 3.45
3305 | TORONTO BUTTONVILLE A | 5 | 17 | 17 | 15.6 | 2.4 | 0
3305 | TORONTO BUTTONVILLE A | 5 | 18 | 17 | 21.575 | 0 | 3.575
3306 | TORONTO BUTTONVILLE A | 5 | 17 | 18 | 15.3 | 2.7 | 0
3306 | TORONTO BUTTONVILLE A | 5 | 18 | 18 | 21.325 | 0 | 3.325
3307 | TORONTO BUTTONVILLE A | 5 | 17 | 19 | 14.9 | 3.1 | 0
3307 | TORONTO BUTTONVILLE A | 5 | 18 | 19 | 19.5 | 0 | 1.5
3308 | TORONTO BUTTONVILLE A | 5 | 17 | 20 | 14.2 | 3.8 | 0
3308 | TORONTO BUTTONVILLE A | 5 | 18 | 20 | 20.6 | 0 | 2.6
3309 | TORONTO BUTTONVILLE A | 5 | 17 | 21 | 13.6 | 4.4 | 0
3309 | TORONTO BUTTONVILLE A | 5 | 18 | 21 | 19.2667 | 0 | 1.2667
3310 | TORONTO BUTTONVILLE A | 5 | 17 | 22 | 14.4 | 3.6 | 0
3310 | TORONTO BUTTONVILLE A | 5 | 18 | 22 | 16.375 | 1.625 | 0
3311 | TORONTO BUTTONVILLE A | 5 | 17 | 23 | 13.6 | 4.4 | 0
3311 | TORONTO BUTTONVILLE A | 5 | 18 | 23 | 16.8333 | 1.1667 | 0
3312 | TORONTO BUTTONVILLE A | 5 | 17 | 24 | 12.8 | 5.2 | 0
3312 | TORONTO BUTTONVILLE A | 5 | 18 | 24 | 14.775 | 3.225 | 0
3313 | TORONTO BUTTONVILLE A | 5 | 18 | 1 | 11.9 | 6.1 | 0
3313 | TORONTO BUTTONVILLE A | 5 | 19 | 1 | 15.6667 | 2.3333 | 0
3314 | TORONTO BUTTONVILLE A | 5 | 18 | 2 | 11.4 | 6.6 | 0
3314 | TORONTO BUTTONVILLE A | 5 | 19 | 2 | 14.9 | 3.1 | 0
3315 | TORONTO BUTTONVILLE A | 5 | 18 | 3 | 11.2 | 6.8 | 0
3315 | TORONTO BUTTONVILLE A | 5 | 19 | 3 | 14.325 | 3.675 | 0
3316 | TORONTO BUTTONVILLE A | 5 | 18 | 4 | 11.1 | 6.9 | 0
3316 | TORONTO BUTTONVILLE A | 5 | 19 | 4 | 12.85 | 5.15 | 0
3317 | TORONTO BUTTONVILLE A | 5 | 18 | 5 | 11.1 | 6.9 | 0
3317 | TORONTO BUTTONVILLE A | 5 | 19 | 5 | 12.4333 | 5.5667 | 0
3318 | TORONTO BUTTONVILLE A | 5 | 18 | 6 | 11.1 | 6.9 | 0
3318 | TORONTO BUTTONVILLE A | 5 | 19 | 6 | 10.8 | 7.2 | 0
3319 | TORONTO BUTTONVILLE A | 5 | 18 | 7 | 11 | 7 | 0
3319 | TORONTO BUTTONVILLE A | 5 | 19 | 7 | 10.875 | 7.125 | 0
3320 | TORONTO BUTTONVILLE A | 5 | 18 | 8 | 11.4 | 6.6 | 0
3320 | TORONTO BUTTONVILLE A | 5 | 19 | 8 | 12.475 | 5.525 | 0
3321 | TORONTO BUTTONVILLE A | 5 | 18 | 9 | 12.2 | 5.8 | 0
3321 | TORONTO BUTTONVILLE A | 5 | 19 | 9 | 14.25 | 3.75 | 0
3322 | TORONTO BUTTONVILLE A | 5 | 18 | 10 | 12.8 | 5.2 | 0
3322 | TORONTO BUTTONVILLE A | 5 | 19 | 10 | 15.05 | 2.95 | 0
3323 | TORONTO BUTTONVILLE A | 5 | 18 | 11 | 12.8 | 5.2 | 0
3323 | TORONTO BUTTONVILLE A | 5 | 19 | 11 | 15.475 | 2.525 | 0
3324 | TORONTO BUTTONVILLE A | 5 | 18 | 12 | 13.4 | 4.6 | 0
3324 | TORONTO BUTTONVILLE A | 5 | 19 | 12 | 15.975 | 2.025 | 0
3325 | TORONTO BUTTONVILLE A | 5 | 18 | 13 | 13.8 | 4.2 | 0
3325 | TORONTO BUTTONVILLE A | 5 | 19 | 13 | 16.2 | 1.8 | 0
3326 | TORONTO BUTTONVILLE A | 5 | 18 | 14 | 13 | 5 | 0
3326 | TORONTO BUTTONVILLE A | 5 | 19 | 14 | 16.45 | 1.55 | 0
3327 | TORONTO BUTTONVILLE A | 5 | 18 | 15 | 13.4 | 4.6 | 0
3327 | TORONTO BUTTONVILLE A | 5 | 19 | 15 | 17.475 | 0.525 | 0
3328 | TORONTO BUTTONVILLE A | 5 | 18 | 16 | 13.6 | 4.4 | 0
3328 | TORONTO BUTTONVILLE A | 5 | 19 | 16 | 18.725 | 0 | 0.725
3329 | TORONTO BUTTONVILLE A | 5 | 18 | 17 | 13.9 | 4.1 | 0
3329 | TORONTO BUTTONVILLE A | 5 | 19 | 17 | 19.125 | 0 | 1.125
3330 | TORONTO BUTTONVILLE A | 5 | 18 | 18 | 13.7 | 4.3 | 0
3330 | TORONTO BUTTONVILLE A | 5 | 19 | 18 | 18.45 | 0 | 0.45
3331 | TORONTO BUTTONVILLE A | 5 | 18 | 19 | 13.5 | 4.5 | 0
3331 | TORONTO BUTTONVILLE A | 5 | 19 | 19 | 18.2 | 0 | 0.2
3332 | TORONTO BUTTONVILLE A | 5 | 18 | 20 | 13.6 | 4.4 | 0
3332 | TORONTO BUTTONVILLE A | 5 | 19 | 20 | 17.4 | 0.6 | 0
3333 | TORONTO BUTTONVILLE A | 5 | 18 | 21 | 13.8 | 4.2 | 0
3333 | TORONTO BUTTONVILLE A | 5 | 19 | 21 | 16.375 | 1.625 | 0
3334 | TORONTO BUTTONVILLE A | 5 | 18 | 22 | 13.5 | 4.5 | 0
3334 | TORONTO BUTTONVILLE A | 5 | 19 | 22 | 15.5 | 2.5 | 0
3335 | TORONTO BUTTONVILLE A | 5 | 18 | 23 | 13.5 | 4.5 | 0
3335 | TORONTO BUTTONVILLE A | 5 | 19 | 23 | 14.55 | 3.45 | 0
3336 | TORONTO BUTTONVILLE A | 5 | 18 | 24 | 14.2 | 3.8 | 0
3336 | TORONTO BUTTONVILLE A | 5 | 19 | 24 | 14.225 | 3.775 | 0
3337 | TORONTO BUTTONVILLE A | 5 | 19 | 1 | 14.4 | 3.6 | 0
3337 | TORONTO BUTTONVILLE A | 5 | 20 | 1 | 13.55 | 4.45 | 0
3338 | TORONTO BUTTONVILLE A | 5 | 19 | 2 | 14.5 | 3.5 | 0
3338 | TORONTO BUTTONVILLE A | 5 | 20 | 2 | 13.6 | 4.4 | 0
3339 | TORONTO BUTTONVILLE A | 5 | 19 | 3 | 14.3 | 3.7 | 0
3339 | TORONTO BUTTONVILLE A | 5 | 20 | 3 | 13.475 | 4.525 | 0
3340 | TORONTO BUTTONVILLE A | 5 | 19 | 4 | 13.4 | 4.6 | 0
3340 | TORONTO BUTTONVILLE A | 5 | 20 | 4 | 12.3667 | 5.6333 | 0
3341 | TORONTO BUTTONVILLE A | 5 | 19 | 5 | 13.2 | 4.8 | 0
3341 | TORONTO BUTTONVILLE A | 5 | 20 | 5 | 12.325 | 5.675 | 0
3342 | TORONTO BUTTONVILLE A | 5 | 19 | 6 | 12.6 | 5.4 | 0
3342 | TORONTO BUTTONVILLE A | 5 | 20 | 6 | 11.2333 | 6.7667 | 0
3343 | TORONTO BUTTONVILLE A | 5 | 19 | 7 | 12.5 | 5.5 | 0
3343 | TORONTO BUTTONVILLE A | 5 | 20 | 7 | 12.95 | 5.05 | 0
3344 | TORONTO BUTTONVILLE A | 5 | 19 | 8 | 12.3 | 5.7 | 0
3344 | TORONTO BUTTONVILLE A | 5 | 20 | 8 | 14.325 | 3.675 | 0
3345 | TORONTO BUTTONVILLE A | 5 | 19 | 9 | 12.4 | 5.6 | 0
3345 | TORONTO BUTTONVILLE A | 5 | 20 | 9 | 15.9 | 2.1 | 0
3346 | TORONTO BUTTONVILLE A | 5 | 19 | 10 | 13.7 | 4.3 | 0
3346 | TORONTO BUTTONVILLE A | 5 | 20 | 10 | 16.5 | 1.5 | 0
3347 | TORONTO BUTTONVILLE A | 5 | 19 | 11 | 15.7 | 2.3 | 0
3347 | TORONTO BUTTONVILLE A | 5 | 20 | 11 | 17.575 | 0.425 | 0
3348 | TORONTO BUTTONVILLE A | 5 | 19 | 12 | 16.1 | 1.9 | 0
3348 | TORONTO BUTTONVILLE A | 5 | 20 | 12 | 17.675 | 0.325 | 0
3349 | TORONTO BUTTONVILLE A | 5 | 19 | 13 | 16.3 | 1.7 | 0
3349 | TORONTO BUTTONVILLE A | 5 | 20 | 13 | 17.725 | 0.275 | 0
3350 | TORONTO BUTTONVILLE A | 5 | 19 | 14 | 16.3 | 1.7 | 0
3350 | TORONTO BUTTONVILLE A | 5 | 20 | 14 | 18.175 | 0 | 0.175
3351 | TORONTO BUTTONVILLE A | 5 | 19 | 15 | 16 | 2 | 0
3351 | TORONTO BUTTONVILLE A | 5 | 20 | 15 | 18.975 | 0 | 0.975
3352 | TORONTO BUTTONVILLE A | 5 | 19 | 16 | 17.3 | 0.7 | 0
3352 | TORONTO BUTTONVILLE A | 5 | 20 | 16 | 18.8 | 0 | 0.8
3353 | TORONTO BUTTONVILLE A | 5 | 19 | 17 | 18 | 0 | 0
3353 | TORONTO BUTTONVILLE A | 5 | 20 | 17 | 18.45 | 0 | 0.45
3354 | TORONTO BUTTONVILLE A | 5 | 19 | 18 | 17.4 | 0.6 | 0
3354 | TORONTO BUTTONVILLE A | 5 | 20 | 18 | 20.0667 | 0 | 2.0667
3355 | TORONTO BUTTONVILLE A | 5 | 19 | 19 | 17.3 | 0.7 | 0
3355 | TORONTO BUTTONVILLE A | 5 | 20 | 19 | 19.3 | 0 | 1.3
3356 | TORONTO BUTTONVILLE A | 5 | 19 | 20 | 17.3 | 0.7 | 0
3356 | TORONTO BUTTONVILLE A | 5 | 20 | 20 | 18.1333 | 0 | 0.13333
3357 | TORONTO BUTTONVILLE A | 5 | 19 | 21 | 16.9 | 1.1 | 0
3357 | TORONTO BUTTONVILLE A | 5 | 20 | 21 | 16.1333 | 1.8667 | 0
3358 | TORONTO BUTTONVILLE A | 5 | 19 | 22 | 16.1 | 1.9 | 0
3358 | TORONTO BUTTONVILLE A | 5 | 20 | 22 | 15.3667 | 2.6333 | 0
3359 | TORONTO BUTTONVILLE A | 5 | 19 | 23 | 15.6 | 2.4 | 0
3359 | TORONTO BUTTONVILLE A | 5 | 20 | 23 | 14.6667 | 3.3333 | 0
3360 | TORONTO BUTTONVILLE A | 5 | 19 | 24 | 14.5 | 3.5 | 0
3360 | TORONTO BUTTONVILLE A | 5 | 20 | 24 | 13.8667 | 4.1333 | 0
3361 | TORONTO BUTTONVILLE A | 5 | 20 | 1 | 13.8 | 4.2 | 0
3361 | TORONTO BUTTONVILLE A | 5 | 21 | 1 | 12.9667 | 5.0333 | 0
3362 | TORONTO BUTTONVILLE A | 5 | 20 | 2 | 13.1 | 4.9 | 0
3362 | TORONTO BUTTONVILLE A | 5 | 21 | 2 | 12.0333 | 5.9667 | 0
3363 | TORONTO BUTTONVILLE A | 5 | 20 | 3 | 13.6 | 4.4 | 0
3363 | TORONTO BUTTONVILLE A | 5 | 21 | 3 | 11.5667 | 6.4333 | 0
3364 | TORONTO BUTTONVILLE A | 5 | 20 | 4 | 12 | 6 | 0
3364 | TORONTO BUTTONVILLE A | 5 | 21 | 4 | 11.0333 | 6.9667 | 0
3365 | TORONTO BUTTONVILLE A | 5 | 20 | 5 | 10.5 | 7.5 | 0
3365 | TORONTO BUTTONVILLE A | 5 | 21 | 5 | 11.6667 | 6.3333 | 0
3366 | TORONTO BUTTONVILLE A | 5 | 20 | 6 | 9.1 | 8.9 | 0
3366 | TORONTO BUTTONVILLE A | 5 | 21 | 6 | 11.1333 | 6.8667 | 0
3367 | TORONTO BUTTONVILLE A | 5 | 20 | 7 | 11.2 | 6.8 | 0
3367 | TORONTO BUTTONVILLE A | 5 | 21 | 7 | 12.3667 | 5.6333 | 0
3368 | TORONTO BUTTONVILLE A | 5 | 20 | 8 | 13.6 | 4.4 | 0
3368 | TORONTO BUTTONVILLE A | 5 | 21 | 8 | 14.2333 | 3.7667 | 0
3369 | TORONTO BUTTONVILLE A | 5 | 20 | 9 | 15 | 3 | 0
3369 | TORONTO BUTTONVILLE A | 5 | 21 | 9 | 16.0667 | 1.9333 | 0
3370 | TORONTO BUTTONVILLE A | 5 | 20 | 10 | 15.6 | 2.4 | 0
3370 | TORONTO BUTTONVILLE A | 5 | 21 | 10 | 17.6667 | 0.33333 | 0
3371 | TORONTO BUTTONVILLE A | 5 | 20 | 11 | 16 | 2 | 0
3371 | TORONTO BUTTONVILLE A | 5 | 21 | 11 | 19.5667 | 0 | 1.5667
3372 | TORONTO BUTTONVILLE A | 5 | 20 | 12 | 16.6 | 1.4 | 0
3372 | TORONTO BUTTONVILLE A | 5 | 21 | 12 | 20.5333 | 0 | 2.5333
3373 | TORONTO BUTTONVILLE A | 5 | 20 | 13 | 17.4 | 0.6 | 0
3373 | TORONTO BUTTONVILLE A | 5 | 21 | 13 | 19.775 | 0 | 1.775
3374 | TORONTO BUTTONVILLE A | 5 | 20 | 14 | 17.8 | 0.2 | 0
3374 | TORONTO BUTTONVILLE A | 5 | 21 | 14 | 20.25 | 0 | 2.25
3375 | TORONTO BUTTONVILLE A | 5 | 20 | 15 | 18.1 | 0 | 0.1
3375 | TORONTO BUTTONVILLE A | 5 | 21 | 15 | 20.85 | 0 | 2.85
3376 | TORONTO BUTTONVILLE A | 5 | 20 | 16 | 19 | 0 | 1
3376 | TORONTO BUTTONVILLE A | 5 | 21 | 16 | 20.875 | 0 | 2.875
3377 | TORONTO BUTTONVILLE A | 5 | 20 | 17 | 18.9 | 0 | 0.9
3377 | TORONTO BUTTONVILLE A | 5 | 21 | 17 | 20.45 | 0 | 2.45
3378 | TORONTO BUTTONVILLE A | 5 | 20 | 18 | 19.2 | 0 | 1.2
3378 | TORONTO BUTTONVILLE A | 5 | 21 | 18 | 20.15 | 0 | 2.15
3379 | TORONTO BUTTONVILLE A | 5 | 20 | 19 | 19.1 | 0 | 1.1
3379 | TORONTO BUTTONVILLE A | 5 | 21 | 19 | 19.925 | 0 | 1.925
3380 | TORONTO BUTTONVILLE A | 5 | 20 | 20 | 18.4 | 0 | 0.4
3380 | TORONTO BUTTONVILLE A | 5 | 21 | 20 | 19.125 | 0 | 1.125
3381 | TORONTO BUTTONVILLE A | 5 | 20 | 21 | 17 | 1 | 0
3381 | TORONTO BUTTONVILLE A | 5 | 21 | 21 | 18.425 | 0 | 0.425
3382 | TORONTO BUTTONVILLE A | 5 | 20 | 22 | 15.5 | 2.5 | 0
3382 | TORONTO BUTTONVILLE A | 5 | 21 | 22 | 17.55 | 0.45 | 0
3383 | TORONTO BUTTONVILLE A | 5 | 20 | 23 | 12.4 | 5.6 | 0
3383 | TORONTO BUTTONVILLE A | 5 | 21 | 23 | 16.75 | 1.25 | 0
3384 | TORONTO BUTTONVILLE A | 5 | 20 | 24 | 11.1 | 6.9 | 0
3384 | TORONTO BUTTONVILLE A | 5 | 21 | 24 | 16.7 | 1.3 | 0
3385 | TORONTO BUTTONVILLE A | 5 | 21 | 1 | 12.2 | 5.8 | 0
3385 | TORONTO BUTTONVILLE A | 5 | 22 | 1 | 16.325 | 1.675 | 0
3386 | TORONTO BUTTONVILLE A | 5 | 21 | 2 | 10.6 | 7.4 | 0
3386 | TORONTO BUTTONVILLE A | 5 | 22 | 2 | 15.725 | 2.275 | 0
3387 | TORONTO BUTTONVILLE A | 5 | 21 | 3 | 9.1 | 8.9 | 0
3387 | TORONTO BUTTONVILLE A | 5 | 22 | 3 | 15 | 3 | 0
3388 | TORONTO BUTTONVILLE A | 5 | 21 | 4 | 8.2 | 9.8 | 0
3388 | TORONTO BUTTONVILLE A | 5 | 22 | 4 | 14.1 | 3.9 | 0
3389 | TORONTO BUTTONVILLE A | 5 | 21 | 5 | 6.7 | 11.3 | 0
3389 | TORONTO BUTTONVILLE A | 5 | 22 | 5 | 13.5 | 4.5 | 0
3390 | TORONTO BUTTONVILLE A | 5 | 21 | 6 | 6.2 | 11.8 | 0
3390 | TORONTO BUTTONVILLE A | 5 | 22 | 6 | 12.975 | 5.025 | 0
3391 | TORONTO BUTTONVILLE A | 5 | 21 | 7 | 8.7 | 9.3 | 0
3391 | TORONTO BUTTONVILLE A | 5 | 22 | 7 | 13.175 | 4.825 | 0
3392 | TORONTO BUTTONVILLE A | 5 | 21 | 8 | 12 | 6 | 0
3392 | TORONTO BUTTONVILLE A | 5 | 22 | 8 | 14 | 4 | 0
3393 | TORONTO BUTTONVILLE A | 5 | 21 | 9 | 14.3 | 3.7 | 0
3393 | TORONTO BUTTONVILLE A | 5 | 22 | 9 | 15.275 | 2.725 | 0
3394 | TORONTO BUTTONVILLE A | 5 | 21 | 10 | 16.2 | 1.8 | 0
3394 | TORONTO BUTTONVILLE A | 5 | 22 | 10 | 16.775 | 1.225 | 0
3395 | TORONTO BUTTONVILLE A | 5 | 21 | 11 | 18 | 0 | 0
3395 | TORONTO BUTTONVILLE A | 5 | 22 | 11 | 17.1 | 0.9 | 0
3396 | TORONTO BUTTONVILLE A | 5 | 21 | 12 | NaN | 1.075 | 0
3396 | TORONTO BUTTONVILLE A | 5 | 22 | 12 | 16.75 | 1.25 | 0
3397 | TORONTO BUTTONVILLE A | 5 | 21 | 13 | 17.3 | 0.7 | 0
3397 | TORONTO BUTTONVILLE A | 5 | 22 | 13 | 16.5 | 1.5 | 0
3398 | TORONTO BUTTONVILLE A | 5 | 21 | 14 | 17.8 | 0.2 | 0
3398 | TORONTO BUTTONVILLE A | 5 | 22 | 14 | 16.625 | 1.375 | 0
3399 | TORONTO BUTTONVILLE A | 5 | 21 | 15 | 19.8 | 0 | 1.8
3399 | TORONTO BUTTONVILLE A | 5 | 22 | 15 | 16.75 | 1.25 | 0
3400 | TORONTO BUTTONVILLE A | 5 | 21 | 16 | 20 | 0 | 2
3400 | TORONTO BUTTONVILLE A | 5 | 22 | 16 | 17.25 | 0.75 | 0
3401 | TORONTO BUTTONVILLE A | 5 | 21 | 17 | 20.5 | 0 | 2.5
3401 | TORONTO BUTTONVILLE A | 5 | 22 | 17 | 17.175 | 0.825 | 0
3402 | TORONTO BUTTONVILLE A | 5 | 21 | 18 | 20.9 | 0 | 2.9
3402 | TORONTO BUTTONVILLE A | 5 | 22 | 18 | 17.3 | 0.7 | 0
3403 | TORONTO BUTTONVILLE A | 5 | 21 | 19 | 21.3 | 0 | 3.3
3403 | TORONTO BUTTONVILLE A | 5 | 22 | 19 | 17.325 | 0.675 | 0
3404 | TORONTO BUTTONVILLE A | 5 | 21 | 20 | 19.7 | 0 | 1.7
3404 | TORONTO BUTTONVILLE A | 5 | 22 | 20 | 16.875 | 1.125 | 0
3405 | TORONTO BUTTONVILLE A | 5 | 21 | 21 | 17.1 | 0.9 | 0
3405 | TORONTO BUTTONVILLE A | 5 | 22 | 21 | 16.25 | 1.75 | 0
3406 | TORONTO BUTTONVILLE A | 5 | 21 | 22 | 15.1 | 2.9 | 0
3406 | TORONTO BUTTONVILLE A | 5 | 22 | 22 | 15.425 | 2.575 | 0
3407 | TORONTO BUTTONVILLE A | 5 | 21 | 23 | 13.4 | 4.6 | 0
3407 | TORONTO BUTTONVILLE A | 5 | 22 | 23 | 14.85 | 3.15 | 0
3408 | TORONTO BUTTONVILLE A | 5 | 21 | 24 | 12.6 | 5.4 | 0
3408 | TORONTO BUTTONVILLE A | 5 | 22 | 24 | 14.3 | 3.7 | 0
3409 | TORONTO BUTTONVILLE A | 5 | 22 | 1 | 11.6 | 6.4 | 0
3409 | TORONTO BUTTONVILLE A | 5 | 23 | 1 | 13.225 | 4.775 | 0
3410 | TORONTO BUTTONVILLE A | 5 | 22 | 2 | 10.8 | 7.2 | 0
3410 | TORONTO BUTTONVILLE A | 5 | 23 | 2 | 12.65 | 5.35 | 0
3411 | TORONTO BUTTONVILLE A | 5 | 22 | 3 | 10.3 | 7.7 | 0
3411 | TORONTO BUTTONVILLE A | 5 | 23 | 3 | 12.15 | 5.85 | 0
3412 | TORONTO BUTTONVILLE A | 5 | 22 | 4 | 9.1 | 8.9 | 0
3412 | TORONTO BUTTONVILLE A | 5 | 23 | 4 | 11.675 | 6.325 | 0
3413 | TORONTO BUTTONVILLE A | 5 | 22 | 5 | 8.7 | 9.3 | 0
3413 | TORONTO BUTTONVILLE A | 5 | 23 | 5 | 11.775 | 6.225 | 0
3414 | TORONTO BUTTONVILLE A | 5 | 22 | 6 | 8.8 | 9.2 | 0
3414 | TORONTO BUTTONVILLE A | 5 | 23 | 6 | 12.375 | 5.625 | 0
3415 | TORONTO BUTTONVILLE A | 5 | 22 | 7 | 11.5 | 6.5 | 0
3415 | TORONTO BUTTONVILLE A | 5 | 23 | 7 | 13.425 | 4.575 | 0
3416 | TORONTO BUTTONVILLE A | 5 | 22 | 8 | 15.2 | 2.8 | 0
3416 | TORONTO BUTTONVILLE A | 5 | 23 | 8 | 15.275 | 2.725 | 0
3417 | TORONTO BUTTONVILLE A | 5 | 22 | 9 | 18.5 | 0 | 0.5
3417 | TORONTO BUTTONVILLE A | 5 | 23 | 9 | 17 | 1 | 0
3418 | TORONTO BUTTONVILLE A | 5 | 22 | 10 | 21.5 | 0 | 3.5
3418 | TORONTO BUTTONVILLE A | 5 | 23 | 10 | 17.5667 | 0.43333 | 0
3419 | TORONTO BUTTONVILLE A | 5 | 22 | 11 | 23.1 | 0 | 5.1
3419 | TORONTO BUTTONVILLE A | 5 | 23 | 11 | 18.125 | 0 | 0.125
3420 | TORONTO BUTTONVILLE A | 5 | 22 | 12 | 24 | 0 | 6
3420 | TORONTO BUTTONVILLE A | 5 | 23 | 12 | 18.4667 | 0 | 0.46667
3421 | TORONTO BUTTONVILLE A | 5 | 22 | 13 | 24.8 | 0 | 6.8
3421 | TORONTO BUTTONVILLE A | 5 | 23 | 13 | 19.45 | 0 | 1.45
3422 | TORONTO BUTTONVILLE A | 5 | 22 | 14 | 25 | 0 | 7
3422 | TORONTO BUTTONVILLE A | 5 | 23 | 14 | 19.975 | 0 | 1.975
3423 | TORONTO BUTTONVILLE A | 5 | 22 | 15 | 25 | 0 | 7
3423 | TORONTO BUTTONVILLE A | 5 | 23 | 15 | 21.825 | 0 | 3.825
3424 | TORONTO BUTTONVILLE A | 5 | 22 | 16 | 24 | 0 | 6
3424 | TORONTO BUTTONVILLE A | 5 | 23 | 16 | 23.1 | 0 | 5.1
3425 | TORONTO BUTTONVILLE A | 5 | 22 | 17 | 24.9 | 0 | 6.9
3425 | TORONTO BUTTONVILLE A | 5 | 23 | 17 | 22.65 | 0 | 4.65
3426 | TORONTO BUTTONVILLE A | 5 | 22 | 18 | 24.4 | 0 | 6.4
3426 | TORONTO BUTTONVILLE A | 5 | 23 | 18 | 22.15 | 0 | 4.15
3427 | TORONTO BUTTONVILLE A | 5 | 22 | 19 | 23.1 | 0 | 5.1
3427 | TORONTO BUTTONVILLE A | 5 | 23 | 19 | 21.15 | 0 | 3.15
3428 | TORONTO BUTTONVILLE A | 5 | 22 | 20 | 22.3 | 0 | 4.3
3428 | TORONTO BUTTONVILLE A | 5 | 23 | 20 | 19.925 | 0 | 1.925
3429 | TORONTO BUTTONVILLE A | 5 | 22 | 21 | 20.4 | 0 | 2.4
3429 | TORONTO BUTTONVILLE A | 5 | 23 | 21 | 18.1 | 0 | 0.1
3430 | TORONTO BUTTONVILLE A | 5 | 22 | 22 | 18.4 | 0 | 0.4
3430 | TORONTO BUTTONVILLE A | 5 | 23 | 22 | 16.9 | 1.1 | 0
3431 | TORONTO BUTTONVILLE A | 5 | 22 | 23 | 18.3 | 0 | 0.3
3431 | TORONTO BUTTONVILLE A | 5 | 23 | 23 | 15.95 | 2.05 | 0
3432 | TORONTO BUTTONVILLE A | 5 | 22 | 24 | 17.1 | 0.9 | 0
3432 | TORONTO BUTTONVILLE A | 5 | 23 | 24 | 15.45 | 2.55 | 0
3433 | TORONTO BUTTONVILLE A | 5 | 23 | 1 | 15.1 | 2.9 | 0
3433 | TORONTO BUTTONVILLE A | 5 | 24 | 1 | 14.625 | 3.375 | 0
3434 | TORONTO BUTTONVILLE A | 5 | 23 | 2 | 14.5 | 3.5 | 0
3434 | TORONTO BUTTONVILLE A | 5 | 24 | 2 | 13.375 | 4.625 | 0
3435 | TORONTO BUTTONVILLE A | 5 | 23 | 3 | 14.5 | 3.5 | 0
3435 | TORONTO BUTTONVILLE A | 5 | 24 | 3 | 12.175 | 5.825 | 0
3436 | TORONTO BUTTONVILLE A | 5 | 23 | 4 | 13.6 | 4.4 | 0
3436 | TORONTO BUTTONVILLE A | 5 | 24 | 4 | 11.875 | 6.125 | 0
3437 | TORONTO BUTTONVILLE A | 5 | 23 | 5 | 12.6 | 5.4 | 0
3437 | TORONTO BUTTONVILLE A | 5 | 24 | 5 | 11.975 | 6.025 | 0
3438 | TORONTO BUTTONVILLE A | 5 | 23 | 6 | 12.8 | 5.2 | 0
3438 | TORONTO BUTTONVILLE A | 5 | 24 | 6 | 11.45 | 6.55 | 0
3439 | TORONTO BUTTONVILLE A | 5 | 23 | 7 | 14.5 | 3.5 | 0
3439 | TORONTO BUTTONVILLE A | 5 | 24 | 7 | 12.45 | 5.55 | 0
3440 | TORONTO BUTTONVILLE A | 5 | 23 | 8 | 17.1 | 0.9 | 0
3440 | TORONTO BUTTONVILLE A | 5 | 24 | 8 | 14.5 | 3.5 | 0
3441 | TORONTO BUTTONVILLE A | 5 | 23 | 9 | 20.3 | 0 | 2.3
3441 | TORONTO BUTTONVILLE A | 5 | 24 | 9 | 16.175 | 1.825 | 0
3442 | TORONTO BUTTONVILLE A | 5 | 23 | 10 | 22.2 | 0 | 4.2
3442 | TORONTO BUTTONVILLE A | 5 | 24 | 10 | 17.475 | 0.525 | 0
3443 | TORONTO BUTTONVILLE A | 5 | 23 | 11 | 24.6 | 0 | 6.6
3443 | TORONTO BUTTONVILLE A | 5 | 24 | 11 | 19.475 | 0 | 1.475
3444 | TORONTO BUTTONVILLE A | 5 | 23 | 12 | 24.4 | 0 | 6.4
3444 | TORONTO BUTTONVILLE A | 5 | 24 | 12 | 20.325 | 0 | 2.325
3445 | TORONTO BUTTONVILLE A | 5 | 23 | 13 | 25.5 | 0 | 7.5
3445 | TORONTO BUTTONVILLE A | 5 | 24 | 13 | 21.175 | 0 | 3.175
3446 | TORONTO BUTTONVILLE A | 5 | 23 | 14 | 25.1 | 0 | 7.1
3446 | TORONTO BUTTONVILLE A | 5 | 24 | 14 | 21.65 | 0 | 3.65
3447 | TORONTO BUTTONVILLE A | 5 | 23 | 15 | 24.9 | 0 | 6.9
3447 | TORONTO BUTTONVILLE A | 5 | 24 | 15 | 22.075 | 0 | 4.075
3448 | TORONTO BUTTONVILLE A | 5 | 23 | 16 | 25.5 | 0 | 7.5
3448 | TORONTO BUTTONVILLE A | 5 | 24 | 16 | 22.4 | 0 | 4.4
3449 | TORONTO BUTTONVILLE A | 5 | 23 | 17 | 25 | 0 | 7
3449 | TORONTO BUTTONVILLE A | 5 | 24 | 17 | 22.975 | 0 | 4.975
3450 | TORONTO BUTTONVILLE A | 5 | 23 | 18 | 24.3 | 0 | 6.3
3450 | TORONTO BUTTONVILLE A | 5 | 24 | 18 | 22.65 | 0 | 4.65
3451 | TORONTO BUTTONVILLE A | 5 | 23 | 19 | 23.9 | 0 | 5.9
3451 | TORONTO BUTTONVILLE A | 5 | 24 | 19 | 22.075 | 0 | 4.075
3452 | TORONTO BUTTONVILLE A | 5 | 23 | 20 | 23 | 0 | 5
3452 | TORONTO BUTTONVILLE A | 5 | 24 | 20 | 20.65 | 0 | 2.65
3453 | TORONTO BUTTONVILLE A | 5 | 23 | 21 | 21.8 | 0 | 3.8
3453 | TORONTO BUTTONVILLE A | 5 | 24 | 21 | 19.425 | 0 | 1.425
3454 | TORONTO BUTTONVILLE A | 5 | 23 | 22 | 21.1 | 0 | 3.1
3454 | TORONTO BUTTONVILLE A | 5 | 24 | 22 | 18.9 | 0 | 0.9
3455 | TORONTO BUTTONVILLE A | 5 | 23 | 23 | 19.2 | 0 | 1.2
3455 | TORONTO BUTTONVILLE A | 5 | 24 | 23 | 17.925 | 0.075 | 0
3456 | TORONTO BUTTONVILLE A | 5 | 23 | 24 | 18.7 | 0 | 0.7
3456 | TORONTO BUTTONVILLE A | 5 | 24 | 24 | 17.2 | 0.8 | 0
3457 | TORONTO BUTTONVILLE A | 5 | 24 | 1 | 18 | 0 | 0
3457 | TORONTO BUTTONVILLE A | 5 | 25 | 1 | 16.375 | 1.625 | 0
3458 | TORONTO BUTTONVILLE A | 5 | 24 | 2 | 18.1 | 0 | 0.1
3458 | TORONTO BUTTONVILLE A | 5 | 25 | 2 | 15.5 | 2.5 | 0
3459 | TORONTO BUTTONVILLE A | 5 | 24 | 3 | 18.7 | 0 | 0.7
3459 | TORONTO BUTTONVILLE A | 5 | 25 | 3 | 14.5 | 3.5 | 0
3460 | TORONTO BUTTONVILLE A | 5 | 24 | 4 | 18.6 | 0 | 0.6
3460 | TORONTO BUTTONVILLE A | 5 | 25 | 4 | 14.175 | 3.825 | 0
3461 | TORONTO BUTTONVILLE A | 5 | 24 | 5 | 17.3 | 0.7 | 0
3461 | TORONTO BUTTONVILLE A | 5 | 25 | 5 | 13.95 | 4.05 | 0
3462 | TORONTO BUTTONVILLE A | 5 | 24 | 6 | 16 | 2 | 0
3462 | TORONTO BUTTONVILLE A | 5 | 25 | 6 | 14.25 | 3.75 | 0
3463 | TORONTO BUTTONVILLE A | 5 | 24 | 7 | 15.9 | 2.1 | 0
3463 | TORONTO BUTTONVILLE A | 5 | 25 | 7 | 14.55 | 3.45 | 0
3464 | TORONTO BUTTONVILLE A | 5 | 24 | 8 | 17.2 | 0.8 | 0
3464 | TORONTO BUTTONVILLE A | 5 | 25 | 8 | 15.6 | 2.4 | 0
3465 | TORONTO BUTTONVILLE A | 5 | 24 | 9 | 18.6 | 0 | 0.6
3465 | TORONTO BUTTONVILLE A | 5 | 25 | 9 | 16.75 | 1.25 | 0
3466 | TORONTO BUTTONVILLE A | 5 | 24 | 10 | 21.4 | 0 | 3.4
3466 | TORONTO BUTTONVILLE A | 5 | 25 | 10 | 18.3 | 0 | 0.3
3467 | TORONTO BUTTONVILLE A | 5 | 24 | 11 | 22.9 | 0 | 4.9
3467 | TORONTO BUTTONVILLE A | 5 | 25 | 11 | 19.175 | 0 | 1.175
3468 | TORONTO BUTTONVILLE A | 5 | 24 | 12 | 24.2 | 0 | 6.2
3468 | TORONTO BUTTONVILLE A | 5 | 25 | 12 | 19.55 | 0 | 1.55
3469 | TORONTO BUTTONVILLE A | 5 | 24 | 13 | 25.6 | 0 | 7.6
3469 | TORONTO BUTTONVILLE A | 5 | 25 | 13 | 20.3 | 0 | 2.3
3470 | TORONTO BUTTONVILLE A | 5 | 24 | 14 | 25.5 | 0 | 7.5
3470 | TORONTO BUTTONVILLE A | 5 | 25 | 14 | 21.25 | 0 | 3.25
3471 | TORONTO BUTTONVILLE A | 5 | 24 | 15 | 25.1 | 0 | 7.1
3471 | TORONTO BUTTONVILLE A | 5 | 25 | 15 | 21.625 | 0 | 3.625
3472 | TORONTO BUTTONVILLE A | 5 | 24 | 16 | 24.7 | 0 | 6.7
3472 | TORONTO BUTTONVILLE A | 5 | 25 | 16 | 22.725 | 0 | 4.725
3473 | TORONTO BUTTONVILLE A | 5 | 24 | 17 | 23.4 | 0 | 5.4
3473 | TORONTO BUTTONVILLE A | 5 | 25 | 17 | 22.725 | 0 | 4.725
3474 | TORONTO BUTTONVILLE A | 5 | 24 | 18 | 23.1 | 0 | 5.1
3474 | TORONTO BUTTONVILLE A | 5 | 25 | 18 | 22.4 | 0 | 4.4
3475 | TORONTO BUTTONVILLE A | 5 | 24 | 19 | 22.1 | 0 | 4.1
3475 | TORONTO BUTTONVILLE A | 5 | 25 | 19 | 22.375 | 0 | 4.375
3476 | TORONTO BUTTONVILLE A | 5 | 24 | 20 | 21.2 | 0 | 3.2
3476 | TORONTO BUTTONVILLE A | 5 | 25 | 20 | 21.825 | 0 | 3.825
3477 | TORONTO BUTTONVILLE A | 5 | 24 | 21 | 19.9 | 0 | 1.9
3477 | TORONTO BUTTONVILLE A | 5 | 25 | 21 | 20.9 | 0 | 2.9
3478 | TORONTO BUTTONVILLE A | 5 | 24 | 22 | 19.5 | 0 | 1.5
3478 | TORONTO BUTTONVILLE A | 5 | 25 | 22 | 20.225 | 0 | 2.225
3479 | TORONTO BUTTONVILLE A | 5 | 24 | 23 | 19.2 | 0 | 1.2
3479 | TORONTO BUTTONVILLE A | 5 | 25 | 23 | 19.55 | 0 | 1.55
3480 | TORONTO BUTTONVILLE A | 5 | 24 | 24 | 19.2 | 0 | 1.2
3480 | TORONTO BUTTONVILLE A | 5 | 25 | 24 | 18.925 | 0 | 0.925
3481 | TORONTO BUTTONVILLE A | 5 | 25 | 1 | 18.3 | 0 | 0.3
3481 | TORONTO BUTTONVILLE A | 5 | 26 | 1 | 19.4 | 0 | 1.4
3482 | TORONTO BUTTONVILLE A | 5 | 25 | 2 | 18.2 | 0 | 0.2
3482 | TORONTO BUTTONVILLE A | 5 | 26 | 2 | 19.4 | 0 | 1.4
3483 | TORONTO BUTTONVILLE A | 5 | 25 | 3 | 18.2 | 0 | 0.2
3483 | TORONTO BUTTONVILLE A | 5 | 26 | 3 | 18.575 | 0 | 0.575
3484 | TORONTO BUTTONVILLE A | 5 | 25 | 4 | 18.1 | 0 | 0.1
3484 | TORONTO BUTTONVILLE A | 5 | 26 | 4 | 18.15 | 0 | 0.15
3485 | TORONTO BUTTONVILLE A | 5 | 25 | 5 | 19.5 | 0 | 1.5
3485 | TORONTO BUTTONVILLE A | 5 | 26 | 5 | 17.45 | 0.55 | 0
3486 | TORONTO BUTTONVILLE A | 5 | 25 | 6 | 19.4 | 0 | 1.4
3486 | TORONTO BUTTONVILLE A | 5 | 26 | 6 | 17.375 | 0.625 | 0
3487 | TORONTO BUTTONVILLE A | 5 | 25 | 7 | 20.5 | 0 | 2.5
3487 | TORONTO BUTTONVILLE A | 5 | 26 | 7 | 18.1 | 0 | 0.1
3488 | TORONTO BUTTONVILLE A | 5 | 25 | 8 | 21.8 | 0 | 3.8
3488 | TORONTO BUTTONVILLE A | 5 | 26 | 8 | 18.825 | 0 | 0.825
3489 | TORONTO BUTTONVILLE A | 5 | 25 | 9 | 23.2 | 0 | 5.2
3489 | TORONTO BUTTONVILLE A | 5 | 26 | 9 | 19.75 | 0 | 1.75
3490 | TORONTO BUTTONVILLE A | 5 | 25 | 10 | 25.2 | 0 | 7.2
3490 | TORONTO BUTTONVILLE A | 5 | 26 | 10 | 20.35 | 0 | 2.35
3491 | TORONTO BUTTONVILLE A | 5 | 25 | 11 | 26.4 | 0 | 8.4
3491 | TORONTO BUTTONVILLE A | 5 | 26 | 11 | 20.55 | 0 | 2.55
3492 | TORONTO BUTTONVILLE A | 5 | 25 | 12 | 27.3 | 0 | 9.3
3492 | TORONTO BUTTONVILLE A | 5 | 26 | 12 | 20.95 | 0 | 2.95
3493 | TORONTO BUTTONVILLE A | 5 | 25 | 13 | 28.6 | 0 | 10.6
3493 | TORONTO BUTTONVILLE A | 5 | 26 | 13 | 21.75 | 0 | 3.75
3494 | TORONTO BUTTONVILLE A | 5 | 25 | 14 | 30.1 | 0 | 12.1
3494 | TORONTO BUTTONVILLE A | 5 | 26 | 14 | 22.175 | 0 | 4.175
3495 | TORONTO BUTTONVILLE A | 5 | 25 | 15 | 30 | 0 | 12
3495 | TORONTO BUTTONVILLE A | 5 | 26 | 15 | 22.3 | 0 | 4.3
3496 | TORONTO BUTTONVILLE A | 5 | 25 | 16 | 29.3 | 0 | 11.3
3496 | TORONTO BUTTONVILLE A | 5 | 26 | 16 | 22.35 | 0 | 4.35
3497 | TORONTO BUTTONVILLE A | 5 | 25 | 17 | 30.1 | 0 | 12.1
3497 | TORONTO BUTTONVILLE A | 5 | 26 | 17 | 22.05 | 0 | 4.05
3498 | TORONTO BUTTONVILLE A | 5 | 25 | 18 | 29.3 | 0 | 11.3
3498 | TORONTO BUTTONVILLE A | 5 | 26 | 18 | 20.3 | 0 | 2.3
3499 | TORONTO BUTTONVILLE A | 5 | 25 | 19 | 28.2 | 0 | 10.2
3499 | TORONTO BUTTONVILLE A | 5 | 26 | 19 | 19.8 | 0 | 1.8
3500 | TORONTO BUTTONVILLE A | 5 | 25 | 20 | 27.3 | 0 | 9.3
3500 | TORONTO BUTTONVILLE A | 5 | 26 | 20 | 18.95 | 0 | 0.95
3501 | TORONTO BUTTONVILLE A | 5 | 25 | 21 | 25.5 | 0 | 7.5
3501 | TORONTO BUTTONVILLE A | 5 | 26 | 21 | 17.5 | 0.5 | 0
3502 | TORONTO BUTTONVILLE A | 5 | 25 | 22 | 24.7 | 0 | 6.7
3502 | TORONTO BUTTONVILLE A | 5 | 26 | 22 | 16.35 | 1.65 | 0
3503 | TORONTO BUTTONVILLE A | 5 | 25 | 23 | 22.2 | 0 | 4.2
3503 | TORONTO BUTTONVILLE A | 5 | 26 | 23 | 15.725 | 2.275 | 0
3504 | TORONTO BUTTONVILLE A | 5 | 25 | 24 | 20 | 0 | 2
3504 | TORONTO BUTTONVILLE A | 5 | 26 | 24 | 14.625 | 3.375 | 0
3505 | TORONTO BUTTONVILLE A | 5 | 26 | 1 | 19.4 | 0 | 1.4
3505 | TORONTO BUTTONVILLE A | 5 | 27 | 1 | 13.8 | 4.2 | 0
3506 | TORONTO BUTTONVILLE A | 5 | 26 | 2 | 18.6 | 0 | 0.6
3506 | TORONTO BUTTONVILLE A | 5 | 27 | 2 | 13.2 | 4.8 | 0
3507 | TORONTO BUTTONVILLE A | 5 | 26 | 3 | 18 | 0 | 0
3507 | TORONTO BUTTONVILLE A | 5 | 27 | 3 | 12.725 | 5.275 | 0
3508 | TORONTO BUTTONVILLE A | 5 | 26 | 4 | 18 | 0 | 0
3508 | TORONTO BUTTONVILLE A | 5 | 27 | 4 | 12.45 | 5.55 | 0
3509 | TORONTO BUTTONVILLE A | 5 | 26 | 5 | 17.3 | 0.7 | 0
3509 | TORONTO BUTTONVILLE A | 5 | 27 | 5 | 12.4 | 5.6 | 0
3510 | TORONTO BUTTONVILLE A | 5 | 26 | 6 | 17.4 | 0.6 | 0
3510 | TORONTO BUTTONVILLE A | 5 | 27 | 6 | 12.475 | 5.525 | 0
3511 | TORONTO BUTTONVILLE A | 5 | 26 | 7 | 18.9 | 0 | 0.9
3511 | TORONTO BUTTONVILLE A | 5 | 27 | 7 | 13.325 | 4.675 | 0
3512 | TORONTO BUTTONVILLE A | 5 | 26 | 8 | 21 | 0 | 3
3512 | TORONTO BUTTONVILLE A | 5 | 27 | 8 | 14.475 | 3.525 | 0
3513 | TORONTO BUTTONVILLE A | 5 | 26 | 9 | 22.9 | 0 | 4.9
3513 | TORONTO BUTTONVILLE A | 5 | 27 | 9 | 15.425 | 2.575 | 0
3514 | TORONTO BUTTONVILLE A | 5 | 26 | 10 | 25.1 | 0 | 7.1
3514 | TORONTO BUTTONVILLE A | 5 | 27 | 10 | 16.6 | 1.4 | 0
3515 | TORONTO BUTTONVILLE A | 5 | 26 | 11 | 27.2 | 0 | 9.2
3515 | TORONTO BUTTONVILLE A | 5 | 27 | 11 | 18.025 | 0 | 0.025
3516 | TORONTO BUTTONVILLE A | 5 | 26 | 12 | 29 | 0 | 11
3516 | TORONTO BUTTONVILLE A | 5 | 27 | 12 | 18.7 | 0 | 0.7
3517 | TORONTO BUTTONVILLE A | 5 | 26 | 13 | 29.6 | 0 | 11.6
3517 | TORONTO BUTTONVILLE A | 5 | 27 | 13 | 19.15 | 0 | 1.15
3518 | TORONTO BUTTONVILLE A | 5 | 26 | 14 | 30.7 | 0 | 12.7
3518 | TORONTO BUTTONVILLE A | 5 | 27 | 14 | 20.2 | 0 | 2.2
3519 | TORONTO BUTTONVILLE A | 5 | 26 | 15 | 30.8 | 0 | 12.8
3519 | TORONTO BUTTONVILLE A | 5 | 27 | 15 | 20.35 | 0 | 2.35
3520 | TORONTO BUTTONVILLE A | 5 | 26 | 16 | 31.6 | 0 | 13.6
3520 | TORONTO BUTTONVILLE A | 5 | 27 | 16 | 20.775 | 0 | 2.775
3521 | TORONTO BUTTONVILLE A | 5 | 26 | 17 | 31.5 | 0 | 13.5
3521 | TORONTO BUTTONVILLE A | 5 | 27 | 17 | 20.5 | 0 | 2.5
3522 | TORONTO BUTTONVILLE A | 5 | 26 | 18 | 31.1 | 0 | 13.1
3522 | TORONTO BUTTONVILLE A | 5 | 27 | 18 | 19.2 | 0 | 1.2
3523 | TORONTO BUTTONVILLE A | 5 | 26 | 19 | 30.7 | 0 | 12.7
3523 | TORONTO BUTTONVILLE A | 5 | 27 | 19 | 18.225 | 0 | 0.225
3524 | TORONTO BUTTONVILLE A | 5 | 26 | 20 | 29.8 | 0 | 11.8
3524 | TORONTO BUTTONVILLE A | 5 | 27 | 20 | 17.175 | 0.825 | 0
3525 | TORONTO BUTTONVILLE A | 5 | 26 | 21 | 25 | 0 | 7
3525 | TORONTO BUTTONVILLE A | 5 | 27 | 21 | 15.55 | 2.45 | 0
3526 | TORONTO BUTTONVILLE A | 5 | 26 | 22 | 23.8 | 0 | 5.8
3526 | TORONTO BUTTONVILLE A | 5 | 27 | 22 | 14.5 | 3.5 | 0
3527 | TORONTO BUTTONVILLE A | 5 | 26 | 23 | 22 | 0 | 4
3527 | TORONTO BUTTONVILLE A | 5 | 27 | 23 | 13.75 | 4.25 | 0
3528 | TORONTO BUTTONVILLE A | 5 | 26 | 24 | 20.8 | 0 | 2.8
3528 | TORONTO BUTTONVILLE A | 5 | 27 | 24 | 13.775 | 4.225 | 0
3529 | TORONTO BUTTONVILLE A | 5 | 27 | 1 | 20.7 | 0 | 2.7
3529 | TORONTO BUTTONVILLE A | 5 | 28 | 1 | 13.15 | 4.85 | 0
3530 | TORONTO BUTTONVILLE A | 5 | 27 | 2 | 19.8 | 0 | 1.8
3530 | TORONTO BUTTONVILLE A | 5 | 28 | 2 | 12.675 | 5.325 | 0
3531 | TORONTO BUTTONVILLE A | 5 | 27 | 3 | 19.9 | 0 | 1.9
3531 | TORONTO BUTTONVILLE A | 5 | 28 | 3 | 11.95 | 6.05 | 0
3532 | TORONTO BUTTONVILLE A | 5 | 27 | 4 | 19.1 | 0 | 1.1
3532 | TORONTO BUTTONVILLE A | 5 | 28 | 4 | 11.6 | 6.4 | 0
3533 | TORONTO BUTTONVILLE A | 5 | 27 | 5 | 18.8 | 0 | 0.8
3533 | TORONTO BUTTONVILLE A | 5 | 28 | 5 | 11.225 | 6.775 | 0
3534 | TORONTO BUTTONVILLE A | 5 | 27 | 6 | 18.7 | 0 | 0.7
3534 | TORONTO BUTTONVILLE A | 5 | 28 | 6 | 10.7 | 7.3 | 0
3535 | TORONTO BUTTONVILLE A | 5 | 27 | 7 | 20.8 | 0 | 2.8
3535 | TORONTO BUTTONVILLE A | 5 | 28 | 7 | 10.525 | 7.475 | 0
3536 | TORONTO BUTTONVILLE A | 5 | 27 | 8 | 24.5 | 0 | 6.5
3536 | TORONTO BUTTONVILLE A | 5 | 28 | 8 | 11.625 | 6.375 | 0
3537 | TORONTO BUTTONVILLE A | 5 | 27 | 9 | 26.3 | 0 | 8.3
3537 | TORONTO BUTTONVILLE A | 5 | 28 | 9 | 13.1 | 4.9 | 0
3538 | TORONTO BUTTONVILLE A | 5 | 27 | 10 | 27.2 | 0 | 9.2
3538 | TORONTO BUTTONVILLE A | 5 | 28 | 10 | 13.6 | 4.4 | 0
3539 | TORONTO BUTTONVILLE A | 5 | 27 | 11 | 27.5 | 0 | 9.5
3539 | TORONTO BUTTONVILLE A | 5 | 28 | 11 | 14.025 | 3.975 | 0
3540 | TORONTO BUTTONVILLE A | 5 | 27 | 12 | 26.8 | 0 | 8.8
3540 | TORONTO BUTTONVILLE A | 5 | 28 | 12 | 14.8 | 3.2 | 0
3541 | TORONTO BUTTONVILLE A | 5 | 27 | 13 | 27.1 | 0 | 9.1
3541 | TORONTO BUTTONVILLE A | 5 | 28 | 13 | 15.225 | 2.775 | 0
3542 | TORONTO BUTTONVILLE A | 5 | 27 | 14 | 27.4 | 0 | 9.4
3542 | TORONTO BUTTONVILLE A | 5 | 28 | 14 | 15.925 | 2.075 | 0
3543 | TORONTO BUTTONVILLE A | 5 | 27 | 15 | 27.9 | 0 | 9.9
3543 | TORONTO BUTTONVILLE A | 5 | 28 | 15 | 16.375 | 1.625 | 0
3544 | TORONTO BUTTONVILLE A | 5 | 27 | 16 | 27.8 | 0 | 9.8
3544 | TORONTO BUTTONVILLE A | 5 | 28 | 16 | 16.7 | 1.3 | 0
3545 | TORONTO BUTTONVILLE A | 5 | 27 | 17 | 28.1 | 0 | 10.1
3545 | TORONTO BUTTONVILLE A | 5 | 28 | 17 | 17.25 | 0.75 | 0
3546 | TORONTO BUTTONVILLE A | 5 | 27 | 18 | 28.5 | 0 | 10.5
3546 | TORONTO BUTTONVILLE A | 5 | 28 | 18 | 17.275 | 0.725 | 0
3547 | TORONTO BUTTONVILLE A | 5 | 27 | 19 | 27.9 | 0 | 9.9
3547 | TORONTO BUTTONVILLE A | 5 | 28 | 19 | 17.275 | 0.725 | 0
3548 | TORONTO BUTTONVILLE A | 5 | 27 | 20 | 27.1 | 0 | 9.1
3548 | TORONTO BUTTONVILLE A | 5 | 28 | 20 | 16.75 | 1.25 | 0
3549 | TORONTO BUTTONVILLE A | 5 | 27 | 21 | 24.2 | 0 | 6.2
3549 | TORONTO BUTTONVILLE A | 5 | 28 | 21 | 15.525 | 2.475 | 0
3550 | TORONTO BUTTONVILLE A | 5 | 27 | 22 | 22.1 | 0 | 4.1
3550 | TORONTO BUTTONVILLE A | 5 | 28 | 22 | 14.925 | 3.075 | 0
3551 | TORONTO BUTTONVILLE A | 5 | 27 | 23 | 21.4 | 0 | 3.4
3551 | TORONTO BUTTONVILLE A | 5 | 28 | 23 | 14.6 | 3.4 | 0
3552 | TORONTO BUTTONVILLE A | 5 | 27 | 24 | 21 | 0 | 3
3552 | TORONTO BUTTONVILLE A | 5 | 28 | 24 | 13.95 | 4.05 | 0
3553 | TORONTO BUTTONVILLE A | 5 | 28 | 1 | 19.6 | 0 | 1.6
3553 | TORONTO BUTTONVILLE A | 5 | 29 | 1 | 13.25 | 4.75 | 0
3554 | TORONTO BUTTONVILLE A | 5 | 28 | 2 | 20 | 0 | 2
3554 | TORONTO BUTTONVILLE A | 5 | 29 | 2 | 13.175 | 4.825 | 0
3555 | TORONTO BUTTONVILLE A | 5 | 28 | 3 | 19.9 | 0 | 1.9
3555 | TORONTO BUTTONVILLE A | 5 | 29 | 3 | 12.75 | 5.25 | 0
3556 | TORONTO BUTTONVILLE A | 5 | 28 | 4 | 20.4 | 0 | 2.4
3556 | TORONTO BUTTONVILLE A | 5 | 29 | 4 | 12.7 | 5.3 | 0
3557 | TORONTO BUTTONVILLE A | 5 | 28 | 5 | 19.8 | 0 | 1.8
3557 | TORONTO BUTTONVILLE A | 5 | 29 | 5 | 12.475 | 5.525 | 0
3558 | TORONTO BUTTONVILLE A | 5 | 28 | 6 | 20.4 | 0 | 2.4
3558 | TORONTO BUTTONVILLE A | 5 | 29 | 6 | 12.6 | 5.4 | 0
3559 | TORONTO BUTTONVILLE A | 5 | 28 | 7 | 20.8 | 0 | 2.8
3559 | TORONTO BUTTONVILLE A | 5 | 29 | 7 | 13.225 | 4.775 | 0
3560 | TORONTO BUTTONVILLE A | 5 | 28 | 8 | 21.2 | 0 | 3.2
3560 | TORONTO BUTTONVILLE A | 5 | 29 | 8 | 14.45 | 3.55 | 0
3561 | TORONTO BUTTONVILLE A | 5 | 28 | 9 | 20.9 | 0 | 2.9
3561 | TORONTO BUTTONVILLE A | 5 | 29 | 9 | 15.45 | 2.55 | 0
3562 | TORONTO BUTTONVILLE A | 5 | 28 | 10 | 21.4 | 0 | 3.4
3562 | TORONTO BUTTONVILLE A | 5 | 29 | 10 | 17.05 | 0.95 | 0
3563 | TORONTO BUTTONVILLE A | 5 | 28 | 11 | 21.7 | 0 | 3.7
3563 | TORONTO BUTTONVILLE A | 5 | 29 | 11 | 17.65 | 0.35 | 0
3564 | TORONTO BUTTONVILLE A | 5 | 28 | 12 | 22.9 | 0 | 4.9
3564 | TORONTO BUTTONVILLE A | 5 | 29 | 12 | 18.8 | 0 | 0.8
3565 | TORONTO BUTTONVILLE A | 5 | 28 | 13 | 23.4 | 0 | 5.4
3565 | TORONTO BUTTONVILLE A | 5 | 29 | 13 | 19.325 | 0 | 1.325
3566 | TORONTO BUTTONVILLE A | 5 | 28 | 14 | 20.9 | 0 | 2.9
3566 | TORONTO BUTTONVILLE A | 5 | 29 | 14 | 20.575 | 0 | 2.575
3567 | TORONTO BUTTONVILLE A | 5 | 28 | 15 | 20.1 | 0 | 2.1
3567 | TORONTO BUTTONVILLE A | 5 | 29 | 15 | 20.875 | 0 | 2.875
3568 | TORONTO BUTTONVILLE A | 5 | 28 | 16 | 19.9 | 0 | 1.9
3568 | TORONTO BUTTONVILLE A | 5 | 29 | 16 | 20.85 | 0 | 2.85
3569 | TORONTO BUTTONVILLE A | 5 | 28 | 17 | 19.6 | 0 | 1.6
3569 | TORONTO BUTTONVILLE A | 5 | 29 | 17 | 20.625 | 0 | 2.625
3570 | TORONTO BUTTONVILLE A | 5 | 28 | 18 | 19.3 | 0 | 1.3
3570 | TORONTO BUTTONVILLE A | 5 | 29 | 18 | 20 | 0 | 2
3571 | TORONTO BUTTONVILLE A | 5 | 28 | 19 | 19.6 | 0 | 1.6
3571 | TORONTO BUTTONVILLE A | 5 | 29 | 19 | 17.9 | 0.1 | 0
3572 | TORONTO BUTTONVILLE A | 5 | 28 | 20 | 19.6 | 0 | 1.6
3572 | TORONTO BUTTONVILLE A | 5 | 29 | 20 | 16.525 | 1.475 | 0
3573 | TORONTO BUTTONVILLE A | 5 | 28 | 21 | 19.6 | 0 | 1.6
3573 | TORONTO BUTTONVILLE A | 5 | 29 | 21 | 15.775 | 2.225 | 0
3574 | TORONTO BUTTONVILLE A | 5 | 28 | 22 | 19.1 | 0 | 1.1
3574 | TORONTO BUTTONVILLE A | 5 | 29 | 22 | 14.85 | 3.15 | 0
3575 | TORONTO BUTTONVILLE A | 5 | 28 | 23 | 19 | 0 | 1
3575 | TORONTO BUTTONVILLE A | 5 | 29 | 23 | 13.85 | 4.15 | 0
3576 | TORONTO BUTTONVILLE A | 5 | 28 | 24 | 18.6 | 0 | 0.6
3576 | TORONTO BUTTONVILLE A | 5 | 29 | 24 | 13.325 | 4.675 | 0
3577 | TORONTO BUTTONVILLE A | 5 | 29 | 1 | 18.6 | 0 | 0.6
3577 | TORONTO BUTTONVILLE A | 5 | 30 | 1 | 12.675 | 5.325 | 0
3578 | TORONTO BUTTONVILLE A | 5 | 29 | 2 | 18.4 | 0 | 0.4
3578 | TORONTO BUTTONVILLE A | 5 | 30 | 2 | 12.6 | 5.4 | 0
3579 | TORONTO BUTTONVILLE A | 5 | 29 | 3 | 18.4 | 0 | 0.4
3579 | TORONTO BUTTONVILLE A | 5 | 30 | 3 | 12.35 | 5.65 | 0
3580 | TORONTO BUTTONVILLE A | 5 | 29 | 4 | 18.6 | 0 | 0.6
3580 | TORONTO BUTTONVILLE A | 5 | 30 | 4 | 11.925 | 6.075 | 0
3581 | TORONTO BUTTONVILLE A | 5 | 29 | 5 | 18.1 | 0 | 0.1
3581 | TORONTO BUTTONVILLE A | 5 | 30 | 5 | 11.5 | 6.5 | 0
3582 | TORONTO BUTTONVILLE A | 5 | 29 | 6 | 17.8 | 0.2 | 0
3582 | TORONTO BUTTONVILLE A | 5 | 30 | 6 | 11.45 | 6.55 | 0
3583 | TORONTO BUTTONVILLE A | 5 | 29 | 7 | 18.7 | 0 | 0.7
3583 | TORONTO BUTTONVILLE A | 5 | 30 | 7 | 13.075 | 4.925 | 0
3584 | TORONTO BUTTONVILLE A | 5 | 29 | 8 | 20.3 | 0 | 2.3
3584 | TORONTO BUTTONVILLE A | 5 | 30 | 8 | 14.775 | 3.225 | 0
3585 | TORONTO BUTTONVILLE A | 5 | 29 | 9 | 21.4 | 0 | 3.4
3585 | TORONTO BUTTONVILLE A | 5 | 30 | 9 | 16.2 | 1.8 | 0
3586 | TORONTO BUTTONVILLE A | 5 | 29 | 10 | 22.9 | 0 | 4.9
3586 | TORONTO BUTTONVILLE A | 5 | 30 | 10 | 18.175 | 0 | 0.175
3587 | TORONTO BUTTONVILLE A | 5 | 29 | 11 | 22.3 | 0 | 4.3
3587 | TORONTO BUTTONVILLE A | 5 | 30 | 11 | 19.6 | 0 | 1.6
3588 | TORONTO BUTTONVILLE A | 5 | 29 | 12 | 20.9 | 0 | 2.9
3588 | TORONTO BUTTONVILLE A | 5 | 30 | 12 | 20.9 | 0 | 2.9
3589 | TORONTO BUTTONVILLE A | 5 | 29 | 13 | 22.4 | 0 | 4.4
3589 | TORONTO BUTTONVILLE A | 5 | 30 | 13 | 21.4 | 0 | 3.4
3590 | TORONTO BUTTONVILLE A | 5 | 29 | 14 | 22.8 | 0 | 4.8
3590 | TORONTO BUTTONVILLE A | 5 | 30 | 14 | 21.35 | 0 | 3.35
3591 | TORONTO BUTTONVILLE A | 5 | 29 | 15 | 23.2 | 0 | 5.2
3591 | TORONTO BUTTONVILLE A | 5 | 30 | 15 | 20.725 | 0 | 2.725
3592 | TORONTO BUTTONVILLE A | 5 | 29 | 16 | 19.6 | 0 | 1.6
3592 | TORONTO BUTTONVILLE A | 5 | 30 | 16 | 21.1 | 0 | 3.1
3593 | TORONTO BUTTONVILLE A | 5 | 29 | 17 | 18.7 | 0 | 0.7
3593 | TORONTO BUTTONVILLE A | 5 | 30 | 17 | 21.225 | 0 | 3.225
3594 | TORONTO BUTTONVILLE A | 5 | 29 | 18 | 16 | 2 | 0
3594 | TORONTO BUTTONVILLE A | 5 | 30 | 18 | 22.075 | 0 | 4.075
3595 | TORONTO BUTTONVILLE A | 5 | 29 | 19 | 15.9 | 2.1 | 0
3595 | TORONTO BUTTONVILLE A | 5 | 30 | 19 | 21.325 | 0 | 3.325
3596 | TORONTO BUTTONVILLE A | 5 | 29 | 20 | 15.7 | 2.3 | 0
3596 | TORONTO BUTTONVILLE A | 5 | 30 | 20 | 20.525 | 0 | 2.525
3597 | TORONTO BUTTONVILLE A | 5 | 29 | 21 | 15.1 | 2.9 | 0
3597 | TORONTO BUTTONVILLE A | 5 | 30 | 21 | 18.6 | 0 | 0.6
3598 | TORONTO BUTTONVILLE A | 5 | 29 | 22 | 15.1 | 2.9 | 0
3598 | TORONTO BUTTONVILLE A | 5 | 30 | 22 | 17.425 | 0.575 | 0
3599 | TORONTO BUTTONVILLE A | 5 | 29 | 23 | 14.8 | 3.2 | 0
3599 | TORONTO BUTTONVILLE A | 5 | 30 | 23 | 16.925 | 1.075 | 0
3600 | TORONTO BUTTONVILLE A | 5 | 29 | 24 | 14.3 | 3.7 | 0
3600 | TORONTO BUTTONVILLE A | 5 | 30 | 24 | 16.375 | 1.625 | 0
3601 | TORONTO BUTTONVILLE A | 5 | 30 | 1 | 14 | 4 | 0
3601 | TORONTO BUTTONVILLE A | 5 | 31 | 1 | 15.875 | 2.125 | 0
3602 | TORONTO BUTTONVILLE A | 5 | 30 | 2 | 13.2 | 4.8 | 0
3602 | TORONTO BUTTONVILLE A | 5 | 31 | 2 | 14.875 | 3.125 | 0
3603 | TORONTO BUTTONVILLE A | 5 | 30 | 3 | 12.2 | 5.8 | 0
3603 | TORONTO BUTTONVILLE A | 5 | 31 | 3 | 13.625 | 4.375 | 0
3604 | TORONTO BUTTONVILLE A | 5 | 30 | 4 | 11.9 | 6.1 | 0
3604 | TORONTO BUTTONVILLE A | 5 | 31 | 4 | 12.7 | 5.3 | 0
3605 | TORONTO BUTTONVILLE A | 5 | 30 | 5 | 11.8 | 6.2 | 0
3605 | TORONTO BUTTONVILLE A | 5 | 31 | 5 | 12.05 | 5.95 | 0
3606 | TORONTO BUTTONVILLE A | 5 | 30 | 6 | 11.9 | 6.1 | 0
3606 | TORONTO BUTTONVILLE A | 5 | 31 | 6 | 12.475 | 5.525 | 0
3607 | TORONTO BUTTONVILLE A | 5 | 30 | 7 | 12.4 | 5.6 | 0
3607 | TORONTO BUTTONVILLE A | 5 | 31 | 7 | 13.4 | 4.6 | 0
3608 | TORONTO BUTTONVILLE A | 5 | 30 | 8 | 13.1 | 4.9 | 0
3608 | TORONTO BUTTONVILLE A | 5 | 31 | 8 | 15.125 | 2.875 | 0
3609 | TORONTO BUTTONVILLE A | 5 | 30 | 9 | 15 | 3 | 0
3609 | TORONTO BUTTONVILLE A | 5 | 31 | 9 | 16.9 | 1.1 | 0
3610 | TORONTO BUTTONVILLE A | 5 | 30 | 10 | 16.1 | 1.9 | 0
3610 | TORONTO BUTTONVILLE A | 5 | 31 | 10 | 18.275 | 0 | 0.275
3611 | TORONTO BUTTONVILLE A | 5 | 30 | 11 | 16 | 2 | 0
3611 | TORONTO BUTTONVILLE A | 5 | 31 | 11 | 19.5 | 0 | 1.5
3612 | TORONTO BUTTONVILLE A | 5 | 30 | 12 | 16.8 | 1.2 | 0
3612 | TORONTO BUTTONVILLE A | 5 | 31 | 12 | 20.725 | 0 | 2.725
3613 | TORONTO BUTTONVILLE A | 5 | 30 | 13 | 17 | 1 | 0
3613 | TORONTO BUTTONVILLE A | 5 | 31 | 13 | 21.55 | 0 | 3.55
3614 | TORONTO BUTTONVILLE A | 5 | 30 | 14 | 17.4 | 0.6 | 0
3614 | TORONTO BUTTONVILLE A | 5 | 31 | 14 | 22.45 | 0 | 4.45
3615 | TORONTO BUTTONVILLE A | 5 | 30 | 15 | 15.1 | 2.9 | 0
3615 | TORONTO BUTTONVILLE A | 5 | 31 | 15 | 22.725 | 0 | 4.725
3616 | TORONTO BUTTONVILLE A | 5 | 30 | 16 | 13.7 | 4.3 | 0
3616 | TORONTO BUTTONVILLE A | 5 | 31 | 16 | 22.975 | 0 | 4.975
3617 | TORONTO BUTTONVILLE A | 5 | 30 | 17 | 13.9 | 4.1 | 0
3617 | TORONTO BUTTONVILLE A | 5 | 31 | 17 | 22.525 | 0 | 4.525
3618 | TORONTO BUTTONVILLE A | 5 | 30 | 18 | 14.2 | 3.8 | 0
3618 | TORONTO BUTTONVILLE A | 5 | 31 | 18 | 21.875 | 0 | 3.875
3619 | TORONTO BUTTONVILLE A | 5 | 30 | 19 | 13.9 | 4.1 | 0
3619 | TORONTO BUTTONVILLE A | 5 | 31 | 19 | 21.325 | 0 | 3.325
3620 | TORONTO BUTTONVILLE A | 5 | 30 | 20 | 12.4 | 5.6 | 0
3620 | TORONTO BUTTONVILLE A | 5 | 31 | 20 | 19.575 | 0 | 1.575
3621 | TORONTO BUTTONVILLE A | 5 | 30 | 21 | 11 | 7 | 0
3621 | TORONTO BUTTONVILLE A | 5 | 31 | 21 | 18.125 | 0 | 0.125
3622 | TORONTO BUTTONVILLE A | 5 | 30 | 22 | 9.9 | 8.1 | 0
3622 | TORONTO BUTTONVILLE A | 5 | 31 | 22 | 17.6 | 0.4 | 0
3623 | TORONTO BUTTONVILLE A | 5 | 30 | 23 | 9.7 | 8.3 | 0
3623 | TORONTO BUTTONVILLE A | 5 | 31 | 23 | 16.3 | 1.7 | 0
3624 | TORONTO BUTTONVILLE A | 5 | 30 | 24 | 8.7 | 9.3 | 0
3624 | TORONTO BUTTONVILLE A | 5 | 31 | 24 | 15.825 | 2.175 | 0
3625 | TORONTO BUTTONVILLE A | 5 | 31 | 1 | 6.7 | 11.3 | 0
3625 | TORONTO BUTTONVILLE A | 6 | 1 | 1 | 15.5 | 2.5 | 0
3626 | TORONTO BUTTONVILLE A | 5 | 31 | 2 | 7.3 | 10.7 | 0
3626 | TORONTO BUTTONVILLE A | 6 | 1 | 2 | 15.2 | 2.8 | 0
3627 | TORONTO BUTTONVILLE A | 5 | 31 | 3 | 7.2 | 10.8 | 0
3627 | TORONTO BUTTONVILLE A | 6 | 1 | 3 | 15.125 | 2.875 | 0
3628 | TORONTO BUTTONVILLE A | 5 | 31 | 4 | 6.8 | 11.2 | 0
3628 | TORONTO BUTTONVILLE A | 6 | 1 | 4 | 14.35 | 3.65 | 0
3629 | TORONTO BUTTONVILLE A | 5 | 31 | 5 | 6.8 | 11.2 | 0
3629 | TORONTO BUTTONVILLE A | 6 | 1 | 5 | 14.225 | 3.775 | 0
3630 | TORONTO BUTTONVILLE A | 5 | 31 | 6 | 7.1 | 10.9 | 0
3630 | TORONTO BUTTONVILLE A | 6 | 1 | 6 | 13.7 | 4.3 | 0
3631 | TORONTO BUTTONVILLE A | 5 | 31 | 7 | 7.7 | 10.3 | 0
3631 | TORONTO BUTTONVILLE A | 6 | 1 | 7 | 14.125 | 3.875 | 0
3632 | TORONTO BUTTONVILLE A | 5 | 31 | 8 | 8.9 | 9.1 | 0
3632 | TORONTO BUTTONVILLE A | 6 | 1 | 8 | 15.9 | 2.1 | 0
3633 | TORONTO BUTTONVILLE A | 5 | 31 | 9 | 10.3 | 7.7 | 0
3633 | TORONTO BUTTONVILLE A | 6 | 1 | 9 | 17.225 | 0.775 | 0
3634 | TORONTO BUTTONVILLE A | 5 | 31 | 10 | 11 | 7 | 0
3634 | TORONTO BUTTONVILLE A | 6 | 1 | 10 | 18.325 | 0 | 0.325
3635 | TORONTO BUTTONVILLE A | 5 | 31 | 11 | 11.8 | 6.2 | 0
3635 | TORONTO BUTTONVILLE A | 6 | 1 | 11 | 19.325 | 0 | 1.325
3636 | TORONTO BUTTONVILLE A | 5 | 31 | 12 | 12.1 | 5.9 | 0
3636 | TORONTO BUTTONVILLE A | 6 | 1 | 12 | 20.25 | 0 | 2.25
3637 | TORONTO BUTTONVILLE A | 5 | 31 | 13 | 12.3 | 5.7 | 0
3637 | TORONTO BUTTONVILLE A | 6 | 1 | 13 | 20.525 | 0 | 2.525
3638 | TORONTO BUTTONVILLE A | 5 | 31 | 14 | 12.7 | 5.3 | 0
3638 | TORONTO BUTTONVILLE A | 6 | 1 | 14 | 20.875 | 0 | 2.875
3639 | TORONTO BUTTONVILLE A | 5 | 31 | 15 | 12.8 | 5.2 | 0
3639 | TORONTO BUTTONVILLE A | 6 | 1 | 15 | 21 | 0 | 3
3640 | TORONTO BUTTONVILLE A | 5 | 31 | 16 | 13.8 | 4.2 | 0
3640 | TORONTO BUTTONVILLE A | 6 | 1 | 16 | 21.9 | 0 | 3.9
3641 | TORONTO BUTTONVILLE A | 5 | 31 | 17 | 13.4 | 4.6 | 0
3641 | TORONTO BUTTONVILLE A | 6 | 1 | 17 | 21.7 | 0 | 3.7
3642 | TORONTO BUTTONVILLE A | 5 | 31 | 18 | 13.2 | 4.8 | 0
3642 | TORONTO BUTTONVILLE A | 6 | 1 | 18 | 21.375 | 0 | 3.375
3643 | TORONTO BUTTONVILLE A | 5 | 31 | 19 | 13 | 5 | 0
3643 | TORONTO BUTTONVILLE A | 6 | 1 | 19 | 19.925 | 0 | 1.925
3644 | TORONTO BUTTONVILLE A | 5 | 31 | 20 | 13.2 | 4.8 | 0
3644 | TORONTO BUTTONVILLE A | 6 | 1 | 20 | 17.8 | 0.2 | 0
3645 | TORONTO BUTTONVILLE A | 5 | 31 | 21 | 13 | 5 | 0
3645 | TORONTO BUTTONVILLE A | 6 | 1 | 21 | 16.625 | 1.375 | 0
3646 | TORONTO BUTTONVILLE A | 5 | 31 | 22 | 12.3 | 5.7 | 0
3646 | TORONTO BUTTONVILLE A | 6 | 1 | 22 | 15.825 | 2.175 | 0
3647 | TORONTO BUTTONVILLE A | 5 | 31 | 23 | 12.4 | 5.6 | 0
3647 | TORONTO BUTTONVILLE A | 6 | 1 | 23 | 14.8 | 3.2 | 0
3648 | TORONTO BUTTONVILLE A | 5 | 31 | 24 | 12.1 | 5.9 | 0
3648 | TORONTO BUTTONVILLE A | 6 | 1 | 24 | 14.65 | 3.35 | 0
3649 | TORONTO BUTTONVILLE A | 6 | 1 | 1 | 11.6 | 6.4 | 0
3649 | TORONTO BUTTONVILLE A | 6 | 2 | 1 | 14.4 | 3.6 | 0
3650 | TORONTO BUTTONVILLE A | 6 | 1 | 2 | 10.2 | 7.8 | 0
3650 | TORONTO BUTTONVILLE A | 6 | 2 | 2 | 14 | 4 | 0
3651 | TORONTO BUTTONVILLE A | 6 | 1 | 3 | 9.8 | 8.2 | 0
3651 | TORONTO BUTTONVILLE A | 6 | 2 | 3 | 13.275 | 4.725 | 0
3652 | TORONTO BUTTONVILLE A | 6 | 1 | 4 | 9.4 | 8.6 | 0
3652 | TORONTO BUTTONVILLE A | 6 | 2 | 4 | 12.55 | 5.45 | 0
3653 | TORONTO BUTTONVILLE A | 6 | 1 | 5 | 9 | 9 | 0
3653 | TORONTO BUTTONVILLE A | 6 | 2 | 5 | 12.1 | 5.9 | 0
3654 | TORONTO BUTTONVILLE A | 6 | 1 | 6 | 7.6 | 10.4 | 0
3654 | TORONTO BUTTONVILLE A | 6 | 2 | 6 | 11.95 | 6.05 | 0
3655 | TORONTO BUTTONVILLE A | 6 | 1 | 7 | 9.2 | 8.8 | 0
3655 | TORONTO BUTTONVILLE A | 6 | 2 | 7 | 12.175 | 5.825 | 0
3656 | TORONTO BUTTONVILLE A | 6 | 1 | 8 | 10.9 | 7.1 | 0
3656 | TORONTO BUTTONVILLE A | 6 | 2 | 8 | 13.275 | 4.725 | 0
3657 | TORONTO BUTTONVILLE A | 6 | 1 | 9 | 13.3 | 4.7 | 0
3657 | TORONTO BUTTONVILLE A | 6 | 2 | 9 | 14.55 | 3.45 | 0
3658 | TORONTO BUTTONVILLE A | 6 | 1 | 10 | 16 | 2 | 0
3658 | TORONTO BUTTONVILLE A | 6 | 2 | 10 | 15.625 | 2.375 | 0
3659 | TORONTO BUTTONVILLE A | 6 | 1 | 11 | 17.7 | 0.3 | 0
3659 | TORONTO BUTTONVILLE A | 6 | 2 | 11 | 17.275 | 0.725 | 0
3660 | TORONTO BUTTONVILLE A | 6 | 1 | 12 | 19.6 | 0 | 1.6
3660 | TORONTO BUTTONVILLE A | 6 | 2 | 12 | 18.65 | 0 | 0.65
3661 | TORONTO BUTTONVILLE A | 6 | 1 | 13 | 19.9 | 0 | 1.9
3661 | TORONTO BUTTONVILLE A | 6 | 2 | 13 | 19.55 | 0 | 1.55
3662 | TORONTO BUTTONVILLE A | 6 | 1 | 14 | 21.6 | 0 | 3.6
3662 | TORONTO BUTTONVILLE A | 6 | 2 | 14 | 20.225 | 0 | 2.225
3663 | TORONTO BUTTONVILLE A | 6 | 1 | 15 | 22.2 | 0 | 4.2
3663 | TORONTO BUTTONVILLE A | 6 | 2 | 15 | 20.85 | 0 | 2.85
3664 | TORONTO BUTTONVILLE A | 6 | 1 | 16 | 22.6 | 0 | 4.6
3664 | TORONTO BUTTONVILLE A | 6 | 2 | 16 | 21.1 | 0 | 3.1
3665 | TORONTO BUTTONVILLE A | 6 | 1 | 17 | 22.9 | 0 | 4.9
3665 | TORONTO BUTTONVILLE A | 6 | 2 | 17 | 21.1 | 0 | 3.1
3666 | TORONTO BUTTONVILLE A | 6 | 1 | 18 | 22.6 | 0 | 4.6
3666 | TORONTO BUTTONVILLE A | 6 | 2 | 18 | 20.6 | 0 | 2.6
3667 | TORONTO BUTTONVILLE A | 6 | 1 | 19 | 21.9 | 0 | 3.9
3667 | TORONTO BUTTONVILLE A | 6 | 2 | 19 | 19.2 | 0 | 1.2
3668 | TORONTO BUTTONVILLE A | 6 | 1 | 20 | 21.1 | 0 | 3.1
3668 | TORONTO BUTTONVILLE A | 6 | 2 | 20 | 17.575 | 0.425 | 0
3669 | TORONTO BUTTONVILLE A | 6 | 1 | 21 | 19.8 | 0 | 1.8
3669 | TORONTO BUTTONVILLE A | 6 | 2 | 21 | 15.925 | 2.075 | 0
3670 | TORONTO BUTTONVILLE A | 6 | 1 | 22 | 18.6 | 0 | 0.6
3670 | TORONTO BUTTONVILLE A | 6 | 2 | 22 | 15.15 | 2.85 | 0
3671 | TORONTO BUTTONVILLE A | 6 | 1 | 23 | 17.4 | 0.6 | 0
3671 | TORONTO BUTTONVILLE A | 6 | 2 | 23 | 13.95 | 4.05 | 0
3672 | TORONTO BUTTONVILLE A | 6 | 1 | 24 | 17.2 | 0.8 | 0
3672 | TORONTO BUTTONVILLE A | 6 | 2 | 24 | 12.825 | 5.175 | 0
3673 | TORONTO BUTTONVILLE A | 6 | 2 | 1 | 17.2 | 0.8 | 0
3673 | TORONTO BUTTONVILLE A | 6 | 3 | 1 | 12.1 | 5.9 | 0
3674 | TORONTO BUTTONVILLE A | 6 | 2 | 2 | 17.1 | 0.9 | 0
3674 | TORONTO BUTTONVILLE A | 6 | 3 | 2 | 11.8 | 6.2 | 0
3675 | TORONTO BUTTONVILLE A | 6 | 2 | 3 | 17.4 | 0.6 | 0
3675 | TORONTO BUTTONVILLE A | 6 | 3 | 3 | 11.775 | 6.225 | 0
3676 | TORONTO BUTTONVILLE A | 6 | 2 | 4 | 16.7 | 1.3 | 0
3676 | TORONTO BUTTONVILLE A | 6 | 3 | 4 | 11.8 | 6.2 | 0
3677 | TORONTO BUTTONVILLE A | 6 | 2 | 5 | 15.1 | 2.9 | 0
3677 | TORONTO BUTTONVILLE A | 6 | 3 | 5 | 11.425 | 6.575 | 0
3678 | TORONTO BUTTONVILLE A | 6 | 2 | 6 | 13.7 | 4.3 | 0
3678 | TORONTO BUTTONVILLE A | 6 | 3 | 6 | 11.55 | 6.45 | 0
3679 | TORONTO BUTTONVILLE A | 6 | 2 | 7 | 13.8 | 4.2 | 0
3679 | TORONTO BUTTONVILLE A | 6 | 3 | 7 | 12.475 | 5.525 | 0
3680 | TORONTO BUTTONVILLE A | 6 | 2 | 8 | 14.1 | 3.9 | 0
3680 | TORONTO BUTTONVILLE A | 6 | 3 | 8 | 13 | 5 | 0
3681 | TORONTO BUTTONVILLE A | 6 | 2 | 9 | 14.1 | 3.9 | 0
3681 | TORONTO BUTTONVILLE A | 6 | 3 | 9 | 13.625 | 4.375 | 0
3682 | TORONTO BUTTONVILLE A | 6 | 2 | 10 | 14.2 | 3.8 | 0
3682 | TORONTO BUTTONVILLE A | 6 | 3 | 10 | 14.2 | 3.8 | 0
3683 | TORONTO BUTTONVILLE A | 6 | 2 | 11 | 15.5 | 2.5 | 0
3683 | TORONTO BUTTONVILLE A | 6 | 3 | 11 | 15.125 | 2.875 | 0
3684 | TORONTO BUTTONVILLE A | 6 | 2 | 12 | 18 | 0 | 0
3684 | TORONTO BUTTONVILLE A | 6 | 3 | 12 | 16.7 | 1.3 | 0
3685 | TORONTO BUTTONVILLE A | 6 | 2 | 13 | 19.5 | 0 | 1.5
3685 | TORONTO BUTTONVILLE A | 6 | 3 | 13 | 17.1 | 0.9 | 0
3686 | TORONTO BUTTONVILLE A | 6 | 2 | 14 | 21.5 | 0 | 3.5
3686 | TORONTO BUTTONVILLE A | 6 | 3 | 14 | 18.075 | 0 | 0.075
3687 | TORONTO BUTTONVILLE A | 6 | 2 | 15 | 22 | 0 | 4
3687 | TORONTO BUTTONVILLE A | 6 | 3 | 15 | 19.325 | 0 | 1.325
3688 | TORONTO BUTTONVILLE A | 6 | 2 | 16 | 22.9 | 0 | 4.9
3688 | TORONTO BUTTONVILLE A | 6 | 3 | 16 | 19.725 | 0 | 1.725
3689 | TORONTO BUTTONVILLE A | 6 | 2 | 17 | 23.5 | 0 | 5.5
3689 | TORONTO BUTTONVILLE A | 6 | 3 | 17 | 19.4 | 0 | 1.4
3690 | TORONTO BUTTONVILLE A | 6 | 2 | 18 | 23.6 | 0 | 5.6
3690 | TORONTO BUTTONVILLE A | 6 | 3 | 18 | 19.4 | 0 | 1.4
3691 | TORONTO BUTTONVILLE A | 6 | 2 | 19 | 23.2 | 0 | 5.2
3691 | TORONTO BUTTONVILLE A | 6 | 3 | 19 | 18.9 | 0 | 0.9
3692 | TORONTO BUTTONVILLE A | 6 | 2 | 20 | 21.4 | 0 | 3.4
3692 | TORONTO BUTTONVILLE A | 6 | 3 | 20 | 17.925 | 0.075 | 0
3693 | TORONTO BUTTONVILLE A | 6 | 2 | 21 | 17.1 | 0.9 | 0
3693 | TORONTO BUTTONVILLE A | 6 | 3 | 21 | 16.675 | 1.325 | 0
3694 | TORONTO BUTTONVILLE A | 6 | 2 | 22 | 14.5 | 3.5 | 0
3694 | TORONTO BUTTONVILLE A | 6 | 3 | 22 | 15.975 | 2.025 | 0
3695 | TORONTO BUTTONVILLE A | 6 | 2 | 23 | 14.1 | 3.9 | 0
3695 | TORONTO BUTTONVILLE A | 6 | 3 | 23 | 15.25 | 2.75 | 0
3696 | TORONTO BUTTONVILLE A | 6 | 2 | 24 | 14.3 | 3.7 | 0
3696 | TORONTO BUTTONVILLE A | 6 | 3 | 24 | 14.525 | 3.475 | 0
3697 | TORONTO BUTTONVILLE A | 6 | 3 | 1 | 14.3 | 3.7 | 0
3697 | TORONTO BUTTONVILLE A | 6 | 4 | 1 | 14.05 | 3.95 | 0
3698 | TORONTO BUTTONVILLE A | 6 | 3 | 2 | 13.9 | 4.1 | 0
3698 | TORONTO BUTTONVILLE A | 6 | 4 | 2 | 13.475 | 4.525 | 0
3699 | TORONTO BUTTONVILLE A | 6 | 3 | 3 | 13.3 | 4.7 | 0
3699 | TORONTO BUTTONVILLE A | 6 | 4 | 3 | 12.75 | 5.25 | 0
3700 | TORONTO BUTTONVILLE A | 6 | 3 | 4 | 13.6 | 4.4 | 0
3700 | TORONTO BUTTONVILLE A | 6 | 4 | 4 | 12.675 | 5.325 | 0
3701 | TORONTO BUTTONVILLE A | 6 | 3 | 5 | 13.7 | 4.3 | 0
3701 | TORONTO BUTTONVILLE A | 6 | 4 | 5 | 12 | 6 | 0
3702 | TORONTO BUTTONVILLE A | 6 | 3 | 6 | 14.8 | 3.2 | 0
3702 | TORONTO BUTTONVILLE A | 6 | 4 | 6 | 11.625 | 6.375 | 0
3703 | TORONTO BUTTONVILLE A | 6 | 3 | 7 | 16.1 | 1.9 | 0
3703 | TORONTO BUTTONVILLE A | 6 | 4 | 7 | 13.125 | 4.875 | 0
3704 | TORONTO BUTTONVILLE A | 6 | 3 | 8 | 16.4 | 1.6 | 0
3704 | TORONTO BUTTONVILLE A | 6 | 4 | 8 | 14.075 | 3.925 | 0
3705 | TORONTO BUTTONVILLE A | 6 | 3 | 9 | 17.9 | 0.1 | 0
3705 | TORONTO BUTTONVILLE A | 6 | 4 | 9 | 14.9 | 3.1 | 0
3706 | TORONTO BUTTONVILLE A | 6 | 3 | 10 | 18 | 0 | 0
3706 | TORONTO BUTTONVILLE A | 6 | 4 | 10 | 15.475 | 2.525 | 0
3707 | TORONTO BUTTONVILLE A | 6 | 3 | 11 | 20.3 | 0 | 2.3
3707 | TORONTO BUTTONVILLE A | 6 | 4 | 11 | 15.8 | 2.2 | 0
3708 | TORONTO BUTTONVILLE A | 6 | 3 | 12 | 22.2 | 0 | 4.2
3708 | TORONTO BUTTONVILLE A | 6 | 4 | 12 | 16.425 | 1.575 | 0
3709 | TORONTO BUTTONVILLE A | 6 | 3 | 13 | 23.5 | 0 | 5.5
3709 | TORONTO BUTTONVILLE A | 6 | 4 | 13 | 17.25 | 0.75 | 0
3710 | TORONTO BUTTONVILLE A | 6 | 3 | 14 | 24.5 | 0 | 6.5
3710 | TORONTO BUTTONVILLE A | 6 | 4 | 14 | 17.525 | 0.475 | 0
3711 | TORONTO BUTTONVILLE A | 6 | 3 | 15 | 25.3 | 0 | 7.3
3711 | TORONTO BUTTONVILLE A | 6 | 4 | 15 | 17.925 | 0.075 | 0
3712 | TORONTO BUTTONVILLE A | 6 | 3 | 16 | 25.4 | 0 | 7.4
3712 | TORONTO BUTTONVILLE A | 6 | 4 | 16 | 17.775 | 0.225 | 0
3713 | TORONTO BUTTONVILLE A | 6 | 3 | 17 | 25.6 | 0 | 7.6
3713 | TORONTO BUTTONVILLE A | 6 | 4 | 17 | 18.125 | 0 | 0.125
3714 | TORONTO BUTTONVILLE A | 6 | 3 | 18 | 25 | 0 | 7
3714 | TORONTO BUTTONVILLE A | 6 | 4 | 18 | 17.925 | 0.075 | 0
3715 | TORONTO BUTTONVILLE A | 6 | 3 | 19 | 23 | 0 | 5
3715 | TORONTO BUTTONVILLE A | 6 | 4 | 19 | 17.275 | 0.725 | 0
3716 | TORONTO BUTTONVILLE A | 6 | 3 | 20 | 22.7 | 0 | 4.7
3716 | TORONTO BUTTONVILLE A | 6 | 4 | 20 | 16.975 | 1.025 | 0
3717 | TORONTO BUTTONVILLE A | 6 | 3 | 21 | 21.2 | 0 | 3.2
3717 | TORONTO BUTTONVILLE A | 6 | 4 | 21 | 15.8 | 2.2 | 0
3718 | TORONTO BUTTONVILLE A | 6 | 3 | 22 | 19.9 | 0 | 1.9
3718 | TORONTO BUTTONVILLE A | 6 | 4 | 22 | 14.8 | 3.2 | 0
3719 | TORONTO BUTTONVILLE A | 6 | 3 | 23 | 18.9 | 0 | 0.9
3719 | TORONTO BUTTONVILLE A | 6 | 4 | 23 | 14.225 | 3.775 | 0
3720 | TORONTO BUTTONVILLE A | 6 | 3 | 24 | 18.3 | 0 | 0.3
3720 | TORONTO BUTTONVILLE A | 6 | 4 | 24 | 13.625 | 4.375 | 0
3721 | TORONTO BUTTONVILLE A | 6 | 4 | 1 | 17.6 | 0.4 | 0
3721 | TORONTO BUTTONVILLE A | 6 | 5 | 1 | 13.275 | 4.725 | 0
3722 | TORONTO BUTTONVILLE A | 6 | 4 | 2 | 17.8 | 0.2 | 0
3722 | TORONTO BUTTONVILLE A | 6 | 5 | 2 | 13.175 | 4.825 | 0
3723 | TORONTO BUTTONVILLE A | 6 | 4 | 3 | 17.8 | 0.2 | 0
3723 | TORONTO BUTTONVILLE A | 6 | 5 | 3 | 13 | 5 | 0
3724 | TORONTO BUTTONVILLE A | 6 | 4 | 4 | 16.3 | 1.7 | 0
3724 | TORONTO BUTTONVILLE A | 6 | 5 | 4 | 13.325 | 4.675 | 0
3725 | TORONTO BUTTONVILLE A | 6 | 4 | 5 | 16.7 | 1.3 | 0
3725 | TORONTO BUTTONVILLE A | 6 | 5 | 5 | 13.7 | 4.3 | 0
3726 | TORONTO BUTTONVILLE A | 6 | 4 | 6 | 17.1 | 0.9 | 0
3726 | TORONTO BUTTONVILLE A | 6 | 5 | 6 | 14.025 | 3.975 | 0
3727 | TORONTO BUTTONVILLE A | 6 | 4 | 7 | 17.5 | 0.5 | 0
3727 | TORONTO BUTTONVILLE A | 6 | 5 | 7 | 14.65 | 3.35 | 0
3728 | TORONTO BUTTONVILLE A | 6 | 4 | 8 | 20.8 | 0 | 2.8
3728 | TORONTO BUTTONVILLE A | 6 | 5 | 8 | 15.625 | 2.375 | 0
3729 | TORONTO BUTTONVILLE A | 6 | 4 | 9 | 23.1 | 0 | 5.1
3729 | TORONTO BUTTONVILLE A | 6 | 5 | 9 | 16.775 | 1.225 | 0
3730 | TORONTO BUTTONVILLE A | 6 | 4 | 10 | 24 | 0 | 6
3730 | TORONTO BUTTONVILLE A | 6 | 5 | 10 | 17.075 | 0.925 | 0
3731 | TORONTO BUTTONVILLE A | 6 | 4 | 11 | 27 | 0 | 9
3731 | TORONTO BUTTONVILLE A | 6 | 5 | 11 | 17.825 | 0.175 | 0
3732 | TORONTO BUTTONVILLE A | 6 | 4 | 12 | 28.5 | 0 | 10.5
3732 | TORONTO BUTTONVILLE A | 6 | 5 | 12 | 18.4 | 0 | 0.4
3733 | TORONTO BUTTONVILLE A | 6 | 4 | 13 | 29.2 | 0 | 11.2
3733 | TORONTO BUTTONVILLE A | 6 | 5 | 13 | 18 | 0 | 0
3734 | TORONTO BUTTONVILLE A | 6 | 4 | 14 | 29.9 | 0 | 11.9
3734 | TORONTO BUTTONVILLE A | 6 | 5 | 14 | 18.375 | 0 | 0.375
3735 | TORONTO BUTTONVILLE A | 6 | 4 | 15 | 29.4 | 0 | 11.4
3735 | TORONTO BUTTONVILLE A | 6 | 5 | 15 | 18.375 | 0 | 0.375
3736 | TORONTO BUTTONVILLE A | 6 | 4 | 16 | 30.7 | 0 | 12.7
3736 | TORONTO BUTTONVILLE A | 6 | 5 | 16 | 17.7 | 0.3 | 0
3737 | TORONTO BUTTONVILLE A | 6 | 4 | 17 | 28.2 | 0 | 10.2
3737 | TORONTO BUTTONVILLE A | 6 | 5 | 17 | 17.65 | 0.35 | 0
3738 | TORONTO BUTTONVILLE A | 6 | 4 | 18 | 27.1 | 0 | 9.1
3738 | TORONTO BUTTONVILLE A | 6 | 5 | 18 | 17.9 | 0.1 | 0
3739 | TORONTO BUTTONVILLE A | 6 | 4 | 19 | 25.9 | 0 | 7.9
3739 | TORONTO BUTTONVILLE A | 6 | 5 | 19 | 17.65 | 0.35 | 0
3740 | TORONTO BUTTONVILLE A | 6 | 4 | 20 | 25.8 | 0 | 7.8
3740 | TORONTO BUTTONVILLE A | 6 | 5 | 20 | 17.025 | 0.975 | 0
3741 | TORONTO BUTTONVILLE A | 6 | 4 | 21 | 23.9 | 0 | 5.9
3741 | TORONTO BUTTONVILLE A | 6 | 5 | 21 | 16.525 | 1.475 | 0
3742 | TORONTO BUTTONVILLE A | 6 | 4 | 22 | 22.6 | 0 | 4.6
3742 | TORONTO BUTTONVILLE A | 6 | 5 | 22 | 16.05 | 1.95 | 0
3743 | TORONTO BUTTONVILLE A | 6 | 4 | 23 | 22 | 0 | 4
3743 | TORONTO BUTTONVILLE A | 6 | 5 | 23 | 15.55 | 2.45 | 0
3744 | TORONTO BUTTONVILLE A | 6 | 4 | 24 | 21 | 0 | 3
3744 | TORONTO BUTTONVILLE A | 6 | 5 | 24 | 15.475 | 2.525 | 0
3745 | TORONTO BUTTONVILLE A | 6 | 5 | 1 | 19.7 | 0 | 1.7
3745 | TORONTO BUTTONVILLE A | 6 | 6 | 1 | 15.45 | 2.55 | 0
3746 | TORONTO BUTTONVILLE A | 6 | 5 | 2 | 18.2 | 0 | 0.2
3746 | TORONTO BUTTONVILLE A | 6 | 6 | 2 | 15.325 | 2.675 | 0
3747 | TORONTO BUTTONVILLE A | 6 | 5 | 3 | 16.1 | 1.9 | 0
3747 | TORONTO BUTTONVILLE A | 6 | 6 | 3 | 15.075 | 2.925 | 0
3748 | TORONTO BUTTONVILLE A | 6 | 5 | 4 | 17.7 | 0.3 | 0
3748 | TORONTO BUTTONVILLE A | 6 | 6 | 4 | 15 | 3 | 0
3749 | TORONTO BUTTONVILLE A | 6 | 5 | 5 | 16.6 | 1.4 | 0
3749 | TORONTO BUTTONVILLE A | 6 | 6 | 5 | 14.975 | 3.025 | 0
3750 | TORONTO BUTTONVILLE A | 6 | 5 | 6 | 16.1 | 1.9 | 0
3750 | TORONTO BUTTONVILLE A | 6 | 6 | 6 | 14.825 | 3.175 | 0
3751 | TORONTO BUTTONVILLE A | 6 | 5 | 7 | 17.6 | 0.4 | 0
3751 | TORONTO BUTTONVILLE A | 6 | 6 | 7 | 15.1 | 2.9 | 0
3752 | TORONTO BUTTONVILLE A | 6 | 5 | 8 | 20.1 | 0 | 2.1
3752 | TORONTO BUTTONVILLE A | 6 | 6 | 8 | 15.8 | 2.2 | 0
3753 | TORONTO BUTTONVILLE A | 6 | 5 | 9 | 22.9 | 0 | 4.9
3753 | TORONTO BUTTONVILLE A | 6 | 6 | 9 | 16.55 | 1.45 | 0
3754 | TORONTO BUTTONVILLE A | 6 | 5 | 10 | 25.1 | 0 | 7.1
3754 | TORONTO BUTTONVILLE A | 6 | 6 | 10 | 18.35 | 0 | 0.35
3755 | TORONTO BUTTONVILLE A | 6 | 5 | 11 | 26.9 | 0 | 8.9
3755 | TORONTO BUTTONVILLE A | 6 | 6 | 11 | 19.1 | 0 | 1.1
3756 | TORONTO BUTTONVILLE A | 6 | 5 | 12 | 28 | 0 | 10
3756 | TORONTO BUTTONVILLE A | 6 | 6 | 12 | 19.875 | 0 | 1.875
3757 | TORONTO BUTTONVILLE A | 6 | 5 | 13 | 19.4 | 0 | 1.4
3757 | TORONTO BUTTONVILLE A | 6 | 6 | 13 | 20.475 | 0 | 2.475
3758 | TORONTO BUTTONVILLE A | 6 | 5 | 14 | 24 | 0 | 6
3758 | TORONTO BUTTONVILLE A | 6 | 6 | 14 | 20.725 | 0 | 2.725
3759 | TORONTO BUTTONVILLE A | 6 | 5 | 15 | 26.5 | 0 | 8.5
3759 | TORONTO BUTTONVILLE A | 6 | 6 | 15 | 21.175 | 0 | 3.175
3760 | TORONTO BUTTONVILLE A | 6 | 5 | 16 | 26.3 | 0 | 8.3
3760 | TORONTO BUTTONVILLE A | 6 | 6 | 16 | 21.05 | 0 | 3.05
3761 | TORONTO BUTTONVILLE A | 6 | 5 | 17 | 26.3 | 0 | 8.3
3761 | TORONTO BUTTONVILLE A | 6 | 6 | 17 | 21.175 | 0 | 3.175
3762 | TORONTO BUTTONVILLE A | 6 | 5 | 18 | 25.6 | 0 | 7.6
3762 | TORONTO BUTTONVILLE A | 6 | 6 | 18 | 20.475 | 0 | 2.475
3763 | TORONTO BUTTONVILLE A | 6 | 5 | 19 | 26.1 | 0 | 8.1
3763 | TORONTO BUTTONVILLE A | 6 | 6 | 19 | 20.025 | 0 | 2.025
3764 | TORONTO BUTTONVILLE A | 6 | 5 | 20 | 24.8 | 0 | 6.8
3764 | TORONTO BUTTONVILLE A | 6 | 6 | 20 | 19.05 | 0 | 1.05
3765 | TORONTO BUTTONVILLE A | 6 | 5 | 21 | 23.6 | 0 | 5.6
3765 | TORONTO BUTTONVILLE A | 6 | 6 | 21 | 18.175 | 0 | 0.175
3766 | TORONTO BUTTONVILLE A | 6 | 5 | 22 | 23 | 0 | 5
3766 | TORONTO BUTTONVILLE A | 6 | 6 | 22 | 17.2 | 0.8 | 0
3767 | TORONTO BUTTONVILLE A | 6 | 5 | 23 | 20.8 | 0 | 2.8
3767 | TORONTO BUTTONVILLE A | 6 | 6 | 23 | 16.675 | 1.325 | 0
3768 | TORONTO BUTTONVILLE A | 6 | 5 | 24 | 20.1 | 0 | 2.1
3768 | TORONTO BUTTONVILLE A | 6 | 6 | 24 | 15.575 | 2.425 | 0
3769 | TORONTO BUTTONVILLE A | 6 | 6 | 1 | 19.6 | 0 | 1.6
3769 | TORONTO BUTTONVILLE A | 6 | 7 | 1 | 14.9 | 3.1 | 0
3770 | TORONTO BUTTONVILLE A | 6 | 6 | 2 | 19.6 | 0 | 1.6
3770 | TORONTO BUTTONVILLE A | 6 | 7 | 2 | 13.95 | 4.05 | 0
3771 | TORONTO BUTTONVILLE A | 6 | 6 | 3 | 19 | 0 | 1
3771 | TORONTO BUTTONVILLE A | 6 | 7 | 3 | 13.575 | 4.425 | 0
3772 | TORONTO BUTTONVILLE A | 6 | 6 | 4 | 17.4 | 0.6 | 0
3772 | TORONTO BUTTONVILLE A | 6 | 7 | 4 | 13.375 | 4.625 | 0
3773 | TORONTO BUTTONVILLE A | 6 | 6 | 5 | 16.6 | 1.4 | 0
3773 | TORONTO BUTTONVILLE A | 6 | 7 | 5 | 13.125 | 4.875 | 0
3774 | TORONTO BUTTONVILLE A | 6 | 6 | 6 | 15.9 | 2.1 | 0
3774 | TORONTO BUTTONVILLE A | 6 | 7 | 6 | 13.325 | 4.675 | 0
3775 | TORONTO BUTTONVILLE A | 6 | 6 | 7 | 16.4 | 1.6 | 0
3775 | TORONTO BUTTONVILLE A | 6 | 7 | 7 | 14.7 | 3.3 | 0
3776 | TORONTO BUTTONVILLE A | 6 | 6 | 8 | 18.4 | 0 | 0.4
3776 | TORONTO BUTTONVILLE A | 6 | 7 | 8 | 16.825 | 1.175 | 0
3777 | TORONTO BUTTONVILLE A | 6 | 6 | 9 | 19.9 | 0 | 1.9
3777 | TORONTO BUTTONVILLE A | 6 | 7 | 9 | 18.2 | 0 | 0.2
3778 | TORONTO BUTTONVILLE A | 6 | 6 | 10 | 21 | 0 | 3
3778 | TORONTO BUTTONVILLE A | 6 | 7 | 10 | 19.725 | 0 | 1.725
3779 | TORONTO BUTTONVILLE A | 6 | 6 | 11 | 22 | 0 | 4
3779 | TORONTO BUTTONVILLE A | 6 | 7 | 11 | 21.15 | 0 | 3.15
3780 | TORONTO BUTTONVILLE A | 6 | 6 | 12 | 22.8 | 0 | 4.8
3780 | TORONTO BUTTONVILLE A | 6 | 7 | 12 | 22.5 | 0 | 4.5
3781 | TORONTO BUTTONVILLE A | 6 | 6 | 13 | 23.7 | 0 | 5.7
3781 | TORONTO BUTTONVILLE A | 6 | 7 | 13 | 23.2 | 0 | 5.2
3782 | TORONTO BUTTONVILLE A | 6 | 6 | 14 | 23.4 | 0 | 5.4
3782 | TORONTO BUTTONVILLE A | 6 | 7 | 14 | 24.45 | 0 | 6.45
3783 | TORONTO BUTTONVILLE A | 6 | 6 | 15 | 22.4 | 0 | 4.4
3783 | TORONTO BUTTONVILLE A | 6 | 7 | 15 | 24.6 | 0 | 6.6
3784 | TORONTO BUTTONVILLE A | 6 | 6 | 16 | 23 | 0 | 5
3784 | TORONTO BUTTONVILLE A | 6 | 7 | 16 | 24.65 | 0 | 6.65
3785 | TORONTO BUTTONVILLE A | 6 | 6 | 17 | 22 | 0 | 4
3785 | TORONTO BUTTONVILLE A | 6 | 7 | 17 | 24.725 | 0 | 6.725
3786 | TORONTO BUTTONVILLE A | 6 | 6 | 18 | 21.3 | 0 | 3.3
3786 | TORONTO BUTTONVILLE A | 6 | 7 | 18 | 24.8 | 0 | 6.8
3787 | TORONTO BUTTONVILLE A | 6 | 6 | 19 | 20.3 | 0 | 2.3
3787 | TORONTO BUTTONVILLE A | 6 | 7 | 19 | 24.575 | 0 | 6.575
3788 | TORONTO BUTTONVILLE A | 6 | 6 | 20 | 19 | 0 | 1
3788 | TORONTO BUTTONVILLE A | 6 | 7 | 20 | 23.5 | 0 | 5.5
3789 | TORONTO BUTTONVILLE A | 6 | 6 | 21 | 17.7 | 0.3 | 0
3789 | TORONTO BUTTONVILLE A | 6 | 7 | 21 | 21.725 | 0 | 3.725
3790 | TORONTO BUTTONVILLE A | 6 | 6 | 22 | 16.5 | 1.5 | 0
3790 | TORONTO BUTTONVILLE A | 6 | 7 | 22 | 20.35 | 0 | 2.35
3791 | TORONTO BUTTONVILLE A | 6 | 6 | 23 | 15.3 | 2.7 | 0
3791 | TORONTO BUTTONVILLE A | 6 | 7 | 23 | 19.125 | 0 | 1.125
3792 | TORONTO BUTTONVILLE A | 6 | 6 | 24 | 14.8 | 3.2 | 0
3792 | TORONTO BUTTONVILLE A | 6 | 7 | 24 | 18.075 | 0 | 0.075
3793 | TORONTO BUTTONVILLE A | 6 | 7 | 1 | 13.9 | 4.1 | 0
3793 | TORONTO BUTTONVILLE A | 6 | 8 | 1 | 17.2 | 0.8 | 0
3794 | TORONTO BUTTONVILLE A | 6 | 7 | 2 | 13.1 | 4.9 | 0
3794 | TORONTO BUTTONVILLE A | 6 | 8 | 2 | 16.6 | 1.4 | 0
3795 | TORONTO BUTTONVILLE A | 6 | 7 | 3 | 12.6 | 5.4 | 0
3795 | TORONTO BUTTONVILLE A | 6 | 8 | 3 | 15.95 | 2.05 | 0
3796 | TORONTO BUTTONVILLE A | 6 | 7 | 4 | 11.7 | 6.3 | 0
3796 | TORONTO BUTTONVILLE A | 6 | 8 | 4 | 15.375 | 2.625 | 0
3797 | TORONTO BUTTONVILLE A | 6 | 7 | 5 | 11.2 | 6.8 | 0
3797 | TORONTO BUTTONVILLE A | 6 | 8 | 5 | 15.1 | 2.9 | 0
3798 | TORONTO BUTTONVILLE A | 6 | 7 | 6 | 10.6 | 7.4 | 0
3798 | TORONTO BUTTONVILLE A | 6 | 8 | 6 | 15.075 | 2.925 | 0
3799 | TORONTO BUTTONVILLE A | 6 | 7 | 7 | 11.2 | 6.8 | 0
3799 | TORONTO BUTTONVILLE A | 6 | 8 | 7 | 16.275 | 1.725 | 0
3800 | TORONTO BUTTONVILLE A | 6 | 7 | 8 | 12 | 6 | 0
3800 | TORONTO BUTTONVILLE A | 6 | 8 | 8 | 18.3 | 0 | 0.3
3801 | TORONTO BUTTONVILLE A | 6 | 7 | 9 | 13.2 | 4.8 | 0
3801 | TORONTO BUTTONVILLE A | 6 | 8 | 9 | 19.6 | 0 | 1.6
3802 | TORONTO BUTTONVILLE A | 6 | 7 | 10 | 14.9 | 3.1 | 0
3802 | TORONTO BUTTONVILLE A | 6 | 8 | 10 | 20.6 | 0 | 2.6
3803 | TORONTO BUTTONVILLE A | 6 | 7 | 11 | 16.5 | 1.5 | 0
3803 | TORONTO BUTTONVILLE A | 6 | 8 | 11 | 21.525 | 0 | 3.525
3804 | TORONTO BUTTONVILLE A | 6 | 7 | 12 | 17.6 | 0.4 | 0
3804 | TORONTO BUTTONVILLE A | 6 | 8 | 12 | 21.9 | 0 | 3.9
3805 | TORONTO BUTTONVILLE A | 6 | 7 | 13 | 18 | 0 | 0
3805 | TORONTO BUTTONVILLE A | 6 | 8 | 13 | 22.575 | 0 | 4.575
3806 | TORONTO BUTTONVILLE A | 6 | 7 | 14 | 19 | 0 | 1
3806 | TORONTO BUTTONVILLE A | 6 | 8 | 14 | 22.625 | 0 | 4.625
3807 | TORONTO BUTTONVILLE A | 6 | 7 | 15 | 19 | 0 | 1
3807 | TORONTO BUTTONVILLE A | 6 | 8 | 15 | 23.325 | 0 | 5.325
3808 | TORONTO BUTTONVILLE A | 6 | 7 | 16 | 19.8 | 0 | 1.8
3808 | TORONTO BUTTONVILLE A | 6 | 8 | 16 | 23.675 | 0 | 5.675
3809 | TORONTO BUTTONVILLE A | 6 | 7 | 17 | 20 | 0 | 2
3809 | TORONTO BUTTONVILLE A | 6 | 8 | 17 | 23.475 | 0 | 5.475
3810 | TORONTO BUTTONVILLE A | 6 | 7 | 18 | 19.6 | 0 | 1.6
3810 | TORONTO BUTTONVILLE A | 6 | 8 | 18 | 23.6 | 0 | 5.6
3811 | TORONTO BUTTONVILLE A | 6 | 7 | 19 | 19.4 | 0 | 1.4
3811 | TORONTO BUTTONVILLE A | 6 | 8 | 19 | 23.15 | 0 | 5.15
3812 | TORONTO BUTTONVILLE A | 6 | 7 | 20 | 18 | 0 | 0
3812 | TORONTO BUTTONVILLE A | 6 | 8 | 20 | 22.45 | 0 | 4.45
3813 | TORONTO BUTTONVILLE A | 6 | 7 | 21 | 16.1 | 1.9 | 0
3813 | TORONTO BUTTONVILLE A | 6 | 8 | 21 | 20.95 | 0 | 2.95
3814 | TORONTO BUTTONVILLE A | 6 | 7 | 22 | 14.4 | 3.6 | 0
3814 | TORONTO BUTTONVILLE A | 6 | 8 | 22 | 19.65 | 0 | 1.65
3815 | TORONTO BUTTONVILLE A | 6 | 7 | 23 | 13.3 | 4.7 | 0
3815 | TORONTO BUTTONVILLE A | 6 | 8 | 23 | 18.45 | 0 | 0.45
3816 | TORONTO BUTTONVILLE A | 6 | 7 | 24 | 12.7 | 5.3 | 0
3816 | TORONTO BUTTONVILLE A | 6 | 8 | 24 | 17.55 | 0.45 | 0
3817 | TORONTO BUTTONVILLE A | 6 | 8 | 1 | 12 | 6 | 0
3817 | TORONTO BUTTONVILLE A | 6 | 9 | 1 | 16.45 | 1.55 | 0
3818 | TORONTO BUTTONVILLE A | 6 | 8 | 2 | 11.9 | 6.1 | 0
3818 | TORONTO BUTTONVILLE A | 6 | 9 | 2 | 16.025 | 1.975 | 0
3819 | TORONTO BUTTONVILLE A | 6 | 8 | 3 | 11.4 | 6.6 | 0
3819 | TORONTO BUTTONVILLE A | 6 | 9 | 3 | 15.625 | 2.375 | 0
3820 | TORONTO BUTTONVILLE A | 6 | 8 | 4 | 11.1 | 6.9 | 0
3820 | TORONTO BUTTONVILLE A | 6 | 9 | 4 | 14.5 | 3.5 | 0
3821 | TORONTO BUTTONVILLE A | 6 | 8 | 5 | 10.6 | 7.4 | 0
3821 | TORONTO BUTTONVILLE A | 6 | 9 | 5 | 14.8 | 3.2 | 0
3822 | TORONTO BUTTONVILLE A | 6 | 8 | 6 | 10.5 | 7.5 | 0
3822 | TORONTO BUTTONVILLE A | 6 | 9 | 6 | 15.425 | 2.575 | 0
3823 | TORONTO BUTTONVILLE A | 6 | 8 | 7 | 12.3 | 5.7 | 0
3823 | TORONTO BUTTONVILLE A | 6 | 9 | 7 | 17.075 | 0.925 | 0
3824 | TORONTO BUTTONVILLE A | 6 | 8 | 8 | 14.6 | 3.4 | 0
3824 | TORONTO BUTTONVILLE A | 6 | 9 | 8 | 18.95 | 0 | 0.95
3825 | TORONTO BUTTONVILLE A | 6 | 8 | 9 | 17 | 1 | 0
3825 | TORONTO BUTTONVILLE A | 6 | 9 | 9 | 20.525 | 0 | 2.525
3826 | TORONTO BUTTONVILLE A | 6 | 8 | 10 | 18.6 | 0 | 0.6
3826 | TORONTO BUTTONVILLE A | 6 | 9 | 10 | 22.425 | 0 | 4.425
3827 | TORONTO BUTTONVILLE A | 6 | 8 | 11 | 19.7 | 0 | 1.7
3827 | TORONTO BUTTONVILLE A | 6 | 9 | 11 | 23.475 | 0 | 5.475
3828 | TORONTO BUTTONVILLE A | 6 | 8 | 12 | 20.5 | 0 | 2.5
3828 | TORONTO BUTTONVILLE A | 6 | 9 | 12 | 24.4 | 0 | 6.4
3829 | TORONTO BUTTONVILLE A | 6 | 8 | 13 | 20.7 | 0 | 2.7
3829 | TORONTO BUTTONVILLE A | 6 | 9 | 13 | 24.525 | 0 | 6.525
3830 | TORONTO BUTTONVILLE A | 6 | 8 | 14 | 21.7 | 0 | 3.7
3830 | TORONTO BUTTONVILLE A | 6 | 9 | 14 | 24.825 | 0 | 6.825
3831 | TORONTO BUTTONVILLE A | 6 | 8 | 15 | 22.7 | 0 | 4.7
3831 | TORONTO BUTTONVILLE A | 6 | 9 | 15 | 23.425 | 0 | 5.425
3832 | TORONTO BUTTONVILLE A | 6 | 8 | 16 | 23 | 0 | 5
3832 | TORONTO BUTTONVILLE A | 6 | 9 | 16 | 24.225 | 0 | 6.225
3833 | TORONTO BUTTONVILLE A | 6 | 8 | 17 | 24 | 0 | 6
3833 | TORONTO BUTTONVILLE A | 6 | 9 | 17 | 24.925 | 0 | 6.925
3834 | TORONTO BUTTONVILLE A | 6 | 8 | 18 | 24.4 | 0 | 6.4
3834 | TORONTO BUTTONVILLE A | 6 | 9 | 18 | 24.5 | 0 | 6.5
3835 | TORONTO BUTTONVILLE A | 6 | 8 | 19 | 23.4 | 0 | 5.4
3835 | TORONTO BUTTONVILLE A | 6 | 9 | 19 | 23.8 | 0 | 5.8
3836 | TORONTO BUTTONVILLE A | 6 | 8 | 20 | 22 | 0 | 4
3836 | TORONTO BUTTONVILLE A | 6 | 9 | 20 | 23 | 0 | 5
3837 | TORONTO BUTTONVILLE A | 6 | 8 | 21 | 19.7 | 0 | 1.7
3837 | TORONTO BUTTONVILLE A | 6 | 9 | 21 | 22.2 | 0 | 4.2
3838 | TORONTO BUTTONVILLE A | 6 | 8 | 22 | 19 | 0 | 1
3838 | TORONTO BUTTONVILLE A | 6 | 9 | 22 | 20.45 | 0 | 2.45
3839 | TORONTO BUTTONVILLE A | 6 | 8 | 23 | 17.7 | 0.3 | 0
3839 | TORONTO BUTTONVILLE A | 6 | 9 | 23 | 19.45 | 0 | 1.45
3840 | TORONTO BUTTONVILLE A | 6 | 8 | 24 | 17.7 | 0.3 | 0
3840 | TORONTO BUTTONVILLE A | 6 | 9 | 24 | 18.425 | 0 | 0.425
3841 | TORONTO BUTTONVILLE A | 6 | 9 | 1 | 16.8 | 1.2 | 0
3841 | TORONTO BUTTONVILLE A | 6 | 10 | 1 | 18.275 | 0 | 0.275
3842 | TORONTO BUTTONVILLE A | 6 | 9 | 2 | 16.7 | 1.3 | 0
3842 | TORONTO BUTTONVILLE A | 6 | 10 | 2 | 17.65 | 0.35 | 0
3843 | TORONTO BUTTONVILLE A | 6 | 9 | 3 | 15.5 | 2.5 | 0
3843 | TORONTO BUTTONVILLE A | 6 | 10 | 3 | 17.625 | 0.375 | 0
3844 | TORONTO BUTTONVILLE A | 6 | 9 | 4 | 14.9 | 3.1 | 0
3844 | TORONTO BUTTONVILLE A | 6 | 10 | 4 | 17.1 | 0.9 | 0
3845 | TORONTO BUTTONVILLE A | 6 | 9 | 5 | 15.6 | 2.4 | 0
3845 | TORONTO BUTTONVILLE A | 6 | 10 | 5 | 16.125 | 1.875 | 0
3846 | TORONTO BUTTONVILLE A | 6 | 9 | 6 | 14.6 | 3.4 | 0
3846 | TORONTO BUTTONVILLE A | 6 | 10 | 6 | 15.775 | 2.225 | 0
3847 | TORONTO BUTTONVILLE A | 6 | 9 | 7 | 16.5 | 1.5 | 0
3847 | TORONTO BUTTONVILLE A | 6 | 10 | 7 | 16.275 | 1.725 | 0
3848 | TORONTO BUTTONVILLE A | 6 | 9 | 8 | 19.1 | 0 | 1.1
3848 | TORONTO BUTTONVILLE A | 6 | 10 | 8 | 17.325 | 0.675 | 0
3849 | TORONTO BUTTONVILLE A | 6 | 9 | 9 | 22.6 | 0 | 4.6
3849 | TORONTO BUTTONVILLE A | 6 | 10 | 9 | 18.8 | 0 | 0.8
3850 | TORONTO BUTTONVILLE A | 6 | 9 | 10 | 24.9 | 0 | 6.9
3850 | TORONTO BUTTONVILLE A | 6 | 10 | 10 | 19.825 | 0 | 1.825
3851 | TORONTO BUTTONVILLE A | 6 | 9 | 11 | 27.9 | 0 | 9.9
3851 | TORONTO BUTTONVILLE A | 6 | 10 | 11 | 20.6 | 0 | 2.6
3852 | TORONTO BUTTONVILLE A | 6 | 9 | 12 | 29.9 | 0 | 11.9
3852 | TORONTO BUTTONVILLE A | 6 | 10 | 12 | 21.15 | 0 | 3.15
3853 | TORONTO BUTTONVILLE A | 6 | 9 | 13 | 31 | 0 | 13
3853 | TORONTO BUTTONVILLE A | 6 | 10 | 13 | 21.2 | 0 | 3.2
3854 | TORONTO BUTTONVILLE A | 6 | 9 | 14 | 31.4 | 0 | 13.4
3854 | TORONTO BUTTONVILLE A | 6 | 10 | 14 | 21.925 | 0 | 3.925
3855 | TORONTO BUTTONVILLE A | 6 | 9 | 15 | 32.5 | 0 | 14.5
3855 | TORONTO BUTTONVILLE A | 6 | 10 | 15 | 22.35 | 0 | 4.35
3856 | TORONTO BUTTONVILLE A | 6 | 9 | 16 | 32.7 | 0 | 14.7
3856 | TORONTO BUTTONVILLE A | 6 | 10 | 16 | 22.65 | 0 | 4.65
3857 | TORONTO BUTTONVILLE A | 6 | 9 | 17 | 31.4 | 0 | 13.4
3857 | TORONTO BUTTONVILLE A | 6 | 10 | 17 | 21.6 | 0 | 3.6
3858 | TORONTO BUTTONVILLE A | 6 | 9 | 18 | 30.6 | 0 | 12.6
3858 | TORONTO BUTTONVILLE A | 6 | 10 | 18 | 21.925 | 0 | 3.925
3859 | TORONTO BUTTONVILLE A | 6 | 9 | 19 | 29.5 | 0 | 11.5
3859 | TORONTO BUTTONVILLE A | 6 | 10 | 19 | 21.525 | 0 | 3.525
3860 | TORONTO BUTTONVILLE A | 6 | 9 | 20 | 28.6 | 0 | 10.6
3860 | TORONTO BUTTONVILLE A | 6 | 10 | 20 | 20.775 | 0 | 2.775
3861 | TORONTO BUTTONVILLE A | 6 | 9 | 21 | 25.7 | 0 | 7.7
3861 | TORONTO BUTTONVILLE A | 6 | 10 | 21 | 19.45 | 0 | 1.45
3862 | TORONTO BUTTONVILLE A | 6 | 9 | 22 | 24.3 | 0 | 6.3
3862 | TORONTO BUTTONVILLE A | 6 | 10 | 22 | 18.65 | 0 | 0.65
3863 | TORONTO BUTTONVILLE A | 6 | 9 | 23 | 20.7 | 0 | 2.7
3863 | TORONTO BUTTONVILLE A | 6 | 10 | 23 | 17.975 | 0.025 | 0
3864 | TORONTO BUTTONVILLE A | 6 | 9 | 24 | 19.8 | 0 | 1.8
3864 | TORONTO BUTTONVILLE A | 6 | 10 | 24 | 17.15 | 0.85 | 0
3865 | TORONTO BUTTONVILLE A | 6 | 10 | 1 | 20.2 | 0 | 2.2
3865 | TORONTO BUTTONVILLE A | 6 | 11 | 1 | 16.575 | 1.425 | 0
3866 | TORONTO BUTTONVILLE A | 6 | 10 | 2 | 20.1 | 0 | 2.1
3866 | TORONTO BUTTONVILLE A | 6 | 11 | 2 | 16.125 | 1.875 | 0
3867 | TORONTO BUTTONVILLE A | 6 | 10 | 3 | 20.4 | 0 | 2.4
3867 | TORONTO BUTTONVILLE A | 6 | 11 | 3 | 15.875 | 2.125 | 0
3868 | TORONTO BUTTONVILLE A | 6 | 10 | 4 | 20.3 | 0 | 2.3
3868 | TORONTO BUTTONVILLE A | 6 | 11 | 4 | 15.85 | 2.15 | 0
3869 | TORONTO BUTTONVILLE A | 6 | 10 | 5 | 20.3 | 0 | 2.3
3869 | TORONTO BUTTONVILLE A | 6 | 11 | 5 | 15.575 | 2.425 | 0
3870 | TORONTO BUTTONVILLE A | 6 | 10 | 6 | 18.5 | 0 | 0.5
3870 | TORONTO BUTTONVILLE A | 6 | 11 | 6 | 15.25 | 2.75 | 0
3871 | TORONTO BUTTONVILLE A | 6 | 10 | 7 | 17.6 | 0.4 | 0
3871 | TORONTO BUTTONVILLE A | 6 | 11 | 7 | 16.05 | 1.95 | 0
3872 | TORONTO BUTTONVILLE A | 6 | 10 | 8 | 18.1 | 0 | 0.1
3872 | TORONTO BUTTONVILLE A | 6 | 11 | 8 | 17.75 | 0.25 | 0
3873 | TORONTO BUTTONVILLE A | 6 | 10 | 9 | 19.4 | 0 | 1.4
3873 | TORONTO BUTTONVILLE A | 6 | 11 | 9 | 19.475 | 0 | 1.475
3874 | TORONTO BUTTONVILLE A | 6 | 10 | 10 | 22.3 | 0 | 4.3
3874 | TORONTO BUTTONVILLE A | 6 | 11 | 10 | 20.875 | 0 | 2.875
3875 | TORONTO BUTTONVILLE A | 6 | 10 | 11 | 25.4 | 0 | 7.4
3875 | TORONTO BUTTONVILLE A | 6 | 11 | 11 | 22.275 | 0 | 4.275
3876 | TORONTO BUTTONVILLE A | 6 | 10 | 12 | 27.3 | 0 | 9.3
3876 | TORONTO BUTTONVILLE A | 6 | 11 | 12 | 22.9 | 0 | 4.9
3877 | TORONTO BUTTONVILLE A | 6 | 10 | 13 | 28.5 | 0 | 10.5
3877 | TORONTO BUTTONVILLE A | 6 | 11 | 13 | 23.7 | 0 | 5.7
3878 | TORONTO BUTTONVILLE A | 6 | 10 | 14 | 29.2 | 0 | 11.2
3878 | TORONTO BUTTONVILLE A | 6 | 11 | 14 | 24.075 | 0 | 6.075
3879 | TORONTO BUTTONVILLE A | 6 | 10 | 15 | 30.6 | 0 | 12.6
3879 | TORONTO BUTTONVILLE A | 6 | 11 | 15 | 24.675 | 0 | 6.675
3880 | TORONTO BUTTONVILLE A | 6 | 10 | 16 | 30.6 | 0 | 12.6
3880 | TORONTO BUTTONVILLE A | 6 | 11 | 16 | 24.675 | 0 | 6.675
3881 | TORONTO BUTTONVILLE A | 6 | 10 | 17 | 30.8 | 0 | 12.8
3881 | TORONTO BUTTONVILLE A | 6 | 11 | 17 | 23.95 | 0 | 5.95
3882 | TORONTO BUTTONVILLE A | 6 | 10 | 18 | 30.7 | 0 | 12.7
3882 | TORONTO BUTTONVILLE A | 6 | 11 | 18 | 23.675 | 0 | 5.675
3883 | TORONTO BUTTONVILLE A | 6 | 10 | 19 | 29.8 | 0 | 11.8
3883 | TORONTO BUTTONVILLE A | 6 | 11 | 19 | 23.15 | 0 | 5.15
3884 | TORONTO BUTTONVILLE A | 6 | 10 | 20 | 29.7 | 0 | 11.7
3884 | TORONTO BUTTONVILLE A | 6 | 11 | 20 | 22.275 | 0 | 4.275
3885 | TORONTO BUTTONVILLE A | 6 | 10 | 21 | 21.1 | 0 | 3.1
3885 | TORONTO BUTTONVILLE A | 6 | 11 | 21 | 20.7 | 0 | 2.7
3886 | TORONTO BUTTONVILLE A | 6 | 10 | 22 | 20.1 | 0 | 2.1
3886 | TORONTO BUTTONVILLE A | 6 | 11 | 22 | 19.6 | 0 | 1.6
3887 | TORONTO BUTTONVILLE A | 6 | 10 | 23 | 19.4 | 0 | 1.4
3887 | TORONTO BUTTONVILLE A | 6 | 11 | 23 | 18.225 | 0 | 0.225
3888 | TORONTO BUTTONVILLE A | 6 | 10 | 24 | NaN | 0.3375 | 0
3888 | TORONTO BUTTONVILLE A | 6 | 11 | 24 | 17.1 | 0.9 | 0
3889 | TORONTO BUTTONVILLE A | 6 | 11 | 1 | 18.9 | 0 | 0.9
3889 | TORONTO BUTTONVILLE A | 6 | 12 | 1 | 16.275 | 1.725 | 0
3890 | TORONTO BUTTONVILLE A | 6 | 11 | 2 | 18.4 | 0 | 0.4
3890 | TORONTO BUTTONVILLE A | 6 | 12 | 2 | 15.2 | 2.8 | 0
3891 | TORONTO BUTTONVILLE A | 6 | 11 | 3 | 19 | 0 | 1
3891 | TORONTO BUTTONVILLE A | 6 | 12 | 3 | 14.625 | 3.375 | 0
3892 | TORONTO BUTTONVILLE A | 6 | 11 | 4 | 18.7 | 0 | 0.7
3892 | TORONTO BUTTONVILLE A | 6 | 12 | 4 | 14.4 | 3.6 | 0
3893 | TORONTO BUTTONVILLE A | 6 | 11 | 5 | 18.6 | 0 | 0.6
3893 | TORONTO BUTTONVILLE A | 6 | 12 | 5 | 14.15 | 3.85 | 0
3894 | TORONTO BUTTONVILLE A | 6 | 11 | 6 | 18.8 | 0 | 0.8
3894 | TORONTO BUTTONVILLE A | 6 | 12 | 6 | 14.025 | 3.975 | 0
3895 | TORONTO BUTTONVILLE A | 6 | 11 | 7 | 17.5 | 0.5 | 0
3895 | TORONTO BUTTONVILLE A | 6 | 12 | 7 | 15.725 | 2.275 | 0
3896 | TORONTO BUTTONVILLE A | 6 | 11 | 8 | 16.5 | 1.5 | 0
3896 | TORONTO BUTTONVILLE A | 6 | 12 | 8 | 18.025 | 0 | 0.025
3897 | TORONTO BUTTONVILLE A | 6 | 11 | 9 | 16.5 | 1.5 | 0
3897 | TORONTO BUTTONVILLE A | 6 | 12 | 9 | 20.325 | 0 | 2.325
3898 | TORONTO BUTTONVILLE A | 6 | 11 | 10 | 17 | 1 | 0
3898 | TORONTO BUTTONVILLE A | 6 | 12 | 10 | 21.875 | 0 | 3.875
3899 | TORONTO BUTTONVILLE A | 6 | 11 | 11 | 19.1 | 0 | 1.1
3899 | TORONTO BUTTONVILLE A | 6 | 12 | 11 | 23.375 | 0 | 5.375
3900 | TORONTO BUTTONVILLE A | 6 | 11 | 12 | 19.5 | 0 | 1.5
3900 | TORONTO BUTTONVILLE A | 6 | 12 | 12 | 24.075 | 0 | 6.075
3901 | TORONTO BUTTONVILLE A | 6 | 11 | 13 | 20.3 | 0 | 2.3
3901 | TORONTO BUTTONVILLE A | 6 | 12 | 13 | 24.6 | 0 | 6.6
3902 | TORONTO BUTTONVILLE A | 6 | 11 | 14 | 20.8 | 0 | 2.8
3902 | TORONTO BUTTONVILLE A | 6 | 12 | 14 | 25.15 | 0 | 7.15
3903 | TORONTO BUTTONVILLE A | 6 | 11 | 15 | 22.8 | 0 | 4.8
3903 | TORONTO BUTTONVILLE A | 6 | 12 | 15 | 25.525 | 0 | 7.525
3904 | TORONTO BUTTONVILLE A | 6 | 11 | 16 | 22.9 | 0 | 4.9
3904 | TORONTO BUTTONVILLE A | 6 | 12 | 16 | 25.975 | 0 | 7.975
3905 | TORONTO BUTTONVILLE A | 6 | 11 | 17 | 22.6 | 0 | 4.6
3905 | TORONTO BUTTONVILLE A | 6 | 12 | 17 | 26.05 | 0 | 8.05
3906 | TORONTO BUTTONVILLE A | 6 | 11 | 18 | 22.5 | 0 | 4.5
3906 | TORONTO BUTTONVILLE A | 6 | 12 | 18 | 25.7 | 0 | 7.7
3907 | TORONTO BUTTONVILLE A | 6 | 11 | 19 | 21.9 | 0 | 3.9
3907 | TORONTO BUTTONVILLE A | 6 | 12 | 19 | 25.1 | 0 | 7.1
3908 | TORONTO BUTTONVILLE A | 6 | 11 | 20 | 21.6 | 0 | 3.6
3908 | TORONTO BUTTONVILLE A | 6 | 12 | 20 | 24.05 | 0 | 6.05
3909 | TORONTO BUTTONVILLE A | 6 | 11 | 21 | 20.9 | 0 | 2.9
3909 | TORONTO BUTTONVILLE A | 6 | 12 | 21 | 23.05 | 0 | 5.05
3910 | TORONTO BUTTONVILLE A | 6 | 11 | 22 | 20 | 0 | 2
3910 | TORONTO BUTTONVILLE A | 6 | 12 | 22 | 22.3 | 0 | 4.3
3911 | TORONTO BUTTONVILLE A | 6 | 11 | 23 | 19.3 | 0 | 1.3
3911 | TORONTO BUTTONVILLE A | 6 | 12 | 23 | 21.8 | 0 | 3.8
3912 | TORONTO BUTTONVILLE A | 6 | 11 | 24 | 19 | 0 | 1
3912 | TORONTO BUTTONVILLE A | 6 | 12 | 24 | 21.35 | 0 | 3.35
3913 | TORONTO BUTTONVILLE A | 6 | 12 | 1 | 18.5 | 0 | 0.5
3913 | TORONTO BUTTONVILLE A | 6 | 13 | 1 | 20.9 | 0 | 2.9
3914 | TORONTO BUTTONVILLE A | 6 | 12 | 2 | 17.8 | 0.2 | 0
3914 | TORONTO BUTTONVILLE A | 6 | 13 | 2 | 20.1 | 0 | 2.1
3915 | TORONTO BUTTONVILLE A | 6 | 12 | 3 | 16.4 | 1.6 | 0
3915 | TORONTO BUTTONVILLE A | 6 | 13 | 3 | 19.65 | 0 | 1.65
3916 | TORONTO BUTTONVILLE A | 6 | 12 | 4 | 14.9 | 3.1 | 0
3916 | TORONTO BUTTONVILLE A | 6 | 13 | 4 | 19.7 | 0 | 1.7
3917 | TORONTO BUTTONVILLE A | 6 | 12 | 5 | 13.8 | 4.2 | 0
3917 | TORONTO BUTTONVILLE A | 6 | 13 | 5 | 19.325 | 0 | 1.325
3918 | TORONTO BUTTONVILLE A | 6 | 12 | 6 | 12.8 | 5.2 | 0
3918 | TORONTO BUTTONVILLE A | 6 | 13 | 6 | 17.65 | 0.35 | 0
3919 | TORONTO BUTTONVILLE A | 6 | 12 | 7 | 12 | 6 | 0
3919 | TORONTO BUTTONVILLE A | 6 | 13 | 7 | 17.575 | 0.425 | 0
3920 | TORONTO BUTTONVILLE A | 6 | 12 | 8 | 12.2 | 5.8 | 0
3920 | TORONTO BUTTONVILLE A | 6 | 13 | 8 | 17.9 | 0.1 | 0
3921 | TORONTO BUTTONVILLE A | 6 | 12 | 9 | 12 | 6 | 0
3921 | TORONTO BUTTONVILLE A | 6 | 13 | 9 | 18.675 | 0 | 0.675
3922 | TORONTO BUTTONVILLE A | 6 | 12 | 10 | 12.5 | 5.5 | 0
3922 | TORONTO BUTTONVILLE A | 6 | 13 | 10 | 19.525 | 0 | 1.525
3923 | TORONTO BUTTONVILLE A | 6 | 12 | 11 | 14.1 | 3.9 | 0
3923 | TORONTO BUTTONVILLE A | 6 | 13 | 11 | 20.225 | 0 | 2.225
3924 | TORONTO BUTTONVILLE A | 6 | 12 | 12 | 14.7 | 3.3 | 0
3924 | TORONTO BUTTONVILLE A | 6 | 13 | 12 | 20.775 | 0 | 2.775
3925 | TORONTO BUTTONVILLE A | 6 | 12 | 13 | 16 | 2 | 0
3925 | TORONTO BUTTONVILLE A | 6 | 13 | 13 | 21.4 | 0 | 3.4
3926 | TORONTO BUTTONVILLE A | 6 | 12 | 14 | 17.3 | 0.7 | 0
3926 | TORONTO BUTTONVILLE A | 6 | 13 | 14 | 21.225 | 0 | 3.225
3927 | TORONTO BUTTONVILLE A | 6 | 12 | 15 | 17 | 1 | 0
3927 | TORONTO BUTTONVILLE A | 6 | 13 | 15 | 21.55 | 0 | 3.55
3928 | TORONTO BUTTONVILLE A | 6 | 12 | 16 | 17 | 1 | 0
3928 | TORONTO BUTTONVILLE A | 6 | 13 | 16 | 22.025 | 0 | 4.025
3929 | TORONTO BUTTONVILLE A | 6 | 12 | 17 | 16 | 2 | 0
3929 | TORONTO BUTTONVILLE A | 6 | 13 | 17 | 20.55 | 0 | 2.55
3930 | TORONTO BUTTONVILLE A | 6 | 12 | 18 | 15.2 | 2.8 | 0
3930 | TORONTO BUTTONVILLE A | 6 | 13 | 18 | 21.075 | 0 | 3.075
3931 | TORONTO BUTTONVILLE A | 6 | 12 | 19 | 15.5 | 2.5 | 0
3931 | TORONTO BUTTONVILLE A | 6 | 13 | 19 | 20.975 | 0 | 2.975
3932 | TORONTO BUTTONVILLE A | 6 | 12 | 20 | 14.3 | 3.7 | 0
3932 | TORONTO BUTTONVILLE A | 6 | 13 | 20 | 20.575 | 0 | 2.575
3933 | TORONTO BUTTONVILLE A | 6 | 12 | 21 | 12.6 | 5.4 | 0
3933 | TORONTO BUTTONVILLE A | 6 | 13 | 21 | 19.3 | 0 | 1.3
3934 | TORONTO BUTTONVILLE A | 6 | 12 | 22 | 11.3 | 6.7 | 0
3934 | TORONTO BUTTONVILLE A | 6 | 13 | 22 | 17.95 | 0.05 | 0
3935 | TORONTO BUTTONVILLE A | 6 | 12 | 23 | 10.6 | 7.4 | 0
3935 | TORONTO BUTTONVILLE A | 6 | 13 | 23 | 17.075 | 0.925 | 0
3936 | TORONTO BUTTONVILLE A | 6 | 12 | 24 | 9.9 | 8.1 | 0
3936 | TORONTO BUTTONVILLE A | 6 | 13 | 24 | 16.625 | 1.375 | 0
3937 | TORONTO BUTTONVILLE A | 6 | 13 | 1 | 8.9 | 9.1 | 0
3937 | TORONTO BUTTONVILLE A | 6 | 14 | 1 | 16.3 | 1.7 | 0
3938 | TORONTO BUTTONVILLE A | 6 | 13 | 2 | 8.7 | 9.3 | 0
3938 | TORONTO BUTTONVILLE A | 6 | 14 | 2 | 15.625 | 2.375 | 0
3939 | TORONTO BUTTONVILLE A | 6 | 13 | 3 | 8.5 | 9.5 | 0
3939 | TORONTO BUTTONVILLE A | 6 | 14 | 3 | 15.15 | 2.85 | 0
3940 | TORONTO BUTTONVILLE A | 6 | 13 | 4 | 8.5 | 9.5 | 0
3940 | TORONTO BUTTONVILLE A | 6 | 14 | 4 | 14.75 | 3.25 | 0
3941 | TORONTO BUTTONVILLE A | 6 | 13 | 5 | 8.7 | 9.3 | 0
3941 | TORONTO BUTTONVILLE A | 6 | 14 | 5 | 14.5 | 3.5 | 0
3942 | TORONTO BUTTONVILLE A | 6 | 13 | 6 | 9 | 9 | 0
3942 | TORONTO BUTTONVILLE A | 6 | 14 | 6 | 14.75 | 3.25 | 0
3943 | TORONTO BUTTONVILLE A | 6 | 13 | 7 | 9.6 | 8.4 | 0
3943 | TORONTO BUTTONVILLE A | 6 | 14 | 7 | 15.6 | 2.4 | 0
3944 | TORONTO BUTTONVILLE A | 6 | 13 | 8 | 10.4 | 7.6 | 0
3944 | TORONTO BUTTONVILLE A | 6 | 14 | 8 | 16.15 | 1.85 | 0
3945 | TORONTO BUTTONVILLE A | 6 | 13 | 9 | 11.8 | 6.2 | 0
3945 | TORONTO BUTTONVILLE A | 6 | 14 | 9 | 16.775 | 1.225 | 0
3946 | TORONTO BUTTONVILLE A | 6 | 13 | 10 | 13.3 | 4.7 | 0
3946 | TORONTO BUTTONVILLE A | 6 | 14 | 10 | 18.3667 | 0 | 0.36667
3947 | TORONTO BUTTONVILLE A | 6 | 13 | 11 | 14.2 | 3.8 | 0
3947 | TORONTO BUTTONVILLE A | 6 | 14 | 11 | 18.6 | 0 | 0.6
3948 | TORONTO BUTTONVILLE A | 6 | 13 | 12 | 14.7 | 3.3 | 0
3948 | TORONTO BUTTONVILLE A | 6 | 14 | 12 | 19.675 | 0 | 1.675
3949 | TORONTO BUTTONVILLE A | 6 | 13 | 13 | 16 | 2 | 0
3949 | TORONTO BUTTONVILLE A | 6 | 14 | 13 | 20.675 | 0 | 2.675
3950 | TORONTO BUTTONVILLE A | 6 | 13 | 14 | 16.4 | 1.6 | 0
3950 | TORONTO BUTTONVILLE A | 6 | 14 | 14 | 21.45 | 0 | 3.45
3951 | TORONTO BUTTONVILLE A | 6 | 13 | 15 | 16.9 | 1.1 | 0
3951 | TORONTO BUTTONVILLE A | 6 | 14 | 15 | 21.225 | 0 | 3.225
3952 | TORONTO BUTTONVILLE A | 6 | 13 | 16 | 17.4 | 0.6 | 0
3952 | TORONTO BUTTONVILLE A | 6 | 14 | 16 | 22.2 | 0 | 4.2
3953 | TORONTO BUTTONVILLE A | 6 | 13 | 17 | 18.8 | 0 | 0.8
3953 | TORONTO BUTTONVILLE A | 6 | 14 | 17 | 22.55 | 0 | 4.55
3954 | TORONTO BUTTONVILLE A | 6 | 13 | 18 | 18.4 | 0 | 0.4
3954 | TORONTO BUTTONVILLE A | 6 | 14 | 18 | 21.775 | 0 | 3.775
3955 | TORONTO BUTTONVILLE A | 6 | 13 | 19 | 17 | 1 | 0
3955 | TORONTO BUTTONVILLE A | 6 | 14 | 19 | 20.575 | 0 | 2.575
3956 | TORONTO BUTTONVILLE A | 6 | 13 | 20 | 15.2 | 2.8 | 0
3956 | TORONTO BUTTONVILLE A | 6 | 14 | 20 | 19.475 | 0 | 1.475
3957 | TORONTO BUTTONVILLE A | 6 | 13 | 21 | 14 | 4 | 0
3957 | TORONTO BUTTONVILLE A | 6 | 14 | 21 | 18.175 | 0 | 0.175
3958 | TORONTO BUTTONVILLE A | 6 | 13 | 22 | 12.4 | 5.6 | 0
3958 | TORONTO BUTTONVILLE A | 6 | 14 | 22 | 17.525 | 0.475 | 0
3959 | TORONTO BUTTONVILLE A | 6 | 13 | 23 | 11.3 | 6.7 | 0
3959 | TORONTO BUTTONVILLE A | 6 | 14 | 23 | 16.75 | 1.25 | 0
3960 | TORONTO BUTTONVILLE A | 6 | 13 | 24 | 10.6 | 7.4 | 0
3960 | TORONTO BUTTONVILLE A | 6 | 14 | 24 | 16.325 | 1.675 | 0
3961 | TORONTO BUTTONVILLE A | 6 | 14 | 1 | 9.2 | 8.8 | 0
3961 | TORONTO BUTTONVILLE A | 6 | 15 | 1 | 15.875 | 2.125 | 0
3962 | TORONTO BUTTONVILLE A | 6 | 14 | 2 | 8.2 | 9.8 | 0
3962 | TORONTO BUTTONVILLE A | 6 | 15 | 2 | 15.1 | 2.9 | 0
3963 | TORONTO BUTTONVILLE A | 6 | 14 | 3 | 7.8 | 10.2 | 0
3963 | TORONTO BUTTONVILLE A | 6 | 15 | 3 | 14.825 | 3.175 | 0
3964 | TORONTO BUTTONVILLE A | 6 | 14 | 4 | 7.2 | 10.8 | 0
3964 | TORONTO BUTTONVILLE A | 6 | 15 | 4 | 15.075 | 2.925 | 0
3965 | TORONTO BUTTONVILLE A | 6 | 14 | 5 | 7.1 | 10.9 | 0
3965 | TORONTO BUTTONVILLE A | 6 | 15 | 5 | 14.875 | 3.125 | 0
3966 | TORONTO BUTTONVILLE A | 6 | 14 | 6 | 7.2 | 10.8 | 0
3966 | TORONTO BUTTONVILLE A | 6 | 15 | 6 | 14.85 | 3.15 | 0
3967 | TORONTO BUTTONVILLE A | 6 | 14 | 7 | 9.6 | 8.4 | 0
3967 | TORONTO BUTTONVILLE A | 6 | 15 | 7 | 15.9 | 2.1 | 0
3968 | TORONTO BUTTONVILLE A | 6 | 14 | 8 | 12.6 | 5.4 | 0
3968 | TORONTO BUTTONVILLE A | 6 | 15 | 8 | 16.9 | 1.1 | 0
3969 | TORONTO BUTTONVILLE A | 6 | 14 | 9 | 14 | 4 | 0
3969 | TORONTO BUTTONVILLE A | 6 | 15 | 9 | 18.25 | 0 | 0.25
3970 | TORONTO BUTTONVILLE A | 6 | 14 | 10 | 15.2 | 2.8 | 0
3970 | TORONTO BUTTONVILLE A | 6 | 15 | 10 | 19.525 | 0 | 1.525
3971 | TORONTO BUTTONVILLE A | 6 | 14 | 11 | 15.7 | 2.3 | 0
3971 | TORONTO BUTTONVILLE A | 6 | 15 | 11 | 19.85 | 0 | 1.85
3972 | TORONTO BUTTONVILLE A | 6 | 14 | 12 | 16.3 | 1.7 | 0
3972 | TORONTO BUTTONVILLE A | 6 | 15 | 12 | 20.1 | 0 | 2.1
3973 | TORONTO BUTTONVILLE A | 6 | 14 | 13 | 17.7 | 0.3 | 0
3973 | TORONTO BUTTONVILLE A | 6 | 15 | 13 | 20.75 | 0 | 2.75
3974 | TORONTO BUTTONVILLE A | 6 | 14 | 14 | 17.1 | 0.9 | 0
3974 | TORONTO BUTTONVILLE A | 6 | 15 | 14 | 20.1 | 0 | 2.1
3975 | TORONTO BUTTONVILLE A | 6 | 14 | 15 | 17.8 | 0.2 | 0
3975 | TORONTO BUTTONVILLE A | 6 | 15 | 15 | 20.4 | 0 | 2.4
3976 | TORONTO BUTTONVILLE A | 6 | 14 | 16 | 17.4 | 0.6 | 0
3976 | TORONTO BUTTONVILLE A | 6 | 15 | 16 | 20.325 | 0 | 2.325
3977 | TORONTO BUTTONVILLE A | 6 | 14 | 17 | 17.6 | 0.4 | 0
3977 | TORONTO BUTTONVILLE A | 6 | 15 | 17 | 20.325 | 0 | 2.325
3978 | TORONTO BUTTONVILLE A | 6 | 14 | 18 | 17.4 | 0.6 | 0
3978 | TORONTO BUTTONVILLE A | 6 | 15 | 18 | 20.175 | 0 | 2.175
3979 | TORONTO BUTTONVILLE A | 6 | 14 | 19 | 17 | 1 | 0
3979 | TORONTO BUTTONVILLE A | 6 | 15 | 19 | 19.075 | 0 | 1.075
3980 | TORONTO BUTTONVILLE A | 6 | 14 | 20 | 16.4 | 1.6 | 0
3980 | TORONTO BUTTONVILLE A | 6 | 15 | 20 | 18.55 | 0 | 0.55
3981 | TORONTO BUTTONVILLE A | 6 | 14 | 21 | 15.2 | 2.8 | 0
3981 | TORONTO BUTTONVILLE A | 6 | 15 | 21 | 17.475 | 0.525 | 0
3982 | TORONTO BUTTONVILLE A | 6 | 14 | 22 | 14.4 | 3.6 | 0
3982 | TORONTO BUTTONVILLE A | 6 | 15 | 22 | 16.675 | 1.325 | 0
3983 | TORONTO BUTTONVILLE A | 6 | 14 | 23 | 12.7 | 5.3 | 0
3983 | TORONTO BUTTONVILLE A | 6 | 15 | 23 | 16.25 | 1.75 | 0
3984 | TORONTO BUTTONVILLE A | 6 | 14 | 24 | 11.2 | 6.8 | 0
3984 | TORONTO BUTTONVILLE A | 6 | 15 | 24 | 15.4 | 2.6 | 0
3985 | TORONTO BUTTONVILLE A | 6 | 15 | 1 | 11.3 | 6.7 | 0
3985 | TORONTO BUTTONVILLE A | 6 | 16 | 1 | 14.775 | 3.225 | 0
3986 | TORONTO BUTTONVILLE A | 6 | 15 | 2 | 10.2 | 7.8 | 0
3986 | TORONTO BUTTONVILLE A | 6 | 16 | 2 | 14.25 | 3.75 | 0
3987 | TORONTO BUTTONVILLE A | 6 | 15 | 3 | 10.2 | 7.8 | 0
3987 | TORONTO BUTTONVILLE A | 6 | 16 | 3 | 13.85 | 4.15 | 0
3988 | TORONTO BUTTONVILLE A | 6 | 15 | 4 | 9.5 | 8.5 | 0
3988 | TORONTO BUTTONVILLE A | 6 | 16 | 4 | 12.825 | 5.175 | 0
3989 | TORONTO BUTTONVILLE A | 6 | 15 | 5 | 9.2 | 8.8 | 0
3989 | TORONTO BUTTONVILLE A | 6 | 16 | 5 | 12.5 | 5.5 | 0
3990 | TORONTO BUTTONVILLE A | 6 | 15 | 6 | 9.1 | 8.9 | 0
3990 | TORONTO BUTTONVILLE A | 6 | 16 | 6 | 12.55 | 5.45 | 0
3991 | TORONTO BUTTONVILLE A | 6 | 15 | 7 | 11.6 | 6.4 | 0
3991 | TORONTO BUTTONVILLE A | 6 | 16 | 7 | 13.8 | 4.2 | 0
3992 | TORONTO BUTTONVILLE A | 6 | 15 | 8 | 14.5 | 3.5 | 0
3992 | TORONTO BUTTONVILLE A | 6 | 16 | 8 | 15.275 | 2.725 | 0
3993 | TORONTO BUTTONVILLE A | 6 | 15 | 9 | 17.1 | 0.9 | 0
3993 | TORONTO BUTTONVILLE A | 6 | 16 | 9 | 17.825 | 0.175 | 0
3994 | TORONTO BUTTONVILLE A | 6 | 15 | 10 | 18.4 | 0 | 0.4
3994 | TORONTO BUTTONVILLE A | 6 | 16 | 10 | 19.9 | 0 | 1.9
3995 | TORONTO BUTTONVILLE A | 6 | 15 | 11 | 19.3 | 0 | 1.3
3995 | TORONTO BUTTONVILLE A | 6 | 16 | 11 | 21.45 | 0 | 3.45
3996 | TORONTO BUTTONVILLE A | 6 | 15 | 12 | 19.2 | 0 | 1.2
3996 | TORONTO BUTTONVILLE A | 6 | 16 | 12 | 21.1667 | 0 | 3.1667
3997 | TORONTO BUTTONVILLE A | 6 | 15 | 13 | 19.9 | 0 | 1.9
3997 | TORONTO BUTTONVILLE A | 6 | 16 | 13 | 23.35 | 0 | 5.35
3998 | TORONTO BUTTONVILLE A | 6 | 15 | 14 | 19.7 | 0 | 1.7
3998 | TORONTO BUTTONVILLE A | 6 | 16 | 14 | 23.875 | 0 | 5.875
3999 | TORONTO BUTTONVILLE A | 6 | 15 | 15 | 19.9 | 0 | 1.9
3999 | TORONTO BUTTONVILLE A | 6 | 16 | 15 | 24.275 | 0 | 6.275
4000 | TORONTO BUTTONVILLE A | 6 | 15 | 16 | 19.9 | 0 | 1.9
4000 | TORONTO BUTTONVILLE A | 6 | 16 | 16 | 23.9 | 0 | 5.9
4001 | TORONTO BUTTONVILLE A | 6 | 15 | 17 | 20.2 | 0 | 2.2
4001 | TORONTO BUTTONVILLE A | 6 | 16 | 17 | 24.1 | 0 | 6.1
4002 | TORONTO BUTTONVILLE A | 6 | 15 | 18 | 20.4 | 0 | 2.4
4002 | TORONTO BUTTONVILLE A | 6 | 16 | 18 | 24.05 | 0 | 6.05
4003 | TORONTO BUTTONVILLE A | 6 | 15 | 19 | 20.2 | 0 | 2.2
4003 | TORONTO BUTTONVILLE A | 6 | 16 | 19 | 23.3 | 0 | 5.3
4004 | TORONTO BUTTONVILLE A | 6 | 15 | 20 | 19.5 | 0 | 1.5
4004 | TORONTO BUTTONVILLE A | 6 | 16 | 20 | 22.175 | 0 | 4.175
4005 | TORONTO BUTTONVILLE A | 6 | 15 | 21 | 18.1 | 0 | 0.1
4005 | TORONTO BUTTONVILLE A | 6 | 16 | 21 | 20.65 | 0 | 2.65
4006 | TORONTO BUTTONVILLE A | 6 | 15 | 22 | 16.6 | 1.4 | 0
4006 | TORONTO BUTTONVILLE A | 6 | 16 | 22 | 18.55 | 0 | 0.55
4007 | TORONTO BUTTONVILLE A | 6 | 15 | 23 | 14.9 | 3.1 | 0
4007 | TORONTO BUTTONVILLE A | 6 | 16 | 23 | 17.925 | 0.075 | 0
4008 | TORONTO BUTTONVILLE A | 6 | 15 | 24 | 13.4 | 4.6 | 0
4008 | TORONTO BUTTONVILLE A | 6 | 16 | 24 | 16.85 | 1.15 | 0
4009 | TORONTO BUTTONVILLE A | 6 | 16 | 1 | 12.6 | 5.4 | 0
4009 | TORONTO BUTTONVILLE A | 6 | 17 | 1 | 16.55 | 1.45 | 0
4010 | TORONTO BUTTONVILLE A | 6 | 16 | 2 | 11.6 | 6.4 | 0
4010 | TORONTO BUTTONVILLE A | 6 | 17 | 2 | 16.125 | 1.875 | 0
4011 | TORONTO BUTTONVILLE A | 6 | 16 | 3 | 11.8 | 6.2 | 0
4011 | TORONTO BUTTONVILLE A | 6 | 17 | 3 | 15.775 | 2.225 | 0
4012 | TORONTO BUTTONVILLE A | 6 | 16 | 4 | 10.9 | 7.1 | 0
4012 | TORONTO BUTTONVILLE A | 6 | 17 | 4 | 15.15 | 2.85 | 0
4013 | TORONTO BUTTONVILLE A | 6 | 16 | 5 | 10 | 8 | 0
4013 | TORONTO BUTTONVILLE A | 6 | 17 | 5 | 14.825 | 3.175 | 0
4014 | TORONTO BUTTONVILLE A | 6 | 16 | 6 | 10.4 | 7.6 | 0
4014 | TORONTO BUTTONVILLE A | 6 | 17 | 6 | 15.125 | 2.875 | 0
4015 | TORONTO BUTTONVILLE A | 6 | 16 | 7 | 13.5 | 4.5 | 0
4015 | TORONTO BUTTONVILLE A | 6 | 17 | 7 | 16.475 | 1.525 | 0
4016 | TORONTO BUTTONVILLE A | 6 | 16 | 8 | 16.8 | 1.2 | 0
4016 | TORONTO BUTTONVILLE A | 6 | 17 | 8 | 19.1 | 0 | 1.1
4017 | TORONTO BUTTONVILLE A | 6 | 16 | 9 | 19.3 | 0 | 1.3
4017 | TORONTO BUTTONVILLE A | 6 | 17 | 9 | 20.975 | 0 | 2.975
4018 | TORONTO BUTTONVILLE A | 6 | 16 | 10 | 20.8 | 0 | 2.8
4018 | TORONTO BUTTONVILLE A | 6 | 17 | 10 | 22.05 | 0 | 4.05
4019 | TORONTO BUTTONVILLE A | 6 | 16 | 11 | 21.6 | 0 | 3.6
4019 | TORONTO BUTTONVILLE A | 6 | 17 | 11 | 23.35 | 0 | 5.35
4020 | TORONTO BUTTONVILLE A | 6 | 16 | 12 | 22 | 0 | 4
4020 | TORONTO BUTTONVILLE A | 6 | 17 | 12 | 24.05 | 0 | 6.05
4021 | TORONTO BUTTONVILLE A | 6 | 16 | 13 | 22.3 | 0 | 4.3
4021 | TORONTO BUTTONVILLE A | 6 | 17 | 13 | 25.2 | 0 | 7.2
4022 | TORONTO BUTTONVILLE A | 6 | 16 | 14 | 22.4 | 0 | 4.4
4022 | TORONTO BUTTONVILLE A | 6 | 17 | 14 | 26.025 | 0 | 8.025
4023 | TORONTO BUTTONVILLE A | 6 | 16 | 15 | 22.5 | 0 | 4.5
4023 | TORONTO BUTTONVILLE A | 6 | 17 | 15 | 24.975 | 0 | 6.975
4024 | TORONTO BUTTONVILLE A | 6 | 16 | 16 | 22.9 | 0 | 4.9
4024 | TORONTO BUTTONVILLE A | 6 | 17 | 16 | 24.375 | 0 | 6.375
4025 | TORONTO BUTTONVILLE A | 6 | 16 | 17 | 23.7 | 0 | 5.7
4025 | TORONTO BUTTONVILLE A | 6 | 17 | 17 | 24.7 | 0 | 6.7
4026 | TORONTO BUTTONVILLE A | 6 | 16 | 18 | 23.2 | 0 | 5.2
4026 | TORONTO BUTTONVILLE A | 6 | 17 | 18 | 24.95 | 0 | 6.95
4027 | TORONTO BUTTONVILLE A | 6 | 16 | 19 | 23.1 | 0 | 5.1
4027 | TORONTO BUTTONVILLE A | 6 | 17 | 19 | 24.325 | 0 | 6.325
4028 | TORONTO BUTTONVILLE A | 6 | 16 | 20 | 22.5 | 0 | 4.5
4028 | TORONTO BUTTONVILLE A | 6 | 17 | 20 | 23.375 | 0 | 5.375
4029 | TORONTO BUTTONVILLE A | 6 | 16 | 21 | 20.1 | 0 | 2.1
4029 | TORONTO BUTTONVILLE A | 6 | 17 | 21 | 22.1 | 0 | 4.1
4030 | TORONTO BUTTONVILLE A | 6 | 16 | 22 | 18.9 | 0 | 0.9
4030 | TORONTO BUTTONVILLE A | 6 | 17 | 22 | 21.25 | 0 | 3.25
4031 | TORONTO BUTTONVILLE A | 6 | 16 | 23 | 16.7 | 1.3 | 0
4031 | TORONTO BUTTONVILLE A | 6 | 17 | 23 | 21.55 | 0 | 3.55
4032 | TORONTO BUTTONVILLE A | 6 | 16 | 24 | 15.6 | 2.4 | 0
4032 | TORONTO BUTTONVILLE A | 6 | 17 | 24 | 21.325 | 0 | 3.325
4033 | TORONTO BUTTONVILLE A | 6 | 17 | 1 | 12.9 | 5.1 | 0
4033 | TORONTO BUTTONVILLE A | 6 | 18 | 1 | 20.375 | 0 | 2.375
4034 | TORONTO BUTTONVILLE A | 6 | 17 | 2 | 12.9 | 5.1 | 0
4034 | TORONTO BUTTONVILLE A | 6 | 18 | 2 | 19.625 | 0 | 1.625
4035 | TORONTO BUTTONVILLE A | 6 | 17 | 3 | 12.2 | 5.8 | 0
4035 | TORONTO BUTTONVILLE A | 6 | 18 | 3 | 19.475 | 0 | 1.475
4036 | TORONTO BUTTONVILLE A | 6 | 17 | 4 | 12.4 | 5.6 | 0
4036 | TORONTO BUTTONVILLE A | 6 | 18 | 4 | 19.475 | 0 | 1.475
4037 | TORONTO BUTTONVILLE A | 6 | 17 | 5 | 12.1 | 5.9 | 0
4037 | TORONTO BUTTONVILLE A | 6 | 18 | 5 | 19.425 | 0 | 1.425
4038 | TORONTO BUTTONVILLE A | 6 | 17 | 6 | 12 | 6 | 0
4038 | TORONTO BUTTONVILLE A | 6 | 18 | 6 | 20.1 | 0 | 2.1
4039 | TORONTO BUTTONVILLE A | 6 | 17 | 7 | 14.7 | 3.3 | 0
4039 | TORONTO BUTTONVILLE A | 6 | 18 | 7 | 20.675 | 0 | 2.675
4040 | TORONTO BUTTONVILLE A | 6 | 17 | 8 | 18.3 | 0 | 0.3
4040 | TORONTO BUTTONVILLE A | 6 | 18 | 8 | 21.925 | 0 | 3.925
4041 | TORONTO BUTTONVILLE A | 6 | 17 | 9 | 20.8 | 0 | 2.8
4041 | TORONTO BUTTONVILLE A | 6 | 18 | 9 | 22.075 | 0 | 4.075
4042 | TORONTO BUTTONVILLE A | 6 | 17 | 10 | 22.4 | 0 | 4.4
4042 | TORONTO BUTTONVILLE A | 6 | 18 | 10 | 23.8 | 0 | 5.8
4043 | TORONTO BUTTONVILLE A | 6 | 17 | 11 | 23.7 | 0 | 5.7
4043 | TORONTO BUTTONVILLE A | 6 | 18 | 11 | 22.7 | 0 | 4.7
4044 | TORONTO BUTTONVILLE A | 6 | 17 | 12 | 24 | 0 | 6
4044 | TORONTO BUTTONVILLE A | 6 | 18 | 12 | 23.7 | 0 | 5.7
4045 | TORONTO BUTTONVILLE A | 6 | 17 | 13 | 24.8 | 0 | 6.8
4045 | TORONTO BUTTONVILLE A | 6 | 18 | 13 | 24.375 | 0 | 6.375
4046 | TORONTO BUTTONVILLE A | 6 | 17 | 14 | 26.1 | 0 | 8.1
4046 | TORONTO BUTTONVILLE A | 6 | 18 | 14 | 25.125 | 0 | 7.125
4047 | TORONTO BUTTONVILLE A | 6 | 17 | 15 | 26.3 | 0 | 8.3
4047 | TORONTO BUTTONVILLE A | 6 | 18 | 15 | 25.3 | 0 | 7.3
4048 | TORONTO BUTTONVILLE A | 6 | 17 | 16 | 27.4 | 0 | 9.4
4048 | TORONTO BUTTONVILLE A | 6 | 18 | 16 | 25.7 | 0 | 7.7
4049 | TORONTO BUTTONVILLE A | 6 | 17 | 17 | 27.6 | 0 | 9.6
4049 | TORONTO BUTTONVILLE A | 6 | 18 | 17 | 25.55 | 0 | 7.55
4050 | TORONTO BUTTONVILLE A | 6 | 17 | 18 | 27.1 | 0 | 9.1
4050 | TORONTO BUTTONVILLE A | 6 | 18 | 18 | 25 | 0 | 7
4051 | TORONTO BUTTONVILLE A | 6 | 17 | 19 | 26.8 | 0 | 8.8
4051 | TORONTO BUTTONVILLE A | 6 | 18 | 19 | 24.475 | 0 | 6.475
4052 | TORONTO BUTTONVILLE A | 6 | 17 | 20 | 25.6 | 0 | 7.6
4052 | TORONTO BUTTONVILLE A | 6 | 18 | 20 | 23.5 | 0 | 5.5
4053 | TORONTO BUTTONVILLE A | 6 | 17 | 21 | 23.3 | 0 | 5.3
4053 | TORONTO BUTTONVILLE A | 6 | 18 | 21 | 22 | 0 | 4
4054 | TORONTO BUTTONVILLE A | 6 | 17 | 22 | 21 | 0 | 3
4054 | TORONTO BUTTONVILLE A | 6 | 18 | 22 | 21.025 | 0 | 3.025
4055 | TORONTO BUTTONVILLE A | 6 | 17 | 23 | 18.4 | 0 | 0.4
4055 | TORONTO BUTTONVILLE A | 6 | 18 | 23 | 20.35 | 0 | 2.35
4056 | TORONTO BUTTONVILLE A | 6 | 17 | 24 | 17.7 | 0.3 | 0
4056 | TORONTO BUTTONVILLE A | 6 | 18 | 24 | 20.6 | 0 | 2.6
4057 | TORONTO BUTTONVILLE A | 6 | 18 | 1 | 16.6 | 1.4 | 0
4057 | TORONTO BUTTONVILLE A | 6 | 19 | 1 | 19.85 | 0 | 1.85
4058 | TORONTO BUTTONVILLE A | 6 | 18 | 2 | 16.1 | 1.9 | 0
4058 | TORONTO BUTTONVILLE A | 6 | 19 | 2 | 18.725 | 0 | 0.725
4059 | TORONTO BUTTONVILLE A | 6 | 18 | 3 | 14.7 | 3.3 | 0
4059 | TORONTO BUTTONVILLE A | 6 | 19 | 3 | 17.95 | 0.05 | 0
4060 | TORONTO BUTTONVILLE A | 6 | 18 | 4 | 14.9 | 3.1 | 0
4060 | TORONTO BUTTONVILLE A | 6 | 19 | 4 | 17.375 | 0.625 | 0
4061 | TORONTO BUTTONVILLE A | 6 | 18 | 5 | 14.2 | 3.8 | 0
4061 | TORONTO BUTTONVILLE A | 6 | 19 | 5 | 16.9 | 1.1 | 0
4062 | TORONTO BUTTONVILLE A | 6 | 18 | 6 | 15 | 3 | 0
4062 | TORONTO BUTTONVILLE A | 6 | 19 | 6 | 16.875 | 1.125 | 0
4063 | TORONTO BUTTONVILLE A | 6 | 18 | 7 | 17 | 1 | 0
4063 | TORONTO BUTTONVILLE A | 6 | 19 | 7 | 18.025 | 0 | 0.025
4064 | TORONTO BUTTONVILLE A | 6 | 18 | 8 | 20.5 | 0 | 2.5
4064 | TORONTO BUTTONVILLE A | 6 | 19 | 8 | 19.3 | 0 | 1.3
4065 | TORONTO BUTTONVILLE A | 6 | 18 | 9 | 22.7 | 0 | 4.7
4065 | TORONTO BUTTONVILLE A | 6 | 19 | 9 | 20.6 | 0 | 2.6
4066 | TORONTO BUTTONVILLE A | 6 | 18 | 10 | 24.3 | 0 | 6.3
4066 | TORONTO BUTTONVILLE A | 6 | 19 | 10 | 22.05 | 0 | 4.05
4067 | TORONTO BUTTONVILLE A | 6 | 18 | 11 | 25.8 | 0 | 7.8
4067 | TORONTO BUTTONVILLE A | 6 | 19 | 11 | 23.275 | 0 | 5.275
4068 | TORONTO BUTTONVILLE A | 6 | 18 | 12 | 25.8 | 0 | 7.8
4068 | TORONTO BUTTONVILLE A | 6 | 19 | 12 | 24.35 | 0 | 6.35
4069 | TORONTO BUTTONVILLE A | 6 | 18 | 13 | 26.7 | 0 | 8.7
4069 | TORONTO BUTTONVILLE A | 6 | 19 | 13 | 24.475 | 0 | 6.475
4070 | TORONTO BUTTONVILLE A | 6 | 18 | 14 | 27.8 | 0 | 9.8
4070 | TORONTO BUTTONVILLE A | 6 | 19 | 14 | 25.125 | 0 | 7.125
4071 | TORONTO BUTTONVILLE A | 6 | 18 | 15 | 29.1 | 0 | 11.1
4071 | TORONTO BUTTONVILLE A | 6 | 19 | 15 | 25.675 | 0 | 7.675
4072 | TORONTO BUTTONVILLE A | 6 | 18 | 16 | 29.1 | 0 | 11.1
4072 | TORONTO BUTTONVILLE A | 6 | 19 | 16 | 24.875 | 0 | 6.875
4073 | TORONTO BUTTONVILLE A | 6 | 18 | 17 | 28.4 | 0 | 10.4
4073 | TORONTO BUTTONVILLE A | 6 | 19 | 17 | 24.55 | 0 | 6.55
4074 | TORONTO BUTTONVILLE A | 6 | 18 | 18 | 28.3 | 0 | 10.3
4074 | TORONTO BUTTONVILLE A | 6 | 19 | 18 | 24.3 | 0 | 6.3
4075 | TORONTO BUTTONVILLE A | 6 | 18 | 19 | 27.4 | 0 | 9.4
4075 | TORONTO BUTTONVILLE A | 6 | 19 | 19 | 23.95 | 0 | 5.95
4076 | TORONTO BUTTONVILLE A | 6 | 18 | 20 | 26.5 | 0 | 8.5
4076 | TORONTO BUTTONVILLE A | 6 | 19 | 20 | 23.575 | 0 | 5.575
4077 | TORONTO BUTTONVILLE A | 6 | 18 | 21 | 25.1 | 0 | 7.1
4077 | TORONTO BUTTONVILLE A | 6 | 19 | 21 | 21.775 | 0 | 3.775
4078 | TORONTO BUTTONVILLE A | 6 | 18 | 22 | 24.1 | 0 | 6.1
4078 | TORONTO BUTTONVILLE A | 6 | 19 | 22 | 20.8 | 0 | 2.8
4079 | TORONTO BUTTONVILLE A | 6 | 18 | 23 | 23.1 | 0 | 5.1
4079 | TORONTO BUTTONVILLE A | 6 | 19 | 23 | 19.625 | 0 | 1.625
4080 | TORONTO BUTTONVILLE A | 6 | 18 | 24 | 22.1 | 0 | 4.1
4080 | TORONTO BUTTONVILLE A | 6 | 19 | 24 | 18.5 | 0 | 0.5
4081 | TORONTO BUTTONVILLE A | 6 | 19 | 1 | 20.6 | 0 | 2.6
4081 | TORONTO BUTTONVILLE A | 6 | 20 | 1 | 17.45 | 0.55 | 0
4082 | TORONTO BUTTONVILLE A | 6 | 19 | 2 | 20 | 0 | 2
4082 | TORONTO BUTTONVILLE A | 6 | 20 | 2 | 16.525 | 1.475 | 0
4083 | TORONTO BUTTONVILLE A | 6 | 19 | 3 | 19.1 | 0 | 1.1
4083 | TORONTO BUTTONVILLE A | 6 | 20 | 3 | 16.35 | 1.65 | 0
4084 | TORONTO BUTTONVILLE A | 6 | 19 | 4 | 18.5 | 0 | 0.5
4084 | TORONTO BUTTONVILLE A | 6 | 20 | 4 | 16 | 2 | 0
4085 | TORONTO BUTTONVILLE A | 6 | 19 | 5 | 18.2 | 0 | 0.2
4085 | TORONTO BUTTONVILLE A | 6 | 20 | 5 | 15.85 | 2.15 | 0
4086 | TORONTO BUTTONVILLE A | 6 | 19 | 6 | 17.9 | 0.1 | 0
4086 | TORONTO BUTTONVILLE A | 6 | 20 | 6 | 15.85 | 2.15 | 0
4087 | TORONTO BUTTONVILLE A | 6 | 19 | 7 | 19.9 | 0 | 1.9
4087 | TORONTO BUTTONVILLE A | 6 | 20 | 7 | 16.475 | 1.525 | 0
4088 | TORONTO BUTTONVILLE A | 6 | 19 | 8 | 21.1 | 0 | 3.1
4088 | TORONTO BUTTONVILLE A | 6 | 20 | 8 | 17.3 | 0.7 | 0
4089 | TORONTO BUTTONVILLE A | 6 | 19 | 9 | 23.2 | 0 | 5.2
4089 | TORONTO BUTTONVILLE A | 6 | 20 | 9 | 18.3 | 0 | 0.3
4090 | TORONTO BUTTONVILLE A | 6 | 19 | 10 | 24.9 | 0 | 6.9
4090 | TORONTO BUTTONVILLE A | 6 | 20 | 10 | 18.9 | 0 | 0.9
4091 | TORONTO BUTTONVILLE A | 6 | 19 | 11 | 25.1 | 0 | 7.1
4091 | TORONTO BUTTONVILLE A | 6 | 20 | 11 | 20.075 | 0 | 2.075
4092 | TORONTO BUTTONVILLE A | 6 | 19 | 12 | 28.1 | 0 | 10.1
4092 | TORONTO BUTTONVILLE A | 6 | 20 | 12 | 21.7 | 0 | 3.7
4093 | TORONTO BUTTONVILLE A | 6 | 19 | 13 | 29 | 0 | 11
4093 | TORONTO BUTTONVILLE A | 6 | 20 | 13 | 22.225 | 0 | 4.225
4094 | TORONTO BUTTONVILLE A | 6 | 19 | 14 | 28.6 | 0 | 10.6
4094 | TORONTO BUTTONVILLE A | 6 | 20 | 14 | 22.775 | 0 | 4.775
4095 | TORONTO BUTTONVILLE A | 6 | 19 | 15 | 29.2 | 0 | 11.2
4095 | TORONTO BUTTONVILLE A | 6 | 20 | 15 | 23.425 | 0 | 5.425
4096 | TORONTO BUTTONVILLE A | 6 | 19 | 16 | 29.6 | 0 | 11.6
4096 | TORONTO BUTTONVILLE A | 6 | 20 | 16 | 23.275 | 0 | 5.275
4097 | TORONTO BUTTONVILLE A | 6 | 19 | 17 | 29.3 | 0 | 11.3
4097 | TORONTO BUTTONVILLE A | 6 | 20 | 17 | 23.4 | 0 | 5.4
4098 | TORONTO BUTTONVILLE A | 6 | 19 | 18 | 30.1 | 0 | 12.1
4098 | TORONTO BUTTONVILLE A | 6 | 20 | 18 | 23.225 | 0 | 5.225
4099 | TORONTO BUTTONVILLE A | 6 | 19 | 19 | 28.3 | 0 | 10.3
4099 | TORONTO BUTTONVILLE A | 6 | 20 | 19 | 21.875 | 0 | 3.875
4100 | TORONTO BUTTONVILLE A | 6 | 19 | 20 | 27 | 0 | 9
4100 | TORONTO BUTTONVILLE A | 6 | 20 | 20 | 20.05 | 0 | 2.05
4101 | TORONTO BUTTONVILLE A | 6 | 19 | 21 | 25.2 | 0 | 7.2
4101 | TORONTO BUTTONVILLE A | 6 | 20 | 21 | 18.6 | 0 | 0.6
4102 | TORONTO BUTTONVILLE A | 6 | 19 | 22 | 23.2 | 0 | 5.2
4102 | TORONTO BUTTONVILLE A | 6 | 20 | 22 | 18.375 | 0 | 0.375
4103 | TORONTO BUTTONVILLE A | 6 | 19 | 23 | 22.6 | 0 | 4.6
4103 | TORONTO BUTTONVILLE A | 6 | 20 | 23 | 18.025 | 0 | 0.025
4104 | TORONTO BUTTONVILLE A | 6 | 19 | 24 | 21.5 | 0 | 3.5
4104 | TORONTO BUTTONVILLE A | 6 | 20 | 24 | 17.575 | 0.425 | 0
4105 | TORONTO BUTTONVILLE A | 6 | 20 | 1 | 20.2 | 0 | 2.2
4105 | TORONTO BUTTONVILLE A | 6 | 21 | 1 | 16.925 | 1.075 | 0
4106 | TORONTO BUTTONVILLE A | 6 | 20 | 2 | 19.7 | 0 | 1.7
4106 | TORONTO BUTTONVILLE A | 6 | 21 | 2 | 16.425 | 1.575 | 0
4107 | TORONTO BUTTONVILLE A | 6 | 20 | 3 | 19.7 | 0 | 1.7
4107 | TORONTO BUTTONVILLE A | 6 | 21 | 3 | 16.05 | 1.95 | 0
4108 | TORONTO BUTTONVILLE A | 6 | 20 | 4 | 19.1 | 0 | 1.1
4108 | TORONTO BUTTONVILLE A | 6 | 21 | 4 | 15.9 | 2.1 | 0
4109 | TORONTO BUTTONVILLE A | 6 | 20 | 5 | 19.1 | 0 | 1.1
4109 | TORONTO BUTTONVILLE A | 6 | 21 | 5 | 15.675 | 2.325 | 0
4110 | TORONTO BUTTONVILLE A | 6 | 20 | 6 | 19.4 | 0 | 1.4
4110 | TORONTO BUTTONVILLE A | 6 | 21 | 6 | 15.375 | 2.625 | 0
4111 | TORONTO BUTTONVILLE A | 6 | 20 | 7 | 21.1 | 0 | 3.1
4111 | TORONTO BUTTONVILLE A | 6 | 21 | 7 | 16.075 | 1.925 | 0
4112 | TORONTO BUTTONVILLE A | 6 | 20 | 8 | 25 | 0 | 7
4112 | TORONTO BUTTONVILLE A | 6 | 21 | 8 | 16.55 | 1.45 | 0
4113 | TORONTO BUTTONVILLE A | 6 | 20 | 9 | 26.2 | 0 | 8.2
4113 | TORONTO BUTTONVILLE A | 6 | 21 | 9 | 17.575 | 0.425 | 0
4114 | TORONTO BUTTONVILLE A | 6 | 20 | 10 | 27.4 | 0 | 9.4
4114 | TORONTO BUTTONVILLE A | 6 | 21 | 10 | 18.625 | 0 | 0.625
4115 | TORONTO BUTTONVILLE A | 6 | 20 | 11 | 28.8 | 0 | 10.8
4115 | TORONTO BUTTONVILLE A | 6 | 21 | 11 | 19.9 | 0 | 1.9
4116 | TORONTO BUTTONVILLE A | 6 | 20 | 12 | 29.4 | 0 | 11.4
4116 | TORONTO BUTTONVILLE A | 6 | 21 | 12 | 21.425 | 0 | 3.425
4117 | TORONTO BUTTONVILLE A | 6 | 20 | 13 | 30.5 | 0 | 12.5
4117 | TORONTO BUTTONVILLE A | 6 | 21 | 13 | 22.475 | 0 | 4.475
4118 | TORONTO BUTTONVILLE A | 6 | 20 | 14 | 30.3 | 0 | 12.3
4118 | TORONTO BUTTONVILLE A | 6 | 21 | 14 | 23.35 | 0 | 5.35
4119 | TORONTO BUTTONVILLE A | 6 | 20 | 15 | 30.6 | 0 | 12.6
4119 | TORONTO BUTTONVILLE A | 6 | 21 | 15 | 23.6 | 0 | 5.6
4120 | TORONTO BUTTONVILLE A | 6 | 20 | 16 | 32.1 | 0 | 14.1
4120 | TORONTO BUTTONVILLE A | 6 | 21 | 16 | 23.975 | 0 | 5.975
4121 | TORONTO BUTTONVILLE A | 6 | 20 | 17 | 31.1 | 0 | 13.1
4121 | TORONTO BUTTONVILLE A | 6 | 21 | 17 | 22.625 | 0 | 4.625
4122 | TORONTO BUTTONVILLE A | 6 | 20 | 18 | 30.4 | 0 | 12.4
4122 | TORONTO BUTTONVILLE A | 6 | 21 | 18 | 21.825 | 0 | 3.825
4123 | TORONTO BUTTONVILLE A | 6 | 20 | 19 | 29.9 | 0 | 11.9
4123 | TORONTO BUTTONVILLE A | 6 | 21 | 19 | 20.675 | 0 | 2.675
4124 | TORONTO BUTTONVILLE A | 6 | 20 | 20 | 28.4 | 0 | 10.4
4124 | TORONTO BUTTONVILLE A | 6 | 21 | 20 | 19.5 | 0 | 1.5
4125 | TORONTO BUTTONVILLE A | 6 | 20 | 21 | 27.5 | 0 | 9.5
4125 | TORONTO BUTTONVILLE A | 6 | 21 | 21 | 17.95 | 0.05 | 0
4126 | TORONTO BUTTONVILLE A | 6 | 20 | 22 | 26 | 0 | 8
4126 | TORONTO BUTTONVILLE A | 6 | 21 | 22 | 16.8 | 1.2 | 0
4127 | TORONTO BUTTONVILLE A | 6 | 20 | 23 | 25.4 | 0 | 7.4
4127 | TORONTO BUTTONVILLE A | 6 | 21 | 23 | 15.375 | 2.625 | 0
4128 | TORONTO BUTTONVILLE A | 6 | 20 | 24 | 24.4 | 0 | 6.4
4128 | TORONTO BUTTONVILLE A | 6 | 21 | 24 | 14.025 | 3.975 | 0
4129 | TORONTO BUTTONVILLE A | 6 | 21 | 1 | 23.3 | 0 | 5.3
4129 | TORONTO BUTTONVILLE A | 6 | 22 | 1 | 13.5 | 4.5 | 0
4130 | TORONTO BUTTONVILLE A | 6 | 21 | 2 | 21.7 | 0 | 3.7
4130 | TORONTO BUTTONVILLE A | 6 | 22 | 2 | 13.225 | 4.775 | 0
4131 | TORONTO BUTTONVILLE A | 6 | 21 | 3 | 20.2 | 0 | 2.2
4131 | TORONTO BUTTONVILLE A | 6 | 22 | 3 | 12.1 | 5.9 | 0
4132 | TORONTO BUTTONVILLE A | 6 | 21 | 4 | 19.2 | 0 | 1.2
4132 | TORONTO BUTTONVILLE A | 6 | 22 | 4 | 12.05 | 5.95 | 0
4133 | TORONTO BUTTONVILLE A | 6 | 21 | 5 | 18.8 | 0 | 0.8
4133 | TORONTO BUTTONVILLE A | 6 | 22 | 5 | 11.725 | 6.275 | 0
4134 | TORONTO BUTTONVILLE A | 6 | 21 | 6 | 18.8 | 0 | 0.8
4134 | TORONTO BUTTONVILLE A | 6 | 22 | 6 | 11.625 | 6.375 | 0
4135 | TORONTO BUTTONVILLE A | 6 | 21 | 7 | 20.1 | 0 | 2.1
4135 | TORONTO BUTTONVILLE A | 6 | 22 | 7 | 13.25 | 4.75 | 0
4136 | TORONTO BUTTONVILLE A | 6 | 21 | 8 | 22.6 | 0 | 4.6
4136 | TORONTO BUTTONVILLE A | 6 | 22 | 8 | 15.225 | 2.775 | 0
4137 | TORONTO BUTTONVILLE A | 6 | 21 | 9 | 25 | 0 | 7
4137 | TORONTO BUTTONVILLE A | 6 | 22 | 9 | 17.05 | 0.95 | 0
4138 | TORONTO BUTTONVILLE A | 6 | 21 | 10 | 26.9 | 0 | 8.9
4138 | TORONTO BUTTONVILLE A | 6 | 22 | 10 | 17.4 | 0.6 | 0
4139 | TORONTO BUTTONVILLE A | 6 | 21 | 11 | 28 | 0 | 10
4139 | TORONTO BUTTONVILLE A | 6 | 22 | 11 | 18.25 | 0 | 0.25
4140 | TORONTO BUTTONVILLE A | 6 | 21 | 12 | 29.6 | 0 | 11.6
4140 | TORONTO BUTTONVILLE A | 6 | 22 | 12 | 18.725 | 0 | 0.725
4141 | TORONTO BUTTONVILLE A | 6 | 21 | 13 | 29.9 | 0 | 11.9
4141 | TORONTO BUTTONVILLE A | 6 | 22 | 13 | 19.35 | 0 | 1.35
4142 | TORONTO BUTTONVILLE A | 6 | 21 | 14 | 29.9 | 0 | 11.9
4142 | TORONTO BUTTONVILLE A | 6 | 22 | 14 | 20.5 | 0 | 2.5
4143 | TORONTO BUTTONVILLE A | 6 | 21 | 15 | 31.1 | 0 | 13.1
4143 | TORONTO BUTTONVILLE A | 6 | 22 | 15 | 21.325 | 0 | 3.325
4144 | TORONTO BUTTONVILLE A | 6 | 21 | 16 | 30.8 | 0 | 12.8
4144 | TORONTO BUTTONVILLE A | 6 | 22 | 16 | 21.3 | 0 | 3.3
4145 | TORONTO BUTTONVILLE A | 6 | 21 | 17 | 29.1 | 0 | 11.1
4145 | TORONTO BUTTONVILLE A | 6 | 22 | 17 | 21.05 | 0 | 3.05
4146 | TORONTO BUTTONVILLE A | 6 | 21 | 18 | 27.5 | 0 | 9.5
4146 | TORONTO BUTTONVILLE A | 6 | 22 | 18 | 20.35 | 0 | 2.35
4147 | TORONTO BUTTONVILLE A | 6 | 21 | 19 | 23.2 | 0 | 5.2
4147 | TORONTO BUTTONVILLE A | 6 | 22 | 19 | 20.125 | 0 | 2.125
4148 | TORONTO BUTTONVILLE A | 6 | 21 | 20 | 23.9 | 0 | 5.9
4148 | TORONTO BUTTONVILLE A | 6 | 22 | 20 | 19.2 | 0 | 1.2
4149 | TORONTO BUTTONVILLE A | 6 | 21 | 21 | 24.1 | 0 | 6.1
4149 | TORONTO BUTTONVILLE A | 6 | 22 | 21 | 18.15 | 0 | 0.15
4150 | TORONTO BUTTONVILLE A | 6 | 21 | 22 | 23.2 | 0 | 5.2
4150 | TORONTO BUTTONVILLE A | 6 | 22 | 22 | 17.225 | 0.775 | 0
4151 | TORONTO BUTTONVILLE A | 6 | 21 | 23 | 22.4 | 0 | 4.4
4151 | TORONTO BUTTONVILLE A | 6 | 22 | 23 | 16.1 | 1.9 | 0
4152 | TORONTO BUTTONVILLE A | 6 | 21 | 24 | 21.9 | 0 | 3.9
4152 | TORONTO BUTTONVILLE A | 6 | 22 | 24 | 15.2 | 2.8 | 0
4153 | TORONTO BUTTONVILLE A | 6 | 22 | 1 | 22.2 | 0 | 4.2
4153 | TORONTO BUTTONVILLE A | 6 | 23 | 1 | 15.05 | 2.95 | 0
4154 | TORONTO BUTTONVILLE A | 6 | 22 | 2 | 21 | 0 | 3
4154 | TORONTO BUTTONVILLE A | 6 | 23 | 2 | 15.275 | 2.725 | 0
4155 | TORONTO BUTTONVILLE A | 6 | 22 | 3 | 20.9 | 0 | 2.9
4155 | TORONTO BUTTONVILLE A | 6 | 23 | 3 | 15.4 | 2.6 | 0
4156 | TORONTO BUTTONVILLE A | 6 | 22 | 4 | 20.8 | 0 | 2.8
4156 | TORONTO BUTTONVILLE A | 6 | 23 | 4 | 15.15 | 2.85 | 0
4157 | TORONTO BUTTONVILLE A | 6 | 22 | 5 | 19.9 | 0 | 1.9
4157 | TORONTO BUTTONVILLE A | 6 | 23 | 5 | 14.675 | 3.325 | 0
4158 | TORONTO BUTTONVILLE A | 6 | 22 | 6 | 19.6 | 0 | 1.6
4158 | TORONTO BUTTONVILLE A | 6 | 23 | 6 | 14.95 | 3.05 | 0
4159 | TORONTO BUTTONVILLE A | 6 | 22 | 7 | 21.6 | 0 | 3.6
4159 | TORONTO BUTTONVILLE A | 6 | 23 | 7 | 15.8 | 2.2 | 0
4160 | TORONTO BUTTONVILLE A | 6 | 22 | 8 | 22.9 | 0 | 4.9
4160 | TORONTO BUTTONVILLE A | 6 | 23 | 8 | 17.05 | 0.95 | 0
4161 | TORONTO BUTTONVILLE A | 6 | 22 | 9 | 23.4 | 0 | 5.4
4161 | TORONTO BUTTONVILLE A | 6 | 23 | 9 | 18.2 | 0 | 0.2
4162 | TORONTO BUTTONVILLE A | 6 | 22 | 10 | 24 | 0 | 6
4162 | TORONTO BUTTONVILLE A | 6 | 23 | 10 | 19.075 | 0 | 1.075
4163 | TORONTO BUTTONVILLE A | 6 | 22 | 11 | 24.9 | 0 | 6.9
4163 | TORONTO BUTTONVILLE A | 6 | 23 | 11 | 19.775 | 0 | 1.775
4164 | TORONTO BUTTONVILLE A | 6 | 22 | 12 | 27 | 0 | 9
4164 | TORONTO BUTTONVILLE A | 6 | 23 | 12 | 20.025 | 0 | 2.025
4165 | TORONTO BUTTONVILLE A | 6 | 22 | 13 | 28.2 | 0 | 10.2
4165 | TORONTO BUTTONVILLE A | 6 | 23 | 13 | 20.625 | 0 | 2.625
4166 | TORONTO BUTTONVILLE A | 6 | 22 | 14 | 28.3 | 0 | 10.3
4166 | TORONTO BUTTONVILLE A | 6 | 23 | 14 | 20.975 | 0 | 2.975
4167 | TORONTO BUTTONVILLE A | 6 | 22 | 15 | 28.6 | 0 | 10.6
4167 | TORONTO BUTTONVILLE A | 6 | 23 | 15 | 21.95 | 0 | 3.95
4168 | TORONTO BUTTONVILLE A | 6 | 22 | 16 | 29.4 | 0 | 11.4
4168 | TORONTO BUTTONVILLE A | 6 | 23 | 16 | 22.25 | 0 | 4.25
4169 | TORONTO BUTTONVILLE A | 6 | 22 | 17 | 28.9 | 0 | 10.9
4169 | TORONTO BUTTONVILLE A | 6 | 23 | 17 | 22.9 | 0 | 4.9
4170 | TORONTO BUTTONVILLE A | 6 | 22 | 18 | 28.4 | 0 | 10.4
4170 | TORONTO BUTTONVILLE A | 6 | 23 | 18 | 22.675 | 0 | 4.675
4171 | TORONTO BUTTONVILLE A | 6 | 22 | 19 | 28.3 | 0 | 10.3
4171 | TORONTO BUTTONVILLE A | 6 | 23 | 19 | 21.975 | 0 | 3.975
4172 | TORONTO BUTTONVILLE A | 6 | 22 | 20 | 25.6 | 0 | 7.6
4172 | TORONTO BUTTONVILLE A | 6 | 23 | 20 | 21.125 | 0 | 3.125
4173 | TORONTO BUTTONVILLE A | 6 | 22 | 21 | 23.9 | 0 | 5.9
4173 | TORONTO BUTTONVILLE A | 6 | 23 | 21 | 20.05 | 0 | 2.05
4174 | TORONTO BUTTONVILLE A | 6 | 22 | 22 | 23.7 | 0 | 5.7
4174 | TORONTO BUTTONVILLE A | 6 | 23 | 22 | 19.575 | 0 | 1.575
4175 | TORONTO BUTTONVILLE A | 6 | 22 | 23 | 23.4 | 0 | 5.4
4175 | TORONTO BUTTONVILLE A | 6 | 23 | 23 | 19 | 0 | 1
4176 | TORONTO BUTTONVILLE A | 6 | 22 | 24 | 23.1 | 0 | 5.1
4176 | TORONTO BUTTONVILLE A | 6 | 23 | 24 | 18.125 | 0 | 0.125
4177 | TORONTO BUTTONVILLE A | 6 | 23 | 1 | 22 | 0 | 4
4177 | TORONTO BUTTONVILLE A | 6 | 24 | 1 | 17.275 | 0.725 | 0
4178 | TORONTO BUTTONVILLE A | 6 | 23 | 2 | 21.7 | 0 | 3.7
4178 | TORONTO BUTTONVILLE A | 6 | 24 | 2 | 16.725 | 1.275 | 0
4179 | TORONTO BUTTONVILLE A | 6 | 23 | 3 | 21.9 | 0 | 3.9
4179 | TORONTO BUTTONVILLE A | 6 | 24 | 3 | 16.55 | 1.45 | 0
4180 | TORONTO BUTTONVILLE A | 6 | 23 | 4 | 21.3 | 0 | 3.3
4180 | TORONTO BUTTONVILLE A | 6 | 24 | 4 | 16.525 | 1.475 | 0
4181 | TORONTO BUTTONVILLE A | 6 | 23 | 5 | 20.7 | 0 | 2.7
4181 | TORONTO BUTTONVILLE A | 6 | 24 | 5 | 16.075 | 1.925 | 0
4182 | TORONTO BUTTONVILLE A | 6 | 23 | 6 | 20.7 | 0 | 2.7
4182 | TORONTO BUTTONVILLE A | 6 | 24 | 6 | 16.375 | 1.625 | 0
4183 | TORONTO BUTTONVILLE A | 6 | 23 | 7 | 21.4 | 0 | 3.4
4183 | TORONTO BUTTONVILLE A | 6 | 24 | 7 | 17.05 | 0.95 | 0
4184 | TORONTO BUTTONVILLE A | 6 | 23 | 8 | 22.5 | 0 | 4.5
4184 | TORONTO BUTTONVILLE A | 6 | 24 | 8 | 17.9 | 0.1 | 0
4185 | TORONTO BUTTONVILLE A | 6 | 23 | 9 | 23.7 | 0 | 5.7
4185 | TORONTO BUTTONVILLE A | 6 | 24 | 9 | 18.75 | 0 | 0.75
4186 | TORONTO BUTTONVILLE A | 6 | 23 | 10 | 24.8 | 0 | 6.8
4186 | TORONTO BUTTONVILLE A | 6 | 24 | 10 | 19.7 | 0 | 1.7
4187 | TORONTO BUTTONVILLE A | 6 | 23 | 11 | 24.6 | 0 | 6.6
4187 | TORONTO BUTTONVILLE A | 6 | 24 | 11 | 20.65 | 0 | 2.65
4188 | TORONTO BUTTONVILLE A | 6 | 23 | 12 | 24.1 | 0 | 6.1
4188 | TORONTO BUTTONVILLE A | 6 | 24 | 12 | 21.3 | 0 | 3.3
4189 | TORONTO BUTTONVILLE A | 6 | 23 | 13 | 22.6 | 0 | 4.6
4189 | TORONTO BUTTONVILLE A | 6 | 24 | 13 | 21.825 | 0 | 3.825
4190 | TORONTO BUTTONVILLE A | 6 | 23 | 14 | 22.4 | 0 | 4.4
4190 | TORONTO BUTTONVILLE A | 6 | 24 | 14 | 22.3 | 0 | 4.3
4191 | TORONTO BUTTONVILLE A | 6 | 23 | 15 | 22 | 0 | 4
4191 | TORONTO BUTTONVILLE A | 6 | 24 | 15 | 22.65 | 0 | 4.65
4192 | TORONTO BUTTONVILLE A | 6 | 23 | 16 | 22.7 | 0 | 4.7
4192 | TORONTO BUTTONVILLE A | 6 | 24 | 16 | 23.25 | 0 | 5.25
4193 | TORONTO BUTTONVILLE A | 6 | 23 | 17 | 21.9 | 0 | 3.9
4193 | TORONTO BUTTONVILLE A | 6 | 24 | 17 | 23.425 | 0 | 5.425
4194 | TORONTO BUTTONVILLE A | 6 | 23 | 18 | 20.9 | 0 | 2.9
4194 | TORONTO BUTTONVILLE A | 6 | 24 | 18 | 22.925 | 0 | 4.925
4195 | TORONTO BUTTONVILLE A | 6 | 23 | 19 | 21.8 | 0 | 3.8
4195 | TORONTO BUTTONVILLE A | 6 | 24 | 19 | 22.55 | 0 | 4.55
4196 | TORONTO BUTTONVILLE A | 6 | 23 | 20 | 22.3 | 0 | 4.3
4196 | TORONTO BUTTONVILLE A | 6 | 24 | 20 | 21.8 | 0 | 3.8
4197 | TORONTO BUTTONVILLE A | 6 | 23 | 21 | 21.9 | 0 | 3.9
4197 | TORONTO BUTTONVILLE A | 6 | 24 | 21 | 20.975 | 0 | 2.975
4198 | TORONTO BUTTONVILLE A | 6 | 23 | 22 | 20.7 | 0 | 2.7
4198 | TORONTO BUTTONVILLE A | 6 | 24 | 22 | 19.75 | 0 | 1.75
4199 | TORONTO BUTTONVILLE A | 6 | 23 | 23 | 18.5 | 0 | 0.5
4199 | TORONTO BUTTONVILLE A | 6 | 24 | 23 | 18.9 | 0 | 0.9
4200 | TORONTO BUTTONVILLE A | 6 | 23 | 24 | 18 | 0 | 0
4200 | TORONTO BUTTONVILLE A | 6 | 24 | 24 | 18.325 | 0 | 0.325
4201 | TORONTO BUTTONVILLE A | 6 | 24 | 1 | 18.1 | 0 | 0.1
4201 | TORONTO BUTTONVILLE A | 6 | 25 | 1 | 17.8 | 0.2 | 0
4202 | TORONTO BUTTONVILLE A | 6 | 24 | 2 | 17.7 | 0.3 | 0
4202 | TORONTO BUTTONVILLE A | 6 | 25 | 2 | 17.525 | 0.475 | 0
4203 | TORONTO BUTTONVILLE A | 6 | 24 | 3 | 17.1 | 0.9 | 0
4203 | TORONTO BUTTONVILLE A | 6 | 25 | 3 | 17.125 | 0.875 | 0
4204 | TORONTO BUTTONVILLE A | 6 | 24 | 4 | 16.4 | 1.6 | 0
4204 | TORONTO BUTTONVILLE A | 6 | 25 | 4 | 17.325 | 0.675 | 0
4205 | TORONTO BUTTONVILLE A | 6 | 24 | 5 | 16.3 | 1.7 | 0
4205 | TORONTO BUTTONVILLE A | 6 | 25 | 5 | 16.9 | 1.1 | 0
4206 | TORONTO BUTTONVILLE A | 6 | 24 | 6 | 15.7 | 2.3 | 0
4206 | TORONTO BUTTONVILLE A | 6 | 25 | 6 | 16.625 | 1.375 | 0
4207 | TORONTO BUTTONVILLE A | 6 | 24 | 7 | 15.8 | 2.2 | 0
4207 | TORONTO BUTTONVILLE A | 6 | 25 | 7 | 17.3 | 0.7 | 0
4208 | TORONTO BUTTONVILLE A | 6 | 24 | 8 | 15.4 | 2.6 | 0
4208 | TORONTO BUTTONVILLE A | 6 | 25 | 8 | 18.275 | 0 | 0.275
4209 | TORONTO BUTTONVILLE A | 6 | 24 | 9 | 16.2 | 1.8 | 0
4209 | TORONTO BUTTONVILLE A | 6 | 25 | 9 | 19.175 | 0 | 1.175
4210 | TORONTO BUTTONVILLE A | 6 | 24 | 10 | 16.6 | 1.4 | 0
4210 | TORONTO BUTTONVILLE A | 6 | 25 | 10 | 20 | 0 | 2
4211 | TORONTO BUTTONVILLE A | 6 | 24 | 11 | 17.2 | 0.8 | 0
4211 | TORONTO BUTTONVILLE A | 6 | 25 | 11 | 21.175 | 0 | 3.175
4212 | TORONTO BUTTONVILLE A | 6 | 24 | 12 | 17.9 | 0.1 | 0
4212 | TORONTO BUTTONVILLE A | 6 | 25 | 12 | 21.45 | 0 | 3.45
4213 | TORONTO BUTTONVILLE A | 6 | 24 | 13 | 18.5 | 0 | 0.5
4213 | TORONTO BUTTONVILLE A | 6 | 25 | 13 | 20.325 | 0 | 2.325
4214 | TORONTO BUTTONVILLE A | 6 | 24 | 14 | 19.8 | 0 | 1.8
4214 | TORONTO BUTTONVILLE A | 6 | 25 | 14 | 21.375 | 0 | 3.375
4215 | TORONTO BUTTONVILLE A | 6 | 24 | 15 | 20 | 0 | 2
4215 | TORONTO BUTTONVILLE A | 6 | 25 | 15 | 21.4 | 0 | 3.4
4216 | TORONTO BUTTONVILLE A | 6 | 24 | 16 | 20.9 | 0 | 2.9
4216 | TORONTO BUTTONVILLE A | 6 | 25 | 16 | 21.075 | 0 | 3.075
4217 | TORONTO BUTTONVILLE A | 6 | 24 | 17 | 21.4 | 0 | 3.4
4217 | TORONTO BUTTONVILLE A | 6 | 25 | 17 | 21.275 | 0 | 3.275
4218 | TORONTO BUTTONVILLE A | 6 | 24 | 18 | 20.9 | 0 | 2.9
4218 | TORONTO BUTTONVILLE A | 6 | 25 | 18 | 21.4 | 0 | 3.4
4219 | TORONTO BUTTONVILLE A | 6 | 24 | 19 | 20.5 | 0 | 2.5
4219 | TORONTO BUTTONVILLE A | 6 | 25 | 19 | 21.15 | 0 | 3.15
4220 | TORONTO BUTTONVILLE A | 6 | 24 | 20 | 20.8 | 0 | 2.8
4220 | TORONTO BUTTONVILLE A | 6 | 25 | 20 | 20.7 | 0 | 2.7
4221 | TORONTO BUTTONVILLE A | 6 | 24 | 21 | 19.6 | 0 | 1.6
4221 | TORONTO BUTTONVILLE A | 6 | 25 | 21 | 19.75 | 0 | 1.75
4222 | TORONTO BUTTONVILLE A | 6 | 24 | 22 | 19 | 0 | 1
4222 | TORONTO BUTTONVILLE A | 6 | 25 | 22 | 18.25 | 0 | 0.25
4223 | TORONTO BUTTONVILLE A | 6 | 24 | 23 | 18.2 | 0 | 0.2
4223 | TORONTO BUTTONVILLE A | 6 | 25 | 23 | 17.475 | 0.525 | 0
4224 | TORONTO BUTTONVILLE A | 6 | 24 | 24 | 17.7 | 0.3 | 0
4224 | TORONTO BUTTONVILLE A | 6 | 25 | 24 | 16.4 | 1.6 | 0
4225 | TORONTO BUTTONVILLE A | 6 | 25 | 1 | 16.7 | 1.3 | 0
4225 | TORONTO BUTTONVILLE A | 6 | 26 | 1 | 16.225 | 1.775 | 0
4226 | TORONTO BUTTONVILLE A | 6 | 25 | 2 | 16.2 | 1.8 | 0
4226 | TORONTO BUTTONVILLE A | 6 | 26 | 2 | 15.7 | 2.3 | 0
4227 | TORONTO BUTTONVILLE A | 6 | 25 | 3 | 15.3 | 2.7 | 0
4227 | TORONTO BUTTONVILLE A | 6 | 26 | 3 | 15.8 | 2.2 | 0
4228 | TORONTO BUTTONVILLE A | 6 | 25 | 4 | 15 | 3 | 0
4228 | TORONTO BUTTONVILLE A | 6 | 26 | 4 | 15.8 | 2.2 | 0
4229 | TORONTO BUTTONVILLE A | 6 | 25 | 5 | 13.9 | 4.1 | 0
4229 | TORONTO BUTTONVILLE A | 6 | 26 | 5 | 15.6 | 2.4 | 0
4230 | TORONTO BUTTONVILLE A | 6 | 25 | 6 | 13.4 | 4.6 | 0
4230 | TORONTO BUTTONVILLE A | 6 | 26 | 6 | 15.725 | 2.275 | 0
4231 | TORONTO BUTTONVILLE A | 6 | 25 | 7 | 14.5 | 3.5 | 0
4231 | TORONTO BUTTONVILLE A | 6 | 26 | 7 | 16.725 | 1.275 | 0
4232 | TORONTO BUTTONVILLE A | 6 | 25 | 8 | 16.5 | 1.5 | 0
4232 | TORONTO BUTTONVILLE A | 6 | 26 | 8 | 18.3 | 0 | 0.3
4233 | TORONTO BUTTONVILLE A | 6 | 25 | 9 | 18.9 | 0 | 0.9
4233 | TORONTO BUTTONVILLE A | 6 | 26 | 9 | 19.85 | 0 | 1.85
4234 | TORONTO BUTTONVILLE A | 6 | 25 | 10 | 20.7 | 0 | 2.7
4234 | TORONTO BUTTONVILLE A | 6 | 26 | 10 | 21.025 | 0 | 3.025
4235 | TORONTO BUTTONVILLE A | 6 | 25 | 11 | 21.2 | 0 | 3.2
4235 | TORONTO BUTTONVILLE A | 6 | 26 | 11 | 21.85 | 0 | 3.85
4236 | TORONTO BUTTONVILLE A | 6 | 25 | 12 | 22 | 0 | 4
4236 | TORONTO BUTTONVILLE A | 6 | 26 | 12 | 23.175 | 0 | 5.175
4237 | TORONTO BUTTONVILLE A | 6 | 25 | 13 | 23.4 | 0 | 5.4
4237 | TORONTO BUTTONVILLE A | 6 | 26 | 13 | 22.65 | 0 | 4.65
4238 | TORONTO BUTTONVILLE A | 6 | 25 | 14 | 24.7 | 0 | 6.7
4238 | TORONTO BUTTONVILLE A | 6 | 26 | 14 | 23.7 | 0 | 5.7
4239 | TORONTO BUTTONVILLE A | 6 | 25 | 15 | 24.3 | 0 | 6.3
4239 | TORONTO BUTTONVILLE A | 6 | 26 | 15 | 22.05 | 0 | 4.05
4240 | TORONTO BUTTONVILLE A | 6 | 25 | 16 | 24.7 | 0 | 6.7
4240 | TORONTO BUTTONVILLE A | 6 | 26 | 16 | 22.225 | 0 | 4.225
4241 | TORONTO BUTTONVILLE A | 6 | 25 | 17 | 24.5 | 0 | 6.5
4241 | TORONTO BUTTONVILLE A | 6 | 26 | 17 | 22.525 | 0 | 4.525
4242 | TORONTO BUTTONVILLE A | 6 | 25 | 18 | 25.1 | 0 | 7.1
4242 | TORONTO BUTTONVILLE A | 6 | 26 | 18 | 22.7 | 0 | 4.7
4243 | TORONTO BUTTONVILLE A | 6 | 25 | 19 | 25.2 | 0 | 7.2
4243 | TORONTO BUTTONVILLE A | 6 | 26 | 19 | 22.55 | 0 | 4.55
4244 | TORONTO BUTTONVILLE A | 6 | 25 | 20 | 24.2 | 0 | 6.2
4244 | TORONTO BUTTONVILLE A | 6 | 26 | 20 | 22.075 | 0 | 4.075
4245 | TORONTO BUTTONVILLE A | 6 | 25 | 21 | 22.5 | 0 | 4.5
4245 | TORONTO BUTTONVILLE A | 6 | 26 | 21 | 21.125 | 0 | 3.125
4246 | TORONTO BUTTONVILLE A | 6 | 25 | 22 | 21 | 0 | 3
4246 | TORONTO BUTTONVILLE A | 6 | 26 | 22 | 20.3 | 0 | 2.3
4247 | TORONTO BUTTONVILLE A | 6 | 25 | 23 | 20.2 | 0 | 2.2
4247 | TORONTO BUTTONVILLE A | 6 | 26 | 23 | 19.7 | 0 | 1.7
4248 | TORONTO BUTTONVILLE A | 6 | 25 | 24 | 18.9 | 0 | 0.9
4248 | TORONTO BUTTONVILLE A | 6 | 26 | 24 | 18.95 | 0 | 0.95
4249 | TORONTO BUTTONVILLE A | 6 | 26 | 1 | 19.2 | 0 | 1.2
4249 | TORONTO BUTTONVILLE A | 6 | 27 | 1 | 18.625 | 0 | 0.625
4250 | TORONTO BUTTONVILLE A | 6 | 26 | 2 | 18.9 | 0 | 0.9
4250 | TORONTO BUTTONVILLE A | 6 | 27 | 2 | 17.9 | 0.1 | 0
4251 | TORONTO BUTTONVILLE A | 6 | 26 | 3 | 18.2 | 0 | 0.2
4251 | TORONTO BUTTONVILLE A | 6 | 27 | 3 | 17.125 | 0.875 | 0
4252 | TORONTO BUTTONVILLE A | 6 | 26 | 4 | 17.5 | 0.5 | 0
4252 | TORONTO BUTTONVILLE A | 6 | 27 | 4 | 17.15 | 0.85 | 0
4253 | TORONTO BUTTONVILLE A | 6 | 26 | 5 | 16.6 | 1.4 | 0
4253 | TORONTO BUTTONVILLE A | 6 | 27 | 5 | 17.3 | 0.7 | 0
4254 | TORONTO BUTTONVILLE A | 6 | 26 | 6 | 16.1 | 1.9 | 0
4254 | TORONTO BUTTONVILLE A | 6 | 27 | 6 | 17.15 | 0.85 | 0
4255 | TORONTO BUTTONVILLE A | 6 | 26 | 7 | 17.5 | 0.5 | 0
4255 | TORONTO BUTTONVILLE A | 6 | 27 | 7 | 17.925 | 0.075 | 0
4256 | TORONTO BUTTONVILLE A | 6 | 26 | 8 | 20.4 | 0 | 2.4
4256 | TORONTO BUTTONVILLE A | 6 | 27 | 8 | 18.9 | 0 | 0.9
4257 | TORONTO BUTTONVILLE A | 6 | 26 | 9 | 22.9 | 0 | 4.9
4257 | TORONTO BUTTONVILLE A | 6 | 27 | 9 | 20.4 | 0 | 2.4
4258 | TORONTO BUTTONVILLE A | 6 | 26 | 10 | 25 | 0 | 7
4258 | TORONTO BUTTONVILLE A | 6 | 27 | 10 | 21.55 | 0 | 3.55
4259 | TORONTO BUTTONVILLE A | 6 | 26 | 11 | 26 | 0 | 8
4259 | TORONTO BUTTONVILLE A | 6 | 27 | 11 | 22.7 | 0 | 4.7
4260 | TORONTO BUTTONVILLE A | 6 | 26 | 12 | 27 | 0 | 9
4260 | TORONTO BUTTONVILLE A | 6 | 27 | 12 | 23 | 0 | 5
4261 | TORONTO BUTTONVILLE A | 6 | 26 | 13 | 27.1 | 0 | 9.1
4261 | TORONTO BUTTONVILLE A | 6 | 27 | 13 | 23.075 | 0 | 5.075
4262 | TORONTO BUTTONVILLE A | 6 | 26 | 14 | 28.1 | 0 | 10.1
4262 | TORONTO BUTTONVILLE A | 6 | 27 | 14 | 23.45 | 0 | 5.45
4263 | TORONTO BUTTONVILLE A | 6 | 26 | 15 | 28.7 | 0 | 10.7
4263 | TORONTO BUTTONVILLE A | 6 | 27 | 15 | 23.9 | 0 | 5.9
4264 | TORONTO BUTTONVILLE A | 6 | 26 | 16 | 28.1 | 0 | 10.1
4264 | TORONTO BUTTONVILLE A | 6 | 27 | 16 | 24.2 | 0 | 6.2
4265 | TORONTO BUTTONVILLE A | 6 | 26 | 17 | 29 | 0 | 11
4265 | TORONTO BUTTONVILLE A | 6 | 27 | 17 | 24.575 | 0 | 6.575
4266 | TORONTO BUTTONVILLE A | 6 | 26 | 18 | 28.3 | 0 | 10.3
4266 | TORONTO BUTTONVILLE A | 6 | 27 | 18 | 24.325 | 0 | 6.325
4267 | TORONTO BUTTONVILLE A | 6 | 26 | 19 | 27.9 | 0 | 9.9
4267 | TORONTO BUTTONVILLE A | 6 | 27 | 19 | 24.175 | 0 | 6.175
4268 | TORONTO BUTTONVILLE A | 6 | 26 | 20 | 27.5 | 0 | 9.5
4268 | TORONTO BUTTONVILLE A | 6 | 27 | 20 | 23.4 | 0 | 5.4
4269 | TORONTO BUTTONVILLE A | 6 | 26 | 21 | 25.8 | 0 | 7.8
4269 | TORONTO BUTTONVILLE A | 6 | 27 | 21 | 22.475 | 0 | 4.475
4270 | TORONTO BUTTONVILLE A | 6 | 26 | 22 | 24.7 | 0 | 6.7
4270 | TORONTO BUTTONVILLE A | 6 | 27 | 22 | 21.975 | 0 | 3.975
4271 | TORONTO BUTTONVILLE A | 6 | 26 | 23 | 23.4 | 0 | 5.4
4271 | TORONTO BUTTONVILLE A | 6 | 27 | 23 | 21.05 | 0 | 3.05
4272 | TORONTO BUTTONVILLE A | 6 | 26 | 24 | 22.2 | 0 | 4.2
4272 | TORONTO BUTTONVILLE A | 6 | 27 | 24 | 20.4 | 0 | 2.4
4273 | TORONTO BUTTONVILLE A | 6 | 27 | 1 | 21 | 0 | 3
4273 | TORONTO BUTTONVILLE A | 6 | 28 | 1 | 19.775 | 0 | 1.775
4274 | TORONTO BUTTONVILLE A | 6 | 27 | 2 | 19.8 | 0 | 1.8
4274 | TORONTO BUTTONVILLE A | 6 | 28 | 2 | 19.15 | 0 | 1.15
4275 | TORONTO BUTTONVILLE A | 6 | 27 | 3 | 19.7 | 0 | 1.7
4275 | TORONTO BUTTONVILLE A | 6 | 28 | 3 | 18.65 | 0 | 0.65
4276 | TORONTO BUTTONVILLE A | 6 | 27 | 4 | 20.5 | 0 | 2.5
4276 | TORONTO BUTTONVILLE A | 6 | 28 | 4 | 18.375 | 0 | 0.375
4277 | TORONTO BUTTONVILLE A | 6 | 27 | 5 | 19 | 0 | 1
4277 | TORONTO BUTTONVILLE A | 6 | 28 | 5 | 18 | 0 | 0
4278 | TORONTO BUTTONVILLE A | 6 | 27 | 6 | 19.2 | 0 | 1.2
4278 | TORONTO BUTTONVILLE A | 6 | 28 | 6 | 18 | 0 | 0
4279 | TORONTO BUTTONVILLE A | 6 | 27 | 7 | 19.7 | 0 | 1.7
4279 | TORONTO BUTTONVILLE A | 6 | 28 | 7 | 19.025 | 0 | 1.025
4280 | TORONTO BUTTONVILLE A | 6 | 27 | 8 | 20.3 | 0 | 2.3
4280 | TORONTO BUTTONVILLE A | 6 | 28 | 8 | 21.05 | 0 | 3.05
4281 | TORONTO BUTTONVILLE A | 6 | 27 | 9 | 20.3 | 0 | 2.3
4281 | TORONTO BUTTONVILLE A | 6 | 28 | 9 | 22.575 | 0 | 4.575
4282 | TORONTO BUTTONVILLE A | 6 | 27 | 10 | 23.1 | 0 | 5.1
4282 | TORONTO BUTTONVILLE A | 6 | 28 | 10 | 23.475 | 0 | 5.475
4283 | TORONTO BUTTONVILLE A | 6 | 27 | 11 | 25.3 | 0 | 7.3
4283 | TORONTO BUTTONVILLE A | 6 | 28 | 11 | 24.425 | 0 | 6.425
4284 | TORONTO BUTTONVILLE A | 6 | 27 | 12 | 25.9 | 0 | 7.9
4284 | TORONTO BUTTONVILLE A | 6 | 28 | 12 | 25.6 | 0 | 7.6
4285 | TORONTO BUTTONVILLE A | 6 | 27 | 13 | 26.9 | 0 | 8.9
4285 | TORONTO BUTTONVILLE A | 6 | 28 | 13 | 26.55 | 0 | 8.55
4286 | TORONTO BUTTONVILLE A | 6 | 27 | 14 | 27.2 | 0 | 9.2
4286 | TORONTO BUTTONVILLE A | 6 | 28 | 14 | 27.425 | 0 | 9.425
4287 | TORONTO BUTTONVILLE A | 6 | 27 | 15 | 28.8 | 0 | 10.8
4287 | TORONTO BUTTONVILLE A | 6 | 28 | 15 | 26.175 | 0 | 8.175
4288 | TORONTO BUTTONVILLE A | 6 | 27 | 16 | 28.4 | 0 | 10.4
4288 | TORONTO BUTTONVILLE A | 6 | 28 | 16 | 26.775 | 0 | 8.775
4289 | TORONTO BUTTONVILLE A | 6 | 27 | 17 | 28.6 | 0 | 10.6
4289 | TORONTO BUTTONVILLE A | 6 | 28 | 17 | 26.65 | 0 | 8.65
4290 | TORONTO BUTTONVILLE A | 6 | 27 | 18 | 27.9 | 0 | 9.9
4290 | TORONTO BUTTONVILLE A | 6 | 28 | 18 | 26.575 | 0 | 8.575
4291 | TORONTO BUTTONVILLE A | 6 | 27 | 19 | 27.8 | 0 | 9.8
4291 | TORONTO BUTTONVILLE A | 6 | 28 | 19 | 25.975 | 0 | 7.975
4292 | TORONTO BUTTONVILLE A | 6 | 27 | 20 | 27 | 0 | 9
4292 | TORONTO BUTTONVILLE A | 6 | 28 | 20 | 25.175 | 0 | 7.175
4293 | TORONTO BUTTONVILLE A | 6 | 27 | 21 | 25.9 | 0 | 7.9
4293 | TORONTO BUTTONVILLE A | 6 | 28 | 21 | 24.3 | 0 | 6.3
4294 | TORONTO BUTTONVILLE A | 6 | 27 | 22 | 21.7 | 0 | 3.7
4294 | TORONTO BUTTONVILLE A | 6 | 28 | 22 | 23.5 | 0 | 5.5
4295 | TORONTO BUTTONVILLE A | 6 | 27 | 23 | 20.6 | 0 | 2.6
4295 | TORONTO BUTTONVILLE A | 6 | 28 | 23 | 22.125 | 0 | 4.125
4296 | TORONTO BUTTONVILLE A | 6 | 27 | 24 | 20.3 | 0 | 2.3
4296 | TORONTO BUTTONVILLE A | 6 | 28 | 24 | 21.725 | 0 | 3.725
4297 | TORONTO BUTTONVILLE A | 6 | 28 | 1 | 19.8 | 0 | 1.8
4297 | TORONTO BUTTONVILLE A | 6 | 29 | 1 | 20.725 | 0 | 2.725
4298 | TORONTO BUTTONVILLE A | 6 | 28 | 2 | 19.6 | 0 | 1.6
4298 | TORONTO BUTTONVILLE A | 6 | 29 | 2 | 20.125 | 0 | 2.125
4299 | TORONTO BUTTONVILLE A | 6 | 28 | 3 | 19 | 0 | 1
4299 | TORONTO BUTTONVILLE A | 6 | 29 | 3 | 19.475 | 0 | 1.475
4300 | TORONTO BUTTONVILLE A | 6 | 28 | 4 | 18 | 0 | 0
4300 | TORONTO BUTTONVILLE A | 6 | 29 | 4 | 19.125 | 0 | 1.125
4301 | TORONTO BUTTONVILLE A | 6 | 28 | 5 | 17.3 | 0.7 | 0
4301 | TORONTO BUTTONVILLE A | 6 | 29 | 5 | 18.6 | 0 | 0.6
4302 | TORONTO BUTTONVILLE A | 6 | 28 | 6 | 16.9 | 1.1 | 0
4302 | TORONTO BUTTONVILLE A | 6 | 29 | 6 | 18.975 | 0 | 0.975
4303 | TORONTO BUTTONVILLE A | 6 | 28 | 7 | 17.8 | 0.2 | 0
4303 | TORONTO BUTTONVILLE A | 6 | 29 | 7 | 19.875 | 0 | 1.875
4304 | TORONTO BUTTONVILLE A | 6 | 28 | 8 | 18.9 | 0 | 0.9
4304 | TORONTO BUTTONVILLE A | 6 | 29 | 8 | 21.325 | 0 | 3.325
4305 | TORONTO BUTTONVILLE A | 6 | 28 | 9 | 20.9 | 0 | 2.9
4305 | TORONTO BUTTONVILLE A | 6 | 29 | 9 | 22.15 | 0 | 4.15
4306 | TORONTO BUTTONVILLE A | 6 | 28 | 10 | 22.3 | 0 | 4.3
4306 | TORONTO BUTTONVILLE A | 6 | 29 | 10 | 23.325 | 0 | 5.325
4307 | TORONTO BUTTONVILLE A | 6 | 28 | 11 | 23.5 | 0 | 5.5
4307 | TORONTO BUTTONVILLE A | 6 | 29 | 11 | 24.425 | 0 | 6.425
4308 | TORONTO BUTTONVILLE A | 6 | 28 | 12 | 24.7 | 0 | 6.7
4308 | TORONTO BUTTONVILLE A | 6 | 29 | 12 | 26.175 | 0 | 8.175
4309 | TORONTO BUTTONVILLE A | 6 | 28 | 13 | 25.6 | 0 | 7.6
4309 | TORONTO BUTTONVILLE A | 6 | 29 | 13 | 27.15 | 0 | 9.15
4310 | TORONTO BUTTONVILLE A | 6 | 28 | 14 | 26.3 | 0 | 8.3
4310 | TORONTO BUTTONVILLE A | 6 | 29 | 14 | 27.4 | 0 | 9.4
4311 | TORONTO BUTTONVILLE A | 6 | 28 | 15 | 26.9 | 0 | 8.9
4311 | TORONTO BUTTONVILLE A | 6 | 29 | 15 | 26.45 | 0 | 8.45
4312 | TORONTO BUTTONVILLE A | 6 | 28 | 16 | 27.7 | 0 | 9.7
4312 | TORONTO BUTTONVILLE A | 6 | 29 | 16 | 26.325 | 0 | 8.325
4313 | TORONTO BUTTONVILLE A | 6 | 28 | 17 | 26.6 | 0 | 8.6
4313 | TORONTO BUTTONVILLE A | 6 | 29 | 17 | 27.35 | 0 | 9.35
4314 | TORONTO BUTTONVILLE A | 6 | 28 | 18 | 26.7 | 0 | 8.7
4314 | TORONTO BUTTONVILLE A | 6 | 29 | 18 | 27.4 | 0 | 9.4
4315 | TORONTO BUTTONVILLE A | 6 | 28 | 19 | 26.4 | 0 | 8.4
4315 | TORONTO BUTTONVILLE A | 6 | 29 | 19 | 26.6 | 0 | 8.6
4316 | TORONTO BUTTONVILLE A | 6 | 28 | 20 | 25.4 | 0 | 7.4
4316 | TORONTO BUTTONVILLE A | 6 | 29 | 20 | 25.25 | 0 | 7.25
4317 | TORONTO BUTTONVILLE A | 6 | 28 | 21 | 24 | 0 | 6
4317 | TORONTO BUTTONVILLE A | 6 | 29 | 21 | 24.4 | 0 | 6.4
4318 | TORONTO BUTTONVILLE A | 6 | 28 | 22 | 22.4 | 0 | 4.4
4318 | TORONTO BUTTONVILLE A | 6 | 29 | 22 | 23.15 | 0 | 5.15
4319 | TORONTO BUTTONVILLE A | 6 | 28 | 23 | 21.6 | 0 | 3.6
4319 | TORONTO BUTTONVILLE A | 6 | 29 | 23 | 22.25 | 0 | 4.25
4320 | TORONTO BUTTONVILLE A | 6 | 28 | 24 | 21.1 | 0 | 3.1
4320 | TORONTO BUTTONVILLE A | 6 | 29 | 24 | 21.525 | 0 | 3.525
4321 | TORONTO BUTTONVILLE A | 6 | 29 | 1 | 20.1 | 0 | 2.1
4321 | TORONTO BUTTONVILLE A | 6 | 30 | 1 | 21.4 | 0 | 3.4
4322 | TORONTO BUTTONVILLE A | 6 | 29 | 2 | 20.1 | 0 | 2.1
4322 | TORONTO BUTTONVILLE A | 6 | 30 | 2 | 20.85 | 0 | 2.85
4323 | TORONTO BUTTONVILLE A | 6 | 29 | 3 | 19.8 | 0 | 1.8
4323 | TORONTO BUTTONVILLE A | 6 | 30 | 3 | 20.85 | 0 | 2.85
4324 | TORONTO BUTTONVILLE A | 6 | 29 | 4 | 19.2 | 0 | 1.2
4324 | TORONTO BUTTONVILLE A | 6 | 30 | 4 | 20.55 | 0 | 2.55
4325 | TORONTO BUTTONVILLE A | 6 | 29 | 5 | 18.8 | 0 | 0.8
4325 | TORONTO BUTTONVILLE A | 6 | 30 | 5 | 20.1 | 0 | 2.1
4326 | TORONTO BUTTONVILLE A | 6 | 29 | 6 | 18.6 | 0 | 0.6
4326 | TORONTO BUTTONVILLE A | 6 | 30 | 6 | 19.7 | 0 | 1.7
4327 | TORONTO BUTTONVILLE A | 6 | 29 | 7 | 20.4 | 0 | 2.4
4327 | TORONTO BUTTONVILLE A | 6 | 30 | 7 | 20.2 | 0 | 2.2
4328 | TORONTO BUTTONVILLE A | 6 | 29 | 8 | 22.2 | 0 | 4.2
4328 | TORONTO BUTTONVILLE A | 6 | 30 | 8 | 21.175 | 0 | 3.175
4329 | TORONTO BUTTONVILLE A | 6 | 29 | 9 | 23.9 | 0 | 5.9
4329 | TORONTO BUTTONVILLE A | 6 | 30 | 9 | 22.25 | 0 | 4.25
4330 | TORONTO BUTTONVILLE A | 6 | 29 | 10 | 26.1 | 0 | 8.1
4330 | TORONTO BUTTONVILLE A | 6 | 30 | 10 | 22.75 | 0 | 4.75
4331 | TORONTO BUTTONVILLE A | 6 | 29 | 11 | 27.2 | 0 | 9.2
4331 | TORONTO BUTTONVILLE A | 6 | 30 | 11 | 24.05 | 0 | 6.05
4332 | TORONTO BUTTONVILLE A | 6 | 29 | 12 | 27.5 | 0 | 9.5
4332 | TORONTO BUTTONVILLE A | 6 | 30 | 12 | 25.25 | 0 | 7.25
4333 | TORONTO BUTTONVILLE A | 6 | 29 | 13 | 28.5 | 0 | 10.5
4333 | TORONTO BUTTONVILLE A | 6 | 30 | 13 | 26.75 | 0 | 8.75
4334 | TORONTO BUTTONVILLE A | 6 | 29 | 14 | 29.9 | 0 | 11.9
4334 | TORONTO BUTTONVILLE A | 6 | 30 | 14 | 26.975 | 0 | 8.975
4335 | TORONTO BUTTONVILLE A | 6 | 29 | 15 | 30.3 | 0 | 12.3
4335 | TORONTO BUTTONVILLE A | 6 | 30 | 15 | 27.9 | 0 | 9.9
4336 | TORONTO BUTTONVILLE A | 6 | 29 | 16 | 30.1 | 0 | 12.1
4336 | TORONTO BUTTONVILLE A | 6 | 30 | 16 | 27.9 | 0 | 9.9
4337 | TORONTO BUTTONVILLE A | 6 | 29 | 17 | 29.5 | 0 | 11.5
4337 | TORONTO BUTTONVILLE A | 6 | 30 | 17 | 27.55 | 0 | 9.55
4338 | TORONTO BUTTONVILLE A | 6 | 29 | 18 | 29.8 | 0 | 11.8
4338 | TORONTO BUTTONVILLE A | 6 | 30 | 18 | 27.375 | 0 | 9.375
4339 | TORONTO BUTTONVILLE A | 6 | 29 | 19 | 29.2 | 0 | 11.2
4339 | TORONTO BUTTONVILLE A | 6 | 30 | 19 | 26.425 | 0 | 8.425
4340 | TORONTO BUTTONVILLE A | 6 | 29 | 20 | 28.1 | 0 | 10.1
4340 | TORONTO BUTTONVILLE A | 6 | 30 | 20 | 25.75 | 0 | 7.75
4341 | TORONTO BUTTONVILLE A | 6 | 29 | 21 | 26.5 | 0 | 8.5
4341 | TORONTO BUTTONVILLE A | 6 | 30 | 21 | 24.65 | 0 | 6.65
4342 | TORONTO BUTTONVILLE A | 6 | 29 | 22 | 24.8 | 0 | 6.8
4342 | TORONTO BUTTONVILLE A | 6 | 30 | 22 | 23.225 | 0 | 5.225
4343 | TORONTO BUTTONVILLE A | 6 | 29 | 23 | 23.4 | 0 | 5.4
4343 | TORONTO BUTTONVILLE A | 6 | 30 | 23 | 22.3 | 0 | 4.3
4344 | TORONTO BUTTONVILLE A | 6 | 29 | 24 | 23.1 | 0 | 5.1
4344 | TORONTO BUTTONVILLE A | 6 | 30 | 24 | 21.55 | 0 | 3.55
4345 | TORONTO BUTTONVILLE A | 6 | 30 | 1 | 21.6 | 0 | 3.6
4345 | TORONTO BUTTONVILLE A | 7 | 1 | 1 | 20.975 | 0 | 2.975
4346 | TORONTO BUTTONVILLE A | 6 | 30 | 2 | 20.6 | 0 | 2.6
4346 | TORONTO BUTTONVILLE A | 7 | 1 | 2 | 20.15 | 0 | 2.15
4347 | TORONTO BUTTONVILLE A | 6 | 30 | 3 | 20.4 | 0 | 2.4
4347 | TORONTO BUTTONVILLE A | 7 | 1 | 3 | 19.225 | 0 | 1.225
4348 | TORONTO BUTTONVILLE A | 6 | 30 | 4 | 19.8 | 0 | 1.8
4348 | TORONTO BUTTONVILLE A | 7 | 1 | 4 | 19.125 | 0 | 1.125
4349 | TORONTO BUTTONVILLE A | 6 | 30 | 5 | 18.7 | 0 | 0.7
4349 | TORONTO BUTTONVILLE A | 7 | 1 | 5 | 18.775 | 0 | 0.775
4350 | TORONTO BUTTONVILLE A | 6 | 30 | 6 | 18.4 | 0 | 0.4
4350 | TORONTO BUTTONVILLE A | 7 | 1 | 6 | 18.725 | 0 | 0.725
4351 | TORONTO BUTTONVILLE A | 6 | 30 | 7 | 19.8 | 0 | 1.8
4351 | TORONTO BUTTONVILLE A | 7 | 1 | 7 | 19.35 | 0 | 1.35
4352 | TORONTO BUTTONVILLE A | 6 | 30 | 8 | 21.9 | 0 | 3.9
4352 | TORONTO BUTTONVILLE A | 7 | 1 | 8 | 20.525 | 0 | 2.525
4353 | TORONTO BUTTONVILLE A | 6 | 30 | 9 | 23.5 | 0 | 5.5
4353 | TORONTO BUTTONVILLE A | 7 | 1 | 9 | 21.925 | 0 | 3.925
4354 | TORONTO BUTTONVILLE A | 6 | 30 | 10 | 24.3 | 0 | 6.3
4354 | TORONTO BUTTONVILLE A | 7 | 1 | 10 | 23.15 | 0 | 5.15
4355 | TORONTO BUTTONVILLE A | 6 | 30 | 11 | 25.3 | 0 | 7.3
4355 | TORONTO BUTTONVILLE A | 7 | 1 | 11 | 24.925 | 0 | 6.925
4356 | TORONTO BUTTONVILLE A | 6 | 30 | 12 | 26.9 | 0 | 8.9
4356 | TORONTO BUTTONVILLE A | 7 | 1 | 12 | 25.85 | 0 | 7.85
4357 | TORONTO BUTTONVILLE A | 6 | 30 | 13 | 25.7 | 0 | 7.7
4357 | TORONTO BUTTONVILLE A | 7 | 1 | 13 | 26.575 | 0 | 8.575
4358 | TORONTO BUTTONVILLE A | 6 | 30 | 14 | 26.8 | 0 | 8.8
4358 | TORONTO BUTTONVILLE A | 7 | 1 | 14 | 27.375 | 0 | 9.375
4359 | TORONTO BUTTONVILLE A | 6 | 30 | 15 | 27 | 0 | 9
4359 | TORONTO BUTTONVILLE A | 7 | 1 | 15 | 27.45 | 0 | 9.45
4360 | TORONTO BUTTONVILLE A | 6 | 30 | 16 | 25.7 | 0 | 7.7
4360 | TORONTO BUTTONVILLE A | 7 | 1 | 16 | 26.975 | 0 | 8.975
4361 | TORONTO BUTTONVILLE A | 6 | 30 | 17 | 26.3 | 0 | 8.3
4361 | TORONTO BUTTONVILLE A | 7 | 1 | 17 | 27 | 0 | 9
4362 | TORONTO BUTTONVILLE A | 6 | 30 | 18 | 25.8 | 0 | 7.8
4362 | TORONTO BUTTONVILLE A | 7 | 1 | 18 | 26.325 | 0 | 8.325
4363 | TORONTO BUTTONVILLE A | 6 | 30 | 19 | 26.8 | 0 | 8.8
4363 | TORONTO BUTTONVILLE A | 7 | 1 | 19 | 26.275 | 0 | 8.275
4364 | TORONTO BUTTONVILLE A | 6 | 30 | 20 | 24.8 | 0 | 6.8
4364 | TORONTO BUTTONVILLE A | 7 | 1 | 20 | 25 | 0 | 7
4365 | TORONTO BUTTONVILLE A | 6 | 30 | 21 | 24.1 | 0 | 6.1
4365 | TORONTO BUTTONVILLE A | 7 | 1 | 21 | 23.1 | 0 | 5.1
4366 | TORONTO BUTTONVILLE A | 6 | 30 | 22 | 22.8 | 0 | 4.8
4366 | TORONTO BUTTONVILLE A | 7 | 1 | 22 | 21.65 | 0 | 3.65
4367 | TORONTO BUTTONVILLE A | 6 | 30 | 23 | 22.4 | 0 | 4.4
4367 | TORONTO BUTTONVILLE A | 7 | 1 | 23 | 21.425 | 0 | 3.425
4368 | TORONTO BUTTONVILLE A | 6 | 30 | 24 | 21.7 | 0 | 3.7
4368 | TORONTO BUTTONVILLE A | 7 | 1 | 24 | 20.875 | 0 | 2.875
4369 | TORONTO BUTTONVILLE A | 7 | 1 | 1 | 20.4 | 0 | 2.4
4369 | TORONTO BUTTONVILLE A | 7 | 2 | 1 | 20.65 | 0 | 2.65
4370 | TORONTO BUTTONVILLE A | 7 | 1 | 2 | 19.3 | 0 | 1.3
4370 | TORONTO BUTTONVILLE A | 7 | 2 | 2 | 20.425 | 0 | 2.425
4371 | TORONTO BUTTONVILLE A | 7 | 1 | 3 | 18.3 | 0 | 0.3
4371 | TORONTO BUTTONVILLE A | 7 | 2 | 3 | 19.825 | 0 | 1.825
4372 | TORONTO BUTTONVILLE A | 7 | 1 | 4 | 18.2 | 0 | 0.2
4372 | TORONTO BUTTONVILLE A | 7 | 2 | 4 | 19.575 | 0 | 1.575
4373 | TORONTO BUTTONVILLE A | 7 | 1 | 5 | 18.1 | 0 | 0.1
4373 | TORONTO BUTTONVILLE A | 7 | 2 | 5 | 19.3 | 0 | 1.3
4374 | TORONTO BUTTONVILLE A | 7 | 1 | 6 | 17.5 | 0 | 0
4374 | TORONTO BUTTONVILLE A | 7 | 2 | 6 | 18.775 | 0 | 0.775
4375 | TORONTO BUTTONVILLE A | 7 | 1 | 7 | 19.7 | 0 | 1.7
4375 | TORONTO BUTTONVILLE A | 7 | 2 | 7 | 19.6 | 0 | 1.6
4376 | TORONTO BUTTONVILLE A | 7 | 1 | 8 | 22.5 | 0 | 4.5
4376 | TORONTO BUTTONVILLE A | 7 | 2 | 8 | 20.675 | 0 | 2.675
4377 | TORONTO BUTTONVILLE A | 7 | 1 | 9 | 24.5 | 0 | 6.5
4377 | TORONTO BUTTONVILLE A | 7 | 2 | 9 | 21.675 | 0 | 3.675
4378 | TORONTO BUTTONVILLE A | 7 | 1 | 10 | 25.8 | 0 | 7.8
4378 | TORONTO BUTTONVILLE A | 7 | 2 | 10 | 22.85 | 0 | 4.85
4379 | TORONTO BUTTONVILLE A | 7 | 1 | 11 | 26.4 | 0 | 8.4
4379 | TORONTO BUTTONVILLE A | 7 | 2 | 11 | 24.225 | 0 | 6.225
4380 | TORONTO BUTTONVILLE A | 7 | 1 | 12 | 26.9 | 0 | 8.9
4380 | TORONTO BUTTONVILLE A | 7 | 2 | 12 | 23.675 | 0 | 5.675
4381 | TORONTO BUTTONVILLE A | 7 | 1 | 13 | 27.7 | 0 | 9.7
4381 | TORONTO BUTTONVILLE A | 7 | 2 | 13 | 25.525 | 0 | 7.525
4382 | TORONTO BUTTONVILLE A | 7 | 1 | 14 | 29.6 | 0 | 11.6
4382 | TORONTO BUTTONVILLE A | 7 | 2 | 14 | 25.15 | 0 | 7.15
4383 | TORONTO BUTTONVILLE A | 7 | 1 | 15 | 29.7 | 0 | 11.7
4383 | TORONTO BUTTONVILLE A | 7 | 2 | 15 | 26.575 | 0 | 8.575
4384 | TORONTO BUTTONVILLE A | 7 | 1 | 16 | 30.6 | 0 | 12.6
4384 | TORONTO BUTTONVILLE A | 7 | 2 | 16 | 25.6 | 0 | 7.6
4385 | TORONTO BUTTONVILLE A | 7 | 1 | 17 | 31.1 | 0 | 13.1
4385 | TORONTO BUTTONVILLE A | 7 | 2 | 17 | 25.875 | 0 | 7.875
4386 | TORONTO BUTTONVILLE A | 7 | 1 | 18 | 30.1 | 0 | 12.1
4386 | TORONTO BUTTONVILLE A | 7 | 2 | 18 | 25.975 | 0 | 7.975
4387 | TORONTO BUTTONVILLE A | 7 | 1 | 19 | 29.6 | 0 | 11.6
4387 | TORONTO BUTTONVILLE A | 7 | 2 | 19 | 25.325 | 0 | 7.325
4388 | TORONTO BUTTONVILLE A | 7 | 1 | 20 | 28.1 | 0 | 10.1
4388 | TORONTO BUTTONVILLE A | 7 | 2 | 20 | 22.975 | 0 | 4.975
4389 | TORONTO BUTTONVILLE A | 7 | 1 | 21 | 26.4 | 0 | 8.4
4389 | TORONTO BUTTONVILLE A | 7 | 2 | 21 | 21.425 | 0 | 3.425
4390 | TORONTO BUTTONVILLE A | 7 | 1 | 22 | 25.1 | 0 | 7.1
4390 | TORONTO BUTTONVILLE A | 7 | 2 | 22 | 20.125 | 0 | 2.125
4391 | TORONTO BUTTONVILLE A | 7 | 1 | 23 | 24.3 | 0 | 6.3
4391 | TORONTO BUTTONVILLE A | 7 | 2 | 23 | 19.525 | 0 | 1.525
4392 | TORONTO BUTTONVILLE A | 7 | 1 | 24 | 23 | 0 | 5
4392 | TORONTO BUTTONVILLE A | 7 | 2 | 24 | 18.675 | 0 | 0.675
4393 | TORONTO BUTTONVILLE A | 7 | 2 | 1 | 22.9 | 0 | 4.9
4393 | TORONTO BUTTONVILLE A | 7 | 3 | 1 | 18.1 | 0 | 0.1
4394 | TORONTO BUTTONVILLE A | 7 | 2 | 2 | 22.4 | 0 | 4.4
4394 | TORONTO BUTTONVILLE A | 7 | 3 | 2 | 17.475 | 0 | 0
4395 | TORONTO BUTTONVILLE A | 7 | 2 | 3 | 22.4 | 0 | 4.4
4395 | TORONTO BUTTONVILLE A | 7 | 3 | 3 | 16.925 | 0 | 0
4396 | TORONTO BUTTONVILLE A | 7 | 2 | 4 | 22.2 | 0 | 4.2
4396 | TORONTO BUTTONVILLE A | 7 | 3 | 4 | 16.5 | 0 | 0
4397 | TORONTO BUTTONVILLE A | 7 | 2 | 5 | 21.4 | 0 | 3.4
4397 | TORONTO BUTTONVILLE A | 7 | 3 | 5 | 16.125 | 0 | 0
4398 | TORONTO BUTTONVILLE A | 7 | 2 | 6 | 21.6 | 0 | 3.6
4398 | TORONTO BUTTONVILLE A | 7 | 3 | 6 | 16.325 | 0 | 0
4399 | TORONTO BUTTONVILLE A | 7 | 2 | 7 | 22.9 | 0 | 4.9
4399 | TORONTO BUTTONVILLE A | 7 | 3 | 7 | 17.6 | 0 | 0
4400 | TORONTO BUTTONVILLE A | 7 | 2 | 8 | 24.9 | 0 | 6.9
4400 | TORONTO BUTTONVILLE A | 7 | 3 | 8 | 19.45 | 0 | 1.45
4401 | TORONTO BUTTONVILLE A | 7 | 2 | 9 | 26.5 | 0 | 8.5
4401 | TORONTO BUTTONVILLE A | 7 | 3 | 9 | 21.25 | 0 | 3.25
4402 | TORONTO BUTTONVILLE A | 7 | 2 | 10 | 28 | 0 | 10
4402 | TORONTO BUTTONVILLE A | 7 | 3 | 10 | 23.15 | 0 | 5.15
4403 | TORONTO BUTTONVILLE A | 7 | 2 | 11 | 29.6 | 0 | 11.6
4403 | TORONTO BUTTONVILLE A | 7 | 3 | 11 | 24.525 | 0 | 6.525
4404 | TORONTO BUTTONVILLE A | 7 | 2 | 12 | 31.5 | 0 | 13.5
4404 | TORONTO BUTTONVILLE A | 7 | 3 | 12 | 25.35 | 0 | 7.35
4405 | TORONTO BUTTONVILLE A | 7 | 2 | 13 | 32 | 0 | 14
4405 | TORONTO BUTTONVILLE A | 7 | 3 | 13 | 26.475 | 0 | 8.475
4406 | TORONTO BUTTONVILLE A | 7 | 2 | 14 | 32.1 | 0 | 14.1
4406 | TORONTO BUTTONVILLE A | 7 | 3 | 14 | 26.85 | 0 | 8.85
4407 | TORONTO BUTTONVILLE A | 7 | 2 | 15 | 32.5 | 0 | 14.5
4407 | TORONTO BUTTONVILLE A | 7 | 3 | 15 | 27.125 | 0 | 9.125
4408 | TORONTO BUTTONVILLE A | 7 | 2 | 16 | 33.1 | 0 | 15.1
4408 | TORONTO BUTTONVILLE A | 7 | 3 | 16 | 27.05 | 0 | 9.05
4409 | TORONTO BUTTONVILLE A | 7 | 2 | 17 | 32.5 | 0 | 14.5
4409 | TORONTO BUTTONVILLE A | 7 | 3 | 17 | 26.75 | 0 | 8.75
4410 | TORONTO BUTTONVILLE A | 7 | 2 | 18 | 31.8 | 0 | 13.8
4410 | TORONTO BUTTONVILLE A | 7 | 3 | 18 | 26.775 | 0 | 8.775
4411 | TORONTO BUTTONVILLE A | 7 | 2 | 19 | 30.9 | 0 | 12.9
4411 | TORONTO BUTTONVILLE A | 7 | 3 | 19 | 26.45 | 0 | 8.45
4412 | TORONTO BUTTONVILLE A | 7 | 2 | 20 | 29.9 | 0 | 11.9
4412 | TORONTO BUTTONVILLE A | 7 | 3 | 20 | 25.575 | 0 | 7.575
4413 | TORONTO BUTTONVILLE A | 7 | 2 | 21 | 28.7 | 0 | 10.7
4413 | TORONTO BUTTONVILLE A | 7 | 3 | 21 | 24.075 | 0 | 6.075
4414 | TORONTO BUTTONVILLE A | 7 | 2 | 22 | 27.5 | 0 | 9.5
4414 | TORONTO BUTTONVILLE A | 7 | 3 | 22 | 22.75 | 0 | 4.75
4415 | TORONTO BUTTONVILLE A | 7 | 2 | 23 | 26.4 | 0 | 8.4
4415 | TORONTO BUTTONVILLE A | 7 | 3 | 23 | 21.025 | 0 | 3.025
4416 | TORONTO BUTTONVILLE A | 7 | 2 | 24 | 25.1 | 0 | 7.1
4416 | TORONTO BUTTONVILLE A | 7 | 3 | 24 | 19.6 | 0 | 1.6
4417 | TORONTO BUTTONVILLE A | 7 | 3 | 1 | 24.6 | 0 | 6.6
4417 | TORONTO BUTTONVILLE A | 7 | 4 | 1 | 18.5 | 0 | 0.5
4418 | TORONTO BUTTONVILLE A | 7 | 3 | 2 | 24.4 | 0 | 6.4
4418 | TORONTO BUTTONVILLE A | 7 | 4 | 2 | 17.2 | 0 | 0
4419 | TORONTO BUTTONVILLE A | 7 | 3 | 3 | 23.6 | 0 | 5.6
4419 | TORONTO BUTTONVILLE A | 7 | 4 | 3 | 16.975 | 0 | 0
4420 | TORONTO BUTTONVILLE A | 7 | 3 | 4 | 23.1 | 0 | 5.1
4420 | TORONTO BUTTONVILLE A | 7 | 4 | 4 | 16.65 | 0 | 0
4421 | TORONTO BUTTONVILLE A | 7 | 3 | 5 | 22.6 | 0 | 4.6
4421 | TORONTO BUTTONVILLE A | 7 | 4 | 5 | 16 | 0 | 0
4422 | TORONTO BUTTONVILLE A | 7 | 3 | 6 | 21.9 | 0 | 3.9
4422 | TORONTO BUTTONVILLE A | 7 | 4 | 6 | 16.125 | 0 | 0
4423 | TORONTO BUTTONVILLE A | 7 | 3 | 7 | 22.3 | 0 | 4.3
4423 | TORONTO BUTTONVILLE A | 7 | 4 | 7 | 18.05 | 0 | 0.05
4424 | TORONTO BUTTONVILLE A | 7 | 3 | 8 | 23.5 | 0 | 5.5
4424 | TORONTO BUTTONVILLE A | 7 | 4 | 8 | 20.4 | 0 | 2.4
4425 | TORONTO BUTTONVILLE A | 7 | 3 | 9 | 25 | 0 | 7
4425 | TORONTO BUTTONVILLE A | 7 | 4 | 9 | 22.175 | 0 | 4.175
4426 | TORONTO BUTTONVILLE A | 7 | 3 | 10 | 26.9 | 0 | 8.9
4426 | TORONTO BUTTONVILLE A | 7 | 4 | 10 | 23.85 | 0 | 5.85
4427 | TORONTO BUTTONVILLE A | 7 | 3 | 11 | 27.6 | 0 | 9.6
4427 | TORONTO BUTTONVILLE A | 7 | 4 | 11 | 25.025 | 0 | 7.025
4428 | TORONTO BUTTONVILLE A | 7 | 3 | 12 | 28.8 | 0 | 10.8
4428 | TORONTO BUTTONVILLE A | 7 | 4 | 12 | 25.65 | 0 | 7.65
4429 | TORONTO BUTTONVILLE A | 7 | 3 | 13 | 29.1 | 0 | 11.1
4429 | TORONTO BUTTONVILLE A | 7 | 4 | 13 | 26.05 | 0 | 8.05
4430 | TORONTO BUTTONVILLE A | 7 | 3 | 14 | 29.6 | 0 | 11.6
4430 | TORONTO BUTTONVILLE A | 7 | 4 | 14 | 26.55 | 0 | 8.55
4431 | TORONTO BUTTONVILLE A | 7 | 3 | 15 | 30.5 | 0 | 12.5
4431 | TORONTO BUTTONVILLE A | 7 | 4 | 15 | 27.275 | 0 | 9.275
4432 | TORONTO BUTTONVILLE A | 7 | 3 | 16 | 30.2 | 0 | 12.2
4432 | TORONTO BUTTONVILLE A | 7 | 4 | 16 | 27.525 | 0 | 9.525
4433 | TORONTO BUTTONVILLE A | 7 | 3 | 17 | 30.6 | 0 | 12.6
4433 | TORONTO BUTTONVILLE A | 7 | 4 | 17 | 27.6 | 0 | 9.6
4434 | TORONTO BUTTONVILLE A | 7 | 3 | 18 | 29.8 | 0 | 11.8
4434 | TORONTO BUTTONVILLE A | 7 | 4 | 18 | 27.275 | 0 | 9.275
4435 | TORONTO BUTTONVILLE A | 7 | 3 | 19 | 29 | 0 | 11
4435 | TORONTO BUTTONVILLE A | 7 | 4 | 19 | 26.825 | 0 | 8.825
4436 | TORONTO BUTTONVILLE A | 7 | 3 | 20 | 28 | 0 | 10
4436 | TORONTO BUTTONVILLE A | 7 | 4 | 20 | 25.55 | 0 | 7.55
4437 | TORONTO BUTTONVILLE A | 7 | 3 | 21 | 26.2 | 0 | 8.2
4437 | TORONTO BUTTONVILLE A | 7 | 4 | 21 | 23.925 | 0 | 5.925
4438 | TORONTO BUTTONVILLE A | 7 | 3 | 22 | 25 | 0 | 7
4438 | TORONTO BUTTONVILLE A | 7 | 4 | 22 | 22.9 | 0 | 4.9
4439 | TORONTO BUTTONVILLE A | 7 | 3 | 23 | 24.1 | 0 | 6.1
4439 | TORONTO BUTTONVILLE A | 7 | 4 | 23 | 21.6 | 0 | 3.6
4440 | TORONTO BUTTONVILLE A | 7 | 3 | 24 | 23.5 | 0 | 5.5
4440 | TORONTO BUTTONVILLE A | 7 | 4 | 24 | 20.925 | 0 | 2.925
4441 | TORONTO BUTTONVILLE A | 7 | 4 | 1 | 22.5 | 0 | 4.5
4441 | TORONTO BUTTONVILLE A | 7 | 5 | 1 | 19.75 | 0 | 1.75
4442 | TORONTO BUTTONVILLE A | 7 | 4 | 2 | 22.2 | 0 | 4.2
4442 | TORONTO BUTTONVILLE A | 7 | 5 | 2 | 19.325 | 0 | 1.325
4443 | TORONTO BUTTONVILLE A | 7 | 4 | 3 | 21.3 | 0 | 3.3
4443 | TORONTO BUTTONVILLE A | 7 | 5 | 3 | 18.825 | 0 | 0.825
4444 | TORONTO BUTTONVILLE A | 7 | 4 | 4 | 20.9 | 0 | 2.9
4444 | TORONTO BUTTONVILLE A | 7 | 5 | 4 | 18.3 | 0 | 0.3
4445 | TORONTO BUTTONVILLE A | 7 | 4 | 5 | 20.4 | 0 | 2.4
4445 | TORONTO BUTTONVILLE A | 7 | 5 | 5 | 18.1 | 0 | 0.1
4446 | TORONTO BUTTONVILLE A | 7 | 4 | 6 | 19.7 | 0 | 1.7
4446 | TORONTO BUTTONVILLE A | 7 | 5 | 6 | 18.225 | 0 | 0.225
4447 | TORONTO BUTTONVILLE A | 7 | 4 | 7 | 20.8 | 0 | 2.8
4447 | TORONTO BUTTONVILLE A | 7 | 5 | 7 | 19.8 | 0 | 1.8
4448 | TORONTO BUTTONVILLE A | 7 | 4 | 8 | 22.3 | 0 | 4.3
4448 | TORONTO BUTTONVILLE A | 7 | 5 | 8 | 22.175 | 0 | 4.175
4449 | TORONTO BUTTONVILLE A | 7 | 4 | 9 | 24.1 | 0 | 6.1
4449 | TORONTO BUTTONVILLE A | 7 | 5 | 9 | 24.1 | 0 | 6.1
4450 | TORONTO BUTTONVILLE A | 7 | 4 | 10 | 25.9 | 0 | 7.9
4450 | TORONTO BUTTONVILLE A | 7 | 5 | 10 | 26.1 | 0 | 8.1
4451 | TORONTO BUTTONVILLE A | 7 | 4 | 11 | 27.4 | 0 | 9.4
4451 | TORONTO BUTTONVILLE A | 7 | 5 | 11 | 27.55 | 0 | 9.55
4452 | TORONTO BUTTONVILLE A | 7 | 4 | 12 | 28.1 | 0 | 10.1
4452 | TORONTO BUTTONVILLE A | 7 | 5 | 12 | 28.5 | 0 | 10.5
4453 | TORONTO BUTTONVILLE A | 7 | 4 | 13 | 28.9 | 0 | 10.9
4453 | TORONTO BUTTONVILLE A | 7 | 5 | 13 | 28.775 | 0 | 10.775
4454 | TORONTO BUTTONVILLE A | 7 | 4 | 14 | 29.3 | 0 | 11.3
4454 | TORONTO BUTTONVILLE A | 7 | 5 | 14 | 29.15 | 0 | 11.15
4455 | TORONTO BUTTONVILLE A | 7 | 4 | 15 | 30.3 | 0 | 12.3
4455 | TORONTO BUTTONVILLE A | 7 | 5 | 15 | 29.2 | 0 | 11.2
4456 | TORONTO BUTTONVILLE A | 7 | 4 | 16 | 30.2 | 0 | 12.2
4456 | TORONTO BUTTONVILLE A | 7 | 5 | 16 | 30.075 | 0 | 12.075
4457 | TORONTO BUTTONVILLE A | 7 | 4 | 17 | 30.4 | 0 | 12.4
4457 | TORONTO BUTTONVILLE A | 7 | 5 | 17 | 29.35 | 0 | 11.35
4458 | TORONTO BUTTONVILLE A | 7 | 4 | 18 | 30.4 | 0 | 12.4
4458 | TORONTO BUTTONVILLE A | 7 | 5 | 18 | 27 | 0 | 9
4459 | TORONTO BUTTONVILLE A | 7 | 4 | 19 | 29.7 | 0 | 11.7
4459 | TORONTO BUTTONVILLE A | 7 | 5 | 19 | 27.675 | 0 | 9.675
4460 | TORONTO BUTTONVILLE A | 7 | 4 | 20 | 27.8 | 0 | 9.8
4460 | TORONTO BUTTONVILLE A | 7 | 5 | 20 | 24.375 | 0 | 6.375
4461 | TORONTO BUTTONVILLE A | 7 | 4 | 21 | 25.6 | 0 | 7.6
4461 | TORONTO BUTTONVILLE A | 7 | 5 | 21 | 22.975 | 0 | 4.975
4462 | TORONTO BUTTONVILLE A | 7 | 4 | 22 | 23.9 | 0 | 5.9
4462 | TORONTO BUTTONVILLE A | 7 | 5 | 22 | 22.75 | 0 | 4.75
4463 | TORONTO BUTTONVILLE A | 7 | 4 | 23 | 23.4 | 0 | 5.4
4463 | TORONTO BUTTONVILLE A | 7 | 5 | 23 | 22.325 | 0 | 4.325
4464 | TORONTO BUTTONVILLE A | 7 | 4 | 24 | 21.6 | 0 | 3.6
4464 | TORONTO BUTTONVILLE A | 7 | 5 | 24 | 21.9 | 0 | 3.9
4465 | TORONTO BUTTONVILLE A | 7 | 5 | 1 | 21.7 | 0 | 3.7
4465 | TORONTO BUTTONVILLE A | 7 | 6 | 1 | 21.2 | 0 | 3.2
4466 | TORONTO BUTTONVILLE A | 7 | 5 | 2 | 20.8 | 0 | 2.8
4466 | TORONTO BUTTONVILLE A | 7 | 6 | 2 | 20.825 | 0 | 2.825
4467 | TORONTO BUTTONVILLE A | 7 | 5 | 3 | 19.6 | 0 | 1.6
4467 | TORONTO BUTTONVILLE A | 7 | 6 | 3 | 20.5 | 0 | 2.5
4468 | TORONTO BUTTONVILLE A | 7 | 5 | 4 | 19.6 | 0 | 1.6
4468 | TORONTO BUTTONVILLE A | 7 | 6 | 4 | 20.175 | 0 | 2.175
4469 | TORONTO BUTTONVILLE A | 7 | 5 | 5 | 19 | 0 | 1
4469 | TORONTO BUTTONVILLE A | 7 | 6 | 5 | 19.575 | 0 | 1.575
4470 | TORONTO BUTTONVILLE A | 7 | 5 | 6 | 17.6 | 0 | 0
4470 | TORONTO BUTTONVILLE A | 7 | 6 | 6 | 19.575 | 0 | 1.575
4471 | TORONTO BUTTONVILLE A | 7 | 5 | 7 | 19.9 | 0 | 1.9
4471 | TORONTO BUTTONVILLE A | 7 | 6 | 7 | 20.625 | 0 | 2.625
4472 | TORONTO BUTTONVILLE A | 7 | 5 | 8 | 22.4 | 0 | 4.4
4472 | TORONTO BUTTONVILLE A | 7 | 6 | 8 | 22.35 | 0 | 4.35
4473 | TORONTO BUTTONVILLE A | 7 | 5 | 9 | 24.1 | 0 | 6.1
4473 | TORONTO BUTTONVILLE A | 7 | 6 | 9 | 23.35 | 0 | 5.35
4474 | TORONTO BUTTONVILLE A | 7 | 5 | 10 | 26.4 | 0 | 8.4
4474 | TORONTO BUTTONVILLE A | 7 | 6 | 10 | 24.65 | 0 | 6.65
4475 | TORONTO BUTTONVILLE A | 7 | 5 | 11 | 28.2 | 0 | 10.2
4475 | TORONTO BUTTONVILLE A | 7 | 6 | 11 | 25.7 | 0 | 7.7
4476 | TORONTO BUTTONVILLE A | 7 | 5 | 12 | 29 | 0 | 11
4476 | TORONTO BUTTONVILLE A | 7 | 6 | 12 | 26.475 | 0 | 8.475
4477 | TORONTO BUTTONVILLE A | 7 | 5 | 13 | 30.2 | 0 | 12.2
4477 | TORONTO BUTTONVILLE A | 7 | 6 | 13 | 27.025 | 0 | 9.025
4478 | TORONTO BUTTONVILLE A | 7 | 5 | 14 | 30.6 | 0 | 12.6
4478 | TORONTO BUTTONVILLE A | 7 | 6 | 14 | 27.45 | 0 | 9.45
4479 | TORONTO BUTTONVILLE A | 7 | 5 | 15 | 30.5 | 0 | 12.5
4479 | TORONTO BUTTONVILLE A | 7 | 6 | 15 | 28.1 | 0 | 10.1
4480 | TORONTO BUTTONVILLE A | 7 | 5 | 16 | 31.4 | 0 | 13.4
4480 | TORONTO BUTTONVILLE A | 7 | 6 | 16 | 28.225 | 0 | 10.225
4481 | TORONTO BUTTONVILLE A | 7 | 5 | 17 | 30.5 | 0 | 12.5
4481 | TORONTO BUTTONVILLE A | 7 | 6 | 17 | 27.8 | 0 | 9.8
4482 | TORONTO BUTTONVILLE A | 7 | 5 | 18 | 30.2 | 0 | 12.2
4482 | TORONTO BUTTONVILLE A | 7 | 6 | 18 | 27.625 | 0 | 9.625
4483 | TORONTO BUTTONVILLE A | 7 | 5 | 19 | 29.7 | 0 | 11.7
4483 | TORONTO BUTTONVILLE A | 7 | 6 | 19 | 26.7 | 0 | 8.7
4484 | TORONTO BUTTONVILLE A | 7 | 5 | 20 | 28.5 | 0 | 10.5
4484 | TORONTO BUTTONVILLE A | 7 | 6 | 20 | 25.575 | 0 | 7.575
4485 | TORONTO BUTTONVILLE A | 7 | 5 | 21 | 26.9 | 0 | 8.9
4485 | TORONTO BUTTONVILLE A | 7 | 6 | 21 | 24.625 | 0 | 6.625
4486 | TORONTO BUTTONVILLE A | 7 | 5 | 22 | 25.6 | 0 | 7.6
4486 | TORONTO BUTTONVILLE A | 7 | 6 | 22 | 23.425 | 0 | 5.425
4487 | TORONTO BUTTONVILLE A | 7 | 5 | 23 | 24.2 | 0 | 6.2
4487 | TORONTO BUTTONVILLE A | 7 | 6 | 23 | 21.775 | 0 | 3.775
4488 | TORONTO BUTTONVILLE A | 7 | 5 | 24 | 23 | 0 | 5
4488 | TORONTO BUTTONVILLE A | 7 | 6 | 24 | 22.9667 | 0 | 4.9667
4489 | TORONTO BUTTONVILLE A | 7 | 6 | 1 | 21.9 | 0 | 3.9
4489 | TORONTO BUTTONVILLE A | 7 | 7 | 1 | 22.6333 | 0 | 4.6333
4490 | TORONTO BUTTONVILLE A | 7 | 6 | 2 | 22.5 | 0 | 4.5
4490 | TORONTO BUTTONVILLE A | 7 | 7 | 2 | 21.8667 | 0 | 3.8667
4491 | TORONTO BUTTONVILLE A | 7 | 6 | 3 | 21.9 | 0 | 3.9
4491 | TORONTO BUTTONVILLE A | 7 | 7 | 3 | 19.6 | 0 | 1.6
4492 | TORONTO BUTTONVILLE A | 7 | 6 | 4 | 21.5 | 0 | 3.5
4492 | TORONTO BUTTONVILLE A | 7 | 7 | 4 | 18.85 | 0 | 0.85
4493 | TORONTO BUTTONVILLE A | 7 | 6 | 5 | 21 | 0 | 3
4493 | TORONTO BUTTONVILLE A | 7 | 7 | 5 | 18.2 | 0 | 0.2
4494 | TORONTO BUTTONVILLE A | 7 | 6 | 6 | 19.1 | 0 | 1.1
4494 | TORONTO BUTTONVILLE A | 7 | 7 | 6 | 18.075 | 0 | 0.075
4495 | TORONTO BUTTONVILLE A | 7 | 6 | 7 | 21.3 | 0 | 3.3
4495 | TORONTO BUTTONVILLE A | 7 | 7 | 7 | 18.675 | 0 | 0.675
4496 | TORONTO BUTTONVILLE A | 7 | 6 | 8 | 23.8 | 0 | 5.8
4496 | TORONTO BUTTONVILLE A | 7 | 7 | 8 | 19.975 | 0 | 1.975
4497 | TORONTO BUTTONVILLE A | 7 | 6 | 9 | 25.2 | 0 | 7.2
4497 | TORONTO BUTTONVILLE A | 7 | 7 | 9 | 20.825 | 0 | 2.825
4498 | TORONTO BUTTONVILLE A | 7 | 6 | 10 | 26.5 | 0 | 8.5
4498 | TORONTO BUTTONVILLE A | 7 | 7 | 10 | 21.55 | 0 | 3.55
4499 | TORONTO BUTTONVILLE A | 7 | 6 | 11 | 27.6 | 0 | 9.6
4499 | TORONTO BUTTONVILLE A | 7 | 7 | 11 | 22.2 | 0 | 4.2
4500 | TORONTO BUTTONVILLE A | 7 | 6 | 12 | 29.2 | 0 | 11.2
4500 | TORONTO BUTTONVILLE A | 7 | 7 | 12 | 22.625 | 0 | 4.625
4501 | TORONTO BUTTONVILLE A | 7 | 6 | 13 | 28.7 | 0 | 10.7
4501 | TORONTO BUTTONVILLE A | 7 | 7 | 13 | 23.075 | 0 | 5.075
4502 | TORONTO BUTTONVILLE A | 7 | 6 | 14 | 29.5 | 0 | 11.5
4502 | TORONTO BUTTONVILLE A | 7 | 7 | 14 | 23.75 | 0 | 5.75
4503 | TORONTO BUTTONVILLE A | 7 | 6 | 15 | 29 | 0 | 11
4503 | TORONTO BUTTONVILLE A | 7 | 7 | 15 | 23.95 | 0 | 5.95
4504 | TORONTO BUTTONVILLE A | 7 | 6 | 16 | 30.3 | 0 | 12.3
4504 | TORONTO BUTTONVILLE A | 7 | 7 | 16 | 24.425 | 0 | 6.425
4505 | TORONTO BUTTONVILLE A | 7 | 6 | 17 | 29.3 | 0 | 11.3
4505 | TORONTO BUTTONVILLE A | 7 | 7 | 17 | 23.7 | 0 | 5.7
4506 | TORONTO BUTTONVILLE A | 7 | 6 | 18 | 28.8 | 0 | 10.8
4506 | TORONTO BUTTONVILLE A | 7 | 7 | 18 | 23.75 | 0 | 5.75
4507 | TORONTO BUTTONVILLE A | 7 | 6 | 19 | 28.2 | 0 | 10.2
4507 | TORONTO BUTTONVILLE A | 7 | 7 | 19 | 22.975 | 0 | 4.975
4508 | TORONTO BUTTONVILLE A | 7 | 6 | 20 | 27 | 0 | 9
4508 | TORONTO BUTTONVILLE A | 7 | 7 | 20 | 20.675 | 0 | 2.675
4509 | TORONTO BUTTONVILLE A | 7 | 6 | 21 | 25.5 | 0 | 7.5
4509 | TORONTO BUTTONVILLE A | 7 | 7 | 21 | 19.325 | 0 | 1.325
4510 | TORONTO BUTTONVILLE A | 7 | 6 | 22 | 24.2 | 0 | 6.2
4510 | TORONTO BUTTONVILLE A | 7 | 7 | 22 | 19.15 | 0 | 1.15
4511 | TORONTO BUTTONVILLE A | 7 | 6 | 23 | 23.6 | 0 | 5.6
4511 | TORONTO BUTTONVILLE A | 7 | 7 | 23 | 18.85 | 0 | 0.85
4512 | TORONTO BUTTONVILLE A | 7 | 6 | 24 | 22.5 | 0 | 4.5
4512 | TORONTO BUTTONVILLE A | 7 | 7 | 24 | 17.9 | 0 | 0
4513 | TORONTO BUTTONVILLE A | 7 | 7 | 1 | 21.3 | 0 | 3.3
4513 | TORONTO BUTTONVILLE A | 7 | 8 | 1 | 16.875 | 0 | 0
4514 | TORONTO BUTTONVILLE A | 7 | 7 | 2 | 20.9 | 0 | 2.9
4514 | TORONTO BUTTONVILLE A | 7 | 8 | 2 | 16.15 | 0 | 0
4515 | TORONTO BUTTONVILLE A | 7 | 7 | 3 | 20.2 | 0 | 2.2
4515 | TORONTO BUTTONVILLE A | 7 | 8 | 3 | 15.6 | 0 | 0
4516 | TORONTO BUTTONVILLE A | 7 | 7 | 4 | 20.2 | 0 | 2.2
4516 | TORONTO BUTTONVILLE A | 7 | 8 | 4 | 15.35 | 0 | 0
4517 | TORONTO BUTTONVILLE A | 7 | 7 | 5 | 20.1 | 0 | 2.1
4517 | TORONTO BUTTONVILLE A | 7 | 8 | 5 | 15.025 | 0 | 0
4518 | TORONTO BUTTONVILLE A | 7 | 7 | 6 | 19.4 | 0 | 1.4
4518 | TORONTO BUTTONVILLE A | 7 | 8 | 6 | 15 | 0 | 0
4519 | TORONTO BUTTONVILLE A | 7 | 7 | 7 | 21.6 | 0 | 3.6
4519 | TORONTO BUTTONVILLE A | 7 | 8 | 7 | 15.575 | 0 | 0
4520 | TORONTO BUTTONVILLE A | 7 | 7 | 8 | 24 | 0 | 6
4520 | TORONTO BUTTONVILLE A | 7 | 8 | 8 | 17.2 | 0 | 0
4521 | TORONTO BUTTONVILLE A | 7 | 7 | 9 | 26.2 | 0 | 8.2
4521 | TORONTO BUTTONVILLE A | 7 | 8 | 9 | 18.875 | 0 | 0.875
4522 | TORONTO BUTTONVILLE A | 7 | 7 | 10 | 28.7 | 0 | 10.7
4522 | TORONTO BUTTONVILLE A | 7 | 8 | 10 | 20.075 | 0 | 2.075
4523 | TORONTO BUTTONVILLE A | 7 | 7 | 11 | 30.5 | 0 | 12.5
4523 | TORONTO BUTTONVILLE A | 7 | 8 | 11 | 20.725 | 0 | 2.725
4524 | TORONTO BUTTONVILLE A | 7 | 7 | 12 | 32.1 | 0 | 14.1
4524 | TORONTO BUTTONVILLE A | 7 | 8 | 12 | 21.4 | 0 | 3.4
4525 | TORONTO BUTTONVILLE A | 7 | 7 | 13 | 32.7 | 0 | 14.7
4525 | TORONTO BUTTONVILLE A | 7 | 8 | 13 | 21.8 | 0 | 3.8
4526 | TORONTO BUTTONVILLE A | 7 | 7 | 14 | 33.2 | 0 | 15.2
4526 | TORONTO BUTTONVILLE A | 7 | 8 | 14 | 22.725 | 0 | 4.725
4527 | TORONTO BUTTONVILLE A | 7 | 7 | 15 | 33.4 | 0 | 15.4
4527 | TORONTO BUTTONVILLE A | 7 | 8 | 15 | 23.425 | 0 | 5.425
4528 | TORONTO BUTTONVILLE A | 7 | 7 | 16 | 33.6 | 0 | 15.6
4528 | TORONTO BUTTONVILLE A | 7 | 8 | 16 | 23.65 | 0 | 5.65
4529 | TORONTO BUTTONVILLE A | 7 | 7 | 17 | 33.1 | 0 | 15.1
4529 | TORONTO BUTTONVILLE A | 7 | 8 | 17 | 23.95 | 0 | 5.95
4530 | TORONTO BUTTONVILLE A | 7 | 7 | 18 | 32.2 | 0 | 14.2
4530 | TORONTO BUTTONVILLE A | 7 | 8 | 18 | 23.775 | 0 | 5.775
4531 | TORONTO BUTTONVILLE A | 7 | 7 | 19 | 31.4 | 0 | 13.4
4531 | TORONTO BUTTONVILLE A | 7 | 8 | 19 | 23.375 | 0 | 5.375
4532 | TORONTO BUTTONVILLE A | 7 | 7 | 20 | 30.4 | 0 | 12.4
4532 | TORONTO BUTTONVILLE A | 7 | 8 | 20 | 22.425 | 0 | 4.425
4533 | TORONTO BUTTONVILLE A | 7 | 7 | 21 | 29.3 | 0 | 11.3
4533 | TORONTO BUTTONVILLE A | 7 | 8 | 21 | 21.15 | 0 | 3.15
4534 | TORONTO BUTTONVILLE A | 7 | 7 | 22 | 27.1 | 0 | 9.1
4534 | TORONTO BUTTONVILLE A | 7 | 8 | 22 | 20.55 | 0 | 2.55
4535 | TORONTO BUTTONVILLE A | 7 | 7 | 23 | 25.5 | 0 | 7.5
4535 | TORONTO BUTTONVILLE A | 7 | 8 | 23 | 19.7 | 0 | 1.7
4536 | TORONTO BUTTONVILLE A | 7 | 7 | 24 | 25.5 | 0 | 7.5
4536 | TORONTO BUTTONVILLE A | 7 | 8 | 24 | 18.7 | 0 | 0.7
4537 | TORONTO BUTTONVILLE A | 7 | 8 | 1 | 24.6 | 0 | 6.6
4537 | TORONTO BUTTONVILLE A | 7 | 9 | 1 | 18.025 | 0 | 0.025
4538 | TORONTO BUTTONVILLE A | 7 | 8 | 2 | 24.4 | 0 | 6.4
4538 | TORONTO BUTTONVILLE A | 7 | 9 | 2 | 17.325 | 0 | 0
4539 | TORONTO BUTTONVILLE A | 7 | 8 | 3 | 24.4 | 0 | 6.4
4539 | TORONTO BUTTONVILLE A | 7 | 9 | 3 | 17.225 | 0 | 0
4540 | TORONTO BUTTONVILLE A | 7 | 8 | 4 | 23.1 | 0 | 5.1
4540 | TORONTO BUTTONVILLE A | 7 | 9 | 4 | 16.75 | 0 | 0
4541 | TORONTO BUTTONVILLE A | 7 | 8 | 5 | 23.5 | 0 | 5.5
4541 | TORONTO BUTTONVILLE A | 7 | 9 | 5 | 16.3 | 0 | 0
4542 | TORONTO BUTTONVILLE A | 7 | 8 | 6 | 23.6 | 0 | 5.6
4542 | TORONTO BUTTONVILLE A | 7 | 9 | 6 | 16.075 | 0 | 0
4543 | TORONTO BUTTONVILLE A | 7 | 8 | 7 | 24.6 | 0 | 6.6
4543 | TORONTO BUTTONVILLE A | 7 | 9 | 7 | 17.2 | 0 | 0
4544 | TORONTO BUTTONVILLE A | 7 | 8 | 8 | 26.8 | 0 | 8.8
4544 | TORONTO BUTTONVILLE A | 7 | 9 | 8 | 18.8 | 0 | 0.8
4545 | TORONTO BUTTONVILLE A | 7 | 8 | 9 | 28.4 | 0 | 10.4
4545 | TORONTO BUTTONVILLE A | 7 | 9 | 9 | 20.075 | 0 | 2.075
4546 | TORONTO BUTTONVILLE A | 7 | 8 | 10 | 28.7 | 0 | 10.7
4546 | TORONTO BUTTONVILLE A | 7 | 9 | 10 | 21.5 | 0 | 3.5
4547 | TORONTO BUTTONVILLE A | 7 | 8 | 11 | 30.2 | 0 | 12.2
4547 | TORONTO BUTTONVILLE A | 7 | 9 | 11 | 23.05 | 0 | 5.05
4548 | TORONTO BUTTONVILLE A | 7 | 8 | 12 | 30.9 | 0 | 12.9
4548 | TORONTO BUTTONVILLE A | 7 | 9 | 12 | 24.375 | 0 | 6.375
4549 | TORONTO BUTTONVILLE A | 7 | 8 | 13 | 31.8 | 0 | 13.8
4549 | TORONTO BUTTONVILLE A | 7 | 9 | 13 | 24.825 | 0 | 6.825
4550 | TORONTO BUTTONVILLE A | 7 | 8 | 14 | 31 | 0 | 13
4550 | TORONTO BUTTONVILLE A | 7 | 9 | 14 | 25.525 | 0 | 7.525
4551 | TORONTO BUTTONVILLE A | 7 | 8 | 15 | 31.2 | 0 | 13.2
4551 | TORONTO BUTTONVILLE A | 7 | 9 | 15 | 26.025 | 0 | 8.025
4552 | TORONTO BUTTONVILLE A | 7 | 8 | 16 | 30.4 | 0 | 12.4
4552 | TORONTO BUTTONVILLE A | 7 | 9 | 16 | 25.8 | 0 | 7.8
4553 | TORONTO BUTTONVILLE A | 7 | 8 | 17 | 31.9 | 0 | 13.9
4553 | TORONTO BUTTONVILLE A | 7 | 9 | 17 | 25.7 | 0 | 7.7
4554 | TORONTO BUTTONVILLE A | 7 | 8 | 18 | 32.1 | 0 | 14.1
4554 | TORONTO BUTTONVILLE A | 7 | 9 | 18 | 25.55 | 0 | 7.55
4555 | TORONTO BUTTONVILLE A | 7 | 8 | 19 | 31.7 | 0 | 13.7
4555 | TORONTO BUTTONVILLE A | 7 | 9 | 19 | 24.925 | 0 | 6.925
4556 | TORONTO BUTTONVILLE A | 7 | 8 | 20 | 29.7 | 0 | 11.7
4556 | TORONTO BUTTONVILLE A | 7 | 9 | 20 | 24.025 | 0 | 6.025
4557 | TORONTO BUTTONVILLE A | 7 | 8 | 21 | 29.5 | 0 | 11.5
4557 | TORONTO BUTTONVILLE A | 7 | 9 | 21 | 23.275 | 0 | 5.275
4558 | TORONTO BUTTONVILLE A | 7 | 8 | 22 | 28.1 | 0 | 10.1
4558 | TORONTO BUTTONVILLE A | 7 | 9 | 22 | 22.125 | 0 | 4.125
4559 | TORONTO BUTTONVILLE A | 7 | 8 | 23 | 26.4 | 0 | 8.4
4559 | TORONTO BUTTONVILLE A | 7 | 9 | 23 | 20.05 | 0 | 2.05
4560 | TORONTO BUTTONVILLE A | 7 | 8 | 24 | 25.8 | 0 | 7.8
4560 | TORONTO BUTTONVILLE A | 7 | 9 | 24 | 19.275 | 0 | 1.275
4561 | TORONTO BUTTONVILLE A | 7 | 9 | 1 | 23.9 | 0 | 5.9
4561 | TORONTO BUTTONVILLE A | 7 | 10 | 1 | 18.475 | 0 | 0.475
4562 | TORONTO BUTTONVILLE A | 7 | 9 | 2 | 24.1 | 0 | 6.1
4562 | TORONTO BUTTONVILLE A | 7 | 10 | 2 | 18 | 0 | 0
4563 | TORONTO BUTTONVILLE A | 7 | 9 | 3 | 23.1 | 0 | 5.1
4563 | TORONTO BUTTONVILLE A | 7 | 10 | 3 | 17.675 | 0 | 0
4564 | TORONTO BUTTONVILLE A | 7 | 9 | 4 | 22.7 | 0 | 4.7
4564 | TORONTO BUTTONVILLE A | 7 | 10 | 4 | 16.95 | 0 | 0
4565 | TORONTO BUTTONVILLE A | 7 | 9 | 5 | 22.3 | 0 | 4.3
4565 | TORONTO BUTTONVILLE A | 7 | 10 | 5 | 16.975 | 0 | 0
4566 | TORONTO BUTTONVILLE A | 7 | 9 | 6 | 21.5 | 0 | 3.5
4566 | TORONTO BUTTONVILLE A | 7 | 10 | 6 | 17.05 | 0 | 0
4567 | TORONTO BUTTONVILLE A | 7 | 9 | 7 | 23.5 | 0 | 5.5
4567 | TORONTO BUTTONVILLE A | 7 | 10 | 7 | 17.725 | 0 | 0
4568 | TORONTO BUTTONVILLE A | 7 | 9 | 8 | 25.2 | 0 | 7.2
4568 | TORONTO BUTTONVILLE A | 7 | 10 | 8 | 19.175 | 0 | 1.175
4569 | TORONTO BUTTONVILLE A | 7 | 9 | 9 | 27.6 | 0 | 9.6
4569 | TORONTO BUTTONVILLE A | 7 | 10 | 9 | 21.45 | 0 | 3.45
4570 | TORONTO BUTTONVILLE A | 7 | 9 | 10 | 29.3 | 0 | 11.3
4570 | TORONTO BUTTONVILLE A | 7 | 10 | 10 | 22.975 | 0 | 4.975
4571 | TORONTO BUTTONVILLE A | 7 | 9 | 11 | 31.2 | 0 | 13.2
4571 | TORONTO BUTTONVILLE A | 7 | 10 | 11 | 24.45 | 0 | 6.45
4572 | TORONTO BUTTONVILLE A | 7 | 9 | 12 | 31.9 | 0 | 13.9
4572 | TORONTO BUTTONVILLE A | 7 | 10 | 12 | 25.325 | 0 | 7.325
4573 | TORONTO BUTTONVILLE A | 7 | 9 | 13 | 33.2 | 0 | 15.2
4573 | TORONTO BUTTONVILLE A | 7 | 10 | 13 | 26.125 | 0 | 8.125
4574 | TORONTO BUTTONVILLE A | 7 | 9 | 14 | 33.7 | 0 | 15.7
4574 | TORONTO BUTTONVILLE A | 7 | 10 | 14 | 26.4 | 0 | 8.4
4575 | TORONTO BUTTONVILLE A | 7 | 9 | 15 | 33.7 | 0 | 15.7
4575 | TORONTO BUTTONVILLE A | 7 | 10 | 15 | 26.35 | 0 | 8.35
4576 | TORONTO BUTTONVILLE A | 7 | 9 | 16 | 34.2 | 0 | 16.2
4576 | TORONTO BUTTONVILLE A | 7 | 10 | 16 | 25.9 | 0 | 7.9
4577 | TORONTO BUTTONVILLE A | 7 | 9 | 17 | 34.2 | 0 | 16.2
4577 | TORONTO BUTTONVILLE A | 7 | 10 | 17 | 26.05 | 0 | 8.05
4578 | TORONTO BUTTONVILLE A | 7 | 9 | 18 | 33.9 | 0 | 15.9
4578 | TORONTO BUTTONVILLE A | 7 | 10 | 18 | 25.55 | 0 | 7.55
4579 | TORONTO BUTTONVILLE A | 7 | 9 | 19 | 32.9 | 0 | 14.9
4579 | TORONTO BUTTONVILLE A | 7 | 10 | 19 | 24.525 | 0 | 6.525
4580 | TORONTO BUTTONVILLE A | 7 | 9 | 20 | 30.6 | 0 | 12.6
4580 | TORONTO BUTTONVILLE A | 7 | 10 | 20 | 23.55 | 0 | 5.55
4581 | TORONTO BUTTONVILLE A | 7 | 9 | 21 | 27.6 | 0 | 9.6
4581 | TORONTO BUTTONVILLE A | 7 | 10 | 21 | 22.225 | 0 | 4.225
4582 | TORONTO BUTTONVILLE A | 7 | 9 | 22 | 27.1 | 0 | 9.1
4582 | TORONTO BUTTONVILLE A | 7 | 10 | 22 | 20.95 | 0 | 2.95
4583 | TORONTO BUTTONVILLE A | 7 | 9 | 23 | 26.6 | 0 | 8.6
4583 | TORONTO BUTTONVILLE A | 7 | 10 | 23 | 20.25 | 0 | 2.25
4584 | TORONTO BUTTONVILLE A | 7 | 9 | 24 | 25.9 | 0 | 7.9
4584 | TORONTO BUTTONVILLE A | 7 | 10 | 24 | 19.725 | 0 | 1.725
4585 | TORONTO BUTTONVILLE A | 7 | 10 | 1 | 25.8 | 0 | 7.8
4585 | TORONTO BUTTONVILLE A | 7 | 11 | 1 | 19.25 | 0 | 1.25
4586 | TORONTO BUTTONVILLE A | 7 | 10 | 2 | 26 | 0 | 8
4586 | TORONTO BUTTONVILLE A | 7 | 11 | 2 | 18.65 | 0 | 0.65
4587 | TORONTO BUTTONVILLE A | 7 | 10 | 3 | 25.3 | 0 | 7.3
4587 | TORONTO BUTTONVILLE A | 7 | 11 | 3 | 17.65 | 0 | 0
4588 | TORONTO BUTTONVILLE A | 7 | 10 | 4 | 25.2 | 0 | 7.2
4588 | TORONTO BUTTONVILLE A | 7 | 11 | 4 | 17.625 | 0 | 0
4589 | TORONTO BUTTONVILLE A | 7 | 10 | 5 | 24.4 | 0 | 6.4
4589 | TORONTO BUTTONVILLE A | 7 | 11 | 5 | 17.375 | 0 | 0
4590 | TORONTO BUTTONVILLE A | 7 | 10 | 6 | 24.3 | 0 | 6.3
4590 | TORONTO BUTTONVILLE A | 7 | 11 | 6 | 16.95 | 0 | 0
4591 | TORONTO BUTTONVILLE A | 7 | 10 | 7 | 24.6 | 0 | 6.6
4591 | TORONTO BUTTONVILLE A | 7 | 11 | 7 | 18.425 | 0 | 0.425
4592 | TORONTO BUTTONVILLE A | 7 | 10 | 8 | 25.7 | 0 | 7.7
4592 | TORONTO BUTTONVILLE A | 7 | 11 | 8 | 19.825 | 0 | 1.825
4593 | TORONTO BUTTONVILLE A | 7 | 10 | 9 | 27.6 | 0 | 9.6
4593 | TORONTO BUTTONVILLE A | 7 | 11 | 9 | 21.125 | 0 | 3.125
4594 | TORONTO BUTTONVILLE A | 7 | 10 | 10 | 28.9 | 0 | 10.9
4594 | TORONTO BUTTONVILLE A | 7 | 11 | 10 | 22.575 | 0 | 4.575
4595 | TORONTO BUTTONVILLE A | 7 | 10 | 11 | 30.2 | 0 | 12.2
4595 | TORONTO BUTTONVILLE A | 7 | 11 | 11 | 23.425 | 0 | 5.425
4596 | TORONTO BUTTONVILLE A | 7 | 10 | 12 | 30.8 | 0 | 12.8
4596 | TORONTO BUTTONVILLE A | 7 | 11 | 12 | 24.05 | 0 | 6.05
4597 | TORONTO BUTTONVILLE A | 7 | 10 | 13 | 31.1 | 0 | 13.1
4597 | TORONTO BUTTONVILLE A | 7 | 11 | 13 | 25.45 | 0 | 7.45
4598 | TORONTO BUTTONVILLE A | 7 | 10 | 14 | 31.6 | 0 | 13.6
4598 | TORONTO BUTTONVILLE A | 7 | 11 | 14 | 25.525 | 0 | 7.525
4599 | TORONTO BUTTONVILLE A | 7 | 10 | 15 | 31.9 | 0 | 13.9
4599 | TORONTO BUTTONVILLE A | 7 | 11 | 15 | 25.55 | 0 | 7.55
4600 | TORONTO BUTTONVILLE A | 7 | 10 | 16 | 32 | 0 | 14
4600 | TORONTO BUTTONVILLE A | 7 | 11 | 16 | 25.725 | 0 | 7.725
4601 | TORONTO BUTTONVILLE A | 7 | 10 | 17 | 31.7 | 0 | 13.7
4601 | TORONTO BUTTONVILLE A | 7 | 11 | 17 | 25.475 | 0 | 7.475
4602 | TORONTO BUTTONVILLE A | 7 | 10 | 18 | 31.3 | 0 | 13.3
4602 | TORONTO BUTTONVILLE A | 7 | 11 | 18 | 25.15 | 0 | 7.15
4603 | TORONTO BUTTONVILLE A | 7 | 10 | 19 | 30.1 | 0 | 12.1
4603 | TORONTO BUTTONVILLE A | 7 | 11 | 19 | 24.725 | 0 | 6.725
4604 | TORONTO BUTTONVILLE A | 7 | 10 | 20 | 29.7 | 0 | 11.7
4604 | TORONTO BUTTONVILLE A | 7 | 11 | 20 | 24.1 | 0 | 6.1
4605 | TORONTO BUTTONVILLE A | 7 | 10 | 21 | 28.1 | 0 | 10.1
4605 | TORONTO BUTTONVILLE A | 7 | 11 | 21 | 22.325 | 0 | 4.325
4606 | TORONTO BUTTONVILLE A | 7 | 10 | 22 | 22 | 0 | 4
4606 | TORONTO BUTTONVILLE A | 7 | 11 | 22 | 20.85 | 0 | 2.85
4607 | TORONTO BUTTONVILLE A | 7 | 10 | 23 | 22.3 | 0 | 4.3
4607 | TORONTO BUTTONVILLE A | 7 | 11 | 23 | 20.075 | 0 | 2.075
4608 | TORONTO BUTTONVILLE A | 7 | 10 | 24 | 22.2 | 0 | 4.2
4608 | TORONTO BUTTONVILLE A | 7 | 11 | 24 | 19.375 | 0 | 1.375
4609 | TORONTO BUTTONVILLE A | 7 | 11 | 1 | 22.6 | 0 | 4.6
4609 | TORONTO BUTTONVILLE A | 7 | 12 | 1 | 18.675 | 0 | 0.675
4610 | TORONTO BUTTONVILLE A | 7 | 11 | 2 | 22 | 0 | 4
4610 | TORONTO BUTTONVILLE A | 7 | 12 | 2 | 18.525 | 0 | 0.525
4611 | TORONTO BUTTONVILLE A | 7 | 11 | 3 | 22.1 | 0 | 4.1
4611 | TORONTO BUTTONVILLE A | 7 | 12 | 3 | 18.325 | 0 | 0.325
4612 | TORONTO BUTTONVILLE A | 7 | 11 | 4 | 22.1 | 0 | 4.1
4612 | TORONTO BUTTONVILLE A | 7 | 12 | 4 | 18.3 | 0 | 0.3
4613 | TORONTO BUTTONVILLE A | 7 | 11 | 5 | 22.1 | 0 | 4.1
4613 | TORONTO BUTTONVILLE A | 7 | 12 | 5 | 18.125 | 0 | 0.125
4614 | TORONTO BUTTONVILLE A | 7 | 11 | 6 | 22.1 | 0 | 4.1
4614 | TORONTO BUTTONVILLE A | 7 | 12 | 6 | 18.125 | 0 | 0.125
4615 | TORONTO BUTTONVILLE A | 7 | 11 | 7 | 21.8 | 0 | 3.8
4615 | TORONTO BUTTONVILLE A | 7 | 12 | 7 | 18.725 | 0 | 0.725
4616 | TORONTO BUTTONVILLE A | 7 | 11 | 8 | 22.4 | 0 | 4.4
4616 | TORONTO BUTTONVILLE A | 7 | 12 | 8 | 20.275 | 0 | 2.275
4617 | TORONTO BUTTONVILLE A | 7 | 11 | 9 | 22.7 | 0 | 4.7
4617 | TORONTO BUTTONVILLE A | 7 | 12 | 9 | 21.575 | 0 | 3.575
4618 | TORONTO BUTTONVILLE A | 7 | 11 | 10 | 22.8 | 0 | 4.8
4618 | TORONTO BUTTONVILLE A | 7 | 12 | 10 | 22.825 | 0 | 4.825
4619 | TORONTO BUTTONVILLE A | 7 | 11 | 11 | 22.8 | 0 | 4.8
4619 | TORONTO BUTTONVILLE A | 7 | 12 | 11 | 23.5 | 0 | 5.5
4620 | TORONTO BUTTONVILLE A | 7 | 11 | 12 | 23.1 | 0 | 5.1
4620 | TORONTO BUTTONVILLE A | 7 | 12 | 12 | 24.3 | 0 | 6.3
4621 | TORONTO BUTTONVILLE A | 7 | 11 | 13 | 25 | 0 | 7
4621 | TORONTO BUTTONVILLE A | 7 | 12 | 13 | 24.375 | 0 | 6.375
4622 | TORONTO BUTTONVILLE A | 7 | 11 | 14 | 25.2 | 0 | 7.2
4622 | TORONTO BUTTONVILLE A | 7 | 12 | 14 | 24.325 | 0 | 6.325
4623 | TORONTO BUTTONVILLE A | 7 | 11 | 15 | 23.8 | 0 | 5.8
4623 | TORONTO BUTTONVILLE A | 7 | 12 | 15 | 24.575 | 0 | 6.575
4624 | TORONTO BUTTONVILLE A | 7 | 11 | 16 | 22.4 | 0 | 4.4
4624 | TORONTO BUTTONVILLE A | 7 | 12 | 16 | 24.675 | 0 | 6.675
4625 | TORONTO BUTTONVILLE A | 7 | 11 | 17 | 22.7 | 0 | 4.7
4625 | TORONTO BUTTONVILLE A | 7 | 12 | 17 | 24.8 | 0 | 6.8
4626 | TORONTO BUTTONVILLE A | 7 | 11 | 18 | 22 | 0 | 4
4626 | TORONTO BUTTONVILLE A | 7 | 12 | 18 | 24.725 | 0 | 6.725
4627 | TORONTO BUTTONVILLE A | 7 | 11 | 19 | 22.5 | 0 | 4.5
4627 | TORONTO BUTTONVILLE A | 7 | 12 | 19 | 24.275 | 0 | 6.275
4628 | TORONTO BUTTONVILLE A | 7 | 11 | 20 | 22.9 | 0 | 4.9
4628 | TORONTO BUTTONVILLE A | 7 | 12 | 20 | 23.575 | 0 | 5.575
4629 | TORONTO BUTTONVILLE A | 7 | 11 | 21 | 22.9 | 0 | 4.9
4629 | TORONTO BUTTONVILLE A | 7 | 12 | 21 | 22.85 | 0 | 4.85
4630 | TORONTO BUTTONVILLE A | 7 | 11 | 22 | 22.7 | 0 | 4.7
4630 | TORONTO BUTTONVILLE A | 7 | 12 | 22 | 22 | 0 | 4
4631 | TORONTO BUTTONVILLE A | 7 | 11 | 23 | 22.1 | 0 | 4.1
4631 | TORONTO BUTTONVILLE A | 7 | 12 | 23 | 21.15 | 0 | 3.15
4632 | TORONTO BUTTONVILLE A | 7 | 11 | 24 | 21.5 | 0 | 3.5
4632 | TORONTO BUTTONVILLE A | 7 | 12 | 24 | 20.725 | 0 | 2.725
4633 | TORONTO BUTTONVILLE A | 7 | 12 | 1 | 20.9 | 0 | 2.9
4633 | TORONTO BUTTONVILLE A | 7 | 13 | 1 | 20.35 | 0 | 2.35
4634 | TORONTO BUTTONVILLE A | 7 | 12 | 2 | 20.5 | 0 | 2.5
4634 | TORONTO BUTTONVILLE A | 7 | 13 | 2 | 20.05 | 0 | 2.05
4635 | TORONTO BUTTONVILLE A | 7 | 12 | 3 | 19.5 | 0 | 1.5
4635 | TORONTO BUTTONVILLE A | 7 | 13 | 3 | 19.5 | 0 | 1.5
4636 | TORONTO BUTTONVILLE A | 7 | 12 | 4 | 19 | 0 | 1
4636 | TORONTO BUTTONVILLE A | 7 | 13 | 4 | 19.1 | 0 | 1.1
4637 | TORONTO BUTTONVILLE A | 7 | 12 | 5 | 19 | 0 | 1
4637 | TORONTO BUTTONVILLE A | 7 | 13 | 5 | 18.825 | 0 | 0.825
4638 | TORONTO BUTTONVILLE A | 7 | 12 | 6 | 18.5 | 0 | 0.5
4638 | TORONTO BUTTONVILLE A | 7 | 13 | 6 | 18.325 | 0 | 0.325
4639 | TORONTO BUTTONVILLE A | 7 | 12 | 7 | 19 | 0 | 1
4639 | TORONTO BUTTONVILLE A | 7 | 13 | 7 | 18.7 | 0 | 0.7
4640 | TORONTO BUTTONVILLE A | 7 | 12 | 8 | 20.5 | 0 | 2.5
4640 | TORONTO BUTTONVILLE A | 7 | 13 | 8 | 19.875 | 0 | 1.875
4641 | TORONTO BUTTONVILLE A | 7 | 12 | 9 | 21.7 | 0 | 3.7
4641 | TORONTO BUTTONVILLE A | 7 | 13 | 9 | 21 | 0 | 3
4642 | TORONTO BUTTONVILLE A | 7 | 12 | 10 | 23.1 | 0 | 5.1
4642 | TORONTO BUTTONVILLE A | 7 | 13 | 10 | 22.15 | 0 | 4.15
4643 | TORONTO BUTTONVILLE A | 7 | 12 | 11 | 24.1 | 0 | 6.1
4643 | TORONTO BUTTONVILLE A | 7 | 13 | 11 | 23.175 | 0 | 5.175
4644 | TORONTO BUTTONVILLE A | 7 | 12 | 12 | 25.1 | 0 | 7.1
4644 | TORONTO BUTTONVILLE A | 7 | 13 | 12 | 23.575 | 0 | 5.575
4645 | TORONTO BUTTONVILLE A | 7 | 12 | 13 | 25.3 | 0 | 7.3
4645 | TORONTO BUTTONVILLE A | 7 | 13 | 13 | 24.35 | 0 | 6.35
4646 | TORONTO BUTTONVILLE A | 7 | 12 | 14 | 25.9 | 0 | 7.9
4646 | TORONTO BUTTONVILLE A | 7 | 13 | 14 | 24.675 | 0 | 6.675
4647 | TORONTO BUTTONVILLE A | 7 | 12 | 15 | 25.6 | 0 | 7.6
4647 | TORONTO BUTTONVILLE A | 7 | 13 | 15 | 24.625 | 0 | 6.625
4648 | TORONTO BUTTONVILLE A | 7 | 12 | 16 | 26.2 | 0 | 8.2
4648 | TORONTO BUTTONVILLE A | 7 | 13 | 16 | 23.3 | 0 | 5.3
4649 | TORONTO BUTTONVILLE A | 7 | 12 | 17 | 22 | 0 | 4
4649 | TORONTO BUTTONVILLE A | 7 | 13 | 17 | 22.85 | 0 | 4.85
4650 | TORONTO BUTTONVILLE A | 7 | 12 | 18 | 22.4 | 0 | 4.4
4650 | TORONTO BUTTONVILLE A | 7 | 13 | 18 | 23.8 | 0 | 5.8
4651 | TORONTO BUTTONVILLE A | 7 | 12 | 19 | 22.4 | 0 | 4.4
4651 | TORONTO BUTTONVILLE A | 7 | 13 | 19 | 23.975 | 0 | 5.975
4652 | TORONTO BUTTONVILLE A | 7 | 12 | 20 | 22.4 | 0 | 4.4
4652 | TORONTO BUTTONVILLE A | 7 | 13 | 20 | 23.95 | 0 | 5.95
4653 | TORONTO BUTTONVILLE A | 7 | 12 | 21 | 21.5 | 0 | 3.5
4653 | TORONTO BUTTONVILLE A | 7 | 13 | 21 | 22.925 | 0 | 4.925
4654 | TORONTO BUTTONVILLE A | 7 | 12 | 22 | 20.6 | 0 | 2.6
4654 | TORONTO BUTTONVILLE A | 7 | 13 | 22 | 21.75 | 0 | 3.75
4655 | TORONTO BUTTONVILLE A | 7 | 12 | 23 | 19.6 | 0 | 1.6
4655 | TORONTO BUTTONVILLE A | 7 | 13 | 23 | 21.675 | 0 | 3.675
4656 | TORONTO BUTTONVILLE A | 7 | 12 | 24 | 19.5 | 0 | 1.5
4656 | TORONTO BUTTONVILLE A | 7 | 13 | 24 | 21.325 | 0 | 3.325
4657 | TORONTO BUTTONVILLE A | 7 | 13 | 1 | 18.8 | 0 | 0.8
4657 | TORONTO BUTTONVILLE A | 7 | 14 | 1 | 20.95 | 0 | 2.95
4658 | TORONTO BUTTONVILLE A | 7 | 13 | 2 | 18.7 | 0 | 0.7
4658 | TORONTO BUTTONVILLE A | 7 | 14 | 2 | 19.95 | 0 | 1.95
4659 | TORONTO BUTTONVILLE A | 7 | 13 | 3 | 18.6 | 0 | 0.6
4659 | TORONTO BUTTONVILLE A | 7 | 14 | 3 | 20.025 | 0 | 2.025
4660 | TORONTO BUTTONVILLE A | 7 | 13 | 4 | 18.5 | 0 | 0.5
4660 | TORONTO BUTTONVILLE A | 7 | 14 | 4 | 19.575 | 0 | 1.575
4661 | TORONTO BUTTONVILLE A | 7 | 13 | 5 | 18.5 | 0 | 0.5
4661 | TORONTO BUTTONVILLE A | 7 | 14 | 5 | 19.675 | 0 | 1.675
4662 | TORONTO BUTTONVILLE A | 7 | 13 | 6 | 18.4 | 0 | 0.4
4662 | TORONTO BUTTONVILLE A | 7 | 14 | 6 | 19.35 | 0 | 1.35
4663 | TORONTO BUTTONVILLE A | 7 | 13 | 7 | 18.7 | 0 | 0.7
4663 | TORONTO BUTTONVILLE A | 7 | 14 | 7 | 19.725 | 0 | 1.725
4664 | TORONTO BUTTONVILLE A | 7 | 13 | 8 | 19.1 | 0 | 1.1
4664 | TORONTO BUTTONVILLE A | 7 | 14 | 8 | 20.45 | 0 | 2.45
4665 | TORONTO BUTTONVILLE A | 7 | 13 | 9 | 19.4 | 0 | 1.4
4665 | TORONTO BUTTONVILLE A | 7 | 14 | 9 | 21.3 | 0 | 3.3
4666 | TORONTO BUTTONVILLE A | 7 | 13 | 10 | 20.2 | 0 | 2.2
4666 | TORONTO BUTTONVILLE A | 7 | 14 | 10 | 21.9 | 0 | 3.9
4667 | TORONTO BUTTONVILLE A | 7 | 13 | 11 | 22.6 | 0 | 4.6
4667 | TORONTO BUTTONVILLE A | 7 | 14 | 11 | 23.225 | 0 | 5.225
4668 | TORONTO BUTTONVILLE A | 7 | 13 | 12 | 21.3 | 0 | 3.3
4668 | TORONTO BUTTONVILLE A | 7 | 14 | 12 | 23.875 | 0 | 5.875
4669 | TORONTO BUTTONVILLE A | 7 | 13 | 13 | 22.1 | 0 | 4.1
4669 | TORONTO BUTTONVILLE A | 7 | 14 | 13 | 24.875 | 0 | 6.875
4670 | TORONTO BUTTONVILLE A | 7 | 13 | 14 | 22.5 | 0 | 4.5
4670 | TORONTO BUTTONVILLE A | 7 | 14 | 14 | 25.8 | 0 | 7.8
4671 | TORONTO BUTTONVILLE A | 7 | 13 | 15 | 23 | 0 | 5
4671 | TORONTO BUTTONVILLE A | 7 | 14 | 15 | 26.325 | 0 | 8.325
4672 | TORONTO BUTTONVILLE A | 7 | 13 | 16 | 24.3 | 0 | 6.3
4672 | TORONTO BUTTONVILLE A | 7 | 14 | 16 | 26.775 | 0 | 8.775
4673 | TORONTO BUTTONVILLE A | 7 | 13 | 17 | 23.9 | 0 | 5.9
4673 | TORONTO BUTTONVILLE A | 7 | 14 | 17 | 26.575 | 0 | 8.575
4674 | TORONTO BUTTONVILLE A | 7 | 13 | 18 | 23.3 | 0 | 5.3
4674 | TORONTO BUTTONVILLE A | 7 | 14 | 18 | 26.475 | 0 | 8.475
4675 | TORONTO BUTTONVILLE A | 7 | 13 | 19 | 23.1 | 0 | 5.1
4675 | TORONTO BUTTONVILLE A | 7 | 14 | 19 | 25.5 | 0 | 7.5
4676 | TORONTO BUTTONVILLE A | 7 | 13 | 20 | 21.8 | 0 | 3.8
4676 | TORONTO BUTTONVILLE A | 7 | 14 | 20 | 23.975 | 0 | 5.975
4677 | TORONTO BUTTONVILLE A | 7 | 13 | 21 | 20.1 | 0 | 2.1
4677 | TORONTO BUTTONVILLE A | 7 | 14 | 21 | 22.625 | 0 | 4.625
4678 | TORONTO BUTTONVILLE A | 7 | 13 | 22 | 19.2 | 0 | 1.2
4678 | TORONTO BUTTONVILLE A | 7 | 14 | 22 | 21.5 | 0 | 3.5
4679 | TORONTO BUTTONVILLE A | 7 | 13 | 23 | 18.8 | 0 | 0.8
4679 | TORONTO BUTTONVILLE A | 7 | 14 | 23 | 20.8 | 0 | 2.8
4680 | TORONTO BUTTONVILLE A | 7 | 13 | 24 | 18.7 | 0 | 0.7
4680 | TORONTO BUTTONVILLE A | 7 | 14 | 24 | 20.2 | 0 | 2.2
4681 | TORONTO BUTTONVILLE A | 7 | 14 | 1 | 18.4 | 0 | 0.4
4681 | TORONTO BUTTONVILLE A | 7 | 15 | 1 | 19.725 | 0 | 1.725
4682 | TORONTO BUTTONVILLE A | 7 | 14 | 2 | 18 | 0 | 0
4682 | TORONTO BUTTONVILLE A | 7 | 15 | 2 | 18.925 | 0 | 0.925
4683 | TORONTO BUTTONVILLE A | 7 | 14 | 3 | 17.5 | 0 | 0
4683 | TORONTO BUTTONVILLE A | 7 | 15 | 3 | 18.225 | 0 | 0.225
4684 | TORONTO BUTTONVILLE A | 7 | 14 | 4 | 17.5 | 0 | 0
4684 | TORONTO BUTTONVILLE A | 7 | 15 | 4 | 18.025 | 0 | 0.025
4685 | TORONTO BUTTONVILLE A | 7 | 14 | 5 | 17.5 | 0 | 0
4685 | TORONTO BUTTONVILLE A | 7 | 15 | 5 | 17.45 | 0 | 0
4686 | TORONTO BUTTONVILLE A | 7 | 14 | 6 | 18 | 0 | 0
4686 | TORONTO BUTTONVILLE A | 7 | 15 | 6 | 17.675 | 0 | 0
4687 | TORONTO BUTTONVILLE A | 7 | 14 | 7 | 18.4 | 0 | 0.4
4687 | TORONTO BUTTONVILLE A | 7 | 15 | 7 | 18.975 | 0 | 0.975
4688 | TORONTO BUTTONVILLE A | 7 | 14 | 8 | 20 | 0 | 2
4688 | TORONTO BUTTONVILLE A | 7 | 15 | 8 | 20.575 | 0 | 2.575
4689 | TORONTO BUTTONVILLE A | 7 | 14 | 9 | 20.9 | 0 | 2.9
4689 | TORONTO BUTTONVILLE A | 7 | 15 | 9 | 22.45 | 0 | 4.45
4690 | TORONTO BUTTONVILLE A | 7 | 14 | 10 | 22.5 | 0 | 4.5
4690 | TORONTO BUTTONVILLE A | 7 | 15 | 10 | 23.45 | 0 | 5.45
4691 | TORONTO BUTTONVILLE A | 7 | 14 | 11 | 22.6 | 0 | 4.6
4691 | TORONTO BUTTONVILLE A | 7 | 15 | 11 | 24.85 | 0 | 6.85
4692 | TORONTO BUTTONVILLE A | 7 | 14 | 12 | 24.5 | 0 | 6.5
4692 | TORONTO BUTTONVILLE A | 7 | 15 | 12 | 26.05 | 0 | 8.05
4693 | TORONTO BUTTONVILLE A | 7 | 14 | 13 | 24.3 | 0 | 6.3
4693 | TORONTO BUTTONVILLE A | 7 | 15 | 13 | 26.525 | 0 | 8.525
4694 | TORONTO BUTTONVILLE A | 7 | 14 | 14 | 26.1 | 0 | 8.1
4694 | TORONTO BUTTONVILLE A | 7 | 15 | 14 | 26.925 | 0 | 8.925
4695 | TORONTO BUTTONVILLE A | 7 | 14 | 15 | 25.4 | 0 | 7.4
4695 | TORONTO BUTTONVILLE A | 7 | 15 | 15 | 28.175 | 0 | 10.175
4696 | TORONTO BUTTONVILLE A | 7 | 14 | 16 | 26 | 0 | 8
4696 | TORONTO BUTTONVILLE A | 7 | 15 | 16 | 28.2 | 0 | 10.2
4697 | TORONTO BUTTONVILLE A | 7 | 14 | 17 | 26 | 0 | 8
4697 | TORONTO BUTTONVILLE A | 7 | 15 | 17 | 28.25 | 0 | 10.25
4698 | TORONTO BUTTONVILLE A | 7 | 14 | 18 | 25.9 | 0 | 7.9
4698 | TORONTO BUTTONVILLE A | 7 | 15 | 18 | 28.075 | 0 | 10.075
4699 | TORONTO BUTTONVILLE A | 7 | 14 | 19 | 25.2 | 0 | 7.2
4699 | TORONTO BUTTONVILLE A | 7 | 15 | 19 | 27.6 | 0 | 9.6
4700 | TORONTO BUTTONVILLE A | 7 | 14 | 20 | 24.7 | 0 | 6.7
4700 | TORONTO BUTTONVILLE A | 7 | 15 | 20 | 25.3 | 0 | 7.3
4701 | TORONTO BUTTONVILLE A | 7 | 14 | 21 | 23.6 | 0 | 5.6
4701 | TORONTO BUTTONVILLE A | 7 | 15 | 21 | 23.65 | 0 | 5.65
4702 | TORONTO BUTTONVILLE A | 7 | 14 | 22 | 22.7 | 0 | 4.7
4702 | TORONTO BUTTONVILLE A | 7 | 15 | 22 | 22.725 | 0 | 4.725
4703 | TORONTO BUTTONVILLE A | 7 | 14 | 23 | 22 | 0 | 4
4703 | TORONTO BUTTONVILLE A | 7 | 15 | 23 | 22.15 | 0 | 4.15
4704 | TORONTO BUTTONVILLE A | 7 | 14 | 24 | 21.2 | 0 | 3.2
4704 | TORONTO BUTTONVILLE A | 7 | 15 | 24 | 21.5 | 0 | 3.5
4705 | TORONTO BUTTONVILLE A | 7 | 15 | 1 | 20.2 | 0 | 2.2
4705 | TORONTO BUTTONVILLE A | 7 | 16 | 1 | 20.925 | 0 | 2.925
4706 | TORONTO BUTTONVILLE A | 7 | 15 | 2 | 18.9 | 0 | 0.9
4706 | TORONTO BUTTONVILLE A | 7 | 16 | 2 | 20.2 | 0 | 2.2
4707 | TORONTO BUTTONVILLE A | 7 | 15 | 3 | 18.2 | 0 | 0.2
4707 | TORONTO BUTTONVILLE A | 7 | 16 | 3 | 19.375 | 0 | 1.375
4708 | TORONTO BUTTONVILLE A | 7 | 15 | 4 | 18 | 0 | 0
4708 | TORONTO BUTTONVILLE A | 7 | 16 | 4 | 19.175 | 0 | 1.175
4709 | TORONTO BUTTONVILLE A | 7 | 15 | 5 | 17.9 | 0 | 0
4709 | TORONTO BUTTONVILLE A | 7 | 16 | 5 | 19.175 | 0 | 1.175
4710 | TORONTO BUTTONVILLE A | 7 | 15 | 6 | 17.7 | 0 | 0
4710 | TORONTO BUTTONVILLE A | 7 | 16 | 6 | 18.8 | 0 | 0.8
4711 | TORONTO BUTTONVILLE A | 7 | 15 | 7 | 18.5 | 0 | 0.5
4711 | TORONTO BUTTONVILLE A | 7 | 16 | 7 | 19.55 | 0 | 1.55
4712 | TORONTO BUTTONVILLE A | 7 | 15 | 8 | 21.4 | 0 | 3.4
4712 | TORONTO BUTTONVILLE A | 7 | 16 | 8 | 20.925 | 0 | 2.925
4713 | TORONTO BUTTONVILLE A | 7 | 15 | 9 | 24 | 0 | 6
4713 | TORONTO BUTTONVILLE A | 7 | 16 | 9 | 23.05 | 0 | 5.05
4714 | TORONTO BUTTONVILLE A | 7 | 15 | 10 | 25.9 | 0 | 7.9
4714 | TORONTO BUTTONVILLE A | 7 | 16 | 10 | 24.975 | 0 | 6.975
4715 | TORONTO BUTTONVILLE A | 7 | 15 | 11 | 26.5 | 0 | 8.5
4715 | TORONTO BUTTONVILLE A | 7 | 16 | 11 | 26.225 | 0 | 8.225
4716 | TORONTO BUTTONVILLE A | 7 | 15 | 12 | 26.5 | 0 | 8.5
4716 | TORONTO BUTTONVILLE A | 7 | 16 | 12 | 26.05 | 0 | 8.05
4717 | TORONTO BUTTONVILLE A | 7 | 15 | 13 | 27.4 | 0 | 9.4
4717 | TORONTO BUTTONVILLE A | 7 | 16 | 13 | 24.275 | 0 | 6.275
4718 | TORONTO BUTTONVILLE A | 7 | 15 | 14 | 27.7 | 0 | 9.7
4718 | TORONTO BUTTONVILLE A | 7 | 16 | 14 | 25.3333 | 0 | 7.3333
4719 | TORONTO BUTTONVILLE A | 7 | 15 | 15 | 28.4 | 0 | 10.4
4719 | TORONTO BUTTONVILLE A | 7 | 16 | 15 | 25.3 | 0 | 7.3
4720 | TORONTO BUTTONVILLE A | 7 | 15 | 16 | 27.9 | 0 | 9.9
4720 | TORONTO BUTTONVILLE A | 7 | 16 | 16 | 23.95 | 0 | 5.95
4721 | TORONTO BUTTONVILLE A | 7 | 15 | 17 | 27.8 | 0 | 9.8
4721 | TORONTO BUTTONVILLE A | 7 | 16 | 17 | 23.6 | 0 | 5.6
4722 | TORONTO BUTTONVILLE A | 7 | 15 | 18 | 27.4 | 0 | 9.4
4722 | TORONTO BUTTONVILLE A | 7 | 16 | 18 | 23.425 | 0 | 5.425
4723 | TORONTO BUTTONVILLE A | 7 | 15 | 19 | 26.2 | 0 | 8.2
4723 | TORONTO BUTTONVILLE A | 7 | 16 | 19 | 23.175 | 0 | 5.175
4724 | TORONTO BUTTONVILLE A | 7 | 15 | 20 | 24.9 | 0 | 6.9
4724 | TORONTO BUTTONVILLE A | 7 | 16 | 20 | 22.5 | 0 | 4.5
4725 | TORONTO BUTTONVILLE A | 7 | 15 | 21 | 23.7 | 0 | 5.7
4725 | TORONTO BUTTONVILLE A | 7 | 16 | 21 | 22.175 | 0 | 4.175
4726 | TORONTO BUTTONVILLE A | 7 | 15 | 22 | 22.9 | 0 | 4.9
4726 | TORONTO BUTTONVILLE A | 7 | 16 | 22 | 21.425 | 0 | 3.425
4727 | TORONTO BUTTONVILLE A | 7 | 15 | 23 | 22.5 | 0 | 4.5
4727 | TORONTO BUTTONVILLE A | 7 | 16 | 23 | 21.075 | 0 | 3.075
4728 | TORONTO BUTTONVILLE A | 7 | 15 | 24 | 21.9 | 0 | 3.9
4728 | TORONTO BUTTONVILLE A | 7 | 16 | 24 | 21.125 | 0 | 3.125
4729 | TORONTO BUTTONVILLE A | 7 | 16 | 1 | 20.9 | 0 | 2.9
4729 | TORONTO BUTTONVILLE A | 7 | 17 | 1 | 21.025 | 0 | 3.025
4730 | TORONTO BUTTONVILLE A | 7 | 16 | 2 | 20.8 | 0 | 2.8
4730 | TORONTO BUTTONVILLE A | 7 | 17 | 2 | 20.875 | 0 | 2.875
4731 | TORONTO BUTTONVILLE A | 7 | 16 | 3 | 20 | 0 | 2
4731 | TORONTO BUTTONVILLE A | 7 | 17 | 3 | 20.375 | 0 | 2.375
4732 | TORONTO BUTTONVILLE A | 7 | 16 | 4 | 20.8 | 0 | 2.8
4732 | TORONTO BUTTONVILLE A | 7 | 17 | 4 | 20.025 | 0 | 2.025
4733 | TORONTO BUTTONVILLE A | 7 | 16 | 5 | 20.8 | 0 | 2.8
4733 | TORONTO BUTTONVILLE A | 7 | 17 | 5 | 19.875 | 0 | 1.875
4734 | TORONTO BUTTONVILLE A | 7 | 16 | 6 | 20.8 | 0 | 2.8
4734 | TORONTO BUTTONVILLE A | 7 | 17 | 6 | 19.95 | 0 | 1.95
4735 | TORONTO BUTTONVILLE A | 7 | 16 | 7 | 21.2 | 0 | 3.2
4735 | TORONTO BUTTONVILLE A | 7 | 17 | 7 | 19.925 | 0 | 1.925
4736 | TORONTO BUTTONVILLE A | 7 | 16 | 8 | 23.7 | 0 | 5.7
4736 | TORONTO BUTTONVILLE A | 7 | 17 | 8 | 20.2 | 0 | 2.2
4737 | TORONTO BUTTONVILLE A | 7 | 16 | 9 | 24.5 | 0 | 6.5
4737 | TORONTO BUTTONVILLE A | 7 | 17 | 9 | 20.775 | 0 | 2.775
4738 | TORONTO BUTTONVILLE A | 7 | 16 | 10 | 24.7 | 0 | 6.7
4738 | TORONTO BUTTONVILLE A | 7 | 17 | 10 | 21.325 | 0 | 3.325
4739 | TORONTO BUTTONVILLE A | 7 | 16 | 11 | 24.4 | 0 | 6.4
4739 | TORONTO BUTTONVILLE A | 7 | 17 | 11 | 21.775 | 0 | 3.775
4740 | TORONTO BUTTONVILLE A | 7 | 16 | 12 | 24.8 | 0 | 6.8
4740 | TORONTO BUTTONVILLE A | 7 | 17 | 12 | 22.575 | 0 | 4.575
4741 | TORONTO BUTTONVILLE A | 7 | 16 | 13 | 24.6 | 0 | 6.6
4741 | TORONTO BUTTONVILLE A | 7 | 17 | 13 | 23.35 | 0 | 5.35
4742 | TORONTO BUTTONVILLE A | 7 | 16 | 14 | 25.1 | 0 | 7.1
4742 | TORONTO BUTTONVILLE A | 7 | 17 | 14 | 23.725 | 0 | 5.725
4743 | TORONTO BUTTONVILLE A | 7 | 16 | 15 | 24.5 | 0 | 6.5
4743 | TORONTO BUTTONVILLE A | 7 | 17 | 15 | 24.6 | 0 | 6.6
4744 | TORONTO BUTTONVILLE A | 7 | 16 | 16 | 25.2 | 0 | 7.2
4744 | TORONTO BUTTONVILLE A | 7 | 17 | 16 | 23.9 | 0 | 5.9
4745 | TORONTO BUTTONVILLE A | 7 | 16 | 17 | 24.2 | 0 | 6.2
4745 | TORONTO BUTTONVILLE A | 7 | 17 | 17 | 24.475 | 0 | 6.475
4746 | TORONTO BUTTONVILLE A | 7 | 16 | 18 | 23.7 | 0 | 5.7
4746 | TORONTO BUTTONVILLE A | 7 | 17 | 18 | 24.05 | 0 | 6.05
4747 | TORONTO BUTTONVILLE A | 7 | 16 | 19 | 23 | 0 | 5
4747 | TORONTO BUTTONVILLE A | 7 | 17 | 19 | 23.425 | 0 | 5.425
4748 | TORONTO BUTTONVILLE A | 7 | 16 | 20 | 22.9 | 0 | 4.9
4748 | TORONTO BUTTONVILLE A | 7 | 17 | 20 | 23.15 | 0 | 5.15
4749 | TORONTO BUTTONVILLE A | 7 | 16 | 21 | 22.6 | 0 | 4.6
4749 | TORONTO BUTTONVILLE A | 7 | 17 | 21 | 22.075 | 0 | 4.075
4750 | TORONTO BUTTONVILLE A | 7 | 16 | 22 | 22.5 | 0 | 4.5
4750 | TORONTO BUTTONVILLE A | 7 | 17 | 22 | 21.375 | 0 | 3.375
4751 | TORONTO BUTTONVILLE A | 7 | 16 | 23 | 22.5 | 0 | 4.5
4751 | TORONTO BUTTONVILLE A | 7 | 17 | 23 | 20.55 | 0 | 2.55
4752 | TORONTO BUTTONVILLE A | 7 | 16 | 24 | 23.1 | 0 | 5.1
4752 | TORONTO BUTTONVILLE A | 7 | 17 | 24 | 20.15 | 0 | 2.15
4753 | TORONTO BUTTONVILLE A | 7 | 17 | 1 | 22.5 | 0 | 4.5
4753 | TORONTO BUTTONVILLE A | 7 | 18 | 1 | 19.5 | 0 | 1.5
4754 | TORONTO BUTTONVILLE A | 7 | 17 | 2 | 21.6 | 0 | 3.6
4754 | TORONTO BUTTONVILLE A | 7 | 18 | 2 | 18.975 | 0 | 0.975
4755 | TORONTO BUTTONVILLE A | 7 | 17 | 3 | 21.2 | 0 | 3.2
4755 | TORONTO BUTTONVILLE A | 7 | 18 | 3 | 18.7 | 0 | 0.7
4756 | TORONTO BUTTONVILLE A | 7 | 17 | 4 | 21.1 | 0 | 3.1
4756 | TORONTO BUTTONVILLE A | 7 | 18 | 4 | 18.375 | 0 | 0.375
4757 | TORONTO BUTTONVILLE A | 7 | 17 | 5 | 21 | 0 | 3
4757 | TORONTO BUTTONVILLE A | 7 | 18 | 5 | 18.05 | 0 | 0.05
4758 | TORONTO BUTTONVILLE A | 7 | 17 | 6 | 20.1 | 0 | 2.1
4758 | TORONTO BUTTONVILLE A | 7 | 18 | 6 | 17.85 | 0 | 0
4759 | TORONTO BUTTONVILLE A | 7 | 17 | 7 | 20.3 | 0 | 2.3
4759 | TORONTO BUTTONVILLE A | 7 | 18 | 7 | 18.575 | 0 | 0.575
4760 | TORONTO BUTTONVILLE A | 7 | 17 | 8 | 21.2 | 0 | 3.2
4760 | TORONTO BUTTONVILLE A | 7 | 18 | 8 | 19.525 | 0 | 1.525
4761 | TORONTO BUTTONVILLE A | 7 | 17 | 9 | 23.1 | 0 | 5.1
4761 | TORONTO BUTTONVILLE A | 7 | 18 | 9 | 20.875 | 0 | 2.875
4762 | TORONTO BUTTONVILLE A | 7 | 17 | 10 | 24.3 | 0 | 6.3
4762 | TORONTO BUTTONVILLE A | 7 | 18 | 10 | 22.275 | 0 | 4.275
4763 | TORONTO BUTTONVILLE A | 7 | 17 | 11 | 25.9 | 0 | 7.9
4763 | TORONTO BUTTONVILLE A | 7 | 18 | 11 | 22.975 | 0 | 4.975
4764 | TORONTO BUTTONVILLE A | 7 | 17 | 12 | 27.5 | 0 | 9.5
4764 | TORONTO BUTTONVILLE A | 7 | 18 | 12 | 24.275 | 0 | 6.275
4765 | TORONTO BUTTONVILLE A | 7 | 17 | 13 | 29 | 0 | 11
4765 | TORONTO BUTTONVILLE A | 7 | 18 | 13 | 25.15 | 0 | 7.15
4766 | TORONTO BUTTONVILLE A | 7 | 17 | 14 | 28.7 | 0 | 10.7
4766 | TORONTO BUTTONVILLE A | 7 | 18 | 14 | 26 | 0 | 8
4767 | TORONTO BUTTONVILLE A | 7 | 17 | 15 | 30.2 | 0 | 12.2
4767 | TORONTO BUTTONVILLE A | 7 | 18 | 15 | 26.475 | 0 | 8.475
4768 | TORONTO BUTTONVILLE A | 7 | 17 | 16 | 30.6 | 0 | 12.6
4768 | TORONTO BUTTONVILLE A | 7 | 18 | 16 | 26.575 | 0 | 8.575
4769 | TORONTO BUTTONVILLE A | 7 | 17 | 17 | 30.9 | 0 | 12.9
4769 | TORONTO BUTTONVILLE A | 7 | 18 | 17 | 26.9 | 0 | 8.9
4770 | TORONTO BUTTONVILLE A | 7 | 17 | 18 | 30.8 | 0 | 12.8
4770 | TORONTO BUTTONVILLE A | 7 | 18 | 18 | 26.35 | 0 | 8.35
4771 | TORONTO BUTTONVILLE A | 7 | 17 | 19 | 30.4 | 0 | 12.4
4771 | TORONTO BUTTONVILLE A | 7 | 18 | 19 | 25.7 | 0 | 7.7
4772 | TORONTO BUTTONVILLE A | 7 | 17 | 20 | 29.5 | 0 | 11.5
4772 | TORONTO BUTTONVILLE A | 7 | 18 | 20 | 24.5 | 0 | 6.5
4773 | TORONTO BUTTONVILLE A | 7 | 17 | 21 | 27.9 | 0 | 9.9
4773 | TORONTO BUTTONVILLE A | 7 | 18 | 21 | 22.725 | 0 | 4.725
4774 | TORONTO BUTTONVILLE A | 7 | 17 | 22 | 26.7 | 0 | 8.7
4774 | TORONTO BUTTONVILLE A | 7 | 18 | 22 | 21.825 | 0 | 3.825
4775 | TORONTO BUTTONVILLE A | 7 | 17 | 23 | 25.4 | 0 | 7.4
4775 | TORONTO BUTTONVILLE A | 7 | 18 | 23 | 20.975 | 0 | 2.975
4776 | TORONTO BUTTONVILLE A | 7 | 17 | 24 | 24.2 | 0 | 6.2
4776 | TORONTO BUTTONVILLE A | 7 | 18 | 24 | 20.725 | 0 | 2.725
4777 | TORONTO BUTTONVILLE A | 7 | 18 | 1 | 23.4 | 0 | 5.4
4777 | TORONTO BUTTONVILLE A | 7 | 19 | 1 | 19.8 | 0 | 1.8
4778 | TORONTO BUTTONVILLE A | 7 | 18 | 2 | 21.1 | 0 | 3.1
4778 | TORONTO BUTTONVILLE A | 7 | 19 | 2 | 19.45 | 0 | 1.45
4779 | TORONTO BUTTONVILLE A | 7 | 18 | 3 | 21.1 | 0 | 3.1
4779 | TORONTO BUTTONVILLE A | 7 | 19 | 3 | 19.1 | 0 | 1.1
4780 | TORONTO BUTTONVILLE A | 7 | 18 | 4 | 21.3 | 0 | 3.3
4780 | TORONTO BUTTONVILLE A | 7 | 19 | 4 | 18.825 | 0 | 0.825
4781 | TORONTO BUTTONVILLE A | 7 | 18 | 5 | 21.2 | 0 | 3.2
4781 | TORONTO BUTTONVILLE A | 7 | 19 | 5 | 18.95 | 0 | 0.95
4782 | TORONTO BUTTONVILLE A | 7 | 18 | 6 | 21.1 | 0 | 3.1
4782 | TORONTO BUTTONVILLE A | 7 | 19 | 6 | 19.05 | 0 | 1.05
4783 | TORONTO BUTTONVILLE A | 7 | 18 | 7 | 22.4 | 0 | 4.4
4783 | TORONTO BUTTONVILLE A | 7 | 19 | 7 | 19.95 | 0 | 1.95
4784 | TORONTO BUTTONVILLE A | 7 | 18 | 8 | 24.7 | 0 | 6.7
4784 | TORONTO BUTTONVILLE A | 7 | 19 | 8 | 21.4 | 0 | 3.4
4785 | TORONTO BUTTONVILLE A | 7 | 18 | 9 | 25.7 | 0 | 7.7
4785 | TORONTO BUTTONVILLE A | 7 | 19 | 9 | 23.175 | 0 | 5.175
4786 | TORONTO BUTTONVILLE A | 7 | 18 | 10 | 27.6 | 0 | 9.6
4786 | TORONTO BUTTONVILLE A | 7 | 19 | 10 | 25.025 | 0 | 7.025
4787 | TORONTO BUTTONVILLE A | 7 | 18 | 11 | 29.1 | 0 | 11.1
4787 | TORONTO BUTTONVILLE A | 7 | 19 | 11 | 25.825 | 0 | 7.825
4788 | TORONTO BUTTONVILLE A | 7 | 18 | 12 | 30.3 | 0 | 12.3
4788 | TORONTO BUTTONVILLE A | 7 | 19 | 12 | 27.575 | 0 | 9.575
4789 | TORONTO BUTTONVILLE A | 7 | 18 | 13 | 30.6 | 0 | 12.6
4789 | TORONTO BUTTONVILLE A | 7 | 19 | 13 | 27.625 | 0 | 9.625
4790 | TORONTO BUTTONVILLE A | 7 | 18 | 14 | 32.2 | 0 | 14.2
4790 | TORONTO BUTTONVILLE A | 7 | 19 | 14 | 26.85 | 0 | 8.85
4791 | TORONTO BUTTONVILLE A | 7 | 18 | 15 | 32.3 | 0 | 14.3
4791 | TORONTO BUTTONVILLE A | 7 | 19 | 15 | 27.85 | 0 | 9.85
4792 | TORONTO BUTTONVILLE A | 7 | 18 | 16 | 32.4 | 0 | 14.4
4792 | TORONTO BUTTONVILLE A | 7 | 19 | 16 | 28.65 | 0 | 10.65
4793 | TORONTO BUTTONVILLE A | 7 | 18 | 17 | 32.2 | 0 | 14.2
4793 | TORONTO BUTTONVILLE A | 7 | 19 | 17 | 28.85 | 0 | 10.85
4794 | TORONTO BUTTONVILLE A | 7 | 18 | 18 | 32.5 | 0 | 14.5
4794 | TORONTO BUTTONVILLE A | 7 | 19 | 18 | 28.35 | 0 | 10.35
4795 | TORONTO BUTTONVILLE A | 7 | 18 | 19 | 31.3 | 0 | 13.3
4795 | TORONTO BUTTONVILLE A | 7 | 19 | 19 | 27.65 | 0 | 9.65
4796 | TORONTO BUTTONVILLE A | 7 | 18 | 20 | 29.5 | 0 | 11.5
4796 | TORONTO BUTTONVILLE A | 7 | 19 | 20 | 26.975 | 0 | 8.975
4797 | TORONTO BUTTONVILLE A | 7 | 18 | 21 | 28.4 | 0 | 10.4
4797 | TORONTO BUTTONVILLE A | 7 | 19 | 21 | 25.5 | 0 | 7.5
4798 | TORONTO BUTTONVILLE A | 7 | 18 | 22 | 28.4 | 0 | 10.4
4798 | TORONTO BUTTONVILLE A | 7 | 19 | 22 | 23.675 | 0 | 5.675
4799 | TORONTO BUTTONVILLE A | 7 | 18 | 23 | 27.3 | 0 | 9.3
4799 | TORONTO BUTTONVILLE A | 7 | 19 | 23 | 22.725 | 0 | 4.725
4800 | TORONTO BUTTONVILLE A | 7 | 18 | 24 | 26.7 | 0 | 8.7
4800 | TORONTO BUTTONVILLE A | 7 | 19 | 24 | 22.1 | 0 | 4.1
4801 | TORONTO BUTTONVILLE A | 7 | 19 | 1 | 25.8 | 0 | 7.8
4801 | TORONTO BUTTONVILLE A | 7 | 20 | 1 | 21.375 | 0 | 3.375
4802 | TORONTO BUTTONVILLE A | 7 | 19 | 2 | 24.4 | 0 | 6.4
4802 | TORONTO BUTTONVILLE A | 7 | 20 | 2 | 20.025 | 0 | 2.025
4803 | TORONTO BUTTONVILLE A | 7 | 19 | 3 | 24.1 | 0 | 6.1
4803 | TORONTO BUTTONVILLE A | 7 | 20 | 3 | 19.8 | 0 | 1.8
4804 | TORONTO BUTTONVILLE A | 7 | 19 | 4 | 24.4 | 0 | 6.4
4804 | TORONTO BUTTONVILLE A | 7 | 20 | 4 | 19.25 | 0 | 1.25
4805 | TORONTO BUTTONVILLE A | 7 | 19 | 5 | 23.1 | 0 | 5.1
4805 | TORONTO BUTTONVILLE A | 7 | 20 | 5 | 19.15 | 0 | 1.15
4806 | TORONTO BUTTONVILLE A | 7 | 19 | 6 | 23.2 | 0 | 5.2
4806 | TORONTO BUTTONVILLE A | 7 | 20 | 6 | 19.1 | 0 | 1.1
4807 | TORONTO BUTTONVILLE A | 7 | 19 | 7 | 24 | 0 | 6
4807 | TORONTO BUTTONVILLE A | 7 | 20 | 7 | 20 | 0 | 2
4808 | TORONTO BUTTONVILLE A | 7 | 19 | 8 | 26 | 0 | 8
4808 | TORONTO BUTTONVILLE A | 7 | 20 | 8 | 21.85 | 0 | 3.85
4809 | TORONTO BUTTONVILLE A | 7 | 19 | 9 | 27.4 | 0 | 9.4
4809 | TORONTO BUTTONVILLE A | 7 | 20 | 9 | 23.65 | 0 | 5.65
4810 | TORONTO BUTTONVILLE A | 7 | 19 | 10 | 29.5 | 0 | 11.5
4810 | TORONTO BUTTONVILLE A | 7 | 20 | 10 | 24.8 | 0 | 6.8
4811 | TORONTO BUTTONVILLE A | 7 | 19 | 11 | 29.5 | 0 | 11.5
4811 | TORONTO BUTTONVILLE A | 7 | 20 | 11 | 25.575 | 0 | 7.575
4812 | TORONTO BUTTONVILLE A | 7 | 19 | 12 | 29.7 | 0 | 11.7
4812 | TORONTO BUTTONVILLE A | 7 | 20 | 12 | 25.425 | 0 | 7.425
4813 | TORONTO BUTTONVILLE A | 7 | 19 | 13 | 25.3 | 0 | 7.3
4813 | TORONTO BUTTONVILLE A | 7 | 20 | 13 | 26.4 | 0 | 8.4
4814 | TORONTO BUTTONVILLE A | 7 | 19 | 14 | 22.6 | 0 | 4.6
4814 | TORONTO BUTTONVILLE A | 7 | 20 | 14 | 27.025 | 0 | 9.025
4815 | TORONTO BUTTONVILLE A | 7 | 19 | 15 | 23.3 | 0 | 5.3
4815 | TORONTO BUTTONVILLE A | 7 | 20 | 15 | 27.95 | 0 | 9.95
4816 | TORONTO BUTTONVILLE A | 7 | 19 | 16 | 26.8 | 0 | 8.8
4816 | TORONTO BUTTONVILLE A | 7 | 20 | 16 | 27.925 | 0 | 9.925
4817 | TORONTO BUTTONVILLE A | 7 | 19 | 17 | 25.7 | 0 | 7.7
4817 | TORONTO BUTTONVILLE A | 7 | 20 | 17 | 26.275 | 0 | 8.275
4818 | TORONTO BUTTONVILLE A | 7 | 19 | 18 | 26.7 | 0 | 8.7
4818 | TORONTO BUTTONVILLE A | 7 | 20 | 18 | 25.425 | 0 | 7.425
4819 | TORONTO BUTTONVILLE A | 7 | 19 | 19 | 26.6 | 0 | 8.6
4819 | TORONTO BUTTONVILLE A | 7 | 20 | 19 | 25.625 | 0 | 7.625
4820 | TORONTO BUTTONVILLE A | 7 | 19 | 20 | 25.5 | 0 | 7.5
4820 | TORONTO BUTTONVILLE A | 7 | 20 | 20 | 25.075 | 0 | 7.075
4821 | TORONTO BUTTONVILLE A | 7 | 19 | 21 | 24.9 | 0 | 6.9
4821 | TORONTO BUTTONVILLE A | 7 | 20 | 21 | 23.975 | 0 | 5.975
4822 | TORONTO BUTTONVILLE A | 7 | 19 | 22 | 24.3 | 0 | 6.3
4822 | TORONTO BUTTONVILLE A | 7 | 20 | 22 | 22.45 | 0 | 4.45
4823 | TORONTO BUTTONVILLE A | 7 | 19 | 23 | 24.2 | 0 | 6.2
4823 | TORONTO BUTTONVILLE A | 7 | 20 | 23 | 22.55 | 0 | 4.55
4824 | TORONTO BUTTONVILLE A | 7 | 19 | 24 | 24 | 0 | 6
4824 | TORONTO BUTTONVILLE A | 7 | 20 | 24 | 21.4 | 0 | 3.4
4825 | TORONTO BUTTONVILLE A | 7 | 20 | 1 | 23.8 | 0 | 5.8
4825 | TORONTO BUTTONVILLE A | 7 | 21 | 1 | 20.95 | 0 | 2.95
4826 | TORONTO BUTTONVILLE A | 7 | 20 | 2 | 23.1 | 0 | 5.1
4826 | TORONTO BUTTONVILLE A | 7 | 21 | 2 | 20.525 | 0 | 2.525
4827 | TORONTO BUTTONVILLE A | 7 | 20 | 3 | 22.6 | 0 | 4.6
4827 | TORONTO BUTTONVILLE A | 7 | 21 | 3 | 20.15 | 0 | 2.15
4828 | TORONTO BUTTONVILLE A | 7 | 20 | 4 | 21.9 | 0 | 3.9
4828 | TORONTO BUTTONVILLE A | 7 | 21 | 4 | 19.475 | 0 | 1.475
4829 | TORONTO BUTTONVILLE A | 7 | 20 | 5 | 21.5 | 0 | 3.5
4829 | TORONTO BUTTONVILLE A | 7 | 21 | 5 | 19.35 | 0 | 1.35
4830 | TORONTO BUTTONVILLE A | 7 | 20 | 6 | 20.9 | 0 | 2.9
4830 | TORONTO BUTTONVILLE A | 7 | 21 | 6 | 18.975 | 0 | 0.975
4831 | TORONTO BUTTONVILLE A | 7 | 20 | 7 | 21.2 | 0 | 3.2
4831 | TORONTO BUTTONVILLE A | 7 | 21 | 7 | 19.675 | 0 | 1.675
4832 | TORONTO BUTTONVILLE A | 7 | 20 | 8 | 22.6 | 0 | 4.6
4832 | TORONTO BUTTONVILLE A | 7 | 21 | 8 | 21.025 | 0 | 3.025
4833 | TORONTO BUTTONVILLE A | 7 | 20 | 9 | 23.9 | 0 | 5.9
4833 | TORONTO BUTTONVILLE A | 7 | 21 | 9 | 21.925 | 0 | 3.925
4834 | TORONTO BUTTONVILLE A | 7 | 20 | 10 | 24.9 | 0 | 6.9
4834 | TORONTO BUTTONVILLE A | 7 | 21 | 10 | 22.85 | 0 | 4.85
4835 | TORONTO BUTTONVILLE A | 7 | 20 | 11 | 26.6 | 0 | 8.6
4835 | TORONTO BUTTONVILLE A | 7 | 21 | 11 | 23.975 | 0 | 5.975
4836 | TORONTO BUTTONVILLE A | 7 | 20 | 12 | 26.7 | 0 | 8.7
4836 | TORONTO BUTTONVILLE A | 7 | 21 | 12 | 24.575 | 0 | 6.575
4837 | TORONTO BUTTONVILLE A | 7 | 20 | 13 | 26.6 | 0 | 8.6
4837 | TORONTO BUTTONVILLE A | 7 | 21 | 13 | 24.825 | 0 | 6.825
4838 | TORONTO BUTTONVILLE A | 7 | 20 | 14 | 27.8 | 0 | 9.8
4838 | TORONTO BUTTONVILLE A | 7 | 21 | 14 | 25.075 | 0 | 7.075
4839 | TORONTO BUTTONVILLE A | 7 | 20 | 15 | 28.4 | 0 | 10.4
4839 | TORONTO BUTTONVILLE A | 7 | 21 | 15 | 25.7 | 0 | 7.7
4840 | TORONTO BUTTONVILLE A | 7 | 20 | 16 | 28.1 | 0 | 10.1
4840 | TORONTO BUTTONVILLE A | 7 | 21 | 16 | 26.375 | 0 | 8.375
4841 | TORONTO BUTTONVILLE A | 7 | 20 | 17 | 26.6 | 0 | 8.6
4841 | TORONTO BUTTONVILLE A | 7 | 21 | 17 | 25.825 | 0 | 7.825
4842 | TORONTO BUTTONVILLE A | 7 | 20 | 18 | 26.2 | 0 | 8.2
4842 | TORONTO BUTTONVILLE A | 7 | 21 | 18 | 25.725 | 0 | 7.725
4843 | TORONTO BUTTONVILLE A | 7 | 20 | 19 | 25.1 | 0 | 7.1
4843 | TORONTO BUTTONVILLE A | 7 | 21 | 19 | 24.8 | 0 | 6.8
4844 | TORONTO BUTTONVILLE A | 7 | 20 | 20 | 22.8 | 0 | 4.8
4844 | TORONTO BUTTONVILLE A | 7 | 21 | 20 | 23.675 | 0 | 5.675
4845 | TORONTO BUTTONVILLE A | 7 | 20 | 21 | 21.2 | 0 | 3.2
4845 | TORONTO BUTTONVILLE A | 7 | 21 | 21 | 22.05 | 0 | 4.05
4846 | TORONTO BUTTONVILLE A | 7 | 20 | 22 | 19.9 | 0 | 1.9
4846 | TORONTO BUTTONVILLE A | 7 | 21 | 22 | 21.25 | 0 | 3.25
4847 | TORONTO BUTTONVILLE A | 7 | 20 | 23 | 19.3 | 0 | 1.3
4847 | TORONTO BUTTONVILLE A | 7 | 21 | 23 | 20.35 | 0 | 2.35
4848 | TORONTO BUTTONVILLE A | 7 | 20 | 24 | 18.4 | 0 | 0.4
4848 | TORONTO BUTTONVILLE A | 7 | 21 | 24 | 19.775 | 0 | 1.775
4849 | TORONTO BUTTONVILLE A | 7 | 21 | 1 | 17.7 | 0 | 0
4849 | TORONTO BUTTONVILLE A | 7 | 22 | 1 | 18.875 | 0 | 0.875
4850 | TORONTO BUTTONVILLE A | 7 | 21 | 2 | 17 | 0 | 0
4850 | TORONTO BUTTONVILLE A | 7 | 22 | 2 | 18.675 | 0 | 0.675
4851 | TORONTO BUTTONVILLE A | 7 | 21 | 3 | 16.8 | 0 | 0
4851 | TORONTO BUTTONVILLE A | 7 | 22 | 3 | 18.1 | 0 | 0.1
4852 | TORONTO BUTTONVILLE A | 7 | 21 | 4 | 16.5 | 0 | 0
4852 | TORONTO BUTTONVILLE A | 7 | 22 | 4 | 17.85 | 0 | 0
4853 | TORONTO BUTTONVILLE A | 7 | 21 | 5 | 16 | 0 | 0
4853 | TORONTO BUTTONVILLE A | 7 | 22 | 5 | 17.125 | 0 | 0
4854 | TORONTO BUTTONVILLE A | 7 | 21 | 6 | 15.6 | 0 | 0
4854 | TORONTO BUTTONVILLE A | 7 | 22 | 6 | 17.125 | 0 | 0
4855 | TORONTO BUTTONVILLE A | 7 | 21 | 7 | 16.1 | 0 | 0
4855 | TORONTO BUTTONVILLE A | 7 | 22 | 7 | 17.85 | 0 | 0
4856 | TORONTO BUTTONVILLE A | 7 | 21 | 8 | 18.5 | 0 | 0.5
4856 | TORONTO BUTTONVILLE A | 7 | 22 | 8 | 18.65 | 0 | 0.65
4857 | TORONTO BUTTONVILLE A | 7 | 21 | 9 | 19.6 | 0 | 1.6
4857 | TORONTO BUTTONVILLE A | 7 | 22 | 9 | 19.475 | 0 | 1.475
4858 | TORONTO BUTTONVILLE A | 7 | 21 | 10 | 21.2 | 0 | 3.2
4858 | TORONTO BUTTONVILLE A | 7 | 22 | 10 | 20.475 | 0 | 2.475
4859 | TORONTO BUTTONVILLE A | 7 | 21 | 11 | 21.6 | 0 | 3.6
4859 | TORONTO BUTTONVILLE A | 7 | 22 | 11 | 21.7 | 0 | 3.7
4860 | TORONTO BUTTONVILLE A | 7 | 21 | 12 | 22 | 0 | 4
4860 | TORONTO BUTTONVILLE A | 7 | 22 | 12 | 22.375 | 0 | 4.375
4861 | TORONTO BUTTONVILLE A | 7 | 21 | 13 | 22.7 | 0 | 4.7
4861 | TORONTO BUTTONVILLE A | 7 | 22 | 13 | 22.625 | 0 | 4.625
4862 | TORONTO BUTTONVILLE A | 7 | 21 | 14 | 24.5 | 0 | 6.5
4862 | TORONTO BUTTONVILLE A | 7 | 22 | 14 | 22.725 | 0 | 4.725
4863 | TORONTO BUTTONVILLE A | 7 | 21 | 15 | 25.7 | 0 | 7.7
4863 | TORONTO BUTTONVILLE A | 7 | 22 | 15 | 23.675 | 0 | 5.675
4864 | TORONTO BUTTONVILLE A | 7 | 21 | 16 | 25.7 | 0 | 7.7
4864 | TORONTO BUTTONVILLE A | 7 | 22 | 16 | 23.475 | 0 | 5.475
4865 | TORONTO BUTTONVILLE A | 7 | 21 | 17 | 24.5 | 0 | 6.5
4865 | TORONTO BUTTONVILLE A | 7 | 22 | 17 | 22.875 | 0 | 4.875
4866 | TORONTO BUTTONVILLE A | 7 | 21 | 18 | 24.7 | 0 | 6.7
4866 | TORONTO BUTTONVILLE A | 7 | 22 | 18 | 22.925 | 0 | 4.925
4867 | TORONTO BUTTONVILLE A | 7 | 21 | 19 | 24.1 | 0 | 6.1
4867 | TORONTO BUTTONVILLE A | 7 | 22 | 19 | 22.7 | 0 | 4.7
4868 | TORONTO BUTTONVILLE A | 7 | 21 | 20 | 23.3 | 0 | 5.3
4868 | TORONTO BUTTONVILLE A | 7 | 22 | 20 | 21.825 | 0 | 3.825
4869 | TORONTO BUTTONVILLE A | 7 | 21 | 21 | 22.1 | 0 | 4.1
4869 | TORONTO BUTTONVILLE A | 7 | 22 | 21 | 20.575 | 0 | 2.575
4870 | TORONTO BUTTONVILLE A | 7 | 21 | 22 | 21.3 | 0 | 3.3
4870 | TORONTO BUTTONVILLE A | 7 | 22 | 22 | 20 | 0 | 2
4871 | TORONTO BUTTONVILLE A | 7 | 21 | 23 | 20.7 | 0 | 2.7
4871 | TORONTO BUTTONVILLE A | 7 | 22 | 23 | 19.2 | 0 | 1.2
4872 | TORONTO BUTTONVILLE A | 7 | 21 | 24 | 20.1 | 0 | 2.1
4872 | TORONTO BUTTONVILLE A | 7 | 22 | 24 | 19.05 | 0 | 1.05
4873 | TORONTO BUTTONVILLE A | 7 | 22 | 1 | 18.6 | 0 | 0.6
4873 | TORONTO BUTTONVILLE A | 7 | 23 | 1 | 18.425 | 0 | 0.425
4874 | TORONTO BUTTONVILLE A | 7 | 22 | 2 | 19.1 | 0 | 1.1
4874 | TORONTO BUTTONVILLE A | 7 | 23 | 2 | 18.425 | 0 | 0.425
4875 | TORONTO BUTTONVILLE A | 7 | 22 | 3 | 18.5 | 0 | 0.5
4875 | TORONTO BUTTONVILLE A | 7 | 23 | 3 | 18.075 | 0 | 0.075
4876 | TORONTO BUTTONVILLE A | 7 | 22 | 4 | 19 | 0 | 1
4876 | TORONTO BUTTONVILLE A | 7 | 23 | 4 | 17.75 | 0 | 0
4877 | TORONTO BUTTONVILLE A | 7 | 22 | 5 | 18.8 | 0 | 0.8
4877 | TORONTO BUTTONVILLE A | 7 | 23 | 5 | 17.375 | 0 | 0
4878 | TORONTO BUTTONVILLE A | 7 | 22 | 6 | 19 | 0 | 1
4878 | TORONTO BUTTONVILLE A | 7 | 23 | 6 | 17.2 | 0 | 0
4879 | TORONTO BUTTONVILLE A | 7 | 22 | 7 | 19.5 | 0 | 1.5
4879 | TORONTO BUTTONVILLE A | 7 | 23 | 7 | 17.75 | 0 | 0
4880 | TORONTO BUTTONVILLE A | 7 | 22 | 8 | 20.2 | 0 | 2.2
4880 | TORONTO BUTTONVILLE A | 7 | 23 | 8 | 19.5 | 0 | 1.5
4881 | TORONTO BUTTONVILLE A | 7 | 22 | 9 | 20.7 | 0 | 2.7
4881 | TORONTO BUTTONVILLE A | 7 | 23 | 9 | 20.55 | 0 | 2.55
4882 | TORONTO BUTTONVILLE A | 7 | 22 | 10 | 21.5 | 0 | 3.5
4882 | TORONTO BUTTONVILLE A | 7 | 23 | 10 | 22.025 | 0 | 4.025
4883 | TORONTO BUTTONVILLE A | 7 | 22 | 11 | 21.7 | 0 | 3.7
4883 | TORONTO BUTTONVILLE A | 7 | 23 | 11 | 22.975 | 0 | 4.975
4884 | TORONTO BUTTONVILLE A | 7 | 22 | 12 | 22.4 | 0 | 4.4
4884 | TORONTO BUTTONVILLE A | 7 | 23 | 12 | 23.35 | 0 | 5.35
4885 | TORONTO BUTTONVILLE A | 7 | 22 | 13 | 24.4 | 0 | 6.4
4885 | TORONTO BUTTONVILLE A | 7 | 23 | 13 | 23.825 | 0 | 5.825
4886 | TORONTO BUTTONVILLE A | 7 | 22 | 14 | 24.4 | 0 | 6.4
4886 | TORONTO BUTTONVILLE A | 7 | 23 | 14 | 24.975 | 0 | 6.975
4887 | TORONTO BUTTONVILLE A | 7 | 22 | 15 | 25.7 | 0 | 7.7
4887 | TORONTO BUTTONVILLE A | 7 | 23 | 15 | 25.175 | 0 | 7.175
4888 | TORONTO BUTTONVILLE A | 7 | 22 | 16 | 24.6 | 0 | 6.6
4888 | TORONTO BUTTONVILLE A | 7 | 23 | 16 | 24.475 | 0 | 6.475
4889 | TORONTO BUTTONVILLE A | 7 | 22 | 17 | 23.6 | 0 | 5.6
4889 | TORONTO BUTTONVILLE A | 7 | 23 | 17 | 25.025 | 0 | 7.025
4890 | TORONTO BUTTONVILLE A | 7 | 22 | 18 | 24.9 | 0 | 6.9
4890 | TORONTO BUTTONVILLE A | 7 | 23 | 18 | 24.45 | 0 | 6.45
4891 | TORONTO BUTTONVILLE A | 7 | 22 | 19 | 24.6 | 0 | 6.6
4891 | TORONTO BUTTONVILLE A | 7 | 23 | 19 | 24.225 | 0 | 6.225
4892 | TORONTO BUTTONVILLE A | 7 | 22 | 20 | 22.6 | 0 | 4.6
4892 | TORONTO BUTTONVILLE A | 7 | 23 | 20 | 23.275 | 0 | 5.275
4893 | TORONTO BUTTONVILLE A | 7 | 22 | 21 | 22.6 | 0 | 4.6
4893 | TORONTO BUTTONVILLE A | 7 | 23 | 21 | 21.9 | 0 | 3.9
4894 | TORONTO BUTTONVILLE A | 7 | 22 | 22 | 22.6 | 0 | 4.6
4894 | TORONTO BUTTONVILLE A | 7 | 23 | 22 | 20.975 | 0 | 2.975
4895 | TORONTO BUTTONVILLE A | 7 | 22 | 23 | 21.7 | 0 | 3.7
4895 | TORONTO BUTTONVILLE A | 7 | 23 | 23 | 20.05 | 0 | 2.05
4896 | TORONTO BUTTONVILLE A | 7 | 22 | 24 | 20.5 | 0 | 2.5
4896 | TORONTO BUTTONVILLE A | 7 | 23 | 24 | 19.15 | 0 | 1.15
4897 | TORONTO BUTTONVILLE A | 7 | 23 | 1 | 19.5 | 0 | 1.5
4897 | TORONTO BUTTONVILLE A | 7 | 24 | 1 | 18.775 | 0 | 0.775
4898 | TORONTO BUTTONVILLE A | 7 | 23 | 2 | 19.3 | 0 | 1.3
4898 | TORONTO BUTTONVILLE A | 7 | 24 | 2 | 18.175 | 0 | 0.175
4899 | TORONTO BUTTONVILLE A | 7 | 23 | 3 | 19.1 | 0 | 1.1
4899 | TORONTO BUTTONVILLE A | 7 | 24 | 3 | 18.15 | 0 | 0.15
4900 | TORONTO BUTTONVILLE A | 7 | 23 | 4 | 18.9 | 0 | 0.9
4900 | TORONTO BUTTONVILLE A | 7 | 24 | 4 | 17.825 | 0 | 0
4901 | TORONTO BUTTONVILLE A | 7 | 23 | 5 | 18.6 | 0 | 0.6
4901 | TORONTO BUTTONVILLE A | 7 | 24 | 5 | 17.425 | 0 | 0
4902 | TORONTO BUTTONVILLE A | 7 | 23 | 6 | 18.6 | 0 | 0.6
4902 | TORONTO BUTTONVILLE A | 7 | 24 | 6 | 16.825 | 0 | 0
4903 | TORONTO BUTTONVILLE A | 7 | 23 | 7 | 19 | 0 | 1
4903 | TORONTO BUTTONVILLE A | 7 | 24 | 7 | 17.375 | 0 | 0
4904 | TORONTO BUTTONVILLE A | 7 | 23 | 8 | 19.3 | 0 | 1.3
4904 | TORONTO BUTTONVILLE A | 7 | 24 | 8 | 19.275 | 0 | 1.275
4905 | TORONTO BUTTONVILLE A | 7 | 23 | 9 | 20.5 | 0 | 2.5
4905 | TORONTO BUTTONVILLE A | 7 | 24 | 9 | 21.125 | 0 | 3.125
4906 | TORONTO BUTTONVILLE A | 7 | 23 | 10 | 22.2 | 0 | 4.2
4906 | TORONTO BUTTONVILLE A | 7 | 24 | 10 | 22.45 | 0 | 4.45
4907 | TORONTO BUTTONVILLE A | 7 | 23 | 11 | 23.3 | 0 | 5.3
4907 | TORONTO BUTTONVILLE A | 7 | 24 | 11 | 23.4333 | 0 | 5.4333
4908 | TORONTO BUTTONVILLE A | 7 | 23 | 12 | 23.8 | 0 | 5.8
4908 | TORONTO BUTTONVILLE A | 7 | 24 | 12 | 23.55 | 0 | 5.55
4909 | TORONTO BUTTONVILLE A | 7 | 23 | 13 | 24.2 | 0 | 6.2
4909 | TORONTO BUTTONVILLE A | 7 | 24 | 13 | 23.325 | 0 | 5.325
4910 | TORONTO BUTTONVILLE A | 7 | 23 | 14 | 25.4 | 0 | 7.4
4910 | TORONTO BUTTONVILLE A | 7 | 24 | 14 | 23.175 | 0 | 5.175
4911 | TORONTO BUTTONVILLE A | 7 | 23 | 15 | 26.1 | 0 | 8.1
4911 | TORONTO BUTTONVILLE A | 7 | 24 | 15 | 23.175 | 0 | 5.175
4912 | TORONTO BUTTONVILLE A | 7 | 23 | 16 | 26.1 | 0 | 8.1
4912 | TORONTO BUTTONVILLE A | 7 | 24 | 16 | 23.55 | 0 | 5.55
4913 | TORONTO BUTTONVILLE A | 7 | 23 | 17 | 25.5 | 0 | 7.5
4913 | TORONTO BUTTONVILLE A | 7 | 24 | 17 | 23.475 | 0 | 5.475
4914 | TORONTO BUTTONVILLE A | 7 | 23 | 18 | 25.8 | 0 | 7.8
4914 | TORONTO BUTTONVILLE A | 7 | 24 | 18 | 23.15 | 0 | 5.15
4915 | TORONTO BUTTONVILLE A | 7 | 23 | 19 | 24.7 | 0 | 6.7
4915 | TORONTO BUTTONVILLE A | 7 | 24 | 19 | 21.75 | 0 | 3.75
4916 | TORONTO BUTTONVILLE A | 7 | 23 | 20 | 23.5 | 0 | 5.5
4916 | TORONTO BUTTONVILLE A | 7 | 24 | 20 | 20.85 | 0 | 2.85
4917 | TORONTO BUTTONVILLE A | 7 | 23 | 21 | 22 | 0 | 4
4917 | TORONTO BUTTONVILLE A | 7 | 24 | 21 | 20.275 | 0 | 2.275
4918 | TORONTO BUTTONVILLE A | 7 | 23 | 22 | 20.6 | 0 | 2.6
4918 | TORONTO BUTTONVILLE A | 7 | 24 | 22 | 20.025 | 0 | 2.025
4919 | TORONTO BUTTONVILLE A | 7 | 23 | 23 | 19.6 | 0 | 1.6
4919 | TORONTO BUTTONVILLE A | 7 | 24 | 23 | 19.45 | 0 | 1.45
4920 | TORONTO BUTTONVILLE A | 7 | 23 | 24 | 18.6 | 0 | 0.6
4920 | TORONTO BUTTONVILLE A | 7 | 24 | 24 | 19.4 | 0 | 1.4
4921 | TORONTO BUTTONVILLE A | 7 | 24 | 1 | 18.6 | 0 | 0.6
4921 | TORONTO BUTTONVILLE A | 7 | 25 | 1 | 19.075 | 0 | 1.075
4922 | TORONTO BUTTONVILLE A | 7 | 24 | 2 | 17.8 | 0 | 0
4922 | TORONTO BUTTONVILLE A | 7 | 25 | 2 | 18.975 | 0 | 0.975
4923 | TORONTO BUTTONVILLE A | 7 | 24 | 3 | 18.3 | 0 | 0.3
4923 | TORONTO BUTTONVILLE A | 7 | 25 | 3 | 18.25 | 0 | 0.25
4924 | TORONTO BUTTONVILLE A | 7 | 24 | 4 | 17.4 | 0 | 0
4924 | TORONTO BUTTONVILLE A | 7 | 25 | 4 | 18.5 | 0 | 0.5
4925 | TORONTO BUTTONVILLE A | 7 | 24 | 5 | 17 | 0 | 0
4925 | TORONTO BUTTONVILLE A | 7 | 25 | 5 | 18.075 | 0 | 0.075
4926 | TORONTO BUTTONVILLE A | 7 | 24 | 6 | 17.3 | 0 | 0
4926 | TORONTO BUTTONVILLE A | 7 | 25 | 6 | 18.2 | 0 | 0.2
4927 | TORONTO BUTTONVILLE A | 7 | 24 | 7 | 17.8 | 0 | 0
4927 | TORONTO BUTTONVILLE A | 7 | 25 | 7 | 18.375 | 0 | 0.375
4928 | TORONTO BUTTONVILLE A | 7 | 24 | 8 | 19.6 | 0 | 1.6
4928 | TORONTO BUTTONVILLE A | 7 | 25 | 8 | 19.375 | 0 | 1.375
4929 | TORONTO BUTTONVILLE A | 7 | 24 | 9 | 21.8 | 0 | 3.8
4929 | TORONTO BUTTONVILLE A | 7 | 25 | 9 | 20.55 | 0 | 2.55
4930 | TORONTO BUTTONVILLE A | 7 | 24 | 10 | 23.4 | 0 | 5.4
4930 | TORONTO BUTTONVILLE A | 7 | 25 | 10 | 21.575 | 0 | 3.575
4931 | TORONTO BUTTONVILLE A | 7 | 24 | 11 | 24.7 | 0 | 6.7
4931 | TORONTO BUTTONVILLE A | 7 | 25 | 11 | 22.975 | 0 | 4.975
4932 | TORONTO BUTTONVILLE A | 7 | 24 | 12 | 24.1 | 0 | 6.1
4932 | TORONTO BUTTONVILLE A | 7 | 25 | 12 | 24.1 | 0 | 6.1
4933 | TORONTO BUTTONVILLE A | 7 | 24 | 13 | 26 | 0 | 8
4933 | TORONTO BUTTONVILLE A | 7 | 25 | 13 | 25.325 | 0 | 7.325
4934 | TORONTO BUTTONVILLE A | 7 | 24 | 14 | 26.5 | 0 | 8.5
4934 | TORONTO BUTTONVILLE A | 7 | 25 | 14 | 26.325 | 0 | 8.325
4935 | TORONTO BUTTONVILLE A | 7 | 24 | 15 | 26.9 | 0 | 8.9
4935 | TORONTO BUTTONVILLE A | 7 | 25 | 15 | 26.775 | 0 | 8.775
4936 | TORONTO BUTTONVILLE A | 7 | 24 | 16 | 27.6 | 0 | 9.6
4936 | TORONTO BUTTONVILLE A | 7 | 25 | 16 | 27.2 | 0 | 9.2
4937 | TORONTO BUTTONVILLE A | 7 | 24 | 17 | 28 | 0 | 10
4937 | TORONTO BUTTONVILLE A | 7 | 25 | 17 | 27.05 | 0 | 9.05
4938 | TORONTO BUTTONVILLE A | 7 | 24 | 18 | 27.6 | 0 | 9.6
4938 | TORONTO BUTTONVILLE A | 7 | 25 | 18 | 26.825 | 0 | 8.825
4939 | TORONTO BUTTONVILLE A | 7 | 24 | 19 | 26.7 | 0 | 8.7
4939 | TORONTO BUTTONVILLE A | 7 | 25 | 19 | 26.1 | 0 | 8.1
4940 | TORONTO BUTTONVILLE A | 7 | 24 | 20 | 25.3 | 0 | 7.3
4940 | TORONTO BUTTONVILLE A | 7 | 25 | 20 | 24.75 | 0 | 6.75
4941 | TORONTO BUTTONVILLE A | 7 | 24 | 21 | 23.7 | 0 | 5.7
4941 | TORONTO BUTTONVILLE A | 7 | 25 | 21 | 22.7 | 0 | 4.7
4942 | TORONTO BUTTONVILLE A | 7 | 24 | 22 | 23.6 | 0 | 5.6
4942 | TORONTO BUTTONVILLE A | 7 | 25 | 22 | 21.375 | 0 | 3.375
4943 | TORONTO BUTTONVILLE A | 7 | 24 | 23 | 22.4 | 0 | 4.4
4943 | TORONTO BUTTONVILLE A | 7 | 25 | 23 | 20.475 | 0 | 2.475
4944 | TORONTO BUTTONVILLE A | 7 | 24 | 24 | 21.7 | 0 | 3.7
4944 | TORONTO BUTTONVILLE A | 7 | 25 | 24 | 19.625 | 0 | 1.625
4945 | TORONTO BUTTONVILLE A | 7 | 25 | 1 | 19.7 | 0 | 1.7
4945 | TORONTO BUTTONVILLE A | 7 | 26 | 1 | 18.875 | 0 | 0.875
4946 | TORONTO BUTTONVILLE A | 7 | 25 | 2 | 19.4 | 0 | 1.4
4946 | TORONTO BUTTONVILLE A | 7 | 26 | 2 | 18.05 | 0 | 0.05
4947 | TORONTO BUTTONVILLE A | 7 | 25 | 3 | 18.3 | 0 | 0.3
4947 | TORONTO BUTTONVILLE A | 7 | 26 | 3 | 17.45 | 0 | 0
4948 | TORONTO BUTTONVILLE A | 7 | 25 | 4 | 17.9 | 0 | 0
4948 | TORONTO BUTTONVILLE A | 7 | 26 | 4 | 16.55 | 0 | 0
4949 | TORONTO BUTTONVILLE A | 7 | 25 | 5 | 18.2 | 0 | 0.2
4949 | TORONTO BUTTONVILLE A | 7 | 26 | 5 | 16.175 | 0 | 0
4950 | TORONTO BUTTONVILLE A | 7 | 25 | 6 | 17.6 | 0 | 0
4950 | TORONTO BUTTONVILLE A | 7 | 26 | 6 | 15.625 | 0 | 0
4951 | TORONTO BUTTONVILLE A | 7 | 25 | 7 | 18.4 | 0 | 0.4
4951 | TORONTO BUTTONVILLE A | 7 | 26 | 7 | 16.9 | 0 | 0
4952 | TORONTO BUTTONVILLE A | 7 | 25 | 8 | 21.3 | 0 | 3.3
4952 | TORONTO BUTTONVILLE A | 7 | 26 | 8 | 20.025 | 0 | 2.025
4953 | TORONTO BUTTONVILLE A | 7 | 25 | 9 | 23.7 | 0 | 5.7
4953 | TORONTO BUTTONVILLE A | 7 | 26 | 9 | 22.925 | 0 | 4.925
4954 | TORONTO BUTTONVILLE A | 7 | 25 | 10 | 26 | 0 | 8
4954 | TORONTO BUTTONVILLE A | 7 | 26 | 10 | 24.65 | 0 | 6.65
4955 | TORONTO BUTTONVILLE A | 7 | 25 | 11 | 27.6 | 0 | 9.6
4955 | TORONTO BUTTONVILLE A | 7 | 26 | 11 | 25.475 | 0 | 7.475
4956 | TORONTO BUTTONVILLE A | 7 | 25 | 12 | 28.5 | 0 | 10.5
4956 | TORONTO BUTTONVILLE A | 7 | 26 | 12 | 26.4 | 0 | 8.4
4957 | TORONTO BUTTONVILLE A | 7 | 25 | 13 | 28.3 | 0 | 10.3
4957 | TORONTO BUTTONVILLE A | 7 | 26 | 13 | 26.175 | 0 | 8.175
4958 | TORONTO BUTTONVILLE A | 7 | 25 | 14 | 28.8 | 0 | 10.8
4958 | TORONTO BUTTONVILLE A | 7 | 26 | 14 | 26.225 | 0 | 8.225
4959 | TORONTO BUTTONVILLE A | 7 | 25 | 15 | 29.6 | 0 | 11.6
4959 | TORONTO BUTTONVILLE A | 7 | 26 | 15 | 27 | 0 | 9
4960 | TORONTO BUTTONVILLE A | 7 | 25 | 16 | 30.1 | 0 | 12.1
4960 | TORONTO BUTTONVILLE A | 7 | 26 | 16 | 26.6 | 0 | 8.6
4961 | TORONTO BUTTONVILLE A | 7 | 25 | 17 | 30 | 0 | 12
4961 | TORONTO BUTTONVILLE A | 7 | 26 | 17 | 24.3 | 0 | 6.3
4962 | TORONTO BUTTONVILLE A | 7 | 25 | 18 | 29.9 | 0 | 11.9
4962 | TORONTO BUTTONVILLE A | 7 | 26 | 18 | 25.3 | 0 | 7.3
4963 | TORONTO BUTTONVILLE A | 7 | 25 | 19 | 29.6 | 0 | 11.6
4963 | TORONTO BUTTONVILLE A | 7 | 26 | 19 | 25.075 | 0 | 7.075
4964 | TORONTO BUTTONVILLE A | 7 | 25 | 20 | 28.8 | 0 | 10.8
4964 | TORONTO BUTTONVILLE A | 7 | 26 | 20 | 23.5 | 0 | 5.5
4965 | TORONTO BUTTONVILLE A | 7 | 25 | 21 | 27.3 | 0 | 9.3
4965 | TORONTO BUTTONVILLE A | 7 | 26 | 21 | 22.15 | 0 | 4.15
4966 | TORONTO BUTTONVILLE A | 7 | 25 | 22 | 25.5 | 0 | 7.5
4966 | TORONTO BUTTONVILLE A | 7 | 26 | 22 | 21.5 | 0 | 3.5
4967 | TORONTO BUTTONVILLE A | 7 | 25 | 23 | 24 | 0 | 6
4967 | TORONTO BUTTONVILLE A | 7 | 26 | 23 | 21 | 0 | 3
4968 | TORONTO BUTTONVILLE A | 7 | 25 | 24 | 23.5 | 0 | 5.5
4968 | TORONTO BUTTONVILLE A | 7 | 26 | 24 | 20.4 | 0 | 2.4
4969 | TORONTO BUTTONVILLE A | 7 | 26 | 1 | 22.8 | 0 | 4.8
4969 | TORONTO BUTTONVILLE A | 7 | 27 | 1 | 19.275 | 0 | 1.275
4970 | TORONTO BUTTONVILLE A | 7 | 26 | 2 | 22 | 0 | 4
4970 | TORONTO BUTTONVILLE A | 7 | 27 | 2 | 18.425 | 0 | 0.425
4971 | TORONTO BUTTONVILLE A | 7 | 26 | 3 | 21.2 | 0 | 3.2
4971 | TORONTO BUTTONVILLE A | 7 | 27 | 3 | 18.475 | 0 | 0.475
4972 | TORONTO BUTTONVILLE A | 7 | 26 | 4 | 21.8 | 0 | 3.8
4972 | TORONTO BUTTONVILLE A | 7 | 27 | 4 | 17.675 | 0 | 0
4973 | TORONTO BUTTONVILLE A | 7 | 26 | 5 | 21.5 | 0 | 3.5
4973 | TORONTO BUTTONVILLE A | 7 | 27 | 5 | 17.3 | 0 | 0
4974 | TORONTO BUTTONVILLE A | 7 | 26 | 6 | 21 | 0 | 3
4974 | TORONTO BUTTONVILLE A | 7 | 27 | 6 | 17.25 | 0 | 0
4975 | TORONTO BUTTONVILLE A | 7 | 26 | 7 | 21.9 | 0 | 3.9
4975 | TORONTO BUTTONVILLE A | 7 | 27 | 7 | 18.175 | 0 | 0.175
4976 | TORONTO BUTTONVILLE A | 7 | 26 | 8 | 23.1 | 0 | 5.1
4976 | TORONTO BUTTONVILLE A | 7 | 27 | 8 | 19.8 | 0 | 1.8
4977 | TORONTO BUTTONVILLE A | 7 | 26 | 9 | 25.3 | 0 | 7.3
4977 | TORONTO BUTTONVILLE A | 7 | 27 | 9 | 21.1 | 0 | 3.1
4978 | TORONTO BUTTONVILLE A | 7 | 26 | 10 | 27.2 | 0 | 9.2
4978 | TORONTO BUTTONVILLE A | 7 | 27 | 10 | 21.925 | 0 | 3.925
4979 | TORONTO BUTTONVILLE A | 7 | 26 | 11 | 29.5 | 0 | 11.5
4979 | TORONTO BUTTONVILLE A | 7 | 27 | 11 | 22.875 | 0 | 4.875
4980 | TORONTO BUTTONVILLE A | 7 | 26 | 12 | 30.7 | 0 | 12.7
4980 | TORONTO BUTTONVILLE A | 7 | 27 | 12 | 23.575 | 0 | 5.575
4981 | TORONTO BUTTONVILLE A | 7 | 26 | 13 | 31.3 | 0 | 13.3
4981 | TORONTO BUTTONVILLE A | 7 | 27 | 13 | 23.725 | 0 | 5.725
4982 | TORONTO BUTTONVILLE A | 7 | 26 | 14 | 31.7 | 0 | 13.7
4982 | TORONTO BUTTONVILLE A | 7 | 27 | 14 | 25.05 | 0 | 7.05
4983 | TORONTO BUTTONVILLE A | 7 | 26 | 15 | 31.8 | 0 | 13.8
4983 | TORONTO BUTTONVILLE A | 7 | 27 | 15 | 25.575 | 0 | 7.575
4984 | TORONTO BUTTONVILLE A | 7 | 26 | 16 | 32.6 | 0 | 14.6
4984 | TORONTO BUTTONVILLE A | 7 | 27 | 16 | 25.825 | 0 | 7.825
4985 | TORONTO BUTTONVILLE A | 7 | 26 | 17 | 31.8 | 0 | 13.8
4985 | TORONTO BUTTONVILLE A | 7 | 27 | 17 | 26.075 | 0 | 8.075
4986 | TORONTO BUTTONVILLE A | 7 | 26 | 18 | 32.9 | 0 | 14.9
4986 | TORONTO BUTTONVILLE A | 7 | 27 | 18 | 26.175 | 0 | 8.175
4987 | TORONTO BUTTONVILLE A | 7 | 26 | 19 | 32.1 | 0 | 14.1
4987 | TORONTO BUTTONVILLE A | 7 | 27 | 19 | 24.9 | 0 | 6.9
4988 | TORONTO BUTTONVILLE A | 7 | 26 | 20 | 31.1 | 0 | 13.1
4988 | TORONTO BUTTONVILLE A | 7 | 27 | 20 | 24.225 | 0 | 6.225
4989 | TORONTO BUTTONVILLE A | 7 | 26 | 21 | 30 | 0 | 12
4989 | TORONTO BUTTONVILLE A | 7 | 27 | 21 | 22.75 | 0 | 4.75
4990 | TORONTO BUTTONVILLE A | 7 | 26 | 22 | 28.6 | 0 | 10.6
4990 | TORONTO BUTTONVILLE A | 7 | 27 | 22 | 21.9 | 0 | 3.9
4991 | TORONTO BUTTONVILLE A | 7 | 26 | 23 | 27.6 | 0 | 9.6
4991 | TORONTO BUTTONVILLE A | 7 | 27 | 23 | 20.425 | 0 | 2.425
4992 | TORONTO BUTTONVILLE A | 7 | 26 | 24 | 26.8 | 0 | 8.8
4992 | TORONTO BUTTONVILLE A | 7 | 27 | 24 | 19.675 | 0 | 1.675
4993 | TORONTO BUTTONVILLE A | 7 | 27 | 1 | 26.2 | 0 | 8.2
4993 | TORONTO BUTTONVILLE A | 7 | 28 | 1 | 19.475 | 0 | 1.475
4994 | TORONTO BUTTONVILLE A | 7 | 27 | 2 | 25.6 | 0 | 7.6
4994 | TORONTO BUTTONVILLE A | 7 | 28 | 2 | 18.9 | 0 | 0.9
4995 | TORONTO BUTTONVILLE A | 7 | 27 | 3 | 25.2 | 0 | 7.2
4995 | TORONTO BUTTONVILLE A | 7 | 28 | 3 | 18.875 | 0 | 0.875
4996 | TORONTO BUTTONVILLE A | 7 | 27 | 4 | 25.3 | 0 | 7.3
4996 | TORONTO BUTTONVILLE A | 7 | 28 | 4 | 18.45 | 0 | 0.45
4997 | TORONTO BUTTONVILLE A | 7 | 27 | 5 | 25.2 | 0 | 7.2
4997 | TORONTO BUTTONVILLE A | 7 | 28 | 5 | 17.85 | 0 | 0
4998 | TORONTO BUTTONVILLE A | 7 | 27 | 6 | 25.3 | 0 | 7.3
4998 | TORONTO BUTTONVILLE A | 7 | 28 | 6 | 17.6 | 0 | 0
4999 | TORONTO BUTTONVILLE A | 7 | 27 | 7 | 25.5 | 0 | 7.5
4999 | TORONTO BUTTONVILLE A | 7 | 28 | 7 | 18.125 | 0 | 0.125
5000 | TORONTO BUTTONVILLE A | 7 | 27 | 8 | 26.6 | 0 | 8.6
5000 | TORONTO BUTTONVILLE A | 7 | 28 | 8 | 18.925 | 0 | 0.925
5001 | TORONTO BUTTONVILLE A | 7 | 27 | 9 | 27.8 | 0 | 9.8
5001 | TORONTO BUTTONVILLE A | 7 | 28 | 9 | 19.925 | 0 | 1.925
5002 | TORONTO BUTTONVILLE A | 7 | 27 | 10 | 28.8 | 0 | 10.8
5002 | TORONTO BUTTONVILLE A | 7 | 28 | 10 | 21.225 | 0 | 3.225
5003 | TORONTO BUTTONVILLE A | 7 | 27 | 11 | 28.1 | 0 | 10.1
5003 | TORONTO BUTTONVILLE A | 7 | 28 | 11 | 22.1 | 0 | 4.1
5004 | TORONTO BUTTONVILLE A | 7 | 27 | 12 | 30.2 | 0 | 12.2
5004 | TORONTO BUTTONVILLE A | 7 | 28 | 12 | 23.025 | 0 | 5.025
5005 | TORONTO BUTTONVILLE A | 7 | 27 | 13 | 25.9 | 0 | 7.9
5005 | TORONTO BUTTONVILLE A | 7 | 28 | 13 | 23.775 | 0 | 5.775
5006 | TORONTO BUTTONVILLE A | 7 | 27 | 14 | 29.1 | 0 | 11.1
5006 | TORONTO BUTTONVILLE A | 7 | 28 | 14 | 24.3 | 0 | 6.3
5007 | TORONTO BUTTONVILLE A | 7 | 27 | 15 | 27.4 | 0 | 9.4
5007 | TORONTO BUTTONVILLE A | 7 | 28 | 15 | 24.225 | 0 | 6.225
5008 | TORONTO BUTTONVILLE A | 7 | 27 | 16 | 29.9 | 0 | 11.9
5008 | TORONTO BUTTONVILLE A | 7 | 28 | 16 | 24.525 | 0 | 6.525
5009 | TORONTO BUTTONVILLE A | 7 | 27 | 17 | 31 | 0 | 13
5009 | TORONTO BUTTONVILLE A | 7 | 28 | 17 | 24.025 | 0 | 6.025
5010 | TORONTO BUTTONVILLE A | 7 | 27 | 18 | 30.9 | 0 | 12.9
5010 | TORONTO BUTTONVILLE A | 7 | 28 | 18 | 23.6 | 0 | 5.6
5011 | TORONTO BUTTONVILLE A | 7 | 27 | 19 | 29.8 | 0 | 11.8
5011 | TORONTO BUTTONVILLE A | 7 | 28 | 19 | 23.275 | 0 | 5.275
5012 | TORONTO BUTTONVILLE A | 7 | 27 | 20 | 28.8 | 0 | 10.8
5012 | TORONTO BUTTONVILLE A | 7 | 28 | 20 | 22.275 | 0 | 4.275
5013 | TORONTO BUTTONVILLE A | 7 | 27 | 21 | 28.1 | 0 | 10.1
5013 | TORONTO BUTTONVILLE A | 7 | 28 | 21 | 20.7 | 0 | 2.7
5014 | TORONTO BUTTONVILLE A | 7 | 27 | 22 | 23.2 | 0 | 5.2
5014 | TORONTO BUTTONVILLE A | 7 | 28 | 22 | 19.75 | 0 | 1.75
5015 | TORONTO BUTTONVILLE A | 7 | 27 | 23 | 22.2 | 0 | 4.2
5015 | TORONTO BUTTONVILLE A | 7 | 28 | 23 | 19 | 0 | 1
5016 | TORONTO BUTTONVILLE A | 7 | 27 | 24 | 22.1 | 0 | 4.1
5016 | TORONTO BUTTONVILLE A | 7 | 28 | 24 | 18.175 | 0 | 0.175
5017 | TORONTO BUTTONVILLE A | 7 | 28 | 1 | 21.6 | 0 | 3.6
5017 | TORONTO BUTTONVILLE A | 7 | 29 | 1 | 17.075 | 0 | 0
5018 | TORONTO BUTTONVILLE A | 7 | 28 | 2 | 20.5 | 0 | 2.5
5018 | TORONTO BUTTONVILLE A | 7 | 29 | 2 | 16.7 | 0 | 0
5019 | TORONTO BUTTONVILLE A | 7 | 28 | 3 | 19.4 | 0 | 1.4
5019 | TORONTO BUTTONVILLE A | 7 | 29 | 3 | 16.575 | 0 | 0
5020 | TORONTO BUTTONVILLE A | 7 | 28 | 4 | 18.9 | 0 | 0.9
5020 | TORONTO BUTTONVILLE A | 7 | 29 | 4 | 16.525 | 0 | 0
5021 | TORONTO BUTTONVILLE A | 7 | 28 | 5 | 18.4 | 0 | 0.4
5021 | TORONTO BUTTONVILLE A | 7 | 29 | 5 | 16.175 | 0 | 0
5022 | TORONTO BUTTONVILLE A | 7 | 28 | 6 | 18 | 0 | 0
5022 | TORONTO BUTTONVILLE A | 7 | 29 | 6 | 16.8 | 0 | 0
5023 | TORONTO BUTTONVILLE A | 7 | 28 | 7 | 18.7 | 0 | 0.7
5023 | TORONTO BUTTONVILLE A | 7 | 29 | 7 | 17.375 | 0 | 0
5024 | TORONTO BUTTONVILLE A | 7 | 28 | 8 | 20.4 | 0 | 2.4
5024 | TORONTO BUTTONVILLE A | 7 | 29 | 8 | 19.425 | 0 | 1.425
5025 | TORONTO BUTTONVILLE A | 7 | 28 | 9 | 22.3 | 0 | 4.3
5025 | TORONTO BUTTONVILLE A | 7 | 29 | 9 | 21.2 | 0 | 3.2
5026 | TORONTO BUTTONVILLE A | 7 | 28 | 10 | 24 | 0 | 6
5026 | TORONTO BUTTONVILLE A | 7 | 29 | 10 | 23.175 | 0 | 5.175
5027 | TORONTO BUTTONVILLE A | 7 | 28 | 11 | 25.2 | 0 | 7.2
5027 | TORONTO BUTTONVILLE A | 7 | 29 | 11 | 23.875 | 0 | 5.875
5028 | TORONTO BUTTONVILLE A | 7 | 28 | 12 | 26.4 | 0 | 8.4
5028 | TORONTO BUTTONVILLE A | 7 | 29 | 12 | 24.65 | 0 | 6.65
5029 | TORONTO BUTTONVILLE A | 7 | 28 | 13 | 26 | 0 | 8
5029 | TORONTO BUTTONVILLE A | 7 | 29 | 13 | 24.75 | 0 | 6.75
5030 | TORONTO BUTTONVILLE A | 7 | 28 | 14 | 27.4 | 0 | 9.4
5030 | TORONTO BUTTONVILLE A | 7 | 29 | 14 | 24.7 | 0 | 6.7
5031 | TORONTO BUTTONVILLE A | 7 | 28 | 15 | 26.2 | 0 | 8.2
5031 | TORONTO BUTTONVILLE A | 7 | 29 | 15 | 25.55 | 0 | 7.55
5032 | TORONTO BUTTONVILLE A | 7 | 28 | 16 | 28.1 | 0 | 10.1
5032 | TORONTO BUTTONVILLE A | 7 | 29 | 16 | 26.375 | 0 | 8.375
5033 | TORONTO BUTTONVILLE A | 7 | 28 | 17 | 28.8 | 0 | 10.8
5033 | TORONTO BUTTONVILLE A | 7 | 29 | 17 | 25.375 | 0 | 7.375
5034 | TORONTO BUTTONVILLE A | 7 | 28 | 18 | 28.4 | 0 | 10.4
5034 | TORONTO BUTTONVILLE A | 7 | 29 | 18 | 24.45 | 0 | 6.45
5035 | TORONTO BUTTONVILLE A | 7 | 28 | 19 | 27.8 | 0 | 9.8
5035 | TORONTO BUTTONVILLE A | 7 | 29 | 19 | 24.1 | 0 | 6.1
5036 | TORONTO BUTTONVILLE A | 7 | 28 | 20 | 26.8 | 0 | 8.8
5036 | TORONTO BUTTONVILLE A | 7 | 29 | 20 | 23.325 | 0 | 5.325
5037 | TORONTO BUTTONVILLE A | 7 | 28 | 21 | 25.4 | 0 | 7.4
5037 | TORONTO BUTTONVILLE A | 7 | 29 | 21 | 21.775 | 0 | 3.775
5038 | TORONTO BUTTONVILLE A | 7 | 28 | 22 | 24.2 | 0 | 6.2
5038 | TORONTO BUTTONVILLE A | 7 | 29 | 22 | 20.675 | 0 | 2.675
5039 | TORONTO BUTTONVILLE A | 7 | 28 | 23 | 22.8 | 0 | 4.8
5039 | TORONTO BUTTONVILLE A | 7 | 29 | 23 | 19.85 | 0 | 1.85
5040 | TORONTO BUTTONVILLE A | 7 | 28 | 24 | 23.1 | 0 | 5.1
5040 | TORONTO BUTTONVILLE A | 7 | 29 | 24 | 19.4 | 0 | 1.4
5041 | TORONTO BUTTONVILLE A | 7 | 29 | 1 | 22.4 | 0 | 4.4
5041 | TORONTO BUTTONVILLE A | 7 | 30 | 1 | 19.075 | 0 | 1.075
5042 | TORONTO BUTTONVILLE A | 7 | 29 | 2 | 21.5 | 0 | 3.5
5042 | TORONTO BUTTONVILLE A | 7 | 30 | 2 | 18.675 | 0 | 0.675
5043 | TORONTO BUTTONVILLE A | 7 | 29 | 3 | 21.9 | 0 | 3.9
5043 | TORONTO BUTTONVILLE A | 7 | 30 | 3 | 18.375 | 0 | 0.375
5044 | TORONTO BUTTONVILLE A | 7 | 29 | 4 | 21.6 | 0 | 3.6
5044 | TORONTO BUTTONVILLE A | 7 | 30 | 4 | 17.75 | 0 | 0
5045 | TORONTO BUTTONVILLE A | 7 | 29 | 5 | 20.9 | 0 | 2.9
5045 | TORONTO BUTTONVILLE A | 7 | 30 | 5 | 17.6 | 0 | 0
5046 | TORONTO BUTTONVILLE A | 7 | 29 | 6 | 19.9 | 0 | 1.9
5046 | TORONTO BUTTONVILLE A | 7 | 30 | 6 | 17 | 0 | 0
5047 | TORONTO BUTTONVILLE A | 7 | 29 | 7 | 18.9 | 0 | 0.9
5047 | TORONTO BUTTONVILLE A | 7 | 30 | 7 | 17.4 | 0 | 0
5048 | TORONTO BUTTONVILLE A | 7 | 29 | 8 | 20 | 0 | 2
5048 | TORONTO BUTTONVILLE A | 7 | 30 | 8 | 18.675 | 0 | 0.675
5049 | TORONTO BUTTONVILLE A | 7 | 29 | 9 | 22.5 | 0 | 4.5
5049 | TORONTO BUTTONVILLE A | 7 | 30 | 9 | 20.075 | 0 | 2.075
5050 | TORONTO BUTTONVILLE A | 7 | 29 | 10 | 23.9 | 0 | 5.9
5050 | TORONTO BUTTONVILLE A | 7 | 30 | 10 | 21.375 | 0 | 3.375
5051 | TORONTO BUTTONVILLE A | 7 | 29 | 11 | 25 | 0 | 7
5051 | TORONTO BUTTONVILLE A | 7 | 30 | 11 | 22.15 | 0 | 4.15
5052 | TORONTO BUTTONVILLE A | 7 | 29 | 12 | 26.3 | 0 | 8.3
5052 | TORONTO BUTTONVILLE A | 7 | 30 | 12 | 23.325 | 0 | 5.325
5053 | TORONTO BUTTONVILLE A | 7 | 29 | 13 | 27.4 | 0 | 9.4
5053 | TORONTO BUTTONVILLE A | 7 | 30 | 13 | 24.225 | 0 | 6.225
5054 | TORONTO BUTTONVILLE A | 7 | 29 | 14 | 27.2 | 0 | 9.2
5054 | TORONTO BUTTONVILLE A | 7 | 30 | 14 | 23.95 | 0 | 5.95
5055 | TORONTO BUTTONVILLE A | 7 | 29 | 15 | 28.3 | 0 | 10.3
5055 | TORONTO BUTTONVILLE A | 7 | 30 | 15 | 24.175 | 0 | 6.175
5056 | TORONTO BUTTONVILLE A | 7 | 29 | 16 | 28.7 | 0 | 10.7
5056 | TORONTO BUTTONVILLE A | 7 | 30 | 16 | 24.525 | 0 | 6.525
5057 | TORONTO BUTTONVILLE A | 7 | 29 | 17 | 27 | 0 | 9
5057 | TORONTO BUTTONVILLE A | 7 | 30 | 17 | 24.825 | 0 | 6.825
5058 | TORONTO BUTTONVILLE A | 7 | 29 | 18 | 27.3 | 0 | 9.3
5058 | TORONTO BUTTONVILLE A | 7 | 30 | 18 | 24.25 | 0 | 6.25
5059 | TORONTO BUTTONVILLE A | 7 | 29 | 19 | 26.8 | 0 | 8.8
5059 | TORONTO BUTTONVILLE A | 7 | 30 | 19 | 23.25 | 0 | 5.25
5060 | TORONTO BUTTONVILLE A | 7 | 29 | 20 | 25.2 | 0 | 7.2
5060 | TORONTO BUTTONVILLE A | 7 | 30 | 20 | 22.05 | 0 | 4.05
5061 | TORONTO BUTTONVILLE A | 7 | 29 | 21 | 24.3 | 0 | 6.3
5061 | TORONTO BUTTONVILLE A | 7 | 30 | 21 | 20.625 | 0 | 2.625
5062 | TORONTO BUTTONVILLE A | 7 | 29 | 22 | 23.6 | 0 | 5.6
5062 | TORONTO BUTTONVILLE A | 7 | 30 | 22 | 19.175 | 0 | 1.175
5063 | TORONTO BUTTONVILLE A | 7 | 29 | 23 | 22.4 | 0 | 4.4
5063 | TORONTO BUTTONVILLE A | 7 | 30 | 23 | 18.45 | 0 | 0.45
5064 | TORONTO BUTTONVILLE A | 7 | 29 | 24 | 20.8 | 0 | 2.8
5064 | TORONTO BUTTONVILLE A | 7 | 30 | 24 | 17.975 | 0 | 0
5065 | TORONTO BUTTONVILLE A | 7 | 30 | 1 | 20.7 | 0 | 2.7
5065 | TORONTO BUTTONVILLE A | 7 | 31 | 1 | 17.275 | 0 | 0
5066 | TORONTO BUTTONVILLE A | 7 | 30 | 2 | 19.2 | 0 | 1.2
5066 | TORONTO BUTTONVILLE A | 7 | 31 | 2 | 16.875 | 0 | 0
5067 | TORONTO BUTTONVILLE A | 7 | 30 | 3 | 17.9 | 0 | 0
5067 | TORONTO BUTTONVILLE A | 7 | 31 | 3 | 16.45 | 0 | 0
5068 | TORONTO BUTTONVILLE A | 7 | 30 | 4 | 17.9 | 0 | 0
5068 | TORONTO BUTTONVILLE A | 7 | 31 | 4 | 15.8 | 0 | 0
5069 | TORONTO BUTTONVILLE A | 7 | 30 | 5 | 17.6 | 0 | 0
5069 | TORONTO BUTTONVILLE A | 7 | 31 | 5 | 15.35 | 0 | 0
5070 | TORONTO BUTTONVILLE A | 7 | 30 | 6 | 16.5 | 0 | 0
5070 | TORONTO BUTTONVILLE A | 7 | 31 | 6 | 15.15 | 0 | 0
5071 | TORONTO BUTTONVILLE A | 7 | 30 | 7 | 17.3 | 0 | 0
5071 | TORONTO BUTTONVILLE A | 7 | 31 | 7 | 16.15 | 0 | 0
5072 | TORONTO BUTTONVILLE A | 7 | 30 | 8 | 19.6 | 0 | 1.6
5072 | TORONTO BUTTONVILLE A | 7 | 31 | 8 | 18.05 | 0 | 0.05
5073 | TORONTO BUTTONVILLE A | 7 | 30 | 9 | 21.6 | 0 | 3.6
5073 | TORONTO BUTTONVILLE A | 7 | 31 | 9 | 19.875 | 0 | 1.875
5074 | TORONTO BUTTONVILLE A | 7 | 30 | 10 | 23.2 | 0 | 5.2
5074 | TORONTO BUTTONVILLE A | 7 | 31 | 10 | 21.5 | 0 | 3.5
5075 | TORONTO BUTTONVILLE A | 7 | 30 | 11 | 24.4 | 0 | 6.4
5075 | TORONTO BUTTONVILLE A | 7 | 31 | 11 | 22.725 | 0 | 4.725
5076 | TORONTO BUTTONVILLE A | 7 | 30 | 12 | 24.9 | 0 | 6.9
5076 | TORONTO BUTTONVILLE A | 7 | 31 | 12 | 23.65 | 0 | 5.65
5077 | TORONTO BUTTONVILLE A | 7 | 30 | 13 | 25 | 0 | 7
5077 | TORONTO BUTTONVILLE A | 7 | 31 | 13 | 24.275 | 0 | 6.275
5078 | TORONTO BUTTONVILLE A | 7 | 30 | 14 | 25.8 | 0 | 7.8
5078 | TORONTO BUTTONVILLE A | 7 | 31 | 14 | 24.775 | 0 | 6.775
5079 | TORONTO BUTTONVILLE A | 7 | 30 | 15 | 26.4 | 0 | 8.4
5079 | TORONTO BUTTONVILLE A | 7 | 31 | 15 | 24.775 | 0 | 6.775
5080 | TORONTO BUTTONVILLE A | 7 | 30 | 16 | 26.8 | 0 | 8.8
5080 | TORONTO BUTTONVILLE A | 7 | 31 | 16 | 24.975 | 0 | 6.975
5081 | TORONTO BUTTONVILLE A | 7 | 30 | 17 | 26.1 | 0 | 8.1
5081 | TORONTO BUTTONVILLE A | 7 | 31 | 17 | 24.575 | 0 | 6.575
5082 | TORONTO BUTTONVILLE A | 7 | 30 | 18 | 26.9 | 0 | 8.9
5082 | TORONTO BUTTONVILLE A | 7 | 31 | 18 | 24.05 | 0 | 6.05
5083 | TORONTO BUTTONVILLE A | 7 | 30 | 19 | 25.1 | 0 | 7.1
5083 | TORONTO BUTTONVILLE A | 7 | 31 | 19 | 22.5 | 0 | 4.5
5084 | TORONTO BUTTONVILLE A | 7 | 30 | 20 | 24.1 | 0 | 6.1
5084 | TORONTO BUTTONVILLE A | 7 | 31 | 20 | 21.925 | 0 | 3.925
5085 | TORONTO BUTTONVILLE A | 7 | 30 | 21 | 22.5 | 0 | 4.5
5085 | TORONTO BUTTONVILLE A | 7 | 31 | 21 | 20.875 | 0 | 2.875
5086 | TORONTO BUTTONVILLE A | 7 | 30 | 22 | 21.5 | 0 | 3.5
5086 | TORONTO BUTTONVILLE A | 7 | 31 | 22 | 20.375 | 0 | 2.375
5087 | TORONTO BUTTONVILLE A | 7 | 30 | 23 | 22.1 | 0 | 4.1
5087 | TORONTO BUTTONVILLE A | 7 | 31 | 23 | 19.7 | 0 | 1.7
5088 | TORONTO BUTTONVILLE A | 7 | 30 | 24 | 20.4 | 0 | 2.4
5088 | TORONTO BUTTONVILLE A | 7 | 31 | 24 | 19.3 | 0 | 1.3
5089 | TORONTO BUTTONVILLE A | 7 | 31 | 1 | 19.1 | 0 | 1.1
5089 | TORONTO BUTTONVILLE A | 8 | 1 | 1 | 19 | 0 | 1
5090 | TORONTO BUTTONVILLE A | 7 | 31 | 2 | 18.4 | 0 | 0.4
5090 | TORONTO BUTTONVILLE A | 8 | 1 | 2 | 18.6 | 0 | 0.6
5091 | TORONTO BUTTONVILLE A | 7 | 31 | 3 | 18.7 | 0 | 0.7
5091 | TORONTO BUTTONVILLE A | 8 | 1 | 3 | 18.175 | 0 | 0.175
5092 | TORONTO BUTTONVILLE A | 7 | 31 | 4 | 18.3 | 0 | 0.3
5092 | TORONTO BUTTONVILLE A | 8 | 1 | 4 | 17.725 | 0 | 0
5093 | TORONTO BUTTONVILLE A | 7 | 31 | 5 | 18.3 | 0 | 0.3
5093 | TORONTO BUTTONVILLE A | 8 | 1 | 5 | 17.725 | 0 | 0
5094 | TORONTO BUTTONVILLE A | 7 | 31 | 6 | 18 | 0 | 0
5094 | TORONTO BUTTONVILLE A | 8 | 1 | 6 | 17.35 | 0 | 0
5095 | TORONTO BUTTONVILLE A | 7 | 31 | 7 | 18.4 | 0 | 0.4
5095 | TORONTO BUTTONVILLE A | 8 | 1 | 7 | 17.625 | 0 | 0
5096 | TORONTO BUTTONVILLE A | 7 | 31 | 8 | 20.6 | 0 | 2.6
5096 | TORONTO BUTTONVILLE A | 8 | 1 | 8 | 19.575 | 0 | 1.575
5097 | TORONTO BUTTONVILLE A | 7 | 31 | 9 | 22.4 | 0 | 4.4
5097 | TORONTO BUTTONVILLE A | 8 | 1 | 9 | 20.9 | 0 | 2.9
5098 | TORONTO BUTTONVILLE A | 7 | 31 | 10 | 24.8 | 0 | 6.8
5098 | TORONTO BUTTONVILLE A | 8 | 1 | 10 | 22.375 | 0 | 4.375
5099 | TORONTO BUTTONVILLE A | 7 | 31 | 11 | 25.2 | 0 | 7.2
5099 | TORONTO BUTTONVILLE A | 8 | 1 | 11 | 23.025 | 0 | 5.025
5100 | TORONTO BUTTONVILLE A | 7 | 31 | 12 | 26.4 | 0 | 8.4
5100 | TORONTO BUTTONVILLE A | 8 | 1 | 12 | 23.95 | 0 | 5.95
5101 | TORONTO BUTTONVILLE A | 7 | 31 | 13 | 26.2 | 0 | 8.2
5101 | TORONTO BUTTONVILLE A | 8 | 1 | 13 | 24.15 | 0 | 6.15
5102 | TORONTO BUTTONVILLE A | 7 | 31 | 14 | 27.1 | 0 | 9.1
5102 | TORONTO BUTTONVILLE A | 8 | 1 | 14 | 24.45 | 0 | 6.45
5103 | TORONTO BUTTONVILLE A | 7 | 31 | 15 | 26.7 | 0 | 8.7
5103 | TORONTO BUTTONVILLE A | 8 | 1 | 15 | 24.725 | 0 | 6.725
5104 | TORONTO BUTTONVILLE A | 7 | 31 | 16 | 27.4 | 0 | 9.4
5104 | TORONTO BUTTONVILLE A | 8 | 1 | 16 | 23.6 | 0 | 5.6
5105 | TORONTO BUTTONVILLE A | 7 | 31 | 17 | 27 | 0 | 9
5105 | TORONTO BUTTONVILLE A | 8 | 1 | 17 | 23.45 | 0 | 5.45
5106 | TORONTO BUTTONVILLE A | 7 | 31 | 18 | 26.3 | 0 | 8.3
5106 | TORONTO BUTTONVILLE A | 8 | 1 | 18 | 23.45 | 0 | 5.45
5107 | TORONTO BUTTONVILLE A | 7 | 31 | 19 | 26.5 | 0 | 8.5
5107 | TORONTO BUTTONVILLE A | 8 | 1 | 19 | 22.15 | 0 | 4.15
5108 | TORONTO BUTTONVILLE A | 7 | 31 | 20 | 25.9 | 0 | 7.9
5108 | TORONTO BUTTONVILLE A | 8 | 1 | 20 | 21.925 | 0 | 3.925
5109 | TORONTO BUTTONVILLE A | 7 | 31 | 21 | 24.2 | 0 | 6.2
5109 | TORONTO BUTTONVILLE A | 8 | 1 | 21 | 21.175 | 0 | 3.175
5110 | TORONTO BUTTONVILLE A | 7 | 31 | 22 | 22.7 | 0 | 4.7
5110 | TORONTO BUTTONVILLE A | 8 | 1 | 22 | 19.9 | 0 | 1.9
5111 | TORONTO BUTTONVILLE A | 7 | 31 | 23 | 21.4 | 0 | 3.4
5111 | TORONTO BUTTONVILLE A | 8 | 1 | 23 | 19.5 | 0 | 1.5
5112 | TORONTO BUTTONVILLE A | 7 | 31 | 24 | 20.4 | 0 | 2.4
5112 | TORONTO BUTTONVILLE A | 8 | 1 | 24 | 18.7 | 0 | 0.7
5113 | TORONTO BUTTONVILLE A | 8 | 1 | 1 | 19.8 | 0 | 1.8
5113 | TORONTO BUTTONVILLE A | 8 | 2 | 1 | 18.075 | 0 | 0.075
5114 | TORONTO BUTTONVILLE A | 8 | 1 | 2 | 19.5 | 0 | 1.5
5114 | TORONTO BUTTONVILLE A | 8 | 2 | 2 | 17.425 | 0 | 0
5115 | TORONTO BUTTONVILLE A | 8 | 1 | 3 | 19.2 | 0 | 1.2
5115 | TORONTO BUTTONVILLE A | 8 | 2 | 3 | 16.8 | 0 | 0
5116 | TORONTO BUTTONVILLE A | 8 | 1 | 4 | 19 | 0 | 1
5116 | TORONTO BUTTONVILLE A | 8 | 2 | 4 | 16.6 | 0 | 0
5117 | TORONTO BUTTONVILLE A | 8 | 1 | 5 | 18.6 | 0 | 0.6
5117 | TORONTO BUTTONVILLE A | 8 | 2 | 5 | 16.075 | 0 | 0
5118 | TORONTO BUTTONVILLE A | 8 | 1 | 6 | 18.1 | 0 | 0.1
5118 | TORONTO BUTTONVILLE A | 8 | 2 | 6 | 16.2 | 0 | 0
5119 | TORONTO BUTTONVILLE A | 8 | 1 | 7 | 18.8 | 0 | 0.8
5119 | TORONTO BUTTONVILLE A | 8 | 2 | 7 | 16.7 | 0 | 0
5120 | TORONTO BUTTONVILLE A | 8 | 1 | 8 | 21.2 | 0 | 3.2
5120 | TORONTO BUTTONVILLE A | 8 | 2 | 8 | 19.2 | 0 | 1.2
5121 | TORONTO BUTTONVILLE A | 8 | 1 | 9 | 23.3 | 0 | 5.3
5121 | TORONTO BUTTONVILLE A | 8 | 2 | 9 | 21.05 | 0 | 3.05
5122 | TORONTO BUTTONVILLE A | 8 | 1 | 10 | 25.3 | 0 | 7.3
5122 | TORONTO BUTTONVILLE A | 8 | 2 | 10 | 23.025 | 0 | 5.025
5123 | TORONTO BUTTONVILLE A | 8 | 1 | 11 | 26.6 | 0 | 8.6
5123 | TORONTO BUTTONVILLE A | 8 | 2 | 11 | 24.65 | 0 | 6.65
5124 | TORONTO BUTTONVILLE A | 8 | 1 | 12 | 28 | 0 | 10
5124 | TORONTO BUTTONVILLE A | 8 | 2 | 12 | 25.575 | 0 | 7.575
5125 | TORONTO BUTTONVILLE A | 8 | 1 | 13 | 28.6 | 0 | 10.6
5125 | TORONTO BUTTONVILLE A | 8 | 2 | 13 | 26.15 | 0 | 8.15
5126 | TORONTO BUTTONVILLE A | 8 | 1 | 14 | 28.6 | 0 | 10.6
5126 | TORONTO BUTTONVILLE A | 8 | 2 | 14 | 26.075 | 0 | 8.075
5127 | TORONTO BUTTONVILLE A | 8 | 1 | 15 | 29.2 | 0 | 11.2
5127 | TORONTO BUTTONVILLE A | 8 | 2 | 15 | 26.25 | 0 | 8.25
5128 | TORONTO BUTTONVILLE A | 8 | 1 | 16 | 28.9 | 0 | 10.9
5128 | TORONTO BUTTONVILLE A | 8 | 2 | 16 | 26.775 | 0 | 8.775
5129 | TORONTO BUTTONVILLE A | 8 | 1 | 17 | 28 | 0 | 10
5129 | TORONTO BUTTONVILLE A | 8 | 2 | 17 | 25.925 | 0 | 7.925
5130 | TORONTO BUTTONVILLE A | 8 | 1 | 18 | 26.7 | 0 | 8.7
5130 | TORONTO BUTTONVILLE A | 8 | 2 | 18 | 24.425 | 0 | 6.425
5131 | TORONTO BUTTONVILLE A | 8 | 1 | 19 | 26 | 0 | 8
5131 | TORONTO BUTTONVILLE A | 8 | 2 | 19 | 24.1 | 0 | 6.1
5132 | TORONTO BUTTONVILLE A | 8 | 1 | 20 | 25.4 | 0 | 7.4
5132 | TORONTO BUTTONVILLE A | 8 | 2 | 20 | 23.5 | 0 | 5.5
5133 | TORONTO BUTTONVILLE A | 8 | 1 | 21 | 24.5 | 0 | 6.5
5133 | TORONTO BUTTONVILLE A | 8 | 2 | 21 | 22.225 | 0 | 4.225
5134 | TORONTO BUTTONVILLE A | 8 | 1 | 22 | 23.3 | 0 | 5.3
5134 | TORONTO BUTTONVILLE A | 8 | 2 | 22 | 21.525 | 0 | 3.525
5135 | TORONTO BUTTONVILLE A | 8 | 1 | 23 | 23.7 | 0 | 5.7
5135 | TORONTO BUTTONVILLE A | 8 | 2 | 23 | 20.025 | 0 | 2.025
5136 | TORONTO BUTTONVILLE A | 8 | 1 | 24 | 22.8 | 0 | 4.8
5136 | TORONTO BUTTONVILLE A | 8 | 2 | 24 | 19.475 | 0 | 1.475
5137 | TORONTO BUTTONVILLE A | 8 | 2 | 1 | 20.9 | 0 | 2.9
5137 | TORONTO BUTTONVILLE A | 8 | 3 | 1 | 18.675 | 0 | 0.675
5138 | TORONTO BUTTONVILLE A | 8 | 2 | 2 | 20.9 | 0 | 2.9
5138 | TORONTO BUTTONVILLE A | 8 | 3 | 2 | 17.525 | 0 | 0
5139 | TORONTO BUTTONVILLE A | 8 | 2 | 3 | 20.9 | 0 | 2.9
5139 | TORONTO BUTTONVILLE A | 8 | 3 | 3 | 17 | 0 | 0
5140 | TORONTO BUTTONVILLE A | 8 | 2 | 4 | 20.3 | 0 | 2.3
5140 | TORONTO BUTTONVILLE A | 8 | 3 | 4 | 16.4 | 0 | 0
5141 | TORONTO BUTTONVILLE A | 8 | 2 | 5 | 19.7 | 0 | 1.7
5141 | TORONTO BUTTONVILLE A | 8 | 3 | 5 | 16.25 | 0 | 0
5142 | TORONTO BUTTONVILLE A | 8 | 2 | 6 | 19.5 | 0 | 1.5
5142 | TORONTO BUTTONVILLE A | 8 | 3 | 6 | 16.375 | 0 | 0
5143 | TORONTO BUTTONVILLE A | 8 | 2 | 7 | 19.3 | 0 | 1.3
5143 | TORONTO BUTTONVILLE A | 8 | 3 | 7 | 17 | 0 | 0
5144 | TORONTO BUTTONVILLE A | 8 | 2 | 8 | 19.4 | 0 | 1.4
5144 | TORONTO BUTTONVILLE A | 8 | 3 | 8 | 19.45 | 0 | 1.45
5145 | TORONTO BUTTONVILLE A | 8 | 2 | 9 | 19.6 | 0 | 1.6
5145 | TORONTO BUTTONVILLE A | 8 | 3 | 9 | 22.1 | 0 | 4.1
5146 | TORONTO BUTTONVILLE A | 8 | 2 | 10 | 20.4 | 0 | 2.4
5146 | TORONTO BUTTONVILLE A | 8 | 3 | 10 | 23.65 | 0 | 5.65
5147 | TORONTO BUTTONVILLE A | 8 | 2 | 11 | 22.1 | 0 | 4.1
5147 | TORONTO BUTTONVILLE A | 8 | 3 | 11 | 24.75 | 0 | 6.75
5148 | TORONTO BUTTONVILLE A | 8 | 2 | 12 | 23.3 | 0 | 5.3
5148 | TORONTO BUTTONVILLE A | 8 | 3 | 12 | 25.4 | 0 | 7.4
5149 | TORONTO BUTTONVILLE A | 8 | 2 | 13 | 25.2 | 0 | 7.2
5149 | TORONTO BUTTONVILLE A | 8 | 3 | 13 | 27.025 | 0 | 9.025
5150 | TORONTO BUTTONVILLE A | 8 | 2 | 14 | 25.2 | 0 | 7.2
5150 | TORONTO BUTTONVILLE A | 8 | 3 | 14 | 26.7 | 0 | 8.7
5151 | TORONTO BUTTONVILLE A | 8 | 2 | 15 | 26.3 | 0 | 8.3
5151 | TORONTO BUTTONVILLE A | 8 | 3 | 15 | 26.7 | 0 | 8.7
5152 | TORONTO BUTTONVILLE A | 8 | 2 | 16 | 26.6 | 0 | 8.6
5152 | TORONTO BUTTONVILLE A | 8 | 3 | 16 | 26.8 | 0 | 8.8
5153 | TORONTO BUTTONVILLE A | 8 | 2 | 17 | 26.4 | 0 | 8.4
5153 | TORONTO BUTTONVILLE A | 8 | 3 | 17 | 26.825 | 0 | 8.825
5154 | TORONTO BUTTONVILLE A | 8 | 2 | 18 | 25.6 | 0 | 7.6
5154 | TORONTO BUTTONVILLE A | 8 | 3 | 18 | 26.575 | 0 | 8.575
5155 | TORONTO BUTTONVILLE A | 8 | 2 | 19 | 23.8 | 0 | 5.8
5155 | TORONTO BUTTONVILLE A | 8 | 3 | 19 | 26.05 | 0 | 8.05
5156 | TORONTO BUTTONVILLE A | 8 | 2 | 20 | 23 | 0 | 5
5156 | TORONTO BUTTONVILLE A | 8 | 3 | 20 | 24.4 | 0 | 6.4
5157 | TORONTO BUTTONVILLE A | 8 | 2 | 21 | 20.9 | 0 | 2.9
5157 | TORONTO BUTTONVILLE A | 8 | 3 | 21 | 23.025 | 0 | 5.025
5158 | TORONTO BUTTONVILLE A | 8 | 2 | 22 | 19.7 | 0 | 1.7
5158 | TORONTO BUTTONVILLE A | 8 | 3 | 22 | 22.3 | 0 | 4.3
5159 | TORONTO BUTTONVILLE A | 8 | 2 | 23 | 18.8 | 0 | 0.8
5159 | TORONTO BUTTONVILLE A | 8 | 3 | 23 | 21.675 | 0 | 3.675
5160 | TORONTO BUTTONVILLE A | 8 | 2 | 24 | 19.1 | 0 | 1.1
5160 | TORONTO BUTTONVILLE A | 8 | 3 | 24 | 20.675 | 0 | 2.675
5161 | TORONTO BUTTONVILLE A | 8 | 3 | 1 | 19.1 | 0 | 1.1
5161 | TORONTO BUTTONVILLE A | 8 | 4 | 1 | 20.075 | 0 | 2.075
5162 | TORONTO BUTTONVILLE A | 8 | 3 | 2 | 19 | 0 | 1
5162 | TORONTO BUTTONVILLE A | 8 | 4 | 2 | 19.325 | 0 | 1.325
5163 | TORONTO BUTTONVILLE A | 8 | 3 | 3 | 18.5 | 0 | 0.5
5163 | TORONTO BUTTONVILLE A | 8 | 4 | 3 | 19.3 | 0 | 1.3
5164 | TORONTO BUTTONVILLE A | 8 | 3 | 4 | 18.1 | 0 | 0.1
5164 | TORONTO BUTTONVILLE A | 8 | 4 | 4 | 18.825 | 0 | 0.825
5165 | TORONTO BUTTONVILLE A | 8 | 3 | 5 | 18.3 | 0 | 0.3
5165 | TORONTO BUTTONVILLE A | 8 | 4 | 5 | 18.475 | 0 | 0.475
5166 | TORONTO BUTTONVILLE A | 8 | 3 | 6 | 18 | 0 | 0
5166 | TORONTO BUTTONVILLE A | 8 | 4 | 6 | 18.175 | 0 | 0.175
5167 | TORONTO BUTTONVILLE A | 8 | 3 | 7 | 18.1 | 0 | 0.1
5167 | TORONTO BUTTONVILLE A | 8 | 4 | 7 | 18.275 | 0 | 0.275
5168 | TORONTO BUTTONVILLE A | 8 | 3 | 8 | 18.7 | 0 | 0.7
5168 | TORONTO BUTTONVILLE A | 8 | 4 | 8 | 19.125 | 0 | 1.125
5169 | TORONTO BUTTONVILLE A | 8 | 3 | 9 | 19.2 | 0 | 1.2
5169 | TORONTO BUTTONVILLE A | 8 | 4 | 9 | 21.175 | 0 | 3.175
5170 | TORONTO BUTTONVILLE A | 8 | 3 | 10 | 19.7 | 0 | 1.7
5170 | TORONTO BUTTONVILLE A | 8 | 4 | 10 | 23.375 | 0 | 5.375
5171 | TORONTO BUTTONVILLE A | 8 | 3 | 11 | 21.4 | 0 | 3.4
5171 | TORONTO BUTTONVILLE A | 8 | 4 | 11 | 24.625 | 0 | 6.625
5172 | TORONTO BUTTONVILLE A | 8 | 3 | 12 | 22.5 | 0 | 4.5
5172 | TORONTO BUTTONVILLE A | 8 | 4 | 12 | 25.825 | 0 | 7.825
5173 | TORONTO BUTTONVILLE A | 8 | 3 | 13 | 24.2 | 0 | 6.2
5173 | TORONTO BUTTONVILLE A | 8 | 4 | 13 | 26.275 | 0 | 8.275
5174 | TORONTO BUTTONVILLE A | 8 | 3 | 14 | 23.4 | 0 | 5.4
5174 | TORONTO BUTTONVILLE A | 8 | 4 | 14 | 26.9 | 0 | 8.9
5175 | TORONTO BUTTONVILLE A | 8 | 3 | 15 | 24.1 | 0 | 6.1
5175 | TORONTO BUTTONVILLE A | 8 | 4 | 15 | 27.075 | 0 | 9.075
5176 | TORONTO BUTTONVILLE A | 8 | 3 | 16 | 23 | 0 | 5
5176 | TORONTO BUTTONVILLE A | 8 | 4 | 16 | 27 | 0 | 9
5177 | TORONTO BUTTONVILLE A | 8 | 3 | 17 | 19.4 | 0 | 1.4
5177 | TORONTO BUTTONVILLE A | 8 | 4 | 17 | 25.95 | 0 | 7.95
5178 | TORONTO BUTTONVILLE A | 8 | 3 | 18 | 19.2 | 0 | 1.2
5178 | TORONTO BUTTONVILLE A | 8 | 4 | 18 | 25.55 | 0 | 7.55
5179 | TORONTO BUTTONVILLE A | 8 | 3 | 19 | 19.5 | 0 | 1.5
5179 | TORONTO BUTTONVILLE A | 8 | 4 | 19 | 25.1 | 0 | 7.1
5180 | TORONTO BUTTONVILLE A | 8 | 3 | 20 | 19.1 | 0 | 1.1
5180 | TORONTO BUTTONVILLE A | 8 | 4 | 20 | 24.075 | 0 | 6.075
5181 | TORONTO BUTTONVILLE A | 8 | 3 | 21 | 19.1 | 0 | 1.1
5181 | TORONTO BUTTONVILLE A | 8 | 4 | 21 | 22.4 | 0 | 4.4
5182 | TORONTO BUTTONVILLE A | 8 | 3 | 22 | 18.9 | 0 | 0.9
5182 | TORONTO BUTTONVILLE A | 8 | 4 | 22 | 21.65 | 0 | 3.65
5183 | TORONTO BUTTONVILLE A | 8 | 3 | 23 | 19 | 0 | 1
5183 | TORONTO BUTTONVILLE A | 8 | 4 | 23 | 20.025 | 0 | 2.025
5184 | TORONTO BUTTONVILLE A | 8 | 3 | 24 | 19.1 | 0 | 1.1
5184 | TORONTO BUTTONVILLE A | 8 | 4 | 24 | 18.9 | 0 | 0.9
5185 | TORONTO BUTTONVILLE A | 8 | 4 | 1 | 19.2 | 0 | 1.2
5185 | TORONTO BUTTONVILLE A | 8 | 5 | 1 | 18.175 | 0 | 0.175
5186 | TORONTO BUTTONVILLE A | 8 | 4 | 2 | 19 | 0 | 1
5186 | TORONTO BUTTONVILLE A | 8 | 5 | 2 | 17.275 | 0 | 0
5187 | TORONTO BUTTONVILLE A | 8 | 4 | 3 | 19.1 | 0 | 1.1
5187 | TORONTO BUTTONVILLE A | 8 | 5 | 3 | 17.1 | 0 | 0
5188 | TORONTO BUTTONVILLE A | 8 | 4 | 4 | 19.4 | 0 | 1.4
5188 | TORONTO BUTTONVILLE A | 8 | 5 | 4 | 16.675 | 0 | 0
5189 | TORONTO BUTTONVILLE A | 8 | 4 | 5 | 19.5 | 0 | 1.5
5189 | TORONTO BUTTONVILLE A | 8 | 5 | 5 | 16.775 | 0 | 0
5190 | TORONTO BUTTONVILLE A | 8 | 4 | 6 | 19.6 | 0 | 1.6
5190 | TORONTO BUTTONVILLE A | 8 | 5 | 6 | 16.075 | 0 | 0
5191 | TORONTO BUTTONVILLE A | 8 | 4 | 7 | 19.6 | 0 | 1.6
5191 | TORONTO BUTTONVILLE A | 8 | 5 | 7 | 16.85 | 0 | 0
5192 | TORONTO BUTTONVILLE A | 8 | 4 | 8 | 19.6 | 0 | 1.6
5192 | TORONTO BUTTONVILLE A | 8 | 5 | 8 | 18.775 | 0 | 0.775
5193 | TORONTO BUTTONVILLE A | 8 | 4 | 9 | 20 | 0 | 2
5193 | TORONTO BUTTONVILLE A | 8 | 5 | 9 | 21.15 | 0 | 3.15
5194 | TORONTO BUTTONVILLE A | 8 | 4 | 10 | 20.3 | 0 | 2.3
5194 | TORONTO BUTTONVILLE A | 8 | 5 | 10 | 23.225 | 0 | 5.225
5195 | TORONTO BUTTONVILLE A | 8 | 4 | 11 | 20.9 | 0 | 2.9
5195 | TORONTO BUTTONVILLE A | 8 | 5 | 11 | 24.875 | 0 | 6.875
5196 | TORONTO BUTTONVILLE A | 8 | 4 | 12 | 21.5 | 0 | 3.5
5196 | TORONTO BUTTONVILLE A | 8 | 5 | 12 | 25.725 | 0 | 7.725
5197 | TORONTO BUTTONVILLE A | 8 | 4 | 13 | 22.6 | 0 | 4.6
5197 | TORONTO BUTTONVILLE A | 8 | 5 | 13 | 26.35 | 0 | 8.35
5198 | TORONTO BUTTONVILLE A | 8 | 4 | 14 | 23.4 | 0 | 5.4
5198 | TORONTO BUTTONVILLE A | 8 | 5 | 14 | 26.675 | 0 | 8.675
5199 | TORONTO BUTTONVILLE A | 8 | 4 | 15 | 22.9 | 0 | 4.9
5199 | TORONTO BUTTONVILLE A | 8 | 5 | 15 | 27.3 | 0 | 9.3
5200 | TORONTO BUTTONVILLE A | 8 | 4 | 16 | 23.8 | 0 | 5.8
5200 | TORONTO BUTTONVILLE A | 8 | 5 | 16 | 27.175 | 0 | 9.175
5201 | TORONTO BUTTONVILLE A | 8 | 4 | 17 | 19.9 | 0 | 1.9
5201 | TORONTO BUTTONVILLE A | 8 | 5 | 17 | 27.175 | 0 | 9.175
5202 | TORONTO BUTTONVILLE A | 8 | 4 | 18 | 20.2 | 0 | 2.2
5202 | TORONTO BUTTONVILLE A | 8 | 5 | 18 | 26.75 | 0 | 8.75
5203 | TORONTO BUTTONVILLE A | 8 | 4 | 19 | 20.3 | 0 | 2.3
5203 | TORONTO BUTTONVILLE A | 8 | 5 | 19 | 26.225 | 0 | 8.225
5204 | TORONTO BUTTONVILLE A | 8 | 4 | 20 | 20.3 | 0 | 2.3
5204 | TORONTO BUTTONVILLE A | 8 | 5 | 20 | 25.225 | 0 | 7.225
5205 | TORONTO BUTTONVILLE A | 8 | 4 | 21 | 19.4 | 0 | 1.4
5205 | TORONTO BUTTONVILLE A | 8 | 5 | 21 | 23.175 | 0 | 5.175
5206 | TORONTO BUTTONVILLE A | 8 | 4 | 22 | 18.5 | 0 | 0.5
5206 | TORONTO BUTTONVILLE A | 8 | 5 | 22 | 22.3 | 0 | 4.3
5207 | TORONTO BUTTONVILLE A | 8 | 4 | 23 | 18.2 | 0 | 0.2
5207 | TORONTO BUTTONVILLE A | 8 | 5 | 23 | 21.325 | 0 | 3.325
5208 | TORONTO BUTTONVILLE A | 8 | 4 | 24 | 18.1 | 0 | 0.1
5208 | TORONTO BUTTONVILLE A | 8 | 5 | 24 | 20.45 | 0 | 2.45
5209 | TORONTO BUTTONVILLE A | 8 | 5 | 1 | 17.4 | 0 | 0
5209 | TORONTO BUTTONVILLE A | 8 | 6 | 1 | 19.95 | 0 | 1.95
5210 | TORONTO BUTTONVILLE A | 8 | 5 | 2 | 16.7 | 0 | 0
5210 | TORONTO BUTTONVILLE A | 8 | 6 | 2 | 19.45 | 0 | 1.45
5211 | TORONTO BUTTONVILLE A | 8 | 5 | 3 | 16.3 | 0 | 0
5211 | TORONTO BUTTONVILLE A | 8 | 6 | 3 | 18.925 | 0 | 0.925
5212 | TORONTO BUTTONVILLE A | 8 | 5 | 4 | 16.1 | 0 | 0
5212 | TORONTO BUTTONVILLE A | 8 | 6 | 4 | 18.65 | 0 | 0.65
5213 | TORONTO BUTTONVILLE A | 8 | 5 | 5 | 15.6 | 0 | 0
5213 | TORONTO BUTTONVILLE A | 8 | 6 | 5 | 18.2 | 0 | 0.2
5214 | TORONTO BUTTONVILLE A | 8 | 5 | 6 | 15.1 | 0 | 0
5214 | TORONTO BUTTONVILLE A | 8 | 6 | 6 | 18 | 0 | 0
5215 | TORONTO BUTTONVILLE A | 8 | 5 | 7 | 15 | 0 | 0
5215 | TORONTO BUTTONVILLE A | 8 | 6 | 7 | 18.65 | 0 | 0.65
5216 | TORONTO BUTTONVILLE A | 8 | 5 | 8 | 16.2 | 0 | 0
5216 | TORONTO BUTTONVILLE A | 8 | 6 | 8 | 20.925 | 0 | 2.925
5217 | TORONTO BUTTONVILLE A | 8 | 5 | 9 | 18 | 0 | 0
5217 | TORONTO BUTTONVILLE A | 8 | 6 | 9 | 22.725 | 0 | 4.725
5218 | TORONTO BUTTONVILLE A | 8 | 5 | 10 | 18.8 | 0 | 0.8
5218 | TORONTO BUTTONVILLE A | 8 | 6 | 10 | 24.225 | 0 | 6.225
5219 | TORONTO BUTTONVILLE A | 8 | 5 | 11 | 20.1 | 0 | 2.1
5219 | TORONTO BUTTONVILLE A | 8 | 6 | 11 | 24.625 | 0 | 6.625
5220 | TORONTO BUTTONVILLE A | 8 | 5 | 12 | 21 | 0 | 3
5220 | TORONTO BUTTONVILLE A | 8 | 6 | 12 | 25.975 | 0 | 7.975
5221 | TORONTO BUTTONVILLE A | 8 | 5 | 13 | 21.3 | 0 | 3.3
5221 | TORONTO BUTTONVILLE A | 8 | 6 | 13 | 26.725 | 0 | 8.725
5222 | TORONTO BUTTONVILLE A | 8 | 5 | 14 | 21.3 | 0 | 3.3
5222 | TORONTO BUTTONVILLE A | 8 | 6 | 14 | 27.275 | 0 | 9.275
5223 | TORONTO BUTTONVILLE A | 8 | 5 | 15 | 22.8 | 0 | 4.8
5223 | TORONTO BUTTONVILLE A | 8 | 6 | 15 | 25.375 | 0 | 7.375
5224 | TORONTO BUTTONVILLE A | 8 | 5 | 16 | 22.8 | 0 | 4.8
5224 | TORONTO BUTTONVILLE A | 8 | 6 | 16 | 24.45 | 0 | 6.45
5225 | TORONTO BUTTONVILLE A | 8 | 5 | 17 | 22.3 | 0 | 4.3
5225 | TORONTO BUTTONVILLE A | 8 | 6 | 17 | 24.8 | 0 | 6.8
5226 | TORONTO BUTTONVILLE A | 8 | 5 | 18 | 21.9 | 0 | 3.9
5226 | TORONTO BUTTONVILLE A | 8 | 6 | 18 | 25.175 | 0 | 7.175
5227 | TORONTO BUTTONVILLE A | 8 | 5 | 19 | 21.1 | 0 | 3.1
5227 | TORONTO BUTTONVILLE A | 8 | 6 | 19 | 24.025 | 0 | 6.025
5228 | TORONTO BUTTONVILLE A | 8 | 5 | 20 | 19.8 | 0 | 1.8
5228 | TORONTO BUTTONVILLE A | 8 | 6 | 20 | 23.45 | 0 | 5.45
5229 | TORONTO BUTTONVILLE A | 8 | 5 | 21 | 18.4 | 0 | 0.4
5229 | TORONTO BUTTONVILLE A | 8 | 6 | 21 | 22.1 | 0 | 4.1
5230 | TORONTO BUTTONVILLE A | 8 | 5 | 22 | 17.6 | 0 | 0
5230 | TORONTO BUTTONVILLE A | 8 | 6 | 22 | 21.6 | 0 | 3.6
5231 | TORONTO BUTTONVILLE A | 8 | 5 | 23 | 16.4 | 0 | 0
5231 | TORONTO BUTTONVILLE A | 8 | 6 | 23 | 21.475 | 0 | 3.475
5232 | TORONTO BUTTONVILLE A | 8 | 5 | 24 | 15.7 | 0 | 0
5232 | TORONTO BUTTONVILLE A | 8 | 6 | 24 | 20.725 | 0 | 2.725
5233 | TORONTO BUTTONVILLE A | 8 | 6 | 1 | 15.2 | 0 | 0
5233 | TORONTO BUTTONVILLE A | 8 | 7 | 1 | 20.225 | 0 | 2.225
5234 | TORONTO BUTTONVILLE A | 8 | 6 | 2 | 13.2 | 0 | 0
5234 | TORONTO BUTTONVILLE A | 8 | 7 | 2 | 19.975 | 0 | 1.975
5235 | TORONTO BUTTONVILLE A | 8 | 6 | 3 | 12.7 | 0 | 0
5235 | TORONTO BUTTONVILLE A | 8 | 7 | 3 | 19.55 | 0 | 1.55
5236 | TORONTO BUTTONVILLE A | 8 | 6 | 4 | 12.5 | 0 | 0
5236 | TORONTO BUTTONVILLE A | 8 | 7 | 4 | 19.075 | 0 | 1.075
5237 | TORONTO BUTTONVILLE A | 8 | 6 | 5 | 12.2 | 0 | 0
5237 | TORONTO BUTTONVILLE A | 8 | 7 | 5 | 18.975 | 0 | 0.975
5238 | TORONTO BUTTONVILLE A | 8 | 6 | 6 | 11.8 | 0 | 0
5238 | TORONTO BUTTONVILLE A | 8 | 7 | 6 | 18.925 | 0 | 0.925
5239 | TORONTO BUTTONVILLE A | 8 | 6 | 7 | 12.4 | 0 | 0
5239 | TORONTO BUTTONVILLE A | 8 | 7 | 7 | 19.2 | 0 | 1.2
5240 | TORONTO BUTTONVILLE A | 8 | 6 | 8 | 15.3 | 0 | 0
5240 | TORONTO BUTTONVILLE A | 8 | 7 | 8 | 20.025 | 0 | 2.025
5241 | TORONTO BUTTONVILLE A | 8 | 6 | 9 | 18.8 | 0 | 0.8
5241 | TORONTO BUTTONVILLE A | 8 | 7 | 9 | 20.825 | 0 | 2.825
5242 | TORONTO BUTTONVILLE A | 8 | 6 | 10 | 20.2 | 0 | 2.2
5242 | TORONTO BUTTONVILLE A | 8 | 7 | 10 | 21.2 | 0 | 3.2
5243 | TORONTO BUTTONVILLE A | 8 | 6 | 11 | 21.6 | 0 | 3.6
5243 | TORONTO BUTTONVILLE A | 8 | 7 | 11 | 22.675 | 0 | 4.675
5244 | TORONTO BUTTONVILLE A | 8 | 6 | 12 | 21.5 | 0 | 3.5
5244 | TORONTO BUTTONVILLE A | 8 | 7 | 12 | 24.075 | 0 | 6.075
5245 | TORONTO BUTTONVILLE A | 8 | 6 | 13 | 22.5 | 0 | 4.5
5245 | TORONTO BUTTONVILLE A | 8 | 7 | 13 | 24.95 | 0 | 6.95
5246 | TORONTO BUTTONVILLE A | 8 | 6 | 14 | 22.7 | 0 | 4.7
5246 | TORONTO BUTTONVILLE A | 8 | 7 | 14 | 25.475 | 0 | 7.475
5247 | TORONTO BUTTONVILLE A | 8 | 6 | 15 | 22.9 | 0 | 4.9
5247 | TORONTO BUTTONVILLE A | 8 | 7 | 15 | 23.025 | 0 | 5.025
5248 | TORONTO BUTTONVILLE A | 8 | 6 | 16 | 24.3 | 0 | 6.3
5248 | TORONTO BUTTONVILLE A | 8 | 7 | 16 | 23.3 | 0 | 5.3
5249 | TORONTO BUTTONVILLE A | 8 | 6 | 17 | 23.1 | 0 | 5.1
5249 | TORONTO BUTTONVILLE A | 8 | 7 | 17 | 24.1 | 0 | 6.1
5250 | TORONTO BUTTONVILLE A | 8 | 6 | 18 | 23.2 | 0 | 5.2
5250 | TORONTO BUTTONVILLE A | 8 | 7 | 18 | 24.3 | 0 | 6.3
5251 | TORONTO BUTTONVILLE A | 8 | 6 | 19 | 22.8 | 0 | 4.8
5251 | TORONTO BUTTONVILLE A | 8 | 7 | 19 | 24.2 | 0 | 6.2
5252 | TORONTO BUTTONVILLE A | 8 | 6 | 20 | 21.3 | 0 | 3.3
5252 | TORONTO BUTTONVILLE A | 8 | 7 | 20 | 23.15 | 0 | 5.15
5253 | TORONTO BUTTONVILLE A | 8 | 6 | 21 | 20.3 | 0 | 2.3
5253 | TORONTO BUTTONVILLE A | 8 | 7 | 21 | 22.325 | 0 | 4.325
5254 | TORONTO BUTTONVILLE A | 8 | 6 | 22 | 19.4 | 0 | 1.4
5254 | TORONTO BUTTONVILLE A | 8 | 7 | 22 | 21.2 | 0 | 3.2
5255 | TORONTO BUTTONVILLE A | 8 | 6 | 23 | 17.2 | 0 | 0
5255 | TORONTO BUTTONVILLE A | 8 | 7 | 23 | 20.15 | 0 | 2.15
5256 | TORONTO BUTTONVILLE A | 8 | 6 | 24 | 15.9 | 0 | 0
5256 | TORONTO BUTTONVILLE A | 8 | 7 | 24 | 19.225 | 0 | 1.225
5257 | TORONTO BUTTONVILLE A | 8 | 7 | 1 | 16.5 | 0 | 0
5257 | TORONTO BUTTONVILLE A | 8 | 8 | 1 | 18.575 | 0 | 0.575
5258 | TORONTO BUTTONVILLE A | 8 | 7 | 2 | 15.5 | 0 | 0
5258 | TORONTO BUTTONVILLE A | 8 | 8 | 2 | 18.675 | 0 | 0.675
5259 | TORONTO BUTTONVILLE A | 8 | 7 | 3 | 15.5 | 0 | 0
5259 | TORONTO BUTTONVILLE A | 8 | 8 | 3 | 18.425 | 0 | 0.425
5260 | TORONTO BUTTONVILLE A | 8 | 7 | 4 | 15.3 | 0 | 0
5260 | TORONTO BUTTONVILLE A | 8 | 8 | 4 | 18.325 | 0 | 0.325
5261 | TORONTO BUTTONVILLE A | 8 | 7 | 5 | 13.4 | 0 | 0
5261 | TORONTO BUTTONVILLE A | 8 | 8 | 5 | 17.75 | 0 | 0
5262 | TORONTO BUTTONVILLE A | 8 | 7 | 6 | 13.8 | 0 | 0
5262 | TORONTO BUTTONVILLE A | 8 | 8 | 6 | 17.475 | 0 | 0
5263 | TORONTO BUTTONVILLE A | 8 | 7 | 7 | 14.8 | 0 | 0
5263 | TORONTO BUTTONVILLE A | 8 | 8 | 7 | 18.175 | 0 | 0.175
5264 | TORONTO BUTTONVILLE A | 8 | 7 | 8 | 17.4 | 0 | 0
5264 | TORONTO BUTTONVILLE A | 8 | 8 | 8 | 19.525 | 0 | 1.525
5265 | TORONTO BUTTONVILLE A | 8 | 7 | 9 | 19.9 | 0 | 1.9
5265 | TORONTO BUTTONVILLE A | 8 | 8 | 9 | 21.025 | 0 | 3.025
5266 | TORONTO BUTTONVILLE A | 8 | 7 | 10 | 22.2 | 0 | 4.2
5266 | TORONTO BUTTONVILLE A | 8 | 8 | 10 | 22.25 | 0 | 4.25
5267 | TORONTO BUTTONVILLE A | 8 | 7 | 11 | 23.4 | 0 | 5.4
5267 | TORONTO BUTTONVILLE A | 8 | 8 | 11 | 22.725 | 0 | 4.725
5268 | TORONTO BUTTONVILLE A | 8 | 7 | 12 | 24.9 | 0 | 6.9
5268 | TORONTO BUTTONVILLE A | 8 | 8 | 12 | 23.6 | 0 | 5.6
5269 | TORONTO BUTTONVILLE A | 8 | 7 | 13 | 24.5 | 0 | 6.5
5269 | TORONTO BUTTONVILLE A | 8 | 8 | 13 | 24.225 | 0 | 6.225
5270 | TORONTO BUTTONVILLE A | 8 | 7 | 14 | 23.8 | 0 | 5.8
5270 | TORONTO BUTTONVILLE A | 8 | 8 | 14 | 24.125 | 0 | 6.125
5271 | TORONTO BUTTONVILLE A | 8 | 7 | 15 | 24.2 | 0 | 6.2
5271 | TORONTO BUTTONVILLE A | 8 | 8 | 15 | 24.35 | 0 | 6.35
5272 | TORONTO BUTTONVILLE A | 8 | 7 | 16 | 25.4 | 0 | 7.4
5272 | TORONTO BUTTONVILLE A | 8 | 8 | 16 | 25 | 0 | 7
5273 | TORONTO BUTTONVILLE A | 8 | 7 | 17 | 25.2 | 0 | 7.2
5273 | TORONTO BUTTONVILLE A | 8 | 8 | 17 | 25.475 | 0 | 7.475
5274 | TORONTO BUTTONVILLE A | 8 | 7 | 18 | 24.2 | 0 | 6.2
5274 | TORONTO BUTTONVILLE A | 8 | 8 | 18 | 24.6 | 0 | 6.6
5275 | TORONTO BUTTONVILLE A | 8 | 7 | 19 | 24.1 | 0 | 6.1
5275 | TORONTO BUTTONVILLE A | 8 | 8 | 19 | 24.475 | 0 | 6.475
5276 | TORONTO BUTTONVILLE A | 8 | 7 | 20 | 22.8 | 0 | 4.8
5276 | TORONTO BUTTONVILLE A | 8 | 8 | 20 | 23.675 | 0 | 5.675
5277 | TORONTO BUTTONVILLE A | 8 | 7 | 21 | 21.4 | 0 | 3.4
5277 | TORONTO BUTTONVILLE A | 8 | 8 | 21 | 22.3 | 0 | 4.3
5278 | TORONTO BUTTONVILLE A | 8 | 7 | 22 | 20.6 | 0 | 2.6
5278 | TORONTO BUTTONVILLE A | 8 | 8 | 22 | 21.6 | 0 | 3.6
5279 | TORONTO BUTTONVILLE A | 8 | 7 | 23 | 18.9 | 0 | 0.9
5279 | TORONTO BUTTONVILLE A | 8 | 8 | 23 | 20.925 | 0 | 2.925
5280 | TORONTO BUTTONVILLE A | 8 | 7 | 24 | 18.4 | 0 | 0.4
5280 | TORONTO BUTTONVILLE A | 8 | 8 | 24 | 20.325 | 0 | 2.325
5281 | TORONTO BUTTONVILLE A | 8 | 8 | 1 | 17.2 | 0 | 0
5281 | TORONTO BUTTONVILLE A | 8 | 9 | 1 | 19.525 | 0 | 1.525
5282 | TORONTO BUTTONVILLE A | 8 | 8 | 2 | 16.2 | 0 | 0
5282 | TORONTO BUTTONVILLE A | 8 | 9 | 2 | 18.85 | 0 | 0.85
5283 | TORONTO BUTTONVILLE A | 8 | 8 | 3 | 15.9 | 0 | 0
5283 | TORONTO BUTTONVILLE A | 8 | 9 | 3 | 18.4 | 0 | 0.4
5284 | TORONTO BUTTONVILLE A | 8 | 8 | 4 | 15.5 | 0 | 0
5284 | TORONTO BUTTONVILLE A | 8 | 9 | 4 | 18.025 | 0 | 0.025
5285 | TORONTO BUTTONVILLE A | 8 | 8 | 5 | 15.9 | 0 | 0
5285 | TORONTO BUTTONVILLE A | 8 | 9 | 5 | 17.775 | 0 | 0
5286 | TORONTO BUTTONVILLE A | 8 | 8 | 6 | 15.8 | 0 | 0
5286 | TORONTO BUTTONVILLE A | 8 | 9 | 6 | 17.475 | 0 | 0
5287 | TORONTO BUTTONVILLE A | 8 | 8 | 7 | 16.3 | 0 | 0
5287 | TORONTO BUTTONVILLE A | 8 | 9 | 7 | 17.9 | 0 | 0
5288 | TORONTO BUTTONVILLE A | 8 | 8 | 8 | 18.9 | 0 | 0.9
5288 | TORONTO BUTTONVILLE A | 8 | 9 | 8 | 19.45 | 0 | 1.45
5289 | TORONTO BUTTONVILLE A | 8 | 8 | 9 | 22.1 | 0 | 4.1
5289 | TORONTO BUTTONVILLE A | 8 | 9 | 9 | 21.9 | 0 | 3.9
5290 | TORONTO BUTTONVILLE A | 8 | 8 | 10 | 23.7 | 0 | 5.7
5290 | TORONTO BUTTONVILLE A | 8 | 9 | 10 | 23.4 | 0 | 5.4
5291 | TORONTO BUTTONVILLE A | 8 | 8 | 11 | 25.1 | 0 | 7.1
5291 | TORONTO BUTTONVILLE A | 8 | 9 | 11 | 24.775 | 0 | 6.775
5292 | TORONTO BUTTONVILLE A | 8 | 8 | 12 | 25.2 | 0 | 7.2
5292 | TORONTO BUTTONVILLE A | 8 | 9 | 12 | 26.475 | 0 | 8.475
5293 | TORONTO BUTTONVILLE A | 8 | 8 | 13 | 26.9 | 0 | 8.9
5293 | TORONTO BUTTONVILLE A | 8 | 9 | 13 | 26.925 | 0 | 8.925
5294 | TORONTO BUTTONVILLE A | 8 | 8 | 14 | 25.5 | 0 | 7.5
5294 | TORONTO BUTTONVILLE A | 8 | 9 | 14 | 27.2 | 0 | 9.2
5295 | TORONTO BUTTONVILLE A | 8 | 8 | 15 | 26.1 | 0 | 8.1
5295 | TORONTO BUTTONVILLE A | 8 | 9 | 15 | 26.95 | 0 | 8.95
5296 | TORONTO BUTTONVILLE A | 8 | 8 | 16 | 26.7 | 0 | 8.7
5296 | TORONTO BUTTONVILLE A | 8 | 9 | 16 | 27.075 | 0 | 9.075
5297 | TORONTO BUTTONVILLE A | 8 | 8 | 17 | 26.8 | 0 | 8.8
5297 | TORONTO BUTTONVILLE A | 8 | 9 | 17 | 26.675 | 0 | 8.675
5298 | TORONTO BUTTONVILLE A | 8 | 8 | 18 | 26.2 | 0 | 8.2
5298 | TORONTO BUTTONVILLE A | 8 | 9 | 18 | 26.625 | 0 | 8.625
5299 | TORONTO BUTTONVILLE A | 8 | 8 | 19 | 25.2 | 0 | 7.2
5299 | TORONTO BUTTONVILLE A | 8 | 9 | 19 | 24.375 | 0 | 6.375
5300 | TORONTO BUTTONVILLE A | 8 | 8 | 20 | 24.3 | 0 | 6.3
5300 | TORONTO BUTTONVILLE A | 8 | 9 | 20 | 23.525 | 0 | 5.525
5301 | TORONTO BUTTONVILLE A | 8 | 8 | 21 | 22.2 | 0 | 4.2
5301 | TORONTO BUTTONVILLE A | 8 | 9 | 21 | 22.225 | 0 | 4.225
5302 | TORONTO BUTTONVILLE A | 8 | 8 | 22 | 21.8 | 0 | 3.8
5302 | TORONTO BUTTONVILLE A | 8 | 9 | 22 | 21.075 | 0 | 3.075
5303 | TORONTO BUTTONVILLE A | 8 | 8 | 23 | 22.1 | 0 | 4.1
5303 | TORONTO BUTTONVILLE A | 8 | 9 | 23 | 20.5 | 0 | 2.5
5304 | TORONTO BUTTONVILLE A | 8 | 8 | 24 | 21.9 | 0 | 3.9
5304 | TORONTO BUTTONVILLE A | 8 | 9 | 24 | 20.15 | 0 | 2.15
5305 | TORONTO BUTTONVILLE A | 8 | 9 | 1 | 21.7 | 0 | 3.7
5305 | TORONTO BUTTONVILLE A | 8 | 10 | 1 | 19.2 | 0 | 1.2
5306 | TORONTO BUTTONVILLE A | 8 | 9 | 2 | 21.4 | 0 | 3.4
5306 | TORONTO BUTTONVILLE A | 8 | 10 | 2 | 18.9 | 0 | 0.9
5307 | TORONTO BUTTONVILLE A | 8 | 9 | 3 | 21.4 | 0 | 3.4
5307 | TORONTO BUTTONVILLE A | 8 | 10 | 3 | 18.425 | 0 | 0.425
5308 | TORONTO BUTTONVILLE A | 8 | 9 | 4 | 21.4 | 0 | 3.4
5308 | TORONTO BUTTONVILLE A | 8 | 10 | 4 | 17.75 | 0 | 0
5309 | TORONTO BUTTONVILLE A | 8 | 9 | 5 | 20.5 | 0 | 2.5
5309 | TORONTO BUTTONVILLE A | 8 | 10 | 5 | 17.7 | 0 | 0
5310 | TORONTO BUTTONVILLE A | 8 | 9 | 6 | 21 | 0 | 3
5310 | TORONTO BUTTONVILLE A | 8 | 10 | 6 | 17.25 | 0 | 0
5311 | TORONTO BUTTONVILLE A | 8 | 9 | 7 | 20.6 | 0 | 2.6
5311 | TORONTO BUTTONVILLE A | 8 | 10 | 7 | 17.5 | 0 | 0
5312 | TORONTO BUTTONVILLE A | 8 | 9 | 8 | 21.2 | 0 | 3.2
5312 | TORONTO BUTTONVILLE A | 8 | 10 | 8 | 19.05 | 0 | 1.05
5313 | TORONTO BUTTONVILLE A | 8 | 9 | 9 | 22.8 | 0 | 4.8
5313 | TORONTO BUTTONVILLE A | 8 | 10 | 9 | 20.775 | 0 | 2.775
5314 | TORONTO BUTTONVILLE A | 8 | 9 | 10 | 24.3 | 0 | 6.3
5314 | TORONTO BUTTONVILLE A | 8 | 10 | 10 | 22.25 | 0 | 4.25
5315 | TORONTO BUTTONVILLE A | 8 | 9 | 11 | 25.8 | 0 | 7.8
5315 | TORONTO BUTTONVILLE A | 8 | 10 | 11 | 23.725 | 0 | 5.725
5316 | TORONTO BUTTONVILLE A | 8 | 9 | 12 | 25.8 | 0 | 7.8
5316 | TORONTO BUTTONVILLE A | 8 | 10 | 12 | 24.175 | 0 | 6.175
5317 | TORONTO BUTTONVILLE A | 8 | 9 | 13 | 27.6 | 0 | 9.6
5317 | TORONTO BUTTONVILLE A | 8 | 10 | 13 | 24.475 | 0 | 6.475
5318 | TORONTO BUTTONVILLE A | 8 | 9 | 14 | 29 | 0 | 11
5318 | TORONTO BUTTONVILLE A | 8 | 10 | 14 | 24.9 | 0 | 6.9
5319 | TORONTO BUTTONVILLE A | 8 | 9 | 15 | 29.4 | 0 | 11.4
5319 | TORONTO BUTTONVILLE A | 8 | 10 | 15 | 24.975 | 0 | 6.975
5320 | TORONTO BUTTONVILLE A | 8 | 9 | 16 | 29.4 | 0 | 11.4
5320 | TORONTO BUTTONVILLE A | 8 | 10 | 16 | 25.025 | 0 | 7.025
5321 | TORONTO BUTTONVILLE A | 8 | 9 | 17 | 29.5 | 0 | 11.5
5321 | TORONTO BUTTONVILLE A | 8 | 10 | 17 | 24.5 | 0 | 6.5
5322 | TORONTO BUTTONVILLE A | 8 | 9 | 18 | 29 | 0 | 11
5322 | TORONTO BUTTONVILLE A | 8 | 10 | 18 | 24.45 | 0 | 6.45
5323 | TORONTO BUTTONVILLE A | 8 | 9 | 19 | 29.2 | 0 | 11.2
5323 | TORONTO BUTTONVILLE A | 8 | 10 | 19 | 23.6 | 0 | 5.6
5324 | TORONTO BUTTONVILLE A | 8 | 9 | 20 | 27.8 | 0 | 9.8
5324 | TORONTO BUTTONVILLE A | 8 | 10 | 20 | 22.475 | 0 | 4.475
5325 | TORONTO BUTTONVILLE A | 8 | 9 | 21 | 26.7 | 0 | 8.7
5325 | TORONTO BUTTONVILLE A | 8 | 10 | 21 | 21.35 | 0 | 3.35
5326 | TORONTO BUTTONVILLE A | 8 | 9 | 22 | 27.1 | 0 | 9.1
5326 | TORONTO BUTTONVILLE A | 8 | 10 | 22 | 20.875 | 0 | 2.875
5327 | TORONTO BUTTONVILLE A | 8 | 9 | 23 | 26.4 | 0 | 8.4
5327 | TORONTO BUTTONVILLE A | 8 | 10 | 23 | 20.025 | 0 | 2.025
5328 | TORONTO BUTTONVILLE A | 8 | 9 | 24 | 25.2 | 0 | 7.2
5328 | TORONTO BUTTONVILLE A | 8 | 10 | 24 | 19.25 | 0 | 1.25
5329 | TORONTO BUTTONVILLE A | 8 | 10 | 1 | 24.6 | 0 | 6.6
5329 | TORONTO BUTTONVILLE A | 8 | 11 | 1 | 18.625 | 0 | 0.625
5330 | TORONTO BUTTONVILLE A | 8 | 10 | 2 | 24.2 | 0 | 6.2
5330 | TORONTO BUTTONVILLE A | 8 | 11 | 2 | 18.25 | 0 | 0.25
5331 | TORONTO BUTTONVILLE A | 8 | 10 | 3 | 24.1 | 0 | 6.1
5331 | TORONTO BUTTONVILLE A | 8 | 11 | 3 | 17.725 | 0 | 0
5332 | TORONTO BUTTONVILLE A | 8 | 10 | 4 | 24.1 | 0 | 6.1
5332 | TORONTO BUTTONVILLE A | 8 | 11 | 4 | 17.65 | 0 | 0
5333 | TORONTO BUTTONVILLE A | 8 | 10 | 5 | 23.8 | 0 | 5.8
5333 | TORONTO BUTTONVILLE A | 8 | 11 | 5 | 16.95 | 0 | 0
5334 | TORONTO BUTTONVILLE A | 8 | 10 | 6 | 23.3 | 0 | 5.3
5334 | TORONTO BUTTONVILLE A | 8 | 11 | 6 | 17.45 | 0 | 0
5335 | TORONTO BUTTONVILLE A | 8 | 10 | 7 | 22.8 | 0 | 4.8
5335 | TORONTO BUTTONVILLE A | 8 | 11 | 7 | 18.075 | 0 | 0.075
5336 | TORONTO BUTTONVILLE A | 8 | 10 | 8 | 24.6 | 0 | 6.6
5336 | TORONTO BUTTONVILLE A | 8 | 11 | 8 | 20.35 | 0 | 2.35
5337 | TORONTO BUTTONVILLE A | 8 | 10 | 9 | 26.3 | 0 | 8.3
5337 | TORONTO BUTTONVILLE A | 8 | 11 | 9 | 22.1 | 0 | 4.1
5338 | TORONTO BUTTONVILLE A | 8 | 10 | 10 | 27.7 | 0 | 9.7
5338 | TORONTO BUTTONVILLE A | 8 | 11 | 10 | 23.4 | 0 | 5.4
5339 | TORONTO BUTTONVILLE A | 8 | 10 | 11 | 28.9 | 0 | 10.9
5339 | TORONTO BUTTONVILLE A | 8 | 11 | 11 | 24.875 | 0 | 6.875
5340 | TORONTO BUTTONVILLE A | 8 | 10 | 12 | 30.1 | 0 | 12.1
5340 | TORONTO BUTTONVILLE A | 8 | 11 | 12 | 25.85 | 0 | 7.85
5341 | TORONTO BUTTONVILLE A | 8 | 10 | 13 | 30 | 0 | 12
5341 | TORONTO BUTTONVILLE A | 8 | 11 | 13 | 25.95 | 0 | 7.95
5342 | TORONTO BUTTONVILLE A | 8 | 10 | 14 | 30.7 | 0 | 12.7
5342 | TORONTO BUTTONVILLE A | 8 | 11 | 14 | 26.225 | 0 | 8.225
5343 | TORONTO BUTTONVILLE A | 8 | 10 | 15 | 31.2 | 0 | 13.2
5343 | TORONTO BUTTONVILLE A | 8 | 11 | 15 | 26.825 | 0 | 8.825
5344 | TORONTO BUTTONVILLE A | 8 | 10 | 16 | 32 | 0 | 14
5344 | TORONTO BUTTONVILLE A | 8 | 11 | 16 | 27.35 | 0 | 9.35
5345 | TORONTO BUTTONVILLE A | 8 | 10 | 17 | 32.1 | 0 | 14.1
5345 | TORONTO BUTTONVILLE A | 8 | 11 | 17 | 26.675 | 0 | 8.675
5346 | TORONTO BUTTONVILLE A | 8 | 10 | 18 | 30.3 | 0 | 12.3
5346 | TORONTO BUTTONVILLE A | 8 | 11 | 18 | 26.225 | 0 | 8.225
5347 | TORONTO BUTTONVILLE A | 8 | 10 | 19 | 29.3 | 0 | 11.3
5347 | TORONTO BUTTONVILLE A | 8 | 11 | 19 | 25.775 | 0 | 7.775
5348 | TORONTO BUTTONVILLE A | 8 | 10 | 20 | 28.7 | 0 | 10.7
5348 | TORONTO BUTTONVILLE A | 8 | 11 | 20 | 24.1 | 0 | 6.1
5349 | TORONTO BUTTONVILLE A | 8 | 10 | 21 | 28.5 | 0 | 10.5
5349 | TORONTO BUTTONVILLE A | 8 | 11 | 21 | 23.1 | 0 | 5.1
5350 | TORONTO BUTTONVILLE A | 8 | 10 | 22 | 26.6 | 0 | 8.6
5350 | TORONTO BUTTONVILLE A | 8 | 11 | 22 | 22.125 | 0 | 4.125
5351 | TORONTO BUTTONVILLE A | 8 | 10 | 23 | 25.2 | 0 | 7.2
5351 | TORONTO BUTTONVILLE A | 8 | 11 | 23 | 21.35 | 0 | 3.35
5352 | TORONTO BUTTONVILLE A | 8 | 10 | 24 | 24.4 | 0 | 6.4
5352 | TORONTO BUTTONVILLE A | 8 | 11 | 24 | 21.375 | 0 | 3.375
5353 | TORONTO BUTTONVILLE A | 8 | 11 | 1 | 23.3 | 0 | 5.3
5353 | TORONTO BUTTONVILLE A | 8 | 12 | 1 | 20.525 | 0 | 2.525
5354 | TORONTO BUTTONVILLE A | 8 | 11 | 2 | 23.4 | 0 | 5.4
5354 | TORONTO BUTTONVILLE A | 8 | 12 | 2 | 19.975 | 0 | 1.975
5355 | TORONTO BUTTONVILLE A | 8 | 11 | 3 | 23 | 0 | 5
5355 | TORONTO BUTTONVILLE A | 8 | 12 | 3 | 19.275 | 0 | 1.275
5356 | TORONTO BUTTONVILLE A | 8 | 11 | 4 | 22.7 | 0 | 4.7
5356 | TORONTO BUTTONVILLE A | 8 | 12 | 4 | 19.275 | 0 | 1.275
5357 | TORONTO BUTTONVILLE A | 8 | 11 | 5 | 22.2 | 0 | 4.2
5357 | TORONTO BUTTONVILLE A | 8 | 12 | 5 | 18.95 | 0 | 0.95
5358 | TORONTO BUTTONVILLE A | 8 | 11 | 6 | 23.1 | 0 | 5.1
5358 | TORONTO BUTTONVILLE A | 8 | 12 | 6 | 19.55 | 0 | 1.55
5359 | TORONTO BUTTONVILLE A | 8 | 11 | 7 | 23.6 | 0 | 5.6
5359 | TORONTO BUTTONVILLE A | 8 | 12 | 7 | 19.9 | 0 | 1.9
5360 | TORONTO BUTTONVILLE A | 8 | 11 | 8 | 24.7 | 0 | 6.7
5360 | TORONTO BUTTONVILLE A | 8 | 12 | 8 | 20.575 | 0 | 2.575
5361 | TORONTO BUTTONVILLE A | 8 | 11 | 9 | 24.9 | 0 | 6.9
5361 | TORONTO BUTTONVILLE A | 8 | 12 | 9 | 21.625 | 0 | 3.625
5362 | TORONTO BUTTONVILLE A | 8 | 11 | 10 | 26.5 | 0 | 8.5
5362 | TORONTO BUTTONVILLE A | 8 | 12 | 10 | 22.75 | 0 | 4.75
5363 | TORONTO BUTTONVILLE A | 8 | 11 | 11 | 26.9 | 0 | 8.9
5363 | TORONTO BUTTONVILLE A | 8 | 12 | 11 | 24.775 | 0 | 6.775
5364 | TORONTO BUTTONVILLE A | 8 | 11 | 12 | 27.5 | 0 | 9.5
5364 | TORONTO BUTTONVILLE A | 8 | 12 | 12 | 25.5 | 0 | 7.5
5365 | TORONTO BUTTONVILLE A | 8 | 11 | 13 | 27.2 | 0 | 9.2
5365 | TORONTO BUTTONVILLE A | 8 | 12 | 13 | 25.975 | 0 | 7.975
5366 | TORONTO BUTTONVILLE A | 8 | 11 | 14 | 27.4 | 0 | 9.4
5366 | TORONTO BUTTONVILLE A | 8 | 12 | 14 | 26.975 | 0 | 8.975
5367 | TORONTO BUTTONVILLE A | 8 | 11 | 15 | 27.9 | 0 | 9.9
5367 | TORONTO BUTTONVILLE A | 8 | 12 | 15 | 26.275 | 0 | 8.275
5368 | TORONTO BUTTONVILLE A | 8 | 11 | 16 | 27.1 | 0 | 9.1
5368 | TORONTO BUTTONVILLE A | 8 | 12 | 16 | 26.225 | 0 | 8.225
5369 | TORONTO BUTTONVILLE A | 8 | 11 | 17 | 27.3 | 0 | 9.3
5369 | TORONTO BUTTONVILLE A | 8 | 12 | 17 | 26.375 | 0 | 8.375
5370 | TORONTO BUTTONVILLE A | 8 | 11 | 18 | 27.6 | 0 | 9.6
5370 | TORONTO BUTTONVILLE A | 8 | 12 | 18 | 26.025 | 0 | 8.025
5371 | TORONTO BUTTONVILLE A | 8 | 11 | 19 | 26.1 | 0 | 8.1
5371 | TORONTO BUTTONVILLE A | 8 | 12 | 19 | 25.325 | 0 | 7.325
5372 | TORONTO BUTTONVILLE A | 8 | 11 | 20 | 24.7 | 0 | 6.7
5372 | TORONTO BUTTONVILLE A | 8 | 12 | 20 | 24.2 | 0 | 6.2
5373 | TORONTO BUTTONVILLE A | 8 | 11 | 21 | 22.8 | 0 | 4.8
5373 | TORONTO BUTTONVILLE A | 8 | 12 | 21 | 23.275 | 0 | 5.275
5374 | TORONTO BUTTONVILLE A | 8 | 11 | 22 | 21.4 | 0 | 3.4
5374 | TORONTO BUTTONVILLE A | 8 | 12 | 22 | 21.975 | 0 | 3.975
5375 | TORONTO BUTTONVILLE A | 8 | 11 | 23 | 20.3 | 0 | 2.3
5375 | TORONTO BUTTONVILLE A | 8 | 12 | 23 | 21.7 | 0 | 3.7
5376 | TORONTO BUTTONVILLE A | 8 | 11 | 24 | 20.1 | 0 | 2.1
5376 | TORONTO BUTTONVILLE A | 8 | 12 | 24 | 20.775 | 0 | 2.775
5377 | TORONTO BUTTONVILLE A | 8 | 12 | 1 | 18.9 | 0 | 0.9
5377 | TORONTO BUTTONVILLE A | 8 | 13 | 1 | 19.725 | 0 | 1.725
5378 | TORONTO BUTTONVILLE A | 8 | 12 | 2 | 17.3 | 0 | 0
5378 | TORONTO BUTTONVILLE A | 8 | 13 | 2 | 19.9 | 0 | 1.9
5379 | TORONTO BUTTONVILLE A | 8 | 12 | 3 | 16.8 | 0 | 0
5379 | TORONTO BUTTONVILLE A | 8 | 13 | 3 | 19.5 | 0 | 1.5
5380 | TORONTO BUTTONVILLE A | 8 | 12 | 4 | 15.6 | 0 | 0
5380 | TORONTO BUTTONVILLE A | 8 | 13 | 4 | 18.875 | 0 | 0.875
5381 | TORONTO BUTTONVILLE A | 8 | 12 | 5 | 15.6 | 0 | 0
5381 | TORONTO BUTTONVILLE A | 8 | 13 | 5 | 18.5 | 0 | 0.5
5382 | TORONTO BUTTONVILLE A | 8 | 12 | 6 | 15.2 | 0 | 0
5382 | TORONTO BUTTONVILLE A | 8 | 13 | 6 | 18.35 | 0 | 0.35
5383 | TORONTO BUTTONVILLE A | 8 | 12 | 7 | 16.7 | 0 | 0
5383 | TORONTO BUTTONVILLE A | 8 | 13 | 7 | 19.075 | 0 | 1.075
5384 | TORONTO BUTTONVILLE A | 8 | 12 | 8 | 19.6 | 0 | 1.6
5384 | TORONTO BUTTONVILLE A | 8 | 13 | 8 | 20.925 | 0 | 2.925
5385 | TORONTO BUTTONVILLE A | 8 | 12 | 9 | 22 | 0 | 4
5385 | TORONTO BUTTONVILLE A | 8 | 13 | 9 | 22.8 | 0 | 4.8
5386 | TORONTO BUTTONVILLE A | 8 | 12 | 10 | 24.6 | 0 | 6.6
5386 | TORONTO BUTTONVILLE A | 8 | 13 | 10 | 24.65 | 0 | 6.65
5387 | TORONTO BUTTONVILLE A | 8 | 12 | 11 | 25.7 | 0 | 7.7
5387 | TORONTO BUTTONVILLE A | 8 | 13 | 11 | 25 | 0 | 7
5388 | TORONTO BUTTONVILLE A | 8 | 12 | 12 | 27.4 | 0 | 9.4
5388 | TORONTO BUTTONVILLE A | 8 | 13 | 12 | 25.9 | 0 | 7.9
5389 | TORONTO BUTTONVILLE A | 8 | 12 | 13 | 28.5 | 0 | 10.5
5389 | TORONTO BUTTONVILLE A | 8 | 13 | 13 | 26.45 | 0 | 8.45
5390 | TORONTO BUTTONVILLE A | 8 | 12 | 14 | 28.8 | 0 | 10.8
5390 | TORONTO BUTTONVILLE A | 8 | 13 | 14 | 26.725 | 0 | 8.725
5391 | TORONTO BUTTONVILLE A | 8 | 12 | 15 | 28.8 | 0 | 10.8
5391 | TORONTO BUTTONVILLE A | 8 | 13 | 15 | 26.375 | 0 | 8.375
5392 | TORONTO BUTTONVILLE A | 8 | 12 | 16 | 29.9 | 0 | 11.9
5392 | TORONTO BUTTONVILLE A | 8 | 13 | 16 | 26.825 | 0 | 8.825
5393 | TORONTO BUTTONVILLE A | 8 | 12 | 17 | 29.9 | 0 | 11.9
5393 | TORONTO BUTTONVILLE A | 8 | 13 | 17 | 27.675 | 0 | 9.675
5394 | TORONTO BUTTONVILLE A | 8 | 12 | 18 | 29.3 | 0 | 11.3
5394 | TORONTO BUTTONVILLE A | 8 | 13 | 18 | 26.55 | 0 | 8.55
5395 | TORONTO BUTTONVILLE A | 8 | 12 | 19 | 28.4 | 0 | 10.4
5395 | TORONTO BUTTONVILLE A | 8 | 13 | 19 | 25.6 | 0 | 7.6
5396 | TORONTO BUTTONVILLE A | 8 | 12 | 20 | 26.4 | 0 | 8.4
5396 | TORONTO BUTTONVILLE A | 8 | 13 | 20 | 24.275 | 0 | 6.275
5397 | TORONTO BUTTONVILLE A | 8 | 12 | 21 | 26 | 0 | 8
5397 | TORONTO BUTTONVILLE A | 8 | 13 | 21 | 22.975 | 0 | 4.975
5398 | TORONTO BUTTONVILLE A | 8 | 12 | 22 | 23.8 | 0 | 5.8
5398 | TORONTO BUTTONVILLE A | 8 | 13 | 22 | 21.55 | 0 | 3.55
5399 | TORONTO BUTTONVILLE A | 8 | 12 | 23 | 20 | 0 | 2
5399 | TORONTO BUTTONVILLE A | 8 | 13 | 23 | 20.775 | 0 | 2.775
5400 | TORONTO BUTTONVILLE A | 8 | 12 | 24 | 19.2 | 0 | 1.2
5400 | TORONTO BUTTONVILLE A | 8 | 13 | 24 | 20.1 | 0 | 2.1
5401 | TORONTO BUTTONVILLE A | 8 | 13 | 1 | 19.2 | 0 | 1.2
5401 | TORONTO BUTTONVILLE A | 8 | 14 | 1 | 19.05 | 0 | 1.05
5402 | TORONTO BUTTONVILLE A | 8 | 13 | 2 | 19.2 | 0 | 1.2
5402 | TORONTO BUTTONVILLE A | 8 | 14 | 2 | 18.35 | 0 | 0.35
5403 | TORONTO BUTTONVILLE A | 8 | 13 | 3 | 18.9 | 0 | 0.9
5403 | TORONTO BUTTONVILLE A | 8 | 14 | 3 | 18.3 | 0 | 0.3
5404 | TORONTO BUTTONVILLE A | 8 | 13 | 4 | 19.1 | 0 | 1.1
5404 | TORONTO BUTTONVILLE A | 8 | 14 | 4 | 17.65 | 0 | 0
5405 | TORONTO BUTTONVILLE A | 8 | 13 | 5 | 17.8 | 0 | 0
5405 | TORONTO BUTTONVILLE A | 8 | 14 | 5 | 17.575 | 0 | 0
5406 | TORONTO BUTTONVILLE A | 8 | 13 | 6 | 18.3 | 0 | 0.3
5406 | TORONTO BUTTONVILLE A | 8 | 14 | 6 | 17.3 | 0 | 0
5407 | TORONTO BUTTONVILLE A | 8 | 13 | 7 | 19.1 | 0 | 1.1
5407 | TORONTO BUTTONVILLE A | 8 | 14 | 7 | 17.375 | 0 | 0
5408 | TORONTO BUTTONVILLE A | 8 | 13 | 8 | 21 | 0 | 3
5408 | TORONTO BUTTONVILLE A | 8 | 14 | 8 | 18.575 | 0 | 0.575
5409 | TORONTO BUTTONVILLE A | 8 | 13 | 9 | 23.5 | 0 | 5.5
5409 | TORONTO BUTTONVILLE A | 8 | 14 | 9 | 19.95 | 0 | 1.95
5410 | TORONTO BUTTONVILLE A | 8 | 13 | 10 | 25.4 | 0 | 7.4
5410 | TORONTO BUTTONVILLE A | 8 | 14 | 10 | 21.325 | 0 | 3.325
5411 | TORONTO BUTTONVILLE A | 8 | 13 | 11 | 26.9 | 0 | 8.9
5411 | TORONTO BUTTONVILLE A | 8 | 14 | 11 | 22.725 | 0 | 4.725
5412 | TORONTO BUTTONVILLE A | 8 | 13 | 12 | 28.3 | 0 | 10.3
5412 | TORONTO BUTTONVILLE A | 8 | 14 | 12 | 24.1 | 0 | 6.1
5413 | TORONTO BUTTONVILLE A | 8 | 13 | 13 | 28.9 | 0 | 10.9
5413 | TORONTO BUTTONVILLE A | 8 | 14 | 13 | 24.3 | 0 | 6.3
5414 | TORONTO BUTTONVILLE A | 8 | 13 | 14 | 28.1 | 0 | 10.1
5414 | TORONTO BUTTONVILLE A | 8 | 14 | 14 | 25.025 | 0 | 7.025
5415 | TORONTO BUTTONVILLE A | 8 | 13 | 15 | 29.2 | 0 | 11.2
5415 | TORONTO BUTTONVILLE A | 8 | 14 | 15 | 25.125 | 0 | 7.125
5416 | TORONTO BUTTONVILLE A | 8 | 13 | 16 | 28.8 | 0 | 10.8
5416 | TORONTO BUTTONVILLE A | 8 | 14 | 16 | 25.775 | 0 | 7.775
5417 | TORONTO BUTTONVILLE A | 8 | 13 | 17 | 29.3 | 0 | 11.3
5417 | TORONTO BUTTONVILLE A | 8 | 14 | 17 | 25.675 | 0 | 7.675
5418 | TORONTO BUTTONVILLE A | 8 | 13 | 18 | 28.3 | 0 | 10.3
5418 | TORONTO BUTTONVILLE A | 8 | 14 | 18 | 25.425 | 0 | 7.425
5419 | TORONTO BUTTONVILLE A | 8 | 13 | 19 | 27.8 | 0 | 9.8
5419 | TORONTO BUTTONVILLE A | 8 | 14 | 19 | 24.05 | 0 | 6.05
5420 | TORONTO BUTTONVILLE A | 8 | 13 | 20 | 26.6 | 0 | 8.6
5420 | TORONTO BUTTONVILLE A | 8 | 14 | 20 | 22.6 | 0 | 4.6
5421 | TORONTO BUTTONVILLE A | 8 | 13 | 21 | 25.3 | 0 | 7.3
5421 | TORONTO BUTTONVILLE A | 8 | 14 | 21 | 21.025 | 0 | 3.025
5422 | TORONTO BUTTONVILLE A | 8 | 13 | 22 | 23.6 | 0 | 5.6
5422 | TORONTO BUTTONVILLE A | 8 | 14 | 22 | 20.05 | 0 | 2.05
5423 | TORONTO BUTTONVILLE A | 8 | 13 | 23 | 21.6 | 0 | 3.6
5423 | TORONTO BUTTONVILLE A | 8 | 14 | 23 | 19.275 | 0 | 1.275
5424 | TORONTO BUTTONVILLE A | 8 | 13 | 24 | 19.8 | 0 | 1.8
5424 | TORONTO BUTTONVILLE A | 8 | 14 | 24 | 18.45 | 0 | 0.45
5425 | TORONTO BUTTONVILLE A | 8 | 14 | 1 | 20.6 | 0 | 2.6
5425 | TORONTO BUTTONVILLE A | 8 | 15 | 1 | 17.725 | 0 | 0
5426 | TORONTO BUTTONVILLE A | 8 | 14 | 2 | 20.4 | 0 | 2.4
5426 | TORONTO BUTTONVILLE A | 8 | 15 | 2 | 17.025 | 0 | 0
5427 | TORONTO BUTTONVILLE A | 8 | 14 | 3 | 19.9 | 0 | 1.9
5427 | TORONTO BUTTONVILLE A | 8 | 15 | 3 | 16.625 | 0 | 0
5428 | TORONTO BUTTONVILLE A | 8 | 14 | 4 | 21.3 | 0 | 3.3
5428 | TORONTO BUTTONVILLE A | 8 | 15 | 4 | 16.45 | 0 | 0
5429 | TORONTO BUTTONVILLE A | 8 | 14 | 5 | 21.2 | 0 | 3.2
5429 | TORONTO BUTTONVILLE A | 8 | 15 | 5 | 16.35 | 0 | 0
5430 | TORONTO BUTTONVILLE A | 8 | 14 | 6 | 19.4 | 0 | 1.4
5430 | TORONTO BUTTONVILLE A | 8 | 15 | 6 | 15.95 | 0 | 0
5431 | TORONTO BUTTONVILLE A | 8 | 14 | 7 | 18.1 | 0 | 0.1
5431 | TORONTO BUTTONVILLE A | 8 | 15 | 7 | 16.55 | 0 | 0
5432 | TORONTO BUTTONVILLE A | 8 | 14 | 8 | 21.7 | 0 | 3.7
5432 | TORONTO BUTTONVILLE A | 8 | 15 | 8 | 18.925 | 0 | 0.925
5433 | TORONTO BUTTONVILLE A | 8 | 14 | 9 | 24 | 0 | 6
5433 | TORONTO BUTTONVILLE A | 8 | 15 | 9 | 20.825 | 0 | 2.825
5434 | TORONTO BUTTONVILLE A | 8 | 14 | 10 | 25.6 | 0 | 7.6
5434 | TORONTO BUTTONVILLE A | 8 | 15 | 10 | 22.375 | 0 | 4.375
5435 | TORONTO BUTTONVILLE A | 8 | 14 | 11 | 26.9 | 0 | 8.9
5435 | TORONTO BUTTONVILLE A | 8 | 15 | 11 | 23.425 | 0 | 5.425
5436 | TORONTO BUTTONVILLE A | 8 | 14 | 12 | 28 | 0 | 10
5436 | TORONTO BUTTONVILLE A | 8 | 15 | 12 | 23.975 | 0 | 5.975
5437 | TORONTO BUTTONVILLE A | 8 | 14 | 13 | 28.3 | 0 | 10.3
5437 | TORONTO BUTTONVILLE A | 8 | 15 | 13 | 23.725 | 0 | 5.725
5438 | TORONTO BUTTONVILLE A | 8 | 14 | 14 | 29 | 0 | 11
5438 | TORONTO BUTTONVILLE A | 8 | 15 | 14 | 24.875 | 0 | 6.875
5439 | TORONTO BUTTONVILLE A | 8 | 14 | 15 | 28.7 | 0 | 10.7
5439 | TORONTO BUTTONVILLE A | 8 | 15 | 15 | 25 | 0 | 7
5440 | TORONTO BUTTONVILLE A | 8 | 14 | 16 | 28.9 | 0 | 10.9
5440 | TORONTO BUTTONVILLE A | 8 | 15 | 16 | 24.375 | 0 | 6.375
5441 | TORONTO BUTTONVILLE A | 8 | 14 | 17 | 28.4 | 0 | 10.4
5441 | TORONTO BUTTONVILLE A | 8 | 15 | 17 | 24.425 | 0 | 6.425
5442 | TORONTO BUTTONVILLE A | 8 | 14 | 18 | 27.8 | 0 | 9.8
5442 | TORONTO BUTTONVILLE A | 8 | 15 | 18 | 24.075 | 0 | 6.075
5443 | TORONTO BUTTONVILLE A | 8 | 14 | 19 | 26.8 | 0 | 8.8
5443 | TORONTO BUTTONVILLE A | 8 | 15 | 19 | 23.7 | 0 | 5.7
5444 | TORONTO BUTTONVILLE A | 8 | 14 | 20 | 25.1 | 0 | 7.1
5444 | TORONTO BUTTONVILLE A | 8 | 15 | 20 | 22.275 | 0 | 4.275
5445 | TORONTO BUTTONVILLE A | 8 | 14 | 21 | 24 | 0 | 6
5445 | TORONTO BUTTONVILLE A | 8 | 15 | 21 | 20.9 | 0 | 2.9
5446 | TORONTO BUTTONVILLE A | 8 | 14 | 22 | 22.3 | 0 | 4.3
5446 | TORONTO BUTTONVILLE A | 8 | 15 | 22 | 20.25 | 0 | 2.25
5447 | TORONTO BUTTONVILLE A | 8 | 14 | 23 | 20.5 | 0 | 2.5
5447 | TORONTO BUTTONVILLE A | 8 | 15 | 23 | 19.525 | 0 | 1.525
5448 | TORONTO BUTTONVILLE A | 8 | 14 | 24 | 18.6 | 0 | 0.6
5448 | TORONTO BUTTONVILLE A | 8 | 15 | 24 | 18.675 | 0 | 0.675
5449 | TORONTO BUTTONVILLE A | 8 | 15 | 1 | 18.9 | 0 | 0.9
5449 | TORONTO BUTTONVILLE A | 8 | 16 | 1 | 17.85 | 0 | 0
5450 | TORONTO BUTTONVILLE A | 8 | 15 | 2 | 18.1 | 0 | 0.1
5450 | TORONTO BUTTONVILLE A | 8 | 16 | 2 | 17.425 | 0 | 0
5451 | TORONTO BUTTONVILLE A | 8 | 15 | 3 | 17.6 | 0 | 0
5451 | TORONTO BUTTONVILLE A | 8 | 16 | 3 | 16.75 | 0 | 0
5452 | TORONTO BUTTONVILLE A | 8 | 15 | 4 | 15.6 | 0 | 0
5452 | TORONTO BUTTONVILLE A | 8 | 16 | 4 | 16.65 | 0 | 0
5453 | TORONTO BUTTONVILLE A | 8 | 15 | 5 | 15.9 | 0 | 0
5453 | TORONTO BUTTONVILLE A | 8 | 16 | 5 | 16.125 | 0 | 0
5454 | TORONTO BUTTONVILLE A | 8 | 15 | 6 | 14.8 | 0 | 0
5454 | TORONTO BUTTONVILLE A | 8 | 16 | 6 | 16.325 | 0 | 0
5455 | TORONTO BUTTONVILLE A | 8 | 15 | 7 | 15.1 | 0 | 0
5455 | TORONTO BUTTONVILLE A | 8 | 16 | 7 | 16.25 | 0 | 0
5456 | TORONTO BUTTONVILLE A | 8 | 15 | 8 | 18.6 | 0 | 0.6
5456 | TORONTO BUTTONVILLE A | 8 | 16 | 8 | 18.075 | 0 | 0.075
5457 | TORONTO BUTTONVILLE A | 8 | 15 | 9 | 20.2 | 0 | 2.2
5457 | TORONTO BUTTONVILLE A | 8 | 16 | 9 | 20.45 | 0 | 2.45
5458 | TORONTO BUTTONVILLE A | 8 | 15 | 10 | 23 | 0 | 5
5458 | TORONTO BUTTONVILLE A | 8 | 16 | 10 | 21.8 | 0 | 3.8
5459 | TORONTO BUTTONVILLE A | 8 | 15 | 11 | 24.6 | 0 | 6.6
5459 | TORONTO BUTTONVILLE A | 8 | 16 | 11 | 23.05 | 0 | 5.05
5460 | TORONTO BUTTONVILLE A | 8 | 15 | 12 | 25.6 | 0 | 7.6
5460 | TORONTO BUTTONVILLE A | 8 | 16 | 12 | 23.825 | 0 | 5.825
5461 | TORONTO BUTTONVILLE A | 8 | 15 | 13 | 26.4 | 0 | 8.4
5461 | TORONTO BUTTONVILLE A | 8 | 16 | 13 | 24.6 | 0 | 6.6
5462 | TORONTO BUTTONVILLE A | 8 | 15 | 14 | 26.5 | 0 | 8.5
5462 | TORONTO BUTTONVILLE A | 8 | 16 | 14 | 25.4 | 0 | 7.4
5463 | TORONTO BUTTONVILLE A | 8 | 15 | 15 | 27.2 | 0 | 9.2
5463 | TORONTO BUTTONVILLE A | 8 | 16 | 15 | 25.125 | 0 | 7.125
5464 | TORONTO BUTTONVILLE A | 8 | 15 | 16 | 26.8 | 0 | 8.8
5464 | TORONTO BUTTONVILLE A | 8 | 16 | 16 | 24.925 | 0 | 6.925
5465 | TORONTO BUTTONVILLE A | 8 | 15 | 17 | 27.4 | 0 | 9.4
5465 | TORONTO BUTTONVILLE A | 8 | 16 | 17 | 24.525 | 0 | 6.525
5466 | TORONTO BUTTONVILLE A | 8 | 15 | 18 | 26.7 | 0 | 8.7
5466 | TORONTO BUTTONVILLE A | 8 | 16 | 18 | 23.725 | 0 | 5.725
5467 | TORONTO BUTTONVILLE A | 8 | 15 | 19 | 24.9 | 0 | 6.9
5467 | TORONTO BUTTONVILLE A | 8 | 16 | 19 | 23.2 | 0 | 5.2
5468 | TORONTO BUTTONVILLE A | 8 | 15 | 20 | 23.8 | 0 | 5.8
5468 | TORONTO BUTTONVILLE A | 8 | 16 | 20 | 22.625 | 0 | 4.625
5469 | TORONTO BUTTONVILLE A | 8 | 15 | 21 | 23.5 | 0 | 5.5
5469 | TORONTO BUTTONVILLE A | 8 | 16 | 21 | 21.575 | 0 | 3.575
5470 | TORONTO BUTTONVILLE A | 8 | 15 | 22 | 23.3 | 0 | 5.3
5470 | TORONTO BUTTONVILLE A | 8 | 16 | 22 | 21.175 | 0 | 3.175
5471 | TORONTO BUTTONVILLE A | 8 | 15 | 23 | 22.9 | 0 | 4.9
5471 | TORONTO BUTTONVILLE A | 8 | 16 | 23 | 20.8 | 0 | 2.8
5472 | TORONTO BUTTONVILLE A | 8 | 15 | 24 | 22.3 | 0 | 4.3
5472 | TORONTO BUTTONVILLE A | 8 | 16 | 24 | 20.575 | 0 | 2.575
5473 | TORONTO BUTTONVILLE A | 8 | 16 | 1 | 21.9 | 0 | 3.9
5473 | TORONTO BUTTONVILLE A | 8 | 17 | 1 | 19.675 | 0 | 1.675
5474 | TORONTO BUTTONVILLE A | 8 | 16 | 2 | 22 | 0 | 4
5474 | TORONTO BUTTONVILLE A | 8 | 17 | 2 | 19.35 | 0 | 1.35
5475 | TORONTO BUTTONVILLE A | 8 | 16 | 3 | 21.8 | 0 | 3.8
5475 | TORONTO BUTTONVILLE A | 8 | 17 | 3 | 18.7 | 0 | 0.7
5476 | TORONTO BUTTONVILLE A | 8 | 16 | 4 | 20.9 | 0 | 2.9
5476 | TORONTO BUTTONVILLE A | 8 | 17 | 4 | 18.575 | 0 | 0.575
5477 | TORONTO BUTTONVILLE A | 8 | 16 | 5 | 20.8 | 0 | 2.8
5477 | TORONTO BUTTONVILLE A | 8 | 17 | 5 | 18.35 | 0 | 0.35
5478 | TORONTO BUTTONVILLE A | 8 | 16 | 6 | 19.9 | 0 | 1.9
5478 | TORONTO BUTTONVILLE A | 8 | 17 | 6 | 18.8 | 0 | 0.8
5479 | TORONTO BUTTONVILLE A | 8 | 16 | 7 | 19.7 | 0 | 1.7
5479 | TORONTO BUTTONVILLE A | 8 | 17 | 7 | 19.125 | 0 | 1.125
5480 | TORONTO BUTTONVILLE A | 8 | 16 | 8 | 21.1 | 0 | 3.1
5480 | TORONTO BUTTONVILLE A | 8 | 17 | 8 | 20.175 | 0 | 2.175
5481 | TORONTO BUTTONVILLE A | 8 | 16 | 9 | 22.3 | 0 | 4.3
5481 | TORONTO BUTTONVILLE A | 8 | 17 | 9 | 20.95 | 0 | 2.95
5482 | TORONTO BUTTONVILLE A | 8 | 16 | 10 | 23 | 0 | 5
5482 | TORONTO BUTTONVILLE A | 8 | 17 | 10 | 21.925 | 0 | 3.925
5483 | TORONTO BUTTONVILLE A | 8 | 16 | 11 | 22.6 | 0 | 4.6
5483 | TORONTO BUTTONVILLE A | 8 | 17 | 11 | 23.4 | 0 | 5.4
5484 | TORONTO BUTTONVILLE A | 8 | 16 | 12 | 21.7 | 0 | 3.7
5484 | TORONTO BUTTONVILLE A | 8 | 17 | 12 | 23.15 | 0 | 5.15
5485 | TORONTO BUTTONVILLE A | 8 | 16 | 13 | 21.5 | 0 | 3.5
5485 | TORONTO BUTTONVILLE A | 8 | 17 | 13 | 24.025 | 0 | 6.025
5486 | TORONTO BUTTONVILLE A | 8 | 16 | 14 | 22.2 | 0 | 4.2
5486 | TORONTO BUTTONVILLE A | 8 | 17 | 14 | 24.15 | 0 | 6.15
5487 | TORONTO BUTTONVILLE A | 8 | 16 | 15 | 23.4 | 0 | 5.4
5487 | TORONTO BUTTONVILLE A | 8 | 17 | 15 | 23.2 | 0 | 5.2
5488 | TORONTO BUTTONVILLE A | 8 | 16 | 16 | 22.5 | 0 | 4.5
5488 | TORONTO BUTTONVILLE A | 8 | 17 | 16 | 22.975 | 0 | 4.975
5489 | TORONTO BUTTONVILLE A | 8 | 16 | 17 | 24.1 | 0 | 6.1
5489 | TORONTO BUTTONVILLE A | 8 | 17 | 17 | 23.5 | 0 | 5.5
5490 | TORONTO BUTTONVILLE A | 8 | 16 | 18 | 23.2 | 0 | 5.2
5490 | TORONTO BUTTONVILLE A | 8 | 17 | 18 | 23.65 | 0 | 5.65
5491 | TORONTO BUTTONVILLE A | 8 | 16 | 19 | 22.1 | 0 | 4.1
5491 | TORONTO BUTTONVILLE A | 8 | 17 | 19 | 23.35 | 0 | 5.35
5492 | TORONTO BUTTONVILLE A | 8 | 16 | 20 | 21.3 | 0 | 3.3
5492 | TORONTO BUTTONVILLE A | 8 | 17 | 20 | 22.475 | 0 | 4.475
5493 | TORONTO BUTTONVILLE A | 8 | 16 | 21 | 20.4 | 0 | 2.4
5493 | TORONTO BUTTONVILLE A | 8 | 17 | 21 | 21.725 | 0 | 3.725
5494 | TORONTO BUTTONVILLE A | 8 | 16 | 22 | 19.6 | 0 | 1.6
5494 | TORONTO BUTTONVILLE A | 8 | 17 | 22 | 20.9 | 0 | 2.9
5495 | TORONTO BUTTONVILLE A | 8 | 16 | 23 | 18.8 | 0 | 0.8
5495 | TORONTO BUTTONVILLE A | 8 | 17 | 23 | 20.725 | 0 | 2.725
5496 | TORONTO BUTTONVILLE A | 8 | 16 | 24 | 18.1 | 0 | 0.1
5496 | TORONTO BUTTONVILLE A | 8 | 17 | 24 | 20.4 | 0 | 2.4
5497 | TORONTO BUTTONVILLE A | 8 | 17 | 1 | 16.8 | 0 | 0
5497 | TORONTO BUTTONVILLE A | 8 | 18 | 1 | 20.1 | 0 | 2.1
5498 | TORONTO BUTTONVILLE A | 8 | 17 | 2 | 17 | 0 | 0
5498 | TORONTO BUTTONVILLE A | 8 | 18 | 2 | 19.7 | 0 | 1.7
5499 | TORONTO BUTTONVILLE A | 8 | 17 | 3 | 16.9 | 0 | 0
5499 | TORONTO BUTTONVILLE A | 8 | 18 | 3 | 19.45 | 0 | 1.45
5500 | TORONTO BUTTONVILLE A | 8 | 17 | 4 | 15.8 | 0 | 0
5500 | TORONTO BUTTONVILLE A | 8 | 18 | 4 | 19.275 | 0 | 1.275
5501 | TORONTO BUTTONVILLE A | 8 | 17 | 5 | 15.6 | 0 | 0
5501 | TORONTO BUTTONVILLE A | 8 | 18 | 5 | 18.9 | 0 | 0.9
5502 | TORONTO BUTTONVILLE A | 8 | 17 | 6 | 16 | 0 | 0
5502 | TORONTO BUTTONVILLE A | 8 | 18 | 6 | 19.3 | 0 | 1.3
5503 | TORONTO BUTTONVILLE A | 8 | 17 | 7 | 16.1 | 0 | 0
5503 | TORONTO BUTTONVILLE A | 8 | 18 | 7 | 19.35 | 0 | 1.35
5504 | TORONTO BUTTONVILLE A | 8 | 17 | 8 | 18.8 | 0 | 0.8
5504 | TORONTO BUTTONVILLE A | 8 | 18 | 8 | 20.175 | 0 | 2.175
5505 | TORONTO BUTTONVILLE A | 8 | 17 | 9 | 20.6 | 0 | 2.6
5505 | TORONTO BUTTONVILLE A | 8 | 18 | 9 | 21.325 | 0 | 3.325
5506 | TORONTO BUTTONVILLE A | 8 | 17 | 10 | 22.5 | 0 | 4.5
5506 | TORONTO BUTTONVILLE A | 8 | 18 | 10 | 22.275 | 0 | 4.275
5507 | TORONTO BUTTONVILLE A | 8 | 17 | 11 | 23.6 | 0 | 5.6
5507 | TORONTO BUTTONVILLE A | 8 | 18 | 11 | 23.15 | 0 | 5.15
5508 | TORONTO BUTTONVILLE A | 8 | 17 | 12 | 23.6 | 0 | 5.6
5508 | TORONTO BUTTONVILLE A | 8 | 18 | 12 | 24.15 | 0 | 6.15
5509 | TORONTO BUTTONVILLE A | 8 | 17 | 13 | 24.8 | 0 | 6.8
5509 | TORONTO BUTTONVILLE A | 8 | 18 | 13 | 24.65 | 0 | 6.65
5510 | TORONTO BUTTONVILLE A | 8 | 17 | 14 | 27 | 0 | 9
5510 | TORONTO BUTTONVILLE A | 8 | 18 | 14 | 24.825 | 0 | 6.825
5511 | TORONTO BUTTONVILLE A | 8 | 17 | 15 | 19.6 | 0 | 1.6
5511 | TORONTO BUTTONVILLE A | 8 | 18 | 15 | 25.5 | 0 | 7.5
5512 | TORONTO BUTTONVILLE A | 8 | 17 | 16 | 22.4 | 0 | 4.4
5512 | TORONTO BUTTONVILLE A | 8 | 18 | 16 | 25.425 | 0 | 7.425
5513 | TORONTO BUTTONVILLE A | 8 | 17 | 17 | 20.1 | 0 | 2.1
5513 | TORONTO BUTTONVILLE A | 8 | 18 | 17 | 25.475 | 0 | 7.475
5514 | TORONTO BUTTONVILLE A | 8 | 17 | 18 | 20.8 | 0 | 2.8
5514 | TORONTO BUTTONVILLE A | 8 | 18 | 18 | 25.075 | 0 | 7.075
5515 | TORONTO BUTTONVILLE A | 8 | 17 | 19 | 20.4 | 0 | 2.4
5515 | TORONTO BUTTONVILLE A | 8 | 18 | 19 | 23.475 | 0 | 5.475
5516 | TORONTO BUTTONVILLE A | 8 | 17 | 20 | 19.7 | 0 | 1.7
5516 | TORONTO BUTTONVILLE A | 8 | 18 | 20 | 22.225 | 0 | 4.225
5517 | TORONTO BUTTONVILLE A | 8 | 17 | 21 | 18.8 | 0 | 0.8
5517 | TORONTO BUTTONVILLE A | 8 | 18 | 21 | 22 | 0 | 4
5518 | TORONTO BUTTONVILLE A | 8 | 17 | 22 | 18.6 | 0 | 0.6
5518 | TORONTO BUTTONVILLE A | 8 | 18 | 22 | 21.65 | 0 | 3.65
5519 | TORONTO BUTTONVILLE A | 8 | 17 | 23 | 18.1 | 0 | 0.1
5519 | TORONTO BUTTONVILLE A | 8 | 18 | 23 | 21.35 | 0 | 3.35
5520 | TORONTO BUTTONVILLE A | 8 | 17 | 24 | 17.4 | 0 | 0
5520 | TORONTO BUTTONVILLE A | 8 | 18 | 24 | 20.95 | 0 | 2.95
5521 | TORONTO BUTTONVILLE A | 8 | 18 | 1 | 17 | 0 | 0
5521 | TORONTO BUTTONVILLE A | 8 | 19 | 1 | 20.375 | 0 | 2.375
5522 | TORONTO BUTTONVILLE A | 8 | 18 | 2 | 16.1 | 0 | 0
5522 | TORONTO BUTTONVILLE A | 8 | 19 | 2 | 19.725 | 0 | 1.725
5523 | TORONTO BUTTONVILLE A | 8 | 18 | 3 | 16.6 | 0 | 0
5523 | TORONTO BUTTONVILLE A | 8 | 19 | 3 | 19.35 | 0 | 1.35
5524 | TORONTO BUTTONVILLE A | 8 | 18 | 4 | 16.2 | 0 | 0
5524 | TORONTO BUTTONVILLE A | 8 | 19 | 4 | 19.05 | 0 | 1.05
5525 | TORONTO BUTTONVILLE A | 8 | 18 | 5 | 15.2 | 0 | 0
5525 | TORONTO BUTTONVILLE A | 8 | 19 | 5 | 18.7 | 0 | 0.7
5526 | TORONTO BUTTONVILLE A | 8 | 18 | 6 | 15.4 | 0 | 0
5526 | TORONTO BUTTONVILLE A | 8 | 19 | 6 | 18.45 | 0 | 0.45
5527 | TORONTO BUTTONVILLE A | 8 | 18 | 7 | 15.2 | 0 | 0
5527 | TORONTO BUTTONVILLE A | 8 | 19 | 7 | 18.325 | 0 | 0.325
5528 | TORONTO BUTTONVILLE A | 8 | 18 | 8 | 17.3 | 0 | 0
5528 | TORONTO BUTTONVILLE A | 8 | 19 | 8 | 19.775 | 0 | 1.775
5529 | TORONTO BUTTONVILLE A | 8 | 18 | 9 | 19.1 | 0 | 1.1
5529 | TORONTO BUTTONVILLE A | 8 | 19 | 9 | 21.3 | 0 | 3.3
5530 | TORONTO BUTTONVILLE A | 8 | 18 | 10 | 20.7 | 0 | 2.7
5530 | TORONTO BUTTONVILLE A | 8 | 19 | 10 | 22.425 | 0 | 4.425
5531 | TORONTO BUTTONVILLE A | 8 | 18 | 11 | 22.1 | 0 | 4.1
5531 | TORONTO BUTTONVILLE A | 8 | 19 | 11 | 22.95 | 0 | 4.95
5532 | TORONTO BUTTONVILLE A | 8 | 18 | 12 | 19.6 | 0 | 1.6
5532 | TORONTO BUTTONVILLE A | 8 | 19 | 12 | 24.3 | 0 | 6.3
5533 | TORONTO BUTTONVILLE A | 8 | 18 | 13 | 22.6 | 0 | 4.6
5533 | TORONTO BUTTONVILLE A | 8 | 19 | 13 | 24.775 | 0 | 6.775
5534 | TORONTO BUTTONVILLE A | 8 | 18 | 14 | 23.5 | 0 | 5.5
5534 | TORONTO BUTTONVILLE A | 8 | 19 | 14 | 25.475 | 0 | 7.475
5535 | TORONTO BUTTONVILLE A | 8 | 18 | 15 | 23 | 0 | 5
5535 | TORONTO BUTTONVILLE A | 8 | 19 | 15 | 25.475 | 0 | 7.475
5536 | TORONTO BUTTONVILLE A | 8 | 18 | 16 | 21.2 | 0 | 3.2
5536 | TORONTO BUTTONVILLE A | 8 | 19 | 16 | 25.475 | 0 | 7.475
5537 | TORONTO BUTTONVILLE A | 8 | 18 | 17 | 22.2 | 0 | 4.2
5537 | TORONTO BUTTONVILLE A | 8 | 19 | 17 | 25.75 | 0 | 7.75
5538 | TORONTO BUTTONVILLE A | 8 | 18 | 18 | 21.4 | 0 | 3.4
5538 | TORONTO BUTTONVILLE A | 8 | 19 | 18 | 24.9 | 0 | 6.9
5539 | TORONTO BUTTONVILLE A | 8 | 18 | 19 | 20.1 | 0 | 2.1
5539 | TORONTO BUTTONVILLE A | 8 | 19 | 19 | 24.225 | 0 | 6.225
5540 | TORONTO BUTTONVILLE A | 8 | 18 | 20 | 18.4 | 0 | 0.4
5540 | TORONTO BUTTONVILLE A | 8 | 19 | 20 | 22.5 | 0 | 4.5
5541 | TORONTO BUTTONVILLE A | 8 | 18 | 21 | 17.1 | 0 | 0
5541 | TORONTO BUTTONVILLE A | 8 | 19 | 21 | 20.8 | 0 | 2.8
5542 | TORONTO BUTTONVILLE A | 8 | 18 | 22 | 16.4 | 0 | 0
5542 | TORONTO BUTTONVILLE A | 8 | 19 | 22 | 19.5 | 0 | 1.5
5543 | TORONTO BUTTONVILLE A | 8 | 18 | 23 | 15.6 | 0 | 0
5543 | TORONTO BUTTONVILLE A | 8 | 19 | 23 | 18.825 | 0 | 0.825
5544 | TORONTO BUTTONVILLE A | 8 | 18 | 24 | 14.4 | 0 | 0
5544 | TORONTO BUTTONVILLE A | 8 | 19 | 24 | 18.375 | 0 | 0.375
5545 | TORONTO BUTTONVILLE A | 8 | 19 | 1 | 14 | 0 | 0
5545 | TORONTO BUTTONVILLE A | 8 | 20 | 1 | 17.55 | 0 | 0
5546 | TORONTO BUTTONVILLE A | 8 | 19 | 2 | 14.2 | 0 | 0
5546 | TORONTO BUTTONVILLE A | 8 | 20 | 2 | 16.725 | 0 | 0
5547 | TORONTO BUTTONVILLE A | 8 | 19 | 3 | 13.1 | 0 | 0
5547 | TORONTO BUTTONVILLE A | 8 | 20 | 3 | 16.725 | 0 | 0
5548 | TORONTO BUTTONVILLE A | 8 | 19 | 4 | 13.7 | 0 | 0
5548 | TORONTO BUTTONVILLE A | 8 | 20 | 4 | 16.425 | 0 | 0
5549 | TORONTO BUTTONVILLE A | 8 | 19 | 5 | 14.5 | 0 | 0
5549 | TORONTO BUTTONVILLE A | 8 | 20 | 5 | 16.425 | 0 | 0
5550 | TORONTO BUTTONVILLE A | 8 | 19 | 6 | 13.8 | 0 | 0
5550 | TORONTO BUTTONVILLE A | 8 | 20 | 6 | 16.25 | 0 | 0
5551 | TORONTO BUTTONVILLE A | 8 | 19 | 7 | 13.2 | 0 | 0
5551 | TORONTO BUTTONVILLE A | 8 | 20 | 7 | 16.675 | 0 | 0
5552 | TORONTO BUTTONVILLE A | 8 | 19 | 8 | 15.8 | 0 | 0
5552 | TORONTO BUTTONVILLE A | 8 | 20 | 8 | 18.725 | 0 | 0.725
5553 | TORONTO BUTTONVILLE A | 8 | 19 | 9 | 18 | 0 | 0
5553 | TORONTO BUTTONVILLE A | 8 | 20 | 9 | 20.85 | 0 | 2.85
5554 | TORONTO BUTTONVILLE A | 8 | 19 | 10 | 18.5 | 0 | 0.5
5554 | TORONTO BUTTONVILLE A | 8 | 20 | 10 | 22.875 | 0 | 4.875
5555 | TORONTO BUTTONVILLE A | 8 | 19 | 11 | 18.5 | 0 | 0.5
5555 | TORONTO BUTTONVILLE A | 8 | 20 | 11 | 24.45 | 0 | 6.45
5556 | TORONTO BUTTONVILLE A | 8 | 19 | 12 | 20.7 | 0 | 2.7
5556 | TORONTO BUTTONVILLE A | 8 | 20 | 12 | 25.65 | 0 | 7.65
5557 | TORONTO BUTTONVILLE A | 8 | 19 | 13 | 20.8 | 0 | 2.8
5557 | TORONTO BUTTONVILLE A | 8 | 20 | 13 | 26.3 | 0 | 8.3
5558 | TORONTO BUTTONVILLE A | 8 | 19 | 14 | 21 | 0 | 3
5558 | TORONTO BUTTONVILLE A | 8 | 20 | 14 | 26.725 | 0 | 8.725
5559 | TORONTO BUTTONVILLE A | 8 | 19 | 15 | 21.1 | 0 | 3.1
5559 | TORONTO BUTTONVILLE A | 8 | 20 | 15 | 27.2 | 0 | 9.2
5560 | TORONTO BUTTONVILLE A | 8 | 19 | 16 | 21.7 | 0 | 3.7
5560 | TORONTO BUTTONVILLE A | 8 | 20 | 16 | 27.15 | 0 | 9.15
5561 | TORONTO BUTTONVILLE A | 8 | 19 | 17 | 21.7 | 0 | 3.7
5561 | TORONTO BUTTONVILLE A | 8 | 20 | 17 | 27.075 | 0 | 9.075
5562 | TORONTO BUTTONVILLE A | 8 | 19 | 18 | 21.3 | 0 | 3.3
5562 | TORONTO BUTTONVILLE A | 8 | 20 | 18 | 26.75 | 0 | 8.75
5563 | TORONTO BUTTONVILLE A | 8 | 19 | 19 | 20.4 | 0 | 2.4
5563 | TORONTO BUTTONVILLE A | 8 | 20 | 19 | 26.05 | 0 | 8.05
5564 | TORONTO BUTTONVILLE A | 8 | 19 | 20 | 17.9 | 0 | 0
5564 | TORONTO BUTTONVILLE A | 8 | 20 | 20 | 24.55 | 0 | 6.55
5565 | TORONTO BUTTONVILLE A | 8 | 19 | 21 | 17.2 | 0 | 0
5565 | TORONTO BUTTONVILLE A | 8 | 20 | 21 | 23.475 | 0 | 5.475
5566 | TORONTO BUTTONVILLE A | 8 | 19 | 22 | 16.3 | 0 | 0
5566 | TORONTO BUTTONVILLE A | 8 | 20 | 22 | 22.625 | 0 | 4.625
5567 | TORONTO BUTTONVILLE A | 8 | 19 | 23 | 15.2 | 0 | 0
5567 | TORONTO BUTTONVILLE A | 8 | 20 | 23 | 21.775 | 0 | 3.775
5568 | TORONTO BUTTONVILLE A | 8 | 19 | 24 | 15.5 | 0 | 0
5568 | TORONTO BUTTONVILLE A | 8 | 20 | 24 | 21.95 | 0 | 3.95
5569 | TORONTO BUTTONVILLE A | 8 | 20 | 1 | 13.8 | 0 | 0
5569 | TORONTO BUTTONVILLE A | 8 | 21 | 1 | 21.375 | 0 | 3.375
5570 | TORONTO BUTTONVILLE A | 8 | 20 | 2 | 13.2 | 0 | 0
5570 | TORONTO BUTTONVILLE A | 8 | 21 | 2 | 20.575 | 0 | 2.575
5571 | TORONTO BUTTONVILLE A | 8 | 20 | 3 | 12.6 | 0 | 0
5571 | TORONTO BUTTONVILLE A | 8 | 21 | 3 | 20.825 | 0 | 2.825
5572 | TORONTO BUTTONVILLE A | 8 | 20 | 4 | 11.1 | 0 | 0
5572 | TORONTO BUTTONVILLE A | 8 | 21 | 4 | 20.725 | 0 | 2.725
5573 | TORONTO BUTTONVILLE A | 8 | 20 | 5 | 11.4 | 0 | 0
5573 | TORONTO BUTTONVILLE A | 8 | 21 | 5 | 20.525 | 0 | 2.525
5574 | TORONTO BUTTONVILLE A | 8 | 20 | 6 | 11 | 0 | 0
5574 | TORONTO BUTTONVILLE A | 8 | 21 | 6 | 20.25 | 0 | 2.25
5575 | TORONTO BUTTONVILLE A | 8 | 20 | 7 | 11.1 | 0 | 0
5575 | TORONTO BUTTONVILLE A | 8 | 21 | 7 | 19.925 | 0 | 1.925
5576 | TORONTO BUTTONVILLE A | 8 | 20 | 8 | 14.9 | 0 | 0
5576 | TORONTO BUTTONVILLE A | 8 | 21 | 8 | 20.75 | 0 | 2.75
5577 | TORONTO BUTTONVILLE A | 8 | 20 | 9 | 18.9 | 0 | 0.9
5577 | TORONTO BUTTONVILLE A | 8 | 21 | 9 | 22.525 | 0 | 4.525
5578 | TORONTO BUTTONVILLE A | 8 | 20 | 10 | 21.6 | 0 | 3.6
5578 | TORONTO BUTTONVILLE A | 8 | 21 | 10 | 24.05 | 0 | 6.05
5579 | TORONTO BUTTONVILLE A | 8 | 20 | 11 | 22.8 | 0 | 4.8
5579 | TORONTO BUTTONVILLE A | 8 | 21 | 11 | 25.15 | 0 | 7.15
5580 | TORONTO BUTTONVILLE A | 8 | 20 | 12 | 24.1 | 0 | 6.1
5580 | TORONTO BUTTONVILLE A | 8 | 21 | 12 | 26.275 | 0 | 8.275
5581 | TORONTO BUTTONVILLE A | 8 | 20 | 13 | 24.7 | 0 | 6.7
5581 | TORONTO BUTTONVILLE A | 8 | 21 | 13 | 26.975 | 0 | 8.975
5582 | TORONTO BUTTONVILLE A | 8 | 20 | 14 | 26.7 | 0 | 8.7
5582 | TORONTO BUTTONVILLE A | 8 | 21 | 14 | 27.025 | 0 | 9.025
5583 | TORONTO BUTTONVILLE A | 8 | 20 | 15 | 26.8 | 0 | 8.8
5583 | TORONTO BUTTONVILLE A | 8 | 21 | 15 | 27.075 | 0 | 9.075
5584 | TORONTO BUTTONVILLE A | 8 | 20 | 16 | 26.7 | 0 | 8.7
5584 | TORONTO BUTTONVILLE A | 8 | 21 | 16 | 27.325 | 0 | 9.325
5585 | TORONTO BUTTONVILLE A | 8 | 20 | 17 | 25.9 | 0 | 7.9
5585 | TORONTO BUTTONVILLE A | 8 | 21 | 17 | 28.15 | 0 | 10.15
5586 | TORONTO BUTTONVILLE A | 8 | 20 | 18 | 25.2 | 0 | 7.2
5586 | TORONTO BUTTONVILLE A | 8 | 21 | 18 | 27.15 | 0 | 9.15
5587 | TORONTO BUTTONVILLE A | 8 | 20 | 19 | 24 | 0 | 6
5587 | TORONTO BUTTONVILLE A | 8 | 21 | 19 | 26.3 | 0 | 8.3
5588 | TORONTO BUTTONVILLE A | 8 | 20 | 20 | 23.1 | 0 | 5.1
5588 | TORONTO BUTTONVILLE A | 8 | 21 | 20 | 25.575 | 0 | 7.575
5589 | TORONTO BUTTONVILLE A | 8 | 20 | 21 | 22.8 | 0 | 4.8
5589 | TORONTO BUTTONVILLE A | 8 | 21 | 21 | 24.525 | 0 | 6.525
5590 | TORONTO BUTTONVILLE A | 8 | 20 | 22 | 21.5 | 0 | 3.5
5590 | TORONTO BUTTONVILLE A | 8 | 21 | 22 | 23.6 | 0 | 5.6
5591 | TORONTO BUTTONVILLE A | 8 | 20 | 23 | 21.3 | 0 | 3.3
5591 | TORONTO BUTTONVILLE A | 8 | 21 | 23 | 22.475 | 0 | 4.475
5592 | TORONTO BUTTONVILLE A | 8 | 20 | 24 | 20.6 | 0 | 2.6
5592 | TORONTO BUTTONVILLE A | 8 | 21 | 24 | 21.275 | 0 | 3.275
5593 | TORONTO BUTTONVILLE A | 8 | 21 | 1 | 20 | 0 | 2
5593 | TORONTO BUTTONVILLE A | 8 | 22 | 1 | 20.5 | 0 | 2.5
5594 | TORONTO BUTTONVILLE A | 8 | 21 | 2 | 19.1 | 0 | 1.1
5594 | TORONTO BUTTONVILLE A | 8 | 22 | 2 | 20.025 | 0 | 2.025
5595 | TORONTO BUTTONVILLE A | 8 | 21 | 3 | 19.9 | 0 | 1.9
5595 | TORONTO BUTTONVILLE A | 8 | 22 | 3 | 19.875 | 0 | 1.875
5596 | TORONTO BUTTONVILLE A | 8 | 21 | 4 | 19.7 | 0 | 1.7
5596 | TORONTO BUTTONVILLE A | 8 | 22 | 4 | 19.625 | 0 | 1.625
5597 | TORONTO BUTTONVILLE A | 8 | 21 | 5 | 18.9 | 0 | 0.9
5597 | TORONTO BUTTONVILLE A | 8 | 22 | 5 | 19.275 | 0 | 1.275
5598 | TORONTO BUTTONVILLE A | 8 | 21 | 6 | 18 | 0 | 0
5598 | TORONTO BUTTONVILLE A | 8 | 22 | 6 | 19.275 | 0 | 1.275
5599 | TORONTO BUTTONVILLE A | 8 | 21 | 7 | 18.7 | 0 | 0.7
5599 | TORONTO BUTTONVILLE A | 8 | 22 | 7 | 19.45 | 0 | 1.45
5600 | TORONTO BUTTONVILLE A | 8 | 21 | 8 | 19.2 | 0 | 1.2
5600 | TORONTO BUTTONVILLE A | 8 | 22 | 8 | 20.3 | 0 | 2.3
5601 | TORONTO BUTTONVILLE A | 8 | 21 | 9 | 20.1 | 0 | 2.1
5601 | TORONTO BUTTONVILLE A | 8 | 22 | 9 | 21.7 | 0 | 3.7
5602 | TORONTO BUTTONVILLE A | 8 | 21 | 10 | 22.5 | 0 | 4.5
5602 | TORONTO BUTTONVILLE A | 8 | 22 | 10 | 21.85 | 0 | 3.85
5603 | TORONTO BUTTONVILLE A | 8 | 21 | 11 | 24.5 | 0 | 6.5
5603 | TORONTO BUTTONVILLE A | 8 | 22 | 11 | 22.55 | 0 | 4.55
5604 | TORONTO BUTTONVILLE A | 8 | 21 | 12 | 25.2 | 0 | 7.2
5604 | TORONTO BUTTONVILLE A | 8 | 22 | 12 | 23.075 | 0 | 5.075
5605 | TORONTO BUTTONVILLE A | 8 | 21 | 13 | 26.2 | 0 | 8.2
5605 | TORONTO BUTTONVILLE A | 8 | 22 | 13 | 23.975 | 0 | 5.975
5606 | TORONTO BUTTONVILLE A | 8 | 21 | 14 | 27.9 | 0 | 9.9
5606 | TORONTO BUTTONVILLE A | 8 | 22 | 14 | 22.475 | 0 | 4.475
5607 | TORONTO BUTTONVILLE A | 8 | 21 | 15 | 29.7 | 0 | 11.7
5607 | TORONTO BUTTONVILLE A | 8 | 22 | 15 | 23.1 | 0 | 5.1
5608 | TORONTO BUTTONVILLE A | 8 | 21 | 16 | 29 | 0 | 11
5608 | TORONTO BUTTONVILLE A | 8 | 22 | 16 | 24.25 | 0 | 6.25
5609 | TORONTO BUTTONVILLE A | 8 | 21 | 17 | 28.6 | 0 | 10.6
5609 | TORONTO BUTTONVILLE A | 8 | 22 | 17 | 24.025 | 0 | 6.025
5610 | TORONTO BUTTONVILLE A | 8 | 21 | 18 | 28.4 | 0 | 10.4
5610 | TORONTO BUTTONVILLE A | 8 | 22 | 18 | 23.925 | 0 | 5.925
5611 | TORONTO BUTTONVILLE A | 8 | 21 | 19 | 27.6 | 0 | 9.6
5611 | TORONTO BUTTONVILLE A | 8 | 22 | 19 | 22.525 | 0 | 4.525
5612 | TORONTO BUTTONVILLE A | 8 | 21 | 20 | 25.1 | 0 | 7.1
5612 | TORONTO BUTTONVILLE A | 8 | 22 | 20 | 20.925 | 0 | 2.925
5613 | TORONTO BUTTONVILLE A | 8 | 21 | 21 | 22.9 | 0 | 4.9
5613 | TORONTO BUTTONVILLE A | 8 | 22 | 21 | 19.675 | 0 | 1.675
5614 | TORONTO BUTTONVILLE A | 8 | 21 | 22 | 22.5 | 0 | 4.5
5614 | TORONTO BUTTONVILLE A | 8 | 22 | 22 | 18.85 | 0 | 0.85
5615 | TORONTO BUTTONVILLE A | 8 | 21 | 23 | 21.4 | 0 | 3.4
5615 | TORONTO BUTTONVILLE A | 8 | 22 | 23 | 18.125 | 0 | 0.125
5616 | TORONTO BUTTONVILLE A | 8 | 21 | 24 | 20.3 | 0 | 2.3
5616 | TORONTO BUTTONVILLE A | 8 | 22 | 24 | 17.425 | 0 | 0
5617 | TORONTO BUTTONVILLE A | 8 | 22 | 1 | 20.1 | 0 | 2.1
5617 | TORONTO BUTTONVILLE A | 8 | 23 | 1 | 16.925 | 0 | 0
5618 | TORONTO BUTTONVILLE A | 8 | 22 | 2 | 19.7 | 0 | 1.7
5618 | TORONTO BUTTONVILLE A | 8 | 23 | 2 | 16.7 | 0 | 0
5619 | TORONTO BUTTONVILLE A | 8 | 22 | 3 | 19.6 | 0 | 1.6
5619 | TORONTO BUTTONVILLE A | 8 | 23 | 3 | 16.025 | 0 | 0
5620 | TORONTO BUTTONVILLE A | 8 | 22 | 4 | 20.3 | 0 | 2.3
5620 | TORONTO BUTTONVILLE A | 8 | 23 | 4 | 16 | 0 | 0
5621 | TORONTO BUTTONVILLE A | 8 | 22 | 5 | 19.6 | 0 | 1.6
5621 | TORONTO BUTTONVILLE A | 8 | 23 | 5 | 16.1 | 0 | 0
5622 | TORONTO BUTTONVILLE A | 8 | 22 | 6 | 20 | 0 | 2
5622 | TORONTO BUTTONVILLE A | 8 | 23 | 6 | 15.5 | 0 | 0
5623 | TORONTO BUTTONVILLE A | 8 | 22 | 7 | 19.7 | 0 | 1.7
5623 | TORONTO BUTTONVILLE A | 8 | 23 | 7 | 16.075 | 0 | 0
5624 | TORONTO BUTTONVILLE A | 8 | 22 | 8 | 20.3 | 0 | 2.3
5624 | TORONTO BUTTONVILLE A | 8 | 23 | 8 | 17.65 | 0 | 0
5625 | TORONTO BUTTONVILLE A | 8 | 22 | 9 | 21.9 | 0 | 3.9
5625 | TORONTO BUTTONVILLE A | 8 | 23 | 9 | 19.425 | 0 | 1.425
5626 | TORONTO BUTTONVILLE A | 8 | 22 | 10 | 24.2 | 0 | 6.2
5626 | TORONTO BUTTONVILLE A | 8 | 23 | 10 | 21.9 | 0 | 3.9
5627 | TORONTO BUTTONVILLE A | 8 | 22 | 11 | 25.4 | 0 | 7.4
5627 | TORONTO BUTTONVILLE A | 8 | 23 | 11 | 22.575 | 0 | 4.575
5628 | TORONTO BUTTONVILLE A | 8 | 22 | 12 | 27.3 | 0 | 9.3
5628 | TORONTO BUTTONVILLE A | 8 | 23 | 12 | 23.775 | 0 | 5.775
5629 | TORONTO BUTTONVILLE A | 8 | 22 | 13 | 28.2 | 0 | 10.2
5629 | TORONTO BUTTONVILLE A | 8 | 23 | 13 | 24.4 | 0 | 6.4
5630 | TORONTO BUTTONVILLE A | 8 | 22 | 14 | 29.5 | 0 | 11.5
5630 | TORONTO BUTTONVILLE A | 8 | 23 | 14 | 24.9 | 0 | 6.9
5631 | TORONTO BUTTONVILLE A | 8 | 22 | 15 | 29.2 | 0 | 11.2
5631 | TORONTO BUTTONVILLE A | 8 | 23 | 15 | 25.075 | 0 | 7.075
5632 | TORONTO BUTTONVILLE A | 8 | 22 | 16 | 25 | 0 | 7
5632 | TORONTO BUTTONVILLE A | 8 | 23 | 16 | 25.15 | 0 | 7.15
5633 | TORONTO BUTTONVILLE A | 8 | 22 | 17 | 26.9 | 0 | 8.9
5633 | TORONTO BUTTONVILLE A | 8 | 23 | 17 | 24.525 | 0 | 6.525
5634 | TORONTO BUTTONVILLE A | 8 | 22 | 18 | 27.9 | 0 | 9.9
5634 | TORONTO BUTTONVILLE A | 8 | 23 | 18 | 24.125 | 0 | 6.125
5635 | TORONTO BUTTONVILLE A | 8 | 22 | 19 | 26.6 | 0 | 8.6
5635 | TORONTO BUTTONVILLE A | 8 | 23 | 19 | 22.725 | 0 | 4.725
5636 | TORONTO BUTTONVILLE A | 8 | 22 | 20 | 22.8 | 0 | 4.8
5636 | TORONTO BUTTONVILLE A | 8 | 23 | 20 | 21.2 | 0 | 3.2
5637 | TORONTO BUTTONVILLE A | 8 | 22 | 21 | 22.4 | 0 | 4.4
5637 | TORONTO BUTTONVILLE A | 8 | 23 | 21 | 20.05 | 0 | 2.05
5638 | TORONTO BUTTONVILLE A | 8 | 22 | 22 | 21.4 | 0 | 3.4
5638 | TORONTO BUTTONVILLE A | 8 | 23 | 22 | 19.025 | 0 | 1.025
5639 | TORONTO BUTTONVILLE A | 8 | 22 | 23 | 20.6 | 0 | 2.6
5639 | TORONTO BUTTONVILLE A | 8 | 23 | 23 | 18.1 | 0 | 0.1
5640 | TORONTO BUTTONVILLE A | 8 | 22 | 24 | 20.3 | 0 | 2.3
5640 | TORONTO BUTTONVILLE A | 8 | 23 | 24 | 17.725 | 0 | 0
5641 | TORONTO BUTTONVILLE A | 8 | 23 | 1 | 20.9 | 0 | 2.9
5641 | TORONTO BUTTONVILLE A | 8 | 24 | 1 | 16.8 | 0 | 0
5642 | TORONTO BUTTONVILLE A | 8 | 23 | 2 | 19.9 | 0 | 1.9
5642 | TORONTO BUTTONVILLE A | 8 | 24 | 2 | 15.875 | 0 | 0
5643 | TORONTO BUTTONVILLE A | 8 | 23 | 3 | 19.6 | 0 | 1.6
5643 | TORONTO BUTTONVILLE A | 8 | 24 | 3 | 15.375 | 0 | 0
5644 | TORONTO BUTTONVILLE A | 8 | 23 | 4 | 18.6 | 0 | 0.6
5644 | TORONTO BUTTONVILLE A | 8 | 24 | 4 | 15.3 | 0 | 0
5645 | TORONTO BUTTONVILLE A | 8 | 23 | 5 | 18.4 | 0 | 0.4
5645 | TORONTO BUTTONVILLE A | 8 | 24 | 5 | 14.475 | 0 | 0
5646 | TORONTO BUTTONVILLE A | 8 | 23 | 6 | 18.4 | 0 | 0.4
5646 | TORONTO BUTTONVILLE A | 8 | 24 | 6 | 14.55 | 0 | 0
5647 | TORONTO BUTTONVILLE A | 8 | 23 | 7 | 18.1 | 0 | 0.1
5647 | TORONTO BUTTONVILLE A | 8 | 24 | 7 | 14.75 | 0 | 0
5648 | TORONTO BUTTONVILLE A | 8 | 23 | 8 | 20.1 | 0 | 2.1
5648 | TORONTO BUTTONVILLE A | 8 | 24 | 8 | 16.675 | 0 | 0
5649 | TORONTO BUTTONVILLE A | 8 | 23 | 9 | 23.1 | 0 | 5.1
5649 | TORONTO BUTTONVILLE A | 8 | 24 | 9 | 18.6 | 0 | 0.6
5650 | TORONTO BUTTONVILLE A | 8 | 23 | 10 | 25.9 | 0 | 7.9
5650 | TORONTO BUTTONVILLE A | 8 | 24 | 10 | 20.675 | 0 | 2.675
5651 | TORONTO BUTTONVILLE A | 8 | 23 | 11 | 28.4 | 0 | 10.4
5651 | TORONTO BUTTONVILLE A | 8 | 24 | 11 | 22.125 | 0 | 4.125
5652 | TORONTO BUTTONVILLE A | 8 | 23 | 12 | 29.8 | 0 | 11.8
5652 | TORONTO BUTTONVILLE A | 8 | 24 | 12 | 23.025 | 0 | 5.025
5653 | TORONTO BUTTONVILLE A | 8 | 23 | 13 | 31.2 | 0 | 13.2
5653 | TORONTO BUTTONVILLE A | 8 | 24 | 13 | 23.5 | 0 | 5.5
5654 | TORONTO BUTTONVILLE A | 8 | 23 | 14 | 31.9 | 0 | 13.9
5654 | TORONTO BUTTONVILLE A | 8 | 24 | 14 | 23.95 | 0 | 5.95
5655 | TORONTO BUTTONVILLE A | 8 | 23 | 15 | 30.1 | 0 | 12.1
5655 | TORONTO BUTTONVILLE A | 8 | 24 | 15 | 24.075 | 0 | 6.075
5656 | TORONTO BUTTONVILLE A | 8 | 23 | 16 | 31.8 | 0 | 13.8
5656 | TORONTO BUTTONVILLE A | 8 | 24 | 16 | 24.575 | 0 | 6.575
5657 | TORONTO BUTTONVILLE A | 8 | 23 | 17 | 30.8 | 0 | 12.8
5657 | TORONTO BUTTONVILLE A | 8 | 24 | 17 | 24.575 | 0 | 6.575
5658 | TORONTO BUTTONVILLE A | 8 | 23 | 18 | 30 | 0 | 12
5658 | TORONTO BUTTONVILLE A | 8 | 24 | 18 | 23.7 | 0 | 5.7
5659 | TORONTO BUTTONVILLE A | 8 | 23 | 19 | 28.8 | 0 | 10.8
5659 | TORONTO BUTTONVILLE A | 8 | 24 | 19 | 22.675 | 0 | 4.675
5660 | TORONTO BUTTONVILLE A | 8 | 23 | 20 | 28 | 0 | 10
5660 | TORONTO BUTTONVILLE A | 8 | 24 | 20 | 21.5 | 0 | 3.5
5661 | TORONTO BUTTONVILLE A | 8 | 23 | 21 | 22.1 | 0 | 4.1
5661 | TORONTO BUTTONVILLE A | 8 | 24 | 21 | 20.625 | 0 | 2.625
5662 | TORONTO BUTTONVILLE A | 8 | 23 | 22 | 21.2 | 0 | 3.2
5662 | TORONTO BUTTONVILLE A | 8 | 24 | 22 | 19.675 | 0 | 1.675
5663 | TORONTO BUTTONVILLE A | 8 | 23 | 23 | 21 | 0 | 3
5663 | TORONTO BUTTONVILLE A | 8 | 24 | 23 | 18.85 | 0 | 0.85
5664 | TORONTO BUTTONVILLE A | 8 | 23 | 24 | 21 | 0 | 3
5664 | TORONTO BUTTONVILLE A | 8 | 24 | 24 | 18.325 | 0 | 0.325
5665 | TORONTO BUTTONVILLE A | 8 | 24 | 1 | 20 | 0 | 2
5665 | TORONTO BUTTONVILLE A | 8 | 25 | 1 | 17.275 | 0 | 0
5666 | TORONTO BUTTONVILLE A | 8 | 24 | 2 | 19.9 | 0 | 1.9
5666 | TORONTO BUTTONVILLE A | 8 | 25 | 2 | 17.3 | 0 | 0
5667 | TORONTO BUTTONVILLE A | 8 | 24 | 3 | 19.3 | 0 | 1.3
5667 | TORONTO BUTTONVILLE A | 8 | 25 | 3 | 16.275 | 0 | 0
5668 | TORONTO BUTTONVILLE A | 8 | 24 | 4 | 19.6 | 0 | 1.6
5668 | TORONTO BUTTONVILLE A | 8 | 25 | 4 | 15.825 | 0 | 0
5669 | TORONTO BUTTONVILLE A | 8 | 24 | 5 | 20.1 | 0 | 2.1
5669 | TORONTO BUTTONVILLE A | 8 | 25 | 5 | 15.875 | 0 | 0
5670 | TORONTO BUTTONVILLE A | 8 | 24 | 6 | 20.6 | 0 | 2.6
5670 | TORONTO BUTTONVILLE A | 8 | 25 | 6 | 15.6 | 0 | 0
5671 | TORONTO BUTTONVILLE A | 8 | 24 | 7 | 20.4 | 0 | 2.4
5671 | TORONTO BUTTONVILLE A | 8 | 25 | 7 | 16.075 | 0 | 0
5672 | TORONTO BUTTONVILLE A | 8 | 24 | 8 | 22 | 0 | 4
5672 | TORONTO BUTTONVILLE A | 8 | 25 | 8 | 17.925 | 0 | 0
5673 | TORONTO BUTTONVILLE A | 8 | 24 | 9 | 24.2 | 0 | 6.2
5673 | TORONTO BUTTONVILLE A | 8 | 25 | 9 | 20.25 | 0 | 2.25
5674 | TORONTO BUTTONVILLE A | 8 | 24 | 10 | 26.4 | 0 | 8.4
5674 | TORONTO BUTTONVILLE A | 8 | 25 | 10 | 21.7 | 0 | 3.7
5675 | TORONTO BUTTONVILLE A | 8 | 24 | 11 | 28.5 | 0 | 10.5
5675 | TORONTO BUTTONVILLE A | 8 | 25 | 11 | 23.125 | 0 | 5.125
5676 | TORONTO BUTTONVILLE A | 8 | 24 | 12 | 28.7 | 0 | 10.7
5676 | TORONTO BUTTONVILLE A | 8 | 25 | 12 | 24.025 | 0 | 6.025
5677 | TORONTO BUTTONVILLE A | 8 | 24 | 13 | 30.2 | 0 | 12.2
5677 | TORONTO BUTTONVILLE A | 8 | 25 | 13 | 23.725 | 0 | 5.725
5678 | TORONTO BUTTONVILLE A | 8 | 24 | 14 | 31 | 0 | 13
5678 | TORONTO BUTTONVILLE A | 8 | 25 | 14 | 24.25 | 0 | 6.25
5679 | TORONTO BUTTONVILLE A | 8 | 24 | 15 | 31.5 | 0 | 13.5
5679 | TORONTO BUTTONVILLE A | 8 | 25 | 15 | 23.75 | 0 | 5.75
5680 | TORONTO BUTTONVILLE A | 8 | 24 | 16 | 31.5 | 0 | 13.5
5680 | TORONTO BUTTONVILLE A | 8 | 25 | 16 | 23.55 | 0 | 5.55
5681 | TORONTO BUTTONVILLE A | 8 | 24 | 17 | 31.2 | 0 | 13.2
5681 | TORONTO BUTTONVILLE A | 8 | 25 | 17 | 23.6 | 0 | 5.6
5682 | TORONTO BUTTONVILLE A | 8 | 24 | 18 | 30.7 | 0 | 12.7
5682 | TORONTO BUTTONVILLE A | 8 | 25 | 18 | 23.125 | 0 | 5.125
5683 | TORONTO BUTTONVILLE A | 8 | 24 | 19 | 29.9 | 0 | 11.9
5683 | TORONTO BUTTONVILLE A | 8 | 25 | 19 | 22.55 | 0 | 4.55
5684 | TORONTO BUTTONVILLE A | 8 | 24 | 20 | 28.7 | 0 | 10.7
5684 | TORONTO BUTTONVILLE A | 8 | 25 | 20 | 21.675 | 0 | 3.675
5685 | TORONTO BUTTONVILLE A | 8 | 24 | 21 | 27.9 | 0 | 9.9
5685 | TORONTO BUTTONVILLE A | 8 | 25 | 21 | 20.55 | 0 | 2.55
5686 | TORONTO BUTTONVILLE A | 8 | 24 | 22 | 27.2 | 0 | 9.2
5686 | TORONTO BUTTONVILLE A | 8 | 25 | 22 | 19.875 | 0 | 1.875
5687 | TORONTO BUTTONVILLE A | 8 | 24 | 23 | 26.2 | 0 | 8.2
5687 | TORONTO BUTTONVILLE A | 8 | 25 | 23 | 19.375 | 0 | 1.375
5688 | TORONTO BUTTONVILLE A | 8 | 24 | 24 | 25.6 | 0 | 7.6
5688 | TORONTO BUTTONVILLE A | 8 | 25 | 24 | 18.65 | 0 | 0.65
5689 | TORONTO BUTTONVILLE A | 8 | 25 | 1 | 24.2 | 0 | 6.2
5689 | TORONTO BUTTONVILLE A | 8 | 26 | 1 | 17.725 | 0 | 0
5690 | TORONTO BUTTONVILLE A | 8 | 25 | 2 | 22.8 | 0 | 4.8
5690 | TORONTO BUTTONVILLE A | 8 | 26 | 2 | 17.575 | 0 | 0
5691 | TORONTO BUTTONVILLE A | 8 | 25 | 3 | 22.7 | 0 | 4.7
5691 | TORONTO BUTTONVILLE A | 8 | 26 | 3 | 17 | 0 | 0
5692 | TORONTO BUTTONVILLE A | 8 | 25 | 4 | 22.2 | 0 | 4.2
5692 | TORONTO BUTTONVILLE A | 8 | 26 | 4 | 16.675 | 0 | 0
5693 | TORONTO BUTTONVILLE A | 8 | 25 | 5 | 22.1 | 0 | 4.1
5693 | TORONTO BUTTONVILLE A | 8 | 26 | 5 | 16.6 | 0 | 0
5694 | TORONTO BUTTONVILLE A | 8 | 25 | 6 | 21.4 | 0 | 3.4
5694 | TORONTO BUTTONVILLE A | 8 | 26 | 6 | 16.7 | 0 | 0
5695 | TORONTO BUTTONVILLE A | 8 | 25 | 7 | 21.1 | 0 | 3.1
5695 | TORONTO BUTTONVILLE A | 8 | 26 | 7 | 17.075 | 0 | 0
5696 | TORONTO BUTTONVILLE A | 8 | 25 | 8 | 22.1 | 0 | 4.1
5696 | TORONTO BUTTONVILLE A | 8 | 26 | 8 | 18.425 | 0 | 0.425
5697 | TORONTO BUTTONVILLE A | 8 | 25 | 9 | 23.2 | 0 | 5.2
5697 | TORONTO BUTTONVILLE A | 8 | 26 | 9 | 20.2 | 0 | 2.2
5698 | TORONTO BUTTONVILLE A | 8 | 25 | 10 | 23.9 | 0 | 5.9
5698 | TORONTO BUTTONVILLE A | 8 | 26 | 10 | 22.3 | 0 | 4.3
5699 | TORONTO BUTTONVILLE A | 8 | 25 | 11 | 24.8 | 0 | 6.8
5699 | TORONTO BUTTONVILLE A | 8 | 26 | 11 | 23.55 | 0 | 5.55
5700 | TORONTO BUTTONVILLE A | 8 | 25 | 12 | 25.1 | 0 | 7.1
5700 | TORONTO BUTTONVILLE A | 8 | 26 | 12 | 24.525 | 0 | 6.525
5701 | TORONTO BUTTONVILLE A | 8 | 25 | 13 | 25.6 | 0 | 7.6
5701 | TORONTO BUTTONVILLE A | 8 | 26 | 13 | 24.75 | 0 | 6.75
5702 | TORONTO BUTTONVILLE A | 8 | 25 | 14 | 25.4 | 0 | 7.4
5702 | TORONTO BUTTONVILLE A | 8 | 26 | 14 | 25.575 | 0 | 7.575
5703 | TORONTO BUTTONVILLE A | 8 | 25 | 15 | 25.6 | 0 | 7.6
5703 | TORONTO BUTTONVILLE A | 8 | 26 | 15 | 26.225 | 0 | 8.225
5704 | TORONTO BUTTONVILLE A | 8 | 25 | 16 | 25.4 | 0 | 7.4
5704 | TORONTO BUTTONVILLE A | 8 | 26 | 16 | 24.275 | 0 | 6.275
5705 | TORONTO BUTTONVILLE A | 8 | 25 | 17 | 24.8 | 0 | 6.8
5705 | TORONTO BUTTONVILLE A | 8 | 26 | 17 | 24.45 | 0 | 6.45
5706 | TORONTO BUTTONVILLE A | 8 | 25 | 18 | 24.5 | 0 | 6.5
5706 | TORONTO BUTTONVILLE A | 8 | 26 | 18 | 24.5 | 0 | 6.5
5707 | TORONTO BUTTONVILLE A | 8 | 25 | 19 | 23 | 0 | 5
5707 | TORONTO BUTTONVILLE A | 8 | 26 | 19 | 23.375 | 0 | 5.375
5708 | TORONTO BUTTONVILLE A | 8 | 25 | 20 | 21.2 | 0 | 3.2
5708 | TORONTO BUTTONVILLE A | 8 | 26 | 20 | 21.95 | 0 | 3.95
5709 | TORONTO BUTTONVILLE A | 8 | 25 | 21 | 20.9 | 0 | 2.9
5709 | TORONTO BUTTONVILLE A | 8 | 26 | 21 | 21.05 | 0 | 3.05
5710 | TORONTO BUTTONVILLE A | 8 | 25 | 22 | 19.8 | 0 | 1.8
5710 | TORONTO BUTTONVILLE A | 8 | 26 | 22 | 20.175 | 0 | 2.175
5711 | TORONTO BUTTONVILLE A | 8 | 25 | 23 | 18.9 | 0 | 0.9
5711 | TORONTO BUTTONVILLE A | 8 | 26 | 23 | 19.325 | 0 | 1.325
5712 | TORONTO BUTTONVILLE A | 8 | 25 | 24 | 17.1 | 0 | 0
5712 | TORONTO BUTTONVILLE A | 8 | 26 | 24 | 18.85 | 0 | 0.85
5713 | TORONTO BUTTONVILLE A | 8 | 26 | 1 | 16.1 | 0 | 0
5713 | TORONTO BUTTONVILLE A | 8 | 27 | 1 | 18.275 | 0 | 0.275
5714 | TORONTO BUTTONVILLE A | 8 | 26 | 2 | 14.9 | 0 | 0
5714 | TORONTO BUTTONVILLE A | 8 | 27 | 2 | 17.775 | 0 | 0
5715 | TORONTO BUTTONVILLE A | 8 | 26 | 3 | 14 | 0 | 0
5715 | TORONTO BUTTONVILLE A | 8 | 27 | 3 | 17.75 | 0 | 0
5716 | TORONTO BUTTONVILLE A | 8 | 26 | 4 | 13.1 | 0 | 0
5716 | TORONTO BUTTONVILLE A | 8 | 27 | 4 | 17.25 | 0 | 0
5717 | TORONTO BUTTONVILLE A | 8 | 26 | 5 | 11.8 | 0 | 0
5717 | TORONTO BUTTONVILLE A | 8 | 27 | 5 | 17.325 | 0 | 0
5718 | TORONTO BUTTONVILLE A | 8 | 26 | 6 | 12 | 0 | 0
5718 | TORONTO BUTTONVILLE A | 8 | 27 | 6 | 17.475 | 0 | 0
5719 | TORONTO BUTTONVILLE A | 8 | 26 | 7 | 12.7 | 0 | 0
5719 | TORONTO BUTTONVILLE A | 8 | 27 | 7 | 16.8 | 0 | 0
5720 | TORONTO BUTTONVILLE A | 8 | 26 | 8 | 13.3 | 0 | 0
5720 | TORONTO BUTTONVILLE A | 8 | 27 | 8 | 17.825 | 0 | 0
5721 | TORONTO BUTTONVILLE A | 8 | 26 | 9 | 15 | 0 | 0
5721 | TORONTO BUTTONVILLE A | 8 | 27 | 9 | 19.15 | 0 | 1.15
5722 | TORONTO BUTTONVILLE A | 8 | 26 | 10 | 16.1 | 0 | 0
5722 | TORONTO BUTTONVILLE A | 8 | 27 | 10 | 20 | 0 | 2
5723 | TORONTO BUTTONVILLE A | 8 | 26 | 11 | 18.2 | 0 | 0.2
5723 | TORONTO BUTTONVILLE A | 8 | 27 | 11 | 21.225 | 0 | 3.225
5724 | TORONTO BUTTONVILLE A | 8 | 26 | 12 | 19.7 | 0 | 1.7
5724 | TORONTO BUTTONVILLE A | 8 | 27 | 12 | 21.975 | 0 | 3.975
5725 | TORONTO BUTTONVILLE A | 8 | 26 | 13 | 19.8 | 0 | 1.8
5725 | TORONTO BUTTONVILLE A | 8 | 27 | 13 | 22.55 | 0 | 4.55
5726 | TORONTO BUTTONVILLE A | 8 | 26 | 14 | 20.5 | 0 | 2.5
5726 | TORONTO BUTTONVILLE A | 8 | 27 | 14 | 22.575 | 0 | 4.575
5727 | TORONTO BUTTONVILLE A | 8 | 26 | 15 | 21.2 | 0 | 3.2
5727 | TORONTO BUTTONVILLE A | 8 | 27 | 15 | 22.725 | 0 | 4.725
5728 | TORONTO BUTTONVILLE A | 8 | 26 | 16 | 21.3 | 0 | 3.3
5728 | TORONTO BUTTONVILLE A | 8 | 27 | 16 | 23.475 | 0 | 5.475
5729 | TORONTO BUTTONVILLE A | 8 | 26 | 17 | 21.3 | 0 | 3.3
5729 | TORONTO BUTTONVILLE A | 8 | 27 | 17 | 23.1 | 0 | 5.1
5730 | TORONTO BUTTONVILLE A | 8 | 26 | 18 | 20.5 | 0 | 2.5
5730 | TORONTO BUTTONVILLE A | 8 | 27 | 18 | 23.025 | 0 | 5.025
5731 | TORONTO BUTTONVILLE A | 8 | 26 | 19 | 19.3 | 0 | 1.3
5731 | TORONTO BUTTONVILLE A | 8 | 27 | 19 | 22.6 | 0 | 4.6
5732 | TORONTO BUTTONVILLE A | 8 | 26 | 20 | 18.9 | 0 | 0.9
5732 | TORONTO BUTTONVILLE A | 8 | 27 | 20 | 22.05 | 0 | 4.05
5733 | TORONTO BUTTONVILLE A | 8 | 26 | 21 | 18.1 | 0 | 0.1
5733 | TORONTO BUTTONVILLE A | 8 | 27 | 21 | 21.5 | 0 | 3.5
5734 | TORONTO BUTTONVILLE A | 8 | 26 | 22 | 17.8 | 0 | 0
5734 | TORONTO BUTTONVILLE A | 8 | 27 | 22 | 21.2 | 0 | 3.2
5735 | TORONTO BUTTONVILLE A | 8 | 26 | 23 | 17.9 | 0 | 0
5735 | TORONTO BUTTONVILLE A | 8 | 27 | 23 | 20.975 | 0 | 2.975
5736 | TORONTO BUTTONVILLE A | 8 | 26 | 24 | 18 | 0 | 0
5736 | TORONTO BUTTONVILLE A | 8 | 27 | 24 | 19.95 | 0 | 1.95
5737 | TORONTO BUTTONVILLE A | 8 | 27 | 1 | 18.2 | 0 | 0.2
5737 | TORONTO BUTTONVILLE A | 8 | 28 | 1 | 19.675 | 0 | 1.675
5738 | TORONTO BUTTONVILLE A | 8 | 27 | 2 | 18.5 | 0 | 0.5
5738 | TORONTO BUTTONVILLE A | 8 | 28 | 2 | 19.6 | 0 | 1.6
5739 | TORONTO BUTTONVILLE A | 8 | 27 | 3 | 18.9 | 0 | 0.9
5739 | TORONTO BUTTONVILLE A | 8 | 28 | 3 | 19.65 | 0 | 1.65
5740 | TORONTO BUTTONVILLE A | 8 | 27 | 4 | 18.8 | 0 | 0.8
5740 | TORONTO BUTTONVILLE A | 8 | 28 | 4 | 19.275 | 0 | 1.275
5741 | TORONTO BUTTONVILLE A | 8 | 27 | 5 | 19.1 | 0 | 1.1
5741 | TORONTO BUTTONVILLE A | 8 | 28 | 5 | 18.975 | 0 | 0.975
5742 | TORONTO BUTTONVILLE A | 8 | 27 | 6 | 19.4 | 0 | 1.4
5742 | TORONTO BUTTONVILLE A | 8 | 28 | 6 | 18.875 | 0 | 0.875
5743 | TORONTO BUTTONVILLE A | 8 | 27 | 7 | 19.8 | 0 | 1.8
5743 | TORONTO BUTTONVILLE A | 8 | 28 | 7 | 18.55 | 0 | 0.55
5744 | TORONTO BUTTONVILLE A | 8 | 27 | 8 | 20.8 | 0 | 2.8
5744 | TORONTO BUTTONVILLE A | 8 | 28 | 8 | 19.55 | 0 | 1.55
5745 | TORONTO BUTTONVILLE A | 8 | 27 | 9 | 22.6 | 0 | 4.6
5745 | TORONTO BUTTONVILLE A | 8 | 28 | 9 | 20.7 | 0 | 2.7
5746 | TORONTO BUTTONVILLE A | 8 | 27 | 10 | 25 | 0 | 7
5746 | TORONTO BUTTONVILLE A | 8 | 28 | 10 | 22.175 | 0 | 4.175
5747 | TORONTO BUTTONVILLE A | 8 | 27 | 11 | 27.2 | 0 | 9.2
5747 | TORONTO BUTTONVILLE A | 8 | 28 | 11 | 23.125 | 0 | 5.125
5748 | TORONTO BUTTONVILLE A | 8 | 27 | 12 | 27.6 | 0 | 9.6
5748 | TORONTO BUTTONVILLE A | 8 | 28 | 12 | 24.35 | 0 | 6.35
5749 | TORONTO BUTTONVILLE A | 8 | 27 | 13 | 28.4 | 0 | 10.4
5749 | TORONTO BUTTONVILLE A | 8 | 28 | 13 | 24.85 | 0 | 6.85
5750 | TORONTO BUTTONVILLE A | 8 | 27 | 14 | 28.3 | 0 | 10.3
5750 | TORONTO BUTTONVILLE A | 8 | 28 | 14 | 25.675 | 0 | 7.675
5751 | TORONTO BUTTONVILLE A | 8 | 27 | 15 | 29.2 | 0 | 11.2
5751 | TORONTO BUTTONVILLE A | 8 | 28 | 15 | 26.45 | 0 | 8.45
5752 | TORONTO BUTTONVILLE A | 8 | 27 | 16 | 27.2 | 0 | 9.2
5752 | TORONTO BUTTONVILLE A | 8 | 28 | 16 | 26.225 | 0 | 8.225
5753 | TORONTO BUTTONVILLE A | 8 | 27 | 17 | 27.4 | 0 | 9.4
5753 | TORONTO BUTTONVILLE A | 8 | 28 | 17 | 25.95 | 0 | 7.95
5754 | TORONTO BUTTONVILLE A | 8 | 27 | 18 | 26 | 0 | 8
5754 | TORONTO BUTTONVILLE A | 8 | 28 | 18 | 24.575 | 0 | 6.575
5755 | TORONTO BUTTONVILLE A | 8 | 27 | 19 | 25 | 0 | 7
5755 | TORONTO BUTTONVILLE A | 8 | 28 | 19 | 23.675 | 0 | 5.675
5756 | TORONTO BUTTONVILLE A | 8 | 27 | 20 | 23.2 | 0 | 5.2
5756 | TORONTO BUTTONVILLE A | 8 | 28 | 20 | 22.75 | 0 | 4.75
5757 | TORONTO BUTTONVILLE A | 8 | 27 | 21 | 21.9 | 0 | 3.9
5757 | TORONTO BUTTONVILLE A | 8 | 28 | 21 | 22.3 | 0 | 4.3
5758 | TORONTO BUTTONVILLE A | 8 | 27 | 22 | 21.1 | 0 | 3.1
5758 | TORONTO BUTTONVILLE A | 8 | 28 | 22 | 21.5 | 0 | 3.5
5759 | TORONTO BUTTONVILLE A | 8 | 27 | 23 | 20.3 | 0 | 2.3
5759 | TORONTO BUTTONVILLE A | 8 | 28 | 23 | 21.2 | 0 | 3.2
5760 | TORONTO BUTTONVILLE A | 8 | 27 | 24 | 19.7 | 0 | 1.7
5760 | TORONTO BUTTONVILLE A | 8 | 28 | 24 | 20.875 | 0 | 2.875
5761 | TORONTO BUTTONVILLE A | 8 | 28 | 1 | 19.4 | 0 | 1.4
5761 | TORONTO BUTTONVILLE A | 8 | 29 | 1 | 20.35 | 0 | 2.35
5762 | TORONTO BUTTONVILLE A | 8 | 28 | 2 | 18.7 | 0 | 0.7
5762 | TORONTO BUTTONVILLE A | 8 | 29 | 2 | 20.15 | 0 | 2.15
5763 | TORONTO BUTTONVILLE A | 8 | 28 | 3 | 17.8 | 0 | 0
5763 | TORONTO BUTTONVILLE A | 8 | 29 | 3 | 20.05 | 0 | 2.05
5764 | TORONTO BUTTONVILLE A | 8 | 28 | 4 | 16.8 | 0 | 0
5764 | TORONTO BUTTONVILLE A | 8 | 29 | 4 | 19.775 | 0 | 1.775
5765 | TORONTO BUTTONVILLE A | 8 | 28 | 5 | 16.3 | 0 | 0
5765 | TORONTO BUTTONVILLE A | 8 | 29 | 5 | 18.875 | 0 | 0.875
5766 | TORONTO BUTTONVILLE A | 8 | 28 | 6 | 16.8 | 0 | 0
5766 | TORONTO BUTTONVILLE A | 8 | 29 | 6 | 18.6 | 0 | 0.6
5767 | TORONTO BUTTONVILLE A | 8 | 28 | 7 | 16.3 | 0 | 0
5767 | TORONTO BUTTONVILLE A | 8 | 29 | 7 | 18.875 | 0 | 0.875
5768 | TORONTO BUTTONVILLE A | 8 | 28 | 8 | 17.4 | 0 | 0
5768 | TORONTO BUTTONVILLE A | 8 | 29 | 8 | 19.85 | 0 | 1.85
5769 | TORONTO BUTTONVILLE A | 8 | 28 | 9 | 18.8 | 0 | 0.8
5769 | TORONTO BUTTONVILLE A | 8 | 29 | 9 | 21.325 | 0 | 3.325
5770 | TORONTO BUTTONVILLE A | 8 | 28 | 10 | 19.6 | 0 | 1.6
5770 | TORONTO BUTTONVILLE A | 8 | 29 | 10 | 22.875 | 0 | 4.875
5771 | TORONTO BUTTONVILLE A | 8 | 28 | 11 | 20.6 | 0 | 2.6
5771 | TORONTO BUTTONVILLE A | 8 | 29 | 11 | 23.675 | 0 | 5.675
5772 | TORONTO BUTTONVILLE A | 8 | 28 | 12 | 21.1 | 0 | 3.1
5772 | TORONTO BUTTONVILLE A | 8 | 29 | 12 | 24.075 | 0 | 6.075
5773 | TORONTO BUTTONVILLE A | 8 | 28 | 13 | 21.8 | 0 | 3.8
5773 | TORONTO BUTTONVILLE A | 8 | 29 | 13 | 24.8 | 0 | 6.8
5774 | TORONTO BUTTONVILLE A | 8 | 28 | 14 | 23.4 | 0 | 5.4
5774 | TORONTO BUTTONVILLE A | 8 | 29 | 14 | 25.725 | 0 | 7.725
5775 | TORONTO BUTTONVILLE A | 8 | 28 | 15 | 23 | 0 | 5
5775 | TORONTO BUTTONVILLE A | 8 | 29 | 15 | 25.05 | 0 | 7.05
5776 | TORONTO BUTTONVILLE A | 8 | 28 | 16 | 21.9 | 0 | 3.9
5776 | TORONTO BUTTONVILLE A | 8 | 29 | 16 | 25.45 | 0 | 7.45
5777 | TORONTO BUTTONVILLE A | 8 | 28 | 17 | 21.3 | 0 | 3.3
5777 | TORONTO BUTTONVILLE A | 8 | 29 | 17 | 25.725 | 0 | 7.725
5778 | TORONTO BUTTONVILLE A | 8 | 28 | 18 | 20.6 | 0 | 2.6
5778 | TORONTO BUTTONVILLE A | 8 | 29 | 18 | 25.15 | 0 | 7.15
5779 | TORONTO BUTTONVILLE A | 8 | 28 | 19 | 20 | 0 | 2
5779 | TORONTO BUTTONVILLE A | 8 | 29 | 19 | 22.675 | 0 | 4.675
5780 | TORONTO BUTTONVILLE A | 8 | 28 | 20 | 19.5 | 0 | 1.5
5780 | TORONTO BUTTONVILLE A | 8 | 29 | 20 | 21.475 | 0 | 3.475
5781 | TORONTO BUTTONVILLE A | 8 | 28 | 21 | 19.5 | 0 | 1.5
5781 | TORONTO BUTTONVILLE A | 8 | 29 | 21 | 20.4 | 0 | 2.4
5782 | TORONTO BUTTONVILLE A | 8 | 28 | 22 | 19 | 0 | 1
5782 | TORONTO BUTTONVILLE A | 8 | 29 | 22 | 19.775 | 0 | 1.775
5783 | TORONTO BUTTONVILLE A | 8 | 28 | 23 | 19.6 | 0 | 1.6
5783 | TORONTO BUTTONVILLE A | 8 | 29 | 23 | 18.85 | 0 | 0.85
5784 | TORONTO BUTTONVILLE A | 8 | 28 | 24 | 19.8 | 0 | 1.8
5784 | TORONTO BUTTONVILLE A | 8 | 29 | 24 | 18.775 | 0 | 0.775
5785 | TORONTO BUTTONVILLE A | 8 | 29 | 1 | 18.8 | 0 | 0.8
5785 | TORONTO BUTTONVILLE A | 8 | 30 | 1 | 18.425 | 0 | 0.425
5786 | TORONTO BUTTONVILLE A | 8 | 29 | 2 | 19 | 0 | 1
5786 | TORONTO BUTTONVILLE A | 8 | 30 | 2 | 18.425 | 0 | 0.425
5787 | TORONTO BUTTONVILLE A | 8 | 29 | 3 | 19.4 | 0 | 1.4
5787 | TORONTO BUTTONVILLE A | 8 | 30 | 3 | 18.2 | 0 | 0.2
5788 | TORONTO BUTTONVILLE A | 8 | 29 | 4 | 20.2 | 0 | 2.2
5788 | TORONTO BUTTONVILLE A | 8 | 30 | 4 | 17.525 | 0 | 0
5789 | TORONTO BUTTONVILLE A | 8 | 29 | 5 | 20.7 | 0 | 2.7
5789 | TORONTO BUTTONVILLE A | 8 | 30 | 5 | 16.65 | 0 | 0
5790 | TORONTO BUTTONVILLE A | 8 | 29 | 6 | 20.7 | 0 | 2.7
5790 | TORONTO BUTTONVILLE A | 8 | 30 | 6 | 16.175 | 0 | 0
5791 | TORONTO BUTTONVILLE A | 8 | 29 | 7 | 20.6 | 0 | 2.6
5791 | TORONTO BUTTONVILLE A | 8 | 30 | 7 | 15.775 | 0 | 0
5792 | TORONTO BUTTONVILLE A | 8 | 29 | 8 | 21.2 | 0 | 3.2
5792 | TORONTO BUTTONVILLE A | 8 | 30 | 8 | 16.775 | 0 | 0
5793 | TORONTO BUTTONVILLE A | 8 | 29 | 9 | 22 | 0 | 4
5793 | TORONTO BUTTONVILLE A | 8 | 30 | 9 | 18.25 | 0 | 0.25
5794 | TORONTO BUTTONVILLE A | 8 | 29 | 10 | 22.3 | 0 | 4.3
5794 | TORONTO BUTTONVILLE A | 8 | 30 | 10 | 19.6 | 0 | 1.6
5795 | TORONTO BUTTONVILLE A | 8 | 29 | 11 | 23.8 | 0 | 5.8
5795 | TORONTO BUTTONVILLE A | 8 | 30 | 11 | 20.4 | 0 | 2.4
5796 | TORONTO BUTTONVILLE A | 8 | 29 | 12 | 24.6 | 0 | 6.6
5796 | TORONTO BUTTONVILLE A | 8 | 30 | 12 | 21.525 | 0 | 3.525
5797 | TORONTO BUTTONVILLE A | 8 | 29 | 13 | 25.1 | 0 | 7.1
5797 | TORONTO BUTTONVILLE A | 8 | 30 | 13 | 22.35 | 0 | 4.35
5798 | TORONTO BUTTONVILLE A | 8 | 29 | 14 | 23.9 | 0 | 5.9
5798 | TORONTO BUTTONVILLE A | 8 | 30 | 14 | 22.85 | 0 | 4.85
5799 | TORONTO BUTTONVILLE A | 8 | 29 | 15 | 20.4 | 0 | 2.4
5799 | TORONTO BUTTONVILLE A | 8 | 30 | 15 | 22.9 | 0 | 4.9
5800 | TORONTO BUTTONVILLE A | 8 | 29 | 16 | 20.8 | 0 | 2.8
5800 | TORONTO BUTTONVILLE A | 8 | 30 | 16 | 23.025 | 0 | 5.025
5801 | TORONTO BUTTONVILLE A | 8 | 29 | 17 | 20.9 | 0 | 2.9
5801 | TORONTO BUTTONVILLE A | 8 | 30 | 17 | 23.05 | 0 | 5.05
5802 | TORONTO BUTTONVILLE A | 8 | 29 | 18 | 20.7 | 0 | 2.7
5802 | TORONTO BUTTONVILLE A | 8 | 30 | 18 | 22.225 | 0 | 4.225
5803 | TORONTO BUTTONVILLE A | 8 | 29 | 19 | 20.5 | 0 | 2.5
5803 | TORONTO BUTTONVILLE A | 8 | 30 | 19 | 21.4 | 0 | 3.4
5804 | TORONTO BUTTONVILLE A | 8 | 29 | 20 | 19.6 | 0 | 1.6
5804 | TORONTO BUTTONVILLE A | 8 | 30 | 20 | 20.075 | 0 | 2.075
5805 | TORONTO BUTTONVILLE A | 8 | 29 | 21 | 18.7 | 0 | 0.7
5805 | TORONTO BUTTONVILLE A | 8 | 30 | 21 | 19.65 | 0 | 1.65
5806 | TORONTO BUTTONVILLE A | 8 | 29 | 22 | 17.9 | 0 | 0
5806 | TORONTO BUTTONVILLE A | 8 | 30 | 22 | 18.55 | 0 | 0.55
5807 | TORONTO BUTTONVILLE A | 8 | 29 | 23 | 17.7 | 0 | 0
5807 | TORONTO BUTTONVILLE A | 8 | 30 | 23 | 17.325 | 0 | 0
5808 | TORONTO BUTTONVILLE A | 8 | 29 | 24 | 16.9 | 0 | 0
5808 | TORONTO BUTTONVILLE A | 8 | 30 | 24 | 16.65 | 0 | 0
5809 | TORONTO BUTTONVILLE A | 8 | 30 | 1 | 16.3 | 0 | 0
5809 | TORONTO BUTTONVILLE A | 8 | 31 | 1 | 16.175 | 0 | 0
5810 | TORONTO BUTTONVILLE A | 8 | 30 | 2 | 15.9 | 0 | 0
5810 | TORONTO BUTTONVILLE A | 8 | 31 | 2 | 16.275 | 0 | 0
5811 | TORONTO BUTTONVILLE A | 8 | 30 | 3 | 15.8 | 0 | 0
5811 | TORONTO BUTTONVILLE A | 8 | 31 | 3 | 16 | 0 | 0
5812 | TORONTO BUTTONVILLE A | 8 | 30 | 4 | 15.5 | 0 | 0
5812 | TORONTO BUTTONVILLE A | 8 | 31 | 4 | 15.75 | 0 | 0
5813 | TORONTO BUTTONVILLE A | 8 | 30 | 5 | 14.6 | 0 | 0
5813 | TORONTO BUTTONVILLE A | 8 | 31 | 5 | 15.425 | 0 | 0
5814 | TORONTO BUTTONVILLE A | 8 | 30 | 6 | 14.5 | 0 | 0
5814 | TORONTO BUTTONVILLE A | 8 | 31 | 6 | 14.875 | 0 | 0
5815 | TORONTO BUTTONVILLE A | 8 | 30 | 7 | 14.4 | 0 | 0
5815 | TORONTO BUTTONVILLE A | 8 | 31 | 7 | 14.925 | 0 | 0
5816 | TORONTO BUTTONVILLE A | 8 | 30 | 8 | 15.9 | 0 | 0
5816 | TORONTO BUTTONVILLE A | 8 | 31 | 8 | 15.5 | 0 | 0
5817 | TORONTO BUTTONVILLE A | 8 | 30 | 9 | 16.8 | 0 | 0
5817 | TORONTO BUTTONVILLE A | 8 | 31 | 9 | 16.8 | 0 | 0
5818 | TORONTO BUTTONVILLE A | 8 | 30 | 10 | 18.2 | 0 | 0.2
5818 | TORONTO BUTTONVILLE A | 8 | 31 | 10 | 17.825 | 0 | 0
5819 | TORONTO BUTTONVILLE A | 8 | 30 | 11 | 19 | 0 | 1
5819 | TORONTO BUTTONVILLE A | 8 | 31 | 11 | 18.925 | 0 | 0.925
5820 | TORONTO BUTTONVILLE A | 8 | 30 | 12 | 19 | 0 | 1
5820 | TORONTO BUTTONVILLE A | 8 | 31 | 12 | 19.65 | 0 | 1.65
5821 | TORONTO BUTTONVILLE A | 8 | 30 | 13 | 21 | 0 | 3
5821 | TORONTO BUTTONVILLE A | 8 | 31 | 13 | 20 | 0 | 2
5822 | TORONTO BUTTONVILLE A | 8 | 30 | 14 | 21.1 | 0 | 3.1
5822 | TORONTO BUTTONVILLE A | 8 | 31 | 14 | 20.575 | 0 | 2.575
5823 | TORONTO BUTTONVILLE A | 8 | 30 | 15 | 21.7 | 0 | 3.7
5823 | TORONTO BUTTONVILLE A | 8 | 31 | 15 | 21.725 | 0 | 3.725
5824 | TORONTO BUTTONVILLE A | 8 | 30 | 16 | 20.7 | 0 | 2.7
5824 | TORONTO BUTTONVILLE A | 8 | 31 | 16 | 20.95 | 0 | 2.95
5825 | TORONTO BUTTONVILLE A | 8 | 30 | 17 | 21.9 | 0 | 3.9
5825 | TORONTO BUTTONVILLE A | 8 | 31 | 17 | 20.575 | 0 | 2.575
5826 | TORONTO BUTTONVILLE A | 8 | 30 | 18 | 21.2 | 0 | 3.2
5826 | TORONTO BUTTONVILLE A | 8 | 31 | 18 | 19.925 | 0 | 1.925
5827 | TORONTO BUTTONVILLE A | 8 | 30 | 19 | 20 | 0 | 2
5827 | TORONTO BUTTONVILLE A | 8 | 31 | 19 | 19.075 | 0 | 1.075
5828 | TORONTO BUTTONVILLE A | 8 | 30 | 20 | 18.2 | 0 | 0.2
5828 | TORONTO BUTTONVILLE A | 8 | 31 | 20 | 17.375 | 0 | 0
5829 | TORONTO BUTTONVILLE A | 8 | 30 | 21 | 17.4 | 0 | 0
5829 | TORONTO BUTTONVILLE A | 8 | 31 | 21 | 16.5 | 0 | 0
5830 | TORONTO BUTTONVILLE A | 8 | 30 | 22 | 16.6 | 0 | 0
5830 | TORONTO BUTTONVILLE A | 8 | 31 | 22 | 15.85 | 0 | 0
5831 | TORONTO BUTTONVILLE A | 8 | 30 | 23 | 16.3 | 0 | 0
5831 | TORONTO BUTTONVILLE A | 8 | 31 | 23 | 15.025 | 0 | 0
5832 | TORONTO BUTTONVILLE A | 8 | 30 | 24 | 16.4 | 0 | 0
5832 | TORONTO BUTTONVILLE A | 8 | 31 | 24 | 13.8 | 0 | 0
5833 | TORONTO BUTTONVILLE A | 8 | 31 | 1 | 15 | 0 | 0
5833 | TORONTO BUTTONVILLE A | 9 | 1 | 1 | 13.575 | 4.425 | 0
5834 | TORONTO BUTTONVILLE A | 8 | 31 | 2 | 14 | 0 | 0
5834 | TORONTO BUTTONVILLE A | 9 | 1 | 2 | 13.1 | 4.9 | 0
5835 | TORONTO BUTTONVILLE A | 8 | 31 | 3 | 14.2 | 0 | 0
5835 | TORONTO BUTTONVILLE A | 9 | 1 | 3 | 12.55 | 5.45 | 0
5836 | TORONTO BUTTONVILLE A | 8 | 31 | 4 | 13.4 | 0 | 0
5836 | TORONTO BUTTONVILLE A | 9 | 1 | 4 | 12.8 | 5.2 | 0
5837 | TORONTO BUTTONVILLE A | 8 | 31 | 5 | 13 | 0 | 0
5837 | TORONTO BUTTONVILLE A | 9 | 1 | 5 | 12.325 | 5.675 | 0
5838 | TORONTO BUTTONVILLE A | 8 | 31 | 6 | 14 | 0 | 0
5838 | TORONTO BUTTONVILLE A | 9 | 1 | 6 | 12.225 | 5.775 | 0
5839 | TORONTO BUTTONVILLE A | 8 | 31 | 7 | 13.8 | 0 | 0
5839 | TORONTO BUTTONVILLE A | 9 | 1 | 7 | 12.625 | 5.375 | 0
5840 | TORONTO BUTTONVILLE A | 8 | 31 | 8 | 15.3 | 0 | 0
5840 | TORONTO BUTTONVILLE A | 9 | 1 | 8 | 14.275 | 3.725 | 0
5841 | TORONTO BUTTONVILLE A | 8 | 31 | 9 | 17.4 | 0 | 0
5841 | TORONTO BUTTONVILLE A | 9 | 1 | 9 | 15.8 | 2.2 | 0
5842 | TORONTO BUTTONVILLE A | 8 | 31 | 10 | 19.6 | 0 | 1.6
5842 | TORONTO BUTTONVILLE A | 9 | 1 | 10 | 17.175 | 0.825 | 0
5843 | TORONTO BUTTONVILLE A | 8 | 31 | 11 | 20.8 | 0 | 2.8
5843 | TORONTO BUTTONVILLE A | 9 | 1 | 11 | 18.325 | 0 | 0.325
5844 | TORONTO BUTTONVILLE A | 8 | 31 | 12 | 21.6 | 0 | 3.6
5844 | TORONTO BUTTONVILLE A | 9 | 1 | 12 | 19.525 | 0 | 1.525
5845 | TORONTO BUTTONVILLE A | 8 | 31 | 13 | 22.8 | 0 | 4.8
5845 | TORONTO BUTTONVILLE A | 9 | 1 | 13 | 20.05 | 0 | 2.05
5846 | TORONTO BUTTONVILLE A | 8 | 31 | 14 | 23.2 | 0 | 5.2
5846 | TORONTO BUTTONVILLE A | 9 | 1 | 14 | 20.75 | 0 | 2.75
5847 | TORONTO BUTTONVILLE A | 8 | 31 | 15 | 23.2 | 0 | 5.2
5847 | TORONTO BUTTONVILLE A | 9 | 1 | 15 | 21.1 | 0 | 3.1
5848 | TORONTO BUTTONVILLE A | 8 | 31 | 16 | 23.1 | 0 | 5.1
5848 | TORONTO BUTTONVILLE A | 9 | 1 | 16 | 21.35 | 0 | 3.35
5849 | TORONTO BUTTONVILLE A | 8 | 31 | 17 | 22.1 | 0 | 4.1
5849 | TORONTO BUTTONVILLE A | 9 | 1 | 17 | 21.225 | 0 | 3.225
5850 | TORONTO BUTTONVILLE A | 8 | 31 | 18 | 21.5 | 0 | 3.5
5850 | TORONTO BUTTONVILLE A | 9 | 1 | 18 | 20.65 | 0 | 2.65
5851 | TORONTO BUTTONVILLE A | 8 | 31 | 19 | 20.6 | 0 | 2.6
5851 | TORONTO BUTTONVILLE A | 9 | 1 | 19 | 19.75 | 0 | 1.75
5852 | TORONTO BUTTONVILLE A | 8 | 31 | 20 | 19.7 | 0 | 1.7
5852 | TORONTO BUTTONVILLE A | 9 | 1 | 20 | 18.4 | 0 | 0.4
5853 | TORONTO BUTTONVILLE A | 8 | 31 | 21 | 19.8 | 0 | 1.8
5853 | TORONTO BUTTONVILLE A | 9 | 1 | 21 | 17.425 | 0.575 | 0
5854 | TORONTO BUTTONVILLE A | 8 | 31 | 22 | 19.6 | 0 | 1.6
5854 | TORONTO BUTTONVILLE A | 9 | 1 | 22 | 16.65 | 1.35 | 0
5855 | TORONTO BUTTONVILLE A | 8 | 31 | 23 | 19.6 | 0 | 1.6
5855 | TORONTO BUTTONVILLE A | 9 | 1 | 23 | 16.35 | 1.65 | 0
5856 | TORONTO BUTTONVILLE A | 8 | 31 | 24 | 19.3 | 0 | 1.3
5856 | TORONTO BUTTONVILLE A | 9 | 1 | 24 | 16.225 | 1.775 | 0
5857 | TORONTO BUTTONVILLE A | 9 | 1 | 1 | 19.1 | 0 | 1.1
5857 | TORONTO BUTTONVILLE A | 9 | 2 | 1 | 15.8 | 2.2 | 0
5858 | TORONTO BUTTONVILLE A | 9 | 1 | 2 | 19.4 | 0 | 1.4
5858 | TORONTO BUTTONVILLE A | 9 | 2 | 2 | 15.575 | 2.425 | 0
5859 | TORONTO BUTTONVILLE A | 9 | 1 | 3 | 19.6 | 0 | 1.6
5859 | TORONTO BUTTONVILLE A | 9 | 2 | 3 | 15.3 | 2.7 | 0
5860 | TORONTO BUTTONVILLE A | 9 | 1 | 4 | 19.4 | 0 | 1.4
5860 | TORONTO BUTTONVILLE A | 9 | 2 | 4 | 14.725 | 3.275 | 0
5861 | TORONTO BUTTONVILLE A | 9 | 1 | 5 | 19.7 | 0 | 1.7
5861 | TORONTO BUTTONVILLE A | 9 | 2 | 5 | 13.95 | 4.05 | 0
5862 | TORONTO BUTTONVILLE A | 9 | 1 | 6 | 19.4 | 0 | 1.4
5862 | TORONTO BUTTONVILLE A | 9 | 2 | 6 | 13.775 | 4.225 | 0
5863 | TORONTO BUTTONVILLE A | 9 | 1 | 7 | 19.5 | 0 | 1.5
5863 | TORONTO BUTTONVILLE A | 9 | 2 | 7 | 14.175 | 3.825 | 0
5864 | TORONTO BUTTONVILLE A | 9 | 1 | 8 | 20.1 | 0 | 2.1
5864 | TORONTO BUTTONVILLE A | 9 | 2 | 8 | 15.475 | 2.525 | 0
5865 | TORONTO BUTTONVILLE A | 9 | 1 | 9 | 21.5 | 0 | 3.5
5865 | TORONTO BUTTONVILLE A | 9 | 2 | 9 | 17.25 | 0.75 | 0
5866 | TORONTO BUTTONVILLE A | 9 | 1 | 10 | 23.4 | 0 | 5.4
5866 | TORONTO BUTTONVILLE A | 9 | 2 | 10 | 19.175 | 0 | 1.175
5867 | TORONTO BUTTONVILLE A | 9 | 1 | 11 | 23.7 | 0 | 5.7
5867 | TORONTO BUTTONVILLE A | 9 | 2 | 11 | 20.4 | 0 | 2.4
5868 | TORONTO BUTTONVILLE A | 9 | 1 | 12 | 25.3 | 0 | 7.3
5868 | TORONTO BUTTONVILLE A | 9 | 2 | 12 | 21.025 | 0 | 3.025
5869 | TORONTO BUTTONVILLE A | 9 | 1 | 13 | 26 | 0 | 8
5869 | TORONTO BUTTONVILLE A | 9 | 2 | 13 | 21.4 | 0 | 3.4
5870 | TORONTO BUTTONVILLE A | 9 | 1 | 14 | 27 | 0 | 9
5870 | TORONTO BUTTONVILLE A | 9 | 2 | 14 | 21.725 | 0 | 3.725
5871 | TORONTO BUTTONVILLE A | 9 | 1 | 15 | 26.7 | 0 | 8.7
5871 | TORONTO BUTTONVILLE A | 9 | 2 | 15 | 22.15 | 0 | 4.15
5872 | TORONTO BUTTONVILLE A | 9 | 1 | 16 | 27.2 | 0 | 9.2
5872 | TORONTO BUTTONVILLE A | 9 | 2 | 16 | 22.1 | 0 | 4.1
5873 | TORONTO BUTTONVILLE A | 9 | 1 | 17 | 26 | 0 | 8
5873 | TORONTO BUTTONVILLE A | 9 | 2 | 17 | 21.225 | 0 | 3.225
5874 | TORONTO BUTTONVILLE A | 9 | 1 | 18 | 24.3 | 0 | 6.3
5874 | TORONTO BUTTONVILLE A | 9 | 2 | 18 | 20.675 | 0 | 2.675
5875 | TORONTO BUTTONVILLE A | 9 | 1 | 19 | 23 | 0 | 5
5875 | TORONTO BUTTONVILLE A | 9 | 2 | 19 | 20.25 | 0 | 2.25
5876 | TORONTO BUTTONVILLE A | 9 | 1 | 20 | 22.4 | 0 | 4.4
5876 | TORONTO BUTTONVILLE A | 9 | 2 | 20 | 19.275 | 0 | 1.275
5877 | TORONTO BUTTONVILLE A | 9 | 1 | 21 | 22 | 0 | 4
5877 | TORONTO BUTTONVILLE A | 9 | 2 | 21 | 19.125 | 0 | 1.125
5878 | TORONTO BUTTONVILLE A | 9 | 1 | 22 | 21.8 | 0 | 3.8
5878 | TORONTO BUTTONVILLE A | 9 | 2 | 22 | 18.65 | 0 | 0.65
5879 | TORONTO BUTTONVILLE A | 9 | 1 | 23 | 22.2 | 0 | 4.2
5879 | TORONTO BUTTONVILLE A | 9 | 2 | 23 | 18.225 | 0 | 0.225
5880 | TORONTO BUTTONVILLE A | 9 | 1 | 24 | 22.2 | 0 | 4.2
5880 | TORONTO BUTTONVILLE A | 9 | 2 | 24 | 17.95 | 0.05 | 0
5881 | TORONTO BUTTONVILLE A | 9 | 2 | 1 | 22.2 | 0 | 4.2
5881 | TORONTO BUTTONVILLE A | 9 | 3 | 1 | 17.45 | 0.55 | 0
5882 | TORONTO BUTTONVILLE A | 9 | 2 | 2 | 21.2 | 0 | 3.2
5882 | TORONTO BUTTONVILLE A | 9 | 3 | 2 | 17.075 | 0.925 | 0
5883 | TORONTO BUTTONVILLE A | 9 | 2 | 3 | 19.7 | 0 | 1.7
5883 | TORONTO BUTTONVILLE A | 9 | 3 | 3 | 16.25 | 1.75 | 0
5884 | TORONTO BUTTONVILLE A | 9 | 2 | 4 | 20.1 | 0 | 2.1
5884 | TORONTO BUTTONVILLE A | 9 | 3 | 4 | 15.475 | 2.525 | 0
5885 | TORONTO BUTTONVILLE A | 9 | 2 | 5 | 20.5 | 0 | 2.5
5885 | TORONTO BUTTONVILLE A | 9 | 3 | 5 | 15.075 | 2.925 | 0
5886 | TORONTO BUTTONVILLE A | 9 | 2 | 6 | 20.7 | 0 | 2.7
5886 | TORONTO BUTTONVILLE A | 9 | 3 | 6 | 15.25 | 2.75 | 0
5887 | TORONTO BUTTONVILLE A | 9 | 2 | 7 | 20.7 | 0 | 2.7
5887 | TORONTO BUTTONVILLE A | 9 | 3 | 7 | 15.275 | 2.725 | 0
5888 | TORONTO BUTTONVILLE A | 9 | 2 | 8 | 21.2 | 0 | 3.2
5888 | TORONTO BUTTONVILLE A | 9 | 3 | 8 | 16.55 | 1.45 | 0
5889 | TORONTO BUTTONVILLE A | 9 | 2 | 9 | 22.2 | 0 | 4.2
5889 | TORONTO BUTTONVILLE A | 9 | 3 | 9 | 17.825 | 0.175 | 0
5890 | TORONTO BUTTONVILLE A | 9 | 2 | 10 | 22.7 | 0 | 4.7
5890 | TORONTO BUTTONVILLE A | 9 | 3 | 10 | 19.15 | 0 | 1.15
5891 | TORONTO BUTTONVILLE A | 9 | 2 | 11 | 25.1 | 0 | 7.1
5891 | TORONTO BUTTONVILLE A | 9 | 3 | 11 | 20.175 | 0 | 2.175
5892 | TORONTO BUTTONVILLE A | 9 | 2 | 12 | 25.4 | 0 | 7.4
5892 | TORONTO BUTTONVILLE A | 9 | 3 | 12 | 22.025 | 0 | 4.025
5893 | TORONTO BUTTONVILLE A | 9 | 2 | 13 | 25.5 | 0 | 7.5
5893 | TORONTO BUTTONVILLE A | 9 | 3 | 13 | 22.275 | 0 | 4.275
5894 | TORONTO BUTTONVILLE A | 9 | 2 | 14 | 27.1 | 0 | 9.1
5894 | TORONTO BUTTONVILLE A | 9 | 3 | 14 | 22.85 | 0 | 4.85
5895 | TORONTO BUTTONVILLE A | 9 | 2 | 15 | 26.8 | 0 | 8.8
5895 | TORONTO BUTTONVILLE A | 9 | 3 | 15 | 23.5 | 0 | 5.5
5896 | TORONTO BUTTONVILLE A | 9 | 2 | 16 | 24.9 | 0 | 6.9
5896 | TORONTO BUTTONVILLE A | 9 | 3 | 16 | 22.4 | 0 | 4.4
5897 | TORONTO BUTTONVILLE A | 9 | 2 | 17 | 25.7 | 0 | 7.7
5897 | TORONTO BUTTONVILLE A | 9 | 3 | 17 | 21.85 | 0 | 3.85
5898 | TORONTO BUTTONVILLE A | 9 | 2 | 18 | 25.3 | 0 | 7.3
5898 | TORONTO BUTTONVILLE A | 9 | 3 | 18 | 21.875 | 0 | 3.875
5899 | TORONTO BUTTONVILLE A | 9 | 2 | 19 | 24.7 | 0 | 6.7
5899 | TORONTO BUTTONVILLE A | 9 | 3 | 19 | 20.975 | 0 | 2.975
5900 | TORONTO BUTTONVILLE A | 9 | 2 | 20 | 23.1 | 0 | 5.1
5900 | TORONTO BUTTONVILLE A | 9 | 3 | 20 | 19.95 | 0 | 1.95
5901 | TORONTO BUTTONVILLE A | 9 | 2 | 21 | 22.1 | 0 | 4.1
5901 | TORONTO BUTTONVILLE A | 9 | 3 | 21 | 19.3 | 0 | 1.3
5902 | TORONTO BUTTONVILLE A | 9 | 2 | 22 | 21.1 | 0 | 3.1
5902 | TORONTO BUTTONVILLE A | 9 | 3 | 22 | 18.675 | 0 | 0.675
5903 | TORONTO BUTTONVILLE A | 9 | 2 | 23 | 20 | 0 | 2
5903 | TORONTO BUTTONVILLE A | 9 | 3 | 23 | 18.325 | 0 | 0.325
5904 | TORONTO BUTTONVILLE A | 9 | 2 | 24 | 19.1 | 0 | 1.1
5904 | TORONTO BUTTONVILLE A | 9 | 3 | 24 | 17.925 | 0.075 | 0
5905 | TORONTO BUTTONVILLE A | 9 | 3 | 1 | 17.1 | 0.9 | 0
5905 | TORONTO BUTTONVILLE A | 9 | 4 | 1 | 17.625 | 0.375 | 0
5906 | TORONTO BUTTONVILLE A | 9 | 3 | 2 | 16.5 | 1.5 | 0
5906 | TORONTO BUTTONVILLE A | 9 | 4 | 2 | 17.15 | 0.85 | 0
5907 | TORONTO BUTTONVILLE A | 9 | 3 | 3 | 16 | 2 | 0
5907 | TORONTO BUTTONVILLE A | 9 | 4 | 3 | 16.925 | 1.075 | 0
5908 | TORONTO BUTTONVILLE A | 9 | 3 | 4 | 15 | 3 | 0
5908 | TORONTO BUTTONVILLE A | 9 | 4 | 4 | 17.05 | 0.95 | 0
5909 | TORONTO BUTTONVILLE A | 9 | 3 | 5 | 14.5 | 3.5 | 0
5909 | TORONTO BUTTONVILLE A | 9 | 4 | 5 | 16.45 | 1.55 | 0
5910 | TORONTO BUTTONVILLE A | 9 | 3 | 6 | 13.4 | 4.6 | 0
5910 | TORONTO BUTTONVILLE A | 9 | 4 | 6 | 15.775 | 2.225 | 0
5911 | TORONTO BUTTONVILLE A | 9 | 3 | 7 | 13.9 | 4.1 | 0
5911 | TORONTO BUTTONVILLE A | 9 | 4 | 7 | 15.4 | 2.6 | 0
5912 | TORONTO BUTTONVILLE A | 9 | 3 | 8 | 15.7 | 2.3 | 0
5912 | TORONTO BUTTONVILLE A | 9 | 4 | 8 | 17.025 | 0.975 | 0
5913 | TORONTO BUTTONVILLE A | 9 | 3 | 9 | 17.4 | 0.6 | 0
5913 | TORONTO BUTTONVILLE A | 9 | 4 | 9 | 18.525 | 0 | 0.525
5914 | TORONTO BUTTONVILLE A | 9 | 3 | 10 | 21.4 | 0 | 3.4
5914 | TORONTO BUTTONVILLE A | 9 | 4 | 10 | 19.85 | 0 | 1.85
5915 | TORONTO BUTTONVILLE A | 9 | 3 | 11 | 22.9 | 0 | 4.9
5915 | TORONTO BUTTONVILLE A | 9 | 4 | 11 | 20.875 | 0 | 2.875
5916 | TORONTO BUTTONVILLE A | 9 | 3 | 12 | 23.8 | 0 | 5.8
5916 | TORONTO BUTTONVILLE A | 9 | 4 | 12 | 22.325 | 0 | 4.325
5917 | TORONTO BUTTONVILLE A | 9 | 3 | 13 | 24.5 | 0 | 6.5
5917 | TORONTO BUTTONVILLE A | 9 | 4 | 13 | 23.475 | 0 | 5.475
5918 | TORONTO BUTTONVILLE A | 9 | 3 | 14 | 25.6 | 0 | 7.6
5918 | TORONTO BUTTONVILLE A | 9 | 4 | 14 | 23.4 | 0 | 5.4
5919 | TORONTO BUTTONVILLE A | 9 | 3 | 15 | 26.5 | 0 | 8.5
5919 | TORONTO BUTTONVILLE A | 9 | 4 | 15 | 24.225 | 0 | 6.225
5920 | TORONTO BUTTONVILLE A | 9 | 3 | 16 | 26.1 | 0 | 8.1
5920 | TORONTO BUTTONVILLE A | 9 | 4 | 16 | 24.125 | 0 | 6.125
5921 | TORONTO BUTTONVILLE A | 9 | 3 | 17 | 27.8 | 0 | 9.8
5921 | TORONTO BUTTONVILLE A | 9 | 4 | 17 | 24.2 | 0 | 6.2
5922 | TORONTO BUTTONVILLE A | 9 | 3 | 18 | 27 | 0 | 9
5922 | TORONTO BUTTONVILLE A | 9 | 4 | 18 | 23.5 | 0 | 5.5
5923 | TORONTO BUTTONVILLE A | 9 | 3 | 19 | 26.2 | 0 | 8.2
5923 | TORONTO BUTTONVILLE A | 9 | 4 | 19 | 21.375 | 0 | 3.375
5924 | TORONTO BUTTONVILLE A | 9 | 3 | 20 | 25.2 | 0 | 7.2
5924 | TORONTO BUTTONVILLE A | 9 | 4 | 20 | 20 | 0 | 2
5925 | TORONTO BUTTONVILLE A | 9 | 3 | 21 | 20.2 | 0 | 2.2
5925 | TORONTO BUTTONVILLE A | 9 | 4 | 21 | 19.5 | 0 | 1.5
5926 | TORONTO BUTTONVILLE A | 9 | 3 | 22 | 19.1 | 0 | 1.1
5926 | TORONTO BUTTONVILLE A | 9 | 4 | 22 | 19.375 | 0 | 1.375
5927 | TORONTO BUTTONVILLE A | 9 | 3 | 23 | 18 | 0 | 0
5927 | TORONTO BUTTONVILLE A | 9 | 4 | 23 | 18.375 | 0 | 0.375
5928 | TORONTO BUTTONVILLE A | 9 | 3 | 24 | 16.4 | 1.6 | 0
5928 | TORONTO BUTTONVILLE A | 9 | 4 | 24 | 17.425 | 0.575 | 0
5929 | TORONTO BUTTONVILLE A | 9 | 4 | 1 | 15.7 | 2.3 | 0
5929 | TORONTO BUTTONVILLE A | 9 | 5 | 1 | 16.425 | 1.575 | 0
5930 | TORONTO BUTTONVILLE A | 9 | 4 | 2 | 14.9 | 3.1 | 0
5930 | TORONTO BUTTONVILLE A | 9 | 5 | 2 | 16.025 | 1.975 | 0
5931 | TORONTO BUTTONVILLE A | 9 | 4 | 3 | 14.2 | 3.8 | 0
5931 | TORONTO BUTTONVILLE A | 9 | 5 | 3 | 16.025 | 1.975 | 0
5932 | TORONTO BUTTONVILLE A | 9 | 4 | 4 | 13.4 | 4.6 | 0
5932 | TORONTO BUTTONVILLE A | 9 | 5 | 4 | 15.525 | 2.475 | 0
5933 | TORONTO BUTTONVILLE A | 9 | 4 | 5 | 13.6 | 4.4 | 0
5933 | TORONTO BUTTONVILLE A | 9 | 5 | 5 | 15.4 | 2.6 | 0
5934 | TORONTO BUTTONVILLE A | 9 | 4 | 6 | 13.7 | 4.3 | 0
5934 | TORONTO BUTTONVILLE A | 9 | 5 | 6 | 15.1 | 2.9 | 0
5935 | TORONTO BUTTONVILLE A | 9 | 4 | 7 | 13.5 | 4.5 | 0
5935 | TORONTO BUTTONVILLE A | 9 | 5 | 7 | 14.825 | 3.175 | 0
5936 | TORONTO BUTTONVILLE A | 9 | 4 | 8 | 15.2 | 2.8 | 0
5936 | TORONTO BUTTONVILLE A | 9 | 5 | 8 | 16.525 | 1.475 | 0
5937 | TORONTO BUTTONVILLE A | 9 | 4 | 9 | 16.7 | 1.3 | 0
5937 | TORONTO BUTTONVILLE A | 9 | 5 | 9 | 18.975 | 0 | 0.975
5938 | TORONTO BUTTONVILLE A | 9 | 4 | 10 | 18 | 0 | 0
5938 | TORONTO BUTTONVILLE A | 9 | 5 | 10 | 20.925 | 0 | 2.925
5939 | TORONTO BUTTONVILLE A | 9 | 4 | 11 | 18.7 | 0 | 0.7
5939 | TORONTO BUTTONVILLE A | 9 | 5 | 11 | 22.075 | 0 | 4.075
5940 | TORONTO BUTTONVILLE A | 9 | 4 | 12 | 19.4 | 0 | 1.4
5940 | TORONTO BUTTONVILLE A | 9 | 5 | 12 | 23.6 | 0 | 5.6
5941 | TORONTO BUTTONVILLE A | 9 | 4 | 13 | 20.1 | 0 | 2.1
5941 | TORONTO BUTTONVILLE A | 9 | 5 | 13 | 23.65 | 0 | 5.65
5942 | TORONTO BUTTONVILLE A | 9 | 4 | 14 | 21.2 | 0 | 3.2
5942 | TORONTO BUTTONVILLE A | 9 | 5 | 14 | 21.575 | 0 | 3.575
5943 | TORONTO BUTTONVILLE A | 9 | 4 | 15 | 21.5 | 0 | 3.5
5943 | TORONTO BUTTONVILLE A | 9 | 5 | 15 | 23.675 | 0 | 5.675
5944 | TORONTO BUTTONVILLE A | 9 | 4 | 16 | 20.6 | 0 | 2.6
5944 | TORONTO BUTTONVILLE A | 9 | 5 | 16 | 24.725 | 0 | 6.725
5945 | TORONTO BUTTONVILLE A | 9 | 4 | 17 | 19.7 | 0 | 1.7
5945 | TORONTO BUTTONVILLE A | 9 | 5 | 17 | 24.2 | 0 | 6.2
5946 | TORONTO BUTTONVILLE A | 9 | 4 | 18 | 20.4 | 0 | 2.4
5946 | TORONTO BUTTONVILLE A | 9 | 5 | 18 | 24.05 | 0 | 6.05
5947 | TORONTO BUTTONVILLE A | 9 | 4 | 19 | 18.6 | 0 | 0.6
5947 | TORONTO BUTTONVILLE A | 9 | 5 | 19 | 22.8 | 0 | 4.8
5948 | TORONTO BUTTONVILLE A | 9 | 4 | 20 | 17.4 | 0.6 | 0
5948 | TORONTO BUTTONVILLE A | 9 | 5 | 20 | 21.375 | 0 | 3.375
5949 | TORONTO BUTTONVILLE A | 9 | 4 | 21 | 16.7 | 1.3 | 0
5949 | TORONTO BUTTONVILLE A | 9 | 5 | 21 | 20.8 | 0 | 2.8
5950 | TORONTO BUTTONVILLE A | 9 | 4 | 22 | 16.3 | 1.7 | 0
5950 | TORONTO BUTTONVILLE A | 9 | 5 | 22 | 19.6 | 0 | 1.6
5951 | TORONTO BUTTONVILLE A | 9 | 4 | 23 | 15.5 | 2.5 | 0
5951 | TORONTO BUTTONVILLE A | 9 | 5 | 23 | 18.7 | 0 | 0.7
5952 | TORONTO BUTTONVILLE A | 9 | 4 | 24 | 14.5 | 3.5 | 0
5952 | TORONTO BUTTONVILLE A | 9 | 5 | 24 | 17.725 | 0.275 | 0
5953 | TORONTO BUTTONVILLE A | 9 | 5 | 1 | 13.9 | 4.1 | 0
5953 | TORONTO BUTTONVILLE A | 9 | 6 | 1 | 16.95 | 1.05 | 0
5954 | TORONTO BUTTONVILLE A | 9 | 5 | 2 | 13.2 | 4.8 | 0
5954 | TORONTO BUTTONVILLE A | 9 | 6 | 2 | 16.4 | 1.6 | 0
5955 | TORONTO BUTTONVILLE A | 9 | 5 | 3 | 13.4 | 4.6 | 0
5955 | TORONTO BUTTONVILLE A | 9 | 6 | 3 | 15.375 | 2.625 | 0
5956 | TORONTO BUTTONVILLE A | 9 | 5 | 4 | 13.3 | 4.7 | 0
5956 | TORONTO BUTTONVILLE A | 9 | 6 | 4 | 15 | 3 | 0
5957 | TORONTO BUTTONVILLE A | 9 | 5 | 5 | 12.3 | 5.7 | 0
5957 | TORONTO BUTTONVILLE A | 9 | 6 | 5 | 14.625 | 3.375 | 0
5958 | TORONTO BUTTONVILLE A | 9 | 5 | 6 | 12.1 | 5.9 | 0
5958 | TORONTO BUTTONVILLE A | 9 | 6 | 6 | 14.5 | 3.5 | 0
5959 | TORONTO BUTTONVILLE A | 9 | 5 | 7 | 12.1 | 5.9 | 0
5959 | TORONTO BUTTONVILLE A | 9 | 6 | 7 | 14.2 | 3.8 | 0
5960 | TORONTO BUTTONVILLE A | 9 | 5 | 8 | 13.4 | 4.6 | 0
5960 | TORONTO BUTTONVILLE A | 9 | 6 | 8 | 14.875 | 3.125 | 0
5961 | TORONTO BUTTONVILLE A | 9 | 5 | 9 | 16.7 | 1.3 | 0
5961 | TORONTO BUTTONVILLE A | 9 | 6 | 9 | 16.725 | 1.275 | 0
5962 | TORONTO BUTTONVILLE A | 9 | 5 | 10 | 18.5 | 0 | 0.5
5962 | TORONTO BUTTONVILLE A | 9 | 6 | 10 | 18.4 | 0 | 0.4
5963 | TORONTO BUTTONVILLE A | 9 | 5 | 11 | 20.1 | 0 | 2.1
5963 | TORONTO BUTTONVILLE A | 9 | 6 | 11 | 19.575 | 0 | 1.575
5964 | TORONTO BUTTONVILLE A | 9 | 5 | 12 | 20.4 | 0 | 2.4
5964 | TORONTO BUTTONVILLE A | 9 | 6 | 12 | 20.475 | 0 | 2.475
5965 | TORONTO BUTTONVILLE A | 9 | 5 | 13 | 19.9 | 0 | 1.9
5965 | TORONTO BUTTONVILLE A | 9 | 6 | 13 | 20.7 | 0 | 2.7
5966 | TORONTO BUTTONVILLE A | 9 | 5 | 14 | 20.3 | 0 | 2.3
5966 | TORONTO BUTTONVILLE A | 9 | 6 | 14 | 20.375 | 0 | 2.375
5967 | TORONTO BUTTONVILLE A | 9 | 5 | 15 | 19.9 | 0 | 1.9
5967 | TORONTO BUTTONVILLE A | 9 | 6 | 15 | 20.7 | 0 | 2.7
5968 | TORONTO BUTTONVILLE A | 9 | 5 | 16 | 20.2 | 0 | 2.2
5968 | TORONTO BUTTONVILLE A | 9 | 6 | 16 | 20.325 | 0 | 2.325
5969 | TORONTO BUTTONVILLE A | 9 | 5 | 17 | 19.6 | 0 | 1.6
5969 | TORONTO BUTTONVILLE A | 9 | 6 | 17 | 20.2 | 0 | 2.2
5970 | TORONTO BUTTONVILLE A | 9 | 5 | 18 | 19.4 | 0 | 1.4
5970 | TORONTO BUTTONVILLE A | 9 | 6 | 18 | 19.425 | 0 | 1.425
5971 | TORONTO BUTTONVILLE A | 9 | 5 | 19 | 18.5 | 0 | 0.5
5971 | TORONTO BUTTONVILLE A | 9 | 6 | 19 | 18.575 | 0 | 0.575
5972 | TORONTO BUTTONVILLE A | 9 | 5 | 20 | 17.5 | 0.5 | 0
5972 | TORONTO BUTTONVILLE A | 9 | 6 | 20 | 17.125 | 0.875 | 0
5973 | TORONTO BUTTONVILLE A | 9 | 5 | 21 | 16.4 | 1.6 | 0
5973 | TORONTO BUTTONVILLE A | 9 | 6 | 21 | 16.25 | 1.75 | 0
5974 | TORONTO BUTTONVILLE A | 9 | 5 | 22 | 15.6 | 2.4 | 0
5974 | TORONTO BUTTONVILLE A | 9 | 6 | 22 | 15.475 | 2.525 | 0
5975 | TORONTO BUTTONVILLE A | 9 | 5 | 23 | 14.6 | 3.4 | 0
5975 | TORONTO BUTTONVILLE A | 9 | 6 | 23 | 14.85 | 3.15 | 0
5976 | TORONTO BUTTONVILLE A | 9 | 5 | 24 | 14.4 | 3.6 | 0
5976 | TORONTO BUTTONVILLE A | 9 | 6 | 24 | 14.025 | 3.975 | 0
5977 | TORONTO BUTTONVILLE A | 9 | 6 | 1 | 13 | 5 | 0
5977 | TORONTO BUTTONVILLE A | 9 | 7 | 1 | 14.05 | 3.95 | 0
5978 | TORONTO BUTTONVILLE A | 9 | 6 | 2 | 12.6 | 5.4 | 0
5978 | TORONTO BUTTONVILLE A | 9 | 7 | 2 | 13.625 | 4.375 | 0
5979 | TORONTO BUTTONVILLE A | 9 | 6 | 3 | 11.9 | 6.1 | 0
5979 | TORONTO BUTTONVILLE A | 9 | 7 | 3 | 13.7 | 4.3 | 0
5980 | TORONTO BUTTONVILLE A | 9 | 6 | 4 | 11.2 | 6.8 | 0
5980 | TORONTO BUTTONVILLE A | 9 | 7 | 4 | 12.65 | 5.35 | 0
5981 | TORONTO BUTTONVILLE A | 9 | 6 | 5 | 10 | 8 | 0
5981 | TORONTO BUTTONVILLE A | 9 | 7 | 5 | 12.275 | 5.725 | 0
5982 | TORONTO BUTTONVILLE A | 9 | 6 | 6 | 9.5 | 8.5 | 0
5982 | TORONTO BUTTONVILLE A | 9 | 7 | 6 | 12.65 | 5.35 | 0
5983 | TORONTO BUTTONVILLE A | 9 | 6 | 7 | 8.2 | 9.8 | 0
5983 | TORONTO BUTTONVILLE A | 9 | 7 | 7 | 12.525 | 5.475 | 0
5984 | TORONTO BUTTONVILLE A | 9 | 6 | 8 | 11.3 | 6.7 | 0
5984 | TORONTO BUTTONVILLE A | 9 | 7 | 8 | 14.05 | 3.95 | 0
5985 | TORONTO BUTTONVILLE A | 9 | 6 | 9 | 15.3 | 2.7 | 0
5985 | TORONTO BUTTONVILLE A | 9 | 7 | 9 | 16.1 | 1.9 | 0
5986 | TORONTO BUTTONVILLE A | 9 | 6 | 10 | 16.8 | 1.2 | 0
5986 | TORONTO BUTTONVILLE A | 9 | 7 | 10 | 18.3 | 0 | 0.3
5987 | TORONTO BUTTONVILLE A | 9 | 6 | 11 | 17.6 | 0.4 | 0
5987 | TORONTO BUTTONVILLE A | 9 | 7 | 11 | 19.225 | 0 | 1.225
5988 | TORONTO BUTTONVILLE A | 9 | 6 | 12 | 18.6 | 0 | 0.6
5988 | TORONTO BUTTONVILLE A | 9 | 7 | 12 | 19.675 | 0 | 1.675
5989 | TORONTO BUTTONVILLE A | 9 | 6 | 13 | 20.3 | 0 | 2.3
5989 | TORONTO BUTTONVILLE A | 9 | 7 | 13 | 20.45 | 0 | 2.45
5990 | TORONTO BUTTONVILLE A | 9 | 6 | 14 | 21.2 | 0 | 3.2
5990 | TORONTO BUTTONVILLE A | 9 | 7 | 14 | 20.825 | 0 | 2.825
5991 | TORONTO BUTTONVILLE A | 9 | 6 | 15 | 21.1 | 0 | 3.1
5991 | TORONTO BUTTONVILLE A | 9 | 7 | 15 | 20.875 | 0 | 2.875
5992 | TORONTO BUTTONVILLE A | 9 | 6 | 16 | 20.8 | 0 | 2.8
5992 | TORONTO BUTTONVILLE A | 9 | 7 | 16 | 20.875 | 0 | 2.875
5993 | TORONTO BUTTONVILLE A | 9 | 6 | 17 | 21.2 | 0 | 3.2
5993 | TORONTO BUTTONVILLE A | 9 | 7 | 17 | 20.35 | 0 | 2.35
5994 | TORONTO BUTTONVILLE A | 9 | 6 | 18 | 20.7 | 0 | 2.7
5994 | TORONTO BUTTONVILLE A | 9 | 7 | 18 | 19.875 | 0 | 1.875
5995 | TORONTO BUTTONVILLE A | 9 | 6 | 19 | 19.6 | 0 | 1.6
5995 | TORONTO BUTTONVILLE A | 9 | 7 | 19 | 16.475 | 1.525 | 0
5996 | TORONTO BUTTONVILLE A | 9 | 6 | 20 | 17.3 | 0.7 | 0
5996 | TORONTO BUTTONVILLE A | 9 | 7 | 20 | 16.075 | 1.925 | 0
5997 | TORONTO BUTTONVILLE A | 9 | 6 | 21 | 17.1 | 0.9 | 0
5997 | TORONTO BUTTONVILLE A | 9 | 7 | 21 | 15.425 | 2.575 | 0
5998 | TORONTO BUTTONVILLE A | 9 | 6 | 22 | 17.2 | 0.8 | 0
5998 | TORONTO BUTTONVILLE A | 9 | 7 | 22 | 14.925 | 3.075 | 0
5999 | TORONTO BUTTONVILLE A | 9 | 6 | 23 | 17.1 | 0.9 | 0
5999 | TORONTO BUTTONVILLE A | 9 | 7 | 23 | 14.5 | 3.5 | 0
6000 | TORONTO BUTTONVILLE A | 9 | 6 | 24 | 16.9 | 1.1 | 0
6000 | TORONTO BUTTONVILLE A | 9 | 7 | 24 | 14.125 | 3.875 | 0
6001 | TORONTO BUTTONVILLE A | 9 | 7 | 1 | 17.2 | 0.8 | 0
6001 | TORONTO BUTTONVILLE A | 9 | 8 | 1 | 14.15 | 3.85 | 0
6002 | TORONTO BUTTONVILLE A | 9 | 7 | 2 | 18.2 | 0 | 0.2
6002 | TORONTO BUTTONVILLE A | 9 | 8 | 2 | 13.8 | 4.2 | 0
6003 | TORONTO BUTTONVILLE A | 9 | 7 | 3 | 18.9 | 0 | 0.9
6003 | TORONTO BUTTONVILLE A | 9 | 8 | 3 | 13.125 | 4.875 | 0
6004 | TORONTO BUTTONVILLE A | 9 | 7 | 4 | 17.9 | 0.1 | 0
6004 | TORONTO BUTTONVILLE A | 9 | 8 | 4 | 13.15 | 4.85 | 0
6005 | TORONTO BUTTONVILLE A | 9 | 7 | 5 | 18.2 | 0 | 0.2
6005 | TORONTO BUTTONVILLE A | 9 | 8 | 5 | 12.925 | 5.075 | 0
6006 | TORONTO BUTTONVILLE A | 9 | 7 | 6 | 18.6 | 0 | 0.6
6006 | TORONTO BUTTONVILLE A | 9 | 8 | 6 | 12.425 | 5.575 | 0
6007 | TORONTO BUTTONVILLE A | 9 | 7 | 7 | 18.9 | 0 | 0.9
6007 | TORONTO BUTTONVILLE A | 9 | 8 | 7 | 12.275 | 5.725 | 0
6008 | TORONTO BUTTONVILLE A | 9 | 7 | 8 | 19.4 | 0 | 1.4
6008 | TORONTO BUTTONVILLE A | 9 | 8 | 8 | 12.95 | 5.05 | 0
6009 | TORONTO BUTTONVILLE A | 9 | 7 | 9 | 20.1 | 0 | 2.1
6009 | TORONTO BUTTONVILLE A | 9 | 8 | 9 | 14.325 | 3.675 | 0
6010 | TORONTO BUTTONVILLE A | 9 | 7 | 10 | 20.7 | 0 | 2.7
6010 | TORONTO BUTTONVILLE A | 9 | 8 | 10 | 15.475 | 2.525 | 0
6011 | TORONTO BUTTONVILLE A | 9 | 7 | 11 | 21.1 | 0 | 3.1
6011 | TORONTO BUTTONVILLE A | 9 | 8 | 11 | 16.55 | 1.45 | 0
6012 | TORONTO BUTTONVILLE A | 9 | 7 | 12 | 21.6 | 0 | 3.6
6012 | TORONTO BUTTONVILLE A | 9 | 8 | 12 | 17.15 | 0.85 | 0
6013 | TORONTO BUTTONVILLE A | 9 | 7 | 13 | 21.9 | 0 | 3.9
6013 | TORONTO BUTTONVILLE A | 9 | 8 | 13 | 17.45 | 0.55 | 0
6014 | TORONTO BUTTONVILLE A | 9 | 7 | 14 | 23.4 | 0 | 5.4
6014 | TORONTO BUTTONVILLE A | 9 | 8 | 14 | 18 | 0 | 0
6015 | TORONTO BUTTONVILLE A | 9 | 7 | 15 | 23.7 | 0 | 5.7
6015 | TORONTO BUTTONVILLE A | 9 | 8 | 15 | 18.6 | 0 | 0.6
6016 | TORONTO BUTTONVILLE A | 9 | 7 | 16 | 19.8 | 0 | 1.8
6016 | TORONTO BUTTONVILLE A | 9 | 8 | 16 | 18.625 | 0 | 0.625
6017 | TORONTO BUTTONVILLE A | 9 | 7 | 17 | 19 | 0 | 1
6017 | TORONTO BUTTONVILLE A | 9 | 8 | 17 | 18.075 | 0 | 0.075
6018 | TORONTO BUTTONVILLE A | 9 | 7 | 18 | 19 | 0 | 1
6018 | TORONTO BUTTONVILLE A | 9 | 8 | 18 | 17.4 | 0.6 | 0
6019 | TORONTO BUTTONVILLE A | 9 | 7 | 19 | 18.5 | 0 | 0.5
6019 | TORONTO BUTTONVILLE A | 9 | 8 | 19 | 16.3 | 1.7 | 0
6020 | TORONTO BUTTONVILLE A | 9 | 7 | 20 | 17.6 | 0.4 | 0
6020 | TORONTO BUTTONVILLE A | 9 | 8 | 20 | 14.85 | 3.15 | 0
6021 | TORONTO BUTTONVILLE A | 9 | 7 | 21 | 16.6 | 1.4 | 0
6021 | TORONTO BUTTONVILLE A | 9 | 8 | 21 | 13.8 | 4.2 | 0
6022 | TORONTO BUTTONVILLE A | 9 | 7 | 22 | 16.7 | 1.3 | 0
6022 | TORONTO BUTTONVILLE A | 9 | 8 | 22 | 13 | 5 | 0
6023 | TORONTO BUTTONVILLE A | 9 | 7 | 23 | 15.8 | 2.2 | 0
6023 | TORONTO BUTTONVILLE A | 9 | 8 | 23 | 12.675 | 5.325 | 0
6024 | TORONTO BUTTONVILLE A | 9 | 7 | 24 | 14.8 | 3.2 | 0
6024 | TORONTO BUTTONVILLE A | 9 | 8 | 24 | 12.125 | 5.875 | 0
6025 | TORONTO BUTTONVILLE A | 9 | 8 | 1 | 14.5 | 3.5 | 0
6025 | TORONTO BUTTONVILLE A | 9 | 9 | 1 | 11.325 | 6.675 | 0
6026 | TORONTO BUTTONVILLE A | 9 | 8 | 2 | 14.4 | 3.6 | 0
6026 | TORONTO BUTTONVILLE A | 9 | 9 | 2 | 10.9 | 7.1 | 0
6027 | TORONTO BUTTONVILLE A | 9 | 8 | 3 | 14.3 | 3.7 | 0
6027 | TORONTO BUTTONVILLE A | 9 | 9 | 3 | 10.25 | 7.75 | 0
6028 | TORONTO BUTTONVILLE A | 9 | 8 | 4 | 14.2 | 3.8 | 0
6028 | TORONTO BUTTONVILLE A | 9 | 9 | 4 | 9.625 | 8.375 | 0
6029 | TORONTO BUTTONVILLE A | 9 | 8 | 5 | 14.2 | 3.8 | 0
6029 | TORONTO BUTTONVILLE A | 9 | 9 | 5 | 9.375 | 8.625 | 0
6030 | TORONTO BUTTONVILLE A | 9 | 8 | 6 | 14.1 | 3.9 | 0
6030 | TORONTO BUTTONVILLE A | 9 | 9 | 6 | 9.425 | 8.575 | 0
6031 | TORONTO BUTTONVILLE A | 9 | 8 | 7 | 14.1 | 3.9 | 0
6031 | TORONTO BUTTONVILLE A | 9 | 9 | 7 | 9.4 | 8.6 | 0
6032 | TORONTO BUTTONVILLE A | 9 | 8 | 8 | 14.1 | 3.9 | 0
6032 | TORONTO BUTTONVILLE A | 9 | 9 | 8 | 10.65 | 7.35 | 0
6033 | TORONTO BUTTONVILLE A | 9 | 8 | 9 | 14 | 4 | 0
6033 | TORONTO BUTTONVILLE A | 9 | 9 | 9 | 12.175 | 5.825 | 0
6034 | TORONTO BUTTONVILLE A | 9 | 8 | 10 | 13.8 | 4.2 | 0
6034 | TORONTO BUTTONVILLE A | 9 | 9 | 10 | 13.725 | 4.275 | 0
6035 | TORONTO BUTTONVILLE A | 9 | 8 | 11 | 14.1 | 3.9 | 0
6035 | TORONTO BUTTONVILLE A | 9 | 9 | 11 | 15.55 | 2.45 | 0
6036 | TORONTO BUTTONVILLE A | 9 | 8 | 12 | 13.9 | 4.1 | 0
6036 | TORONTO BUTTONVILLE A | 9 | 9 | 12 | 16.15 | 1.85 | 0
6037 | TORONTO BUTTONVILLE A | 9 | 8 | 13 | 14.8 | 3.2 | 0
6037 | TORONTO BUTTONVILLE A | 9 | 9 | 13 | 16.6 | 1.4 | 0
6038 | TORONTO BUTTONVILLE A | 9 | 8 | 14 | 14.9 | 3.1 | 0
6038 | TORONTO BUTTONVILLE A | 9 | 9 | 14 | 17.325 | 0.675 | 0
6039 | TORONTO BUTTONVILLE A | 9 | 8 | 15 | 14.9 | 3.1 | 0
6039 | TORONTO BUTTONVILLE A | 9 | 9 | 15 | 17.525 | 0.475 | 0
6040 | TORONTO BUTTONVILLE A | 9 | 8 | 16 | 15 | 3 | 0
6040 | TORONTO BUTTONVILLE A | 9 | 9 | 16 | 17.725 | 0.275 | 0
6041 | TORONTO BUTTONVILLE A | 9 | 8 | 17 | 14.7 | 3.3 | 0
6041 | TORONTO BUTTONVILLE A | 9 | 9 | 17 | 17.35 | 0.65 | 0
6042 | TORONTO BUTTONVILLE A | 9 | 8 | 18 | 14.6 | 3.4 | 0
6042 | TORONTO BUTTONVILLE A | 9 | 9 | 18 | 16.625 | 1.375 | 0
6043 | TORONTO BUTTONVILLE A | 9 | 8 | 19 | 14.5 | 3.5 | 0
6043 | TORONTO BUTTONVILLE A | 9 | 9 | 19 | 15.85 | 2.15 | 0
6044 | TORONTO BUTTONVILLE A | 9 | 8 | 20 | 14.2 | 3.8 | 0
6044 | TORONTO BUTTONVILLE A | 9 | 9 | 20 | 14.325 | 3.675 | 0
6045 | TORONTO BUTTONVILLE A | 9 | 8 | 21 | 14.3 | 3.7 | 0
6045 | TORONTO BUTTONVILLE A | 9 | 9 | 21 | 13.35 | 4.65 | 0
6046 | TORONTO BUTTONVILLE A | 9 | 8 | 22 | 14.5 | 3.5 | 0
6046 | TORONTO BUTTONVILLE A | 9 | 9 | 22 | 12.675 | 5.325 | 0
6047 | TORONTO BUTTONVILLE A | 9 | 8 | 23 | 14.3 | 3.7 | 0
6047 | TORONTO BUTTONVILLE A | 9 | 9 | 23 | 11.975 | 6.025 | 0
6048 | TORONTO BUTTONVILLE A | 9 | 8 | 24 | 14.1 | 3.9 | 0
6048 | TORONTO BUTTONVILLE A | 9 | 9 | 24 | 11.525 | 6.475 | 0
6049 | TORONTO BUTTONVILLE A | 9 | 9 | 1 | 14.2 | 3.8 | 0
6049 | TORONTO BUTTONVILLE A | 9 | 10 | 1 | 11.525 | 6.475 | 0
6050 | TORONTO BUTTONVILLE A | 9 | 9 | 2 | 14.2 | 3.8 | 0
6050 | TORONTO BUTTONVILLE A | 9 | 10 | 2 | 11.475 | 6.525 | 0
6051 | TORONTO BUTTONVILLE A | 9 | 9 | 3 | 14.1 | 3.9 | 0
6051 | TORONTO BUTTONVILLE A | 9 | 10 | 3 | 11.125 | 6.875 | 0
6052 | TORONTO BUTTONVILLE A | 9 | 9 | 4 | 13.9 | 4.1 | 0
6052 | TORONTO BUTTONVILLE A | 9 | 10 | 4 | 10.85 | 7.15 | 0
6053 | TORONTO BUTTONVILLE A | 9 | 9 | 5 | 13.9 | 4.1 | 0
6053 | TORONTO BUTTONVILLE A | 9 | 10 | 5 | 10.85 | 7.15 | 0
6054 | TORONTO BUTTONVILLE A | 9 | 9 | 6 | 13.6 | 4.4 | 0
6054 | TORONTO BUTTONVILLE A | 9 | 10 | 6 | 11.2 | 6.8 | 0
6055 | TORONTO BUTTONVILLE A | 9 | 9 | 7 | 13.6 | 4.4 | 0
6055 | TORONTO BUTTONVILLE A | 9 | 10 | 7 | 11.05 | 6.95 | 0
6056 | TORONTO BUTTONVILLE A | 9 | 9 | 8 | 13.4 | 4.6 | 0
6056 | TORONTO BUTTONVILLE A | 9 | 10 | 8 | 12.3 | 5.7 | 0
6057 | TORONTO BUTTONVILLE A | 9 | 9 | 9 | 14 | 4 | 0
6057 | TORONTO BUTTONVILLE A | 9 | 10 | 9 | 14.55 | 3.45 | 0
6058 | TORONTO BUTTONVILLE A | 9 | 9 | 10 | 14.4 | 3.6 | 0
6058 | TORONTO BUTTONVILLE A | 9 | 10 | 10 | 16.075 | 1.925 | 0
6059 | TORONTO BUTTONVILLE A | 9 | 9 | 11 | 15 | 3 | 0
6059 | TORONTO BUTTONVILLE A | 9 | 10 | 11 | 16.925 | 1.075 | 0
6060 | TORONTO BUTTONVILLE A | 9 | 9 | 12 | 15.8 | 2.2 | 0
6060 | TORONTO BUTTONVILLE A | 9 | 10 | 12 | 17.725 | 0.275 | 0
6061 | TORONTO BUTTONVILLE A | 9 | 9 | 13 | 16.2 | 1.8 | 0
6061 | TORONTO BUTTONVILLE A | 9 | 10 | 13 | 17.3 | 0.7 | 0
6062 | TORONTO BUTTONVILLE A | 9 | 9 | 14 | 16.4 | 1.6 | 0
6062 | TORONTO BUTTONVILLE A | 9 | 10 | 14 | 18 | 0 | 0
6063 | TORONTO BUTTONVILLE A | 9 | 9 | 15 | 16.6 | 1.4 | 0
6063 | TORONTO BUTTONVILLE A | 9 | 10 | 15 | 18.475 | 0 | 0.475
6064 | TORONTO BUTTONVILLE A | 9 | 9 | 16 | 17.1 | 0.9 | 0
6064 | TORONTO BUTTONVILLE A | 9 | 10 | 16 | 18.675 | 0 | 0.675
6065 | TORONTO BUTTONVILLE A | 9 | 9 | 17 | 17.5 | 0.5 | 0
6065 | TORONTO BUTTONVILLE A | 9 | 10 | 17 | 18.4 | 0 | 0.4
6066 | TORONTO BUTTONVILLE A | 9 | 9 | 18 | 17.5 | 0.5 | 0
6066 | TORONTO BUTTONVILLE A | 9 | 10 | 18 | 17.875 | 0.125 | 0
6067 | TORONTO BUTTONVILLE A | 9 | 9 | 19 | 17.4 | 0.6 | 0
6067 | TORONTO BUTTONVILLE A | 9 | 10 | 19 | 16.95 | 1.05 | 0
6068 | TORONTO BUTTONVILLE A | 9 | 9 | 20 | 17.1 | 0.9 | 0
6068 | TORONTO BUTTONVILLE A | 9 | 10 | 20 | 15.875 | 2.125 | 0
6069 | TORONTO BUTTONVILLE A | 9 | 9 | 21 | 16.6 | 1.4 | 0
6069 | TORONTO BUTTONVILLE A | 9 | 10 | 21 | 15.9 | 2.1 | 0
6070 | TORONTO BUTTONVILLE A | 9 | 9 | 22 | 16.4 | 1.6 | 0
6070 | TORONTO BUTTONVILLE A | 9 | 10 | 22 | 15.2 | 2.8 | 0
6071 | TORONTO BUTTONVILLE A | 9 | 9 | 23 | 16.4 | 1.6 | 0
6071 | TORONTO BUTTONVILLE A | 9 | 10 | 23 | 15.775 | 2.225 | 0
6072 | TORONTO BUTTONVILLE A | 9 | 9 | 24 | 16.2 | 1.8 | 0
6072 | TORONTO BUTTONVILLE A | 9 | 10 | 24 | 15.35 | 2.65 | 0
6073 | TORONTO BUTTONVILLE A | 9 | 10 | 1 | 16.1 | 1.9 | 0
6073 | TORONTO BUTTONVILLE A | 9 | 11 | 1 | 14.875 | 3.125 | 0
6074 | TORONTO BUTTONVILLE A | 9 | 10 | 2 | 16.1 | 1.9 | 0
6074 | TORONTO BUTTONVILLE A | 9 | 11 | 2 | 14.725 | 3.275 | 0
6075 | TORONTO BUTTONVILLE A | 9 | 10 | 3 | 16.1 | 1.9 | 0
6075 | TORONTO BUTTONVILLE A | 9 | 11 | 3 | 14.15 | 3.85 | 0
6076 | TORONTO BUTTONVILLE A | 9 | 10 | 4 | 16 | 2 | 0
6076 | TORONTO BUTTONVILLE A | 9 | 11 | 4 | 13.725 | 4.275 | 0
6077 | TORONTO BUTTONVILLE A | 9 | 10 | 5 | 16.1 | 1.9 | 0
6077 | TORONTO BUTTONVILLE A | 9 | 11 | 5 | 13.325 | 4.675 | 0
6078 | TORONTO BUTTONVILLE A | 9 | 10 | 6 | 16.4 | 1.6 | 0
6078 | TORONTO BUTTONVILLE A | 9 | 11 | 6 | 13.475 | 4.525 | 0
6079 | TORONTO BUTTONVILLE A | 9 | 10 | 7 | 16.5 | 1.5 | 0
6079 | TORONTO BUTTONVILLE A | 9 | 11 | 7 | 13.95 | 4.05 | 0
6080 | TORONTO BUTTONVILLE A | 9 | 10 | 8 | 17 | 1 | 0
6080 | TORONTO BUTTONVILLE A | 9 | 11 | 8 | 15.1 | 2.9 | 0
6081 | TORONTO BUTTONVILLE A | 9 | 10 | 9 | 15.2 | 2.8 | 0
6081 | TORONTO BUTTONVILLE A | 9 | 11 | 9 | 17.35 | 0.65 | 0
6082 | TORONTO BUTTONVILLE A | 9 | 10 | 10 | 16.5 | 1.5 | 0
6082 | TORONTO BUTTONVILLE A | 9 | 11 | 10 | 19.15 | 0 | 1.15
6083 | TORONTO BUTTONVILLE A | 9 | 10 | 11 | 17 | 1 | 0
6083 | TORONTO BUTTONVILLE A | 9 | 11 | 11 | 20.875 | 0 | 2.875
6084 | TORONTO BUTTONVILLE A | 9 | 10 | 12 | 17.4 | 0.6 | 0
6084 | TORONTO BUTTONVILLE A | 9 | 11 | 12 | 21.425 | 0 | 3.425
6085 | TORONTO BUTTONVILLE A | 9 | 10 | 13 | 18 | 0 | 0
6085 | TORONTO BUTTONVILLE A | 9 | 11 | 13 | 22.4 | 0 | 4.4
6086 | TORONTO BUTTONVILLE A | 9 | 10 | 14 | 18.1 | 0 | 0.1
6086 | TORONTO BUTTONVILLE A | 9 | 11 | 14 | 22.775 | 0 | 4.775
6087 | TORONTO BUTTONVILLE A | 9 | 10 | 15 | 17.9 | 0.1 | 0
6087 | TORONTO BUTTONVILLE A | 9 | 11 | 15 | 23.125 | 0 | 5.125
6088 | TORONTO BUTTONVILLE A | 9 | 10 | 16 | 17.5 | 0.5 | 0
6088 | TORONTO BUTTONVILLE A | 9 | 11 | 16 | 23.275 | 0 | 5.275
6089 | TORONTO BUTTONVILLE A | 9 | 10 | 17 | 16.4 | 1.6 | 0
6089 | TORONTO BUTTONVILLE A | 9 | 11 | 17 | 22.975 | 0 | 4.975
6090 | TORONTO BUTTONVILLE A | 9 | 10 | 18 | 15.7 | 2.3 | 0
6090 | TORONTO BUTTONVILLE A | 9 | 11 | 18 | 22.375 | 0 | 4.375
6091 | TORONTO BUTTONVILLE A | 9 | 10 | 19 | 14.5 | 3.5 | 0
6091 | TORONTO BUTTONVILLE A | 9 | 11 | 19 | 20.875 | 0 | 2.875
6092 | TORONTO BUTTONVILLE A | 9 | 10 | 20 | 13.9 | 4.1 | 0
6092 | TORONTO BUTTONVILLE A | 9 | 11 | 20 | 19.1 | 0 | 1.1
6093 | TORONTO BUTTONVILLE A | 9 | 10 | 21 | 13.5 | 4.5 | 0
6093 | TORONTO BUTTONVILLE A | 9 | 11 | 21 | 18.55 | 0 | 0.55
6094 | TORONTO BUTTONVILLE A | 9 | 10 | 22 | 13.4 | 4.6 | 0
6094 | TORONTO BUTTONVILLE A | 9 | 11 | 22 | 17.8 | 0.2 | 0
6095 | TORONTO BUTTONVILLE A | 9 | 10 | 23 | 12.6 | 5.4 | 0
6095 | TORONTO BUTTONVILLE A | 9 | 11 | 23 | 17.05 | 0.95 | 0
6096 | TORONTO BUTTONVILLE A | 9 | 10 | 24 | 12.8 | 5.2 | 0
6096 | TORONTO BUTTONVILLE A | 9 | 11 | 24 | 16.375 | 1.625 | 0
6097 | TORONTO BUTTONVILLE A | 9 | 11 | 1 | 13.1 | 4.9 | 0
6097 | TORONTO BUTTONVILLE A | 9 | 12 | 1 | 15.925 | 2.075 | 0
6098 | TORONTO BUTTONVILLE A | 9 | 11 | 2 | 12.8 | 5.2 | 0
6098 | TORONTO BUTTONVILLE A | 9 | 12 | 2 | 14.95 | 3.05 | 0
6099 | TORONTO BUTTONVILLE A | 9 | 11 | 3 | 12.4 | 5.6 | 0
6099 | TORONTO BUTTONVILLE A | 9 | 12 | 3 | 14.45 | 3.55 | 0
6100 | TORONTO BUTTONVILLE A | 9 | 11 | 4 | 12.1 | 5.9 | 0
6100 | TORONTO BUTTONVILLE A | 9 | 12 | 4 | 13.725 | 4.275 | 0
6101 | TORONTO BUTTONVILLE A | 9 | 11 | 5 | 11.9 | 6.1 | 0
6101 | TORONTO BUTTONVILLE A | 9 | 12 | 5 | 13.6 | 4.4 | 0
6102 | TORONTO BUTTONVILLE A | 9 | 11 | 6 | 11.7 | 6.3 | 0
6102 | TORONTO BUTTONVILLE A | 9 | 12 | 6 | 13.25 | 4.75 | 0
6103 | TORONTO BUTTONVILLE A | 9 | 11 | 7 | 11.5 | 6.5 | 0
6103 | TORONTO BUTTONVILLE A | 9 | 12 | 7 | 13.225 | 4.775 | 0
6104 | TORONTO BUTTONVILLE A | 9 | 11 | 8 | 11.5 | 6.5 | 0
6104 | TORONTO BUTTONVILLE A | 9 | 12 | 8 | 14.325 | 3.675 | 0
6105 | TORONTO BUTTONVILLE A | 9 | 11 | 9 | 11.7 | 6.3 | 0
6105 | TORONTO BUTTONVILLE A | 9 | 12 | 9 | 16.5 | 1.5 | 0
6106 | TORONTO BUTTONVILLE A | 9 | 11 | 10 | 12.3 | 5.7 | 0
6106 | TORONTO BUTTONVILLE A | 9 | 12 | 10 | 17.95 | 0.05 | 0
6107 | TORONTO BUTTONVILLE A | 9 | 11 | 11 | 13.3 | 4.7 | 0
6107 | TORONTO BUTTONVILLE A | 9 | 12 | 11 | 19.375 | 0 | 1.375
6108 | TORONTO BUTTONVILLE A | 9 | 11 | 12 | 14.7 | 3.3 | 0
6108 | TORONTO BUTTONVILLE A | 9 | 12 | 12 | 20.1 | 0 | 2.1
6109 | TORONTO BUTTONVILLE A | 9 | 11 | 13 | 15.4 | 2.6 | 0
6109 | TORONTO BUTTONVILLE A | 9 | 12 | 13 | 21.05 | 0 | 3.05
6110 | TORONTO BUTTONVILLE A | 9 | 11 | 14 | 16.7 | 1.3 | 0
6110 | TORONTO BUTTONVILLE A | 9 | 12 | 14 | 21.875 | 0 | 3.875
6111 | TORONTO BUTTONVILLE A | 9 | 11 | 15 | 17.9 | 0.1 | 0
6111 | TORONTO BUTTONVILLE A | 9 | 12 | 15 | 22.725 | 0 | 4.725
6112 | TORONTO BUTTONVILLE A | 9 | 11 | 16 | 17.9 | 0.1 | 0
6112 | TORONTO BUTTONVILLE A | 9 | 12 | 16 | 22.9 | 0 | 4.9
6113 | TORONTO BUTTONVILLE A | 9 | 11 | 17 | 17.4 | 0.6 | 0
6113 | TORONTO BUTTONVILLE A | 9 | 12 | 17 | 22.1 | 0 | 4.1
6114 | TORONTO BUTTONVILLE A | 9 | 11 | 18 | 16.7 | 1.3 | 0
6114 | TORONTO BUTTONVILLE A | 9 | 12 | 18 | 21.8 | 0 | 3.8
6115 | TORONTO BUTTONVILLE A | 9 | 11 | 19 | 14.9 | 3.1 | 0
6115 | TORONTO BUTTONVILLE A | 9 | 12 | 19 | 20.2 | 0 | 2.2
6116 | TORONTO BUTTONVILLE A | 9 | 11 | 20 | 13.1 | 4.9 | 0
6116 | TORONTO BUTTONVILLE A | 9 | 12 | 20 | 18.75 | 0 | 0.75
6117 | TORONTO BUTTONVILLE A | 9 | 11 | 21 | 12.5 | 5.5 | 0
6117 | TORONTO BUTTONVILLE A | 9 | 12 | 21 | 17.525 | 0.475 | 0
6118 | TORONTO BUTTONVILLE A | 9 | 11 | 22 | 12.2 | 5.8 | 0
6118 | TORONTO BUTTONVILLE A | 9 | 12 | 22 | 16.2 | 1.8 | 0
6119 | TORONTO BUTTONVILLE A | 9 | 11 | 23 | 9.9 | 8.1 | 0
6119 | TORONTO BUTTONVILLE A | 9 | 12 | 23 | 15.3 | 2.7 | 0
6120 | TORONTO BUTTONVILLE A | 9 | 11 | 24 | 10 | 8 | 0
6120 | TORONTO BUTTONVILLE A | 9 | 12 | 24 | 14.725 | 3.275 | 0
6121 | TORONTO BUTTONVILLE A | 9 | 12 | 1 | 9.1 | 8.9 | 0
6121 | TORONTO BUTTONVILLE A | 9 | 13 | 1 | 14.35 | 3.65 | 0
6122 | TORONTO BUTTONVILLE A | 9 | 12 | 2 | 8.3 | 9.7 | 0
6122 | TORONTO BUTTONVILLE A | 9 | 13 | 2 | 14.2 | 3.8 | 0
6123 | TORONTO BUTTONVILLE A | 9 | 12 | 3 | 8.7 | 9.3 | 0
6123 | TORONTO BUTTONVILLE A | 9 | 13 | 3 | 14 | 4 | 0
6124 | TORONTO BUTTONVILLE A | 9 | 12 | 4 | 8.9 | 9.1 | 0
6124 | TORONTO BUTTONVILLE A | 9 | 13 | 4 | 12.825 | 5.175 | 0
6125 | TORONTO BUTTONVILLE A | 9 | 12 | 5 | 8 | 10 | 0
6125 | TORONTO BUTTONVILLE A | 9 | 13 | 5 | 12.575 | 5.425 | 0
6126 | TORONTO BUTTONVILLE A | 9 | 12 | 6 | 9.1 | 8.9 | 0
6126 | TORONTO BUTTONVILLE A | 9 | 13 | 6 | 12.425 | 5.575 | 0
6127 | TORONTO BUTTONVILLE A | 9 | 12 | 7 | 10.3 | 7.7 | 0
6127 | TORONTO BUTTONVILLE A | 9 | 13 | 7 | 12.775 | 5.225 | 0
6128 | TORONTO BUTTONVILLE A | 9 | 12 | 8 | 10.8 | 7.2 | 0
6128 | TORONTO BUTTONVILLE A | 9 | 13 | 8 | 14.55 | 3.45 | 0
6129 | TORONTO BUTTONVILLE A | 9 | 12 | 9 | 13.1 | 4.9 | 0
6129 | TORONTO BUTTONVILLE A | 9 | 13 | 9 | 17.275 | 0.725 | 0
6130 | TORONTO BUTTONVILLE A | 9 | 12 | 10 | 14.9 | 3.1 | 0
6130 | TORONTO BUTTONVILLE A | 9 | 13 | 10 | 18.875 | 0 | 0.875
6131 | TORONTO BUTTONVILLE A | 9 | 12 | 11 | 16.3 | 1.7 | 0
6131 | TORONTO BUTTONVILLE A | 9 | 13 | 11 | 19.65 | 0 | 1.65
6132 | TORONTO BUTTONVILLE A | 9 | 12 | 12 | 17.3 | 0.7 | 0
6132 | TORONTO BUTTONVILLE A | 9 | 13 | 12 | 20.225 | 0 | 2.225
6133 | TORONTO BUTTONVILLE A | 9 | 12 | 13 | 18.6 | 0 | 0.6
6133 | TORONTO BUTTONVILLE A | 9 | 13 | 13 | 21.225 | 0 | 3.225
6134 | TORONTO BUTTONVILLE A | 9 | 12 | 14 | 19 | 0 | 1
6134 | TORONTO BUTTONVILLE A | 9 | 13 | 14 | 21.9 | 0 | 3.9
6135 | TORONTO BUTTONVILLE A | 9 | 12 | 15 | 19.6 | 0 | 1.6
6135 | TORONTO BUTTONVILLE A | 9 | 13 | 15 | 22.375 | 0 | 4.375
6136 | TORONTO BUTTONVILLE A | 9 | 12 | 16 | 18.7 | 0 | 0.7
6136 | TORONTO BUTTONVILLE A | 9 | 13 | 16 | 22.475 | 0 | 4.475
6137 | TORONTO BUTTONVILLE A | 9 | 12 | 17 | 19.1 | 0 | 1.1
6137 | TORONTO BUTTONVILLE A | 9 | 13 | 17 | 22.475 | 0 | 4.475
6138 | TORONTO BUTTONVILLE A | 9 | 12 | 18 | 19.6 | 0 | 1.6
6138 | TORONTO BUTTONVILLE A | 9 | 13 | 18 | 21.875 | 0 | 3.875
6139 | TORONTO BUTTONVILLE A | 9 | 12 | 19 | 19.4 | 0 | 1.4
6139 | TORONTO BUTTONVILLE A | 9 | 13 | 19 | 21 | 0 | 3
6140 | TORONTO BUTTONVILLE A | 9 | 12 | 20 | 19 | 0 | 1
6140 | TORONTO BUTTONVILLE A | 9 | 13 | 20 | 19.625 | 0 | 1.625
6141 | TORONTO BUTTONVILLE A | 9 | 12 | 21 | 19.2 | 0 | 1.2
6141 | TORONTO BUTTONVILLE A | 9 | 13 | 21 | 19.075 | 0 | 1.075
6142 | TORONTO BUTTONVILLE A | 9 | 12 | 22 | 19.7 | 0 | 1.7
6142 | TORONTO BUTTONVILLE A | 9 | 13 | 22 | 18 | 0 | 0
6143 | TORONTO BUTTONVILLE A | 9 | 12 | 23 | 20.2 | 0 | 2.2
6143 | TORONTO BUTTONVILLE A | 9 | 13 | 23 | 17.6 | 0.4 | 0
6144 | TORONTO BUTTONVILLE A | 9 | 12 | 24 | 19.7 | 0 | 1.7
6144 | TORONTO BUTTONVILLE A | 9 | 13 | 24 | 17.3 | 0.7 | 0
6145 | TORONTO BUTTONVILLE A | 9 | 13 | 1 | 19.2 | 0 | 1.2
6145 | TORONTO BUTTONVILLE A | 9 | 14 | 1 | 16.625 | 1.375 | 0
6146 | TORONTO BUTTONVILLE A | 9 | 13 | 2 | 19.2 | 0 | 1.2
6146 | TORONTO BUTTONVILLE A | 9 | 14 | 2 | 16.15 | 1.85 | 0
6147 | TORONTO BUTTONVILLE A | 9 | 13 | 3 | 19 | 0 | 1
6147 | TORONTO BUTTONVILLE A | 9 | 14 | 3 | 16.15 | 1.85 | 0
6148 | TORONTO BUTTONVILLE A | 9 | 13 | 4 | 19 | 0 | 1
6148 | TORONTO BUTTONVILLE A | 9 | 14 | 4 | 16.075 | 1.925 | 0
6149 | TORONTO BUTTONVILLE A | 9 | 13 | 5 | 19.3 | 0 | 1.3
6149 | TORONTO BUTTONVILLE A | 9 | 14 | 5 | 16.275 | 1.725 | 0
6150 | TORONTO BUTTONVILLE A | 9 | 13 | 6 | 19.1 | 0 | 1.1
6150 | TORONTO BUTTONVILLE A | 9 | 14 | 6 | 16.2 | 1.8 | 0
6151 | TORONTO BUTTONVILLE A | 9 | 13 | 7 | 18.8 | 0 | 0.8
6151 | TORONTO BUTTONVILLE A | 9 | 14 | 7 | 15.6 | 2.4 | 0
6152 | TORONTO BUTTONVILLE A | 9 | 13 | 8 | 19.9 | 0 | 1.9
6152 | TORONTO BUTTONVILLE A | 9 | 14 | 8 | 16.65 | 1.35 | 0
6153 | TORONTO BUTTONVILLE A | 9 | 13 | 9 | 20 | 0 | 2
6153 | TORONTO BUTTONVILLE A | 9 | 14 | 9 | 18.45 | 0 | 0.45
6154 | TORONTO BUTTONVILLE A | 9 | 13 | 10 | 20 | 0 | 2
6154 | TORONTO BUTTONVILLE A | 9 | 14 | 10 | 20.125 | 0 | 2.125
6155 | TORONTO BUTTONVILLE A | 9 | 13 | 11 | 20.2 | 0 | 2.2
6155 | TORONTO BUTTONVILLE A | 9 | 14 | 11 | 21.875 | 0 | 3.875
6156 | TORONTO BUTTONVILLE A | 9 | 13 | 12 | 21.6 | 0 | 3.6
6156 | TORONTO BUTTONVILLE A | 9 | 14 | 12 | 22.35 | 0 | 4.35
6157 | TORONTO BUTTONVILLE A | 9 | 13 | 13 | 23.9 | 0 | 5.9
6157 | TORONTO BUTTONVILLE A | 9 | 14 | 13 | 23.025 | 0 | 5.025
6158 | TORONTO BUTTONVILLE A | 9 | 13 | 14 | 25 | 0 | 7
6158 | TORONTO BUTTONVILLE A | 9 | 14 | 14 | 24.15 | 0 | 6.15
6159 | TORONTO BUTTONVILLE A | 9 | 13 | 15 | 23 | 0 | 5
6159 | TORONTO BUTTONVILLE A | 9 | 14 | 15 | 25.125 | 0 | 7.125
6160 | TORONTO BUTTONVILLE A | 9 | 13 | 16 | 22.9 | 0 | 4.9
6160 | TORONTO BUTTONVILLE A | 9 | 14 | 16 | 24.825 | 0 | 6.825
6161 | TORONTO BUTTONVILLE A | 9 | 13 | 17 | 22.4 | 0 | 4.4
6161 | TORONTO BUTTONVILLE A | 9 | 14 | 17 | 24.95 | 0 | 6.95
6162 | TORONTO BUTTONVILLE A | 9 | 13 | 18 | 21.5 | 0 | 3.5
6162 | TORONTO BUTTONVILLE A | 9 | 14 | 18 | 24.475 | 0 | 6.475
6163 | TORONTO BUTTONVILLE A | 9 | 13 | 19 | 20.1 | 0 | 2.1
6163 | TORONTO BUTTONVILLE A | 9 | 14 | 19 | 23.55 | 0 | 5.55
6164 | TORONTO BUTTONVILLE A | 9 | 13 | 20 | 18.8 | 0 | 0.8
6164 | TORONTO BUTTONVILLE A | 9 | 14 | 20 | 22.575 | 0 | 4.575
6165 | TORONTO BUTTONVILLE A | 9 | 13 | 21 | 17.7 | 0.3 | 0
6165 | TORONTO BUTTONVILLE A | 9 | 14 | 21 | 21.35 | 0 | 3.35
6166 | TORONTO BUTTONVILLE A | 9 | 13 | 22 | 16.5 | 1.5 | 0
6166 | TORONTO BUTTONVILLE A | 9 | 14 | 22 | 20.475 | 0 | 2.475
6167 | TORONTO BUTTONVILLE A | 9 | 13 | 23 | 15.8 | 2.2 | 0
6167 | TORONTO BUTTONVILLE A | 9 | 14 | 23 | 20.125 | 0 | 2.125
6168 | TORONTO BUTTONVILLE A | 9 | 13 | 24 | 15.5 | 2.5 | 0
6168 | TORONTO BUTTONVILLE A | 9 | 14 | 24 | 18.3 | 0 | 0.3
6169 | TORONTO BUTTONVILLE A | 9 | 14 | 1 | 14.4 | 3.6 | 0
6169 | TORONTO BUTTONVILLE A | 9 | 15 | 1 | 17.7 | 0.3 | 0
6170 | TORONTO BUTTONVILLE A | 9 | 14 | 2 | 14.4 | 3.6 | 0
6170 | TORONTO BUTTONVILLE A | 9 | 15 | 2 | 17.05 | 0.95 | 0
6171 | TORONTO BUTTONVILLE A | 9 | 14 | 3 | 13.5 | 4.5 | 0
6171 | TORONTO BUTTONVILLE A | 9 | 15 | 3 | 16.275 | 1.725 | 0
6172 | TORONTO BUTTONVILLE A | 9 | 14 | 4 | 12.8 | 5.2 | 0
6172 | TORONTO BUTTONVILLE A | 9 | 15 | 4 | 16.1 | 1.9 | 0
6173 | TORONTO BUTTONVILLE A | 9 | 14 | 5 | 13 | 5 | 0
6173 | TORONTO BUTTONVILLE A | 9 | 15 | 5 | 15.75 | 2.25 | 0
6174 | TORONTO BUTTONVILLE A | 9 | 14 | 6 | 13 | 5 | 0
6174 | TORONTO BUTTONVILLE A | 9 | 15 | 6 | 15.725 | 2.275 | 0
6175 | TORONTO BUTTONVILLE A | 9 | 14 | 7 | 11.9 | 6.1 | 0
6175 | TORONTO BUTTONVILLE A | 9 | 15 | 7 | 15.575 | 2.425 | 0
6176 | TORONTO BUTTONVILLE A | 9 | 14 | 8 | 12.3 | 5.7 | 0
6176 | TORONTO BUTTONVILLE A | 9 | 15 | 8 | 16.8 | 1.2 | 0
6177 | TORONTO BUTTONVILLE A | 9 | 14 | 9 | 12.8 | 5.2 | 0
6177 | TORONTO BUTTONVILLE A | 9 | 15 | 9 | 18.35 | 0 | 0.35
6178 | TORONTO BUTTONVILLE A | 9 | 14 | 10 | 13.4 | 4.6 | 0
6178 | TORONTO BUTTONVILLE A | 9 | 15 | 10 | 20.35 | 0 | 2.35
6179 | TORONTO BUTTONVILLE A | 9 | 14 | 11 | 14.3 | 3.7 | 0
6179 | TORONTO BUTTONVILLE A | 9 | 15 | 11 | 20.825 | 0 | 2.825
6180 | TORONTO BUTTONVILLE A | 9 | 14 | 12 | 14.7 | 3.3 | 0
6180 | TORONTO BUTTONVILLE A | 9 | 15 | 12 | 21.475 | 0 | 3.475
6181 | TORONTO BUTTONVILLE A | 9 | 14 | 13 | 15.9 | 2.1 | 0
6181 | TORONTO BUTTONVILLE A | 9 | 15 | 13 | 21.675 | 0 | 3.675
6182 | TORONTO BUTTONVILLE A | 9 | 14 | 14 | 16.5 | 1.5 | 0
6182 | TORONTO BUTTONVILLE A | 9 | 15 | 14 | 22.5 | 0 | 4.5
6183 | TORONTO BUTTONVILLE A | 9 | 14 | 15 | 16.9 | 1.1 | 0
6183 | TORONTO BUTTONVILLE A | 9 | 15 | 15 | 22.125 | 0 | 4.125
6184 | TORONTO BUTTONVILLE A | 9 | 14 | 16 | 16.1 | 1.9 | 0
6184 | TORONTO BUTTONVILLE A | 9 | 15 | 16 | 22.525 | 0 | 4.525
6185 | TORONTO BUTTONVILLE A | 9 | 14 | 17 | 15.7 | 2.3 | 0
6185 | TORONTO BUTTONVILLE A | 9 | 15 | 17 | 22.675 | 0 | 4.675
6186 | TORONTO BUTTONVILLE A | 9 | 14 | 18 | 14.6 | 3.4 | 0
6186 | TORONTO BUTTONVILLE A | 9 | 15 | 18 | 22.125 | 0 | 4.125
6187 | TORONTO BUTTONVILLE A | 9 | 14 | 19 | 13.2 | 4.8 | 0
6187 | TORONTO BUTTONVILLE A | 9 | 15 | 19 | 21.025 | 0 | 3.025
6188 | TORONTO BUTTONVILLE A | 9 | 14 | 20 | 11.2 | 6.8 | 0
6188 | TORONTO BUTTONVILLE A | 9 | 15 | 20 | 20.175 | 0 | 2.175
6189 | TORONTO BUTTONVILLE A | 9 | 14 | 21 | 9.7 | 8.3 | 0
6189 | TORONTO BUTTONVILLE A | 9 | 15 | 21 | 19.45 | 0 | 1.45
6190 | TORONTO BUTTONVILLE A | 9 | 14 | 22 | 8.9 | 9.1 | 0
6190 | TORONTO BUTTONVILLE A | 9 | 15 | 22 | 18.65 | 0 | 0.65
6191 | TORONTO BUTTONVILLE A | 9 | 14 | 23 | 8.6 | 9.4 | 0
6191 | TORONTO BUTTONVILLE A | 9 | 15 | 23 | 18.325 | 0 | 0.325
6192 | TORONTO BUTTONVILLE A | 9 | 14 | 24 | 7.5 | 10.5 | 0
6192 | TORONTO BUTTONVILLE A | 9 | 15 | 24 | 17.95 | 0.05 | 0
6193 | TORONTO BUTTONVILLE A | 9 | 15 | 1 | 7.7 | 10.3 | 0
6193 | TORONTO BUTTONVILLE A | 9 | 16 | 1 | 16.85 | 1.15 | 0
6194 | TORONTO BUTTONVILLE A | 9 | 15 | 2 | 6 | 12 | 0
6194 | TORONTO BUTTONVILLE A | 9 | 16 | 2 | 16.225 | 1.775 | 0
6195 | TORONTO BUTTONVILLE A | 9 | 15 | 3 | 6.8 | 11.2 | 0
6195 | TORONTO BUTTONVILLE A | 9 | 16 | 3 | 16.175 | 1.825 | 0
6196 | TORONTO BUTTONVILLE A | 9 | 15 | 4 | 6.3 | 11.7 | 0
6196 | TORONTO BUTTONVILLE A | 9 | 16 | 4 | 15.475 | 2.525 | 0
6197 | TORONTO BUTTONVILLE A | 9 | 15 | 5 | 5.5 | 12.5 | 0
6197 | TORONTO BUTTONVILLE A | 9 | 16 | 5 | 15.65 | 2.35 | 0
6198 | TORONTO BUTTONVILLE A | 9 | 15 | 6 | 6.1 | 11.9 | 0
6198 | TORONTO BUTTONVILLE A | 9 | 16 | 6 | 15.2 | 2.8 | 0
6199 | TORONTO BUTTONVILLE A | 9 | 15 | 7 | 5.5 | 12.5 | 0
6199 | TORONTO BUTTONVILLE A | 9 | 16 | 7 | 15 | 3 | 0
6200 | TORONTO BUTTONVILLE A | 9 | 15 | 8 | 6.2 | 11.8 | 0
6200 | TORONTO BUTTONVILLE A | 9 | 16 | 8 | 16.3 | 1.7 | 0
6201 | TORONTO BUTTONVILLE A | 9 | 15 | 9 | 8.8 | 9.2 | 0
6201 | TORONTO BUTTONVILLE A | 9 | 16 | 9 | 18.2 | 0 | 0.2
6202 | TORONTO BUTTONVILLE A | 9 | 15 | 10 | 12.1 | 5.9 | 0
6202 | TORONTO BUTTONVILLE A | 9 | 16 | 10 | 20.375 | 0 | 2.375
6203 | TORONTO BUTTONVILLE A | 9 | 15 | 11 | 15.4 | 2.6 | 0
6203 | TORONTO BUTTONVILLE A | 9 | 16 | 11 | 21.975 | 0 | 3.975
6204 | TORONTO BUTTONVILLE A | 9 | 15 | 12 | 16.2 | 1.8 | 0
6204 | TORONTO BUTTONVILLE A | 9 | 16 | 12 | 22.875 | 0 | 4.875
6205 | TORONTO BUTTONVILLE A | 9 | 15 | 13 | 16.7 | 1.3 | 0
6205 | TORONTO BUTTONVILLE A | 9 | 16 | 13 | 23.2 | 0 | 5.2
6206 | TORONTO BUTTONVILLE A | 9 | 15 | 14 | 17.4 | 0.6 | 0
6206 | TORONTO BUTTONVILLE A | 9 | 16 | 14 | 23.525 | 0 | 5.525
6207 | TORONTO BUTTONVILLE A | 9 | 15 | 15 | 18 | 0 | 0
6207 | TORONTO BUTTONVILLE A | 9 | 16 | 15 | 23.525 | 0 | 5.525
6208 | TORONTO BUTTONVILLE A | 9 | 15 | 16 | 18.5 | 0 | 0.5
6208 | TORONTO BUTTONVILLE A | 9 | 16 | 16 | 23.825 | 0 | 5.825
6209 | TORONTO BUTTONVILLE A | 9 | 15 | 17 | 18.2 | 0 | 0.2
6209 | TORONTO BUTTONVILLE A | 9 | 16 | 17 | 23.5 | 0 | 5.5
6210 | TORONTO BUTTONVILLE A | 9 | 15 | 18 | 17.6 | 0.4 | 0
6210 | TORONTO BUTTONVILLE A | 9 | 16 | 18 | 22.625 | 0 | 4.625
6211 | TORONTO BUTTONVILLE A | 9 | 15 | 19 | 16.4 | 1.6 | 0
6211 | TORONTO BUTTONVILLE A | 9 | 16 | 19 | 21.175 | 0 | 3.175
6212 | TORONTO BUTTONVILLE A | 9 | 15 | 20 | 15.9 | 2.1 | 0
6212 | TORONTO BUTTONVILLE A | 9 | 16 | 20 | 19.875 | 0 | 1.875
6213 | TORONTO BUTTONVILLE A | 9 | 15 | 21 | 15.4 | 2.6 | 0
6213 | TORONTO BUTTONVILLE A | 9 | 16 | 21 | 18.6 | 0 | 0.6
6214 | TORONTO BUTTONVILLE A | 9 | 15 | 22 | 15.1 | 2.9 | 0
6214 | TORONTO BUTTONVILLE A | 9 | 16 | 22 | 17.425 | 0.575 | 0
6215 | TORONTO BUTTONVILLE A | 9 | 15 | 23 | 14.8 | 3.2 | 0
6215 | TORONTO BUTTONVILLE A | 9 | 16 | 23 | 16.2 | 1.8 | 0
6216 | TORONTO BUTTONVILLE A | 9 | 15 | 24 | 14.5 | 3.5 | 0
6216 | TORONTO BUTTONVILLE A | 9 | 16 | 24 | 15.825 | 2.175 | 0
6217 | TORONTO BUTTONVILLE A | 9 | 16 | 1 | 14.5 | 3.5 | 0
6217 | TORONTO BUTTONVILLE A | 9 | 17 | 1 | 15.05 | 2.95 | 0
6218 | TORONTO BUTTONVILLE A | 9 | 16 | 2 | 14.2 | 3.8 | 0
6218 | TORONTO BUTTONVILLE A | 9 | 17 | 2 | 14.275 | 3.725 | 0
6219 | TORONTO BUTTONVILLE A | 9 | 16 | 3 | 14 | 4 | 0
6219 | TORONTO BUTTONVILLE A | 9 | 17 | 3 | 14.275 | 3.725 | 0
6220 | TORONTO BUTTONVILLE A | 9 | 16 | 4 | 14.3 | 3.7 | 0
6220 | TORONTO BUTTONVILLE A | 9 | 17 | 4 | 14.2 | 3.8 | 0
6221 | TORONTO BUTTONVILLE A | 9 | 16 | 5 | 14.2 | 3.8 | 0
6221 | TORONTO BUTTONVILLE A | 9 | 17 | 5 | 13.8 | 4.2 | 0
6222 | TORONTO BUTTONVILLE A | 9 | 16 | 6 | 13.7 | 4.3 | 0
6222 | TORONTO BUTTONVILLE A | 9 | 17 | 6 | 14 | 4 | 0
6223 | TORONTO BUTTONVILLE A | 9 | 16 | 7 | 14 | 4 | 0
6223 | TORONTO BUTTONVILLE A | 9 | 17 | 7 | 14.05 | 3.95 | 0
6224 | TORONTO BUTTONVILLE A | 9 | 16 | 8 | 14.9 | 3.1 | 0
6224 | TORONTO BUTTONVILLE A | 9 | 17 | 8 | 15.625 | 2.375 | 0
6225 | TORONTO BUTTONVILLE A | 9 | 16 | 9 | 17 | 1 | 0
6225 | TORONTO BUTTONVILLE A | 9 | 17 | 9 | 17.5 | 0.5 | 0
6226 | TORONTO BUTTONVILLE A | 9 | 16 | 10 | 18.3 | 0 | 0.3
6226 | TORONTO BUTTONVILLE A | 9 | 17 | 10 | 19.5 | 0 | 1.5
6227 | TORONTO BUTTONVILLE A | 9 | 16 | 11 | 20 | 0 | 2
6227 | TORONTO BUTTONVILLE A | 9 | 17 | 11 | 21.875 | 0 | 3.875
6228 | TORONTO BUTTONVILLE A | 9 | 16 | 12 | 21.8 | 0 | 3.8
6228 | TORONTO BUTTONVILLE A | 9 | 17 | 12 | 23.225 | 0 | 5.225
6229 | TORONTO BUTTONVILLE A | 9 | 16 | 13 | 22.4 | 0 | 4.4
6229 | TORONTO BUTTONVILLE A | 9 | 17 | 13 | 24.45 | 0 | 6.45
6230 | TORONTO BUTTONVILLE A | 9 | 16 | 14 | 23.9 | 0 | 5.9
6230 | TORONTO BUTTONVILLE A | 9 | 17 | 14 | 25.45 | 0 | 7.45
6231 | TORONTO BUTTONVILLE A | 9 | 16 | 15 | 24.4 | 0 | 6.4
6231 | TORONTO BUTTONVILLE A | 9 | 17 | 15 | 25.675 | 0 | 7.675
6232 | TORONTO BUTTONVILLE A | 9 | 16 | 16 | 23.6 | 0 | 5.6
6232 | TORONTO BUTTONVILLE A | 9 | 17 | 16 | 25.5 | 0 | 7.5
6233 | TORONTO BUTTONVILLE A | 9 | 16 | 17 | 23.1 | 0 | 5.1
6233 | TORONTO BUTTONVILLE A | 9 | 17 | 17 | 25.375 | 0 | 7.375
6234 | TORONTO BUTTONVILLE A | 9 | 16 | 18 | 22.5 | 0 | 4.5
6234 | TORONTO BUTTONVILLE A | 9 | 17 | 18 | 24.55 | 0 | 6.55
6235 | TORONTO BUTTONVILLE A | 9 | 16 | 19 | 21.9 | 0 | 3.9
6235 | TORONTO BUTTONVILLE A | 9 | 17 | 19 | 23.025 | 0 | 5.025
6236 | TORONTO BUTTONVILLE A | 9 | 16 | 20 | 20.8 | 0 | 2.8
6236 | TORONTO BUTTONVILLE A | 9 | 17 | 20 | 21.1 | 0 | 3.1
6237 | TORONTO BUTTONVILLE A | 9 | 16 | 21 | 19.8 | 0 | 1.8
6237 | TORONTO BUTTONVILLE A | 9 | 17 | 21 | 19.85 | 0 | 1.85
6238 | TORONTO BUTTONVILLE A | 9 | 16 | 22 | 19.2 | 0 | 1.2
6238 | TORONTO BUTTONVILLE A | 9 | 17 | 22 | 18.65 | 0 | 0.65
6239 | TORONTO BUTTONVILLE A | 9 | 16 | 23 | 18 | 0 | 0
6239 | TORONTO BUTTONVILLE A | 9 | 17 | 23 | 18.175 | 0 | 0.175
6240 | TORONTO BUTTONVILLE A | 9 | 16 | 24 | 17.1 | 0.9 | 0
6240 | TORONTO BUTTONVILLE A | 9 | 17 | 24 | 17.475 | 0.525 | 0
6241 | TORONTO BUTTONVILLE A | 9 | 17 | 1 | 16.6 | 1.4 | 0
6241 | TORONTO BUTTONVILLE A | 9 | 18 | 1 | 16.725 | 1.275 | 0
6242 | TORONTO BUTTONVILLE A | 9 | 17 | 2 | 16 | 2 | 0
6242 | TORONTO BUTTONVILLE A | 9 | 18 | 2 | 16.025 | 1.975 | 0
6243 | TORONTO BUTTONVILLE A | 9 | 17 | 3 | 15.2 | 2.8 | 0
6243 | TORONTO BUTTONVILLE A | 9 | 18 | 3 | 15.65 | 2.35 | 0
6244 | TORONTO BUTTONVILLE A | 9 | 17 | 4 | 14.2 | 3.8 | 0
6244 | TORONTO BUTTONVILLE A | 9 | 18 | 4 | 16.275 | 1.725 | 0
6245 | TORONTO BUTTONVILLE A | 9 | 17 | 5 | 13.2 | 4.8 | 0
6245 | TORONTO BUTTONVILLE A | 9 | 18 | 5 | 16.45 | 1.55 | 0
6246 | TORONTO BUTTONVILLE A | 9 | 17 | 6 | 12.9 | 5.1 | 0
6246 | TORONTO BUTTONVILLE A | 9 | 18 | 6 | 15.95 | 2.05 | 0
6247 | TORONTO BUTTONVILLE A | 9 | 17 | 7 | 12.6 | 5.4 | 0
6247 | TORONTO BUTTONVILLE A | 9 | 18 | 7 | 15.975 | 2.025 | 0
6248 | TORONTO BUTTONVILLE A | 9 | 17 | 8 | 13.1 | 4.9 | 0
6248 | TORONTO BUTTONVILLE A | 9 | 18 | 8 | 17 | 1 | 0
6249 | TORONTO BUTTONVILLE A | 9 | 17 | 9 | 14.9 | 3.1 | 0
6249 | TORONTO BUTTONVILLE A | 9 | 18 | 9 | 18.725 | 0 | 0.725
6250 | TORONTO BUTTONVILLE A | 9 | 17 | 10 | 15.7 | 2.3 | 0
6250 | TORONTO BUTTONVILLE A | 9 | 18 | 10 | 20.05 | 0 | 2.05
6251 | TORONTO BUTTONVILLE A | 9 | 17 | 11 | 15.8 | 2.2 | 0
6251 | TORONTO BUTTONVILLE A | 9 | 18 | 11 | 22 | 0 | 4
6252 | TORONTO BUTTONVILLE A | 9 | 17 | 12 | 15.6 | 2.4 | 0
6252 | TORONTO BUTTONVILLE A | 9 | 18 | 12 | 22.85 | 0 | 4.85
6253 | TORONTO BUTTONVILLE A | 9 | 17 | 13 | 16.2 | 1.8 | 0
6253 | TORONTO BUTTONVILLE A | 9 | 18 | 13 | 23.35 | 0 | 5.35
6254 | TORONTO BUTTONVILLE A | 9 | 17 | 14 | 16.4 | 1.6 | 0
6254 | TORONTO BUTTONVILLE A | 9 | 18 | 14 | 24.125 | 0 | 6.125
6255 | TORONTO BUTTONVILLE A | 9 | 17 | 15 | 16.8 | 1.2 | 0
6255 | TORONTO BUTTONVILLE A | 9 | 18 | 15 | 24.25 | 0 | 6.25
6256 | TORONTO BUTTONVILLE A | 9 | 17 | 16 | 18.3 | 0 | 0.3
6256 | TORONTO BUTTONVILLE A | 9 | 18 | 16 | 24.4 | 0 | 6.4
6257 | TORONTO BUTTONVILLE A | 9 | 17 | 17 | 17.2 | 0.8 | 0
6257 | TORONTO BUTTONVILLE A | 9 | 18 | 17 | 23.725 | 0 | 5.725
6258 | TORONTO BUTTONVILLE A | 9 | 17 | 18 | 16.4 | 1.6 | 0
6258 | TORONTO BUTTONVILLE A | 9 | 18 | 18 | 22.225 | 0 | 4.225
6259 | TORONTO BUTTONVILLE A | 9 | 17 | 19 | 13.4 | 4.6 | 0
6259 | TORONTO BUTTONVILLE A | 9 | 18 | 19 | 20.325 | 0 | 2.325
6260 | TORONTO BUTTONVILLE A | 9 | 17 | 20 | 11.2 | 6.8 | 0
6260 | TORONTO BUTTONVILLE A | 9 | 18 | 20 | 18.275 | 0 | 0.275
6261 | TORONTO BUTTONVILLE A | 9 | 17 | 21 | 10.1 | 7.9 | 0
6261 | TORONTO BUTTONVILLE A | 9 | 18 | 21 | 17.025 | 0.975 | 0
6262 | TORONTO BUTTONVILLE A | 9 | 17 | 22 | 8.7 | 9.3 | 0
6262 | TORONTO BUTTONVILLE A | 9 | 18 | 22 | 16.15 | 1.85 | 0
6263 | TORONTO BUTTONVILLE A | 9 | 17 | 23 | 7.8 | 10.2 | 0
6263 | TORONTO BUTTONVILLE A | 9 | 18 | 23 | 15.65 | 2.35 | 0
6264 | TORONTO BUTTONVILLE A | 9 | 17 | 24 | 7.9 | 10.1 | 0
6264 | TORONTO BUTTONVILLE A | 9 | 18 | 24 | 15.275 | 2.725 | 0
6265 | TORONTO BUTTONVILLE A | 9 | 18 | 1 | 8.2 | 9.8 | 0
6265 | TORONTO BUTTONVILLE A | 9 | 19 | 1 | 15.2 | 2.8 | 0
6266 | TORONTO BUTTONVILLE A | 9 | 18 | 2 | 7.8 | 10.2 | 0
6266 | TORONTO BUTTONVILLE A | 9 | 19 | 2 | 14.925 | 3.075 | 0
6267 | TORONTO BUTTONVILLE A | 9 | 18 | 3 | 6.5 | 11.5 | 0
6267 | TORONTO BUTTONVILLE A | 9 | 19 | 3 | 14.825 | 3.175 | 0
6268 | TORONTO BUTTONVILLE A | 9 | 18 | 4 | 5.8 | 12.2 | 0
6268 | TORONTO BUTTONVILLE A | 9 | 19 | 4 | 14.725 | 3.275 | 0
6269 | TORONTO BUTTONVILLE A | 9 | 18 | 5 | 5.2 | 12.8 | 0
6269 | TORONTO BUTTONVILLE A | 9 | 19 | 5 | 14.15 | 3.85 | 0
6270 | TORONTO BUTTONVILLE A | 9 | 18 | 6 | 5.9 | 12.1 | 0
6270 | TORONTO BUTTONVILLE A | 9 | 19 | 6 | 13.9 | 4.1 | 0
6271 | TORONTO BUTTONVILLE A | 9 | 18 | 7 | 4.6 | 13.4 | 0
6271 | TORONTO BUTTONVILLE A | 9 | 19 | 7 | 13.625 | 4.375 | 0
6272 | TORONTO BUTTONVILLE A | 9 | 18 | 8 | 6.9 | 11.1 | 0
6272 | TORONTO BUTTONVILLE A | 9 | 19 | 8 | 14.25 | 3.75 | 0
6273 | TORONTO BUTTONVILLE A | 9 | 18 | 9 | 10.3 | 7.7 | 0
6273 | TORONTO BUTTONVILLE A | 9 | 19 | 9 | 16.6 | 1.4 | 0
6274 | TORONTO BUTTONVILLE A | 9 | 18 | 10 | 12.3 | 5.7 | 0
6274 | TORONTO BUTTONVILLE A | 9 | 19 | 10 | 18.45 | 0 | 0.45
6275 | TORONTO BUTTONVILLE A | 9 | 18 | 11 | 13.7 | 4.3 | 0
6275 | TORONTO BUTTONVILLE A | 9 | 19 | 11 | 19.7 | 0 | 1.7
6276 | TORONTO BUTTONVILLE A | 9 | 18 | 12 | 14.1 | 3.9 | 0
6276 | TORONTO BUTTONVILLE A | 9 | 19 | 12 | 20.825 | 0 | 2.825
6277 | TORONTO BUTTONVILLE A | 9 | 18 | 13 | 14.6 | 3.4 | 0
6277 | TORONTO BUTTONVILLE A | 9 | 19 | 13 | 21.9 | 0 | 3.9
6278 | TORONTO BUTTONVILLE A | 9 | 18 | 14 | 15 | 3 | 0
6278 | TORONTO BUTTONVILLE A | 9 | 19 | 14 | 22.55 | 0 | 4.55
6279 | TORONTO BUTTONVILLE A | 9 | 18 | 15 | 14.3 | 3.7 | 0
6279 | TORONTO BUTTONVILLE A | 9 | 19 | 15 | 22.625 | 0 | 4.625
6280 | TORONTO BUTTONVILLE A | 9 | 18 | 16 | 14.4 | 3.6 | 0
6280 | TORONTO BUTTONVILLE A | 9 | 19 | 16 | 22.75 | 0 | 4.75
6281 | TORONTO BUTTONVILLE A | 9 | 18 | 17 | 12.9 | 5.1 | 0
6281 | TORONTO BUTTONVILLE A | 9 | 19 | 17 | 22.375 | 0 | 4.375
6282 | TORONTO BUTTONVILLE A | 9 | 18 | 18 | 12.9 | 5.1 | 0
6282 | TORONTO BUTTONVILLE A | 9 | 19 | 18 | 21.425 | 0 | 3.425
6283 | TORONTO BUTTONVILLE A | 9 | 18 | 19 | 11 | 7 | 0
6283 | TORONTO BUTTONVILLE A | 9 | 19 | 19 | 19.6 | 0 | 1.6
6284 | TORONTO BUTTONVILLE A | 9 | 18 | 20 | 9.3 | 8.7 | 0
6284 | TORONTO BUTTONVILLE A | 9 | 19 | 20 | 18.025 | 0 | 0.025
6285 | TORONTO BUTTONVILLE A | 9 | 18 | 21 | 8.1 | 9.9 | 0
6285 | TORONTO BUTTONVILLE A | 9 | 19 | 21 | 17.325 | 0.675 | 0
6286 | TORONTO BUTTONVILLE A | 9 | 18 | 22 | 6.8 | 11.2 | 0
6286 | TORONTO BUTTONVILLE A | 9 | 19 | 22 | 16.45 | 1.55 | 0
6287 | TORONTO BUTTONVILLE A | 9 | 18 | 23 | 6.3 | 11.7 | 0
6287 | TORONTO BUTTONVILLE A | 9 | 19 | 23 | 15.675 | 2.325 | 0
6288 | TORONTO BUTTONVILLE A | 9 | 18 | 24 | 5.2 | 12.8 | 0
6288 | TORONTO BUTTONVILLE A | 9 | 19 | 24 | 14.775 | 3.225 | 0
6289 | TORONTO BUTTONVILLE A | 9 | 19 | 1 | 5.5 | 12.5 | 0
6289 | TORONTO BUTTONVILLE A | 9 | 20 | 1 | 14.225 | 3.775 | 0
6290 | TORONTO BUTTONVILLE A | 9 | 19 | 2 | 4.6 | 13.4 | 0
6290 | TORONTO BUTTONVILLE A | 9 | 20 | 2 | 13.85 | 4.15 | 0
6291 | TORONTO BUTTONVILLE A | 9 | 19 | 3 | 4.2 | 13.8 | 0
6291 | TORONTO BUTTONVILLE A | 9 | 20 | 3 | 13.425 | 4.575 | 0
6292 | TORONTO BUTTONVILLE A | 9 | 19 | 4 | 2.9 | 15.1 | 0
6292 | TORONTO BUTTONVILLE A | 9 | 20 | 4 | 12.825 | 5.175 | 0
6293 | TORONTO BUTTONVILLE A | 9 | 19 | 5 | 2.7 | 15.3 | 0
6293 | TORONTO BUTTONVILLE A | 9 | 20 | 5 | 12.85 | 5.15 | 0
6294 | TORONTO BUTTONVILLE A | 9 | 19 | 6 | 2.7 | 15.3 | 0
6294 | TORONTO BUTTONVILLE A | 9 | 20 | 6 | 12.525 | 5.475 | 0
6295 | TORONTO BUTTONVILLE A | 9 | 19 | 7 | 2.4 | 15.6 | 0
6295 | TORONTO BUTTONVILLE A | 9 | 20 | 7 | 12.475 | 5.525 | 0
6296 | TORONTO BUTTONVILLE A | 9 | 19 | 8 | 3.5 | 14.5 | 0
6296 | TORONTO BUTTONVILLE A | 9 | 20 | 8 | 13.975 | 4.025 | 0
6297 | TORONTO BUTTONVILLE A | 9 | 19 | 9 | 8 | 10 | 0
6297 | TORONTO BUTTONVILLE A | 9 | 20 | 9 | 16.6 | 1.4 | 0
6298 | TORONTO BUTTONVILLE A | 9 | 19 | 10 | 10.7 | 7.3 | 0
6298 | TORONTO BUTTONVILLE A | 9 | 20 | 10 | 18.55 | 0 | 0.55
6299 | TORONTO BUTTONVILLE A | 9 | 19 | 11 | 11.5 | 6.5 | 0
6299 | TORONTO BUTTONVILLE A | 9 | 20 | 11 | 20.025 | 0 | 2.025
6300 | TORONTO BUTTONVILLE A | 9 | 19 | 12 | 11.7 | 6.3 | 0
6300 | TORONTO BUTTONVILLE A | 9 | 20 | 12 | 21.3 | 0 | 3.3
6301 | TORONTO BUTTONVILLE A | 9 | 19 | 13 | 13.5 | 4.5 | 0
6301 | TORONTO BUTTONVILLE A | 9 | 20 | 13 | 22.4 | 0 | 4.4
6302 | TORONTO BUTTONVILLE A | 9 | 19 | 14 | 14.6 | 3.4 | 0
6302 | TORONTO BUTTONVILLE A | 9 | 20 | 14 | 22.8 | 0 | 4.8
6303 | TORONTO BUTTONVILLE A | 9 | 19 | 15 | 13.2 | 4.8 | 0
6303 | TORONTO BUTTONVILLE A | 9 | 20 | 15 | 22.475 | 0 | 4.475
6304 | TORONTO BUTTONVILLE A | 9 | 19 | 16 | 13.7 | 4.3 | 0
6304 | TORONTO BUTTONVILLE A | 9 | 20 | 16 | 22.2 | 0 | 4.2
6305 | TORONTO BUTTONVILLE A | 9 | 19 | 17 | 14 | 4 | 0
6305 | TORONTO BUTTONVILLE A | 9 | 20 | 17 | 22.175 | 0 | 4.175
6306 | TORONTO BUTTONVILLE A | 9 | 19 | 18 | 12.1 | 5.9 | 0
6306 | TORONTO BUTTONVILLE A | 9 | 20 | 18 | 21.425 | 0 | 3.425
6307 | TORONTO BUTTONVILLE A | 9 | 19 | 19 | 11.7 | 6.3 | 0
6307 | TORONTO BUTTONVILLE A | 9 | 20 | 19 | 20.8 | 0 | 2.8
6308 | TORONTO BUTTONVILLE A | 9 | 19 | 20 | 11 | 7 | 0
6308 | TORONTO BUTTONVILLE A | 9 | 20 | 20 | 19.525 | 0 | 1.525
6309 | TORONTO BUTTONVILLE A | 9 | 19 | 21 | 10.3 | 7.7 | 0
6309 | TORONTO BUTTONVILLE A | 9 | 20 | 21 | 18.725 | 0 | 0.725
6310 | TORONTO BUTTONVILLE A | 9 | 19 | 22 | 9.5 | 8.5 | 0
6310 | TORONTO BUTTONVILLE A | 9 | 20 | 22 | 18.25 | 0 | 0.25
6311 | TORONTO BUTTONVILLE A | 9 | 19 | 23 | 8.3 | 9.7 | 0
6311 | TORONTO BUTTONVILLE A | 9 | 20 | 23 | 18 | 0 | 0
6312 | TORONTO BUTTONVILLE A | 9 | 19 | 24 | 8.1 | 9.9 | 0
6312 | TORONTO BUTTONVILLE A | 9 | 20 | 24 | 18.025 | 0 | 0.025
6313 | TORONTO BUTTONVILLE A | 9 | 20 | 1 | 8.7 | 9.3 | 0
6313 | TORONTO BUTTONVILLE A | 9 | 21 | 1 | 18.15 | 0 | 0.15
6314 | TORONTO BUTTONVILLE A | 9 | 20 | 2 | 8.8 | 9.2 | 0
6314 | TORONTO BUTTONVILLE A | 9 | 21 | 2 | 17.95 | 0.05 | 0
6315 | TORONTO BUTTONVILLE A | 9 | 20 | 3 | 8.3 | 9.7 | 0
6315 | TORONTO BUTTONVILLE A | 9 | 21 | 3 | 17.875 | 0.125 | 0
6316 | TORONTO BUTTONVILLE A | 9 | 20 | 4 | 7.1 | 10.9 | 0
6316 | TORONTO BUTTONVILLE A | 9 | 21 | 4 | 17.625 | 0.375 | 0
6317 | TORONTO BUTTONVILLE A | 9 | 20 | 5 | 7.2 | 10.8 | 0
6317 | TORONTO BUTTONVILLE A | 9 | 21 | 5 | 17.375 | 0.625 | 0
6318 | TORONTO BUTTONVILLE A | 9 | 20 | 6 | 7.4 | 10.6 | 0
6318 | TORONTO BUTTONVILLE A | 9 | 21 | 6 | 17.25 | 0.75 | 0
6319 | TORONTO BUTTONVILLE A | 9 | 20 | 7 | 7.9 | 10.1 | 0
6319 | TORONTO BUTTONVILLE A | 9 | 21 | 7 | 17.25 | 0.75 | 0
6320 | TORONTO BUTTONVILLE A | 9 | 20 | 8 | 8.2 | 9.8 | 0
6320 | TORONTO BUTTONVILLE A | 9 | 21 | 8 | 18.2 | 0 | 0.2
6321 | TORONTO BUTTONVILLE A | 9 | 20 | 9 | 10.6 | 7.4 | 0
6321 | TORONTO BUTTONVILLE A | 9 | 21 | 9 | 20.825 | 0 | 2.825
6322 | TORONTO BUTTONVILLE A | 9 | 20 | 10 | 12.8 | 5.2 | 0
6322 | TORONTO BUTTONVILLE A | 9 | 21 | 10 | 22.975 | 0 | 4.975
6323 | TORONTO BUTTONVILLE A | 9 | 20 | 11 | 13.7 | 4.3 | 0
6323 | TORONTO BUTTONVILLE A | 9 | 21 | 11 | 24.65 | 0 | 6.65
6324 | TORONTO BUTTONVILLE A | 9 | 20 | 12 | 14.7 | 3.3 | 0
6324 | TORONTO BUTTONVILLE A | 9 | 21 | 12 | 26.05 | 0 | 8.05
6325 | TORONTO BUTTONVILLE A | 9 | 20 | 13 | 14.3 | 3.7 | 0
6325 | TORONTO BUTTONVILLE A | 9 | 21 | 13 | 26.875 | 0 | 8.875
6326 | TORONTO BUTTONVILLE A | 9 | 20 | 14 | 15.3 | 2.7 | 0
6326 | TORONTO BUTTONVILLE A | 9 | 21 | 14 | 27.075 | 0 | 9.075
6327 | TORONTO BUTTONVILLE A | 9 | 20 | 15 | 14.7 | 3.3 | 0
6327 | TORONTO BUTTONVILLE A | 9 | 21 | 15 | 27.25 | 0 | 9.25
6328 | TORONTO BUTTONVILLE A | 9 | 20 | 16 | 15.9 | 2.1 | 0
6328 | TORONTO BUTTONVILLE A | 9 | 21 | 16 | 26.85 | 0 | 8.85
6329 | TORONTO BUTTONVILLE A | 9 | 20 | 17 | 15.2 | 2.8 | 0
6329 | TORONTO BUTTONVILLE A | 9 | 21 | 17 | 26.275 | 0 | 8.275
6330 | TORONTO BUTTONVILLE A | 9 | 20 | 18 | 14.9 | 3.1 | 0
6330 | TORONTO BUTTONVILLE A | 9 | 21 | 18 | 23.775 | 0 | 5.775
6331 | TORONTO BUTTONVILLE A | 9 | 20 | 19 | 13.4 | 4.6 | 0
6331 | TORONTO BUTTONVILLE A | 9 | 21 | 19 | 22.75 | 0 | 4.75
6332 | TORONTO BUTTONVILLE A | 9 | 20 | 20 | 12.3 | 5.7 | 0
6332 | TORONTO BUTTONVILLE A | 9 | 21 | 20 | 21.375 | 0 | 3.375
6333 | TORONTO BUTTONVILLE A | 9 | 20 | 21 | 10 | 8 | 0
6333 | TORONTO BUTTONVILLE A | 9 | 21 | 21 | 20.15 | 0 | 2.15
6334 | TORONTO BUTTONVILLE A | 9 | 20 | 22 | 8.9 | 9.1 | 0
6334 | TORONTO BUTTONVILLE A | 9 | 21 | 22 | 19.35 | 0 | 1.35
6335 | TORONTO BUTTONVILLE A | 9 | 20 | 23 | 6.9 | 11.1 | 0
6335 | TORONTO BUTTONVILLE A | 9 | 21 | 23 | 18.25 | 0 | 0.25
6336 | TORONTO BUTTONVILLE A | 9 | 20 | 24 | 6.5 | 11.5 | 0
6336 | TORONTO BUTTONVILLE A | 9 | 21 | 24 | 17.65 | 0.35 | 0
6337 | TORONTO BUTTONVILLE A | 9 | 21 | 1 | 6.2 | 11.8 | 0
6337 | TORONTO BUTTONVILLE A | 9 | 22 | 1 | 16.925 | 1.075 | 0
6338 | TORONTO BUTTONVILLE A | 9 | 21 | 2 | 5.7 | 12.3 | 0
6338 | TORONTO BUTTONVILLE A | 9 | 22 | 2 | 16.55 | 1.45 | 0
6339 | TORONTO BUTTONVILLE A | 9 | 21 | 3 | 5.3 | 12.7 | 0
6339 | TORONTO BUTTONVILLE A | 9 | 22 | 3 | 16.05 | 1.95 | 0
6340 | TORONTO BUTTONVILLE A | 9 | 21 | 4 | 4.5 | 13.5 | 0
6340 | TORONTO BUTTONVILLE A | 9 | 22 | 4 | 16.05 | 1.95 | 0
6341 | TORONTO BUTTONVILLE A | 9 | 21 | 5 | 4.8 | 13.2 | 0
6341 | TORONTO BUTTONVILLE A | 9 | 22 | 5 | 15.7 | 2.3 | 0
6342 | TORONTO BUTTONVILLE A | 9 | 21 | 6 | 4 | 14 | 0
6342 | TORONTO BUTTONVILLE A | 9 | 22 | 6 | 15 | 3 | 0
6343 | TORONTO BUTTONVILLE A | 9 | 21 | 7 | 5.3 | 12.7 | 0
6343 | TORONTO BUTTONVILLE A | 9 | 22 | 7 | 15.375 | 2.625 | 0
6344 | TORONTO BUTTONVILLE A | 9 | 21 | 8 | 7.1 | 10.9 | 0
6344 | TORONTO BUTTONVILLE A | 9 | 22 | 8 | 15.725 | 2.275 | 0
6345 | TORONTO BUTTONVILLE A | 9 | 21 | 9 | 11 | 7 | 0
6345 | TORONTO BUTTONVILLE A | 9 | 22 | 9 | 17.1 | 0.9 | 0
6346 | TORONTO BUTTONVILLE A | 9 | 21 | 10 | 13.8 | 4.2 | 0
6346 | TORONTO BUTTONVILLE A | 9 | 22 | 10 | 18.15 | 0 | 0.15
6347 | TORONTO BUTTONVILLE A | 9 | 21 | 11 | 16.6 | 1.4 | 0
6347 | TORONTO BUTTONVILLE A | 9 | 22 | 11 | 19.575 | 0 | 1.575
6348 | TORONTO BUTTONVILLE A | 9 | 21 | 12 | 17.8 | 0.2 | 0
6348 | TORONTO BUTTONVILLE A | 9 | 22 | 12 | 20.7 | 0 | 2.7
6349 | TORONTO BUTTONVILLE A | 9 | 21 | 13 | 18.8 | 0 | 0.8
6349 | TORONTO BUTTONVILLE A | 9 | 22 | 13 | 21.225 | 0 | 3.225
6350 | TORONTO BUTTONVILLE A | 9 | 21 | 14 | 18.6 | 0 | 0.6
6350 | TORONTO BUTTONVILLE A | 9 | 22 | 14 | 22.1 | 0 | 4.1
6351 | TORONTO BUTTONVILLE A | 9 | 21 | 15 | 19.2 | 0 | 1.2
6351 | TORONTO BUTTONVILLE A | 9 | 22 | 15 | 22.3 | 0 | 4.3
6352 | TORONTO BUTTONVILLE A | 9 | 21 | 16 | 18.7 | 0 | 0.7
6352 | TORONTO BUTTONVILLE A | 9 | 22 | 16 | 22.05 | 0 | 4.05
6353 | TORONTO BUTTONVILLE A | 9 | 21 | 17 | 18.1 | 0 | 0.1
6353 | TORONTO BUTTONVILLE A | 9 | 22 | 17 | 21.875 | 0 | 3.875
6354 | TORONTO BUTTONVILLE A | 9 | 21 | 18 | 16.8 | 1.2 | 0
6354 | TORONTO BUTTONVILLE A | 9 | 22 | 18 | 20.9 | 0 | 2.9
6355 | TORONTO BUTTONVILLE A | 9 | 21 | 19 | 14.9 | 3.1 | 0
6355 | TORONTO BUTTONVILLE A | 9 | 22 | 19 | 19.65 | 0 | 1.65
6356 | TORONTO BUTTONVILLE A | 9 | 21 | 20 | 13.6 | 4.4 | 0
6356 | TORONTO BUTTONVILLE A | 9 | 22 | 20 | 18.65 | 0 | 0.65
6357 | TORONTO BUTTONVILLE A | 9 | 21 | 21 | 12.9 | 5.1 | 0
6357 | TORONTO BUTTONVILLE A | 9 | 22 | 21 | 18.1 | 0 | 0.1
6358 | TORONTO BUTTONVILLE A | 9 | 21 | 22 | 10.5 | 7.5 | 0
6358 | TORONTO BUTTONVILLE A | 9 | 22 | 22 | 17.2 | 0.8 | 0
6359 | TORONTO BUTTONVILLE A | 9 | 21 | 23 | 8.8 | 9.2 | 0
6359 | TORONTO BUTTONVILLE A | 9 | 22 | 23 | 16.525 | 1.475 | 0
6360 | TORONTO BUTTONVILLE A | 9 | 21 | 24 | 8.8 | 9.2 | 0
6360 | TORONTO BUTTONVILLE A | 9 | 22 | 24 | 16.2 | 1.8 | 0
6361 | TORONTO BUTTONVILLE A | 9 | 22 | 1 | 7.5 | 10.5 | 0
6361 | TORONTO BUTTONVILLE A | 9 | 23 | 1 | 15.425 | 2.575 | 0
6362 | TORONTO BUTTONVILLE A | 9 | 22 | 2 | 7.2 | 10.8 | 0
6362 | TORONTO BUTTONVILLE A | 9 | 23 | 2 | 15.45 | 2.55 | 0
6363 | TORONTO BUTTONVILLE A | 9 | 22 | 3 | 6.2 | 11.8 | 0
6363 | TORONTO BUTTONVILLE A | 9 | 23 | 3 | 14.95 | 3.05 | 0
6364 | TORONTO BUTTONVILLE A | 9 | 22 | 4 | 6.6 | 11.4 | 0
6364 | TORONTO BUTTONVILLE A | 9 | 23 | 4 | 14.575 | 3.425 | 0
6365 | TORONTO BUTTONVILLE A | 9 | 22 | 5 | 6.4 | 11.6 | 0
6365 | TORONTO BUTTONVILLE A | 9 | 23 | 5 | 14.35 | 3.65 | 0
6366 | TORONTO BUTTONVILLE A | 9 | 22 | 6 | 6.4 | 11.6 | 0
6366 | TORONTO BUTTONVILLE A | 9 | 23 | 6 | 14.25 | 3.75 | 0
6367 | TORONTO BUTTONVILLE A | 9 | 22 | 7 | 6.5 | 11.5 | 0
6367 | TORONTO BUTTONVILLE A | 9 | 23 | 7 | 14.075 | 3.925 | 0
6368 | TORONTO BUTTONVILLE A | 9 | 22 | 8 | 6.6 | 11.4 | 0
6368 | TORONTO BUTTONVILLE A | 9 | 23 | 8 | 15.35 | 2.65 | 0
6369 | TORONTO BUTTONVILLE A | 9 | 22 | 9 | 11.1 | 6.9 | 0
6369 | TORONTO BUTTONVILLE A | 9 | 23 | 9 | 17.575 | 0.425 | 0
6370 | TORONTO BUTTONVILLE A | 9 | 22 | 10 | 14.4 | 3.6 | 0
6370 | TORONTO BUTTONVILLE A | 9 | 23 | 10 | 19.375 | 0 | 1.375
6371 | TORONTO BUTTONVILLE A | 9 | 22 | 11 | 17.1 | 0.9 | 0
6371 | TORONTO BUTTONVILLE A | 9 | 23 | 11 | 21.075 | 0 | 3.075
6372 | TORONTO BUTTONVILLE A | 9 | 22 | 12 | 18.5 | 0 | 0.5
6372 | TORONTO BUTTONVILLE A | 9 | 23 | 12 | 21.45 | 0 | 3.45
6373 | TORONTO BUTTONVILLE A | 9 | 22 | 13 | 19.9 | 0 | 1.9
6373 | TORONTO BUTTONVILLE A | 9 | 23 | 13 | 21.175 | 0 | 3.175
6374 | TORONTO BUTTONVILLE A | 9 | 22 | 14 | 21.1 | 0 | 3.1
6374 | TORONTO BUTTONVILLE A | 9 | 23 | 14 | 22.325 | 0 | 4.325
6375 | TORONTO BUTTONVILLE A | 9 | 22 | 15 | 21.1 | 0 | 3.1
6375 | TORONTO BUTTONVILLE A | 9 | 23 | 15 | 22.725 | 0 | 4.725
6376 | TORONTO BUTTONVILLE A | 9 | 22 | 16 | 21.1 | 0 | 3.1
6376 | TORONTO BUTTONVILLE A | 9 | 23 | 16 | 23.1 | 0 | 5.1
6377 | TORONTO BUTTONVILLE A | 9 | 22 | 17 | 21.1 | 0 | 3.1
6377 | TORONTO BUTTONVILLE A | 9 | 23 | 17 | 21.85 | 0 | 3.85
6378 | TORONTO BUTTONVILLE A | 9 | 22 | 18 | 20.3 | 0 | 2.3
6378 | TORONTO BUTTONVILLE A | 9 | 23 | 18 | 20.975 | 0 | 2.975
6379 | TORONTO BUTTONVILLE A | 9 | 22 | 19 | 18.6 | 0 | 0.6
6379 | TORONTO BUTTONVILLE A | 9 | 23 | 19 | 19.5 | 0 | 1.5
6380 | TORONTO BUTTONVILLE A | 9 | 22 | 20 | 16.7 | 1.3 | 0
6380 | TORONTO BUTTONVILLE A | 9 | 23 | 20 | 18.25 | 0 | 0.25
6381 | TORONTO BUTTONVILLE A | 9 | 22 | 21 | 16.2 | 1.8 | 0
6381 | TORONTO BUTTONVILLE A | 9 | 23 | 21 | 17.3 | 0.7 | 0
6382 | TORONTO BUTTONVILLE A | 9 | 22 | 22 | 16.4 | 1.6 | 0
6382 | TORONTO BUTTONVILLE A | 9 | 23 | 22 | 16.325 | 1.675 | 0
6383 | TORONTO BUTTONVILLE A | 9 | 22 | 23 | 15.2 | 2.8 | 0
6383 | TORONTO BUTTONVILLE A | 9 | 23 | 23 | 15.725 | 2.275 | 0
6384 | TORONTO BUTTONVILLE A | 9 | 22 | 24 | 14.8 | 3.2 | 0
6384 | TORONTO BUTTONVILLE A | 9 | 23 | 24 | 15.55 | 2.45 | 0
6385 | TORONTO BUTTONVILLE A | 9 | 23 | 1 | 13.1 | 4.9 | 0
6385 | TORONTO BUTTONVILLE A | 9 | 24 | 1 | 14.7 | 3.3 | 0
6386 | TORONTO BUTTONVILLE A | 9 | 23 | 2 | 12.7 | 5.3 | 0
6386 | TORONTO BUTTONVILLE A | 9 | 24 | 2 | 14.725 | 3.275 | 0
6387 | TORONTO BUTTONVILLE A | 9 | 23 | 3 | 15.7 | 2.3 | 0
6387 | TORONTO BUTTONVILLE A | 9 | 24 | 3 | 14.175 | 3.825 | 0
6388 | TORONTO BUTTONVILLE A | 9 | 23 | 4 | 15.1 | 2.9 | 0
6388 | TORONTO BUTTONVILLE A | 9 | 24 | 4 | 13.6 | 4.4 | 0
6389 | TORONTO BUTTONVILLE A | 9 | 23 | 5 | 14.3 | 3.7 | 0
6389 | TORONTO BUTTONVILLE A | 9 | 24 | 5 | 13.2 | 4.8 | 0
6390 | TORONTO BUTTONVILLE A | 9 | 23 | 6 | 14.8 | 3.2 | 0
6390 | TORONTO BUTTONVILLE A | 9 | 24 | 6 | 12.975 | 5.025 | 0
6391 | TORONTO BUTTONVILLE A | 9 | 23 | 7 | 14.4 | 3.6 | 0
6391 | TORONTO BUTTONVILLE A | 9 | 24 | 7 | 12.95 | 5.05 | 0
6392 | TORONTO BUTTONVILLE A | 9 | 23 | 8 | 14.3 | 3.7 | 0
6392 | TORONTO BUTTONVILLE A | 9 | 24 | 8 | 13.625 | 4.375 | 0
6393 | TORONTO BUTTONVILLE A | 9 | 23 | 9 | 16.6 | 1.4 | 0
6393 | TORONTO BUTTONVILLE A | 9 | 24 | 9 | 14.825 | 3.175 | 0
6394 | TORONTO BUTTONVILLE A | 9 | 23 | 10 | 19 | 0 | 1
6394 | TORONTO BUTTONVILLE A | 9 | 24 | 10 | 16.575 | 1.425 | 0
6395 | TORONTO BUTTONVILLE A | 9 | 23 | 11 | 20.9 | 0 | 2.9
6395 | TORONTO BUTTONVILLE A | 9 | 24 | 11 | 17.925 | 0.075 | 0
6396 | TORONTO BUTTONVILLE A | 9 | 23 | 12 | 22.7 | 0 | 4.7
6396 | TORONTO BUTTONVILLE A | 9 | 24 | 12 | 19.275 | 0 | 1.275
6397 | TORONTO BUTTONVILLE A | 9 | 23 | 13 | 23.7 | 0 | 5.7
6397 | TORONTO BUTTONVILLE A | 9 | 24 | 13 | 20.525 | 0 | 2.525
6398 | TORONTO BUTTONVILLE A | 9 | 23 | 14 | 24.9 | 0 | 6.9
6398 | TORONTO BUTTONVILLE A | 9 | 24 | 14 | 21.375 | 0 | 3.375
6399 | TORONTO BUTTONVILLE A | 9 | 23 | 15 | 25.8 | 0 | 7.8
6399 | TORONTO BUTTONVILLE A | 9 | 24 | 15 | 21.4 | 0 | 3.4
6400 | TORONTO BUTTONVILLE A | 9 | 23 | 16 | 25.9 | 0 | 7.9
6400 | TORONTO BUTTONVILLE A | 9 | 24 | 16 | 21.25 | 0 | 3.25
6401 | TORONTO BUTTONVILLE A | 9 | 23 | 17 | 26.1 | 0 | 8.1
6401 | TORONTO BUTTONVILLE A | 9 | 24 | 17 | 21.15 | 0 | 3.15
6402 | TORONTO BUTTONVILLE A | 9 | 23 | 18 | 25 | 0 | 7
6402 | TORONTO BUTTONVILLE A | 9 | 24 | 18 | 20.85 | 0 | 2.85
6403 | TORONTO BUTTONVILLE A | 9 | 23 | 19 | 22.6 | 0 | 4.6
6403 | TORONTO BUTTONVILLE A | 9 | 24 | 19 | 19.6 | 0 | 1.6
6404 | TORONTO BUTTONVILLE A | 9 | 23 | 20 | 21 | 0 | 3
6404 | TORONTO BUTTONVILLE A | 9 | 24 | 20 | 18.675 | 0 | 0.675
6405 | TORONTO BUTTONVILLE A | 9 | 23 | 21 | 18.2 | 0 | 0.2
6405 | TORONTO BUTTONVILLE A | 9 | 24 | 21 | 18.05 | 0 | 0.05
6406 | TORONTO BUTTONVILLE A | 9 | 23 | 22 | 15.8 | 2.2 | 0
6406 | TORONTO BUTTONVILLE A | 9 | 24 | 22 | 16.525 | 1.475 | 0
6407 | TORONTO BUTTONVILLE A | 9 | 23 | 23 | 15.3 | 2.7 | 0
6407 | TORONTO BUTTONVILLE A | 9 | 24 | 23 | 15.775 | 2.225 | 0
6408 | TORONTO BUTTONVILLE A | 9 | 23 | 24 | 14.3 | 3.7 | 0
6408 | TORONTO BUTTONVILLE A | 9 | 24 | 24 | 15.025 | 2.975 | 0
6409 | TORONTO BUTTONVILLE A | 9 | 24 | 1 | 12.6 | 5.4 | 0
6409 | TORONTO BUTTONVILLE A | 9 | 25 | 1 | 14.15 | 3.85 | 0
6410 | TORONTO BUTTONVILLE A | 9 | 24 | 2 | 11.9 | 6.1 | 0
6410 | TORONTO BUTTONVILLE A | 9 | 25 | 2 | 13.5 | 4.5 | 0
6411 | TORONTO BUTTONVILLE A | 9 | 24 | 3 | 11.1 | 6.9 | 0
6411 | TORONTO BUTTONVILLE A | 9 | 25 | 3 | 13.525 | 4.475 | 0
6412 | TORONTO BUTTONVILLE A | 9 | 24 | 4 | 10.5 | 7.5 | 0
6412 | TORONTO BUTTONVILLE A | 9 | 25 | 4 | 13.5 | 4.5 | 0
6413 | TORONTO BUTTONVILLE A | 9 | 24 | 5 | 9.7 | 8.3 | 0
6413 | TORONTO BUTTONVILLE A | 9 | 25 | 5 | 13.75 | 4.25 | 0
6414 | TORONTO BUTTONVILLE A | 9 | 24 | 6 | 10.2 | 7.8 | 0
6414 | TORONTO BUTTONVILLE A | 9 | 25 | 6 | 13.65 | 4.35 | 0
6415 | TORONTO BUTTONVILLE A | 9 | 24 | 7 | 9.6 | 8.4 | 0
6415 | TORONTO BUTTONVILLE A | 9 | 25 | 7 | 14.1 | 3.9 | 0
6416 | TORONTO BUTTONVILLE A | 9 | 24 | 8 | 10.7 | 7.3 | 0
6416 | TORONTO BUTTONVILLE A | 9 | 25 | 8 | 14.9 | 3.1 | 0
6417 | TORONTO BUTTONVILLE A | 9 | 24 | 9 | 14.8 | 3.2 | 0
6417 | TORONTO BUTTONVILLE A | 9 | 25 | 9 | 17.35 | 0.65 | 0
6418 | TORONTO BUTTONVILLE A | 9 | 24 | 10 | 18.5 | 0 | 0.5
6418 | TORONTO BUTTONVILLE A | 9 | 25 | 10 | 20.375 | 0 | 2.375
6419 | TORONTO BUTTONVILLE A | 9 | 24 | 11 | 20.5 | 0 | 2.5
6419 | TORONTO BUTTONVILLE A | 9 | 25 | 11 | 22 | 0 | 4
6420 | TORONTO BUTTONVILLE A | 9 | 24 | 12 | 22.9 | 0 | 4.9
6420 | TORONTO BUTTONVILLE A | 9 | 25 | 12 | 23.025 | 0 | 5.025
6421 | TORONTO BUTTONVILLE A | 9 | 24 | 13 | 23.7 | 0 | 5.7
6421 | TORONTO BUTTONVILLE A | 9 | 25 | 13 | 23.475 | 0 | 5.475
6422 | TORONTO BUTTONVILLE A | 9 | 24 | 14 | 24.5 | 0 | 6.5
6422 | TORONTO BUTTONVILLE A | 9 | 25 | 14 | 24 | 0 | 6
6423 | TORONTO BUTTONVILLE A | 9 | 24 | 15 | 25.8 | 0 | 7.8
6423 | TORONTO BUTTONVILLE A | 9 | 25 | 15 | 24.325 | 0 | 6.325
6424 | TORONTO BUTTONVILLE A | 9 | 24 | 16 | 25.1 | 0 | 7.1
6424 | TORONTO BUTTONVILLE A | 9 | 25 | 16 | 23.2 | 0 | 5.2
6425 | TORONTO BUTTONVILLE A | 9 | 24 | 17 | 23.9 | 0 | 5.9
6425 | TORONTO BUTTONVILLE A | 9 | 25 | 17 | 22.475 | 0 | 4.475
6426 | TORONTO BUTTONVILLE A | 9 | 24 | 18 | 22.7 | 0 | 4.7
6426 | TORONTO BUTTONVILLE A | 9 | 25 | 18 | 21.975 | 0 | 3.975
6427 | TORONTO BUTTONVILLE A | 9 | 24 | 19 | 21.1 | 0 | 3.1
6427 | TORONTO BUTTONVILLE A | 9 | 25 | 19 | 21.2 | 0 | 3.2
6428 | TORONTO BUTTONVILLE A | 9 | 24 | 20 | 19.3 | 0 | 1.3
6428 | TORONTO BUTTONVILLE A | 9 | 25 | 20 | 20.6 | 0 | 2.6
6429 | TORONTO BUTTONVILLE A | 9 | 24 | 21 | 18.5 | 0 | 0.5
6429 | TORONTO BUTTONVILLE A | 9 | 25 | 21 | 19.975 | 0 | 1.975
6430 | TORONTO BUTTONVILLE A | 9 | 24 | 22 | 16.9 | 1.1 | 0
6430 | TORONTO BUTTONVILLE A | 9 | 25 | 22 | 19.375 | 0 | 1.375
6431 | TORONTO BUTTONVILLE A | 9 | 24 | 23 | 16.3 | 1.7 | 0
6431 | TORONTO BUTTONVILLE A | 9 | 25 | 23 | 18.925 | 0 | 0.925
6432 | TORONTO BUTTONVILLE A | 9 | 24 | 24 | 16.3 | 1.7 | 0
6432 | TORONTO BUTTONVILLE A | 9 | 25 | 24 | 18.075 | 0 | 0.075
6433 | TORONTO BUTTONVILLE A | 9 | 25 | 1 | 16.7 | 1.3 | 0
6433 | TORONTO BUTTONVILLE A | 9 | 26 | 1 | 18.05 | 0 | 0.05
6434 | TORONTO BUTTONVILLE A | 9 | 25 | 2 | 16.1 | 1.9 | 0
6434 | TORONTO BUTTONVILLE A | 9 | 26 | 2 | 17.45 | 0.55 | 0
6435 | TORONTO BUTTONVILLE A | 9 | 25 | 3 | 15.7 | 2.3 | 0
6435 | TORONTO BUTTONVILLE A | 9 | 26 | 3 | 17.325 | 0.675 | 0
6436 | TORONTO BUTTONVILLE A | 9 | 25 | 4 | 14.4 | 3.6 | 0
6436 | TORONTO BUTTONVILLE A | 9 | 26 | 4 | 17.1 | 0.9 | 0
6437 | TORONTO BUTTONVILLE A | 9 | 25 | 5 | 14.1 | 3.9 | 0
6437 | TORONTO BUTTONVILLE A | 9 | 26 | 5 | 16.7 | 1.3 | 0
6438 | TORONTO BUTTONVILLE A | 9 | 25 | 6 | 12.9 | 5.1 | 0
6438 | TORONTO BUTTONVILLE A | 9 | 26 | 6 | 16.1 | 1.9 | 0
6439 | TORONTO BUTTONVILLE A | 9 | 25 | 7 | 14.5 | 3.5 | 0
6439 | TORONTO BUTTONVILLE A | 9 | 26 | 7 | 16.125 | 1.875 | 0
6440 | TORONTO BUTTONVILLE A | 9 | 25 | 8 | 15.3 | 2.7 | 0
6440 | TORONTO BUTTONVILLE A | 9 | 26 | 8 | 16.5 | 1.5 | 0
6441 | TORONTO BUTTONVILLE A | 9 | 25 | 9 | 16.2 | 1.8 | 0
6441 | TORONTO BUTTONVILLE A | 9 | 26 | 9 | 17.625 | 0.375 | 0
6442 | TORONTO BUTTONVILLE A | 9 | 25 | 10 | 17.3 | 0.7 | 0
6442 | TORONTO BUTTONVILLE A | 9 | 26 | 10 | 19.15 | 0 | 1.15
6443 | TORONTO BUTTONVILLE A | 9 | 25 | 11 | 19.2 | 0 | 1.2
6443 | TORONTO BUTTONVILLE A | 9 | 26 | 11 | 19.85 | 0 | 1.85
6444 | TORONTO BUTTONVILLE A | 9 | 25 | 12 | 21 | 0 | 3
6444 | TORONTO BUTTONVILLE A | 9 | 26 | 12 | 21.375 | 0 | 3.375
6445 | TORONTO BUTTONVILLE A | 9 | 25 | 13 | 22.9 | 0 | 4.9
6445 | TORONTO BUTTONVILLE A | 9 | 26 | 13 | 20.825 | 0 | 2.825
6446 | TORONTO BUTTONVILLE A | 9 | 25 | 14 | 24.6 | 0 | 6.6
6446 | TORONTO BUTTONVILLE A | 9 | 26 | 14 | 21.95 | 0 | 3.95
6447 | TORONTO BUTTONVILLE A | 9 | 25 | 15 | 25.4 | 0 | 7.4
6447 | TORONTO BUTTONVILLE A | 9 | 26 | 15 | 20.85 | 0 | 2.85
6448 | TORONTO BUTTONVILLE A | 9 | 25 | 16 | 24.7 | 0 | 6.7
6448 | TORONTO BUTTONVILLE A | 9 | 26 | 16 | 21.125 | 0 | 3.125
6449 | TORONTO BUTTONVILLE A | 9 | 25 | 17 | 24.6 | 0 | 6.6
6449 | TORONTO BUTTONVILLE A | 9 | 26 | 17 | 21.125 | 0 | 3.125
6450 | TORONTO BUTTONVILLE A | 9 | 25 | 18 | 23.6 | 0 | 5.6
6450 | TORONTO BUTTONVILLE A | 9 | 26 | 18 | 20.4 | 0 | 2.4
6451 | TORONTO BUTTONVILLE A | 9 | 25 | 19 | 21.5 | 0 | 3.5
6451 | TORONTO BUTTONVILLE A | 9 | 26 | 19 | 19.075 | 0 | 1.075
6452 | TORONTO BUTTONVILLE A | 9 | 25 | 20 | 19.4 | 0 | 1.4
6452 | TORONTO BUTTONVILLE A | 9 | 26 | 20 | 17.85 | 0.15 | 0
6453 | TORONTO BUTTONVILLE A | 9 | 25 | 21 | 17 | 1 | 0
6453 | TORONTO BUTTONVILLE A | 9 | 26 | 21 | 16.925 | 1.075 | 0
6454 | TORONTO BUTTONVILLE A | 9 | 25 | 22 | 16.2 | 1.8 | 0
6454 | TORONTO BUTTONVILLE A | 9 | 26 | 22 | 16.125 | 1.875 | 0
6455 | TORONTO BUTTONVILLE A | 9 | 25 | 23 | 16.2 | 1.8 | 0
6455 | TORONTO BUTTONVILLE A | 9 | 26 | 23 | 15.475 | 2.525 | 0
6456 | TORONTO BUTTONVILLE A | 9 | 25 | 24 | 15.4 | 2.6 | 0
6456 | TORONTO BUTTONVILLE A | 9 | 26 | 24 | 14 | 4 | 0
6457 | TORONTO BUTTONVILLE A | 9 | 26 | 1 | 15.9 | 2.1 | 0
6457 | TORONTO BUTTONVILLE A | 9 | 27 | 1 | 13.8 | 4.2 | 0
6458 | TORONTO BUTTONVILLE A | 9 | 26 | 2 | 15.4 | 2.6 | 0
6458 | TORONTO BUTTONVILLE A | 9 | 27 | 2 | 13.45 | 4.55 | 0
6459 | TORONTO BUTTONVILLE A | 9 | 26 | 3 | 14.9 | 3.1 | 0
6459 | TORONTO BUTTONVILLE A | 9 | 27 | 3 | 13.5 | 4.5 | 0
6460 | TORONTO BUTTONVILLE A | 9 | 26 | 4 | 14.9 | 3.1 | 0
6460 | TORONTO BUTTONVILLE A | 9 | 27 | 4 | 13.175 | 4.825 | 0
6461 | TORONTO BUTTONVILLE A | 9 | 26 | 5 | 13.5 | 4.5 | 0
6461 | TORONTO BUTTONVILLE A | 9 | 27 | 5 | 12.575 | 5.425 | 0
6462 | TORONTO BUTTONVILLE A | 9 | 26 | 6 | 13.7 | 4.3 | 0
6462 | TORONTO BUTTONVILLE A | 9 | 27 | 6 | 12.575 | 5.425 | 0
6463 | TORONTO BUTTONVILLE A | 9 | 26 | 7 | 13.8 | 4.2 | 0
6463 | TORONTO BUTTONVILLE A | 9 | 27 | 7 | 12.425 | 5.575 | 0
6464 | TORONTO BUTTONVILLE A | 9 | 26 | 8 | 13.4 | 4.6 | 0
6464 | TORONTO BUTTONVILLE A | 9 | 27 | 8 | 13.15 | 4.85 | 0
6465 | TORONTO BUTTONVILLE A | 9 | 26 | 9 | 14.3 | 3.7 | 0
6465 | TORONTO BUTTONVILLE A | 9 | 27 | 9 | 16.075 | 1.925 | 0
6466 | TORONTO BUTTONVILLE A | 9 | 26 | 10 | 16.6 | 1.4 | 0
6466 | TORONTO BUTTONVILLE A | 9 | 27 | 10 | 18.225 | 0 | 0.225
6467 | TORONTO BUTTONVILLE A | 9 | 26 | 11 | 20.6 | 0 | 2.6
6467 | TORONTO BUTTONVILLE A | 9 | 27 | 11 | 20.075 | 0 | 2.075
6468 | TORONTO BUTTONVILLE A | 9 | 26 | 12 | 23.9 | 0 | 5.9
6468 | TORONTO BUTTONVILLE A | 9 | 27 | 12 | 21.275 | 0 | 3.275
6469 | TORONTO BUTTONVILLE A | 9 | 26 | 13 | 24.6 | 0 | 6.6
6469 | TORONTO BUTTONVILLE A | 9 | 27 | 13 | 21.9 | 0 | 3.9
6470 | TORONTO BUTTONVILLE A | 9 | 26 | 14 | 24.1 | 0 | 6.1
6470 | TORONTO BUTTONVILLE A | 9 | 27 | 14 | 21.05 | 0 | 3.05
6471 | TORONTO BUTTONVILLE A | 9 | 26 | 15 | 24.4 | 0 | 6.4
6471 | TORONTO BUTTONVILLE A | 9 | 27 | 15 | 20.85 | 0 | 2.85
6472 | TORONTO BUTTONVILLE A | 9 | 26 | 16 | 24.5 | 0 | 6.5
6472 | TORONTO BUTTONVILLE A | 9 | 27 | 16 | 21.025 | 0 | 3.025
6473 | TORONTO BUTTONVILLE A | 9 | 26 | 17 | 25.2 | 0 | 7.2
6473 | TORONTO BUTTONVILLE A | 9 | 27 | 17 | 20.575 | 0 | 2.575
6474 | TORONTO BUTTONVILLE A | 9 | 26 | 18 | 24 | 0 | 6
6474 | TORONTO BUTTONVILLE A | 9 | 27 | 18 | 19.55 | 0 | 1.55
6475 | TORONTO BUTTONVILLE A | 9 | 26 | 19 | 22.7 | 0 | 4.7
6475 | TORONTO BUTTONVILLE A | 9 | 27 | 19 | 18.5 | 0 | 0.5
6476 | TORONTO BUTTONVILLE A | 9 | 26 | 20 | 21.1 | 0 | 3.1
6476 | TORONTO BUTTONVILLE A | 9 | 27 | 20 | 17.325 | 0.675 | 0
6477 | TORONTO BUTTONVILLE A | 9 | 26 | 21 | 20.8 | 0 | 2.8
6477 | TORONTO BUTTONVILLE A | 9 | 27 | 21 | 16.7 | 1.3 | 0
6478 | TORONTO BUTTONVILLE A | 9 | 26 | 22 | 20 | 0 | 2
6478 | TORONTO BUTTONVILLE A | 9 | 27 | 22 | 16 | 2 | 0
6479 | TORONTO BUTTONVILLE A | 9 | 26 | 23 | 20 | 0 | 2
6479 | TORONTO BUTTONVILLE A | 9 | 27 | 23 | 15.3 | 2.7 | 0
6480 | TORONTO BUTTONVILLE A | 9 | 26 | 24 | 19.1 | 0 | 1.1
6480 | TORONTO BUTTONVILLE A | 9 | 27 | 24 | 14.725 | 3.275 | 0
6481 | TORONTO BUTTONVILLE A | 9 | 27 | 1 | 19 | 0 | 1
6481 | TORONTO BUTTONVILLE A | 9 | 28 | 1 | 13.7 | 4.3 | 0
6482 | TORONTO BUTTONVILLE A | 9 | 27 | 2 | 19.1 | 0 | 1.1
6482 | TORONTO BUTTONVILLE A | 9 | 28 | 2 | 13.15 | 4.85 | 0
6483 | TORONTO BUTTONVILLE A | 9 | 27 | 3 | 19.3 | 0 | 1.3
6483 | TORONTO BUTTONVILLE A | 9 | 28 | 3 | 12.85 | 5.15 | 0
6484 | TORONTO BUTTONVILLE A | 9 | 27 | 4 | 19.3 | 0 | 1.3
6484 | TORONTO BUTTONVILLE A | 9 | 28 | 4 | 12.125 | 5.875 | 0
6485 | TORONTO BUTTONVILLE A | 9 | 27 | 5 | 19.2 | 0 | 1.2
6485 | TORONTO BUTTONVILLE A | 9 | 28 | 5 | 12.175 | 5.825 | 0
6486 | TORONTO BUTTONVILLE A | 9 | 27 | 6 | 19.2 | 0 | 1.2
6486 | TORONTO BUTTONVILLE A | 9 | 28 | 6 | 12.275 | 5.725 | 0
6487 | TORONTO BUTTONVILLE A | 9 | 27 | 7 | 19.1 | 0 | 1.1
6487 | TORONTO BUTTONVILLE A | 9 | 28 | 7 | 11.975 | 6.025 | 0
6488 | TORONTO BUTTONVILLE A | 9 | 27 | 8 | 19.3 | 0 | 1.3
6488 | TORONTO BUTTONVILLE A | 9 | 28 | 8 | 12.6 | 5.4 | 0
6489 | TORONTO BUTTONVILLE A | 9 | 27 | 9 | 19.9 | 0 | 1.9
6489 | TORONTO BUTTONVILLE A | 9 | 28 | 9 | 14.2 | 3.8 | 0
6490 | TORONTO BUTTONVILLE A | 9 | 27 | 10 | 20.8 | 0 | 2.8
6490 | TORONTO BUTTONVILLE A | 9 | 28 | 10 | 15.7 | 2.3 | 0
6491 | TORONTO BUTTONVILLE A | 9 | 27 | 11 | 22.1 | 0 | 4.1
6491 | TORONTO BUTTONVILLE A | 9 | 28 | 11 | 16.475 | 1.525 | 0
6492 | TORONTO BUTTONVILLE A | 9 | 27 | 12 | 24.3 | 0 | 6.3
6492 | TORONTO BUTTONVILLE A | 9 | 28 | 12 | 17.15 | 0.85 | 0
6493 | TORONTO BUTTONVILLE A | 9 | 27 | 13 | 24.9 | 0 | 6.9
6493 | TORONTO BUTTONVILLE A | 9 | 28 | 13 | 17.2 | 0.8 | 0
6494 | TORONTO BUTTONVILLE A | 9 | 27 | 14 | 25.2 | 0 | 7.2
6494 | TORONTO BUTTONVILLE A | 9 | 28 | 14 | 17.6 | 0.4 | 0
6495 | TORONTO BUTTONVILLE A | 9 | 27 | 15 | 25.4 | 0 | 7.4
6495 | TORONTO BUTTONVILLE A | 9 | 28 | 15 | 18.275 | 0 | 0.275
6496 | TORONTO BUTTONVILLE A | 9 | 27 | 16 | 25.3 | 0 | 7.3
6496 | TORONTO BUTTONVILLE A | 9 | 28 | 16 | 17.75 | 0.25 | 0
6497 | TORONTO BUTTONVILLE A | 9 | 27 | 17 | 25.6 | 0 | 7.6
6497 | TORONTO BUTTONVILLE A | 9 | 28 | 17 | 17 | 1 | 0
6498 | TORONTO BUTTONVILLE A | 9 | 27 | 18 | 23.6 | 0 | 5.6
6498 | TORONTO BUTTONVILLE A | 9 | 28 | 18 | 15.625 | 2.375 | 0
6499 | TORONTO BUTTONVILLE A | 9 | 27 | 19 | 22.9 | 0 | 4.9
6499 | TORONTO BUTTONVILLE A | 9 | 28 | 19 | 14.45 | 3.55 | 0
6500 | TORONTO BUTTONVILLE A | 9 | 27 | 20 | 22.3 | 0 | 4.3
6500 | TORONTO BUTTONVILLE A | 9 | 28 | 20 | 13.375 | 4.625 | 0
6501 | TORONTO BUTTONVILLE A | 9 | 27 | 21 | 21.7 | 0 | 3.7
6501 | TORONTO BUTTONVILLE A | 9 | 28 | 21 | 12.125 | 5.875 | 0
6502 | TORONTO BUTTONVILLE A | 9 | 27 | 22 | 21.1 | 0 | 3.1
6502 | TORONTO BUTTONVILLE A | 9 | 28 | 22 | 11.575 | 6.425 | 0
6503 | TORONTO BUTTONVILLE A | 9 | 27 | 23 | 22.1 | 0 | 4.1
6503 | TORONTO BUTTONVILLE A | 9 | 28 | 23 | 11 | 7 | 0
6504 | TORONTO BUTTONVILLE A | 9 | 27 | 24 | 21.3 | 0 | 3.3
6504 | TORONTO BUTTONVILLE A | 9 | 28 | 24 | 10.575 | 7.425 | 0
6505 | TORONTO BUTTONVILLE A | 9 | 28 | 1 | 20.5 | 0 | 2.5
6505 | TORONTO BUTTONVILLE A | 9 | 29 | 1 | 9.925 | 8.075 | 0
6506 | TORONTO BUTTONVILLE A | 9 | 28 | 2 | 20.5 | 0 | 2.5
6506 | TORONTO BUTTONVILLE A | 9 | 29 | 2 | 9.75 | 8.25 | 0
6507 | TORONTO BUTTONVILLE A | 9 | 28 | 3 | 19.8 | 0 | 1.8
6507 | TORONTO BUTTONVILLE A | 9 | 29 | 3 | 9.45 | 8.55 | 0
6508 | TORONTO BUTTONVILLE A | 9 | 28 | 4 | 19.6 | 0 | 1.6
6508 | TORONTO BUTTONVILLE A | 9 | 29 | 4 | 8.675 | 9.325 | 0
6509 | TORONTO BUTTONVILLE A | 9 | 28 | 5 | 18.6 | 0 | 0.6
6509 | TORONTO BUTTONVILLE A | 9 | 29 | 5 | 8.3 | 9.7 | 0
6510 | TORONTO BUTTONVILLE A | 9 | 28 | 6 | 17.7 | 0.3 | 0
6510 | TORONTO BUTTONVILLE A | 9 | 29 | 6 | 8.425 | 9.575 | 0
6511 | TORONTO BUTTONVILLE A | 9 | 28 | 7 | 17.6 | 0.4 | 0
6511 | TORONTO BUTTONVILLE A | 9 | 29 | 7 | 8.575 | 9.425 | 0
6512 | TORONTO BUTTONVILLE A | 9 | 28 | 8 | 18.5 | 0 | 0.5
6512 | TORONTO BUTTONVILLE A | 9 | 29 | 8 | 9.05 | 8.95 | 0
6513 | TORONTO BUTTONVILLE A | 9 | 28 | 9 | 19.8 | 0 | 1.8
6513 | TORONTO BUTTONVILLE A | 9 | 29 | 9 | 10.975 | 7.025 | 0
6514 | TORONTO BUTTONVILLE A | 9 | 28 | 10 | 21.5 | 0 | 3.5
6514 | TORONTO BUTTONVILLE A | 9 | 29 | 10 | 12.175 | 5.825 | 0
6515 | TORONTO BUTTONVILLE A | 9 | 28 | 11 | 22.4 | 0 | 4.4
6515 | TORONTO BUTTONVILLE A | 9 | 29 | 11 | 13.5 | 4.5 | 0
6516 | TORONTO BUTTONVILLE A | 9 | 28 | 12 | 23.6 | 0 | 5.6
6516 | TORONTO BUTTONVILLE A | 9 | 29 | 12 | 14.1 | 3.9 | 0
6517 | TORONTO BUTTONVILLE A | 9 | 28 | 13 | 25 | 0 | 7
6517 | TORONTO BUTTONVILLE A | 9 | 29 | 13 | 14.6 | 3.4 | 0
6518 | TORONTO BUTTONVILLE A | 9 | 28 | 14 | 24.8 | 0 | 6.8
6518 | TORONTO BUTTONVILLE A | 9 | 29 | 14 | 15.375 | 2.625 | 0
6519 | TORONTO BUTTONVILLE A | 9 | 28 | 15 | 25.4 | 0 | 7.4
6519 | TORONTO BUTTONVILLE A | 9 | 29 | 15 | 15.7 | 2.3 | 0
6520 | TORONTO BUTTONVILLE A | 9 | 28 | 16 | 25.2 | 0 | 7.2
6520 | TORONTO BUTTONVILLE A | 9 | 29 | 16 | 15.825 | 2.175 | 0
6521 | TORONTO BUTTONVILLE A | 9 | 28 | 17 | 24.7 | 0 | 6.7
6521 | TORONTO BUTTONVILLE A | 9 | 29 | 17 | 15.325 | 2.675 | 0
6522 | TORONTO BUTTONVILLE A | 9 | 28 | 18 | 23.7 | 0 | 5.7
6522 | TORONTO BUTTONVILLE A | 9 | 29 | 18 | 14.075 | 3.925 | 0
6523 | TORONTO BUTTONVILLE A | 9 | 28 | 19 | 23.4 | 0 | 5.4
6523 | TORONTO BUTTONVILLE A | 9 | 29 | 19 | 12.6 | 5.4 | 0
6524 | TORONTO BUTTONVILLE A | 9 | 28 | 20 | 23.2 | 0 | 5.2
6524 | TORONTO BUTTONVILLE A | 9 | 29 | 20 | 11.8 | 6.2 | 0
6525 | TORONTO BUTTONVILLE A | 9 | 28 | 21 | 20.7 | 0 | 2.7
6525 | TORONTO BUTTONVILLE A | 9 | 29 | 21 | 11.1 | 6.9 | 0
6526 | TORONTO BUTTONVILLE A | 9 | 28 | 22 | 19.2 | 0 | 1.2
6526 | TORONTO BUTTONVILLE A | 9 | 29 | 22 | 10.525 | 7.475 | 0
6527 | TORONTO BUTTONVILLE A | 9 | 28 | 23 | 19.1 | 0 | 1.1
6527 | TORONTO BUTTONVILLE A | 9 | 29 | 23 | 10.125 | 7.875 | 0
6528 | TORONTO BUTTONVILLE A | 9 | 28 | 24 | 18.8 | 0 | 0.8
6528 | TORONTO BUTTONVILLE A | 9 | 29 | 24 | 9.575 | 8.425 | 0
6529 | TORONTO BUTTONVILLE A | 9 | 29 | 1 | 15.4 | 2.6 | 0
6529 | TORONTO BUTTONVILLE A | 9 | 30 | 1 | 9.55 | 8.45 | 0
6530 | TORONTO BUTTONVILLE A | 9 | 29 | 2 | 14.5 | 3.5 | 0
6530 | TORONTO BUTTONVILLE A | 9 | 30 | 2 | 9.25 | 8.75 | 0
6531 | TORONTO BUTTONVILLE A | 9 | 29 | 3 | 14.2 | 3.8 | 0
6531 | TORONTO BUTTONVILLE A | 9 | 30 | 3 | 9.5 | 8.5 | 0
6532 | TORONTO BUTTONVILLE A | 9 | 29 | 4 | 13.4 | 4.6 | 0
6532 | TORONTO BUTTONVILLE A | 9 | 30 | 4 | 9.5 | 8.5 | 0
6533 | TORONTO BUTTONVILLE A | 9 | 29 | 5 | 13.4 | 4.6 | 0
6533 | TORONTO BUTTONVILLE A | 9 | 30 | 5 | 8.975 | 9.025 | 0
6534 | TORONTO BUTTONVILLE A | 9 | 29 | 6 | 13.2 | 4.8 | 0
6534 | TORONTO BUTTONVILLE A | 9 | 30 | 6 | 8.5 | 9.5 | 0
6535 | TORONTO BUTTONVILLE A | 9 | 29 | 7 | 12.8 | 5.2 | 0
6535 | TORONTO BUTTONVILLE A | 9 | 30 | 7 | 8.175 | 9.825 | 0
6536 | TORONTO BUTTONVILLE A | 9 | 29 | 8 | 12.8 | 5.2 | 0
6536 | TORONTO BUTTONVILLE A | 9 | 30 | 8 | 8.825 | 9.175 | 0
6537 | TORONTO BUTTONVILLE A | 9 | 29 | 9 | 13.4 | 4.6 | 0
6537 | TORONTO BUTTONVILLE A | 9 | 30 | 9 | 10.25 | 7.75 | 0
6538 | TORONTO BUTTONVILLE A | 9 | 29 | 10 | 14.7 | 3.3 | 0
6538 | TORONTO BUTTONVILLE A | 9 | 30 | 10 | 11.6 | 6.4 | 0
6539 | TORONTO BUTTONVILLE A | 9 | 29 | 11 | 15.1 | 2.9 | 0
6539 | TORONTO BUTTONVILLE A | 9 | 30 | 11 | 12.075 | 5.925 | 0
6540 | TORONTO BUTTONVILLE A | 9 | 29 | 12 | 16.3 | 1.7 | 0
6540 | TORONTO BUTTONVILLE A | 9 | 30 | 12 | 12.875 | 5.125 | 0
6541 | TORONTO BUTTONVILLE A | 9 | 29 | 13 | 16.9 | 1.1 | 0
6541 | TORONTO BUTTONVILLE A | 9 | 30 | 13 | 13.375 | 4.625 | 0
6542 | TORONTO BUTTONVILLE A | 9 | 29 | 14 | 17.5 | 0.5 | 0
6542 | TORONTO BUTTONVILLE A | 9 | 30 | 14 | 13.675 | 4.325 | 0
6543 | TORONTO BUTTONVILLE A | 9 | 29 | 15 | 17.4 | 0.6 | 0
6543 | TORONTO BUTTONVILLE A | 9 | 30 | 15 | 13.8 | 4.2 | 0
6544 | TORONTO BUTTONVILLE A | 9 | 29 | 16 | 18.1 | 0 | 0.1
6544 | TORONTO BUTTONVILLE A | 9 | 30 | 16 | 13.925 | 4.075 | 0
6545 | TORONTO BUTTONVILLE A | 9 | 29 | 17 | 18.2 | 0 | 0.2
6545 | TORONTO BUTTONVILLE A | 9 | 30 | 17 | 13.625 | 4.375 | 0
6546 | TORONTO BUTTONVILLE A | 9 | 29 | 18 | 17.4 | 0.6 | 0
6546 | TORONTO BUTTONVILLE A | 9 | 30 | 18 | 13.175 | 4.825 | 0
6547 | TORONTO BUTTONVILLE A | 9 | 29 | 19 | 16.9 | 1.1 | 0
6547 | TORONTO BUTTONVILLE A | 9 | 30 | 19 | 12.325 | 5.675 | 0
6548 | TORONTO BUTTONVILLE A | 9 | 29 | 20 | 16 | 2 | 0
6548 | TORONTO BUTTONVILLE A | 9 | 30 | 20 | 11.65 | 6.35 | 0
6549 | TORONTO BUTTONVILLE A | 9 | 29 | 21 | 14.5 | 3.5 | 0
6549 | TORONTO BUTTONVILLE A | 9 | 30 | 21 | 11.175 | 6.825 | 0
6550 | TORONTO BUTTONVILLE A | 9 | 29 | 22 | 13.7 | 4.3 | 0
6550 | TORONTO BUTTONVILLE A | 9 | 30 | 22 | 11.075 | 6.925 | 0
6551 | TORONTO BUTTONVILLE A | 9 | 29 | 23 | 14 | 4 | 0
6551 | TORONTO BUTTONVILLE A | 9 | 30 | 23 | 10.825 | 7.175 | 0
6552 | TORONTO BUTTONVILLE A | 9 | 29 | 24 | 13.8 | 4.2 | 0
6552 | TORONTO BUTTONVILLE A | 9 | 30 | 24 | 10.7 | 7.3 | 0
6553 | TORONTO BUTTONVILLE A | 9 | 30 | 1 | 13.2 | 4.8 | 0
6553 | TORONTO BUTTONVILLE A | 10 | 1 | 1 | 10.45 | 7.55 | 0
6554 | TORONTO BUTTONVILLE A | 9 | 30 | 2 | 12.8 | 5.2 | 0
6554 | TORONTO BUTTONVILLE A | 10 | 1 | 2 | 10.075 | 7.925 | 0
6555 | TORONTO BUTTONVILLE A | 9 | 30 | 3 | 12.5 | 5.5 | 0
6555 | TORONTO BUTTONVILLE A | 10 | 1 | 3 | 9.825 | 8.175 | 0
6556 | TORONTO BUTTONVILLE A | 9 | 30 | 4 | 12.3 | 5.7 | 0
6556 | TORONTO BUTTONVILLE A | 10 | 1 | 4 | 9 | 9 | 0
6557 | TORONTO BUTTONVILLE A | 9 | 30 | 5 | 12.1 | 5.9 | 0
6557 | TORONTO BUTTONVILLE A | 10 | 1 | 5 | 9.075 | 8.925 | 0
6558 | TORONTO BUTTONVILLE A | 9 | 30 | 6 | 11.6 | 6.4 | 0
6558 | TORONTO BUTTONVILLE A | 10 | 1 | 6 | 8.425 | 9.575 | 0
6559 | TORONTO BUTTONVILLE A | 9 | 30 | 7 | 10.9 | 7.1 | 0
6559 | TORONTO BUTTONVILLE A | 10 | 1 | 7 | 8.35 | 9.65 | 0
6560 | TORONTO BUTTONVILLE A | 9 | 30 | 8 | 11.2 | 6.8 | 0
6560 | TORONTO BUTTONVILLE A | 10 | 1 | 8 | 9.1 | 8.9 | 0
6561 | TORONTO BUTTONVILLE A | 9 | 30 | 9 | 12.9 | 5.1 | 0
6561 | TORONTO BUTTONVILLE A | 10 | 1 | 9 | 11.6 | 6.4 | 0
6562 | TORONTO BUTTONVILLE A | 9 | 30 | 10 | 13.1 | 4.9 | 0
6562 | TORONTO BUTTONVILLE A | 10 | 1 | 10 | 14.4 | 3.6 | 0
6563 | TORONTO BUTTONVILLE A | 9 | 30 | 11 | 13.7 | 4.3 | 0
6563 | TORONTO BUTTONVILLE A | 10 | 1 | 11 | 15.775 | 2.225 | 0
6564 | TORONTO BUTTONVILLE A | 9 | 30 | 12 | 14 | 4 | 0
6564 | TORONTO BUTTONVILLE A | 10 | 1 | 12 | 17.15 | 0.85 | 0
6565 | TORONTO BUTTONVILLE A | 9 | 30 | 13 | 15.9 | 2.1 | 0
6565 | TORONTO BUTTONVILLE A | 10 | 1 | 13 | 18.325 | 0 | 0.325
6566 | TORONTO BUTTONVILLE A | 9 | 30 | 14 | 16.4 | 1.6 | 0
6566 | TORONTO BUTTONVILLE A | 10 | 1 | 14 | 18.825 | 0 | 0.825
6567 | TORONTO BUTTONVILLE A | 9 | 30 | 15 | 18 | 0 | 0
6567 | TORONTO BUTTONVILLE A | 10 | 1 | 15 | 18.975 | 0 | 0.975
6568 | TORONTO BUTTONVILLE A | 9 | 30 | 16 | 13.8 | 4.2 | 0
6568 | TORONTO BUTTONVILLE A | 10 | 1 | 16 | 18.4 | 0 | 0.4
6569 | TORONTO BUTTONVILLE A | 9 | 30 | 17 | 12.7 | 5.3 | 0
6569 | TORONTO BUTTONVILLE A | 10 | 1 | 17 | 16.975 | 1.025 | 0
6570 | TORONTO BUTTONVILLE A | 9 | 30 | 18 | 11.4 | 6.6 | 0
6570 | TORONTO BUTTONVILLE A | 10 | 1 | 18 | 16.425 | 1.575 | 0
6571 | TORONTO BUTTONVILLE A | 9 | 30 | 19 | 11.4 | 6.6 | 0
6571 | TORONTO BUTTONVILLE A | 10 | 1 | 19 | 15.5 | 2.5 | 0
6572 | TORONTO BUTTONVILLE A | 9 | 30 | 20 | 11 | 7 | 0
6572 | TORONTO BUTTONVILLE A | 10 | 1 | 20 | 14.925 | 3.075 | 0
6573 | TORONTO BUTTONVILLE A | 9 | 30 | 21 | 11 | 7 | 0
6573 | TORONTO BUTTONVILLE A | 10 | 1 | 21 | 14 | 4 | 0
6574 | TORONTO BUTTONVILLE A | 9 | 30 | 22 | 10.6 | 7.4 | 0
6574 | TORONTO BUTTONVILLE A | 10 | 1 | 22 | 13.35 | 4.65 | 0
6575 | TORONTO BUTTONVILLE A | 9 | 30 | 23 | 10.9 | 7.1 | 0
6575 | TORONTO BUTTONVILLE A | 10 | 1 | 23 | 13.15 | 4.85 | 0
6576 | TORONTO BUTTONVILLE A | 9 | 30 | 24 | 11.2 | 6.8 | 0
6576 | TORONTO BUTTONVILLE A | 10 | 1 | 24 | 13.25 | 4.75 | 0
6577 | TORONTO BUTTONVILLE A | 10 | 1 | 1 | 11 | 7 | 0
6577 | TORONTO BUTTONVILLE A | 10 | 2 | 1 | 12.775 | 5.225 | 0
6578 | TORONTO BUTTONVILLE A | 10 | 1 | 2 | 10.9 | 7.1 | 0
6578 | TORONTO BUTTONVILLE A | 10 | 2 | 2 | 13.7667 | 4.2333 | 0
6579 | TORONTO BUTTONVILLE A | 10 | 1 | 3 | 10.9 | 7.1 | 0
6579 | TORONTO BUTTONVILLE A | 10 | 2 | 3 | 12.7 | 5.3 | 0
6580 | TORONTO BUTTONVILLE A | 10 | 1 | 4 | 10.8 | 7.2 | 0
6580 | TORONTO BUTTONVILLE A | 10 | 2 | 4 | 12.1333 | 5.8667 | 0
6581 | TORONTO BUTTONVILLE A | 10 | 1 | 5 | 10.9 | 7.1 | 0
6581 | TORONTO BUTTONVILLE A | 10 | 2 | 5 | 12.3 | 5.7 | 0
6582 | TORONTO BUTTONVILLE A | 10 | 1 | 6 | 10.5 | 7.5 | 0
6582 | TORONTO BUTTONVILLE A | 10 | 2 | 6 | 12.0333 | 5.9667 | 0
6583 | TORONTO BUTTONVILLE A | 10 | 1 | 7 | 10.1 | 7.9 | 0
6583 | TORONTO BUTTONVILLE A | 10 | 2 | 7 | 11.35 | 6.65 | 0
6584 | TORONTO BUTTONVILLE A | 10 | 1 | 8 | 10.4 | 7.6 | 0
6584 | TORONTO BUTTONVILLE A | 10 | 2 | 8 | 11.775 | 6.225 | 0
6585 | TORONTO BUTTONVILLE A | 10 | 1 | 9 | 11.8 | 6.2 | 0
6585 | TORONTO BUTTONVILLE A | 10 | 2 | 9 | 13.325 | 4.675 | 0
6586 | TORONTO BUTTONVILLE A | 10 | 1 | 10 | 13.3 | 4.7 | 0
6586 | TORONTO BUTTONVILLE A | 10 | 2 | 10 | 14.55 | 3.45 | 0
6587 | TORONTO BUTTONVILLE A | 10 | 1 | 11 | 13.8 | 4.2 | 0
6587 | TORONTO BUTTONVILLE A | 10 | 2 | 11 | 15.4 | 2.6 | 0
6588 | TORONTO BUTTONVILLE A | 10 | 1 | 12 | 14.2 | 3.8 | 0
6588 | TORONTO BUTTONVILLE A | 10 | 2 | 12 | 16.275 | 1.725 | 0
6589 | TORONTO BUTTONVILLE A | 10 | 1 | 13 | 15.1 | 2.9 | 0
6589 | TORONTO BUTTONVILLE A | 10 | 2 | 13 | 16.975 | 1.025 | 0
6590 | TORONTO BUTTONVILLE A | 10 | 1 | 14 | 13.7 | 4.3 | 0
6590 | TORONTO BUTTONVILLE A | 10 | 2 | 14 | 17.125 | 0.875 | 0
6591 | TORONTO BUTTONVILLE A | 10 | 1 | 15 | 16.4 | 1.6 | 0
6591 | TORONTO BUTTONVILLE A | 10 | 2 | 15 | 17.175 | 0.825 | 0
6592 | TORONTO BUTTONVILLE A | 10 | 1 | 16 | 15.2 | 2.8 | 0
6592 | TORONTO BUTTONVILLE A | 10 | 2 | 16 | 17.475 | 0.525 | 0
6593 | TORONTO BUTTONVILLE A | 10 | 1 | 17 | 15.4 | 2.6 | 0
6593 | TORONTO BUTTONVILLE A | 10 | 2 | 17 | 17.2 | 0.8 | 0
6594 | TORONTO BUTTONVILLE A | 10 | 1 | 18 | 15.5 | 2.5 | 0
6594 | TORONTO BUTTONVILLE A | 10 | 2 | 18 | 16.375 | 1.625 | 0
6595 | TORONTO BUTTONVILLE A | 10 | 1 | 19 | 13.7 | 4.3 | 0
6595 | TORONTO BUTTONVILLE A | 10 | 2 | 19 | 15.175 | 2.825 | 0
6596 | TORONTO BUTTONVILLE A | 10 | 1 | 20 | 12.9 | 5.1 | 0
6596 | TORONTO BUTTONVILLE A | 10 | 2 | 20 | 14.2 | 3.8 | 0
6597 | TORONTO BUTTONVILLE A | 10 | 1 | 21 | 12.2 | 5.8 | 0
6597 | TORONTO BUTTONVILLE A | 10 | 2 | 21 | 14.025 | 3.975 | 0
6598 | TORONTO BUTTONVILLE A | 10 | 1 | 22 | 10.9 | 7.1 | 0
6598 | TORONTO BUTTONVILLE A | 10 | 2 | 22 | 13.1 | 4.9 | 0
6599 | TORONTO BUTTONVILLE A | 10 | 1 | 23 | 9.5 | 8.5 | 0
6599 | TORONTO BUTTONVILLE A | 10 | 2 | 23 | 12.575 | 5.425 | 0
6600 | TORONTO BUTTONVILLE A | 10 | 1 | 24 | 9.8 | 8.2 | 0
6600 | TORONTO BUTTONVILLE A | 10 | 2 | 24 | 12.075 | 5.925 | 0
6601 | TORONTO BUTTONVILLE A | 10 | 2 | 1 | 10 | 8 | 0
6601 | TORONTO BUTTONVILLE A | 10 | 3 | 1 | 11.85 | 6.15 | 0
6602 | TORONTO BUTTONVILLE A | 10 | 2 | 2 | 9 | 9 | 0
6602 | TORONTO BUTTONVILLE A | 10 | 3 | 2 | 11.275 | 6.725 | 0
6603 | TORONTO BUTTONVILLE A | 10 | 2 | 3 | 8.5 | 9.5 | 0
6603 | TORONTO BUTTONVILLE A | 10 | 3 | 3 | 10.65 | 7.35 | 0
6604 | TORONTO BUTTONVILLE A | 10 | 2 | 4 | 7 | 11 | 0
6604 | TORONTO BUTTONVILLE A | 10 | 3 | 4 | 10.4 | 7.6 | 0
6605 | TORONTO BUTTONVILLE A | 10 | 2 | 5 | 7.1 | 10.9 | 0
6605 | TORONTO BUTTONVILLE A | 10 | 3 | 5 | 10.55 | 7.45 | 0
6606 | TORONTO BUTTONVILLE A | 10 | 2 | 6 | 7.7 | 10.3 | 0
6606 | TORONTO BUTTONVILLE A | 10 | 3 | 6 | 10.725 | 7.275 | 0
6607 | TORONTO BUTTONVILLE A | 10 | 2 | 7 | 8.8 | 9.2 | 0
6607 | TORONTO BUTTONVILLE A | 10 | 3 | 7 | 10.65 | 7.35 | 0
6608 | TORONTO BUTTONVILLE A | 10 | 2 | 8 | 9.2 | 8.8 | 0
6608 | TORONTO BUTTONVILLE A | 10 | 3 | 8 | 11.05 | 6.95 | 0
6609 | TORONTO BUTTONVILLE A | 10 | 2 | 9 | 10.2 | 7.8 | 0
6609 | TORONTO BUTTONVILLE A | 10 | 3 | 9 | 11.975 | 6.025 | 0
6610 | TORONTO BUTTONVILLE A | 10 | 2 | 10 | 11 | 7 | 0
6610 | TORONTO BUTTONVILLE A | 10 | 3 | 10 | 13.3 | 4.7 | 0
6611 | TORONTO BUTTONVILLE A | 10 | 2 | 11 | 12.1 | 5.9 | 0
6611 | TORONTO BUTTONVILLE A | 10 | 3 | 11 | 14.475 | 3.525 | 0
6612 | TORONTO BUTTONVILLE A | 10 | 2 | 12 | 12.9 | 5.1 | 0
6612 | TORONTO BUTTONVILLE A | 10 | 3 | 12 | 15.3 | 2.7 | 0
6613 | TORONTO BUTTONVILLE A | 10 | 2 | 13 | 12.6 | 5.4 | 0
6613 | TORONTO BUTTONVILLE A | 10 | 3 | 13 | 15.85 | 2.15 | 0
6614 | TORONTO BUTTONVILLE A | 10 | 2 | 14 | 13.1 | 4.9 | 0
6614 | TORONTO BUTTONVILLE A | 10 | 3 | 14 | 16.35 | 1.65 | 0
6615 | TORONTO BUTTONVILLE A | 10 | 2 | 15 | 14.1 | 3.9 | 0
6615 | TORONTO BUTTONVILLE A | 10 | 3 | 15 | 16.9 | 1.1 | 0
6616 | TORONTO BUTTONVILLE A | 10 | 2 | 16 | 13 | 5 | 0
6616 | TORONTO BUTTONVILLE A | 10 | 3 | 16 | 16.8 | 1.2 | 0
6617 | TORONTO BUTTONVILLE A | 10 | 2 | 17 | 12.5 | 5.5 | 0
6617 | TORONTO BUTTONVILLE A | 10 | 3 | 17 | 16.525 | 1.475 | 0
6618 | TORONTO BUTTONVILLE A | 10 | 2 | 18 | 11.3 | 6.7 | 0
6618 | TORONTO BUTTONVILLE A | 10 | 3 | 18 | 15.925 | 2.075 | 0
6619 | TORONTO BUTTONVILLE A | 10 | 2 | 19 | 10.5 | 7.5 | 0
6619 | TORONTO BUTTONVILLE A | 10 | 3 | 19 | 15.25 | 2.75 | 0
6620 | TORONTO BUTTONVILLE A | 10 | 2 | 20 | 9.9 | 8.1 | 0
6620 | TORONTO BUTTONVILLE A | 10 | 3 | 20 | 14.45 | 3.55 | 0
6621 | TORONTO BUTTONVILLE A | 10 | 2 | 21 | 9 | 9 | 0
6621 | TORONTO BUTTONVILLE A | 10 | 3 | 21 | 14.275 | 3.725 | 0
6622 | TORONTO BUTTONVILLE A | 10 | 2 | 22 | 7.9 | 10.1 | 0
6622 | TORONTO BUTTONVILLE A | 10 | 3 | 22 | 14.1 | 3.9 | 0
6623 | TORONTO BUTTONVILLE A | 10 | 2 | 23 | 7.1 | 10.9 | 0
6623 | TORONTO BUTTONVILLE A | 10 | 3 | 23 | 14 | 4 | 0
6624 | TORONTO BUTTONVILLE A | 10 | 2 | 24 | 6.5 | 11.5 | 0
6624 | TORONTO BUTTONVILLE A | 10 | 3 | 24 | 13.85 | 4.15 | 0
6625 | TORONTO BUTTONVILLE A | 10 | 3 | 1 | 5.9 | 12.1 | 0
6625 | TORONTO BUTTONVILLE A | 10 | 4 | 1 | 13.275 | 4.725 | 0
6626 | TORONTO BUTTONVILLE A | 10 | 3 | 2 | 5.1 | 12.9 | 0
6626 | TORONTO BUTTONVILLE A | 10 | 4 | 2 | 13.65 | 4.35 | 0
6627 | TORONTO BUTTONVILLE A | 10 | 3 | 3 | 4.5 | 13.5 | 0
6627 | TORONTO BUTTONVILLE A | 10 | 4 | 3 | 13.9 | 4.1 | 0
6628 | TORONTO BUTTONVILLE A | 10 | 3 | 4 | 4 | 14 | 0
6628 | TORONTO BUTTONVILLE A | 10 | 4 | 4 | 14.5 | 3.5 | 0
6629 | TORONTO BUTTONVILLE A | 10 | 3 | 5 | 3.7 | 14.3 | 0
6629 | TORONTO BUTTONVILLE A | 10 | 4 | 5 | 15.475 | 2.525 | 0
6630 | TORONTO BUTTONVILLE A | 10 | 3 | 6 | 3.5 | 14.5 | 0
6630 | TORONTO BUTTONVILLE A | 10 | 4 | 6 | 15.575 | 2.425 | 0
6631 | TORONTO BUTTONVILLE A | 10 | 3 | 7 | 3.7 | 14.3 | 0
6631 | TORONTO BUTTONVILLE A | 10 | 4 | 7 | 15.7 | 2.3 | 0
6632 | TORONTO BUTTONVILLE A | 10 | 3 | 8 | 3 | 15 | 0
6632 | TORONTO BUTTONVILLE A | 10 | 4 | 8 | 15.75 | 2.25 | 0
6633 | TORONTO BUTTONVILLE A | 10 | 3 | 9 | 6 | 12 | 0
6633 | TORONTO BUTTONVILLE A | 10 | 4 | 9 | 15.2 | 2.8 | 0
6634 | TORONTO BUTTONVILLE A | 10 | 3 | 10 | 9.5 | 8.5 | 0
6634 | TORONTO BUTTONVILLE A | 10 | 4 | 10 | 15.475 | 2.525 | 0
6635 | TORONTO BUTTONVILLE A | 10 | 3 | 11 | 10.2 | 7.8 | 0
6635 | TORONTO BUTTONVILLE A | 10 | 4 | 11 | 16.025 | 1.975 | 0
6636 | TORONTO BUTTONVILLE A | 10 | 3 | 12 | 10.5 | 7.5 | 0
6636 | TORONTO BUTTONVILLE A | 10 | 4 | 12 | 16.35 | 1.65 | 0
6637 | TORONTO BUTTONVILLE A | 10 | 3 | 13 | 12.4 | 5.6 | 0
6637 | TORONTO BUTTONVILLE A | 10 | 4 | 13 | 16.025 | 1.975 | 0
6638 | TORONTO BUTTONVILLE A | 10 | 3 | 14 | 12.2 | 5.8 | 0
6638 | TORONTO BUTTONVILLE A | 10 | 4 | 14 | 15.9 | 2.1 | 0
6639 | TORONTO BUTTONVILLE A | 10 | 3 | 15 | 13.3 | 4.7 | 0
6639 | TORONTO BUTTONVILLE A | 10 | 4 | 15 | 15.875 | 2.125 | 0
6640 | TORONTO BUTTONVILLE A | 10 | 3 | 16 | 12.1 | 5.9 | 0
6640 | TORONTO BUTTONVILLE A | 10 | 4 | 16 | 16.1 | 1.9 | 0
6641 | TORONTO BUTTONVILLE A | 10 | 3 | 17 | 11.7 | 6.3 | 0
6641 | TORONTO BUTTONVILLE A | 10 | 4 | 17 | 16.05 | 1.95 | 0
6642 | TORONTO BUTTONVILLE A | 10 | 3 | 18 | 11.4 | 6.6 | 0
6642 | TORONTO BUTTONVILLE A | 10 | 4 | 18 | 15.55 | 2.45 | 0
6643 | TORONTO BUTTONVILLE A | 10 | 3 | 19 | 10.9 | 7.1 | 0
6643 | TORONTO BUTTONVILLE A | 10 | 4 | 19 | 12.975 | 5.025 | 0
6644 | TORONTO BUTTONVILLE A | 10 | 3 | 20 | 10.4 | 7.6 | 0
6644 | TORONTO BUTTONVILLE A | 10 | 4 | 20 | 12.075 | 5.925 | 0
6645 | TORONTO BUTTONVILLE A | 10 | 3 | 21 | 10.2 | 7.8 | 0
6645 | TORONTO BUTTONVILLE A | 10 | 4 | 21 | 11.45 | 6.55 | 0
6646 | TORONTO BUTTONVILLE A | 10 | 3 | 22 | 9.9 | 8.1 | 0
6646 | TORONTO BUTTONVILLE A | 10 | 4 | 22 | 10.7 | 7.3 | 0
6647 | TORONTO BUTTONVILLE A | 10 | 3 | 23 | 8.9 | 9.1 | 0
6647 | TORONTO BUTTONVILLE A | 10 | 4 | 23 | 10.325 | 7.675 | 0
6648 | TORONTO BUTTONVILLE A | 10 | 3 | 24 | 8.3 | 9.7 | 0
6648 | TORONTO BUTTONVILLE A | 10 | 4 | 24 | 9.8 | 8.2 | 0
6649 | TORONTO BUTTONVILLE A | 10 | 4 | 1 | 6.9 | 11.1 | 0
6649 | TORONTO BUTTONVILLE A | 10 | 5 | 1 | 9.025 | 8.975 | 0
6650 | TORONTO BUTTONVILLE A | 10 | 4 | 2 | 6.3 | 11.7 | 0
6650 | TORONTO BUTTONVILLE A | 10 | 5 | 2 | 8.625 | 9.375 | 0
6651 | TORONTO BUTTONVILLE A | 10 | 4 | 3 | 5.8 | 12.2 | 0
6651 | TORONTO BUTTONVILLE A | 10 | 5 | 3 | 7.975 | 10.025 | 0
6652 | TORONTO BUTTONVILLE A | 10 | 4 | 4 | 6.1 | 11.9 | 0
6652 | TORONTO BUTTONVILLE A | 10 | 5 | 4 | 8.05 | 9.95 | 0
6653 | TORONTO BUTTONVILLE A | 10 | 4 | 5 | 6.3 | 11.7 | 0
6653 | TORONTO BUTTONVILLE A | 10 | 5 | 5 | 8.25 | 9.75 | 0
6654 | TORONTO BUTTONVILLE A | 10 | 4 | 6 | 6 | 12 | 0
6654 | TORONTO BUTTONVILLE A | 10 | 5 | 6 | 8.05 | 9.95 | 0
6655 | TORONTO BUTTONVILLE A | 10 | 4 | 7 | 6.2 | 11.8 | 0
6655 | TORONTO BUTTONVILLE A | 10 | 5 | 7 | 8.075 | 9.925 | 0
6656 | TORONTO BUTTONVILLE A | 10 | 4 | 8 | 6.5 | 11.5 | 0
6656 | TORONTO BUTTONVILLE A | 10 | 5 | 8 | 8.925 | 9.075 | 0
6657 | TORONTO BUTTONVILLE A | 10 | 4 | 9 | 7.2 | 10.8 | 0
6657 | TORONTO BUTTONVILLE A | 10 | 5 | 9 | 10.525 | 7.475 | 0
6658 | TORONTO BUTTONVILLE A | 10 | 4 | 10 | 8.1 | 9.9 | 0
6658 | TORONTO BUTTONVILLE A | 10 | 5 | 10 | 11.45 | 6.55 | 0
6659 | TORONTO BUTTONVILLE A | 10 | 4 | 11 | 8.7 | 9.3 | 0
6659 | TORONTO BUTTONVILLE A | 10 | 5 | 11 | 13.075 | 4.925 | 0
6660 | TORONTO BUTTONVILLE A | 10 | 4 | 12 | 8.5 | 9.5 | 0
6660 | TORONTO BUTTONVILLE A | 10 | 5 | 12 | 13.525 | 4.475 | 0
6661 | TORONTO BUTTONVILLE A | 10 | 4 | 13 | 9 | 9 | 0
6661 | TORONTO BUTTONVILLE A | 10 | 5 | 13 | 14.675 | 3.325 | 0
6662 | TORONTO BUTTONVILLE A | 10 | 4 | 14 | 9.5 | 8.5 | 0
6662 | TORONTO BUTTONVILLE A | 10 | 5 | 14 | 15.2 | 2.8 | 0
6663 | TORONTO BUTTONVILLE A | 10 | 4 | 15 | 10.1 | 7.9 | 0
6663 | TORONTO BUTTONVILLE A | 10 | 5 | 15 | 15.2 | 2.8 | 0
6664 | TORONTO BUTTONVILLE A | 10 | 4 | 16 | 10.3 | 7.7 | 0
6664 | TORONTO BUTTONVILLE A | 10 | 5 | 16 | 15.35 | 2.65 | 0
6665 | TORONTO BUTTONVILLE A | 10 | 4 | 17 | 10.6 | 7.4 | 0
6665 | TORONTO BUTTONVILLE A | 10 | 5 | 17 | 15.075 | 2.925 | 0
6666 | TORONTO BUTTONVILLE A | 10 | 4 | 18 | 10.6 | 7.4 | 0
6666 | TORONTO BUTTONVILLE A | 10 | 5 | 18 | 14.625 | 3.375 | 0
6667 | TORONTO BUTTONVILLE A | 10 | 4 | 19 | 10.4 | 7.6 | 0
6667 | TORONTO BUTTONVILLE A | 10 | 5 | 19 | 14.1 | 3.9 | 0
6668 | TORONTO BUTTONVILLE A | 10 | 4 | 20 | 10.2 | 7.8 | 0
6668 | TORONTO BUTTONVILLE A | 10 | 5 | 20 | 13.8 | 4.2 | 0
6669 | TORONTO BUTTONVILLE A | 10 | 4 | 21 | 10.1 | 7.9 | 0
6669 | TORONTO BUTTONVILLE A | 10 | 5 | 21 | 13.7 | 4.3 | 0
6670 | TORONTO BUTTONVILLE A | 10 | 4 | 22 | 8.9 | 9.1 | 0
6670 | TORONTO BUTTONVILLE A | 10 | 5 | 22 | 13.45 | 4.55 | 0
6671 | TORONTO BUTTONVILLE A | 10 | 4 | 23 | 8.5 | 9.5 | 0
6671 | TORONTO BUTTONVILLE A | 10 | 5 | 23 | 13.25 | 4.75 | 0
6672 | TORONTO BUTTONVILLE A | 10 | 4 | 24 | 8 | 10 | 0
6672 | TORONTO BUTTONVILLE A | 10 | 5 | 24 | 12.925 | 5.075 | 0
6673 | TORONTO BUTTONVILLE A | 10 | 5 | 1 | 8.8 | 9.2 | 0
6673 | TORONTO BUTTONVILLE A | 10 | 6 | 1 | 12.475 | 5.525 | 0
6674 | TORONTO BUTTONVILLE A | 10 | 5 | 2 | 8.9 | 9.1 | 0
6674 | TORONTO BUTTONVILLE A | 10 | 6 | 2 | 12.8 | 5.2 | 0
6675 | TORONTO BUTTONVILLE A | 10 | 5 | 3 | 9.4 | 8.6 | 0
6675 | TORONTO BUTTONVILLE A | 10 | 6 | 3 | 12.575 | 5.425 | 0
6676 | TORONTO BUTTONVILLE A | 10 | 5 | 4 | 9 | 9 | 0
6676 | TORONTO BUTTONVILLE A | 10 | 6 | 4 | 12.275 | 5.725 | 0
6677 | TORONTO BUTTONVILLE A | 10 | 5 | 5 | 9.1 | 8.9 | 0
6677 | TORONTO BUTTONVILLE A | 10 | 6 | 5 | 11.975 | 6.025 | 0
6678 | TORONTO BUTTONVILLE A | 10 | 5 | 6 | 8.8 | 9.2 | 0
6678 | TORONTO BUTTONVILLE A | 10 | 6 | 6 | 12.275 | 5.725 | 0
6679 | TORONTO BUTTONVILLE A | 10 | 5 | 7 | 8.7 | 9.3 | 0
6679 | TORONTO BUTTONVILLE A | 10 | 6 | 7 | 12.35 | 5.65 | 0
6680 | TORONTO BUTTONVILLE A | 10 | 5 | 8 | 8 | 10 | 0
6680 | TORONTO BUTTONVILLE A | 10 | 6 | 8 | 12.475 | 5.525 | 0
6681 | TORONTO BUTTONVILLE A | 10 | 5 | 9 | 9.9 | 8.1 | 0
6681 | TORONTO BUTTONVILLE A | 10 | 6 | 9 | 13.25 | 4.75 | 0
6682 | TORONTO BUTTONVILLE A | 10 | 5 | 10 | 9.8 | 8.2 | 0
6682 | TORONTO BUTTONVILLE A | 10 | 6 | 10 | 14.25 | 3.75 | 0
6683 | TORONTO BUTTONVILLE A | 10 | 5 | 11 | 11.3 | 6.7 | 0
6683 | TORONTO BUTTONVILLE A | 10 | 6 | 11 | 15.3 | 2.7 | 0
6684 | TORONTO BUTTONVILLE A | 10 | 5 | 12 | 12.2 | 5.8 | 0
6684 | TORONTO BUTTONVILLE A | 10 | 6 | 12 | 15.775 | 2.225 | 0
6685 | TORONTO BUTTONVILLE A | 10 | 5 | 13 | 13.5 | 4.5 | 0
6685 | TORONTO BUTTONVILLE A | 10 | 6 | 13 | 16.9 | 1.1 | 0
6686 | TORONTO BUTTONVILLE A | 10 | 5 | 14 | 14.7 | 3.3 | 0
6686 | TORONTO BUTTONVILLE A | 10 | 6 | 14 | 17.225 | 0.775 | 0
6687 | TORONTO BUTTONVILLE A | 10 | 5 | 15 | 14.1 | 3.9 | 0
6687 | TORONTO BUTTONVILLE A | 10 | 6 | 15 | 17.725 | 0.275 | 0
6688 | TORONTO BUTTONVILLE A | 10 | 5 | 16 | 14 | 4 | 0
6688 | TORONTO BUTTONVILLE A | 10 | 6 | 16 | 17.85 | 0.15 | 0
6689 | TORONTO BUTTONVILLE A | 10 | 5 | 17 | 14.2 | 3.8 | 0
6689 | TORONTO BUTTONVILLE A | 10 | 6 | 17 | 18.275 | 0 | 0.275
6690 | TORONTO BUTTONVILLE A | 10 | 5 | 18 | 12.8 | 5.2 | 0
6690 | TORONTO BUTTONVILLE A | 10 | 6 | 18 | 17.475 | 0.525 | 0
6691 | TORONTO BUTTONVILLE A | 10 | 5 | 19 | 11.7 | 6.3 | 0
6691 | TORONTO BUTTONVILLE A | 10 | 6 | 19 | 16.425 | 1.575 | 0
6692 | TORONTO BUTTONVILLE A | 10 | 5 | 20 | 10.6 | 7.4 | 0
6692 | TORONTO BUTTONVILLE A | 10 | 6 | 20 | 15.85 | 2.15 | 0
6693 | TORONTO BUTTONVILLE A | 10 | 5 | 21 | 10.2 | 7.8 | 0
6693 | TORONTO BUTTONVILLE A | 10 | 6 | 21 | 15.225 | 2.775 | 0
6694 | TORONTO BUTTONVILLE A | 10 | 5 | 22 | 10.8 | 7.2 | 0
6694 | TORONTO BUTTONVILLE A | 10 | 6 | 22 | 15.375 | 2.625 | 0
6695 | TORONTO BUTTONVILLE A | 10 | 5 | 23 | 10 | 8 | 0
6695 | TORONTO BUTTONVILLE A | 10 | 6 | 23 | 15.3 | 2.7 | 0
6696 | TORONTO BUTTONVILLE A | 10 | 5 | 24 | 9.3 | 8.7 | 0
6696 | TORONTO BUTTONVILLE A | 10 | 6 | 24 | 14.825 | 3.175 | 0
6697 | TORONTO BUTTONVILLE A | 10 | 6 | 1 | 9 | 9 | 0
6697 | TORONTO BUTTONVILLE A | 10 | 7 | 1 | 14.45 | 3.55 | 0
6698 | TORONTO BUTTONVILLE A | 10 | 6 | 2 | 8 | 10 | 0
6698 | TORONTO BUTTONVILLE A | 10 | 7 | 2 | 14.25 | 3.75 | 0
6699 | TORONTO BUTTONVILLE A | 10 | 6 | 3 | 7.4 | 10.6 | 0
6699 | TORONTO BUTTONVILLE A | 10 | 7 | 3 | 14.2 | 3.8 | 0
6700 | TORONTO BUTTONVILLE A | 10 | 6 | 4 | 7 | 11 | 0
6700 | TORONTO BUTTONVILLE A | 10 | 7 | 4 | 13.8 | 4.2 | 0
6701 | TORONTO BUTTONVILLE A | 10 | 6 | 5 | 5.4 | 12.6 | 0
6701 | TORONTO BUTTONVILLE A | 10 | 7 | 5 | 13.725 | 4.275 | 0
6702 | TORONTO BUTTONVILLE A | 10 | 6 | 6 | 8.6 | 9.4 | 0
6702 | TORONTO BUTTONVILLE A | 10 | 7 | 6 | 14.175 | 3.825 | 0
6703 | TORONTO BUTTONVILLE A | 10 | 6 | 7 | 9.6 | 8.4 | 0
6703 | TORONTO BUTTONVILLE A | 10 | 7 | 7 | 14.475 | 3.525 | 0
6704 | TORONTO BUTTONVILLE A | 10 | 6 | 8 | 10.1 | 7.9 | 0
6704 | TORONTO BUTTONVILLE A | 10 | 7 | 8 | 14.6 | 3.4 | 0
6705 | TORONTO BUTTONVILLE A | 10 | 6 | 9 | 11.7 | 6.3 | 0
6705 | TORONTO BUTTONVILLE A | 10 | 7 | 9 | 15.35 | 2.65 | 0
6706 | TORONTO BUTTONVILLE A | 10 | 6 | 10 | 12.6 | 5.4 | 0
6706 | TORONTO BUTTONVILLE A | 10 | 7 | 10 | 15.975 | 2.025 | 0
6707 | TORONTO BUTTONVILLE A | 10 | 6 | 11 | 13.5 | 4.5 | 0
6707 | TORONTO BUTTONVILLE A | 10 | 7 | 11 | 16.475 | 1.525 | 0
6708 | TORONTO BUTTONVILLE A | 10 | 6 | 12 | 16.1 | 1.9 | 0
6708 | TORONTO BUTTONVILLE A | 10 | 7 | 12 | 17.125 | 0.875 | 0
6709 | TORONTO BUTTONVILLE A | 10 | 6 | 13 | 17.3 | 0.7 | 0
6709 | TORONTO BUTTONVILLE A | 10 | 7 | 13 | 17.025 | 0.975 | 0
6710 | TORONTO BUTTONVILLE A | 10 | 6 | 14 | 17.6 | 0.4 | 0
6710 | TORONTO BUTTONVILLE A | 10 | 7 | 14 | 17.6 | 0.4 | 0
6711 | TORONTO BUTTONVILLE A | 10 | 6 | 15 | 18 | 0 | 0
6711 | TORONTO BUTTONVILLE A | 10 | 7 | 15 | 18.525 | 0 | 0.525
6712 | TORONTO BUTTONVILLE A | 10 | 6 | 16 | 18.2 | 0 | 0.2
6712 | TORONTO BUTTONVILLE A | 10 | 7 | 16 | 18.75 | 0 | 0.75
6713 | TORONTO BUTTONVILLE A | 10 | 6 | 17 | 16.9 | 1.1 | 0
6713 | TORONTO BUTTONVILLE A | 10 | 7 | 17 | 18.3 | 0 | 0.3
6714 | TORONTO BUTTONVILLE A | 10 | 6 | 18 | 17.7 | 0.3 | 0
6714 | TORONTO BUTTONVILLE A | 10 | 7 | 18 | 17.875 | 0.125 | 0
6715 | TORONTO BUTTONVILLE A | 10 | 6 | 19 | 16.6 | 1.4 | 0
6715 | TORONTO BUTTONVILLE A | 10 | 7 | 19 | 17.1 | 0.9 | 0
6716 | TORONTO BUTTONVILLE A | 10 | 6 | 20 | 16.4 | 1.6 | 0
6716 | TORONTO BUTTONVILLE A | 10 | 7 | 20 | 15.975 | 2.025 | 0
6717 | TORONTO BUTTONVILLE A | 10 | 6 | 21 | 15.8 | 2.2 | 0
6717 | TORONTO BUTTONVILLE A | 10 | 7 | 21 | 15.15 | 2.85 | 0
6718 | TORONTO BUTTONVILLE A | 10 | 6 | 22 | 15.2 | 2.8 | 0
6718 | TORONTO BUTTONVILLE A | 10 | 7 | 22 | 14.55 | 3.45 | 0
6719 | TORONTO BUTTONVILLE A | 10 | 6 | 23 | 14 | 4 | 0
6719 | TORONTO BUTTONVILLE A | 10 | 7 | 23 | 14.025 | 3.975 | 0
6720 | TORONTO BUTTONVILLE A | 10 | 6 | 24 | 13.6 | 4.4 | 0
6720 | TORONTO BUTTONVILLE A | 10 | 7 | 24 | 13.775 | 4.225 | 0
6721 | TORONTO BUTTONVILLE A | 10 | 7 | 1 | 13.7 | 4.3 | 0
6721 | TORONTO BUTTONVILLE A | 10 | 8 | 1 | 13.725 | 4.275 | 0
6722 | TORONTO BUTTONVILLE A | 10 | 7 | 2 | 12.8 | 5.2 | 0
6722 | TORONTO BUTTONVILLE A | 10 | 8 | 2 | 12.5 | 5.5 | 0
6723 | TORONTO BUTTONVILLE A | 10 | 7 | 3 | 12.9 | 5.1 | 0
6723 | TORONTO BUTTONVILLE A | 10 | 8 | 3 | 12.275 | 5.725 | 0
6724 | TORONTO BUTTONVILLE A | 10 | 7 | 4 | 13.3 | 4.7 | 0
6724 | TORONTO BUTTONVILLE A | 10 | 8 | 4 | 12.175 | 5.825 | 0
6725 | TORONTO BUTTONVILLE A | 10 | 7 | 5 | 14 | 4 | 0
6725 | TORONTO BUTTONVILLE A | 10 | 8 | 5 | 12.5 | 5.5 | 0
6726 | TORONTO BUTTONVILLE A | 10 | 7 | 6 | 13.3 | 4.7 | 0
6726 | TORONTO BUTTONVILLE A | 10 | 8 | 6 | 12.225 | 5.775 | 0
6727 | TORONTO BUTTONVILLE A | 10 | 7 | 7 | 13.6 | 4.4 | 0
6727 | TORONTO BUTTONVILLE A | 10 | 8 | 7 | 12.05 | 5.95 | 0
6728 | TORONTO BUTTONVILLE A | 10 | 7 | 8 | 12.9 | 5.1 | 0
6728 | TORONTO BUTTONVILLE A | 10 | 8 | 8 | 12.6 | 5.4 | 0
6729 | TORONTO BUTTONVILLE A | 10 | 7 | 9 | 13.4 | 4.6 | 0
6729 | TORONTO BUTTONVILLE A | 10 | 8 | 9 | 13.575 | 4.425 | 0
6730 | TORONTO BUTTONVILLE A | 10 | 7 | 10 | 14.8 | 3.2 | 0
6730 | TORONTO BUTTONVILLE A | 10 | 8 | 10 | 14.65 | 3.35 | 0
6731 | TORONTO BUTTONVILLE A | 10 | 7 | 11 | 15.9 | 2.1 | 0
6731 | TORONTO BUTTONVILLE A | 10 | 8 | 11 | 15.95 | 2.05 | 0
6732 | TORONTO BUTTONVILLE A | 10 | 7 | 12 | 13.9 | 4.1 | 0
6732 | TORONTO BUTTONVILLE A | 10 | 8 | 12 | 16.475 | 1.525 | 0
6733 | TORONTO BUTTONVILLE A | 10 | 7 | 13 | 16.6 | 1.4 | 0
6733 | TORONTO BUTTONVILLE A | 10 | 8 | 13 | 17.25 | 0.75 | 0
6734 | TORONTO BUTTONVILLE A | 10 | 7 | 14 | 17.1 | 0.9 | 0
6734 | TORONTO BUTTONVILLE A | 10 | 8 | 14 | 17.7 | 0.3 | 0
6735 | TORONTO BUTTONVILLE A | 10 | 7 | 15 | 15.7 | 2.3 | 0
6735 | TORONTO BUTTONVILLE A | 10 | 8 | 15 | 18.225 | 0 | 0.225
6736 | TORONTO BUTTONVILLE A | 10 | 7 | 16 | 16.8 | 1.2 | 0
6736 | TORONTO BUTTONVILLE A | 10 | 8 | 16 | 18.675 | 0 | 0.675
6737 | TORONTO BUTTONVILLE A | 10 | 7 | 17 | 15.8 | 2.2 | 0
6737 | TORONTO BUTTONVILLE A | 10 | 8 | 17 | 17.6 | 0.4 | 0
6738 | TORONTO BUTTONVILLE A | 10 | 7 | 18 | 15.2 | 2.8 | 0
6738 | TORONTO BUTTONVILLE A | 10 | 8 | 18 | 17.15 | 0.85 | 0
6739 | TORONTO BUTTONVILLE A | 10 | 7 | 19 | 13.2 | 4.8 | 0
6739 | TORONTO BUTTONVILLE A | 10 | 8 | 19 | 15.85 | 2.15 | 0
6740 | TORONTO BUTTONVILLE A | 10 | 7 | 20 | 12.4 | 5.6 | 0
6740 | TORONTO BUTTONVILLE A | 10 | 8 | 20 | 15.025 | 2.975 | 0
6741 | TORONTO BUTTONVILLE A | 10 | 7 | 21 | 11.9 | 6.1 | 0
6741 | TORONTO BUTTONVILLE A | 10 | 8 | 21 | 14.2 | 3.8 | 0
6742 | TORONTO BUTTONVILLE A | 10 | 7 | 22 | 11.7 | 6.3 | 0
6742 | TORONTO BUTTONVILLE A | 10 | 8 | 22 | 13.7 | 4.3 | 0
6743 | TORONTO BUTTONVILLE A | 10 | 7 | 23 | 10.9 | 7.1 | 0
6743 | TORONTO BUTTONVILLE A | 10 | 8 | 23 | 13.575 | 4.425 | 0
6744 | TORONTO BUTTONVILLE A | 10 | 7 | 24 | 10.7 | 7.3 | 0
6744 | TORONTO BUTTONVILLE A | 10 | 8 | 24 | 13.25 | 4.75 | 0
6745 | TORONTO BUTTONVILLE A | 10 | 8 | 1 | 10.3 | 7.7 | 0
6745 | TORONTO BUTTONVILLE A | 10 | 9 | 1 | 12.975 | 5.025 | 0
6746 | TORONTO BUTTONVILLE A | 10 | 8 | 2 | 9.5 | 8.5 | 0
6746 | TORONTO BUTTONVILLE A | 10 | 9 | 2 | 12.625 | 5.375 | 0
6747 | TORONTO BUTTONVILLE A | 10 | 8 | 3 | 7.1 | 10.9 | 0
6747 | TORONTO BUTTONVILLE A | 10 | 9 | 3 | 12.75 | 5.25 | 0
6748 | TORONTO BUTTONVILLE A | 10 | 8 | 4 | 6.6 | 11.4 | 0
6748 | TORONTO BUTTONVILLE A | 10 | 9 | 4 | 12.4 | 5.6 | 0
6749 | TORONTO BUTTONVILLE A | 10 | 8 | 5 | 5.6 | 12.4 | 0
6749 | TORONTO BUTTONVILLE A | 10 | 9 | 5 | 12.475 | 5.525 | 0
6750 | TORONTO BUTTONVILLE A | 10 | 8 | 6 | 5.9 | 12.1 | 0
6750 | TORONTO BUTTONVILLE A | 10 | 9 | 6 | 12.225 | 5.775 | 0
6751 | TORONTO BUTTONVILLE A | 10 | 8 | 7 | 6.1 | 11.9 | 0
6751 | TORONTO BUTTONVILLE A | 10 | 9 | 7 | 12.425 | 5.575 | 0
6752 | TORONTO BUTTONVILLE A | 10 | 8 | 8 | 6.2 | 11.8 | 0
6752 | TORONTO BUTTONVILLE A | 10 | 9 | 8 | 12.875 | 5.125 | 0
6753 | TORONTO BUTTONVILLE A | 10 | 8 | 9 | 7.7 | 10.3 | 0
6753 | TORONTO BUTTONVILLE A | 10 | 9 | 9 | 14.775 | 3.225 | 0
6754 | TORONTO BUTTONVILLE A | 10 | 8 | 10 | 10.8 | 7.2 | 0
6754 | TORONTO BUTTONVILLE A | 10 | 9 | 10 | 16.325 | 1.675 | 0
6755 | TORONTO BUTTONVILLE A | 10 | 8 | 11 | 11.5 | 6.5 | 0
6755 | TORONTO BUTTONVILLE A | 10 | 9 | 11 | 18.425 | 0 | 0.425
6756 | TORONTO BUTTONVILLE A | 10 | 8 | 12 | 13.7 | 4.3 | 0
6756 | TORONTO BUTTONVILLE A | 10 | 9 | 12 | 20.075 | 0 | 2.075
6757 | TORONTO BUTTONVILLE A | 10 | 8 | 13 | 13 | 5 | 0
6757 | TORONTO BUTTONVILLE A | 10 | 9 | 13 | 20.875 | 0 | 2.875
6758 | TORONTO BUTTONVILLE A | 10 | 8 | 14 | 10.2 | 7.8 | 0
6758 | TORONTO BUTTONVILLE A | 10 | 9 | 14 | 20.45 | 0 | 2.45
6759 | TORONTO BUTTONVILLE A | 10 | 8 | 15 | 12.5 | 5.5 | 0
6759 | TORONTO BUTTONVILLE A | 10 | 9 | 15 | 21 | 0 | 3
6760 | TORONTO BUTTONVILLE A | 10 | 8 | 16 | 12.6 | 5.4 | 0
6760 | TORONTO BUTTONVILLE A | 10 | 9 | 16 | 20.75 | 0 | 2.75
6761 | TORONTO BUTTONVILLE A | 10 | 8 | 17 | 11.7 | 6.3 | 0
6761 | TORONTO BUTTONVILLE A | 10 | 9 | 17 | 20.825 | 0 | 2.825
6762 | TORONTO BUTTONVILLE A | 10 | 8 | 18 | 12.1 | 5.9 | 0
6762 | TORONTO BUTTONVILLE A | 10 | 9 | 18 | 20.025 | 0 | 2.025
6763 | TORONTO BUTTONVILLE A | 10 | 8 | 19 | 11 | 7 | 0
6763 | TORONTO BUTTONVILLE A | 10 | 9 | 19 | 18.25 | 0 | 0.25
6764 | TORONTO BUTTONVILLE A | 10 | 8 | 20 | 10.3 | 7.7 | 0
6764 | TORONTO BUTTONVILLE A | 10 | 9 | 20 | 17.375 | 0.625 | 0
6765 | TORONTO BUTTONVILLE A | 10 | 8 | 21 | 8.6 | 9.4 | 0
6765 | TORONTO BUTTONVILLE A | 10 | 9 | 21 | 16.775 | 1.225 | 0
6766 | TORONTO BUTTONVILLE A | 10 | 8 | 22 | 7.8 | 10.2 | 0
6766 | TORONTO BUTTONVILLE A | 10 | 9 | 22 | 15.775 | 2.225 | 0
6767 | TORONTO BUTTONVILLE A | 10 | 8 | 23 | 7.3 | 10.7 | 0
6767 | TORONTO BUTTONVILLE A | 10 | 9 | 23 | 15.4 | 2.6 | 0
6768 | TORONTO BUTTONVILLE A | 10 | 8 | 24 | 6.2 | 11.8 | 0
6768 | TORONTO BUTTONVILLE A | 10 | 9 | 24 | 14.8 | 3.2 | 0
6769 | TORONTO BUTTONVILLE A | 10 | 9 | 1 | 5.3 | 12.7 | 0
6769 | TORONTO BUTTONVILLE A | 10 | 10 | 1 | 14.175 | 3.825 | 0
6770 | TORONTO BUTTONVILLE A | 10 | 9 | 2 | 4.2 | 13.8 | 0
6770 | TORONTO BUTTONVILLE A | 10 | 10 | 2 | 13.35 | 4.65 | 0
6771 | TORONTO BUTTONVILLE A | 10 | 9 | 3 | 3.3 | 14.7 | 0
6771 | TORONTO BUTTONVILLE A | 10 | 10 | 3 | 12.775 | 5.225 | 0
6772 | TORONTO BUTTONVILLE A | 10 | 9 | 4 | 2.8 | 15.2 | 0
6772 | TORONTO BUTTONVILLE A | 10 | 10 | 4 | 12.85 | 5.15 | 0
6773 | TORONTO BUTTONVILLE A | 10 | 9 | 5 | 3.4 | 14.6 | 0
6773 | TORONTO BUTTONVILLE A | 10 | 10 | 5 | 12.8 | 5.2 | 0
6774 | TORONTO BUTTONVILLE A | 10 | 9 | 6 | 3 | 15 | 0
6774 | TORONTO BUTTONVILLE A | 10 | 10 | 6 | 12.875 | 5.125 | 0
6775 | TORONTO BUTTONVILLE A | 10 | 9 | 7 | 3 | 15 | 0
6775 | TORONTO BUTTONVILLE A | 10 | 10 | 7 | 12.9 | 5.1 | 0
6776 | TORONTO BUTTONVILLE A | 10 | 9 | 8 | 3.9 | 14.1 | 0
6776 | TORONTO BUTTONVILLE A | 10 | 10 | 8 | 13.625 | 4.375 | 0
6777 | TORONTO BUTTONVILLE A | 10 | 9 | 9 | 7.6 | 10.4 | 0
6777 | TORONTO BUTTONVILLE A | 10 | 10 | 9 | 15.925 | 2.075 | 0
6778 | TORONTO BUTTONVILLE A | 10 | 9 | 10 | 11.6 | 6.4 | 0
6778 | TORONTO BUTTONVILLE A | 10 | 10 | 10 | 17.9 | 0.1 | 0
6779 | TORONTO BUTTONVILLE A | 10 | 9 | 11 | 12.9 | 5.1 | 0
6779 | TORONTO BUTTONVILLE A | 10 | 10 | 11 | 19.85 | 0 | 1.85
6780 | TORONTO BUTTONVILLE A | 10 | 9 | 12 | 14.4 | 3.6 | 0
6780 | TORONTO BUTTONVILLE A | 10 | 10 | 12 | 20.375 | 0 | 2.375
6781 | TORONTO BUTTONVILLE A | 10 | 9 | 13 | 15.5 | 2.5 | 0
6781 | TORONTO BUTTONVILLE A | 10 | 10 | 13 | 20.7 | 0 | 2.7
6782 | TORONTO BUTTONVILLE A | 10 | 9 | 14 | 15 | 3 | 0
6782 | TORONTO BUTTONVILLE A | 10 | 10 | 14 | 20.675 | 0 | 2.675
6783 | TORONTO BUTTONVILLE A | 10 | 9 | 15 | 15.5 | 2.5 | 0
6783 | TORONTO BUTTONVILLE A | 10 | 10 | 15 | 21.2 | 0 | 3.2
6784 | TORONTO BUTTONVILLE A | 10 | 9 | 16 | 16.4 | 1.6 | 0
6784 | TORONTO BUTTONVILLE A | 10 | 10 | 16 | 21 | 0 | 3
6785 | TORONTO BUTTONVILLE A | 10 | 9 | 17 | 15.9 | 2.1 | 0
6785 | TORONTO BUTTONVILLE A | 10 | 10 | 17 | 20.575 | 0 | 2.575
6786 | TORONTO BUTTONVILLE A | 10 | 9 | 18 | 14.7 | 3.3 | 0
6786 | TORONTO BUTTONVILLE A | 10 | 10 | 18 | 18.95 | 0 | 0.95
6787 | TORONTO BUTTONVILLE A | 10 | 9 | 19 | 13.5 | 4.5 | 0
6787 | TORONTO BUTTONVILLE A | 10 | 10 | 19 | 17.175 | 0.825 | 0
6788 | TORONTO BUTTONVILLE A | 10 | 9 | 20 | 12.5 | 5.5 | 0
6788 | TORONTO BUTTONVILLE A | 10 | 10 | 20 | 16.25 | 1.75 | 0
6789 | TORONTO BUTTONVILLE A | 10 | 9 | 21 | 12.1 | 5.9 | 0
6789 | TORONTO BUTTONVILLE A | 10 | 10 | 21 | 15.775 | 2.225 | 0
6790 | TORONTO BUTTONVILLE A | 10 | 9 | 22 | 13.3 | 4.7 | 0
6790 | TORONTO BUTTONVILLE A | 10 | 10 | 22 | 15.2 | 2.8 | 0
6791 | TORONTO BUTTONVILLE A | 10 | 9 | 23 | 15.4 | 2.6 | 0
6791 | TORONTO BUTTONVILLE A | 10 | 10 | 23 | 14.95 | 3.05 | 0
6792 | TORONTO BUTTONVILLE A | 10 | 9 | 24 | 16.5 | 1.5 | 0
6792 | TORONTO BUTTONVILLE A | 10 | 10 | 24 | 15.075 | 2.925 | 0
6793 | TORONTO BUTTONVILLE A | 10 | 10 | 1 | 17 | 1 | 0
6793 | TORONTO BUTTONVILLE A | 10 | 11 | 1 | 14.5 | 3.5 | 0
6794 | TORONTO BUTTONVILLE A | 10 | 10 | 2 | 16.5 | 1.5 | 0
6794 | TORONTO BUTTONVILLE A | 10 | 11 | 2 | 14.5 | 3.5 | 0
6795 | TORONTO BUTTONVILLE A | 10 | 10 | 3 | 16.2 | 1.8 | 0
6795 | TORONTO BUTTONVILLE A | 10 | 11 | 3 | 14.55 | 3.45 | 0
6796 | TORONTO BUTTONVILLE A | 10 | 10 | 4 | 16.2 | 1.8 | 0
6796 | TORONTO BUTTONVILLE A | 10 | 11 | 4 | 14.225 | 3.775 | 0
6797 | TORONTO BUTTONVILLE A | 10 | 10 | 5 | 15.2 | 2.8 | 0
6797 | TORONTO BUTTONVILLE A | 10 | 11 | 5 | 14.375 | 3.625 | 0
6798 | TORONTO BUTTONVILLE A | 10 | 10 | 6 | 15.2 | 2.8 | 0
6798 | TORONTO BUTTONVILLE A | 10 | 11 | 6 | 14.2 | 3.8 | 0
6799 | TORONTO BUTTONVILLE A | 10 | 10 | 7 | 15.2 | 2.8 | 0
6799 | TORONTO BUTTONVILLE A | 10 | 11 | 7 | 14.35 | 3.65 | 0
6800 | TORONTO BUTTONVILLE A | 10 | 10 | 8 | 16.1 | 1.9 | 0
6800 | TORONTO BUTTONVILLE A | 10 | 11 | 8 | 14.225 | 3.775 | 0
6801 | TORONTO BUTTONVILLE A | 10 | 10 | 9 | 17.6 | 0.4 | 0
6801 | TORONTO BUTTONVILLE A | 10 | 11 | 9 | 15.025 | 2.975 | 0
6802 | TORONTO BUTTONVILLE A | 10 | 10 | 10 | 19.2 | 0 | 1.2
6802 | TORONTO BUTTONVILLE A | 10 | 11 | 10 | 15.725 | 2.275 | 0
6803 | TORONTO BUTTONVILLE A | 10 | 10 | 11 | 20.8 | 0 | 2.8
6803 | TORONTO BUTTONVILLE A | 10 | 11 | 11 | 16.525 | 1.475 | 0
6804 | TORONTO BUTTONVILLE A | 10 | 10 | 12 | 21.6 | 0 | 3.6
6804 | TORONTO BUTTONVILLE A | 10 | 11 | 12 | 16.525 | 1.475 | 0
6805 | TORONTO BUTTONVILLE A | 10 | 10 | 13 | 21.1 | 0 | 3.1
6805 | TORONTO BUTTONVILLE A | 10 | 11 | 13 | 16.325 | 1.675 | 0
6806 | TORONTO BUTTONVILLE A | 10 | 10 | 14 | 20.8 | 0 | 2.8
6806 | TORONTO BUTTONVILLE A | 10 | 11 | 14 | 16.425 | 1.575 | 0
6807 | TORONTO BUTTONVILLE A | 10 | 10 | 15 | 20.4 | 0 | 2.4
6807 | TORONTO BUTTONVILLE A | 10 | 11 | 15 | 16.4 | 1.6 | 0
6808 | TORONTO BUTTONVILLE A | 10 | 10 | 16 | 17.4 | 0.6 | 0
6808 | TORONTO BUTTONVILLE A | 10 | 11 | 16 | 16.125 | 1.875 | 0
6809 | TORONTO BUTTONVILLE A | 10 | 10 | 17 | 18.1 | 0 | 0.1
6809 | TORONTO BUTTONVILLE A | 10 | 11 | 17 | 15.375 | 2.625 | 0
6810 | TORONTO BUTTONVILLE A | 10 | 10 | 18 | 17.3 | 0.7 | 0
6810 | TORONTO BUTTONVILLE A | 10 | 11 | 18 | 14.125 | 3.875 | 0
6811 | TORONTO BUTTONVILLE A | 10 | 10 | 19 | 14.6 | 3.4 | 0
6811 | TORONTO BUTTONVILLE A | 10 | 11 | 19 | 13.125 | 4.875 | 0
6812 | TORONTO BUTTONVILLE A | 10 | 10 | 20 | 13.7 | 4.3 | 0
6812 | TORONTO BUTTONVILLE A | 10 | 11 | 20 | 12.875 | 5.125 | 0
6813 | TORONTO BUTTONVILLE A | 10 | 10 | 21 | 13 | 5 | 0
6813 | TORONTO BUTTONVILLE A | 10 | 11 | 21 | 12.85 | 5.15 | 0
6814 | TORONTO BUTTONVILLE A | 10 | 10 | 22 | 12.2 | 5.8 | 0
6814 | TORONTO BUTTONVILLE A | 10 | 11 | 22 | 12.575 | 5.425 | 0
6815 | TORONTO BUTTONVILLE A | 10 | 10 | 23 | 11.4 | 6.6 | 0
6815 | TORONTO BUTTONVILLE A | 10 | 11 | 23 | 12.325 | 5.675 | 0
6816 | TORONTO BUTTONVILLE A | 10 | 10 | 24 | 9.9 | 8.1 | 0
6816 | TORONTO BUTTONVILLE A | 10 | 11 | 24 | 12.05 | 5.95 | 0
6817 | TORONTO BUTTONVILLE A | 10 | 11 | 1 | 8.5 | 9.5 | 0
6817 | TORONTO BUTTONVILLE A | 10 | 12 | 1 | 11.575 | 6.425 | 0
6818 | TORONTO BUTTONVILLE A | 10 | 11 | 2 | 7.3 | 10.7 | 0
6818 | TORONTO BUTTONVILLE A | 10 | 12 | 2 | 11.225 | 6.775 | 0
6819 | TORONTO BUTTONVILLE A | 10 | 11 | 3 | 6 | 12 | 0
6819 | TORONTO BUTTONVILLE A | 10 | 12 | 3 | 10.675 | 7.325 | 0
6820 | TORONTO BUTTONVILLE A | 10 | 11 | 4 | 5.2 | 12.8 | 0
6820 | TORONTO BUTTONVILLE A | 10 | 12 | 4 | 10.6 | 7.4 | 0
6821 | TORONTO BUTTONVILLE A | 10 | 11 | 5 | 4.3 | 13.7 | 0
6821 | TORONTO BUTTONVILLE A | 10 | 12 | 5 | 10.025 | 7.975 | 0
6822 | TORONTO BUTTONVILLE A | 10 | 11 | 6 | 3.7 | 14.3 | 0
6822 | TORONTO BUTTONVILLE A | 10 | 12 | 6 | 10.3 | 7.7 | 0
6823 | TORONTO BUTTONVILLE A | 10 | 11 | 7 | 3.6 | 14.4 | 0
6823 | TORONTO BUTTONVILLE A | 10 | 12 | 7 | 10.375 | 7.625 | 0
6824 | TORONTO BUTTONVILLE A | 10 | 11 | 8 | 4.2 | 13.8 | 0
6824 | TORONTO BUTTONVILLE A | 10 | 12 | 8 | 10.55 | 7.45 | 0
6825 | TORONTO BUTTONVILLE A | 10 | 11 | 9 | 6.2 | 11.8 | 0
6825 | TORONTO BUTTONVILLE A | 10 | 12 | 9 | 11.425 | 6.575 | 0
6826 | TORONTO BUTTONVILLE A | 10 | 11 | 10 | 7.4 | 10.6 | 0
6826 | TORONTO BUTTONVILLE A | 10 | 12 | 10 | 11.9 | 6.1 | 0
6827 | TORONTO BUTTONVILLE A | 10 | 11 | 11 | 9.6 | 8.4 | 0
6827 | TORONTO BUTTONVILLE A | 10 | 12 | 11 | 12.7 | 5.3 | 0
6828 | TORONTO BUTTONVILLE A | 10 | 11 | 12 | 9.2 | 8.8 | 0
6828 | TORONTO BUTTONVILLE A | 10 | 12 | 12 | 13.05 | 4.95 | 0
6829 | TORONTO BUTTONVILLE A | 10 | 11 | 13 | 11 | 7 | 0
6829 | TORONTO BUTTONVILLE A | 10 | 12 | 13 | 13.625 | 4.375 | 0
6830 | TORONTO BUTTONVILLE A | 10 | 11 | 14 | 11.3 | 6.7 | 0
6830 | TORONTO BUTTONVILLE A | 10 | 12 | 14 | 14.3 | 3.7 | 0
6831 | TORONTO BUTTONVILLE A | 10 | 11 | 15 | 11.3 | 6.7 | 0
6831 | TORONTO BUTTONVILLE A | 10 | 12 | 15 | 14.1 | 3.9 | 0
6832 | TORONTO BUTTONVILLE A | 10 | 11 | 16 | 11.3 | 6.7 | 0
6832 | TORONTO BUTTONVILLE A | 10 | 12 | 16 | 13.975 | 4.025 | 0
6833 | TORONTO BUTTONVILLE A | 10 | 11 | 17 | 10.5 | 7.5 | 0
6833 | TORONTO BUTTONVILLE A | 10 | 12 | 17 | 14.05 | 3.95 | 0
6834 | TORONTO BUTTONVILLE A | 10 | 11 | 18 | 9.8 | 8.2 | 0
6834 | TORONTO BUTTONVILLE A | 10 | 12 | 18 | 13.225 | 4.775 | 0
6835 | TORONTO BUTTONVILLE A | 10 | 11 | 19 | 8.9 | 9.1 | 0
6835 | TORONTO BUTTONVILLE A | 10 | 12 | 19 | 12.575 | 5.425 | 0
6836 | TORONTO BUTTONVILLE A | 10 | 11 | 20 | 7.8 | 10.2 | 0
6836 | TORONTO BUTTONVILLE A | 10 | 12 | 20 | 12.1 | 5.9 | 0
6837 | TORONTO BUTTONVILLE A | 10 | 11 | 21 | 7.3 | 10.7 | 0
6837 | TORONTO BUTTONVILLE A | 10 | 12 | 21 | 11.9 | 6.1 | 0
6838 | TORONTO BUTTONVILLE A | 10 | 11 | 22 | 6.9 | 11.1 | 0
6838 | TORONTO BUTTONVILLE A | 10 | 12 | 22 | 11.7 | 6.3 | 0
6839 | TORONTO BUTTONVILLE A | 10 | 11 | 23 | 6.9 | 11.1 | 0
6839 | TORONTO BUTTONVILLE A | 10 | 12 | 23 | 11.325 | 6.675 | 0
6840 | TORONTO BUTTONVILLE A | 10 | 11 | 24 | 6.6 | 11.4 | 0
6840 | TORONTO BUTTONVILLE A | 10 | 12 | 24 | 10.975 | 7.025 | 0
6841 | TORONTO BUTTONVILLE A | 10 | 12 | 1 | 6.3 | 11.7 | 0
6841 | TORONTO BUTTONVILLE A | 10 | 13 | 1 | 10.75 | 7.25 | 0
6842 | TORONTO BUTTONVILLE A | 10 | 12 | 2 | 6.4 | 11.6 | 0
6842 | TORONTO BUTTONVILLE A | 10 | 13 | 2 | 10.4 | 7.6 | 0
6843 | TORONTO BUTTONVILLE A | 10 | 12 | 3 | 6.1 | 11.9 | 0
6843 | TORONTO BUTTONVILLE A | 10 | 13 | 3 | 9.825 | 8.175 | 0
6844 | TORONTO BUTTONVILLE A | 10 | 12 | 4 | 6.7 | 11.3 | 0
6844 | TORONTO BUTTONVILLE A | 10 | 13 | 4 | 9.575 | 8.425 | 0
6845 | TORONTO BUTTONVILLE A | 10 | 12 | 5 | 6.3 | 11.7 | 0
6845 | TORONTO BUTTONVILLE A | 10 | 13 | 5 | 9.55 | 8.45 | 0
6846 | TORONTO BUTTONVILLE A | 10 | 12 | 6 | 7.5 | 10.5 | 0
6846 | TORONTO BUTTONVILLE A | 10 | 13 | 6 | 9.25 | 8.75 | 0
6847 | TORONTO BUTTONVILLE A | 10 | 12 | 7 | 8.3 | 9.7 | 0
6847 | TORONTO BUTTONVILLE A | 10 | 13 | 7 | 8.825 | 9.175 | 0
6848 | TORONTO BUTTONVILLE A | 10 | 12 | 8 | 8.4 | 9.6 | 0
6848 | TORONTO BUTTONVILLE A | 10 | 13 | 8 | 9.3 | 8.7 | 0
6849 | TORONTO BUTTONVILLE A | 10 | 12 | 9 | 10 | 8 | 0
6849 | TORONTO BUTTONVILLE A | 10 | 13 | 9 | 10.6 | 7.4 | 0
6850 | TORONTO BUTTONVILLE A | 10 | 12 | 10 | 11.5 | 6.5 | 0
6850 | TORONTO BUTTONVILLE A | 10 | 13 | 10 | 12.6 | 5.4 | 0
6851 | TORONTO BUTTONVILLE A | 10 | 12 | 11 | 13.2 | 4.8 | 0
6851 | TORONTO BUTTONVILLE A | 10 | 13 | 11 | 13.45 | 4.55 | 0
6852 | TORONTO BUTTONVILLE A | 10 | 12 | 12 | 14.2 | 3.8 | 0
6852 | TORONTO BUTTONVILLE A | 10 | 13 | 12 | 14.5 | 3.5 | 0
6853 | TORONTO BUTTONVILLE A | 10 | 12 | 13 | 14.4 | 3.6 | 0
6853 | TORONTO BUTTONVILLE A | 10 | 13 | 13 | 15 | 3 | 0
6854 | TORONTO BUTTONVILLE A | 10 | 12 | 14 | 14.9 | 3.1 | 0
6854 | TORONTO BUTTONVILLE A | 10 | 13 | 14 | 15.15 | 2.85 | 0
6855 | TORONTO BUTTONVILLE A | 10 | 12 | 15 | 15.6 | 2.4 | 0
6855 | TORONTO BUTTONVILLE A | 10 | 13 | 15 | 15.625 | 2.375 | 0
6856 | TORONTO BUTTONVILLE A | 10 | 12 | 16 | 15.2 | 2.8 | 0
6856 | TORONTO BUTTONVILLE A | 10 | 13 | 16 | 15.85 | 2.15 | 0
6857 | TORONTO BUTTONVILLE A | 10 | 12 | 17 | 14.1 | 3.9 | 0
6857 | TORONTO BUTTONVILLE A | 10 | 13 | 17 | 15.75 | 2.25 | 0
6858 | TORONTO BUTTONVILLE A | 10 | 12 | 18 | 14.3 | 3.7 | 0
6858 | TORONTO BUTTONVILLE A | 10 | 13 | 18 | 15.375 | 2.625 | 0
6859 | TORONTO BUTTONVILLE A | 10 | 12 | 19 | 14.3 | 3.7 | 0
6859 | TORONTO BUTTONVILLE A | 10 | 13 | 19 | 14.825 | 3.175 | 0
6860 | TORONTO BUTTONVILLE A | 10 | 12 | 20 | 14.3 | 3.7 | 0
6860 | TORONTO BUTTONVILLE A | 10 | 13 | 20 | 14.05 | 3.95 | 0
6861 | TORONTO BUTTONVILLE A | 10 | 12 | 21 | 14.4 | 3.6 | 0
6861 | TORONTO BUTTONVILLE A | 10 | 13 | 21 | 13.075 | 4.925 | 0
6862 | TORONTO BUTTONVILLE A | 10 | 12 | 22 | 14.2 | 3.8 | 0
6862 | TORONTO BUTTONVILLE A | 10 | 13 | 22 | 12.85 | 5.15 | 0
6863 | TORONTO BUTTONVILLE A | 10 | 12 | 23 | 12.7 | 5.3 | 0
6863 | TORONTO BUTTONVILLE A | 10 | 13 | 23 | 11.4 | 6.6 | 0
6864 | TORONTO BUTTONVILLE A | 10 | 12 | 24 | 11.9 | 6.1 | 0
6864 | TORONTO BUTTONVILLE A | 10 | 13 | 24 | 10.925 | 7.075 | 0
6865 | TORONTO BUTTONVILLE A | 10 | 13 | 1 | 12 | 6 | 0
6865 | TORONTO BUTTONVILLE A | 10 | 14 | 1 | 10.15 | 7.85 | 0
6866 | TORONTO BUTTONVILLE A | 10 | 13 | 2 | 12.2 | 5.8 | 0
6866 | TORONTO BUTTONVILLE A | 10 | 14 | 2 | 9.25 | 8.75 | 0
6867 | TORONTO BUTTONVILLE A | 10 | 13 | 3 | 12.2 | 5.8 | 0
6867 | TORONTO BUTTONVILLE A | 10 | 14 | 3 | 9.075 | 8.925 | 0
6868 | TORONTO BUTTONVILLE A | 10 | 13 | 4 | 11.9 | 6.1 | 0
6868 | TORONTO BUTTONVILLE A | 10 | 14 | 4 | 8.65 | 9.35 | 0
6869 | TORONTO BUTTONVILLE A | 10 | 13 | 5 | 11.9 | 6.1 | 0
6869 | TORONTO BUTTONVILLE A | 10 | 14 | 5 | 8.475 | 9.525 | 0
6870 | TORONTO BUTTONVILLE A | 10 | 13 | 6 | 11.7 | 6.3 | 0
6870 | TORONTO BUTTONVILLE A | 10 | 14 | 6 | 8.525 | 9.475 | 0
6871 | TORONTO BUTTONVILLE A | 10 | 13 | 7 | 10.7 | 7.3 | 0
6871 | TORONTO BUTTONVILLE A | 10 | 14 | 7 | 8.825 | 9.175 | 0
6872 | TORONTO BUTTONVILLE A | 10 | 13 | 8 | 10.2 | 7.8 | 0
6872 | TORONTO BUTTONVILLE A | 10 | 14 | 8 | 9.05 | 8.95 | 0
6873 | TORONTO BUTTONVILLE A | 10 | 13 | 9 | 11.1 | 6.9 | 0
6873 | TORONTO BUTTONVILLE A | 10 | 14 | 9 | 10.075 | 7.925 | 0
6874 | TORONTO BUTTONVILLE A | 10 | 13 | 10 | 12.1 | 5.9 | 0
6874 | TORONTO BUTTONVILLE A | 10 | 14 | 10 | 12.375 | 5.625 | 0
6875 | TORONTO BUTTONVILLE A | 10 | 13 | 11 | 13.5 | 4.5 | 0
6875 | TORONTO BUTTONVILLE A | 10 | 14 | 11 | 14.2 | 3.8 | 0
6876 | TORONTO BUTTONVILLE A | 10 | 13 | 12 | 14.6 | 3.4 | 0
6876 | TORONTO BUTTONVILLE A | 10 | 14 | 12 | 15.2 | 2.8 | 0
6877 | TORONTO BUTTONVILLE A | 10 | 13 | 13 | 15.9 | 2.1 | 0
6877 | TORONTO BUTTONVILLE A | 10 | 14 | 13 | 15.825 | 2.175 | 0
6878 | TORONTO BUTTONVILLE A | 10 | 13 | 14 | 16.5 | 1.5 | 0
6878 | TORONTO BUTTONVILLE A | 10 | 14 | 14 | 16.1 | 1.9 | 0
6879 | TORONTO BUTTONVILLE A | 10 | 13 | 15 | 17.9 | 0.1 | 0
6879 | TORONTO BUTTONVILLE A | 10 | 14 | 15 | 16.15 | 1.85 | 0
6880 | TORONTO BUTTONVILLE A | 10 | 13 | 16 | 17.8 | 0.2 | 0
6880 | TORONTO BUTTONVILLE A | 10 | 14 | 16 | 16.35 | 1.65 | 0
6881 | TORONTO BUTTONVILLE A | 10 | 13 | 17 | 17.6 | 0.4 | 0
6881 | TORONTO BUTTONVILLE A | 10 | 14 | 17 | 15.925 | 2.075 | 0
6882 | TORONTO BUTTONVILLE A | 10 | 13 | 18 | 16.6 | 1.4 | 0
6882 | TORONTO BUTTONVILLE A | 10 | 14 | 18 | 15.1 | 2.9 | 0
6883 | TORONTO BUTTONVILLE A | 10 | 13 | 19 | 15.1 | 2.9 | 0
6883 | TORONTO BUTTONVILLE A | 10 | 14 | 19 | 13.675 | 4.325 | 0
6884 | TORONTO BUTTONVILLE A | 10 | 13 | 20 | 13.3 | 4.7 | 0
6884 | TORONTO BUTTONVILLE A | 10 | 14 | 20 | 13 | 5 | 0
6885 | TORONTO BUTTONVILLE A | 10 | 13 | 21 | 13.2 | 4.8 | 0
6885 | TORONTO BUTTONVILLE A | 10 | 14 | 21 | 12.2 | 5.8 | 0
6886 | TORONTO BUTTONVILLE A | 10 | 13 | 22 | 11.9 | 6.1 | 0
6886 | TORONTO BUTTONVILLE A | 10 | 14 | 22 | 11.7 | 6.3 | 0
6887 | TORONTO BUTTONVILLE A | 10 | 13 | 23 | 12.8 | 5.2 | 0
6887 | TORONTO BUTTONVILLE A | 10 | 14 | 23 | 11.175 | 6.825 | 0
6888 | TORONTO BUTTONVILLE A | 10 | 13 | 24 | 12.1 | 5.9 | 0
6888 | TORONTO BUTTONVILLE A | 10 | 14 | 24 | 10.875 | 7.125 | 0
6889 | TORONTO BUTTONVILLE A | 10 | 14 | 1 | 12 | 6 | 0
6889 | TORONTO BUTTONVILLE A | 10 | 15 | 1 | 10.75 | 7.25 | 0
6890 | TORONTO BUTTONVILLE A | 10 | 14 | 2 | 10.9 | 7.1 | 0
6890 | TORONTO BUTTONVILLE A | 10 | 15 | 2 | 10.7 | 7.3 | 0
6891 | TORONTO BUTTONVILLE A | 10 | 14 | 3 | 10.5 | 7.5 | 0
6891 | TORONTO BUTTONVILLE A | 10 | 15 | 3 | 10.225 | 7.775 | 0
6892 | TORONTO BUTTONVILLE A | 10 | 14 | 4 | 8.9 | 9.1 | 0
6892 | TORONTO BUTTONVILLE A | 10 | 15 | 4 | 10.775 | 7.225 | 0
6893 | TORONTO BUTTONVILLE A | 10 | 14 | 5 | 8.8 | 9.2 | 0
6893 | TORONTO BUTTONVILLE A | 10 | 15 | 5 | 10.975 | 7.025 | 0
6894 | TORONTO BUTTONVILLE A | 10 | 14 | 6 | 9.2 | 8.8 | 0
6894 | TORONTO BUTTONVILLE A | 10 | 15 | 6 | 10.7 | 7.3 | 0
6895 | TORONTO BUTTONVILLE A | 10 | 14 | 7 | 8.3 | 9.7 | 0
6895 | TORONTO BUTTONVILLE A | 10 | 15 | 7 | 10.925 | 7.075 | 0
6896 | TORONTO BUTTONVILLE A | 10 | 14 | 8 | 8.4 | 9.6 | 0
6896 | TORONTO BUTTONVILLE A | 10 | 15 | 8 | 11.475 | 6.525 | 0
6897 | TORONTO BUTTONVILLE A | 10 | 14 | 9 | 10.2 | 7.8 | 0
6897 | TORONTO BUTTONVILLE A | 10 | 15 | 9 | 12.8 | 5.2 | 0
6898 | TORONTO BUTTONVILLE A | 10 | 14 | 10 | 12.6 | 5.4 | 0
6898 | TORONTO BUTTONVILLE A | 10 | 15 | 10 | 14.15 | 3.85 | 0
6899 | TORONTO BUTTONVILLE A | 10 | 14 | 11 | 14.3 | 3.7 | 0
6899 | TORONTO BUTTONVILLE A | 10 | 15 | 11 | 15.2 | 2.8 | 0
6900 | TORONTO BUTTONVILLE A | 10 | 14 | 12 | 15.6 | 2.4 | 0
6900 | TORONTO BUTTONVILLE A | 10 | 15 | 12 | 15.825 | 2.175 | 0
6901 | TORONTO BUTTONVILLE A | 10 | 14 | 13 | 16.8 | 1.2 | 0
6901 | TORONTO BUTTONVILLE A | 10 | 15 | 13 | 16.6 | 1.4 | 0
6902 | TORONTO BUTTONVILLE A | 10 | 14 | 14 | 16.5 | 1.5 | 0
6902 | TORONTO BUTTONVILLE A | 10 | 15 | 14 | 16.875 | 1.125 | 0
6903 | TORONTO BUTTONVILLE A | 10 | 14 | 15 | 16.6 | 1.4 | 0
6903 | TORONTO BUTTONVILLE A | 10 | 15 | 15 | 16.85 | 1.15 | 0
6904 | TORONTO BUTTONVILLE A | 10 | 14 | 16 | 16.3 | 1.7 | 0
6904 | TORONTO BUTTONVILLE A | 10 | 15 | 16 | 15.35 | 2.65 | 0
6905 | TORONTO BUTTONVILLE A | 10 | 14 | 17 | 15.3 | 2.7 | 0
6905 | TORONTO BUTTONVILLE A | 10 | 15 | 17 | 15.075 | 2.925 | 0
6906 | TORONTO BUTTONVILLE A | 10 | 14 | 18 | 14.2 | 3.8 | 0
6906 | TORONTO BUTTONVILLE A | 10 | 15 | 18 | 13.45 | 4.55 | 0
6907 | TORONTO BUTTONVILLE A | 10 | 14 | 19 | 13.3 | 4.7 | 0
6907 | TORONTO BUTTONVILLE A | 10 | 15 | 19 | 12.175 | 5.825 | 0
6908 | TORONTO BUTTONVILLE A | 10 | 14 | 20 | 13.1 | 4.9 | 0
6908 | TORONTO BUTTONVILLE A | 10 | 15 | 20 | 10.425 | 7.575 | 0
6909 | TORONTO BUTTONVILLE A | 10 | 14 | 21 | 12.8 | 5.2 | 0
6909 | TORONTO BUTTONVILLE A | 10 | 15 | 21 | 9.625 | 8.375 | 0
6910 | TORONTO BUTTONVILLE A | 10 | 14 | 22 | 12.2 | 5.8 | 0
6910 | TORONTO BUTTONVILLE A | 10 | 15 | 22 | 9.25 | 8.75 | 0
6911 | TORONTO BUTTONVILLE A | 10 | 14 | 23 | 12 | 6 | 0
6911 | TORONTO BUTTONVILLE A | 10 | 15 | 23 | 8.875 | 9.125 | 0
6912 | TORONTO BUTTONVILLE A | 10 | 14 | 24 | 11.9 | 6.1 | 0
6912 | TORONTO BUTTONVILLE A | 10 | 15 | 24 | 8.575 | 9.425 | 0
6913 | TORONTO BUTTONVILLE A | 10 | 15 | 1 | 12.5 | 5.5 | 0
6913 | TORONTO BUTTONVILLE A | 10 | 16 | 1 | 8.775 | 9.225 | 0
6914 | TORONTO BUTTONVILLE A | 10 | 15 | 2 | 12.6 | 5.4 | 0
6914 | TORONTO BUTTONVILLE A | 10 | 16 | 2 | 8.575 | 9.425 | 0
6915 | TORONTO BUTTONVILLE A | 10 | 15 | 3 | 12.5 | 5.5 | 0
6915 | TORONTO BUTTONVILLE A | 10 | 16 | 3 | 8.425 | 9.575 | 0
6916 | TORONTO BUTTONVILLE A | 10 | 15 | 4 | 12.3 | 5.7 | 0
6916 | TORONTO BUTTONVILLE A | 10 | 16 | 4 | 8.1 | 9.9 | 0
6917 | TORONTO BUTTONVILLE A | 10 | 15 | 5 | 14.1 | 3.9 | 0
6917 | TORONTO BUTTONVILLE A | 10 | 16 | 5 | 8.05 | 9.95 | 0
6918 | TORONTO BUTTONVILLE A | 10 | 15 | 6 | 15.6 | 2.4 | 0
6918 | TORONTO BUTTONVILLE A | 10 | 16 | 6 | 7.65 | 10.35 | 0
6919 | TORONTO BUTTONVILLE A | 10 | 15 | 7 | 14.9 | 3.1 | 0
6919 | TORONTO BUTTONVILLE A | 10 | 16 | 7 | 7.4 | 10.6 | 0
6920 | TORONTO BUTTONVILLE A | 10 | 15 | 8 | 14.5 | 3.5 | 0
6920 | TORONTO BUTTONVILLE A | 10 | 16 | 8 | 7.675 | 10.325 | 0
6921 | TORONTO BUTTONVILLE A | 10 | 15 | 9 | 14.3 | 3.7 | 0
6921 | TORONTO BUTTONVILLE A | 10 | 16 | 9 | 8.175 | 9.825 | 0
6922 | TORONTO BUTTONVILLE A | 10 | 15 | 10 | 14.6 | 3.4 | 0
6922 | TORONTO BUTTONVILLE A | 10 | 16 | 10 | 8.8 | 9.2 | 0
6923 | TORONTO BUTTONVILLE A | 10 | 15 | 11 | 13.7 | 4.3 | 0
6923 | TORONTO BUTTONVILLE A | 10 | 16 | 11 | 9.25 | 8.75 | 0
6924 | TORONTO BUTTONVILLE A | 10 | 15 | 12 | 12.2 | 5.8 | 0
6924 | TORONTO BUTTONVILLE A | 10 | 16 | 12 | 9.45 | 8.55 | 0
6925 | TORONTO BUTTONVILLE A | 10 | 15 | 13 | 11.2 | 6.8 | 0
6925 | TORONTO BUTTONVILLE A | 10 | 16 | 13 | 10.175 | 7.825 | 0
6926 | TORONTO BUTTONVILLE A | 10 | 15 | 14 | 11.1 | 6.9 | 0
6926 | TORONTO BUTTONVILLE A | 10 | 16 | 14 | 10.525 | 7.475 | 0
6927 | TORONTO BUTTONVILLE A | 10 | 15 | 15 | 11 | 7 | 0
6927 | TORONTO BUTTONVILLE A | 10 | 16 | 15 | 10.425 | 7.575 | 0
6928 | TORONTO BUTTONVILLE A | 10 | 15 | 16 | 10.8 | 7.2 | 0
6928 | TORONTO BUTTONVILLE A | 10 | 16 | 16 | 10.975 | 7.025 | 0
6929 | TORONTO BUTTONVILLE A | 10 | 15 | 17 | 10.3 | 7.7 | 0
6929 | TORONTO BUTTONVILLE A | 10 | 16 | 17 | 10.825 | 7.175 | 0
6930 | TORONTO BUTTONVILLE A | 10 | 15 | 18 | 10.3 | 7.7 | 0
6930 | TORONTO BUTTONVILLE A | 10 | 16 | 18 | 10.225 | 7.775 | 0
6931 | TORONTO BUTTONVILLE A | 10 | 15 | 19 | 9.8 | 8.2 | 0
6931 | TORONTO BUTTONVILLE A | 10 | 16 | 19 | 9.475 | 8.525 | 0
6932 | TORONTO BUTTONVILLE A | 10 | 15 | 20 | 9.7 | 8.3 | 0
6932 | TORONTO BUTTONVILLE A | 10 | 16 | 20 | 8.475 | 9.525 | 0
6933 | TORONTO BUTTONVILLE A | 10 | 15 | 21 | 9.4 | 8.6 | 0
6933 | TORONTO BUTTONVILLE A | 10 | 16 | 21 | 8.075 | 9.925 | 0
6934 | TORONTO BUTTONVILLE A | 10 | 15 | 22 | 9.2 | 8.8 | 0
6934 | TORONTO BUTTONVILLE A | 10 | 16 | 22 | 7.6 | 10.4 | 0
6935 | TORONTO BUTTONVILLE A | 10 | 15 | 23 | 8.7 | 9.3 | 0
6935 | TORONTO BUTTONVILLE A | 10 | 16 | 23 | 7.35 | 10.65 | 0
6936 | TORONTO BUTTONVILLE A | 10 | 15 | 24 | 8.8 | 9.2 | 0
6936 | TORONTO BUTTONVILLE A | 10 | 16 | 24 | 7.05 | 10.95 | 0
6937 | TORONTO BUTTONVILLE A | 10 | 16 | 1 | 8.2 | 9.8 | 0
6937 | TORONTO BUTTONVILLE A | 10 | 17 | 1 | 6.55 | 11.45 | 0
6938 | TORONTO BUTTONVILLE A | 10 | 16 | 2 | 7.9 | 10.1 | 0
6938 | TORONTO BUTTONVILLE A | 10 | 17 | 2 | 6.3 | 11.7 | 0
6939 | TORONTO BUTTONVILLE A | 10 | 16 | 3 | 7.3 | 10.7 | 0
6939 | TORONTO BUTTONVILLE A | 10 | 17 | 3 | 6 | 12 | 0
6940 | TORONTO BUTTONVILLE A | 10 | 16 | 4 | 6.7 | 11.3 | 0
6940 | TORONTO BUTTONVILLE A | 10 | 17 | 4 | 5.975 | 12.025 | 0
6941 | TORONTO BUTTONVILLE A | 10 | 16 | 5 | 6.5 | 11.5 | 0
6941 | TORONTO BUTTONVILLE A | 10 | 17 | 5 | 5.9 | 12.1 | 0
6942 | TORONTO BUTTONVILLE A | 10 | 16 | 6 | 6.3 | 11.7 | 0
6942 | TORONTO BUTTONVILLE A | 10 | 17 | 6 | 5.675 | 12.325 | 0
6943 | TORONTO BUTTONVILLE A | 10 | 16 | 7 | 5.7 | 12.3 | 0
6943 | TORONTO BUTTONVILLE A | 10 | 17 | 7 | 5.775 | 12.225 | 0
6944 | TORONTO BUTTONVILLE A | 10 | 16 | 8 | 4.8 | 13.2 | 0
6944 | TORONTO BUTTONVILLE A | 10 | 17 | 8 | 5.875 | 12.125 | 0
6945 | TORONTO BUTTONVILLE A | 10 | 16 | 9 | 5.7 | 12.3 | 0
6945 | TORONTO BUTTONVILLE A | 10 | 17 | 9 | 7.5 | 10.5 | 0
6946 | TORONTO BUTTONVILLE A | 10 | 16 | 10 | 7.2 | 10.8 | 0
6946 | TORONTO BUTTONVILLE A | 10 | 17 | 10 | 8.225 | 9.775 | 0
6947 | TORONTO BUTTONVILLE A | 10 | 16 | 11 | 7.9 | 10.1 | 0
6947 | TORONTO BUTTONVILLE A | 10 | 17 | 11 | 9.575 | 8.425 | 0
6948 | TORONTO BUTTONVILLE A | 10 | 16 | 12 | 8.7 | 9.3 | 0
6948 | TORONTO BUTTONVILLE A | 10 | 17 | 12 | 10.9 | 7.1 | 0
6949 | TORONTO BUTTONVILLE A | 10 | 16 | 13 | 9.7 | 8.3 | 0
6949 | TORONTO BUTTONVILLE A | 10 | 17 | 13 | 10.325 | 7.675 | 0
6950 | TORONTO BUTTONVILLE A | 10 | 16 | 14 | 10.8 | 7.2 | 0
6950 | TORONTO BUTTONVILLE A | 10 | 17 | 14 | 10.9 | 7.1 | 0
6951 | TORONTO BUTTONVILLE A | 10 | 16 | 15 | 10.9 | 7.1 | 0
6951 | TORONTO BUTTONVILLE A | 10 | 17 | 15 | 11.775 | 6.225 | 0
6952 | TORONTO BUTTONVILLE A | 10 | 16 | 16 | 11.2 | 6.8 | 0
6952 | TORONTO BUTTONVILLE A | 10 | 17 | 16 | 11.45 | 6.55 | 0
6953 | TORONTO BUTTONVILLE A | 10 | 16 | 17 | 10.2 | 7.8 | 0
6953 | TORONTO BUTTONVILLE A | 10 | 17 | 17 | 11.05 | 6.95 | 0
6954 | TORONTO BUTTONVILLE A | 10 | 16 | 18 | 9.9 | 8.1 | 0
6954 | TORONTO BUTTONVILLE A | 10 | 17 | 18 | 10.125 | 7.875 | 0
6955 | TORONTO BUTTONVILLE A | 10 | 16 | 19 | 8.7 | 9.3 | 0
6955 | TORONTO BUTTONVILLE A | 10 | 17 | 19 | 9.4 | 8.6 | 0
6956 | TORONTO BUTTONVILLE A | 10 | 16 | 20 | 7 | 11 | 0
6956 | TORONTO BUTTONVILLE A | 10 | 17 | 20 | 8.875 | 9.125 | 0
6957 | TORONTO BUTTONVILLE A | 10 | 16 | 21 | 6.7 | 11.3 | 0
6957 | TORONTO BUTTONVILLE A | 10 | 17 | 21 | 8.4 | 9.6 | 0
6958 | TORONTO BUTTONVILLE A | 10 | 16 | 22 | 5.6 | 12.4 | 0
6958 | TORONTO BUTTONVILLE A | 10 | 17 | 22 | 7.925 | 10.075 | 0
6959 | TORONTO BUTTONVILLE A | 10 | 16 | 23 | 5.1 | 12.9 | 0
6959 | TORONTO BUTTONVILLE A | 10 | 17 | 23 | 7.875 | 10.125 | 0
6960 | TORONTO BUTTONVILLE A | 10 | 16 | 24 | 4.7 | 13.3 | 0
6960 | TORONTO BUTTONVILLE A | 10 | 17 | 24 | 7.4 | 10.6 | 0
6961 | TORONTO BUTTONVILLE A | 10 | 17 | 1 | 3.9 | 14.1 | 0
6961 | TORONTO BUTTONVILLE A | 10 | 18 | 1 | 7 | 11 | 0
6962 | TORONTO BUTTONVILLE A | 10 | 17 | 2 | 3.3 | 14.7 | 0
6962 | TORONTO BUTTONVILLE A | 10 | 18 | 2 | 6.025 | 11.975 | 0
6963 | TORONTO BUTTONVILLE A | 10 | 17 | 3 | 2.4 | 15.6 | 0
6963 | TORONTO BUTTONVILLE A | 10 | 18 | 3 | 5.55 | 12.45 | 0
6964 | TORONTO BUTTONVILLE A | 10 | 17 | 4 | 1.3 | 16.7 | 0
6964 | TORONTO BUTTONVILLE A | 10 | 18 | 4 | 5.375 | 12.625 | 0
6965 | TORONTO BUTTONVILLE A | 10 | 17 | 5 | 0.5 | 17.5 | 0
6965 | TORONTO BUTTONVILLE A | 10 | 18 | 5 | 4.925 | 13.075 | 0
6966 | TORONTO BUTTONVILLE A | 10 | 17 | 6 | 0.5 | 17.5 | 0
6966 | TORONTO BUTTONVILLE A | 10 | 18 | 6 | 5.125 | 12.875 | 0
6967 | TORONTO BUTTONVILLE A | 10 | 17 | 7 | 0.5 | 17.5 | 0
6967 | TORONTO BUTTONVILLE A | 10 | 18 | 7 | 4.975 | 13.025 | 0
6968 | TORONTO BUTTONVILLE A | 10 | 17 | 8 | 0.9 | 17.1 | 0
6968 | TORONTO BUTTONVILLE A | 10 | 18 | 8 | 5.05 | 12.95 | 0
6969 | TORONTO BUTTONVILLE A | 10 | 17 | 9 | 6.7 | 11.3 | 0
6969 | TORONTO BUTTONVILLE A | 10 | 18 | 9 | 6.525 | 11.475 | 0
6970 | TORONTO BUTTONVILLE A | 10 | 17 | 10 | 9.4 | 8.6 | 0
6970 | TORONTO BUTTONVILLE A | 10 | 18 | 10 | 7.825 | 10.175 | 0
6971 | TORONTO BUTTONVILLE A | 10 | 17 | 11 | 10.8 | 7.2 | 0
6971 | TORONTO BUTTONVILLE A | 10 | 18 | 11 | 8.775 | 9.225 | 0
6972 | TORONTO BUTTONVILLE A | 10 | 17 | 12 | 11.7 | 6.3 | 0
6972 | TORONTO BUTTONVILLE A | 10 | 18 | 12 | 10.225 | 7.775 | 0
6973 | TORONTO BUTTONVILLE A | 10 | 17 | 13 | 11.5 | 6.5 | 0
6973 | TORONTO BUTTONVILLE A | 10 | 18 | 13 | 10.9 | 7.1 | 0
6974 | TORONTO BUTTONVILLE A | 10 | 17 | 14 | 12.9 | 5.1 | 0
6974 | TORONTO BUTTONVILLE A | 10 | 18 | 14 | 11.375 | 6.625 | 0
6975 | TORONTO BUTTONVILLE A | 10 | 17 | 15 | 12.4 | 5.6 | 0
6975 | TORONTO BUTTONVILLE A | 10 | 18 | 15 | 12.475 | 5.525 | 0
6976 | TORONTO BUTTONVILLE A | 10 | 17 | 16 | 12.8 | 5.2 | 0
6976 | TORONTO BUTTONVILLE A | 10 | 18 | 16 | 12.65 | 5.35 | 0
6977 | TORONTO BUTTONVILLE A | 10 | 17 | 17 | 12.4 | 5.6 | 0
6977 | TORONTO BUTTONVILLE A | 10 | 18 | 17 | 12.275 | 5.725 | 0
6978 | TORONTO BUTTONVILLE A | 10 | 17 | 18 | 11.3 | 6.7 | 0
6978 | TORONTO BUTTONVILLE A | 10 | 18 | 18 | 11 | 7 | 0
6979 | TORONTO BUTTONVILLE A | 10 | 17 | 19 | 9.9 | 8.1 | 0
6979 | TORONTO BUTTONVILLE A | 10 | 18 | 19 | 9.625 | 8.375 | 0
6980 | TORONTO BUTTONVILLE A | 10 | 17 | 20 | 9.3 | 8.7 | 0
6980 | TORONTO BUTTONVILLE A | 10 | 18 | 20 | 8.675 | 9.325 | 0
6981 | TORONTO BUTTONVILLE A | 10 | 17 | 21 | 8.6 | 9.4 | 0
6981 | TORONTO BUTTONVILLE A | 10 | 18 | 21 | 8 | 10 | 0
6982 | TORONTO BUTTONVILLE A | 10 | 17 | 22 | 8.8 | 9.2 | 0
6982 | TORONTO BUTTONVILLE A | 10 | 18 | 22 | 7.5 | 10.5 | 0
6983 | TORONTO BUTTONVILLE A | 10 | 17 | 23 | 9.2 | 8.8 | 0
6983 | TORONTO BUTTONVILLE A | 10 | 18 | 23 | 6.825 | 11.175 | 0
6984 | TORONTO BUTTONVILLE A | 10 | 17 | 24 | 9.3 | 8.7 | 0
6984 | TORONTO BUTTONVILLE A | 10 | 18 | 24 | 6.55 | 11.45 | 0
6985 | TORONTO BUTTONVILLE A | 10 | 18 | 1 | 9.2 | 8.8 | 0
6985 | TORONTO BUTTONVILLE A | 10 | 19 | 1 | 6.45 | 11.55 | 0
6986 | TORONTO BUTTONVILLE A | 10 | 18 | 2 | 9.1 | 8.9 | 0
6986 | TORONTO BUTTONVILLE A | 10 | 19 | 2 | 6.175 | 11.825 | 0
6987 | TORONTO BUTTONVILLE A | 10 | 18 | 3 | 9.5 | 8.5 | 0
6987 | TORONTO BUTTONVILLE A | 10 | 19 | 3 | 6.375 | 11.625 | 0
6988 | TORONTO BUTTONVILLE A | 10 | 18 | 4 | 10.3 | 7.7 | 0
6988 | TORONTO BUTTONVILLE A | 10 | 19 | 4 | 6.175 | 11.825 | 0
6989 | TORONTO BUTTONVILLE A | 10 | 18 | 5 | 10.6 | 7.4 | 0
6989 | TORONTO BUTTONVILLE A | 10 | 19 | 5 | 6.175 | 11.825 | 0
6990 | TORONTO BUTTONVILLE A | 10 | 18 | 6 | 11.2 | 6.8 | 0
6990 | TORONTO BUTTONVILLE A | 10 | 19 | 6 | 6.175 | 11.825 | 0
6991 | TORONTO BUTTONVILLE A | 10 | 18 | 7 | 11.3 | 6.7 | 0
6991 | TORONTO BUTTONVILLE A | 10 | 19 | 7 | 6.125 | 11.875 | 0
6992 | TORONTO BUTTONVILLE A | 10 | 18 | 8 | 11.4 | 6.6 | 0
6992 | TORONTO BUTTONVILLE A | 10 | 19 | 8 | 6.375 | 11.625 | 0
6993 | TORONTO BUTTONVILLE A | 10 | 18 | 9 | 11.6 | 6.4 | 0
6993 | TORONTO BUTTONVILLE A | 10 | 19 | 9 | 7.975 | 10.025 | 0
6994 | TORONTO BUTTONVILLE A | 10 | 18 | 10 | 12.3 | 5.7 | 0
6994 | TORONTO BUTTONVILLE A | 10 | 19 | 10 | 10.475 | 7.525 | 0
6995 | TORONTO BUTTONVILLE A | 10 | 18 | 11 | 12.4 | 5.6 | 0
6995 | TORONTO BUTTONVILLE A | 10 | 19 | 11 | 13 | 5 | 0
6996 | TORONTO BUTTONVILLE A | 10 | 18 | 12 | 12.6 | 5.4 | 0
6996 | TORONTO BUTTONVILLE A | 10 | 19 | 12 | 14.225 | 3.775 | 0
6997 | TORONTO BUTTONVILLE A | 10 | 18 | 13 | 12.7 | 5.3 | 0
6997 | TORONTO BUTTONVILLE A | 10 | 19 | 13 | 15.25 | 2.75 | 0
6998 | TORONTO BUTTONVILLE A | 10 | 18 | 14 | 12.5 | 5.5 | 0
6998 | TORONTO BUTTONVILLE A | 10 | 19 | 14 | 16.475 | 1.525 | 0
6999 | TORONTO BUTTONVILLE A | 10 | 18 | 15 | 12.5 | 5.5 | 0
6999 | TORONTO BUTTONVILLE A | 10 | 19 | 15 | 16.925 | 1.075 | 0
7000 | TORONTO BUTTONVILLE A | 10 | 18 | 16 | 12.8 | 5.2 | 0
7000 | TORONTO BUTTONVILLE A | 10 | 19 | 16 | 16.65 | 1.35 | 0
7001 | TORONTO BUTTONVILLE A | 10 | 18 | 17 | 13 | 5 | 0
7001 | TORONTO BUTTONVILLE A | 10 | 19 | 17 | 15.9 | 2.1 | 0
7002 | TORONTO BUTTONVILLE A | 10 | 18 | 18 | 12.8 | 5.2 | 0
7002 | TORONTO BUTTONVILLE A | 10 | 19 | 18 | 14.675 | 3.325 | 0
7003 | TORONTO BUTTONVILLE A | 10 | 18 | 19 | 13 | 5 | 0
7003 | TORONTO BUTTONVILLE A | 10 | 19 | 19 | 13.3 | 4.7 | 0
7004 | TORONTO BUTTONVILLE A | 10 | 18 | 20 | 12.7 | 5.3 | 0
7004 | TORONTO BUTTONVILLE A | 10 | 19 | 20 | 12.4 | 5.6 | 0
7005 | TORONTO BUTTONVILLE A | 10 | 18 | 21 | 12.3 | 5.7 | 0
7005 | TORONTO BUTTONVILLE A | 10 | 19 | 21 | 11.625 | 6.375 | 0
7006 | TORONTO BUTTONVILLE A | 10 | 18 | 22 | 10.6 | 7.4 | 0
7006 | TORONTO BUTTONVILLE A | 10 | 19 | 22 | 11.175 | 6.825 | 0
7007 | TORONTO BUTTONVILLE A | 10 | 18 | 23 | 10.6 | 7.4 | 0
7007 | TORONTO BUTTONVILLE A | 10 | 19 | 23 | 10.5 | 7.5 | 0
7008 | TORONTO BUTTONVILLE A | 10 | 18 | 24 | 9.6 | 8.4 | 0
7008 | TORONTO BUTTONVILLE A | 10 | 19 | 24 | 9.75 | 8.25 | 0
7009 | TORONTO BUTTONVILLE A | 10 | 19 | 1 | 6.5 | 11.5 | 0
7009 | TORONTO BUTTONVILLE A | 10 | 20 | 1 | 8.975 | 9.025 | 0
7010 | TORONTO BUTTONVILLE A | 10 | 19 | 2 | 6.1 | 11.9 | 0
7010 | TORONTO BUTTONVILLE A | 10 | 20 | 2 | 9.35 | 8.65 | 0
7011 | TORONTO BUTTONVILLE A | 10 | 19 | 3 | 6 | 12 | 0
7011 | TORONTO BUTTONVILLE A | 10 | 20 | 3 | 9.275 | 8.725 | 0
7012 | TORONTO BUTTONVILLE A | 10 | 19 | 4 | 6.1 | 11.9 | 0
7012 | TORONTO BUTTONVILLE A | 10 | 20 | 4 | 9.475 | 8.525 | 0
7013 | TORONTO BUTTONVILLE A | 10 | 19 | 5 | 6.2 | 11.8 | 0
7013 | TORONTO BUTTONVILLE A | 10 | 20 | 5 | 9.525 | 8.475 | 0
7014 | TORONTO BUTTONVILLE A | 10 | 19 | 6 | 5.8 | 12.2 | 0
7014 | TORONTO BUTTONVILLE A | 10 | 20 | 6 | 9.4 | 8.6 | 0
7015 | TORONTO BUTTONVILLE A | 10 | 19 | 7 | 5.7 | 12.3 | 0
7015 | TORONTO BUTTONVILLE A | 10 | 20 | 7 | 8.4 | 9.6 | 0
7016 | TORONTO BUTTONVILLE A | 10 | 19 | 8 | 5.6 | 12.4 | 0
7016 | TORONTO BUTTONVILLE A | 10 | 20 | 8 | 8.375 | 9.625 | 0
7017 | TORONTO BUTTONVILLE A | 10 | 19 | 9 | 6 | 12 | 0
7017 | TORONTO BUTTONVILLE A | 10 | 20 | 9 | 10.475 | 7.525 | 0
7018 | TORONTO BUTTONVILLE A | 10 | 19 | 10 | 6.1 | 11.9 | 0
7018 | TORONTO BUTTONVILLE A | 10 | 20 | 10 | 12.05 | 5.95 | 0
7019 | TORONTO BUTTONVILLE A | 10 | 19 | 11 | 6.2 | 11.8 | 0
7019 | TORONTO BUTTONVILLE A | 10 | 20 | 11 | 13.925 | 4.075 | 0
7020 | TORONTO BUTTONVILLE A | 10 | 19 | 12 | 6.7 | 11.3 | 0
7020 | TORONTO BUTTONVILLE A | 10 | 20 | 12 | 15.025 | 2.975 | 0
7021 | TORONTO BUTTONVILLE A | 10 | 19 | 13 | 6.9 | 11.1 | 0
7021 | TORONTO BUTTONVILLE A | 10 | 20 | 13 | 15.425 | 2.575 | 0
7022 | TORONTO BUTTONVILLE A | 10 | 19 | 14 | 7.2 | 10.8 | 0
7022 | TORONTO BUTTONVILLE A | 10 | 20 | 14 | 16.65 | 1.35 | 0
7023 | TORONTO BUTTONVILLE A | 10 | 19 | 15 | 7.5 | 10.5 | 0
7023 | TORONTO BUTTONVILLE A | 10 | 20 | 15 | 16.4 | 1.6 | 0
7024 | TORONTO BUTTONVILLE A | 10 | 19 | 16 | 7.4 | 10.6 | 0
7024 | TORONTO BUTTONVILLE A | 10 | 20 | 16 | 16.55 | 1.45 | 0
7025 | TORONTO BUTTONVILLE A | 10 | 19 | 17 | 7.4 | 10.6 | 0
7025 | TORONTO BUTTONVILLE A | 10 | 20 | 17 | 16.1 | 1.9 | 0
7026 | TORONTO BUTTONVILLE A | 10 | 19 | 18 | 7.5 | 10.5 | 0
7026 | TORONTO BUTTONVILLE A | 10 | 20 | 18 | 14.825 | 3.175 | 0
7027 | TORONTO BUTTONVILLE A | 10 | 19 | 19 | 7.3 | 10.7 | 0
7027 | TORONTO BUTTONVILLE A | 10 | 20 | 19 | 12.875 | 5.125 | 0
7028 | TORONTO BUTTONVILLE A | 10 | 19 | 20 | 7.3 | 10.7 | 0
7028 | TORONTO BUTTONVILLE A | 10 | 20 | 20 | 12.2 | 5.8 | 0
7029 | TORONTO BUTTONVILLE A | 10 | 19 | 21 | 6.9 | 11.1 | 0
7029 | TORONTO BUTTONVILLE A | 10 | 20 | 21 | 10.6 | 7.4 | 0
7030 | TORONTO BUTTONVILLE A | 10 | 19 | 22 | 6.7 | 11.3 | 0
7030 | TORONTO BUTTONVILLE A | 10 | 20 | 22 | 10.7 | 7.3 | 0
7031 | TORONTO BUTTONVILLE A | 10 | 19 | 23 | 6.5 | 11.5 | 0
7031 | TORONTO BUTTONVILLE A | 10 | 20 | 23 | 10.05 | 7.95 | 0
7032 | TORONTO BUTTONVILLE A | 10 | 19 | 24 | 6.1 | 11.9 | 0
7032 | TORONTO BUTTONVILLE A | 10 | 20 | 24 | 9.475 | 8.525 | 0
7033 | TORONTO BUTTONVILLE A | 10 | 20 | 1 | 6.2 | 11.8 | 0
7033 | TORONTO BUTTONVILLE A | 10 | 21 | 1 | 8.325 | 9.675 | 0
7034 | TORONTO BUTTONVILLE A | 10 | 20 | 2 | 5.6 | 12.4 | 0
7034 | TORONTO BUTTONVILLE A | 10 | 21 | 2 | 7.625 | 10.375 | 0
7035 | TORONTO BUTTONVILLE A | 10 | 20 | 3 | 5.6 | 12.4 | 0
7035 | TORONTO BUTTONVILLE A | 10 | 21 | 3 | 7.125 | 10.875 | 0
7036 | TORONTO BUTTONVILLE A | 10 | 20 | 4 | 5.7 | 12.3 | 0
7036 | TORONTO BUTTONVILLE A | 10 | 21 | 4 | 6.825 | 11.175 | 0
7037 | TORONTO BUTTONVILLE A | 10 | 20 | 5 | 5.4 | 12.6 | 0
7037 | TORONTO BUTTONVILLE A | 10 | 21 | 5 | 6.35 | 11.65 | 0
7038 | TORONTO BUTTONVILLE A | 10 | 20 | 6 | 5.5 | 12.5 | 0
7038 | TORONTO BUTTONVILLE A | 10 | 21 | 6 | 6.275 | 11.725 | 0
7039 | TORONTO BUTTONVILLE A | 10 | 20 | 7 | 5.6 | 12.4 | 0
7039 | TORONTO BUTTONVILLE A | 10 | 21 | 7 | 6.025 | 11.975 | 0
7040 | TORONTO BUTTONVILLE A | 10 | 20 | 8 | 5.8 | 12.2 | 0
7040 | TORONTO BUTTONVILLE A | 10 | 21 | 8 | 6.2 | 11.8 | 0
7041 | TORONTO BUTTONVILLE A | 10 | 20 | 9 | 6.2 | 11.8 | 0
7041 | TORONTO BUTTONVILLE A | 10 | 21 | 9 | 8.25 | 9.75 | 0
7042 | TORONTO BUTTONVILLE A | 10 | 20 | 10 | 7 | 11 | 0
7042 | TORONTO BUTTONVILLE A | 10 | 21 | 10 | 10.05 | 7.95 | 0
7043 | TORONTO BUTTONVILLE A | 10 | 20 | 11 | 8.8 | 9.2 | 0
7043 | TORONTO BUTTONVILLE A | 10 | 21 | 11 | 11.725 | 6.275 | 0
7044 | TORONTO BUTTONVILLE A | 10 | 20 | 12 | 9 | 9 | 0
7044 | TORONTO BUTTONVILLE A | 10 | 21 | 12 | 12.725 | 5.275 | 0
7045 | TORONTO BUTTONVILLE A | 10 | 20 | 13 | 9.6 | 8.4 | 0
7045 | TORONTO BUTTONVILLE A | 10 | 21 | 13 | 12.775 | 5.225 | 0
7046 | TORONTO BUTTONVILLE A | 10 | 20 | 14 | 10 | 8 | 0
7046 | TORONTO BUTTONVILLE A | 10 | 21 | 14 | 13.4 | 4.6 | 0
7047 | TORONTO BUTTONVILLE A | 10 | 20 | 15 | 9.4 | 8.6 | 0
7047 | TORONTO BUTTONVILLE A | 10 | 21 | 15 | 13.925 | 4.075 | 0
7048 | TORONTO BUTTONVILLE A | 10 | 20 | 16 | 10.7 | 7.3 | 0
7048 | TORONTO BUTTONVILLE A | 10 | 21 | 16 | 14 | 4 | 0
7049 | TORONTO BUTTONVILLE A | 10 | 20 | 17 | 9.8 | 8.2 | 0
7049 | TORONTO BUTTONVILLE A | 10 | 21 | 17 | 14.075 | 3.925 | 0
7050 | TORONTO BUTTONVILLE A | 10 | 20 | 18 | 9.1 | 8.9 | 0
7050 | TORONTO BUTTONVILLE A | 10 | 21 | 18 | 13.525 | 4.475 | 0
7051 | TORONTO BUTTONVILLE A | 10 | 20 | 19 | 8.9 | 9.1 | 0
7051 | TORONTO BUTTONVILLE A | 10 | 21 | 19 | 12.8 | 5.2 | 0
7052 | TORONTO BUTTONVILLE A | 10 | 20 | 20 | 7.6 | 10.4 | 0
7052 | TORONTO BUTTONVILLE A | 10 | 21 | 20 | 12.175 | 5.825 | 0
7053 | TORONTO BUTTONVILLE A | 10 | 20 | 21 | 6.8 | 11.2 | 0
7053 | TORONTO BUTTONVILLE A | 10 | 21 | 21 | 11.575 | 6.425 | 0
7054 | TORONTO BUTTONVILLE A | 10 | 20 | 22 | 7.3 | 10.7 | 0
7054 | TORONTO BUTTONVILLE A | 10 | 21 | 22 | 10.6 | 7.4 | 0
7055 | TORONTO BUTTONVILLE A | 10 | 20 | 23 | 7.1 | 10.9 | 0
7055 | TORONTO BUTTONVILLE A | 10 | 21 | 23 | 10 | 8 | 0
7056 | TORONTO BUTTONVILLE A | 10 | 20 | 24 | 7.6 | 10.4 | 0
7056 | TORONTO BUTTONVILLE A | 10 | 21 | 24 | 9.55 | 8.45 | 0
7057 | TORONTO BUTTONVILLE A | 10 | 21 | 1 | 7.3 | 10.7 | 0
7057 | TORONTO BUTTONVILLE A | 10 | 22 | 1 | 9.025 | 8.975 | 0
7058 | TORONTO BUTTONVILLE A | 10 | 21 | 2 | 7.2 | 10.8 | 0
7058 | TORONTO BUTTONVILLE A | 10 | 22 | 2 | 8.3 | 9.7 | 0
7059 | TORONTO BUTTONVILLE A | 10 | 21 | 3 | 7 | 11 | 0
7059 | TORONTO BUTTONVILLE A | 10 | 22 | 3 | 7.825 | 10.175 | 0
7060 | TORONTO BUTTONVILLE A | 10 | 21 | 4 | 7.4 | 10.6 | 0
7060 | TORONTO BUTTONVILLE A | 10 | 22 | 4 | 7.475 | 10.525 | 0
7061 | TORONTO BUTTONVILLE A | 10 | 21 | 5 | 9.1 | 8.9 | 0
7061 | TORONTO BUTTONVILLE A | 10 | 22 | 5 | 7.425 | 10.575 | 0
7062 | TORONTO BUTTONVILLE A | 10 | 21 | 6 | 9.9 | 8.1 | 0
7062 | TORONTO BUTTONVILLE A | 10 | 22 | 6 | 7.4 | 10.6 | 0
7063 | TORONTO BUTTONVILLE A | 10 | 21 | 7 | 10.4 | 7.6 | 0
7063 | TORONTO BUTTONVILLE A | 10 | 22 | 7 | 6.675 | 11.325 | 0
7064 | TORONTO BUTTONVILLE A | 10 | 21 | 8 | 11.6 | 6.4 | 0
7064 | TORONTO BUTTONVILLE A | 10 | 22 | 8 | 7.125 | 10.875 | 0
7065 | TORONTO BUTTONVILLE A | 10 | 21 | 9 | 13.1 | 4.9 | 0
7065 | TORONTO BUTTONVILLE A | 10 | 22 | 9 | 8.375 | 9.625 | 0
7066 | TORONTO BUTTONVILLE A | 10 | 21 | 10 | 13.6 | 4.4 | 0
7066 | TORONTO BUTTONVILLE A | 10 | 22 | 10 | 9.825 | 8.175 | 0
7067 | TORONTO BUTTONVILLE A | 10 | 21 | 11 | 14.1 | 3.9 | 0
7067 | TORONTO BUTTONVILLE A | 10 | 22 | 11 | 11.45 | 6.55 | 0
7068 | TORONTO BUTTONVILLE A | 10 | 21 | 12 | 15.5 | 2.5 | 0
7068 | TORONTO BUTTONVILLE A | 10 | 22 | 12 | 12.65 | 5.35 | 0
7069 | TORONTO BUTTONVILLE A | 10 | 21 | 13 | 15.4 | 2.6 | 0
7069 | TORONTO BUTTONVILLE A | 10 | 22 | 13 | 13.275 | 4.725 | 0
7070 | TORONTO BUTTONVILLE A | 10 | 21 | 14 | 14.7 | 3.3 | 0
7070 | TORONTO BUTTONVILLE A | 10 | 22 | 14 | 13.85 | 4.15 | 0
7071 | TORONTO BUTTONVILLE A | 10 | 21 | 15 | 15.6 | 2.4 | 0
7071 | TORONTO BUTTONVILLE A | 10 | 22 | 15 | 13.925 | 4.075 | 0
7072 | TORONTO BUTTONVILLE A | 10 | 21 | 16 | 14.7 | 3.3 | 0
7072 | TORONTO BUTTONVILLE A | 10 | 22 | 16 | 13.7 | 4.3 | 0
7073 | TORONTO BUTTONVILLE A | 10 | 21 | 17 | 14.1 | 3.9 | 0
7073 | TORONTO BUTTONVILLE A | 10 | 22 | 17 | 12.925 | 5.075 | 0
7074 | TORONTO BUTTONVILLE A | 10 | 21 | 18 | 12.8 | 5.2 | 0
7074 | TORONTO BUTTONVILLE A | 10 | 22 | 18 | 11.7 | 6.3 | 0
7075 | TORONTO BUTTONVILLE A | 10 | 21 | 19 | 11.6 | 6.4 | 0
7075 | TORONTO BUTTONVILLE A | 10 | 22 | 19 | 10.6 | 7.4 | 0
7076 | TORONTO BUTTONVILLE A | 10 | 21 | 20 | 10.6 | 7.4 | 0
7076 | TORONTO BUTTONVILLE A | 10 | 22 | 20 | 10.4 | 7.6 | 0
7077 | TORONTO BUTTONVILLE A | 10 | 21 | 21 | 8.3 | 9.7 | 0
7077 | TORONTO BUTTONVILLE A | 10 | 22 | 21 | 9.475 | 8.525 | 0
7078 | TORONTO BUTTONVILLE A | 10 | 21 | 22 | 8.2 | 9.8 | 0
7078 | TORONTO BUTTONVILLE A | 10 | 22 | 22 | 8.45 | 9.55 | 0
7079 | TORONTO BUTTONVILLE A | 10 | 21 | 23 | 6.7 | 11.3 | 0
7079 | TORONTO BUTTONVILLE A | 10 | 22 | 23 | 7.85 | 10.15 | 0
7080 | TORONTO BUTTONVILLE A | 10 | 21 | 24 | 5.9 | 12.1 | 0
7080 | TORONTO BUTTONVILLE A | 10 | 22 | 24 | 7.375 | 10.625 | 0
7081 | TORONTO BUTTONVILLE A | 10 | 22 | 1 | 7 | 11 | 0
7081 | TORONTO BUTTONVILLE A | 10 | 23 | 1 | 7.625 | 10.375 | 0
7082 | TORONTO BUTTONVILLE A | 10 | 22 | 2 | 8.5 | 9.5 | 0
7082 | TORONTO BUTTONVILLE A | 10 | 23 | 2 | 7.175 | 10.825 | 0
7083 | TORONTO BUTTONVILLE A | 10 | 22 | 3 | 8 | 10 | 0
7083 | TORONTO BUTTONVILLE A | 10 | 23 | 3 | 6.75 | 11.25 | 0
7084 | TORONTO BUTTONVILLE A | 10 | 22 | 4 | 7.8 | 10.2 | 0
7084 | TORONTO BUTTONVILLE A | 10 | 23 | 4 | 6.05 | 11.95 | 0
7085 | TORONTO BUTTONVILLE A | 10 | 22 | 5 | 7.9 | 10.1 | 0
7085 | TORONTO BUTTONVILLE A | 10 | 23 | 5 | 5.45 | 12.55 | 0
7086 | TORONTO BUTTONVILLE A | 10 | 22 | 6 | 7.9 | 10.1 | 0
7086 | TORONTO BUTTONVILLE A | 10 | 23 | 6 | 5.65 | 12.35 | 0
7087 | TORONTO BUTTONVILLE A | 10 | 22 | 7 | 8.5 | 9.5 | 0
7087 | TORONTO BUTTONVILLE A | 10 | 23 | 7 | 6.125 | 11.875 | 0
7088 | TORONTO BUTTONVILLE A | 10 | 22 | 8 | 8.7 | 9.3 | 0
7088 | TORONTO BUTTONVILLE A | 10 | 23 | 8 | 6.4 | 11.6 | 0
7089 | TORONTO BUTTONVILLE A | 10 | 22 | 9 | 8.5 | 9.5 | 0
7089 | TORONTO BUTTONVILLE A | 10 | 23 | 9 | 7.6 | 10.4 | 0
7090 | TORONTO BUTTONVILLE A | 10 | 22 | 10 | 9.4 | 8.6 | 0
7090 | TORONTO BUTTONVILLE A | 10 | 23 | 10 | 8.8 | 9.2 | 0
7091 | TORONTO BUTTONVILLE A | 10 | 22 | 11 | 10 | 8 | 0
7091 | TORONTO BUTTONVILLE A | 10 | 23 | 11 | 10.25 | 7.75 | 0
7092 | TORONTO BUTTONVILLE A | 10 | 22 | 12 | 10.5 | 7.5 | 0
7092 | TORONTO BUTTONVILLE A | 10 | 23 | 12 | 11.375 | 6.625 | 0
7093 | TORONTO BUTTONVILLE A | 10 | 22 | 13 | 10.9 | 7.1 | 0
7093 | TORONTO BUTTONVILLE A | 10 | 23 | 13 | 11.425 | 6.575 | 0
7094 | TORONTO BUTTONVILLE A | 10 | 22 | 14 | 11.4 | 6.6 | 0
7094 | TORONTO BUTTONVILLE A | 10 | 23 | 14 | 11.675 | 6.325 | 0
7095 | TORONTO BUTTONVILLE A | 10 | 22 | 15 | 11.6 | 6.4 | 0
7095 | TORONTO BUTTONVILLE A | 10 | 23 | 15 | 11.825 | 6.175 | 0
7096 | TORONTO BUTTONVILLE A | 10 | 22 | 16 | 11.7 | 6.3 | 0
7096 | TORONTO BUTTONVILLE A | 10 | 23 | 16 | 12 | 6 | 0
7097 | TORONTO BUTTONVILLE A | 10 | 22 | 17 | 11.7 | 6.3 | 0
7097 | TORONTO BUTTONVILLE A | 10 | 23 | 17 | 11.45 | 6.55 | 0
7098 | TORONTO BUTTONVILLE A | 10 | 22 | 18 | 11.5 | 6.5 | 0
7098 | TORONTO BUTTONVILLE A | 10 | 23 | 18 | 10.7 | 7.3 | 0
7099 | TORONTO BUTTONVILLE A | 10 | 22 | 19 | 11.2 | 6.8 | 0
7099 | TORONTO BUTTONVILLE A | 10 | 23 | 19 | 9.975 | 8.025 | 0
7100 | TORONTO BUTTONVILLE A | 10 | 22 | 20 | 11 | 7 | 0
7100 | TORONTO BUTTONVILLE A | 10 | 23 | 20 | 9.55 | 8.45 | 0
7101 | TORONTO BUTTONVILLE A | 10 | 22 | 21 | 10.9 | 7.1 | 0
7101 | TORONTO BUTTONVILLE A | 10 | 23 | 21 | 9.025 | 8.975 | 0
7102 | TORONTO BUTTONVILLE A | 10 | 22 | 22 | 10.9 | 7.1 | 0
7102 | TORONTO BUTTONVILLE A | 10 | 23 | 22 | 9.125 | 8.875 | 0
7103 | TORONTO BUTTONVILLE A | 10 | 22 | 23 | 11.1 | 6.9 | 0
7103 | TORONTO BUTTONVILLE A | 10 | 23 | 23 | 8.575 | 9.425 | 0
7104 | TORONTO BUTTONVILLE A | 10 | 22 | 24 | 11.5 | 6.5 | 0
7104 | TORONTO BUTTONVILLE A | 10 | 23 | 24 | 8.15 | 9.85 | 0
7105 | TORONTO BUTTONVILLE A | 10 | 23 | 1 | 11.7 | 6.3 | 0
7105 | TORONTO BUTTONVILLE A | 10 | 24 | 1 | 7.425 | 10.575 | 0
7106 | TORONTO BUTTONVILLE A | 10 | 23 | 2 | 11.8 | 6.2 | 0
7106 | TORONTO BUTTONVILLE A | 10 | 24 | 2 | 7.275 | 10.725 | 0
7107 | TORONTO BUTTONVILLE A | 10 | 23 | 3 | 12 | 6 | 0
7107 | TORONTO BUTTONVILLE A | 10 | 24 | 3 | 7.325 | 10.675 | 0
7108 | TORONTO BUTTONVILLE A | 10 | 23 | 4 | 12 | 6 | 0
7108 | TORONTO BUTTONVILLE A | 10 | 24 | 4 | 7.225 | 10.775 | 0
7109 | TORONTO BUTTONVILLE A | 10 | 23 | 5 | 12.1 | 5.9 | 0
7109 | TORONTO BUTTONVILLE A | 10 | 24 | 5 | 7.075 | 10.925 | 0
7110 | TORONTO BUTTONVILLE A | 10 | 23 | 6 | 11.9 | 6.1 | 0
7110 | TORONTO BUTTONVILLE A | 10 | 24 | 6 | 6.5 | 11.5 | 0
7111 | TORONTO BUTTONVILLE A | 10 | 23 | 7 | 12 | 6 | 0
7111 | TORONTO BUTTONVILLE A | 10 | 24 | 7 | 7.25 | 10.75 | 0
7112 | TORONTO BUTTONVILLE A | 10 | 23 | 8 | 11.8 | 6.2 | 0
7112 | TORONTO BUTTONVILLE A | 10 | 24 | 8 | 7.175 | 10.825 | 0
7113 | TORONTO BUTTONVILLE A | 10 | 23 | 9 | 12.1 | 5.9 | 0
7113 | TORONTO BUTTONVILLE A | 10 | 24 | 9 | 7.825 | 10.175 | 0
7114 | TORONTO BUTTONVILLE A | 10 | 23 | 10 | 12.6 | 5.4 | 0
7114 | TORONTO BUTTONVILLE A | 10 | 24 | 10 | 9.525 | 8.475 | 0
7115 | TORONTO BUTTONVILLE A | 10 | 23 | 11 | 15.1 | 2.9 | 0
7115 | TORONTO BUTTONVILLE A | 10 | 24 | 11 | 10.4 | 7.6 | 0
7116 | TORONTO BUTTONVILLE A | 10 | 23 | 12 | 18.4 | 0 | 0.4
7116 | TORONTO BUTTONVILLE A | 10 | 24 | 12 | 10.875 | 7.125 | 0
7117 | TORONTO BUTTONVILLE A | 10 | 23 | 13 | 21.3 | 0 | 3.3
7117 | TORONTO BUTTONVILLE A | 10 | 24 | 13 | 10.9 | 7.1 | 0
7118 | TORONTO BUTTONVILLE A | 10 | 23 | 14 | 23.1 | 0 | 5.1
7118 | TORONTO BUTTONVILLE A | 10 | 24 | 14 | 11.3 | 6.7 | 0
7119 | TORONTO BUTTONVILLE A | 10 | 23 | 15 | 23.7 | 0 | 5.7
7119 | TORONTO BUTTONVILLE A | 10 | 24 | 15 | 10.7 | 7.3 | 0
7120 | TORONTO BUTTONVILLE A | 10 | 23 | 16 | 23.7 | 0 | 5.7
7120 | TORONTO BUTTONVILLE A | 10 | 24 | 16 | 10.475 | 7.525 | 0
7121 | TORONTO BUTTONVILLE A | 10 | 23 | 17 | 23.3 | 0 | 5.3
7121 | TORONTO BUTTONVILLE A | 10 | 24 | 17 | 10.275 | 7.725 | 0
7122 | TORONTO BUTTONVILLE A | 10 | 23 | 18 | 22.9 | 0 | 4.9
7122 | TORONTO BUTTONVILLE A | 10 | 24 | 18 | 9.425 | 8.575 | 0
7123 | TORONTO BUTTONVILLE A | 10 | 23 | 19 | 22.1 | 0 | 4.1
7123 | TORONTO BUTTONVILLE A | 10 | 24 | 19 | 8.425 | 9.575 | 0
7124 | TORONTO BUTTONVILLE A | 10 | 23 | 20 | 19.6 | 0 | 1.6
7124 | TORONTO BUTTONVILLE A | 10 | 24 | 20 | 7.5 | 10.5 | 0
7125 | TORONTO BUTTONVILLE A | 10 | 23 | 21 | 19.4 | 0 | 1.4
7125 | TORONTO BUTTONVILLE A | 10 | 24 | 21 | 7.225 | 10.775 | 0
7126 | TORONTO BUTTONVILLE A | 10 | 23 | 22 | 18.4 | 0 | 0.4
7126 | TORONTO BUTTONVILLE A | 10 | 24 | 22 | 7 | 11 | 0
7127 | TORONTO BUTTONVILLE A | 10 | 23 | 23 | 16.4 | 1.6 | 0
7127 | TORONTO BUTTONVILLE A | 10 | 24 | 23 | 6.375 | 11.625 | 0
7128 | TORONTO BUTTONVILLE A | 10 | 23 | 24 | 11.5 | 6.5 | 0
7128 | TORONTO BUTTONVILLE A | 10 | 24 | 24 | 6.35 | 11.65 | 0
7129 | TORONTO BUTTONVILLE A | 10 | 24 | 1 | 9.2 | 8.8 | 0
7129 | TORONTO BUTTONVILLE A | 10 | 25 | 1 | 6.525 | 11.475 | 0
7130 | TORONTO BUTTONVILLE A | 10 | 24 | 2 | 8.2 | 9.8 | 0
7130 | TORONTO BUTTONVILLE A | 10 | 25 | 2 | 6.125 | 11.875 | 0
7131 | TORONTO BUTTONVILLE A | 10 | 24 | 3 | 7.7 | 10.3 | 0
7131 | TORONTO BUTTONVILLE A | 10 | 25 | 3 | 5.825 | 12.175 | 0
7132 | TORONTO BUTTONVILLE A | 10 | 24 | 4 | 5.9 | 12.1 | 0
7132 | TORONTO BUTTONVILLE A | 10 | 25 | 4 | 5.55 | 12.45 | 0
7133 | TORONTO BUTTONVILLE A | 10 | 24 | 5 | 4.8 | 13.2 | 0
7133 | TORONTO BUTTONVILLE A | 10 | 25 | 5 | 5.325 | 12.675 | 0
7134 | TORONTO BUTTONVILLE A | 10 | 24 | 6 | 4.6 | 13.4 | 0
7134 | TORONTO BUTTONVILLE A | 10 | 25 | 6 | 5.45 | 12.55 | 0
7135 | TORONTO BUTTONVILLE A | 10 | 24 | 7 | 4.6 | 13.4 | 0
7135 | TORONTO BUTTONVILLE A | 10 | 25 | 7 | 5.4 | 12.6 | 0
7136 | TORONTO BUTTONVILLE A | 10 | 24 | 8 | 4.3 | 13.7 | 0
7136 | TORONTO BUTTONVILLE A | 10 | 25 | 8 | 5.5 | 12.5 | 0
7137 | TORONTO BUTTONVILLE A | 10 | 24 | 9 | 3.6 | 14.4 | 0
7137 | TORONTO BUTTONVILLE A | 10 | 25 | 9 | 5.75 | 12.25 | 0
7138 | TORONTO BUTTONVILLE A | 10 | 24 | 10 | 4.3 | 13.7 | 0
7138 | TORONTO BUTTONVILLE A | 10 | 25 | 10 | 6.575 | 11.425 | 0
7139 | TORONTO BUTTONVILLE A | 10 | 24 | 11 | 4.9 | 13.1 | 0
7139 | TORONTO BUTTONVILLE A | 10 | 25 | 11 | 7.875 | 10.125 | 0
7140 | TORONTO BUTTONVILLE A | 10 | 24 | 12 | 5.6 | 12.4 | 0
7140 | TORONTO BUTTONVILLE A | 10 | 25 | 12 | 8.25 | 9.75 | 0
7141 | TORONTO BUTTONVILLE A | 10 | 24 | 13 | 7 | 11 | 0
7141 | TORONTO BUTTONVILLE A | 10 | 25 | 13 | 8.875 | 9.125 | 0
7142 | TORONTO BUTTONVILLE A | 10 | 24 | 14 | 6.7 | 11.3 | 0
7142 | TORONTO BUTTONVILLE A | 10 | 25 | 14 | 9 | 9 | 0
7143 | TORONTO BUTTONVILLE A | 10 | 24 | 15 | 6.9 | 11.1 | 0
7143 | TORONTO BUTTONVILLE A | 10 | 25 | 15 | 9.125 | 8.875 | 0
7144 | TORONTO BUTTONVILLE A | 10 | 24 | 16 | 7 | 11 | 0
7144 | TORONTO BUTTONVILLE A | 10 | 25 | 16 | 9.05 | 8.95 | 0
7145 | TORONTO BUTTONVILLE A | 10 | 24 | 17 | 6.7 | 11.3 | 0
7145 | TORONTO BUTTONVILLE A | 10 | 25 | 17 | 8.375 | 9.625 | 0
7146 | TORONTO BUTTONVILLE A | 10 | 24 | 18 | 6 | 12 | 0
7146 | TORONTO BUTTONVILLE A | 10 | 25 | 18 | 7.975 | 10.025 | 0
7147 | TORONTO BUTTONVILLE A | 10 | 24 | 19 | 4.8 | 13.2 | 0
7147 | TORONTO BUTTONVILLE A | 10 | 25 | 19 | 7.3 | 10.7 | 0
7148 | TORONTO BUTTONVILLE A | 10 | 24 | 20 | 4.1 | 13.9 | 0
7148 | TORONTO BUTTONVILLE A | 10 | 25 | 20 | 7.025 | 10.975 | 0
7149 | TORONTO BUTTONVILLE A | 10 | 24 | 21 | 3 | 15 | 0
7149 | TORONTO BUTTONVILLE A | 10 | 25 | 21 | 6.45 | 11.55 | 0
7150 | TORONTO BUTTONVILLE A | 10 | 24 | 22 | 2.5 | 15.5 | 0
7150 | TORONTO BUTTONVILLE A | 10 | 25 | 22 | 5.95 | 12.05 | 0
7151 | TORONTO BUTTONVILLE A | 10 | 24 | 23 | 2.4 | 15.6 | 0
7151 | TORONTO BUTTONVILLE A | 10 | 25 | 23 | 5.75 | 12.25 | 0
7152 | TORONTO BUTTONVILLE A | 10 | 24 | 24 | 2.1 | 15.9 | 0
7152 | TORONTO BUTTONVILLE A | 10 | 25 | 24 | 4.7 | 13.3 | 0
7153 | TORONTO BUTTONVILLE A | 10 | 25 | 1 | 2.2 | 15.8 | 0
7153 | TORONTO BUTTONVILLE A | 10 | 26 | 1 | 4.475 | 13.525 | 0
7154 | TORONTO BUTTONVILLE A | 10 | 25 | 2 | 1.7 | 16.3 | 0
7154 | TORONTO BUTTONVILLE A | 10 | 26 | 2 | 4 | 14 | 0
7155 | TORONTO BUTTONVILLE A | 10 | 25 | 3 | 1.9 | 16.1 | 0
7155 | TORONTO BUTTONVILLE A | 10 | 26 | 3 | 3.175 | 14.825 | 0
7156 | TORONTO BUTTONVILLE A | 10 | 25 | 4 | 2 | 16 | 0
7156 | TORONTO BUTTONVILLE A | 10 | 26 | 4 | 3.275 | 14.725 | 0
7157 | TORONTO BUTTONVILLE A | 10 | 25 | 5 | 1.7 | 16.3 | 0
7157 | TORONTO BUTTONVILLE A | 10 | 26 | 5 | 3.15 | 14.85 | 0
7158 | TORONTO BUTTONVILLE A | 10 | 25 | 6 | 1.3 | 16.7 | 0
7158 | TORONTO BUTTONVILLE A | 10 | 26 | 6 | 2.95 | 15.05 | 0
7159 | TORONTO BUTTONVILLE A | 10 | 25 | 7 | 0.9 | 17.1 | 0
7159 | TORONTO BUTTONVILLE A | 10 | 26 | 7 | 2.975 | 15.025 | 0
7160 | TORONTO BUTTONVILLE A | 10 | 25 | 8 | 1 | 17 | 0
7160 | TORONTO BUTTONVILLE A | 10 | 26 | 8 | 2.95 | 15.05 | 0
7161 | TORONTO BUTTONVILLE A | 10 | 25 | 9 | 1.8 | 16.2 | 0
7161 | TORONTO BUTTONVILLE A | 10 | 26 | 9 | 4 | 14 | 0
7162 | TORONTO BUTTONVILLE A | 10 | 25 | 10 | 2.7 | 15.3 | 0
7162 | TORONTO BUTTONVILLE A | 10 | 26 | 10 | 5.375 | 12.625 | 0
7163 | TORONTO BUTTONVILLE A | 10 | 25 | 11 | 4.2 | 13.8 | 0
7163 | TORONTO BUTTONVILLE A | 10 | 26 | 11 | 6.575 | 11.425 | 0
7164 | TORONTO BUTTONVILLE A | 10 | 25 | 12 | 4.8 | 13.2 | 0
7164 | TORONTO BUTTONVILLE A | 10 | 26 | 12 | 7.425 | 10.575 | 0
7165 | TORONTO BUTTONVILLE A | 10 | 25 | 13 | 5.5 | 12.5 | 0
7165 | TORONTO BUTTONVILLE A | 10 | 26 | 13 | 7.75 | 10.25 | 0
7166 | TORONTO BUTTONVILLE A | 10 | 25 | 14 | 5.8 | 12.2 | 0
7166 | TORONTO BUTTONVILLE A | 10 | 26 | 14 | 7.7 | 10.3 | 0
7167 | TORONTO BUTTONVILLE A | 10 | 25 | 15 | 5.7 | 12.3 | 0
7167 | TORONTO BUTTONVILLE A | 10 | 26 | 15 | 7.85 | 10.15 | 0
7168 | TORONTO BUTTONVILLE A | 10 | 25 | 16 | 5.8 | 12.2 | 0
7168 | TORONTO BUTTONVILLE A | 10 | 26 | 16 | 7.75 | 10.25 | 0
7169 | TORONTO BUTTONVILLE A | 10 | 25 | 17 | 5.9 | 12.1 | 0
7169 | TORONTO BUTTONVILLE A | 10 | 26 | 17 | 7.5 | 10.5 | 0
7170 | TORONTO BUTTONVILLE A | 10 | 25 | 18 | 5.4 | 12.6 | 0
7170 | TORONTO BUTTONVILLE A | 10 | 26 | 18 | 7.025 | 10.975 | 0
7171 | TORONTO BUTTONVILLE A | 10 | 25 | 19 | 5.1 | 12.9 | 0
7171 | TORONTO BUTTONVILLE A | 10 | 26 | 19 | 6.775 | 11.225 | 0
7172 | TORONTO BUTTONVILLE A | 10 | 25 | 20 | 4.4 | 13.6 | 0
7172 | TORONTO BUTTONVILLE A | 10 | 26 | 20 | 6.425 | 11.575 | 0
7173 | TORONTO BUTTONVILLE A | 10 | 25 | 21 | 4.1 | 13.9 | 0
7173 | TORONTO BUTTONVILLE A | 10 | 26 | 21 | 6.325 | 11.675 | 0
7174 | TORONTO BUTTONVILLE A | 10 | 25 | 22 | 3.8 | 14.2 | 0
7174 | TORONTO BUTTONVILLE A | 10 | 26 | 22 | 6.425 | 11.575 | 0
7175 | TORONTO BUTTONVILLE A | 10 | 25 | 23 | 3.7 | 14.3 | 0
7175 | TORONTO BUTTONVILLE A | 10 | 26 | 23 | 6.6 | 11.4 | 0
7176 | TORONTO BUTTONVILLE A | 10 | 25 | 24 | 3.7 | 14.3 | 0
7176 | TORONTO BUTTONVILLE A | 10 | 26 | 24 | 6.475 | 11.525 | 0
7177 | TORONTO BUTTONVILLE A | 10 | 26 | 1 | 3.8 | 14.2 | 0
7177 | TORONTO BUTTONVILLE A | 10 | 27 | 1 | 6.4 | 11.6 | 0
7178 | TORONTO BUTTONVILLE A | 10 | 26 | 2 | 3.7 | 14.3 | 0
7178 | TORONTO BUTTONVILLE A | 10 | 27 | 2 | 6.2 | 11.8 | 0
7179 | TORONTO BUTTONVILLE A | 10 | 26 | 3 | 3.9 | 14.1 | 0
7179 | TORONTO BUTTONVILLE A | 10 | 27 | 3 | 6.025 | 11.975 | 0
7180 | TORONTO BUTTONVILLE A | 10 | 26 | 4 | 3.9 | 14.1 | 0
7180 | TORONTO BUTTONVILLE A | 10 | 27 | 4 | 5.95 | 12.05 | 0
7181 | TORONTO BUTTONVILLE A | 10 | 26 | 5 | 3.7 | 14.3 | 0
7181 | TORONTO BUTTONVILLE A | 10 | 27 | 5 | 6.075 | 11.925 | 0
7182 | TORONTO BUTTONVILLE A | 10 | 26 | 6 | 3.2 | 14.8 | 0
7182 | TORONTO BUTTONVILLE A | 10 | 27 | 6 | 6.025 | 11.975 | 0
7183 | TORONTO BUTTONVILLE A | 10 | 26 | 7 | 2.7 | 15.3 | 0
7183 | TORONTO BUTTONVILLE A | 10 | 27 | 7 | 5.95 | 12.05 | 0
7184 | TORONTO BUTTONVILLE A | 10 | 26 | 8 | 2.8 | 15.2 | 0
7184 | TORONTO BUTTONVILLE A | 10 | 27 | 8 | 5.8 | 12.2 | 0
7185 | TORONTO BUTTONVILLE A | 10 | 26 | 9 | 2.9 | 15.1 | 0
7185 | TORONTO BUTTONVILLE A | 10 | 27 | 9 | 6.725 | 11.275 | 0
7186 | TORONTO BUTTONVILLE A | 10 | 26 | 10 | 3.8 | 14.2 | 0
7186 | TORONTO BUTTONVILLE A | 10 | 27 | 10 | 8.1 | 9.9 | 0
7187 | TORONTO BUTTONVILLE A | 10 | 26 | 11 | 5 | 13 | 0
7187 | TORONTO BUTTONVILLE A | 10 | 27 | 11 | 9.675 | 8.325 | 0
7188 | TORONTO BUTTONVILLE A | 10 | 26 | 12 | 5.5 | 12.5 | 0
7188 | TORONTO BUTTONVILLE A | 10 | 27 | 12 | 10.5 | 7.5 | 0
7189 | TORONTO BUTTONVILLE A | 10 | 26 | 13 | 5.7 | 12.3 | 0
7189 | TORONTO BUTTONVILLE A | 10 | 27 | 13 | 11.3 | 6.7 | 0
7190 | TORONTO BUTTONVILLE A | 10 | 26 | 14 | 6.9 | 11.1 | 0
7190 | TORONTO BUTTONVILLE A | 10 | 27 | 14 | 11.7 | 6.3 | 0
7191 | TORONTO BUTTONVILLE A | 10 | 26 | 15 | 7.2 | 10.8 | 0
7191 | TORONTO BUTTONVILLE A | 10 | 27 | 15 | 12.05 | 5.95 | 0
7192 | TORONTO BUTTONVILLE A | 10 | 26 | 16 | 7.5 | 10.5 | 0
7192 | TORONTO BUTTONVILLE A | 10 | 27 | 16 | 11.9 | 6.1 | 0
7193 | TORONTO BUTTONVILLE A | 10 | 26 | 17 | 7.5 | 10.5 | 0
7193 | TORONTO BUTTONVILLE A | 10 | 27 | 17 | 11.25 | 6.75 | 0
7194 | TORONTO BUTTONVILLE A | 10 | 26 | 18 | 7.2 | 10.8 | 0
7194 | TORONTO BUTTONVILLE A | 10 | 27 | 18 | 9.975 | 8.025 | 0
7195 | TORONTO BUTTONVILLE A | 10 | 26 | 19 | 6.7 | 11.3 | 0
7195 | TORONTO BUTTONVILLE A | 10 | 27 | 19 | 8.9 | 9.1 | 0
7196 | TORONTO BUTTONVILLE A | 10 | 26 | 20 | 6.4 | 11.6 | 0
7196 | TORONTO BUTTONVILLE A | 10 | 27 | 20 | 8.2 | 9.8 | 0
7197 | TORONTO BUTTONVILLE A | 10 | 26 | 21 | 6.4 | 11.6 | 0
7197 | TORONTO BUTTONVILLE A | 10 | 27 | 21 | 8.025 | 9.975 | 0
7198 | TORONTO BUTTONVILLE A | 10 | 26 | 22 | 6.2 | 11.8 | 0
7198 | TORONTO BUTTONVILLE A | 10 | 27 | 22 | 8.025 | 9.975 | 0
7199 | TORONTO BUTTONVILLE A | 10 | 26 | 23 | 6 | 12 | 0
7199 | TORONTO BUTTONVILLE A | 10 | 27 | 23 | 7.85 | 10.15 | 0
7200 | TORONTO BUTTONVILLE A | 10 | 26 | 24 | 6.1 | 11.9 | 0
7200 | TORONTO BUTTONVILLE A | 10 | 27 | 24 | 7.25 | 10.75 | 0
7201 | TORONTO BUTTONVILLE A | 10 | 27 | 1 | 5.8 | 12.2 | 0
7201 | TORONTO BUTTONVILLE A | 10 | 28 | 1 | 6.275 | 11.725 | 0
7202 | TORONTO BUTTONVILLE A | 10 | 27 | 2 | 5.5 | 12.5 | 0
7202 | TORONTO BUTTONVILLE A | 10 | 28 | 2 | 5.8 | 12.2 | 0
7203 | TORONTO BUTTONVILLE A | 10 | 27 | 3 | 5 | 13 | 0
7203 | TORONTO BUTTONVILLE A | 10 | 28 | 3 | 5.425 | 12.575 | 0
7204 | TORONTO BUTTONVILLE A | 10 | 27 | 4 | 4.8 | 13.2 | 0
7204 | TORONTO BUTTONVILLE A | 10 | 28 | 4 | 5.325 | 12.675 | 0
7205 | TORONTO BUTTONVILLE A | 10 | 27 | 5 | 4.5 | 13.5 | 0
7205 | TORONTO BUTTONVILLE A | 10 | 28 | 5 | 5.2 | 12.8 | 0
7206 | TORONTO BUTTONVILLE A | 10 | 27 | 6 | 4.2 | 13.8 | 0
7206 | TORONTO BUTTONVILLE A | 10 | 28 | 6 | 5.075 | 12.925 | 0
7207 | TORONTO BUTTONVILLE A | 10 | 27 | 7 | 3.9 | 14.1 | 0
7207 | TORONTO BUTTONVILLE A | 10 | 28 | 7 | 4.825 | 13.175 | 0
7208 | TORONTO BUTTONVILLE A | 10 | 27 | 8 | 4 | 14 | 0
7208 | TORONTO BUTTONVILLE A | 10 | 28 | 8 | 5.175 | 12.825 | 0
7209 | TORONTO BUTTONVILLE A | 10 | 27 | 9 | 4.3 | 13.7 | 0
7209 | TORONTO BUTTONVILLE A | 10 | 28 | 9 | 6.35 | 11.65 | 0
7210 | TORONTO BUTTONVILLE A | 10 | 27 | 10 | 4.7 | 13.3 | 0
7210 | TORONTO BUTTONVILLE A | 10 | 28 | 10 | 7.025 | 10.975 | 0
7211 | TORONTO BUTTONVILLE A | 10 | 27 | 11 | 4.8 | 13.2 | 0
7211 | TORONTO BUTTONVILLE A | 10 | 28 | 11 | 7.75 | 10.25 | 0
7212 | TORONTO BUTTONVILLE A | 10 | 27 | 12 | 4.9 | 13.1 | 0
7212 | TORONTO BUTTONVILLE A | 10 | 28 | 12 | 8.225 | 9.775 | 0
7213 | TORONTO BUTTONVILLE A | 10 | 27 | 13 | 4.7 | 13.3 | 0
7213 | TORONTO BUTTONVILLE A | 10 | 28 | 13 | 8.55 | 9.45 | 0
7214 | TORONTO BUTTONVILLE A | 10 | 27 | 14 | 5.2 | 12.8 | 0
7214 | TORONTO BUTTONVILLE A | 10 | 28 | 14 | 9.1 | 8.9 | 0
7215 | TORONTO BUTTONVILLE A | 10 | 27 | 15 | 4.4 | 13.6 | 0
7215 | TORONTO BUTTONVILLE A | 10 | 28 | 15 | 9 | 9 | 0
7216 | TORONTO BUTTONVILLE A | 10 | 27 | 16 | 4.5 | 13.5 | 0
7216 | TORONTO BUTTONVILLE A | 10 | 28 | 16 | 9.25 | 8.75 | 0
7217 | TORONTO BUTTONVILLE A | 10 | 27 | 17 | 4.5 | 13.5 | 0
7217 | TORONTO BUTTONVILLE A | 10 | 28 | 17 | 8.925 | 9.075 | 0
7218 | TORONTO BUTTONVILLE A | 10 | 27 | 18 | 4.5 | 13.5 | 0
7218 | TORONTO BUTTONVILLE A | 10 | 28 | 18 | 8.375 | 9.625 | 0
7219 | TORONTO BUTTONVILLE A | 10 | 27 | 19 | 4.1 | 13.9 | 0
7219 | TORONTO BUTTONVILLE A | 10 | 28 | 19 | 7.575 | 10.425 | 0
7220 | TORONTO BUTTONVILLE A | 10 | 27 | 20 | 3.9 | 14.1 | 0
7220 | TORONTO BUTTONVILLE A | 10 | 28 | 20 | 6.8 | 11.2 | 0
7221 | TORONTO BUTTONVILLE A | 10 | 27 | 21 | 3.8 | 14.2 | 0
7221 | TORONTO BUTTONVILLE A | 10 | 28 | 21 | 6.275 | 11.725 | 0
7222 | TORONTO BUTTONVILLE A | 10 | 27 | 22 | 3.7 | 14.3 | 0
7222 | TORONTO BUTTONVILLE A | 10 | 28 | 22 | 5.675 | 12.325 | 0
7223 | TORONTO BUTTONVILLE A | 10 | 27 | 23 | 3.3 | 14.7 | 0
7223 | TORONTO BUTTONVILLE A | 10 | 28 | 23 | 5.425 | 12.575 | 0
7224 | TORONTO BUTTONVILLE A | 10 | 27 | 24 | 2 | 16 | 0
7224 | TORONTO BUTTONVILLE A | 10 | 28 | 24 | 5.15 | 12.85 | 0
7225 | TORONTO BUTTONVILLE A | 10 | 28 | 1 | 1.9 | 16.1 | 0
7225 | TORONTO BUTTONVILLE A | 10 | 29 | 1 | 5.025 | 12.975 | 0
7226 | TORONTO BUTTONVILLE A | 10 | 28 | 2 | 2.2 | 15.8 | 0
7226 | TORONTO BUTTONVILLE A | 10 | 29 | 2 | 5 | 13 | 0
7227 | TORONTO BUTTONVILLE A | 10 | 28 | 3 | 2 | 16 | 0
7227 | TORONTO BUTTONVILLE A | 10 | 29 | 3 | 4.85 | 13.15 | 0
7228 | TORONTO BUTTONVILLE A | 10 | 28 | 4 | 2.3 | 15.7 | 0
7228 | TORONTO BUTTONVILLE A | 10 | 29 | 4 | 4.675 | 13.325 | 0
7229 | TORONTO BUTTONVILLE A | 10 | 28 | 5 | 2.8 | 15.2 | 0
7229 | TORONTO BUTTONVILLE A | 10 | 29 | 5 | 5.175 | 12.825 | 0
7230 | TORONTO BUTTONVILLE A | 10 | 28 | 6 | 3.1 | 14.9 | 0
7230 | TORONTO BUTTONVILLE A | 10 | 29 | 6 | 5.825 | 12.175 | 0
7231 | TORONTO BUTTONVILLE A | 10 | 28 | 7 | 2.8 | 15.2 | 0
7231 | TORONTO BUTTONVILLE A | 10 | 29 | 7 | 6.2 | 11.8 | 0
7232 | TORONTO BUTTONVILLE A | 10 | 28 | 8 | 2.1 | 15.9 | 0
7232 | TORONTO BUTTONVILLE A | 10 | 29 | 8 | 6.3 | 11.7 | 0
7233 | TORONTO BUTTONVILLE A | 10 | 28 | 9 | 3.9 | 14.1 | 0
7233 | TORONTO BUTTONVILLE A | 10 | 29 | 9 | 6.7 | 11.3 | 0
7234 | TORONTO BUTTONVILLE A | 10 | 28 | 10 | 4.5 | 13.5 | 0
7234 | TORONTO BUTTONVILLE A | 10 | 29 | 10 | 7.175 | 10.825 | 0
7235 | TORONTO BUTTONVILLE A | 10 | 28 | 11 | 6.4 | 11.6 | 0
7235 | TORONTO BUTTONVILLE A | 10 | 29 | 11 | 7.85 | 10.15 | 0
7236 | TORONTO BUTTONVILLE A | 10 | 28 | 12 | 7.8 | 10.2 | 0
7236 | TORONTO BUTTONVILLE A | 10 | 29 | 12 | 8.9 | 9.1 | 0
7237 | TORONTO BUTTONVILLE A | 10 | 28 | 13 | 9 | 9 | 0
7237 | TORONTO BUTTONVILLE A | 10 | 29 | 13 | 9.375 | 8.625 | 0
7238 | TORONTO BUTTONVILLE A | 10 | 28 | 14 | 10.1 | 7.9 | 0
7238 | TORONTO BUTTONVILLE A | 10 | 29 | 14 | 10.075 | 7.925 | 0
7239 | TORONTO BUTTONVILLE A | 10 | 28 | 15 | 11.1 | 6.9 | 0
7239 | TORONTO BUTTONVILLE A | 10 | 29 | 15 | 10.675 | 7.325 | 0
7240 | TORONTO BUTTONVILLE A | 10 | 28 | 16 | 11 | 7 | 0
7240 | TORONTO BUTTONVILLE A | 10 | 29 | 16 | 10.7 | 7.3 | 0
7241 | TORONTO BUTTONVILLE A | 10 | 28 | 17 | 10.7 | 7.3 | 0
7241 | TORONTO BUTTONVILLE A | 10 | 29 | 17 | 10.5 | 7.5 | 0
7242 | TORONTO BUTTONVILLE A | 10 | 28 | 18 | 9.9 | 8.1 | 0
7242 | TORONTO BUTTONVILLE A | 10 | 29 | 18 | 9.975 | 8.025 | 0
7243 | TORONTO BUTTONVILLE A | 10 | 28 | 19 | 8.9 | 9.1 | 0
7243 | TORONTO BUTTONVILLE A | 10 | 29 | 19 | 9.45 | 8.55 | 0
7244 | TORONTO BUTTONVILLE A | 10 | 28 | 20 | 7.9 | 10.1 | 0
7244 | TORONTO BUTTONVILLE A | 10 | 29 | 20 | 8.825 | 9.175 | 0
7245 | TORONTO BUTTONVILLE A | 10 | 28 | 21 | 6.7 | 11.3 | 0
7245 | TORONTO BUTTONVILLE A | 10 | 29 | 21 | 8.25 | 9.75 | 0
7246 | TORONTO BUTTONVILLE A | 10 | 28 | 22 | 3.9 | 14.1 | 0
7246 | TORONTO BUTTONVILLE A | 10 | 29 | 22 | 7.425 | 10.575 | 0
7247 | TORONTO BUTTONVILLE A | 10 | 28 | 23 | 5 | 13 | 0
7247 | TORONTO BUTTONVILLE A | 10 | 29 | 23 | 7 | 11 | 0
7248 | TORONTO BUTTONVILLE A | 10 | 28 | 24 | 5.3 | 12.7 | 0
7248 | TORONTO BUTTONVILLE A | 10 | 29 | 24 | 6.4 | 11.6 | 0
7249 | TORONTO BUTTONVILLE A | 10 | 29 | 1 | 3.9 | 14.1 | 0
7249 | TORONTO BUTTONVILLE A | 10 | 30 | 1 | 5.8 | 12.2 | 0
7250 | TORONTO BUTTONVILLE A | 10 | 29 | 2 | 3.6 | 14.4 | 0
7250 | TORONTO BUTTONVILLE A | 10 | 30 | 2 | 5.55 | 12.45 | 0
7251 | TORONTO BUTTONVILLE A | 10 | 29 | 3 | 2.4 | 15.6 | 0
7251 | TORONTO BUTTONVILLE A | 10 | 30 | 3 | 5.45 | 12.55 | 0
7252 | TORONTO BUTTONVILLE A | 10 | 29 | 4 | 2.6 | 15.4 | 0
7252 | TORONTO BUTTONVILLE A | 10 | 30 | 4 | 5.175 | 12.825 | 0
7253 | TORONTO BUTTONVILLE A | 10 | 29 | 5 | 2.4 | 15.6 | 0
7253 | TORONTO BUTTONVILLE A | 10 | 30 | 5 | 4.925 | 13.075 | 0
7254 | TORONTO BUTTONVILLE A | 10 | 29 | 6 | 2.8 | 15.2 | 0
7254 | TORONTO BUTTONVILLE A | 10 | 30 | 6 | 5.15 | 12.85 | 0
7255 | TORONTO BUTTONVILLE A | 10 | 29 | 7 | 3.3 | 14.7 | 0
7255 | TORONTO BUTTONVILLE A | 10 | 30 | 7 | 4.7 | 13.3 | 0
7256 | TORONTO BUTTONVILLE A | 10 | 29 | 8 | 3.3 | 14.7 | 0
7256 | TORONTO BUTTONVILLE A | 10 | 30 | 8 | 4.525 | 13.475 | 0
7257 | TORONTO BUTTONVILLE A | 10 | 29 | 9 | 4.6 | 13.4 | 0
7257 | TORONTO BUTTONVILLE A | 10 | 30 | 9 | 5.575 | 12.425 | 0
7258 | TORONTO BUTTONVILLE A | 10 | 29 | 10 | 6.1 | 11.9 | 0
7258 | TORONTO BUTTONVILLE A | 10 | 30 | 10 | 6.65 | 11.35 | 0
7259 | TORONTO BUTTONVILLE A | 10 | 29 | 11 | 7.7 | 10.3 | 0
7259 | TORONTO BUTTONVILLE A | 10 | 30 | 11 | 7.75 | 10.25 | 0
7260 | TORONTO BUTTONVILLE A | 10 | 29 | 12 | 9.1 | 8.9 | 0
7260 | TORONTO BUTTONVILLE A | 10 | 30 | 12 | 8.15 | 9.85 | 0
7261 | TORONTO BUTTONVILLE A | 10 | 29 | 13 | 9.6 | 8.4 | 0
7261 | TORONTO BUTTONVILLE A | 10 | 30 | 13 | 8.45 | 9.55 | 0
7262 | TORONTO BUTTONVILLE A | 10 | 29 | 14 | 9.8 | 8.2 | 0
7262 | TORONTO BUTTONVILLE A | 10 | 30 | 14 | 8.525 | 9.475 | 0
7263 | TORONTO BUTTONVILLE A | 10 | 29 | 15 | 8.1 | 9.9 | 0
7263 | TORONTO BUTTONVILLE A | 10 | 30 | 15 | 8.825 | 9.175 | 0
7264 | TORONTO BUTTONVILLE A | 10 | 29 | 16 | 6.8 | 11.2 | 0
7264 | TORONTO BUTTONVILLE A | 10 | 30 | 16 | 8.525 | 9.475 | 0
7265 | TORONTO BUTTONVILLE A | 10 | 29 | 17 | 5.6 | 12.4 | 0
7265 | TORONTO BUTTONVILLE A | 10 | 30 | 17 | 7.925 | 10.075 | 0
7266 | TORONTO BUTTONVILLE A | 10 | 29 | 18 | 5.1 | 12.9 | 0
7266 | TORONTO BUTTONVILLE A | 10 | 30 | 18 | 7.45 | 10.55 | 0
7267 | TORONTO BUTTONVILLE A | 10 | 29 | 19 | 4.4 | 13.6 | 0
7267 | TORONTO BUTTONVILLE A | 10 | 30 | 19 | 7.05 | 10.95 | 0
7268 | TORONTO BUTTONVILLE A | 10 | 29 | 20 | 3 | 15 | 0
7268 | TORONTO BUTTONVILLE A | 10 | 30 | 20 | 6.625 | 11.375 | 0
7269 | TORONTO BUTTONVILLE A | 10 | 29 | 21 | 2.8 | 15.2 | 0
7269 | TORONTO BUTTONVILLE A | 10 | 30 | 21 | 6.65 | 11.35 | 0
7270 | TORONTO BUTTONVILLE A | 10 | 29 | 22 | 2.8 | 15.2 | 0
7270 | TORONTO BUTTONVILLE A | 10 | 30 | 22 | 6.975 | 11.025 | 0
7271 | TORONTO BUTTONVILLE A | 10 | 29 | 23 | 2 | 16 | 0
7271 | TORONTO BUTTONVILLE A | 10 | 30 | 23 | 7.075 | 10.925 | 0
7272 | TORONTO BUTTONVILLE A | 10 | 29 | 24 | 2 | 16 | 0
7272 | TORONTO BUTTONVILLE A | 10 | 30 | 24 | 7.05 | 10.95 | 0
7273 | TORONTO BUTTONVILLE A | 10 | 30 | 1 | 1.7 | 16.3 | 0
7273 | TORONTO BUTTONVILLE A | 10 | 31 | 1 | 6.925 | 11.075 | 0
7274 | TORONTO BUTTONVILLE A | 10 | 30 | 2 | 1.6 | 16.4 | 0
7274 | TORONTO BUTTONVILLE A | 10 | 31 | 2 | 6.925 | 11.075 | 0
7275 | TORONTO BUTTONVILLE A | 10 | 30 | 3 | 1.2 | 16.8 | 0
7275 | TORONTO BUTTONVILLE A | 10 | 31 | 3 | 6.75 | 11.25 | 0
7276 | TORONTO BUTTONVILLE A | 10 | 30 | 4 | 0.8 | 17.2 | 0
7276 | TORONTO BUTTONVILLE A | 10 | 31 | 4 | 6.5 | 11.5 | 0
7277 | TORONTO BUTTONVILLE A | 10 | 30 | 5 | 0.3 | 17.7 | 0
7277 | TORONTO BUTTONVILLE A | 10 | 31 | 5 | 6.625 | 11.375 | 0
7278 | TORONTO BUTTONVILLE A | 10 | 30 | 6 | 0 | 18 | 0
7278 | TORONTO BUTTONVILLE A | 10 | 31 | 6 | 6.575 | 11.425 | 0
7279 | TORONTO BUTTONVILLE A | 10 | 30 | 7 | -0.4 | 18.4 | 0
7279 | TORONTO BUTTONVILLE A | 10 | 31 | 7 | 6.8 | 11.2 | 0
7280 | TORONTO BUTTONVILLE A | 10 | 30 | 8 | -0.8 | 18.8 | 0
7280 | TORONTO BUTTONVILLE A | 10 | 31 | 8 | 6.925 | 11.075 | 0
7281 | TORONTO BUTTONVILLE A | 10 | 30 | 9 | -1 | 19 | 0
7281 | TORONTO BUTTONVILLE A | 10 | 31 | 9 | 7.25 | 10.75 | 0
7282 | TORONTO BUTTONVILLE A | 10 | 30 | 10 | -0.6 | 18.6 | 0
7282 | TORONTO BUTTONVILLE A | 10 | 31 | 10 | 7.75 | 10.25 | 0
7283 | TORONTO BUTTONVILLE A | 10 | 30 | 11 | -0.1 | 18.1 | 0
7283 | TORONTO BUTTONVILLE A | 10 | 31 | 11 | 8.425 | 9.575 | 0
7284 | TORONTO BUTTONVILLE A | 10 | 30 | 12 | 0.2 | 17.8 | 0
7284 | TORONTO BUTTONVILLE A | 10 | 31 | 12 | 9 | 9 | 0
7285 | TORONTO BUTTONVILLE A | 10 | 30 | 13 | 0.9 | 17.1 | 0
7285 | TORONTO BUTTONVILLE A | 10 | 31 | 13 | 9.675 | 8.325 | 0
7286 | TORONTO BUTTONVILLE A | 10 | 30 | 14 | 1.8 | 16.2 | 0
7286 | TORONTO BUTTONVILLE A | 10 | 31 | 14 | 11.4667 | 6.5333 | 0
7287 | TORONTO BUTTONVILLE A | 10 | 30 | 15 | 2 | 16 | 0
7287 | TORONTO BUTTONVILLE A | 10 | 31 | 15 | 11.6 | 6.4 | 0
7288 | TORONTO BUTTONVILLE A | 10 | 30 | 16 | 1.7 | 16.3 | 0
7288 | TORONTO BUTTONVILLE A | 10 | 31 | 16 | 11.6667 | 6.3333 | 0
7289 | TORONTO BUTTONVILLE A | 10 | 30 | 17 | 1 | 17 | 0
7289 | TORONTO BUTTONVILLE A | 10 | 31 | 17 | 9.625 | 8.375 | 0
7290 | TORONTO BUTTONVILLE A | 10 | 30 | 18 | 0.4 | 17.6 | 0
7290 | TORONTO BUTTONVILLE A | 10 | 31 | 18 | 9.175 | 8.825 | 0
7291 | TORONTO BUTTONVILLE A | 10 | 30 | 19 | -0.4 | 18.4 | 0
7291 | TORONTO BUTTONVILLE A | 10 | 31 | 19 | 8.9 | 9.1 | 0
7292 | TORONTO BUTTONVILLE A | 10 | 30 | 20 | -0.8 | 18.8 | 0
7292 | TORONTO BUTTONVILLE A | 10 | 31 | 20 | 7.95 | 10.05 | 0
7293 | TORONTO BUTTONVILLE A | 10 | 30 | 21 | -1.4 | 19.4 | 0
7293 | TORONTO BUTTONVILLE A | 10 | 31 | 21 | 7.775 | 10.225 | 0
7294 | TORONTO BUTTONVILLE A | 10 | 30 | 22 | -1.9 | 19.9 | 0
7294 | TORONTO BUTTONVILLE A | 10 | 31 | 22 | 7.25 | 10.75 | 0
7295 | TORONTO BUTTONVILLE A | 10 | 30 | 23 | -2.2 | 20.2 | 0
7295 | TORONTO BUTTONVILLE A | 10 | 31 | 23 | 6.625 | 11.375 | 0
7296 | TORONTO BUTTONVILLE A | 10 | 30 | 24 | -2.6 | 20.6 | 0
7296 | TORONTO BUTTONVILLE A | 10 | 31 | 24 | 5.925 | 12.075 | 0
7297 | TORONTO BUTTONVILLE A | 10 | 31 | 1 | -3.3 | 21.3 | 0
7297 | TORONTO BUTTONVILLE A | 11 | 1 | 1 | 5.425 | 12.575 | 0
7298 | TORONTO BUTTONVILLE A | 10 | 31 | 2 | -3.7 | 21.7 | 0
7298 | TORONTO BUTTONVILLE A | 11 | 1 | 2 | 5 | 13 | 0
7299 | TORONTO BUTTONVILLE A | 10 | 31 | 3 | -3.8 | 21.8 | 0
7299 | TORONTO BUTTONVILLE A | 11 | 1 | 3 | 4.525 | 13.475 | 0
7300 | TORONTO BUTTONVILLE A | 10 | 31 | 4 | -4.7 | 22.7 | 0
7300 | TORONTO BUTTONVILLE A | 11 | 1 | 4 | 4.15 | 13.85 | 0
7301 | TORONTO BUTTONVILLE A | 10 | 31 | 5 | -5.3 | 23.3 | 0
7301 | TORONTO BUTTONVILLE A | 11 | 1 | 5 | 3.925 | 14.075 | 0
7302 | TORONTO BUTTONVILLE A | 10 | 31 | 6 | -5.6 | 23.6 | 0
7302 | TORONTO BUTTONVILLE A | 11 | 1 | 6 | 3.825 | 14.175 | 0
7303 | TORONTO BUTTONVILLE A | 10 | 31 | 7 | -5.5 | 23.5 | 0
7303 | TORONTO BUTTONVILLE A | 11 | 1 | 7 | 3.95 | 14.05 | 0
7304 | TORONTO BUTTONVILLE A | 10 | 31 | 8 | -6 | 24 | 0
7304 | TORONTO BUTTONVILLE A | 11 | 1 | 8 | 4.175 | 13.825 | 0
7305 | TORONTO BUTTONVILLE A | 10 | 31 | 9 | -3.3 | 21.3 | 0
7305 | TORONTO BUTTONVILLE A | 11 | 1 | 9 | 4.625 | 13.375 | 0
7306 | TORONTO BUTTONVILLE A | 10 | 31 | 10 | -0.1 | 18.1 | 0
7306 | TORONTO BUTTONVILLE A | 11 | 1 | 10 | 5.2 | 12.8 | 0
7307 | TORONTO BUTTONVILLE A | 10 | 31 | 11 | 1.2 | 16.8 | 0
7307 | TORONTO BUTTONVILLE A | 11 | 1 | 11 | 6.025 | 11.975 | 0
7308 | TORONTO BUTTONVILLE A | 10 | 31 | 12 | 2.7 | 15.3 | 0
7308 | TORONTO BUTTONVILLE A | 11 | 1 | 12 | 6.175 | 11.825 | 0
7309 | TORONTO BUTTONVILLE A | 10 | 31 | 13 | 4.1 | 13.9 | 0
7309 | TORONTO BUTTONVILLE A | 11 | 1 | 13 | 6.75 | 11.25 | 0
7310 | TORONTO BUTTONVILLE A | 10 | 31 | 14 | 4.8 | 13.2 | 0
7310 | TORONTO BUTTONVILLE A | 11 | 1 | 14 | 7.15 | 10.85 | 0
7311 | TORONTO BUTTONVILLE A | 10 | 31 | 15 | 5.1 | 12.9 | 0
7311 | TORONTO BUTTONVILLE A | 11 | 1 | 15 | 6.85 | 11.15 | 0
7312 | TORONTO BUTTONVILLE A | 10 | 31 | 16 | 4.8 | 13.2 | 0
7312 | TORONTO BUTTONVILLE A | 11 | 1 | 16 | 6.275 | 11.725 | 0
7313 | TORONTO BUTTONVILLE A | 10 | 31 | 17 | 4.6 | 13.4 | 0
7313 | TORONTO BUTTONVILLE A | 11 | 1 | 17 | 5.875 | 12.125 | 0
7314 | TORONTO BUTTONVILLE A | 10 | 31 | 18 | 4.4 | 13.6 | 0
7314 | TORONTO BUTTONVILLE A | 11 | 1 | 18 | 5.525 | 12.475 | 0
7315 | TORONTO BUTTONVILLE A | 10 | 31 | 19 | 5.2 | 12.8 | 0
7315 | TORONTO BUTTONVILLE A | 11 | 1 | 19 | 5.175 | 12.825 | 0
7316 | TORONTO BUTTONVILLE A | 10 | 31 | 20 | 5.2 | 12.8 | 0
7316 | TORONTO BUTTONVILLE A | 11 | 1 | 20 | 4.95 | 13.05 | 0
7317 | TORONTO BUTTONVILLE A | 10 | 31 | 21 | 4.6 | 13.4 | 0
7317 | TORONTO BUTTONVILLE A | 11 | 1 | 21 | 4.9 | 13.1 | 0
7318 | TORONTO BUTTONVILLE A | 10 | 31 | 22 | 3.8 | 14.2 | 0
7318 | TORONTO BUTTONVILLE A | 11 | 1 | 22 | 4.6 | 13.4 | 0
7319 | TORONTO BUTTONVILLE A | 10 | 31 | 23 | 3.9 | 14.1 | 0
7319 | TORONTO BUTTONVILLE A | 11 | 1 | 23 | 4.3 | 13.7 | 0
7320 | TORONTO BUTTONVILLE A | 10 | 31 | 24 | 3.4 | 14.6 | 0
7320 | TORONTO BUTTONVILLE A | 11 | 1 | 24 | 3.95 | 14.05 | 0
7321 | TORONTO BUTTONVILLE A | 11 | 1 | 1 | 4.3 | 13.7 | 0
7321 | TORONTO BUTTONVILLE A | 11 | 2 | 1 | 3.725 | 14.275 | 0
7322 | TORONTO BUTTONVILLE A | 11 | 1 | 2 | 5.8 | 12.2 | 0
7322 | TORONTO BUTTONVILLE A | 11 | 2 | 2 | 3.575 | 14.425 | 0
7323 | TORONTO BUTTONVILLE A | 11 | 1 | 3 | 7.2 | 10.8 | 0
7323 | TORONTO BUTTONVILLE A | 11 | 2 | 3 | 3.025 | 14.975 | 0
7324 | TORONTO BUTTONVILLE A | 11 | 1 | 4 | 8.4 | 9.6 | 0
7324 | TORONTO BUTTONVILLE A | 11 | 2 | 4 | 3.225 | 14.775 | 0
7325 | TORONTO BUTTONVILLE A | 11 | 1 | 5 | 8.7 | 9.3 | 0
7325 | TORONTO BUTTONVILLE A | 11 | 2 | 5 | 4.075 | 13.925 | 0
7326 | TORONTO BUTTONVILLE A | 11 | 1 | 6 | 9.4 | 8.6 | 0
7326 | TORONTO BUTTONVILLE A | 11 | 2 | 6 | 4.3 | 13.7 | 0
7327 | TORONTO BUTTONVILLE A | 11 | 1 | 7 | 9.6 | 8.4 | 0
7327 | TORONTO BUTTONVILLE A | 11 | 2 | 7 | 4.5 | 13.5 | 0
7328 | TORONTO BUTTONVILLE A | 11 | 1 | 8 | 10.4 | 7.6 | 0
7328 | TORONTO BUTTONVILLE A | 11 | 2 | 8 | 4.425 | 13.575 | 0
7329 | TORONTO BUTTONVILLE A | 11 | 1 | 9 | 10.9 | 7.1 | 0
7329 | TORONTO BUTTONVILLE A | 11 | 2 | 9 | 4.775 | 13.225 | 0
7330 | TORONTO BUTTONVILLE A | 11 | 1 | 10 | 9.8 | 8.2 | 0
7330 | TORONTO BUTTONVILLE A | 11 | 2 | 10 | 5.85 | 12.15 | 0
7331 | TORONTO BUTTONVILLE A | 11 | 1 | 11 | 7.6 | 10.4 | 0
7331 | TORONTO BUTTONVILLE A | 11 | 2 | 11 | 7.3 | 10.7 | 0
7332 | TORONTO BUTTONVILLE A | 11 | 1 | 12 | 6.7 | 11.3 | 0
7332 | TORONTO BUTTONVILLE A | 11 | 2 | 12 | 7.65 | 10.35 | 0
7333 | TORONTO BUTTONVILLE A | 11 | 1 | 13 | 7.5 | 10.5 | 0
7333 | TORONTO BUTTONVILLE A | 11 | 2 | 13 | 7.625 | 10.375 | 0
7334 | TORONTO BUTTONVILLE A | 11 | 1 | 14 | 6.9 | 11.1 | 0
7334 | TORONTO BUTTONVILLE A | 11 | 2 | 14 | 7.625 | 10.375 | 0
7335 | TORONTO BUTTONVILLE A | 11 | 1 | 15 | 5.6 | 12.4 | 0
7335 | TORONTO BUTTONVILLE A | 11 | 2 | 15 | 8.1 | 9.9 | 0
7336 | TORONTO BUTTONVILLE A | 11 | 1 | 16 | 1.9 | 16.1 | 0
7336 | TORONTO BUTTONVILLE A | 11 | 2 | 16 | 7.65 | 10.35 | 0
7337 | TORONTO BUTTONVILLE A | 11 | 1 | 17 | 3.1 | 14.9 | 0
7337 | TORONTO BUTTONVILLE A | 11 | 2 | 17 | 7.25 | 10.75 | 0
7338 | TORONTO BUTTONVILLE A | 11 | 1 | 18 | 2.3 | 15.7 | 0
7338 | TORONTO BUTTONVILLE A | 11 | 2 | 18 | 7.225 | 10.775 | 0
7339 | TORONTO BUTTONVILLE A | 11 | 1 | 19 | 1.4 | 16.6 | 0
7339 | TORONTO BUTTONVILLE A | 11 | 2 | 19 | 7.125 | 10.875 | 0
7340 | TORONTO BUTTONVILLE A | 11 | 1 | 20 | 1 | 17 | 0
7340 | TORONTO BUTTONVILLE A | 11 | 2 | 20 | 6.575 | 11.425 | 0
7341 | TORONTO BUTTONVILLE A | 11 | 1 | 21 | 1.3 | 16.7 | 0
7341 | TORONTO BUTTONVILLE A | 11 | 2 | 21 | 6.175 | 11.825 | 0
7342 | TORONTO BUTTONVILLE A | 11 | 1 | 22 | 0.9 | 17.1 | 0
7342 | TORONTO BUTTONVILLE A | 11 | 2 | 22 | 5.95 | 12.05 | 0
7343 | TORONTO BUTTONVILLE A | 11 | 1 | 23 | 0.6 | 17.4 | 0
7343 | TORONTO BUTTONVILLE A | 11 | 2 | 23 | 5.8 | 12.2 | 0
7344 | TORONTO BUTTONVILLE A | 11 | 1 | 24 | 0.9 | 17.1 | 0
7344 | TORONTO BUTTONVILLE A | 11 | 2 | 24 | 5.3 | 12.7 | 0
7345 | TORONTO BUTTONVILLE A | 11 | 2 | 1 | -0.2 | 18.2 | 0
7345 | TORONTO BUTTONVILLE A | 11 | 3 | 1 | 4.55 | 13.45 | 0
7346 | TORONTO BUTTONVILLE A | 11 | 2 | 2 | -0.7 | 18.7 | 0
7346 | TORONTO BUTTONVILLE A | 11 | 3 | 2 | 4.325 | 13.675 | 0
7347 | TORONTO BUTTONVILLE A | 11 | 2 | 3 | -1.2 | 19.2 | 0
7347 | TORONTO BUTTONVILLE A | 11 | 3 | 3 | 3.875 | 14.125 | 0
7348 | TORONTO BUTTONVILLE A | 11 | 2 | 4 | -0.6 | 18.6 | 0
7348 | TORONTO BUTTONVILLE A | 11 | 3 | 4 | 3.65 | 14.35 | 0
7349 | TORONTO BUTTONVILLE A | 11 | 2 | 5 | -1.9 | 19.9 | 0
7349 | TORONTO BUTTONVILLE A | 11 | 3 | 5 | 3.65 | 14.35 | 0
7350 | TORONTO BUTTONVILLE A | 11 | 2 | 6 | -2.5 | 20.5 | 0
7350 | TORONTO BUTTONVILLE A | 11 | 3 | 6 | 3.575 | 14.425 | 0
7351 | TORONTO BUTTONVILLE A | 11 | 2 | 7 | -2.9 | 20.9 | 0
7351 | TORONTO BUTTONVILLE A | 11 | 3 | 7 | 3.475 | 14.525 | 0
7352 | TORONTO BUTTONVILLE A | 11 | 2 | 8 | -2.2 | 20.2 | 0
7352 | TORONTO BUTTONVILLE A | 11 | 3 | 8 | 3.325 | 14.675 | 0
7353 | TORONTO BUTTONVILLE A | 11 | 2 | 9 | -2.1 | 20.1 | 0
7353 | TORONTO BUTTONVILLE A | 11 | 3 | 9 | 3.575 | 14.425 | 0
7354 | TORONTO BUTTONVILLE A | 11 | 2 | 10 | -1.4 | 19.4 | 0
7354 | TORONTO BUTTONVILLE A | 11 | 3 | 10 | 4.825 | 13.175 | 0
7355 | TORONTO BUTTONVILLE A | 11 | 2 | 11 | -0.4 | 18.4 | 0
7355 | TORONTO BUTTONVILLE A | 11 | 3 | 11 | 5.675 | 12.325 | 0
7356 | TORONTO BUTTONVILLE A | 11 | 2 | 12 | 0.5 | 17.5 | 0
7356 | TORONTO BUTTONVILLE A | 11 | 3 | 12 | 6.425 | 11.575 | 0
7357 | TORONTO BUTTONVILLE A | 11 | 2 | 13 | 1.4 | 16.6 | 0
7357 | TORONTO BUTTONVILLE A | 11 | 3 | 13 | 6.4 | 11.6 | 0
7358 | TORONTO BUTTONVILLE A | 11 | 2 | 14 | 2.2 | 15.8 | 0
7358 | TORONTO BUTTONVILLE A | 11 | 3 | 14 | 6.9 | 11.1 | 0
7359 | TORONTO BUTTONVILLE A | 11 | 2 | 15 | 2.8 | 15.2 | 0
7359 | TORONTO BUTTONVILLE A | 11 | 3 | 15 | 6.325 | 11.675 | 0
7360 | TORONTO BUTTONVILLE A | 11 | 2 | 16 | 3.3 | 14.7 | 0
7360 | TORONTO BUTTONVILLE A | 11 | 3 | 16 | 6.25 | 11.75 | 0
7361 | TORONTO BUTTONVILLE A | 11 | 2 | 17 | 3.3 | 14.7 | 0
7361 | TORONTO BUTTONVILLE A | 11 | 3 | 17 | 5.85 | 12.15 | 0
7362 | TORONTO BUTTONVILLE A | 11 | 2 | 18 | 3.7 | 14.3 | 0
7362 | TORONTO BUTTONVILLE A | 11 | 3 | 18 | 4.775 | 13.225 | 0
7363 | TORONTO BUTTONVILLE A | 11 | 2 | 19 | 4.2 | 13.8 | 0
7363 | TORONTO BUTTONVILLE A | 11 | 3 | 19 | 4.225 | 13.775 | 0
7364 | TORONTO BUTTONVILLE A | 11 | 2 | 20 | 4.5 | 13.5 | 0
7364 | TORONTO BUTTONVILLE A | 11 | 3 | 20 | 3.675 | 14.325 | 0
7365 | TORONTO BUTTONVILLE A | 11 | 2 | 21 | 4.5 | 13.5 | 0
7365 | TORONTO BUTTONVILLE A | 11 | 3 | 21 | 2.975 | 15.025 | 0
7366 | TORONTO BUTTONVILLE A | 11 | 2 | 22 | 5.8 | 12.2 | 0
7366 | TORONTO BUTTONVILLE A | 11 | 3 | 22 | 2.475 | 15.525 | 0
7367 | TORONTO BUTTONVILLE A | 11 | 2 | 23 | 6 | 12 | 0
7367 | TORONTO BUTTONVILLE A | 11 | 3 | 23 | 2 | 16 | 0
7368 | TORONTO BUTTONVILLE A | 11 | 2 | 24 | 6.2 | 11.8 | 0
7368 | TORONTO BUTTONVILLE A | 11 | 3 | 24 | 1 | 17 | 0
7369 | TORONTO BUTTONVILLE A | 11 | 3 | 1 | 6.3 | 11.7 | 0
7369 | TORONTO BUTTONVILLE A | 11 | 4 | 1 | 0.225 | 17.775 | 0
7370 | TORONTO BUTTONVILLE A | 11 | 3 | 2 | 6.5 | 11.5 | 0
7370 | TORONTO BUTTONVILLE A | 11 | 4 | 2 | 0.275 | 17.725 | 0
7371 | TORONTO BUTTONVILLE A | 11 | 3 | 3 | 6.3 | 11.7 | 0
7371 | TORONTO BUTTONVILLE A | 11 | 4 | 3 | 0.35 | 17.65 | 0
7372 | TORONTO BUTTONVILLE A | 11 | 3 | 4 | 6.5 | 11.5 | 0
7372 | TORONTO BUTTONVILLE A | 11 | 4 | 4 | 0.3 | 17.7 | 0
7373 | TORONTO BUTTONVILLE A | 11 | 3 | 5 | 6.3 | 11.7 | 0
7373 | TORONTO BUTTONVILLE A | 11 | 4 | 5 | 0.325 | 17.675 | 0
7374 | TORONTO BUTTONVILLE A | 11 | 3 | 6 | 3.7 | 14.3 | 0
7374 | TORONTO BUTTONVILLE A | 11 | 4 | 6 | 0.575 | 17.425 | 0
7375 | TORONTO BUTTONVILLE A | 11 | 3 | 7 | 4 | 14 | 0
7375 | TORONTO BUTTONVILLE A | 11 | 4 | 7 | 0.5 | 17.5 | 0
7376 | TORONTO BUTTONVILLE A | 11 | 3 | 8 | 3.5 | 14.5 | 0
7376 | TORONTO BUTTONVILLE A | 11 | 4 | 8 | 1.075 | 16.925 | 0
7377 | TORONTO BUTTONVILLE A | 11 | 3 | 9 | 3.5 | 14.5 | 0
7377 | TORONTO BUTTONVILLE A | 11 | 4 | 9 | 2.15 | 15.85 | 0
7378 | TORONTO BUTTONVILLE A | 11 | 3 | 10 | 2.8 | 15.2 | 0
7378 | TORONTO BUTTONVILLE A | 11 | 4 | 10 | 3.875 | 14.125 | 0
7379 | TORONTO BUTTONVILLE A | 11 | 3 | 11 | 3.1 | 14.9 | 0
7379 | TORONTO BUTTONVILLE A | 11 | 4 | 11 | 5.15 | 12.85 | 0
7380 | TORONTO BUTTONVILLE A | 11 | 3 | 12 | 4 | 14 | 0
7380 | TORONTO BUTTONVILLE A | 11 | 4 | 12 | 6.25 | 11.75 | 0
7381 | TORONTO BUTTONVILLE A | 11 | 3 | 13 | 4.2 | 13.8 | 0
7381 | TORONTO BUTTONVILLE A | 11 | 4 | 13 | 7.05 | 10.95 | 0
7382 | TORONTO BUTTONVILLE A | 11 | 3 | 14 | 4.3 | 13.7 | 0
7382 | TORONTO BUTTONVILLE A | 11 | 4 | 14 | 7.35 | 10.65 | 0
7383 | TORONTO BUTTONVILLE A | 11 | 3 | 15 | 4.5 | 13.5 | 0
7383 | TORONTO BUTTONVILLE A | 11 | 4 | 15 | 7.275 | 10.725 | 0
7384 | TORONTO BUTTONVILLE A | 11 | 3 | 16 | 4.5 | 13.5 | 0
7384 | TORONTO BUTTONVILLE A | 11 | 4 | 16 | 7.025 | 10.975 | 0
7385 | TORONTO BUTTONVILLE A | 11 | 3 | 17 | 4.9 | 13.1 | 0
7385 | TORONTO BUTTONVILLE A | 11 | 4 | 17 | 6.625 | 11.375 | 0
7386 | TORONTO BUTTONVILLE A | 11 | 3 | 18 | 4.5 | 13.5 | 0
7386 | TORONTO BUTTONVILLE A | 11 | 4 | 18 | 6.275 | 11.725 | 0
7387 | TORONTO BUTTONVILLE A | 11 | 3 | 19 | 4.1 | 13.9 | 0
7387 | TORONTO BUTTONVILLE A | 11 | 4 | 19 | 6.1 | 11.9 | 0
7388 | TORONTO BUTTONVILLE A | 11 | 3 | 20 | 4.2 | 13.8 | 0
7388 | TORONTO BUTTONVILLE A | 11 | 4 | 20 | 6.025 | 11.975 | 0
7389 | TORONTO BUTTONVILLE A | 11 | 3 | 21 | 4.3 | 13.7 | 0
7389 | TORONTO BUTTONVILLE A | 11 | 4 | 21 | 5.575 | 12.425 | 0
7390 | TORONTO BUTTONVILLE A | 11 | 3 | 22 | 4.6 | 13.4 | 0
7390 | TORONTO BUTTONVILLE A | 11 | 4 | 22 | 5.125 | 12.875 | 0
7391 | TORONTO BUTTONVILLE A | 11 | 3 | 23 | 4.4 | 13.6 | 0
7391 | TORONTO BUTTONVILLE A | 11 | 4 | 23 | 4.7 | 13.3 | 0
7392 | TORONTO BUTTONVILLE A | 11 | 3 | 24 | 4 | 14 | 0
7392 | TORONTO BUTTONVILLE A | 11 | 4 | 24 | 4.8 | 13.2 | 0
7393 | TORONTO BUTTONVILLE A | 11 | 4 | 1 | 3.5 | 14.5 | 0
7393 | TORONTO BUTTONVILLE A | 11 | 5 | 1 | 4.975 | 13.025 | 0
7394 | TORONTO BUTTONVILLE A | 11 | 4 | 2 | 3.1 | 14.9 | 0
7394 | TORONTO BUTTONVILLE A | 11 | 5 | 2 | 4.8 | 13.2 | 0
7395 | TORONTO BUTTONVILLE A | 11 | 4 | 3 | 2.1 | 15.9 | 0
7395 | TORONTO BUTTONVILLE A | 11 | 5 | 3 | 5 | 13 | 0
7396 | TORONTO BUTTONVILLE A | 11 | 4 | 4 | 2.1 | 15.9 | 0
7396 | TORONTO BUTTONVILLE A | 11 | 5 | 4 | 4.375 | 13.625 | 0
7397 | TORONTO BUTTONVILLE A | 11 | 4 | 5 | 1.2 | 16.8 | 0
7397 | TORONTO BUTTONVILLE A | 11 | 5 | 5 | 4.55 | 13.45 | 0
7398 | TORONTO BUTTONVILLE A | 11 | 4 | 6 | 0.6 | 17.4 | 0
7398 | TORONTO BUTTONVILLE A | 11 | 5 | 6 | 4.45 | 13.55 | 0
7399 | TORONTO BUTTONVILLE A | 11 | 4 | 7 | 1.4 | 16.6 | 0
7399 | TORONTO BUTTONVILLE A | 11 | 5 | 7 | 4.65 | 13.35 | 0
7400 | TORONTO BUTTONVILLE A | 11 | 4 | 8 | 1.1 | 16.9 | 0
7400 | TORONTO BUTTONVILLE A | 11 | 5 | 8 | 4.65 | 13.35 | 0
7401 | TORONTO BUTTONVILLE A | 11 | 4 | 9 | 8 | 10 | 0
7401 | TORONTO BUTTONVILLE A | 11 | 5 | 9 | 5.3 | 12.7 | 0
7402 | TORONTO BUTTONVILLE A | 11 | 4 | 10 | 10.1 | 7.9 | 0
7402 | TORONTO BUTTONVILLE A | 11 | 5 | 10 | 6.175 | 11.825 | 0
7403 | TORONTO BUTTONVILLE A | 11 | 4 | 11 | 12.9 | 5.1 | 0
7403 | TORONTO BUTTONVILLE A | 11 | 5 | 11 | 6.95 | 11.05 | 0
7404 | TORONTO BUTTONVILLE A | 11 | 4 | 12 | 15 | 3 | 0
7404 | TORONTO BUTTONVILLE A | 11 | 5 | 12 | 7.775 | 10.225 | 0
7405 | TORONTO BUTTONVILLE A | 11 | 4 | 13 | 16.4 | 1.6 | 0
7405 | TORONTO BUTTONVILLE A | 11 | 5 | 13 | 8.675 | 9.325 | 0
7406 | TORONTO BUTTONVILLE A | 11 | 4 | 14 | 16.4 | 1.6 | 0
7406 | TORONTO BUTTONVILLE A | 11 | 5 | 14 | 9.325 | 8.675 | 0
7407 | TORONTO BUTTONVILLE A | 11 | 4 | 15 | 16.9 | 1.1 | 0
7407 | TORONTO BUTTONVILLE A | 11 | 5 | 15 | 9.9 | 8.1 | 0
7408 | TORONTO BUTTONVILLE A | 11 | 4 | 16 | 17.6 | 0.4 | 0
7408 | TORONTO BUTTONVILLE A | 11 | 5 | 16 | 10 | 8 | 0
7409 | TORONTO BUTTONVILLE A | 11 | 4 | 17 | 17.7 | 0.3 | 0
7409 | TORONTO BUTTONVILLE A | 11 | 5 | 17 | 9.85 | 8.15 | 0
7410 | TORONTO BUTTONVILLE A | 11 | 4 | 18 | 16.2 | 1.8 | 0
7410 | TORONTO BUTTONVILLE A | 11 | 5 | 18 | 9.2 | 8.8 | 0
7411 | TORONTO BUTTONVILLE A | 11 | 4 | 19 | 14.7 | 3.3 | 0
7411 | TORONTO BUTTONVILLE A | 11 | 5 | 19 | 8.55 | 9.45 | 0
7412 | TORONTO BUTTONVILLE A | 11 | 4 | 20 | 12.5 | 5.5 | 0
7412 | TORONTO BUTTONVILLE A | 11 | 5 | 20 | 8.175 | 9.825 | 0
7413 | TORONTO BUTTONVILLE A | 11 | 4 | 21 | 12.9 | 5.1 | 0
7413 | TORONTO BUTTONVILLE A | 11 | 5 | 21 | 7.55 | 10.45 | 0
7414 | TORONTO BUTTONVILLE A | 11 | 4 | 22 | 14.9 | 3.1 | 0
7414 | TORONTO BUTTONVILLE A | 11 | 5 | 22 | 7.4 | 10.6 | 0
7415 | TORONTO BUTTONVILLE A | 11 | 4 | 23 | 14.3 | 3.7 | 0
7415 | TORONTO BUTTONVILLE A | 11 | 5 | 23 | 7.5 | 10.5 | 0
7416 | TORONTO BUTTONVILLE A | 11 | 4 | 24 | 13.5 | 4.5 | 0
7416 | TORONTO BUTTONVILLE A | 11 | 5 | 24 | 6.35 | 11.65 | 0
7417 | TORONTO BUTTONVILLE A | 11 | 5 | 1 | 13.5 | 4.5 | 0
7417 | TORONTO BUTTONVILLE A | 11 | 6 | 1 | 5.6 | 12.4 | 0
7418 | TORONTO BUTTONVILLE A | 11 | 5 | 2 | 12.9 | 5.1 | 0
7418 | TORONTO BUTTONVILLE A | 11 | 6 | 2 | 4.95 | 13.05 | 0
7419 | TORONTO BUTTONVILLE A | 11 | 5 | 3 | 12.6 | 5.4 | 0
7419 | TORONTO BUTTONVILLE A | 11 | 6 | 3 | 4.675 | 13.325 | 0
7420 | TORONTO BUTTONVILLE A | 11 | 5 | 4 | 12.6 | 5.4 | 0
7420 | TORONTO BUTTONVILLE A | 11 | 6 | 4 | 4.1 | 13.9 | 0
7421 | TORONTO BUTTONVILLE A | 11 | 5 | 5 | 11.8 | 6.2 | 0
7421 | TORONTO BUTTONVILLE A | 11 | 6 | 5 | 3.4 | 14.6 | 0
7422 | TORONTO BUTTONVILLE A | 11 | 5 | 6 | 11.1 | 6.9 | 0
7422 | TORONTO BUTTONVILLE A | 11 | 6 | 6 | 2.85 | 15.15 | 0
7423 | TORONTO BUTTONVILLE A | 11 | 5 | 7 | 11 | 7 | 0
7423 | TORONTO BUTTONVILLE A | 11 | 6 | 7 | 3 | 15 | 0
7424 | TORONTO BUTTONVILLE A | 11 | 5 | 8 | 10.2 | 7.8 | 0
7424 | TORONTO BUTTONVILLE A | 11 | 6 | 8 | 2.8 | 15.2 | 0
7425 | TORONTO BUTTONVILLE A | 11 | 5 | 9 | 11.1 | 6.9 | 0
7425 | TORONTO BUTTONVILLE A | 11 | 6 | 9 | 3.625 | 14.375 | 0
7426 | TORONTO BUTTONVILLE A | 11 | 5 | 10 | 13.4 | 4.6 | 0
7426 | TORONTO BUTTONVILLE A | 11 | 6 | 10 | 4.775 | 13.225 | 0
7427 | TORONTO BUTTONVILLE A | 11 | 5 | 11 | 14.4 | 3.6 | 0
7427 | TORONTO BUTTONVILLE A | 11 | 6 | 11 | 6.175 | 11.825 | 0
7428 | TORONTO BUTTONVILLE A | 11 | 5 | 12 | 14.5 | 3.5 | 0
7428 | TORONTO BUTTONVILLE A | 11 | 6 | 12 | 6.825 | 11.175 | 0
7429 | TORONTO BUTTONVILLE A | 11 | 5 | 13 | 17.2 | 0.8 | 0
7429 | TORONTO BUTTONVILLE A | 11 | 6 | 13 | 8.25 | 9.75 | 0
7430 | TORONTO BUTTONVILLE A | 11 | 5 | 14 | 17 | 1 | 0
7430 | TORONTO BUTTONVILLE A | 11 | 6 | 14 | 9.225 | 8.775 | 0
7431 | TORONTO BUTTONVILLE A | 11 | 5 | 15 | 17.4 | 0.6 | 0
7431 | TORONTO BUTTONVILLE A | 11 | 6 | 15 | 8.775 | 9.225 | 0
7432 | TORONTO BUTTONVILLE A | 11 | 5 | 16 | 17.6 | 0.4 | 0
7432 | TORONTO BUTTONVILLE A | 11 | 6 | 16 | 8.375 | 9.625 | 0
7433 | TORONTO BUTTONVILLE A | 11 | 5 | 17 | 16.2 | 1.8 | 0
7433 | TORONTO BUTTONVILLE A | 11 | 6 | 17 | 7.6 | 10.4 | 0
7434 | TORONTO BUTTONVILLE A | 11 | 5 | 18 | 15.2 | 2.8 | 0
7434 | TORONTO BUTTONVILLE A | 11 | 6 | 18 | 6.975 | 11.025 | 0
7435 | TORONTO BUTTONVILLE A | 11 | 5 | 19 | 15.5 | 2.5 | 0
7435 | TORONTO BUTTONVILLE A | 11 | 6 | 19 | 6.275 | 11.725 | 0
7436 | TORONTO BUTTONVILLE A | 11 | 5 | 20 | 15.6 | 2.4 | 0
7436 | TORONTO BUTTONVILLE A | 11 | 6 | 20 | 5.95 | 12.05 | 0
7437 | TORONTO BUTTONVILLE A | 11 | 5 | 21 | 15.1 | 2.9 | 0
7437 | TORONTO BUTTONVILLE A | 11 | 6 | 21 | 5.9 | 12.1 | 0
7438 | TORONTO BUTTONVILLE A | 11 | 5 | 22 | 14 | 4 | 0
7438 | TORONTO BUTTONVILLE A | 11 | 6 | 22 | 5.475 | 12.525 | 0
7439 | TORONTO BUTTONVILLE A | 11 | 5 | 23 | 12.7 | 5.3 | 0
7439 | TORONTO BUTTONVILLE A | 11 | 6 | 23 | 4.6 | 13.4 | 0
7440 | TORONTO BUTTONVILLE A | 11 | 5 | 24 | 13.1 | 4.9 | 0
7440 | TORONTO BUTTONVILLE A | 11 | 6 | 24 | 4.75 | 13.25 | 0
7441 | TORONTO BUTTONVILLE A | 11 | 6 | 1 | 12.1 | 5.9 | 0
7441 | TORONTO BUTTONVILLE A | 11 | 7 | 1 | 4.55 | 13.45 | 0
7442 | TORONTO BUTTONVILLE A | 11 | 6 | 2 | 10.7 | 7.3 | 0
7442 | TORONTO BUTTONVILLE A | 11 | 7 | 2 | 3.775 | 14.225 | 0
7443 | TORONTO BUTTONVILLE A | 11 | 6 | 3 | 9.6 | 8.4 | 0
7443 | TORONTO BUTTONVILLE A | 11 | 7 | 3 | 3.125 | 14.875 | 0
7444 | TORONTO BUTTONVILLE A | 11 | 6 | 4 | 7.9 | 10.1 | 0
7444 | TORONTO BUTTONVILLE A | 11 | 7 | 4 | 2.65 | 15.35 | 0
7445 | TORONTO BUTTONVILLE A | 11 | 6 | 5 | 9.9 | 8.1 | 0
7445 | TORONTO BUTTONVILLE A | 11 | 7 | 5 | 2.3 | 15.7 | 0
7446 | TORONTO BUTTONVILLE A | 11 | 6 | 6 | 7.8 | 10.2 | 0
7446 | TORONTO BUTTONVILLE A | 11 | 7 | 6 | 1.925 | 16.075 | 0
7447 | TORONTO BUTTONVILLE A | 11 | 6 | 7 | 7 | 11 | 0
7447 | TORONTO BUTTONVILLE A | 11 | 7 | 7 | 1.65 | 16.35 | 0
7448 | TORONTO BUTTONVILLE A | 11 | 6 | 8 | 4.3 | 13.7 | 0
7448 | TORONTO BUTTONVILLE A | 11 | 7 | 8 | 1.675 | 16.325 | 0
7449 | TORONTO BUTTONVILLE A | 11 | 6 | 9 | 8.6 | 9.4 | 0
7449 | TORONTO BUTTONVILLE A | 11 | 7 | 9 | 2.175 | 15.825 | 0
7450 | TORONTO BUTTONVILLE A | 11 | 6 | 10 | 12.5 | 5.5 | 0
7450 | TORONTO BUTTONVILLE A | 11 | 7 | 10 | 4.5 | 13.5 | 0
7451 | TORONTO BUTTONVILLE A | 11 | 6 | 11 | 14.8 | 3.2 | 0
7451 | TORONTO BUTTONVILLE A | 11 | 7 | 11 | 5.3 | 12.7 | 0
7452 | TORONTO BUTTONVILLE A | 11 | 6 | 12 | 17.4 | 0.6 | 0
7452 | TORONTO BUTTONVILLE A | 11 | 7 | 12 | 6.25 | 11.75 | 0
7453 | TORONTO BUTTONVILLE A | 11 | 6 | 13 | 18.5 | 0 | 0.5
7453 | TORONTO BUTTONVILLE A | 11 | 7 | 13 | 6.3 | 11.7 | 0
7454 | TORONTO BUTTONVILLE A | 11 | 6 | 14 | 19.3 | 0 | 1.3
7454 | TORONTO BUTTONVILLE A | 11 | 7 | 14 | 7.2 | 10.8 | 0
7455 | TORONTO BUTTONVILLE A | 11 | 6 | 15 | 19.9 | 0 | 1.9
7455 | TORONTO BUTTONVILLE A | 11 | 7 | 15 | 6.7 | 11.3 | 0
7456 | TORONTO BUTTONVILLE A | 11 | 6 | 16 | 20.2 | 0 | 2.2
7456 | TORONTO BUTTONVILLE A | 11 | 7 | 16 | 6.85 | 11.15 | 0
7457 | TORONTO BUTTONVILLE A | 11 | 6 | 17 | 20.4 | 0 | 2.4
7457 | TORONTO BUTTONVILLE A | 11 | 7 | 17 | 6.775 | 11.225 | 0
7458 | TORONTO BUTTONVILLE A | 11 | 6 | 18 | 18.9 | 0 | 0.9
7458 | TORONTO BUTTONVILLE A | 11 | 7 | 18 | 5.575 | 12.425 | 0
7459 | TORONTO BUTTONVILLE A | 11 | 6 | 19 | 17.3 | 0.7 | 0
7459 | TORONTO BUTTONVILLE A | 11 | 7 | 19 | 5.15 | 12.85 | 0
7460 | TORONTO BUTTONVILLE A | 11 | 6 | 20 | 16.1 | 1.9 | 0
7460 | TORONTO BUTTONVILLE A | 11 | 7 | 20 | 4.375 | 13.625 | 0
7461 | TORONTO BUTTONVILLE A | 11 | 6 | 21 | 15 | 3 | 0
7461 | TORONTO BUTTONVILLE A | 11 | 7 | 21 | 4.025 | 13.975 | 0
7462 | TORONTO BUTTONVILLE A | 11 | 6 | 22 | 13.7 | 4.3 | 0
7462 | TORONTO BUTTONVILLE A | 11 | 7 | 22 | 3.525 | 14.475 | 0
7463 | TORONTO BUTTONVILLE A | 11 | 6 | 23 | 13.7 | 4.3 | 0
7463 | TORONTO BUTTONVILLE A | 11 | 7 | 23 | 2.925 | 15.075 | 0
7464 | TORONTO BUTTONVILLE A | 11 | 6 | 24 | 12.9 | 5.1 | 0
7464 | TORONTO BUTTONVILLE A | 11 | 7 | 24 | 2.3 | 15.7 | 0
7465 | TORONTO BUTTONVILLE A | 11 | 7 | 1 | 13 | 5 | 0
7465 | TORONTO BUTTONVILLE A | 11 | 8 | 1 | 1.725 | 16.275 | 0
7466 | TORONTO BUTTONVILLE A | 11 | 7 | 2 | 12.4 | 5.6 | 0
7466 | TORONTO BUTTONVILLE A | 11 | 8 | 2 | 0.975 | 17.025 | 0
7467 | TORONTO BUTTONVILLE A | 11 | 7 | 3 | 11.2 | 6.8 | 0
7467 | TORONTO BUTTONVILLE A | 11 | 8 | 3 | 0.5 | 17.5 | 0
7468 | TORONTO BUTTONVILLE A | 11 | 7 | 4 | 9.1 | 8.9 | 0
7468 | TORONTO BUTTONVILLE A | 11 | 8 | 4 | 0.225 | 17.775 | 0
7469 | TORONTO BUTTONVILLE A | 11 | 7 | 5 | 11.7 | 6.3 | 0
7469 | TORONTO BUTTONVILLE A | 11 | 8 | 5 | 0.075 | 17.925 | 0
7470 | TORONTO BUTTONVILLE A | 11 | 7 | 6 | 10.3 | 7.7 | 0
7470 | TORONTO BUTTONVILLE A | 11 | 8 | 6 | -0.1 | 18.1 | 0
7471 | TORONTO BUTTONVILLE A | 11 | 7 | 7 | 9.3 | 8.7 | 0
7471 | TORONTO BUTTONVILLE A | 11 | 8 | 7 | -0.225 | 18.225 | 0
7472 | TORONTO BUTTONVILLE A | 11 | 7 | 8 | 8.8 | 9.2 | 0
7472 | TORONTO BUTTONVILLE A | 11 | 8 | 8 | -0.25 | 18.25 | 0
7473 | TORONTO BUTTONVILLE A | 11 | 7 | 9 | 10.2 | 7.8 | 0
7473 | TORONTO BUTTONVILLE A | 11 | 8 | 9 | 0.4 | 17.6 | 0
7474 | TORONTO BUTTONVILLE A | 11 | 7 | 10 | 12.8 | 5.2 | 0
7474 | TORONTO BUTTONVILLE A | 11 | 8 | 10 | 3.025 | 14.975 | 0
7475 | TORONTO BUTTONVILLE A | 11 | 7 | 11 | 15 | 3 | 0
7475 | TORONTO BUTTONVILLE A | 11 | 8 | 11 | 4.45 | 13.55 | 0
7476 | TORONTO BUTTONVILLE A | 11 | 7 | 12 | 17.3 | 0.7 | 0
7476 | TORONTO BUTTONVILLE A | 11 | 8 | 12 | 5.65 | 12.35 | 0
7477 | TORONTO BUTTONVILLE A | 11 | 7 | 13 | 20 | 0 | 2
7477 | TORONTO BUTTONVILLE A | 11 | 8 | 13 | 6.4 | 11.6 | 0
7478 | TORONTO BUTTONVILLE A | 11 | 7 | 14 | 20.9 | 0 | 2.9
7478 | TORONTO BUTTONVILLE A | 11 | 8 | 14 | 6.725 | 11.275 | 0
7479 | TORONTO BUTTONVILLE A | 11 | 7 | 15 | 21.3 | 0 | 3.3
7479 | TORONTO BUTTONVILLE A | 11 | 8 | 15 | 7.25 | 10.75 | 0
7480 | TORONTO BUTTONVILLE A | 11 | 7 | 16 | 21 | 0 | 3
7480 | TORONTO BUTTONVILLE A | 11 | 8 | 16 | 7.4 | 10.6 | 0
7481 | TORONTO BUTTONVILLE A | 11 | 7 | 17 | 20.4 | 0 | 2.4
7481 | TORONTO BUTTONVILLE A | 11 | 8 | 17 | 7.025 | 10.975 | 0
7482 | TORONTO BUTTONVILLE A | 11 | 7 | 18 | 18.8 | 0 | 0.8
7482 | TORONTO BUTTONVILLE A | 11 | 8 | 18 | 5.775 | 12.225 | 0
7483 | TORONTO BUTTONVILLE A | 11 | 7 | 19 | 17 | 1 | 0
7483 | TORONTO BUTTONVILLE A | 11 | 8 | 19 | 5.55 | 12.45 | 0
7484 | TORONTO BUTTONVILLE A | 11 | 7 | 20 | 16.1 | 1.9 | 0
7484 | TORONTO BUTTONVILLE A | 11 | 8 | 20 | 5.2 | 12.8 | 0
7485 | TORONTO BUTTONVILLE A | 11 | 7 | 21 | 15.1 | 2.9 | 0
7485 | TORONTO BUTTONVILLE A | 11 | 8 | 21 | 4.35 | 13.65 | 0
7486 | TORONTO BUTTONVILLE A | 11 | 7 | 22 | 14.1 | 3.9 | 0
7486 | TORONTO BUTTONVILLE A | 11 | 8 | 22 | 3.375 | 14.625 | 0
7487 | TORONTO BUTTONVILLE A | 11 | 7 | 23 | 13.2 | 4.8 | 0
7487 | TORONTO BUTTONVILLE A | 11 | 8 | 23 | 2.025 | 15.975 | 0
7488 | TORONTO BUTTONVILLE A | 11 | 7 | 24 | 12.2 | 5.8 | 0
7488 | TORONTO BUTTONVILLE A | 11 | 8 | 24 | 1.725 | 16.275 | 0
7489 | TORONTO BUTTONVILLE A | 11 | 8 | 1 | 11.7 | 6.3 | 0
7489 | TORONTO BUTTONVILLE A | 11 | 9 | 1 | 1.05 | 16.95 | 0
7490 | TORONTO BUTTONVILLE A | 11 | 8 | 2 | 8.8 | 9.2 | 0
7490 | TORONTO BUTTONVILLE A | 11 | 9 | 2 | 0.325 | 17.675 | 0
7491 | TORONTO BUTTONVILLE A | 11 | 8 | 3 | 7.2 | 10.8 | 0
7491 | TORONTO BUTTONVILLE A | 11 | 9 | 3 | 0.2 | 17.8 | 0
7492 | TORONTO BUTTONVILLE A | 11 | 8 | 4 | 6.4 | 11.6 | 0
7492 | TORONTO BUTTONVILLE A | 11 | 9 | 4 | 0.075 | 17.925 | 0
7493 | TORONTO BUTTONVILLE A | 11 | 8 | 5 | 5.3 | 12.7 | 0
7493 | TORONTO BUTTONVILLE A | 11 | 9 | 5 | 0.475 | 17.525 | 0
7494 | TORONTO BUTTONVILLE A | 11 | 8 | 6 | 4.8 | 13.2 | 0
7494 | TORONTO BUTTONVILLE A | 11 | 9 | 6 | 0.8 | 17.2 | 0
7495 | TORONTO BUTTONVILLE A | 11 | 8 | 7 | 4.7 | 13.3 | 0
7495 | TORONTO BUTTONVILLE A | 11 | 9 | 7 | 2.025 | 15.975 | 0
7496 | TORONTO BUTTONVILLE A | 11 | 8 | 8 | 4.8 | 13.2 | 0
7496 | TORONTO BUTTONVILLE A | 11 | 9 | 8 | 2.2 | 15.8 | 0
7497 | TORONTO BUTTONVILLE A | 11 | 8 | 9 | 6.3 | 11.7 | 0
7497 | TORONTO BUTTONVILLE A | 11 | 9 | 9 | 2.85 | 15.15 | 0
7498 | TORONTO BUTTONVILLE A | 11 | 8 | 10 | 10.4 | 7.6 | 0
7498 | TORONTO BUTTONVILLE A | 11 | 9 | 10 | 3.65 | 14.35 | 0
7499 | TORONTO BUTTONVILLE A | 11 | 8 | 11 | 16.1 | 1.9 | 0
7499 | TORONTO BUTTONVILLE A | 11 | 9 | 11 | 3.95 | 14.05 | 0
7500 | TORONTO BUTTONVILLE A | 11 | 8 | 12 | 18.4 | 0 | 0.4
7500 | TORONTO BUTTONVILLE A | 11 | 9 | 12 | 5.05 | 12.95 | 0
7501 | TORONTO BUTTONVILLE A | 11 | 8 | 13 | 19.9 | 0 | 1.9
7501 | TORONTO BUTTONVILLE A | 11 | 9 | 13 | 5.325 | 12.675 | 0
7502 | TORONTO BUTTONVILLE A | 11 | 8 | 14 | 21.4 | 0 | 3.4
7502 | TORONTO BUTTONVILLE A | 11 | 9 | 14 | 5.175 | 12.825 | 0
7503 | TORONTO BUTTONVILLE A | 11 | 8 | 15 | 21.7 | 0 | 3.7
7503 | TORONTO BUTTONVILLE A | 11 | 9 | 15 | 5.75 | 12.25 | 0
7504 | TORONTO BUTTONVILLE A | 11 | 8 | 16 | 21 | 0 | 3
7504 | TORONTO BUTTONVILLE A | 11 | 9 | 16 | 5.8 | 12.2 | 0
7505 | TORONTO BUTTONVILLE A | 11 | 8 | 17 | 19.5 | 0 | 1.5
7505 | TORONTO BUTTONVILLE A | 11 | 9 | 17 | 5.375 | 12.625 | 0
7506 | TORONTO BUTTONVILLE A | 11 | 8 | 18 | 17.9 | 0.1 | 0
7506 | TORONTO BUTTONVILLE A | 11 | 9 | 18 | 5.375 | 12.625 | 0
7507 | TORONTO BUTTONVILLE A | 11 | 8 | 19 | 16.1 | 1.9 | 0
7507 | TORONTO BUTTONVILLE A | 11 | 9 | 19 | 5.175 | 12.825 | 0
7508 | TORONTO BUTTONVILLE A | 11 | 8 | 20 | 13.5 | 4.5 | 0
7508 | TORONTO BUTTONVILLE A | 11 | 9 | 20 | 4.1 | 13.9 | 0
7509 | TORONTO BUTTONVILLE A | 11 | 8 | 21 | 10.8 | 7.2 | 0
7509 | TORONTO BUTTONVILLE A | 11 | 9 | 21 | 3.925 | 14.075 | 0
7510 | TORONTO BUTTONVILLE A | 11 | 8 | 22 | 9.4 | 8.6 | 0
7510 | TORONTO BUTTONVILLE A | 11 | 9 | 22 | 3.525 | 14.475 | 0
7511 | TORONTO BUTTONVILLE A | 11 | 8 | 23 | 9.6 | 8.4 | 0
7511 | TORONTO BUTTONVILLE A | 11 | 9 | 23 | 3.05 | 14.95 | 0
7512 | TORONTO BUTTONVILLE A | 11 | 8 | 24 | 8.4 | 9.6 | 0
7512 | TORONTO BUTTONVILLE A | 11 | 9 | 24 | 2.575 | 15.425 | 0
7513 | TORONTO BUTTONVILLE A | 11 | 9 | 1 | 8.3 | 9.7 | 0
7513 | TORONTO BUTTONVILLE A | 11 | 10 | 1 | 2 | 16 | 0
7514 | TORONTO BUTTONVILLE A | 11 | 9 | 2 | 7.7 | 10.3 | 0
7514 | TORONTO BUTTONVILLE A | 11 | 10 | 2 | 1.15 | 16.85 | 0
7515 | TORONTO BUTTONVILLE A | 11 | 9 | 3 | 7.5 | 10.5 | 0
7515 | TORONTO BUTTONVILLE A | 11 | 10 | 3 | 0.65 | 17.35 | 0
7516 | TORONTO BUTTONVILLE A | 11 | 9 | 4 | 7.3 | 10.7 | 0
7516 | TORONTO BUTTONVILLE A | 11 | 10 | 4 | 0.075 | 17.925 | 0
7517 | TORONTO BUTTONVILLE A | 11 | 9 | 5 | 7 | 11 | 0
7517 | TORONTO BUTTONVILLE A | 11 | 10 | 5 | -0.55 | 18.55 | 0
7518 | TORONTO BUTTONVILLE A | 11 | 9 | 6 | 7.2 | 10.8 | 0
7518 | TORONTO BUTTONVILLE A | 11 | 10 | 6 | -0.675 | 18.675 | 0
7519 | TORONTO BUTTONVILLE A | 11 | 9 | 7 | 7 | 11 | 0
7519 | TORONTO BUTTONVILLE A | 11 | 10 | 7 | -0.975 | 18.975 | 0
7520 | TORONTO BUTTONVILLE A | 11 | 9 | 8 | 7.1 | 10.9 | 0
7520 | TORONTO BUTTONVILLE A | 11 | 10 | 8 | -1.65 | 19.65 | 0
7521 | TORONTO BUTTONVILLE A | 11 | 9 | 9 | 8.6 | 9.4 | 0
7521 | TORONTO BUTTONVILLE A | 11 | 10 | 9 | -1.425 | 19.425 | 0
7522 | TORONTO BUTTONVILLE A | 11 | 9 | 10 | 11.5 | 6.5 | 0
7522 | TORONTO BUTTONVILLE A | 11 | 10 | 10 | -0.275 | 18.275 | 0
7523 | TORONTO BUTTONVILLE A | 11 | 9 | 11 | 14.2 | 3.8 | 0
7523 | TORONTO BUTTONVILLE A | 11 | 10 | 11 | 1.075 | 16.925 | 0
7524 | TORONTO BUTTONVILLE A | 11 | 9 | 12 | 17.3 | 0.7 | 0
7524 | TORONTO BUTTONVILLE A | 11 | 10 | 12 | 1.825 | 16.175 | 0
7525 | TORONTO BUTTONVILLE A | 11 | 9 | 13 | 19 | 0 | 1
7525 | TORONTO BUTTONVILLE A | 11 | 10 | 13 | 2.275 | 15.725 | 0
7526 | TORONTO BUTTONVILLE A | 11 | 9 | 14 | 19.9 | 0 | 1.9
7526 | TORONTO BUTTONVILLE A | 11 | 10 | 14 | 3.15 | 14.85 | 0
7527 | TORONTO BUTTONVILLE A | 11 | 9 | 15 | 20.8 | 0 | 2.8
7527 | TORONTO BUTTONVILLE A | 11 | 10 | 15 | 3.375 | 14.625 | 0
7528 | TORONTO BUTTONVILLE A | 11 | 9 | 16 | 20.5 | 0 | 2.5
7528 | TORONTO BUTTONVILLE A | 11 | 10 | 16 | 3.45 | 14.55 | 0
7529 | TORONTO BUTTONVILLE A | 11 | 9 | 17 | 20.1 | 0 | 2.1
7529 | TORONTO BUTTONVILLE A | 11 | 10 | 17 | 2.975 | 15.025 | 0
7530 | TORONTO BUTTONVILLE A | 11 | 9 | 18 | 17.1 | 0.9 | 0
7530 | TORONTO BUTTONVILLE A | 11 | 10 | 18 | 2.375 | 15.625 | 0
7531 | TORONTO BUTTONVILLE A | 11 | 9 | 19 | 12.8 | 5.2 | 0
7531 | TORONTO BUTTONVILLE A | 11 | 10 | 19 | 1.8 | 16.2 | 0
7532 | TORONTO BUTTONVILLE A | 11 | 9 | 20 | 12 | 6 | 0
7532 | TORONTO BUTTONVILLE A | 11 | 10 | 20 | 1.075 | 16.925 | 0
7533 | TORONTO BUTTONVILLE A | 11 | 9 | 21 | 10.3 | 7.7 | 0
7533 | TORONTO BUTTONVILLE A | 11 | 10 | 21 | -0.125 | 18.125 | 0
7534 | TORONTO BUTTONVILLE A | 11 | 9 | 22 | 9.5 | 8.5 | 0
7534 | TORONTO BUTTONVILLE A | 11 | 10 | 22 | -0.9 | 18.9 | 0
7535 | TORONTO BUTTONVILLE A | 11 | 9 | 23 | 8.4 | 9.6 | 0
7535 | TORONTO BUTTONVILLE A | 11 | 10 | 23 | -1.25 | 19.25 | 0
7536 | TORONTO BUTTONVILLE A | 11 | 9 | 24 | 8.5 | 9.5 | 0
7536 | TORONTO BUTTONVILLE A | 11 | 10 | 24 | -1.625 | 19.625 | 0
7537 | TORONTO BUTTONVILLE A | 11 | 10 | 1 | 8.4 | 9.6 | 0
7537 | TORONTO BUTTONVILLE A | 11 | 11 | 1 | -2.4 | 20.4 | 0
7538 | TORONTO BUTTONVILLE A | 11 | 10 | 2 | 8.5 | 9.5 | 0
7538 | TORONTO BUTTONVILLE A | 11 | 11 | 2 | -1.875 | 19.875 | 0
7539 | TORONTO BUTTONVILLE A | 11 | 10 | 3 | 7.7 | 10.3 | 0
7539 | TORONTO BUTTONVILLE A | 11 | 11 | 3 | -1.9 | 19.9 | 0
7540 | TORONTO BUTTONVILLE A | 11 | 10 | 4 | 7.3 | 10.7 | 0
7540 | TORONTO BUTTONVILLE A | 11 | 11 | 4 | -2.25 | 20.25 | 0
7541 | TORONTO BUTTONVILLE A | 11 | 10 | 5 | 7.2 | 10.8 | 0
7541 | TORONTO BUTTONVILLE A | 11 | 11 | 5 | -1.9 | 19.9 | 0
7542 | TORONTO BUTTONVILLE A | 11 | 10 | 6 | 7.3 | 10.7 | 0
7542 | TORONTO BUTTONVILLE A | 11 | 11 | 6 | -1.775 | 19.775 | 0
7543 | TORONTO BUTTONVILLE A | 11 | 10 | 7 | 7.7 | 10.3 | 0
7543 | TORONTO BUTTONVILLE A | 11 | 11 | 7 | -1.95 | 19.95 | 0
7544 | TORONTO BUTTONVILLE A | 11 | 10 | 8 | 8.5 | 9.5 | 0
7544 | TORONTO BUTTONVILLE A | 11 | 11 | 8 | -2.05 | 20.05 | 0
7545 | TORONTO BUTTONVILLE A | 11 | 10 | 9 | 9.7 | 8.3 | 0
7545 | TORONTO BUTTONVILLE A | 11 | 11 | 9 | -1.775 | 19.775 | 0
7546 | TORONTO BUTTONVILLE A | 11 | 10 | 10 | 12 | 6 | 0
7546 | TORONTO BUTTONVILLE A | 11 | 11 | 10 | -0.15 | 18.15 | 0
7547 | TORONTO BUTTONVILLE A | 11 | 10 | 11 | 15.9 | 2.1 | 0
7547 | TORONTO BUTTONVILLE A | 11 | 11 | 11 | 0.75 | 17.25 | 0
7548 | TORONTO BUTTONVILLE A | 11 | 10 | 12 | 19.9 | 0 | 1.9
7548 | TORONTO BUTTONVILLE A | 11 | 11 | 12 | 1.475 | 16.525 | 0
7549 | TORONTO BUTTONVILLE A | 11 | 10 | 13 | 21.2 | 0 | 3.2
7549 | TORONTO BUTTONVILLE A | 11 | 11 | 13 | 1.65 | 16.35 | 0
7550 | TORONTO BUTTONVILLE A | 11 | 10 | 14 | 22.8 | 0 | 4.8
7550 | TORONTO BUTTONVILLE A | 11 | 11 | 14 | 1.875 | 16.125 | 0
7551 | TORONTO BUTTONVILLE A | 11 | 10 | 15 | 23 | 0 | 5
7551 | TORONTO BUTTONVILLE A | 11 | 11 | 15 | 1.65 | 16.35 | 0
7552 | TORONTO BUTTONVILLE A | 11 | 10 | 16 | 22.7 | 0 | 4.7
7552 | TORONTO BUTTONVILLE A | 11 | 11 | 16 | 1.55 | 16.45 | 0
7553 | TORONTO BUTTONVILLE A | 11 | 10 | 17 | 21.4 | 0 | 3.4
7553 | TORONTO BUTTONVILLE A | 11 | 11 | 17 | 1.375 | 16.625 | 0
7554 | TORONTO BUTTONVILLE A | 11 | 10 | 18 | 19.9 | 0 | 1.9
7554 | TORONTO BUTTONVILLE A | 11 | 11 | 18 | 1.2 | 16.8 | 0
7555 | TORONTO BUTTONVILLE A | 11 | 10 | 19 | 19 | 0 | 1
7555 | TORONTO BUTTONVILLE A | 11 | 11 | 19 | 1.1 | 16.9 | 0
7556 | TORONTO BUTTONVILLE A | 11 | 10 | 20 | 18.2 | 0 | 0.2
7556 | TORONTO BUTTONVILLE A | 11 | 11 | 20 | 1.375 | 16.625 | 0
7557 | TORONTO BUTTONVILLE A | 11 | 10 | 21 | 17.9 | 0.1 | 0
7557 | TORONTO BUTTONVILLE A | 11 | 11 | 21 | 1.6 | 16.4 | 0
7558 | TORONTO BUTTONVILLE A | 11 | 10 | 22 | 16.9 | 1.1 | 0
7558 | TORONTO BUTTONVILLE A | 11 | 11 | 22 | 1.475 | 16.525 | 0
7559 | TORONTO BUTTONVILLE A | 11 | 10 | 23 | 15 | 3 | 0
7559 | TORONTO BUTTONVILLE A | 11 | 11 | 23 | 1.15 | 16.85 | 0
7560 | TORONTO BUTTONVILLE A | 11 | 10 | 24 | 13.7 | 4.3 | 0
7560 | TORONTO BUTTONVILLE A | 11 | 11 | 24 | 1.325 | 16.675 | 0
7561 | TORONTO BUTTONVILLE A | 11 | 11 | 1 | 13.6 | 4.4 | 0
7561 | TORONTO BUTTONVILLE A | 11 | 12 | 1 | 1.375 | 16.625 | 0
7562 | TORONTO BUTTONVILLE A | 11 | 11 | 2 | 15.8 | 2.2 | 0
7562 | TORONTO BUTTONVILLE A | 11 | 12 | 2 | 0.875 | 17.125 | 0
7563 | TORONTO BUTTONVILLE A | 11 | 11 | 3 | 15.7 | 2.3 | 0
7563 | TORONTO BUTTONVILLE A | 11 | 12 | 3 | 0.875 | 17.125 | 0
7564 | TORONTO BUTTONVILLE A | 11 | 11 | 4 | 14.1 | 3.9 | 0
7564 | TORONTO BUTTONVILLE A | 11 | 12 | 4 | 0.9 | 17.1 | 0
7565 | TORONTO BUTTONVILLE A | 11 | 11 | 5 | 16.7 | 1.3 | 0
7565 | TORONTO BUTTONVILLE A | 11 | 12 | 5 | 0.8 | 17.2 | 0
7566 | TORONTO BUTTONVILLE A | 11 | 11 | 6 | 17.6 | 0.4 | 0
7566 | TORONTO BUTTONVILLE A | 11 | 12 | 6 | 0.675 | 17.325 | 0
7567 | TORONTO BUTTONVILLE A | 11 | 11 | 7 | 16.3 | 1.7 | 0
7567 | TORONTO BUTTONVILLE A | 11 | 12 | 7 | 0.35 | 17.65 | 0
7568 | TORONTO BUTTONVILLE A | 11 | 11 | 8 | 16.3 | 1.7 | 0
7568 | TORONTO BUTTONVILLE A | 11 | 12 | 8 | 0.1 | 17.9 | 0
7569 | TORONTO BUTTONVILLE A | 11 | 11 | 9 | 16.5 | 1.5 | 0
7569 | TORONTO BUTTONVILLE A | 11 | 12 | 9 | 0.2 | 17.8 | 0
7570 | TORONTO BUTTONVILLE A | 11 | 11 | 10 | 16.4 | 1.6 | 0
7570 | TORONTO BUTTONVILLE A | 11 | 12 | 10 | 0.9 | 17.1 | 0
7571 | TORONTO BUTTONVILLE A | 11 | 11 | 11 | 17.8 | 0.2 | 0
7571 | TORONTO BUTTONVILLE A | 11 | 12 | 11 | 1.8 | 16.2 | 0
7572 | TORONTO BUTTONVILLE A | 11 | 11 | 12 | 17.1 | 0.9 | 0
7572 | TORONTO BUTTONVILLE A | 11 | 12 | 12 | 2.975 | 15.025 | 0
7573 | TORONTO BUTTONVILLE A | 11 | 11 | 13 | 17.3 | 0.7 | 0
7573 | TORONTO BUTTONVILLE A | 11 | 12 | 13 | 3.65 | 14.35 | 0
7574 | TORONTO BUTTONVILLE A | 11 | 11 | 14 | 16.4 | 1.6 | 0
7574 | TORONTO BUTTONVILLE A | 11 | 12 | 14 | 3.825 | 14.175 | 0
7575 | TORONTO BUTTONVILLE A | 11 | 11 | 15 | 15.3 | 2.7 | 0
7575 | TORONTO BUTTONVILLE A | 11 | 12 | 15 | 3.825 | 14.175 | 0
7576 | TORONTO BUTTONVILLE A | 11 | 11 | 16 | 13.1 | 4.9 | 0
7576 | TORONTO BUTTONVILLE A | 11 | 12 | 16 | 3.6 | 14.4 | 0
7577 | TORONTO BUTTONVILLE A | 11 | 11 | 17 | 10.5 | 7.5 | 0
7577 | TORONTO BUTTONVILLE A | 11 | 12 | 17 | 3.225 | 14.775 | 0
7578 | TORONTO BUTTONVILLE A | 11 | 11 | 18 | 8.1 | 9.9 | 0
7578 | TORONTO BUTTONVILLE A | 11 | 12 | 18 | 2.725 | 15.275 | 0
7579 | TORONTO BUTTONVILLE A | 11 | 11 | 19 | 6.5 | 11.5 | 0
7579 | TORONTO BUTTONVILLE A | 11 | 12 | 19 | 1.85 | 16.15 | 0
7580 | TORONTO BUTTONVILLE A | 11 | 11 | 20 | 5.8 | 12.2 | 0
7580 | TORONTO BUTTONVILLE A | 11 | 12 | 20 | 1.6 | 16.4 | 0
7581 | TORONTO BUTTONVILLE A | 11 | 11 | 21 | 5.9 | 12.1 | 0
7581 | TORONTO BUTTONVILLE A | 11 | 12 | 21 | 1.45 | 16.55 | 0
7582 | TORONTO BUTTONVILLE A | 11 | 11 | 22 | 6 | 12 | 0
7582 | TORONTO BUTTONVILLE A | 11 | 12 | 22 | 1.25 | 16.75 | 0
7583 | TORONTO BUTTONVILLE A | 11 | 11 | 23 | 5.8 | 12.2 | 0
7583 | TORONTO BUTTONVILLE A | 11 | 12 | 23 | 1.075 | 16.925 | 0
7584 | TORONTO BUTTONVILLE A | 11 | 11 | 24 | 5.8 | 12.2 | 0
7584 | TORONTO BUTTONVILLE A | 11 | 12 | 24 | 0.8 | 17.2 | 0
7585 | TORONTO BUTTONVILLE A | 11 | 12 | 1 | 5.3 | 12.7 | 0
7585 | TORONTO BUTTONVILLE A | 11 | 13 | 1 | -0.425 | 18.425 | 0
7586 | TORONTO BUTTONVILLE A | 11 | 12 | 2 | 5.3 | 12.7 | 0
7586 | TORONTO BUTTONVILLE A | 11 | 13 | 2 | -1.075 | 19.075 | 0
7587 | TORONTO BUTTONVILLE A | 11 | 12 | 3 | 4.9 | 13.1 | 0
7587 | TORONTO BUTTONVILLE A | 11 | 13 | 3 | -1.7 | 19.7 | 0
7588 | TORONTO BUTTONVILLE A | 11 | 12 | 4 | 4.9 | 13.1 | 0
7588 | TORONTO BUTTONVILLE A | 11 | 13 | 4 | -1.875 | 19.875 | 0
7589 | TORONTO BUTTONVILLE A | 11 | 12 | 5 | 5 | 13 | 0
7589 | TORONTO BUTTONVILLE A | 11 | 13 | 5 | -2.225 | 20.225 | 0
7590 | TORONTO BUTTONVILLE A | 11 | 12 | 6 | 5 | 13 | 0
7590 | TORONTO BUTTONVILLE A | 11 | 13 | 6 | -2.175 | 20.175 | 0
7591 | TORONTO BUTTONVILLE A | 11 | 12 | 7 | 4.5 | 13.5 | 0
7591 | TORONTO BUTTONVILLE A | 11 | 13 | 7 | -1.925 | 19.925 | 0
7592 | TORONTO BUTTONVILLE A | 11 | 12 | 8 | 4.5 | 13.5 | 0
7592 | TORONTO BUTTONVILLE A | 11 | 13 | 8 | -1.975 | 19.975 | 0
7593 | TORONTO BUTTONVILLE A | 11 | 12 | 9 | 4.5 | 13.5 | 0
7593 | TORONTO BUTTONVILLE A | 11 | 13 | 9 | -1.825 | 19.825 | 0
7594 | TORONTO BUTTONVILLE A | 11 | 12 | 10 | 5.6 | 12.4 | 0
7594 | TORONTO BUTTONVILLE A | 11 | 13 | 10 | -1.4 | 19.4 | 0
7595 | TORONTO BUTTONVILLE A | 11 | 12 | 11 | 6.1 | 11.9 | 0
7595 | TORONTO BUTTONVILLE A | 11 | 13 | 11 | -0.775 | 18.775 | 0
7596 | TORONTO BUTTONVILLE A | 11 | 12 | 12 | 7 | 11 | 0
7596 | TORONTO BUTTONVILLE A | 11 | 13 | 12 | 0.025 | 17.975 | 0
7597 | TORONTO BUTTONVILLE A | 11 | 12 | 13 | 8.1 | 9.9 | 0
7597 | TORONTO BUTTONVILLE A | 11 | 13 | 13 | 0.675 | 17.325 | 0
7598 | TORONTO BUTTONVILLE A | 11 | 12 | 14 | 8.5 | 9.5 | 0
7598 | TORONTO BUTTONVILLE A | 11 | 13 | 14 | 0.925 | 17.075 | 0
7599 | TORONTO BUTTONVILLE A | 11 | 12 | 15 | 10 | 8 | 0
7599 | TORONTO BUTTONVILLE A | 11 | 13 | 15 | 1.225 | 16.775 | 0
7600 | TORONTO BUTTONVILLE A | 11 | 12 | 16 | 9.8 | 8.2 | 0
7600 | TORONTO BUTTONVILLE A | 11 | 13 | 16 | 1.35 | 16.65 | 0
7601 | TORONTO BUTTONVILLE A | 11 | 12 | 17 | 8 | 10 | 0
7601 | TORONTO BUTTONVILLE A | 11 | 13 | 17 | 1.2 | 16.8 | 0
7602 | TORONTO BUTTONVILLE A | 11 | 12 | 18 | 6.6 | 11.4 | 0
7602 | TORONTO BUTTONVILLE A | 11 | 13 | 18 | 0.95 | 17.05 | 0
7603 | TORONTO BUTTONVILLE A | 11 | 12 | 19 | 5.7 | 12.3 | 0
7603 | TORONTO BUTTONVILLE A | 11 | 13 | 19 | 0.625 | 17.375 | 0
7604 | TORONTO BUTTONVILLE A | 11 | 12 | 20 | 4.6 | 13.4 | 0
7604 | TORONTO BUTTONVILLE A | 11 | 13 | 20 | 0.65 | 17.35 | 0
7605 | TORONTO BUTTONVILLE A | 11 | 12 | 21 | 3.2 | 14.8 | 0
7605 | TORONTO BUTTONVILLE A | 11 | 13 | 21 | 0.5 | 17.5 | 0
7606 | TORONTO BUTTONVILLE A | 11 | 12 | 22 | 1.8 | 16.2 | 0
7606 | TORONTO BUTTONVILLE A | 11 | 13 | 22 | 0.275 | 17.725 | 0
7607 | TORONTO BUTTONVILLE A | 11 | 12 | 23 | 2 | 16 | 0
7607 | TORONTO BUTTONVILLE A | 11 | 13 | 23 | 0.05 | 17.95 | 0
7608 | TORONTO BUTTONVILLE A | 11 | 12 | 24 | 1.1 | 16.9 | 0
7608 | TORONTO BUTTONVILLE A | 11 | 13 | 24 | 0.1 | 17.9 | 0
7609 | TORONTO BUTTONVILLE A | 11 | 13 | 1 | 1.3 | 16.7 | 0
7609 | TORONTO BUTTONVILLE A | 11 | 14 | 1 | 0.125 | 17.875 | 0
7610 | TORONTO BUTTONVILLE A | 11 | 13 | 2 | 1.7 | 16.3 | 0
7610 | TORONTO BUTTONVILLE A | 11 | 14 | 2 | -0.1 | 18.1 | 0
7611 | TORONTO BUTTONVILLE A | 11 | 13 | 3 | 2.1 | 15.9 | 0
7611 | TORONTO BUTTONVILLE A | 11 | 14 | 3 | -0.125 | 18.125 | 0
7612 | TORONTO BUTTONVILLE A | 11 | 13 | 4 | 2.1 | 15.9 | 0
7612 | TORONTO BUTTONVILLE A | 11 | 14 | 4 | -0.375 | 18.375 | 0
7613 | TORONTO BUTTONVILLE A | 11 | 13 | 5 | 2.6 | 15.4 | 0
7613 | TORONTO BUTTONVILLE A | 11 | 14 | 5 | -0.525 | 18.525 | 0
7614 | TORONTO BUTTONVILLE A | 11 | 13 | 6 | 2.2 | 15.8 | 0
7614 | TORONTO BUTTONVILLE A | 11 | 14 | 6 | -0.525 | 18.525 | 0
7615 | TORONTO BUTTONVILLE A | 11 | 13 | 7 | 2.3 | 15.7 | 0
7615 | TORONTO BUTTONVILLE A | 11 | 14 | 7 | -0.525 | 18.525 | 0
7616 | TORONTO BUTTONVILLE A | 11 | 13 | 8 | 1.4 | 16.6 | 0
7616 | TORONTO BUTTONVILLE A | 11 | 14 | 8 | -0.6 | 18.6 | 0
7617 | TORONTO BUTTONVILLE A | 11 | 13 | 9 | 2.7 | 15.3 | 0
7617 | TORONTO BUTTONVILLE A | 11 | 14 | 9 | -0.575 | 18.575 | 0
7618 | TORONTO BUTTONVILLE A | 11 | 13 | 10 | 3.5 | 14.5 | 0
7618 | TORONTO BUTTONVILLE A | 11 | 14 | 10 | -0.3 | 18.3 | 0
7619 | TORONTO BUTTONVILLE A | 11 | 13 | 11 | 5.2 | 12.8 | 0
7619 | TORONTO BUTTONVILLE A | 11 | 14 | 11 | 0.125 | 17.875 | 0
7620 | TORONTO BUTTONVILLE A | 11 | 13 | 12 | 6.4 | 11.6 | 0
7620 | TORONTO BUTTONVILLE A | 11 | 14 | 12 | 0.475 | 17.525 | 0
7621 | TORONTO BUTTONVILLE A | 11 | 13 | 13 | 7.1 | 10.9 | 0
7621 | TORONTO BUTTONVILLE A | 11 | 14 | 13 | 1.025 | 16.975 | 0
7622 | TORONTO BUTTONVILLE A | 11 | 13 | 14 | 7.1 | 10.9 | 0
7622 | TORONTO BUTTONVILLE A | 11 | 14 | 14 | 1.6 | 16.4 | 0
7623 | TORONTO BUTTONVILLE A | 11 | 13 | 15 | 8.1 | 9.9 | 0
7623 | TORONTO BUTTONVILLE A | 11 | 14 | 15 | 2.125 | 15.875 | 0
7624 | TORONTO BUTTONVILLE A | 11 | 13 | 16 | 8.1 | 9.9 | 0
7624 | TORONTO BUTTONVILLE A | 11 | 14 | 16 | 1.625 | 16.375 | 0
7625 | TORONTO BUTTONVILLE A | 11 | 13 | 17 | 7.9 | 10.1 | 0
7625 | TORONTO BUTTONVILLE A | 11 | 14 | 17 | 1.025 | 16.975 | 0
7626 | TORONTO BUTTONVILLE A | 11 | 13 | 18 | 7.4 | 10.6 | 0
7626 | TORONTO BUTTONVILLE A | 11 | 14 | 18 | 0.35 | 17.65 | 0
7627 | TORONTO BUTTONVILLE A | 11 | 13 | 19 | 6.3 | 11.7 | 0
7627 | TORONTO BUTTONVILLE A | 11 | 14 | 19 | -0.325 | 18.325 | 0
7628 | TORONTO BUTTONVILLE A | 11 | 13 | 20 | 5.4 | 12.6 | 0
7628 | TORONTO BUTTONVILLE A | 11 | 14 | 20 | -0.775 | 18.775 | 0
7629 | TORONTO BUTTONVILLE A | 11 | 13 | 21 | 4.8 | 13.2 | 0
7629 | TORONTO BUTTONVILLE A | 11 | 14 | 21 | -1.075 | 19.075 | 0
7630 | TORONTO BUTTONVILLE A | 11 | 13 | 22 | 4.8 | 13.2 | 0
7630 | TORONTO BUTTONVILLE A | 11 | 14 | 22 | -1.225 | 19.225 | 0
7631 | TORONTO BUTTONVILLE A | 11 | 13 | 23 | 4.7 | 13.3 | 0
7631 | TORONTO BUTTONVILLE A | 11 | 14 | 23 | -1.45 | 19.45 | 0
7632 | TORONTO BUTTONVILLE A | 11 | 13 | 24 | 4.5 | 13.5 | 0
7632 | TORONTO BUTTONVILLE A | 11 | 14 | 24 | -1.65 | 19.65 | 0
7633 | TORONTO BUTTONVILLE A | 11 | 14 | 1 | 4.2 | 13.8 | 0
7633 | TORONTO BUTTONVILLE A | 11 | 15 | 1 | -1.8 | 19.8 | 0
7634 | TORONTO BUTTONVILLE A | 11 | 14 | 2 | 3.9 | 14.1 | 0
7634 | TORONTO BUTTONVILLE A | 11 | 15 | 2 | -1.85 | 19.85 | 0
7635 | TORONTO BUTTONVILLE A | 11 | 14 | 3 | 3.6 | 14.4 | 0
7635 | TORONTO BUTTONVILLE A | 11 | 15 | 3 | -1.9 | 19.9 | 0
7636 | TORONTO BUTTONVILLE A | 11 | 14 | 4 | 3.2 | 14.8 | 0
7636 | TORONTO BUTTONVILLE A | 11 | 15 | 4 | -1.3 | 19.3 | 0
7637 | TORONTO BUTTONVILLE A | 11 | 14 | 5 | 3 | 15 | 0
7637 | TORONTO BUTTONVILLE A | 11 | 15 | 5 | -0.85 | 18.85 | 0
7638 | TORONTO BUTTONVILLE A | 11 | 14 | 6 | 2.9 | 15.1 | 0
7638 | TORONTO BUTTONVILLE A | 11 | 15 | 6 | -0.85 | 18.85 | 0
7639 | TORONTO BUTTONVILLE A | 11 | 14 | 7 | 2.7 | 15.3 | 0
7639 | TORONTO BUTTONVILLE A | 11 | 15 | 7 | -0.7 | 18.7 | 0
7640 | TORONTO BUTTONVILLE A | 11 | 14 | 8 | 2.7 | 15.3 | 0
7640 | TORONTO BUTTONVILLE A | 11 | 15 | 8 | -0.525 | 18.525 | 0
7641 | TORONTO BUTTONVILLE A | 11 | 14 | 9 | 2.5 | 15.5 | 0
7641 | TORONTO BUTTONVILLE A | 11 | 15 | 9 | -6.9389e-17 | 18 | 0
7642 | TORONTO BUTTONVILLE A | 11 | 14 | 10 | 3.8 | 14.2 | 0
7642 | TORONTO BUTTONVILLE A | 11 | 15 | 10 | 1 | 17 | 0
7643 | TORONTO BUTTONVILLE A | 11 | 14 | 11 | 5.4 | 12.6 | 0
7643 | TORONTO BUTTONVILLE A | 11 | 15 | 11 | 1.625 | 16.375 | 0
7644 | TORONTO BUTTONVILLE A | 11 | 14 | 12 | 5.3 | 12.7 | 0
7644 | TORONTO BUTTONVILLE A | 11 | 15 | 12 | 2.275 | 15.725 | 0
7645 | TORONTO BUTTONVILLE A | 11 | 14 | 13 | 6.1 | 11.9 | 0
7645 | TORONTO BUTTONVILLE A | 11 | 15 | 13 | 2.5 | 15.5 | 0
7646 | TORONTO BUTTONVILLE A | 11 | 14 | 14 | 6.9 | 11.1 | 0
7646 | TORONTO BUTTONVILLE A | 11 | 15 | 14 | 2.4 | 15.6 | 0
7647 | TORONTO BUTTONVILLE A | 11 | 14 | 15 | 7.5 | 10.5 | 0
7647 | TORONTO BUTTONVILLE A | 11 | 15 | 15 | 2.625 | 15.375 | 0
7648 | TORONTO BUTTONVILLE A | 11 | 14 | 16 | 7.2 | 10.8 | 0
7648 | TORONTO BUTTONVILLE A | 11 | 15 | 16 | 3 | 15 | 0
7649 | TORONTO BUTTONVILLE A | 11 | 14 | 17 | 6.5 | 11.5 | 0
7649 | TORONTO BUTTONVILLE A | 11 | 15 | 17 | 2.9 | 15.1 | 0
7650 | TORONTO BUTTONVILLE A | 11 | 14 | 18 | 4.8 | 13.2 | 0
7650 | TORONTO BUTTONVILLE A | 11 | 15 | 18 | 2.425 | 15.575 | 0
7651 | TORONTO BUTTONVILLE A | 11 | 14 | 19 | 4 | 14 | 0
7651 | TORONTO BUTTONVILLE A | 11 | 15 | 19 | 2.2 | 15.8 | 0
7652 | TORONTO BUTTONVILLE A | 11 | 14 | 20 | 3.5 | 14.5 | 0
7652 | TORONTO BUTTONVILLE A | 11 | 15 | 20 | 1.925 | 16.075 | 0
7653 | TORONTO BUTTONVILLE A | 11 | 14 | 21 | 3.2 | 14.8 | 0
7653 | TORONTO BUTTONVILLE A | 11 | 15 | 21 | 1.675 | 16.325 | 0
7654 | TORONTO BUTTONVILLE A | 11 | 14 | 22 | 3.1 | 14.9 | 0
7654 | TORONTO BUTTONVILLE A | 11 | 15 | 22 | 1.15 | 16.85 | 0
7655 | TORONTO BUTTONVILLE A | 11 | 14 | 23 | 2.8 | 15.2 | 0
7655 | TORONTO BUTTONVILLE A | 11 | 15 | 23 | 0.575 | 17.425 | 0
7656 | TORONTO BUTTONVILLE A | 11 | 14 | 24 | 2.1 | 15.9 | 0
7656 | TORONTO BUTTONVILLE A | 11 | 15 | 24 | 0.1 | 17.9 | 0
7657 | TORONTO BUTTONVILLE A | 11 | 15 | 1 | 4.3 | 13.7 | 0
7657 | TORONTO BUTTONVILLE A | 11 | 16 | 1 | 0.1 | 17.9 | 0
7658 | TORONTO BUTTONVILLE A | 11 | 15 | 2 | 5 | 13 | 0
7658 | TORONTO BUTTONVILLE A | 11 | 16 | 2 | -0.05 | 18.05 | 0
7659 | TORONTO BUTTONVILLE A | 11 | 15 | 3 | 5.3 | 12.7 | 0
7659 | TORONTO BUTTONVILLE A | 11 | 16 | 3 | -0.375 | 18.375 | 0
7660 | TORONTO BUTTONVILLE A | 11 | 15 | 4 | 5.5 | 12.5 | 0
7660 | TORONTO BUTTONVILLE A | 11 | 16 | 4 | -0.425 | 18.425 | 0
7661 | TORONTO BUTTONVILLE A | 11 | 15 | 5 | 4.2 | 13.8 | 0
7661 | TORONTO BUTTONVILLE A | 11 | 16 | 5 | -0.8 | 18.8 | 0
7662 | TORONTO BUTTONVILLE A | 11 | 15 | 6 | 4.1 | 13.9 | 0
7662 | TORONTO BUTTONVILLE A | 11 | 16 | 6 | -1.15 | 19.15 | 0
7663 | TORONTO BUTTONVILLE A | 11 | 15 | 7 | 4.3 | 13.7 | 0
7663 | TORONTO BUTTONVILLE A | 11 | 16 | 7 | -1.25 | 19.25 | 0
7664 | TORONTO BUTTONVILLE A | 11 | 15 | 8 | 5.3 | 12.7 | 0
7664 | TORONTO BUTTONVILLE A | 11 | 16 | 8 | -1.6 | 19.6 | 0
7665 | TORONTO BUTTONVILLE A | 11 | 15 | 9 | 6.1 | 11.9 | 0
7665 | TORONTO BUTTONVILLE A | 11 | 16 | 9 | -1.225 | 19.225 | 0
7666 | TORONTO BUTTONVILLE A | 11 | 15 | 10 | 6.1 | 11.9 | 0
7666 | TORONTO BUTTONVILLE A | 11 | 16 | 10 | -1.6 | 19.6 | 0
7667 | TORONTO BUTTONVILLE A | 11 | 15 | 11 | 6.2 | 11.8 | 0
7667 | TORONTO BUTTONVILLE A | 11 | 16 | 11 | -0.76667 | 18.7667 | 0
7668 | TORONTO BUTTONVILLE A | 11 | 15 | 12 | 6.4 | 11.6 | 0
7668 | TORONTO BUTTONVILLE A | 11 | 16 | 12 | 0.033333 | 17.9667 | 0
7669 | TORONTO BUTTONVILLE A | 11 | 15 | 13 | 7.3 | 10.7 | 0
7669 | TORONTO BUTTONVILLE A | 11 | 16 | 13 | 0.1 | 17.9 | 0
7670 | TORONTO BUTTONVILLE A | 11 | 15 | 14 | 10.1 | 7.9 | 0
7670 | TORONTO BUTTONVILLE A | 11 | 16 | 14 | 0.23333 | 17.7667 | 0
7671 | TORONTO BUTTONVILLE A | 11 | 15 | 15 | 11 | 7 | 0
7671 | TORONTO BUTTONVILLE A | 11 | 16 | 15 | 0.53333 | 17.4667 | 0
7672 | TORONTO BUTTONVILLE A | 11 | 15 | 16 | 12 | 6 | 0
7672 | TORONTO BUTTONVILLE A | 11 | 16 | 16 | 1.65 | 16.35 | 0
7673 | TORONTO BUTTONVILLE A | 11 | 15 | 17 | 9.9 | 8.1 | 0
7673 | TORONTO BUTTONVILLE A | 11 | 16 | 17 | 1.15 | 16.85 | 0
7674 | TORONTO BUTTONVILLE A | 11 | 15 | 18 | 9.4 | 8.6 | 0
7674 | TORONTO BUTTONVILLE A | 11 | 16 | 18 | 0.45 | 17.55 | 0
7675 | TORONTO BUTTONVILLE A | 11 | 15 | 19 | 7.2 | 10.8 | 0
7675 | TORONTO BUTTONVILLE A | 11 | 16 | 19 | 0.125 | 17.875 | 0
7676 | TORONTO BUTTONVILLE A | 11 | 15 | 20 | 7.4 | 10.6 | 0
7676 | TORONTO BUTTONVILLE A | 11 | 16 | 20 | -0.625 | 18.625 | 0
7677 | TORONTO BUTTONVILLE A | 11 | 15 | 21 | 6.5 | 11.5 | 0
7677 | TORONTO BUTTONVILLE A | 11 | 16 | 21 | -0.725 | 18.725 | 0
7678 | TORONTO BUTTONVILLE A | 11 | 15 | 22 | 5.6 | 12.4 | 0
7678 | TORONTO BUTTONVILLE A | 11 | 16 | 22 | -1.075 | 19.075 | 0
7679 | TORONTO BUTTONVILLE A | 11 | 15 | 23 | 5.4 | 12.6 | 0
7679 | TORONTO BUTTONVILLE A | 11 | 16 | 23 | -1.65 | 19.65 | 0
7680 | TORONTO BUTTONVILLE A | 11 | 15 | 24 | 5.3 | 12.7 | 0
7680 | TORONTO BUTTONVILLE A | 11 | 16 | 24 | -1.55 | 19.55 | 0
7681 | TORONTO BUTTONVILLE A | 11 | 16 | 1 | 4.4 | 13.6 | 0
7681 | TORONTO BUTTONVILLE A | 11 | 17 | 1 | -1.675 | 19.675 | 0
7682 | TORONTO BUTTONVILLE A | 11 | 16 | 2 | 3.8 | 14.2 | 0
7682 | TORONTO BUTTONVILLE A | 11 | 17 | 2 | -1.7 | 19.7 | 0
7683 | TORONTO BUTTONVILLE A | 11 | 16 | 3 | 3.9 | 14.1 | 0
7683 | TORONTO BUTTONVILLE A | 11 | 17 | 3 | -1.325 | 19.325 | 0
7684 | TORONTO BUTTONVILLE A | 11 | 16 | 4 | 3.6 | 14.4 | 0
7684 | TORONTO BUTTONVILLE A | 11 | 17 | 4 | -1.075 | 19.075 | 0
7685 | TORONTO BUTTONVILLE A | 11 | 16 | 5 | 3.3 | 14.7 | 0
7685 | TORONTO BUTTONVILLE A | 11 | 17 | 5 | -1.225 | 19.225 | 0
7686 | TORONTO BUTTONVILLE A | 11 | 16 | 6 | 3.4 | 14.6 | 0
7686 | TORONTO BUTTONVILLE A | 11 | 17 | 6 | -1.575 | 19.575 | 0
7687 | TORONTO BUTTONVILLE A | 11 | 16 | 7 | 3.6 | 14.4 | 0
7687 | TORONTO BUTTONVILLE A | 11 | 17 | 7 | -1.6 | 19.6 | 0
7688 | TORONTO BUTTONVILLE A | 11 | 16 | 8 | 3.5 | 14.5 | 0
7688 | TORONTO BUTTONVILLE A | 11 | 17 | 8 | -1.275 | 19.275 | 0
7689 | TORONTO BUTTONVILLE A | 11 | 16 | 9 | 3.5 | 14.5 | 0
7689 | TORONTO BUTTONVILLE A | 11 | 17 | 9 | -0.625 | 18.625 | 0
7690 | TORONTO BUTTONVILLE A | 11 | 16 | 10 | 3.5 | 14.5 | 0
7690 | TORONTO BUTTONVILLE A | 11 | 17 | 10 | 0.275 | 17.725 | 0
7691 | TORONTO BUTTONVILLE A | 11 | 16 | 11 | 3.8 | 14.2 | 0
7691 | TORONTO BUTTONVILLE A | 11 | 17 | 11 | 0.95 | 17.05 | 0
7692 | TORONTO BUTTONVILLE A | 11 | 16 | 12 | 4.2 | 13.8 | 0
7692 | TORONTO BUTTONVILLE A | 11 | 17 | 12 | 1.8 | 16.2 | 0
7693 | TORONTO BUTTONVILLE A | 11 | 16 | 13 | 3.8 | 14.2 | 0
7693 | TORONTO BUTTONVILLE A | 11 | 17 | 13 | 2.45 | 15.55 | 0
7694 | TORONTO BUTTONVILLE A | 11 | 16 | 14 | 3.6 | 14.4 | 0
7694 | TORONTO BUTTONVILLE A | 11 | 17 | 14 | 2.425 | 15.575 | 0
7695 | TORONTO BUTTONVILLE A | 11 | 16 | 15 | 3.6 | 14.4 | 0
7695 | TORONTO BUTTONVILLE A | 11 | 17 | 15 | 2.675 | 15.325 | 0
7696 | TORONTO BUTTONVILLE A | 11 | 16 | 16 | 3.2 | 14.8 | 0
7696 | TORONTO BUTTONVILLE A | 11 | 17 | 16 | 2.45 | 15.55 | 0
7697 | TORONTO BUTTONVILLE A | 11 | 16 | 17 | 3.2 | 14.8 | 0
7697 | TORONTO BUTTONVILLE A | 11 | 17 | 17 | 2.075 | 15.925 | 0
7698 | TORONTO BUTTONVILLE A | 11 | 16 | 18 | 3.1 | 14.9 | 0
7698 | TORONTO BUTTONVILLE A | 11 | 17 | 18 | 1.675 | 16.325 | 0
7699 | TORONTO BUTTONVILLE A | 11 | 16 | 19 | 3 | 15 | 0
7699 | TORONTO BUTTONVILLE A | 11 | 17 | 19 | 1.525 | 16.475 | 0
7700 | TORONTO BUTTONVILLE A | 11 | 16 | 20 | 2.9 | 15.1 | 0
7700 | TORONTO BUTTONVILLE A | 11 | 17 | 20 | 2.45 | 15.55 | 0
7701 | TORONTO BUTTONVILLE A | 11 | 16 | 21 | 2.8 | 15.2 | 0
7701 | TORONTO BUTTONVILLE A | 11 | 17 | 21 | 2.85 | 15.15 | 0
7702 | TORONTO BUTTONVILLE A | 11 | 16 | 22 | 2.8 | 15.2 | 0
7702 | TORONTO BUTTONVILLE A | 11 | 17 | 22 | 3.175 | 14.825 | 0
7703 | TORONTO BUTTONVILLE A | 11 | 16 | 23 | 2.7 | 15.3 | 0
7703 | TORONTO BUTTONVILLE A | 11 | 17 | 23 | 3.5 | 14.5 | 0
7704 | TORONTO BUTTONVILLE A | 11 | 16 | 24 | 2.6 | 15.4 | 0
7704 | TORONTO BUTTONVILLE A | 11 | 17 | 24 | 3.175 | 14.825 | 0
7705 | TORONTO BUTTONVILLE A | 11 | 17 | 1 | 2.3 | 15.7 | 0
7705 | TORONTO BUTTONVILLE A | 11 | 18 | 1 | 3.4 | 14.6 | 0
7706 | TORONTO BUTTONVILLE A | 11 | 17 | 2 | 2.2 | 15.8 | 0
7706 | TORONTO BUTTONVILLE A | 11 | 18 | 2 | 3.175 | 14.825 | 0
7707 | TORONTO BUTTONVILLE A | 11 | 17 | 3 | 1.7 | 16.3 | 0
7707 | TORONTO BUTTONVILLE A | 11 | 18 | 3 | 2.975 | 15.025 | 0
7708 | TORONTO BUTTONVILLE A | 11 | 17 | 4 | 1.5 | 16.5 | 0
7708 | TORONTO BUTTONVILLE A | 11 | 18 | 4 | 2.4 | 15.6 | 0
7709 | TORONTO BUTTONVILLE A | 11 | 17 | 5 | 1.2 | 16.8 | 0
7709 | TORONTO BUTTONVILLE A | 11 | 18 | 5 | 2.15 | 15.85 | 0
7710 | TORONTO BUTTONVILLE A | 11 | 17 | 6 | 0.9 | 17.1 | 0
7710 | TORONTO BUTTONVILLE A | 11 | 18 | 6 | 2.1 | 15.9 | 0
7711 | TORONTO BUTTONVILLE A | 11 | 17 | 7 | 0.5 | 17.5 | 0
7711 | TORONTO BUTTONVILLE A | 11 | 18 | 7 | 1.975 | 16.025 | 0
7712 | TORONTO BUTTONVILLE A | 11 | 17 | 8 | 1.1 | 16.9 | 0
7712 | TORONTO BUTTONVILLE A | 11 | 18 | 8 | 2.025 | 15.975 | 0
7713 | TORONTO BUTTONVILLE A | 11 | 17 | 9 | 1.3 | 16.7 | 0
7713 | TORONTO BUTTONVILLE A | 11 | 18 | 9 | 2.05 | 15.95 | 0
7714 | TORONTO BUTTONVILLE A | 11 | 17 | 10 | 1.3 | 16.7 | 0
7714 | TORONTO BUTTONVILLE A | 11 | 18 | 10 | 2.3 | 15.7 | 0
7715 | TORONTO BUTTONVILLE A | 11 | 17 | 11 | 2.5 | 15.5 | 0
7715 | TORONTO BUTTONVILLE A | 11 | 18 | 11 | 2.625 | 15.375 | 0
7716 | TORONTO BUTTONVILLE A | 11 | 17 | 12 | 2.1 | 15.9 | 0
7716 | TORONTO BUTTONVILLE A | 11 | 18 | 12 | 2.825 | 15.175 | 0
7717 | TORONTO BUTTONVILLE A | 11 | 17 | 13 | 1.6 | 16.4 | 0
7717 | TORONTO BUTTONVILLE A | 11 | 18 | 13 | 2.975 | 15.025 | 0
7718 | TORONTO BUTTONVILLE A | 11 | 17 | 14 | 0.4 | 17.6 | 0
7718 | TORONTO BUTTONVILLE A | 11 | 18 | 14 | 3.325 | 14.675 | 0
7719 | TORONTO BUTTONVILLE A | 11 | 17 | 15 | 0.8 | 17.2 | 0
7719 | TORONTO BUTTONVILLE A | 11 | 18 | 15 | 3.275 | 14.725 | 0
7720 | TORONTO BUTTONVILLE A | 11 | 17 | 16 | -0.3 | 18.3 | 0
7720 | TORONTO BUTTONVILLE A | 11 | 18 | 16 | 3.175 | 14.825 | 0
7721 | TORONTO BUTTONVILLE A | 11 | 17 | 17 | -0.2 | 18.2 | 0
7721 | TORONTO BUTTONVILLE A | 11 | 18 | 17 | 3.15 | 14.85 | 0
7722 | TORONTO BUTTONVILLE A | 11 | 17 | 18 | -1.1 | 19.1 | 0
7722 | TORONTO BUTTONVILLE A | 11 | 18 | 18 | 3.225 | 14.775 | 0
7723 | TORONTO BUTTONVILLE A | 11 | 17 | 19 | -2.1 | 20.1 | 0
7723 | TORONTO BUTTONVILLE A | 11 | 18 | 19 | 3.35 | 14.65 | 0
7724 | TORONTO BUTTONVILLE A | 11 | 17 | 20 | -1.6 | 19.6 | 0
7724 | TORONTO BUTTONVILLE A | 11 | 18 | 20 | 2.825 | 15.175 | 0
7725 | TORONTO BUTTONVILLE A | 11 | 17 | 21 | -2.5 | 20.5 | 0
7725 | TORONTO BUTTONVILLE A | 11 | 18 | 21 | 3.025 | 14.975 | 0
7726 | TORONTO BUTTONVILLE A | 11 | 17 | 22 | -3.1 | 21.1 | 0
7726 | TORONTO BUTTONVILLE A | 11 | 18 | 22 | 2.875 | 15.125 | 0
7727 | TORONTO BUTTONVILLE A | 11 | 17 | 23 | -4.5 | 22.5 | 0
7727 | TORONTO BUTTONVILLE A | 11 | 18 | 23 | 2.175 | 15.825 | 0
7728 | TORONTO BUTTONVILLE A | 11 | 17 | 24 | -5.7 | 23.7 | 0
7728 | TORONTO BUTTONVILLE A | 11 | 18 | 24 | 1.775 | 16.225 | 0
7729 | TORONTO BUTTONVILLE A | 11 | 18 | 1 | -6.2 | 24.2 | 0
7729 | TORONTO BUTTONVILLE A | 11 | 19 | 1 | 1.15 | 16.85 | 0
7730 | TORONTO BUTTONVILLE A | 11 | 18 | 2 | -6.4 | 24.4 | 0
7730 | TORONTO BUTTONVILLE A | 11 | 19 | 2 | 0.5 | 17.5 | 0
7731 | TORONTO BUTTONVILLE A | 11 | 18 | 3 | -6.4 | 24.4 | 0
7731 | TORONTO BUTTONVILLE A | 11 | 19 | 3 | -0.075 | 18.075 | 0
7732 | TORONTO BUTTONVILLE A | 11 | 18 | 4 | -6.6 | 24.6 | 0
7732 | TORONTO BUTTONVILLE A | 11 | 19 | 4 | -0.075 | 18.075 | 0
7733 | TORONTO BUTTONVILLE A | 11 | 18 | 5 | -6.6 | 24.6 | 0
7733 | TORONTO BUTTONVILLE A | 11 | 19 | 5 | -0.075 | 18.075 | 0
7734 | TORONTO BUTTONVILLE A | 11 | 18 | 6 | -6.4 | 24.4 | 0
7734 | TORONTO BUTTONVILLE A | 11 | 19 | 6 | -0.075 | 18.075 | 0
7735 | TORONTO BUTTONVILLE A | 11 | 18 | 7 | -6 | 24 | 0
7735 | TORONTO BUTTONVILLE A | 11 | 19 | 7 | -0.25 | 18.25 | 0
7736 | TORONTO BUTTONVILLE A | 11 | 18 | 8 | -6.1 | 24.1 | 0
7736 | TORONTO BUTTONVILLE A | 11 | 19 | 8 | -0.3 | 18.3 | 0
7737 | TORONTO BUTTONVILLE A | 11 | 18 | 9 | -5.7 | 23.7 | 0
7737 | TORONTO BUTTONVILLE A | 11 | 19 | 9 | 0.025 | 17.975 | 0
7738 | TORONTO BUTTONVILLE A | 11 | 18 | 10 | -5.3 | 23.3 | 0
7738 | TORONTO BUTTONVILLE A | 11 | 19 | 10 | 0.975 | 17.025 | 0
7739 | TORONTO BUTTONVILLE A | 11 | 18 | 11 | -4.7 | 22.7 | 0
7739 | TORONTO BUTTONVILLE A | 11 | 19 | 11 | 2.15 | 15.85 | 0
7740 | TORONTO BUTTONVILLE A | 11 | 18 | 12 | -3.9 | 21.9 | 0
7740 | TORONTO BUTTONVILLE A | 11 | 19 | 12 | 2.9 | 15.1 | 0
7741 | TORONTO BUTTONVILLE A | 11 | 18 | 13 | -2.7 | 20.7 | 0
7741 | TORONTO BUTTONVILLE A | 11 | 19 | 13 | 3 | 15 | 0
7742 | TORONTO BUTTONVILLE A | 11 | 18 | 14 | -1.6 | 19.6 | 0
7742 | TORONTO BUTTONVILLE A | 11 | 19 | 14 | 3.125 | 14.875 | 0
7743 | TORONTO BUTTONVILLE A | 11 | 18 | 15 | -1 | 19 | 0
7743 | TORONTO BUTTONVILLE A | 11 | 19 | 15 | 3.325 | 14.675 | 0
7744 | TORONTO BUTTONVILLE A | 11 | 18 | 16 | -0.6 | 18.6 | 0
7744 | TORONTO BUTTONVILLE A | 11 | 19 | 16 | 3.325 | 14.675 | 0
7745 | TORONTO BUTTONVILLE A | 11 | 18 | 17 | -0.2 | 18.2 | 0
7745 | TORONTO BUTTONVILLE A | 11 | 19 | 17 | 2.75 | 15.25 | 0
7746 | TORONTO BUTTONVILLE A | 11 | 18 | 18 | -0.6 | 18.6 | 0
7746 | TORONTO BUTTONVILLE A | 11 | 19 | 18 | 2 | 16 | 0
7747 | TORONTO BUTTONVILLE A | 11 | 18 | 19 | -1.2 | 19.2 | 0
7747 | TORONTO BUTTONVILLE A | 11 | 19 | 19 | 1.725 | 16.275 | 0
7748 | TORONTO BUTTONVILLE A | 11 | 18 | 20 | -1.3 | 19.3 | 0
7748 | TORONTO BUTTONVILLE A | 11 | 19 | 20 | 1.175 | 16.825 | 0
7749 | TORONTO BUTTONVILLE A | 11 | 18 | 21 | -2.5 | 20.5 | 0
7749 | TORONTO BUTTONVILLE A | 11 | 19 | 21 | 1.1 | 16.9 | 0
7750 | TORONTO BUTTONVILLE A | 11 | 18 | 22 | -1.9 | 19.9 | 0
7750 | TORONTO BUTTONVILLE A | 11 | 19 | 22 | 0.85 | 17.15 | 0
7751 | TORONTO BUTTONVILLE A | 11 | 18 | 23 | -1.7 | 19.7 | 0
7751 | TORONTO BUTTONVILLE A | 11 | 19 | 23 | 0.95 | 17.05 | 0
7752 | TORONTO BUTTONVILLE A | 11 | 18 | 24 | -2.4 | 20.4 | 0
7752 | TORONTO BUTTONVILLE A | 11 | 19 | 24 | 0.875 | 17.125 | 0
7753 | TORONTO BUTTONVILLE A | 11 | 19 | 1 | -1.3 | 19.3 | 0
7753 | TORONTO BUTTONVILLE A | 11 | 20 | 1 | 0.65 | 17.35 | 0
7754 | TORONTO BUTTONVILLE A | 11 | 19 | 2 | 0.6 | 17.4 | 0
7754 | TORONTO BUTTONVILLE A | 11 | 20 | 2 | 0.65 | 17.35 | 0
7755 | TORONTO BUTTONVILLE A | 11 | 19 | 3 | 1.3 | 16.7 | 0
7755 | TORONTO BUTTONVILLE A | 11 | 20 | 3 | 0.35 | 17.65 | 0
7756 | TORONTO BUTTONVILLE A | 11 | 19 | 4 | 2.3 | 15.7 | 0
7756 | TORONTO BUTTONVILLE A | 11 | 20 | 4 | -0.1 | 18.1 | 0
7757 | TORONTO BUTTONVILLE A | 11 | 19 | 5 | 2.2 | 15.8 | 0
7757 | TORONTO BUTTONVILLE A | 11 | 20 | 5 | -0.4 | 18.4 | 0
7758 | TORONTO BUTTONVILLE A | 11 | 19 | 6 | 4.3 | 13.7 | 0
7758 | TORONTO BUTTONVILLE A | 11 | 20 | 6 | -0.125 | 18.125 | 0
7759 | TORONTO BUTTONVILLE A | 11 | 19 | 7 | 4.5 | 13.5 | 0
7759 | TORONTO BUTTONVILLE A | 11 | 20 | 7 | -0.05 | 18.05 | 0
7760 | TORONTO BUTTONVILLE A | 11 | 19 | 8 | 4.9 | 13.1 | 0
7760 | TORONTO BUTTONVILLE A | 11 | 20 | 8 | 0.05 | 17.95 | 0
7761 | TORONTO BUTTONVILLE A | 11 | 19 | 9 | 5.5 | 12.5 | 0
7761 | TORONTO BUTTONVILLE A | 11 | 20 | 9 | 0.575 | 17.425 | 0
7762 | TORONTO BUTTONVILLE A | 11 | 19 | 10 | 6.2 | 11.8 | 0
7762 | TORONTO BUTTONVILLE A | 11 | 20 | 10 | 1.25 | 16.75 | 0
7763 | TORONTO BUTTONVILLE A | 11 | 19 | 11 | 7.3 | 10.7 | 0
7763 | TORONTO BUTTONVILLE A | 11 | 20 | 11 | 1.75 | 16.25 | 0
7764 | TORONTO BUTTONVILLE A | 11 | 19 | 12 | 8.9 | 9.1 | 0
7764 | TORONTO BUTTONVILLE A | 11 | 20 | 12 | 2.875 | 15.125 | 0
7765 | TORONTO BUTTONVILLE A | 11 | 19 | 13 | 10 | 8 | 0
7765 | TORONTO BUTTONVILLE A | 11 | 20 | 13 | 2.925 | 15.075 | 0
7766 | TORONTO BUTTONVILLE A | 11 | 19 | 14 | 11.9 | 6.1 | 0
7766 | TORONTO BUTTONVILLE A | 11 | 20 | 14 | 3.1 | 14.9 | 0
7767 | TORONTO BUTTONVILLE A | 11 | 19 | 15 | 12.8 | 5.2 | 0
7767 | TORONTO BUTTONVILLE A | 11 | 20 | 15 | 3.325 | 14.675 | 0
7768 | TORONTO BUTTONVILLE A | 11 | 19 | 16 | 13.2 | 4.8 | 0
7768 | TORONTO BUTTONVILLE A | 11 | 20 | 16 | 3.075 | 14.925 | 0
7769 | TORONTO BUTTONVILLE A | 11 | 19 | 17 | 13 | 5 | 0
7769 | TORONTO BUTTONVILLE A | 11 | 20 | 17 | 2.95 | 15.05 | 0
7770 | TORONTO BUTTONVILLE A | 11 | 19 | 18 | 12.8 | 5.2 | 0
7770 | TORONTO BUTTONVILLE A | 11 | 20 | 18 | 2.4 | 15.6 | 0
7771 | TORONTO BUTTONVILLE A | 11 | 19 | 19 | 13.9 | 4.1 | 0
7771 | TORONTO BUTTONVILLE A | 11 | 20 | 19 | 2.225 | 15.775 | 0
7772 | TORONTO BUTTONVILLE A | 11 | 19 | 20 | 13.9 | 4.1 | 0
7772 | TORONTO BUTTONVILLE A | 11 | 20 | 20 | 2.525 | 15.475 | 0
7773 | TORONTO BUTTONVILLE A | 11 | 19 | 21 | 14.1 | 3.9 | 0
7773 | TORONTO BUTTONVILLE A | 11 | 20 | 21 | 2.15 | 15.85 | 0
7774 | TORONTO BUTTONVILLE A | 11 | 19 | 22 | 14.6 | 3.4 | 0
7774 | TORONTO BUTTONVILLE A | 11 | 20 | 22 | 1.85 | 16.15 | 0
7775 | TORONTO BUTTONVILLE A | 11 | 19 | 23 | 14.1 | 3.9 | 0
7775 | TORONTO BUTTONVILLE A | 11 | 20 | 23 | 1.375 | 16.625 | 0
7776 | TORONTO BUTTONVILLE A | 11 | 19 | 24 | 14 | 4 | 0
7776 | TORONTO BUTTONVILLE A | 11 | 20 | 24 | 1.775 | 16.225 | 0
7777 | TORONTO BUTTONVILLE A | 11 | 20 | 1 | 13.5 | 4.5 | 0
7777 | TORONTO BUTTONVILLE A | 11 | 21 | 1 | 1.15 | 16.85 | 0
7778 | TORONTO BUTTONVILLE A | 11 | 20 | 2 | 13.6 | 4.4 | 0
7778 | TORONTO BUTTONVILLE A | 11 | 21 | 2 | 1.15 | 16.85 | 0
7779 | TORONTO BUTTONVILLE A | 11 | 20 | 3 | 13.1 | 4.9 | 0
7779 | TORONTO BUTTONVILLE A | 11 | 21 | 3 | 0.975 | 17.025 | 0
7780 | TORONTO BUTTONVILLE A | 11 | 20 | 4 | 12.6 | 5.4 | 0
7780 | TORONTO BUTTONVILLE A | 11 | 21 | 4 | 0.75 | 17.25 | 0
7781 | TORONTO BUTTONVILLE A | 11 | 20 | 5 | 12.6 | 5.4 | 0
7781 | TORONTO BUTTONVILLE A | 11 | 21 | 5 | 0.4 | 17.6 | 0
7782 | TORONTO BUTTONVILLE A | 11 | 20 | 6 | 12.8 | 5.2 | 0
7782 | TORONTO BUTTONVILLE A | 11 | 21 | 6 | 0.25 | 17.75 | 0
7783 | TORONTO BUTTONVILLE A | 11 | 20 | 7 | 12.8 | 5.2 | 0
7783 | TORONTO BUTTONVILLE A | 11 | 21 | 7 | 0.8 | 17.2 | 0
7784 | TORONTO BUTTONVILLE A | 11 | 20 | 8 | 12.5 | 5.5 | 0
7784 | TORONTO BUTTONVILLE A | 11 | 21 | 8 | 0.575 | 17.425 | 0
7785 | TORONTO BUTTONVILLE A | 11 | 20 | 9 | 12.4 | 5.6 | 0
7785 | TORONTO BUTTONVILLE A | 11 | 21 | 9 | 0.925 | 17.075 | 0
7786 | TORONTO BUTTONVILLE A | 11 | 20 | 10 | 12.9 | 5.1 | 0
7786 | TORONTO BUTTONVILLE A | 11 | 21 | 10 | 1.575 | 16.425 | 0
7787 | TORONTO BUTTONVILLE A | 11 | 20 | 11 | 13.9 | 4.1 | 0
7787 | TORONTO BUTTONVILLE A | 11 | 21 | 11 | 3.4 | 14.6 | 0
7788 | TORONTO BUTTONVILLE A | 11 | 20 | 12 | 15 | 3 | 0
7788 | TORONTO BUTTONVILLE A | 11 | 21 | 12 | 3.975 | 14.025 | 0
7789 | TORONTO BUTTONVILLE A | 11 | 20 | 13 | 16.2 | 1.8 | 0
7789 | TORONTO BUTTONVILLE A | 11 | 21 | 13 | 4.25 | 13.75 | 0
7790 | TORONTO BUTTONVILLE A | 11 | 20 | 14 | 16.8 | 1.2 | 0
7790 | TORONTO BUTTONVILLE A | 11 | 21 | 14 | 4.325 | 13.675 | 0
7791 | TORONTO BUTTONVILLE A | 11 | 20 | 15 | 17.1 | 0.9 | 0
7791 | TORONTO BUTTONVILLE A | 11 | 21 | 15 | 4.1 | 13.9 | 0
7792 | TORONTO BUTTONVILLE A | 11 | 20 | 16 | 16.1 | 1.9 | 0
7792 | TORONTO BUTTONVILLE A | 11 | 21 | 16 | 4.1 | 13.9 | 0
7793 | TORONTO BUTTONVILLE A | 11 | 20 | 17 | 15.4 | 2.6 | 0
7793 | TORONTO BUTTONVILLE A | 11 | 21 | 17 | 3.225 | 14.775 | 0
7794 | TORONTO BUTTONVILLE A | 11 | 20 | 18 | 14.5 | 3.5 | 0
7794 | TORONTO BUTTONVILLE A | 11 | 21 | 18 | 2.5 | 15.5 | 0
7795 | TORONTO BUTTONVILLE A | 11 | 20 | 19 | 13.6 | 4.4 | 0
7795 | TORONTO BUTTONVILLE A | 11 | 21 | 19 | 2.1 | 15.9 | 0
7796 | TORONTO BUTTONVILLE A | 11 | 20 | 20 | 12.6 | 5.4 | 0
7796 | TORONTO BUTTONVILLE A | 11 | 21 | 20 | 2.025 | 15.975 | 0
7797 | TORONTO BUTTONVILLE A | 11 | 20 | 21 | 11.5 | 6.5 | 0
7797 | TORONTO BUTTONVILLE A | 11 | 21 | 21 | 1.425 | 16.575 | 0
7798 | TORONTO BUTTONVILLE A | 11 | 20 | 22 | 7.9 | 10.1 | 0
7798 | TORONTO BUTTONVILLE A | 11 | 21 | 22 | 1.1 | 16.9 | 0
7799 | TORONTO BUTTONVILLE A | 11 | 20 | 23 | 7.7 | 10.3 | 0
7799 | TORONTO BUTTONVILLE A | 11 | 21 | 23 | 0.825 | 17.175 | 0
7800 | TORONTO BUTTONVILLE A | 11 | 20 | 24 | 7 | 11 | 0
7800 | TORONTO BUTTONVILLE A | 11 | 21 | 24 | 0.7 | 17.3 | 0
7801 | TORONTO BUTTONVILLE A | 11 | 21 | 1 | 6.3 | 11.7 | 0
7801 | TORONTO BUTTONVILLE A | 11 | 22 | 1 | 0.65 | 17.35 | 0
7802 | TORONTO BUTTONVILLE A | 11 | 21 | 2 | 5.8 | 12.2 | 0
7802 | TORONTO BUTTONVILLE A | 11 | 22 | 2 | 0.175 | 17.825 | 0
7803 | TORONTO BUTTONVILLE A | 11 | 21 | 3 | 5.4 | 12.6 | 0
7803 | TORONTO BUTTONVILLE A | 11 | 22 | 3 | -0.375 | 18.375 | 0
7804 | TORONTO BUTTONVILLE A | 11 | 21 | 4 | 4 | 14 | 0
7804 | TORONTO BUTTONVILLE A | 11 | 22 | 4 | -1.125 | 19.125 | 0
7805 | TORONTO BUTTONVILLE A | 11 | 21 | 5 | 3.5 | 14.5 | 0
7805 | TORONTO BUTTONVILLE A | 11 | 22 | 5 | -2 | 20 | 0
7806 | TORONTO BUTTONVILLE A | 11 | 21 | 6 | 3.5 | 14.5 | 0
7806 | TORONTO BUTTONVILLE A | 11 | 22 | 6 | -2.325 | 20.325 | 0
7807 | TORONTO BUTTONVILLE A | 11 | 21 | 7 | 3.4 | 14.6 | 0
7807 | TORONTO BUTTONVILLE A | 11 | 22 | 7 | -2.625 | 20.625 | 0
7808 | TORONTO BUTTONVILLE A | 11 | 21 | 8 | 3.4 | 14.6 | 0
7808 | TORONTO BUTTONVILLE A | 11 | 22 | 8 | -3.05 | 21.05 | 0
7809 | TORONTO BUTTONVILLE A | 11 | 21 | 9 | 3.5 | 14.5 | 0
7809 | TORONTO BUTTONVILLE A | 11 | 22 | 9 | -2.925 | 20.925 | 0
7810 | TORONTO BUTTONVILLE A | 11 | 21 | 10 | 3.6 | 14.4 | 0
7810 | TORONTO BUTTONVILLE A | 11 | 22 | 10 | -2.55 | 20.55 | 0
7811 | TORONTO BUTTONVILLE A | 11 | 21 | 11 | 4 | 14 | 0
7811 | TORONTO BUTTONVILLE A | 11 | 22 | 11 | -2.15 | 20.15 | 0
7812 | TORONTO BUTTONVILLE A | 11 | 21 | 12 | 4.4 | 13.6 | 0
7812 | TORONTO BUTTONVILLE A | 11 | 22 | 12 | -2.125 | 20.125 | 0
7813 | TORONTO BUTTONVILLE A | 11 | 21 | 13 | 4.2 | 13.8 | 0
7813 | TORONTO BUTTONVILLE A | 11 | 22 | 13 | -2.025 | 20.025 | 0
7814 | TORONTO BUTTONVILLE A | 11 | 21 | 14 | 4.2 | 13.8 | 0
7814 | TORONTO BUTTONVILLE A | 11 | 22 | 14 | -1.75 | 19.75 | 0
7815 | TORONTO BUTTONVILLE A | 11 | 21 | 15 | 4.2 | 13.8 | 0
7815 | TORONTO BUTTONVILLE A | 11 | 22 | 15 | -1.775 | 19.775 | 0
7816 | TORONTO BUTTONVILLE A | 11 | 21 | 16 | 4.2 | 13.8 | 0
7816 | TORONTO BUTTONVILLE A | 11 | 22 | 16 | -1.725 | 19.725 | 0
7817 | TORONTO BUTTONVILLE A | 11 | 21 | 17 | 3.9 | 14.1 | 0
7817 | TORONTO BUTTONVILLE A | 11 | 22 | 17 | -2.1 | 20.1 | 0
7818 | TORONTO BUTTONVILLE A | 11 | 21 | 18 | 3.6 | 14.4 | 0
7818 | TORONTO BUTTONVILLE A | 11 | 22 | 18 | -2.75 | 20.75 | 0
7819 | TORONTO BUTTONVILLE A | 11 | 21 | 19 | 3.4 | 14.6 | 0
7819 | TORONTO BUTTONVILLE A | 11 | 22 | 19 | -3.075 | 21.075 | 0
7820 | TORONTO BUTTONVILLE A | 11 | 21 | 20 | 2.5 | 15.5 | 0
7820 | TORONTO BUTTONVILLE A | 11 | 22 | 20 | -3.525 | 21.525 | 0
7821 | TORONTO BUTTONVILLE A | 11 | 21 | 21 | 2.4 | 15.6 | 0
7821 | TORONTO BUTTONVILLE A | 11 | 22 | 21 | -3.675 | 21.675 | 0
7822 | TORONTO BUTTONVILLE A | 11 | 21 | 22 | 2.4 | 15.6 | 0
7822 | TORONTO BUTTONVILLE A | 11 | 22 | 22 | -4.025 | 22.025 | 0
7823 | TORONTO BUTTONVILLE A | 11 | 21 | 23 | 2.2 | 15.8 | 0
7823 | TORONTO BUTTONVILLE A | 11 | 22 | 23 | -4.325 | 22.325 | 0
7824 | TORONTO BUTTONVILLE A | 11 | 21 | 24 | 2.1 | 15.9 | 0
7824 | TORONTO BUTTONVILLE A | 11 | 22 | 24 | -4.475 | 22.475 | 0
7825 | TORONTO BUTTONVILLE A | 11 | 22 | 1 | 1.3 | 16.7 | 0
7825 | TORONTO BUTTONVILLE A | 11 | 23 | 1 | -4.625 | 22.625 | 0
7826 | TORONTO BUTTONVILLE A | 11 | 22 | 2 | 0.7 | 17.3 | 0
7826 | TORONTO BUTTONVILLE A | 11 | 23 | 2 | -4.4 | 22.4 | 0
7827 | TORONTO BUTTONVILLE A | 11 | 22 | 3 | -1.2 | 19.2 | 0
7827 | TORONTO BUTTONVILLE A | 11 | 23 | 3 | -3.275 | 21.275 | 0
7828 | TORONTO BUTTONVILLE A | 11 | 22 | 4 | -0.7 | 18.7 | 0
7828 | TORONTO BUTTONVILLE A | 11 | 23 | 4 | -3.275 | 21.275 | 0
7829 | TORONTO BUTTONVILLE A | 11 | 22 | 5 | -0.4 | 18.4 | 0
7829 | TORONTO BUTTONVILLE A | 11 | 23 | 5 | -3.05 | 21.05 | 0
7830 | TORONTO BUTTONVILLE A | 11 | 22 | 6 | -0.1 | 18.1 | 0
7830 | TORONTO BUTTONVILLE A | 11 | 23 | 6 | -3.375 | 21.375 | 0
7831 | TORONTO BUTTONVILLE A | 11 | 22 | 7 | 0.1 | 17.9 | 0
7831 | TORONTO BUTTONVILLE A | 11 | 23 | 7 | -3.225 | 21.225 | 0
7832 | TORONTO BUTTONVILLE A | 11 | 22 | 8 | 0.2 | 17.8 | 0
7832 | TORONTO BUTTONVILLE A | 11 | 23 | 8 | -3.175 | 21.175 | 0
7833 | TORONTO BUTTONVILLE A | 11 | 22 | 9 | 0.6 | 17.4 | 0
7833 | TORONTO BUTTONVILLE A | 11 | 23 | 9 | -2.9 | 20.9 | 0
7834 | TORONTO BUTTONVILLE A | 11 | 22 | 10 | 1 | 17 | 0
7834 | TORONTO BUTTONVILLE A | 11 | 23 | 10 | -2 | 20 | 0
7835 | TORONTO BUTTONVILLE A | 11 | 22 | 11 | -0.6 | 18.6 | 0
7835 | TORONTO BUTTONVILLE A | 11 | 23 | 11 | -0.8 | 18.8 | 0
7836 | TORONTO BUTTONVILLE A | 11 | 22 | 12 | -0.8 | 18.8 | 0
7836 | TORONTO BUTTONVILLE A | 11 | 23 | 12 | 0.475 | 17.525 | 0
7837 | TORONTO BUTTONVILLE A | 11 | 22 | 13 | -0.6 | 18.6 | 0
7837 | TORONTO BUTTONVILLE A | 11 | 23 | 13 | 1.525 | 16.475 | 0
7838 | TORONTO BUTTONVILLE A | 11 | 22 | 14 | -0.3 | 18.3 | 0
7838 | TORONTO BUTTONVILLE A | 11 | 23 | 14 | 2.25 | 15.75 | 0
7839 | TORONTO BUTTONVILLE A | 11 | 22 | 15 | 0.1 | 17.9 | 0
7839 | TORONTO BUTTONVILLE A | 11 | 23 | 15 | 2.7 | 15.3 | 0
7840 | TORONTO BUTTONVILLE A | 11 | 22 | 16 | 0.1 | 17.9 | 0
7840 | TORONTO BUTTONVILLE A | 11 | 23 | 16 | 2.875 | 15.125 | 0
7841 | TORONTO BUTTONVILLE A | 11 | 22 | 17 | 0.2 | 17.8 | 0
7841 | TORONTO BUTTONVILLE A | 11 | 23 | 17 | 1.925 | 16.075 | 0
7842 | TORONTO BUTTONVILLE A | 11 | 22 | 18 | 0.2 | 17.8 | 0
7842 | TORONTO BUTTONVILLE A | 11 | 23 | 18 | 1.1 | 16.9 | 0
7843 | TORONTO BUTTONVILLE A | 11 | 22 | 19 | 0.1 | 17.9 | 0
7843 | TORONTO BUTTONVILLE A | 11 | 23 | 19 | 0.675 | 17.325 | 0
7844 | TORONTO BUTTONVILLE A | 11 | 22 | 20 | -0.4 | 18.4 | 0
7844 | TORONTO BUTTONVILLE A | 11 | 23 | 20 | 0.7 | 17.3 | 0
7845 | TORONTO BUTTONVILLE A | 11 | 22 | 21 | -0.5 | 18.5 | 0
7845 | TORONTO BUTTONVILLE A | 11 | 23 | 21 | 0.35 | 17.65 | 0
7846 | TORONTO BUTTONVILLE A | 11 | 22 | 22 | -0.8 | 18.8 | 0
7846 | TORONTO BUTTONVILLE A | 11 | 23 | 22 | -0.125 | 18.125 | 0
7847 | TORONTO BUTTONVILLE A | 11 | 22 | 23 | -0.7 | 18.7 | 0
7847 | TORONTO BUTTONVILLE A | 11 | 23 | 23 | -0.5 | 18.5 | 0
7848 | TORONTO BUTTONVILLE A | 11 | 22 | 24 | -0.8 | 18.8 | 0
7848 | TORONTO BUTTONVILLE A | 11 | 23 | 24 | -0.575 | 18.575 | 0
7849 | TORONTO BUTTONVILLE A | 11 | 23 | 1 | -0.5 | 18.5 | 0
7849 | TORONTO BUTTONVILLE A | 11 | 24 | 1 | -0.825 | 18.825 | 0
7850 | TORONTO BUTTONVILLE A | 11 | 23 | 2 | -0.4 | 18.4 | 0
7850 | TORONTO BUTTONVILLE A | 11 | 24 | 2 | -0.975 | 18.975 | 0
7851 | TORONTO BUTTONVILLE A | 11 | 23 | 3 | -0.7 | 18.7 | 0
7851 | TORONTO BUTTONVILLE A | 11 | 24 | 3 | -1.2 | 19.2 | 0
7852 | TORONTO BUTTONVILLE A | 11 | 23 | 4 | -0.7 | 18.7 | 0
7852 | TORONTO BUTTONVILLE A | 11 | 24 | 4 | -1.5 | 19.5 | 0
7853 | TORONTO BUTTONVILLE A | 11 | 23 | 5 | -0.4 | 18.4 | 0
7853 | TORONTO BUTTONVILLE A | 11 | 24 | 5 | -2 | 20 | 0
7854 | TORONTO BUTTONVILLE A | 11 | 23 | 6 | -0.8 | 18.8 | 0
7854 | TORONTO BUTTONVILLE A | 11 | 24 | 6 | -1.875 | 19.875 | 0
7855 | TORONTO BUTTONVILLE A | 11 | 23 | 7 | -0.9 | 18.9 | 0
7855 | TORONTO BUTTONVILLE A | 11 | 24 | 7 | -2.5 | 20.5 | 0
7856 | TORONTO BUTTONVILLE A | 11 | 23 | 8 | -1.3 | 19.3 | 0
7856 | TORONTO BUTTONVILLE A | 11 | 24 | 8 | -1.75 | 19.75 | 0
7857 | TORONTO BUTTONVILLE A | 11 | 23 | 9 | -0.7 | 18.7 | 0
7857 | TORONTO BUTTONVILLE A | 11 | 24 | 9 | -1.15 | 19.15 | 0
7858 | TORONTO BUTTONVILLE A | 11 | 23 | 10 | 0.1 | 17.9 | 0
7858 | TORONTO BUTTONVILLE A | 11 | 24 | 10 | 0.55 | 17.45 | 0
7859 | TORONTO BUTTONVILLE A | 11 | 23 | 11 | 0.9 | 17.1 | 0
7859 | TORONTO BUTTONVILLE A | 11 | 24 | 11 | 3.175 | 14.825 | 0
7860 | TORONTO BUTTONVILLE A | 11 | 23 | 12 | 1.9 | 16.1 | 0
7860 | TORONTO BUTTONVILLE A | 11 | 24 | 12 | 4.4 | 13.6 | 0
7861 | TORONTO BUTTONVILLE A | 11 | 23 | 13 | 2.3 | 15.7 | 0
7861 | TORONTO BUTTONVILLE A | 11 | 24 | 13 | 4.8 | 13.2 | 0
7862 | TORONTO BUTTONVILLE A | 11 | 23 | 14 | 2.1 | 15.9 | 0
7862 | TORONTO BUTTONVILLE A | 11 | 24 | 14 | 5.525 | 12.475 | 0
7863 | TORONTO BUTTONVILLE A | 11 | 23 | 15 | 2.5 | 15.5 | 0
7863 | TORONTO BUTTONVILLE A | 11 | 24 | 15 | 5.875 | 12.125 | 0
7864 | TORONTO BUTTONVILLE A | 11 | 23 | 16 | 2.8 | 15.2 | 0
7864 | TORONTO BUTTONVILLE A | 11 | 24 | 16 | 6.275 | 11.725 | 0
7865 | TORONTO BUTTONVILLE A | 11 | 23 | 17 | 3.1 | 14.9 | 0
7865 | TORONTO BUTTONVILLE A | 11 | 24 | 17 | 6.125 | 11.875 | 0
7866 | TORONTO BUTTONVILLE A | 11 | 23 | 18 | 3.1 | 14.9 | 0
7866 | TORONTO BUTTONVILLE A | 11 | 24 | 18 | 5.55 | 12.45 | 0
7867 | TORONTO BUTTONVILLE A | 11 | 23 | 19 | 2.9 | 15.1 | 0
7867 | TORONTO BUTTONVILLE A | 11 | 24 | 19 | 5.35 | 12.65 | 0
7868 | TORONTO BUTTONVILLE A | 11 | 23 | 20 | 2.4 | 15.6 | 0
7868 | TORONTO BUTTONVILLE A | 11 | 24 | 20 | 5.65 | 12.35 | 0
7869 | TORONTO BUTTONVILLE A | 11 | 23 | 21 | 2.2 | 15.8 | 0
7869 | TORONTO BUTTONVILLE A | 11 | 24 | 21 | 5.6 | 12.4 | 0
7870 | TORONTO BUTTONVILLE A | 11 | 23 | 22 | 1.5 | 16.5 | 0
7870 | TORONTO BUTTONVILLE A | 11 | 24 | 22 | 5.775 | 12.225 | 0
7871 | TORONTO BUTTONVILLE A | 11 | 23 | 23 | 1.7 | 16.3 | 0
7871 | TORONTO BUTTONVILLE A | 11 | 24 | 23 | 5.475 | 12.525 | 0
7872 | TORONTO BUTTONVILLE A | 11 | 23 | 24 | 1.4 | 16.6 | 0
7872 | TORONTO BUTTONVILLE A | 11 | 24 | 24 | 5.5 | 12.5 | 0
7873 | TORONTO BUTTONVILLE A | 11 | 24 | 1 | 1.3 | 16.7 | 0
7873 | TORONTO BUTTONVILLE A | 11 | 25 | 1 | 5.725 | 12.275 | 0
7874 | TORONTO BUTTONVILLE A | 11 | 24 | 2 | 1.1 | 16.9 | 0
7874 | TORONTO BUTTONVILLE A | 11 | 25 | 2 | 5.575 | 12.425 | 0
7875 | TORONTO BUTTONVILLE A | 11 | 24 | 3 | 1.1 | 16.9 | 0
7875 | TORONTO BUTTONVILLE A | 11 | 25 | 3 | 5.375 | 12.625 | 0
7876 | TORONTO BUTTONVILLE A | 11 | 24 | 4 | 0.4 | 17.6 | 0
7876 | TORONTO BUTTONVILLE A | 11 | 25 | 4 | 5.425 | 12.575 | 0
7877 | TORONTO BUTTONVILLE A | 11 | 24 | 5 | -0.5 | 18.5 | 0
7877 | TORONTO BUTTONVILLE A | 11 | 25 | 5 | 5.35 | 12.65 | 0
7878 | TORONTO BUTTONVILLE A | 11 | 24 | 6 | -0.8 | 18.8 | 0
7878 | TORONTO BUTTONVILLE A | 11 | 25 | 6 | 5.325 | 12.675 | 0
7879 | TORONTO BUTTONVILLE A | 11 | 24 | 7 | -1.8 | 19.8 | 0
7879 | TORONTO BUTTONVILLE A | 11 | 25 | 7 | 5.4 | 12.6 | 0
7880 | TORONTO BUTTONVILLE A | 11 | 24 | 8 | -1.9 | 19.9 | 0
7880 | TORONTO BUTTONVILLE A | 11 | 25 | 8 | 5.025 | 12.975 | 0
7881 | TORONTO BUTTONVILLE A | 11 | 24 | 9 | -2.1 | 20.1 | 0
7881 | TORONTO BUTTONVILLE A | 11 | 25 | 9 | 4.85 | 13.15 | 0
7882 | TORONTO BUTTONVILLE A | 11 | 24 | 10 | -2.1 | 20.1 | 0
7882 | TORONTO BUTTONVILLE A | 11 | 25 | 10 | 5.275 | 12.725 | 0
7883 | TORONTO BUTTONVILLE A | 11 | 24 | 11 | -1.9 | 19.9 | 0
7883 | TORONTO BUTTONVILLE A | 11 | 25 | 11 | 5.95 | 12.05 | 0
7884 | TORONTO BUTTONVILLE A | 11 | 24 | 12 | -1.7 | 19.7 | 0
7884 | TORONTO BUTTONVILLE A | 11 | 25 | 12 | 6.575 | 11.425 | 0
7885 | TORONTO BUTTONVILLE A | 11 | 24 | 13 | -1.4 | 19.4 | 0
7885 | TORONTO BUTTONVILLE A | 11 | 25 | 13 | 6.8 | 11.2 | 0
7886 | TORONTO BUTTONVILLE A | 11 | 24 | 14 | -1.4 | 19.4 | 0
7886 | TORONTO BUTTONVILLE A | 11 | 25 | 14 | 6.75 | 11.25 | 0
7887 | TORONTO BUTTONVILLE A | 11 | 24 | 15 | -1.3 | 19.3 | 0
7887 | TORONTO BUTTONVILLE A | 11 | 25 | 15 | 6.875 | 11.125 | 0
7888 | TORONTO BUTTONVILLE A | 11 | 24 | 16 | -1.5 | 19.5 | 0
7888 | TORONTO BUTTONVILLE A | 11 | 25 | 16 | 6.625 | 11.375 | 0
7889 | TORONTO BUTTONVILLE A | 11 | 24 | 17 | -1.2 | 19.2 | 0
7889 | TORONTO BUTTONVILLE A | 11 | 25 | 17 | 6.15 | 11.85 | 0
7890 | TORONTO BUTTONVILLE A | 11 | 24 | 18 | -1.3 | 19.3 | 0
7890 | TORONTO BUTTONVILLE A | 11 | 25 | 18 | 5.8 | 12.2 | 0
7891 | TORONTO BUTTONVILLE A | 11 | 24 | 19 | -0.6 | 18.6 | 0
7891 | TORONTO BUTTONVILLE A | 11 | 25 | 19 | 5.725 | 12.275 | 0
7892 | TORONTO BUTTONVILLE A | 11 | 24 | 20 | -0.1 | 18.1 | 0
7892 | TORONTO BUTTONVILLE A | 11 | 25 | 20 | 5.425 | 12.575 | 0
7893 | TORONTO BUTTONVILLE A | 11 | 24 | 21 | 0.1 | 17.9 | 0
7893 | TORONTO BUTTONVILLE A | 11 | 25 | 21 | 4.825 | 13.175 | 0
7894 | TORONTO BUTTONVILLE A | 11 | 24 | 22 | -1 | 19 | 0
7894 | TORONTO BUTTONVILLE A | 11 | 25 | 22 | 4.475 | 13.525 | 0
7895 | TORONTO BUTTONVILLE A | 11 | 24 | 23 | -0.6 | 18.6 | 0
7895 | TORONTO BUTTONVILLE A | 11 | 25 | 23 | 4.075 | 13.925 | 0
7896 | TORONTO BUTTONVILLE A | 11 | 24 | 24 | 0.1 | 17.9 | 0
7896 | TORONTO BUTTONVILLE A | 11 | 25 | 24 | 3.425 | 14.575 | 0
7897 | TORONTO BUTTONVILLE A | 11 | 25 | 1 | 0.5 | 17.5 | 0
7897 | TORONTO BUTTONVILLE A | 11 | 26 | 1 | 2.825 | 15.175 | 0
7898 | TORONTO BUTTONVILLE A | 11 | 25 | 2 | 0.4 | 17.6 | 0
7898 | TORONTO BUTTONVILLE A | 11 | 26 | 2 | 2.375 | 15.625 | 0
7899 | TORONTO BUTTONVILLE A | 11 | 25 | 3 | 0.6 | 17.4 | 0
7899 | TORONTO BUTTONVILLE A | 11 | 26 | 3 | 2.125 | 15.875 | 0
7900 | TORONTO BUTTONVILLE A | 11 | 25 | 4 | 1 | 17 | 0
7900 | TORONTO BUTTONVILLE A | 11 | 26 | 4 | 1.7 | 16.3 | 0
7901 | TORONTO BUTTONVILLE A | 11 | 25 | 5 | 1.3 | 16.7 | 0
7901 | TORONTO BUTTONVILLE A | 11 | 26 | 5 | 1 | 17 | 0
7902 | TORONTO BUTTONVILLE A | 11 | 25 | 6 | 1.6 | 16.4 | 0
7902 | TORONTO BUTTONVILLE A | 11 | 26 | 6 | 0.825 | 17.175 | 0
7903 | TORONTO BUTTONVILLE A | 11 | 25 | 7 | 2.2 | 15.8 | 0
7903 | TORONTO BUTTONVILLE A | 11 | 26 | 7 | 1.175 | 16.825 | 0
7904 | TORONTO BUTTONVILLE A | 11 | 25 | 8 | 1.8 | 16.2 | 0
7904 | TORONTO BUTTONVILLE A | 11 | 26 | 8 | 0.975 | 17.025 | 0
7905 | TORONTO BUTTONVILLE A | 11 | 25 | 9 | 1.6 | 16.4 | 0
7905 | TORONTO BUTTONVILLE A | 11 | 26 | 9 | 1.65 | 16.35 | 0
7906 | TORONTO BUTTONVILLE A | 11 | 25 | 10 | 1.7 | 16.3 | 0
7906 | TORONTO BUTTONVILLE A | 11 | 26 | 10 | 2.025 | 15.975 | 0
7907 | TORONTO BUTTONVILLE A | 11 | 25 | 11 | 2.1 | 15.9 | 0
7907 | TORONTO BUTTONVILLE A | 11 | 26 | 11 | 2.25 | 15.75 | 0
7908 | TORONTO BUTTONVILLE A | 11 | 25 | 12 | 3 | 15 | 0
7908 | TORONTO BUTTONVILLE A | 11 | 26 | 12 | 2.725 | 15.275 | 0
7909 | TORONTO BUTTONVILLE A | 11 | 25 | 13 | 3.5 | 14.5 | 0
7909 | TORONTO BUTTONVILLE A | 11 | 26 | 13 | 3.05 | 14.95 | 0
7910 | TORONTO BUTTONVILLE A | 11 | 25 | 14 | 4 | 14 | 0
7910 | TORONTO BUTTONVILLE A | 11 | 26 | 14 | 3.425 | 14.575 | 0
7911 | TORONTO BUTTONVILLE A | 11 | 25 | 15 | 5.1 | 12.9 | 0
7911 | TORONTO BUTTONVILLE A | 11 | 26 | 15 | 3.775 | 14.225 | 0
7912 | TORONTO BUTTONVILLE A | 11 | 25 | 16 | 5.5 | 12.5 | 0
7912 | TORONTO BUTTONVILLE A | 11 | 26 | 16 | 3.775 | 14.225 | 0
7913 | TORONTO BUTTONVILLE A | 11 | 25 | 17 | 5.6 | 12.4 | 0
7913 | TORONTO BUTTONVILLE A | 11 | 26 | 17 | 3.65 | 14.35 | 0
7914 | TORONTO BUTTONVILLE A | 11 | 25 | 18 | 4.8 | 13.2 | 0
7914 | TORONTO BUTTONVILLE A | 11 | 26 | 18 | 2.925 | 15.075 | 0
7915 | TORONTO BUTTONVILLE A | 11 | 25 | 19 | 4.4 | 13.6 | 0
7915 | TORONTO BUTTONVILLE A | 11 | 26 | 19 | 2.6 | 15.4 | 0
7916 | TORONTO BUTTONVILLE A | 11 | 25 | 20 | 4.4 | 13.6 | 0
7916 | TORONTO BUTTONVILLE A | 11 | 26 | 20 | 1.775 | 16.225 | 0
7917 | TORONTO BUTTONVILLE A | 11 | 25 | 21 | 5.1 | 12.9 | 0
7917 | TORONTO BUTTONVILLE A | 11 | 26 | 21 | 1.15 | 16.85 | 0
7918 | TORONTO BUTTONVILLE A | 11 | 25 | 22 | 5.5 | 12.5 | 0
7918 | TORONTO BUTTONVILLE A | 11 | 26 | 22 | 1.025 | 16.975 | 0
7919 | TORONTO BUTTONVILLE A | 11 | 25 | 23 | 5.4 | 12.6 | 0
7919 | TORONTO BUTTONVILLE A | 11 | 26 | 23 | 1.35 | 16.65 | 0
7920 | TORONTO BUTTONVILLE A | 11 | 25 | 24 | 5.9 | 12.1 | 0
7920 | TORONTO BUTTONVILLE A | 11 | 26 | 24 | 1.55 | 16.45 | 0
7921 | TORONTO BUTTONVILLE A | 11 | 26 | 1 | 5.8 | 12.2 | 0
7921 | TORONTO BUTTONVILLE A | 11 | 27 | 1 | 1.65 | 16.35 | 0
7922 | TORONTO BUTTONVILLE A | 11 | 26 | 2 | 6.1 | 11.9 | 0
7922 | TORONTO BUTTONVILLE A | 11 | 27 | 2 | 1.8 | 16.2 | 0
7923 | TORONTO BUTTONVILLE A | 11 | 26 | 3 | 6 | 12 | 0
7923 | TORONTO BUTTONVILLE A | 11 | 27 | 3 | 1.725 | 16.275 | 0
7924 | TORONTO BUTTONVILLE A | 11 | 26 | 4 | 5.9 | 12.1 | 0
7924 | TORONTO BUTTONVILLE A | 11 | 27 | 4 | 1.575 | 16.425 | 0
7925 | TORONTO BUTTONVILLE A | 11 | 26 | 5 | 6 | 12 | 0
7925 | TORONTO BUTTONVILLE A | 11 | 27 | 5 | 1.2 | 16.8 | 0
7926 | TORONTO BUTTONVILLE A | 11 | 26 | 6 | 6.3 | 11.7 | 0
7926 | TORONTO BUTTONVILLE A | 11 | 27 | 6 | 0.925 | 17.075 | 0
7927 | TORONTO BUTTONVILLE A | 11 | 26 | 7 | 6.5 | 11.5 | 0
7927 | TORONTO BUTTONVILLE A | 11 | 27 | 7 | 0.65 | 17.35 | 0
7928 | TORONTO BUTTONVILLE A | 11 | 26 | 8 | 6.7 | 11.3 | 0
7928 | TORONTO BUTTONVILLE A | 11 | 27 | 8 | 0.525 | 17.475 | 0
7929 | TORONTO BUTTONVILLE A | 11 | 26 | 9 | 6.7 | 11.3 | 0
7929 | TORONTO BUTTONVILLE A | 11 | 27 | 9 | 0.2 | 17.8 | 0
7930 | TORONTO BUTTONVILLE A | 11 | 26 | 10 | 7.3 | 10.7 | 0
7930 | TORONTO BUTTONVILLE A | 11 | 27 | 10 | 0.35 | 17.65 | 0
7931 | TORONTO BUTTONVILLE A | 11 | 26 | 11 | 7.9 | 10.1 | 0
7931 | TORONTO BUTTONVILLE A | 11 | 27 | 11 | 0.75 | 17.25 | 0
7932 | TORONTO BUTTONVILLE A | 11 | 26 | 12 | 8.4 | 9.6 | 0
7932 | TORONTO BUTTONVILLE A | 11 | 27 | 12 | 1.3 | 16.7 | 0
7933 | TORONTO BUTTONVILLE A | 11 | 26 | 13 | 9.1 | 8.9 | 0
7933 | TORONTO BUTTONVILLE A | 11 | 27 | 13 | 1.75 | 16.25 | 0
7934 | TORONTO BUTTONVILLE A | 11 | 26 | 14 | 9 | 9 | 0
7934 | TORONTO BUTTONVILLE A | 11 | 27 | 14 | 1.725 | 16.275 | 0
7935 | TORONTO BUTTONVILLE A | 11 | 26 | 15 | 9.8 | 8.2 | 0
7935 | TORONTO BUTTONVILLE A | 11 | 27 | 15 | 1.9 | 16.1 | 0
7936 | TORONTO BUTTONVILLE A | 11 | 26 | 16 | 10.6 | 7.4 | 0
7936 | TORONTO BUTTONVILLE A | 11 | 27 | 16 | 2.05 | 15.95 | 0
7937 | TORONTO BUTTONVILLE A | 11 | 26 | 17 | 10.3 | 7.7 | 0
7937 | TORONTO BUTTONVILLE A | 11 | 27 | 17 | 1.925 | 16.075 | 0
7938 | TORONTO BUTTONVILLE A | 11 | 26 | 18 | 9.4 | 8.6 | 0
7938 | TORONTO BUTTONVILLE A | 11 | 27 | 18 | 1.625 | 16.375 | 0
7939 | TORONTO BUTTONVILLE A | 11 | 26 | 19 | 8.5 | 9.5 | 0
7939 | TORONTO BUTTONVILLE A | 11 | 27 | 19 | 1.225 | 16.775 | 0
7940 | TORONTO BUTTONVILLE A | 11 | 26 | 20 | 7.8 | 10.2 | 0
7940 | TORONTO BUTTONVILLE A | 11 | 27 | 20 | 0.725 | 17.275 | 0
7941 | TORONTO BUTTONVILLE A | 11 | 26 | 21 | 7.5 | 10.5 | 0
7941 | TORONTO BUTTONVILLE A | 11 | 27 | 21 | 0.35 | 17.65 | 0
7942 | TORONTO BUTTONVILLE A | 11 | 26 | 22 | 7.4 | 10.6 | 0
7942 | TORONTO BUTTONVILLE A | 11 | 27 | 22 | 0.05 | 17.95 | 0
7943 | TORONTO BUTTONVILLE A | 11 | 26 | 23 | 7.2 | 10.8 | 0
7943 | TORONTO BUTTONVILLE A | 11 | 27 | 23 | -0.275 | 18.275 | 0
7944 | TORONTO BUTTONVILLE A | 11 | 26 | 24 | 7.1 | 10.9 | 0
7944 | TORONTO BUTTONVILLE A | 11 | 27 | 24 | -0.5 | 18.5 | 0
7945 | TORONTO BUTTONVILLE A | 11 | 27 | 1 | 7.1 | 10.9 | 0
7945 | TORONTO BUTTONVILLE A | 11 | 28 | 1 | -0.525 | 18.525 | 0
7946 | TORONTO BUTTONVILLE A | 11 | 27 | 2 | 6.9 | 11.1 | 0
7946 | TORONTO BUTTONVILLE A | 11 | 28 | 2 | -0.6 | 18.6 | 0
7947 | TORONTO BUTTONVILLE A | 11 | 27 | 3 | 6.8 | 11.2 | 0
7947 | TORONTO BUTTONVILLE A | 11 | 28 | 3 | -0.425 | 18.425 | 0
7948 | TORONTO BUTTONVILLE A | 11 | 27 | 4 | 6.8 | 11.2 | 0
7948 | TORONTO BUTTONVILLE A | 11 | 28 | 4 | -0.65 | 18.65 | 0
7949 | TORONTO BUTTONVILLE A | 11 | 27 | 5 | 6.8 | 11.2 | 0
7949 | TORONTO BUTTONVILLE A | 11 | 28 | 5 | -0.85 | 18.85 | 0
7950 | TORONTO BUTTONVILLE A | 11 | 27 | 6 | 6.8 | 11.2 | 0
7950 | TORONTO BUTTONVILLE A | 11 | 28 | 6 | -1.05 | 19.05 | 0
7951 | TORONTO BUTTONVILLE A | 11 | 27 | 7 | 6.8 | 11.2 | 0
7951 | TORONTO BUTTONVILLE A | 11 | 28 | 7 | -0.3 | 18.3 | 0
7952 | TORONTO BUTTONVILLE A | 11 | 27 | 8 | 6.4 | 11.6 | 0
7952 | TORONTO BUTTONVILLE A | 11 | 28 | 8 | -0.5 | 18.5 | 0
7953 | TORONTO BUTTONVILLE A | 11 | 27 | 9 | 6.4 | 11.6 | 0
7953 | TORONTO BUTTONVILLE A | 11 | 28 | 9 | -0.8 | 18.8 | 0
7954 | TORONTO BUTTONVILLE A | 11 | 27 | 10 | 6.3 | 11.7 | 0
7954 | TORONTO BUTTONVILLE A | 11 | 28 | 10 | 0.125 | 17.875 | 0
7955 | TORONTO BUTTONVILLE A | 11 | 27 | 11 | 6.6 | 11.4 | 0
7955 | TORONTO BUTTONVILLE A | 11 | 28 | 11 | 1.525 | 16.475 | 0
7956 | TORONTO BUTTONVILLE A | 11 | 27 | 12 | 6.8 | 11.2 | 0
7956 | TORONTO BUTTONVILLE A | 11 | 28 | 12 | 2.525 | 15.475 | 0
7957 | TORONTO BUTTONVILLE A | 11 | 27 | 13 | 7.1 | 10.9 | 0
7957 | TORONTO BUTTONVILLE A | 11 | 28 | 13 | 3.35 | 14.65 | 0
7958 | TORONTO BUTTONVILLE A | 11 | 27 | 14 | 7.5 | 10.5 | 0
7958 | TORONTO BUTTONVILLE A | 11 | 28 | 14 | 4.1 | 13.9 | 0
7959 | TORONTO BUTTONVILLE A | 11 | 27 | 15 | 7.2 | 10.8 | 0
7959 | TORONTO BUTTONVILLE A | 11 | 28 | 15 | 4.575 | 13.425 | 0
7960 | TORONTO BUTTONVILLE A | 11 | 27 | 16 | 7 | 11 | 0
7960 | TORONTO BUTTONVILLE A | 11 | 28 | 16 | 4.4 | 13.6 | 0
7961 | TORONTO BUTTONVILLE A | 11 | 27 | 17 | 6.8 | 11.2 | 0
7961 | TORONTO BUTTONVILLE A | 11 | 28 | 17 | 3.65 | 14.35 | 0
7962 | TORONTO BUTTONVILLE A | 11 | 27 | 18 | 6.4 | 11.6 | 0
7962 | TORONTO BUTTONVILLE A | 11 | 28 | 18 | 3.025 | 14.975 | 0
7963 | TORONTO BUTTONVILLE A | 11 | 27 | 19 | 6.2 | 11.8 | 0
7963 | TORONTO BUTTONVILLE A | 11 | 28 | 19 | 2.85 | 15.15 | 0
7964 | TORONTO BUTTONVILLE A | 11 | 27 | 20 | 6 | 12 | 0
7964 | TORONTO BUTTONVILLE A | 11 | 28 | 20 | 2.075 | 15.925 | 0
7965 | TORONTO BUTTONVILLE A | 11 | 27 | 21 | 5.8 | 12.2 | 0
7965 | TORONTO BUTTONVILLE A | 11 | 28 | 21 | 2.2 | 15.8 | 0
7966 | TORONTO BUTTONVILLE A | 11 | 27 | 22 | 5.7 | 12.3 | 0
7966 | TORONTO BUTTONVILLE A | 11 | 28 | 22 | 2.225 | 15.775 | 0
7967 | TORONTO BUTTONVILLE A | 11 | 27 | 23 | 5.3 | 12.7 | 0
7967 | TORONTO BUTTONVILLE A | 11 | 28 | 23 | 2.175 | 15.825 | 0
7968 | TORONTO BUTTONVILLE A | 11 | 27 | 24 | 5.3 | 12.7 | 0
7968 | TORONTO BUTTONVILLE A | 11 | 28 | 24 | 1.425 | 16.575 | 0
7969 | TORONTO BUTTONVILLE A | 11 | 28 | 1 | 5.2 | 12.8 | 0
7969 | TORONTO BUTTONVILLE A | 11 | 29 | 1 | 0.6 | 17.4 | 0
7970 | TORONTO BUTTONVILLE A | 11 | 28 | 2 | 5 | 13 | 0
7970 | TORONTO BUTTONVILLE A | 11 | 29 | 2 | 0.325 | 17.675 | 0
7971 | TORONTO BUTTONVILLE A | 11 | 28 | 3 | 5.1 | 12.9 | 0
7971 | TORONTO BUTTONVILLE A | 11 | 29 | 3 | 0.075 | 17.925 | 0
7972 | TORONTO BUTTONVILLE A | 11 | 28 | 4 | 5.1 | 12.9 | 0
7972 | TORONTO BUTTONVILLE A | 11 | 29 | 4 | -0.425 | 18.425 | 0
7973 | TORONTO BUTTONVILLE A | 11 | 28 | 5 | 4.1 | 13.9 | 0
7973 | TORONTO BUTTONVILLE A | 11 | 29 | 5 | -0.925 | 18.925 | 0
7974 | TORONTO BUTTONVILLE A | 11 | 28 | 6 | 3.8 | 14.2 | 0
7974 | TORONTO BUTTONVILLE A | 11 | 29 | 6 | -0.85 | 18.85 | 0
7975 | TORONTO BUTTONVILLE A | 11 | 28 | 7 | 3.4 | 14.6 | 0
7975 | TORONTO BUTTONVILLE A | 11 | 29 | 7 | -1 | 19 | 0
7976 | TORONTO BUTTONVILLE A | 11 | 28 | 8 | 3.1 | 14.9 | 0
7976 | TORONTO BUTTONVILLE A | 11 | 29 | 8 | -0.85 | 18.85 | 0
7977 | TORONTO BUTTONVILLE A | 11 | 28 | 9 | 2.8 | 15.2 | 0
7977 | TORONTO BUTTONVILLE A | 11 | 29 | 9 | -0.9 | 18.9 | 0
7978 | TORONTO BUTTONVILLE A | 11 | 28 | 10 | 3.1 | 14.9 | 0
7978 | TORONTO BUTTONVILLE A | 11 | 29 | 10 | -0.4 | 18.4 | 0
7979 | TORONTO BUTTONVILLE A | 11 | 28 | 11 | 4.4 | 13.6 | 0
7979 | TORONTO BUTTONVILLE A | 11 | 29 | 11 | -0.075 | 18.075 | 0
7980 | TORONTO BUTTONVILLE A | 11 | 28 | 12 | 5 | 13 | 0
7980 | TORONTO BUTTONVILLE A | 11 | 29 | 12 | 0.325 | 17.675 | 0
7981 | TORONTO BUTTONVILLE A | 11 | 28 | 13 | 5.3 | 12.7 | 0
7981 | TORONTO BUTTONVILLE A | 11 | 29 | 13 | 0.725 | 17.275 | 0
7982 | TORONTO BUTTONVILLE A | 11 | 28 | 14 | 5.9 | 12.1 | 0
7982 | TORONTO BUTTONVILLE A | 11 | 29 | 14 | 0.7 | 17.3 | 0
7983 | TORONTO BUTTONVILLE A | 11 | 28 | 15 | 6.3 | 11.7 | 0
7983 | TORONTO BUTTONVILLE A | 11 | 29 | 15 | 0.8 | 17.2 | 0
7984 | TORONTO BUTTONVILLE A | 11 | 28 | 16 | 6.4 | 11.6 | 0
7984 | TORONTO BUTTONVILLE A | 11 | 29 | 16 | 1.2 | 16.8 | 0
7985 | TORONTO BUTTONVILLE A | 11 | 28 | 17 | 5.9 | 12.1 | 0
7985 | TORONTO BUTTONVILLE A | 11 | 29 | 17 | 0.8 | 17.2 | 0
7986 | TORONTO BUTTONVILLE A | 11 | 28 | 18 | 5.3 | 12.7 | 0
7986 | TORONTO BUTTONVILLE A | 11 | 29 | 18 | 0.05 | 17.95 | 0
7987 | TORONTO BUTTONVILLE A | 11 | 28 | 19 | 4.7 | 13.3 | 0
7987 | TORONTO BUTTONVILLE A | 11 | 29 | 19 | -0.325 | 18.325 | 0
7988 | TORONTO BUTTONVILLE A | 11 | 28 | 20 | 4 | 14 | 0
7988 | TORONTO BUTTONVILLE A | 11 | 29 | 20 | -0.55 | 18.55 | 0
7989 | TORONTO BUTTONVILLE A | 11 | 28 | 21 | 3.5 | 14.5 | 0
7989 | TORONTO BUTTONVILLE A | 11 | 29 | 21 | -0.65 | 18.65 | 0
7990 | TORONTO BUTTONVILLE A | 11 | 28 | 22 | 3.1 | 14.9 | 0
7990 | TORONTO BUTTONVILLE A | 11 | 29 | 22 | -0.925 | 18.925 | 0
7991 | TORONTO BUTTONVILLE A | 11 | 28 | 23 | 2.9 | 15.1 | 0
7991 | TORONTO BUTTONVILLE A | 11 | 29 | 23 | -1.075 | 19.075 | 0
7992 | TORONTO BUTTONVILLE A | 11 | 28 | 24 | 3 | 15 | 0
7992 | TORONTO BUTTONVILLE A | 11 | 29 | 24 | -1.225 | 19.225 | 0
7993 | TORONTO BUTTONVILLE A | 11 | 29 | 1 | 3 | 15 | 0
7993 | TORONTO BUTTONVILLE A | 11 | 30 | 1 | -1.275 | 19.275 | 0
7994 | TORONTO BUTTONVILLE A | 11 | 29 | 2 | 2.9 | 15.1 | 0
7994 | TORONTO BUTTONVILLE A | 11 | 30 | 2 | -1.475 | 19.475 | 0
7995 | TORONTO BUTTONVILLE A | 11 | 29 | 3 | 2.8 | 15.2 | 0
7995 | TORONTO BUTTONVILLE A | 11 | 30 | 3 | -2.175 | 20.175 | 0
7996 | TORONTO BUTTONVILLE A | 11 | 29 | 4 | 2.7 | 15.3 | 0
7996 | TORONTO BUTTONVILLE A | 11 | 30 | 4 | -2.75 | 20.75 | 0
7997 | TORONTO BUTTONVILLE A | 11 | 29 | 5 | 2.6 | 15.4 | 0
7997 | TORONTO BUTTONVILLE A | 11 | 30 | 5 | -3.175 | 21.175 | 0
7998 | TORONTO BUTTONVILLE A | 11 | 29 | 6 | 2.1 | 15.9 | 0
7998 | TORONTO BUTTONVILLE A | 11 | 30 | 6 | -3.2 | 21.2 | 0
7999 | TORONTO BUTTONVILLE A | 11 | 29 | 7 | 1.8 | 16.2 | 0
7999 | TORONTO BUTTONVILLE A | 11 | 30 | 7 | -2.6 | 20.6 | 0
8000 | TORONTO BUTTONVILLE A | 11 | 29 | 8 | 0.8 | 17.2 | 0
8000 | TORONTO BUTTONVILLE A | 11 | 30 | 8 | -2.05 | 20.05 | 0
8001 | TORONTO BUTTONVILLE A | 11 | 29 | 9 | 0.5 | 17.5 | 0
8001 | TORONTO BUTTONVILLE A | 11 | 30 | 9 | -2.225 | 20.225 | 0
8002 | TORONTO BUTTONVILLE A | 11 | 29 | 10 | 2.7 | 15.3 | 0
8002 | TORONTO BUTTONVILLE A | 11 | 30 | 10 | -1.2 | 19.2 | 0
8003 | TORONTO BUTTONVILLE A | 11 | 29 | 11 | 4.3 | 13.7 | 0
8003 | TORONTO BUTTONVILLE A | 11 | 30 | 11 | -0.625 | 18.625 | 0
8004 | TORONTO BUTTONVILLE A | 11 | 29 | 12 | 6.4 | 11.6 | 0
8004 | TORONTO BUTTONVILLE A | 11 | 30 | 12 | 0.325 | 17.675 | 0
8005 | TORONTO BUTTONVILLE A | 11 | 29 | 13 | 7.9 | 10.1 | 0
8005 | TORONTO BUTTONVILLE A | 11 | 30 | 13 | 0.775 | 17.225 | 0
8006 | TORONTO BUTTONVILLE A | 11 | 29 | 14 | 9.8 | 8.2 | 0
8006 | TORONTO BUTTONVILLE A | 11 | 30 | 14 | 1 | 17 | 0
8007 | TORONTO BUTTONVILLE A | 11 | 29 | 15 | 10.5 | 7.5 | 0
8007 | TORONTO BUTTONVILLE A | 11 | 30 | 15 | 1.25 | 16.75 | 0
8008 | TORONTO BUTTONVILLE A | 11 | 29 | 16 | 9.7 | 8.3 | 0
8008 | TORONTO BUTTONVILLE A | 11 | 30 | 16 | 1.35 | 16.65 | 0
8009 | TORONTO BUTTONVILLE A | 11 | 29 | 17 | 8.6 | 9.4 | 0
8009 | TORONTO BUTTONVILLE A | 11 | 30 | 17 | 1.325 | 16.675 | 0
8010 | TORONTO BUTTONVILLE A | 11 | 29 | 18 | 7.6 | 10.4 | 0
8010 | TORONTO BUTTONVILLE A | 11 | 30 | 18 | 1.2 | 16.8 | 0
8011 | TORONTO BUTTONVILLE A | 11 | 29 | 19 | 7.1 | 10.9 | 0
8011 | TORONTO BUTTONVILLE A | 11 | 30 | 19 | 1.025 | 16.975 | 0
8012 | TORONTO BUTTONVILLE A | 11 | 29 | 20 | 6.8 | 11.2 | 0
8012 | TORONTO BUTTONVILLE A | 11 | 30 | 20 | 0.975 | 17.025 | 0
8013 | TORONTO BUTTONVILLE A | 11 | 29 | 21 | 6.5 | 11.5 | 0
8013 | TORONTO BUTTONVILLE A | 11 | 30 | 21 | 0.975 | 17.025 | 0
8014 | TORONTO BUTTONVILLE A | 11 | 29 | 22 | 6.5 | 11.5 | 0
8014 | TORONTO BUTTONVILLE A | 11 | 30 | 22 | 1.125 | 16.875 | 0
8015 | TORONTO BUTTONVILLE A | 11 | 29 | 23 | 6.2 | 11.8 | 0
8015 | TORONTO BUTTONVILLE A | 11 | 30 | 23 | 1.2 | 16.8 | 0
8016 | TORONTO BUTTONVILLE A | 11 | 29 | 24 | 6 | 12 | 0
8016 | TORONTO BUTTONVILLE A | 11 | 30 | 24 | 1.175 | 16.825 | 0
8017 | TORONTO BUTTONVILLE A | 11 | 30 | 1 | 4.3 | 13.7 | 0
8017 | TORONTO BUTTONVILLE A | 12 | 1 | 1 | 0.875 | 17.125 | 0
8018 | TORONTO BUTTONVILLE A | 11 | 30 | 2 | 3.9 | 14.1 | 0
8018 | TORONTO BUTTONVILLE A | 12 | 1 | 2 | 0.4 | 17.6 | 0
8019 | TORONTO BUTTONVILLE A | 11 | 30 | 3 | 3.6 | 14.4 | 0
8019 | TORONTO BUTTONVILLE A | 12 | 1 | 3 | 0.2 | 17.8 | 0
8020 | TORONTO BUTTONVILLE A | 11 | 30 | 4 | 2.9 | 15.1 | 0
8020 | TORONTO BUTTONVILLE A | 12 | 1 | 4 | -0.025 | 18.025 | 0
8021 | TORONTO BUTTONVILLE A | 11 | 30 | 5 | 2.6 | 15.4 | 0
8021 | TORONTO BUTTONVILLE A | 12 | 1 | 5 | -0.3 | 18.3 | 0
8022 | TORONTO BUTTONVILLE A | 11 | 30 | 6 | 3.2 | 14.8 | 0
8022 | TORONTO BUTTONVILLE A | 12 | 1 | 6 | -0.35 | 18.35 | 0
8023 | TORONTO BUTTONVILLE A | 11 | 30 | 7 | 3 | 15 | 0
8023 | TORONTO BUTTONVILLE A | 12 | 1 | 7 | -0.45 | 18.45 | 0
8024 | TORONTO BUTTONVILLE A | 11 | 30 | 8 | 3.4 | 14.6 | 0
8024 | TORONTO BUTTONVILLE A | 12 | 1 | 8 | -0.525 | 18.525 | 0
8025 | TORONTO BUTTONVILLE A | 11 | 30 | 9 | 3.7 | 14.3 | 0
8025 | TORONTO BUTTONVILLE A | 12 | 1 | 9 | -0.625 | 18.625 | 0
8026 | TORONTO BUTTONVILLE A | 11 | 30 | 10 | 4.6 | 13.4 | 0
8026 | TORONTO BUTTONVILLE A | 12 | 1 | 10 | 0.025 | 17.975 | 0
8027 | TORONTO BUTTONVILLE A | 11 | 30 | 11 | 4.2 | 13.8 | 0
8027 | TORONTO BUTTONVILLE A | 12 | 1 | 11 | 0.725 | 17.275 | 0
8028 | TORONTO BUTTONVILLE A | 11 | 30 | 12 | 4.2 | 13.8 | 0
8028 | TORONTO BUTTONVILLE A | 12 | 1 | 12 | 1.45 | 16.55 | 0
8029 | TORONTO BUTTONVILLE A | 11 | 30 | 13 | 3.6 | 14.4 | 0
8029 | TORONTO BUTTONVILLE A | 12 | 1 | 13 | 1.875 | 16.125 | 0
8030 | TORONTO BUTTONVILLE A | 11 | 30 | 14 | 3.1 | 14.9 | 0
8030 | TORONTO BUTTONVILLE A | 12 | 1 | 14 | 2.3 | 15.7 | 0
8031 | TORONTO BUTTONVILLE A | 11 | 30 | 15 | 3.1 | 14.9 | 0
8031 | TORONTO BUTTONVILLE A | 12 | 1 | 15 | 2.45 | 15.55 | 0
8032 | TORONTO BUTTONVILLE A | 11 | 30 | 16 | 2.6 | 15.4 | 0
8032 | TORONTO BUTTONVILLE A | 12 | 1 | 16 | 2.425 | 15.575 | 0
8033 | TORONTO BUTTONVILLE A | 11 | 30 | 17 | 2 | 16 | 0
8033 | TORONTO BUTTONVILLE A | 12 | 1 | 17 | 2.35 | 15.65 | 0
8034 | TORONTO BUTTONVILLE A | 11 | 30 | 18 | 2.3 | 15.7 | 0
8034 | TORONTO BUTTONVILLE A | 12 | 1 | 18 | 2.125 | 15.875 | 0
8035 | TORONTO BUTTONVILLE A | 11 | 30 | 19 | 2.4 | 15.6 | 0
8035 | TORONTO BUTTONVILLE A | 12 | 1 | 19 | 1.75 | 16.25 | 0
8036 | TORONTO BUTTONVILLE A | 11 | 30 | 20 | 2 | 16 | 0
8036 | TORONTO BUTTONVILLE A | 12 | 1 | 20 | 1.375 | 16.625 | 0
8037 | TORONTO BUTTONVILLE A | 11 | 30 | 21 | 1.8 | 16.2 | 0
8037 | TORONTO BUTTONVILLE A | 12 | 1 | 21 | 0.925 | 17.075 | 0
8038 | TORONTO BUTTONVILLE A | 11 | 30 | 22 | 1.1 | 16.9 | 0
8038 | TORONTO BUTTONVILLE A | 12 | 1 | 22 | 0.575 | 17.425 | 0
8039 | TORONTO BUTTONVILLE A | 11 | 30 | 23 | 0.6 | 17.4 | 0
8039 | TORONTO BUTTONVILLE A | 12 | 1 | 23 | 0.75 | 17.25 | 0
8040 | TORONTO BUTTONVILLE A | 11 | 30 | 24 | 0.1 | 17.9 | 0
8040 | TORONTO BUTTONVILLE A | 12 | 1 | 24 | 0.825 | 17.175 | 0
8041 | TORONTO BUTTONVILLE A | 12 | 1 | 1 | -0.3 | 18.3 | 0
8041 | TORONTO BUTTONVILLE A | 12 | 2 | 1 | 1.2 | 16.8 | 0
8042 | TORONTO BUTTONVILLE A | 12 | 1 | 2 | -0.8 | 18.8 | 0
8042 | TORONTO BUTTONVILLE A | 12 | 2 | 2 | 1.15 | 16.85 | 0
8043 | TORONTO BUTTONVILLE A | 12 | 1 | 3 | -1.1 | 19.1 | 0
8043 | TORONTO BUTTONVILLE A | 12 | 2 | 3 | 1.125 | 16.875 | 0
8044 | TORONTO BUTTONVILLE A | 12 | 1 | 4 | -1.4 | 19.4 | 0
8044 | TORONTO BUTTONVILLE A | 12 | 2 | 4 | 0.925 | 17.075 | 0
8045 | TORONTO BUTTONVILLE A | 12 | 1 | 5 | -1.8 | 19.8 | 0
8045 | TORONTO BUTTONVILLE A | 12 | 2 | 5 | 1.025 | 16.975 | 0
8046 | TORONTO BUTTONVILLE A | 12 | 1 | 6 | -2 | 20 | 0
8046 | TORONTO BUTTONVILLE A | 12 | 2 | 6 | 1.15 | 16.85 | 0
8047 | TORONTO BUTTONVILLE A | 12 | 1 | 7 | -2 | 20 | 0
8047 | TORONTO BUTTONVILLE A | 12 | 2 | 7 | 1.425 | 16.575 | 0
8048 | TORONTO BUTTONVILLE A | 12 | 1 | 8 | -2.2 | 20.2 | 0
8048 | TORONTO BUTTONVILLE A | 12 | 2 | 8 | 1.55 | 16.45 | 0
8049 | TORONTO BUTTONVILLE A | 12 | 1 | 9 | -2.1 | 20.1 | 0
8049 | TORONTO BUTTONVILLE A | 12 | 2 | 9 | 1.775 | 16.225 | 0
8050 | TORONTO BUTTONVILLE A | 12 | 1 | 10 | -1.9 | 19.9 | 0
8050 | TORONTO BUTTONVILLE A | 12 | 2 | 10 | 2.275 | 15.725 | 0
8051 | TORONTO BUTTONVILLE A | 12 | 1 | 11 | -1.6 | 19.6 | 0
8051 | TORONTO BUTTONVILLE A | 12 | 2 | 11 | 3.05 | 14.95 | 0
8052 | TORONTO BUTTONVILLE A | 12 | 1 | 12 | -1.2 | 19.2 | 0
8052 | TORONTO BUTTONVILLE A | 12 | 2 | 12 | 3.725 | 14.275 | 0
8053 | TORONTO BUTTONVILLE A | 12 | 1 | 13 | -1 | 19 | 0
8053 | TORONTO BUTTONVILLE A | 12 | 2 | 13 | 4.375 | 13.625 | 0
8054 | TORONTO BUTTONVILLE A | 12 | 1 | 14 | -0.7 | 18.7 | 0
8054 | TORONTO BUTTONVILLE A | 12 | 2 | 14 | 4.775 | 13.225 | 0
8055 | TORONTO BUTTONVILLE A | 12 | 1 | 15 | -0.7 | 18.7 | 0
8055 | TORONTO BUTTONVILLE A | 12 | 2 | 15 | 5.15 | 12.85 | 0
8056 | TORONTO BUTTONVILLE A | 12 | 1 | 16 | -0.9 | 18.9 | 0
8056 | TORONTO BUTTONVILLE A | 12 | 2 | 16 | 5.1 | 12.9 | 0
8057 | TORONTO BUTTONVILLE A | 12 | 1 | 17 | -1.1 | 19.1 | 0
8057 | TORONTO BUTTONVILLE A | 12 | 2 | 17 | 4.875 | 13.125 | 0
8058 | TORONTO BUTTONVILLE A | 12 | 1 | 18 | -1.2 | 19.2 | 0
8058 | TORONTO BUTTONVILLE A | 12 | 2 | 18 | 3.25 | 14.75 | 0
8059 | TORONTO BUTTONVILLE A | 12 | 1 | 19 | -1.1 | 19.1 | 0
8059 | TORONTO BUTTONVILLE A | 12 | 2 | 19 | 2.75 | 15.25 | 0
8060 | TORONTO BUTTONVILLE A | 12 | 1 | 20 | -1.4 | 19.4 | 0
8060 | TORONTO BUTTONVILLE A | 12 | 2 | 20 | 2.425 | 15.575 | 0
8061 | TORONTO BUTTONVILLE A | 12 | 1 | 21 | -1.6 | 19.6 | 0
8061 | TORONTO BUTTONVILLE A | 12 | 2 | 21 | 2.5 | 15.5 | 0
8062 | TORONTO BUTTONVILLE A | 12 | 1 | 22 | -2.3 | 20.3 | 0
8062 | TORONTO BUTTONVILLE A | 12 | 2 | 22 | 2.6 | 15.4 | 0
8063 | TORONTO BUTTONVILLE A | 12 | 1 | 23 | -2.5 | 20.5 | 0
8063 | TORONTO BUTTONVILLE A | 12 | 2 | 23 | 1.45 | 16.55 | 0
8064 | TORONTO BUTTONVILLE A | 12 | 1 | 24 | -2 | 20 | 0
8064 | TORONTO BUTTONVILLE A | 12 | 2 | 24 | 0.7 | 17.3 | 0
8065 | TORONTO BUTTONVILLE A | 12 | 2 | 1 | -2.2 | 20.2 | 0
8065 | TORONTO BUTTONVILLE A | 12 | 3 | 1 | 0.6 | 17.4 | 0
8066 | TORONTO BUTTONVILLE A | 12 | 2 | 2 | -1.8 | 19.8 | 0
8066 | TORONTO BUTTONVILLE A | 12 | 3 | 2 | -0.1 | 18.1 | 0
8067 | TORONTO BUTTONVILLE A | 12 | 2 | 3 | -1.9 | 19.9 | 0
8067 | TORONTO BUTTONVILLE A | 12 | 3 | 3 | 0.225 | 17.775 | 0
8068 | TORONTO BUTTONVILLE A | 12 | 2 | 4 | -1.8 | 19.8 | 0
8068 | TORONTO BUTTONVILLE A | 12 | 3 | 4 | -0.075 | 18.075 | 0
8069 | TORONTO BUTTONVILLE A | 12 | 2 | 5 | -1.9 | 19.9 | 0
8069 | TORONTO BUTTONVILLE A | 12 | 3 | 5 | -0.625 | 18.625 | 0
8070 | TORONTO BUTTONVILLE A | 12 | 2 | 6 | -1.5 | 19.5 | 0
8070 | TORONTO BUTTONVILLE A | 12 | 3 | 6 | -0.725 | 18.725 | 0
8071 | TORONTO BUTTONVILLE A | 12 | 2 | 7 | -1.1 | 19.1 | 0
8071 | TORONTO BUTTONVILLE A | 12 | 3 | 7 | -0.675 | 18.675 | 0
8072 | TORONTO BUTTONVILLE A | 12 | 2 | 8 | -1.3 | 19.3 | 0
8072 | TORONTO BUTTONVILLE A | 12 | 3 | 8 | -1.65 | 19.65 | 0
8073 | TORONTO BUTTONVILLE A | 12 | 2 | 9 | -1.4 | 19.4 | 0
8073 | TORONTO BUTTONVILLE A | 12 | 3 | 9 | -2.225 | 20.225 | 0
8074 | TORONTO BUTTONVILLE A | 12 | 2 | 10 | -0.7 | 18.7 | 0
8074 | TORONTO BUTTONVILLE A | 12 | 3 | 10 | -1.825 | 19.825 | 0
8075 | TORONTO BUTTONVILLE A | 12 | 2 | 11 | 0 | 18 | 0
8075 | TORONTO BUTTONVILLE A | 12 | 3 | 11 | -0.575 | 18.575 | 0
8076 | TORONTO BUTTONVILLE A | 12 | 2 | 12 | 0.5 | 17.5 | 0
8076 | TORONTO BUTTONVILLE A | 12 | 3 | 12 | 0.375 | 17.625 | 0
8077 | TORONTO BUTTONVILLE A | 12 | 2 | 13 | 1.3 | 16.7 | 0
8077 | TORONTO BUTTONVILLE A | 12 | 3 | 13 | 1.1 | 16.9 | 0
8078 | TORONTO BUTTONVILLE A | 12 | 2 | 14 | 2.2 | 15.8 | 0
8078 | TORONTO BUTTONVILLE A | 12 | 3 | 14 | 1.6 | 16.4 | 0
8079 | TORONTO BUTTONVILLE A | 12 | 2 | 15 | 2.8 | 15.2 | 0
8079 | TORONTO BUTTONVILLE A | 12 | 3 | 15 | 2.325 | 15.675 | 0
8080 | TORONTO BUTTONVILLE A | 12 | 2 | 16 | 3.7 | 14.3 | 0
8080 | TORONTO BUTTONVILLE A | 12 | 3 | 16 | 2.375 | 15.625 | 0
8081 | TORONTO BUTTONVILLE A | 12 | 2 | 17 | 3.5 | 14.5 | 0
8081 | TORONTO BUTTONVILLE A | 12 | 3 | 17 | 1.65 | 16.35 | 0
8082 | TORONTO BUTTONVILLE A | 12 | 2 | 18 | 2.6 | 15.4 | 0
8082 | TORONTO BUTTONVILLE A | 12 | 3 | 18 | 1.175 | 16.825 | 0
8083 | TORONTO BUTTONVILLE A | 12 | 2 | 19 | 1.9 | 16.1 | 0
8083 | TORONTO BUTTONVILLE A | 12 | 3 | 19 | 0.725 | 17.275 | 0
8084 | TORONTO BUTTONVILLE A | 12 | 2 | 20 | 1.4 | 16.6 | 0
8084 | TORONTO BUTTONVILLE A | 12 | 3 | 20 | 0.575 | 17.425 | 0
8085 | TORONTO BUTTONVILLE A | 12 | 2 | 21 | 0.8 | 17.2 | 0
8085 | TORONTO BUTTONVILLE A | 12 | 3 | 21 | 0.325 | 17.675 | 0
8086 | TORONTO BUTTONVILLE A | 12 | 2 | 22 | 0.6 | 17.4 | 0
8086 | TORONTO BUTTONVILLE A | 12 | 3 | 22 | -0.2 | 18.2 | 0
8087 | TORONTO BUTTONVILLE A | 12 | 2 | 23 | 1 | 17 | 0
8087 | TORONTO BUTTONVILLE A | 12 | 3 | 23 | -0.475 | 18.475 | 0
8088 | TORONTO BUTTONVILLE A | 12 | 2 | 24 | 0.6 | 17.4 | 0
8088 | TORONTO BUTTONVILLE A | 12 | 3 | 24 | -1.05 | 19.05 | 0
8089 | TORONTO BUTTONVILLE A | 12 | 3 | 1 | 0.4 | 17.6 | 0
8089 | TORONTO BUTTONVILLE A | 12 | 4 | 1 | -1.4 | 19.4 | 0
8090 | TORONTO BUTTONVILLE A | 12 | 3 | 2 | 0.2 | 17.8 | 0
8090 | TORONTO BUTTONVILLE A | 12 | 4 | 2 | -1.35 | 19.35 | 0
8091 | TORONTO BUTTONVILLE A | 12 | 3 | 3 | -0.7 | 18.7 | 0
8091 | TORONTO BUTTONVILLE A | 12 | 4 | 3 | -1.375 | 19.375 | 0
8092 | TORONTO BUTTONVILLE A | 12 | 3 | 4 | -0.5 | 18.5 | 0
8092 | TORONTO BUTTONVILLE A | 12 | 4 | 4 | -1.35 | 19.35 | 0
8093 | TORONTO BUTTONVILLE A | 12 | 3 | 5 | 0 | 18 | 0
8093 | TORONTO BUTTONVILLE A | 12 | 4 | 5 | -1.275 | 19.275 | 0
8094 | TORONTO BUTTONVILLE A | 12 | 3 | 6 | -0.4 | 18.4 | 0
8094 | TORONTO BUTTONVILLE A | 12 | 4 | 6 | -1.125 | 19.125 | 0
8095 | TORONTO BUTTONVILLE A | 12 | 3 | 7 | -0.4 | 18.4 | 0
8095 | TORONTO BUTTONVILLE A | 12 | 4 | 7 | -0.725 | 18.725 | 0
8096 | TORONTO BUTTONVILLE A | 12 | 3 | 8 | -0.4 | 18.4 | 0
8096 | TORONTO BUTTONVILLE A | 12 | 4 | 8 | -0.675 | 18.675 | 0
8097 | TORONTO BUTTONVILLE A | 12 | 3 | 9 | -0.1 | 18.1 | 0
8097 | TORONTO BUTTONVILLE A | 12 | 4 | 9 | -0.625 | 18.625 | 0
8098 | TORONTO BUTTONVILLE A | 12 | 3 | 10 | 0.9 | 17.1 | 0
8098 | TORONTO BUTTONVILLE A | 12 | 4 | 10 | -0.2 | 18.2 | 0
8099 | TORONTO BUTTONVILLE A | 12 | 3 | 11 | 1.8 | 16.2 | 0
8099 | TORONTO BUTTONVILLE A | 12 | 4 | 11 | 0.7 | 17.3 | 0
8100 | TORONTO BUTTONVILLE A | 12 | 3 | 12 | 2 | 16 | 0
8100 | TORONTO BUTTONVILLE A | 12 | 4 | 12 | 1.375 | 16.625 | 0
8101 | TORONTO BUTTONVILLE A | 12 | 3 | 13 | 2.9 | 15.1 | 0
8101 | TORONTO BUTTONVILLE A | 12 | 4 | 13 | 1.825 | 16.175 | 0
8102 | TORONTO BUTTONVILLE A | 12 | 3 | 14 | 3.2 | 14.8 | 0
8102 | TORONTO BUTTONVILLE A | 12 | 4 | 14 | 2.425 | 15.575 | 0
8103 | TORONTO BUTTONVILLE A | 12 | 3 | 15 | 3.9 | 14.1 | 0
8103 | TORONTO BUTTONVILLE A | 12 | 4 | 15 | 2.425 | 15.575 | 0
8104 | TORONTO BUTTONVILLE A | 12 | 3 | 16 | 3.6 | 14.4 | 0
8104 | TORONTO BUTTONVILLE A | 12 | 4 | 16 | 2.125 | 15.875 | 0
8105 | TORONTO BUTTONVILLE A | 12 | 3 | 17 | 3.4 | 14.6 | 0
8105 | TORONTO BUTTONVILLE A | 12 | 4 | 17 | 2.075 | 15.925 | 0
8106 | TORONTO BUTTONVILLE A | 12 | 3 | 18 | 3.4 | 14.6 | 0
8106 | TORONTO BUTTONVILLE A | 12 | 4 | 18 | 1.6 | 16.4 | 0
8107 | TORONTO BUTTONVILLE A | 12 | 3 | 19 | 3.5 | 14.5 | 0
8107 | TORONTO BUTTONVILLE A | 12 | 4 | 19 | 1.475 | 16.525 | 0
8108 | TORONTO BUTTONVILLE A | 12 | 3 | 20 | 3.3 | 14.7 | 0
8108 | TORONTO BUTTONVILLE A | 12 | 4 | 20 | 1.175 | 16.825 | 0
8109 | TORONTO BUTTONVILLE A | 12 | 3 | 21 | 3.2 | 14.8 | 0
8109 | TORONTO BUTTONVILLE A | 12 | 4 | 21 | 1.2 | 16.8 | 0
8110 | TORONTO BUTTONVILLE A | 12 | 3 | 22 | 3.2 | 14.8 | 0
8110 | TORONTO BUTTONVILLE A | 12 | 4 | 22 | 1.2 | 16.8 | 0
8111 | TORONTO BUTTONVILLE A | 12 | 3 | 23 | 3.2 | 14.8 | 0
8111 | TORONTO BUTTONVILLE A | 12 | 4 | 23 | 1.125 | 16.875 | 0
8112 | TORONTO BUTTONVILLE A | 12 | 3 | 24 | 3.4 | 14.6 | 0
8112 | TORONTO BUTTONVILLE A | 12 | 4 | 24 | 0.875 | 17.125 | 0
8113 | TORONTO BUTTONVILLE A | 12 | 4 | 1 | 3.4 | 14.6 | 0
8113 | TORONTO BUTTONVILLE A | 12 | 5 | 1 | 0.375 | 17.625 | 0
8114 | TORONTO BUTTONVILLE A | 12 | 4 | 2 | 2.9 | 15.1 | 0
8114 | TORONTO BUTTONVILLE A | 12 | 5 | 2 | 0.175 | 17.825 | 0
8115 | TORONTO BUTTONVILLE A | 12 | 4 | 3 | 3.1 | 14.9 | 0
8115 | TORONTO BUTTONVILLE A | 12 | 5 | 3 | -0.1 | 18.1 | 0
8116 | TORONTO BUTTONVILLE A | 12 | 4 | 4 | 3 | 15 | 0
8116 | TORONTO BUTTONVILLE A | 12 | 5 | 4 | -0.35 | 18.35 | 0
8117 | TORONTO BUTTONVILLE A | 12 | 4 | 5 | 2.6 | 15.4 | 0
8117 | TORONTO BUTTONVILLE A | 12 | 5 | 5 | -1.1 | 19.1 | 0
8118 | TORONTO BUTTONVILLE A | 12 | 4 | 6 | 1.9 | 16.1 | 0
8118 | TORONTO BUTTONVILLE A | 12 | 5 | 6 | -1.05 | 19.05 | 0
8119 | TORONTO BUTTONVILLE A | 12 | 4 | 7 | 1.1 | 16.9 | 0
8119 | TORONTO BUTTONVILLE A | 12 | 5 | 7 | -0.675 | 18.675 | 0
8120 | TORONTO BUTTONVILLE A | 12 | 4 | 8 | 1.1 | 16.9 | 0
8120 | TORONTO BUTTONVILLE A | 12 | 5 | 8 | -0.4 | 18.4 | 0
8121 | TORONTO BUTTONVILLE A | 12 | 4 | 9 | 0.9 | 17.1 | 0
8121 | TORONTO BUTTONVILLE A | 12 | 5 | 9 | -0.15 | 18.15 | 0
8122 | TORONTO BUTTONVILLE A | 12 | 4 | 10 | 0.4 | 17.6 | 0
8122 | TORONTO BUTTONVILLE A | 12 | 5 | 10 | 0.275 | 17.725 | 0
8123 | TORONTO BUTTONVILLE A | 12 | 4 | 11 | 0.4 | 17.6 | 0
8123 | TORONTO BUTTONVILLE A | 12 | 5 | 11 | 1.075 | 16.925 | 0
8124 | TORONTO BUTTONVILLE A | 12 | 4 | 12 | 0.4 | 17.6 | 0
8124 | TORONTO BUTTONVILLE A | 12 | 5 | 12 | 1.95 | 16.05 | 0
8125 | TORONTO BUTTONVILLE A | 12 | 4 | 13 | 0.8 | 17.2 | 0
8125 | TORONTO BUTTONVILLE A | 12 | 5 | 13 | 2.625 | 15.375 | 0
8126 | TORONTO BUTTONVILLE A | 12 | 4 | 14 | 1.7 | 16.3 | 0
8126 | TORONTO BUTTONVILLE A | 12 | 5 | 14 | 2.8 | 15.2 | 0
8127 | TORONTO BUTTONVILLE A | 12 | 4 | 15 | 2.4 | 15.6 | 0
8127 | TORONTO BUTTONVILLE A | 12 | 5 | 15 | 2.525 | 15.475 | 0
8128 | TORONTO BUTTONVILLE A | 12 | 4 | 16 | 2.6 | 15.4 | 0
8128 | TORONTO BUTTONVILLE A | 12 | 5 | 16 | 2.025 | 15.975 | 0
8129 | TORONTO BUTTONVILLE A | 12 | 4 | 17 | 2.4 | 15.6 | 0
8129 | TORONTO BUTTONVILLE A | 12 | 5 | 17 | 1.625 | 16.375 | 0
8130 | TORONTO BUTTONVILLE A | 12 | 4 | 18 | 2.4 | 15.6 | 0
8130 | TORONTO BUTTONVILLE A | 12 | 5 | 18 | 1.325 | 16.675 | 0
8131 | TORONTO BUTTONVILLE A | 12 | 4 | 19 | 2.4 | 15.6 | 0
8131 | TORONTO BUTTONVILLE A | 12 | 5 | 19 | 0.875 | 17.125 | 0
8132 | TORONTO BUTTONVILLE A | 12 | 4 | 20 | 2.1 | 15.9 | 0
8132 | TORONTO BUTTONVILLE A | 12 | 5 | 20 | 0.65 | 17.35 | 0
8133 | TORONTO BUTTONVILLE A | 12 | 4 | 21 | 1.9 | 16.1 | 0
8133 | TORONTO BUTTONVILLE A | 12 | 5 | 21 | 0.5 | 17.5 | 0
8134 | TORONTO BUTTONVILLE A | 12 | 4 | 22 | 2.1 | 15.9 | 0
8134 | TORONTO BUTTONVILLE A | 12 | 5 | 22 | 0.2 | 17.8 | 0
8135 | TORONTO BUTTONVILLE A | 12 | 4 | 23 | 1.5 | 16.5 | 0
8135 | TORONTO BUTTONVILLE A | 12 | 5 | 23 | 0.25 | 17.75 | 0
8136 | TORONTO BUTTONVILLE A | 12 | 4 | 24 | 0.8 | 17.2 | 0
8136 | TORONTO BUTTONVILLE A | 12 | 5 | 24 | 0.175 | 17.825 | 0
8137 | TORONTO BUTTONVILLE A | 12 | 5 | 1 | 0 | 18 | 0
8137 | TORONTO BUTTONVILLE A | 12 | 6 | 1 | 0 | 18 | 0
8138 | TORONTO BUTTONVILLE A | 12 | 5 | 2 | 0.7 | 17.3 | 0
8138 | TORONTO BUTTONVILLE A | 12 | 6 | 2 | 0.025 | 17.975 | 0
8139 | TORONTO BUTTONVILLE A | 12 | 5 | 3 | 1.1 | 16.9 | 0
8139 | TORONTO BUTTONVILLE A | 12 | 6 | 3 | 0.275 | 17.725 | 0
8140 | TORONTO BUTTONVILLE A | 12 | 5 | 4 | 0.8 | 17.2 | 0
8140 | TORONTO BUTTONVILLE A | 12 | 6 | 4 | 0.3 | 17.7 | 0
8141 | TORONTO BUTTONVILLE A | 12 | 5 | 5 | 0.2 | 17.8 | 0
8141 | TORONTO BUTTONVILLE A | 12 | 6 | 5 | 0.025 | 17.975 | 0
8142 | TORONTO BUTTONVILLE A | 12 | 5 | 6 | 0.5 | 17.5 | 0
8142 | TORONTO BUTTONVILLE A | 12 | 6 | 6 | 0.775 | 17.225 | 0
8143 | TORONTO BUTTONVILLE A | 12 | 5 | 7 | 0.3 | 17.7 | 0
8143 | TORONTO BUTTONVILLE A | 12 | 6 | 7 | 0.9 | 17.1 | 0
8144 | TORONTO BUTTONVILLE A | 12 | 5 | 8 | 0.1 | 17.9 | 0
8144 | TORONTO BUTTONVILLE A | 12 | 6 | 8 | 0.9 | 17.1 | 0
8145 | TORONTO BUTTONVILLE A | 12 | 5 | 9 | -0.2 | 18.2 | 0
8145 | TORONTO BUTTONVILLE A | 12 | 6 | 9 | 0.925 | 17.075 | 0
8146 | TORONTO BUTTONVILLE A | 12 | 5 | 10 | -0.6 | 18.6 | 0
8146 | TORONTO BUTTONVILLE A | 12 | 6 | 10 | 1.45 | 16.55 | 0
8147 | TORONTO BUTTONVILLE A | 12 | 5 | 11 | -0.8 | 18.8 | 0
8147 | TORONTO BUTTONVILLE A | 12 | 6 | 11 | 1.7 | 16.3 | 0
8148 | TORONTO BUTTONVILLE A | 12 | 5 | 12 | -0.6 | 18.6 | 0
8148 | TORONTO BUTTONVILLE A | 12 | 6 | 12 | 1.675 | 16.325 | 0
8149 | TORONTO BUTTONVILLE A | 12 | 5 | 13 | -0.4 | 18.4 | 0
8149 | TORONTO BUTTONVILLE A | 12 | 6 | 13 | 1.425 | 16.575 | 0
8150 | TORONTO BUTTONVILLE A | 12 | 5 | 14 | -0.7 | 18.7 | 0
8150 | TORONTO BUTTONVILLE A | 12 | 6 | 14 | 1.75 | 16.25 | 0
8151 | TORONTO BUTTONVILLE A | 12 | 5 | 15 | -1.3 | 19.3 | 0
8151 | TORONTO BUTTONVILLE A | 12 | 6 | 15 | 0.975 | 17.025 | 0
8152 | TORONTO BUTTONVILLE A | 12 | 5 | 16 | -1.3 | 19.3 | 0
8152 | TORONTO BUTTONVILLE A | 12 | 6 | 16 | 0.975 | 17.025 | 0
8153 | TORONTO BUTTONVILLE A | 12 | 5 | 17 | -2.2 | 20.2 | 0
8153 | TORONTO BUTTONVILLE A | 12 | 6 | 17 | 0.575 | 17.425 | 0
8154 | TORONTO BUTTONVILLE A | 12 | 5 | 18 | -3.5 | 21.5 | 0
8154 | TORONTO BUTTONVILLE A | 12 | 6 | 18 | -0.125 | 18.125 | 0
8155 | TORONTO BUTTONVILLE A | 12 | 5 | 19 | -3.7 | 21.7 | 0
8155 | TORONTO BUTTONVILLE A | 12 | 6 | 19 | -0.5 | 18.5 | 0
8156 | TORONTO BUTTONVILLE A | 12 | 5 | 20 | -3.7 | 21.7 | 0
8156 | TORONTO BUTTONVILLE A | 12 | 6 | 20 | -0.65 | 18.65 | 0
8157 | TORONTO BUTTONVILLE A | 12 | 5 | 21 | -3.8 | 21.8 | 0
8157 | TORONTO BUTTONVILLE A | 12 | 6 | 21 | -0.875 | 18.875 | 0
8158 | TORONTO BUTTONVILLE A | 12 | 5 | 22 | -3.8 | 21.8 | 0
8158 | TORONTO BUTTONVILLE A | 12 | 6 | 22 | -1.375 | 19.375 | 0
8159 | TORONTO BUTTONVILLE A | 12 | 5 | 23 | -3.9 | 21.9 | 0
8159 | TORONTO BUTTONVILLE A | 12 | 6 | 23 | -1.7 | 19.7 | 0
8160 | TORONTO BUTTONVILLE A | 12 | 5 | 24 | -4.2 | 22.2 | 0
8160 | TORONTO BUTTONVILLE A | 12 | 6 | 24 | -2.275 | 20.275 | 0
8161 | TORONTO BUTTONVILLE A | 12 | 6 | 1 | -4.3 | 22.3 | 0
8161 | TORONTO BUTTONVILLE A | 12 | 7 | 1 | -2.925 | 20.925 | 0
8162 | TORONTO BUTTONVILLE A | 12 | 6 | 2 | -4.5 | 22.5 | 0
8162 | TORONTO BUTTONVILLE A | 12 | 7 | 2 | -3.575 | 21.575 | 0
8163 | TORONTO BUTTONVILLE A | 12 | 6 | 3 | -4.5 | 22.5 | 0
8163 | TORONTO BUTTONVILLE A | 12 | 7 | 3 | -3.7 | 21.7 | 0
8164 | TORONTO BUTTONVILLE A | 12 | 6 | 4 | -4.4 | 22.4 | 0
8164 | TORONTO BUTTONVILLE A | 12 | 7 | 4 | -3.925 | 21.925 | 0
8165 | TORONTO BUTTONVILLE A | 12 | 6 | 5 | -4.5 | 22.5 | 0
8165 | TORONTO BUTTONVILLE A | 12 | 7 | 5 | -4.25 | 22.25 | 0
8166 | TORONTO BUTTONVILLE A | 12 | 6 | 6 | -4.5 | 22.5 | 0
8166 | TORONTO BUTTONVILLE A | 12 | 7 | 6 | -4.6 | 22.6 | 0
8167 | TORONTO BUTTONVILLE A | 12 | 6 | 7 | -5.2 | 23.2 | 0
8167 | TORONTO BUTTONVILLE A | 12 | 7 | 7 | -5.475 | 23.475 | 0
8168 | TORONTO BUTTONVILLE A | 12 | 6 | 8 | -5.6 | 23.6 | 0
8168 | TORONTO BUTTONVILLE A | 12 | 7 | 8 | -5.9 | 23.9 | 0
8169 | TORONTO BUTTONVILLE A | 12 | 6 | 9 | -5.5 | 23.5 | 0
8169 | TORONTO BUTTONVILLE A | 12 | 7 | 9 | -6.125 | 24.125 | 0
8170 | TORONTO BUTTONVILLE A | 12 | 6 | 10 | -4.9 | 22.9 | 0
8170 | TORONTO BUTTONVILLE A | 12 | 7 | 10 | -5.65 | 23.65 | 0
8171 | TORONTO BUTTONVILLE A | 12 | 6 | 11 | -3.2 | 21.2 | 0
8171 | TORONTO BUTTONVILLE A | 12 | 7 | 11 | -4.9 | 22.9 | 0
8172 | TORONTO BUTTONVILLE A | 12 | 6 | 12 | -2.4 | 20.4 | 0
8172 | TORONTO BUTTONVILLE A | 12 | 7 | 12 | -4.025 | 22.025 | 0
8173 | TORONTO BUTTONVILLE A | 12 | 6 | 13 | -0.9 | 18.9 | 0
8173 | TORONTO BUTTONVILLE A | 12 | 7 | 13 | -3.775 | 21.775 | 0
8174 | TORONTO BUTTONVILLE A | 12 | 6 | 14 | -0.5 | 18.5 | 0
8174 | TORONTO BUTTONVILLE A | 12 | 7 | 14 | -3.5 | 21.5 | 0
8175 | TORONTO BUTTONVILLE A | 12 | 6 | 15 | -0.2 | 18.2 | 0
8175 | TORONTO BUTTONVILLE A | 12 | 7 | 15 | -3.325 | 21.325 | 0
8176 | TORONTO BUTTONVILLE A | 12 | 6 | 16 | -0.1 | 18.1 | 0
8176 | TORONTO BUTTONVILLE A | 12 | 7 | 16 | -2.925 | 20.925 | 0
8177 | TORONTO BUTTONVILLE A | 12 | 6 | 17 | -1 | 19 | 0
8177 | TORONTO BUTTONVILLE A | 12 | 7 | 17 | -3.625 | 21.625 | 0
8178 | TORONTO BUTTONVILLE A | 12 | 6 | 18 | -1.8 | 19.8 | 0
8178 | TORONTO BUTTONVILLE A | 12 | 7 | 18 | -3.55 | 21.55 | 0
8179 | TORONTO BUTTONVILLE A | 12 | 6 | 19 | -2.4 | 20.4 | 0
8179 | TORONTO BUTTONVILLE A | 12 | 7 | 19 | -3.75 | 21.75 | 0
8180 | TORONTO BUTTONVILLE A | 12 | 6 | 20 | -3 | 21 | 0
8180 | TORONTO BUTTONVILLE A | 12 | 7 | 20 | -4.125 | 22.125 | 0
8181 | TORONTO BUTTONVILLE A | 12 | 6 | 21 | -3.7 | 21.7 | 0
8181 | TORONTO BUTTONVILLE A | 12 | 7 | 21 | -4.65 | 22.65 | 0
8182 | TORONTO BUTTONVILLE A | 12 | 6 | 22 | -4.2 | 22.2 | 0
8182 | TORONTO BUTTONVILLE A | 12 | 7 | 22 | -5.05 | 23.05 | 0
8183 | TORONTO BUTTONVILLE A | 12 | 6 | 23 | -4.5 | 22.5 | 0
8183 | TORONTO BUTTONVILLE A | 12 | 7 | 23 | -5.575 | 23.575 | 0
8184 | TORONTO BUTTONVILLE A | 12 | 6 | 24 | -4.5 | 22.5 | 0
8184 | TORONTO BUTTONVILLE A | 12 | 7 | 24 | -5.675 | 23.675 | 0
8185 | TORONTO BUTTONVILLE A | 12 | 7 | 1 | -4.7 | 22.7 | 0
8185 | TORONTO BUTTONVILLE A | 12 | 8 | 1 | -6.175 | 24.175 | 0
8186 | TORONTO BUTTONVILLE A | 12 | 7 | 2 | -5.4 | 23.4 | 0
8186 | TORONTO BUTTONVILLE A | 12 | 8 | 2 | -6.125 | 24.125 | 0
8187 | TORONTO BUTTONVILLE A | 12 | 7 | 3 | -6.1 | 24.1 | 0
8187 | TORONTO BUTTONVILLE A | 12 | 8 | 3 | -6.175 | 24.175 | 0
8188 | TORONTO BUTTONVILLE A | 12 | 7 | 4 | -6 | 24 | 0
8188 | TORONTO BUTTONVILLE A | 12 | 8 | 4 | -6 | 24 | 0
8189 | TORONTO BUTTONVILLE A | 12 | 7 | 5 | -5.8 | 23.8 | 0
8189 | TORONTO BUTTONVILLE A | 12 | 8 | 5 | -6.3 | 24.3 | 0
8190 | TORONTO BUTTONVILLE A | 12 | 7 | 6 | -5.8 | 23.8 | 0
8190 | TORONTO BUTTONVILLE A | 12 | 8 | 6 | -6.65 | 24.65 | 0
8191 | TORONTO BUTTONVILLE A | 12 | 7 | 7 | -5.8 | 23.8 | 0
8191 | TORONTO BUTTONVILLE A | 12 | 8 | 7 | -5.775 | 23.775 | 0
8192 | TORONTO BUTTONVILLE A | 12 | 7 | 8 | -6.1 | 24.1 | 0
8192 | TORONTO BUTTONVILLE A | 12 | 8 | 8 | -4.45 | 22.45 | 0
8193 | TORONTO BUTTONVILLE A | 12 | 7 | 9 | -5.5 | 23.5 | 0
8193 | TORONTO BUTTONVILLE A | 12 | 8 | 9 | -4.35 | 22.35 | 0
8194 | TORONTO BUTTONVILLE A | 12 | 7 | 10 | -4.2 | 22.2 | 0
8194 | TORONTO BUTTONVILLE A | 12 | 8 | 10 | -3.325 | 21.325 | 0
8195 | TORONTO BUTTONVILLE A | 12 | 7 | 11 | -2.5 | 20.5 | 0
8195 | TORONTO BUTTONVILLE A | 12 | 8 | 11 | -2.2 | 20.2 | 0
8196 | TORONTO BUTTONVILLE A | 12 | 7 | 12 | -2.2 | 20.2 | 0
8196 | TORONTO BUTTONVILLE A | 12 | 8 | 12 | -1.025 | 19.025 | 0
8197 | TORONTO BUTTONVILLE A | 12 | 7 | 13 | -1.9 | 19.9 | 0
8197 | TORONTO BUTTONVILLE A | 12 | 8 | 13 | -0.45 | 18.45 | 0
8198 | TORONTO BUTTONVILLE A | 12 | 7 | 14 | -2.1 | 20.1 | 0
8198 | TORONTO BUTTONVILLE A | 12 | 8 | 14 | 0.2 | 17.8 | 0
8199 | TORONTO BUTTONVILLE A | 12 | 7 | 15 | -2.8 | 20.8 | 0
8199 | TORONTO BUTTONVILLE A | 12 | 8 | 15 | 0.475 | 17.525 | 0
8200 | TORONTO BUTTONVILLE A | 12 | 7 | 16 | -4 | 22 | 0
8200 | TORONTO BUTTONVILLE A | 12 | 8 | 16 | 0.475 | 17.525 | 0
8201 | TORONTO BUTTONVILLE A | 12 | 7 | 17 | -3.9 | 21.9 | 0
8201 | TORONTO BUTTONVILLE A | 12 | 8 | 17 | 0.275 | 17.725 | 0
8202 | TORONTO BUTTONVILLE A | 12 | 7 | 18 | -4 | 22 | 0
8202 | TORONTO BUTTONVILLE A | 12 | 8 | 18 | 0.025 | 17.975 | 0
8203 | TORONTO BUTTONVILLE A | 12 | 7 | 19 | -4.2 | 22.2 | 0
8203 | TORONTO BUTTONVILLE A | 12 | 8 | 19 | -0.225 | 18.225 | 0
8204 | TORONTO BUTTONVILLE A | 12 | 7 | 20 | -4 | 22 | 0
8204 | TORONTO BUTTONVILLE A | 12 | 8 | 20 | -0.55 | 18.55 | 0
8205 | TORONTO BUTTONVILLE A | 12 | 7 | 21 | -4.2 | 22.2 | 0
8205 | TORONTO BUTTONVILLE A | 12 | 8 | 21 | -0.7 | 18.7 | 0
8206 | TORONTO BUTTONVILLE A | 12 | 7 | 22 | -4.6 | 22.6 | 0
8206 | TORONTO BUTTONVILLE A | 12 | 8 | 22 | -0.525 | 18.525 | 0
8207 | TORONTO BUTTONVILLE A | 12 | 7 | 23 | -4.8 | 22.8 | 0
8207 | TORONTO BUTTONVILLE A | 12 | 8 | 23 | -0.875 | 18.875 | 0
8208 | TORONTO BUTTONVILLE A | 12 | 7 | 24 | -5.2 | 23.2 | 0
8208 | TORONTO BUTTONVILLE A | 12 | 8 | 24 | -0.825 | 18.825 | 0
8209 | TORONTO BUTTONVILLE A | 12 | 8 | 1 | -5.4 | 23.4 | 0
8209 | TORONTO BUTTONVILLE A | 12 | 9 | 1 | -0.725 | 18.725 | 0
8210 | TORONTO BUTTONVILLE A | 12 | 8 | 2 | -5.8 | 23.8 | 0
8210 | TORONTO BUTTONVILLE A | 12 | 9 | 2 | -1.05 | 19.05 | 0
8211 | TORONTO BUTTONVILLE A | 12 | 8 | 3 | -6.1 | 24.1 | 0
8211 | TORONTO BUTTONVILLE A | 12 | 9 | 3 | -0.8 | 18.8 | 0
8212 | TORONTO BUTTONVILLE A | 12 | 8 | 4 | -6.4 | 24.4 | 0
8212 | TORONTO BUTTONVILLE A | 12 | 9 | 4 | -1.175 | 19.175 | 0
8213 | TORONTO BUTTONVILLE A | 12 | 8 | 5 | -6.3 | 24.3 | 0
8213 | TORONTO BUTTONVILLE A | 12 | 9 | 5 | -1.275 | 19.275 | 0
8214 | TORONTO BUTTONVILLE A | 12 | 8 | 6 | -6.7 | 24.7 | 0
8214 | TORONTO BUTTONVILLE A | 12 | 9 | 6 | -1.725 | 19.725 | 0
8215 | TORONTO BUTTONVILLE A | 12 | 8 | 7 | -7.3 | 25.3 | 0
8215 | TORONTO BUTTONVILLE A | 12 | 9 | 7 | -2.525 | 20.525 | 0
8216 | TORONTO BUTTONVILLE A | 12 | 8 | 8 | -7.4 | 25.4 | 0
8216 | TORONTO BUTTONVILLE A | 12 | 9 | 8 | -2.475 | 20.475 | 0
8217 | TORONTO BUTTONVILLE A | 12 | 8 | 9 | -7.4 | 25.4 | 0
8217 | TORONTO BUTTONVILLE A | 12 | 9 | 9 | -2.8 | 20.8 | 0
8218 | TORONTO BUTTONVILLE A | 12 | 8 | 10 | -5.6 | 23.6 | 0
8218 | TORONTO BUTTONVILLE A | 12 | 9 | 10 | -1.475 | 19.475 | 0
8219 | TORONTO BUTTONVILLE A | 12 | 8 | 11 | -3.1 | 21.1 | 0
8219 | TORONTO BUTTONVILLE A | 12 | 9 | 11 | -0.9 | 18.9 | 0
8220 | TORONTO BUTTONVILLE A | 12 | 8 | 12 | -1.4 | 19.4 | 0
8220 | TORONTO BUTTONVILLE A | 12 | 9 | 12 | -0.025 | 18.025 | 0
8221 | TORONTO BUTTONVILLE A | 12 | 8 | 13 | -0.6 | 18.6 | 0
8221 | TORONTO BUTTONVILLE A | 12 | 9 | 13 | 0.25 | 17.75 | 0
8222 | TORONTO BUTTONVILLE A | 12 | 8 | 14 | -0.5 | 18.5 | 0
8222 | TORONTO BUTTONVILLE A | 12 | 9 | 14 | 0.45 | 17.55 | 0
8223 | TORONTO BUTTONVILLE A | 12 | 8 | 15 | 0.5 | 17.5 | 0
8223 | TORONTO BUTTONVILLE A | 12 | 9 | 15 | 0.625 | 17.375 | 0
8224 | TORONTO BUTTONVILLE A | 12 | 8 | 16 | 0.5 | 17.5 | 0
8224 | TORONTO BUTTONVILLE A | 12 | 9 | 16 | 0.4 | 17.6 | 0
8225 | TORONTO BUTTONVILLE A | 12 | 8 | 17 | 0.4 | 17.6 | 0
8225 | TORONTO BUTTONVILLE A | 12 | 9 | 17 | 0.2 | 17.8 | 0
8226 | TORONTO BUTTONVILLE A | 12 | 8 | 18 | 0.1 | 17.9 | 0
8226 | TORONTO BUTTONVILLE A | 12 | 9 | 18 | 0.1 | 17.9 | 0
8227 | TORONTO BUTTONVILLE A | 12 | 8 | 19 | 0.2 | 17.8 | 0
8227 | TORONTO BUTTONVILLE A | 12 | 9 | 19 | 0.625 | 17.375 | 0
8228 | TORONTO BUTTONVILLE A | 12 | 8 | 20 | 1 | 17 | 0
8228 | TORONTO BUTTONVILLE A | 12 | 9 | 20 | 1.025 | 16.975 | 0
8229 | TORONTO BUTTONVILLE A | 12 | 8 | 21 | 1 | 17 | 0
8229 | TORONTO BUTTONVILLE A | 12 | 9 | 21 | 1.125 | 16.875 | 0
8230 | TORONTO BUTTONVILLE A | 12 | 8 | 22 | 1 | 17 | 0
8230 | TORONTO BUTTONVILLE A | 12 | 9 | 22 | 0.95 | 17.05 | 0
8231 | TORONTO BUTTONVILLE A | 12 | 8 | 23 | 0.6 | 17.4 | 0
8231 | TORONTO BUTTONVILLE A | 12 | 9 | 23 | 0.975 | 17.025 | 0
8232 | TORONTO BUTTONVILLE A | 12 | 8 | 24 | 0.9 | 17.1 | 0
8232 | TORONTO BUTTONVILLE A | 12 | 9 | 24 | 1.125 | 16.875 | 0
8233 | TORONTO BUTTONVILLE A | 12 | 9 | 1 | 1.2 | 16.8 | 0
8233 | TORONTO BUTTONVILLE A | 12 | 10 | 1 | 1.325 | 16.675 | 0
8234 | TORONTO BUTTONVILLE A | 12 | 9 | 2 | 1.2 | 16.8 | 0
8234 | TORONTO BUTTONVILLE A | 12 | 10 | 2 | 1.5 | 16.5 | 0
8235 | TORONTO BUTTONVILLE A | 12 | 9 | 3 | 1.2 | 16.8 | 0
8235 | TORONTO BUTTONVILLE A | 12 | 10 | 3 | 1.9 | 16.1 | 0
8236 | TORONTO BUTTONVILLE A | 12 | 9 | 4 | -0.2 | 18.2 | 0
8236 | TORONTO BUTTONVILLE A | 12 | 10 | 4 | 1.425 | 16.575 | 0
8237 | TORONTO BUTTONVILLE A | 12 | 9 | 5 | -0.2 | 18.2 | 0
8237 | TORONTO BUTTONVILLE A | 12 | 10 | 5 | 0.95 | 17.05 | 0
8238 | TORONTO BUTTONVILLE A | 12 | 9 | 6 | -0.1 | 18.1 | 0
8238 | TORONTO BUTTONVILLE A | 12 | 10 | 6 | 0.2 | 17.8 | 0
8239 | TORONTO BUTTONVILLE A | 12 | 9 | 7 | -0.1 | 18.1 | 0
8239 | TORONTO BUTTONVILLE A | 12 | 10 | 7 | -0.4 | 18.4 | 0
8240 | TORONTO BUTTONVILLE A | 12 | 9 | 8 | 0.1 | 17.9 | 0
8240 | TORONTO BUTTONVILLE A | 12 | 10 | 8 | -0.525 | 18.525 | 0
8241 | TORONTO BUTTONVILLE A | 12 | 9 | 9 | 0.2 | 17.8 | 0
8241 | TORONTO BUTTONVILLE A | 12 | 10 | 9 | -0.75 | 18.75 | 0
8242 | TORONTO BUTTONVILLE A | 12 | 9 | 10 | 0.6 | 17.4 | 0
8242 | TORONTO BUTTONVILLE A | 12 | 10 | 10 | -0.35 | 18.35 | 0
8243 | TORONTO BUTTONVILLE A | 12 | 9 | 11 | 1.1 | 16.9 | 0
8243 | TORONTO BUTTONVILLE A | 12 | 10 | 11 | 0.025 | 17.975 | 0
8244 | TORONTO BUTTONVILLE A | 12 | 9 | 12 | 1.4 | 16.6 | 0
8244 | TORONTO BUTTONVILLE A | 12 | 10 | 12 | 0.3 | 17.7 | 0
8245 | TORONTO BUTTONVILLE A | 12 | 9 | 13 | 1.7 | 16.3 | 0
8245 | TORONTO BUTTONVILLE A | 12 | 10 | 13 | 0.3 | 17.7 | 0
8246 | TORONTO BUTTONVILLE A | 12 | 9 | 14 | 2 | 16 | 0
8246 | TORONTO BUTTONVILLE A | 12 | 10 | 14 | 0.65 | 17.35 | 0
8247 | TORONTO BUTTONVILLE A | 12 | 9 | 15 | 2.4 | 15.6 | 0
8247 | TORONTO BUTTONVILLE A | 12 | 10 | 15 | 0.6 | 17.4 | 0
8248 | TORONTO BUTTONVILLE A | 12 | 9 | 16 | 3.8 | 14.2 | 0
8248 | TORONTO BUTTONVILLE A | 12 | 10 | 16 | 0.35 | 17.65 | 0
8249 | TORONTO BUTTONVILLE A | 12 | 9 | 17 | 3.7 | 14.3 | 0
8249 | TORONTO BUTTONVILLE A | 12 | 10 | 17 | -0.2 | 18.2 | 0
8250 | TORONTO BUTTONVILLE A | 12 | 9 | 18 | 3.1 | 14.9 | 0
8250 | TORONTO BUTTONVILLE A | 12 | 10 | 18 | -0.85 | 18.85 | 0
8251 | TORONTO BUTTONVILLE A | 12 | 9 | 19 | 3 | 15 | 0
8251 | TORONTO BUTTONVILLE A | 12 | 10 | 19 | -1.85 | 19.85 | 0
8252 | TORONTO BUTTONVILLE A | 12 | 9 | 20 | 3 | 15 | 0
8252 | TORONTO BUTTONVILLE A | 12 | 10 | 20 | -2 | 20 | 0
8253 | TORONTO BUTTONVILLE A | 12 | 9 | 21 | 2.8 | 15.2 | 0
8253 | TORONTO BUTTONVILLE A | 12 | 10 | 21 | -2.025 | 20.025 | 0
8254 | TORONTO BUTTONVILLE A | 12 | 9 | 22 | 2.5 | 15.5 | 0
8254 | TORONTO BUTTONVILLE A | 12 | 10 | 22 | -2.025 | 20.025 | 0
8255 | TORONTO BUTTONVILLE A | 12 | 9 | 23 | 2.9 | 15.1 | 0
8255 | TORONTO BUTTONVILLE A | 12 | 10 | 23 | -1.85 | 19.85 | 0
8256 | TORONTO BUTTONVILLE A | 12 | 9 | 24 | 3 | 15 | 0
8256 | TORONTO BUTTONVILLE A | 12 | 10 | 24 | -2.225 | 20.225 | 0
8257 | TORONTO BUTTONVILLE A | 12 | 10 | 1 | 3.1 | 14.9 | 0
8257 | TORONTO BUTTONVILLE A | 12 | 11 | 1 | -2.425 | 20.425 | 0
8258 | TORONTO BUTTONVILLE A | 12 | 10 | 2 | 2.9 | 15.1 | 0
8258 | TORONTO BUTTONVILLE A | 12 | 11 | 2 | -2.55 | 20.55 | 0
8259 | TORONTO BUTTONVILLE A | 12 | 10 | 3 | 2.8 | 15.2 | 0
8259 | TORONTO BUTTONVILLE A | 12 | 11 | 3 | -2.75 | 20.75 | 0
8260 | TORONTO BUTTONVILLE A | 12 | 10 | 4 | 2.7 | 15.3 | 0
8260 | TORONTO BUTTONVILLE A | 12 | 11 | 4 | -2.8 | 20.8 | 0
8261 | TORONTO BUTTONVILLE A | 12 | 10 | 5 | 2.2 | 15.8 | 0
8261 | TORONTO BUTTONVILLE A | 12 | 11 | 5 | -2.95 | 20.95 | 0
8262 | TORONTO BUTTONVILLE A | 12 | 10 | 6 | 2 | 16 | 0
8262 | TORONTO BUTTONVILLE A | 12 | 11 | 6 | -3.15 | 21.15 | 0
8263 | TORONTO BUTTONVILLE A | 12 | 10 | 7 | 1.4 | 16.6 | 0
8263 | TORONTO BUTTONVILLE A | 12 | 11 | 7 | -3.05 | 21.05 | 0
8264 | TORONTO BUTTONVILLE A | 12 | 10 | 8 | 1.7 | 16.3 | 0
8264 | TORONTO BUTTONVILLE A | 12 | 11 | 8 | -2.95 | 20.95 | 0
8265 | TORONTO BUTTONVILLE A | 12 | 10 | 9 | 2.1 | 15.9 | 0
8265 | TORONTO BUTTONVILLE A | 12 | 11 | 9 | -2.825 | 20.825 | 0
8266 | TORONTO BUTTONVILLE A | 12 | 10 | 10 | 3.2 | 14.8 | 0
8266 | TORONTO BUTTONVILLE A | 12 | 11 | 10 | -2.375 | 20.375 | 0
8267 | TORONTO BUTTONVILLE A | 12 | 10 | 11 | 3.7 | 14.3 | 0
8267 | TORONTO BUTTONVILLE A | 12 | 11 | 11 | -1.075 | 19.075 | 0
8268 | TORONTO BUTTONVILLE A | 12 | 10 | 12 | 4 | 14 | 0
8268 | TORONTO BUTTONVILLE A | 12 | 11 | 12 | -0.05 | 18.05 | 0
8269 | TORONTO BUTTONVILLE A | 12 | 10 | 13 | 4.2 | 13.8 | 0
8269 | TORONTO BUTTONVILLE A | 12 | 11 | 13 | 0.75 | 17.25 | 0
8270 | TORONTO BUTTONVILLE A | 12 | 10 | 14 | 4.5 | 13.5 | 0
8270 | TORONTO BUTTONVILLE A | 12 | 11 | 14 | 1.375 | 16.625 | 0
8271 | TORONTO BUTTONVILLE A | 12 | 10 | 15 | 4.4 | 13.6 | 0
8271 | TORONTO BUTTONVILLE A | 12 | 11 | 15 | 1.625 | 16.375 | 0
8272 | TORONTO BUTTONVILLE A | 12 | 10 | 16 | 4.3 | 13.7 | 0
8272 | TORONTO BUTTONVILLE A | 12 | 11 | 16 | 1.55 | 16.45 | 0
8273 | TORONTO BUTTONVILLE A | 12 | 10 | 17 | 4.4 | 13.6 | 0
8273 | TORONTO BUTTONVILLE A | 12 | 11 | 17 | -0.2 | 18.2 | 0
8274 | TORONTO BUTTONVILLE A | 12 | 10 | 18 | 3.8 | 14.2 | 0
8274 | TORONTO BUTTONVILLE A | 12 | 11 | 18 | -1.875 | 19.875 | 0
8275 | TORONTO BUTTONVILLE A | 12 | 10 | 19 | 3.5 | 14.5 | 0
8275 | TORONTO BUTTONVILLE A | 12 | 11 | 19 | -2.425 | 20.425 | 0
8276 | TORONTO BUTTONVILLE A | 12 | 10 | 20 | 3.2 | 14.8 | 0
8276 | TORONTO BUTTONVILLE A | 12 | 11 | 20 | -2.6 | 20.6 | 0
8277 | TORONTO BUTTONVILLE A | 12 | 10 | 21 | 3.1 | 14.9 | 0
8277 | TORONTO BUTTONVILLE A | 12 | 11 | 21 | -2.375 | 20.375 | 0
8278 | TORONTO BUTTONVILLE A | 12 | 10 | 22 | 2.2 | 15.8 | 0
8278 | TORONTO BUTTONVILLE A | 12 | 11 | 22 | -2.1 | 20.1 | 0
8279 | TORONTO BUTTONVILLE A | 12 | 10 | 23 | 0.9 | 17.1 | 0
8279 | TORONTO BUTTONVILLE A | 12 | 11 | 23 | -2.775 | 20.775 | 0
8280 | TORONTO BUTTONVILLE A | 12 | 10 | 24 | -0.4 | 18.4 | 0
8280 | TORONTO BUTTONVILLE A | 12 | 11 | 24 | -2.675 | 20.675 | 0
8281 | TORONTO BUTTONVILLE A | 12 | 11 | 1 | -1.6 | 19.6 | 0
8281 | TORONTO BUTTONVILLE A | 12 | 12 | 1 | -2.975 | 20.975 | 0
8282 | TORONTO BUTTONVILLE A | 12 | 11 | 2 | -0.9 | 18.9 | 0
8282 | TORONTO BUTTONVILLE A | 12 | 12 | 2 | -2.9 | 20.9 | 0
8283 | TORONTO BUTTONVILLE A | 12 | 11 | 3 | -0.4 | 18.4 | 0
8283 | TORONTO BUTTONVILLE A | 12 | 12 | 3 | -3.2 | 21.2 | 0
8284 | TORONTO BUTTONVILLE A | 12 | 11 | 4 | -1.2 | 19.2 | 0
8284 | TORONTO BUTTONVILLE A | 12 | 12 | 4 | -3.45 | 21.45 | 0
8285 | TORONTO BUTTONVILLE A | 12 | 11 | 5 | -1.2 | 19.2 | 0
8285 | TORONTO BUTTONVILLE A | 12 | 12 | 5 | -3.425 | 21.425 | 0
8286 | TORONTO BUTTONVILLE A | 12 | 11 | 6 | -1.5 | 19.5 | 0
8286 | TORONTO BUTTONVILLE A | 12 | 12 | 6 | -3.725 | 21.725 | 0
8287 | TORONTO BUTTONVILLE A | 12 | 11 | 7 | -1.2 | 19.2 | 0
8287 | TORONTO BUTTONVILLE A | 12 | 12 | 7 | -3.875 | 21.875 | 0
8288 | TORONTO BUTTONVILLE A | 12 | 11 | 8 | -0.5 | 18.5 | 0
8288 | TORONTO BUTTONVILLE A | 12 | 12 | 8 | -4.175 | 22.175 | 0
8289 | TORONTO BUTTONVILLE A | 12 | 11 | 9 | -0.6 | 18.6 | 0
8289 | TORONTO BUTTONVILLE A | 12 | 12 | 9 | -4.225 | 22.225 | 0
8290 | TORONTO BUTTONVILLE A | 12 | 11 | 10 | -0.1 | 18.1 | 0
8290 | TORONTO BUTTONVILLE A | 12 | 12 | 10 | -3.025 | 21.025 | 0
8291 | TORONTO BUTTONVILLE A | 12 | 11 | 11 | 1.4 | 16.6 | 0
8291 | TORONTO BUTTONVILLE A | 12 | 12 | 11 | -2.3 | 20.3 | 0
8292 | TORONTO BUTTONVILLE A | 12 | 11 | 12 | 3.1 | 14.9 | 0
8292 | TORONTO BUTTONVILLE A | 12 | 12 | 12 | -2.075 | 20.075 | 0
8293 | TORONTO BUTTONVILLE A | 12 | 11 | 13 | 5.8 | 12.2 | 0
8293 | TORONTO BUTTONVILLE A | 12 | 12 | 13 | -1.525 | 19.525 | 0
8294 | TORONTO BUTTONVILLE A | 12 | 11 | 14 | 7.2 | 10.8 | 0
8294 | TORONTO BUTTONVILLE A | 12 | 12 | 14 | -1.075 | 19.075 | 0
8295 | TORONTO BUTTONVILLE A | 12 | 11 | 15 | 7.5 | 10.5 | 0
8295 | TORONTO BUTTONVILLE A | 12 | 12 | 15 | -1.025 | 19.025 | 0
8296 | TORONTO BUTTONVILLE A | 12 | 11 | 16 | 6.7 | 11.3 | 0
8296 | TORONTO BUTTONVILLE A | 12 | 12 | 16 | -0.825 | 18.825 | 0
8297 | TORONTO BUTTONVILLE A | 12 | 11 | 17 | 5.8 | 12.2 | 0
8297 | TORONTO BUTTONVILLE A | 12 | 12 | 17 | -1.4 | 19.4 | 0
8298 | TORONTO BUTTONVILLE A | 12 | 11 | 18 | 4.9 | 13.1 | 0
8298 | TORONTO BUTTONVILLE A | 12 | 12 | 18 | -1.55 | 19.55 | 0
8299 | TORONTO BUTTONVILLE A | 12 | 11 | 19 | 4.4 | 13.6 | 0
8299 | TORONTO BUTTONVILLE A | 12 | 12 | 19 | -1.775 | 19.775 | 0
8300 | TORONTO BUTTONVILLE A | 12 | 11 | 20 | 4.5 | 13.5 | 0
8300 | TORONTO BUTTONVILLE A | 12 | 12 | 20 | -1.925 | 19.925 | 0
8301 | TORONTO BUTTONVILLE A | 12 | 11 | 21 | 3.5 | 14.5 | 0
8301 | TORONTO BUTTONVILLE A | 12 | 12 | 21 | -2.175 | 20.175 | 0
8302 | TORONTO BUTTONVILLE A | 12 | 11 | 22 | 3.1 | 14.9 | 0
8302 | TORONTO BUTTONVILLE A | 12 | 12 | 22 | -2.5 | 20.5 | 0
8303 | TORONTO BUTTONVILLE A | 12 | 11 | 23 | 3 | 15 | 0
8303 | TORONTO BUTTONVILLE A | 12 | 12 | 23 | -2.55 | 20.55 | 0
8304 | TORONTO BUTTONVILLE A | 12 | 11 | 24 | 2.9 | 15.1 | 0
8304 | TORONTO BUTTONVILLE A | 12 | 12 | 24 | -2.8 | 20.8 | 0
8305 | TORONTO BUTTONVILLE A | 12 | 12 | 1 | 2.9 | 15.1 | 0
8305 | TORONTO BUTTONVILLE A | 12 | 13 | 1 | -2.975 | 20.975 | 0
8306 | TORONTO BUTTONVILLE A | 12 | 12 | 2 | 3 | 15 | 0
8306 | TORONTO BUTTONVILLE A | 12 | 13 | 2 | -3.2 | 21.2 | 0
8307 | TORONTO BUTTONVILLE A | 12 | 12 | 3 | 2.7 | 15.3 | 0
8307 | TORONTO BUTTONVILLE A | 12 | 13 | 3 | -3.55 | 21.55 | 0
8308 | TORONTO BUTTONVILLE A | 12 | 12 | 4 | 2.9 | 15.1 | 0
8308 | TORONTO BUTTONVILLE A | 12 | 13 | 4 | -3.9 | 21.9 | 0
8309 | TORONTO BUTTONVILLE A | 12 | 12 | 5 | 2.8 | 15.2 | 0
8309 | TORONTO BUTTONVILLE A | 12 | 13 | 5 | -4.025 | 22.025 | 0
8310 | TORONTO BUTTONVILLE A | 12 | 12 | 6 | 2.6 | 15.4 | 0
8310 | TORONTO BUTTONVILLE A | 12 | 13 | 6 | -4.45 | 22.45 | 0
8311 | TORONTO BUTTONVILLE A | 12 | 12 | 7 | 2.5 | 15.5 | 0
8311 | TORONTO BUTTONVILLE A | 12 | 13 | 7 | -4.6 | 22.6 | 0
8312 | TORONTO BUTTONVILLE A | 12 | 12 | 8 | 2.5 | 15.5 | 0
8312 | TORONTO BUTTONVILLE A | 12 | 13 | 8 | -4.7 | 22.7 | 0
8313 | TORONTO BUTTONVILLE A | 12 | 12 | 9 | 2.9 | 15.1 | 0
8313 | TORONTO BUTTONVILLE A | 12 | 13 | 9 | -4.475 | 22.475 | 0
8314 | TORONTO BUTTONVILLE A | 12 | 12 | 10 | 3 | 15 | 0
8314 | TORONTO BUTTONVILLE A | 12 | 13 | 10 | -3.5 | 21.5 | 0
8315 | TORONTO BUTTONVILLE A | 12 | 12 | 11 | 2.9 | 15.1 | 0
8315 | TORONTO BUTTONVILLE A | 12 | 13 | 11 | -1.575 | 19.575 | 0
8316 | TORONTO BUTTONVILLE A | 12 | 12 | 12 | 3.6 | 14.4 | 0
8316 | TORONTO BUTTONVILLE A | 12 | 13 | 12 | -0.45 | 18.45 | 0
8317 | TORONTO BUTTONVILLE A | 12 | 12 | 13 | 3.3 | 14.7 | 0
8317 | TORONTO BUTTONVILLE A | 12 | 13 | 13 | 0.275 | 17.725 | 0
8318 | TORONTO BUTTONVILLE A | 12 | 12 | 14 | 3.4 | 14.6 | 0
8318 | TORONTO BUTTONVILLE A | 12 | 13 | 14 | 1.175 | 16.825 | 0
8319 | TORONTO BUTTONVILLE A | 12 | 12 | 15 | 3.5 | 14.5 | 0
8319 | TORONTO BUTTONVILLE A | 12 | 13 | 15 | 1.25 | 16.75 | 0
8320 | TORONTO BUTTONVILLE A | 12 | 12 | 16 | 3.6 | 14.4 | 0
8320 | TORONTO BUTTONVILLE A | 12 | 13 | 16 | 1.15 | 16.85 | 0
8321 | TORONTO BUTTONVILLE A | 12 | 12 | 17 | 3.9 | 14.1 | 0
8321 | TORONTO BUTTONVILLE A | 12 | 13 | 17 | 0.525 | 17.475 | 0
8322 | TORONTO BUTTONVILLE A | 12 | 12 | 18 | 4.8 | 13.2 | 0
8322 | TORONTO BUTTONVILLE A | 12 | 13 | 18 | -0.1 | 18.1 | 0
8323 | TORONTO BUTTONVILLE A | 12 | 12 | 19 | 5.6 | 12.4 | 0
8323 | TORONTO BUTTONVILLE A | 12 | 13 | 19 | -0.5 | 18.5 | 0
8324 | TORONTO BUTTONVILLE A | 12 | 12 | 20 | 5.7 | 12.3 | 0
8324 | TORONTO BUTTONVILLE A | 12 | 13 | 20 | -0.85 | 18.85 | 0
8325 | TORONTO BUTTONVILLE A | 12 | 12 | 21 | 5.6 | 12.4 | 0
8325 | TORONTO BUTTONVILLE A | 12 | 13 | 21 | -0.825 | 18.825 | 0
8326 | TORONTO BUTTONVILLE A | 12 | 12 | 22 | 7 | 11 | 0
8326 | TORONTO BUTTONVILLE A | 12 | 13 | 22 | -1.1 | 19.1 | 0
8327 | TORONTO BUTTONVILLE A | 12 | 12 | 23 | 7.5 | 10.5 | 0
8327 | TORONTO BUTTONVILLE A | 12 | 13 | 23 | -1.375 | 19.375 | 0
8328 | TORONTO BUTTONVILLE A | 12 | 12 | 24 | 8.2 | 9.8 | 0
8328 | TORONTO BUTTONVILLE A | 12 | 13 | 24 | -1.4 | 19.4 | 0
8329 | TORONTO BUTTONVILLE A | 12 | 13 | 1 | 6.8 | 11.2 | 0
8329 | TORONTO BUTTONVILLE A | 12 | 14 | 1 | -1.75 | 19.75 | 0
8330 | TORONTO BUTTONVILLE A | 12 | 13 | 2 | 6.1 | 11.9 | 0
8330 | TORONTO BUTTONVILLE A | 12 | 14 | 2 | -2.25 | 20.25 | 0
8331 | TORONTO BUTTONVILLE A | 12 | 13 | 3 | 5 | 13 | 0
8331 | TORONTO BUTTONVILLE A | 12 | 14 | 3 | -2.7 | 20.7 | 0
8332 | TORONTO BUTTONVILLE A | 12 | 13 | 4 | 3.8 | 14.2 | 0
8332 | TORONTO BUTTONVILLE A | 12 | 14 | 4 | -3.15 | 21.15 | 0
8333 | TORONTO BUTTONVILLE A | 12 | 13 | 5 | 1.9 | 16.1 | 0
8333 | TORONTO BUTTONVILLE A | 12 | 14 | 5 | -3.4 | 21.4 | 0
8334 | TORONTO BUTTONVILLE A | 12 | 13 | 6 | 1.2 | 16.8 | 0
8334 | TORONTO BUTTONVILLE A | 12 | 14 | 6 | -3.3 | 21.3 | 0
8335 | TORONTO BUTTONVILLE A | 12 | 13 | 7 | 0.8 | 17.2 | 0
8335 | TORONTO BUTTONVILLE A | 12 | 14 | 7 | -3.5 | 21.5 | 0
8336 | TORONTO BUTTONVILLE A | 12 | 13 | 8 | 0.3 | 17.7 | 0
8336 | TORONTO BUTTONVILLE A | 12 | 14 | 8 | -3.75 | 21.75 | 0
8337 | TORONTO BUTTONVILLE A | 12 | 13 | 9 | -0.3 | 18.3 | 0
8337 | TORONTO BUTTONVILLE A | 12 | 14 | 9 | -3.45 | 21.45 | 0
8338 | TORONTO BUTTONVILLE A | 12 | 13 | 10 | -0.9 | 18.9 | 0
8338 | TORONTO BUTTONVILLE A | 12 | 14 | 10 | -2.75 | 20.75 | 0
8339 | TORONTO BUTTONVILLE A | 12 | 13 | 11 | -1 | 19 | 0
8339 | TORONTO BUTTONVILLE A | 12 | 14 | 11 | -2.075 | 20.075 | 0
8340 | TORONTO BUTTONVILLE A | 12 | 13 | 12 | -1 | 19 | 0
8340 | TORONTO BUTTONVILLE A | 12 | 14 | 12 | -1.525 | 19.525 | 0
8341 | TORONTO BUTTONVILLE A | 12 | 13 | 13 | -0.6 | 18.6 | 0
8341 | TORONTO BUTTONVILLE A | 12 | 14 | 13 | -0.6 | 18.6 | 0
8342 | TORONTO BUTTONVILLE A | 12 | 13 | 14 | -0.1 | 18.1 | 0
8342 | TORONTO BUTTONVILLE A | 12 | 14 | 14 | 0.125 | 17.875 | 0
8343 | TORONTO BUTTONVILLE A | 12 | 13 | 15 | 0 | 18 | 0
8343 | TORONTO BUTTONVILLE A | 12 | 14 | 15 | 0.55 | 17.45 | 0
8344 | TORONTO BUTTONVILLE A | 12 | 13 | 16 | 0.4 | 17.6 | 0
8344 | TORONTO BUTTONVILLE A | 12 | 14 | 16 | 0.775 | 17.225 | 0
8345 | TORONTO BUTTONVILLE A | 12 | 13 | 17 | 0.3 | 17.7 | 0
8345 | TORONTO BUTTONVILLE A | 12 | 14 | 17 | 0.4 | 17.6 | 0
8346 | TORONTO BUTTONVILLE A | 12 | 13 | 18 | 0.5 | 17.5 | 0
8346 | TORONTO BUTTONVILLE A | 12 | 14 | 18 | 0.075 | 17.925 | 0
8347 | TORONTO BUTTONVILLE A | 12 | 13 | 19 | 0.4 | 17.6 | 0
8347 | TORONTO BUTTONVILLE A | 12 | 14 | 19 | -0.35 | 18.35 | 0
8348 | TORONTO BUTTONVILLE A | 12 | 13 | 20 | 0.4 | 17.6 | 0
8348 | TORONTO BUTTONVILLE A | 12 | 14 | 20 | -0.35 | 18.35 | 0
8349 | TORONTO BUTTONVILLE A | 12 | 13 | 21 | 0.4 | 17.6 | 0
8349 | TORONTO BUTTONVILLE A | 12 | 14 | 21 | -0.55 | 18.55 | 0
8350 | TORONTO BUTTONVILLE A | 12 | 13 | 22 | 0.1 | 17.9 | 0
8350 | TORONTO BUTTONVILLE A | 12 | 14 | 22 | -0.9 | 18.9 | 0
8351 | TORONTO BUTTONVILLE A | 12 | 13 | 23 | 0.1 | 17.9 | 0
8351 | TORONTO BUTTONVILLE A | 12 | 14 | 23 | -0.9 | 18.9 | 0
8352 | TORONTO BUTTONVILLE A | 12 | 13 | 24 | 0.1 | 17.9 | 0
8352 | TORONTO BUTTONVILLE A | 12 | 14 | 24 | -0.55 | 18.55 | 0
8353 | TORONTO BUTTONVILLE A | 12 | 14 | 1 | -0.1 | 18.1 | 0
8353 | TORONTO BUTTONVILLE A | 12 | 15 | 1 | -1.05 | 19.05 | 0
8354 | TORONTO BUTTONVILLE A | 12 | 14 | 2 | -0.3 | 18.3 | 0
8354 | TORONTO BUTTONVILLE A | 12 | 15 | 2 | -1.55 | 19.55 | 0
8355 | TORONTO BUTTONVILLE A | 12 | 14 | 3 | -0.2 | 18.2 | 0
8355 | TORONTO BUTTONVILLE A | 12 | 15 | 3 | -1.6 | 19.6 | 0
8356 | TORONTO BUTTONVILLE A | 12 | 14 | 4 | -0.2 | 18.2 | 0
8356 | TORONTO BUTTONVILLE A | 12 | 15 | 4 | -2.25 | 20.25 | 0
8357 | TORONTO BUTTONVILLE A | 12 | 14 | 5 | -0.2 | 18.2 | 0
8357 | TORONTO BUTTONVILLE A | 12 | 15 | 5 | -2.05 | 20.05 | 0
8358 | TORONTO BUTTONVILLE A | 12 | 14 | 6 | -0.3 | 18.3 | 0
8358 | TORONTO BUTTONVILLE A | 12 | 15 | 6 | -2.3 | 20.3 | 0
8359 | TORONTO BUTTONVILLE A | 12 | 14 | 7 | -0.2 | 18.2 | 0
8359 | TORONTO BUTTONVILLE A | 12 | 15 | 7 | -1.875 | 19.875 | 0
8360 | TORONTO BUTTONVILLE A | 12 | 14 | 8 | -0.3 | 18.3 | 0
8360 | TORONTO BUTTONVILLE A | 12 | 15 | 8 | -1.625 | 19.625 | 0
8361 | TORONTO BUTTONVILLE A | 12 | 14 | 9 | 0 | 18 | 0
8361 | TORONTO BUTTONVILLE A | 12 | 15 | 9 | -1.3 | 19.3 | 0
8362 | TORONTO BUTTONVILLE A | 12 | 14 | 10 | 0 | 18 | 0
8362 | TORONTO BUTTONVILLE A | 12 | 15 | 10 | -1.075 | 19.075 | 0
8363 | TORONTO BUTTONVILLE A | 12 | 14 | 11 | 0.4 | 17.6 | 0
8363 | TORONTO BUTTONVILLE A | 12 | 15 | 11 | -0.65 | 18.65 | 0
8364 | TORONTO BUTTONVILLE A | 12 | 14 | 12 | 0.7 | 17.3 | 0
8364 | TORONTO BUTTONVILLE A | 12 | 15 | 12 | -0.275 | 18.275 | 0
8365 | TORONTO BUTTONVILLE A | 12 | 14 | 13 | 1 | 17 | 0
8365 | TORONTO BUTTONVILLE A | 12 | 15 | 13 | -0.05 | 18.05 | 0
8366 | TORONTO BUTTONVILLE A | 12 | 14 | 14 | 1 | 17 | 0
8366 | TORONTO BUTTONVILLE A | 12 | 15 | 14 | 0.025 | 17.975 | 0
8367 | TORONTO BUTTONVILLE A | 12 | 14 | 15 | 1 | 17 | 0
8367 | TORONTO BUTTONVILLE A | 12 | 15 | 15 | 0.125 | 17.875 | 0
8368 | TORONTO BUTTONVILLE A | 12 | 14 | 16 | 1.1 | 16.9 | 0
8368 | TORONTO BUTTONVILLE A | 12 | 15 | 16 | 0.15 | 17.85 | 0
8369 | TORONTO BUTTONVILLE A | 12 | 14 | 17 | 0.7 | 17.3 | 0
8369 | TORONTO BUTTONVILLE A | 12 | 15 | 17 | 0.125 | 17.875 | 0
8370 | TORONTO BUTTONVILLE A | 12 | 14 | 18 | -0.6 | 18.6 | 0
8370 | TORONTO BUTTONVILLE A | 12 | 15 | 18 | -0.25 | 18.25 | 0
8371 | TORONTO BUTTONVILLE A | 12 | 14 | 19 | -1 | 19 | 0
8371 | TORONTO BUTTONVILLE A | 12 | 15 | 19 | -0.4 | 18.4 | 0
8372 | TORONTO BUTTONVILLE A | 12 | 14 | 20 | -1.2 | 19.2 | 0
8372 | TORONTO BUTTONVILLE A | 12 | 15 | 20 | -0.5 | 18.5 | 0
8373 | TORONTO BUTTONVILLE A | 12 | 14 | 21 | -1.5 | 19.5 | 0
8373 | TORONTO BUTTONVILLE A | 12 | 15 | 21 | -0.5 | 18.5 | 0
8374 | TORONTO BUTTONVILLE A | 12 | 14 | 22 | -2 | 20 | 0
8374 | TORONTO BUTTONVILLE A | 12 | 15 | 22 | -0.675 | 18.675 | 0
8375 | TORONTO BUTTONVILLE A | 12 | 14 | 23 | -1.9 | 19.9 | 0
8375 | TORONTO BUTTONVILLE A | 12 | 15 | 23 | -0.675 | 18.675 | 0
8376 | TORONTO BUTTONVILLE A | 12 | 14 | 24 | -2.2 | 20.2 | 0
8376 | TORONTO BUTTONVILLE A | 12 | 15 | 24 | -0.2 | 18.2 | 0
8377 | TORONTO BUTTONVILLE A | 12 | 15 | 1 | -2.4 | 20.4 | 0
8377 | TORONTO BUTTONVILLE A | 12 | 16 | 1 | -0.4 | 18.4 | 0
8378 | TORONTO BUTTONVILLE A | 12 | 15 | 2 | -2.6 | 20.6 | 0
8378 | TORONTO BUTTONVILLE A | 12 | 16 | 2 | -0.225 | 18.225 | 0
8379 | TORONTO BUTTONVILLE A | 12 | 15 | 3 | -2.9 | 20.9 | 0
8379 | TORONTO BUTTONVILLE A | 12 | 16 | 3 | -0.175 | 18.175 | 0
8380 | TORONTO BUTTONVILLE A | 12 | 15 | 4 | -3.5 | 21.5 | 0
8380 | TORONTO BUTTONVILLE A | 12 | 16 | 4 | -0.55 | 18.55 | 0
8381 | TORONTO BUTTONVILLE A | 12 | 15 | 5 | -4.1 | 22.1 | 0
8381 | TORONTO BUTTONVILLE A | 12 | 16 | 5 | -0.6 | 18.6 | 0
8382 | TORONTO BUTTONVILLE A | 12 | 15 | 6 | -4.7 | 22.7 | 0
8382 | TORONTO BUTTONVILLE A | 12 | 16 | 6 | -0.025 | 18.025 | 0
8383 | TORONTO BUTTONVILLE A | 12 | 15 | 7 | -4.6 | 22.6 | 0
8383 | TORONTO BUTTONVILLE A | 12 | 16 | 7 | 0.15 | 17.85 | 0
8384 | TORONTO BUTTONVILLE A | 12 | 15 | 8 | -4.6 | 22.6 | 0
8384 | TORONTO BUTTONVILLE A | 12 | 16 | 8 | 0.225 | 17.775 | 0
8385 | TORONTO BUTTONVILLE A | 12 | 15 | 9 | -6 | 24 | 0
8385 | TORONTO BUTTONVILLE A | 12 | 16 | 9 | 0.475 | 17.525 | 0
8386 | TORONTO BUTTONVILLE A | 12 | 15 | 10 | -6.2 | 24.2 | 0
8386 | TORONTO BUTTONVILLE A | 12 | 16 | 10 | 0.95 | 17.05 | 0
8387 | TORONTO BUTTONVILLE A | 12 | 15 | 11 | -6.4 | 24.4 | 0
8387 | TORONTO BUTTONVILLE A | 12 | 16 | 11 | 1.25 | 16.75 | 0
8388 | TORONTO BUTTONVILLE A | 12 | 15 | 12 | -5.9 | 23.9 | 0
8388 | TORONTO BUTTONVILLE A | 12 | 16 | 12 | 1.85 | 16.15 | 0
8389 | TORONTO BUTTONVILLE A | 12 | 15 | 13 | -5.1 | 23.1 | 0
8389 | TORONTO BUTTONVILLE A | 12 | 16 | 13 | 2.725 | 15.275 | 0
8390 | TORONTO BUTTONVILLE A | 12 | 15 | 14 | -4.9 | 22.9 | 0
8390 | TORONTO BUTTONVILLE A | 12 | 16 | 14 | 3.3 | 14.7 | 0
8391 | TORONTO BUTTONVILLE A | 12 | 15 | 15 | -4.5 | 22.5 | 0
8391 | TORONTO BUTTONVILLE A | 12 | 16 | 15 | 3.775 | 14.225 | 0
8392 | TORONTO BUTTONVILLE A | 12 | 15 | 16 | -4.6 | 22.6 | 0
8392 | TORONTO BUTTONVILLE A | 12 | 16 | 16 | 3.325 | 14.675 | 0
8393 | TORONTO BUTTONVILLE A | 12 | 15 | 17 | -5.5 | 23.5 | 0
8393 | TORONTO BUTTONVILLE A | 12 | 16 | 17 | 2.9 | 15.1 | 0
8394 | TORONTO BUTTONVILLE A | 12 | 15 | 18 | -6.2 | 24.2 | 0
8394 | TORONTO BUTTONVILLE A | 12 | 16 | 18 | 1.775 | 16.225 | 0
8395 | TORONTO BUTTONVILLE A | 12 | 15 | 19 | -6.8 | 24.8 | 0
8395 | TORONTO BUTTONVILLE A | 12 | 16 | 19 | 1.15 | 16.85 | 0
8396 | TORONTO BUTTONVILLE A | 12 | 15 | 20 | -7 | 25 | 0
8396 | TORONTO BUTTONVILLE A | 12 | 16 | 20 | 0.775 | 17.225 | 0
8397 | TORONTO BUTTONVILLE A | 12 | 15 | 21 | -7.3 | 25.3 | 0
8397 | TORONTO BUTTONVILLE A | 12 | 16 | 21 | 0.075 | 17.925 | 0
8398 | TORONTO BUTTONVILLE A | 12 | 15 | 22 | -8 | 26 | 0
8398 | TORONTO BUTTONVILLE A | 12 | 16 | 22 | -0.825 | 18.825 | 0
8399 | TORONTO BUTTONVILLE A | 12 | 15 | 23 | -8.6 | 26.6 | 0
8399 | TORONTO BUTTONVILLE A | 12 | 16 | 23 | -1.45 | 19.45 | 0
8400 | TORONTO BUTTONVILLE A | 12 | 15 | 24 | -8.6 | 26.6 | 0
8400 | TORONTO BUTTONVILLE A | 12 | 16 | 24 | -2 | 20 | 0
8401 | TORONTO BUTTONVILLE A | 12 | 16 | 1 | -8.7 | 26.7 | 0
8401 | TORONTO BUTTONVILLE A | 12 | 17 | 1 | -2.35 | 20.35 | 0
8402 | TORONTO BUTTONVILLE A | 12 | 16 | 2 | -8.8 | 26.8 | 0
8402 | TORONTO BUTTONVILLE A | 12 | 17 | 2 | -2.775 | 20.775 | 0
8403 | TORONTO BUTTONVILLE A | 12 | 16 | 3 | -8.9 | 26.9 | 0
8403 | TORONTO BUTTONVILLE A | 12 | 17 | 3 | -3.15 | 21.15 | 0
8404 | TORONTO BUTTONVILLE A | 12 | 16 | 4 | -9 | 27 | 0
8404 | TORONTO BUTTONVILLE A | 12 | 17 | 4 | -3.225 | 21.225 | 0
8405 | TORONTO BUTTONVILLE A | 12 | 16 | 5 | -9.3 | 27.3 | 0
8405 | TORONTO BUTTONVILLE A | 12 | 17 | 5 | -3.1 | 21.1 | 0
8406 | TORONTO BUTTONVILLE A | 12 | 16 | 6 | -9.6 | 27.6 | 0
8406 | TORONTO BUTTONVILLE A | 12 | 17 | 6 | -3.675 | 21.675 | 0
8407 | TORONTO BUTTONVILLE A | 12 | 16 | 7 | -9.7 | 27.7 | 0
8407 | TORONTO BUTTONVILLE A | 12 | 17 | 7 | -4.1 | 22.1 | 0
8408 | TORONTO BUTTONVILLE A | 12 | 16 | 8 | -9.7 | 27.7 | 0
8408 | TORONTO BUTTONVILLE A | 12 | 17 | 8 | -4.1 | 22.1 | 0
8409 | TORONTO BUTTONVILLE A | 12 | 16 | 9 | -10.2 | 28.2 | 0
8409 | TORONTO BUTTONVILLE A | 12 | 17 | 9 | -3.925 | 21.925 | 0
8410 | TORONTO BUTTONVILLE A | 12 | 16 | 10 | -10.2 | 28.2 | 0
8410 | TORONTO BUTTONVILLE A | 12 | 17 | 10 | -3.1 | 21.1 | 0
8411 | TORONTO BUTTONVILLE A | 12 | 16 | 11 | -10 | 28 | 0
8411 | TORONTO BUTTONVILLE A | 12 | 17 | 11 | -2.475 | 20.475 | 0
8412 | TORONTO BUTTONVILLE A | 12 | 16 | 12 | -9.4 | 27.4 | 0
8412 | TORONTO BUTTONVILLE A | 12 | 17 | 12 | -1.775 | 19.775 | 0
8413 | TORONTO BUTTONVILLE A | 12 | 16 | 13 | -8.8 | 26.8 | 0
8413 | TORONTO BUTTONVILLE A | 12 | 17 | 13 | -1.325 | 19.325 | 0
8414 | TORONTO BUTTONVILLE A | 12 | 16 | 14 | -8 | 26 | 0
8414 | TORONTO BUTTONVILLE A | 12 | 17 | 14 | -1.15 | 19.15 | 0
8415 | TORONTO BUTTONVILLE A | 12 | 16 | 15 | -7.8 | 25.8 | 0
8415 | TORONTO BUTTONVILLE A | 12 | 17 | 15 | -1.05 | 19.05 | 0
8416 | TORONTO BUTTONVILLE A | 12 | 16 | 16 | -7.4 | 25.4 | 0
8416 | TORONTO BUTTONVILLE A | 12 | 17 | 16 | -0.75 | 18.75 | 0
8417 | TORONTO BUTTONVILLE A | 12 | 16 | 17 | -7.2 | 25.2 | 0
8417 | TORONTO BUTTONVILLE A | 12 | 17 | 17 | -1.1 | 19.1 | 0
8418 | TORONTO BUTTONVILLE A | 12 | 16 | 18 | -7.3 | 25.3 | 0
8418 | TORONTO BUTTONVILLE A | 12 | 17 | 18 | -1.525 | 19.525 | 0
8419 | TORONTO BUTTONVILLE A | 12 | 16 | 19 | -7.3 | 25.3 | 0
8419 | TORONTO BUTTONVILLE A | 12 | 17 | 19 | -2.225 | 20.225 | 0
8420 | TORONTO BUTTONVILLE A | 12 | 16 | 20 | -7.2 | 25.2 | 0
8420 | TORONTO BUTTONVILLE A | 12 | 17 | 20 | -2.775 | 20.775 | 0
8421 | TORONTO BUTTONVILLE A | 12 | 16 | 21 | -7.4 | 25.4 | 0
8421 | TORONTO BUTTONVILLE A | 12 | 17 | 21 | -3.125 | 21.125 | 0
8422 | TORONTO BUTTONVILLE A | 12 | 16 | 22 | -7.5 | 25.5 | 0
8422 | TORONTO BUTTONVILLE A | 12 | 17 | 22 | -3.2 | 21.2 | 0
8423 | TORONTO BUTTONVILLE A | 12 | 16 | 23 | -7.7 | 25.7 | 0
8423 | TORONTO BUTTONVILLE A | 12 | 17 | 23 | -3.275 | 21.275 | 0
8424 | TORONTO BUTTONVILLE A | 12 | 16 | 24 | -8.2 | 26.2 | 0
8424 | TORONTO BUTTONVILLE A | 12 | 17 | 24 | -3.225 | 21.225 | 0
8425 | TORONTO BUTTONVILLE A | 12 | 17 | 1 | -8.6 | 26.6 | 0
8425 | TORONTO BUTTONVILLE A | 12 | 18 | 1 | -3.125 | 21.125 | 0
8426 | TORONTO BUTTONVILLE A | 12 | 17 | 2 | -8.1 | 26.1 | 0
8426 | TORONTO BUTTONVILLE A | 12 | 18 | 2 | -3.325 | 21.325 | 0
8427 | TORONTO BUTTONVILLE A | 12 | 17 | 3 | -8.2 | 26.2 | 0
8427 | TORONTO BUTTONVILLE A | 12 | 18 | 3 | -3.5 | 21.5 | 0
8428 | TORONTO BUTTONVILLE A | 12 | 17 | 4 | -8.1 | 26.1 | 0
8428 | TORONTO BUTTONVILLE A | 12 | 18 | 4 | -3.675 | 21.675 | 0
8429 | TORONTO BUTTONVILLE A | 12 | 17 | 5 | -8.2 | 26.2 | 0
8429 | TORONTO BUTTONVILLE A | 12 | 18 | 5 | -3.9 | 21.9 | 0
8430 | TORONTO BUTTONVILLE A | 12 | 17 | 6 | -8.2 | 26.2 | 0
8430 | TORONTO BUTTONVILLE A | 12 | 18 | 6 | -4.325 | 22.325 | 0
8431 | TORONTO BUTTONVILLE A | 12 | 17 | 7 | -8.1 | 26.1 | 0
8431 | TORONTO BUTTONVILLE A | 12 | 18 | 7 | -4.3 | 22.3 | 0
8432 | TORONTO BUTTONVILLE A | 12 | 17 | 8 | -8 | 26 | 0
8432 | TORONTO BUTTONVILLE A | 12 | 18 | 8 | -4.35 | 22.35 | 0
8433 | TORONTO BUTTONVILLE A | 12 | 17 | 9 | -7.9 | 25.9 | 0
8433 | TORONTO BUTTONVILLE A | 12 | 18 | 9 | -4.3 | 22.3 | 0
8434 | TORONTO BUTTONVILLE A | 12 | 17 | 10 | -8.2 | 26.2 | 0
8434 | TORONTO BUTTONVILLE A | 12 | 18 | 10 | -4.875 | 22.875 | 0
8435 | TORONTO BUTTONVILLE A | 12 | 17 | 11 | -7.6 | 25.6 | 0
8435 | TORONTO BUTTONVILLE A | 12 | 18 | 11 | -4.925 | 22.925 | 0
8436 | TORONTO BUTTONVILLE A | 12 | 17 | 12 | -6.6 | 24.6 | 0
8436 | TORONTO BUTTONVILLE A | 12 | 18 | 12 | -4.825 | 22.825 | 0
8437 | TORONTO BUTTONVILLE A | 12 | 17 | 13 | -5.6 | 23.6 | 0
8437 | TORONTO BUTTONVILLE A | 12 | 18 | 13 | -4.4 | 22.4 | 0
8438 | TORONTO BUTTONVILLE A | 12 | 17 | 14 | -4.3 | 22.3 | 0
8438 | TORONTO BUTTONVILLE A | 12 | 18 | 14 | -4.125 | 22.125 | 0
8439 | TORONTO BUTTONVILLE A | 12 | 17 | 15 | -3.6 | 21.6 | 0
8439 | TORONTO BUTTONVILLE A | 12 | 18 | 15 | -4.025 | 22.025 | 0
8440 | TORONTO BUTTONVILLE A | 12 | 17 | 16 | -3 | 21 | 0
8440 | TORONTO BUTTONVILLE A | 12 | 18 | 16 | -3.825 | 21.825 | 0
8441 | TORONTO BUTTONVILLE A | 12 | 17 | 17 | -4.2 | 22.2 | 0
8441 | TORONTO BUTTONVILLE A | 12 | 18 | 17 | -3.8 | 21.8 | 0
8442 | TORONTO BUTTONVILLE A | 12 | 17 | 18 | -5.1 | 23.1 | 0
8442 | TORONTO BUTTONVILLE A | 12 | 18 | 18 | -4.35 | 22.35 | 0
8443 | TORONTO BUTTONVILLE A | 12 | 17 | 19 | -5.9 | 23.9 | 0
8443 | TORONTO BUTTONVILLE A | 12 | 18 | 19 | -4.525 | 22.525 | 0
8444 | TORONTO BUTTONVILLE A | 12 | 17 | 20 | -6.5 | 24.5 | 0
8444 | TORONTO BUTTONVILLE A | 12 | 18 | 20 | -4.875 | 22.875 | 0
8445 | TORONTO BUTTONVILLE A | 12 | 17 | 21 | -6.8 | 24.8 | 0
8445 | TORONTO BUTTONVILLE A | 12 | 18 | 21 | -4.975 | 22.975 | 0
8446 | TORONTO BUTTONVILLE A | 12 | 17 | 22 | -7.8 | 25.8 | 0
8446 | TORONTO BUTTONVILLE A | 12 | 18 | 22 | -5.175 | 23.175 | 0
8447 | TORONTO BUTTONVILLE A | 12 | 17 | 23 | -8 | 26 | 0
8447 | TORONTO BUTTONVILLE A | 12 | 18 | 23 | -5.5 | 23.5 | 0
8448 | TORONTO BUTTONVILLE A | 12 | 17 | 24 | -8 | 26 | 0
8448 | TORONTO BUTTONVILLE A | 12 | 18 | 24 | -5.925 | 23.925 | 0
8449 | TORONTO BUTTONVILLE A | 12 | 18 | 1 | -8.2 | 26.2 | 0
8449 | TORONTO BUTTONVILLE A | 12 | 19 | 1 | -5.775 | 23.775 | 0
8450 | TORONTO BUTTONVILLE A | 12 | 18 | 2 | -8.5 | 26.5 | 0
8450 | TORONTO BUTTONVILLE A | 12 | 19 | 2 | -5.975 | 23.975 | 0
8451 | TORONTO BUTTONVILLE A | 12 | 18 | 3 | -9 | 27 | 0
8451 | TORONTO BUTTONVILLE A | 12 | 19 | 3 | -5.35 | 23.35 | 0
8452 | TORONTO BUTTONVILLE A | 12 | 18 | 4 | -9.8 | 27.8 | 0
8452 | TORONTO BUTTONVILLE A | 12 | 19 | 4 | -5.2 | 23.2 | 0
8453 | TORONTO BUTTONVILLE A | 12 | 18 | 5 | -9.9 | 27.9 | 0
8453 | TORONTO BUTTONVILLE A | 12 | 19 | 5 | -5.125 | 23.125 | 0
8454 | TORONTO BUTTONVILLE A | 12 | 18 | 6 | -10.6 | 28.6 | 0
8454 | TORONTO BUTTONVILLE A | 12 | 19 | 6 | -5.2 | 23.2 | 0
8455 | TORONTO BUTTONVILLE A | 12 | 18 | 7 | -10 | 28 | 0
8455 | TORONTO BUTTONVILLE A | 12 | 19 | 7 | -5.125 | 23.125 | 0
8456 | TORONTO BUTTONVILLE A | 12 | 18 | 8 | -10.5 | 28.5 | 0
8456 | TORONTO BUTTONVILLE A | 12 | 19 | 8 | -4.825 | 22.825 | 0
8457 | TORONTO BUTTONVILLE A | 12 | 18 | 9 | -10.2 | 28.2 | 0
8457 | TORONTO BUTTONVILLE A | 12 | 19 | 9 | -4.65 | 22.65 | 0
8458 | TORONTO BUTTONVILLE A | 12 | 18 | 10 | -8.5 | 26.5 | 0
8458 | TORONTO BUTTONVILLE A | 12 | 19 | 10 | -3.7 | 21.7 | 0
8459 | TORONTO BUTTONVILLE A | 12 | 18 | 11 | -6.6 | 24.6 | 0
8459 | TORONTO BUTTONVILLE A | 12 | 19 | 11 | -2.95 | 20.95 | 0
8460 | TORONTO BUTTONVILLE A | 12 | 18 | 12 | -4.8 | 22.8 | 0
8460 | TORONTO BUTTONVILLE A | 12 | 19 | 12 | -2.3 | 20.3 | 0
8461 | TORONTO BUTTONVILLE A | 12 | 18 | 13 | -4 | 22 | 0
8461 | TORONTO BUTTONVILLE A | 12 | 19 | 13 | -1.6 | 19.6 | 0
8462 | TORONTO BUTTONVILLE A | 12 | 18 | 14 | -2.6 | 20.6 | 0
8462 | TORONTO BUTTONVILLE A | 12 | 19 | 14 | -1 | 19 | 0
8463 | TORONTO BUTTONVILLE A | 12 | 18 | 15 | -2.4 | 20.4 | 0
8463 | TORONTO BUTTONVILLE A | 12 | 19 | 15 | -0.925 | 18.925 | 0
8464 | TORONTO BUTTONVILLE A | 12 | 18 | 16 | -1.6 | 19.6 | 0
8464 | TORONTO BUTTONVILLE A | 12 | 19 | 16 | -0.95 | 18.95 | 0
8465 | TORONTO BUTTONVILLE A | 12 | 18 | 17 | -2 | 20 | 0
8465 | TORONTO BUTTONVILLE A | 12 | 19 | 17 | -1.05 | 19.05 | 0
8466 | TORONTO BUTTONVILLE A | 12 | 18 | 18 | -3.7 | 21.7 | 0
8466 | TORONTO BUTTONVILLE A | 12 | 19 | 18 | -1.55 | 19.55 | 0
8467 | TORONTO BUTTONVILLE A | 12 | 18 | 19 | -4.5 | 22.5 | 0
8467 | TORONTO BUTTONVILLE A | 12 | 19 | 19 | -2.325 | 20.325 | 0
8468 | TORONTO BUTTONVILLE A | 12 | 18 | 20 | -5 | 23 | 0
8468 | TORONTO BUTTONVILLE A | 12 | 19 | 20 | -2.8 | 20.8 | 0
8469 | TORONTO BUTTONVILLE A | 12 | 18 | 21 | -5.4 | 23.4 | 0
8469 | TORONTO BUTTONVILLE A | 12 | 19 | 21 | -3.175 | 21.175 | 0
8470 | TORONTO BUTTONVILLE A | 12 | 18 | 22 | -6.7 | 24.7 | 0
8470 | TORONTO BUTTONVILLE A | 12 | 19 | 22 | -3.2 | 21.2 | 0
8471 | TORONTO BUTTONVILLE A | 12 | 18 | 23 | -6.7 | 24.7 | 0
8471 | TORONTO BUTTONVILLE A | 12 | 19 | 23 | -3.35 | 21.35 | 0
8472 | TORONTO BUTTONVILLE A | 12 | 18 | 24 | -6.5 | 24.5 | 0
8472 | TORONTO BUTTONVILLE A | 12 | 19 | 24 | -3.625 | 21.625 | 0
8473 | TORONTO BUTTONVILLE A | 12 | 19 | 1 | -7.7 | 25.7 | 0
8473 | TORONTO BUTTONVILLE A | 12 | 20 | 1 | -3.95 | 21.95 | 0
8474 | TORONTO BUTTONVILLE A | 12 | 19 | 2 | -6.2 | 24.2 | 0
8474 | TORONTO BUTTONVILLE A | 12 | 20 | 2 | -5 | 23 | 0
8475 | TORONTO BUTTONVILLE A | 12 | 19 | 3 | -5.2 | 23.2 | 0
8475 | TORONTO BUTTONVILLE A | 12 | 20 | 3 | -5.4 | 23.4 | 0
8476 | TORONTO BUTTONVILLE A | 12 | 19 | 4 | -4.4 | 22.4 | 0
8476 | TORONTO BUTTONVILLE A | 12 | 20 | 4 | -5.575 | 23.575 | 0
8477 | TORONTO BUTTONVILLE A | 12 | 19 | 5 | -3.9 | 21.9 | 0
8477 | TORONTO BUTTONVILLE A | 12 | 20 | 5 | -5.975 | 23.975 | 0
8478 | TORONTO BUTTONVILLE A | 12 | 19 | 6 | -3.6 | 21.6 | 0
8478 | TORONTO BUTTONVILLE A | 12 | 20 | 6 | -5.75 | 23.75 | 0
8479 | TORONTO BUTTONVILLE A | 12 | 19 | 7 | -3.4 | 21.4 | 0
8479 | TORONTO BUTTONVILLE A | 12 | 20 | 7 | -5.375 | 23.375 | 0
8480 | TORONTO BUTTONVILLE A | 12 | 19 | 8 | -3.3 | 21.3 | 0
8480 | TORONTO BUTTONVILLE A | 12 | 20 | 8 | -4.625 | 22.625 | 0
8481 | TORONTO BUTTONVILLE A | 12 | 19 | 9 | -1.4 | 19.4 | 0
8481 | TORONTO BUTTONVILLE A | 12 | 20 | 9 | -4.625 | 22.625 | 0
8482 | TORONTO BUTTONVILLE A | 12 | 19 | 10 | 0 | 18 | 0
8482 | TORONTO BUTTONVILLE A | 12 | 20 | 10 | -3.75 | 21.75 | 0
8483 | TORONTO BUTTONVILLE A | 12 | 19 | 11 | 1.1 | 16.9 | 0
8483 | TORONTO BUTTONVILLE A | 12 | 20 | 11 | -2.5 | 20.5 | 0
8484 | TORONTO BUTTONVILLE A | 12 | 19 | 12 | 1.6 | 16.4 | 0
8484 | TORONTO BUTTONVILLE A | 12 | 20 | 12 | -1.65 | 19.65 | 0
8485 | TORONTO BUTTONVILLE A | 12 | 19 | 13 | 1.6 | 16.4 | 0
8485 | TORONTO BUTTONVILLE A | 12 | 20 | 13 | -1.05 | 19.05 | 0
8486 | TORONTO BUTTONVILLE A | 12 | 19 | 14 | 1.1 | 16.9 | 0
8486 | TORONTO BUTTONVILLE A | 12 | 20 | 14 | -0.525 | 18.525 | 0
8487 | TORONTO BUTTONVILLE A | 12 | 19 | 15 | 1.3 | 16.7 | 0
8487 | TORONTO BUTTONVILLE A | 12 | 20 | 15 | -0.1 | 18.1 | 0
8488 | TORONTO BUTTONVILLE A | 12 | 19 | 16 | 0.6 | 17.4 | 0
8488 | TORONTO BUTTONVILLE A | 12 | 20 | 16 | 0.325 | 17.675 | 0
8489 | TORONTO BUTTONVILLE A | 12 | 19 | 17 | 0.3 | 17.7 | 0
8489 | TORONTO BUTTONVILLE A | 12 | 20 | 17 | -0.225 | 18.225 | 0
8490 | TORONTO BUTTONVILLE A | 12 | 19 | 18 | 0.6 | 17.4 | 0
8490 | TORONTO BUTTONVILLE A | 12 | 20 | 18 | -0.8 | 18.8 | 0
8491 | TORONTO BUTTONVILLE A | 12 | 19 | 19 | 0.6 | 17.4 | 0
8491 | TORONTO BUTTONVILLE A | 12 | 20 | 19 | -1.5 | 19.5 | 0
8492 | TORONTO BUTTONVILLE A | 12 | 19 | 20 | 0.7 | 17.3 | 0
8492 | TORONTO BUTTONVILLE A | 12 | 20 | 20 | -1.875 | 19.875 | 0
8493 | TORONTO BUTTONVILLE A | 12 | 19 | 21 | 1 | 17 | 0
8493 | TORONTO BUTTONVILLE A | 12 | 20 | 21 | -2.55 | 20.55 | 0
8494 | TORONTO BUTTONVILLE A | 12 | 19 | 22 | 0.8 | 17.2 | 0
8494 | TORONTO BUTTONVILLE A | 12 | 20 | 22 | -2.525 | 20.525 | 0
8495 | TORONTO BUTTONVILLE A | 12 | 19 | 23 | 1.1 | 16.9 | 0
8495 | TORONTO BUTTONVILLE A | 12 | 20 | 23 | -2.675 | 20.675 | 0
8496 | TORONTO BUTTONVILLE A | 12 | 19 | 24 | 1.4 | 16.6 | 0
8496 | TORONTO BUTTONVILLE A | 12 | 20 | 24 | -2.075 | 20.075 | 0
8497 | TORONTO BUTTONVILLE A | 12 | 20 | 1 | 1 | 17 | 0
8497 | TORONTO BUTTONVILLE A | 12 | 21 | 1 | -2.325 | 20.325 | 0
8498 | TORONTO BUTTONVILLE A | 12 | 20 | 2 | 0.8 | 17.2 | 0
8498 | TORONTO BUTTONVILLE A | 12 | 21 | 2 | -2.225 | 20.225 | 0
8499 | TORONTO BUTTONVILLE A | 12 | 20 | 3 | 1 | 17 | 0
8499 | TORONTO BUTTONVILLE A | 12 | 21 | 3 | -2.15 | 20.15 | 0
8500 | TORONTO BUTTONVILLE A | 12 | 20 | 4 | 1.3 | 16.7 | 0
8500 | TORONTO BUTTONVILLE A | 12 | 21 | 4 | -2.225 | 20.225 | 0
8501 | TORONTO BUTTONVILLE A | 12 | 20 | 5 | 1.5 | 16.5 | 0
8501 | TORONTO BUTTONVILLE A | 12 | 21 | 5 | -2.475 | 20.475 | 0
8502 | TORONTO BUTTONVILLE A | 12 | 20 | 6 | 1.7 | 16.3 | 0
8502 | TORONTO BUTTONVILLE A | 12 | 21 | 6 | -2.25 | 20.25 | 0
8503 | TORONTO BUTTONVILLE A | 12 | 20 | 7 | 1.7 | 16.3 | 0
8503 | TORONTO BUTTONVILLE A | 12 | 21 | 7 | -2.3 | 20.3 | 0
8504 | TORONTO BUTTONVILLE A | 12 | 20 | 8 | 1.8 | 16.2 | 0
8504 | TORONTO BUTTONVILLE A | 12 | 21 | 8 | -2.6 | 20.6 | 0
8505 | TORONTO BUTTONVILLE A | 12 | 20 | 9 | 2 | 16 | 0
8505 | TORONTO BUTTONVILLE A | 12 | 21 | 9 | -2.8 | 20.8 | 0
8506 | TORONTO BUTTONVILLE A | 12 | 20 | 10 | 2.1 | 15.9 | 0
8506 | TORONTO BUTTONVILLE A | 12 | 21 | 10 | -2.4 | 20.4 | 0
8507 | TORONTO BUTTONVILLE A | 12 | 20 | 11 | 2.5 | 15.5 | 0
8507 | TORONTO BUTTONVILLE A | 12 | 21 | 11 | -1.975 | 19.975 | 0
8508 | TORONTO BUTTONVILLE A | 12 | 20 | 12 | 2.6 | 15.4 | 0
8508 | TORONTO BUTTONVILLE A | 12 | 21 | 12 | -1.5 | 19.5 | 0
8509 | TORONTO BUTTONVILLE A | 12 | 20 | 13 | 2.7 | 15.3 | 0
8509 | TORONTO BUTTONVILLE A | 12 | 21 | 13 | -0.725 | 18.725 | 0
8510 | TORONTO BUTTONVILLE A | 12 | 20 | 14 | 3.1 | 14.9 | 0
8510 | TORONTO BUTTONVILLE A | 12 | 21 | 14 | 0.05 | 17.95 | 0
8511 | TORONTO BUTTONVILLE A | 12 | 20 | 15 | 3.9 | 14.1 | 0
8511 | TORONTO BUTTONVILLE A | 12 | 21 | 15 | 0.275 | 17.725 | 0
8512 | TORONTO BUTTONVILLE A | 12 | 20 | 16 | 4 | 14 | 0
8512 | TORONTO BUTTONVILLE A | 12 | 21 | 16 | -0.025 | 18.025 | 0
8513 | TORONTO BUTTONVILLE A | 12 | 20 | 17 | 3.8 | 14.2 | 0
8513 | TORONTO BUTTONVILLE A | 12 | 21 | 17 | -0.325 | 18.325 | 0
8514 | TORONTO BUTTONVILLE A | 12 | 20 | 18 | 3.6 | 14.4 | 0
8514 | TORONTO BUTTONVILLE A | 12 | 21 | 18 | -0.65 | 18.65 | 0
8515 | TORONTO BUTTONVILLE A | 12 | 20 | 19 | 3.3 | 14.7 | 0
8515 | TORONTO BUTTONVILLE A | 12 | 21 | 19 | -0.85 | 18.85 | 0
8516 | TORONTO BUTTONVILLE A | 12 | 20 | 20 | 3.2 | 14.8 | 0
8516 | TORONTO BUTTONVILLE A | 12 | 21 | 20 | -1.175 | 19.175 | 0
8517 | TORONTO BUTTONVILLE A | 12 | 20 | 21 | 3.5 | 14.5 | 0
8517 | TORONTO BUTTONVILLE A | 12 | 21 | 21 | -1.35 | 19.35 | 0
8518 | TORONTO BUTTONVILLE A | 12 | 20 | 22 | 3.3 | 14.7 | 0
8518 | TORONTO BUTTONVILLE A | 12 | 21 | 22 | -1.85 | 19.85 | 0
8519 | TORONTO BUTTONVILLE A | 12 | 20 | 23 | 2.6 | 15.4 | 0
8519 | TORONTO BUTTONVILLE A | 12 | 21 | 23 | -2.375 | 20.375 | 0
8520 | TORONTO BUTTONVILLE A | 12 | 20 | 24 | 2 | 16 | 0
8520 | TORONTO BUTTONVILLE A | 12 | 21 | 24 | -2.025 | 20.025 | 0
8521 | TORONTO BUTTONVILLE A | 12 | 21 | 1 | 1.4 | 16.6 | 0
8521 | TORONTO BUTTONVILLE A | 12 | 22 | 1 | -2.2 | 20.2 | 0
8522 | TORONTO BUTTONVILLE A | 12 | 21 | 2 | 0.7 | 17.3 | 0
8522 | TORONTO BUTTONVILLE A | 12 | 22 | 2 | -2.575 | 20.575 | 0
8523 | TORONTO BUTTONVILLE A | 12 | 21 | 3 | 0 | 18 | 0
8523 | TORONTO BUTTONVILLE A | 12 | 22 | 3 | -2.775 | 20.775 | 0
8524 | TORONTO BUTTONVILLE A | 12 | 21 | 4 | -1 | 19 | 0
8524 | TORONTO BUTTONVILLE A | 12 | 22 | 4 | -1.325 | 19.325 | 0
8525 | TORONTO BUTTONVILLE A | 12 | 21 | 5 | -1.3 | 19.3 | 0
8525 | TORONTO BUTTONVILLE A | 12 | 22 | 5 | -1.95 | 19.95 | 0
8526 | TORONTO BUTTONVILLE A | 12 | 21 | 6 | -1.2 | 19.2 | 0
8526 | TORONTO BUTTONVILLE A | 12 | 22 | 6 | -2.7 | 20.7 | 0
8527 | TORONTO BUTTONVILLE A | 12 | 21 | 7 | -0.7 | 18.7 | 0
8527 | TORONTO BUTTONVILLE A | 12 | 22 | 7 | -2.8 | 20.8 | 0
8528 | TORONTO BUTTONVILLE A | 12 | 21 | 8 | -0.8 | 18.8 | 0
8528 | TORONTO BUTTONVILLE A | 12 | 22 | 8 | -3.125 | 21.125 | 0
8529 | TORONTO BUTTONVILLE A | 12 | 21 | 9 | -0.1 | 18.1 | 0
8529 | TORONTO BUTTONVILLE A | 12 | 22 | 9 | -4.1 | 22.1 | 0
8530 | TORONTO BUTTONVILLE A | 12 | 21 | 10 | 0.5 | 17.5 | 0
8530 | TORONTO BUTTONVILLE A | 12 | 22 | 10 | -3.75 | 21.75 | 0
8531 | TORONTO BUTTONVILLE A | 12 | 21 | 11 | 1.2 | 16.8 | 0
8531 | TORONTO BUTTONVILLE A | 12 | 22 | 11 | -2.35 | 20.35 | 0
8532 | TORONTO BUTTONVILLE A | 12 | 21 | 12 | 2 | 16 | 0
8532 | TORONTO BUTTONVILLE A | 12 | 22 | 12 | -1.65 | 19.65 | 0
8533 | TORONTO BUTTONVILLE A | 12 | 21 | 13 | 2.7 | 15.3 | 0
8533 | TORONTO BUTTONVILLE A | 12 | 22 | 13 | -1.15 | 19.15 | 0
8534 | TORONTO BUTTONVILLE A | 12 | 21 | 14 | 3.4 | 14.6 | 0
8534 | TORONTO BUTTONVILLE A | 12 | 22 | 14 | -0.725 | 18.725 | 0
8535 | TORONTO BUTTONVILLE A | 12 | 21 | 15 | 3.5 | 14.5 | 0
8535 | TORONTO BUTTONVILLE A | 12 | 22 | 15 | -0.925 | 18.925 | 0
8536 | TORONTO BUTTONVILLE A | 12 | 21 | 16 | 2.5 | 15.5 | 0
8536 | TORONTO BUTTONVILLE A | 12 | 22 | 16 | -0.85 | 18.85 | 0
8537 | TORONTO BUTTONVILLE A | 12 | 21 | 17 | 2.4 | 15.6 | 0
8537 | TORONTO BUTTONVILLE A | 12 | 22 | 17 | -1.2 | 19.2 | 0
8538 | TORONTO BUTTONVILLE A | 12 | 21 | 18 | 1.7 | 16.3 | 0
8538 | TORONTO BUTTONVILLE A | 12 | 22 | 18 | -1.7 | 19.7 | 0
8539 | TORONTO BUTTONVILLE A | 12 | 21 | 19 | 1.5 | 16.5 | 0
8539 | TORONTO BUTTONVILLE A | 12 | 22 | 19 | -2.175 | 20.175 | 0
8540 | TORONTO BUTTONVILLE A | 12 | 21 | 20 | 1.4 | 16.6 | 0
8540 | TORONTO BUTTONVILLE A | 12 | 22 | 20 | -2.375 | 20.375 | 0
8541 | TORONTO BUTTONVILLE A | 12 | 21 | 21 | 1.2 | 16.8 | 0
8541 | TORONTO BUTTONVILLE A | 12 | 22 | 21 | -2.6 | 20.6 | 0
8542 | TORONTO BUTTONVILLE A | 12 | 21 | 22 | 1.2 | 16.8 | 0
8542 | TORONTO BUTTONVILLE A | 12 | 22 | 22 | -2.625 | 20.625 | 0
8543 | TORONTO BUTTONVILLE A | 12 | 21 | 23 | 1.4 | 16.6 | 0
8543 | TORONTO BUTTONVILLE A | 12 | 22 | 23 | -2.65 | 20.65 | 0
8544 | TORONTO BUTTONVILLE A | 12 | 21 | 24 | 1.4 | 16.6 | 0
8544 | TORONTO BUTTONVILLE A | 12 | 22 | 24 | -2.775 | 20.775 | 0
8545 | TORONTO BUTTONVILLE A | 12 | 22 | 1 | 1.1 | 16.9 | 0
8545 | TORONTO BUTTONVILLE A | 12 | 23 | 1 | -2.725 | 20.725 | 0
8546 | TORONTO BUTTONVILLE A | 12 | 22 | 2 | 0.8 | 17.2 | 0
8546 | TORONTO BUTTONVILLE A | 12 | 23 | 2 | -2.5 | 20.5 | 0
8547 | TORONTO BUTTONVILLE A | 12 | 22 | 3 | 0.6 | 17.4 | 0
8547 | TORONTO BUTTONVILLE A | 12 | 23 | 3 | -2.725 | 20.725 | 0
8548 | TORONTO BUTTONVILLE A | 12 | 22 | 4 | 1 | 17 | 0
8548 | TORONTO BUTTONVILLE A | 12 | 23 | 4 | -2.975 | 20.975 | 0
8549 | TORONTO BUTTONVILLE A | 12 | 22 | 5 | 0.8 | 17.2 | 0
8549 | TORONTO BUTTONVILLE A | 12 | 23 | 5 | -3.275 | 21.275 | 0
8550 | TORONTO BUTTONVILLE A | 12 | 22 | 6 | 0.8 | 17.2 | 0
8550 | TORONTO BUTTONVILLE A | 12 | 23 | 6 | -3.45 | 21.45 | 0
8551 | TORONTO BUTTONVILLE A | 12 | 22 | 7 | 0.2 | 17.8 | 0
8551 | TORONTO BUTTONVILLE A | 12 | 23 | 7 | -3.575 | 21.575 | 0
8552 | TORONTO BUTTONVILLE A | 12 | 22 | 8 | 0 | 18 | 0
8552 | TORONTO BUTTONVILLE A | 12 | 23 | 8 | -3.425 | 21.425 | 0
8553 | TORONTO BUTTONVILLE A | 12 | 22 | 9 | -0.3 | 18.3 | 0
8553 | TORONTO BUTTONVILLE A | 12 | 23 | 9 | -3.025 | 21.025 | 0
8554 | TORONTO BUTTONVILLE A | 12 | 22 | 10 | 0.8 | 17.2 | 0
8554 | TORONTO BUTTONVILLE A | 12 | 23 | 10 | -2.275 | 20.275 | 0
8555 | TORONTO BUTTONVILLE A | 12 | 22 | 11 | 1.3 | 16.7 | 0
8555 | TORONTO BUTTONVILLE A | 12 | 23 | 11 | -1.8 | 19.8 | 0
8556 | TORONTO BUTTONVILLE A | 12 | 22 | 12 | 1.8 | 16.2 | 0
8556 | TORONTO BUTTONVILLE A | 12 | 23 | 12 | -0.8 | 18.8 | 0
8557 | TORONTO BUTTONVILLE A | 12 | 22 | 13 | 1.8 | 16.2 | 0
8557 | TORONTO BUTTONVILLE A | 12 | 23 | 13 | 0.175 | 17.825 | 0
8558 | TORONTO BUTTONVILLE A | 12 | 22 | 14 | 1.8 | 16.2 | 0
8558 | TORONTO BUTTONVILLE A | 12 | 23 | 14 | 1.2 | 16.8 | 0
8559 | TORONTO BUTTONVILLE A | 12 | 22 | 15 | 1.8 | 16.2 | 0
8559 | TORONTO BUTTONVILLE A | 12 | 23 | 15 | 1.375 | 16.625 | 0
8560 | TORONTO BUTTONVILLE A | 12 | 22 | 16 | 1.8 | 16.2 | 0
8560 | TORONTO BUTTONVILLE A | 12 | 23 | 16 | 1.425 | 16.575 | 0
8561 | TORONTO BUTTONVILLE A | 12 | 22 | 17 | 1.5 | 16.5 | 0
8561 | TORONTO BUTTONVILLE A | 12 | 23 | 17 | 0.7 | 17.3 | 0
8562 | TORONTO BUTTONVILLE A | 12 | 22 | 18 | 1.4 | 16.6 | 0
8562 | TORONTO BUTTONVILLE A | 12 | 23 | 18 | 0.05 | 17.95 | 0
8563 | TORONTO BUTTONVILLE A | 12 | 22 | 19 | 1.2 | 16.8 | 0
8563 | TORONTO BUTTONVILLE A | 12 | 23 | 19 | -0.475 | 18.475 | 0
8564 | TORONTO BUTTONVILLE A | 12 | 22 | 20 | 1.1 | 16.9 | 0
8564 | TORONTO BUTTONVILLE A | 12 | 23 | 20 | -0.325 | 18.325 | 0
8565 | TORONTO BUTTONVILLE A | 12 | 22 | 21 | 0.8 | 17.2 | 0
8565 | TORONTO BUTTONVILLE A | 12 | 23 | 21 | -0.625 | 18.625 | 0
8566 | TORONTO BUTTONVILLE A | 12 | 22 | 22 | 0.8 | 17.2 | 0
8566 | TORONTO BUTTONVILLE A | 12 | 23 | 22 | -0.8 | 18.8 | 0
8567 | TORONTO BUTTONVILLE A | 12 | 22 | 23 | 0.8 | 17.2 | 0
8567 | TORONTO BUTTONVILLE A | 12 | 23 | 23 | -0.875 | 18.875 | 0
8568 | TORONTO BUTTONVILLE A | 12 | 22 | 24 | 0.6 | 17.4 | 0
8568 | TORONTO BUTTONVILLE A | 12 | 23 | 24 | -1.025 | 19.025 | 0
8569 | TORONTO BUTTONVILLE A | 12 | 23 | 1 | 0.3 | 17.7 | 0
8569 | TORONTO BUTTONVILLE A | 12 | 24 | 1 | -1 | 19 | 0
8570 | TORONTO BUTTONVILLE A | 12 | 23 | 2 | 0.5 | 17.5 | 0
8570 | TORONTO BUTTONVILLE A | 12 | 24 | 2 | -1.175 | 19.175 | 0
8571 | TORONTO BUTTONVILLE A | 12 | 23 | 3 | 0.4 | 17.6 | 0
8571 | TORONTO BUTTONVILLE A | 12 | 24 | 3 | -1.525 | 19.525 | 0
8572 | TORONTO BUTTONVILLE A | 12 | 23 | 4 | 0.5 | 17.5 | 0
8572 | TORONTO BUTTONVILLE A | 12 | 24 | 4 | -1.7 | 19.7 | 0
8573 | TORONTO BUTTONVILLE A | 12 | 23 | 5 | 0.5 | 17.5 | 0
8573 | TORONTO BUTTONVILLE A | 12 | 24 | 5 | -1.475 | 19.475 | 0
8574 | TORONTO BUTTONVILLE A | 12 | 23 | 6 | 0.6 | 17.4 | 0
8574 | TORONTO BUTTONVILLE A | 12 | 24 | 6 | -2.15 | 20.15 | 0
8575 | TORONTO BUTTONVILLE A | 12 | 23 | 7 | 0.8 | 17.2 | 0
8575 | TORONTO BUTTONVILLE A | 12 | 24 | 7 | -2.35 | 20.35 | 0
8576 | TORONTO BUTTONVILLE A | 12 | 23 | 8 | 0.9 | 17.1 | 0
8576 | TORONTO BUTTONVILLE A | 12 | 24 | 8 | -2.8 | 20.8 | 0
8577 | TORONTO BUTTONVILLE A | 12 | 23 | 9 | 1.3 | 16.7 | 0
8577 | TORONTO BUTTONVILLE A | 12 | 24 | 9 | -3.25 | 21.25 | 0
8578 | TORONTO BUTTONVILLE A | 12 | 23 | 10 | 1.6 | 16.4 | 0
8578 | TORONTO BUTTONVILLE A | 12 | 24 | 10 | -3 | 21 | 0
8579 | TORONTO BUTTONVILLE A | 12 | 23 | 11 | 2.1 | 15.9 | 0
8579 | TORONTO BUTTONVILLE A | 12 | 24 | 11 | -1.925 | 19.925 | 0
8580 | TORONTO BUTTONVILLE A | 12 | 23 | 12 | 2.5 | 15.5 | 0
8580 | TORONTO BUTTONVILLE A | 12 | 24 | 12 | -1.225 | 19.225 | 0
8581 | TORONTO BUTTONVILLE A | 12 | 23 | 13 | 3.3 | 14.7 | 0
8581 | TORONTO BUTTONVILLE A | 12 | 24 | 13 | -0.775 | 18.775 | 0
8582 | TORONTO BUTTONVILLE A | 12 | 23 | 14 | 3.6 | 14.4 | 0
8582 | TORONTO BUTTONVILLE A | 12 | 24 | 14 | -0.775 | 18.775 | 0
8583 | TORONTO BUTTONVILLE A | 12 | 23 | 15 | 3.9 | 14.1 | 0
8583 | TORONTO BUTTONVILLE A | 12 | 24 | 15 | -0.775 | 18.775 | 0
8584 | TORONTO BUTTONVILLE A | 12 | 23 | 16 | 3.7 | 14.3 | 0
8584 | TORONTO BUTTONVILLE A | 12 | 24 | 16 | -0.625 | 18.625 | 0
8585 | TORONTO BUTTONVILLE A | 12 | 23 | 17 | 3.2 | 14.8 | 0
8585 | TORONTO BUTTONVILLE A | 12 | 24 | 17 | -0.65 | 18.65 | 0
8586 | TORONTO BUTTONVILLE A | 12 | 23 | 18 | 2.9 | 15.1 | 0
8586 | TORONTO BUTTONVILLE A | 12 | 24 | 18 | -1.025 | 19.025 | 0
8587 | TORONTO BUTTONVILLE A | 12 | 23 | 19 | 3.1 | 14.9 | 0
8587 | TORONTO BUTTONVILLE A | 12 | 24 | 19 | -1.55 | 19.55 | 0
8588 | TORONTO BUTTONVILLE A | 12 | 23 | 20 | 3.8 | 14.2 | 0
8588 | TORONTO BUTTONVILLE A | 12 | 24 | 20 | -1.875 | 19.875 | 0
8589 | TORONTO BUTTONVILLE A | 12 | 23 | 21 | 5.5 | 12.5 | 0
8589 | TORONTO BUTTONVILLE A | 12 | 24 | 21 | -1.85 | 19.85 | 0
8590 | TORONTO BUTTONVILLE A | 12 | 23 | 22 | 5.8 | 12.2 | 0
8590 | TORONTO BUTTONVILLE A | 12 | 24 | 22 | -1.725 | 19.725 | 0
8591 | TORONTO BUTTONVILLE A | 12 | 23 | 23 | 6.1 | 11.9 | 0
8591 | TORONTO BUTTONVILLE A | 12 | 24 | 23 | -1.75 | 19.75 | 0
8592 | TORONTO BUTTONVILLE A | 12 | 23 | 24 | 5.6 | 12.4 | 0
8592 | TORONTO BUTTONVILLE A | 12 | 24 | 24 | -1.7 | 19.7 | 0
8593 | TORONTO BUTTONVILLE A | 12 | 24 | 1 | 5.3 | 12.7 | 0
8593 | TORONTO BUTTONVILLE A | 12 | 25 | 1 | -1.775 | 19.775 | 0
8594 | TORONTO BUTTONVILLE A | 12 | 24 | 2 | 5.2 | 12.8 | 0
8594 | TORONTO BUTTONVILLE A | 12 | 25 | 2 | -1.65 | 19.65 | 0
8595 | TORONTO BUTTONVILLE A | 12 | 24 | 3 | 4.4 | 13.6 | 0
8595 | TORONTO BUTTONVILLE A | 12 | 25 | 3 | -1.825 | 19.825 | 0
8596 | TORONTO BUTTONVILLE A | 12 | 24 | 4 | 4.4 | 13.6 | 0
8596 | TORONTO BUTTONVILLE A | 12 | 25 | 4 | -2.1 | 20.1 | 0
8597 | TORONTO BUTTONVILLE A | 12 | 24 | 5 | 4.4 | 13.6 | 0
8597 | TORONTO BUTTONVILLE A | 12 | 25 | 5 | -2.25 | 20.25 | 0
8598 | TORONTO BUTTONVILLE A | 12 | 24 | 6 | 4.9 | 13.1 | 0
8598 | TORONTO BUTTONVILLE A | 12 | 25 | 6 | -2.425 | 20.425 | 0
8599 | TORONTO BUTTONVILLE A | 12 | 24 | 7 | 5.7 | 12.3 | 0
8599 | TORONTO BUTTONVILLE A | 12 | 25 | 7 | -2.575 | 20.575 | 0
8600 | TORONTO BUTTONVILLE A | 12 | 24 | 8 | 6 | 12 | 0
8600 | TORONTO BUTTONVILLE A | 12 | 25 | 8 | -2.6 | 20.6 | 0
8601 | TORONTO BUTTONVILLE A | 12 | 24 | 9 | 7.1 | 10.9 | 0
8601 | TORONTO BUTTONVILLE A | 12 | 25 | 9 | -2.725 | 20.725 | 0
8602 | TORONTO BUTTONVILLE A | 12 | 24 | 10 | 8.2 | 9.8 | 0
8602 | TORONTO BUTTONVILLE A | 12 | 25 | 10 | -1.75 | 19.75 | 0
8603 | TORONTO BUTTONVILLE A | 12 | 24 | 11 | 8.3 | 9.7 | 0
8603 | TORONTO BUTTONVILLE A | 12 | 25 | 11 | -1.325 | 19.325 | 0
8604 | TORONTO BUTTONVILLE A | 12 | 24 | 12 | 9 | 9 | 0
8604 | TORONTO BUTTONVILLE A | 12 | 25 | 12 | -0.6 | 18.6 | 0
8605 | TORONTO BUTTONVILLE A | 12 | 24 | 13 | 8.4 | 9.6 | 0
8605 | TORONTO BUTTONVILLE A | 12 | 25 | 13 | 0.075 | 17.925 | 0
8606 | TORONTO BUTTONVILLE A | 12 | 24 | 14 | 4.3 | 13.7 | 0
8606 | TORONTO BUTTONVILLE A | 12 | 25 | 14 | 0.2 | 17.8 | 0
8607 | TORONTO BUTTONVILLE A | 12 | 24 | 15 | 3.5 | 14.5 | 0
8607 | TORONTO BUTTONVILLE A | 12 | 25 | 15 | 0.375 | 17.625 | 0
8608 | TORONTO BUTTONVILLE A | 12 | 24 | 16 | 2.5 | 15.5 | 0
8608 | TORONTO BUTTONVILLE A | 12 | 25 | 16 | 0.4 | 17.6 | 0
8609 | TORONTO BUTTONVILLE A | 12 | 24 | 17 | 2.4 | 15.6 | 0
8609 | TORONTO BUTTONVILLE A | 12 | 25 | 17 | 0.05 | 17.95 | 0
8610 | TORONTO BUTTONVILLE A | 12 | 24 | 18 | 1.4 | 16.6 | 0
8610 | TORONTO BUTTONVILLE A | 12 | 25 | 18 | -0.45 | 18.45 | 0
8611 | TORONTO BUTTONVILLE A | 12 | 24 | 19 | 0.5 | 17.5 | 0
8611 | TORONTO BUTTONVILLE A | 12 | 25 | 19 | -0.975 | 18.975 | 0
8612 | TORONTO BUTTONVILLE A | 12 | 24 | 20 | -0.7 | 18.7 | 0
8612 | TORONTO BUTTONVILLE A | 12 | 25 | 20 | -1.25 | 19.25 | 0
8613 | TORONTO BUTTONVILLE A | 12 | 24 | 21 | -1.2 | 19.2 | 0
8613 | TORONTO BUTTONVILLE A | 12 | 25 | 21 | -1.575 | 19.575 | 0
8614 | TORONTO BUTTONVILLE A | 12 | 24 | 22 | -1.5 | 19.5 | 0
8614 | TORONTO BUTTONVILLE A | 12 | 25 | 22 | -1.75 | 19.75 | 0
8615 | TORONTO BUTTONVILLE A | 12 | 24 | 23 | -2 | 20 | 0
8615 | TORONTO BUTTONVILLE A | 12 | 25 | 23 | -1.9 | 19.9 | 0
8616 | TORONTO BUTTONVILLE A | 12 | 24 | 24 | -2.3 | 20.3 | 0
8616 | TORONTO BUTTONVILLE A | 12 | 25 | 24 | -2.25 | 20.25 | 0
8617 | TORONTO BUTTONVILLE A | 12 | 25 | 1 | -2.2 | 20.2 | 0
8617 | TORONTO BUTTONVILLE A | 12 | 26 | 1 | -2.375 | 20.375 | 0
8618 | TORONTO BUTTONVILLE A | 12 | 25 | 2 | -2.2 | 20.2 | 0
8618 | TORONTO BUTTONVILLE A | 12 | 26 | 2 | -2.575 | 20.575 | 0
8619 | TORONTO BUTTONVILLE A | 12 | 25 | 3 | -2.1 | 20.1 | 0
8619 | TORONTO BUTTONVILLE A | 12 | 26 | 3 | -3 | 21 | 0
8620 | TORONTO BUTTONVILLE A | 12 | 25 | 4 | -2.1 | 20.1 | 0
8620 | TORONTO BUTTONVILLE A | 12 | 26 | 4 | -3.475 | 21.475 | 0
8621 | TORONTO BUTTONVILLE A | 12 | 25 | 5 | -2.1 | 20.1 | 0
8621 | TORONTO BUTTONVILLE A | 12 | 26 | 5 | -3.625 | 21.625 | 0
8622 | TORONTO BUTTONVILLE A | 12 | 25 | 6 | -2.4 | 20.4 | 0
8622 | TORONTO BUTTONVILLE A | 12 | 26 | 6 | -3.75 | 21.75 | 0
8623 | TORONTO BUTTONVILLE A | 12 | 25 | 7 | -2 | 20 | 0
8623 | TORONTO BUTTONVILLE A | 12 | 26 | 7 | -3.6 | 21.6 | 0
8624 | TORONTO BUTTONVILLE A | 12 | 25 | 8 | -2.3 | 20.3 | 0
8624 | TORONTO BUTTONVILLE A | 12 | 26 | 8 | -3.65 | 21.65 | 0
8625 | TORONTO BUTTONVILLE A | 12 | 25 | 9 | -2.2 | 20.2 | 0
8625 | TORONTO BUTTONVILLE A | 12 | 26 | 9 | -3.625 | 21.625 | 0
8626 | TORONTO BUTTONVILLE A | 12 | 25 | 10 | -1.9 | 19.9 | 0
8626 | TORONTO BUTTONVILLE A | 12 | 26 | 10 | -3.25 | 21.25 | 0
8627 | TORONTO BUTTONVILLE A | 12 | 25 | 11 | -1.4 | 19.4 | 0
8627 | TORONTO BUTTONVILLE A | 12 | 26 | 11 | -2.675 | 20.675 | 0
8628 | TORONTO BUTTONVILLE A | 12 | 25 | 12 | -1.1 | 19.1 | 0
8628 | TORONTO BUTTONVILLE A | 12 | 26 | 12 | -2.275 | 20.275 | 0
8629 | TORONTO BUTTONVILLE A | 12 | 25 | 13 | -1.5 | 19.5 | 0
8629 | TORONTO BUTTONVILLE A | 12 | 26 | 13 | -2 | 20 | 0
8630 | TORONTO BUTTONVILLE A | 12 | 25 | 14 | -1.7 | 19.7 | 0
8630 | TORONTO BUTTONVILLE A | 12 | 26 | 14 | -1.825 | 19.825 | 0
8631 | TORONTO BUTTONVILLE A | 12 | 25 | 15 | -2.2 | 20.2 | 0
8631 | TORONTO BUTTONVILLE A | 12 | 26 | 15 | -1.8 | 19.8 | 0
8632 | TORONTO BUTTONVILLE A | 12 | 25 | 16 | -2.3 | 20.3 | 0
8632 | TORONTO BUTTONVILLE A | 12 | 26 | 16 | -1.95 | 19.95 | 0
8633 | TORONTO BUTTONVILLE A | 12 | 25 | 17 | -2.3 | 20.3 | 0
8633 | TORONTO BUTTONVILLE A | 12 | 26 | 17 | -2.55 | 20.55 | 0
8634 | TORONTO BUTTONVILLE A | 12 | 25 | 18 | -2.5 | 20.5 | 0
8634 | TORONTO BUTTONVILLE A | 12 | 26 | 18 | -3.225 | 21.225 | 0
8635 | TORONTO BUTTONVILLE A | 12 | 25 | 19 | -3.2 | 21.2 | 0
8635 | TORONTO BUTTONVILLE A | 12 | 26 | 19 | -3.625 | 21.625 | 0
8636 | TORONTO BUTTONVILLE A | 12 | 25 | 20 | -3.9 | 21.9 | 0
8636 | TORONTO BUTTONVILLE A | 12 | 26 | 20 | -4.025 | 22.025 | 0
8637 | TORONTO BUTTONVILLE A | 12 | 25 | 21 | -4.2 | 22.2 | 0
8637 | TORONTO BUTTONVILLE A | 12 | 26 | 21 | -4.175 | 22.175 | 0
8638 | TORONTO BUTTONVILLE A | 12 | 25 | 22 | -4.5 | 22.5 | 0
8638 | TORONTO BUTTONVILLE A | 12 | 26 | 22 | -4.825 | 22.825 | 0
8639 | TORONTO BUTTONVILLE A | 12 | 25 | 23 | -4.9 | 22.9 | 0
8639 | TORONTO BUTTONVILLE A | 12 | 26 | 23 | -5.45 | 23.45 | 0
8640 | TORONTO BUTTONVILLE A | 12 | 25 | 24 | -5.3 | 23.3 | 0
8640 | TORONTO BUTTONVILLE A | 12 | 26 | 24 | -5.775 | 23.775 | 0
8641 | TORONTO BUTTONVILLE A | 12 | 26 | 1 | -5.3 | 23.3 | 0
8641 | TORONTO BUTTONVILLE A | 12 | 27 | 1 | -6.525 | 24.525 | 0
8642 | TORONTO BUTTONVILLE A | 12 | 26 | 2 | -4.9 | 22.9 | 0
8642 | TORONTO BUTTONVILLE A | 12 | 27 | 2 | -6.9 | 24.9 | 0
8643 | TORONTO BUTTONVILLE A | 12 | 26 | 3 | -4.9 | 22.9 | 0
8643 | TORONTO BUTTONVILLE A | 12 | 27 | 3 | -6.975 | 24.975 | 0
8644 | TORONTO BUTTONVILLE A | 12 | 26 | 4 | -4.8 | 22.8 | 0
8644 | TORONTO BUTTONVILLE A | 12 | 27 | 4 | -6.975 | 24.975 | 0
8645 | TORONTO BUTTONVILLE A | 12 | 26 | 5 | -4.7 | 22.7 | 0
8645 | TORONTO BUTTONVILLE A | 12 | 27 | 5 | -7.025 | 25.025 | 0
8646 | TORONTO BUTTONVILLE A | 12 | 26 | 6 | -4.2 | 22.2 | 0
8646 | TORONTO BUTTONVILLE A | 12 | 27 | 6 | -7.05 | 25.05 | 0
8647 | TORONTO BUTTONVILLE A | 12 | 26 | 7 | -4.5 | 22.5 | 0
8647 | TORONTO BUTTONVILLE A | 12 | 27 | 7 | -7.025 | 25.025 | 0
8648 | TORONTO BUTTONVILLE A | 12 | 26 | 8 | -4.8 | 22.8 | 0
8648 | TORONTO BUTTONVILLE A | 12 | 27 | 8 | -6.975 | 24.975 | 0
8649 | TORONTO BUTTONVILLE A | 12 | 26 | 9 | -4.9 | 22.9 | 0
8649 | TORONTO BUTTONVILLE A | 12 | 27 | 9 | -6.625 | 24.625 | 0
8650 | TORONTO BUTTONVILLE A | 12 | 26 | 10 | -4.9 | 22.9 | 0
8650 | TORONTO BUTTONVILLE A | 12 | 27 | 10 | -6.075 | 24.075 | 0
8651 | TORONTO BUTTONVILLE A | 12 | 26 | 11 | -4.6 | 22.6 | 0
8651 | TORONTO BUTTONVILLE A | 12 | 27 | 11 | -4.65 | 22.65 | 0
8652 | TORONTO BUTTONVILLE A | 12 | 26 | 12 | -4.1 | 22.1 | 0
8652 | TORONTO BUTTONVILLE A | 12 | 27 | 12 | -3.55 | 21.55 | 0
8653 | TORONTO BUTTONVILLE A | 12 | 26 | 13 | -3.7 | 21.7 | 0
8653 | TORONTO BUTTONVILLE A | 12 | 27 | 13 | -3.975 | 21.975 | 0
8654 | TORONTO BUTTONVILLE A | 12 | 26 | 14 | -3.2 | 21.2 | 0
8654 | TORONTO BUTTONVILLE A | 12 | 27 | 14 | -3.75 | 21.75 | 0
8655 | TORONTO BUTTONVILLE A | 12 | 26 | 15 | -3 | 21 | 0
8655 | TORONTO BUTTONVILLE A | 12 | 27 | 15 | -4.15 | 22.15 | 0
8656 | TORONTO BUTTONVILLE A | 12 | 26 | 16 | -3.2 | 21.2 | 0
8656 | TORONTO BUTTONVILLE A | 12 | 27 | 16 | -4.325 | 22.325 | 0
8657 | TORONTO BUTTONVILLE A | 12 | 26 | 17 | -2.8 | 20.8 | 0
8657 | TORONTO BUTTONVILLE A | 12 | 27 | 17 | -4.475 | 22.475 | 0
8658 | TORONTO BUTTONVILLE A | 12 | 26 | 18 | -2.8 | 20.8 | 0
8658 | TORONTO BUTTONVILLE A | 12 | 27 | 18 | -4.525 | 22.525 | 0
8659 | TORONTO BUTTONVILLE A | 12 | 26 | 19 | -2.9 | 20.9 | 0
8659 | TORONTO BUTTONVILLE A | 12 | 27 | 19 | -4.325 | 22.325 | 0
8660 | TORONTO BUTTONVILLE A | 12 | 26 | 20 | -3.1 | 21.1 | 0
8660 | TORONTO BUTTONVILLE A | 12 | 27 | 20 | -4.5 | 22.5 | 0
8661 | TORONTO BUTTONVILLE A | 12 | 26 | 21 | -3.2 | 21.2 | 0
8661 | TORONTO BUTTONVILLE A | 12 | 27 | 21 | -4.675 | 22.675 | 0
8662 | TORONTO BUTTONVILLE A | 12 | 26 | 22 | -2.9 | 20.9 | 0
8662 | TORONTO BUTTONVILLE A | 12 | 27 | 22 | -4.725 | 22.725 | 0
8663 | TORONTO BUTTONVILLE A | 12 | 26 | 23 | -3.5 | 21.5 | 0
8663 | TORONTO BUTTONVILLE A | 12 | 27 | 23 | -4.775 | 22.775 | 0
8664 | TORONTO BUTTONVILLE A | 12 | 26 | 24 | -3.8 | 21.8 | 0
8664 | TORONTO BUTTONVILLE A | 12 | 27 | 24 | -4.65 | 22.65 | 0
8665 | TORONTO BUTTONVILLE A | 12 | 27 | 1 | -3.5 | 21.5 | 0
8665 | TORONTO BUTTONVILLE A | 12 | 28 | 1 | -4.65 | 22.65 | 0
8666 | TORONTO BUTTONVILLE A | 12 | 27 | 2 | -3 | 21 | 0
8666 | TORONTO BUTTONVILLE A | 12 | 28 | 2 | -4.725 | 22.725 | 0
8667 | TORONTO BUTTONVILLE A | 12 | 27 | 3 | -3 | 21 | 0
8667 | TORONTO BUTTONVILLE A | 12 | 28 | 3 | -4.675 | 22.675 | 0
8668 | TORONTO BUTTONVILLE A | 12 | 27 | 4 | -3 | 21 | 0
8668 | TORONTO BUTTONVILLE A | 12 | 28 | 4 | -4.3 | 22.3 | 0
8669 | TORONTO BUTTONVILLE A | 12 | 27 | 5 | -3.1 | 21.1 | 0
8669 | TORONTO BUTTONVILLE A | 12 | 28 | 5 | -4.05 | 22.05 | 0
8670 | TORONTO BUTTONVILLE A | 12 | 27 | 6 | -3 | 21 | 0
8670 | TORONTO BUTTONVILLE A | 12 | 28 | 6 | -3.65 | 21.65 | 0
8671 | TORONTO BUTTONVILLE A | 12 | 27 | 7 | -3 | 21 | 0
8671 | TORONTO BUTTONVILLE A | 12 | 28 | 7 | -3.85 | 21.85 | 0
8672 | TORONTO BUTTONVILLE A | 12 | 27 | 8 | -2.9 | 20.9 | 0
8672 | TORONTO BUTTONVILLE A | 12 | 28 | 8 | -3.7 | 21.7 | 0
8673 | TORONTO BUTTONVILLE A | 12 | 27 | 9 | -2.9 | 20.9 | 0
8673 | TORONTO BUTTONVILLE A | 12 | 28 | 9 | -3.05 | 21.05 | 0
8674 | TORONTO BUTTONVILLE A | 12 | 27 | 10 | -2.6 | 20.6 | 0
8674 | TORONTO BUTTONVILLE A | 12 | 28 | 10 | -2.425 | 20.425 | 0
8675 | TORONTO BUTTONVILLE A | 12 | 27 | 11 | -1.9 | 19.9 | 0
8675 | TORONTO BUTTONVILLE A | 12 | 28 | 11 | -1.975 | 19.975 | 0
8676 | TORONTO BUTTONVILLE A | 12 | 27 | 12 | -1.7 | 19.7 | 0
8676 | TORONTO BUTTONVILLE A | 12 | 28 | 12 | -1.125 | 19.125 | 0
8677 | TORONTO BUTTONVILLE A | 12 | 27 | 13 | -1.4 | 19.4 | 0
8677 | TORONTO BUTTONVILLE A | 12 | 28 | 13 | -0.375 | 18.375 | 0
8678 | TORONTO BUTTONVILLE A | 12 | 27 | 14 | -1.1 | 19.1 | 0
8678 | TORONTO BUTTONVILLE A | 12 | 28 | 14 | -0.1 | 18.1 | 0
8679 | TORONTO BUTTONVILLE A | 12 | 27 | 15 | -0.5 | 18.5 | 0
8679 | TORONTO BUTTONVILLE A | 12 | 28 | 15 | 0.1 | 17.9 | 0
8680 | TORONTO BUTTONVILLE A | 12 | 27 | 16 | -0.4 | 18.4 | 0
8680 | TORONTO BUTTONVILLE A | 12 | 28 | 16 | 0.425 | 17.575 | 0
8681 | TORONTO BUTTONVILLE A | 12 | 27 | 17 | -0.6 | 18.6 | 0
8681 | TORONTO BUTTONVILLE A | 12 | 28 | 17 | 0.15 | 17.85 | 0
8682 | TORONTO BUTTONVILLE A | 12 | 27 | 18 | -0.7 | 18.7 | 0
8682 | TORONTO BUTTONVILLE A | 12 | 28 | 18 | -0.225 | 18.225 | 0
8683 | TORONTO BUTTONVILLE A | 12 | 27 | 19 | -0.8 | 18.8 | 0
8683 | TORONTO BUTTONVILLE A | 12 | 28 | 19 | -0.875 | 18.875 | 0
8684 | TORONTO BUTTONVILLE A | 12 | 27 | 20 | -0.1 | 18.1 | 0
8684 | TORONTO BUTTONVILLE A | 12 | 28 | 20 | -1.5 | 19.5 | 0
8685 | TORONTO BUTTONVILLE A | 12 | 27 | 21 | 0.8 | 17.2 | 0
8685 | TORONTO BUTTONVILLE A | 12 | 28 | 21 | -1.6 | 19.6 | 0
8686 | TORONTO BUTTONVILLE A | 12 | 27 | 22 | 1.1 | 16.9 | 0
8686 | TORONTO BUTTONVILLE A | 12 | 28 | 22 | -1.575 | 19.575 | 0
8687 | TORONTO BUTTONVILLE A | 12 | 27 | 23 | 1.1 | 16.9 | 0
8687 | TORONTO BUTTONVILLE A | 12 | 28 | 23 | -2.35 | 20.35 | 0
8688 | TORONTO BUTTONVILLE A | 12 | 27 | 24 | 1.2 | 16.8 | 0
8688 | TORONTO BUTTONVILLE A | 12 | 28 | 24 | -2.7 | 20.7 | 0
8689 | TORONTO BUTTONVILLE A | 12 | 28 | 1 | 1.2 | 16.8 | 0
8689 | TORONTO BUTTONVILLE A | 12 | 29 | 1 | -2.825 | 20.825 | 0
8690 | TORONTO BUTTONVILLE A | 12 | 28 | 2 | 1.5 | 16.5 | 0
8690 | TORONTO BUTTONVILLE A | 12 | 29 | 2 | -3.35 | 21.35 | 0
8691 | TORONTO BUTTONVILLE A | 12 | 28 | 3 | 2.3 | 15.7 | 0
8691 | TORONTO BUTTONVILLE A | 12 | 29 | 3 | -3.75 | 21.75 | 0
8692 | TORONTO BUTTONVILLE A | 12 | 28 | 4 | 3.1 | 14.9 | 0
8692 | TORONTO BUTTONVILLE A | 12 | 29 | 4 | -4.1 | 22.1 | 0
8693 | TORONTO BUTTONVILLE A | 12 | 28 | 5 | 3.1 | 14.9 | 0
8693 | TORONTO BUTTONVILLE A | 12 | 29 | 5 | -4.425 | 22.425 | 0
8694 | TORONTO BUTTONVILLE A | 12 | 28 | 6 | 3.4 | 14.6 | 0
8694 | TORONTO BUTTONVILLE A | 12 | 29 | 6 | -4.775 | 22.775 | 0
8695 | TORONTO BUTTONVILLE A | 12 | 28 | 7 | 3.7 | 14.3 | 0
8695 | TORONTO BUTTONVILLE A | 12 | 29 | 7 | -5 | 23 | 0
8696 | TORONTO BUTTONVILLE A | 12 | 28 | 8 | 3.9 | 14.1 | 0
8696 | TORONTO BUTTONVILLE A | 12 | 29 | 8 | -5.25 | 23.25 | 0
8697 | TORONTO BUTTONVILLE A | 12 | 28 | 9 | 3.9 | 14.1 | 0
8697 | TORONTO BUTTONVILLE A | 12 | 29 | 9 | -5.5 | 23.5 | 0
8698 | TORONTO BUTTONVILLE A | 12 | 28 | 10 | 3 | 15 | 0
8698 | TORONTO BUTTONVILLE A | 12 | 29 | 10 | -5.475 | 23.475 | 0
8699 | TORONTO BUTTONVILLE A | 12 | 28 | 11 | 2.1 | 15.9 | 0
8699 | TORONTO BUTTONVILLE A | 12 | 29 | 11 | -5.15 | 23.15 | 0
8700 | TORONTO BUTTONVILLE A | 12 | 28 | 12 | 2.5 | 15.5 | 0
8700 | TORONTO BUTTONVILLE A | 12 | 29 | 12 | -4.45 | 22.45 | 0
8701 | TORONTO BUTTONVILLE A | 12 | 28 | 13 | 2.2 | 15.8 | 0
8701 | TORONTO BUTTONVILLE A | 12 | 29 | 13 | -3.525 | 21.525 | 0
8702 | TORONTO BUTTONVILLE A | 12 | 28 | 14 | 1.9 | 16.1 | 0
8702 | TORONTO BUTTONVILLE A | 12 | 29 | 14 | -3.8 | 21.8 | 0
8703 | TORONTO BUTTONVILLE A | 12 | 28 | 15 | 1.8 | 16.2 | 0
8703 | TORONTO BUTTONVILLE A | 12 | 29 | 15 | -3.7 | 21.7 | 0
8704 | TORONTO BUTTONVILLE A | 12 | 28 | 16 | 1.4 | 16.6 | 0
8704 | TORONTO BUTTONVILLE A | 12 | 29 | 16 | -3.625 | 21.625 | 0
8705 | TORONTO BUTTONVILLE A | 12 | 28 | 17 | 1.1 | 16.9 | 0
8705 | TORONTO BUTTONVILLE A | 12 | 29 | 17 | -3.875 | 21.875 | 0
8706 | TORONTO BUTTONVILLE A | 12 | 28 | 18 | 0.3 | 17.7 | 0
8706 | TORONTO BUTTONVILLE A | 12 | 29 | 18 | -4.225 | 22.225 | 0
8707 | TORONTO BUTTONVILLE A | 12 | 28 | 19 | -0.7 | 18.7 | 0
8707 | TORONTO BUTTONVILLE A | 12 | 29 | 19 | -4.925 | 22.925 | 0
8708 | TORONTO BUTTONVILLE A | 12 | 28 | 20 | -1.5 | 19.5 | 0
8708 | TORONTO BUTTONVILLE A | 12 | 29 | 20 | -5.4 | 23.4 | 0
8709 | TORONTO BUTTONVILLE A | 12 | 28 | 21 | -1.8 | 19.8 | 0
8709 | TORONTO BUTTONVILLE A | 12 | 29 | 21 | -5.5 | 23.5 | 0
8710 | TORONTO BUTTONVILLE A | 12 | 28 | 22 | -2.4 | 20.4 | 0
8710 | TORONTO BUTTONVILLE A | 12 | 29 | 22 | -5.725 | 23.725 | 0
8711 | TORONTO BUTTONVILLE A | 12 | 28 | 23 | -2.6 | 20.6 | 0
8711 | TORONTO BUTTONVILLE A | 12 | 29 | 23 | -5.55 | 23.55 | 0
8712 | TORONTO BUTTONVILLE A | 12 | 28 | 24 | -3.3 | 21.3 | 0
8712 | TORONTO BUTTONVILLE A | 12 | 29 | 24 | -5.15 | 23.15 | 0
8713 | TORONTO BUTTONVILLE A | 12 | 29 | 1 | -3.1 | 21.1 | 0
8713 | TORONTO BUTTONVILLE A | 12 | 30 | 1 | -4.65 | 22.65 | 0
8714 | TORONTO BUTTONVILLE A | 12 | 29 | 2 | -3.7 | 21.7 | 0
8714 | TORONTO BUTTONVILLE A | 12 | 30 | 2 | -4.7 | 22.7 | 0
8715 | TORONTO BUTTONVILLE A | 12 | 29 | 3 | -4.3 | 22.3 | 0
8715 | TORONTO BUTTONVILLE A | 12 | 30 | 3 | -4.1 | 22.1 | 0
8716 | TORONTO BUTTONVILLE A | 12 | 29 | 4 | -4.8 | 22.8 | 0
8716 | TORONTO BUTTONVILLE A | 12 | 30 | 4 | -4.5 | 22.5 | 0
8717 | TORONTO BUTTONVILLE A | 12 | 29 | 5 | -4.7 | 22.7 | 0
8717 | TORONTO BUTTONVILLE A | 12 | 30 | 5 | -4.5 | 22.5 | 0
8718 | TORONTO BUTTONVILLE A | 12 | 29 | 6 | -4.5 | 22.5 | 0
8718 | TORONTO BUTTONVILLE A | 12 | 30 | 6 | -4.6 | 22.6 | 0
8719 | TORONTO BUTTONVILLE A | 12 | 29 | 7 | -4.7 | 22.7 | 0
8719 | TORONTO BUTTONVILLE A | 12 | 30 | 7 | -4.125 | 22.125 | 0
8720 | TORONTO BUTTONVILLE A | 12 | 29 | 8 | -5.5 | 23.5 | 0
8720 | TORONTO BUTTONVILLE A | 12 | 30 | 8 | -4.3 | 22.3 | 0
8721 | TORONTO BUTTONVILLE A | 12 | 29 | 9 | -5 | 23 | 0
8721 | TORONTO BUTTONVILLE A | 12 | 30 | 9 | -4 | 22 | 0
8722 | TORONTO BUTTONVILLE A | 12 | 29 | 10 | -4.5 | 22.5 | 0
8722 | TORONTO BUTTONVILLE A | 12 | 30 | 10 | -3.625 | 21.625 | 0
8723 | TORONTO BUTTONVILLE A | 12 | 29 | 11 | -3.7 | 21.7 | 0
8723 | TORONTO BUTTONVILLE A | 12 | 30 | 11 | -2.85 | 20.85 | 0
8724 | TORONTO BUTTONVILLE A | 12 | 29 | 12 | -2.8 | 20.8 | 0
8724 | TORONTO BUTTONVILLE A | 12 | 30 | 12 | -1.625 | 19.625 | 0
8725 | TORONTO BUTTONVILLE A | 12 | 29 | 13 | -2.5 | 20.5 | 0
8725 | TORONTO BUTTONVILLE A | 12 | 30 | 13 | -0.85 | 18.85 | 0
8726 | TORONTO BUTTONVILLE A | 12 | 29 | 14 | -2.1 | 20.1 | 0
8726 | TORONTO BUTTONVILLE A | 12 | 30 | 14 | 0.075 | 17.925 | 0
8727 | TORONTO BUTTONVILLE A | 12 | 29 | 15 | -2.4 | 20.4 | 0
8727 | TORONTO BUTTONVILLE A | 12 | 30 | 15 | 0.475 | 17.525 | 0
8728 | TORONTO BUTTONVILLE A | 12 | 29 | 16 | -2.3 | 20.3 | 0
8728 | TORONTO BUTTONVILLE A | 12 | 30 | 16 | 0.325 | 17.675 | 0
8729 | TORONTO BUTTONVILLE A | 12 | 29 | 17 | -2.8 | 20.8 | 0
8729 | TORONTO BUTTONVILLE A | 12 | 30 | 17 | -0.5 | 18.5 | 0
8730 | TORONTO BUTTONVILLE A | 12 | 29 | 18 | -2.9 | 20.9 | 0
8730 | TORONTO BUTTONVILLE A | 12 | 30 | 18 | -1.2 | 19.2 | 0
8731 | TORONTO BUTTONVILLE A | 12 | 29 | 19 | -3.4 | 21.4 | 0
8731 | TORONTO BUTTONVILLE A | 12 | 30 | 19 | -1.925 | 19.925 | 0
8732 | TORONTO BUTTONVILLE A | 12 | 29 | 20 | -3.7 | 21.7 | 0
8732 | TORONTO BUTTONVILLE A | 12 | 30 | 20 | -2.7 | 20.7 | 0
8733 | TORONTO BUTTONVILLE A | 12 | 29 | 21 | -4.3 | 22.3 | 0
8733 | TORONTO BUTTONVILLE A | 12 | 30 | 21 | -3.25 | 21.25 | 0
8734 | TORONTO BUTTONVILLE A | 12 | 29 | 22 | -4.7 | 22.7 | 0
8734 | TORONTO BUTTONVILLE A | 12 | 30 | 22 | -3.625 | 21.625 | 0
8735 | TORONTO BUTTONVILLE A | 12 | 29 | 23 | -4.9 | 22.9 | 0
8735 | TORONTO BUTTONVILLE A | 12 | 30 | 23 | -3.9 | 21.9 | 0
8736 | TORONTO BUTTONVILLE A | 12 | 29 | 24 | -5.1 | 23.1 | 0
8736 | TORONTO BUTTONVILLE A | 12 | 30 | 24 | -4.5 | 22.5 | 0
8737 | TORONTO BUTTONVILLE A | 12 | 30 | 1 | -4.7 | 22.7 | 0
8737 | TORONTO BUTTONVILLE A | 12 | 31 | 1 | -5.125 | 23.125 | 0
8738 | TORONTO BUTTONVILLE A | 12 | 30 | 2 | -4.5 | 22.5 | 0
8738 | TORONTO BUTTONVILLE A | 12 | 31 | 2 | -5.275 | 23.275 | 0
8739 | TORONTO BUTTONVILLE A | 12 | 30 | 3 | -4.6 | 22.6 | 0
8739 | TORONTO BUTTONVILLE A | 12 | 31 | 3 | -5.75 | 23.75 | 0
8740 | TORONTO BUTTONVILLE A | 12 | 30 | 4 | -3.8 | 21.8 | 0
8740 | TORONTO BUTTONVILLE A | 12 | 31 | 4 | -6.4 | 24.4 | 0
8741 | TORONTO BUTTONVILLE A | 12 | 30 | 5 | -2 | 20 | 0
8741 | TORONTO BUTTONVILLE A | 12 | 31 | 5 | -6.6 | 24.6 | 0
8742 | TORONTO BUTTONVILLE A | 12 | 30 | 6 | -1.6 | 19.6 | 0
8742 | TORONTO BUTTONVILLE A | 12 | 31 | 6 | -6.725 | 24.725 | 0
8743 | TORONTO BUTTONVILLE A | 12 | 30 | 7 | -3 | 21 | 0
8743 | TORONTO BUTTONVILLE A | 12 | 31 | 7 | -6.6 | 24.6 | 0
8744 | TORONTO BUTTONVILLE A | 12 | 30 | 8 | -3 | 21 | 0
8744 | TORONTO BUTTONVILLE A | 12 | 31 | 8 | -6.475 | 24.475 | 0
8745 | TORONTO BUTTONVILLE A | 12 | 30 | 9 | -2.5 | 20.5 | 0
8745 | TORONTO BUTTONVILLE A | 12 | 31 | 9 | -6.4 | 24.4 | 0
8746 | TORONTO BUTTONVILLE A | 12 | 30 | 10 | -2 | 20 | 0
8746 | TORONTO BUTTONVILLE A | 12 | 31 | 10 | -5.65 | 23.65 | 0
8747 | TORONTO BUTTONVILLE A | 12 | 30 | 11 | -0.3 | 18.3 | 0
8747 | TORONTO BUTTONVILLE A | 12 | 31 | 11 | -4.65 | 22.65 | 0
8748 | TORONTO BUTTONVILLE A | 12 | 30 | 12 | -0.2 | 18.2 | 0
8748 | TORONTO BUTTONVILLE A | 12 | 31 | 12 | -3.75 | 21.75 | 0
8749 | TORONTO BUTTONVILLE A | 12 | 30 | 13 | 0 | 18 | 0
8749 | TORONTO BUTTONVILLE A | 12 | 31 | 13 | -2.975 | 20.975 | 0
8750 | TORONTO BUTTONVILLE A | 12 | 30 | 14 | 1.3 | 16.7 | 0
8750 | TORONTO BUTTONVILLE A | 12 | 31 | 14 | -2.375 | 20.375 | 0
8751 | TORONTO BUTTONVILLE A | 12 | 30 | 15 | 3 | 15 | 0
8751 | TORONTO BUTTONVILLE A | 12 | 31 | 15 | -2.3 | 20.3 | 0
8752 | TORONTO BUTTONVILLE A | 12 | 30 | 16 | 3.5 | 14.5 | 0
8752 | TORONTO BUTTONVILLE A | 12 | 31 | 16 | -2.1 | 20.1 | 0
8753 | TORONTO BUTTONVILLE A | 12 | 30 | 17 | 4 | 14 | 0
8753 | TORONTO BUTTONVILLE A | 12 | 31 | 17 | -2.35 | 20.35 | 0
8754 | TORONTO BUTTONVILLE A | 12 | 30 | 18 | 4.2 | 13.8 | 0
8754 | TORONTO BUTTONVILLE A | 12 | 31 | 18 | -2.825 | 20.825 | 0
8755 | TORONTO BUTTONVILLE A | 12 | 30 | 19 | 4.3 | 13.7 | 0
8755 | TORONTO BUTTONVILLE A | 12 | 31 | 19 | -3.05 | 21.05 | 0
8756 | TORONTO BUTTONVILLE A | 12 | 30 | 20 | 4.6 | 13.4 | 0
8756 | TORONTO BUTTONVILLE A | 12 | 31 | 20 | -3.3 | 21.3 | 0
8757 | TORONTO BUTTONVILLE A | 12 | 30 | 21 | 4.5 | 13.5 | 0
8757 | TORONTO BUTTONVILLE A | 12 | 31 | 21 | -3.55 | 21.55 | 0
8758 | TORONTO BUTTONVILLE A | 12 | 30 | 22 | 3.8 | 14.2 | 0
8758 | TORONTO BUTTONVILLE A | 12 | 31 | 22 | -3.35 | 21.35 | 0
8759 | TORONTO BUTTONVILLE A | 12 | 30 | 23 | 3 | 15 | 0
8759 | TORONTO BUTTONVILLE A | 12 | 31 | 23 | -3.3 | 21.3 | 0
8760 | TORONTO BUTTONVILLE A | 12 | 30 | 24 | 2.3 | 15.7 | 0
8760 | TORONTO BUTTONVILLE A | 12 | 31 | 24 | -3.55 | 21.55 | 0

## Res Home HPs
Total # of residential homes assumed to electrify space heating with heat pumps in each scenario
Tables below show calculations of residential household conversions based on scenario definitions.
The total number of residential homes assumed to electrify space heating with heat pumps in each scenario is:
|  | Electrification scenario | 6365582 | homes
|  | Diversified scenario | 2778772 | homes
Note that this electrification is incremental above the roughly 400,000 homes with heat pumps in 2020.
Electrification Scenario
Total Number of Households (IESO APO)
|  | 2020 | 2030 | 2040 | 2050
| Households (#millions) | 5.8157 | 6.56 | 7.19 | 7.9647
| New Builds (#millions) | 0 | 0.74426 | 0.63 | 0.77468
| Space Heating | Percent of households per technology type
|  | 2020 | 2030 | 2040 | 2050
| RNG / H2 Gas HP | 0% | 4% | 6% | 10%
| Electric ASHP | 6.954% | 14% | 52% | 75%
| Electric GSHP | 0% | 3.5% | 7% | 10%
| Hybrid | 0% | 0% | 0% | 0%
| Other | 11.43% | 10% | 8% | 5%
| Natural Gas Furnace | 81.61% | 68% | 27% | 0%
| Total | 100% | 99.5% | 100% | 100%
Percent of new builds per technology type
| RNG / H2 Gas HP | 10.17%
| Electric ASHP | 60.17%
| Electric GSHP | 29.65%
| Hybrid | 0%
| Total | 100%
| Space Heating | Incremental number of new households per technology type each year (millions)
|  | 2020 | 2030 | 2040 | 2050
| RNG / H2 Gas HP | 0 | 0.075727 | 0.064101 | 0.078822
| Electric ASHP | 0 | 0.44786 | 0.3791 | 0.46616
| Electric GSHP | 0 | 0.22068 | 0.1868 | 0.2297
| Check | 1 | 1 | 1 | 1
| Space Heating | Cumulative number of total households per technology type (millions)
|  | 2020 | 2030 | 2040 | 2050
| RNG / H2 Gas HP | 0 | 0.2624 | 0.4314 | 0.79647
| Electric ASHP | 0.4044 | 0.9184 | 3.7388 | 5.9735
| Electric GSHP | 0 | 0.2296 | 0.5033 | 0.79647
| Hybrid | 0 | 0 | 0 | 0
| Other | 0.6649 | 0.656 | 0.5752 | 0.39823
| Natural Gas Furnace | 4.7464 | 4.4608 | 1.9413 | 0
| Total | 5.8157 | 6.5272 | 7.19 | 7.9647
Total # of res. homes assumed to electrify space heat with heat pumps
6365582
Diversified Scenario
Total Number of Households (IESO APO)
|  | 2020 | 2030 | 2040 | 2050
| Households (#millions) | 5.8157 | 6.56 | 7.19 | 7.9647
| New Builds (#millions) | 0 | 0.74426 | 0.63 | 0.77468
| Space Heating | Percent of households per technology type
|  | 2020 | 2030 | 2040 | 2050
| RNG / H2 Gas HP | 0% | 6% | 34% | 55%
| Electric ASHP | 7% | 12.5% | 24% | 30%
| Electric GSHP | 0% | 3.5% | 7% | 10%
| Hybrid | 0% | 0% | 0% | 0%
| Other | 11% | 10% | 7% | 5%
| Natural Gas Furnace | 81.61% | 68% | 28% | 0%
| Total | 99.61% | 100% | 100% | 100%
Percent of new builds per technology type
| RNG / H2 Gas HP | 40.17%
| Electric ASHP | 30.17%
| Electric GSHP | 29.65%
| Hybrid | 0%
| Total | 100%
| Space Heating | Incremental number of new households per technology type each year (millions)
|  | 2020 | 2030 | 2040 | 2050
| RNG / H2 Gas HP | 0 | 0.29901 | 0.2531 | 0.31123
| Electric ASHP | 0 | 0.22458 | 0.1901 | 0.23376
| Electric GSHP | 0 | 0.22068 | 0.1868 | 0.2297
| Check | 1 | 1 | 1 | 1
| Space Heating | Cumulative number of total households per technology type (millions)
|  | 2020 | 2030 | 2040 | 2050
| RNG / H2 Gas HP | 0 | 0.3936 | 2.4446 | 4.3806
| Electric ASHP | 0.4071 | 0.82 | 1.7256 | 2.3894
| Electric GSHP | 0 | 0.2296 | 0.5033 | 0.79647
| Hybrid | 0 | 0 | 0 | 0
| Other | 0.63973 | 0.656 | 0.5033 | 0.39823
| Natural Gas Furnace | 4.7464 | 4.4608 | 2.0132 | 0
| Total | 5.7933 | 6.56 | 7.19 | 7.9647
Total # of res. homes assumed to electrify space heat with heat pumps
2778772
Equipment Conversion Pathways:
(Note that for Sensitivity 4, any starting category customer could get a hybrid HP)
Equipment Conversion Pathways:
(Note that for Sensitivity 4, any starting category customer could get a hybrid HP)
New Home Assumptions:
80% of added GSHPs are installed in new construction homes, the rest are retrofitted into existing homes
Of the remaining new construction homes, 50% install an ASHP and 50% install a gas HP
Equipment Conversion Pathways:
New Home Assumptions:
80% of added GSHPs are installed in new construction homes, the rest are retrofitted into existing homes
Of the remaining new construction homes, most install an ASHP and the remainder install a gas HP

## Peak Demand - RES and COM
Peak electricity demand projections separated by the residential and commercial sectors
The calculations use hourly electricity demand profiles for the "winter peak" representative day, by scenario, by subsector, and by decade.
The calculations sum (1) the residential and commercial subsectors' share of 2020 electric peak (e.g., "baseline"), and (2) the incremental new electric peak due to electrification.
Note that growth in incremental peak demand for buildings derives from electrification of space heating and other end uses (water heating, cooking, laundry, etc.), as well as demographic changes.
Electric peak demand by scenario, by subsector, and by decade (MW)
|  |  | Electrification Scenario |  | 2020 | 2030 | 2040 | 2050
|  |  |  | Total Residential electric peak (MW) | 8013.7575 | 16304.1309 | 33826.9739 | 37916.7926
|  |  |  | Total Commercial electric peak (MW) | 7699.4925 | 12377.3697 | 18420.8846 | 21813.6625
|  |  | Diversification Scenario |  | 2020 | 2030 | 2040 | 2050
|  |  |  | Total Residential electric peak (MW) | 8013.7575 | 13157.349 | 15801.6237 | 17210.8616
|  |  |  | Total Commercial electric peak (MW) | 7699.4925 | 11232.3068 | 12693.3685 | 14088.4569
| Electrification Scenario - Hourly Load Profile | [10 empty] | Diversified Scenario - Hourly Load Profile
[6 empty] | Decade |  | 2020 | 2030 | 2040 | 2050 | [5 empty] | Decade |  | 2020 | 2030 | 2040 | 2050
[6 empty] | Peak Hour |  | 18 | 8 | 8 | 8 | [5 empty] | Peak Hour |  | 18 | 8 | 23 | 23
[6 empty] | Baseline Peak | Baseline | 21525 | 20360 | 20360 | 20360 | [5 empty] | Baseline Peak | Baseline | 21525 | 20360 | 19163 | 19163
[6 empty] | Sum of Buildings Incremental Peak | Buildings | 0 | 13818.7006 | 37385.0585 | 44867.6551 | [5 empty] | Sum of Buildings Incremental Peak | Buildings | 0 | 9526.8558 | 14506.0022 | 17310.3285
[6 empty] | Residential share of buildings baseline peak (MW) | 37.23% | 8013.7575 | 7580.028 | 7580.028 | 7580.028 | [5 empty] | Residential share of buildings baseline peak (MW) | 37.23% | 8013.7575 | 7580.028 | 7134.3849 | 7134.3849
[6 empty] | Sum of Buildings(Residential) Incremental Peak (MW) | Residential | 0 | 8724.1029 | 26246.9459 | 30336.7646 | [5 empty] | Sum of Buildings(Residential) Incremental Peak (MW) | Residential | 0 | 5577.321 | 8667.2388 | 10076.4767
[6 empty] | Total Residential electric peak (MW) | Total | 8013.7575 | 16304.1309 | 33826.9739 | 37916.7926 | [5 empty] | Total Residential electric peak (MW) | Total | 8013.7575 | 13157.349 | 15801.6237 | 17210.8616
[6 empty] | Commercial share of buildings baseline peak (MW) | 35.77% | 7699.4925 | 7282.772 | 7282.772 | 7282.772 | [5 empty] | Commercial share of buildings baseline peak (MW) | 35.77% | 7699.4925 | 7282.772 | 6854.6051 | 6854.6051
[6 empty] | Sum of Buildings(Commercial) Incremental Peak (MW) | Commercial | 0 | 5094.5977 | 11138.1126 | 14530.8905 | [5 empty] | Sum of Buildings(Commercial) Incremental Peak (MW) | Commercial | 0 | 3949.5348 | 5838.7634 | 7233.8518
[6 empty] | Total Commercial electric peak (MW) | Total | 7699.4925 | 12377.3697 | 18420.8846 | 21813.6625 | [5 empty] | Total Commercial electric peak (MW) | Total | 7699.4925 | 11232.3068 | 12693.3685 | 14088.4569
| Tbl_Electrification_Hourly_Demand | [10 empty] | Tbl_Diversified_Hourly_Demand
| DemandSector | DemandSubSector | EnergyCarrier | Season | SubRegion | Timestep | Loadshape | 2020 | 2030 | 2040 | 2050 | DemandSector | DemandSubSector | EnergyCarrier | Season | SubRegion | Timestep | Loadshape | 2020 | 2030 | 2040 | 2050
| Buildings | Residential | Electricity | Winter Peak | Ontario | 1 |  | 0 | 7190.6618 | 21649.8539 | 25021.8479 | Buildings | Residential | Electricity | Winter Peak | Ontario | 1 |  | 0 | 4629.0313 | 8667.2388 | 10076.4767
| Buildings | Residential | Electricity | Winter Peak | Ontario | 2 |  | 0 | 7385.7035 | 22234.6004 | 25697.8982 | Buildings | Residential | Electricity | Winter Peak | Ontario | 2 |  | 0 | 4749.71 | 8892.6051 | 10336.124
| Buildings | Residential | Electricity | Winter Peak | Ontario | 3 |  | 0 | 7500.1827 | 22577.8696 | 26094.7613 | Buildings | Residential | Electricity | Winter Peak | Ontario | 3 |  | 0 | 4820.6472 | 9025.0929 | 10488.818
| Buildings | Residential | Electricity | Winter Peak | Ontario | 4 |  | 0 | 7650.6035 | 23028.9584 | 26616.2733 | Buildings | Residential | Electricity | Winter Peak | Ontario | 4 |  | 0 | 4913.9493 | 9199.3628 | 10689.7136
| Buildings | Residential | Electricity | Winter Peak | Ontario | 5 |  | 0 | 8075.3781 | 24302.5488 | 28088.7168 | Buildings | Residential | Electricity | Winter Peak | Ontario | 5 |  | 0 | 5176.9496 | 9690.5358 | 11255.6902
| Buildings | Residential | Electricity | Winter Peak | Ontario | 6 |  | 0 | 8765.9296 | 26372.2856 | 30481.6806 | Buildings | Residential | Electricity | Winter Peak | Ontario | 6 |  | 0 | 5603.0842 | 10486.1962 | 12171.8089
| Buildings | Residential | Electricity | Winter Peak | Ontario | 7 |  | 0 | 8599.55 | 25873.6879 | 29905.2105 | Buildings | Residential | Electricity | Winter Peak | Ontario | 7 |  | 0 | 5500.5671 | 10294.8001 | 11951.5148
| Buildings | Residential | Electricity | Winter Peak | Ontario | 8 |  | 0 | 8724.1029 | 26246.9459 | 30336.7646 | Buildings | Residential | Electricity | Winter Peak | Ontario | 8 |  | 0 | 5577.321 | 10438.0984 | 12116.4535
| Buildings | Residential | Electricity | Winter Peak | Ontario | 9 |  | 0 | 8314.2225 | 25018.5176 | 28916.488 | Buildings | Residential | Electricity | Winter Peak | Ontario | 9 |  | 0 | 5324.5324 | 9966.1205 | 11573.0948
| Buildings | Residential | Electricity | Winter Peak | Ontario | 10 |  | 0 | 8154.4183 | 24539.4945 | 28362.6618 | Buildings | Residential | Electricity | Winter Peak | Ontario | 10 |  | 0 | 5225.8121 | 9781.7807 | 11360.7933
| Buildings | Residential | Electricity | Winter Peak | Ontario | 11 |  | 0 | 7462.9045 | 22466.0708 | 25965.5094 | Buildings | Residential | Electricity | Winter Peak | Ontario | 11 |  | 0 | 4797.5105 | 8981.8763 | 10438.9915
| Buildings | Residential | Electricity | Winter Peak | Ontario | 12 |  | 0 | 6701.8392 | 20183.9492 | 23327.0889 | Buildings | Residential | Electricity | Winter Peak | Ontario | 12 |  | 0 | 4325.8254 | 8100.9097 | 9423.6206
| Buildings | Residential | Electricity | Winter Peak | Ontario | 13 |  | 0 | 6272.6112 | 18896.2788 | 21838.4341 | Buildings | Residential | Electricity | Winter Peak | Ontario | 13 |  | 0 | 4058.6423 | 7601.7463 | 8847.7174
| Buildings | Residential | Electricity | Winter Peak | Ontario | 14 |  | 0 | 5763.3912 | 17368.0066 | 20071.6813 | Buildings | Residential | Electricity | Winter Peak | Ontario | 14 |  | 0 | 3740.4356 | 7007.105 | 8161.0407
| Buildings | Residential | Electricity | Winter Peak | Ontario | 15 |  | 0 | 5567.6468 | 16780.3459 | 19392.3363 | Buildings | Residential | Electricity | Winter Peak | Ontario | 15 |  | 0 | 3617.7398 | 6777.7732 | 7896.0258
| Buildings | Residential | Electricity | Winter Peak | Ontario | 16 |  | 0 | 5306.0382 | 15994.9641 | 18484.4212 | Buildings | Residential | Electricity | Winter Peak | Ontario | 16 |  | 0 | 3453.7896 | 6471.3364 | 7541.9238
| Buildings | Residential | Electricity | Winter Peak | Ontario | 17 |  | 0 | 5111.5521 | 15411.0492 | 17809.4093 | Buildings | Residential | Electricity | Winter Peak | Ontario | 17 |  | 0 | 3331.8203 | 6243.3549 | 7278.4384
| Buildings | Residential | Electricity | Winter Peak | Ontario | 18 |  | 0 | 5632.4096 | 16974.7879 | 19617.1132 | Buildings | Residential | Electricity | Winter Peak | Ontario | 18 |  | 0 | 3658.3581 | 6853.6963 | 7983.7742
| Buildings | Residential | Electricity | Winter Peak | Ontario | 19 |  | 0 | 5829.6217 | 17566.8181 | 20301.5128 | Buildings | Residential | Electricity | Winter Peak | Ontario | 19 |  | 0 | 3781.9014 | 7084.6031 | 8250.5731
| Buildings | Residential | Electricity | Winter Peak | Ontario | 20 |  | 0 | 5829.6217 | 17566.8181 | 20301.5128 | Buildings | Residential | Electricity | Winter Peak | Ontario | 20 |  | 0 | 3781.9014 | 7084.6031 | 8250.5731
| Buildings | Residential | Electricity | Winter Peak | Ontario | 21 |  | 0 | 5862.9245 | 17666.7821 | 20417.0743 | Buildings | Residential | Electricity | Winter Peak | Ontario | 21 |  | 0 | 3802.7426 | 7123.5535 | 8295.5673
| Buildings | Residential | Electricity | Winter Peak | Ontario | 22 |  | 0 | 6031.3442 | 18172.2758 | 21001.4452 | Buildings | Residential | Electricity | Winter Peak | Ontario | 22 |  | 0 | 3908.0492 | 7320.3504 | 8522.8547
| Buildings | Residential | Electricity | Winter Peak | Ontario | 23 |  | 0 | 7190.6618 | 21649.8539 | 25021.8479 | Buildings | Residential | Electricity | Winter Peak | Ontario | 23 |  | 0 | 4629.0313 | 8667.2388 | 10076.4767
| Buildings | Residential | Electricity | Winter Peak | Ontario | 24 |  | 0 | 6961.8468 | 20963.7425 | 24228.6157 | Buildings | Residential | Electricity | Winter Peak | Ontario | 24 |  | 0 | 4487.2397 | 8402.4171 | 9771.2632
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 1 |  | 0 | 4199.1171 | 9187.2978 | 11985.119 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 1 |  | 0 | 3278.0111 | 5838.7634 | 7233.8518
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 2 |  | 0 | 4313.0152 | 9435.4399 | 12308.9377 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 2 |  | 0 | 3363.4687 | 5990.5835 | 7420.2513
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 3 |  | 0 | 4379.8674 | 9581.1091 | 12499.0296 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 3 |  | 0 | 3413.7023 | 6079.8351 | 7529.8696
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 4 |  | 0 | 4467.7084 | 9772.5324 | 12748.8267 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 4 |  | 0 | 3479.7735 | 6197.2336 | 7674.0915
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 5 |  | 0 | 4715.7631 | 10312.9913 | 13454.1067 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 5 |  | 0 | 3666.015 | 6528.1167 | 8080.4032
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 6 |  | 0 | 5119.0232 | 11191.3015 | 14600.3033 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 6 |  | 0 | 3967.7787 | 7064.1205 | 8738.0802
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 7 |  | 0 | 5021.8629 | 10979.7174 | 14324.1821 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 7 |  | 0 | 3895.1821 | 6935.1848 | 8579.9322
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 8 |  | 0 | 5094.5977 | 11138.1126 | 14530.8905 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 8 |  | 0 | 3949.5348 | 7031.719 | 8698.3409
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 9 |  | 0 | 4855.2407 | 10616.8186 | 13850.5977 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 9 |  | 0 | 3770.5246 | 6713.7668 | 8308.2664
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 10 |  | 0 | 4761.9201 | 10413.5412 | 13585.3226 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 10 |  | 0 | 3700.6166 | 6589.5847 | 8155.8562
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 11 |  | 0 | 4358.0981 | 9533.6664 | 12437.1197 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 11 |  | 0 | 3397.3182 | 6050.7218 | 7494.0994
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 12 |  | 0 | 3913.6603 | 8565.2288 | 11173.3528 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 12 |  | 0 | 3063.2983 | 5457.2508 | 6765.1697
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 13 |  | 0 | 3663.0049 | 8018.7951 | 10460.3078 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 13 |  | 0 | 2874.0947 | 5120.9848 | 6351.7317
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 14 |  | 0 | 3365.6366 | 7370.2599 | 9614.0577 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 14 |  | 0 | 2648.7592 | 4720.3994 | 5858.77
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 15 |  | 0 | 3251.3281 | 7120.8811 | 9288.6608 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 15 |  | 0 | 2561.8731 | 4565.908 | 5668.5171
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 16 |  | 0 | 3098.557 | 6787.5977 | 8853.782 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 16 |  | 0 | 2445.7732 | 4359.474 | 5414.3091
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 17 |  | 0 | 2984.9834 | 6539.8085 | 8530.4606 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 17 |  | 0 | 2359.4016 | 4205.8923 | 5225.1542
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 18 |  | 0 | 3289.1475 | 7203.3942 | 9396.3258 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 18 |  | 0 | 2590.6367 | 4617.0542 | 5731.5112
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 19 |  | 0 | 3404.3131 | 7454.6272 | 9724.1438 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 19 |  | 0 | 2678.1229 | 4772.6067 | 5923.0449
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 20 |  | 0 | 3404.3131 | 7454.6272 | 9724.1438 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 20 |  | 0 | 2678.1229 | 4772.6067 | 5923.0449
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 21 |  | 0 | 3423.7608 | 7497.0478 | 9779.4961 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 21 |  | 0 | 2692.8814 | 4798.8459 | 5955.3459
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 22 |  | 0 | 3522.1126 | 7711.5583 | 10059.4017 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 22 |  | 0 | 2767.4534 | 4931.42 | 6118.5144
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 23 |  | 0 | 4199.1171 | 9187.2978 | 11985.119 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 23 |  | 0 | 3278.0111 | 5838.7634 | 7233.8518
| Buildings | Commercial | Electricity | Winter Peak | Ontario | 24 |  | 0 | 4065.4964 | 8896.1407 | 11605.1717 | Buildings | Commercial | Electricity | Winter Peak | Ontario | 24 |  | 0 | 3177.6025 | 5660.364 | 7014.7406
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 1 |  | 17163 | 17163 | 17163 | 17163 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 1 |  | 17163 | 17163 | 17163 | 17163
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 2 |  | 17017 | 17017 | 17017 | 17017 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 2 |  | 17017 | 17017 | 17017 | 17017
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 3 |  | 16744 | 16744 | 16744 | 16744 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 3 |  | 16744 | 16744 | 16744 | 16744
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 4 |  | 16722 | 16722 | 16722 | 16722 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 4 |  | 16722 | 16722 | 16722 | 16722
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 5 |  | 16969 | 16969 | 16969 | 16969 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 5 |  | 16969 | 16969 | 16969 | 16969
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 6 |  | 17590 | 17590 | 17590 | 17590 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 6 |  | 17590 | 17590 | 17590 | 17590
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 7 |  | 18773 | 18773 | 18773 | 18773 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 7 |  | 18773 | 18773 | 18773 | 18773
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 8 |  | 20360 | 20360 | 20360 | 20360 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 8 |  | 20360 | 20360 | 20360 | 20360
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 9 |  | 20534 | 20534 | 20534 | 20534 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 9 |  | 20534 | 20534 | 20534 | 20534
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 10 |  | 20369 | 20369 | 20369 | 20369 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 10 |  | 20369 | 20369 | 20369 | 20369
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 11 |  | 20364 | 20364 | 20364 | 20364 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 11 |  | 20364 | 20364 | 20364 | 20364
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 12 |  | 20304 | 20304 | 20304 | 20304 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 12 |  | 20304 | 20304 | 20304 | 20304
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 13 |  | 20103 | 20103 | 20103 | 20103 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 13 |  | 20103 | 20103 | 20103 | 20103
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 14 |  | 19838 | 19838 | 19838 | 19838 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 14 |  | 19838 | 19838 | 19838 | 19838
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 15 |  | 19533 | 19533 | 19533 | 19533 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 15 |  | 19533 | 19533 | 19533 | 19533
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 16 |  | 19584 | 19584 | 19584 | 19584 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 16 |  | 19584 | 19584 | 19584 | 19584
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 17 |  | 20356 | 20356 | 20356 | 20356 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 17 |  | 20356 | 20356 | 20356 | 20356
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 18 |  | 21525 | 21525 | 21525 | 21525 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 18 |  | 21525 | 21525 | 21525 | 21525
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 19 |  | 21274 | 21274 | 21274 | 21274 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 19 |  | 21274 | 21274 | 21274 | 21274
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 20 |  | 20875 | 20875 | 20875 | 20875 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 20 |  | 20875 | 20875 | 20875 | 20875
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 21 |  | 20574 | 20574 | 20574 | 20574 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 21 |  | 20574 | 20574 | 20574 | 20574
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 22 |  | 20176 | 20176 | 20176 | 20176 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 22 |  | 20176 | 20176 | 20176 | 20176
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 23 |  | 19163 | 19163 | 19163 | 19163 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 23 |  | 19163 | 19163 | 19163 | 19163
| Baseline | Baseline | Electricity | Winter Peak | Ontario | 24 |  | 18090 | 18090 | 18090 | 18090 | Baseline | Baseline | Electricity | Winter Peak | Ontario | 24 |  | 18090 | 18090 | 18090 | 18090